## Info
Document description
This model Energy at Risk model has been developed to calculated Energy at Risk (EaR) in terms of Expected Unsureved Energy (EUE) and the cost of EUE. The modelling inputs, calculation steps and outputs are described in the 'Modelling Steps' tab. Further detail on EaR/EUE calculations can be found in AusNet's Network Planning Policy and Guidelines.
Tab # | Tab Name | Description | Source/ Inputs
0.1 | Modelling Steps | E@R model process flowchart and underlying equations | N/A
0.2 | Modelling Example & QA | Example E@R model calculations and data flow; also used to validate base case | N/A
0.3 | QA | Quality assurance and data validation | Entire workbook
1.1 | Output for AusNet's NPV Model | Aggregates Supply Risk ($M) and EUE (MWh) for input into AusNet’s NPV model | Summary tab
2.1 | Key Model Assumptions & Inputs | E@R model inputs and asset selection | Augmentation plans from RPs/EPCs, Embedded Generation DB, Demand Management DB
2.2 | Tx PoF | Transformer Probabilities of Failure | Provided by Asset Management Team
2.3 | Customer No. and Volume per Feeder | Customer consumption data | Provided by Finance Team
2.4 | AER VCR Rates (2024) | AER 2024 VCR rates | AER VCR Factsheet
2.5 | Forecast - Summer | Summer Forecast Data | Extract from Forecasting Toolbox
2.6 | Forecast- Winter | Winter Forecast Data | Extract from Forecasting Toolbox
2.7 | Ratings | Station Rating Data | AMS 20-101 / Provided by Asset mangement Team
2.8 | FT (Forecast & Transfers) | Forecast, transfer & PF inputs | Forecast Summer , Forecast Winter , NP Transfer Sheet, PF = avg. max demand PF across stations
2.9 | Load Duration Curves | Load duration curve data | LDC Tool; data sourced from PI SCADA Historian and AEMO
3.1 | Capacity N | Option N capacity calculated | FT Sheet, Ratings & Key Model Assumptions
3.2 | Capacity N-1 | Option N-1 capacity calculated | FT Sheet, Ratings & Key Model Assumptions
3.3 | Capacity N-1 | Option N-2 capacity calculated | FT Sheet, Ratings & Key Model Assumptions
3.4 | Demand | Calculates maximum demand | FT Sheet & Key Model Assumptions
3.5 | MD Weighted LDC | Maps maximum demand forecast to load duration curve | Demand Sheet & Load Duration Curve Sheet
3.6 | Locational VCR | Calculates tailored VCR by location using feeder energy mix and AER rates | AER VCR Rates (2024) & Customer No./Volume per Feeder
3.7 | E@R N | Calculates N EUE using capacity and demand inputs | MD Weighted LDC & Capacity N
3.8 | E@R N-1 | Calculates N-1 EUE using capacity and demand inputs | MD Weighted LDC & Capacity N-1
3.9 | E@R N-2 | Calculates N-2 EUE using capacity and demand inputs | MD Weighted LDC & Capacity N-2
4 | POF N,N-1 & N-2 Risk | Calculates Station N , N-1 & N-2 PoF's from Tx PoF Data & MTTR | TX PoF & Key Model Assumptions
4.1 | Summary | Collates weighted EUE and calculates supply risk | E@R & Locational VCR
Revision table
Date | Editted by | Change
2025-10-14 | HT | Draft Version 2.1
2025-10-20 | HT | Version 2.2
2025-11-10 | HT | Version 2.3 Example Page Update and General Refinements

## Modelling Steps
Eq1. Locational VCR |  | Data Inputs |  |  | Calculations |  |  |  |  | Outputs
|  |  | Customer No. and Vol per Feeder |  | Eq1.
Locational VCR
Eq2. Maximum Demand
AER Latetst VCR Rates
Eq3. Options & Do nothing Capacity
Eq6. & Eq7.
Load Forecast
[9 empty] | Summary Sheet | Output for AusNet's NPV Model
Eq4. Help Sheet | Re Name Forecasted LDC add Forecast MD to eq
Transfer Capacity
Eq2.
Eq5. Energy at Risk ( Option/ Do Nothing Capacity) |  |  |  |  | Options & Do Nothing Max Demand
Embeded Generation
Eq6. Weighted Expected Unserved Energy
[6 empty] | Eq.4 | Eq.5
Demand Mangement Capacity
[6 empty] | Forecasted LDC |  | Energy @ Risk Sheet
Eq7. Supply Risk
Load Duration Curves
|  |  | Asset Ratings |  | Eq3.
Options & Do Nothing Capacity
Planned & Proposed Works

## Modelling Steps Example & QA
End of Sheet
Data Inputs |  |  | Calculations | [12 empty] | Outputs
AER VCR Rates(2024 |  |  | Locational (Tailored VCR)
Category | Rate |  | Base case |  | Energy Usage (CY 2024 kWh) | Energy Usage (CY 2024 %) | Tailored VCR
Dec 24 AER VCR ($/kWh) - Res | 49.23 |  | Dec 24 AER VCR ($/kWh) - Res | 49.23 | 67934749.1441 | 34.06% | 16.7657
Dec 24 AER VCR ($/kWh) - Com | 34.39 |  | Dec 24 AER VCR ($/kWh) - Com | 34.39 | 101368150.4504 | 50.82% | 17.4756
Dec 24 AER VCR ($/kWh) - Ind | 33.49 |  | Dec 24 AER VCR ($/kWh) - Ind | 33.49 | 17726336.2671 | 8.886% | 2.976
Dec 24 AER VCR ($/kWh) - Agr | 22.25 |  | Dec 24 AER VCR ($/kWh) - Agr | 22.25 | 12451243.5083 | 6.242% | 1.3888
[5 empty] | 199480479.3698 |  | 38.6062
Customer No. and Vol per Feeder | [6 empty] | 38606.1513 | [8 empty] | Summary |  | Outputs for NPV model
COMMERCIAL | 101368150.4504 | [14 empty] | Year | 2031 | Year | 2031
[16 empty] | E@R MWh | 1.8981 | E@R MWh | 1.8981
RESIDENTL | 67934749.1441 | [14 empty] | cost of EUE ($) | 73276.699 | cost of EUE ($M) | 0.073277
FARM | 12451243.5083
INDUSTRIAL | 17726336.2671
Forecast (FCT)
Forecast | 2031
Summer POE50 | 67.5138
Summer POE10 | 73.0705
Winter POE50 | 65.9652
Winter POE10 | 68.6243
Transfer Capacity |  |  | Option Max Demand |  |  |  | MD Weighted LDC |  |  | E@R (N) |  | E@R (N-1) |  | E@R (N-2)
Year | 2031 |  | Forecast | 2031 |  |  | % of MD | Summer - AD - Hours | FY31 | % of MD | FY31 | % of MD | FY31 | % of MD | FY31
Capacity | 1.58 |  | Summer POE50 | 65.9338 |  |  | 100% | 0 | 65.9338 | 100% |  | 100% |  | 100%
|  |  | Summer POE10 | 71.4905 |  |  | 99% | 0 | 65.2745 | 99% |  | 99% | 0 | 99% | 0
Embedded Generation |  |  | Winter POE50 | 64.3852 |  |  | 98% | 0 | 64.6151 | 98% |  | 98% | 0 | 98% | 0
|  |  | Winter POE10 | 67.0443 |  |  | 97% | 0.37816 | 63.9558 | 97% |  | 97% | 7.2931 | 97% | 24.3105
Year | 2031 | [5 empty] | 95% | 2.269 | 62.6371 | 95% |  | 95% | 34.5953 | 95% | 119.6823
Capacity | 0 | [5 empty] | 90% | 5.6725 | 59.3404 | 90% |  | 90% | 54.4175 | 90% | 207.574
[7 empty] | 85% | 15.8829 | 56.0437 | 85% |  | 85% | 129.5917 | 85% | 589.0613
Demand Mangement | [6 empty] | 80% | 31.0095 | 52.747 | 80% |  | 80% | 142.1201 | 80% | 822.8158
[7 empty] | 75% | 72.9857 | 49.4504 | 75% |  | 75% | 256.0006 | 75% | 2144.9312
Year | 2031 | [5 empty] | 70% | 150.5094 | 46.1537 | 70% |  | 70% | 217.2224 | 70% | 3705.7879
Capacity | 0 | [5 empty] | 65% | 359.6342 | 42.857 | 65% |  | 65% | 42.2143 | 65% | 9307.1689
[7 empty] | 60% | 689.7717 | 39.5603 | 60% |  | 60% |  | 60% | 13604.5115
LDC | [6 empty] | 55% | 1095.5419 | 36.2636 | 55% |  | 55% |  | 55% | 15383.539
[7 empty] | 50% | 1666.1918 | 32.9669 | 50% |  | 50% |  | 50% | 19753.1897
% of MD | Summer - AD - Duration % | Summer - AD - Hours |  |  |  |  | 45% | 2506.0947 | 29.6702 | 45% |  | 45% |  | 45% | 26304.5489
100% | 0% | 0 |  |  |  |  | 40% | 3164.4787 | 26.3735 | 40% |  | 40% |  | 40% | 18449.1513
99% | 0% | 0 |  |  |  |  | 35% | 3551.3408 | 23.0768 | 35% |  | 35% |  | 35% | 9565.2339
98% | 0% | 0 |  |  |  |  | 30% | 3758.953 | 19.7801 | 30% |  | 30% |  | 30% | 4448.8155
97% | 0.00861% | 0.37816 |  |  |  |  | 25% | 3926.4798 | 16.4835 | 25% |  | 25% |  | 25% | 3037.5617
95% | 0.05166% | 2.269 |  |  |  |  | 20% | 4050.5177 | 13.1868 | 20% |  | 20% |  | 20% | 1840.1154
90% | 0.1292% | 5.6725 |  |  |  |  | 15% | 4152.622 | 9.8901 | 15% |  | 15% |  | 15% | 1178.1226
85% | 0.3616% | 15.8829 |  |  |  |  | 10% | 4248.2976 | 6.5934 | 10% |  | 10% |  | 10% | 788.5318
80% | 0.706% | 31.0095 |  |  |  |  | 5% | 4361.7469 | 3.2967 | 5% |  | 5% |  | 5% | 561.0108
75% | 1.662% | 72.9857 |  |  |  |  | 9.992e-14% | 4391.6218 | 6.5881e-14 | 9.992e-14% |  | 9.992e-14% |  | 9.992e-14% | 49.2443
70% | 3.427% | 150.5094 | [7 empty] | Total E@R | 0 | Total E@R | 883.4549 | Total E@R | 131884.9083
65% | 8.188% | 359.6342 | [7 empty] | Total WE@R | 0 | Total WE@R | 0.27342 | Total WE@R | 0.005342
60% | 15.71% | 689.7717 |  |  |  |  | MD Weighted LDC
55% | 24.94% | 1095.5419
50% | 37.94% | 1666.1918 |  |  |  |  | % of MD | Summer - MD - Hours | FY31
45% | 57.06% | 2506.0947 |  |  |  |  | 100% | 0 | 71.4905 | E@R (N) |  | E@R (N-1) |  | E@R (N-2)
40% | 72.05% | 3164.4787 |  |  |  |  | 99% | 1.5127 | 70.7756
35% | 80.86% | 3551.3408 |  |  |  |  | 98% | 2.269 | 70.0607 | % of MD | FY31 | % of MD | FY31 | % of MD | FY31
30% | 85.59% | 3758.953 |  |  |  |  | 97% | 3.7816 | 69.3458 | 100% |  | 100% |  | 100%
25% | 89.4% | 3926.4798 |  |  |  |  | 95% | 6.0506 | 67.916 | 99% |  | 99% | 39.5304 | 99% | 107.6
20% | 92.22% | 4050.5177 |  |  |  |  | 90% | 16.2611 | 64.3415 | 98% |  | 98% | 19.2245 | 98% | 53.2593
15% | 94.55% | 4152.622 |  |  |  |  | 85% | 26.4715 | 60.767 | 97% |  | 97% | 37.3676 | 97% | 105.4372
10% | 96.73% | 4248.2976 |  |  |  |  | 80% | 34.0348 | 57.1924 | 95% |  | 95% | 53.6182 | 95% | 155.7226
5% | 99.31% | 4361.7469 |  |  |  |  | 75% | 48.405 | 53.6179 | 90% |  | 90% | 215.7337 | 90% | 675.2033
9.992e-14% | 99.99% | 4391.6218 |  |  |  |  | 70% | 76.3892 | 50.0434 | 85% |  | 85% | 179.2362 | 85% | 638.7059
[7 empty] | 65% | 114.2056 | 46.4689 | 80% |  | 80% | 105.7324 | 80% | 446.0803
[7 empty] | 60% | 178.1154 | 42.8943 | 75% |  | 75% | 149.5248 | 75% | 796.1857
[7 empty] | 55% | 311.6074 | 39.3198 | 70% |  | 70% | 191.1497 | 70% | 1450.4368
LDC | [6 empty] | 50% | 636.0723 | 35.7453 | 65% |  | 65% | 123.1346 | 65% | 1824.8739
[7 empty] | 45% | 1179.4944 | 32.1707 | 60% |  | 60% | 19.2874 | 60% | 2855.5897
% of MD | Summer - MD - Duration % | Summer - MD - Hours |  |  |  |  | 40% | 1808.3816 | 28.5962 | 55% |  | 55% |  | 55% | 5487.4633
100% | 0% | 0 |  |  |  |  | 35% | 2779.1293 | 25.0217 | 50% |  | 50% |  | 50% | 12177.9916
99% | 0.03444% | 1.5127 |  |  |  |  | 30% | 3814.165 | 21.4472 | 45% |  | 45% |  | 45% | 18453.5301
98% | 0.05166% | 2.269 |  |  |  |  | 25% | 4166.9923 | 17.8726 | 40% |  | 40% |  | 40% | 19107.7811
97% | 0.0861% | 3.7816 |  |  |  |  | 20% | 4282.7105 | 14.2981 | 35% |  | 35% |  | 35% | 26024.729
95% | 0.1378% | 6.0506 |  |  |  |  | 15% | 4364.7722 | 10.7236 | 30% |  | 30% |  | 30% | 24048.4582
90% | 0.3702% | 16.2611 |  |  |  |  | 10% | 4391.6218 | 7.1491 | 25% |  | 25% |  | 25% | 6936.5483
85% | 0.6027% | 26.4715 |  |  |  |  | 5% | 4391.6218 | 3.5745 | 20% |  | 20% |  | 20% | 1861.3713
80% | 0.7749% | 34.0348 |  |  |  |  | 9.992e-14% | 4391.6218 | 7.1433e-14 | 15% |  | 15% |  | 15% | 1026.6605
75% | 1.102% | 48.405 | [7 empty] | 10% |  | 10% |  | 10% | 239.9371
70% | 1.739% | 76.3892 | [7 empty] | 5% |  | 5% |  | 5% | 0
65% | 2.6% | 114.2056 | [7 empty] | 9.992e-14% |  | 9.992e-14% |  | 9.992e-14% | 0
60% | 4.055% | 178.1154 | [7 empty] | Total E@R | 0 | Total E@R | 1133.5396 | Total E@R | 124473.5651
55% | 7.095% | 311.6074 |  |  |  |  | MD Weighted LDC |  |  | Total WE@R | 0 | Total WE@R | 0.15035 | Total WE@R | 0.0021608
50% | 14.48% | 636.0723
45% | 26.86% | 1179.4944 |  |  |  |  | % of MD | Winter - AD - Hours | FY31
40% | 41.17% | 1808.3816 |  |  |  |  | 100% | 0 | 64.3852
35% | 63.28% | 2779.1293 |  |  |  |  | 99% | 1.486 | 63.7413 | E@R (N) |  | E@R (N-1) |  | E@R (N-2)
30% | 86.84% | 3814.165 |  |  |  |  | 98% | 3.2692 | 63.0975
25% | 94.88% | 4166.9923 |  |  |  |  | 97% | 6.8356 | 62.4536 | % of MD | FY31 | % of MD | FY31 | % of MD | FY31
20% | 97.51% | 4282.7105 |  |  |  |  | 95% | 17.5347 | 61.1659 | 100% |  | 100% |  | 100%
15% | 99.38% | 4364.7722 |  |  |  |  | 90% | 78.7576 | 57.9467 | 99% |  | 99% | 22.2353 | 99% | 95.1975
10% | 99.99% | 4391.6218 |  |  |  |  | 85% | 236.8672 | 54.7274 | 98% |  | 98% | 25.5342 | 98% | 113.0889
5% | 99.99% | 4391.6218 |  |  |  |  | 80% | 497.5104 | 51.5081 | 97% |  | 97% | 48.7723 | 97% | 223.8816
9.992e-14% | 99.99% | 4391.6218 |  |  |  |  | 75% | 803.6248 | 48.2889 | 95% |  | 95% | 135.9838 | 95% | 661.3119
[7 empty] | 70% | 1155.2107 | 45.0696 | 90% |  | 90% | 640.1647 | 90% | 3646.209
[7 empty] | 65% | 1553.1596 | 41.8504 | 85% |  | 85% | 1144.2449 | 85% | 8907.4274
[7 empty] | 60% | 2026.2996 | 38.6311 | 80% |  | 80% | 1047.2057 | 80% | 13844.7828
LDC | [6 empty] | 55% | 2598.4068 | 35.4119 | 75% |  | 75% | 275.7172 | 75% | 15274.6593
[7 empty] | 50% | 3233.5201 | 32.1926 | 70% |  | 70% |  | 70% | 16411.7675
% of MD | Winter - AD (P50) - Duration % | Winter - AD - Hours |  |  |  |  | 45% | 3775.313 | 28.9733 | 65% |  | 65% |  | 65% | 17294.8562
100% | 0% | 0 |  |  |  |  | 40% | 4072.8088 | 25.7541 | 60% |  | 60% |  | 60% | 19039.5064
99% | 0.03383% | 1.486 |  |  |  |  | 35% | 4198.821 | 22.5348 | 55% |  | 55% |  | 55% | 21180.255
98% | 0.07443% | 3.2692 |  |  |  |  | 30% | 4271.3374 | 19.3156 | 50% |  | 50% |  | 50% | 21468.2395
97% | 0.1556% | 6.8356 |  |  |  |  | 25% | 4321.8611 | 16.0963 | 45% |  | 45% |  | 45% | 16569.6328
95% | 0.3992% | 17.5347 |  |  |  |  | 20% | 4353.067 | 12.877 | 40% |  | 40% |  | 40% | 8140.5849
90% | 1.793% | 78.7576 |  |  |  |  | 15% | 4369.4129 | 9.6578 | 35% |  | 35% |  | 35% | 3042.494
85% | 5.393% | 236.8672 |  |  |  |  | 10% | 4378.6261 | 6.4385 | 30% |  | 30% |  | 30% | 1517.42
80% | 11.33% | 497.5104 |  |  |  |  | 5% | 4391.7028 | 3.2193 | 25% |  | 25% |  | 25% | 894.5698
75% | 18.3% | 803.6248 |  |  |  |  | 9.992e-14% | 4391.7028 | 6.4334e-14 | 20% |  | 20% |  | 20% | 452.0687
70% | 26.3% | 1155.2107 | [7 empty] | 15% |  | 15% |  | 15% | 184.1761
65% | 35.36% | 1553.1596 | [7 empty] | 10% |  | 10% |  | 10% | 74.1488
60% | 46.14% | 2026.2996 | [7 empty] | 5% |  | 5% |  | 5% | 63.1461
55% | 59.16% | 2598.4068 | [7 empty] | 9.992e-14% |  | 9.992e-14% |  | 9.992e-14% | 0
50% | 73.62% | 3233.5201 |  |  |  |  | MD Weighted LDC |  |  | Total E@R | 0 | Total E@R | 3339.858 | Total E@R | 169099.4242
45% | 85.96% | 3775.313 | [7 empty] | Total WE@R | 0 | Total WE@R | 0.8782 | Total WE@R | 0.0058193
40% | 92.73% | 4072.8088 |  |  |  |  | % of MD | Winter - MD - Hours | FY31
35% | 95.6% | 4198.821 |  |  |  |  | 100% | 0 | 67.0443 | E@R (N) |  | E@R (N) |  | E@R (N)
30% | 97.25% | 4271.3374 |  |  |  |  | 99% | 1.486 | 66.3739
25% | 98.4% | 4321.8611 |  |  |  |  | 98% | 3.2692 | 65.7034 | % of MD | FY31 | % of MD | FY31 | % of MD | FY31
20% | 99.11% | 4353.067 |  |  |  |  | 97% | 6.8356 | 65.033 | 100% |  | 100% |  | 100%
15% | 99.49% | 4369.4129 |  |  |  |  | 95% | 17.5347 | 63.6921 | 99% |  | 99% | 26.167 | 99% | 99.1293
10% | 99.7% | 4378.6261 |  |  |  |  | 90% | 78.7576 | 60.3399 | 98% |  | 98% | 30.2049 | 98% | 117.7596
5% | 99.99% | 4391.7028 |  |  |  |  | 85% | 236.8672 | 56.9877 | 97% |  | 97% | 58.0187 | 97% | 233.1281
9.992e-14% | 99.99% | 4391.7028 |  |  |  |  | 80% | 497.5104 | 53.6355 | 95% |  | 95% | 163.2964 | 95% | 688.6245
[7 empty] | 75% | 803.6248 | 50.2832 | 90% |  | 90% | 790.7554 | 90% | 3796.7998
[7 empty] | 70% | 1155.2107 | 46.931 | 85% |  | 85% | 1512.1274 | 85% | 9275.3098
[7 empty] | 65% | 1553.1596 | 43.5788 | 80% |  | 80% | 1619.0041 | 80% | 14416.5812
LDC | [6 empty] | 60% | 2026.2996 | 40.2266 | 75% |  | 75% | 875.2908 | 75% | 15905.5125
[7 empty] | 55% | 2598.4068 | 36.8744 | 70% |  | 70% | 73.4213 | 70% | 17089.584
% of MD | Winter - MD (P10) - Duration % | Winter - MD - Hours |  |  |  |  | 50% | 3233.5201 | 33.5222 | 65% |  | 65% |  | 65% | 18009.1448
100% | 0% | 0 |  |  |  |  | 45% | 3775.313 | 30.1699 | 60% |  | 60% |  | 60% | 19825.8502
99% | 0.03383% | 1.486 |  |  |  |  | 40% | 4072.8088 | 26.8177 | 55% |  | 55% |  | 55% | 22055.013
98% | 0.07443% | 3.2692 |  |  |  |  | 35% | 4198.821 | 23.4655 | 50% |  | 50% |  | 50% | 22354.8915
97% | 0.1556% | 6.8356 |  |  |  |  | 30% | 4271.3374 | 20.1133 | 45% |  | 45% |  | 45% | 17253.9692
95% | 0.3992% | 17.5347 |  |  |  |  | 25% | 4321.8611 | 16.7611 | 40% |  | 40% |  | 40% | 8476.7963
90% | 1.793% | 78.7576 |  |  |  |  | 20% | 4353.067 | 13.4089 | 35% |  | 35% |  | 35% | 3168.1509
85% | 5.393% | 236.8672 |  |  |  |  | 15% | 4369.4129 | 10.0566 | 30% |  | 30% |  | 30% | 1580.0904
80% | 11.33% | 497.5104 |  |  |  |  | 10% | 4378.6261 | 6.7044 | 25% |  | 25% |  | 25% | 931.5161
75% | 18.3% | 803.6248 |  |  |  |  | 5% | 4391.7028 | 3.3522 | 20% |  | 20% |  | 20% | 470.7394
70% | 26.3% | 1155.2107 |  |  |  |  | 9.992e-14% | 4391.7028 | 6.6991e-14 | 15% |  | 15% |  | 15% | 191.7827
65% | 35.36% | 1553.1596 | [7 empty] | 10% |  | 10% |  | 10% | 77.2112
60% | 46.14% | 2026.2996 | [7 empty] | 5% |  | 5% |  | 5% | 65.7541
55% | 59.16% | 2598.4068 | [7 empty] | 9.992e-14% |  | 9.992e-14% | 0 | 9.992e-14% | 0
50% | 73.62% | 3233.5201 | [7 empty] | Total E@R | 0 | Total E@R | 5148.2859 | Total E@R | 176083.3386
45% | 85.96% | 3775.313 | [7 empty] | Total WE@R | 0 | Total WE@R | 0.58017 | Total WE@R | 0.002597
40% | 92.73% | 4072.8088
35% | 95.6% | 4198.821
30% | 97.25% | 4271.3374
25% | 98.4% | 4321.8611
20% | 99.11% | 4353.067
15% | 99.49% | 4369.4129
10% | 99.7% | 4378.6261
5% | 99.99% | 4391.7028
9.992e-14% | 99.99% | 4391.7028
Ratings (MVA) |  |  |  | Option Capacity
SCR (N) | 91.9 |  |  | Year | 2031
SCR (N-1) | 45 |  |  | SCR (N) | 91.9
SCR (N-2) | 0 |  |  | SCR (N-1) | 45
WCR (N) | 95.7 |  |  | SCR (N-2) | 0
WCR (N-1) | 49.1 |  |  | WCR (N) | 95.7
WCR (N-2) | 0 |  |  | WCR (N-1) | 49.1
|  |  |  | WCR (N-2) | 0
Planned Works
Year | 2031
Capacity (N) | 0
Capacity (N-1) | 0
Capacity (N-2) | 0
Power Factor
Value | 1
End of Sheet

## QA
Overall Status
Good
Number | Check Name | Status | Info
1 | Forecast | Good | Confirms POE10 forecast is higher than POE50
2 | Option Maximum Demand | Good | Confirms whether transfers, embedded generation, and demand management contribute to demand reduction when present
3 | EUE Base Case | Good | Confirms Do Nothing/Base Case EUE for FY31 is the same as the example / checks model in Modelling Steps Example Sheet
4 | Feeder Consumption | Good | Confirms if aggregated feeder energy consumption by customer category matches with total feeder energy consumption (excluding uncategorised consumption)

## Output for AusNet's NPV model
Involuntary load shedding (NER 5.17.1(c)(4)(ii))
Base Case
Cost
Option 1 - Do Nothing / Base Case | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Cost of EUE ($M) | 0.00013013 | 0.0045354 | 0.015907 | 0.02253 | 0.030537 | 0.04405 | 0.073277 | 0.10689 | 0.16079 | 0.25784 | 0.26283 | 0.26751 | 0.36579 | 0.54793 | 0.51363 | 0.51363 | 0.51363 | 0.51363 | 0.51363 | 0.51363 | 0.51363 | 0.51363 | 0.51363 | 0.51363 | 0.51363 | 0.51363 | 0.51363 | 0.51363 | 0.51363 | 0.51363
Total EUE (MWh) | 0.0033707 | 0.11748 | 0.41204 | 0.58358 | 0.79099 | 1.141 | 1.8981 | 2.7688 | 4.165 | 6.6787 | 6.808 | 6.9292 | 9.4749 | 14.1927 | 13.3044 | 13.3044 | 13.3044 | 13.3044 | 13.3044 | 13.3044 | 13.3044 | 13.3044 | 13.3044 | 13.3044 | 13.3044 | 13.3044 | 13.3044 | 13.3044 | 13.3044 | 13.3044
Residual Values
Option 2 - 1A New PHS ZSS + Four new feeders | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Cost of Avoided EUE ($M) | 0.00013013 | 0.0045354 | 0.015907 | 9.2025e-05 | 0.00014609 | 0.00022602 | 0.00034547 | 0.00050919 | 0.0007361 | 0.0010487 | 0.0013994 | 0.0018424 | 0.0024646 | 0.0033655 | 0.0040864 | 0.0040864 | 0.0040864 | 0.0040864 | 0.0040864 | 0.0040864 | 0.0040864 | 0.0040864 | 0.0040864 | 0.0040864 | 0.0040864 | 0.0040864 | 0.0040864 | 0.0040864 | 0.0040864 | 0.0040864
Total EUE (MWh) | 0.0033707 | 0.11748 | 0.41204 | 0.0023837 | 0.003784 | 0.0058546 | 0.0089485 | 0.013189 | 0.019067 | 0.027165 | 0.036247 | 0.047723 | 0.06384 | 0.087174 | 0.10585 | 0.10585 | 0.10585 | 0.10585 | 0.10585 | 0.10585 | 0.10585 | 0.10585 | 0.10585 | 0.10585 | 0.10585 | 0.10585 | 0.10585 | 0.10585 | 0.10585 | 0.10585
Option 3 - 2A PHM 3rd Tx + Switchroom + Three new feeders + OFR12 New Feeder | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Cost of Avoided EUE ($M) | 0.00013013 | 0.0045354 | 0.015907 | 3.1666e-06 | 5.3194e-06 | 9.1408e-06 | 1.7313e-05 | 2.8909e-05 | 4.9015e-05 | 8.6489e-05 | 0.00010449 | 0.00012388 | 0.00018723 | 0.00030398 | 0.00032875 | 0.00032875 | 0.00032875 | 0.00032875 | 0.00032875 | 0.00032875 | 0.00032875 | 0.00032875 | 0.00032875 | 0.00032875 | 0.00032875 | 0.00032875 | 0.00032875 | 0.00032875 | 0.00032875 | 0.00032875
Total EUE (MWh) | 0.0033707 | 0.11748 | 0.41204 | 8.2023e-05 | 0.00013779 | 0.00023677 | 0.00044845 | 0.00074881 | 0.0012696 | 0.0022403 | 0.0027066 | 0.0032087 | 0.0048497 | 0.0078739 | 0.0085154 | 0.0085154 | 0.0085154 | 0.0085154 | 0.0085154 | 0.0085154 | 0.0085154 | 0.0085154 | 0.0085154 | 0.0085154 | 0.0085154 | 0.0085154 | 0.0085154 | 0.0085154 | 0.0085154 | 0.0085154
Option 4 - 3A OFR 3rd Tx + Switchroom + Three new feeders + OFR12 New Feeder | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Cost of Avoided EUE ($M) | 0.00013013 | 0.0045354 | 0.015907 | 0.00066466 | 0.00087957 | 0.0012416 | 0.0019956 | 0.0032437 | 0.0063526 | 0.024285 | 0.013867 | 0.012853 | 0.021613 | 0.051345 | 0.035669 | 0.035669 | 0.035669 | 0.035669 | 0.035669 | 0.035669 | 0.035669 | 0.035669 | 0.035669 | 0.035669 | 0.035669 | 0.035669 | 0.035669 | 0.035669 | 0.035669 | 0.035669
Total EUE (MWh) | 0.0033707 | 0.11748 | 0.41204 | 0.017217 | 0.022783 | 0.032161 | 0.05169 | 0.084021 | 0.16455 | 0.62905 | 0.3592 | 0.33292 | 0.55983 | 1.33 | 0.92393 | 0.92393 | 0.92393 | 0.92393 | 0.92393 | 0.92393 | 0.92393 | 0.92393 | 0.92393 | 0.92393 | 0.92393 | 0.92393 | 0.92393 | 0.92393 | 0.92393 | 0.92393
Option 5 - 4A LLG 2nd Tx + Switchroom + Three new feeders + OFR12 New Feeder | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Cost of Avoided EUE ($M) | 0.00013013 | 0.0045354 | 0.015907 | 9.2025e-05 | 0.00014609 | 0.00022602 | 0.00034547 | 0.00050919 | 0.0007361 | 0.0010487 | 0.0013994 | 0.0018424 | 0.0024646 | 0.0033655 | 0.0040864 | 0.0040864 | 0.0040864 | 0.0040864 | 0.0040864 | 0.0040864 | 0.0040864 | 0.0040864 | 0.0040864 | 0.0040864 | 0.0040864 | 0.0040864 | 0.0040864 | 0.0040864 | 0.0040864 | 0.0040864
Total EUE (MWh) | 0.0033707 | 0.11748 | 0.41204 | 0.0023837 | 0.003784 | 0.0058546 | 0.0089485 | 0.013189 | 0.019067 | 0.027165 | 0.036247 | 0.047723 | 0.06384 | 0.087174 | 0.10585 | 0.10585 | 0.10585 | 0.10585 | 0.10585 | 0.10585 | 0.10585 | 0.10585 | 0.10585 | 0.10585 | 0.10585 | 0.10585 | 0.10585 | 0.10585 | 0.10585 | 0.10585
Option 6 - Non Network | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Cost of Avoided EUE ($M) | 3.3419e-05 | 0.00041611 | 0.0011432 | 0.0015396 | 0.0020656 | 0.0030427 | 0.0057947 | 0.0097087 | 0.018798 | 0.050181 | 0.036071 | 0.031333 | 0.052033 | 0.10587 | 0.081225 | 0.081225 | 0.081225 | 0.081225 | 0.081225 | 0.081225 | 0.081225 | 0.081225 | 0.081225 | 0.081225 | 0.081225 | 0.081225 | 0.081225 | 0.081225 | 0.081225 | 0.081225
Total EUE (MWh) | 0.00086563 | 0.010778 | 0.029611 | 0.039881 | 0.053504 | 0.078814 | 0.1501 | 0.25148 | 0.48692 | 1.2998 | 0.93434 | 0.81161 | 1.3478 | 2.7424 | 2.1039 | 2.1039 | 2.1039 | 2.1039 | 2.1039 | 2.1039 | 2.1039 | 2.1039 | 2.1039 | 2.1039 | 2.1039 | 2.1039 | 2.1039 | 2.1039 | 2.1039 | 2.1039
Option 7 - | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Cost of Avoided EUE ($M) | 0.00013013 | 0.0045354 | 0.015907 | 0.02253 | 0.030537 | 0.04405 | 0.073277 | 0.10689 | 0.16079 | 0.25784 | 0.26283 | 0.26751 | 0.36579 | 0.54793 | 0.51363 | 0.51363 | 0.51363 | 0.51363 | 0.51363 | 0.51363 | 0.51363 | 0.51363 | 0.51363 | 0.51363 | 0.51363 | 0.51363 | 0.51363 | 0.51363 | 0.51363 | 0.51363
Total EUE (MWh) | 0.0033707 | 0.11748 | 0.41204 | 0.58358 | 0.79099 | 1.141 | 1.8981 | 2.7688 | 4.165 | 6.6787 | 6.808 | 6.9292 | 9.4749 | 14.1927 | 13.3044 | 13.3044 | 13.3044 | 13.3044 | 13.3044 | 13.3044 | 13.3044 | 13.3044 | 13.3044 | 13.3044 | 13.3044 | 13.3044 | 13.3044 | 13.3044 | 13.3044 | 13.3044
Option 8 - | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Cost of Avoided EUE ($M) | 0.00013013 | 0.0045354 | 0.015907 | 0.02253 | 0.030537 | 0.04405 | 0.073277 | 0.10689 | 0.16079 | 0.25784 | 0.26283 | 0.26751 | 0.36579 | 0.54793 | 0.51363 | 0.51363 | 0.51363 | 0.51363 | 0.51363 | 0.51363 | 0.51363 | 0.51363 | 0.51363 | 0.51363 | 0.51363 | 0.51363 | 0.51363 | 0.51363 | 0.51363 | 0.51363
Total EUE (MWh) | 0.0033707 | 0.11748 | 0.41204 | 0.58358 | 0.79099 | 1.141 | 1.8981 | 2.7688 | 4.165 | 6.6787 | 6.808 | 6.9292 | 9.4749 | 14.1927 | 13.3044 | 13.3044 | 13.3044 | 13.3044 | 13.3044 | 13.3044 | 13.3044 | 13.3044 | 13.3044 | 13.3044 | 13.3044 | 13.3044 | 13.3044 | 13.3044 | 13.3044 | 13.3044

## Key Model Assumption & Inputs
Select ZSS & Region | PHM | Central | MTTR
Probability Weighting for 10% POE MDs | 30% |  |  | Central | North | East | For Analysis
Probability Weighting for 50% POE MDs | 70% |  | N-1 MTTR (years) | 0.3858 | 0.1418 | 0.3858 | 0.3858
First year of analysis | FY25 |  | N-2 MTTR (years) | 0.2344 | 0.049 | 0.2344 | 0.2344
Select Sensitivity Variant | Forecast Sensitivity
Low | 90% |  | PV Factor's |  |  | PoF Sensitvity
Options | Name |  | Summer | 1.33 |  | Varaint
Option 1 - Do Nothing / Base Case | Do Nothing / Base Case |  | Winter | 1.13 |  | Base | 100%
Option 2 - 1A New PHS ZSS + Four new feeders | 1A New PHS ZSS + Four new feeders
Option 3 - 2A PHM 3rd Tx + Switchroom + Three new feeders + OFR12 New Feeder | 2A PHM 3rd Tx + Switchroom + Three new feeders + OFR12 New Feeder |  | Demand Response
Option 4 - 3A OFR 3rd Tx + Switchroom + Three new feeders + OFR12 New Feeder | 3A OFR 3rd Tx + Switchroom + Three new feeders + OFR12 New Feeder |  | Average Rate % | 20%
Option 5 - 4A LLG 2nd Tx + Switchroom + Three new feeders + OFR12 New Feeder | 4A LLG 2nd Tx + Switchroom + Three new feeders + OFR12 New Feeder
Option 6 - Non Network | Non Network
Option 7 -
Option 8 -
Added Capacity (MVA) | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39
Added Capacity (MVA) Option 1 N | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 1 N-1 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 1 N-2 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 2 N | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 2 N-1 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 2 N-2 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 3 N |  |  |  | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45
Added Capacity (MVA) Option 3 N-1 |  |  |  | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45
Added Capacity (MVA) Option 3 N-2 |  |  |  | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45
Added Capacity (MVA) Option 4 N | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 4 N-1 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 4 N-2 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 5 N | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 5 N-1 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 5 N-2 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 6 N | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 6 N-1 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 6 N-2 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 7 N | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 7 N-1 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 7 N-2 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 8 N | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 8 N-1 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 8 N-2 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Embedded Generation (MVA) | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39
Avaliable Embedded Generation (MVA) Option 1 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Embedded Generation (MVA) Option 2 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Embedded Generation (MVA) Option 3 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Embedded Generation (MVA) Option 4 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Embedded Generation (MVA) Option 5 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Embedded Generation (MVA) Option 6 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Embedded Generation (MVA) Option 7 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Embedded Generation (MVA) Option 8 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Demand Management (MVA) | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39
Avaliable Demand Management (MVA) Option 1 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Demand Management (MVA) Option 2 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Demand Management (MVA) Option 3 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Demand Management (MVA) Option 4 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Demand Management (MVA) Option 5 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Demand Management (MVA) Option 6 | 7.7456 | 9.9603 | 10.5358 | 10.4984 | 10.4969 | 10.5537 | 10.7079 | 10.8089 | 10.9091 | 11.0267 | 11.1341 | 11.2396 | 11.2492 | 11.3728 | 11.2743
Added Demand Management (MVA) Option 7 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Demand Management (MVA) Option 8 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Transfers (MVA) | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39
Planned Transfers (MVA) Option 1 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Transfers (MVA) Option 2 |  |  |  | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29
Added Transfers (MVA) Option 3 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Transfers (MVA) Option 4 |  |  |  | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5
Added Transfers (MVA) Option 5 |  |  |  | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29
Added Transfers (MVA) Option 6 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Transfers (MVA) Option 7 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Transfers (MVA) Option 8 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Block Loads Not in Forecast (MVA) | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39
Block Loads (MVA) | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Base | FY25: 100%
High | FY25: 110%
Low | FY25: 90%

## Tx PoF
Transformer Failure Rates for individual Transformers
[5 empty] | 10 | 8 | 10 | 6 | 8 | 6 | 6 | 10 | 6
Zone | arm_asset_id | floc | user_status | Age | Major Winding insulation | Accelerated cellulose Aging | Winding insulating liquid | Hot metal fault covered by paper | Chemical contamination, degradation | Physical & chemical contamination, degradation | Physical contamination | Short Circuit Concern | OLTC | WMA Health Score | WMA CS | WMA effective age | WMA Beta | WMA Eta | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WGI | 30192717 | DS-WGI-TRNFMR-9000004493 |  | 59 | 5 | 3 | 1 | 5 | 2 | 1 | 5 | 5 | 5 | 351.4286 | 4 | 60 | 3.5 | 82 | 1.976% | 1.976% | 2.058% | 2.142% | 2.227% | 2.315% | 2.405% | 2.496% | 2.59% | 2.686% | 2.783% | 2.883% | 2.985% | 3.089% | 3.195% | 3.303% | 3.413% | 3.525% | 3.639% | 3.755% | 3.873% | 3.994% | 4.116% | 4.241% | 4.368% | 4.497% | 4.628% | 4.761% | 4.897% | 5.034%
WGI | 30111322 | DS-WGI-TRNFMR-9000003147 |  | 59 | 5 | 5 | 1 | 3 | 2 | 1 | 4 | 5 | 5 | 348.5714 | 3 | 44 | 3.5 | 82 | 0.9218% | 0.9218% | 0.9742% | 1.028% | 1.084% | 1.142% | 1.201% | 1.262% | 1.325% | 1.39% | 1.457% | 1.525% | 1.596% | 1.668% | 1.742% | 1.818% | 1.896% | 1.976% | 2.058% | 2.142% | 2.227% | 2.315% | 2.405% | 2.496% | 2.59% | 2.686% | 2.783% | 2.883% | 2.985% | 3.089%
EPG | 30026486 | DS-EPG-TRNFMR-9000010175 |  | 45 | 5 | 3 | 2 | 1 | 2 | 1 | 4 | 5 | 5 | 322.8571 | 3 | 44 | 3.5 | 84.05 | 0.8458% | 0.8458% | 0.8939% | 0.9436% | 0.9949% | 1.048% | 1.102% | 1.159% | 1.216% | 1.276% | 1.337% | 1.4% | 1.465% | 1.531% | 1.599% | 1.669% | 1.741% | 1.814% | 1.889% | 1.966% | 2.045% | 2.125% | 2.208% | 2.292% | 2.378% | 2.466% | 2.556% | 2.648% | 2.741% | 2.837%
EPG | 30058367 | DS-EPG-TRNFMR-9000010174 |  | 45 | 5 | 3 | 2 | 1 | 2 | 1 | 4 | 5 | 5 | 322.8571 | 3 | 44 | 3.5 | 84.05 | 0.8458% | 0.8458% | 0.8939% | 0.9436% | 0.9949% | 1.048% | 1.102% | 1.159% | 1.216% | 1.276% | 1.337% | 1.4% | 1.465% | 1.531% | 1.599% | 1.669% | 1.741% | 1.814% | 1.889% | 1.966% | 2.045% | 2.125% | 2.208% | 2.292% | 2.378% | 2.466% | 2.556% | 2.648% | 2.741% | 2.837%
WGI | 30475971 | DS-WGI-TRNFMR-9000007146 |  | 49 | 5 | 5 | 1 | 1 | 1 | 1 | 2 | 5 | 1 | 268.5714 | 3 | 44 | 3.5 | 82 | 0.9218% | 0.9218% | 0.9742% | 1.028% | 1.084% | 1.142% | 1.201% | 1.262% | 1.325% | 1.39% | 1.457% | 1.525% | 1.596% | 1.668% | 1.742% | 1.818% | 1.896% | 1.976% | 2.058% | 2.142% | 2.227% | 2.315% | 2.405% | 2.496% | 2.59% | 2.686% | 2.783% | 2.883% | 2.985% | 3.089%
EPG | 30209984 | DS-EPG-TRNFMR-9000007095 |  | 24 | 3 | 3 | 1 | 3 | 2 | 1 | 4 | 3 | 3 | 251.4286 | 3 | 44 | 3.5 | 84.05 | 0.8458% | 0.8458% | 0.8939% | 0.9436% | 0.9949% | 1.048% | 1.102% | 1.159% | 1.216% | 1.276% | 1.337% | 1.4% | 1.465% | 1.531% | 1.599% | 1.669% | 1.741% | 1.814% | 1.889% | 1.966% | 2.045% | 2.125% | 2.208% | 2.292% | 2.378% | 2.466% | 2.556% | 2.648% | 2.741% | 2.837%
CLN | 30338702 | DS-CLN-TRNFMR-9000006730 |  | 21 | 3 | 2 | 2 | 3 | 1 | 1 | 3 | 3 | 2 | 225.7143 | 2 | 24 | 3.5 | 84.05 | 0.1909% | 0.1909% | 0.211% | 0.2322% | 0.2547% | 0.2785% | 0.3035% | 0.3298% | 0.3575% | 0.3865% | 0.4168% | 0.4486% | 0.4817% | 0.5162% | 0.5522% | 0.5897% | 0.6286% | 0.669% | 0.7109% | 0.7543% | 0.7993% | 0.8458% | 0.8939% | 0.9436% | 0.9949% | 1.048% | 1.102% | 1.159% | 1.216% | 1.276%
CRE | 30165029 | DS-CRE-TRNFMR-9000525811 |  | 13 | 3 | 2 | 1 | 3 | 2 | 1 | 4 | 2 | 2 | 217.1429 | 2 | 24 | 3.5 | 84.05 | 0.1909% | 0.1909% | 0.211% | 0.2322% | 0.2547% | 0.2785% | 0.3035% | 0.3298% | 0.3575% | 0.3865% | 0.4168% | 0.4486% | 0.4817% | 0.5162% | 0.5522% | 0.5897% | 0.6286% | 0.669% | 0.7109% | 0.7543% | 0.7993% | 0.8458% | 0.8939% | 0.9436% | 0.9949% | 1.048% | 1.102% | 1.159% | 1.216% | 1.276%
LLG | 30359074 | DS-LLG-TRNFMR-9000007796 |  | 20 | 1 | 2 | 1 | 2 | 1 | 1 | 5 | 3 | 2 | 191.4286 | 2 | 24 | 3.5 | 84.05 | 0.1909% | 0.1909% | 0.211% | 0.2322% | 0.2547% | 0.2785% | 0.3035% | 0.3298% | 0.3575% | 0.3865% | 0.4168% | 0.4486% | 0.4817% | 0.5162% | 0.5522% | 0.5897% | 0.6286% | 0.669% | 0.7109% | 0.7543% | 0.7993% | 0.8458% | 0.8939% | 0.9436% | 0.9949% | 1.048% | 1.102% | 1.159% | 1.216% | 1.276%
CRE | 30380287 | DS-CRE-TRNFMR-9000525810 |  | 13 | 2 | 2 | 1 | 1 | 2 | 1 | 3 | 2 | 2 | 177.1429 | 2 | 24 | 3.5 | 84.05 | 0.1909% | 0.1909% | 0.211% | 0.2322% | 0.2547% | 0.2785% | 0.3035% | 0.3298% | 0.3575% | 0.3865% | 0.4168% | 0.4486% | 0.4817% | 0.5162% | 0.5522% | 0.5897% | 0.6286% | 0.669% | 0.7109% | 0.7543% | 0.7993% | 0.8458% | 0.8939% | 0.9436% | 0.9949% | 1.048% | 1.102% | 1.159% | 1.216% | 1.276%
CLN | 30000439 | DS-CLN-TRNFMR-9000001306 |  | 19 | 2 | 2 | 1 | 1 | 1 | 1 | 3 | 2 | 2 | 165.7143 | 2 | 24 | 3.5 | 84.05 | 0.1909% | 0.1909% | 0.211% | 0.2322% | 0.2547% | 0.2785% | 0.3035% | 0.3298% | 0.3575% | 0.3865% | 0.4168% | 0.4486% | 0.4817% | 0.5162% | 0.5522% | 0.5897% | 0.6286% | 0.669% | 0.7109% | 0.7543% | 0.7993% | 0.8458% | 0.8939% | 0.9436% | 0.9949% | 1.048% | 1.102% | 1.159% | 1.216% | 1.276%
OFR | 30035965 | DS-OFR-TRNFMR-9000014181 |  | 16 | 2 | 2 | 1 | 1 | 1 | 1 | 3 | 2 | 2 | 165.7143 | 2 | 24 | 3.5 | 84.05 | 0.1909% | 0.1909% | 0.211% | 0.2322% | 0.2547% | 0.2785% | 0.3035% | 0.3298% | 0.3575% | 0.3865% | 0.4168% | 0.4486% | 0.4817% | 0.5162% | 0.5522% | 0.5897% | 0.6286% | 0.669% | 0.7109% | 0.7543% | 0.7993% | 0.8458% | 0.8939% | 0.9436% | 0.9949% | 1.048% | 1.102% | 1.159% | 1.216% | 1.276%
KLO | 30002764 | DS-KLO-TRNFMR-9000412348 |  | 15 | 1 | 2 | 1 | 1 | 1 | 1 | 4 | 2 | 2 | 160 | 2 | 24 | 3.5 | 84.05 | 0.1909% | 0.1909% | 0.211% | 0.2322% | 0.2547% | 0.2785% | 0.3035% | 0.3298% | 0.3575% | 0.3865% | 0.4168% | 0.4486% | 0.4817% | 0.5162% | 0.5522% | 0.5897% | 0.6286% | 0.669% | 0.7109% | 0.7543% | 0.7993% | 0.8458% | 0.8939% | 0.9436% | 0.9949% | 1.048% | 1.102% | 1.159% | 1.216% | 1.276%
OFR | 30221642 | DS-OFR-TRNFMR-9000016122 |  | 16 | 1 | 2 | 1 | 1 | 1 | 1 | 3 | 2 | 2 | 151.4286 | 2 | 24 | 3.5 | 84.05 | 0.1909% | 0.1909% | 0.211% | 0.2322% | 0.2547% | 0.2785% | 0.3035% | 0.3298% | 0.3575% | 0.3865% | 0.4168% | 0.4486% | 0.4817% | 0.5162% | 0.5522% | 0.5897% | 0.6286% | 0.669% | 0.7109% | 0.7543% | 0.7993% | 0.8458% | 0.8939% | 0.9436% | 0.9949% | 1.048% | 1.102% | 1.159% | 1.216% | 1.276%
KLO | 30208816 | DS-KLO-TRNFMR-9000412347 |  | 15 | 1 | 2 | 1 | 1 | 1 | 1 | 3 | 2 | 2 | 151.4286 | 2 | 24 | 3.5 | 84.05 | 0.1909% | 0.1909% | 0.211% | 0.2322% | 0.2547% | 0.2785% | 0.3035% | 0.3298% | 0.3575% | 0.3865% | 0.4168% | 0.4486% | 0.4817% | 0.5162% | 0.5522% | 0.5897% | 0.6286% | 0.669% | 0.7109% | 0.7543% | 0.7993% | 0.8458% | 0.8939% | 0.9436% | 0.9949% | 1.048% | 1.102% | 1.159% | 1.216% | 1.276%
PHM | 32944656 | DS-PHM-TRNFMR-9000004393 |  | 8 | 2 | 2 | 1 | 1 | 1 | 1 | 3 | 1 | 1 | 142.8571 | 1 | 8 | 3.5 | 84.05 | 0.01357% | 0.01357% | 0.01791% | 0.023% | 0.02887% | 0.03555% | 0.04308% | 0.0515% | 0.06084% | 0.07112% | 0.08238% | 0.09465% | 0.1079% | 0.1223% | 0.1378% | 0.1543% | 0.172% | 0.1909% | 0.211% | 0.2322% | 0.2547% | 0.2785% | 0.3035% | 0.3298% | 0.3575% | 0.3865% | 0.4168% | 0.4486% | 0.4817% | 0.5162%
PHM | 32944654 | DS-PHM-TRNFMR-9000007050 |  | 8 | 2 | 2 | 1 | 1 | 1 | 1 | 3 | 1 | 1 | 142.8571 | 1 | 8 | 3.5 | 84.05 | 0.01357% | 0.01357% | 0.01791% | 0.023% | 0.02887% | 0.03555% | 0.04308% | 0.0515% | 0.06084% | 0.07112% | 0.08238% | 0.09465% | 0.1079% | 0.1223% | 0.1378% | 0.1543% | 0.172% | 0.1909% | 0.211% | 0.2322% | 0.2547% | 0.2785% | 0.3035% | 0.3298% | 0.3575% | 0.3865% | 0.4168% | 0.4486% | 0.4817% | 0.5162%

## AER VCR Rates(2024)
Category | Rate | Notes
Dec 24 AER VCR ($/kWh) - Res | 49.23 | Vic Av Res
Dec 24 AER VCR ($/kWh) - Com | 34.39 | Vic Av Com
Dec 24 AER VCR ($/kWh) - Ind | 33.49 | Vic Av Ind
Dec 24 AER VCR ($/kWh) - Agr | 22.25 | Vic Av Agr

## Customer No. and Vol per Feeder
CUSTOMER_CLASS | Feeder | VOL | CUST_NO | ZSS | Customer mix received from AusNet Financial Planning & Strategy on 25/7/2025
COMMERCIAL | bra11 | 9860526.7854 | 168 | bra
COMMERCIAL | bge13 | 654988.62 | 45 | bge
COMMERCIAL | phi11 | 1878610.03 | 37 | phi
NCONUML | moe11 | 47447.48 | 18 | moe
NCONUML | drn13 | 27414.73 | 17 | drn
COMMERCIAL | smg34 | 5224461.8 | 1 | smg
FARM | wgl13 | 901266.5312 | 97 | wgl
FARM | msd2 | 2808295.5668 | 471 | msd
NCONUML | elm34 | 86758.8 | 34 | elm
| rwt36 | 703.54 | 2 | rwt
COMMERCIAL | lga41 | 1099100.22 | 2 | lga
| bdl33 | 4298.82 | 8 | bdl
NCONUML | smr14 | 27225.34 | 18 | smr
COMMERCIAL | cln24 | 4484028.8333 | 290 | cln
RESIDENTL | ofr14 | 13024383.6958 | 3554 | ofr
NCONUML | bdl43 | 100361.9983 | 38 | bdl
| ofr22 | 16469.09 | 22 | ofr
NCONUML | rwn33 | 8721.79 | 7 | rwn
LIGHTING | hpk12 | 342838 | 1 | hpk
COMMERCIAL | bra23 | 6262297.01 | 84 | bra
FARM | tt1 | 1865.76 | 1 | tt
LIGHTING | mfa14 | 787800.53 | 1 | mfa
RESIDENTL | brt22 | 9968534.1043 | 1376 | brt
RESIDENTL | mwl25 | 4092575.372 | 493 | mwl
NCONUML | wgi22 | 83961.44 | 23 | wgi
INDUSTRIAL | ldl22 | 4379901.5885 | 45 | ldl
RESIDENTL | phm22 | 3628742.5283 | 796 | phm
FARM | mfa23 | 2691321.6324 | 201 | mfa
NCONUML | rwn32 | 60415.37 | 23 | rwn
FARM | cre22 | 55644.16 | 17 | cre
RESIDENTL | elm24 | 17367685.5307 | 2999 | elm
COMMERCIAL | tt9 | 7181168.3052 | 213 | tt
COMMERCIAL | kms12 | 15257134.8455 | 395 | kms
NCONUML | cyn31 | 24759.23 | 14 | cyn
| llg12 | 26420.7189 | 15 | llg
LIGHTING | ruba22 | 247422.69 | 1 | ruba
RESIDENTL | wt12 | 10803758.701 | 2579 | wt
COMMERCIAL | bwn14 | 6975240.1 | 156 | bwn
NCONUML | bge12 | 37366.03 | 11 | bge
NCONUML | rwn24 | 30489.76 | 21 | rwn
FARM | sfs1 | 113380.09 | 9 | sfs
| bwr13 | 80076.52 | 46 | bwr
FARM | wt13 | 37228.86 | 3 | wt
FARM | cre23 | 226478.55 | 9 | cre
COMMERCIAL | rwn22 | 1886562.0146 | 72 | rwn
| tgn23 | 13898.1302 | 15 | tgn
FARM | ldl22 | 7887.95 | 1 | ldl
RESIDENTL | fgy21 | 7153989.4877 | 1047 | fgy
FARM | mjg11 | 735019.886 | 74 | mjg
| ldl14 | 17432.2687 | 11 | ldl
INDUSTRIAL | ldl24 | 64751.4 | 12 | ldl
| sle13 | 253.3245 | 2 | sle
FARM | moe21 | 6301170.9744 | 504 | moe
FARM | bge23 | 671977.1074 | 66 | bge
RESIDENTL | elm32 | 19949095.4752 | 2463 | elm
COMMERCIAL | ftr12 | 1975462.7263 | 113 | ftr
RESIDENTL | lyd12 | 6657897.88 | 1592 | lyd
RESIDENTL | epg31 | 11862355.3417 | 3027 | epg
NCONUML | ofr11 | 57102.89 | 18 | ofr
FARM | moe11 | 65350.2807 | 7 | moe
FARM | nla32 | 1181128.1259 | 84 | nla
FARM | smr24 | 4141783.4574 | 392 | smr
RESIDENTL | fgy13 | 7970231.1446 | 1518 | fgy
FARM | bdl41 | 1305847.5951 | 258 | bdl
NCONUML | elm23 | 62172.37 | 40 | elm
| elm22 | 20617.5429 | 26 | elm
NCONUML | cre21 | 58240.1 | 18 | cre
FARM | phm32 | 50851.13 | 8 | phm
INDUSTRIAL | lga21 | 208132.02 | 16 | lga
INDUSTRIAL | nrn13 | 39703.59 | 6 | nrn
RESIDENTL | hpk22 | 18949862.0449 | 4569 | hpk
NCONUML | cyn13 | 17637.49 | 6 | cyn
COMMERCIAL | cre31 | 14851829.6913 | 363 | cre
COMMERCIAL | epg32 | 5001490.9226 | 156 | epg
| phm32 | 41386.12 | 47 | phm
NCONUML | wo33 | 6875.31 | 2 | wo
FARM | wgl21 | 5056187.7677 | 366 | wgl
INDUSTRIAL | cre22 | 240829.25 | 4 | cre
RESIDENTL | wgi34 | 3671110.7601 | 570 | wgi
INDUSTRIAL | ldl12 | 10352583.7 | 7 | ldl
INDUSTRIAL | wyk12 | 149433.7 | 6 | wyk
INDUSTRIAL | cyn14 | 23200.151 | 3 | cyn
| wo11 | 4136.2425 | 3 | wo
| msd4 | 20521.76 | 37 | msd
FARM | mby12 | 52034.88 | 19 | mby
COMMERCIAL | rwt22 | 7145877.6761 | 143 | rwt
COMMERCIAL | wo12 | 23719023.8 | 1 | wo
RESIDENTL | wn2 | 17414453.5902 | 3500 | wn
COMMERCIAL | wots25 | 3483725.2811 | 72 | wots
RESIDENTL | bwr33 | 46024.67 | 2 | bwr
RESIDENTL | wn3 | 12349888.6736 | 2099 | wn
RESIDENTL | bn24 | 2992797.8263 | 559 | bn
| bra21 | 41455.7142 | 65 | bra
INDUSTRIAL | hpk14 | 16381.88 | 4 | hpk
RESIDENTL | epg32 | 14811809.1158 | 3829 | epg
COMMERCIAL | cln14 | 10141314.5039 | 129 | cln
FARM | smg31 | 14995.46 | 5 | smg
INDUSTRIAL | drn22 | 2117102.6666 | 12 | drn
NCONUML | drn12 | 43785.8374 | 16 | drn
INDUSTRIAL | fgy34 | 128392.6893 | 5 | fgy
NCONUML | fgy31 | 6707.46 | 4 | fgy
| wt8 | 7059.0655 | 13 | wt
| bwn12 | 6521.57 | 6 | bwn
COMMERCIAL | myt12 | 10774273.2986 | 307 | myt
COMMERCIAL | ldl21 | 5339830.9491 | 117 | ldl
| cln21 | 32425.72 | 66 | cln
INDUSTRIAL | fgy14 | 162921.94 | 7 | fgy
| tgn12 | 22490.11 | 3 | tgn
COMMERCIAL | epg12 | 8214339.5389 | 163 | epg
NCONUML | moe23 | 69334.91 | 17 | moe
FARM | cyn14 | 7715.15 | 1 | cyn
RESIDENTL | lyd14 | 10580841.4317 | 1203 | lyd
COMMERCIAL | smg23 | 21963007.1063 | 434 | smg
INDUSTRIAL | bra33 | 2076536.62 | 34 | bra
INDUSTRIAL | rwt14 | 2271244.55 | 44 | rwt
COMMERCIAL | lga14 | 2174194.9787 | 115 | lga
INDUSTRIAL | myt22 | 3176.32 | 3 | myt
FARM | cyn21 | 10230.57 | 2 | cyn
| klo24 | 65411.35 | 119 | klo
COMMERCIAL | brt21 | 6571769.7252 | 216 | brt
FARM | kms11 | 665243.0597 | 75 | kms
| elm34 | 25999.6869 | 33 | elm
INDUSTRIAL | mwl11 | 366139.79 | 15 | mwl
INDUSTRIAL | lyd14 | 80895.88 | 12 | lyd
LIGHTING | cpk11 | 1086.88 | 1 | cpk
NCONUML | fgy23 | 34402.31 | 12 | fgy
| bra32 | 15753.982 | 22 | bra
RESIDENTL | epg12 | 26391788.5687 | 6905 | epg
COMMERCIAL | cyn24 | 15647575.1097 | 304 | cyn
INDUSTRIAL | phm21 | 511727.73 | 19 | phm
NCONUML | ftr12 | 5424.58 | 5 | ftr
| bwa23 | 5447.575 | 8 | bwa
NCONUML | llg12 | 4182.92 | 3 | llg
COMMERCIAL | drn13 | 5299129.684 | 96 | drn
INDUSTRIAL | hpk21 | 31624.71 | 8 | hpk
INDUSTRIAL | wyk23 | 1500537.4334 | 28 | wyk
RESIDENTL | lga12 | 4152631.2896 | 644 | lga
RESIDENTL | cyn11 | 6009338.551 | 1440 | cyn
NCONUML | fgy24 | 70027.41 | 43 | fgy
| moe23 | 74726.3012 | 22 | moe
COMMERCIAL | elm24 | 3531802.26 | 46 | elm
LIGHTING | elm33 | 1000.47 | 1 | elm
RESIDENTL | smg23 | 6500499.5996 | 1411 | smg
FARM | msd4 | 1851245.0012 | 252 | msd
COMMERCIAL | lga24 | 21693950.3379 | 92 | lga
COMMERCIAL | ldl11 | 7360578.73 | 74 | ldl
NCONUML | rve13 | 29515.6981 | 24 | rve
COMMERCIAL | trc01 | 365242.5067 | 42 | trc
COMMERCIAL | wt15 | 1164715.6471 | 30 | wt
COMMERCIAL | bra14 | 811059.401 | 59 | bra
| ftr21 | 17034.7542 | 20 | ftr
RESIDENTL | bra23 | 7643359.408 | 1736 | bra
INDUSTRIAL | cpk11 | 59065.36 | 14 | cpk
INDUSTRIAL | hpk12 | 531460.54 | 46 | hpk
FARM | fgy23 | 137430.23 | 3 | fgy
INDUSTRIAL | tt4 | 77015.1997 | 16 | tt
FARM | cpk22 | 45399.86 | 6 | cpk
INDUSTRIAL | yn31 | 1004932.7745 | 6 | yn
FARM | myt22 | 1873055.6433 | 191 | myt
| cpk12 | 20188.43 | 32 | cpk
RESIDENTL | bwa22 | 6606654.3694 | 1106 | bwa
| mfa34 | 1434.55 | 6 | mfa
| nla31 | 4780.58 | 5 | nla
FARM | mdg1 | 36782.2 | 6 | mdg
RESIDENTL | mwl21 | 3605605.4081 | 859 | mwl
COMMERCIAL | phm33 | 14452041.4603 | 180 | phm
INDUSTRIAL | ofr23 | 154535.41 | 17 | ofr
INDUSTRIAL | elm21 | 177435.466 | 7 | elm
INDUSTRIAL | wt5 | 89.11 | 1 | wt
FARM | llg13 | 1917532.2118 | 152 | llg
INDUSTRIAL | klk21 | 41156.68 | 10 | klk
NCONUML | wt9 | 48247.64 | 17 | wt
FARM | mdi1 | 153288.2952 | 21 | mdi
INDUSTRIAL | nrn14 | 19245.31 | 5 | nrn
INDUSTRIAL | wgl12 | 500659.11 | 16 | wgl
FARM | fgy13 | 80534.51 | 6 | fgy
INDUSTRIAL | bwr14 | 1597974.48 | 1 | bwr
LIGHTING | bn11 | 103048.5 | 1 | bn
RESIDENTL | klo14 | 40411755.0117 | 10946 | klo
RESIDENTL | fgy33 | 9101921.8028 | 1763 | fgy
LIGHTING | cre31 | 2308168.51 | 1 | cre
RESIDENTL | wn5 | 8555201.9981 | 1156 | wn
COMMERCIAL | mfa22 | 5299491.9938 | 179 | mfa
COMMERCIAL | lyd11 | 3798691.89 | 62 | lyd
LIGHTING | bn24 | 2014.81 | 1 | bn
COMMERCIAL | cf1 | 9360587.4941 | 189 | cf
FARM | lga11 | 4665290.6529 | 555 | lga
RESIDENTL | lyd13 | 10895753.2364 | 2051 | lyd
NCONUML | cre33 | 35388.67 | 19 | cre
| smg32 | 685.05 | 3 | smg
INDUSTRIAL | cyn11 | 1966971.1028 | 55 | cyn
COMMERCIAL | wn2 | 10157994.9798 | 156 | wn
| phm21 | 32464.7212 | 22 | phm
| sfs1 | 13890.635 | 10 | sfs
NCONUML | tt12 | 15011.94 | 8 | tt
FARM | lga21 | 1065599.6961 | 147 | lga
| ldl12 | 52350.63 | 6 | ldl
INDUSTRIAL | smg31 | 231921 | 9 | smg
LIGHTING | myt12 | 813470.88 | 6 | myt
| smr24 | 66801.9 | 34 | smr
NCONUML | cre32 | 49453.4427 | 23 | cre
INDUSTRIAL | bdl44 | 2337630.2078 | 41 | bdl
| rve11 | 302066.1 | 12 | rve
FARM | wo31 | 3245.01 | 1 | wo
LIGHTING | ofr13 | 171706.2 | 2 | ofr
RESIDENTL | tt9 | 13181645.445 | 3553 | tt
COMMERCIAL | wgl11 | 13522117.9742 | 216 | wgl
COMMERCIAL | hpk24 | 15242696.9791 | 271 | hpk
COMMERCIAL | bwr34 | 12222544.1423 | 437 | bwr
NCONUML | nla34 | 19980.17 | 11 | nla
FARM | bwr24 | 9303.26 | 1 | bwr
| wgi23 | 15962.8799 | 36 | wgi
RESIDENTL | cln13 | 18593732.5659 | 6830 | cln
RESIDENTL | lga13 | 1879247.7046 | 295 | lga
RESIDENTL | cnr3 | 108696.4186 | 22 | cnr
| wgl12 | 112644.3661 | 43 | wgl
COMMERCIAL | cln12 | 8203266.5202 | 86 | cln
NCONUML | ofr21 | 100427.35 | 34 | ofr
RESIDENTL | drn24 | 10021102.8231 | 2473 | drn
COMMERCIAL | cyn31 | 1940881.6507 | 53 | cyn
NCONUML | ldl24 | 34534.3 | 19 | ldl
COMMERCIAL | ofr13 | 9302944.2987 | 197 | ofr
| wots13 | 58538.6484 | 32 | wots
| cpk23 | 23360.0808 | 24 | cpk
NCONUML | cln11 | 4587.8606 | 9 | cln
| wt15 | 51811.4 | 11 | wt
COMMERCIAL | epg24 | 26841528 | 1 | epg
FARM | drn22 | 329138.5031 | 52 | drn
| mfa31 | 16838.31 | 22 | mfa
COMMERCIAL | bra32 | 4055727.3404 | 158 | bra
COMMERCIAL | cpk21 | 14974774.5549 | 258 | cpk
INDUSTRIAL | myt21 | 335981.9667 | 19 | myt
FARM | nrn14 | 139044.47 | 14 | nrn
| wt5 | 22324.85 | 13 | wt
INDUSTRIAL | mfa23 | 139940.33 | 14 | mfa
FARM | wyk12 | 2634438.6357 | 233 | wyk
RESIDENTL | epg23 | 3653084.6682 | 932 | epg
COMMERCIAL | tgn11 | 2525258.71 | 85 | tgn
| wt13 | 22551.0062 | 37 | wt
| cyn13 | 10533.28 | 7 | cyn
INDUSTRIAL | fgy13 | 259435.94 | 2 | fgy
RESIDENTL | cln12 | 23908773.0216 | 6775 | cln
COMMERCIAL | brt22 | 9042592.2197 | 210 | brt
COMMERCIAL | rwt25 | 7526054.6961 | 146 | rwt
FARM | mfa31 | 218040.8355 | 21 | mfa
COMMERCIAL | cln22 | 3248277.4443 | 37 | cln
NCONUML | bdl33 | 22970.8 | 8 | bdl
COMMERCIAL | fgy12 | 74427.591 | 4 | fgy
RESIDENTL | mwl16 | 8188909.2298 | 1700 | mwl
INDUSTRIAL | moe25 | 612177.9824 | 16 | moe
COMMERCIAL | tt7 | 24970154.3491 | 341 | tt
INDUSTRIAL | bwr24 | 4118148.7987 | 125 | bwr
RESIDENTL | moe13 | 2791200.4315 | 357 | moe
FARM | wyk24 | 694188.3378 | 94 | wyk
NCONUML | wo14 | 36996.26 | 12 | wo
RESIDENTL | bra13 | 6470560.8911 | 1572 | bra
RESIDENTL | tt7 | 39398.92 | 9 | tt
FARM | epg34 | 15821.91 | 5 | epg
INDUSTRIAL | yn35 | 6582.38 | 2 | yn
NCONUML | bwa23 | 749.23 | 1 | bwa
FARM | sle13 | 1461316.56 | 213 | sle
COMMERCIAL | cpk13 | 4127340.5971 | 198 | cpk
INDUSTRIAL | ldl14 | 1064067.7426 | 16 | ldl
| rwt14 | 62105.3312 | 18 | rwt
LIGHTING | hpk13 | 14513.85 | 1 | hpk
RESIDENTL | klk22 | 940238.19 | 128 | klk
COMMERCIAL | mwl25 | 259300.06 | 16 | mwl
| mjg11 | 96977.3135 | 7 | mjg
RESIDENTL | hpk24 | 4867180.3451 | 1284 | hpk
FARM | ftr21 | 6703423.0704 | 705 | ftr
FARM | smr12 | 441800.25 | 44 | smr
FARM | bwr13 | 73574.54 | 13 | bwr
| ldl22 | 9241.11 | 9 | ldl
FARM | wo22 | 35676.335 | 7 | wo
NCONUML | moe12 | 9318.9 | 3 | moe
INDUSTRIAL | bdl31 | 1561951.6978 | 44 | bdl
COMMERCIAL | ofr14 | 8393968.2568 | 77 | ofr
NCONUML | tgn23 | 48562.71 | 16 | tgn
NCONUML | cyn21 | 25127.29 | 5 | cyn
FARM | phm34 | 22945.58 | 3 | phm
INDUSTRIAL | cyn33 | 36519.92 | 4 | cyn
LIGHTING | bm8b32 | 1070.04 | 1 | bmb
FARM | llg12 | 5311057.9488 | 488 | llg
NCONUML | rwt32 | 94072.85 | 46 | rwt
COMMERCIAL | myt11 | 912988.53 | 42 | myt
INDUSTRIAL | cpk22 | 129954.91 | 11 | cpk
| cre22 | 20388.051 | 33 | cre
RESIDENTL | ldl21 | 5451727.7741 | 1502 | ldl
FARM | bdl44 | 8189534.7866 | 736 | bdl
INDUSTRIAL | bn11 | 1899511.3657 | 45 | bn
INDUSTRIAL | wgi31 | 152399.6 | 19 | wgi
INDUSTRIAL | mdi1 | 16.0426 | 1 | mdi
| ofr11 | 90492.4817 | 79 | ofr
LIGHTING | kms11 | 547479.19 | 1 | kms
RESIDENTL | phi12 | 18738852.0082 | 4967 | phi
COMMERCIAL | bwr12 | 7897915.6022 | 287 | bwr
FARM | msd1 | 2520603.4144 | 354 | msd
COMMERCIAL | tgn44 | 4662112.18 | 89 | tgn
NCONUML | uwy1 | 29815.85 | 15 | uwy
NCONUML | lga22 | 54192.29 | 17 | lga
NCONUML | lga23 | 17186.13 | 6 | lga
INDUSTRIAL | hpk13 | 1952010.47 | 3 | hpk
FARM | drn23 | 391232.6382 | 58 | drn
FARM | ldl23 | 5910515.5529 | 453 | ldl
FARM | bdl31 | 55336.85 | 12 | bdl
RESIDENTL | bwr34 | 11176240.016 | 2984 | bwr
RESIDENTL | ofr13 | 5689359.8131 | 1445 | ofr
NCONUML | bra21 | 145563.002 | 72 | bra
COMMERCIAL | cf2 | 1114027.3697 | 138 | cf
RESIDENTL | bdl32 | 16368580.902 | 3124 | bdl
COMMERCIAL | smr22 | 10240657.5236 | 95 | smr
NCONUML | rve12 | 34563.18 | 21 | rve
COMMERCIAL | cnr3 | 208527.63 | 11 | cnr
| elm25 | 9741.0155 | 15 | elm
INDUSTRIAL | lyd13 | 30651.21 | 5 | lyd
INDUSTRIAL | mby12 | 279353.09 | 7 | mby
INDUSTRIAL | epg21 | 31298.6803 | 2 | epg
FARM | wgl12 | 7817936.5802 | 624 | wgl
COMMERCIAL | moe13 | 1401894.0174 | 82 | moe
RESIDENTL | lga14 | 7239522.4699 | 1158 | lga
RESIDENTL | epg35 | 308209.78 | 22 | epg
FARM | hpk14 | 29274.39 | 5 | hpk
LIGHTING | bn22 | 341591.58 | 1 | bn
NCONUML | bge11 | 85890.46 | 45 | bge
NCONUML | wt7 | 26985.19 | 18 | wt
| wo31 | 27869.149 | 41 | wo
INDUSTRIAL | elm32 | 759094.4258 | 68 | elm
NCONUML | cre23 | 95638.5 | 25 | cre
RESIDENTL | cln23 | 19292170.1488 | 4992 | cln
| lga21 | 17263.28 | 18 | lga
NCONUML | bwn12 | 35975.24 | 12 | bwn
| fgy31 | 1671.76 | 6 | fgy
NCONUML | ftr23 | 39743.6852 | 30 | ftr
NCONUML | smg21 | 9405.11 | 5 | smg
RESIDENTL | epg13 | 24819451.0174 | 7299 | epg
RESIDENTL | ruba22 | 5955886.59 | 1080 | ruba
INDUSTRIAL | bwr23 | 1917390.4058 | 110 | bwr
COMMERCIAL | bn23 | 4585306.9 | 117 | bn
| fgy24 | 60212.15 | 95 | fgy
LIGHTING | brt21 | 27441.26 | 1 | brt
COMMERCIAL | mby14 | 13812.56 | 3 | mby
RESIDENTL | drn21 | 15235611.8074 | 3585 | drn
RESIDENTL | nrn11 | 3368324.1063 | 703 | nrn
NCONUML | cln21 | 97183.1897 | 28 | cln
NCONUML | tgn12 | 26909.78 | 9 | tgn
FARM | moe22 | 48531.59 | 7 | moe
RESIDENTL | bra14 | 17287022.2386 | 4193 | bra
RESIDENTL | brt21 | 8587133.8204 | 1368 | brt
INDUSTRIAL | ldl23 | 2181365.61 | 45 | ldl
NCONUML | klo24 | 121410.57 | 41 | klo
INDUSTRIAL | wt8 | 22231.36 | 5 | wt
| bdl41 | 27628.4721 | 32 | bdl
COMMERCIAL | sle14 | 13227565.7623 | 343 | sle
| smr14 | 17300.3116 | 19 | smr
INDUSTRIAL | llg11 | 439641.21 | 9 | llg
| wgi22 | 13903.1 | 35 | wgi
NCONUML | moe22 | 34069.45 | 10 | moe
| ftr12 | 15921.46 | 17 | ftr
COMMERCIAL | epg11 | 902129.45 | 16 | epg
RESIDENTL | cpk13 | 21255549.7429 | 4974 | cpk
| fgy23 | 9273.25 | 10 | fgy
FARM | cyn12 | 9105.46 | 2 | cyn
INDUSTRIAL | rwn31 | 527467.66 | 22 | rwn
RESIDENTL | bm8b32 | 357081.227 | 62 | bmb
FARM | ruba22 | 1060033.1321 | 158 | ruba
INDUSTRIAL | cnr1 | 88077.93 | 3 | cnr
FARM | cpk12 | 972803.9358 | 91 | cpk
COMMERCIAL | wo14 | 14658340.7796 | 304 | wo
COMMERCIAL | tt5 | 6134357.4395 | 224 | tt
INDUSTRIAL | wo11 | 18559582.74 | 7 | wo
| wgl23 | 17798.7289 | 12 | wgl
NCONUML | cyn12 | 64730.9 | 21 | cyn
COMMERCIAL | bwr33 | 3515549.759 | 83 | bwr
COMMERCIAL | cyn22 | 10287381.4837 | 183 | cyn
COMMERCIAL | rwt32 | 5482054.6843 | 198 | rwt
INDUSTRIAL | nrn12 | 7260.73 | 2 | nrn
RESIDENTL | cln22 | 8137131.1146 | 3340 | cln
| kms12 | 36774.1343 | 44 | kms
| cyn24 | 12784.0842 | 11 | cyn
| smg33 | 11524.64 | 21 | smg
COMMERCIAL | rve11 | 18192998.0721 | 274 | rve
FARM | wt5 | 8146.48 | 2 | wt
INDUSTRIAL | bge23 | 983662.8538 | 7 | bge
| msd2 | 9983.6 | 13 | msd
| bra12 | 98134.87 | 2 | bra
RESIDENTL | hpk23 | 13762355.5073 | 3377 | hpk
COMMERCIAL | smr13 | 15057236.7589 | 394 | smr
INDUSTRIAL | rwt21 | 372221.49 | 45 | rwt
FARM | rve12 | 22362.86 | 5 | rve
NCONUML | fgy32 | 32042.28 | 18 | fgy
INDUSTRIAL | smr12 | 37387308.69 | 3 | smr
NCONUML | mfa34 | 19451.19 | 8 | mfa
FARM | wots13 | 4844280.0942 | 510 | wots
COMMERCIAL | drn21 | 3220798.94 | 52 | drn
INDUSTRIAL | wo31 | 765.77 | 1 | wo
| fgy32 | 8528.5063 | 10 | fgy
INDUSTRIAL | bwr32 | 3058614 | 72 | bwr
| elm23 | 20831.6 | 30 | elm
INDUSTRIAL | mwl12 | 574569.29 | 12 | mwl
RESIDENTL | cpk21 | 7771248.352 | 1679 | cpk
COMMERCIAL | wots11 | 6621581.9604 | 243 | wots
INDUSTRIAL | ftr21 | 313604.8 | 24 | ftr
NCONUML | lyd11 | 43059.75 | 9 | lyd
FARM | phm21 | 25361.56 | 3 | phm
INDUSTRIAL | wyk13 | 453974.55 | 15 | wyk
INDUSTRIAL | mdg1 | 21781.42 | 1 | mdg
INDUSTRIAL | tt1 | 7434378.9861 | 77 | tt
INDUSTRIAL | wgi34 | 1206209.57 | 8 | wgi
LIGHTING | wgi33 | 1050486.0487 | 2 | wgi
COMMERCIAL | wgl15 | 27996457.3831 | 596 | wgl
RESIDENTL | bge23 | 16900476.9279 | 2094 | bge
INDUSTRIAL | bwr13 | 2417661.2776 | 147 | bwr
NCONUML | epg23 | 28250.73 | 7 | epg
INDUSTRIAL | drn14 | 25996.95 | 2 | drn
RESIDENTL | drn14 | 23831050.9741 | 4399 | drn
RESIDENTL | rwt31 | 5842296.4371 | 1436 | rwt
COMMERCIAL | drn24 | 1717660.9 | 35 | drn
FARM | epg14 | 3614.72 | 1 | epg
RESIDENTL | smr13 | 11225814.5464 | 2447 | smr
COMMERCIAL | wots12 | 14359758.4732 | 371 | wots
COMMERCIAL | klk11 | 3080934.4269 | 114 | klk
NCONUML | mwl14 | 31252.61 | 13 | mwl
INDUSTRIAL | sle11 | 266690.1 | 32 | sle
NCONUML | epg31 | 41319.36 | 24 | epg
RESIDENTL | cf1 | 4176161.3871 | 493 | cf
INDUSTRIAL | phm34 | 816155.12 | 6 | phm
FARM | rwn34 | 20402.21 | 4 | rwn
| mby12 | 1524.95 | 3 | mby
RESIDENTL | wgi31 | 14866992.8529 | 3617 | wgi
RESIDENTL | wots25 | 16858284.9544 | 3532 | wots
RESIDENTL | cre33 | 21876811.5892 | 4235 | cre
RESIDENTL | fgy34 | 4606270.9018 | 975 | fgy
RESIDENTL | cyn32 | 15011504.2579 | 3573 | cyn
RESIDENTL | klk11 | 9194980.7775 | 1227 | klk
INDUSTRIAL | fgy33 | 1452360.19 | 13 | fgy
INDUSTRIAL | wgl13 | 6688610.4344 | 14 | wgl
| tgn41 | 12751.16 | 13 | tgn
COMMERCIAL | klk22 | 85830.78 | 8 | klk
| mby11 | 4292.69 | 12 | mby
FARM | drn12 | 9939.61 | 1 | drn
RESIDENTL | rwn24 | 15617115.6722 | 2794 | rwn
RESIDENTL | cre32 | 8053371.5554 | 2218 | cre
COMMERCIAL | bwn11 | 5920812.2037 | 76 | bwn
NCONUML | smg33 | 19709.42 | 12 | smg
INDUSTRIAL | mby11 | 90387.22 | 16 | mby
COMMERCIAL | tgn41 | 8173213.7745 | 338 | tgn
INDUSTRIAL | wn7 | 3582803.57 | 9 | wn
FARM | bwr23 | 29264.76 | 8 | bwr
RESIDENTL | bwn13 | 8026926.4045 | 1629 | bwn
FARM | wgi24 | 1757204.2906 | 142 | wgi
| rve13 | 21148.03 | 29 | rve
RESIDENTL | wgl21 | 23764201.6622 | 4642 | wgl
COMMERCIAL | wn1 | 22168293.2818 | 620 | wn
INDUSTRIAL | cyn32 | 738566.1077 | 85 | cyn
| hpk21 | 27858.58 | 57 | hpk
COMMERCIAL | klo11 | 2030116.61 | 11 | klo
INDUSTRIAL | bn22 | 260832.7234 | 23 | bn
| ofr24 | 25053.77 | 43 | ofr
| drn12 | 30292.1138 | 29 | drn
COMMERCIAL | smg22 | 18806077.0677 | 136 | smg
COMMERCIAL | bwa22 | 4509592.2057 | 144 | bwa
COMMERCIAL | drn12 | 15118769.4919 | 112 | drn
| ldl23 | 80304.9161 | 48 | ldl
| rwn32 | 14306.27 | 22 | rwn
| drn23 | 12868.4314 | 15 | drn
RESIDENTL | mwl22 | 12904194.2639 | 2809 | mwl
COMMERCIAL | tt6 | 3682930.1298 | 115 | tt
COMMERCIAL | bra24 | 3429037.1414 | 127 | bra
NCONUML | hpk11 | 112614.82 | 31 | hpk
RESIDENTL | mfa21 | 12551518.2306 | 1921 | mfa
RESIDENTL | bge22 | 19945240.9452 | 3164 | bge
| tt4 | 9710.0483 | 41 | tt
NCONUML | phm22 | 22255.8232 | 9 | phm
COMMERCIAL | fgy21 | 1241019.6707 | 34 | fgy
INDUSTRIAL | nla31 | 516137.35 | 16 | nla
FARM | wyk13 | 707273.0378 | 84 | wyk
NCONUML | elm25 | 44655.33 | 20 | elm
| ofr23 | 28214.1089 | 26 | ofr
INDUSTRIAL | ruba22 | 167892.49 | 8 | ruba
FARM | hpk21 | 3124.97 | 1 | hpk
FARM | wn4 | 999664.927 | 129 | wn
COMMERCIAL | wn6 | 8795190.5545 | 246 | wn
| cre23 | 50195.43 | 25 | cre
COMMERCIAL | bwr22 | 15914202.1636 | 269 | bwr
INDUSTRIAL | elm22 | 545216.4127 | 27 | elm
NCONUML | bwr32 | 46210.27 | 31 | bwr
COMMERCIAL | moe12 | 4799517.76 | 51 | moe
| drn22 | 43438.5 | 28 | drn
FARM | bn22 | 13032.09 | 3 | bn
FARM | ldl24 | 222231.4641 | 11 | ldl
| bdl31 | 24144.6762 | 16 | bdl
FARM | cpk11 | 227979.0877 | 18 | cpk
FARM | elm33 | 50441.5205 | 4 | elm
INDUSTRIAL | rve13 | 147824.4003 | 10 | rve
COMMERCIAL | uwy1 | 603856.89 | 33 | uwy
FARM | mfa21 | 13347321.3386 | 701 | mfa
RESIDENTL | wo14 | 1446838.665 | 266 | wo
NCONUML | rwt14 | 102266.96 | 37 | rwt
| kms11 | 9612.23 | 20 | kms
RESIDENTL | phi11 | 5828644.3864 | 1391 | phi
COMMERCIAL | tgn12 | 10174331.2835 | 242 | tgn
LIGHTING | drn21 | 522455.53 | 1 | drn
INDUSTRIAL | smr22 | 2060432.23 | 13 | smr
| moe21 | 19173.8011 | 29 | moe
NCONUML | fgy12 | 1668.8419 | 4 | fgy
COMMERCIAL | elm25 | 2590499.6378 | 73 | elm
| epg34 | 11737.1961 | 27 | epg
COMMERCIAL | cpk23 | 2022573.8223 | 44 | cpk
COMMERCIAL | sle31 | 4198591.4215 | 178 | sle
FARM | nrn13 | 23844.37 | 5 | nrn
FARM | elm26 | 83060.0495 | 12 | elm
INDUSTRIAL | rve12 | 67014.5 | 12 | rve
INDUSTRIAL | moe21 | 304282.5341 | 37 | moe
COMMERCIAL | ofr21 | 9424773.56 | 126 | ofr
FARM | wn3 | 4385381.9629 | 585 | wn
FARM | klk21 | 574949.1868 | 82 | klk
NCONUML | wyk13 | 97422.66 | 49 | wyk
FARM | bwn12 | 14573.05 | 3 | bwn
NCONUML | msd2 | 8161.26 | 6 | msd
COMMERCIAL | elm31 | 474386.1613 | 1 | elm
RESIDENTL | rwt35 | 12065.95 | 2 | rwt
RESIDENTL | wt6 | 15702930.1084 | 3397 | wt
RESIDENTL | cln24 | 3991370.9732 | 1090 | cln
COMMERCIAL | smg21 | 2744632.8687 | 43 | smg
| myt21 | 64545.94 | 22 | myt
RESIDENTL | lga22 | 9862202.3617 | 1608 | lga
INDUSTRIAL | cyn13 | 4447831.06 | 67 | cyn
COMMERCIAL | ruba12 | 6703349.3664 | 290 | ruba
| smr23 | 7378.7014 | 9 | smr
FARM | phi13 | 230339.12 | 15 | phi
RESIDENTL | wt11 | 8665012.8839 | 2213 | wt
RESIDENTL | bge13 | 9255563.8982 | 1458 | bge
COMMERCIAL | bge11 | 11367890.3817 | 330 | bge
COMMERCIAL | wgi23 | 2290528.82 | 95 | wgi
COMMERCIAL | epg35 | 29855241.8371 | 304 | epg
NCONUML | mwl23 | 55631.52 | 20 | mwl
RESIDENTL | tgn11 | 18615536.7391 | 4196 | tgn
RESIDENTL | klo24 | 35150523.3753 | 8219 | klo
| wgi32 | 32777.55 | 36 | wgi
| uwy1 | 1895.86 | 6 | uwy
COMMERCIAL | wots24 | 5008654.6646 | 265 | wots
INDUSTRIAL | phi13 | 601326.64 | 38 | phi
LIGHTING | cf1 | 76883.018 | 3 | cf
RESIDENTL | cre21 | 18876617.5647 | 4715 | cre
INDUSTRIAL | wo32 | 73086.25 | 1 | wo
COMMERCIAL | lga13 | 621321.4861 | 47 | lga
FARM | cnr2 | 245915.51 | 48 | cnr
COMMERCIAL | bge22 | 4521687.9575 | 100 | bge
INDUSTRIAL | cyn12 | 101425.5 | 5 | cyn
FARM | drn11 | 51881.33 | 8 | drn
INDUSTRIAL | wo23 | 212041.78 | 1 | wo
RESIDENTL | lga23 | 5064870.5947 | 821 | lga
RESIDENTL | bn12 | 3438265.7182 | 625 | bn
RESIDENTL | bra21 | 23268334.8963 | 5707 | bra
| bdl42 | 11198.42 | 14 | bdl
FARM | cnr1 | 2440.03 | 2 | cnr
| phm34 | 68320.3174 | 32 | phm
FARM | rwt31 | 12148.87 | 1 | rwt
| smg31 | 8879.89 | 17 | smg
LIGHTING | tgn11 | 1064655.8 | 1 | tgn
FARM | llg14 | 4195351.6172 | 347 | llg
FARM | mwl11 | 2401732.236 | 295 | mwl
INDUSTRIAL | brt22 | 103539.39 | 15 | brt
COMMERCIAL | mwl14 | 15268408.4249 | 139 | mwl
RESIDENTL | wn1 | 4757807.4084 | 1039 | wn
COMMERCIAL | wo33 | 4706642.85 | 27 | wo
| nrn14 | 10562.91 | 10 | nrn
RESIDENTL | wgl15 | 10836827.2608 | 2158 | wgl
RESIDENTL | mfa22 | 4069843.249 | 701 | mfa
NCONUML | wyk24 | 96009.71 | 32 | wyk
NCONUML | rwn34 | 17137.95 | 21 | rwn
NCONUML | rve11 | 32578.28 | 16 | rve
INDUSTRIAL | klk11 | 54511.69 | 7 | klk
RESIDENTL | tt2 | 73044.37 | 7 | tt
COMMERCIAL | rwn32 | 3002784.6794 | 97 | rwn
NCONUML | tt1 | 9612.49 | 4 | tt
NCONUML | bwr23 | 79898.93 | 30 | bwr
NCONUML | epg14 | 19866.64 | 14 | epg
| elm26 | 27328.755 | 32 | elm
INDUSTRIAL | bdl32 | 418697.92 | 34 | bdl
FARM | wt11 | 3746.97 | 1 | wt
NCONUML | ofr23 | 50364.93 | 30 | ofr
INDUSTRIAL | smg23 | 412547.84 | 9 | smg
LIGHTING | klo14 | 3058096.87 | 1 | klo
| nrn13 | 13473.67 | 22 | nrn
FARM | bra12 | 12444.91 | 1 | bra
COMMERCIAL | cre21 | 15222170.3645 | 489 | cre
INDUSTRIAL | wgi32 | 984365.53 | 33 | wgi
NCONUML | rwt25 | 118451.05 | 54 | rwt
INDUSTRIAL | mwe236 | 280541.09 | 16 | mwe
RESIDENTL | epg33 | 183201.2006 | 6 | epg
INDUSTRIAL | elm33 | 243571.284 | 12 | elm
RESIDENTL | ldl11 | 13512975.3636 | 2241 | ldl
| mwl12 | 15850.97 | 9 | mwl
INDUSTRIAL | fgy21 | 6595081.67 | 18 | fgy
LIGHTING | smr24 | 109914.08 | 1 | smr
RESIDENTL | rwt25 | 10768082.8154 | 2324 | rwt
INDUSTRIAL | rwt15 | 3409961.2906 | 83 | rwt
INDUSTRIAL | phi12 | 3418741.3516 | 25 | phi
INDUSTRIAL | bwa22 | 1592049.74 | 9 | bwa
NCONUML | wo22 | 90587.46 | 26 | wo
INDUSTRIAL | ldl21 | 599666.7 | 44 | ldl
INDUSTRIAL | wt6 | 1814.16 | 1 | wt
NCONUML | ofr22 | 9198.59 | 2 | ofr
INDUSTRIAL | bra13 | 1860337.5903 | 47 | bra
COMMERCIAL | fgy24 | 2616699.5517 | 109 | fgy
RESIDENTL | epg11 | 6094828.0666 | 1503 | epg
NCONUML | rwt36 | 1279.88 | 1 | rwt
RESIDENTL | bwn14 | 23184606.5946 | 3016 | bwn
COMMERCIAL | bra31 | 7996775.7312 | 141 | bra
| nla32 | 13550.62 | 15 | nla
FARM | brt11 | 223967.42 | 33 | brt
| hpk12 | 10433.13 | 13 | hpk
INDUSTRIAL | llg13 | 899195.7591 | 21 | llg
INDUSTRIAL | wgl21 | 1687828.17 | 29 | wgl
INDUSTRIAL | cnr2 | 615523.18 | 19 | cnr
INDUSTRIAL | mfa14 | 499885.98 | 5 | mfa
RESIDENTL | drn13 | 15714620.5428 | 2698 | drn
FARM | kms12 | 1180373.8068 | 156 | kms
COMMERCIAL | rwn24 | 15303994.2605 | 63 | rwn
NCONUML | wn4 | 65357.11 | 21 | wn
COMMERCIAL | rwn33 | 562037.42 | 22 | rwn
| moe22 | 3614.75 | 12 | moe
| wgl13 | 39374.2 | 44 | wgl
| moe11 | 8193.3901 | 21 | moe
COMMERCIAL | wt7 | 4475658.5866 | 198 | wt
NCONUML | bwr13 | 106489.72 | 46 | bwr
NCONUML | kms12 | 115620.45 | 45 | kms
NCONUML | cyn24 | 41312.6858 | 21 | cyn
COMMERCIAL | mwl13 | 8520395.3383 | 232 | mwl
COMMERCIAL | cyn32 | 10902527.7138 | 351 | cyn
INDUSTRIAL | tgn31 | 3050316.88 | 29 | tgn
| wo13 | 12961.22 | 9 | wo
NCONUML | bra12 | 30121.15 | 6 | bra
| mwl24 | 4141.68 | 3 | mwl
RESIDENTL | ftr22 | 5196242.6186 | 1010 | ftr
| cyn12 | 33132.831 | 28 | cyn
| mwl11 | 4217.9 | 11 | mwl
NCONUML | sle13 | 9744.3474 | 7 | sle
RESIDENTL | sle14 | 16027394.2978 | 4223 | sle
RESIDENTL | wgl23 | 5362246.1099 | 739 | wgl
COMMERCIAL | cre23 | 25513720.5265 | 132 | cre
RESIDENTL | bdl43 | 5886157.096 | 1122 | bdl
RESIDENTL | bge21 | 100743.92 | 11 | bge
RESIDENTL | smg22 | 10427736.14 | 2476 | smg
FARM | rwn31 | 347566.14 | 21 | rwn
INDUSTRIAL | bn12 | 8173831.79 | 6 | bn
| wgi24 | 27543.5394 | 32 | wgi
| mfa23 | 2828.28 | 3 | mfa
NCONUML | elm22 | 93887.89 | 42 | elm
INDUSTRIAL | wots13 | 2426481.9937 | 28 | wots
RESIDENTL | mwl13 | 9372820.2657 | 1896 | mwl
COMMERCIAL | epg31 | 8736205.1691 | 170 | epg
| bdl44 | 43009.9658 | 33 | bdl
COMMERCIAL | wgl24 | 14484234.4559 | 200 | wgl
INDUSTRIAL | wn3 | 1104797.78 | 30 | wn
| wgi33 | 38017.7186 | 28 | wgi
NCONUML | wo31 | 91536.41 | 24 | wo
FARM | ldl14 | 3990495.203 | 142 | ldl
NCONUML | wyk12 | 43139.17 | 24 | wyk
INDUSTRIAL | mwl15 | 15961047.4 | 1 | mwl
LIGHTING | bdl32 | 23514.52 | 1 | bdl
| rve12 | 15159.19 | 33 | rve
NCONUML | phm34 | 55440.25 | 17 | phm
COMMERCIAL | phm22 | 18761180.3018 | 732 | phm
RESIDENTL | cyn22 | 8715945.6121 | 2142 | cyn
FARM | fgy31 | 3345.68 | 2 | fgy
RESIDENTL | smr22 | 8159798.5324 | 1327 | smr
RESIDENTL | cyn23 | 7298806.6664 | 1621 | cyn
FARM | bdl42 | 2407309.4815 | 483 | bdl
| wyk23 | 31976.68 | 33 | wyk
INDUSTRIAL | rwn26 | 257525.5397 | 10 | rwn
NCONUML | bwn11 | 91006.47 | 23 | bwn
COMMERCIAL | cyn23 | 7883296.3431 | 299 | cyn
| moe15 | 19145.0797 | 16 | moe
| drn11 | 44271.4909 | 65 | drn
INDUSTRIAL | moe22 | 88009.47 | 4 | moe
NCONUML | mdg1 | 4146.1 | 9 | mdg
FARM | bra33 | 5568.67 | 1 | bra
LIGHTING | bwa22 | 75542.46 | 1 | bwa
NCONUML | hpk14 | 64164.68 | 20 | hpk
NCONUML |  | 262.3928 | 5 | #REF!
INDUSTRIAL | cln13 | 2016187.9013 | 2 | cln
FARM | ofr11 | 1184021.9516 | 51 | ofr
FARM | phm31 | 2011038.4476 | 90 | phm
NCONUML | elm21 | 62554.36 | 23 | elm
NCONUML | wt8 | 36862.33 | 14 | wt
NCONUML | cnr1 | 1922.85 | 2 | cnr
INDUSTRIAL | cre31 | 212230.18 | 2 | cre
COMMERCIAL | mfa34 | 8313764.4144 | 170 | mfa
INDUSTRIAL | tt5 | 637183.9506 | 23 | tt
INDUSTRIAL | llg14 | 1201432.9268 | 29 | llg
RESIDENTL | wo23 | 1549813.7708 | 361 | wo
| bwr23 | 25383.1703 | 47 | bwr
| sle11 | 3997.21 | 10 | sle
NCONUML | epg22 | 8538.04 | 7 | epg
NCONUML | bwr24 | 20744.02 | 14 | bwr
INDUSTRIAL | myt12 | 952524.23 | 20 | myt
| ftr23 | 53453.1274 | 33 | ftr
RESIDENTL | bra11 | 9331476.9371 | 2277 | bra
FARM | ldl13 | 3504918.0126 | 302 | ldl
| brt11 | 8693.81 | 14 | brt
INDUSTRIAL | phm31 | 91642.7039 | 2 | phm
COMMERCIAL | bdl43 | 22280533.2345 | 523 | bdl
FARM | moe23 | 4928404.5033 | 365 | moe
| klk21 | 7164.56 | 8 | klk
| wt7 | 8483.27 | 17 | wt
FARM | llg11 | 4501914.1562 | 365 | llg
LIGHTING | cf2 | 13221.322 | 1 | cf
| tgn31 | 23134.1673 | 13 | tgn
RESIDENTL | nla31 | 3471883.5329 | 742 | nla
COMMERCIAL | bdl31 | 6479518.62 | 206 | bdl
COMMERCIAL | smr23 | 799486.21 | 26 | smr
INDUSTRIAL | rve11 | 154936.16 | 21 | rve
RESIDENTL | bm8b33 | 130717.0048 | 17 | bmb
FARM | phi12 | 364625.9 | 40 | phi
INDUSTRIAL | klk22 | 5518.6 | 1 | klk
RESIDENTL | llg12 | 7619865.2998 | 1210 | llg
RESIDENTL | cln21 | 24090170.4832 | 5877 | cln
NCONUML | cpk11 | 17830.25 | 17 | cpk
COMMERCIAL | ruba22 | 3463594.5603 | 120 | ruba
NCONUML | brt22 | 9306.55 | 7 | brt
INDUSTRIAL | epg32 | 7635590.16 | 5 | epg
INDUSTRIAL | cln12 | 360384.55 | 1 | cln
COMMERCIAL | bwr13 | 10101102.0366 | 288 | bwr
COMMERCIAL | wo22 | 9017310.64 | 153 | wo
INDUSTRIAL | hpk24 | 9439809.63 | 31 | hpk
COMMERCIAL | cpk12 | 5057421.24 | 115 | cpk
| lyd14 | 55928.8081 | 17 | lyd
INDUSTRIAL | klo11 | 67703.26 | 1 | klo
RESIDENTL | ldl14 | 11349760.1474 | 1905 | ldl
LIGHTING | myt21 | 2294.9 | 1 | myt
RESIDENTL | rwn22 | 13452598.5118 | 2640 | rwn
COMMERCIAL | bm8b32 | 168652.4116 | 16 | bmb
INDUSTRIAL | bdl34 | 328519.77 | 31 | bdl
| tt12 | 16952.1045 | 5 | tt
RESIDENTL | wots24 | 6979604.5034 | 1172 | wots
INDUSTRIAL | wyk24 | 160679.33 | 16 | wyk
COMMERCIAL | klo12 | 12237846.22 | 9 | klo
RESIDENTL | wo33 | 232024.16 | 58 | wo
COMMERCIAL | bn24 | 3468313.5774 | 163 | bn
COMMERCIAL | lga12 | 9341312.33 | 61 | lga
| msd1 | 16071.3636 | 20 | msd
INDUSTRIAL | ofr24 | 300622.14 | 4 | ofr
INDUSTRIAL | bwn13 | 24333.45 | 4 | bwn
| tt1 | 26786.62 | 3 | tt
INDUSTRIAL | rwt31 | 22449174.23 | 3 | rwt
FARM | mfa14 | 28798.91 | 1 | mfa
| bwr32 | 10607.4826 | 52 | bwr
INDUSTRIAL | wn4 | 1120535.2101 | 54 | wn
RESIDENTL | bwr12 | 975012.274 | 199 | bwr
INDUSTRIAL | wgi24 | 1432383.73 | 33 | wgi
| llg13 | 135285.4952 | 24 | llg
| rwn34 | 10950.9 | 10 | rwn
FARM | elm34 | 16399.68 | 6 | elm
RESIDENTL | ruba12 | 12797333.4035 | 1890 | ruba
COMMERCIAL | hpk22 | 5875279.82 | 181 | hpk
| cln11 | 262675.9461 | 229 | cln
RESIDENTL | cf2 | 494427.3912 | 409 | cf
FARM | elm22 | 15544.2323 | 4 | elm
INDUSTRIAL | smg32 | 67645.78 | 1 | smg
FARM | bwa23 | 3495492.525 | 169 | bwa
NCONUML | phm24 | 66511.6 | 15 | phm
NCONUML | wgi23 | 35701.3 | 15 | wgi
NCONUML | epg35 | 18576.68 | 9 | epg
NCONUML | llg13 | 26801.83 | 12 | llg
LIGHTING | phi13 | 74566.47 | 1 | phi
| ldl24 | 28689.7774 | 48 | ldl
| bge11 | 41147.6131 | 30 | bge
RESIDENTL | ofr21 | 18456788.2346 | 4412 | ofr
INDUSTRIAL | ofr11 | 52339.71 | 6 | ofr
COMMERCIAL | nrn11 | 8254682.48 | 13 | nrn
FARM | moe15 | 1053275.4428 | 126 | moe
INDUSTRIAL | lyd12 | 15947.41 | 3 | lyd
INDUSTRIAL | wt10 | 5540.7 | 1 | wt
RESIDENTL | rwt21 | 965731.93 | 282 | rwt
FARM | wo13 | 51683.13 | 6 | wo
INDUSTRIAL | epg34 | 25722.81 | 2 | epg
COMMERCIAL | lys36 | 31611.41 | 1 | lys
RESIDENTL | wn6 | 17451542.0984 | 3750 | wn
NCONUML | hpk12 | 23613.79 | 7 | hpk
INDUSTRIAL | ruba24 | 189283.4035 | 13 | ruba
| nrn12 | 36108.6 | 9 | nrn
NCONUML | nla32 | 30069.03 | 18 | nla
COMMERCIAL | bm8b31 | 174913.9253 | 14 | bmb
| wo22 | 26321.2427 | 38 | wo
INDUSTRIAL | fgy31 | 4952.61 | 1 | fgy
RESIDENTL | cln14 | 25051991.2109 | 8311 | cln
RESIDENTL | lga24 | 3807672.9803 | 653 | lga
RESIDENTL | bra31 | 2624204.8049 | 649 | bra
COMMERCIAL | cln21 | 7282112.3749 | 104 | cln
COMMERCIAL | ftr23 | 8984637.4811 | 336 | ftr
RESIDENTL | klo13 | 97850.5847 | 89 | klo
INDUSTRIAL | ofr14 | 250.62 | 1 | ofr
FARM | mwl24 | 966080.4815 | 75 | mwl
NCONUML | bdl41 | 86032.0652 | 28 | bdl
INDUSTRIAL | epg13 | 201122.3196 | 20 | epg
COMMERCIAL | tgn23 | 6173474.1124 | 95 | tgn
| moe12 | 11374.0239 | 16 | moe
INDUSTRIAL | drn11 | 8297.91 | 2 | drn
| wn4 | 46461.2191 | 29 | wn
NCONUML | wgl13 | 85005.64 | 23 | wgl
INDUSTRIAL | ftr22 | 264831.3749 | 23 | ftr
NCONUML | mjg11 | 5653.43 | 3 | mjg
RESIDENTL | klo12 | 526.2 | 1 | klo
COMMERCIAL | cln11 | 18408618.7138 | 182 | cln
NCONUML | wo13 | 11132.69 | 4 | wo
COMMERCIAL | yn38 | 28127.08 | 5 | yn
NCONUML | mwl24 | 19701.6 | 5 | mwl
RESIDENTL | wots12 | 7880580.6899 | 1786 | wots
COMMERCIAL | tgn43 | 5598797.62 | 126 | tgn
NCONUML | mfa23 | 6277.17 | 3 | mfa
NCONUML | bra32 | 63005.82 | 38 | bra
FARM | bdl34 | 247623.03 | 51 | bdl
INDUSTRIAL | wn5 | 6299826.69 | 33 | wn
| mby13 | 155.9226 | 1 | mby
FARM | ofr23 | 2419763.5413 | 305 | ofr
NCONUML | cre22 | 86458.6773 | 42 | cre
NCONUML | hpk23 | 84001.53 | 23 | hpk
RESIDENTL | bra24 | 8260262.5707 | 1824 | bra
| cyn14 | 12637.7523 | 26 | cyn
LIGHTING | wgl11 | 2443513.25 | 2 | wgl
NCONUML | wgi24 | 69610.83 | 24 | wgi
COMMERCIAL | klo14 | 11961206.944 | 269 | klo
FARM | drn14 | 379625.3327 | 36 | drn
RESIDENTL | bwr22 | 1941843.629 | 510 | bwr
| llg14 | 42684.6726 | 22 | llg
INDUSTRIAL | drn21 | 709809.96 | 3 | drn
INDUSTRIAL | tgn42 | 199383.97 | 5 | tgn
RESIDENTL | sle32 | 6677118.757 | 1350 | sle
RESIDENTL | myt12 | 14552002.0991 | 2380 | myt
FARM | myt21 | 821475.54 | 124 | myt
| bn11 | 39921.12 | 40 | bn
NCONUML | mby12 | 15769.2 | 4 | mby
NCONUML | bdl44 | 1602.59 | 5 | bdl
COMMERCIAL | tt12 | 10810239.5174 | 467 | tt
NCONUML | wn7 | 7884.6 | 2 | wn
| bdl34 | 14430.17 | 36 | bdl
RESIDENTL | lyd11 | 11014119.7855 | 2574 | lyd
FARM | wyk23 | 2329152.6841 | 202 | wyk
| epg23 | 66262.7623 | 20 | epg
RESIDENTL | rwt32 | 15157646.1346 | 3808 | rwt
RESIDENTL | cre31 | 23125994.5084 | 5990 | cre
FARM | bn11 | 9012293.1298 | 1372 | bn
COMMERCIAL |  | 2470964.7554 | 79 | #REF!
INDUSTRIAL | kms11 | 3849512.37 | 9 | kms
RESIDENTL | sle31 | 15232222.0022 | 4728 | sle
RESIDENTL | myt11 | 3230941.4261 | 365 | myt
| wyk12 | 33744.4845 | 17 | wyk
| lga11 | 13750.1489 | 25 | lga
COMMERCIAL | cre33 | 14716025.8299 | 132 | cre
RESIDENTL | trc01 | 404888.8876 | 85 | trc
| moe25 | 10579.3743 | 23 | moe
NCONUML | msd1 | 8725.66 | 9 | msd
RESIDENTL | mwl14 | 1637810.9082 | 178 | mwl
FARM | wn5 | 10157746.9699 | 1090 | wn
INDUSTRIAL | bwr33 | 13101695.07 | 41 | bwr
NCONUML | ofr24 | 72292.73 | 18 | ofr
| mdg1 | 5594.13 | 4 | mdg
FARM | wgi33 | 86057.74 | 7 | wgi
RESIDENTL | rwt22 | 12512450.4989 | 3066 | rwt
RESIDENTL | cnr2 | 3844076.3719 | 1054 | cnr
| hpk14 | 17565.23 | 35 | hpk
NCONUML | drn23 | 37389.78 | 20 | drn
RESIDENTL | tgn44 | 11943542.7304 | 2804 | tgn
| tgn42 | 0 | 1 | tgn
NCONUML | rwt22 | 27503.296 | 22 | rwt
FARM | mwl16 | 172184.54 | 14 | mwl
COMMERCIAL | nla34 | 1413700.5844 | 93 | nla
| epg22 | 2049.9261 | 2 | epg
FARM | tgn41 | 3728231.4432 | 423 | tgn
COMMERCIAL | lga23 | 3382991.9134 | 119 | lga
NCONUML | sle31 | 61055.23 | 20 | sle
NCONUML | tgn44 | 66469.79 | 20 | tgn
| phm24 | 18272.6834 | 34 | phm
RESIDENTL | hpk11 | 16523367.4098 | 4141 | hpk
| hpk13 | 40054.7485 | 22 | hpk
| bwr24 | 10180.34 | 28 | bwr
COMMERCIAL | bdl33 | 34051046.7333 | 257 | bdl
COMMERCIAL | wt9 | 7035668.1433 | 128 | wt
NCONUML | wt15 | 16005.53 | 14 | wt
FARM | ruba24 | 730484.142 | 55 | ruba
NCONUML | cpk23 | 20021.69 | 18 | cpk
INDUSTRIAL | mwl21 | 320021.87 | 5 | mwl
COMMERCIAL | hpk23 | 12064171.7331 | 206 | hpk
INDUSTRIAL | wt11 | 2563605.84 | 2 | wt
RESIDENTL | wt15 | 8580853.2399 | 1947 | wt
| elm21 | 24345.52 | 16 | elm
INDUSTRIAL | mwl16 | 183545.9668 | 9 | mwl
FARM | rve13 | 9637.99 | 1 | rve
NCONUML | drn22 | 69938.3 | 27 | drn
NCONUML | bdl31 | 70697.58 | 29 | bdl
NCONUML | bwa24 | 1320.25 | 1 | bwa
COMMERCIAL | mwl23 | 10773058.8537 | 154 | mwl
COMMERCIAL | elm23 | 5093994.3825 | 95 | elm
FARM | smr23 | 1078615.6398 | 156 | smr
| cpk11 | 37835.6667 | 47 | cpk
INDUSTRIAL | bra14 | 14750.52 | 4 | bra
RESIDENTL | rwn33 | 5693275.4596 | 1153 | rwn
| bn22 | 41634.09 | 21 | bn
INDUSTRIAL | tt2 | 11531135.8238 | 100 | tt
INDUSTRIAL | wt12 | 3871876.0911 | 67 | wt
INDUSTRIAL | mwl22 | 292678.42 | 8 | mwl
RESIDENTL | bn23 | 8695284.412 | 1665 | bn
COMMERCIAL | cyn11 | 9621618.8569 | 233 | cyn
| cyn21 | 22400.14 | 28 | cyn
INDUSTRIAL | mjg11 | 1321804.29 | 13 | mjg
INDUSTRIAL | cf2 | 1970.494 | 2 | cf
RESIDENTL | tt5 | 6560032.4165 | 1633 | tt
COMMERCIAL | smr14 | 6818307.6657 | 239 | smr
COMMERCIAL | smg33 | 1348313.99 | 14 | smg
RESIDENTL | rwt15 | 11066767.0768 | 2454 | rwt
COMMERCIAL | cre32 | 14440881.1645 | 427 | cre
INDUSTRIAL | smr24 | 4639865.5557 | 45 | smr
COMMERCIAL | fgy23 | 10185283.97 | 98 | fgy
COMMERCIAL | hpk11 | 3476478.711 | 53 | hpk
| cre32 | 19011.64 | 13 | cre
NCONUML | wgl23 | 12760.41 | 6 | wgl
COMMERCIAL | nrn15 | 84419.81 | 3 | nrn
NCONUML | moe15 | 22748.39 | 11 | moe
RESIDENTL | tt12 | 86039.86 | 6 | tt
RESIDENTL | cyn31 | 8632445.7043 | 2077 | cyn
RESIDENTL | wgl24 | 16633542.8094 | 2715 | wgl
COMMERCIAL | wgi22 | 6881286.006 | 159 | wgi
INDUSTRIAL | smr13 | 992080.85 | 26 | smr
NCONUML | cpk12 | 17033.61 | 10 | cpk
NCONUML | ftr21 | 16597.26 | 11 | ftr
FARM | mwl12 | 18529.37 | 2 | mwl
INDUSTRIAL | epg33 | 1129768.4897 | 4 | epg
| wyk13 | 9658.4809 | 15 | wyk
LIGHTING | trc01 | 669938.2281 | 2 | trc
FARM | hpk13 | 2305.94 | 1 | hpk
RESIDENTL | tt6 | 19150788.3328 | 4695 | tt
FARM | tgn31 | 5369095.0164 | 562 | tgn
NCONUML | wgl24 | 11028.97 | 10 | wgl
INDUSTRIAL | brt11 | 82545.9018 | 12 | brt
LIGHTING | mby11 | 10728.24 | 1 | mby
NCONUML | myt21 | 24178.1 | 12 | myt
| wt10 | 6115.9374 | 5 | wt
RESIDENTL | bge12 | 9796026.1467 | 1789 | bge
FARM | myt11 | 2640136.7565 | 257 | myt
NCONUML | cyn11 | 21168.08 | 13 | cyn
INDUSTRIAL |  | 942329979.1078 | 12 | #REF!
INDUSTRIAL | elm34 | 168803.0667 | 15 | elm
| brt22 | 30486.3216 | 18 | brt
INDUSTRIAL | epg11 | 6777.42 | 2 | epg
RESIDENTL | elm34 | 19825611.7814 | 4189 | elm
COMMERCIAL | sle13 | 974523.8832 | 109 | sle
INDUSTRIAL | lga13 | 207007.5439 | 9 | lga
RESIDENTL | mwl23 | 3618535.6291 | 812 | mwl
| fgy14 | 28887.99 | 26 | fgy
COMMERCIAL | mby13 | 2521770.2974 | 71 | mby
| lga12 | 14720.56 | 12 | lga
RESIDENTL | cpk12 | 17343162.547 | 2927 | cpk
COMMERCIAL | wt5 | 19785711.5258 | 118 | wt
INDUSTRIAL | drn24 | 4643890.64 | 3 | drn
FARM | drn21 | 13254.24 | 1 | drn
NCONUML | mwl11 | 360.93 | 3 | mwl
RESIDENTL | epg34 | 15669683.4078 | 3862 | epg
NCONUML | wt10 | 27658.61 | 16 | wt
LIGHTING | rwt14 | 962126.36 | 3 | rwt
COMMERCIAL | drn23 | 5472888.3558 | 161 | drn
LIGHTING | bwn11 | 6340546.01 | 1 | bwn
INDUSTRIAL | sfs1 | 80102.39 | 5 | sfs
COMMERCIAL | phm34 | 4610839.9937 | 66 | phm
COMMERCIAL | mfa31 | 3803351.87 | 100 | mfa
INDUSTRIAL | rwt25 | 2203508.65 | 42 | rwt
| bwa22 | 41045.3074 | 24 | bwa
FARM | smr13 | 139441.5096 | 27 | smr
NCONUML | phi12 | 84007.84 | 24 | phi
| fgy21 | 10377.87 | 9 | fgy
NCONUML | rwt15 | 44056.974 | 28 | rwt
LIGHTING | nla34 | 5187.52 | 1 | nla
RESIDENTL | sfs1 | 6449039.4989 | 958 | sfs
RESIDENTL | msd4 | 16354350.3097 | 2395 | msd
INDUSTRIAL | phm33 | 724516.58 | 21 | phm
COMMERCIAL | wgl14 | 59932538.6 | 1 | wgl
COMMERCIAL | rwt31 | 3904134.109 | 54 | rwt
RESIDENTL | wt5 | 5466545.168 | 1335 | wt
FARM | ftr22 | 3872176.8459 | 271 | ftr
| wn5 | 51237.831 | 23 | wn
INDUSTRIAL | kms12 | 880994.04 | 26 | kms
NCONUML | rwt31 | 27889.28 | 18 | rwt
RESIDENTL | elm22 | 20622579.4478 | 3120 | elm
| bn24 | 7126.586 | 9 | bn
FARM | wots11 | 7572710.4051 | 689 | wots
INDUSTRIAL | myt11 | 122662.09 | 11 | myt
NCONUML | bdl32 | 81716.25 | 38 | bdl
NCONUML | cyn33 | 39860.39 | 20 | cyn
| lga13 | 7900.07 | 12 | lga
COMMERCIAL | wn7 | 705796.26 | 31 | wn
RESIDENTL | tgn23 | 12995258.1614 | 2157 | tgn
RESIDENTL | wgl12 | 18309192.1093 | 3011 | wgl
NCONUML | drn14 | 58816.42 | 20 | drn
INDUSTRIAL | tt9 | 1853761.73 | 4 | tt
RESIDENTL | kms12 | 23913269.0041 | 4277 | kms
COMMERCIAL | wgi33 | 13737748.8552 | 364 | wgi
COMMERCIAL | phm21 | 28428865.0993 | 838 | phm
FARM | sle32 | 5441049.7096 | 310 | sle
NCONUML | cyn32 | 58907.16 | 38 | cyn
INDUSTRIAL | msd2 | 165834.72 | 18 | msd
COMMERCIAL | bwr23 | 26845428.111 | 233 | bwr
RESIDENTL | msd2 | 5810770.2828 | 1153 | msd
FARM | klk11 | 2014936.8264 | 177 | klk
| wots12 | 13459.1171 | 22 | wots
INDUSTRIAL | rwn24 | 4339629.96 | 13 | rwn
INDUSTRIAL | tgn41 | 1853911.3546 | 62 | tgn
COMMERCIAL | smg32 | 6595824.87 | 22 | smg
| wgi34 | 86239.94 | 15 | wgi
RESIDENTL | bn22 | 13286130.4589 | 3118 | bn
RESIDENTL | mfa31 | 9237847.4317 | 2206 | mfa
COMMERCIAL | wgi34 | 9571334.08 | 60 | wgi
RESIDENTL | mdi1 | 176577.17 | 31 | mdi
NCONUML | rwn31 | 16738.19 | 15 | rwn
INDUSTRIAL | drn13 | 239296.9 | 11 | drn
INDUSTRIAL | bdl43 | 306419.52 | 21 | bdl
NCONUML | wo23 | 56204.51 | 16 | wo
COMMERCIAL | ftr21 | 2804675.8206 | 100 | ftr
COMMERCIAL | bwa23 | 206762.2501 | 23 | bwa
NCONUML | mfa21 | 28416.84 | 12 | mfa
| cln23 | 52144.7804 | 85 | cln
RESIDENTL | rve11 | 2276471.0008 | 508 | rve
COMMERCIAL | ofr24 | 6649904.8426 | 113 | ofr
NCONUML | phi13 | 105028.33 | 33 | phi
FARM | smg22 | 25054.15 | 4 | smg
FARM | bwn11 | 18419.1 | 1 | bwn
INDUSTRIAL | epg31 | 360181.3871 | 31 | epg
COMMERCIAL | fgy14 | 7872993.2117 | 231 | fgy
| ldl11 | 24480.7 | 22 | ldl
INDUSTRIAL | wgl24 | 939120.3004 | 39 | wgl
| phm22 | 31542.7748 | 10 | phm
COMMERCIAL | moe15 | 2469270.3666 | 172 | moe
| cnr3 | 100.0469 | 1 | cnr
RESIDENTL | bwn12 | 4456239.3509 | 1013 | bwn
COMMERCIAL | mwl24 | 5791496.4979 | 78 | mwl
COMMERCIAL | wo13 | 2493976.37 | 46 | wo
RESIDENTL | elm25 | 10534980.5572 | 2009 | elm
RESIDENTL | phm32 | 14466986.7977 | 3288 | phm
COMMERCIAL | ofr11 | 14130002.2904 | 224 | ofr
INDUSTRIAL | bge13 | 1057475.88 | 11 | bge
RESIDENTL | ofr22 | 7907197.5875 | 2174 | ofr
INDUSTRIAL | lga22 | 745287.81 | 44 | lga
FARM | hpk22 | 33600.65 | 5 | hpk
COMMERCIAL | epg23 | 63543126.9632 | 711 | epg
NCONUML | epg34 | 29379.47 | 21 | epg
| mwl23 | 14018.9088 | 10 | mwl
FARM | lyd14 | 350081.37 | 31 | lyd
| elm33 | 18371.0537 | 30 | elm
RESIDENTL | bwn11 | 14758921.2622 | 2984 | bwn
| cyn33 | 33636.86 | 37 | cyn
INDUSTRIAL | ldl13 | 1566146.5513 | 31 | ldl
NCONUML | smg32 | 19512.15 | 10 | smg
NCONUML | lga21 | 24931.49 | 9 | lga
RESIDENTL | mfa34 | 6438005.323 | 995 | mfa
COMMERCIAL | lga22 | 10229963.6597 | 340 | lga
COMMERCIAL | wgi31 | 4363035.5887 | 128 | wgi
| wt9 | 17175.83 | 21 | wt
INDUSTRIAL | mfa21 | 1292894.4886 | 57 | mfa
FARM | wgi32 | 343056.5273 | 19 | wgi
COMMERCIAL | bge21 | 44944.8 | 1 | bge
INDUSTRIAL | elm26 | 46289.86 | 5 | elm
NCONUML | msd4 | 12187.83 | 6 | msd
COMMERCIAL | bra21 | 14789918.5926 | 289 | bra
| cpk22 | 7305.07 | 12 | cpk
NCONUML | phm32 | 76324.09 | 20 | phm
NCONUML | sfs1 | 44865.78 | 10 | sfs
COMMERCIAL | lyd13 | 6072257.17 | 42 | lyd
FARM | cyn33 | 36456.98 | 4 | cyn
NCONUML | phm21 | 71428.0533 | 24 | phm
COMMERCIAL | sle32 | 5434267.6149 | 190 | sle
NCONUML | smg31 | 21751.86 | 17 | smg
NCONUML | wots11 | 25057.91 | 11 | wots
RESIDENTL | tgn43 | 15724147.9465 | 3608 | tgn
INDUSTRIAL | cyn21 | 9259443.95 | 23 | cyn
INDUSTRIAL | bn23 | 1923467.13 | 19 | bn
NCONUML | nrn14 | 79150.17 | 17 | nrn
NCONUML | cyn22 | 32483.16 | 10 | cyn
NCONUML | wgl12 | 47271.49 | 20 | wgl
COMMERCIAL | phm24 | 600129.57 | 25 | phm
NCONUML | lga11 | 25837.14 | 8 | lga
NCONUML | tgn41 | 7415.11 | 5 | tgn
RESIDENTL | wgl11 | 17118670.1537 | 3818 | wgl
RESIDENTL | wots11 | 15871220.8415 | 2910 | wots
| rwn31 | 40233.5106 | 27 | rwn
COMMERCIAL | elm32 | 8171019.0636 | 263 | elm
FARM | mby11 | 1335559.7721 | 187 | mby
INDUSTRIAL | mwl25 | 33119.15 | 8 | mwl
FARM | rwn26 | 5055.63 | 2 | rwn
| nla34 | 8234.98 | 10 | nla
RESIDENTL |  | 349105.8277 | 492 | #REF!
FARM | epg13 | 82815.8863 | 12 | epg
| wyk24 | 32167.14 | 30 | wyk
FARM | sle11 | 16862.17 | 6 | sle
COMMERCIAL | bm8b33 | 3349.12 | 2 | bmb
RESIDENTL | smg21 | 17914575.4009 | 3718 | smg
INDUSTRIAL | bdl42 | 622534.62 | 24 | bdl
| yn38 | 7519.7419 | 1 | yn
| phi13 | 28221.5917 | 27 | phi
| epg14 | 9258.9052 | 38 | epg
FARM | nla31 | 1791184.5035 | 140 | nla
INDUSTRIAL | wgi33 | 1188063.8119 | 37 | wgi
LIGHTING | phm33 | 4303153.65 | 2 | phm
RESIDENTL | phm33 | 12878778.4238 | 2134 | phm
COMMERCIAL | wgl23 | 3870974.8784 | 252 | wgl
NCONUML | wt5 | 58508.56 | 14 | wt
NCONUML | bwn14 | 81385.02 | 37 | bwn
NCONUML | mfa31 | 49958.93 | 14 | mfa
COMMERCIAL | bra12 | 23355928.37 | 122 | bra
NCONUML | wt13 | 98966.19 | 41 | wt
COMMERCIAL | klo24 | 13267963.2484 | 244 | klo
COMMERCIAL | bge12 | 6262328.83 | 64 | bge
COMMERCIAL | wn4 | 10511680.2174 | 332 | wn
INDUSTRIAL | tt6 | 2940006.87 | 14 | tt
FARM | cln13 | 4519.0334 | 1 | cln
RESIDENTL | bwa23 | 1839261.5711 | 259 | bwa
RESIDENTL | smr12 | 601661.7559 | 102 | smr
NCONUML | bra31 | 17155.48 | 11 | bra
FARM | cln22 | 84599.56 | 6 | cln
RESIDENTL | moe23 | 10757204.18 | 1872 | moe
FARM | bn23 | 4995698.9571 | 709 | bn
INDUSTRIAL | bwr12 | 7576207.2428 | 317 | bwr
COMMERCIAL | elm33 | 8652520.7547 | 229 | elm
RESIDENTL | tgn12 | 769554.192 | 239 | tgn
NCONUML | bn23 | 5729.17 | 9 | bn
| cyn11 | 35169.6447 | 13 | cyn
INDUSTRIAL | wots12 | 5742170.47 | 22 | wots
INDUSTRIAL | llg12 | 8080777.31 | 18 | llg
NCONUML | ofr14 | 11958.45 | 3 | ofr
RESIDENTL | rwn34 | 11161403.5989 | 1490 | rwn
RESIDENTL | fgy12 | 975691.3435 | 398 | fgy
COMMERCIAL | wyk24 | 11852940.7836 | 290 | wyk
COMMERCIAL | smr12 | 1199230.8 | 20 | smr
INDUSTRIAL | wgl11 | 590499.13 | 17 | wgl
INDUSTRIAL | moe13 | 8896507.14 | 13 | moe
INDUSTRIAL | wots11 | 14616083.73 | 22 | wots
NCONUML | epg13 | 4325.18 | 2 | epg
NCONUML | bn22 | 72789.04 | 38 | bn
RESIDENTL | bwr23 | 15381612.1105 | 3589 | bwr
NCONUML | cln13 | 19538.3161 | 10 | cln
COMMERCIAL | bwa24 | 4350900.07 | 4 | bwa
COMMERCIAL | bwr32 | 11258727.4704 | 251 | bwr
RESIDENTL | bra32 | 8710928.5985 | 2041 | bra
FARM | klo14 | 681766.459 | 92 | klo
INDUSTRIAL | tt7 | 9353368.9205 | 125 | tt
RESIDENTL | wo11 | 815896.564 | 156 | wo
LIGHTING | mwl24 | 803944.3 | 2 | mwl
COMMERCIAL | bwr24 | 7860784.794 | 262 | bwr
COMMERCIAL | drn14 | 5284276.4061 | 147 | drn
NCONUML | hpk24 | 27055.52 | 10 | hpk
| cyn32 | 34865.18 | 48 | cyn
| bra23 | 7974.72 | 25 | bra
RESIDENTL | rve13 | 16767421.4281 | 3587 | rve
COMMERCIAL | bwn13 | 11531398.8601 | 263 | bwn
FARM | cln23 | 76487.94 | 5 | cln
NCONUML | ruba24 | 1482.28 | 4 | ruba
COMMERCIAL | msd1 | 4448954.738 | 126 | msd
| phm31 | 2299.25 | 4 | phm
LIGHTING | wn1 | 677520.74 | 1 | wn
COMMERCIAL | wt8 | 2125517.5597 | 71 | wt
RESIDENTL | bdl33 | 5101200.3632 | 906 | bdl
COMMERCIAL | rwt21 | 33203170.5825 | 281 | rwt
FARM |  | 15223.9488 | 53 | #REF!
| fgy13 | 16173.63 | 19 | fgy
| wt11 | 14907.843 | 20 | wt
RESIDENTL | mwl24 | 4259131.5949 | 729 | mwl
INDUSTRIAL | bwn12 | 375603.57 | 33 | bwn
| lyd12 | 10355.6 | 16 | lyd
| lyd13 | 31235.27 | 24 | lyd
| elm32 | 28931.8643 | 22 | elm
RESIDENTL | ldl13 | 20183081.1078 | 3515 | ldl
COMMERCIAL | epg14 | 4722560.1631 | 66 | epg
FARM | epg32 | 616929.8369 | 16 | epg
| smg23 | 6841.4304 | 12 | smg
NCONUML | mwl16 | 31954.29 | 10 | mwl
COMMERCIAL | ofr22 | 3955299.41 | 63 | ofr
FARM | wgl24 | 9990463.449 | 886 | wgl
COMMERCIAL | llg14 | 8402501.0583 | 280 | llg
COMMERCIAL | wgi24 | 3234685.3433 | 136 | wgi
FARM | cnr3 | 47812.597 | 17 | cnr
| epg33 | 55263.0616 | 6 | epg
INDUSTRIAL | bra24 | 1115020.317 | 14 | bra
NCONUML | wgi33 | 84992.31 | 23 | wgi
FARM | rwt15 | 1849.17 | 1 | rwt
RESIDENTL | ldl12 | 620798.3677 | 119 | ldl
INDUSTRIAL | bwr22 | 8606432.4227 | 334 | bwr
FARM | cf2 | 2033.193 | 1 | cf
NCONUML | klo14 | 36515.49 | 28 | klo
INDUSTRIAL | trc01 | 31629.57 | 2 | trc
RESIDENTL | lga21 | 9412760.8279 | 1623 | lga
RESIDENTL | wt13 | 15834142.0313 | 3223 | wt
RESIDENTL | cyn13 | 3260017.5153 | 858 | cyn
INDUSTRIAL | ofr21 | 138382.59 | 9 | ofr
NCONUML | sle32 | 22407.43 | 13 | sle
COMMERCIAL | lyd12 | 210380 | 9 | lyd
NCONUML | wyk23 | 87622.06 | 45 | wyk
| fgy33 | 11652.67 | 18 | fgy
INDUSTRIAL | hpk22 | 98414.21 | 14 | hpk
NCONUML | sle11 | 59204.61 | 19 | sle
RESIDENTL | bwr13 | 20902397.8318 | 4170 | bwr
COMMERCIAL | rwn34 | 3999387.7688 | 144 | rwn
| hpk22 | 19671.58 | 41 | hpk
FARM | klk22 | 332413.14 | 10 | klk
INDUSTRIAL | wn1 | 2988984.92 | 20 | wn
NCONUML | rwn26 | 27156.61 | 25 | rwn
| bwr33 | 13120.641 | 3 | bwr
NCONUML | mby11 | 20114.34 | 7 | mby
RESIDENTL | smg33 | 11198068.0634 | 2626 | smg
FARM | bn12 | 813334.585 | 146 | bn
FARM | bdl32 | 1026406.0127 | 170 | bdl
FARM | drn24 | 15422429 | 2 | drn
LIGHTING | cre21 | 378603.77 | 3 | cre
RESIDENTL | smg32 | 834640.09 | 219 | smg
| wt12 | 39199.7023 | 19 | wt
FARM | bwn14 | 804408.7 | 76 | bwn
NCONUML | bwr33 | 16865.43 | 3 | bwr
INDUSTRIAL | rwn22 | 12871.85 | 4 | rwn
NCONUML | drn11 | 63307.01 | 20 | drn
INDUSTRIAL | mwl13 | 228128.43 | 11 | mwl
COMMERCIAL | elm22 | 6567142.5918 | 154 | elm
FARM | trc01 | 521142.3328 | 100 | trc
COMMERCIAL | rwt14 | 11855990.576 | 301 | rwt
INDUSTRIAL | sle14 | 1780526.4437 | 64 | sle
RESIDENTL | smr24 | 17064871.7804 | 2952 | smr
FARM | bwa22 | 1586063.9755 | 254 | bwa
NCONUML | tt4 | 37478.54 | 17 | tt
| tt9 | 28146.8116 | 74 | tt
COMMERCIAL | epg34 | 4040655.8363 | 65 | epg
FARM | nrn11 | 7816.07 | 2 | nrn
LIGHTING | cpk23 | 1632459.3 | 1 | cpk
RESIDENTL | fgy31 | 4476808.4262 | 913 | fgy
COMMERCIAL | fgy33 | 6399813.6929 | 132 | fgy
| cnr2 | 20535.9245 | 15 | cnr
INDUSTRIAL | sle32 | 10933678.58 | 25 | sle
| bra13 | 120577.89 | 18 | bra
RESIDENTL | wgi23 | 12118480.0079 | 2685 | wgi
INDUSTRIAL | wn6 | 922850.6842 | 19 | wn
LIGHTING | tgn44 | 752.53 | 1 | tgn
RESIDENTL | wt8 | 8250779.9392 | 1851 | wt
COMMERCIAL | moe25 | 5695010.3572 | 176 | moe
FARM | wgi34 | 4315044.5216 | 374 | wgi
INDUSTRIAL | fgy32 | 667572.7217 | 61 | fgy
NCONUML | wo32 | 55386.46 | 14 | wo
INDUSTRIAL | lys36 | 1267258.48 | 1 | lys
| bn12 | 10728.35 | 13 | bn
NCONUML | brt11 | 10828.27 | 7 | brt
| drn21 | 27694.76 | 39 | drn
| drn24 | 16030.7 | 26 | drn
RESIDENTL | cpk23 | 11646034.7633 | 2466 | cpk
RESIDENTL | wots13 | 7948103.7952 | 1344 | wots
FARM | wgl23 | 3908847.1376 | 390 | wgl
COMMERCIAL | wyk13 | 4417313.7071 | 191 | wyk
NCONUML | klk21 | 10664.54 | 6 | klk
INDUSTRIAL | smg22 | 31514.93 | 2 | smg
RESIDENTL | wgi22 | 12719214.8315 | 3088 | wgi
| cpk13 | 49314.0333 | 41 | cpk
COMMERCIAL | bdl41 | 11311068.2286 | 367 | bdl
NCONUML | nrn12 | 43208.48 | 18 | nrn
RESIDENTL | fgy23 | 5177398.3937 | 1023 | fgy
NCONUML | brt21 | 3240.29 | 5 | brt
NCONUML | tgn31 | 2100.01 | 7 | tgn
RESIDENTL | mjg11 | 6256821.3625 | 1064 | mjg
INDUSTRIAL | lga24 | 175905.212 | 21 | lga
COMMERCIAL | moe21 | 6644337.36 | 291 | moe
INDUSTRIAL | bwn14 | 326743.47 | 17 | bwn
INDUSTRIAL | phm22 | 15545673.5732 | 29 | phm
LIGHTING | klo24 | 2201282.63 | 3 | klo
FARM | epg12 | 13782.33 | 2 | epg
INDUSTRIAL | cln14 | 247.5387 | 1 | cln
FARM | bge13 | 383352.554 | 75 | bge
NCONUML | bra14 | 25509.54 | 26 | bra
RESIDENTL | fgy24 | 17189073.2659 | 3574 | fgy
NCONUML | lyd14 | 37348.84 | 18 | lyd
FARM | fgy21 | 91303 | 9 | fgy
INDUSTRIAL | elm24 | 6476.78 | 2 | elm
FARM | bra24 | 985.88 | 1 | bra
COMMERCIAL | ldl24 | 1420329.0926 | 55 | ldl
INDUSTRIAL | wots24 | 329358.8434 | 32 | wots
| moe13 | 6325.43 | 5 | moe
COMMERCIAL | cyn14 | 5422735.5047 | 221 | cyn
LIGHTING | smg21 | 4640189.26 | 4 | smg
COMMERCIAL | tgn42 | 24454733.755 | 420 | tgn
INDUSTRIAL | lga14 | 502652.15 | 16 | lga
INDUSTRIAL | cre33 | 377497.19 | 17 | cre
FARM | ldl11 | 223383.36 | 16 | ldl
INDUSTRIAL | bn24 | 28582582.13 | 34 | bn
COMMERCIAL | tt1 | 14308038.8686 | 155 | tt
| wn3 | 30735.58 | 33 | wn
NCONUML | ldl21 | 10778.31 | 7 | ldl
NCONUML | wt6 | 188781.23 | 35 | wt
RESIDENTL | elm23 | 20356024.4153 | 3325 | elm
COMMERCIAL | drn11 | 4003224.2127 | 79 | drn
COMMERCIAL | bra34 | 7850026.49 | 9 | bra
FARM | cyn32 | 3133.97 | 2 | cyn
FARM | cpk23 | 18946.87 | 2 | cpk
FARM | wt15 | 5251.96 | 1 | wt
NCONUML | wgi32 | 95036.63 | 31 | wgi
COMMERCIAL | phm32 | 13343791.1884 | 221 | phm
COMMERCIAL | epg22 | 38007492.3668 | 89 | epg
INDUSTRIAL | wgl15 | 1553419.6108 | 26 | wgl
FARM | phm33 | 7138587.5126 | 545 | phm
LIGHTING | bra32 | 1301740.84 | 1 | bra
COMMERCIAL | bra22 | 30448240 | 1 | bra
COMMERCIAL | msd4 | 11090376.2999 | 395 | msd
COMMERCIAL | lyd14 | 7038791.6959 | 51 | lyd
| phi12 | 701365.4285 | 34 | phi
| nrn11 | 5120.38 | 9 | nrn
INDUSTRIAL | smg21 | 777155.28 | 5 | smg
NCONUML | nla31 | 5002.08 | 5 | nla
RESIDENTL | wyk13 | 19583843.7522 | 3346 | wyk
RESIDENTL | tgn41 | 6800482.2089 | 1104 | tgn
COMMERCIAL | fgy34 | 7285642.6158 | 201 | fgy
FARM | wgl11 | 5210774.8775 | 355 | wgl
FARM | tgn11 | 616949.6887 | 82 | tgn
NCONUML | wn5 | 5268.61 | 9 | wn
NCONUML | bdl42 | 6088.6 | 9 | bdl
INDUSTRIAL | hpk23 | 515987.93 | 6 | hpk
FARM | tgn44 | 47621.17 | 6 | tgn
| smr13 | 35140.976 | 19 | smr
| wgi31 | 18377.08 | 37 | wgi
NCONUML | bwr34 | 85519.21 | 30 | bwr
| bdl32 | 24365.9844 | 40 | bdl
COMMERCIAL | fgy13 | 5672167.28 | 57 | fgy
INDUSTRIAL | sle31 | 621920.2305 | 85 | sle
NCONUML | cyn23 | 72679.67 | 24 | cyn
NCONUML | hpk22 | 92149.17 | 38 | hpk
RESIDENTL | cre23 | 13902510.3441 | 3180 | cre
COMMERCIAL | lga21 | 4415159.211 | 179 | lga
| cre33 | 51988.0123 | 70 | cre
INDUSTRIAL | bra32 | 800790.5812 | 33 | bra
| rwn26 | 43959.1499 | 36 | rwn
NCONUML | ftr22 | 27457.1971 | 11 | ftr
FARM | cyn23 | 28738.28 | 3 | cyn
FARM | wn2 | 2722540.844 | 262 | wn
FARM | wots25 | 1192605.1156 | 155 | wots
COMMERCIAL | lga11 | 2601951.4442 | 115 | lga
COMMERCIAL | cnr1 | 836269.15 | 40 | cnr
RESIDENTL | cre22 | 15737441.9951 | 3931 | cre
RESIDENTL | cyn24 | 3227627.7482 | 729 | cyn
| drn14 | 42739.5968 | 43 | drn
NCONUML | wgi34 | 240.62 | 2 | wgi
COMMERCIAL | mdi1 | 200221.43 | 4 | mdi
LIGHTING | lga22 | 290997.27 | 1 | lga
RESIDENTL | sle13 | 2426821.6594 | 1643 | sle
RESIDENTL | mby12 | 3267894.3821 | 609 | mby
FARM | wgi31 | 368672.79 | 43 | wgi
INDUSTRIAL | cyn24 | 15644182.2427 | 207 | cyn
| fgy34 | 3433.61 | 11 | fgy
RESIDENTL | bge11 | 15368827.4604 | 2654 | bge
RESIDENTL | ftr12 | 3825364.7454 | 636 | ftr
| mfa21 | 17049.39 | 26 | mfa
COMMERCIAL | wgi21 | 45541.7604 | 2 | wgi
INDUSTRIAL | wo14 | 2975508 | 24 | wo
COMMERCIAL | wgl12 | 5759083.9004 | 210 | wgl
INDUSTRIAL | moe23 | 765740.5661 | 26 | moe
COMMERCIAL | hpk14 | 5487941.7 | 85 | hpk
NCONUML | tt2 | 10017.24 | 3 | tt
INDUSTRIAL | cpk13 | 1507420.269 | 6 | cpk
INDUSTRIAL | lga41 | 52440142.6 | 1 | lga
NCONUML | elm26 | 60173.53 | 25 | elm
FARM | cf1 | 12492.747 | 1 | cf
RESIDENTL | bwr32 | 11435795.4629 | 2903 | bwr
NCONUML | cln23 | 19017.15 | 5 | cln
RESIDENTL | bdl41 | 18711766.0554 | 3582 | bdl
RESIDENTL | tt4 | 9918702.5206 | 2673 | tt
NCONUML | nrn13 | 44749.68 | 14 | nrn
NCONUML | mwl12 | 43601.75 | 11 | mwl
FARM | cln12 | 30466.72 | 1 | cln
INDUSTRIAL | cpk21 | 122110.94 | 5 | cpk
NCONUML | epg11 | 2275 | 2 | epg
FARM | brt22 | 1064314.9433 | 146 | brt
NCONUML | moe21 | 60919.67 | 15 | moe
RESIDENTL | ldl22 | 4948357.507 | 1104 | ldl
INDUSTRIAL | epg22 | 206880.17 | 13 | epg
NCONUML | cln12 | 55224.6632 | 17 | cln
| wo14 | 16653.0726 | 14 | wo
INDUSTRIAL | wo13 | 14774006.15 | 3 | wo
INDUSTRIAL | wgi22 | 729700.7 | 28 | wgi
COMMERCIAL | msd2 | 2629949.014 | 87 | msd
NCONUML | ldl22 | 11421.24 | 5 | ldl
RESIDENTL | wo22 | 17812297.6729 | 4125 | wo
FARM | mwl25 | 2028215.2676 | 224 | mwl
| cln14 | 46492.03 | 68 | cln
INDUSTRIAL | smr14 | 413387.45 | 34 | smr
FARM | rwn33 | 39914.72 | 5 | rwn
NCONUML | tt7 | 28203.83 | 11 | tt
INDUSTRIAL | lga11 | 317451.8284 | 16 | lga
INDUSTRIAL | tt12 | 6074893.6495 | 86 | tt
INDUSTRIAL | rwn32 | 87972.96 | 1 | rwn
RESIDENTL | myt21 | 10899844.0445 | 1487 | myt
RESIDENTL | cyn14 | 9596207.6734 | 2758 | cyn
RESIDENTL | kms11 | 9874885.3712 | 1972 | kms
COMMERCIAL | wo32 | 9961950.2687 | 147 | wo
NCONUML | hpk21 | 96497.83 | 40 | hpk
FARM | mwl13 | 248036.6173 | 7 | mwl
RESIDENTL | smr23 | 3447913.5369 | 523 | smr
INDUSTRIAL | nla32 | 1443086.18 | 25 | nla
| rwt32 | 35174.87 | 36 | rwt
INDUSTRIAL | moe11 | 65970.59 | 6 | moe
INDUSTRIAL | wo33 | 33298223.9508 | 7 | wo
INDUSTRIAL | bra31 | 2919.84 | 1 | bra
RESIDENTL | moe15 | 9740983.6859 | 1552 | moe
RESIDENTL | moe12 | 4538532.291 | 887 | moe
INDUSTRIAL | bdl41 | 1328921.5447 | 34 | bdl
NCONUML | tt6 | 36560.52 | 20 | tt
RESIDENTL | uwy1 | 6496143.3356 | 1032 | uwy
RESIDENTL | wgi32 | 16438958.2366 | 3917 | wgi
COMMERCIAL | rwn31 | 2125446.8547 | 72 | rwn
| ldl13 | 45979.2126 | 34 | ldl
LIGHTING | hpk23 | 2010173.36 | 1 | hpk
RESIDENTL | fgy14 | 9703108.5669 | 2483 | fgy
FARM | rwn24 | 30208.83 | 4 | rwn
COMMERCIAL | wo23 | 11409957.4027 | 304 | wo
| myt12 | 115131.3847 | 34 | myt
| bge13 | 13458.3255 | 19 | bge
| sle32 | 15918.6359 | 20 | sle
FARM | epg11 | 14625.27 | 2 | epg
NCONUML | mwl21 | 34561.25 | 17 | mwl
COMMERCIAL | nrn12 | 21654160.6835 | 271 | nrn
COMMERCIAL | llg13 | 15983000.2277 | 99 | llg
| lga22 | 14116.8478 | 12 | lga
FARM | hpk11 | 14620.89 | 5 | hpk
RESIDENTL | ofr11 | 25072251.243 | 5672 | ofr
FARM | ftr12 | 9732520.1395 | 879 | ftr
RESIDENTL | epg21 | 580054.4394 | 151 | epg
FARM | bge22 | 343097.1961 | 60 | bge
COMMERCIAL | sfs1 | 1879673.1771 | 124 | sfs
| cln24 | 61460.6675 | 37 | cln
NCONUML | smg22 | 48204.28 | 25 | smg
RESIDENTL | phm34 | 11301839.7716 | 2904 | phm
RESIDENTL | phm31 | 2762476.4376 | 550 | phm
NCONUML | smr13 | 69764.68 | 26 | smr
RESIDENTL | wyk12 | 12357178.5976 | 1789 | wyk
INDUSTRIAL | sle13 | 125251.914 | 47 | sle
FARM | phm24 | 689286.43 | 52 | phm
| cre31 | 63798.4484 | 85 | cre
INDUSTRIAL | bge12 | 121322.77 | 7 | bge
FARM | wots12 | 5076.62 | 1 | wots
NCONUML | cf1 | 1922.85 | 2 | cf
RESIDENTL | wo31 | 20016820.444 | 4554 | wo
FARM | smr22 | 1275801.32 | 154 | smr
FARM | lga22 | 1443457.6222 | 105 | lga
COMMERCIAL | mwl22 | 10003347.9587 | 192 | mwl
FARM | bn24 | 2239563.0749 | 370 | bn
NCONUML | wots25 | 45798.68 | 13 | wots
NCONUML | wgi31 | 79233.36 | 21 | wgi
FARM | epg23 | 30049.96 | 2 | epg
NCONUML | klk11 | 24723.1 | 13 | klk
| mwl14 | 3593.32 | 2 | mwl
RESIDENTL | mdg1 | 4384126.608 | 684 | mdg
RESIDENTL | nrn14 | 9562152.1887 | 1877 | nrn
LIGHTING | msd4 | 139319.89 | 1 | msd
LIGHTING | sfs1 | 1558457.9 | 1 | sfs
| klo14 | 120043.1087 | 185 | klo
RESIDENTL | hpk14 | 17025183.7337 | 3944 | hpk
FARM | lga12 | 4046898.7707 | 351 | lga
COMMERCIAL | ldl14 | 12475957.7156 | 266 | ldl
RESIDENTL | bn11 | 14382992.5485 | 2912 | bn
COMMERCIAL | bdl34 | 6213094.4744 | 204 | bdl
FARM | lyd11 | 23799.7 | 3 | lyd
| mwl22 | 10189.434 | 23 | mwl
NCONUML | cf2 | 120.31 | 1 | cf
| epg32 | 18473.04 | 31 | epg
RESIDENTL | bdl34 | 21922135.2151 | 5106 | bdl
COMMERCIAL | rwn26 | 3719056.4225 | 81 | rwn
INDUSTRIAL | mby13 | 219583.33 | 2 | mby
NCONUML | fgy33 | 40029.49 | 14 | fgy
| ftr22 | 13372.1897 | 14 | ftr
NCONUML | mwl13 | 53127.87 | 17 | mwl
INDUSTRIAL | rwt32 | 132361.99 | 4 | rwt
COMMERCIAL | phm23 | 17053480.4 | 2 | phm
COMMERCIAL | bra13 | 19208526.3529 | 181 | bra
FARM | wn1 | 37241.96 | 7 | wn
FARM | bm8b33 | 1540.9 | 2 | bmb
COMMERCIAL | wt10 | 13883699.3972 | 155 | wt
INDUSTRIAL | uwy1 | 90405.23 | 3 | uwy
RESIDENTL | ldl23 | 26005181.5029 | 4084 | ldl
FARM | klo24 | 194259.84 | 22 | klo
| hpk11 | 33718.6052 | 42 | hpk
NCONUML | phm33 | 47915.862 | 19 | phm
FARM | wn6 | 4543418.3442 | 605 | wn
COMMERCIAL | cyn21 | 3633643.5973 | 195 | cyn
INDUSTRIAL | wo22 | 393144.5 | 11 | wo
RESIDENTL | tgn42 | 795534.2193 | 223 | tgn
INDUSTRIAL | mwl23 | 715134.0252 | 54 | mwl
| rwt22 | 26934.55 | 52 | rwt
COMMERCIAL | phm31 | 4117822.4369 | 32 | phm
RESIDENTL | epg22 | 39578.43 | 14 | epg
RESIDENTL | nla32 | 6559402.1513 | 1220 | nla
RESIDENTL | myt22 | 1017937.6841 | 120 | myt
| wgl15 | 30619.4 | 19 | wgl
LIGHTING | mjg11 | 68938.73 | 1 | mjg
COMMERCIAL | phi12 | 2400712.314 | 73 | phi
COMMERCIAL | rwt36 | 2264519.95 | 43 | rwt
INDUSTRIAL | wgi23 | 157973.74 | 15 | wgi
NCONUML | elm24 | 74942.52 | 25 | elm
RESIDENTL | wt10 | 3332972.5881 | 860 | wt
NCONUML | ruba22 | 360.93 | 3 | ruba
FARM | phi11 | 82538.05 | 19 | phi
| bra11 | 11169.2884 | 32 | bra
INDUSTRIAL | moe15 | 1465208.8927 | 46 | moe
| tt5 | 13084.5535 | 33 | tt
LIGHTING | elm34 | 2971413.79 | 6 | elm
FARM | rwt25 | 33966.32 | 4 | rwt
RESIDENTL | moe11 | 9711471.9521 | 1967 | moe
INDUSTRIAL | rwt22 | 12240.297 | 2 | rwt
FARM | tgn23 | 1979366.6929 | 215 | tgn
COMMERCIAL | elm34 | 4840398.0166 | 153 | elm
NCONUML | phi11 | 19831.48 | 5 | phi
NCONUML | bra13 | 31922.03 | 14 | bra
RESIDENTL | mwl11 | 7113484.1589 | 1047 | mwl
| sle14 | 9929.5555 | 28 | sle
COMMERCIAL | cpk11 | 7316179.79 | 51 | cpk
| cyn31 | 5192.9 | 11 | cyn
NCONUML | epg12 | 1563.57 | 9 | epg
| epg11 | 4794.77 | 9 | epg
INDUSTRIAL | bwa23 | 17470876.21 | 8 | bwa
FARM | cln21 | 792.83 | 1 | cln
COMMERCIAL | wn3 | 8489705.5245 | 275 | wn
COMMERCIAL | bwn12 | 29123057.9665 | 274 | bwn
NCONUML | bra23 | 28962.5293 | 21 | bra
| bge12 | 5967.8256 | 14 | bge
INDUSTRIAL | tgn12 | 464065.58 | 15 | tgn
LIGHTING | fgy31 | 1047083.29 | 1 | fgy
NCONUML | moe25 | 63582.44 | 18 | moe
NCONUML | fgy21 | 30728.13 | 12 | fgy
INDUSTRIAL | lyd11 | 151654.68 | 9 | lyd
FARM | bwn13 | 5960.02 | 1 | bwn
RESIDENTL | lga11 | 6965787.8425 | 1044 | lga
NCONUML | bwr22 | 31744.79 | 14 | bwr
COMMERCIAL | llg12 | 3977405.3306 | 115 | llg
COMMERCIAL | mfa21 | 3716072.0048 | 197 | mfa
INDUSTRIAL | phm32 | 1008.48 | 1 | phm
COMMERCIAL | nrn13 | 3605622.38 | 41 | nrn
FARM | cyn22 | 1131.4275 | 1 | cyn
INDUSTRIAL | ftr23 | 1828762.8842 | 76 | ftr
INDUSTRIAL | mfa31 | 463955.39 | 14 | mfa
INDUSTRIAL | bge11 | 395339.98 | 10 | bge
RESIDENTL | wo13 | 2691801.805 | 586 | wo
RESIDENTL | llg11 | 4969161.4408 | 709 | llg
| cpk21 | 8908.612 | 12 | cpk
INDUSTRIAL | cre23 | 238715.04 | 8 | cre
COMMERCIAL | epg33 | 43303826.6612 | 357 | epg
FARM | ofr21 | 60907.55 | 6 | ofr
COMMERCIAL | cpk22 | 8802072.7366 | 32 | cpk
NCONUML | bra24 | 34184.91 | 27 | bra
NCONUML | wn6 | 84222.69 | 35 | wn
FARM | mfa22 | 15017348.1505 | 702 | mfa
FARM | lga24 | 2675198.7919 | 323 | lga
COMMERCIAL | phi13 | 13565764.588 | 480 | phi
FARM | lga13 | 6142984.8245 | 572 | lga
NCONUML | wn2 | 74469.51 | 25 | wn
COMMERCIAL | wyk23 | 9043742.9219 | 306 | wyk
INDUSTRIAL | cyn31 | 110897.03 | 2 | cyn
RESIDENTL | wt7 | 9398293.9689 | 2293 | wt
COMMERCIAL | rwt15 | 2407529.701 | 118 | rwt
| wots11 | 29868.01 | 43 | wots
COMMERCIAL | wt12 | 9788397.4198 | 246 | wt
FARM | wots24 | 5049980.8194 | 706 | wots
COMMERCIAL | ftr22 | 3919173.7529 | 139 | ftr
INDUSTRIAL | ruba12 | 859698.6565 | 35 | ruba
| wots25 | 37134.4365 | 43 | wots
RESIDENTL | ofr24 | 14317680.0438 | 3420 | ofr
COMMERCIAL | bdl32 | 9327480.3168 | 349 | bdl
NCONUML | trc01 | 2600.11 | 1 | trc
RESIDENTL | wgi33 | 15074294.4922 | 2906 | wgi
RESIDENTL | wyk24 | 16651462.561 | 3130 | wyk
NCONUML | wn1 | 109135.95 | 32 | wn
NCONUML | fgy34 | 69468.4 | 26 | fgy
| tgn43 | 23585.3 | 37 | tgn
| bwn11 | 22540.96 | 33 | bwn
COMMERCIAL | bn11 | 11469939.8143 | 448 | bn
RESIDENTL | wn7 | 334597.06 | 81 | wn
FARM | lga23 | 6580772.0568 | 604 | lga
RESIDENTL | mby13 | 1114988.13 | 129 | mby
INDUSTRIAL | moe12 | 309363.05 | 10 | moe
NCONUML | wgl21 | 72341.71 | 26 | wgl
| rwn22 | 13422.17 | 20 | rwn
FARM | ofr13 | 1726.88 | 2 | ofr
INDUSTRIAL | smg33 | 3791.86 | 1 | smg
COMMERCIAL | cnr2 | 2241662.7301 | 123 | cnr
NCONUML | bwn13 | 114734.08 | 27 | bwn
INDUSTRIAL | tgn43 | 8336.37 | 2 | tgn
NCONUML | bra33 | 54640.5039 | 38 | bra
LIGHTING | drn23 | 137376.82 | 1 | drn
COMMERCIAL | wt11 | 6045415.4763 | 137 | wt
| wo23 | 3425.76 | 13 | wo
RESIDENTL | drn11 | 23689909.4015 | 5897 | drn
RESIDENTL | bra33 | 17227071.6094 | 3920 | bra
FARM | cre21 | 1165190.53 | 9 | cre
| wo32 | 20472.5797 | 26 | wo
NCONUML | mfa22 | 12133.93 | 8 | mfa
COMMERCIAL | fgy32 | 10874129.2215 | 316 | fgy
INDUSTRIAL | bdl33 | 6444229.03 | 34 | bdl
NCONUML | cnr3 | 880.96 | 3 | cnr
COMMERCIAL | bwr14 | 64319.73 | 1 | bwr
NCONUML | ldl11 | 15379.88 | 9 | ldl
FARM | bdl33 | 333127.23 | 48 | bdl
INDUSTRIAL | elm23 | 351538.3612 | 12 | elm
NCONUML | lga14 | 16509.29 | 6 | lga
NCONUML | rwt21 | 45520.76 | 13 | rwt
INDUSTRIAL | mwl24 | 3823292.43 | 15 | mwl
RESIDENTL | epg14 | 8906284.5994 | 2218 | epg
NCONUML | drn21 | 11559.57 | 6 | drn
FARM | ldl21 | 4274.77 | 1 | ldl
| lga14 | 13272.15 | 11 | lga
LIGHTING | wo22 | 1145144.2306 | 3 | wo
LIGHTING | bdl33 | 755365.47 | 1 | bdl
INDUSTRIAL | lga12 | 340570.559 | 7 | lga
RESIDENTL | ofr23 | 20573594.8025 | 3065 | ofr
LIGHTING | tgn12 | 393.8997 | 1 | tgn
RESIDENTL | fgy32 | 4718000.0914 | 1180 | fgy
COMMERCIAL | moe11 | 6876107.6583 | 169 | moe
COMMERCIAL | wgl13 | 16726185.3211 | 289 | wgl
COMMERCIAL | cre22 | 19152716.1468 | 212 | cre
RESIDENTL | drn12 | 16081122.8597 | 3986 | drn
COMMERCIAL | mfa23 | 8005013.26 | 78 | mfa
| cln13 | 39224.5517 | 61 | cln
INDUSTRIAL | mfa22 | 1793714.26 | 36 | mfa
LIGHTING | smr23 | 37560.88 | 1 | smr
RESIDENTL | rwn32 | 6727398.7344 | 1603 | rwn
FARM | lga14 | 4550189.1065 | 436 | lga
| cln12 | 24735.6225 | 51 | cln
COMMERCIAL | kms11 | 4936701.5866 | 120 | kms
RESIDENTL | smr14 | 10997106.9114 | 1697 | smr
| epg13 | 194183.3358 | 102 | epg
| brt21 | 9723.1397 | 7 | brt
INDUSTRIAL | drn12 | 10032.09 | 2 | drn
| tt7 | 34871.95 | 3 | tt
INDUSTRIAL | wots25 | 7153785.931 | 7 | wots
FARM | tgn43 | 14451.81 | 2 | tgn
NCONUML | ldl14 | 38917.21 | 26 | ldl
INDUSTRIAL | brt21 | 238786.6 | 10 | brt
| llg11 | 8477.8 | 10 | llg
RESIDENTL | wgi24 | 12721878.952 | 3596 | wgi
RESIDENTL | cyn21 | 10508542.767 | 2257 | cyn
INDUSTRIAL | bra11 | 3982632.29 | 3 | bra
INDUSTRIAL | phi11 | 184139.3994 | 13 | phi
| hpk24 | 8609.4373 | 14 | hpk
NCONUML | ldl13 | 24965.12 | 22 | ldl
RESIDENTL | hpk21 | 20637351.8958 | 5254 | hpk
RESIDENTL | wgl13 | 19626090.0794 | 4751 | wgl
COMMERCIAL | elm21 | 12124007.57 | 258 | elm
COMMERCIAL | wt13 | 23168272.4303 | 498 | wt
| hpk23 | 55023.71 | 41 | hpk
COMMERCIAL | mdg1 | 1157212.0402 | 52 | mdg
NCONUML | wt11 | 64055.27 | 25 | wt
NCONUML | phm31 | 9383.328 | 4 | phm
COMMERCIAL | bge23 | 4904566.2339 | 176 | bge
NCONUML | smg23 | 17942.69 | 11 | smg
| mwl16 | 4764.4783 | 12 | mwl
COMMERCIAL | hpk12 | 20352329.5415 | 361 | hpk
RESIDENTL | ruba24 | 4395729.6843 | 894 | ruba
COMMERCIAL | nla32 | 3390681.6399 | 175 | nla
NCONUML | lyd12 | 44439.84 | 9 | lyd
| cln22 | 289385.5413 | 85 | cln
NCONUML | cpk21 | 53769.1 | 26 | cpk
| ruba22 | 8482.6526 | 15 | ruba
COMMERCIAL | myt22 | 191990.12 | 18 | myt
RESIDENTL | mby11 | 5261006.6685 | 922 | mby
RESIDENTL | rwn26 | 21195116.3973 | 2454 | rwn
| rwt31 | 14608.62 | 19 | rwt
INDUSTRIAL | epg35 | 1615230.05 | 4 | epg
| bge23 | 30837.693 | 28 | bge
NCONUML | bdl34 | 70291.97 | 25 | bdl
NCONUML | ofr13 | 30258.73 | 11 | ofr
| klk11 | 25230.2094 | 21 | klk
NCONUML | bn12 | 1241.66 | 2 | bn
COMMERCIAL | wgi32 | 5461052.6827 | 195 | wgi
NCONUML | ldl12 | 45990.38 | 14 | ldl
INDUSTRIAL | bra23 | 3394433.4433 | 42 | bra
| wo33 | 4138.8 | 1 | wo
NCONUML | myt12 | 33269.22 | 16 | myt
INDUSTRIAL | ldl11 | 1468879.69 | 10 | ldl
RESIDENTL | msd1 | 8481569.4252 | 1750 | msd
NCONUML | bn11 | 57126.91 | 28 | bn
INDUSTRIAL | ftr12 | 2824402.5 | 31 | ftr
INDUSTRIAL | hpk11 | 29483.41 | 8 | hpk
NCONUML | epg33 | 5589.26 | 2 | epg
COMMERCIAL | wo31 | 10532525.1457 | 139 | wo
| wgl21 | 38182.04 | 53 | wgl
| bge22 | 25062.3495 | 31 | bge
RESIDENTL | tt1 | 171030.69 | 8 | tt
INDUSTRIAL | bwr34 | 134229.36 | 26 | bwr
COMMERCIAL | bra33 | 14409139.6368 | 303 | bra
COMMERCIAL | bdl44 | 4495186.894 | 197 | bdl
| bwn13 | 12482.8878 | 14 | bwn
NCONUML | wn3 | 40552.61 | 16 | wn
NCONUML | smr24 | 41055.27 | 16 | smr
INDUSTRIAL | mwl14 | 4499194.0326 | 50 | mwl
| wots24 | 36833.8626 | 36 | wots
NCONUML | wt12 | 74491.29 | 36 | wt
COMMERCIAL | smg31 | 17181337.4 | 81 | smg
FARM | lyd13 | 146611.14 | 18 | lyd
NCONUML | wots12 | 53576.05 | 15 | wots
INDUSTRIAL | fgy12 | 30820.7097 | 2 | fgy
FARM | myt12 | 4025860.4278 | 600 | myt
INDUSTRIAL | cyn22 | 204983.76 | 12 | cyn
COMMERCIAL | cyn33 | 3196035.4476 | 122 | cyn
COMMERCIAL | mby12 | 1853426.4391 | 89 | mby
NCONUML | tgn43 | 111938.06 | 34 | tgn
NCONUML | wo11 | 17571.55 | 5 | wo
INDUSTRIAL | epg12 | 1405424.52 | 3 | epg
| cf2 | 30699.57 | 2 | cf
COMMERCIAL | llg11 | 3213282.749 | 85 | llg
LIGHTING | rwn24 | 1936572.72 | 3 | rwn
INDUSTRIAL | cln24 | 15633.29 | 3 | cln
FARM | sle31 | 4999785.6618 | 315 | sle
INDUSTRIAL | cf1 | 129164.746 | 4 | cf
| ruba12 | 126134.0367 | 24 | ruba
| bwr12 | 18318.3952 | 15 | bwr
FARM | elm32 | 382389.8968 | 32 | elm
| ofr21 | 113717.1 | 52 | ofr
INDUSTRIAL | wn2 | 282430.54 | 13 | wn
NCONUML | bge22 | 82280.88 | 49 | bge
NCONUML | cnr2 | 33661.17 | 17 | cnr
NCONUML | wots13 | 10386.18 | 6 | wots
FARM | elm24 | 39172.3194 | 4 | elm
COMMERCIAL | nrn14 | 6896476.1265 | 116 | nrn
NCONUML | ruba12 | 27603.68 | 16 | ruba
NCONUML | hpk13 | 50290.3 | 16 | hpk
NCONUML | bra11 | 44798.92 | 35 | bra
| rwt21 | 23376.2409 | 6 | rwt
RESIDENTL | drn23 | 20613814.4846 | 2434 | drn
RESIDENTL | rwt36 | 2676215.9999 | 821 | rwt
RESIDENTL | llg13 | 6857833.0372 | 1230 | llg
COMMERCIAL | wyk12 | 4295149.2844 | 131 | wyk
INDUSTRIAL | ofr13 | 1622296.11 | 21 | ofr
| bra14 | 30334.7783 | 42 | bra
INDUSTRIAL | tgn11 | 3321263.75 | 18 | tgn
LIGHTING | mby13 | 9944.78 | 1 | mby
RESIDENTL | cln11 | 39284605.9906 | 12154 | cln
COMMERCIAL | drn22 | 10741065.2473 | 246 | drn
RESIDENTL | wo32 | 11244170.0715 | 2343 | wo
| bra33 | 27895.4569 | 47 | bra
COMMERCIAL | epg21 | 21867278.1603 | 75 | epg
INDUSTRIAL | cre21 | 293542.6 | 2 | cre
RESIDENTL | bwr24 | 1834966.95 | 415 | bwr
RESIDENTL | hpk13 | 8888406.848 | 2283 | hpk
NCONUML | moe13 | 240.62 | 2 | moe
RESIDENTL | mwl12 | 3605926.3697 | 887 | mwl
| elm24 | 29520.3106 | 27 | elm
COMMERCIAL | tgn31 | 5251765.7474 | 163 | tgn
| rwt25 | 17882.0217 | 23 | rwt
RESIDENTL | moe21 | 9438147.1697 | 1978 | moe
COMMERCIAL | mjg11 | 16973320.0649 | 258 | mjg
COMMERCIAL | moe22 | 1619971.835 | 34 | moe
NCONUML | cpk13 | 44472.2623 | 32 | cpk
| phi11 | 13149.9006 | 9 | phi
FARM | cyn11 | 2814.65 | 1 | cyn
FARM | cyn24 | 25049.8 | 2 | cyn
FARM | drn13 | 379220.8035 | 25 | drn
COMMERCIAL | mwe236 | 663523.2 | 21 | mwe
INDUSTRIAL | phm24 | 35612.08 | 4 | phm
INDUSTRIAL | bge22 | 36211.2493 | 9 | bge
RESIDENTL | cnr1 | 478523.9112 | 104 | cnr
| lga24 | 10918.35 | 11 | lga
NCONUML | sle14 | 98131.7526 | 34 | sle
NCONUML | tt5 | 14462.54 | 12 | tt
| epg12 | 53720.6497 | 70 | epg
NCONUML | kms11 | 42647.24 | 13 | kms
FARM | elm23 | 38507.8 | 8 | elm
COMMERCIAL | cyn12 | 12045879.7132 | 241 | cyn
INDUSTRIAL | fgy23 | 1420677.79 | 11 | fgy
COMMERCIAL | mfa14 | 259168.13 | 17 | mfa
| bra31 | 49797.7422 | 13 | bra
COMMERCIAL | mwl12 | 1780079.4127 | 78 | mwl
| bwr22 | 2405.71 | 25 | bwr
INDUSTRIAL | fgy24 | 415478.9 | 15 | fgy
COMMERCIAL | hpk13 | 9763023.5697 | 134 | hpk
| cyn22 | 22272.33 | 22 | cyn
| ldl21 | 13369.5383 | 42 | ldl
| wt6 | 17591.4373 | 23 | wt
RESIDENTL | wn4 | 11276854.4814 | 2349 | wn
FARM | mwl14 | 451834.7532 | 54 | mwl
RESIDENTL | bm8b31 | 357131.6719 | 111 | bmb
NCONUML | cyn14 | 48577.9677 | 22 | cyn
FARM | cre32 | 5136.47 | 1 | cre
FARM | bwr34 | 4550.33 | 1 | bwr
RESIDENTL | llg14 | 14855712.1657 | 2170 | llg
FARM | smg33 | 29400.19 | 7 | smg
RESIDENTL | drn22 | 21996972.8148 | 3999 | drn
NCONUML | elm32 | 42948.38 | 25 | elm
INDUSTRIAL | klo14 | 587332.99 | 17 | klo
| tgn11 | 22256.53 | 32 | tgn
INDUSTRIAL | tgn44 | 4536032.57 | 9 | tgn
COMMERCIAL | ldl23 | 15994398.5627 | 272 | ldl
| wn6 | 146062.0009 | 59 | wn
COMMERCIAL | tt2 | 18806104.6367 | 399 | tt
COMMERCIAL | brt11 | 4047117.81 | 129 | brt
NCONUML | llg14 | 65195.01 | 40 | llg
FARM | fgy24 | 95940.3 | 9 | fgy
NCONUML | fgy14 | 61562.37 | 33 | fgy
COMMERCIAL | rve12 | 3272242.91 | 54 | rve
INDUSTRIAL | cpk23 | 208291.634 | 5 | cpk
| lga23 | 41697.3391 | 21 | lga
INDUSTRIAL | yn38 | 642769.3081 | 6 | yn
COMMERCIAL | bwa21 | 7920817.52 | 6 | bwa
INDUSTRIAL | elm25 | 2097.04 | 1 | elm
COMMERCIAL | wots13 | 3416108.1488 | 213 | wots
FARM | wgi22 | 191494.2501 | 24 | wgi
NCONUML | fgy13 | 27847.71 | 7 | fgy
| bra24 | 9840.15 | 27 | bra
FARM | ofr14 | 100163.6258 | 21 | ofr
NCONUML | nrn11 | 16820.36 | 5 | nrn
RESIDENTL | smg31 | 12434679.8443 | 2879 | smg
COMMERCIAL | smr24 | 15083854.4686 | 348 | smr
| lyd11 | 12152.66 | 25 | lyd
INDUSTRIAL | bra12 | 1282907.1727 | 55 | bra
FARM | wgl15 | 3297105.6723 | 233 | wgl
INDUSTRIAL | msd1 | 544058.7154 | 15 | msd
| epg31 | 13971.3347 | 31 | epg
INDUSTRIAL | wgl23 | 572354.5027 | 44 | wgl
INDUSTRIAL | cpk12 | 343353.79 | 14 | cpk
INDUSTRIAL | mfa34 | 4790944.63 | 37 | mfa
| wn2 | 65478.1843 | 60 | wn
INDUSTRIAL | drn23 | 222019.33 | 21 | drn
| klo11 | 24997.4 | 1 | klo
COMMERCIAL | cyn13 | 11562540.4133 | 213 | cyn
| tgn44 | 15598.29 | 27 | tgn
| wn1 | 5093 | 9 | wn
NCONUML | wots24 | 22958.48 | 11 | wots
RESIDENTL | ftr21 | 5974099.1685 | 1654 | ftr
NCONUML | wgl11 | 116770.29 | 32 | wgl
FARM | phm22 | 2513172.8482 | 159 | phm
| mfa22 | 25912.0235 | 15 | mfa
| tt2 | 5693.01 | 1 | tt
RESIDENTL | cyn12 | 11384819.6049 | 2642 | cyn
COMMERCIAL | mby11 | 1920906.95 | 83 | mby
RESIDENTL | bdl42 | 7579399.6648 | 1528 | bdl
COMMERCIAL | sle11 | 16789466.3124 | 430 | sle
COMMERCIAL | bdl42 | 3935066.2305 | 228 | bdl
NCONUML | rwn22 | 25304.89 | 19 | rwn
INDUSTRIAL | cre32 | 1414910.91 | 33 | cre
INDUSTRIAL | bwn11 | 121807.37 | 8 | bwn
NCONUML | smr22 | 29006.3 | 13 | smr
RESIDENTL | phm24 | 12991887.5254 | 2975 | phm
RESIDENTL | phm21 | 5600884.0097 | 1319 | phm
NCONUML | ldl23 | 93357.12 | 44 | ldl
RESIDENTL | ldl24 | 19255310.9766 | 3964 | ldl
INDUSTRIAL | bra21 | 9682528.358 | 10 | bra
| sle31 | 21276.5675 | 34 | sle
| myt11 | 11671.01 | 10 | myt
RESIDENTL | elm21 | 10927220.6891 | 2208 | elm
COMMERCIAL | epg13 | 13081700.0195 | 121 | epg
COMMERCIAL | hpk21 | 6771211.022 | 80 | hpk
NCONUML | bwr12 | 55323.1848 | 22 | bwr
| trc01 | 7370.1419 | 1 | trc
| epg35 | 12733.43 | 3 | epg
INDUSTRIAL | bge21 | 30163.23 | 3 | bge
RESIDENTL | tgn31 | 10330935.5842 | 1504 | tgn
COMMERCIAL | moe23 | 8180066.6029 | 204 | moe
FARM | bra21 | 5211.11 | 2 | bra
LIGHTING | llg12 | 9573.66 | 1 | llg
RESIDENTL | bdl31 | 18828777.9984 | 3534 | bdl
COMMERCIAL | nla31 | 1365542.8767 | 73 | nla
INDUSTRIAL | klo24 | 421040.3606 | 14 | klo
FARM | bdl43 | 35833.9 | 4 | bdl
FARM | cyn31 | 3324.08 | 1 | cyn
FARM | sle14 | 508528.62 | 59 | sle
FARM | fgy34 | 3609.3 | 1 | fgy
RESIDENTL | elm26 | 19204314.084 | 3128 | elm
COMMERCIAL | ldl13 | 4974121.0157 | 271 | ldl
NCONUML | tgn42 | 32526.3 | 9 | tgn
RESIDENTL | nrn13 | 11128338.9236 | 2708 | nrn
| drn13 | 33230.29 | 35 | drn
RESIDENTL | mfa14 | 15628.16 | 8 | mfa
RESIDENTL | rwt14 | 5266292.5405 | 1232 | rwt
FARM | ftr23 | 7584335.745 | 587 | ftr
FARM | moe12 | 2890738.1544 | 266 | moe
RESIDENTL | klk21 | 6022162.144 | 692 | klk
COMMERCIAL | bn22 | 11917129.8815 | 407 | bn
COMMERCIAL | cln13 | 10498926.3291 | 102 | cln
INDUSTRIAL | cln11 | 955300.36 | 11 | cln
FARM | bge11 | 1450445.3683 | 132 | bge
| mwl25 | 368.2898 | 2 | mwl
| rwn33 | 13688.96 | 19 | rwn
| bdl43 | 33766.9817 | 15 | bdl
NCONUML | cln14 | 95979.5703 | 31 | cln
NCONUML | lga24 | 7306.35 | 4 | lga
| bn23 | 36133.4118 | 23 | bn
| ofr14 | 18460.3638 | 32 | ofr
FARM | wo14 | 29381.84 | 3 | wo
FARM | cln24 | 15169.45 | 1 | cln
FARM | smg21 | 2813.13 | 1 | smg
FARM | uwy1 | 50419.26 | 6 | uwy
RESIDENTL | cpk11 | 18255270.9798 | 3705 | cpk
INDUSTRIAL | rwn34 | 151721.8975 | 12 | rwn
FARM | mfa34 | 8352796.4311 | 398 | mfa
INDUSTRIAL | cyn23 | 283668.3977 | 39 | cyn
COMMERCIAL | cln23 | 7919442.4187 | 94 | cln
| rwn24 | 145239.1574 | 36 | rwn
INDUSTRIAL | cln21 | 91173.7471 | 8 | cln
INDUSTRIAL | wots23 | 9771996.01 | 2 | wots
COMMERCIAL | ofr23 | 7962081.4442 | 137 | ofr
FARM | cln11 | 5358747.3528 | 175 | cln
INDUSTRIAL | epg23 | 1603069.098 | 49 | epg
NCONUML | elm33 | 106570.09 | 33 | elm
| tt6 | 16214.4725 | 50 | tt
NCONUML | lga12 | 120.31 | 1 | lga
RESIDENTL | moe25 | 15202048.016 | 3044 | moe
RESIDENTL | moe22 | 6183768.6959 | 1343 | moe
RESIDENTL | mfa23 | 1535883.9368 | 206 | mfa
FARM | rwn22 | 76017.25 | 13 | rwn
COMMERCIAL | fgy31 | 26687.08 | 5 | fgy
RESIDENTL | elm33 | 17751529.9107 | 3238 | elm
COMMERCIAL | ldl22 | 7642772.3181 | 272 | ldl
NCONUML | llg11 | 13058.17 | 7 | llg
| ruba24 | 72607.09 | 10 | ruba
FARM | rwt32 | 21924.18 | 3 | rwt
FARM | ruba12 | 5735958.293 | 534 | ruba
FARM | brt21 | 526055.8565 | 65 | brt
| rwt15 | 24735.76 | 50 | rwt
NCONUML | bge13 | 40077 | 45 | bge
COMMERCIAL | klk21 | 1344972.0506 | 75 | klk
INDUSTRIAL | msd4 | 532825.24 | 27 | msd
| mwl21 | 2371.576 | 7 | mwl
RESIDENTL | wt9 | 13126762.7947 | 2901 | wt
FARM | wgi23 | 957555.9102 | 143 | wgi
| wgl24 | 12928.4076 | 27 | wgl
NCONUML | tgn11 | 50804.93 | 14 | tgn
LIGHTING | hpk22 | 402155.12 | 2 | hpk
INDUSTRIAL | wt13 | 198794.34 | 24 | wt
LIGHTING | wots24 | 69082.45 | 1 | wots
| ofr13 | 25120.5182 | 29 | ofr
| cre21 | 98632.2224 | 69 | cre
| smg22 | 13378.71 | 23 | smg
COMMERCIAL | tt4 | 4770691.1401 | 169 | tt
COMMERCIAL | elm26 | 2765254.86 | 47 | elm
NCONUML | bwa22 | 120.31 | 1 | bwa
| cyn23 | 386495.78 | 52 | cyn
INDUSTRIAL | nla34 | 227255.6563 | 13 | nla
FARM | mwl22 | 63.01 | 1 | mwl
| cf1 | 5771.13 | 3 | cf
NCONUML | cpk22 | 15413.02 | 10 | cpk
NCONUML | lyd13 | 28195.47 | 10 | lyd
NCONUML | cre31 | 35482.06 | 18 | cre
COMMERCIAL | wo11 | 6006584.4175 | 54 | wo
INDUSTRIAL | wt7 | 2382042.5333 | 25 | wt
| bwr34 | 19530.96 | 64 | bwr
NCONUML | bge23 | 57838.96 | 34 | bge
INDUSTRIAL | tgn23 | 187420.5 | 24 | tgn
RESIDENTL | cyn33 | 17836008.3498 | 3662 | cyn
RESIDENTL | nla34 | 7124747.0562 | 1408 | nla
| wgl11 | 21820.8596 | 38 | wgl
COMMERCIAL | bn12 | 3658135.6563 | 31 | bn
| mwl13 | 7054.2121 | 17 | mwl
COMMERCIAL | rwt26 | 65754589.65 | 1 | rwt
FARM | wt9 | 2789.4 | 1 | wt
RESIDENTL | bdl44 | 10906570.4152 | 1766 | bdl
FARM | cre33 | 2156267.3416 | 81 | cre
COMMERCIAL | wgl21 | 7364849.9167 | 150 | wgl
COMMERCIAL | wn5 | 3727109.367 | 208 | wn
NCONUML | mwl22 | 81020 | 27 | mwl
NCONUML | bn24 | 14677.57 | 9 | bn
| smr22 | 9887.67 | 15 | smr
|  | 8782.36 | 2 | #REF!
RESIDENTL | sle11 | 5311421.2716 | 1344 | sle
RESIDENTL | nw13 | 126364.0108 | 18 | nw
RESIDENTL | ftr23 | 12909653.9148 | 2620 | ftr
COMMERCIAL | mwl11 | 1278518.3133 | 72 | mwl
LIGHTING | llg13 | 66328.6913 | 1 | llg
NCONUML | klk22 | 2600.11 | 1 | klk
RESIDENTL | wyk23 | 22445865.182 | 3391 | wyk
COMMERCIAL | wt6 | 6354339.6482 | 191 | wt
RESIDENTL | brt11 | 6592458.6386 | 1001 | brt
NCONUML | tt9 | 66916.75 | 41 | tt
FARM | smr14 | 4406259.38 | 487 | smr
NCONUML | epg32 | 55568.91 | 13 | epg
RESIDENTL | rwn31 | 17135173.2235 | 2210 | rwn
| phm33 | 20993.1171 | 27 | phm
NCONUML | myt11 | 6079.5 | 6 | myt
RESIDENTL | nrn12 | 2807836.1314 | 591 | nrn
COMMERCIAL | mwl16 | 411566.3345 | 42 | mwl
INDUSTRIAL | lga23 | 1068068.6578 | 23 | lga
COMMERCIAL | ldl12 | 15390056.6509 | 380 | ldl
FARM | nla34 | 624678.3932 | 78 | nla
COMMERCIAL | rve13 | 1685040.429 | 44 | rve
NCONUML | drn24 | 11009.3526 | 4 | drn
COMMERCIAL | myt21 | 6919383.7104 | 251 | myt
FARM | moe13 | 3478506.4958 | 306 | moe
COMMERCIAL | mwl21 | 9182796.6603 | 240 | mwl
NCONUML | wgl15 | 97647.0301 | 36 | wgl
| bwn14 | 31300.22 | 31 | bwn
RESIDENTL | cpk22 | 8203984.593 | 1482 | cpk
RESIDENTL | rve12 | 17634581.2748 | 3656 | rve
RESIDENTL | phi13 | 17016004.0328 | 4317 | phi
RESIDENTL | hpk12 | 5058413.1519 | 1238 | hpk
COMMERCIAL | ruba24 | 4555190.3466 | 105 | ruba
FARM | cln14 | 51639.06 | 13 | cln
INDUSTRIAL | wt9 | 148098.11 | 5 | wt
| smg21 | 44014.37 | 27 | smg
INDUSTRIAL | smr23 | 883845.12 | 6 | smr

## Forecast - Summer
Forecasting Application - 13/10/2025
asset_type | asset | extremum | scenario | demand_year | season | poe | customer_count | pv_capacity | value | forecast_round | unit | region
zone_sub | cln | maximum |  | 2022 | Summer | 50 | 38619 | 72.2578 | 77.9086 | 202503 | MVA | central
zone_sub | cln | maximum |  | 2022 | Summer | 10 | 38619 | 72.2578 | 91.3183 | 202503 | MVA | central
zone_sub | cln | maximum |  | 2023 | Summer | 10 | 41429 | 81.3604 | 97.5884 | 202503 | MVA | central
zone_sub | cln | maximum |  | 2023 | Summer | 50 | 41429 | 81.3604 | 83.3369 | 202503 | MVA | central
zone_sub | cln | maximum |  | 2024 | Summer | 10 | 44846 | 94.6588 | 104.9463 | 202503 | MVA | central
zone_sub | cln | maximum |  | 2024 | Summer | 50 | 44846 | 94.6588 | 89.7351 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2025 | Summer | 10 |  |  | 119.6766 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2025 | Summer | 50 |  |  | 104.3341 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2026 | Summer | 10 |  |  | 124.2514 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2026 | Summer | 50 |  |  | 108.3435 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2027 | Summer | 10 |  |  | 128.0364 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2027 | Summer | 50 |  |  | 111.4611 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2028 | Summer | 10 |  |  | 131.3686 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2028 | Summer | 50 |  |  | 115.2173 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2029 | Summer | 10 |  |  | 136.7682 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2029 | Summer | 50 |  |  | 119.0984 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2030 | Summer | 10 |  |  | 141.634 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2030 | Summer | 50 |  |  | 123.2461 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2031 | Summer | 10 |  |  | 148.4809 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2031 | Summer | 50 |  |  | 128.0275 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2032 | Summer | 10 |  |  | 155.6302 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2032 | Summer | 50 |  |  | 133.6994 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2033 | Summer | 10 |  |  | 161.4365 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2033 | Summer | 50 |  |  | 139.0092 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2034 | Summer | 10 |  |  | 166.8996 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2034 | Summer | 50 |  |  | 144.6013 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2035 | Summer | 10 |  |  | 175.1342 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2035 | Summer | 50 |  |  | 154.2938 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2036 | Summer | 10 |  |  | 181.0486 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2036 | Summer | 50 |  |  | 157.43 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2037 | Summer | 10 |  |  | 187.0195 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2037 | Summer | 50 |  |  | 163.5566 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2038 | Summer | 10 |  |  | 193.3671 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2038 | Summer | 50 |  |  | 168.1999 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2039 | Summer | 10 |  |  | 192.0421 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2039 | Summer | 50 |  |  | 167.0472 | 202503 | MVA | central
zone_sub | cre | maximum |  | 2022 | Summer | 10 | 24937 | 39.5122 | 71.3044 | 202503 | MVA | central
zone_sub | cre | maximum |  | 2022 | Summer | 50 | 24937 | 39.5122 | 64.1683 | 202503 | MVA | central
zone_sub | cre | maximum |  | 2023 | Summer | 10 | 25835 | 43.8704 | 73.6781 | 202503 | MVA | central
zone_sub | cre | maximum |  | 2023 | Summer | 50 | 25835 | 43.8704 | 65.8328 | 202503 | MVA | central
zone_sub | cre | maximum |  | 2024 | Summer | 10 | 26314 | 48.9572 | 74.7994 | 202503 | MVA | central
zone_sub | cre | maximum |  | 2024 | Summer | 50 | 26314 | 48.9572 | 66.0879 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2025 | Summer | 10 |  |  | 89.8342 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2025 | Summer | 50 |  |  | 80.6612 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2026 | Summer | 10 |  |  | 90.653 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2026 | Summer | 50 |  |  | 81.4056 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2027 | Summer | 10 |  |  | 89.7773 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2027 | Summer | 50 |  |  | 80.6131 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2028 | Summer | 10 |  |  | 94.9573 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2028 | Summer | 50 |  |  | 85.9509 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2029 | Summer | 10 |  |  | 94.8385 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2029 | Summer | 50 |  |  | 85.6114 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2030 | Summer | 10 |  |  | 96.1186 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2030 | Summer | 50 |  |  | 85.7941 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2031 | Summer | 10 |  |  | 97.2062 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2031 | Summer | 50 |  |  | 86.4866 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2032 | Summer | 10 |  |  | 98.0786 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2032 | Summer | 50 |  |  | 87.2925 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2033 | Summer | 10 |  |  | 98.8781 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2033 | Summer | 50 |  |  | 88.2343 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2034 | Summer | 10 |  |  | 99.6475 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2034 | Summer | 50 |  |  | 88.9575 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2035 | Summer | 10 |  |  | 99.2707 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2035 | Summer | 50 |  |  | 89.8044 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2036 | Summer | 10 |  |  | 99.9981 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2036 | Summer | 50 |  |  | 89.5675 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2037 | Summer | 10 |  |  | 101.1509 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2037 | Summer | 50 |  |  | 90.5821 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2038 | Summer | 10 |  |  | 101.3208 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2038 | Summer | 50 |  |  | 90.3196 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2039 | Summer | 10 |  |  | 99.6095 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2039 | Summer | 50 |  |  | 88.5146 | 202503 | MVA | central
zone_sub | epg | maximum |  | 2022 | Summer | 10 | 29371 | 40.0067 | 87.2498 | 202503 | MVA | central
zone_sub | epg | maximum |  | 2022 | Summer | 50 | 29371 | 40.0067 | 72.9666 | 202503 | MVA | central
zone_sub | epg | maximum |  | 2023 | Summer | 10 | 30422 | 45.1511 | 90.3071 | 202503 | MVA | central
zone_sub | epg | maximum |  | 2023 | Summer | 50 | 30422 | 45.1511 | 75.7012 | 202503 | MVA | central
zone_sub | epg | maximum |  | 2024 | Summer | 10 | 32118 | 51.557 | 95.8895 | 202503 | MVA | central
zone_sub | epg | maximum |  | 2024 | Summer | 50 | 32118 | 51.557 | 79.9844 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2025 | Summer | 10 |  |  | 109.0669 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2025 | Summer | 50 |  |  | 92.5622 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2026 | Summer | 10 |  |  | 118.5447 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2026 | Summer | 50 |  |  | 101.6723 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2027 | Summer | 10 |  |  | 121.4869 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2027 | Summer | 50 |  |  | 104.4042 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2028 | Summer | 10 |  |  | 119.8786 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2028 | Summer | 50 |  |  | 102.6031 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2029 | Summer | 10 |  |  | 121.9204 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2029 | Summer | 50 |  |  | 105.5757 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2030 | Summer | 10 |  |  | 124.6444 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2030 | Summer | 50 |  |  | 106.371 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2031 | Summer | 10 |  |  | 127.5507 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2031 | Summer | 50 |  |  | 110.1341 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2032 | Summer | 10 |  |  | 131.8742 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2032 | Summer | 50 |  |  | 112.2581 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2033 | Summer | 10 |  |  | 136.3355 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2033 | Summer | 50 |  |  | 113.9316 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2034 | Summer | 10 |  |  | 140.9437 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2034 | Summer | 50 |  |  | 117.5793 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2035 | Summer | 10 |  |  | 144.5914 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2035 | Summer | 50 |  |  | 120.4726 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2036 | Summer | 50 |  |  | 128.0797 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2036 | Summer | 10 |  |  | 149.6115 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2037 | Summer | 10 |  |  | 152.9797 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2037 | Summer | 50 |  |  | 129.922 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2038 | Summer | 10 |  |  | 155.1715 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2038 | Summer | 50 |  |  | 132.5568 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2039 | Summer | 10 |  |  | 152.1644 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2039 | Summer | 50 |  |  | 125.7761 | 202503 | MVA | central
zone_sub | klo | maximum |  | 2022 | Summer | 10 | 14879 | 23.0226 | 53.5677 | 202503 | MVA | central
zone_sub | klo | maximum |  | 2022 | Summer | 50 | 14879 | 23.0226 | 41.9423 | 202503 | MVA | central
zone_sub | klo | maximum |  | 2023 | Summer | 10 | 17175 | 27.7177 | 61.121 | 202503 | MVA | central
zone_sub | klo | maximum |  | 2023 | Summer | 50 | 17175 | 27.7177 | 48.3019 | 202503 | MVA | central
zone_sub | klo | maximum |  | 2024 | Summer | 10 | 19951 | 34.2052 | 70.1897 | 202503 | MVA | central
zone_sub | klo | maximum |  | 2024 | Summer | 50 | 19951 | 34.2052 | 55.7613 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2025 | Summer | 10 |  |  | 83.6879 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2025 | Summer | 50 |  |  | 68.2523 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2026 | Summer | 10 |  |  | 94.1984 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2026 | Summer | 50 |  |  | 77.9353 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2027 | Summer | 10 |  |  | 102.4436 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2027 | Summer | 50 |  |  | 84.7194 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2028 | Summer | 10 |  |  | 118.3247 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2028 | Summer | 50 |  |  | 99.6669 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2029 | Summer | 10 |  |  | 126.3487 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2029 | Summer | 50 |  |  | 106.8624 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2030 | Summer | 10 |  |  | 135.5692 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2030 | Summer | 50 |  |  | 115.5707 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2031 | Summer | 10 |  |  | 148.561 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2031 | Summer | 50 |  |  | 127.0156 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2032 | Summer | 10 |  |  | 164.8827 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2032 | Summer | 50 |  |  | 137.8179 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2033 | Summer | 10 |  |  | 180.5841 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2033 | Summer | 50 |  |  | 151.2391 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2034 | Summer | 10 |  |  | 196.9964 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2034 | Summer | 50 |  |  | 164.8814 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2035 | Summer | 10 |  |  | 212.9758 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2035 | Summer | 50 |  |  | 181.5355 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2036 | Summer | 10 |  |  | 230.0573 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2036 | Summer | 50 |  |  | 195.8954 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2037 | Summer | 10 |  |  | 248.4456 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2037 | Summer | 50 |  |  | 212.2991 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2038 | Summer | 10 |  |  | 266.5409 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2038 | Summer | 50 |  |  | 225.6959 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2039 | Summer | 10 |  |  | 272.6357 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2039 | Summer | 50 |  |  | 228.9049 | 202503 | MVA | central
zone_sub | ofr | maximum |  | 2022 | Summer | 10 | 23246 | 35.5119 | 59.9776 | 202503 | MVA | central
zone_sub | ofr | maximum |  | 2022 | Summer | 50 | 23246 | 35.5119 | 53.856 | 202503 | MVA | central
zone_sub | ofr | maximum |  | 2023 | Summer | 10 | 24109 | 39.5748 | 62.0639 | 202503 | MVA | central
zone_sub | ofr | maximum |  | 2023 | Summer | 50 | 24109 | 39.5748 | 55.451 | 202503 | MVA | central
zone_sub | ofr | maximum |  | 2024 | Summer | 10 | 24997 | 44.4669 | 64.073 | 202503 | MVA | central
zone_sub | ofr | maximum |  | 2024 | Summer | 50 | 24997 | 44.4669 | 56.9594 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2025 | Summer | 10 |  |  | 69.589 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2025 | Summer | 50 |  |  | 61.9907 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2026 | Summer | 10 |  |  | 76.597 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2026 | Summer | 50 |  |  | 68.9791 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2027 | Summer | 10 |  |  | 81.5678 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2027 | Summer | 50 |  |  | 74.0072 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2028 | Summer | 10 |  |  | 84.5283 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2028 | Summer | 50 |  |  | 76.6284 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2029 | Summer | 10 |  |  | 86.8984 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2029 | Summer | 50 |  |  | 78.9811 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2030 | Summer | 10 |  |  | 88.8048 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2030 | Summer | 50 |  |  | 80.4506 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2031 | Summer | 10 |  |  | 90.6365 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2031 | Summer | 50 |  |  | 82.1352 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2032 | Summer | 10 |  |  | 92.2256 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2032 | Summer | 50 |  |  | 83.4813 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2033 | Summer | 10 |  |  | 92.9929 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2033 | Summer | 50 |  |  | 84.3346 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2034 | Summer | 10 |  |  | 94.1573 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2034 | Summer | 50 |  |  | 86.446 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2035 | Summer | 10 |  |  | 95.4952 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2035 | Summer | 50 |  |  | 87.894 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2036 | Summer | 10 |  |  | 96.8516 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2036 | Summer | 50 |  |  | 88.627 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2037 | Summer | 10 |  |  | 98.5806 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2037 | Summer | 50 |  |  | 90.0391 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2038 | Summer | 10 |  |  | 98.8168 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2038 | Summer | 50 |  |  | 89.5765 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2039 | Summer | 10 |  |  | 97.8239 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2039 | Summer | 50 |  |  | 88.3981 | 202503 | MVA | central
zone_sub | phm | maximum |  | 2022 | Summer | 50 | 16270 | 23.521 | 51.4174 | 202503 | MVA | central
zone_sub | phm | maximum |  | 2022 | Summer | 10 | 16270 | 23.521 | 56.9097 | 202503 | MVA | central
zone_sub | phm | maximum |  | 2023 | Summer | 10 | 16562 | 25.5412 | 57.758 | 202503 | MVA | central
zone_sub | phm | maximum |  | 2023 | Summer | 50 | 16562 | 25.5412 | 52.1386 | 202503 | MVA | central
zone_sub | phm | maximum |  | 2024 | Summer | 10 | 16854 | 27.7496 | 58.7282 | 202503 | MVA | central
zone_sub | phm | maximum |  | 2024 | Summer | 50 | 16854 | 27.7496 | 52.8621 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2025 | Summer | 10 |  |  | 75.5207 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2025 | Summer | 50 |  |  | 69.621 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2026 | Summer | 10 |  |  | 79.8845 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2026 | Summer | 50 |  |  | 74.1527 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2027 | Summer | 10 |  |  | 79.6008 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2027 | Summer | 50 |  |  | 73.9998 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2028 | Summer | 10 |  |  | 79.5894 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2028 | Summer | 50 |  |  | 73.965 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2029 | Summer | 10 |  |  | 80.0199 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2029 | Summer | 50 |  |  | 74.4648 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2030 | Summer | 10 |  |  | 81.1895 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2030 | Summer | 50 |  |  | 75.0153 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2031 | Summer | 10 |  |  | 81.9552 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2031 | Summer | 50 |  |  | 76.1566 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2032 | Summer | 10 |  |  | 82.7146 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2032 | Summer | 50 |  |  | 76.9783 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2033 | Summer | 10 |  |  | 83.6062 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2033 | Summer | 50 |  |  | 77.4148 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2034 | Summer | 10 |  |  | 84.4206 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2034 | Summer | 50 |  |  | 77.8841 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2035 | Summer | 10 |  |  | 85.2206 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2035 | Summer | 50 |  |  | 78.3211 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2036 | Summer | 10 |  |  | 85.2937 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2036 | Summer | 50 |  |  | 79.127 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2037 | Summer | 10 |  |  | 86.2309 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2037 | Summer | 50 |  |  | 80.1321 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2038 | Summer | 10 |  |  | 85.4841 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2038 | Summer | 50 |  |  | 80.0404 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2039 | Summer | 10 |  |  | 79.3417 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2039 | Summer | 50 |  |  | 73.3195 | 202503 | MVA | central
zone_sub | llg | maximum |  | 2022 | Summer | 10 | 7174 | 11.5134 | 25.3928 | 202503 | MVA | central
zone_sub | llg | maximum |  | 2022 | Summer | 50 | 7174 | 11.5134 | 23.4346 | 202503 | MVA | central
zone_sub | llg | maximum |  | 2023 | Summer | 10 | 7235 | 12.7349 | 25.4543 | 202503 | MVA | central
zone_sub | llg | maximum |  | 2023 | Summer | 50 | 7235 | 12.7349 | 23.4406 | 202503 | MVA | central
zone_sub | llg | maximum |  | 2024 | Summer | 10 | 7295 | 13.7538 | 25.544 | 202503 | MVA | central
zone_sub | llg | maximum |  | 2024 | Summer | 50 | 7295 | 13.7538 | 23.5081 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2025 | Summer | 10 |  |  | 28.7312 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2025 | Summer | 50 |  |  | 26.0976 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2026 | Summer | 10 |  |  | 33.0834 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2026 | Summer | 50 |  |  | 30.4575 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2027 | Summer | 10 |  |  | 33.0249 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2027 | Summer | 50 |  |  | 30.4247 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2028 | Summer | 10 |  |  | 33.0633 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2028 | Summer | 50 |  |  | 30.3952 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2029 | Summer | 10 |  |  | 33.1822 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2029 | Summer | 50 |  |  | 30.8677 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2030 | Summer | 10 |  |  | 33.5865 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2030 | Summer | 50 |  |  | 31.5616 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2031 | Summer | 10 |  |  | 33.8573 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2031 | Summer | 50 |  |  | 32.037 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2032 | Summer | 10 |  |  | 34.0794 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2032 | Summer | 50 |  |  | 31.4591 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2033 | Summer | 10 |  |  | 34.1121 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2033 | Summer | 50 |  |  | 31.5166 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2034 | Summer | 10 |  |  | 34.3124 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2034 | Summer | 50 |  |  | 31.792 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2035 | Summer | 10 |  |  | 34.3834 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2035 | Summer | 50 |  |  | 32.8827 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2036 | Summer | 10 |  |  | 34.3832 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2036 | Summer | 50 |  |  | 31.8492 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2037 | Summer | 10 |  |  | 34.3374 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2037 | Summer | 50 |  |  | 31.7885 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2038 | Summer | 10 |  |  | 34.3276 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2038 | Summer | 50 |  |  | 31.7234 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2039 | Summer | 10 |  |  | 32.6827 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2039 | Summer | 50 |  |  | 30.3101 | 202503 | MVA | central
zone_sub | wgi | maximum |  | 2022 | Summer | 10 | 21696 | 27.3902 | 50.299 | 202503 | MVA | east
zone_sub | wgi | maximum |  | 2022 | Summer | 50 | 21696 | 27.3902 | 41.2414 | 202503 | MVA | east
zone_sub | wgi | maximum |  | 2023 | Summer | 10 | 22045 | 30.4273 | 50.6919 | 202503 | MVA | east
zone_sub | wgi | maximum |  | 2023 | Summer | 50 | 22045 | 30.4273 | 41.4384 | 202503 | MVA | east
zone_sub | wgi | maximum |  | 2024 | Summer | 10 | 22388 | 33.5461 | 51.0465 | 202503 | MVA | east
zone_sub | wgi | maximum |  | 2024 | Summer | 50 | 22388 | 33.5461 | 41.5121 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2025 | Summer | 10 |  |  | 54.5057 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2025 | Summer | 50 |  |  | 44.6075 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2026 | Summer | 10 |  |  | 54.6012 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2026 | Summer | 50 |  |  | 44.9185 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2027 | Summer | 10 |  |  | 54.4983 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2027 | Summer | 50 |  |  | 44.7661 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2028 | Summer | 10 |  |  | 54.5247 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2028 | Summer | 50 |  |  | 44.911 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2029 | Summer | 10 |  |  | 54.7136 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2029 | Summer | 50 |  |  | 44.9706 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2030 | Summer | 10 |  |  | 55.0965 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2030 | Summer | 50 |  |  | 45.1615 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2031 | Summer | 10 |  |  | 55.7707 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2031 | Summer | 50 |  |  | 45.5541 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2032 | Summer | 50 |  |  | 45.8843 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2032 | Summer | 10 |  |  | 56.122 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2033 | Summer | 10 |  |  | 56.3761 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2033 | Summer | 50 |  |  | 46.0363 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2034 | Summer | 10 |  |  | 56.7608 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2034 | Summer | 50 |  |  | 45.9008 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2035 | Summer | 10 |  |  | 57.2519 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2035 | Summer | 50 |  |  | 46.4689 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2036 | Summer | 10 |  |  | 57.8457 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2036 | Summer | 50 |  |  | 46.559 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2037 | Summer | 10 |  |  | 58.1569 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2037 | Summer | 50 |  |  | 46.4523 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2038 | Summer | 10 |  |  | 58.056 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2038 | Summer | 50 |  |  | 46.6661 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2039 | Summer | 10 |  |  | 56.811 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2039 | Summer | 50 |  |  | 45.5652 | 202503 | MVA | east

## Forecast- Winter
Forecasting Application - 13/10/2025
asset_type | asset | extremum | scenario | demand_year | season | poe | customer_count | pv_capacity | value | forecast_round | unit | region
zone_sub | cln | maximum |  | 2022 | Winter | 10 | 38619 | 72.2578 | 63.0362 | 202503 | MVA | central
zone_sub | cln | maximum |  | 2022 | Winter | 50 | 38619 | 72.2578 | 58.8161 | 202503 | MVA | central
zone_sub | cln | maximum |  | 2023 | Winter | 10 | 41429 | 81.3604 | 67.9918 | 202503 | MVA | central
zone_sub | cln | maximum |  | 2023 | Winter | 50 | 41429 | 81.3604 | 63.4647 | 202503 | MVA | central
zone_sub | cln | maximum |  | 2024 | Winter | 10 | 44846 | 94.6588 | 74.018 | 202503 | MVA | central
zone_sub | cln | maximum |  | 2024 | Winter | 50 | 44846 | 94.6588 | 69.1182 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2025 | Winter | 10 |  |  | 89.4372 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2025 | Winter | 50 |  |  | 84.5179 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2026 | Winter | 10 |  |  | 93.2911 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2026 | Winter | 50 |  |  | 88.1502 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2027 | Winter | 10 |  |  | 98.0701 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2027 | Winter | 50 |  |  | 92.8679 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2028 | Winter | 10 |  |  | 102.5171 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2028 | Winter | 50 |  |  | 97.437 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2029 | Winter | 10 |  |  | 107.2692 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2029 | Winter | 50 |  |  | 101.4753 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2030 | Winter | 10 |  |  | 112.2902 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2030 | Winter | 50 |  |  | 107.1286 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2031 | Winter | 10 |  |  | 119.5588 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2031 | Winter | 50 |  |  | 113.3315 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2032 | Winter | 10 |  |  | 125.8642 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2032 | Winter | 50 |  |  | 119.6901 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2033 | Winter | 10 |  |  | 131.807 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2033 | Winter | 50 |  |  | 125.9989 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2034 | Winter | 10 |  |  | 137.993 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2034 | Winter | 50 |  |  | 131.579 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2035 | Winter | 10 |  |  | 145.465 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2035 | Winter | 50 |  |  | 137.6925 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2036 | Winter | 10 |  |  | 147.8036 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2036 | Winter | 50 |  |  | 139.8743 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2037 | Winter | 10 |  |  | 155.8793 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2037 | Winter | 50 |  |  | 147.8441 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2038 | Winter | 10 |  |  | 163.4009 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2038 | Winter | 50 |  |  | 156.1056 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2039 | Winter | 10 |  |  | 133.5693 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2039 | Winter | 50 |  |  | 127.2077 | 202503 | MVA | central
zone_sub | cre | maximum |  | 2022 | Winter | 10 | 24937 | 39.5122 | 50.635 | 202503 | MVA | central
zone_sub | cre | maximum |  | 2022 | Winter | 50 | 24937 | 39.5122 | 48.3881 | 202503 | MVA | central
zone_sub | cre | maximum |  | 2023 | Winter | 10 | 25835 | 43.8704 | 52.4586 | 202503 | MVA | central
zone_sub | cre | maximum |  | 2023 | Winter | 50 | 25835 | 43.8704 | 50.1308 | 202503 | MVA | central
zone_sub | cre | maximum |  | 2024 | Winter | 10 | 26314 | 48.9572 | 53.4328 | 202503 | MVA | central
zone_sub | cre | maximum |  | 2024 | Winter | 50 | 26314 | 48.9572 | 51.0617 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2025 | Winter | 10 |  |  | 68.4471 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2025 | Winter | 50 |  |  | 65.7336 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2026 | Winter | 10 |  |  | 69.4459 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2026 | Winter | 50 |  |  | 66.605 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2027 | Winter | 10 |  |  | 69.249 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2027 | Winter | 50 |  |  | 66.728 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2028 | Winter | 10 |  |  | 74.3386 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2028 | Winter | 50 |  |  | 72.0847 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2029 | Winter | 10 |  |  | 74.5773 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2029 | Winter | 50 |  |  | 72.2361 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2030 | Winter | 10 |  |  | 76.3193 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2030 | Winter | 50 |  |  | 74.0669 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2031 | Winter | 10 |  |  | 77.7248 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2031 | Winter | 50 |  |  | 75.6012 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2032 | Winter | 10 |  |  | 79.2116 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2032 | Winter | 50 |  |  | 76.7507 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2033 | Winter | 10 |  |  | 79.7367 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2033 | Winter | 50 |  |  | 77.8762 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2034 | Winter | 10 |  |  | 80.3545 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2034 | Winter | 50 |  |  | 78.6625 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2035 | Winter | 10 |  |  | 81.081 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2035 | Winter | 50 |  |  | 79.0014 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2036 | Winter | 10 |  |  | 80.0375 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2036 | Winter | 50 |  |  | 78.1499 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2037 | Winter | 10 |  |  | 83.4116 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2037 | Winter | 50 |  |  | 80.9567 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2038 | Winter | 10 |  |  | 84.3767 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2038 | Winter | 50 |  |  | 81.4995 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2039 | Winter | 10 |  |  | 72.4681 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2039 | Winter | 50 |  |  | 69.0004 | 202503 | MVA | central
zone_sub | epg | maximum |  | 2022 | Winter | 10 | 29371 | 40.0067 | 65.9271 | 202503 | MVA | central
zone_sub | epg | maximum |  | 2022 | Winter | 50 | 29371 | 40.0067 | 59.4269 | 202503 | MVA | central
zone_sub | epg | maximum |  | 2023 | Winter | 10 | 30422 | 45.1511 | 68.3101 | 202503 | MVA | central
zone_sub | epg | maximum |  | 2023 | Winter | 50 | 30422 | 45.1511 | 61.7598 | 202503 | MVA | central
zone_sub | epg | maximum |  | 2024 | Winter | 50 | 32118 | 51.557 | 65.5719 | 202503 | MVA | central
zone_sub | epg | maximum |  | 2024 | Winter | 10 | 32118 | 51.557 | 72.1952 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2025 | Winter | 10 |  |  | 85.9871 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2025 | Winter | 50 |  |  | 79.3939 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2026 | Winter | 10 |  |  | 95.0802 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2026 | Winter | 50 |  |  | 89.3565 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2027 | Winter | 10 |  |  | 100.5082 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2027 | Winter | 50 |  |  | 92.7492 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2028 | Winter | 10 |  |  | 99.8778 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2028 | Winter | 50 |  |  | 93.3308 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2029 | Winter | 10 |  |  | 103.1049 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2029 | Winter | 50 |  |  | 96.5577 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2030 | Winter | 10 |  |  | 109.1359 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2030 | Winter | 50 |  |  | 102.3455 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2031 | Winter | 10 |  |  | 112.51 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2031 | Winter | 50 |  |  | 104.2867 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2032 | Winter | 10 |  |  | 121.7799 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2032 | Winter | 50 |  |  | 114.0182 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2033 | Winter | 10 |  |  | 127.6696 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2033 | Winter | 50 |  |  | 119.7255 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2034 | Winter | 10 |  |  | 133.3287 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2034 | Winter | 50 |  |  | 125.5482 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2035 | Winter | 10 |  |  | 135.1129 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2035 | Winter | 50 |  |  | 126.6853 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2036 | Winter | 10 |  |  | 142.2751 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2036 | Winter | 50 |  |  | 134.3407 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2037 | Winter | 10 |  |  | 149.629 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2037 | Winter | 50 |  |  | 142.1357 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2038 | Winter | 10 |  |  | 150.109 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2038 | Winter | 50 |  |  | 141.9626 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2039 | Winter | 10 |  |  | 116.0207 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2039 | Winter | 50 |  |  | 101.3122 | 202503 | MVA | central
zone_sub | klo | maximum |  | 2022 | Winter | 10 | 14879 | 23.0226 | 48.7862 | 202503 | MVA | central
zone_sub | klo | maximum |  | 2022 | Winter | 50 | 14879 | 23.0226 | 43.3886 | 202503 | MVA | central
zone_sub | klo | maximum |  | 2023 | Winter | 10 | 17175 | 27.7177 | 56.3067 | 202503 | MVA | central
zone_sub | klo | maximum |  | 2023 | Winter | 50 | 17175 | 27.7177 | 50.077 | 202503 | MVA | central
zone_sub | klo | maximum |  | 2024 | Winter | 10 | 19951 | 34.2052 | 65.4015 | 202503 | MVA | central
zone_sub | klo | maximum |  | 2024 | Winter | 50 | 19951 | 34.2052 | 58.1655 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2025 | Winter | 10 |  |  | 79.8942 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2025 | Winter | 50 |  |  | 72.3119 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2026 | Winter | 10 |  |  | 92.3723 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2026 | Winter | 50 |  |  | 83.7626 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2027 | Winter | 10 |  |  | 102.9502 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2027 | Winter | 50 |  |  | 93.3778 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2028 | Winter | 10 |  |  | 120.3965 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2028 | Winter | 50 |  |  | 109.8362 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2029 | Winter | 10 |  |  | 129.7211 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2029 | Winter | 50 |  |  | 118.6301 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2030 | Winter | 10 |  |  | 142.5707 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2030 | Winter | 50 |  |  | 129.8167 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2031 | Winter | 10 |  |  | 159.4027 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2031 | Winter | 50 |  |  | 143.8497 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2032 | Winter | 10 |  |  | 178.8568 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2032 | Winter | 50 |  |  | 161.743 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2033 | Winter | 10 |  |  | 196.8658 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2033 | Winter | 50 |  |  | 178.8635 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2034 | Winter | 10 |  |  | 214.3536 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2034 | Winter | 50 |  |  | 194.8729 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2035 | Winter | 10 |  |  | 235.0946 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2035 | Winter | 50 |  |  | 213.0243 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2036 | Winter | 10 |  |  | 246.5584 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2036 | Winter | 50 |  |  | 225.0657 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2037 | Winter | 10 |  |  | 273.2503 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2037 | Winter | 50 |  |  | 249.8153 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2038 | Winter | 10 |  |  | 298.8878 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2038 | Winter | 50 |  |  | 271.7276 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2039 | Winter | 10 |  |  | 252.4111 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2039 | Winter | 50 |  |  | 227.0702 | 202503 | MVA | central
zone_sub | llg | maximum |  | 2022 | Winter | 10 | 7174 | 11.5134 | 22.426 | 202503 | MVA | central
zone_sub | llg | maximum |  | 2022 | Winter | 50 | 7174 | 11.5134 | 20.2322 | 202503 | MVA | central
zone_sub | llg | maximum |  | 2023 | Winter | 10 | 7235 | 12.7349 | 22.5982 | 202503 | MVA | central
zone_sub | llg | maximum |  | 2023 | Winter | 50 | 7235 | 12.7349 | 20.4035 | 202503 | MVA | central
zone_sub | llg | maximum |  | 2024 | Winter | 10 | 7295 | 13.7538 | 22.7705 | 202503 | MVA | central
zone_sub | llg | maximum |  | 2024 | Winter | 50 | 7295 | 13.7538 | 20.5738 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2025 | Winter | 10 |  |  | 26.1225 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2025 | Winter | 50 |  |  | 23.9159 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2026 | Winter | 10 |  |  | 30.6829 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2026 | Winter | 50 |  |  | 28.4398 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2027 | Winter | 10 |  |  | 31.049 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2027 | Winter | 50 |  |  | 28.8402 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2028 | Winter | 10 |  |  | 31.3064 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2028 | Winter | 50 |  |  | 29.108 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2029 | Winter | 10 |  |  | 31.5714 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2029 | Winter | 50 |  |  | 29.4846 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2030 | Winter | 10 |  |  | 32.5932 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2030 | Winter | 50 |  |  | 30.3426 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2031 | Winter | 10 |  |  | 33.1905 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2031 | Winter | 50 |  |  | 31.0163 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2032 | Winter | 10 |  |  | 33.8014 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2032 | Winter | 50 |  |  | 31.6154 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2033 | Winter | 10 |  |  | 34.0793 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2033 | Winter | 50 |  |  | 31.8255 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2034 | Winter | 10 |  |  | 34.2253 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2034 | Winter | 50 |  |  | 32.0656 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2035 | Winter | 10 |  |  | 33.7185 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2035 | Winter | 50 |  |  | 31.7299 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2036 | Winter | 10 |  |  | 33.9832 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2036 | Winter | 50 |  |  | 31.9069 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2037 | Winter | 10 |  |  | 34.9987 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2037 | Winter | 50 |  |  | 32.7389 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2038 | Winter | 10 |  |  | 34.5209 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2038 | Winter | 50 |  |  | 32.3709 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2039 | Winter | 10 |  |  | 28.3277 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2039 | Winter | 50 |  |  | 26.2847 | 202503 | MVA | central
zone_sub | ofr | maximum |  | 2022 | Winter | 10 | 23246 | 35.5119 | 49.8939 | 202503 | MVA | central
zone_sub | ofr | maximum |  | 2022 | Winter | 50 | 23246 | 35.5119 | 46.8764 | 202503 | MVA | central
zone_sub | ofr | maximum |  | 2023 | Winter | 10 | 24109 | 39.5748 | 51.7437 | 202503 | MVA | central
zone_sub | ofr | maximum |  | 2023 | Winter | 50 | 24109 | 39.5748 | 48.6149 | 202503 | MVA | central
zone_sub | ofr | maximum |  | 2024 | Winter | 10 | 24997 | 44.4669 | 53.6497 | 202503 | MVA | central
zone_sub | ofr | maximum |  | 2024 | Winter | 50 | 24997 | 44.4669 | 50.4065 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2025 | Winter | 10 |  |  | 59.4536 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2025 | Winter | 50 |  |  | 56.1183 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2026 | Winter | 10 |  |  | 66.5595 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2026 | Winter | 50 |  |  | 63.2802 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2027 | Winter | 10 |  |  | 72.8129 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2027 | Winter | 50 |  |  | 69.3039 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2028 | Winter | 10 |  |  | 76.0509 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2028 | Winter | 50 |  |  | 72.5305 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2029 | Winter | 10 |  |  | 78.6773 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2029 | Winter | 50 |  |  | 74.8582 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2030 | Winter | 10 |  |  | 81.1629 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2030 | Winter | 50 |  |  | 77.5373 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2031 | Winter | 10 |  |  | 83.2732 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2031 | Winter | 50 |  |  | 79.5294 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2032 | Winter | 10 |  |  | 85.4834 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2032 | Winter | 50 |  |  | 81.7407 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2033 | Winter | 10 |  |  | 86.4197 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2033 | Winter | 50 |  |  | 82.8706 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2034 | Winter | 10 |  |  | 87.7259 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2034 | Winter | 50 |  |  | 83.8526 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2035 | Winter | 10 |  |  | 90.1815 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2035 | Winter | 50 |  |  | 86.3425 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2036 | Winter | 10 |  |  | 89.3155 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2036 | Winter | 50 |  |  | 84.7668 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2037 | Winter | 10 |  |  | 92.5351 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2037 | Winter | 50 |  |  | 88.8524 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2038 | Winter | 10 |  |  | 94.3753 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2038 | Winter | 50 |  |  | 94.1939 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2039 | Winter | 10 |  |  | 80.6717 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2039 | Winter | 50 |  |  | 77.1549 | 202503 | MVA | central
zone_sub | phm | maximum |  | 2022 | Winter | 10 | 16270 | 23.521 | 48.1658 | 202503 | MVA | central
zone_sub | phm | maximum |  | 2022 | Winter | 50 | 16270 | 23.521 | 45.1092 | 202503 | MVA | central
zone_sub | phm | maximum |  | 2023 | Winter | 10 | 16562 | 25.5412 | 49.0318 | 202503 | MVA | central
zone_sub | phm | maximum |  | 2023 | Winter | 50 | 16562 | 25.5412 | 45.9202 | 202503 | MVA | central
zone_sub | phm | maximum |  | 2024 | Winter | 10 | 16854 | 27.7496 | 49.8978 | 202503 | MVA | central
zone_sub | phm | maximum |  | 2024 | Winter | 50 | 16854 | 27.7496 | 46.7311 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2025 | Winter | 10 |  |  | 67.0847 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2025 | Winter | 50 |  |  | 64.1376 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2026 | Winter | 10 |  |  | 71.7531 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2026 | Winter | 50 |  |  | 68.6294 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2027 | Winter | 10 |  |  | 72.4584 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2027 | Winter | 50 |  |  | 69.3785 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2028 | Winter | 10 |  |  | 72.887 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2028 | Winter | 50 |  |  | 69.9467 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2029 | Winter | 10 |  |  | 73.8781 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2029 | Winter | 50 |  |  | 70.9603 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2030 | Winter | 10 |  |  | 76.2493 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2030 | Winter | 50 |  |  | 73.2946 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2031 | Winter | 10 |  |  | 77.5227 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2031 | Winter | 50 |  |  | 74.8388 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2032 | Winter | 10 |  |  | 79.9897 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2032 | Winter | 50 |  |  | 76.8149 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2033 | Winter | 10 |  |  | 87.5343 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2033 | Winter | 50 |  |  | 77.8299 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2034 | Winter | 10 |  |  | 81.2629 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2034 | Winter | 50 |  |  | 78.7091 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2035 | Winter | 10 |  |  | 80.0205 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2035 | Winter | 50 |  |  | 77.0055 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2036 | Winter | 10 |  |  | 81.6454 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2036 | Winter | 50 |  |  | 78.9538 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2037 | Winter | 10 |  |  | 85.2253 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2037 | Winter | 50 |  |  | 82.0295 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2038 | Winter | 10 |  |  | 82.7648 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2038 | Winter | 50 |  |  | 79.6564 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2039 | Winter | 10 |  |  | 67.0558 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2039 | Winter | 50 |  |  | 63.9852 | 202503 | MVA | central
zone_sub | wgi | maximum |  | 2022 | Winter | 10 | 21696 | 27.3902 | 41.941 | 202503 | MVA | east
zone_sub | wgi | maximum |  | 2022 | Winter | 50 | 21696 | 27.3902 | 38.234 | 202503 | MVA | east
zone_sub | wgi | maximum |  | 2023 | Winter | 10 | 22045 | 30.4273 | 42.6315 | 202503 | MVA | east
zone_sub | wgi | maximum |  | 2023 | Winter | 50 | 22045 | 30.4273 | 38.883 | 202503 | MVA | east
zone_sub | wgi | maximum |  | 2024 | Winter | 10 | 22388 | 33.5461 | 43.3126 | 202503 | MVA | east
zone_sub | wgi | maximum |  | 2024 | Winter | 50 | 22388 | 33.5461 | 39.5207 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2025 | Winter | 10 |  |  | 47.2482 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2025 | Winter | 50 |  |  | 43.6466 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2026 | Winter | 10 |  |  | 47.6557 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2026 | Winter | 50 |  |  | 44.0841 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2027 | Winter | 10 |  |  | 49.0622 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2027 | Winter | 50 |  |  | 44.625 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2028 | Winter | 10 |  |  | 49.028 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2028 | Winter | 50 |  |  | 45.3431 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2029 | Winter | 10 |  |  | 49.3373 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2029 | Winter | 50 |  |  | 46.0239 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2030 | Winter | 10 |  |  | 50.5469 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2030 | Winter | 50 |  |  | 47.2137 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2031 | Winter | 10 |  |  | 54.0224 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2031 | Winter | 50 |  |  | 50.206 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2032 | Winter | 10 |  |  | 55.4565 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2032 | Winter | 50 |  |  | 51.8155 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2033 | Winter | 10 |  |  | 54.099 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2033 | Winter | 50 |  |  | 50.6413 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2034 | Winter | 10 |  |  | 57.8491 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2034 | Winter | 50 |  |  | 54.2764 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2035 | Winter | 10 |  |  | 56.2746 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2035 | Winter | 50 |  |  | 54.9313 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2036 | Winter | 10 |  |  | 57.6913 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2036 | Winter | 50 |  |  | 55.4021 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2037 | Winter | 10 |  |  | 58.7122 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2037 | Winter | 50 |  |  | 57.6212 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2038 | Winter | 10 |  |  | 58.2928 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2038 | Winter | 50 |  |  | 57.9824 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2039 | Winter | 10 |  |  | 49.2493 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2039 | Winter | 50 |  |  | 45.4578 | 202503 | MVA | east

## Ratings
STATION OUTPUT RATING (TRANSFORMER SUMMATION) SUMMARY
|  |  | Station N Rating |  | Station N-1 Rating |  | Station N-2 Rating
|  |  | SCR | WCR | SCR | WCR | SCR | WCR | Remarks | Remarks | Bus Target | Station Cap Bank
S/S Name | No. TX | Name Plate MVA | MVA | MVA | MVA | MVA | MVA | MVA | For N-1 Ratings | N-2 | Voltage kV | MVAr
CLN | 3 | 99 | 130.95 | 142.95 | 89.2 | 97.8 | 44.6 | 48.9
LLG | 1 | 33 | 47.4 | 48.3 | 0 | 0 | 0 | 0 | N rating only |  | 22 | 4
OFR | 2 | 66 | 93.2 | 93.2 | 45.2 | 48 | 0 | 0 | Loss of T1 or T2 |  | 22 | 6
PHM | 2 | 66 | 91.9 | 95.7 | 45 | 49.1 | 0 | 0 | Loss of T1 or T2 |  | 22 | 12

## Power Factor
asset_type | asset | PF
zone_sub | cln | 1
zone_sub | llg | 0.99
zone_sub | ofr | 1
zone_sub | phm | 1

## FT
Forecast tool (MVA) |  | Forecast Capacity & Transfers
ZSS |  | PHM
Summer
[5 empty] | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads
DY (Apr 1 to Mar 30) |  | 2022/23 | 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2028/29 | 2029/30 | 2030/31 | 2031/32 | 2032/33 | 2033/34 | 2034/35 | 2035/36 | 2036/37 | 2037/38 | 2038/39
DY (Apr 1 to Mar 30) |  | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038
FY (Jul 1 to Jun 30) |  | 2022/23 | 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2028/29 | 2029/30 | 2030/31 | 2031/32 | 2032/33 | 2033/34 | 2034/35 | 2035/36 | 2036/37 | 2037/38 | 2038/39
FY (Jul 1 to Jun 30) |  |  |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39
Summer POE50 | 50 |  |  | 52.8621 | 69.621 | 74.1527 | 73.9998 | 73.965 | 74.4648 | 75.0153 | 76.1566 | 76.9783 | 77.4148 | 77.8841 | 78.3211 | 79.127 | 80.1321 | 80.0404
Summer POE10 | 10 |  |  | 58.7282 | 75.5207 | 79.8845 | 79.6008 | 79.5894 | 80.0199 | 81.1895 | 81.9552 | 82.7146 | 83.6062 | 84.4206 | 85.2206 | 85.2937 | 86.2309 | 85.4841
Winter
[5 empty] | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads
DM (Apr 1 to Mar 30) |  |  |  | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2028/29 | 2029/30 | 2030/31 | 2031/32 | 2032/33 | 2033/34 | 2034/35 | 2035/36 | 2036/37 | 2037/38 | 2038/39
DY (Apr 1 to Mar 30) |  |  |  | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038
FY (Jul 1 to Jun 30) |  |  |  | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2028/29 | 2029/30 | 2030/31 | 2031/32 | 2032/33 | 2033/34 | 2034/35 | 2035/36 | 2036/37 | 2037/38 | 2038/39
FY (Jul 1 to Jun 30) |  |  |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39
Winter POE50 | 50 |  |  | 46.7311 | 64.1376 | 68.6294 | 69.3785 | 69.9467 | 70.9603 | 73.2946 | 74.8388 | 76.8149 | 77.8299 | 78.7091 | 77.0055 | 78.9538 | 82.0295 | 79.6564
Winter POE10 | 10 |  |  | 49.8978 | 67.0847 | 71.7531 | 72.4584 | 72.887 | 73.8781 | 76.2493 | 77.5227 | 79.9897 | 87.5343 | 81.2629 | 80.0205 | 81.6454 | 85.2253 | 82.7648
Transfers (MVA)
|  | Feeder | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39
|  | PHM | 1.7 | 1.7 | 1.67 | 1.65 | 1.62 | 1.6 | 1.58 | 1.55 | 1.53 | 1.51 | 1.48 | 1.46 | 1.44 | 1.42 | 1.4
|  | PowerFactor | 1

## Load Duration Curves
Station
PHM
POE10
[6 empty] | Stations | KLO |  | EPG |  | CRE |  | CLN |  | PHM |  | OFR |  | LLG |  | WGI
| % of MD | Winter - MD (P10) - Duration % | Winter - MD - Hours | Summer - MD - Duration % | Summer - MD - Hours | %MD | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration %
| 100% | 0% | 0 | 0% | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| 99% | 0.03383% | 1.486 | 0.03444% | 1.5127 | 99% | 0.01722% | 0.02707% | 0% | 0.04737% | 0% | 0% | 0.00861% | 0.01353% | 0.03444% | 0.03383% | 0.01722% | 0.0203% | 0.02583% | 0.006767% | 0% | 0.006767%
| 98% | 0.07443% | 3.2692 | 0.05166% | 2.269 | 98% | 0.01722% | 0.07443% | 0.00861% | 0.08797% | 0.02583% | 0.01353% | 0.02583% | 0.0203% | 0.05166% | 0.07443% | 0.02583% | 0.0812% | 0.04305% | 0.0203% | 0% | 0.006767%
| 97% | 0.1556% | 6.8356 | 0.0861% | 3.7816 | 97% | 0.02583% | 0.09474% | 0.02583% | 0.1421% | 0.04305% | 0.02707% | 0.05166% | 0.03383% | 0.0861% | 0.1556% | 0.04305% | 0.1083% | 0.05166% | 0.04737% | 0.00861% | 0.006767%
| 95% | 0.3992% | 17.5347 | 0.1378% | 6.0506 | 95% | 0.05166% | 0.1895% | 0.09471% | 0.3519% | 0.0861% | 0.08797% | 0.1033% | 0.05413% | 0.1378% | 0.3992% | 0.07749% | 0.1759% | 0.09471% | 0.09474% | 0.00861% | 0.03383%
| 90% | 1.793% | 78.7576 | 0.3702% | 16.2611 | 90% | 0.0861% | 0.9135% | 0.1894% | 1.786% | 0.1894% | 0.7579% | 0.1808% | 0.07443% | 0.3702% | 1.793% | 0.2066% | 0.8932% | 0.353% | 0.2639% | 0.01722% | 0.1962%
| 85% | 5.393% | 236.8672 | 0.6027% | 26.4715 | 85% | 0.1205% | 2.355% | 0.353% | 4.588% | 0.2669% | 2.761% | 0.3272% | 0.318% | 0.6027% | 5.393% | 0.3702% | 2.68% | 0.7147% | 0.7443% | 0.02583% | 0.9135%
| 80% | 11.33% | 497.5104 | 0.7749% | 34.0348 | 80% | 0.31% | 5.616% | 0.6458% | 8.885% | 0.4219% | 6.787% | 0.4477% | 0.9406% | 0.7749% | 11.33% | 0.5683% | 6.11% | 1.317% | 1.915% | 0.06027% | 2.118%
| 75% | 18.3% | 803.6248 | 1.102% | 48.405 | 75% | 0.4822% | 9.995% | 0.9988% | 14.05% | 0.5338% | 11.76% | 0.5855% | 2.876% | 1.102% | 18.3% | 0.7491% | 10.38% | 2.764% | 4.601% | 0.07749% | 4.486%
| 70% | 26.3% | 1155.2107 | 1.739% | 76.3892 | 70% | 0.7491% | 14.12% | 1.498% | 19.88% | 0.8438% | 17.56% | 0.7921% | 7.376% | 1.739% | 26.3% | 0.9557% | 15.73% | 6.225% | 8.837% | 0.1292% | 8.607%
| 65% | 35.36% | 1553.1596 | 2.6% | 114.2056 | 65% | 1.154% | 18.84% | 2.265% | 27.11% | 1.102% | 25.21% | 1.05% | 12.51% | 2.6% | 35.36% | 1.541% | 22.03% | 12.05% | 15.25% | 0.1464% | 14.03%
| 60% | 46.14% | 2026.2996 | 4.055% | 178.1154 | 60% | 1.602% | 25.14% | 3.203% | 35.21% | 1.627% | 33.62% | 1.748% | 18.2% | 4.055% | 46.14% | 2.247% | 29.44% | 20.92% | 25.15% | 0.2583% | 21.29%
| 55% | 59.16% | 2598.4068 | 7.095% | 311.6074 | 55% | 2.411% | 33.56% | 4.357% | 45.33% | 2.48% | 42.68% | 2.419% | 25.42% | 7.095% | 59.16% | 3.496% | 37.5% | 33.11% | 37.15% | 0.8094% | 29.85%
| 50% | 73.62% | 3233.5201 | 14.48% | 636.0723 | 50% | 4.598% | 44.25% | 6.303% | 58.26% | 3.84% | 54.87% | 4.064% | 34.04% | 14.48% | 73.62% | 5.881% | 47.91% | 47.93% | 51.32% | 2.17% | 39.4%
| 45% | 85.96% | 3775.313 | 26.86% | 1179.4944 | 45% | 9.592% | 58.98% | 10.8% | 69.36% | 6.535% | 71.48% | 8.378% | 45.63% | 26.86% | 85.96% | 11.13% | 62.3% | 62.8% | 65.85% | 4.753% | 49.36%
| 40% | 92.73% | 4072.8088 | 41.17% | 1808.3816 | 40% | 19.83% | 71.65% | 21.2% | 75.98% | 14.01% | 84.31% | 16.88% | 65.51% | 41.17% | 92.73% | 21.13% | 79.32% | 76.24% | 79.08% | 8.662% | 59.42%
| 35% | 95.6% | 4198.821 | 63.28% | 2779.1293 | 35% | 37.74% | 78.94% | 37.58% | 85.16% | 27.53% | 88.52% | 26.59% | 78.66% | 63.28% | 95.6% | 34.85% | 87.21% | 86.9% | 88.41% | 15.86% | 68.26%
| 30% | 97.25% | 4271.3374 | 86.84% | 3814.165 | 30% | 66.82% | 83.24% | 57.09% | 93.38% | 49.73% | 90.98% | 45.59% | 83.41% | 86.84% | 97.25% | 59.02% | 90.02% | 92.6% | 93.97% | 28.71% | 75.35%
| 25% | 98.4% | 4321.8611 | 94.88% | 4166.9923 | 25% | 77.33% | 87.43% | 77.75% | 96.1% | 81.07% | 93.44% | 72.26% | 87.95% | 94.88% | 98.4% | 83.32% | 92.46% | 96.47% | 96.66% | 44.75% | 80.55%
| 20% | 99.11% | 4353.067 | 97.51% | 4282.7105 | 20% | 85.59% | 92.06% | 96.84% | 97.65% | 89.22% | 95.65% | 79.18% | 93.87% | 97.51% | 99.11% | 91.2% | 94.84% | 98.65% | 98.41% | 56.7% | 84.95%
| 15% | 99.49% | 4369.4129 | 99.38% | 4364.7722 | 15% | 96.14% | 98.9% | 99.64% | 98.65% | 96.11% | 97.43% | 86.26% | 99.55% | 99.38% | 99.49% | 97.48% | 97.23% | 99.31% | 99.14% | 68.25% | 89.03%
| 10% | 99.7% | 4378.6261 | 99.99% | 4391.6218 | 10% | 99.99% | 99.99% | 99.99% | 99.16% | 99.9% | 98.78% | 98.3% | 99.6% | 99.99% | 99.7% | 99.99% | 99.59% | 99.63% | 99.41% | 79.5% | 92.79%
| 5% | 99.99% | 4391.7028 | 99.99% | 4391.6218 | 5% | 99.99% | 99.99% | 99.99% | 99.49% | 99.99% | 99.76% | 99.99% | 99.61% | 99.99% | 99.99% | 99.99% | 99.99% | 99.68% | 99.6% | 90.07% | 96.81%
| 9.992e-14% | 99.99% | 4391.7028 | 99.99% | 4391.6218 | 0% | 99.99% | 99.99% | 99.99% | 99.99% | 99.99% | 99.99% | 99.99% | 99.63% | 99.99% | 99.99% | 99.99% | 99.99% | 99.71% | 99.63% | 99.99% | 99.99%
POE 50
[6 empty] | Stations | KLO |  | EPG |  | CRE |  | CLN |  | PHM |  | OFR |  | LLG |  | WGI
| % of MD | Winter - AD (P50) - Duration % | Winter - AD - Hours | Summer - AD - Duration % | Summer - AD - Hours | %MD | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration %
| 100% | 0% | 0 | 0% | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| 99% | 0.03383% | 1.486 | 0% | 0 | 99% | 0.03444% | 0.02707% | 0.04305% | 0.04737% | 0% | 0% | 0% | 0.01353% | 0% | 0.03383% | 0% | 0.0203% | 0.00861% | 0.006767% | 0.00861% | 0.006767%
| 98% | 0.07443% | 3.2692 | 0% | 0 | 98% | 0.05166% | 0.07443% | 0.07749% | 0.08797% | 0% | 0.01353% | 0.00861% | 0.0203% | 0% | 0.07443% | 0.00861% | 0.0812% | 0.00861% | 0.0203% | 0.00861% | 0.006767%
| 97% | 0.1556% | 6.8356 | 0.00861% | 0.37816 | 97% | 0.06888% | 0.09474% | 0.07749% | 0.1421% | 0.02583% | 0.02707% | 0.01722% | 0.03383% | 0.00861% | 0.1556% | 0.01722% | 0.1083% | 0.01722% | 0.0406% | 0.00861% | 0.006767%
| 95% | 0.3992% | 17.5347 | 0.05166% | 2.269 | 95% | 0.0861% | 0.1895% | 0.1378% | 0.3519% | 0.04305% | 0.08797% | 0.02583% | 0.05413% | 0.05166% | 0.3992% | 0.04305% | 0.1759% | 0.01722% | 0.1015% | 0.01722% | 0.03383%
| 90% | 1.793% | 78.7576 | 0.1292% | 5.6725 | 90% | 0.1292% | 0.9135% | 0.2583% | 1.786% | 0.1119% | 0.7579% | 0.1033% | 0.07443% | 0.1292% | 1.793% | 0.1033% | 0.8932% | 0.0861% | 0.3451% | 0.2066% | 0.1962%
| 85% | 5.393% | 236.8672 | 0.3616% | 15.8829 | 85% | 0.2497% | 2.355% | 0.465% | 4.588% | 0.2755% | 2.761% | 0.1808% | 0.318% | 0.3616% | 5.393% | 0.2066% | 2.68% | 0.31% | 0.9% | 0.9213% | 0.9135%
| 80% | 11.33% | 497.5104 | 0.706% | 31.0095 | 80% | 0.4133% | 5.616% | 0.7835% | 8.885% | 0.6113% | 6.787% | 0.2669% | 0.9406% | 0.706% | 11.33% | 0.6286% | 6.11% | 0.8008% | 2.517% | 2.153% | 2.118%
| 75% | 18.3% | 803.6248 | 1.662% | 72.9857 | 75% | 0.8352% | 9.995% | 1.257% | 14.05% | 0.9902% | 11.76% | 0.4047% | 2.876% | 1.662% | 18.3% | 1.309% | 10.38% | 1.834% | 5.562% | 4.486% | 4.486%
| 70% | 26.3% | 1155.2107 | 3.427% | 150.5094 | 70% | 1.619% | 14.12% | 2.101% | 19.88% | 1.911% | 17.56% | 0.8008% | 7.376% | 3.427% | 26.3% | 2.419% | 15.73% | 4.374% | 10.11% | 7.672% | 8.607%
| 65% | 35.36% | 1553.1596 | 8.188% | 359.6342 | 65% | 3.057% | 18.84% | 4.288% | 27.11% | 3.504% | 25.21% | 1.352% | 12.51% | 8.188% | 35.36% | 4.598% | 22.03% | 9.179% | 17.54% | 11.87% | 14.03%
| 60% | 46.14% | 2026.2996 | 15.71% | 689.7717 | 60% | 5.528% | 25.14% | 9.342% | 35.21% | 7.758% | 33.62% | 3.573% | 18.2% | 15.71% | 46.14% | 9.17% | 29.44% | 16.83% | 27.53% | 18.5% | 21.29%
| 55% | 59.16% | 2598.4068 | 24.94% | 1095.5419 | 55% | 11.8% | 33.56% | 17.61% | 45.33% | 16.05% | 42.68% | 8.283% | 25.42% | 24.94% | 59.16% | 14.93% | 37.5% | 27.43% | 40.02% | 27.37% | 29.85%
| 50% | 73.62% | 3233.5201 | 37.94% | 1666.1918 | 50% | 21.47% | 44.25% | 28.46% | 58.26% | 24.85% | 54.87% | 17.57% | 34.04% | 37.94% | 73.62% | 22.35% | 47.91% | 40.6% | 54.15% | 38.39% | 39.4%
| 45% | 85.96% | 3775.313 | 57.06% | 2506.0947 | 45% | 35.07% | 58.98% | 42.44% | 69.36% | 37.15% | 71.48% | 28.59% | 45.63% | 57.06% | 85.96% | 36.95% | 62.3% | 53.97% | 68.39% | 48.48% | 49.36%
| 40% | 92.73% | 4072.8088 | 72.05% | 3164.4787 | 40% | 60.78% | 71.65% | 63.35% | 75.98% | 61.17% | 84.31% | 46.88% | 65.51% | 72.05% | 92.73% | 55.62% | 79.32% | 65.21% | 80.79% | 56.57% | 59.42%
| 35% | 95.6% | 4198.821 | 80.86% | 3551.3408 | 35% | 70.59% | 78.94% | 76.04% | 85.16% | 71.05% | 88.52% | 69.68% | 78.66% | 80.86% | 95.6% | 68.46% | 87.21% | 75.09% | 89.43% | 63.94% | 68.26%
| 30% | 97.25% | 4271.3374 | 85.59% | 3758.953 | 30% | 76.73% | 83.24% | 80.97% | 93.38% | 75.06% | 90.98% | 76.64% | 83.41% | 85.59% | 97.25% | 74.6% | 90.02% | 81.51% | 94.17% | 70.48% | 75.35%
| 25% | 98.4% | 4321.8611 | 89.4% | 3926.4798 | 25% | 83.08% | 87.43% | 85.41% | 96.1% | 78.56% | 93.44% | 83.93% | 87.95% | 89.4% | 98.4% | 78.93% | 92.46% | 86.44% | 96.81% | 76.48% | 80.55%
| 20% | 99.11% | 4353.067 | 92.22% | 4050.5177 | 20% | 91.12% | 92.06% | 89.28% | 97.65% | 81.79% | 95.65% | 91.73% | 93.87% | 92.22% | 99.11% | 84.56% | 94.84% | 90.52% | 98.48% | 81.71% | 84.95%
| 15% | 99.49% | 4369.4129 | 94.55% | 4152.622 | 15% | 99.18% | 98.9% | 92.61% | 98.65% | 86.18% | 97.43% | 98.93% | 99.55% | 94.55% | 99.49% | 92.06% | 97.23% | 93.75% | 99.28% | 86.58% | 89.03%
| 10% | 99.7% | 4378.6261 | 96.73% | 4248.2976 | 10% | 99.99% | 99.99% | 95.16% | 99.16% | 91.73% | 98.78% | 99.75% | 99.6% | 96.73% | 99.7% | 99.06% | 99.59% | 96.19% | 99.59% | 91.64% | 92.79%
| 5% | 99.99% | 4391.7028 | 99.31% | 4361.7469 | 5% | 99.99% | 99.99% | 97.15% | 99.49% | 97.84% | 99.76% | 99.99% | 99.61% | 99.31% | 99.99% | 99.99% | 99.99% | 98.14% | 99.77% | 96.54% | 96.81%
| 9.992e-14% | 99.99% | 4391.7028 | 99.99% | 4391.6218 | 0% | 99.99% | 99.99% | 99.99% | 99.99% | 99.99% | 99.99% | 99.99% | 99.63% | 99.99% | 99.99% | 99.99% | 99.99% | 99.78% | 99.99% | 99.99% | 99.99%
POE10
|  | Summer | Winter
| Year | 2019/2020 | 2023
| Start | 2024-10-01 | 2024-04-01
| End | 2025-04-01 | 2024-10-01
| Days | 183 | 183
| Hours | 4392 | 4392
POE50
|  | Summer | Winter
| Year | 2023/2024 | 2023
| Start | 2023-10-01 | 2024-04-01
| End | 2024-04-01 | 2024-10-01
| Days | 183 | 183
| Hours | 4392 | 4392

## Capacity N
Option 1 - Do Nothing / Base Case - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N Rating (MVA) - Option 1 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7
SCR N Rating (MVA) - Option 1 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9
Planned Additional Capacity (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2 - 1A New PHS ZSS + Four new feeders - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N Rating (MVA) - Option 2 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7
SCR N Rating (MVA) - Option 2 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 - 2A PHM 3rd Tx + Switchroom + Three new feeders + OFR12 New Feeder - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N Rating (MVA) - Option 3 | 95.7 | 95.7 | 95.7 | 140.7 | 140.7 | 140.7 | 140.7 | 140.7 | 140.7 | 140.7 | 140.7 | 140.7 | 140.7 | 140.7 | 140.7 | 140.7 | 140.7 | 140.7 | 140.7 | 140.7 | 140.7 | 140.7 | 140.7 | 140.7 | 140.7 | 140.7 | 140.7 | 140.7 | 140.7 | 140.7
SCR N Rating (MVA) - Option 3 | 91.9 | 91.9 | 91.9 | 136.9 | 136.9 | 136.9 | 136.9 | 136.9 | 136.9 | 136.9 | 136.9 | 136.9 | 136.9 | 136.9 | 136.9 | 136.9 | 136.9 | 136.9 | 136.9 | 136.9 | 136.9 | 136.9 | 136.9 | 136.9 | 136.9 | 136.9 | 136.9 | 136.9 | 136.9 | 136.9
Capacity Added (MVA) | 0 | 0 | 0 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45
Option 4 - 3A OFR 3rd Tx + Switchroom + Three new feeders + OFR12 New Feeder - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N Rating (MVA) - Option 4 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7
SCR N Rating (MVA) - Option 4 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 - 4A LLG 2nd Tx + Switchroom + Three new feeders + OFR12 New Feeder - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N Rating (MVA) - Option 5 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7
SCR N Rating (MVA) - Option 5 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 6 - Non Network - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N Rating (MVA) - Option 6 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7
SCR N Rating (MVA) - Option 6 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 7 - - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N Rating (MVA) - Option 7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7
SCR N Rating (MVA) - Option 7 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 8 - - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N Rating (MVA) - Option 8 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7
SCR N Rating (MVA) - Option 8 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Capacity N-1
Option 1 - Do Nothing / Base Case - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-1 Rating (MVA) - Option 1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1
SCR N-1 Rating (MVA) - Option 1 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45
Planned Additional Capacity (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2 - 1A New PHS ZSS + Four new feeders - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-1 Rating (MVA) - Option 2 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1
SCR N-1 Rating (MVA) - Option 2 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 - 2A PHM 3rd Tx + Switchroom + Three new feeders + OFR12 New Feeder - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-1 Rating (MVA) - Option 3 | 49.1 | 49.1 | 49.1 | 94.1 | 94.1 | 94.1 | 94.1 | 94.1 | 94.1 | 94.1 | 94.1 | 94.1 | 94.1 | 94.1 | 94.1 | 94.1 | 94.1 | 94.1 | 94.1 | 94.1 | 94.1 | 94.1 | 94.1 | 94.1 | 94.1 | 94.1 | 94.1 | 94.1 | 94.1 | 94.1
SCR N-1 Rating (MVA) - Option 3 | 45 | 45 | 45 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90
Capacity Added (MVA) | 0 | 0 | 0 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45
Option 4 - 3A OFR 3rd Tx + Switchroom + Three new feeders + OFR12 New Feeder - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-1 Rating (MVA) - Option 4 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1
SCR N-1 Rating (MVA) - Option 4 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 - 4A LLG 2nd Tx + Switchroom + Three new feeders + OFR12 New Feeder - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-1 Rating (MVA) - Option 5 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1
SCR N-1 Rating (MVA) - Option 5 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 6 - Non Network - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-1 Rating (MVA) - Option 6 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1
SCR N-1 Rating (MVA) - Option 6 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 7 - - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-1 Rating (MVA) - Option 7 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1
SCR N-1 Rating (MVA) - Option 7 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 8 - - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-1 Rating (MVA) - Option 8 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1
SCR N-1 Rating (MVA) - Option 8 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Capacity N-2
Option 1 - Do Nothing / Base Case - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-2 Rating (MVA) - Option 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCR N-2 Rating (MVA) - Option 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Planned Additional Capacity (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2 - 1A New PHS ZSS + Four new feeders - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-2 Rating (MVA) - Option 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCR N-2 Rating (MVA) - Option 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 - 2A PHM 3rd Tx + Switchroom + Three new feeders + OFR12 New Feeder - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-2 Rating (MVA) - Option 3 | 0 | 0 | 0 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45
SCR N-2 Rating (MVA) - Option 3 | 0 | 0 | 0 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45
Capacity Added (MVA) | 0 | 0 | 0 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45
Option 4 - 3A OFR 3rd Tx + Switchroom + Three new feeders + OFR12 New Feeder - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-2 Rating (MVA) - Option 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCR N-2 Rating (MVA) - Option 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 - 4A LLG 2nd Tx + Switchroom + Three new feeders + OFR12 New Feeder - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-2 Rating (MVA) - Option 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCR N-2 Rating (MVA) - Option 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 6 - Non Network - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-2 Rating (MVA) - Option 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCR N-2 Rating (MVA) - Option 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 7 - - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-2 Rating (MVA) - Option 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCR N-2 Rating (MVA) - Option 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 8 - - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-2 Rating (MVA) - Option 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCR N-2 Rating (MVA) - Option 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Demand
Option 1 - Do Nothing / Base Case
Winter Season | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Maximum Demand (MVA) - P50 | 42.058 | 57.7239 | 61.7664 | 62.4406 | 62.9521 | 63.8643 | 65.9652 | 67.3549 | 69.1334 | 70.0469 | 70.8382 | 69.305 | 71.0585 | 73.8266 | 71.6908 | 71.6908 | 71.6908 | 71.6908 | 71.6908 | 71.6908 | 71.6908 | 71.6908 | 71.6908 | 71.6908 | 71.6908 | 71.6908 | 71.6908 | 71.6908 | 71.6908 | 71.6908
Maximum Demand (MVA) - P10 | 44.908 | 60.3763 | 64.5778 | 65.2125 | 65.5983 | 66.4903 | 68.6243 | 69.7704 | 71.9908 | 78.7809 | 73.1366 | 72.0185 | 73.4808 | 76.7027 | 74.4883 | 74.4883 | 74.4883 | 74.4883 | 74.4883 | 74.4883 | 74.4883 | 74.4883 | 74.4883 | 74.4883 | 74.4883 | 74.4883 | 74.4883 | 74.4883 | 74.4883 | 74.4883
Block loads (MVA) not in the forecast | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Available Transfers (MVA) | 1.7 | 1.7 | 1.67 | 1.65 | 1.62 | 1.6 | 1.58 | 1.55 | 1.53 | 1.51 | 1.48 | 1.46 | 1.44 | 1.42 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4
Demand management (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Embedded generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Maximum Demand (MVA) - Option 1 Winter POE50 | 40.358 | 56.0239 | 60.0964 | 60.7906 | 61.3321 | 62.2643 | 64.3852 | 65.8049 | 67.6034 | 68.5369 | 69.3582 | 67.845 | 69.6185 | 72.4066 | 70.2908 | 70.2908 | 70.2908 | 70.2908 | 70.2908 | 70.2908 | 70.2908 | 70.2908 | 70.2908 | 70.2908 | 70.2908 | 70.2908 | 70.2908 | 70.2908 | 70.2908 | 70.2908
Total Maximum Demand (MVA) - Option 1 Winter POE10 | 43.208 | 58.6763 | 62.9078 | 63.5625 | 63.9783 | 64.8903 | 67.0443 | 68.2204 | 70.4608 | 77.2709 | 71.6566 | 70.5585 | 72.0408 | 75.2827 | 73.0883 | 73.0883 | 73.0883 | 73.0883 | 73.0883 | 73.0883 | 73.0883 | 73.0883 | 73.0883 | 73.0883 | 73.0883 | 73.0883 | 73.0883 | 73.0883 | 73.0883 | 73.0883
Summer Season | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Maximum Demand (MVA) - P50 | 47.5759 | 62.6589 | 66.7374 | 66.5999 | 66.5685 | 67.0184 | 67.5138 | 68.5409 | 69.2804 | 69.6733 | 70.0957 | 70.489 | 71.2143 | 72.1189 | 72.0364 | 72.0364 | 72.0364 | 72.0364 | 72.0364 | 72.0364 | 72.0364 | 72.0364 | 72.0364 | 72.0364 | 72.0364 | 72.0364 | 72.0364 | 72.0364 | 72.0364 | 72.0364
Maximum Demand (MVA) - P10 | 52.8554 | 67.9686 | 71.8961 | 71.6407 | 71.6305 | 72.0179 | 73.0705 | 73.7597 | 74.4432 | 75.2456 | 75.9785 | 76.6986 | 76.7643 | 77.6078 | 76.9357 | 76.9357 | 76.9357 | 76.9357 | 76.9357 | 76.9357 | 76.9357 | 76.9357 | 76.9357 | 76.9357 | 76.9357 | 76.9357 | 76.9357 | 76.9357 | 76.9357 | 76.9357
Block loads (MVA) not in the forecast | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Available Transfers (MVA) | 1.7 | 1.7 | 1.67 | 1.65 | 1.62 | 1.6 | 1.58 | 1.55 | 1.53 | 1.51 | 1.48 | 1.46 | 1.44 | 1.42 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4
Demand management (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Embedded generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Maximum Demand (MVA) - Option 1 Summer POE50 | 45.8759 | 60.9589 | 65.0674 | 64.9499 | 64.9485 | 65.4184 | 65.9338 | 66.9909 | 67.7504 | 68.1633 | 68.6157 | 69.029 | 69.7743 | 70.6989 | 70.6364 | 70.6364 | 70.6364 | 70.6364 | 70.6364 | 70.6364 | 70.6364 | 70.6364 | 70.6364 | 70.6364 | 70.6364 | 70.6364 | 70.6364 | 70.6364 | 70.6364 | 70.6364
Total Maximum Demand (MVA) - Option 1 Summer POE10 | 51.1554 | 66.2686 | 70.2261 | 69.9907 | 70.0105 | 70.4179 | 71.4905 | 72.2097 | 72.9132 | 73.7356 | 74.4985 | 75.2386 | 75.3243 | 76.1878 | 75.5357 | 75.5357 | 75.5357 | 75.5357 | 75.5357 | 75.5357 | 75.5357 | 75.5357 | 75.5357 | 75.5357 | 75.5357 | 75.5357 | 75.5357 | 75.5357 | 75.5357 | 75.5357
Option 2 - 1A New PHS ZSS + Four new feeders
Year | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Added Transfers (MVA) | 0 | 0 | 0 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29
Added Demand management (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Added Embedded generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Maximum Demand (MVA) - Option 2 Winter POE50 | 40.358 | 56.0239 | 60.0964 | 31.7906 | 32.3321 | 33.2643 | 35.3852 | 36.8049 | 38.6034 | 39.5369 | 40.3582 | 38.845 | 40.6185 | 43.4066 | 41.2908 | 41.2908 | 41.2908 | 41.2908 | 41.2908 | 41.2908 | 41.2908 | 41.2908 | 41.2908 | 41.2908 | 41.2908 | 41.2908 | 41.2908 | 41.2908 | 41.2908 | 41.2908
Total Maximum Demand (MVA) - Option 2 Winter POE10 | 43.208 | 58.6763 | 62.9078 | 34.5625 | 34.9783 | 35.8903 | 38.0443 | 39.2204 | 41.4608 | 48.2709 | 42.6566 | 41.5585 | 43.0408 | 46.2827 | 44.0883 | 44.0883 | 44.0883 | 44.0883 | 44.0883 | 44.0883 | 44.0883 | 44.0883 | 44.0883 | 44.0883 | 44.0883 | 44.0883 | 44.0883 | 44.0883 | 44.0883 | 44.0883
Total Maximum Demand (MVA) - Option 2 Summer POE50 | 45.8759 | 60.9589 | 65.0674 | 35.9499 | 35.9485 | 36.4184 | 36.9338 | 37.9909 | 38.7504 | 39.1633 | 39.6157 | 40.029 | 40.7743 | 41.6989 | 41.6364 | 41.6364 | 41.6364 | 41.6364 | 41.6364 | 41.6364 | 41.6364 | 41.6364 | 41.6364 | 41.6364 | 41.6364 | 41.6364 | 41.6364 | 41.6364 | 41.6364 | 41.6364
Total Maximum Demand (MVA) - Option 2 Summer POE10 | 51.1554 | 66.2686 | 70.2261 | 40.9907 | 41.0105 | 41.4179 | 42.4905 | 43.2097 | 43.9132 | 44.7356 | 45.4985 | 46.2386 | 46.3243 | 47.1878 | 46.5357 | 46.5357 | 46.5357 | 46.5357 | 46.5357 | 46.5357 | 46.5357 | 46.5357 | 46.5357 | 46.5357 | 46.5357 | 46.5357 | 46.5357 | 46.5357 | 46.5357 | 46.5357
Option 3 - 2A PHM 3rd Tx + Switchroom + Three new feeders + OFR12 New Feeder
Year | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Added Transfers (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Added Demand management (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Added Embedded generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Maximum Demand (MVA) - Option 3 Winter POE50 | 40.358 | 56.0239 | 60.0964 | 60.7906 | 61.3321 | 62.2643 | 64.3852 | 65.8049 | 67.6034 | 68.5369 | 69.3582 | 67.845 | 69.6185 | 72.4066 | 70.2908 | 70.2908 | 70.2908 | 70.2908 | 70.2908 | 70.2908 | 70.2908 | 70.2908 | 70.2908 | 70.2908 | 70.2908 | 70.2908 | 70.2908 | 70.2908 | 70.2908 | 70.2908
Total Maximum Demand (MVA) - Option 3 Winter POE10 | 43.208 | 58.6763 | 62.9078 | 63.5625 | 63.9783 | 64.8903 | 67.0443 | 68.2204 | 70.4608 | 77.2709 | 71.6566 | 70.5585 | 72.0408 | 75.2827 | 73.0883 | 73.0883 | 73.0883 | 73.0883 | 73.0883 | 73.0883 | 73.0883 | 73.0883 | 73.0883 | 73.0883 | 73.0883 | 73.0883 | 73.0883 | 73.0883 | 73.0883 | 73.0883
Total Maximum Demand (MVA) - Option 3 Summer POE50 | 45.8759 | 60.9589 | 65.0674 | 64.9499 | 64.9485 | 65.4184 | 65.9338 | 66.9909 | 67.7504 | 68.1633 | 68.6157 | 69.029 | 69.7743 | 70.6989 | 70.6364 | 70.6364 | 70.6364 | 70.6364 | 70.6364 | 70.6364 | 70.6364 | 70.6364 | 70.6364 | 70.6364 | 70.6364 | 70.6364 | 70.6364 | 70.6364 | 70.6364 | 70.6364
Total Maximum Demand (MVA) - Option 3 Summer POE10 | 51.1554 | 66.2686 | 70.2261 | 69.9907 | 70.0105 | 70.4179 | 71.4905 | 72.2097 | 72.9132 | 73.7356 | 74.4985 | 75.2386 | 75.3243 | 76.1878 | 75.5357 | 75.5357 | 75.5357 | 75.5357 | 75.5357 | 75.5357 | 75.5357 | 75.5357 | 75.5357 | 75.5357 | 75.5357 | 75.5357 | 75.5357 | 75.5357 | 75.5357 | 75.5357
Option 4 - 3A OFR 3rd Tx + Switchroom + Three new feeders + OFR12 New Feeder
Year | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Added Transfers (MVA) | 0 | 0 | 0 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5
Added Demand management (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Added Embedded generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Maximum Demand (MVA) - Option 4 Winter POE50 | 40.358 | 56.0239 | 60.0964 | 46.2906 | 46.8321 | 47.7643 | 49.8852 | 51.3049 | 53.1034 | 54.0369 | 54.8582 | 53.345 | 55.1185 | 57.9066 | 55.7908 | 55.7908 | 55.7908 | 55.7908 | 55.7908 | 55.7908 | 55.7908 | 55.7908 | 55.7908 | 55.7908 | 55.7908 | 55.7908 | 55.7908 | 55.7908 | 55.7908 | 55.7908
Total Maximum Demand (MVA) - Option 4 Winter POE10 | 43.208 | 58.6763 | 62.9078 | 49.0625 | 49.4783 | 50.3903 | 52.5443 | 53.7204 | 55.9608 | 62.7709 | 57.1566 | 56.0585 | 57.5408 | 60.7827 | 58.5883 | 58.5883 | 58.5883 | 58.5883 | 58.5883 | 58.5883 | 58.5883 | 58.5883 | 58.5883 | 58.5883 | 58.5883 | 58.5883 | 58.5883 | 58.5883 | 58.5883 | 58.5883
Total Maximum Demand (MVA) - Option 4 Summer POE50 | 45.8759 | 60.9589 | 65.0674 | 50.4499 | 50.4485 | 50.9184 | 51.4338 | 52.4909 | 53.2504 | 53.6633 | 54.1157 | 54.529 | 55.2743 | 56.1989 | 56.1364 | 56.1364 | 56.1364 | 56.1364 | 56.1364 | 56.1364 | 56.1364 | 56.1364 | 56.1364 | 56.1364 | 56.1364 | 56.1364 | 56.1364 | 56.1364 | 56.1364 | 56.1364
Total Maximum Demand (MVA) - Option 4 Summer POE10 | 51.1554 | 66.2686 | 70.2261 | 55.4907 | 55.5105 | 55.9179 | 56.9905 | 57.7097 | 58.4132 | 59.2356 | 59.9985 | 60.7386 | 60.8243 | 61.6878 | 61.0357 | 61.0357 | 61.0357 | 61.0357 | 61.0357 | 61.0357 | 61.0357 | 61.0357 | 61.0357 | 61.0357 | 61.0357 | 61.0357 | 61.0357 | 61.0357 | 61.0357 | 61.0357
Option 5 - 4A LLG 2nd Tx + Switchroom + Three new feeders + OFR12 New Feeder
Year | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Added Transfers (MVA) | 0 | 0 | 0 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29
Added Demand management (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Added Embedded generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Maximum Demand (MVA) - Option 5 Winter POE50 | 40.358 | 56.0239 | 60.0964 | 31.7906 | 32.3321 | 33.2643 | 35.3852 | 36.8049 | 38.6034 | 39.5369 | 40.3582 | 38.845 | 40.6185 | 43.4066 | 41.2908 | 41.2908 | 41.2908 | 41.2908 | 41.2908 | 41.2908 | 41.2908 | 41.2908 | 41.2908 | 41.2908 | 41.2908 | 41.2908 | 41.2908 | 41.2908 | 41.2908 | 41.2908
Total Maximum Demand (MVA) - Option 5 Winter POE10 | 43.208 | 58.6763 | 62.9078 | 34.5625 | 34.9783 | 35.8903 | 38.0443 | 39.2204 | 41.4608 | 48.2709 | 42.6566 | 41.5585 | 43.0408 | 46.2827 | 44.0883 | 44.0883 | 44.0883 | 44.0883 | 44.0883 | 44.0883 | 44.0883 | 44.0883 | 44.0883 | 44.0883 | 44.0883 | 44.0883 | 44.0883 | 44.0883 | 44.0883 | 44.0883
Total Maximum Demand (MVA) - Option 5 Summer POE50 | 45.8759 | 60.9589 | 65.0674 | 35.9499 | 35.9485 | 36.4184 | 36.9338 | 37.9909 | 38.7504 | 39.1633 | 39.6157 | 40.029 | 40.7743 | 41.6989 | 41.6364 | 41.6364 | 41.6364 | 41.6364 | 41.6364 | 41.6364 | 41.6364 | 41.6364 | 41.6364 | 41.6364 | 41.6364 | 41.6364 | 41.6364 | 41.6364 | 41.6364 | 41.6364
Total Maximum Demand (MVA) - Option 5 Summer POE10 | 51.1554 | 66.2686 | 70.2261 | 40.9907 | 41.0105 | 41.4179 | 42.4905 | 43.2097 | 43.9132 | 44.7356 | 45.4985 | 46.2386 | 46.3243 | 47.1878 | 46.5357 | 46.5357 | 46.5357 | 46.5357 | 46.5357 | 46.5357 | 46.5357 | 46.5357 | 46.5357 | 46.5357 | 46.5357 | 46.5357 | 46.5357 | 46.5357 | 46.5357 | 46.5357
Option 6 - Non Network
Year | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Added Transfers (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Added Demand management (MVA) | 7.7456 | 9.9603 | 10.5358 | 10.4984 | 10.4969 | 10.5537 | 10.7079 | 10.8089 | 10.9091 | 11.0267 | 11.1341 | 11.2396 | 11.2492 | 11.3728 | 11.2743 | 11.2743 | 11.2743 | 11.2743 | 11.2743 | 11.2743 | 11.2743 | 11.2743 | 11.2743 | 11.2743 | 11.2743 | 11.2743 | 11.2743 | 11.2743 | 11.2743 | 11.2743
Added Embedded generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Maximum Demand (MVA) - Option 6 Winter POE50 | 32.6124 | 46.0636 | 49.5606 | 50.2922 | 50.8351 | 51.7106 | 53.6772 | 54.9959 | 56.6943 | 57.5103 | 58.2241 | 56.6054 | 58.3692 | 61.0337 | 59.0164 | 59.0164 | 59.0164 | 59.0164 | 59.0164 | 59.0164 | 59.0164 | 59.0164 | 59.0164 | 59.0164 | 59.0164 | 59.0164 | 59.0164 | 59.0164 | 59.0164 | 59.0164
Total Maximum Demand (MVA) - Option 6 Winter POE10 | 35.4624 | 48.716 | 52.372 | 53.0641 | 53.4814 | 54.3366 | 56.3364 | 57.4115 | 59.5517 | 66.2442 | 60.5225 | 59.3189 | 60.7916 | 63.9099 | 61.814 | 61.814 | 61.814 | 61.814 | 61.814 | 61.814 | 61.814 | 61.814 | 61.814 | 61.814 | 61.814 | 61.814 | 61.814 | 61.814 | 61.814 | 61.814
Total Maximum Demand (MVA) - Option 6 Summer POE50 | 38.1303 | 50.9986 | 54.5316 | 54.4514 | 54.4515 | 54.8647 | 55.2259 | 56.182 | 56.8413 | 57.1366 | 57.4816 | 57.7894 | 58.5251 | 59.326 | 59.362 | 59.362 | 59.362 | 59.362 | 59.362 | 59.362 | 59.362 | 59.362 | 59.362 | 59.362 | 59.362 | 59.362 | 59.362 | 59.362 | 59.362 | 59.362
Total Maximum Demand (MVA) - Option 6 Summer POE10 | 43.4098 | 56.3083 | 59.6903 | 59.4923 | 59.5136 | 59.8642 | 60.7826 | 61.4008 | 62.0041 | 62.7089 | 63.3644 | 63.9989 | 64.075 | 64.8149 | 64.2613 | 64.2613 | 64.2613 | 64.2613 | 64.2613 | 64.2613 | 64.2613 | 64.2613 | 64.2613 | 64.2613 | 64.2613 | 64.2613 | 64.2613 | 64.2613 | 64.2613 | 64.2613
Option 7 -
Year | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Added Transfers (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Added Demand management (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Added Embedded generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Maximum Demand (MVA) - Option 7 Winter POE50 | 40.358 | 56.0239 | 60.0964 | 60.7906 | 61.3321 | 62.2643 | 64.3852 | 65.8049 | 67.6034 | 68.5369 | 69.3582 | 67.845 | 69.6185 | 72.4066 | 70.2908 | 70.2908 | 70.2908 | 70.2908 | 70.2908 | 70.2908 | 70.2908 | 70.2908 | 70.2908 | 70.2908 | 70.2908 | 70.2908 | 70.2908 | 70.2908 | 70.2908 | 70.2908
Total Maximum Demand (MVA) - Option 7 Winter POE10 | 43.208 | 58.6763 | 62.9078 | 63.5625 | 63.9783 | 64.8903 | 67.0443 | 68.2204 | 70.4608 | 77.2709 | 71.6566 | 70.5585 | 72.0408 | 75.2827 | 73.0883 | 73.0883 | 73.0883 | 73.0883 | 73.0883 | 73.0883 | 73.0883 | 73.0883 | 73.0883 | 73.0883 | 73.0883 | 73.0883 | 73.0883 | 73.0883 | 73.0883 | 73.0883
Total Maximum Demand (MVA) - Option 7 Summer POE50 | 45.8759 | 60.9589 | 65.0674 | 64.9499 | 64.9485 | 65.4184 | 65.9338 | 66.9909 | 67.7504 | 68.1633 | 68.6157 | 69.029 | 69.7743 | 70.6989 | 70.6364 | 70.6364 | 70.6364 | 70.6364 | 70.6364 | 70.6364 | 70.6364 | 70.6364 | 70.6364 | 70.6364 | 70.6364 | 70.6364 | 70.6364 | 70.6364 | 70.6364 | 70.6364
Total Maximum Demand (MVA) - Option 7 Summer POE10 | 51.1554 | 66.2686 | 70.2261 | 69.9907 | 70.0105 | 70.4179 | 71.4905 | 72.2097 | 72.9132 | 73.7356 | 74.4985 | 75.2386 | 75.3243 | 76.1878 | 75.5357 | 75.5357 | 75.5357 | 75.5357 | 75.5357 | 75.5357 | 75.5357 | 75.5357 | 75.5357 | 75.5357 | 75.5357 | 75.5357 | 75.5357 | 75.5357 | 75.5357 | 75.5357
Option 8 -
Year | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Added Transfers (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Added Demand management (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Added Embedded generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Maximum Demand (MVA) - Option 8 Winter POE50 | 40.358 | 56.0239 | 60.0964 | 60.7906 | 61.3321 | 62.2643 | 64.3852 | 65.8049 | 67.6034 | 68.5369 | 69.3582 | 67.845 | 69.6185 | 72.4066 | 70.2908 | 70.2908 | 70.2908 | 70.2908 | 70.2908 | 70.2908 | 70.2908 | 70.2908 | 70.2908 | 70.2908 | 70.2908 | 70.2908 | 70.2908 | 70.2908 | 70.2908 | 70.2908
Total Maximum Demand (MVA) - Option 8 Winter POE10 | 43.208 | 58.6763 | 62.9078 | 63.5625 | 63.9783 | 64.8903 | 67.0443 | 68.2204 | 70.4608 | 77.2709 | 71.6566 | 70.5585 | 72.0408 | 75.2827 | 73.0883 | 73.0883 | 73.0883 | 73.0883 | 73.0883 | 73.0883 | 73.0883 | 73.0883 | 73.0883 | 73.0883 | 73.0883 | 73.0883 | 73.0883 | 73.0883 | 73.0883 | 73.0883
Total Maximum Demand (MVA) - Option 8 Summer POE50 | 45.8759 | 60.9589 | 65.0674 | 64.9499 | 64.9485 | 65.4184 | 65.9338 | 66.9909 | 67.7504 | 68.1633 | 68.6157 | 69.029 | 69.7743 | 70.6989 | 70.6364 | 70.6364 | 70.6364 | 70.6364 | 70.6364 | 70.6364 | 70.6364 | 70.6364 | 70.6364 | 70.6364 | 70.6364 | 70.6364 | 70.6364 | 70.6364 | 70.6364 | 70.6364
Total Maximum Demand (MVA) - Option 8 Summer POE10 | 51.1554 | 66.2686 | 70.2261 | 69.9907 | 70.0105 | 70.4179 | 71.4905 | 72.2097 | 72.9132 | 73.7356 | 74.4985 | 75.2386 | 75.3243 | 76.1878 | 75.5357 | 75.5357 | 75.5357 | 75.5357 | 75.5357 | 75.5357 | 75.5357 | 75.5357 | 75.5357 | 75.5357 | 75.5357 | 75.5357 | 75.5357 | 75.5357 | 75.5357 | 75.5357

## Forecasted LDC
Option 1 - Do Nothing / Base Case
Winter Season | [31 empty] | Winter Season
P50 | [31 empty] | P10
% of MD | Winter - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Winter - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 40.358 | 56.0239 | 60.0964 | 60.7906 | 61.3321 | 62.2643 | 64.3852 | 65.8049 | 67.6034 | 68.5369 | 69.3582 | 67.845 | 69.6185 | 72.4066 | 70.2908 | 70.2908 | 70.2908 | 70.2908 | 70.2908 | 70.2908 | 70.2908 | 70.2908 | 70.2908 | 70.2908 | 70.2908 | 70.2908 | 70.2908 | 70.2908 | 70.2908 | 70.2908 | 100% | 0 | 43.208 | 58.6763 | 62.9078 | 63.5625 | 63.9783 | 64.8903 | 67.0443 | 68.2204 | 70.4608 | 77.2709 | 71.6566 | 70.5585 | 72.0408 | 75.2827 | 73.0883 | 73.0883 | 73.0883 | 73.0883 | 73.0883 | 73.0883 | 73.0883 | 73.0883 | 73.0883 | 73.0883 | 73.0883 | 73.0883 | 73.0883 | 73.0883 | 73.0883 | 73.0883
99% | 1.486 | 39.9544 | 55.4636 | 59.4955 | 60.1827 | 60.7187 | 61.6416 | 63.7413 | 65.1468 | 66.9274 | 67.8516 | 68.6646 | 67.1665 | 68.9223 | 71.6825 | 69.5879 | 69.5879 | 69.5879 | 69.5879 | 69.5879 | 69.5879 | 69.5879 | 69.5879 | 69.5879 | 69.5879 | 69.5879 | 69.5879 | 69.5879 | 69.5879 | 69.5879 | 69.5879 | 99% | 1.486 | 42.7759 | 58.0895 | 62.2787 | 62.9269 | 63.3385 | 64.2414 | 66.3739 | 67.5382 | 69.7562 | 76.4982 | 70.9401 | 69.8529 | 71.3204 | 74.5299 | 72.3575 | 72.3575 | 72.3575 | 72.3575 | 72.3575 | 72.3575 | 72.3575 | 72.3575 | 72.3575 | 72.3575 | 72.3575 | 72.3575 | 72.3575 | 72.3575 | 72.3575 | 72.3575
98% | 3.2692 | 39.5508 | 54.9034 | 58.8945 | 59.5748 | 60.1054 | 61.019 | 63.0975 | 64.4888 | 66.2513 | 67.1662 | 67.9711 | 66.4881 | 68.2261 | 70.9584 | 68.885 | 68.885 | 68.885 | 68.885 | 68.885 | 68.885 | 68.885 | 68.885 | 68.885 | 68.885 | 68.885 | 68.885 | 68.885 | 68.885 | 68.885 | 68.885 | 98% | 3.2692 | 42.3438 | 57.5027 | 61.6497 | 62.2913 | 62.6987 | 63.5925 | 65.7034 | 66.856 | 69.0516 | 75.7255 | 70.2235 | 69.1473 | 70.6 | 73.7771 | 71.6266 | 71.6266 | 71.6266 | 71.6266 | 71.6266 | 71.6266 | 71.6266 | 71.6266 | 71.6266 | 71.6266 | 71.6266 | 71.6266 | 71.6266 | 71.6266 | 71.6266 | 71.6266
97% | 6.8356 | 39.1473 | 54.3431 | 58.2935 | 58.9669 | 59.4921 | 60.3964 | 62.4536 | 63.8307 | 65.5753 | 66.4808 | 67.2775 | 65.8096 | 67.5299 | 70.2344 | 68.1821 | 68.1821 | 68.1821 | 68.1821 | 68.1821 | 68.1821 | 68.1821 | 68.1821 | 68.1821 | 68.1821 | 68.1821 | 68.1821 | 68.1821 | 68.1821 | 68.1821 | 68.1821 | 97% | 6.8356 | 41.9118 | 56.916 | 61.0206 | 61.6557 | 62.0589 | 62.9436 | 65.033 | 66.1738 | 68.3469 | 74.9528 | 69.5069 | 68.4417 | 69.8796 | 73.0243 | 70.8957 | 70.8957 | 70.8957 | 70.8957 | 70.8957 | 70.8957 | 70.8957 | 70.8957 | 70.8957 | 70.8957 | 70.8957 | 70.8957 | 70.8957 | 70.8957 | 70.8957 | 70.8957
95% | 17.5347 | 38.3401 | 53.2227 | 57.0916 | 57.7511 | 58.2655 | 59.1511 | 61.1659 | 62.5146 | 64.2232 | 65.1101 | 65.8903 | 64.4527 | 66.1375 | 68.7862 | 66.7762 | 66.7762 | 66.7762 | 66.7762 | 66.7762 | 66.7762 | 66.7762 | 66.7762 | 66.7762 | 66.7762 | 66.7762 | 66.7762 | 66.7762 | 66.7762 | 66.7762 | 66.7762 | 95% | 17.5347 | 41.0476 | 55.7425 | 59.7624 | 60.3844 | 60.7794 | 61.6458 | 63.6921 | 64.8094 | 66.9377 | 73.4073 | 68.0738 | 67.0306 | 68.4388 | 71.5186 | 69.4339 | 69.4339 | 69.4339 | 69.4339 | 69.4339 | 69.4339 | 69.4339 | 69.4339 | 69.4339 | 69.4339 | 69.4339 | 69.4339 | 69.4339 | 69.4339 | 69.4339 | 69.4339
90% | 78.7576 | 36.3222 | 50.4215 | 54.0868 | 54.7116 | 55.1988 | 56.0379 | 57.9467 | 59.2244 | 60.8431 | 61.6833 | 62.4224 | 61.0605 | 62.6566 | 65.1659 | 63.2617 | 63.2617 | 63.2617 | 63.2617 | 63.2617 | 63.2617 | 63.2617 | 63.2617 | 63.2617 | 63.2617 | 63.2617 | 63.2617 | 63.2617 | 63.2617 | 63.2617 | 63.2617 | 90% | 78.7576 | 38.8872 | 52.8086 | 56.617 | 57.2063 | 57.5804 | 58.4013 | 60.3399 | 61.3984 | 63.4147 | 69.5438 | 64.491 | 63.5026 | 64.8368 | 67.7545 | 65.7795 | 65.7795 | 65.7795 | 65.7795 | 65.7795 | 65.7795 | 65.7795 | 65.7795 | 65.7795 | 65.7795 | 65.7795 | 65.7795 | 65.7795 | 65.7795 | 65.7795 | 65.7795
85% | 236.8672 | 34.3043 | 47.6203 | 51.082 | 51.672 | 52.1322 | 52.9246 | 54.7274 | 55.9342 | 57.4629 | 58.2564 | 58.9545 | 57.6682 | 59.1757 | 61.5456 | 59.7472 | 59.7472 | 59.7472 | 59.7472 | 59.7472 | 59.7472 | 59.7472 | 59.7472 | 59.7472 | 59.7472 | 59.7472 | 59.7472 | 59.7472 | 59.7472 | 59.7472 | 59.7472 | 85% | 236.8672 | 36.7268 | 49.8748 | 53.4716 | 54.0282 | 54.3815 | 55.1567 | 56.9877 | 57.9873 | 59.8917 | 65.6803 | 60.9081 | 59.9747 | 61.2347 | 63.9903 | 62.1251 | 62.1251 | 62.1251 | 62.1251 | 62.1251 | 62.1251 | 62.1251 | 62.1251 | 62.1251 | 62.1251 | 62.1251 | 62.1251 | 62.1251 | 62.1251 | 62.1251 | 62.1251
80% | 497.5104 | 32.2864 | 44.8191 | 48.0771 | 48.6325 | 49.0656 | 49.8114 | 51.5081 | 52.6439 | 54.0827 | 54.8296 | 55.4866 | 54.276 | 55.6948 | 57.9252 | 56.2326 | 56.2326 | 56.2326 | 56.2326 | 56.2326 | 56.2326 | 56.2326 | 56.2326 | 56.2326 | 56.2326 | 56.2326 | 56.2326 | 56.2326 | 56.2326 | 56.2326 | 56.2326 | 80% | 497.5104 | 34.5664 | 46.941 | 50.3262 | 50.85 | 51.1826 | 51.9122 | 53.6355 | 54.5763 | 56.3686 | 61.8167 | 57.3253 | 56.4468 | 57.6327 | 60.2262 | 58.4707 | 58.4707 | 58.4707 | 58.4707 | 58.4707 | 58.4707 | 58.4707 | 58.4707 | 58.4707 | 58.4707 | 58.4707 | 58.4707 | 58.4707 | 58.4707 | 58.4707 | 58.4707
75% | 803.6248 | 30.2685 | 42.0179 | 45.0723 | 45.593 | 45.999 | 46.6982 | 48.2889 | 49.3537 | 50.7026 | 51.4027 | 52.0187 | 50.8837 | 52.2138 | 54.3049 | 52.7181 | 52.7181 | 52.7181 | 52.7181 | 52.7181 | 52.7181 | 52.7181 | 52.7181 | 52.7181 | 52.7181 | 52.7181 | 52.7181 | 52.7181 | 52.7181 | 52.7181 | 52.7181 | 75% | 803.6248 | 32.406 | 44.0072 | 47.1809 | 47.6719 | 47.9837 | 48.6677 | 50.2832 | 51.1653 | 52.8456 | 57.9532 | 53.7425 | 52.9189 | 54.0306 | 56.4621 | 54.8163 | 54.8163 | 54.8163 | 54.8163 | 54.8163 | 54.8163 | 54.8163 | 54.8163 | 54.8163 | 54.8163 | 54.8163 | 54.8163 | 54.8163 | 54.8163 | 54.8163 | 54.8163
70% | 1155.2107 | 28.2506 | 39.2167 | 42.0675 | 42.5534 | 42.9324 | 43.585 | 45.0696 | 46.0634 | 47.3224 | 47.9759 | 48.5508 | 47.4915 | 48.7329 | 50.6846 | 49.2035 | 49.2035 | 49.2035 | 49.2035 | 49.2035 | 49.2035 | 49.2035 | 49.2035 | 49.2035 | 49.2035 | 49.2035 | 49.2035 | 49.2035 | 49.2035 | 49.2035 | 49.2035 | 70% | 1155.2107 | 30.2456 | 41.0734 | 44.0355 | 44.4938 | 44.7848 | 45.4232 | 46.931 | 47.7543 | 49.3225 | 54.0896 | 50.1596 | 49.3909 | 50.4286 | 52.6979 | 51.1618 | 51.1618 | 51.1618 | 51.1618 | 51.1618 | 51.1618 | 51.1618 | 51.1618 | 51.1618 | 51.1618 | 51.1618 | 51.1618 | 51.1618 | 51.1618 | 51.1618 | 51.1618
65% | 1553.1596 | 26.2327 | 36.4155 | 39.0627 | 39.5139 | 39.8658 | 40.4718 | 41.8504 | 42.7732 | 43.9422 | 44.549 | 45.0828 | 44.0992 | 45.252 | 47.0643 | 45.689 | 45.689 | 45.689 | 45.689 | 45.689 | 45.689 | 45.689 | 45.689 | 45.689 | 45.689 | 45.689 | 45.689 | 45.689 | 45.689 | 45.689 | 45.689 | 65% | 1553.1596 | 28.0852 | 38.1396 | 40.8901 | 41.3157 | 41.5859 | 42.1787 | 43.5788 | 44.3433 | 45.7995 | 50.2261 | 46.5768 | 45.863 | 46.8266 | 48.9338 | 47.5074 | 47.5074 | 47.5074 | 47.5074 | 47.5074 | 47.5074 | 47.5074 | 47.5074 | 47.5074 | 47.5074 | 47.5074 | 47.5074 | 47.5074 | 47.5074 | 47.5074 | 47.5074
60% | 2026.2996 | 24.2148 | 33.6143 | 36.0579 | 36.4744 | 36.7992 | 37.3586 | 38.6311 | 39.4829 | 40.562 | 41.1222 | 41.6149 | 40.707 | 41.7711 | 43.4439 | 42.1745 | 42.1745 | 42.1745 | 42.1745 | 42.1745 | 42.1745 | 42.1745 | 42.1745 | 42.1745 | 42.1745 | 42.1745 | 42.1745 | 42.1745 | 42.1745 | 42.1745 | 42.1745 | 60% | 2026.2996 | 25.9248 | 35.2058 | 37.7447 | 38.1375 | 38.387 | 38.9342 | 40.2266 | 40.9322 | 42.2765 | 46.3625 | 42.994 | 42.3351 | 43.2245 | 45.1696 | 43.853 | 43.853 | 43.853 | 43.853 | 43.853 | 43.853 | 43.853 | 43.853 | 43.853 | 43.853 | 43.853 | 43.853 | 43.853 | 43.853 | 43.853 | 43.853
55% | 2598.4068 | 22.1969 | 30.8131 | 33.053 | 33.4348 | 33.7326 | 34.2454 | 35.4119 | 36.1927 | 37.1819 | 37.6953 | 38.147 | 37.3147 | 38.2902 | 39.8236 | 38.6599 | 38.6599 | 38.6599 | 38.6599 | 38.6599 | 38.6599 | 38.6599 | 38.6599 | 38.6599 | 38.6599 | 38.6599 | 38.6599 | 38.6599 | 38.6599 | 38.6599 | 38.6599 | 55% | 2598.4068 | 23.7644 | 32.272 | 34.5993 | 34.9594 | 35.188 | 35.6897 | 36.8744 | 37.5212 | 38.7534 | 42.499 | 39.4111 | 38.8072 | 39.6225 | 41.4055 | 40.1986 | 40.1986 | 40.1986 | 40.1986 | 40.1986 | 40.1986 | 40.1986 | 40.1986 | 40.1986 | 40.1986 | 40.1986 | 40.1986 | 40.1986 | 40.1986 | 40.1986 | 40.1986
50% | 3233.5201 | 20.179 | 28.0119 | 30.0482 | 30.3953 | 30.666 | 31.1321 | 32.1926 | 32.9024 | 33.8017 | 34.2685 | 34.6791 | 33.9225 | 34.8092 | 36.2033 | 35.1454 | 35.1454 | 35.1454 | 35.1454 | 35.1454 | 35.1454 | 35.1454 | 35.1454 | 35.1454 | 35.1454 | 35.1454 | 35.1454 | 35.1454 | 35.1454 | 35.1454 | 35.1454 | 50% | 3233.5201 | 21.604 | 29.3381 | 31.4539 | 31.7813 | 31.9891 | 32.4451 | 33.5222 | 34.1102 | 35.2304 | 38.6354 | 35.8283 | 35.2792 | 36.0204 | 37.6414 | 36.5442 | 36.5442 | 36.5442 | 36.5442 | 36.5442 | 36.5442 | 36.5442 | 36.5442 | 36.5442 | 36.5442 | 36.5442 | 36.5442 | 36.5442 | 36.5442 | 36.5442 | 36.5442
45% | 3775.313 | 18.1611 | 25.2107 | 27.0434 | 27.3558 | 27.5994 | 28.0189 | 28.9733 | 29.6122 | 30.4215 | 30.8416 | 31.2112 | 30.5302 | 31.3283 | 32.583 | 31.6309 | 31.6309 | 31.6309 | 31.6309 | 31.6309 | 31.6309 | 31.6309 | 31.6309 | 31.6309 | 31.6309 | 31.6309 | 31.6309 | 31.6309 | 31.6309 | 31.6309 | 31.6309 | 45% | 3775.313 | 19.4436 | 26.4043 | 28.3085 | 28.6031 | 28.7902 | 29.2006 | 30.1699 | 30.6992 | 31.7073 | 34.7719 | 32.2455 | 31.7513 | 32.4184 | 33.8772 | 32.8898 | 32.8898 | 32.8898 | 32.8898 | 32.8898 | 32.8898 | 32.8898 | 32.8898 | 32.8898 | 32.8898 | 32.8898 | 32.8898 | 32.8898 | 32.8898 | 32.8898 | 32.8898
40% | 4072.8088 | 16.1432 | 22.4095 | 24.0386 | 24.3162 | 24.5328 | 24.9057 | 25.7541 | 26.322 | 27.0414 | 27.4148 | 27.7433 | 27.138 | 27.8474 | 28.9626 | 28.1163 | 28.1163 | 28.1163 | 28.1163 | 28.1163 | 28.1163 | 28.1163 | 28.1163 | 28.1163 | 28.1163 | 28.1163 | 28.1163 | 28.1163 | 28.1163 | 28.1163 | 28.1163 | 40% | 4072.8088 | 17.2832 | 23.4705 | 25.1631 | 25.425 | 25.5913 | 25.9561 | 26.8177 | 27.2882 | 28.1843 | 30.9084 | 28.6627 | 28.2234 | 28.8163 | 30.1131 | 29.2353 | 29.2353 | 29.2353 | 29.2353 | 29.2353 | 29.2353 | 29.2353 | 29.2353 | 29.2353 | 29.2353 | 29.2353 | 29.2353 | 29.2353 | 29.2353 | 29.2353 | 29.2353
35% | 4198.821 | 14.1253 | 19.6083 | 21.0337 | 21.2767 | 21.4662 | 21.7925 | 22.5348 | 23.0317 | 23.6612 | 23.9879 | 24.2754 | 23.7457 | 24.3665 | 25.3423 | 24.6018 | 24.6018 | 24.6018 | 24.6018 | 24.6018 | 24.6018 | 24.6018 | 24.6018 | 24.6018 | 24.6018 | 24.6018 | 24.6018 | 24.6018 | 24.6018 | 24.6018 | 24.6018 | 35% | 4198.821 | 15.1228 | 20.5367 | 22.0177 | 22.2469 | 22.3924 | 22.7116 | 23.4655 | 23.8771 | 24.6613 | 27.0448 | 25.0798 | 24.6955 | 25.2143 | 26.349 | 25.5809 | 25.5809 | 25.5809 | 25.5809 | 25.5809 | 25.5809 | 25.5809 | 25.5809 | 25.5809 | 25.5809 | 25.5809 | 25.5809 | 25.5809 | 25.5809 | 25.5809 | 25.5809
30% | 4271.3374 | 12.1074 | 16.8072 | 18.0289 | 18.2372 | 18.3996 | 18.6793 | 19.3156 | 19.7415 | 20.281 | 20.5611 | 20.8075 | 20.3535 | 20.8855 | 21.722 | 21.0872 | 21.0872 | 21.0872 | 21.0872 | 21.0872 | 21.0872 | 21.0872 | 21.0872 | 21.0872 | 21.0872 | 21.0872 | 21.0872 | 21.0872 | 21.0872 | 21.0872 | 21.0872 | 30% | 4271.3374 | 12.9624 | 17.6029 | 18.8723 | 19.0688 | 19.1935 | 19.4671 | 20.1133 | 20.4661 | 21.1382 | 23.1813 | 21.497 | 21.1675 | 21.6123 | 22.5848 | 21.9265 | 21.9265 | 21.9265 | 21.9265 | 21.9265 | 21.9265 | 21.9265 | 21.9265 | 21.9265 | 21.9265 | 21.9265 | 21.9265 | 21.9265 | 21.9265 | 21.9265 | 21.9265
25% | 4321.8611 | 10.0895 | 14.006 | 15.0241 | 15.1977 | 15.333 | 15.5661 | 16.0963 | 16.4512 | 16.9009 | 17.1342 | 17.3396 | 16.9612 | 17.4046 | 18.1016 | 17.5727 | 17.5727 | 17.5727 | 17.5727 | 17.5727 | 17.5727 | 17.5727 | 17.5727 | 17.5727 | 17.5727 | 17.5727 | 17.5727 | 17.5727 | 17.5727 | 17.5727 | 17.5727 | 25% | 4321.8611 | 10.802 | 14.6691 | 15.727 | 15.8906 | 15.9946 | 16.2226 | 16.7611 | 17.0551 | 17.6152 | 19.3177 | 17.9142 | 17.6396 | 18.0102 | 18.8207 | 18.2721 | 18.2721 | 18.2721 | 18.2721 | 18.2721 | 18.2721 | 18.2721 | 18.2721 | 18.2721 | 18.2721 | 18.2721 | 18.2721 | 18.2721 | 18.2721 | 18.2721 | 18.2721
20% | 4353.067 | 8.0716 | 11.2048 | 12.0193 | 12.1581 | 12.2664 | 12.4529 | 12.877 | 13.161 | 13.5207 | 13.7074 | 13.8716 | 13.569 | 13.9237 | 14.4813 | 14.0582 | 14.0582 | 14.0582 | 14.0582 | 14.0582 | 14.0582 | 14.0582 | 14.0582 | 14.0582 | 14.0582 | 14.0582 | 14.0582 | 14.0582 | 14.0582 | 14.0582 | 14.0582 | 20% | 4353.067 | 8.6416 | 11.7353 | 12.5816 | 12.7125 | 12.7957 | 12.9781 | 13.4089 | 13.6441 | 14.0922 | 15.4542 | 14.3313 | 14.1117 | 14.4082 | 15.0565 | 14.6177 | 14.6177 | 14.6177 | 14.6177 | 14.6177 | 14.6177 | 14.6177 | 14.6177 | 14.6177 | 14.6177 | 14.6177 | 14.6177 | 14.6177 | 14.6177 | 14.6177 | 14.6177
15% | 4369.4129 | 6.0537 | 8.4036 | 9.0145 | 9.1186 | 9.1998 | 9.3396 | 9.6578 | 9.8707 | 10.1405 | 10.2805 | 10.4037 | 10.1767 | 10.4428 | 10.861 | 10.5436 | 10.5436 | 10.5436 | 10.5436 | 10.5436 | 10.5436 | 10.5436 | 10.5436 | 10.5436 | 10.5436 | 10.5436 | 10.5436 | 10.5436 | 10.5436 | 10.5436 | 10.5436 | 15% | 4369.4129 | 6.4812 | 8.8014 | 9.4362 | 9.5344 | 9.5967 | 9.7335 | 10.0566 | 10.2331 | 10.5691 | 11.5906 | 10.7485 | 10.5838 | 10.8061 | 11.2924 | 10.9633 | 10.9633 | 10.9633 | 10.9633 | 10.9633 | 10.9633 | 10.9633 | 10.9633 | 10.9633 | 10.9633 | 10.9633 | 10.9633 | 10.9633 | 10.9633 | 10.9633 | 10.9633
10% | 4378.6261 | 4.0358 | 5.6024 | 6.0096 | 6.0791 | 6.1332 | 6.2264 | 6.4385 | 6.5805 | 6.7603 | 6.8537 | 6.9358 | 6.7845 | 6.9618 | 7.2407 | 7.0291 | 7.0291 | 7.0291 | 7.0291 | 7.0291 | 7.0291 | 7.0291 | 7.0291 | 7.0291 | 7.0291 | 7.0291 | 7.0291 | 7.0291 | 7.0291 | 7.0291 | 7.0291 | 10% | 4378.6261 | 4.3208 | 5.8676 | 6.2908 | 6.3563 | 6.3978 | 6.489 | 6.7044 | 6.822 | 7.0461 | 7.7271 | 7.1657 | 7.0558 | 7.2041 | 7.5283 | 7.3088 | 7.3088 | 7.3088 | 7.3088 | 7.3088 | 7.3088 | 7.3088 | 7.3088 | 7.3088 | 7.3088 | 7.3088 | 7.3088 | 7.3088 | 7.3088 | 7.3088 | 7.3088
5% | 4391.7028 | 2.0179 | 2.8012 | 3.0048 | 3.0395 | 3.0666 | 3.1132 | 3.2193 | 3.2902 | 3.3802 | 3.4268 | 3.4679 | 3.3922 | 3.4809 | 3.6203 | 3.5145 | 3.5145 | 3.5145 | 3.5145 | 3.5145 | 3.5145 | 3.5145 | 3.5145 | 3.5145 | 3.5145 | 3.5145 | 3.5145 | 3.5145 | 3.5145 | 3.5145 | 3.5145 | 5% | 4391.7028 | 2.1604 | 2.9338 | 3.1454 | 3.1781 | 3.1989 | 3.2445 | 3.3522 | 3.411 | 3.523 | 3.8635 | 3.5828 | 3.5279 | 3.602 | 3.7641 | 3.6544 | 3.6544 | 3.6544 | 3.6544 | 3.6544 | 3.6544 | 3.6544 | 3.6544 | 3.6544 | 3.6544 | 3.6544 | 3.6544 | 3.6544 | 3.6544 | 3.6544 | 3.6544
9.992e-14% | 4391.7028 | 4.0326e-14 | 5.5979e-14 | 6.0048e-14 | 6.0742e-14 | 6.1283e-14 | 6.2215e-14 | 6.4334e-14 | 6.5752e-14 | 6.7549e-14 | 6.8482e-14 | 6.9303e-14 | 6.7791e-14 | 6.9563e-14 | 7.2349e-14 | 7.0235e-14 | 7.0235e-14 | 7.0235e-14 | 7.0235e-14 | 7.0235e-14 | 7.0235e-14 | 7.0235e-14 | 7.0235e-14 | 7.0235e-14 | 7.0235e-14 | 7.0235e-14 | 7.0235e-14 | 7.0235e-14 | 7.0235e-14 | 7.0235e-14 | 7.0235e-14 | 9.992e-14% | 4391.7028 | 4.3173e-14 | 5.8629e-14 | 6.2858e-14 | 6.3512e-14 | 6.3927e-14 | 6.4838e-14 | 6.6991e-14 | 6.8166e-14 | 7.0404e-14 | 7.7209e-14 | 7.1599e-14 | 7.0502e-14 | 7.1983e-14 | 7.5223e-14 | 7.303e-14 | 7.303e-14 | 7.303e-14 | 7.303e-14 | 7.303e-14 | 7.303e-14 | 7.303e-14 | 7.303e-14 | 7.303e-14 | 7.303e-14 | 7.303e-14 | 7.303e-14 | 7.303e-14 | 7.303e-14 | 7.303e-14 | 7.303e-14
Summer Season | [31 empty] | Summer Season
P50 | [31 empty] | P10
% of MD | Summer - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Summer - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 45.8759 | 60.9589 | 65.0674 | 64.9499 | 64.9485 | 65.4184 | 65.9338 | 66.9909 | 67.7504 | 68.1633 | 68.6157 | 69.029 | 69.7743 | 70.6989 | 70.6364 | 70.6364 | 70.6364 | 70.6364 | 70.6364 | 70.6364 | 70.6364 | 70.6364 | 70.6364 | 70.6364 | 70.6364 | 70.6364 | 70.6364 | 70.6364 | 70.6364 | 70.6364 | 100% | 0 | 51.1554 | 66.2686 | 70.2261 | 69.9907 | 70.0105 | 70.4179 | 71.4905 | 72.2097 | 72.9132 | 73.7356 | 74.4985 | 75.2386 | 75.3243 | 76.1878 | 75.5357 | 75.5357 | 75.5357 | 75.5357 | 75.5357 | 75.5357 | 75.5357 | 75.5357 | 75.5357 | 75.5357 | 75.5357 | 75.5357 | 75.5357 | 75.5357 | 75.5357 | 75.5357
99% | 0 | 45.4171 | 60.3493 | 64.4168 | 64.3004 | 64.299 | 64.7642 | 65.2745 | 66.321 | 67.0729 | 67.4817 | 67.9295 | 68.3387 | 69.0766 | 69.9919 | 69.93 | 69.93 | 69.93 | 69.93 | 69.93 | 69.93 | 69.93 | 69.93 | 69.93 | 69.93 | 69.93 | 69.93 | 69.93 | 69.93 | 69.93 | 69.93 | 99% | 1.5127 | 50.6438 | 65.6059 | 69.5238 | 69.2908 | 69.3104 | 69.7137 | 70.7756 | 71.4876 | 72.184 | 72.9983 | 73.7535 | 74.4862 | 74.571 | 75.4259 | 74.7803 | 74.7803 | 74.7803 | 74.7803 | 74.7803 | 74.7803 | 74.7803 | 74.7803 | 74.7803 | 74.7803 | 74.7803 | 74.7803 | 74.7803 | 74.7803 | 74.7803 | 74.7803
98% | 0 | 44.9584 | 59.7397 | 63.7661 | 63.6509 | 63.6495 | 64.11 | 64.6151 | 65.6511 | 66.3954 | 66.8001 | 67.2434 | 67.6484 | 68.3788 | 69.2849 | 69.2236 | 69.2236 | 69.2236 | 69.2236 | 69.2236 | 69.2236 | 69.2236 | 69.2236 | 69.2236 | 69.2236 | 69.2236 | 69.2236 | 69.2236 | 69.2236 | 69.2236 | 69.2236 | 98% | 2.269 | 50.1322 | 64.9433 | 68.8216 | 68.5909 | 68.6103 | 69.0096 | 70.0607 | 70.7655 | 71.4549 | 72.2609 | 73.0085 | 73.7338 | 73.8178 | 74.664 | 74.0249 | 74.0249 | 74.0249 | 74.0249 | 74.0249 | 74.0249 | 74.0249 | 74.0249 | 74.0249 | 74.0249 | 74.0249 | 74.0249 | 74.0249 | 74.0249 | 74.0249 | 74.0249
97% | 0.37816 | 44.4996 | 59.1301 | 63.1154 | 63.0014 | 63 | 63.4558 | 63.9558 | 64.9812 | 65.7179 | 66.1184 | 66.5572 | 66.9581 | 67.6811 | 68.5779 | 68.5173 | 68.5173 | 68.5173 | 68.5173 | 68.5173 | 68.5173 | 68.5173 | 68.5173 | 68.5173 | 68.5173 | 68.5173 | 68.5173 | 68.5173 | 68.5173 | 68.5173 | 68.5173 | 97% | 3.7816 | 49.6207 | 64.2806 | 68.1193 | 67.891 | 67.9102 | 68.3054 | 69.3458 | 70.0434 | 70.7258 | 71.5236 | 72.2636 | 72.9814 | 73.0646 | 73.9022 | 73.2696 | 73.2696 | 73.2696 | 73.2696 | 73.2696 | 73.2696 | 73.2696 | 73.2696 | 73.2696 | 73.2696 | 73.2696 | 73.2696 | 73.2696 | 73.2696 | 73.2696 | 73.2696
95% | 2.269 | 43.5821 | 57.911 | 61.8141 | 61.7024 | 61.701 | 62.1474 | 62.6371 | 63.6414 | 64.3629 | 64.7552 | 65.1849 | 65.5776 | 66.2856 | 67.1639 | 67.1046 | 67.1046 | 67.1046 | 67.1046 | 67.1046 | 67.1046 | 67.1046 | 67.1046 | 67.1046 | 67.1046 | 67.1046 | 67.1046 | 67.1046 | 67.1046 | 67.1046 | 67.1046 | 95% | 6.0506 | 48.5976 | 62.9552 | 66.7148 | 66.4912 | 66.51 | 66.897 | 67.916 | 68.5992 | 69.2675 | 70.0488 | 70.7736 | 71.4766 | 71.5581 | 72.3784 | 71.7589 | 71.7589 | 71.7589 | 71.7589 | 71.7589 | 71.7589 | 71.7589 | 71.7589 | 71.7589 | 71.7589 | 71.7589 | 71.7589 | 71.7589 | 71.7589 | 71.7589 | 71.7589
90% | 5.6725 | 41.2883 | 54.863 | 58.5607 | 58.4549 | 58.4536 | 58.8765 | 59.3404 | 60.2918 | 60.9754 | 61.347 | 61.7541 | 62.1261 | 62.7969 | 63.629 | 63.5727 | 63.5727 | 63.5727 | 63.5727 | 63.5727 | 63.5727 | 63.5727 | 63.5727 | 63.5727 | 63.5727 | 63.5727 | 63.5727 | 63.5727 | 63.5727 | 63.5727 | 63.5727 | 90% | 16.2611 | 46.0398 | 59.6418 | 63.2035 | 62.9917 | 63.0094 | 63.3761 | 64.3415 | 64.9887 | 65.6218 | 66.3621 | 67.0487 | 67.7147 | 67.7919 | 68.569 | 67.9821 | 67.9821 | 67.9821 | 67.9821 | 67.9821 | 67.9821 | 67.9821 | 67.9821 | 67.9821 | 67.9821 | 67.9821 | 67.9821 | 67.9821 | 67.9821 | 67.9821 | 67.9821
85% | 15.8829 | 38.9945 | 51.8151 | 55.3073 | 55.2074 | 55.2062 | 55.6056 | 56.0437 | 56.9423 | 57.5879 | 57.9388 | 58.3233 | 58.6747 | 59.3082 | 60.094 | 60.0409 | 60.0409 | 60.0409 | 60.0409 | 60.0409 | 60.0409 | 60.0409 | 60.0409 | 60.0409 | 60.0409 | 60.0409 | 60.0409 | 60.0409 | 60.0409 | 60.0409 | 60.0409 | 85% | 26.4715 | 43.482 | 56.3283 | 59.6922 | 59.4921 | 59.5089 | 59.8552 | 60.767 | 61.3783 | 61.9762 | 62.6753 | 63.3237 | 63.9528 | 64.0256 | 64.7596 | 64.2053 | 64.2053 | 64.2053 | 64.2053 | 64.2053 | 64.2053 | 64.2053 | 64.2053 | 64.2053 | 64.2053 | 64.2053 | 64.2053 | 64.2053 | 64.2053 | 64.2053 | 64.2053
80% | 31.0095 | 36.7007 | 48.7671 | 52.0539 | 51.9599 | 51.9588 | 52.3347 | 52.747 | 53.5928 | 54.2003 | 54.5307 | 54.8925 | 55.2232 | 55.8194 | 56.5591 | 56.5091 | 56.5091 | 56.5091 | 56.5091 | 56.5091 | 56.5091 | 56.5091 | 56.5091 | 56.5091 | 56.5091 | 56.5091 | 56.5091 | 56.5091 | 56.5091 | 56.5091 | 56.5091 | 80% | 34.0348 | 40.9243 | 53.0149 | 56.1809 | 55.9926 | 56.0084 | 56.3343 | 57.1924 | 57.7678 | 58.3305 | 58.9885 | 59.5988 | 60.1908 | 60.2594 | 60.9502 | 60.4285 | 60.4285 | 60.4285 | 60.4285 | 60.4285 | 60.4285 | 60.4285 | 60.4285 | 60.4285 | 60.4285 | 60.4285 | 60.4285 | 60.4285 | 60.4285 | 60.4285 | 60.4285
75% | 72.9857 | 34.4069 | 45.7192 | 48.8006 | 48.7124 | 48.7113 | 49.0638 | 49.4504 | 50.2432 | 50.8128 | 51.1225 | 51.4618 | 51.7718 | 52.3307 | 53.0241 | 52.9773 | 52.9773 | 52.9773 | 52.9773 | 52.9773 | 52.9773 | 52.9773 | 52.9773 | 52.9773 | 52.9773 | 52.9773 | 52.9773 | 52.9773 | 52.9773 | 52.9773 | 52.9773 | 75% | 48.405 | 38.3665 | 49.7015 | 52.6696 | 52.493 | 52.5079 | 52.8134 | 53.6179 | 54.1573 | 54.6849 | 55.3017 | 55.8739 | 56.4289 | 56.4932 | 57.1408 | 56.6517 | 56.6517 | 56.6517 | 56.6517 | 56.6517 | 56.6517 | 56.6517 | 56.6517 | 56.6517 | 56.6517 | 56.6517 | 56.6517 | 56.6517 | 56.6517 | 56.6517 | 56.6517
70% | 150.5094 | 32.1131 | 42.6712 | 45.5472 | 45.4649 | 45.4639 | 45.7929 | 46.1537 | 46.8937 | 47.4253 | 47.7143 | 48.031 | 48.3203 | 48.842 | 49.4892 | 49.4455 | 49.4455 | 49.4455 | 49.4455 | 49.4455 | 49.4455 | 49.4455 | 49.4455 | 49.4455 | 49.4455 | 49.4455 | 49.4455 | 49.4455 | 49.4455 | 49.4455 | 49.4455 | 70% | 76.3892 | 35.8087 | 46.388 | 49.1583 | 48.9935 | 49.0073 | 49.2925 | 50.0434 | 50.5468 | 51.0392 | 51.6149 | 52.149 | 52.667 | 52.727 | 53.3315 | 52.875 | 52.875 | 52.875 | 52.875 | 52.875 | 52.875 | 52.875 | 52.875 | 52.875 | 52.875 | 52.875 | 52.875 | 52.875 | 52.875 | 52.875 | 52.875
65% | 359.6342 | 29.8193 | 39.6233 | 42.2938 | 42.2174 | 42.2165 | 42.5219 | 42.857 | 43.5441 | 44.0378 | 44.3062 | 44.6002 | 44.8689 | 45.3533 | 45.9543 | 45.9136 | 45.9136 | 45.9136 | 45.9136 | 45.9136 | 45.9136 | 45.9136 | 45.9136 | 45.9136 | 45.9136 | 45.9136 | 45.9136 | 45.9136 | 45.9136 | 45.9136 | 45.9136 | 65% | 114.2056 | 33.251 | 43.0746 | 45.647 | 45.494 | 45.5068 | 45.7716 | 46.4689 | 46.9363 | 47.3936 | 47.9282 | 48.424 | 48.9051 | 48.9608 | 49.5221 | 49.0982 | 49.0982 | 49.0982 | 49.0982 | 49.0982 | 49.0982 | 49.0982 | 49.0982 | 49.0982 | 49.0982 | 49.0982 | 49.0982 | 49.0982 | 49.0982 | 49.0982 | 49.0982
60% | 689.7717 | 27.5255 | 36.5753 | 39.0405 | 38.9699 | 38.9691 | 39.251 | 39.5603 | 40.1946 | 40.6503 | 40.898 | 41.1694 | 41.4174 | 41.8646 | 42.4193 | 42.3818 | 42.3818 | 42.3818 | 42.3818 | 42.3818 | 42.3818 | 42.3818 | 42.3818 | 42.3818 | 42.3818 | 42.3818 | 42.3818 | 42.3818 | 42.3818 | 42.3818 | 42.3818 | 60% | 178.1154 | 30.6932 | 39.7612 | 42.1357 | 41.9944 | 42.0063 | 42.2508 | 42.8943 | 43.3258 | 43.7479 | 44.2414 | 44.6991 | 45.1431 | 45.1946 | 45.7127 | 45.3214 | 45.3214 | 45.3214 | 45.3214 | 45.3214 | 45.3214 | 45.3214 | 45.3214 | 45.3214 | 45.3214 | 45.3214 | 45.3214 | 45.3214 | 45.3214 | 45.3214 | 45.3214
55% | 1095.5419 | 25.2317 | 33.5274 | 35.7871 | 35.7224 | 35.7217 | 35.9801 | 36.2636 | 36.845 | 37.2627 | 37.4898 | 37.7386 | 37.966 | 38.3759 | 38.8844 | 38.85 | 38.85 | 38.85 | 38.85 | 38.85 | 38.85 | 38.85 | 38.85 | 38.85 | 38.85 | 38.85 | 38.85 | 38.85 | 38.85 | 38.85 | 38.85 | 55% | 311.6074 | 28.1354 | 36.4477 | 38.6243 | 38.4949 | 38.5058 | 38.7299 | 39.3198 | 39.7153 | 40.1022 | 40.5546 | 40.9742 | 41.3812 | 41.4284 | 41.9033 | 41.5446 | 41.5446 | 41.5446 | 41.5446 | 41.5446 | 41.5446 | 41.5446 | 41.5446 | 41.5446 | 41.5446 | 41.5446 | 41.5446 | 41.5446 | 41.5446 | 41.5446 | 41.5446
50% | 1666.1918 | 22.9379 | 30.4794 | 32.5337 | 32.4749 | 32.4742 | 32.7092 | 32.9669 | 33.4955 | 33.8752 | 34.0817 | 34.3078 | 34.5145 | 34.8872 | 35.3494 | 35.3182 | 35.3182 | 35.3182 | 35.3182 | 35.3182 | 35.3182 | 35.3182 | 35.3182 | 35.3182 | 35.3182 | 35.3182 | 35.3182 | 35.3182 | 35.3182 | 35.3182 | 35.3182 | 50% | 636.0723 | 25.5777 | 33.1343 | 35.113 | 34.9954 | 35.0052 | 35.209 | 35.7453 | 36.1049 | 36.4566 | 36.8678 | 37.2493 | 37.6193 | 37.6621 | 38.0939 | 37.7678 | 37.7678 | 37.7678 | 37.7678 | 37.7678 | 37.7678 | 37.7678 | 37.7678 | 37.7678 | 37.7678 | 37.7678 | 37.7678 | 37.7678 | 37.7678 | 37.7678 | 37.7678
45% | 2506.0947 | 20.6442 | 27.4315 | 29.2803 | 29.2274 | 29.2268 | 29.4383 | 29.6702 | 30.1459 | 30.4877 | 30.6735 | 30.8771 | 31.0631 | 31.3984 | 31.8145 | 31.7864 | 31.7864 | 31.7864 | 31.7864 | 31.7864 | 31.7864 | 31.7864 | 31.7864 | 31.7864 | 31.7864 | 31.7864 | 31.7864 | 31.7864 | 31.7864 | 31.7864 | 31.7864 | 45% | 1179.4944 | 23.0199 | 29.8209 | 31.6017 | 31.4958 | 31.5047 | 31.6881 | 32.1707 | 32.4944 | 32.8109 | 33.181 | 33.5243 | 33.8573 | 33.8959 | 34.2845 | 33.991 | 33.991 | 33.991 | 33.991 | 33.991 | 33.991 | 33.991 | 33.991 | 33.991 | 33.991 | 33.991 | 33.991 | 33.991 | 33.991 | 33.991 | 33.991
40% | 3164.4787 | 18.3504 | 24.3836 | 26.027 | 25.9799 | 25.9794 | 26.1673 | 26.3735 | 26.7964 | 27.1002 | 27.2653 | 27.4463 | 27.6116 | 27.9097 | 28.2795 | 28.2546 | 28.2546 | 28.2546 | 28.2546 | 28.2546 | 28.2546 | 28.2546 | 28.2546 | 28.2546 | 28.2546 | 28.2546 | 28.2546 | 28.2546 | 28.2546 | 28.2546 | 28.2546 | 40% | 1808.3816 | 20.4621 | 26.5075 | 28.0904 | 27.9963 | 28.0042 | 28.1672 | 28.5962 | 28.8839 | 29.1653 | 29.4942 | 29.7994 | 30.0954 | 30.1297 | 30.4751 | 30.2143 | 30.2143 | 30.2143 | 30.2143 | 30.2143 | 30.2143 | 30.2143 | 30.2143 | 30.2143 | 30.2143 | 30.2143 | 30.2143 | 30.2143 | 30.2143 | 30.2143 | 30.2143
35% | 3551.3408 | 16.0566 | 21.3356 | 22.7736 | 22.7325 | 22.732 | 22.8964 | 23.0768 | 23.4468 | 23.7126 | 23.8572 | 24.0155 | 24.1602 | 24.421 | 24.7446 | 24.7227 | 24.7227 | 24.7227 | 24.7227 | 24.7227 | 24.7227 | 24.7227 | 24.7227 | 24.7227 | 24.7227 | 24.7227 | 24.7227 | 24.7227 | 24.7227 | 24.7227 | 24.7227 | 35% | 2779.1293 | 17.9044 | 23.194 | 24.5791 | 24.4968 | 24.5037 | 24.6463 | 25.0217 | 25.2734 | 25.5196 | 25.8075 | 26.0745 | 26.3335 | 26.3635 | 26.6657 | 26.4375 | 26.4375 | 26.4375 | 26.4375 | 26.4375 | 26.4375 | 26.4375 | 26.4375 | 26.4375 | 26.4375 | 26.4375 | 26.4375 | 26.4375 | 26.4375 | 26.4375 | 26.4375
30% | 3758.953 | 13.7628 | 18.2877 | 19.5202 | 19.485 | 19.4845 | 19.6255 | 19.7801 | 20.0973 | 20.3251 | 20.449 | 20.5847 | 20.7087 | 20.9323 | 21.2097 | 21.1909 | 21.1909 | 21.1909 | 21.1909 | 21.1909 | 21.1909 | 21.1909 | 21.1909 | 21.1909 | 21.1909 | 21.1909 | 21.1909 | 21.1909 | 21.1909 | 21.1909 | 21.1909 | 30% | 3814.165 | 15.3466 | 19.8806 | 21.0678 | 20.9972 | 21.0031 | 21.1254 | 21.4472 | 21.6629 | 21.8739 | 22.1207 | 22.3496 | 22.5716 | 22.5973 | 22.8563 | 22.6607 | 22.6607 | 22.6607 | 22.6607 | 22.6607 | 22.6607 | 22.6607 | 22.6607 | 22.6607 | 22.6607 | 22.6607 | 22.6607 | 22.6607 | 22.6607 | 22.6607 | 22.6607
25% | 3926.4798 | 11.469 | 15.2397 | 16.2669 | 16.2375 | 16.2371 | 16.3546 | 16.4835 | 16.7477 | 16.9376 | 17.0408 | 17.1539 | 17.2573 | 17.4436 | 17.6747 | 17.6591 | 17.6591 | 17.6591 | 17.6591 | 17.6591 | 17.6591 | 17.6591 | 17.6591 | 17.6591 | 17.6591 | 17.6591 | 17.6591 | 17.6591 | 17.6591 | 17.6591 | 17.6591 | 25% | 4166.9923 | 12.7888 | 16.5672 | 17.5565 | 17.4977 | 17.5026 | 17.6045 | 17.8726 | 18.0524 | 18.2283 | 18.4339 | 18.6246 | 18.8096 | 18.8311 | 19.0469 | 18.8839 | 18.8839 | 18.8839 | 18.8839 | 18.8839 | 18.8839 | 18.8839 | 18.8839 | 18.8839 | 18.8839 | 18.8839 | 18.8839 | 18.8839 | 18.8839 | 18.8839 | 18.8839
20% | 4050.5177 | 9.1752 | 12.1918 | 13.0135 | 12.99 | 12.9897 | 13.0837 | 13.1868 | 13.3982 | 13.5501 | 13.6327 | 13.7231 | 13.8058 | 13.9549 | 14.1398 | 14.1273 | 14.1273 | 14.1273 | 14.1273 | 14.1273 | 14.1273 | 14.1273 | 14.1273 | 14.1273 | 14.1273 | 14.1273 | 14.1273 | 14.1273 | 14.1273 | 14.1273 | 14.1273 | 20% | 4282.7105 | 10.2311 | 13.2537 | 14.0452 | 13.9981 | 14.0021 | 14.0836 | 14.2981 | 14.4419 | 14.5826 | 14.7471 | 14.8997 | 15.0477 | 15.0649 | 15.2376 | 15.1071 | 15.1071 | 15.1071 | 15.1071 | 15.1071 | 15.1071 | 15.1071 | 15.1071 | 15.1071 | 15.1071 | 15.1071 | 15.1071 | 15.1071 | 15.1071 | 15.1071 | 15.1071
15% | 4152.622 | 6.8814 | 9.1438 | 9.7601 | 9.7425 | 9.7423 | 9.8128 | 9.8901 | 10.0486 | 10.1626 | 10.2245 | 10.2924 | 10.3544 | 10.4661 | 10.6048 | 10.5955 | 10.5955 | 10.5955 | 10.5955 | 10.5955 | 10.5955 | 10.5955 | 10.5955 | 10.5955 | 10.5955 | 10.5955 | 10.5955 | 10.5955 | 10.5955 | 10.5955 | 10.5955 | 15% | 4364.7722 | 7.6733 | 9.9403 | 10.5339 | 10.4986 | 10.5016 | 10.5627 | 10.7236 | 10.8315 | 10.937 | 11.0603 | 11.1748 | 11.2858 | 11.2986 | 11.4282 | 11.3303 | 11.3303 | 11.3303 | 11.3303 | 11.3303 | 11.3303 | 11.3303 | 11.3303 | 11.3303 | 11.3303 | 11.3303 | 11.3303 | 11.3303 | 11.3303 | 11.3303 | 11.3303
10% | 4248.2976 | 4.5876 | 6.0959 | 6.5067 | 6.495 | 6.4948 | 6.5418 | 6.5934 | 6.6991 | 6.775 | 6.8163 | 6.8616 | 6.9029 | 6.9774 | 7.0699 | 7.0636 | 7.0636 | 7.0636 | 7.0636 | 7.0636 | 7.0636 | 7.0636 | 7.0636 | 7.0636 | 7.0636 | 7.0636 | 7.0636 | 7.0636 | 7.0636 | 7.0636 | 7.0636 | 10% | 4391.6218 | 5.1155 | 6.6269 | 7.0226 | 6.9991 | 7.001 | 7.0418 | 7.1491 | 7.221 | 7.2913 | 7.3736 | 7.4499 | 7.5239 | 7.5324 | 7.6188 | 7.5536 | 7.5536 | 7.5536 | 7.5536 | 7.5536 | 7.5536 | 7.5536 | 7.5536 | 7.5536 | 7.5536 | 7.5536 | 7.5536 | 7.5536 | 7.5536 | 7.5536 | 7.5536
5% | 4361.7469 | 2.2938 | 3.0479 | 3.2534 | 3.2475 | 3.2474 | 3.2709 | 3.2967 | 3.3495 | 3.3875 | 3.4082 | 3.4308 | 3.4515 | 3.4887 | 3.5349 | 3.5318 | 3.5318 | 3.5318 | 3.5318 | 3.5318 | 3.5318 | 3.5318 | 3.5318 | 3.5318 | 3.5318 | 3.5318 | 3.5318 | 3.5318 | 3.5318 | 3.5318 | 3.5318 | 5% | 4391.6218 | 2.5578 | 3.3134 | 3.5113 | 3.4995 | 3.5005 | 3.5209 | 3.5745 | 3.6105 | 3.6457 | 3.6868 | 3.7249 | 3.7619 | 3.7662 | 3.8094 | 3.7768 | 3.7768 | 3.7768 | 3.7768 | 3.7768 | 3.7768 | 3.7768 | 3.7768 | 3.7768 | 3.7768 | 3.7768 | 3.7768 | 3.7768 | 3.7768 | 3.7768 | 3.7768
9.992e-14% | 4391.6218 | 4.5839e-14 | 6.091e-14 | 6.5015e-14 | 6.4898e-14 | 6.4897e-14 | 6.5366e-14 | 6.5881e-14 | 6.6937e-14 | 6.7696e-14 | 6.8109e-14 | 6.8561e-14 | 6.8974e-14 | 6.9719e-14 | 7.0642e-14 | 7.058e-14 | 7.058e-14 | 7.058e-14 | 7.058e-14 | 7.058e-14 | 7.058e-14 | 7.058e-14 | 7.058e-14 | 7.058e-14 | 7.058e-14 | 7.058e-14 | 7.058e-14 | 7.058e-14 | 7.058e-14 | 7.058e-14 | 7.058e-14 | 9.992e-14% | 4391.6218 | 5.1114e-14 | 6.6216e-14 | 7.017e-14 | 6.9935e-14 | 6.9955e-14 | 7.0362e-14 | 7.1433e-14 | 7.2152e-14 | 7.2855e-14 | 7.3677e-14 | 7.4439e-14 | 7.5178e-14 | 7.5264e-14 | 7.6127e-14 | 7.5475e-14 | 7.5475e-14 | 7.5475e-14 | 7.5475e-14 | 7.5475e-14 | 7.5475e-14 | 7.5475e-14 | 7.5475e-14 | 7.5475e-14 | 7.5475e-14 | 7.5475e-14 | 7.5475e-14 | 7.5475e-14 | 7.5475e-14 | 7.5475e-14 | 7.5475e-14
Option 2
Winter Season | [31 empty] | Winter Season
P50 | [31 empty] | P10
% of MD | Winter - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Winter - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 40.358 | 56.0239 | 60.0964 | 31.7906 | 32.3321 | 33.2643 | 35.3852 | 36.8049 | 38.6034 | 39.5369 | 40.3582 | 38.845 | 40.6185 | 43.4066 | 41.2908 | 41.2908 | 41.2908 | 41.2908 | 41.2908 | 41.2908 | 41.2908 | 41.2908 | 41.2908 | 41.2908 | 41.2908 | 41.2908 | 41.2908 | 41.2908 | 41.2908 | 41.2908 | 100% | 0 | 43.208 | 58.6763 | 62.9078 | 34.5625 | 34.9783 | 35.8903 | 38.0443 | 39.2204 | 41.4608 | 48.2709 | 42.6566 | 41.5585 | 43.0408 | 46.2827 | 44.0883 | 44.0883 | 44.0883 | 44.0883 | 44.0883 | 44.0883 | 44.0883 | 44.0883 | 44.0883 | 44.0883 | 44.0883 | 44.0883 | 44.0883 | 44.0883 | 44.0883 | 44.0883
99% | 1.486 | 39.9544 | 55.4636 | 59.4955 | 31.4727 | 32.0087 | 32.9316 | 35.0313 | 36.4368 | 38.2174 | 39.1416 | 39.9546 | 38.4565 | 40.2123 | 42.9725 | 40.8779 | 40.8779 | 40.8779 | 40.8779 | 40.8779 | 40.8779 | 40.8779 | 40.8779 | 40.8779 | 40.8779 | 40.8779 | 40.8779 | 40.8779 | 40.8779 | 40.8779 | 40.8779 | 99% | 1.486 | 42.7759 | 58.0895 | 62.2787 | 34.2169 | 34.6285 | 35.5314 | 37.6639 | 38.8282 | 41.0462 | 47.7882 | 42.2301 | 41.1429 | 42.6104 | 45.8199 | 43.6475 | 43.6475 | 43.6475 | 43.6475 | 43.6475 | 43.6475 | 43.6475 | 43.6475 | 43.6475 | 43.6475 | 43.6475 | 43.6475 | 43.6475 | 43.6475 | 43.6475 | 43.6475
98% | 3.2692 | 39.5508 | 54.9034 | 58.8945 | 31.1548 | 31.6854 | 32.599 | 34.6775 | 36.0688 | 37.8313 | 38.7462 | 39.5511 | 38.0681 | 39.8061 | 42.5384 | 40.465 | 40.465 | 40.465 | 40.465 | 40.465 | 40.465 | 40.465 | 40.465 | 40.465 | 40.465 | 40.465 | 40.465 | 40.465 | 40.465 | 40.465 | 40.465 | 98% | 3.2692 | 42.3438 | 57.5027 | 61.6497 | 33.8713 | 34.2787 | 35.1725 | 37.2834 | 38.436 | 40.6316 | 47.3055 | 41.8035 | 40.7273 | 42.18 | 45.3571 | 43.2066 | 43.2066 | 43.2066 | 43.2066 | 43.2066 | 43.2066 | 43.2066 | 43.2066 | 43.2066 | 43.2066 | 43.2066 | 43.2066 | 43.2066 | 43.2066 | 43.2066 | 43.2066
97% | 6.8356 | 39.1473 | 54.3431 | 58.2935 | 30.8369 | 31.3621 | 32.2664 | 34.3236 | 35.7007 | 37.4453 | 38.3508 | 39.1475 | 37.6796 | 39.3999 | 42.1044 | 40.0521 | 40.0521 | 40.0521 | 40.0521 | 40.0521 | 40.0521 | 40.0521 | 40.0521 | 40.0521 | 40.0521 | 40.0521 | 40.0521 | 40.0521 | 40.0521 | 40.0521 | 40.0521 | 97% | 6.8356 | 41.9118 | 56.916 | 61.0206 | 33.5257 | 33.9289 | 34.8136 | 36.903 | 38.0438 | 40.2169 | 46.8228 | 41.3769 | 40.3117 | 41.7496 | 44.8943 | 42.7657 | 42.7657 | 42.7657 | 42.7657 | 42.7657 | 42.7657 | 42.7657 | 42.7657 | 42.7657 | 42.7657 | 42.7657 | 42.7657 | 42.7657 | 42.7657 | 42.7657 | 42.7657
95% | 17.5347 | 38.3401 | 53.2227 | 57.0916 | 30.2011 | 30.7155 | 31.6011 | 33.6159 | 34.9646 | 36.6732 | 37.5601 | 38.3403 | 36.9027 | 38.5875 | 41.2362 | 39.2262 | 39.2262 | 39.2262 | 39.2262 | 39.2262 | 39.2262 | 39.2262 | 39.2262 | 39.2262 | 39.2262 | 39.2262 | 39.2262 | 39.2262 | 39.2262 | 39.2262 | 39.2262 | 95% | 17.5347 | 41.0476 | 55.7425 | 59.7624 | 32.8344 | 33.2294 | 34.0958 | 36.1421 | 37.2594 | 39.3877 | 45.8573 | 40.5238 | 39.4806 | 40.8888 | 43.9686 | 41.8839 | 41.8839 | 41.8839 | 41.8839 | 41.8839 | 41.8839 | 41.8839 | 41.8839 | 41.8839 | 41.8839 | 41.8839 | 41.8839 | 41.8839 | 41.8839 | 41.8839 | 41.8839
90% | 78.7576 | 36.3222 | 50.4215 | 54.0868 | 28.6116 | 29.0988 | 29.9379 | 31.8467 | 33.1244 | 34.7431 | 35.5833 | 36.3224 | 34.9605 | 36.5566 | 39.0659 | 37.1617 | 37.1617 | 37.1617 | 37.1617 | 37.1617 | 37.1617 | 37.1617 | 37.1617 | 37.1617 | 37.1617 | 37.1617 | 37.1617 | 37.1617 | 37.1617 | 37.1617 | 37.1617 | 90% | 78.7576 | 38.8872 | 52.8086 | 56.617 | 31.1063 | 31.4804 | 32.3013 | 34.2399 | 35.2984 | 37.3147 | 43.4438 | 38.391 | 37.4026 | 38.7368 | 41.6545 | 39.6795 | 39.6795 | 39.6795 | 39.6795 | 39.6795 | 39.6795 | 39.6795 | 39.6795 | 39.6795 | 39.6795 | 39.6795 | 39.6795 | 39.6795 | 39.6795 | 39.6795 | 39.6795
85% | 236.8672 | 34.3043 | 47.6203 | 51.082 | 27.022 | 27.4822 | 28.2746 | 30.0774 | 31.2842 | 32.8129 | 33.6064 | 34.3045 | 33.0182 | 34.5257 | 36.8956 | 35.0972 | 35.0972 | 35.0972 | 35.0972 | 35.0972 | 35.0972 | 35.0972 | 35.0972 | 35.0972 | 35.0972 | 35.0972 | 35.0972 | 35.0972 | 35.0972 | 35.0972 | 35.0972 | 85% | 236.8672 | 36.7268 | 49.8748 | 53.4716 | 29.3782 | 29.7315 | 30.5067 | 32.3377 | 33.3373 | 35.2417 | 41.0303 | 36.2581 | 35.3247 | 36.5847 | 39.3403 | 37.4751 | 37.4751 | 37.4751 | 37.4751 | 37.4751 | 37.4751 | 37.4751 | 37.4751 | 37.4751 | 37.4751 | 37.4751 | 37.4751 | 37.4751 | 37.4751 | 37.4751 | 37.4751
80% | 497.5104 | 32.2864 | 44.8191 | 48.0771 | 25.4325 | 25.8656 | 26.6114 | 28.3081 | 29.4439 | 30.8827 | 31.6296 | 32.2866 | 31.076 | 32.4948 | 34.7252 | 33.0326 | 33.0326 | 33.0326 | 33.0326 | 33.0326 | 33.0326 | 33.0326 | 33.0326 | 33.0326 | 33.0326 | 33.0326 | 33.0326 | 33.0326 | 33.0326 | 33.0326 | 33.0326 | 80% | 497.5104 | 34.5664 | 46.941 | 50.3262 | 27.65 | 27.9826 | 28.7122 | 30.4355 | 31.3763 | 33.1686 | 38.6167 | 34.1253 | 33.2468 | 34.4327 | 37.0262 | 35.2707 | 35.2707 | 35.2707 | 35.2707 | 35.2707 | 35.2707 | 35.2707 | 35.2707 | 35.2707 | 35.2707 | 35.2707 | 35.2707 | 35.2707 | 35.2707 | 35.2707 | 35.2707
75% | 803.6248 | 30.2685 | 42.0179 | 45.0723 | 23.843 | 24.249 | 24.9482 | 26.5389 | 27.6037 | 28.9526 | 29.6527 | 30.2687 | 29.1337 | 30.4638 | 32.5549 | 30.9681 | 30.9681 | 30.9681 | 30.9681 | 30.9681 | 30.9681 | 30.9681 | 30.9681 | 30.9681 | 30.9681 | 30.9681 | 30.9681 | 30.9681 | 30.9681 | 30.9681 | 30.9681 | 75% | 803.6248 | 32.406 | 44.0072 | 47.1809 | 25.9219 | 26.2337 | 26.9177 | 28.5332 | 29.4153 | 31.0956 | 36.2032 | 31.9925 | 31.1689 | 32.2806 | 34.7121 | 33.0663 | 33.0663 | 33.0663 | 33.0663 | 33.0663 | 33.0663 | 33.0663 | 33.0663 | 33.0663 | 33.0663 | 33.0663 | 33.0663 | 33.0663 | 33.0663 | 33.0663 | 33.0663
70% | 1155.2107 | 28.2506 | 39.2167 | 42.0675 | 22.2534 | 22.6324 | 23.285 | 24.7696 | 25.7634 | 27.0224 | 27.6759 | 28.2508 | 27.1915 | 28.4329 | 30.3846 | 28.9035 | 28.9035 | 28.9035 | 28.9035 | 28.9035 | 28.9035 | 28.9035 | 28.9035 | 28.9035 | 28.9035 | 28.9035 | 28.9035 | 28.9035 | 28.9035 | 28.9035 | 28.9035 | 70% | 1155.2107 | 30.2456 | 41.0734 | 44.0355 | 24.1938 | 24.4848 | 25.1232 | 26.631 | 27.4543 | 29.0225 | 33.7896 | 29.8596 | 29.0909 | 30.1286 | 32.3979 | 30.8618 | 30.8618 | 30.8618 | 30.8618 | 30.8618 | 30.8618 | 30.8618 | 30.8618 | 30.8618 | 30.8618 | 30.8618 | 30.8618 | 30.8618 | 30.8618 | 30.8618 | 30.8618
65% | 1553.1596 | 26.2327 | 36.4155 | 39.0627 | 20.6639 | 21.0158 | 21.6218 | 23.0004 | 23.9232 | 25.0922 | 25.699 | 26.2328 | 25.2492 | 26.402 | 28.2143 | 26.839 | 26.839 | 26.839 | 26.839 | 26.839 | 26.839 | 26.839 | 26.839 | 26.839 | 26.839 | 26.839 | 26.839 | 26.839 | 26.839 | 26.839 | 26.839 | 65% | 1553.1596 | 28.0852 | 38.1396 | 40.8901 | 22.4657 | 22.7359 | 23.3287 | 24.7288 | 25.4933 | 26.9495 | 31.3761 | 27.7268 | 27.013 | 27.9766 | 30.0838 | 28.6574 | 28.6574 | 28.6574 | 28.6574 | 28.6574 | 28.6574 | 28.6574 | 28.6574 | 28.6574 | 28.6574 | 28.6574 | 28.6574 | 28.6574 | 28.6574 | 28.6574 | 28.6574
60% | 2026.2996 | 24.2148 | 33.6143 | 36.0579 | 19.0744 | 19.3992 | 19.9586 | 21.2311 | 22.0829 | 23.162 | 23.7222 | 24.2149 | 23.307 | 24.3711 | 26.0439 | 24.7745 | 24.7745 | 24.7745 | 24.7745 | 24.7745 | 24.7745 | 24.7745 | 24.7745 | 24.7745 | 24.7745 | 24.7745 | 24.7745 | 24.7745 | 24.7745 | 24.7745 | 24.7745 | 60% | 2026.2996 | 25.9248 | 35.2058 | 37.7447 | 20.7375 | 20.987 | 21.5342 | 22.8266 | 23.5322 | 24.8765 | 28.9625 | 25.594 | 24.9351 | 25.8245 | 27.7696 | 26.453 | 26.453 | 26.453 | 26.453 | 26.453 | 26.453 | 26.453 | 26.453 | 26.453 | 26.453 | 26.453 | 26.453 | 26.453 | 26.453 | 26.453 | 26.453
55% | 2598.4068 | 22.1969 | 30.8131 | 33.053 | 17.4848 | 17.7826 | 18.2954 | 19.4619 | 20.2427 | 21.2319 | 21.7453 | 22.197 | 21.3647 | 22.3402 | 23.8736 | 22.7099 | 22.7099 | 22.7099 | 22.7099 | 22.7099 | 22.7099 | 22.7099 | 22.7099 | 22.7099 | 22.7099 | 22.7099 | 22.7099 | 22.7099 | 22.7099 | 22.7099 | 22.7099 | 55% | 2598.4068 | 23.7644 | 32.272 | 34.5993 | 19.0094 | 19.238 | 19.7397 | 20.9244 | 21.5712 | 22.8034 | 26.549 | 23.4611 | 22.8572 | 23.6725 | 25.4555 | 24.2486 | 24.2486 | 24.2486 | 24.2486 | 24.2486 | 24.2486 | 24.2486 | 24.2486 | 24.2486 | 24.2486 | 24.2486 | 24.2486 | 24.2486 | 24.2486 | 24.2486 | 24.2486
50% | 3233.5201 | 20.179 | 28.0119 | 30.0482 | 15.8953 | 16.166 | 16.6321 | 17.6926 | 18.4024 | 19.3017 | 19.7685 | 20.1791 | 19.4225 | 20.3092 | 21.7033 | 20.6454 | 20.6454 | 20.6454 | 20.6454 | 20.6454 | 20.6454 | 20.6454 | 20.6454 | 20.6454 | 20.6454 | 20.6454 | 20.6454 | 20.6454 | 20.6454 | 20.6454 | 20.6454 | 50% | 3233.5201 | 21.604 | 29.3381 | 31.4539 | 17.2813 | 17.4891 | 17.9451 | 19.0222 | 19.6102 | 20.7304 | 24.1354 | 21.3283 | 20.7792 | 21.5204 | 23.1414 | 22.0442 | 22.0442 | 22.0442 | 22.0442 | 22.0442 | 22.0442 | 22.0442 | 22.0442 | 22.0442 | 22.0442 | 22.0442 | 22.0442 | 22.0442 | 22.0442 | 22.0442 | 22.0442
45% | 3775.313 | 18.1611 | 25.2107 | 27.0434 | 14.3058 | 14.5494 | 14.9689 | 15.9233 | 16.5622 | 17.3715 | 17.7916 | 18.1612 | 17.4802 | 18.2783 | 19.533 | 18.5809 | 18.5809 | 18.5809 | 18.5809 | 18.5809 | 18.5809 | 18.5809 | 18.5809 | 18.5809 | 18.5809 | 18.5809 | 18.5809 | 18.5809 | 18.5809 | 18.5809 | 18.5809 | 45% | 3775.313 | 19.4436 | 26.4043 | 28.3085 | 15.5531 | 15.7402 | 16.1506 | 17.1199 | 17.6492 | 18.6573 | 21.7219 | 19.1955 | 18.7013 | 19.3684 | 20.8272 | 19.8398 | 19.8398 | 19.8398 | 19.8398 | 19.8398 | 19.8398 | 19.8398 | 19.8398 | 19.8398 | 19.8398 | 19.8398 | 19.8398 | 19.8398 | 19.8398 | 19.8398 | 19.8398
40% | 4072.8088 | 16.1432 | 22.4095 | 24.0386 | 12.7162 | 12.9328 | 13.3057 | 14.1541 | 14.722 | 15.4414 | 15.8148 | 16.1433 | 15.538 | 16.2474 | 17.3626 | 16.5163 | 16.5163 | 16.5163 | 16.5163 | 16.5163 | 16.5163 | 16.5163 | 16.5163 | 16.5163 | 16.5163 | 16.5163 | 16.5163 | 16.5163 | 16.5163 | 16.5163 | 16.5163 | 40% | 4072.8088 | 17.2832 | 23.4705 | 25.1631 | 13.825 | 13.9913 | 14.3561 | 15.2177 | 15.6882 | 16.5843 | 19.3084 | 17.0627 | 16.6234 | 17.2163 | 18.5131 | 17.6353 | 17.6353 | 17.6353 | 17.6353 | 17.6353 | 17.6353 | 17.6353 | 17.6353 | 17.6353 | 17.6353 | 17.6353 | 17.6353 | 17.6353 | 17.6353 | 17.6353 | 17.6353
35% | 4198.821 | 14.1253 | 19.6083 | 21.0337 | 11.1267 | 11.3162 | 11.6425 | 12.3848 | 12.8817 | 13.5112 | 13.8379 | 14.1254 | 13.5957 | 14.2165 | 15.1923 | 14.4518 | 14.4518 | 14.4518 | 14.4518 | 14.4518 | 14.4518 | 14.4518 | 14.4518 | 14.4518 | 14.4518 | 14.4518 | 14.4518 | 14.4518 | 14.4518 | 14.4518 | 14.4518 | 35% | 4198.821 | 15.1228 | 20.5367 | 22.0177 | 12.0969 | 12.2424 | 12.5616 | 13.3155 | 13.7271 | 14.5113 | 16.8948 | 14.9298 | 14.5455 | 15.0643 | 16.199 | 15.4309 | 15.4309 | 15.4309 | 15.4309 | 15.4309 | 15.4309 | 15.4309 | 15.4309 | 15.4309 | 15.4309 | 15.4309 | 15.4309 | 15.4309 | 15.4309 | 15.4309 | 15.4309
30% | 4271.3374 | 12.1074 | 16.8072 | 18.0289 | 9.5372 | 9.6996 | 9.9793 | 10.6156 | 11.0415 | 11.581 | 11.8611 | 12.1075 | 11.6535 | 12.1855 | 13.022 | 12.3872 | 12.3872 | 12.3872 | 12.3872 | 12.3872 | 12.3872 | 12.3872 | 12.3872 | 12.3872 | 12.3872 | 12.3872 | 12.3872 | 12.3872 | 12.3872 | 12.3872 | 12.3872 | 30% | 4271.3374 | 12.9624 | 17.6029 | 18.8723 | 10.3688 | 10.4935 | 10.7671 | 11.4133 | 11.7661 | 12.4382 | 14.4813 | 12.797 | 12.4675 | 12.9123 | 13.8848 | 13.2265 | 13.2265 | 13.2265 | 13.2265 | 13.2265 | 13.2265 | 13.2265 | 13.2265 | 13.2265 | 13.2265 | 13.2265 | 13.2265 | 13.2265 | 13.2265 | 13.2265 | 13.2265
25% | 4321.8611 | 10.0895 | 14.006 | 15.0241 | 7.9477 | 8.083 | 8.3161 | 8.8463 | 9.2012 | 9.6509 | 9.8842 | 10.0896 | 9.7112 | 10.1546 | 10.8516 | 10.3227 | 10.3227 | 10.3227 | 10.3227 | 10.3227 | 10.3227 | 10.3227 | 10.3227 | 10.3227 | 10.3227 | 10.3227 | 10.3227 | 10.3227 | 10.3227 | 10.3227 | 10.3227 | 25% | 4321.8611 | 10.802 | 14.6691 | 15.727 | 8.6406 | 8.7446 | 8.9726 | 9.5111 | 9.8051 | 10.3652 | 12.0677 | 10.6642 | 10.3896 | 10.7602 | 11.5707 | 11.0221 | 11.0221 | 11.0221 | 11.0221 | 11.0221 | 11.0221 | 11.0221 | 11.0221 | 11.0221 | 11.0221 | 11.0221 | 11.0221 | 11.0221 | 11.0221 | 11.0221 | 11.0221
20% | 4353.067 | 8.0716 | 11.2048 | 12.0193 | 6.3581 | 6.4664 | 6.6529 | 7.077 | 7.361 | 7.7207 | 7.9074 | 8.0716 | 7.769 | 8.1237 | 8.6813 | 8.2582 | 8.2582 | 8.2582 | 8.2582 | 8.2582 | 8.2582 | 8.2582 | 8.2582 | 8.2582 | 8.2582 | 8.2582 | 8.2582 | 8.2582 | 8.2582 | 8.2582 | 8.2582 | 20% | 4353.067 | 8.6416 | 11.7353 | 12.5816 | 6.9125 | 6.9957 | 7.1781 | 7.6089 | 7.8441 | 8.2922 | 9.6542 | 8.5313 | 8.3117 | 8.6082 | 9.2565 | 8.8177 | 8.8177 | 8.8177 | 8.8177 | 8.8177 | 8.8177 | 8.8177 | 8.8177 | 8.8177 | 8.8177 | 8.8177 | 8.8177 | 8.8177 | 8.8177 | 8.8177 | 8.8177
15% | 4369.4129 | 6.0537 | 8.4036 | 9.0145 | 4.7686 | 4.8498 | 4.9896 | 5.3078 | 5.5207 | 5.7905 | 5.9305 | 6.0537 | 5.8267 | 6.0928 | 6.511 | 6.1936 | 6.1936 | 6.1936 | 6.1936 | 6.1936 | 6.1936 | 6.1936 | 6.1936 | 6.1936 | 6.1936 | 6.1936 | 6.1936 | 6.1936 | 6.1936 | 6.1936 | 6.1936 | 15% | 4369.4129 | 6.4812 | 8.8014 | 9.4362 | 5.1844 | 5.2467 | 5.3835 | 5.7066 | 5.8831 | 6.2191 | 7.2406 | 6.3985 | 6.2338 | 6.4561 | 6.9424 | 6.6133 | 6.6133 | 6.6133 | 6.6133 | 6.6133 | 6.6133 | 6.6133 | 6.6133 | 6.6133 | 6.6133 | 6.6133 | 6.6133 | 6.6133 | 6.6133 | 6.6133 | 6.6133
10% | 4378.6261 | 4.0358 | 5.6024 | 6.0096 | 3.1791 | 3.2332 | 3.3264 | 3.5385 | 3.6805 | 3.8603 | 3.9537 | 4.0358 | 3.8845 | 4.0618 | 4.3407 | 4.1291 | 4.1291 | 4.1291 | 4.1291 | 4.1291 | 4.1291 | 4.1291 | 4.1291 | 4.1291 | 4.1291 | 4.1291 | 4.1291 | 4.1291 | 4.1291 | 4.1291 | 4.1291 | 10% | 4378.6261 | 4.3208 | 5.8676 | 6.2908 | 3.4563 | 3.4978 | 3.589 | 3.8044 | 3.922 | 4.1461 | 4.8271 | 4.2657 | 4.1558 | 4.3041 | 4.6283 | 4.4088 | 4.4088 | 4.4088 | 4.4088 | 4.4088 | 4.4088 | 4.4088 | 4.4088 | 4.4088 | 4.4088 | 4.4088 | 4.4088 | 4.4088 | 4.4088 | 4.4088 | 4.4088
5% | 4391.7028 | 2.0179 | 2.8012 | 3.0048 | 1.5895 | 1.6166 | 1.6632 | 1.7693 | 1.8402 | 1.9302 | 1.9768 | 2.0179 | 1.9422 | 2.0309 | 2.1703 | 2.0645 | 2.0645 | 2.0645 | 2.0645 | 2.0645 | 2.0645 | 2.0645 | 2.0645 | 2.0645 | 2.0645 | 2.0645 | 2.0645 | 2.0645 | 2.0645 | 2.0645 | 2.0645 | 5% | 4391.7028 | 2.1604 | 2.9338 | 3.1454 | 1.7281 | 1.7489 | 1.7945 | 1.9022 | 1.961 | 2.073 | 2.4135 | 2.1328 | 2.0779 | 2.152 | 2.3141 | 2.2044 | 2.2044 | 2.2044 | 2.2044 | 2.2044 | 2.2044 | 2.2044 | 2.2044 | 2.2044 | 2.2044 | 2.2044 | 2.2044 | 2.2044 | 2.2044 | 2.2044 | 2.2044
9.992e-14% | 4391.7028 | 4.0326e-14 | 5.5979e-14 | 6.0048e-14 | 3.1765e-14 | 3.2306e-14 | 3.3238e-14 | 3.5357e-14 | 3.6775e-14 | 3.8573e-14 | 3.9505e-14 | 4.0326e-14 | 3.8814e-14 | 4.0586e-14 | 4.3372e-14 | 4.1258e-14 | 4.1258e-14 | 4.1258e-14 | 4.1258e-14 | 4.1258e-14 | 4.1258e-14 | 4.1258e-14 | 4.1258e-14 | 4.1258e-14 | 4.1258e-14 | 4.1258e-14 | 4.1258e-14 | 4.1258e-14 | 4.1258e-14 | 4.1258e-14 | 4.1258e-14 | 9.992e-14% | 4391.7028 | 4.3173e-14 | 5.8629e-14 | 6.2858e-14 | 3.4535e-14 | 3.495e-14 | 3.5862e-14 | 3.8014e-14 | 3.9189e-14 | 4.1428e-14 | 4.8232e-14 | 4.2623e-14 | 4.1525e-14 | 4.3006e-14 | 4.6246e-14 | 4.4053e-14 | 4.4053e-14 | 4.4053e-14 | 4.4053e-14 | 4.4053e-14 | 4.4053e-14 | 4.4053e-14 | 4.4053e-14 | 4.4053e-14 | 4.4053e-14 | 4.4053e-14 | 4.4053e-14 | 4.4053e-14 | 4.4053e-14 | 4.4053e-14 | 4.4053e-14
Summer Season | [31 empty] | Summer Season
P50 | [31 empty] | P10
% of MD | Summer - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Summer - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 45.8759 | 60.9589 | 65.0674 | 35.9499 | 35.9485 | 36.4184 | 36.9338 | 37.9909 | 38.7504 | 39.1633 | 39.6157 | 40.029 | 40.7743 | 41.6989 | 41.6364 | 41.6364 | 41.6364 | 41.6364 | 41.6364 | 41.6364 | 41.6364 | 41.6364 | 41.6364 | 41.6364 | 41.6364 | 41.6364 | 41.6364 | 41.6364 | 41.6364 | 41.6364 | 100% | 0 | 51.1554 | 66.2686 | 70.2261 | 40.9907 | 41.0105 | 41.4179 | 42.4905 | 43.2097 | 43.9132 | 44.7356 | 45.4985 | 46.2386 | 46.3243 | 47.1878 | 46.5357 | 46.5357 | 46.5357 | 46.5357 | 46.5357 | 46.5357 | 46.5357 | 46.5357 | 46.5357 | 46.5357 | 46.5357 | 46.5357 | 46.5357 | 46.5357 | 46.5357 | 46.5357
99% | 0 | 45.4171 | 60.3493 | 64.4168 | 35.5904 | 35.589 | 36.0542 | 36.5645 | 37.611 | 38.3629 | 38.7717 | 39.2195 | 39.6287 | 40.3666 | 41.2819 | 41.22 | 41.22 | 41.22 | 41.22 | 41.22 | 41.22 | 41.22 | 41.22 | 41.22 | 41.22 | 41.22 | 41.22 | 41.22 | 41.22 | 41.22 | 41.22 | 99% | 1.5127 | 50.6438 | 65.6059 | 69.5238 | 40.5808 | 40.6004 | 41.0037 | 42.0656 | 42.7776 | 43.474 | 44.2883 | 45.0435 | 45.7762 | 45.861 | 46.7159 | 46.0703 | 46.0703 | 46.0703 | 46.0703 | 46.0703 | 46.0703 | 46.0703 | 46.0703 | 46.0703 | 46.0703 | 46.0703 | 46.0703 | 46.0703 | 46.0703 | 46.0703 | 46.0703
98% | 0 | 44.9584 | 59.7397 | 63.7661 | 35.2309 | 35.2295 | 35.69 | 36.1951 | 37.2311 | 37.9754 | 38.3801 | 38.8234 | 39.2284 | 39.9588 | 40.8649 | 40.8036 | 40.8036 | 40.8036 | 40.8036 | 40.8036 | 40.8036 | 40.8036 | 40.8036 | 40.8036 | 40.8036 | 40.8036 | 40.8036 | 40.8036 | 40.8036 | 40.8036 | 40.8036 | 98% | 2.269 | 50.1322 | 64.9433 | 68.8216 | 40.1709 | 40.1903 | 40.5896 | 41.6407 | 42.3455 | 43.0349 | 43.8409 | 44.5885 | 45.3138 | 45.3978 | 46.244 | 45.6049 | 45.6049 | 45.6049 | 45.6049 | 45.6049 | 45.6049 | 45.6049 | 45.6049 | 45.6049 | 45.6049 | 45.6049 | 45.6049 | 45.6049 | 45.6049 | 45.6049 | 45.6049
97% | 0.37816 | 44.4996 | 59.1301 | 63.1154 | 34.8714 | 34.87 | 35.3258 | 35.8258 | 36.8512 | 37.5879 | 37.9884 | 38.4272 | 38.8281 | 39.5511 | 40.4479 | 40.3873 | 40.3873 | 40.3873 | 40.3873 | 40.3873 | 40.3873 | 40.3873 | 40.3873 | 40.3873 | 40.3873 | 40.3873 | 40.3873 | 40.3873 | 40.3873 | 40.3873 | 40.3873 | 97% | 3.7816 | 49.6207 | 64.2806 | 68.1193 | 39.761 | 39.7802 | 40.1754 | 41.2158 | 41.9134 | 42.5958 | 43.3936 | 44.1336 | 44.8514 | 44.9346 | 45.7722 | 45.1396 | 45.1396 | 45.1396 | 45.1396 | 45.1396 | 45.1396 | 45.1396 | 45.1396 | 45.1396 | 45.1396 | 45.1396 | 45.1396 | 45.1396 | 45.1396 | 45.1396 | 45.1396
95% | 2.269 | 43.5821 | 57.911 | 61.8141 | 34.1524 | 34.151 | 34.5974 | 35.0871 | 36.0914 | 36.8129 | 37.2052 | 37.6349 | 38.0276 | 38.7356 | 39.6139 | 39.5546 | 39.5546 | 39.5546 | 39.5546 | 39.5546 | 39.5546 | 39.5546 | 39.5546 | 39.5546 | 39.5546 | 39.5546 | 39.5546 | 39.5546 | 39.5546 | 39.5546 | 39.5546 | 95% | 6.0506 | 48.5976 | 62.9552 | 66.7148 | 38.9412 | 38.96 | 39.347 | 40.366 | 41.0492 | 41.7175 | 42.4988 | 43.2236 | 43.9266 | 44.0081 | 44.8284 | 44.2089 | 44.2089 | 44.2089 | 44.2089 | 44.2089 | 44.2089 | 44.2089 | 44.2089 | 44.2089 | 44.2089 | 44.2089 | 44.2089 | 44.2089 | 44.2089 | 44.2089 | 44.2089
90% | 5.6725 | 41.2883 | 54.863 | 58.5607 | 32.3549 | 32.3536 | 32.7765 | 33.2404 | 34.1918 | 34.8754 | 35.247 | 35.6541 | 36.0261 | 36.6969 | 37.529 | 37.4727 | 37.4727 | 37.4727 | 37.4727 | 37.4727 | 37.4727 | 37.4727 | 37.4727 | 37.4727 | 37.4727 | 37.4727 | 37.4727 | 37.4727 | 37.4727 | 37.4727 | 37.4727 | 90% | 16.2611 | 46.0398 | 59.6418 | 63.2035 | 36.8917 | 36.9094 | 37.2761 | 38.2415 | 38.8887 | 39.5218 | 40.2621 | 40.9487 | 41.6147 | 41.6919 | 42.469 | 41.8821 | 41.8821 | 41.8821 | 41.8821 | 41.8821 | 41.8821 | 41.8821 | 41.8821 | 41.8821 | 41.8821 | 41.8821 | 41.8821 | 41.8821 | 41.8821 | 41.8821 | 41.8821
85% | 15.8829 | 38.9945 | 51.8151 | 55.3073 | 30.5574 | 30.5562 | 30.9556 | 31.3937 | 32.2923 | 32.9379 | 33.2888 | 33.6733 | 34.0247 | 34.6582 | 35.444 | 35.3909 | 35.3909 | 35.3909 | 35.3909 | 35.3909 | 35.3909 | 35.3909 | 35.3909 | 35.3909 | 35.3909 | 35.3909 | 35.3909 | 35.3909 | 35.3909 | 35.3909 | 35.3909 | 85% | 26.4715 | 43.482 | 56.3283 | 59.6922 | 34.8421 | 34.8589 | 35.2052 | 36.117 | 36.7283 | 37.3262 | 38.0253 | 38.6737 | 39.3028 | 39.3756 | 40.1096 | 39.5553 | 39.5553 | 39.5553 | 39.5553 | 39.5553 | 39.5553 | 39.5553 | 39.5553 | 39.5553 | 39.5553 | 39.5553 | 39.5553 | 39.5553 | 39.5553 | 39.5553 | 39.5553
80% | 31.0095 | 36.7007 | 48.7671 | 52.0539 | 28.7599 | 28.7588 | 29.1347 | 29.547 | 30.3928 | 31.0003 | 31.3307 | 31.6925 | 32.0232 | 32.6194 | 33.3591 | 33.3091 | 33.3091 | 33.3091 | 33.3091 | 33.3091 | 33.3091 | 33.3091 | 33.3091 | 33.3091 | 33.3091 | 33.3091 | 33.3091 | 33.3091 | 33.3091 | 33.3091 | 33.3091 | 80% | 34.0348 | 40.9243 | 53.0149 | 56.1809 | 32.7926 | 32.8084 | 33.1343 | 33.9924 | 34.5678 | 35.1305 | 35.7885 | 36.3988 | 36.9908 | 37.0594 | 37.7502 | 37.2285 | 37.2285 | 37.2285 | 37.2285 | 37.2285 | 37.2285 | 37.2285 | 37.2285 | 37.2285 | 37.2285 | 37.2285 | 37.2285 | 37.2285 | 37.2285 | 37.2285 | 37.2285
75% | 72.9857 | 34.4069 | 45.7192 | 48.8006 | 26.9624 | 26.9613 | 27.3138 | 27.7004 | 28.4932 | 29.0628 | 29.3725 | 29.7118 | 30.0218 | 30.5807 | 31.2741 | 31.2273 | 31.2273 | 31.2273 | 31.2273 | 31.2273 | 31.2273 | 31.2273 | 31.2273 | 31.2273 | 31.2273 | 31.2273 | 31.2273 | 31.2273 | 31.2273 | 31.2273 | 31.2273 | 75% | 48.405 | 38.3665 | 49.7015 | 52.6696 | 30.743 | 30.7579 | 31.0634 | 31.8679 | 32.4073 | 32.9349 | 33.5517 | 34.1239 | 34.6789 | 34.7432 | 35.3908 | 34.9017 | 34.9017 | 34.9017 | 34.9017 | 34.9017 | 34.9017 | 34.9017 | 34.9017 | 34.9017 | 34.9017 | 34.9017 | 34.9017 | 34.9017 | 34.9017 | 34.9017 | 34.9017
70% | 150.5094 | 32.1131 | 42.6712 | 45.5472 | 25.1649 | 25.1639 | 25.4929 | 25.8537 | 26.5937 | 27.1253 | 27.4143 | 27.731 | 28.0203 | 28.542 | 29.1892 | 29.1455 | 29.1455 | 29.1455 | 29.1455 | 29.1455 | 29.1455 | 29.1455 | 29.1455 | 29.1455 | 29.1455 | 29.1455 | 29.1455 | 29.1455 | 29.1455 | 29.1455 | 29.1455 | 70% | 76.3892 | 35.8087 | 46.388 | 49.1583 | 28.6935 | 28.7073 | 28.9925 | 29.7434 | 30.2468 | 30.7392 | 31.3149 | 31.849 | 32.367 | 32.427 | 33.0315 | 32.575 | 32.575 | 32.575 | 32.575 | 32.575 | 32.575 | 32.575 | 32.575 | 32.575 | 32.575 | 32.575 | 32.575 | 32.575 | 32.575 | 32.575 | 32.575
65% | 359.6342 | 29.8193 | 39.6233 | 42.2938 | 23.3674 | 23.3665 | 23.6719 | 24.007 | 24.6941 | 25.1878 | 25.4562 | 25.7502 | 26.0189 | 26.5033 | 27.1043 | 27.0636 | 27.0636 | 27.0636 | 27.0636 | 27.0636 | 27.0636 | 27.0636 | 27.0636 | 27.0636 | 27.0636 | 27.0636 | 27.0636 | 27.0636 | 27.0636 | 27.0636 | 27.0636 | 65% | 114.2056 | 33.251 | 43.0746 | 45.647 | 26.644 | 26.6568 | 26.9216 | 27.6189 | 28.0863 | 28.5436 | 29.0782 | 29.574 | 30.0551 | 30.1108 | 30.6721 | 30.2482 | 30.2482 | 30.2482 | 30.2482 | 30.2482 | 30.2482 | 30.2482 | 30.2482 | 30.2482 | 30.2482 | 30.2482 | 30.2482 | 30.2482 | 30.2482 | 30.2482 | 30.2482
60% | 689.7717 | 27.5255 | 36.5753 | 39.0405 | 21.5699 | 21.5691 | 21.851 | 22.1603 | 22.7946 | 23.2503 | 23.498 | 23.7694 | 24.0174 | 24.4646 | 25.0193 | 24.9818 | 24.9818 | 24.9818 | 24.9818 | 24.9818 | 24.9818 | 24.9818 | 24.9818 | 24.9818 | 24.9818 | 24.9818 | 24.9818 | 24.9818 | 24.9818 | 24.9818 | 24.9818 | 60% | 178.1154 | 30.6932 | 39.7612 | 42.1357 | 24.5944 | 24.6063 | 24.8508 | 25.4943 | 25.9258 | 26.3479 | 26.8414 | 27.2991 | 27.7431 | 27.7946 | 28.3127 | 27.9214 | 27.9214 | 27.9214 | 27.9214 | 27.9214 | 27.9214 | 27.9214 | 27.9214 | 27.9214 | 27.9214 | 27.9214 | 27.9214 | 27.9214 | 27.9214 | 27.9214 | 27.9214
55% | 1095.5419 | 25.2317 | 33.5274 | 35.7871 | 19.7724 | 19.7717 | 20.0301 | 20.3136 | 20.895 | 21.3127 | 21.5398 | 21.7886 | 22.016 | 22.4259 | 22.9344 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 55% | 311.6074 | 28.1354 | 36.4477 | 38.6243 | 22.5449 | 22.5558 | 22.7799 | 23.3698 | 23.7653 | 24.1522 | 24.6046 | 25.0242 | 25.4312 | 25.4784 | 25.9533 | 25.5946 | 25.5946 | 25.5946 | 25.5946 | 25.5946 | 25.5946 | 25.5946 | 25.5946 | 25.5946 | 25.5946 | 25.5946 | 25.5946 | 25.5946 | 25.5946 | 25.5946 | 25.5946
50% | 1666.1918 | 22.9379 | 30.4794 | 32.5337 | 17.9749 | 17.9742 | 18.2092 | 18.4669 | 18.9955 | 19.3752 | 19.5817 | 19.8078 | 20.0145 | 20.3872 | 20.8494 | 20.8182 | 20.8182 | 20.8182 | 20.8182 | 20.8182 | 20.8182 | 20.8182 | 20.8182 | 20.8182 | 20.8182 | 20.8182 | 20.8182 | 20.8182 | 20.8182 | 20.8182 | 20.8182 | 50% | 636.0723 | 25.5777 | 33.1343 | 35.113 | 20.4954 | 20.5052 | 20.709 | 21.2453 | 21.6049 | 21.9566 | 22.3678 | 22.7493 | 23.1193 | 23.1621 | 23.5939 | 23.2678 | 23.2678 | 23.2678 | 23.2678 | 23.2678 | 23.2678 | 23.2678 | 23.2678 | 23.2678 | 23.2678 | 23.2678 | 23.2678 | 23.2678 | 23.2678 | 23.2678 | 23.2678
45% | 2506.0947 | 20.6442 | 27.4315 | 29.2803 | 16.1774 | 16.1768 | 16.3883 | 16.6202 | 17.0959 | 17.4377 | 17.6235 | 17.8271 | 18.0131 | 18.3484 | 18.7645 | 18.7364 | 18.7364 | 18.7364 | 18.7364 | 18.7364 | 18.7364 | 18.7364 | 18.7364 | 18.7364 | 18.7364 | 18.7364 | 18.7364 | 18.7364 | 18.7364 | 18.7364 | 18.7364 | 45% | 1179.4944 | 23.0199 | 29.8209 | 31.6017 | 18.4458 | 18.4547 | 18.6381 | 19.1207 | 19.4444 | 19.7609 | 20.131 | 20.4743 | 20.8073 | 20.8459 | 21.2345 | 20.941 | 20.941 | 20.941 | 20.941 | 20.941 | 20.941 | 20.941 | 20.941 | 20.941 | 20.941 | 20.941 | 20.941 | 20.941 | 20.941 | 20.941 | 20.941
40% | 3164.4787 | 18.3504 | 24.3836 | 26.027 | 14.3799 | 14.3794 | 14.5673 | 14.7735 | 15.1964 | 15.5002 | 15.6653 | 15.8463 | 16.0116 | 16.3097 | 16.6795 | 16.6546 | 16.6546 | 16.6546 | 16.6546 | 16.6546 | 16.6546 | 16.6546 | 16.6546 | 16.6546 | 16.6546 | 16.6546 | 16.6546 | 16.6546 | 16.6546 | 16.6546 | 16.6546 | 40% | 1808.3816 | 20.4621 | 26.5075 | 28.0904 | 16.3963 | 16.4042 | 16.5672 | 16.9962 | 17.2839 | 17.5653 | 17.8942 | 18.1994 | 18.4954 | 18.5297 | 18.8751 | 18.6143 | 18.6143 | 18.6143 | 18.6143 | 18.6143 | 18.6143 | 18.6143 | 18.6143 | 18.6143 | 18.6143 | 18.6143 | 18.6143 | 18.6143 | 18.6143 | 18.6143 | 18.6143
35% | 3551.3408 | 16.0566 | 21.3356 | 22.7736 | 12.5825 | 12.582 | 12.7464 | 12.9268 | 13.2968 | 13.5626 | 13.7072 | 13.8655 | 14.0102 | 14.271 | 14.5946 | 14.5727 | 14.5727 | 14.5727 | 14.5727 | 14.5727 | 14.5727 | 14.5727 | 14.5727 | 14.5727 | 14.5727 | 14.5727 | 14.5727 | 14.5727 | 14.5727 | 14.5727 | 14.5727 | 35% | 2779.1293 | 17.9044 | 23.194 | 24.5791 | 14.3468 | 14.3537 | 14.4963 | 14.8717 | 15.1234 | 15.3696 | 15.6575 | 15.9245 | 16.1835 | 16.2135 | 16.5157 | 16.2875 | 16.2875 | 16.2875 | 16.2875 | 16.2875 | 16.2875 | 16.2875 | 16.2875 | 16.2875 | 16.2875 | 16.2875 | 16.2875 | 16.2875 | 16.2875 | 16.2875 | 16.2875
30% | 3758.953 | 13.7628 | 18.2877 | 19.5202 | 10.785 | 10.7845 | 10.9255 | 11.0801 | 11.3973 | 11.6251 | 11.749 | 11.8847 | 12.0087 | 12.2323 | 12.5097 | 12.4909 | 12.4909 | 12.4909 | 12.4909 | 12.4909 | 12.4909 | 12.4909 | 12.4909 | 12.4909 | 12.4909 | 12.4909 | 12.4909 | 12.4909 | 12.4909 | 12.4909 | 12.4909 | 30% | 3814.165 | 15.3466 | 19.8806 | 21.0678 | 12.2972 | 12.3031 | 12.4254 | 12.7472 | 12.9629 | 13.1739 | 13.4207 | 13.6496 | 13.8716 | 13.8973 | 14.1563 | 13.9607 | 13.9607 | 13.9607 | 13.9607 | 13.9607 | 13.9607 | 13.9607 | 13.9607 | 13.9607 | 13.9607 | 13.9607 | 13.9607 | 13.9607 | 13.9607 | 13.9607 | 13.9607
25% | 3926.4798 | 11.469 | 15.2397 | 16.2669 | 8.9875 | 8.9871 | 9.1046 | 9.2335 | 9.4977 | 9.6876 | 9.7908 | 9.9039 | 10.0073 | 10.1936 | 10.4247 | 10.4091 | 10.4091 | 10.4091 | 10.4091 | 10.4091 | 10.4091 | 10.4091 | 10.4091 | 10.4091 | 10.4091 | 10.4091 | 10.4091 | 10.4091 | 10.4091 | 10.4091 | 10.4091 | 25% | 4166.9923 | 12.7888 | 16.5672 | 17.5565 | 10.2477 | 10.2526 | 10.3545 | 10.6226 | 10.8024 | 10.9783 | 11.1839 | 11.3746 | 11.5596 | 11.5811 | 11.7969 | 11.6339 | 11.6339 | 11.6339 | 11.6339 | 11.6339 | 11.6339 | 11.6339 | 11.6339 | 11.6339 | 11.6339 | 11.6339 | 11.6339 | 11.6339 | 11.6339 | 11.6339 | 11.6339
20% | 4050.5177 | 9.1752 | 12.1918 | 13.0135 | 7.19 | 7.1897 | 7.2837 | 7.3868 | 7.5982 | 7.7501 | 7.8327 | 7.9231 | 8.0058 | 8.1549 | 8.3398 | 8.3273 | 8.3273 | 8.3273 | 8.3273 | 8.3273 | 8.3273 | 8.3273 | 8.3273 | 8.3273 | 8.3273 | 8.3273 | 8.3273 | 8.3273 | 8.3273 | 8.3273 | 8.3273 | 20% | 4282.7105 | 10.2311 | 13.2537 | 14.0452 | 8.1981 | 8.2021 | 8.2836 | 8.4981 | 8.6419 | 8.7826 | 8.9471 | 9.0997 | 9.2477 | 9.2649 | 9.4376 | 9.3071 | 9.3071 | 9.3071 | 9.3071 | 9.3071 | 9.3071 | 9.3071 | 9.3071 | 9.3071 | 9.3071 | 9.3071 | 9.3071 | 9.3071 | 9.3071 | 9.3071 | 9.3071
15% | 4152.622 | 6.8814 | 9.1438 | 9.7601 | 5.3925 | 5.3923 | 5.4628 | 5.5401 | 5.6986 | 5.8126 | 5.8745 | 5.9424 | 6.0044 | 6.1161 | 6.2548 | 6.2455 | 6.2455 | 6.2455 | 6.2455 | 6.2455 | 6.2455 | 6.2455 | 6.2455 | 6.2455 | 6.2455 | 6.2455 | 6.2455 | 6.2455 | 6.2455 | 6.2455 | 6.2455 | 15% | 4364.7722 | 7.6733 | 9.9403 | 10.5339 | 6.1486 | 6.1516 | 6.2127 | 6.3736 | 6.4815 | 6.587 | 6.7103 | 6.8248 | 6.9358 | 6.9486 | 7.0782 | 6.9803 | 6.9803 | 6.9803 | 6.9803 | 6.9803 | 6.9803 | 6.9803 | 6.9803 | 6.9803 | 6.9803 | 6.9803 | 6.9803 | 6.9803 | 6.9803 | 6.9803 | 6.9803
10% | 4248.2976 | 4.5876 | 6.0959 | 6.5067 | 3.595 | 3.5948 | 3.6418 | 3.6934 | 3.7991 | 3.875 | 3.9163 | 3.9616 | 4.0029 | 4.0774 | 4.1699 | 4.1636 | 4.1636 | 4.1636 | 4.1636 | 4.1636 | 4.1636 | 4.1636 | 4.1636 | 4.1636 | 4.1636 | 4.1636 | 4.1636 | 4.1636 | 4.1636 | 4.1636 | 4.1636 | 10% | 4391.6218 | 5.1155 | 6.6269 | 7.0226 | 4.0991 | 4.101 | 4.1418 | 4.2491 | 4.321 | 4.3913 | 4.4736 | 4.5499 | 4.6239 | 4.6324 | 4.7188 | 4.6536 | 4.6536 | 4.6536 | 4.6536 | 4.6536 | 4.6536 | 4.6536 | 4.6536 | 4.6536 | 4.6536 | 4.6536 | 4.6536 | 4.6536 | 4.6536 | 4.6536 | 4.6536
5% | 4361.7469 | 2.2938 | 3.0479 | 3.2534 | 1.7975 | 1.7974 | 1.8209 | 1.8467 | 1.8995 | 1.9375 | 1.9582 | 1.9808 | 2.0015 | 2.0387 | 2.0849 | 2.0818 | 2.0818 | 2.0818 | 2.0818 | 2.0818 | 2.0818 | 2.0818 | 2.0818 | 2.0818 | 2.0818 | 2.0818 | 2.0818 | 2.0818 | 2.0818 | 2.0818 | 2.0818 | 5% | 4391.6218 | 2.5578 | 3.3134 | 3.5113 | 2.0495 | 2.0505 | 2.0709 | 2.1245 | 2.1605 | 2.1957 | 2.2368 | 2.2749 | 2.3119 | 2.3162 | 2.3594 | 2.3268 | 2.3268 | 2.3268 | 2.3268 | 2.3268 | 2.3268 | 2.3268 | 2.3268 | 2.3268 | 2.3268 | 2.3268 | 2.3268 | 2.3268 | 2.3268 | 2.3268 | 2.3268
9.992e-14% | 4391.6218 | 4.5839e-14 | 6.091e-14 | 6.5015e-14 | 3.5921e-14 | 3.592e-14 | 3.6389e-14 | 3.6904e-14 | 3.7961e-14 | 3.8719e-14 | 3.9132e-14 | 3.9584e-14 | 3.9997e-14 | 4.0742e-14 | 4.1666e-14 | 4.1603e-14 | 4.1603e-14 | 4.1603e-14 | 4.1603e-14 | 4.1603e-14 | 4.1603e-14 | 4.1603e-14 | 4.1603e-14 | 4.1603e-14 | 4.1603e-14 | 4.1603e-14 | 4.1603e-14 | 4.1603e-14 | 4.1603e-14 | 4.1603e-14 | 4.1603e-14 | 9.992e-14% | 4391.6218 | 5.1114e-14 | 6.6216e-14 | 7.017e-14 | 4.0958e-14 | 4.0978e-14 | 4.1385e-14 | 4.2457e-14 | 4.3175e-14 | 4.3878e-14 | 4.47e-14 | 4.5462e-14 | 4.6202e-14 | 4.6287e-14 | 4.715e-14 | 4.6498e-14 | 4.6498e-14 | 4.6498e-14 | 4.6498e-14 | 4.6498e-14 | 4.6498e-14 | 4.6498e-14 | 4.6498e-14 | 4.6498e-14 | 4.6498e-14 | 4.6498e-14 | 4.6498e-14 | 4.6498e-14 | 4.6498e-14 | 4.6498e-14 | 4.6498e-14
Option 3
Winter Season | [31 empty] | Winter Season
P50 | [31 empty] | P10
% of MD | Winter - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Winter - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 40.358 | 56.0239 | 60.0964 | 60.7906 | 61.3321 | 62.2643 | 64.3852 | 65.8049 | 67.6034 | 68.5369 | 69.3582 | 67.845 | 69.6185 | 72.4066 | 70.2908 | 70.2908 | 70.2908 | 70.2908 | 70.2908 | 70.2908 | 70.2908 | 70.2908 | 70.2908 | 70.2908 | 70.2908 | 70.2908 | 70.2908 | 70.2908 | 70.2908 | 70.2908 | 100% | 0 | 43.208 | 58.6763 | 62.9078 | 63.5625 | 63.9783 | 64.8903 | 67.0443 | 68.2204 | 70.4608 | 77.2709 | 71.6566 | 70.5585 | 72.0408 | 75.2827 | 73.0883 | 73.0883 | 73.0883 | 73.0883 | 73.0883 | 73.0883 | 73.0883 | 73.0883 | 73.0883 | 73.0883 | 73.0883 | 73.0883 | 73.0883 | 73.0883 | 73.0883 | 73.0883
99% | 1.486 | 39.9544 | 55.4636 | 59.4955 | 60.1827 | 60.7187 | 61.6416 | 63.7413 | 65.1468 | 66.9274 | 67.8516 | 68.6646 | 67.1665 | 68.9223 | 71.6825 | 69.5879 | 69.5879 | 69.5879 | 69.5879 | 69.5879 | 69.5879 | 69.5879 | 69.5879 | 69.5879 | 69.5879 | 69.5879 | 69.5879 | 69.5879 | 69.5879 | 69.5879 | 69.5879 | 99% | 1.486 | 42.7759 | 58.0895 | 62.2787 | 62.9269 | 63.3385 | 64.2414 | 66.3739 | 67.5382 | 69.7562 | 76.4982 | 70.9401 | 69.8529 | 71.3204 | 74.5299 | 72.3575 | 72.3575 | 72.3575 | 72.3575 | 72.3575 | 72.3575 | 72.3575 | 72.3575 | 72.3575 | 72.3575 | 72.3575 | 72.3575 | 72.3575 | 72.3575 | 72.3575 | 72.3575
98% | 3.2692 | 39.5508 | 54.9034 | 58.8945 | 59.5748 | 60.1054 | 61.019 | 63.0975 | 64.4888 | 66.2513 | 67.1662 | 67.9711 | 66.4881 | 68.2261 | 70.9584 | 68.885 | 68.885 | 68.885 | 68.885 | 68.885 | 68.885 | 68.885 | 68.885 | 68.885 | 68.885 | 68.885 | 68.885 | 68.885 | 68.885 | 68.885 | 68.885 | 98% | 3.2692 | 42.3438 | 57.5027 | 61.6497 | 62.2913 | 62.6987 | 63.5925 | 65.7034 | 66.856 | 69.0516 | 75.7255 | 70.2235 | 69.1473 | 70.6 | 73.7771 | 71.6266 | 71.6266 | 71.6266 | 71.6266 | 71.6266 | 71.6266 | 71.6266 | 71.6266 | 71.6266 | 71.6266 | 71.6266 | 71.6266 | 71.6266 | 71.6266 | 71.6266 | 71.6266
97% | 6.8356 | 39.1473 | 54.3431 | 58.2935 | 58.9669 | 59.4921 | 60.3964 | 62.4536 | 63.8307 | 65.5753 | 66.4808 | 67.2775 | 65.8096 | 67.5299 | 70.2344 | 68.1821 | 68.1821 | 68.1821 | 68.1821 | 68.1821 | 68.1821 | 68.1821 | 68.1821 | 68.1821 | 68.1821 | 68.1821 | 68.1821 | 68.1821 | 68.1821 | 68.1821 | 68.1821 | 97% | 6.8356 | 41.9118 | 56.916 | 61.0206 | 61.6557 | 62.0589 | 62.9436 | 65.033 | 66.1738 | 68.3469 | 74.9528 | 69.5069 | 68.4417 | 69.8796 | 73.0243 | 70.8957 | 70.8957 | 70.8957 | 70.8957 | 70.8957 | 70.8957 | 70.8957 | 70.8957 | 70.8957 | 70.8957 | 70.8957 | 70.8957 | 70.8957 | 70.8957 | 70.8957 | 70.8957
95% | 17.5347 | 38.3401 | 53.2227 | 57.0916 | 57.7511 | 58.2655 | 59.1511 | 61.1659 | 62.5146 | 64.2232 | 65.1101 | 65.8903 | 64.4527 | 66.1375 | 68.7862 | 66.7762 | 66.7762 | 66.7762 | 66.7762 | 66.7762 | 66.7762 | 66.7762 | 66.7762 | 66.7762 | 66.7762 | 66.7762 | 66.7762 | 66.7762 | 66.7762 | 66.7762 | 66.7762 | 95% | 17.5347 | 41.0476 | 55.7425 | 59.7624 | 60.3844 | 60.7794 | 61.6458 | 63.6921 | 64.8094 | 66.9377 | 73.4073 | 68.0738 | 67.0306 | 68.4388 | 71.5186 | 69.4339 | 69.4339 | 69.4339 | 69.4339 | 69.4339 | 69.4339 | 69.4339 | 69.4339 | 69.4339 | 69.4339 | 69.4339 | 69.4339 | 69.4339 | 69.4339 | 69.4339 | 69.4339
90% | 78.7576 | 36.3222 | 50.4215 | 54.0868 | 54.7116 | 55.1988 | 56.0379 | 57.9467 | 59.2244 | 60.8431 | 61.6833 | 62.4224 | 61.0605 | 62.6566 | 65.1659 | 63.2617 | 63.2617 | 63.2617 | 63.2617 | 63.2617 | 63.2617 | 63.2617 | 63.2617 | 63.2617 | 63.2617 | 63.2617 | 63.2617 | 63.2617 | 63.2617 | 63.2617 | 63.2617 | 90% | 78.7576 | 38.8872 | 52.8086 | 56.617 | 57.2063 | 57.5804 | 58.4013 | 60.3399 | 61.3984 | 63.4147 | 69.5438 | 64.491 | 63.5026 | 64.8368 | 67.7545 | 65.7795 | 65.7795 | 65.7795 | 65.7795 | 65.7795 | 65.7795 | 65.7795 | 65.7795 | 65.7795 | 65.7795 | 65.7795 | 65.7795 | 65.7795 | 65.7795 | 65.7795 | 65.7795
85% | 236.8672 | 34.3043 | 47.6203 | 51.082 | 51.672 | 52.1322 | 52.9246 | 54.7274 | 55.9342 | 57.4629 | 58.2564 | 58.9545 | 57.6682 | 59.1757 | 61.5456 | 59.7472 | 59.7472 | 59.7472 | 59.7472 | 59.7472 | 59.7472 | 59.7472 | 59.7472 | 59.7472 | 59.7472 | 59.7472 | 59.7472 | 59.7472 | 59.7472 | 59.7472 | 59.7472 | 85% | 236.8672 | 36.7268 | 49.8748 | 53.4716 | 54.0282 | 54.3815 | 55.1567 | 56.9877 | 57.9873 | 59.8917 | 65.6803 | 60.9081 | 59.9747 | 61.2347 | 63.9903 | 62.1251 | 62.1251 | 62.1251 | 62.1251 | 62.1251 | 62.1251 | 62.1251 | 62.1251 | 62.1251 | 62.1251 | 62.1251 | 62.1251 | 62.1251 | 62.1251 | 62.1251 | 62.1251
80% | 497.5104 | 32.2864 | 44.8191 | 48.0771 | 48.6325 | 49.0656 | 49.8114 | 51.5081 | 52.6439 | 54.0827 | 54.8296 | 55.4866 | 54.276 | 55.6948 | 57.9252 | 56.2326 | 56.2326 | 56.2326 | 56.2326 | 56.2326 | 56.2326 | 56.2326 | 56.2326 | 56.2326 | 56.2326 | 56.2326 | 56.2326 | 56.2326 | 56.2326 | 56.2326 | 56.2326 | 80% | 497.5104 | 34.5664 | 46.941 | 50.3262 | 50.85 | 51.1826 | 51.9122 | 53.6355 | 54.5763 | 56.3686 | 61.8167 | 57.3253 | 56.4468 | 57.6327 | 60.2262 | 58.4707 | 58.4707 | 58.4707 | 58.4707 | 58.4707 | 58.4707 | 58.4707 | 58.4707 | 58.4707 | 58.4707 | 58.4707 | 58.4707 | 58.4707 | 58.4707 | 58.4707 | 58.4707
75% | 803.6248 | 30.2685 | 42.0179 | 45.0723 | 45.593 | 45.999 | 46.6982 | 48.2889 | 49.3537 | 50.7026 | 51.4027 | 52.0187 | 50.8837 | 52.2138 | 54.3049 | 52.7181 | 52.7181 | 52.7181 | 52.7181 | 52.7181 | 52.7181 | 52.7181 | 52.7181 | 52.7181 | 52.7181 | 52.7181 | 52.7181 | 52.7181 | 52.7181 | 52.7181 | 52.7181 | 75% | 803.6248 | 32.406 | 44.0072 | 47.1809 | 47.6719 | 47.9837 | 48.6677 | 50.2832 | 51.1653 | 52.8456 | 57.9532 | 53.7425 | 52.9189 | 54.0306 | 56.4621 | 54.8163 | 54.8163 | 54.8163 | 54.8163 | 54.8163 | 54.8163 | 54.8163 | 54.8163 | 54.8163 | 54.8163 | 54.8163 | 54.8163 | 54.8163 | 54.8163 | 54.8163 | 54.8163
70% | 1155.2107 | 28.2506 | 39.2167 | 42.0675 | 42.5534 | 42.9324 | 43.585 | 45.0696 | 46.0634 | 47.3224 | 47.9759 | 48.5508 | 47.4915 | 48.7329 | 50.6846 | 49.2035 | 49.2035 | 49.2035 | 49.2035 | 49.2035 | 49.2035 | 49.2035 | 49.2035 | 49.2035 | 49.2035 | 49.2035 | 49.2035 | 49.2035 | 49.2035 | 49.2035 | 49.2035 | 70% | 1155.2107 | 30.2456 | 41.0734 | 44.0355 | 44.4938 | 44.7848 | 45.4232 | 46.931 | 47.7543 | 49.3225 | 54.0896 | 50.1596 | 49.3909 | 50.4286 | 52.6979 | 51.1618 | 51.1618 | 51.1618 | 51.1618 | 51.1618 | 51.1618 | 51.1618 | 51.1618 | 51.1618 | 51.1618 | 51.1618 | 51.1618 | 51.1618 | 51.1618 | 51.1618 | 51.1618
65% | 1553.1596 | 26.2327 | 36.4155 | 39.0627 | 39.5139 | 39.8658 | 40.4718 | 41.8504 | 42.7732 | 43.9422 | 44.549 | 45.0828 | 44.0992 | 45.252 | 47.0643 | 45.689 | 45.689 | 45.689 | 45.689 | 45.689 | 45.689 | 45.689 | 45.689 | 45.689 | 45.689 | 45.689 | 45.689 | 45.689 | 45.689 | 45.689 | 45.689 | 65% | 1553.1596 | 28.0852 | 38.1396 | 40.8901 | 41.3157 | 41.5859 | 42.1787 | 43.5788 | 44.3433 | 45.7995 | 50.2261 | 46.5768 | 45.863 | 46.8266 | 48.9338 | 47.5074 | 47.5074 | 47.5074 | 47.5074 | 47.5074 | 47.5074 | 47.5074 | 47.5074 | 47.5074 | 47.5074 | 47.5074 | 47.5074 | 47.5074 | 47.5074 | 47.5074 | 47.5074
60% | 2026.2996 | 24.2148 | 33.6143 | 36.0579 | 36.4744 | 36.7992 | 37.3586 | 38.6311 | 39.4829 | 40.562 | 41.1222 | 41.6149 | 40.707 | 41.7711 | 43.4439 | 42.1745 | 42.1745 | 42.1745 | 42.1745 | 42.1745 | 42.1745 | 42.1745 | 42.1745 | 42.1745 | 42.1745 | 42.1745 | 42.1745 | 42.1745 | 42.1745 | 42.1745 | 42.1745 | 60% | 2026.2996 | 25.9248 | 35.2058 | 37.7447 | 38.1375 | 38.387 | 38.9342 | 40.2266 | 40.9322 | 42.2765 | 46.3625 | 42.994 | 42.3351 | 43.2245 | 45.1696 | 43.853 | 43.853 | 43.853 | 43.853 | 43.853 | 43.853 | 43.853 | 43.853 | 43.853 | 43.853 | 43.853 | 43.853 | 43.853 | 43.853 | 43.853 | 43.853
55% | 2598.4068 | 22.1969 | 30.8131 | 33.053 | 33.4348 | 33.7326 | 34.2454 | 35.4119 | 36.1927 | 37.1819 | 37.6953 | 38.147 | 37.3147 | 38.2902 | 39.8236 | 38.6599 | 38.6599 | 38.6599 | 38.6599 | 38.6599 | 38.6599 | 38.6599 | 38.6599 | 38.6599 | 38.6599 | 38.6599 | 38.6599 | 38.6599 | 38.6599 | 38.6599 | 38.6599 | 55% | 2598.4068 | 23.7644 | 32.272 | 34.5993 | 34.9594 | 35.188 | 35.6897 | 36.8744 | 37.5212 | 38.7534 | 42.499 | 39.4111 | 38.8072 | 39.6225 | 41.4055 | 40.1986 | 40.1986 | 40.1986 | 40.1986 | 40.1986 | 40.1986 | 40.1986 | 40.1986 | 40.1986 | 40.1986 | 40.1986 | 40.1986 | 40.1986 | 40.1986 | 40.1986 | 40.1986
50% | 3233.5201 | 20.179 | 28.0119 | 30.0482 | 30.3953 | 30.666 | 31.1321 | 32.1926 | 32.9024 | 33.8017 | 34.2685 | 34.6791 | 33.9225 | 34.8092 | 36.2033 | 35.1454 | 35.1454 | 35.1454 | 35.1454 | 35.1454 | 35.1454 | 35.1454 | 35.1454 | 35.1454 | 35.1454 | 35.1454 | 35.1454 | 35.1454 | 35.1454 | 35.1454 | 35.1454 | 50% | 3233.5201 | 21.604 | 29.3381 | 31.4539 | 31.7813 | 31.9891 | 32.4451 | 33.5222 | 34.1102 | 35.2304 | 38.6354 | 35.8283 | 35.2792 | 36.0204 | 37.6414 | 36.5442 | 36.5442 | 36.5442 | 36.5442 | 36.5442 | 36.5442 | 36.5442 | 36.5442 | 36.5442 | 36.5442 | 36.5442 | 36.5442 | 36.5442 | 36.5442 | 36.5442 | 36.5442
45% | 3775.313 | 18.1611 | 25.2107 | 27.0434 | 27.3558 | 27.5994 | 28.0189 | 28.9733 | 29.6122 | 30.4215 | 30.8416 | 31.2112 | 30.5302 | 31.3283 | 32.583 | 31.6309 | 31.6309 | 31.6309 | 31.6309 | 31.6309 | 31.6309 | 31.6309 | 31.6309 | 31.6309 | 31.6309 | 31.6309 | 31.6309 | 31.6309 | 31.6309 | 31.6309 | 31.6309 | 45% | 3775.313 | 19.4436 | 26.4043 | 28.3085 | 28.6031 | 28.7902 | 29.2006 | 30.1699 | 30.6992 | 31.7073 | 34.7719 | 32.2455 | 31.7513 | 32.4184 | 33.8772 | 32.8898 | 32.8898 | 32.8898 | 32.8898 | 32.8898 | 32.8898 | 32.8898 | 32.8898 | 32.8898 | 32.8898 | 32.8898 | 32.8898 | 32.8898 | 32.8898 | 32.8898 | 32.8898
40% | 4072.8088 | 16.1432 | 22.4095 | 24.0386 | 24.3162 | 24.5328 | 24.9057 | 25.7541 | 26.322 | 27.0414 | 27.4148 | 27.7433 | 27.138 | 27.8474 | 28.9626 | 28.1163 | 28.1163 | 28.1163 | 28.1163 | 28.1163 | 28.1163 | 28.1163 | 28.1163 | 28.1163 | 28.1163 | 28.1163 | 28.1163 | 28.1163 | 28.1163 | 28.1163 | 28.1163 | 40% | 4072.8088 | 17.2832 | 23.4705 | 25.1631 | 25.425 | 25.5913 | 25.9561 | 26.8177 | 27.2882 | 28.1843 | 30.9084 | 28.6627 | 28.2234 | 28.8163 | 30.1131 | 29.2353 | 29.2353 | 29.2353 | 29.2353 | 29.2353 | 29.2353 | 29.2353 | 29.2353 | 29.2353 | 29.2353 | 29.2353 | 29.2353 | 29.2353 | 29.2353 | 29.2353 | 29.2353
35% | 4198.821 | 14.1253 | 19.6083 | 21.0337 | 21.2767 | 21.4662 | 21.7925 | 22.5348 | 23.0317 | 23.6612 | 23.9879 | 24.2754 | 23.7457 | 24.3665 | 25.3423 | 24.6018 | 24.6018 | 24.6018 | 24.6018 | 24.6018 | 24.6018 | 24.6018 | 24.6018 | 24.6018 | 24.6018 | 24.6018 | 24.6018 | 24.6018 | 24.6018 | 24.6018 | 24.6018 | 35% | 4198.821 | 15.1228 | 20.5367 | 22.0177 | 22.2469 | 22.3924 | 22.7116 | 23.4655 | 23.8771 | 24.6613 | 27.0448 | 25.0798 | 24.6955 | 25.2143 | 26.349 | 25.5809 | 25.5809 | 25.5809 | 25.5809 | 25.5809 | 25.5809 | 25.5809 | 25.5809 | 25.5809 | 25.5809 | 25.5809 | 25.5809 | 25.5809 | 25.5809 | 25.5809 | 25.5809
30% | 4271.3374 | 12.1074 | 16.8072 | 18.0289 | 18.2372 | 18.3996 | 18.6793 | 19.3156 | 19.7415 | 20.281 | 20.5611 | 20.8075 | 20.3535 | 20.8855 | 21.722 | 21.0872 | 21.0872 | 21.0872 | 21.0872 | 21.0872 | 21.0872 | 21.0872 | 21.0872 | 21.0872 | 21.0872 | 21.0872 | 21.0872 | 21.0872 | 21.0872 | 21.0872 | 21.0872 | 30% | 4271.3374 | 12.9624 | 17.6029 | 18.8723 | 19.0688 | 19.1935 | 19.4671 | 20.1133 | 20.4661 | 21.1382 | 23.1813 | 21.497 | 21.1675 | 21.6123 | 22.5848 | 21.9265 | 21.9265 | 21.9265 | 21.9265 | 21.9265 | 21.9265 | 21.9265 | 21.9265 | 21.9265 | 21.9265 | 21.9265 | 21.9265 | 21.9265 | 21.9265 | 21.9265 | 21.9265
25% | 4321.8611 | 10.0895 | 14.006 | 15.0241 | 15.1977 | 15.333 | 15.5661 | 16.0963 | 16.4512 | 16.9009 | 17.1342 | 17.3396 | 16.9612 | 17.4046 | 18.1016 | 17.5727 | 17.5727 | 17.5727 | 17.5727 | 17.5727 | 17.5727 | 17.5727 | 17.5727 | 17.5727 | 17.5727 | 17.5727 | 17.5727 | 17.5727 | 17.5727 | 17.5727 | 17.5727 | 25% | 4321.8611 | 10.802 | 14.6691 | 15.727 | 15.8906 | 15.9946 | 16.2226 | 16.7611 | 17.0551 | 17.6152 | 19.3177 | 17.9142 | 17.6396 | 18.0102 | 18.8207 | 18.2721 | 18.2721 | 18.2721 | 18.2721 | 18.2721 | 18.2721 | 18.2721 | 18.2721 | 18.2721 | 18.2721 | 18.2721 | 18.2721 | 18.2721 | 18.2721 | 18.2721 | 18.2721
20% | 4353.067 | 8.0716 | 11.2048 | 12.0193 | 12.1581 | 12.2664 | 12.4529 | 12.877 | 13.161 | 13.5207 | 13.7074 | 13.8716 | 13.569 | 13.9237 | 14.4813 | 14.0582 | 14.0582 | 14.0582 | 14.0582 | 14.0582 | 14.0582 | 14.0582 | 14.0582 | 14.0582 | 14.0582 | 14.0582 | 14.0582 | 14.0582 | 14.0582 | 14.0582 | 14.0582 | 20% | 4353.067 | 8.6416 | 11.7353 | 12.5816 | 12.7125 | 12.7957 | 12.9781 | 13.4089 | 13.6441 | 14.0922 | 15.4542 | 14.3313 | 14.1117 | 14.4082 | 15.0565 | 14.6177 | 14.6177 | 14.6177 | 14.6177 | 14.6177 | 14.6177 | 14.6177 | 14.6177 | 14.6177 | 14.6177 | 14.6177 | 14.6177 | 14.6177 | 14.6177 | 14.6177 | 14.6177
15% | 4369.4129 | 6.0537 | 8.4036 | 9.0145 | 9.1186 | 9.1998 | 9.3396 | 9.6578 | 9.8707 | 10.1405 | 10.2805 | 10.4037 | 10.1767 | 10.4428 | 10.861 | 10.5436 | 10.5436 | 10.5436 | 10.5436 | 10.5436 | 10.5436 | 10.5436 | 10.5436 | 10.5436 | 10.5436 | 10.5436 | 10.5436 | 10.5436 | 10.5436 | 10.5436 | 10.5436 | 15% | 4369.4129 | 6.4812 | 8.8014 | 9.4362 | 9.5344 | 9.5967 | 9.7335 | 10.0566 | 10.2331 | 10.5691 | 11.5906 | 10.7485 | 10.5838 | 10.8061 | 11.2924 | 10.9633 | 10.9633 | 10.9633 | 10.9633 | 10.9633 | 10.9633 | 10.9633 | 10.9633 | 10.9633 | 10.9633 | 10.9633 | 10.9633 | 10.9633 | 10.9633 | 10.9633 | 10.9633
10% | 4378.6261 | 4.0358 | 5.6024 | 6.0096 | 6.0791 | 6.1332 | 6.2264 | 6.4385 | 6.5805 | 6.7603 | 6.8537 | 6.9358 | 6.7845 | 6.9618 | 7.2407 | 7.0291 | 7.0291 | 7.0291 | 7.0291 | 7.0291 | 7.0291 | 7.0291 | 7.0291 | 7.0291 | 7.0291 | 7.0291 | 7.0291 | 7.0291 | 7.0291 | 7.0291 | 7.0291 | 10% | 4378.6261 | 4.3208 | 5.8676 | 6.2908 | 6.3563 | 6.3978 | 6.489 | 6.7044 | 6.822 | 7.0461 | 7.7271 | 7.1657 | 7.0558 | 7.2041 | 7.5283 | 7.3088 | 7.3088 | 7.3088 | 7.3088 | 7.3088 | 7.3088 | 7.3088 | 7.3088 | 7.3088 | 7.3088 | 7.3088 | 7.3088 | 7.3088 | 7.3088 | 7.3088 | 7.3088
5% | 4391.7028 | 2.0179 | 2.8012 | 3.0048 | 3.0395 | 3.0666 | 3.1132 | 3.2193 | 3.2902 | 3.3802 | 3.4268 | 3.4679 | 3.3922 | 3.4809 | 3.6203 | 3.5145 | 3.5145 | 3.5145 | 3.5145 | 3.5145 | 3.5145 | 3.5145 | 3.5145 | 3.5145 | 3.5145 | 3.5145 | 3.5145 | 3.5145 | 3.5145 | 3.5145 | 3.5145 | 5% | 4391.7028 | 2.1604 | 2.9338 | 3.1454 | 3.1781 | 3.1989 | 3.2445 | 3.3522 | 3.411 | 3.523 | 3.8635 | 3.5828 | 3.5279 | 3.602 | 3.7641 | 3.6544 | 3.6544 | 3.6544 | 3.6544 | 3.6544 | 3.6544 | 3.6544 | 3.6544 | 3.6544 | 3.6544 | 3.6544 | 3.6544 | 3.6544 | 3.6544 | 3.6544 | 3.6544
9.992e-14% | 4391.7028 | 4.0326e-14 | 5.5979e-14 | 6.0048e-14 | 6.0742e-14 | 6.1283e-14 | 6.2215e-14 | 6.4334e-14 | 6.5752e-14 | 6.7549e-14 | 6.8482e-14 | 6.9303e-14 | 6.7791e-14 | 6.9563e-14 | 7.2349e-14 | 7.0235e-14 | 7.0235e-14 | 7.0235e-14 | 7.0235e-14 | 7.0235e-14 | 7.0235e-14 | 7.0235e-14 | 7.0235e-14 | 7.0235e-14 | 7.0235e-14 | 7.0235e-14 | 7.0235e-14 | 7.0235e-14 | 7.0235e-14 | 7.0235e-14 | 7.0235e-14 | 9.992e-14% | 4391.7028 | 4.3173e-14 | 5.8629e-14 | 6.2858e-14 | 6.3512e-14 | 6.3927e-14 | 6.4838e-14 | 6.6991e-14 | 6.8166e-14 | 7.0404e-14 | 7.7209e-14 | 7.1599e-14 | 7.0502e-14 | 7.1983e-14 | 7.5223e-14 | 7.303e-14 | 7.303e-14 | 7.303e-14 | 7.303e-14 | 7.303e-14 | 7.303e-14 | 7.303e-14 | 7.303e-14 | 7.303e-14 | 7.303e-14 | 7.303e-14 | 7.303e-14 | 7.303e-14 | 7.303e-14 | 7.303e-14 | 7.303e-14
Summer Season | [31 empty] | Summer Season
P50 | [31 empty] | P10
% of MD | Summer - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Summer - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 45.8759 | 60.9589 | 65.0674 | 64.9499 | 64.9485 | 65.4184 | 65.9338 | 66.9909 | 67.7504 | 68.1633 | 68.6157 | 69.029 | 69.7743 | 70.6989 | 70.6364 | 70.6364 | 70.6364 | 70.6364 | 70.6364 | 70.6364 | 70.6364 | 70.6364 | 70.6364 | 70.6364 | 70.6364 | 70.6364 | 70.6364 | 70.6364 | 70.6364 | 70.6364 | 100% | 0 | 51.1554 | 66.2686 | 70.2261 | 69.9907 | 70.0105 | 70.4179 | 71.4905 | 72.2097 | 72.9132 | 73.7356 | 74.4985 | 75.2386 | 75.3243 | 76.1878 | 75.5357 | 75.5357 | 75.5357 | 75.5357 | 75.5357 | 75.5357 | 75.5357 | 75.5357 | 75.5357 | 75.5357 | 75.5357 | 75.5357 | 75.5357 | 75.5357 | 75.5357 | 75.5357
99% | 0 | 45.4171 | 60.3493 | 64.4168 | 64.3004 | 64.299 | 64.7642 | 65.2745 | 66.321 | 67.0729 | 67.4817 | 67.9295 | 68.3387 | 69.0766 | 69.9919 | 69.93 | 69.93 | 69.93 | 69.93 | 69.93 | 69.93 | 69.93 | 69.93 | 69.93 | 69.93 | 69.93 | 69.93 | 69.93 | 69.93 | 69.93 | 69.93 | 99% | 1.5127 | 50.6438 | 65.6059 | 69.5238 | 69.2908 | 69.3104 | 69.7137 | 70.7756 | 71.4876 | 72.184 | 72.9983 | 73.7535 | 74.4862 | 74.571 | 75.4259 | 74.7803 | 74.7803 | 74.7803 | 74.7803 | 74.7803 | 74.7803 | 74.7803 | 74.7803 | 74.7803 | 74.7803 | 74.7803 | 74.7803 | 74.7803 | 74.7803 | 74.7803 | 74.7803
98% | 0 | 44.9584 | 59.7397 | 63.7661 | 63.6509 | 63.6495 | 64.11 | 64.6151 | 65.6511 | 66.3954 | 66.8001 | 67.2434 | 67.6484 | 68.3788 | 69.2849 | 69.2236 | 69.2236 | 69.2236 | 69.2236 | 69.2236 | 69.2236 | 69.2236 | 69.2236 | 69.2236 | 69.2236 | 69.2236 | 69.2236 | 69.2236 | 69.2236 | 69.2236 | 69.2236 | 98% | 2.269 | 50.1322 | 64.9433 | 68.8216 | 68.5909 | 68.6103 | 69.0096 | 70.0607 | 70.7655 | 71.4549 | 72.2609 | 73.0085 | 73.7338 | 73.8178 | 74.664 | 74.0249 | 74.0249 | 74.0249 | 74.0249 | 74.0249 | 74.0249 | 74.0249 | 74.0249 | 74.0249 | 74.0249 | 74.0249 | 74.0249 | 74.0249 | 74.0249 | 74.0249 | 74.0249
97% | 0.37816 | 44.4996 | 59.1301 | 63.1154 | 63.0014 | 63 | 63.4558 | 63.9558 | 64.9812 | 65.7179 | 66.1184 | 66.5572 | 66.9581 | 67.6811 | 68.5779 | 68.5173 | 68.5173 | 68.5173 | 68.5173 | 68.5173 | 68.5173 | 68.5173 | 68.5173 | 68.5173 | 68.5173 | 68.5173 | 68.5173 | 68.5173 | 68.5173 | 68.5173 | 68.5173 | 97% | 3.7816 | 49.6207 | 64.2806 | 68.1193 | 67.891 | 67.9102 | 68.3054 | 69.3458 | 70.0434 | 70.7258 | 71.5236 | 72.2636 | 72.9814 | 73.0646 | 73.9022 | 73.2696 | 73.2696 | 73.2696 | 73.2696 | 73.2696 | 73.2696 | 73.2696 | 73.2696 | 73.2696 | 73.2696 | 73.2696 | 73.2696 | 73.2696 | 73.2696 | 73.2696 | 73.2696
95% | 2.269 | 43.5821 | 57.911 | 61.8141 | 61.7024 | 61.701 | 62.1474 | 62.6371 | 63.6414 | 64.3629 | 64.7552 | 65.1849 | 65.5776 | 66.2856 | 67.1639 | 67.1046 | 67.1046 | 67.1046 | 67.1046 | 67.1046 | 67.1046 | 67.1046 | 67.1046 | 67.1046 | 67.1046 | 67.1046 | 67.1046 | 67.1046 | 67.1046 | 67.1046 | 67.1046 | 95% | 6.0506 | 48.5976 | 62.9552 | 66.7148 | 66.4912 | 66.51 | 66.897 | 67.916 | 68.5992 | 69.2675 | 70.0488 | 70.7736 | 71.4766 | 71.5581 | 72.3784 | 71.7589 | 71.7589 | 71.7589 | 71.7589 | 71.7589 | 71.7589 | 71.7589 | 71.7589 | 71.7589 | 71.7589 | 71.7589 | 71.7589 | 71.7589 | 71.7589 | 71.7589 | 71.7589
90% | 5.6725 | 41.2883 | 54.863 | 58.5607 | 58.4549 | 58.4536 | 58.8765 | 59.3404 | 60.2918 | 60.9754 | 61.347 | 61.7541 | 62.1261 | 62.7969 | 63.629 | 63.5727 | 63.5727 | 63.5727 | 63.5727 | 63.5727 | 63.5727 | 63.5727 | 63.5727 | 63.5727 | 63.5727 | 63.5727 | 63.5727 | 63.5727 | 63.5727 | 63.5727 | 63.5727 | 90% | 16.2611 | 46.0398 | 59.6418 | 63.2035 | 62.9917 | 63.0094 | 63.3761 | 64.3415 | 64.9887 | 65.6218 | 66.3621 | 67.0487 | 67.7147 | 67.7919 | 68.569 | 67.9821 | 67.9821 | 67.9821 | 67.9821 | 67.9821 | 67.9821 | 67.9821 | 67.9821 | 67.9821 | 67.9821 | 67.9821 | 67.9821 | 67.9821 | 67.9821 | 67.9821 | 67.9821
85% | 15.8829 | 38.9945 | 51.8151 | 55.3073 | 55.2074 | 55.2062 | 55.6056 | 56.0437 | 56.9423 | 57.5879 | 57.9388 | 58.3233 | 58.6747 | 59.3082 | 60.094 | 60.0409 | 60.0409 | 60.0409 | 60.0409 | 60.0409 | 60.0409 | 60.0409 | 60.0409 | 60.0409 | 60.0409 | 60.0409 | 60.0409 | 60.0409 | 60.0409 | 60.0409 | 60.0409 | 85% | 26.4715 | 43.482 | 56.3283 | 59.6922 | 59.4921 | 59.5089 | 59.8552 | 60.767 | 61.3783 | 61.9762 | 62.6753 | 63.3237 | 63.9528 | 64.0256 | 64.7596 | 64.2053 | 64.2053 | 64.2053 | 64.2053 | 64.2053 | 64.2053 | 64.2053 | 64.2053 | 64.2053 | 64.2053 | 64.2053 | 64.2053 | 64.2053 | 64.2053 | 64.2053 | 64.2053
80% | 31.0095 | 36.7007 | 48.7671 | 52.0539 | 51.9599 | 51.9588 | 52.3347 | 52.747 | 53.5928 | 54.2003 | 54.5307 | 54.8925 | 55.2232 | 55.8194 | 56.5591 | 56.5091 | 56.5091 | 56.5091 | 56.5091 | 56.5091 | 56.5091 | 56.5091 | 56.5091 | 56.5091 | 56.5091 | 56.5091 | 56.5091 | 56.5091 | 56.5091 | 56.5091 | 56.5091 | 80% | 34.0348 | 40.9243 | 53.0149 | 56.1809 | 55.9926 | 56.0084 | 56.3343 | 57.1924 | 57.7678 | 58.3305 | 58.9885 | 59.5988 | 60.1908 | 60.2594 | 60.9502 | 60.4285 | 60.4285 | 60.4285 | 60.4285 | 60.4285 | 60.4285 | 60.4285 | 60.4285 | 60.4285 | 60.4285 | 60.4285 | 60.4285 | 60.4285 | 60.4285 | 60.4285 | 60.4285
75% | 72.9857 | 34.4069 | 45.7192 | 48.8006 | 48.7124 | 48.7113 | 49.0638 | 49.4504 | 50.2432 | 50.8128 | 51.1225 | 51.4618 | 51.7718 | 52.3307 | 53.0241 | 52.9773 | 52.9773 | 52.9773 | 52.9773 | 52.9773 | 52.9773 | 52.9773 | 52.9773 | 52.9773 | 52.9773 | 52.9773 | 52.9773 | 52.9773 | 52.9773 | 52.9773 | 52.9773 | 75% | 48.405 | 38.3665 | 49.7015 | 52.6696 | 52.493 | 52.5079 | 52.8134 | 53.6179 | 54.1573 | 54.6849 | 55.3017 | 55.8739 | 56.4289 | 56.4932 | 57.1408 | 56.6517 | 56.6517 | 56.6517 | 56.6517 | 56.6517 | 56.6517 | 56.6517 | 56.6517 | 56.6517 | 56.6517 | 56.6517 | 56.6517 | 56.6517 | 56.6517 | 56.6517 | 56.6517
70% | 150.5094 | 32.1131 | 42.6712 | 45.5472 | 45.4649 | 45.4639 | 45.7929 | 46.1537 | 46.8937 | 47.4253 | 47.7143 | 48.031 | 48.3203 | 48.842 | 49.4892 | 49.4455 | 49.4455 | 49.4455 | 49.4455 | 49.4455 | 49.4455 | 49.4455 | 49.4455 | 49.4455 | 49.4455 | 49.4455 | 49.4455 | 49.4455 | 49.4455 | 49.4455 | 49.4455 | 70% | 76.3892 | 35.8087 | 46.388 | 49.1583 | 48.9935 | 49.0073 | 49.2925 | 50.0434 | 50.5468 | 51.0392 | 51.6149 | 52.149 | 52.667 | 52.727 | 53.3315 | 52.875 | 52.875 | 52.875 | 52.875 | 52.875 | 52.875 | 52.875 | 52.875 | 52.875 | 52.875 | 52.875 | 52.875 | 52.875 | 52.875 | 52.875 | 52.875
65% | 359.6342 | 29.8193 | 39.6233 | 42.2938 | 42.2174 | 42.2165 | 42.5219 | 42.857 | 43.5441 | 44.0378 | 44.3062 | 44.6002 | 44.8689 | 45.3533 | 45.9543 | 45.9136 | 45.9136 | 45.9136 | 45.9136 | 45.9136 | 45.9136 | 45.9136 | 45.9136 | 45.9136 | 45.9136 | 45.9136 | 45.9136 | 45.9136 | 45.9136 | 45.9136 | 45.9136 | 65% | 114.2056 | 33.251 | 43.0746 | 45.647 | 45.494 | 45.5068 | 45.7716 | 46.4689 | 46.9363 | 47.3936 | 47.9282 | 48.424 | 48.9051 | 48.9608 | 49.5221 | 49.0982 | 49.0982 | 49.0982 | 49.0982 | 49.0982 | 49.0982 | 49.0982 | 49.0982 | 49.0982 | 49.0982 | 49.0982 | 49.0982 | 49.0982 | 49.0982 | 49.0982 | 49.0982
60% | 689.7717 | 27.5255 | 36.5753 | 39.0405 | 38.9699 | 38.9691 | 39.251 | 39.5603 | 40.1946 | 40.6503 | 40.898 | 41.1694 | 41.4174 | 41.8646 | 42.4193 | 42.3818 | 42.3818 | 42.3818 | 42.3818 | 42.3818 | 42.3818 | 42.3818 | 42.3818 | 42.3818 | 42.3818 | 42.3818 | 42.3818 | 42.3818 | 42.3818 | 42.3818 | 42.3818 | 60% | 178.1154 | 30.6932 | 39.7612 | 42.1357 | 41.9944 | 42.0063 | 42.2508 | 42.8943 | 43.3258 | 43.7479 | 44.2414 | 44.6991 | 45.1431 | 45.1946 | 45.7127 | 45.3214 | 45.3214 | 45.3214 | 45.3214 | 45.3214 | 45.3214 | 45.3214 | 45.3214 | 45.3214 | 45.3214 | 45.3214 | 45.3214 | 45.3214 | 45.3214 | 45.3214 | 45.3214
55% | 1095.5419 | 25.2317 | 33.5274 | 35.7871 | 35.7224 | 35.7217 | 35.9801 | 36.2636 | 36.845 | 37.2627 | 37.4898 | 37.7386 | 37.966 | 38.3759 | 38.8844 | 38.85 | 38.85 | 38.85 | 38.85 | 38.85 | 38.85 | 38.85 | 38.85 | 38.85 | 38.85 | 38.85 | 38.85 | 38.85 | 38.85 | 38.85 | 38.85 | 55% | 311.6074 | 28.1354 | 36.4477 | 38.6243 | 38.4949 | 38.5058 | 38.7299 | 39.3198 | 39.7153 | 40.1022 | 40.5546 | 40.9742 | 41.3812 | 41.4284 | 41.9033 | 41.5446 | 41.5446 | 41.5446 | 41.5446 | 41.5446 | 41.5446 | 41.5446 | 41.5446 | 41.5446 | 41.5446 | 41.5446 | 41.5446 | 41.5446 | 41.5446 | 41.5446 | 41.5446
50% | 1666.1918 | 22.9379 | 30.4794 | 32.5337 | 32.4749 | 32.4742 | 32.7092 | 32.9669 | 33.4955 | 33.8752 | 34.0817 | 34.3078 | 34.5145 | 34.8872 | 35.3494 | 35.3182 | 35.3182 | 35.3182 | 35.3182 | 35.3182 | 35.3182 | 35.3182 | 35.3182 | 35.3182 | 35.3182 | 35.3182 | 35.3182 | 35.3182 | 35.3182 | 35.3182 | 35.3182 | 50% | 636.0723 | 25.5777 | 33.1343 | 35.113 | 34.9954 | 35.0052 | 35.209 | 35.7453 | 36.1049 | 36.4566 | 36.8678 | 37.2493 | 37.6193 | 37.6621 | 38.0939 | 37.7678 | 37.7678 | 37.7678 | 37.7678 | 37.7678 | 37.7678 | 37.7678 | 37.7678 | 37.7678 | 37.7678 | 37.7678 | 37.7678 | 37.7678 | 37.7678 | 37.7678 | 37.7678
45% | 2506.0947 | 20.6442 | 27.4315 | 29.2803 | 29.2274 | 29.2268 | 29.4383 | 29.6702 | 30.1459 | 30.4877 | 30.6735 | 30.8771 | 31.0631 | 31.3984 | 31.8145 | 31.7864 | 31.7864 | 31.7864 | 31.7864 | 31.7864 | 31.7864 | 31.7864 | 31.7864 | 31.7864 | 31.7864 | 31.7864 | 31.7864 | 31.7864 | 31.7864 | 31.7864 | 31.7864 | 45% | 1179.4944 | 23.0199 | 29.8209 | 31.6017 | 31.4958 | 31.5047 | 31.6881 | 32.1707 | 32.4944 | 32.8109 | 33.181 | 33.5243 | 33.8573 | 33.8959 | 34.2845 | 33.991 | 33.991 | 33.991 | 33.991 | 33.991 | 33.991 | 33.991 | 33.991 | 33.991 | 33.991 | 33.991 | 33.991 | 33.991 | 33.991 | 33.991 | 33.991
40% | 3164.4787 | 18.3504 | 24.3836 | 26.027 | 25.9799 | 25.9794 | 26.1673 | 26.3735 | 26.7964 | 27.1002 | 27.2653 | 27.4463 | 27.6116 | 27.9097 | 28.2795 | 28.2546 | 28.2546 | 28.2546 | 28.2546 | 28.2546 | 28.2546 | 28.2546 | 28.2546 | 28.2546 | 28.2546 | 28.2546 | 28.2546 | 28.2546 | 28.2546 | 28.2546 | 28.2546 | 40% | 1808.3816 | 20.4621 | 26.5075 | 28.0904 | 27.9963 | 28.0042 | 28.1672 | 28.5962 | 28.8839 | 29.1653 | 29.4942 | 29.7994 | 30.0954 | 30.1297 | 30.4751 | 30.2143 | 30.2143 | 30.2143 | 30.2143 | 30.2143 | 30.2143 | 30.2143 | 30.2143 | 30.2143 | 30.2143 | 30.2143 | 30.2143 | 30.2143 | 30.2143 | 30.2143 | 30.2143
35% | 3551.3408 | 16.0566 | 21.3356 | 22.7736 | 22.7325 | 22.732 | 22.8964 | 23.0768 | 23.4468 | 23.7126 | 23.8572 | 24.0155 | 24.1602 | 24.421 | 24.7446 | 24.7227 | 24.7227 | 24.7227 | 24.7227 | 24.7227 | 24.7227 | 24.7227 | 24.7227 | 24.7227 | 24.7227 | 24.7227 | 24.7227 | 24.7227 | 24.7227 | 24.7227 | 24.7227 | 35% | 2779.1293 | 17.9044 | 23.194 | 24.5791 | 24.4968 | 24.5037 | 24.6463 | 25.0217 | 25.2734 | 25.5196 | 25.8075 | 26.0745 | 26.3335 | 26.3635 | 26.6657 | 26.4375 | 26.4375 | 26.4375 | 26.4375 | 26.4375 | 26.4375 | 26.4375 | 26.4375 | 26.4375 | 26.4375 | 26.4375 | 26.4375 | 26.4375 | 26.4375 | 26.4375 | 26.4375
30% | 3758.953 | 13.7628 | 18.2877 | 19.5202 | 19.485 | 19.4845 | 19.6255 | 19.7801 | 20.0973 | 20.3251 | 20.449 | 20.5847 | 20.7087 | 20.9323 | 21.2097 | 21.1909 | 21.1909 | 21.1909 | 21.1909 | 21.1909 | 21.1909 | 21.1909 | 21.1909 | 21.1909 | 21.1909 | 21.1909 | 21.1909 | 21.1909 | 21.1909 | 21.1909 | 21.1909 | 30% | 3814.165 | 15.3466 | 19.8806 | 21.0678 | 20.9972 | 21.0031 | 21.1254 | 21.4472 | 21.6629 | 21.8739 | 22.1207 | 22.3496 | 22.5716 | 22.5973 | 22.8563 | 22.6607 | 22.6607 | 22.6607 | 22.6607 | 22.6607 | 22.6607 | 22.6607 | 22.6607 | 22.6607 | 22.6607 | 22.6607 | 22.6607 | 22.6607 | 22.6607 | 22.6607 | 22.6607
25% | 3926.4798 | 11.469 | 15.2397 | 16.2669 | 16.2375 | 16.2371 | 16.3546 | 16.4835 | 16.7477 | 16.9376 | 17.0408 | 17.1539 | 17.2573 | 17.4436 | 17.6747 | 17.6591 | 17.6591 | 17.6591 | 17.6591 | 17.6591 | 17.6591 | 17.6591 | 17.6591 | 17.6591 | 17.6591 | 17.6591 | 17.6591 | 17.6591 | 17.6591 | 17.6591 | 17.6591 | 25% | 4166.9923 | 12.7888 | 16.5672 | 17.5565 | 17.4977 | 17.5026 | 17.6045 | 17.8726 | 18.0524 | 18.2283 | 18.4339 | 18.6246 | 18.8096 | 18.8311 | 19.0469 | 18.8839 | 18.8839 | 18.8839 | 18.8839 | 18.8839 | 18.8839 | 18.8839 | 18.8839 | 18.8839 | 18.8839 | 18.8839 | 18.8839 | 18.8839 | 18.8839 | 18.8839 | 18.8839
20% | 4050.5177 | 9.1752 | 12.1918 | 13.0135 | 12.99 | 12.9897 | 13.0837 | 13.1868 | 13.3982 | 13.5501 | 13.6327 | 13.7231 | 13.8058 | 13.9549 | 14.1398 | 14.1273 | 14.1273 | 14.1273 | 14.1273 | 14.1273 | 14.1273 | 14.1273 | 14.1273 | 14.1273 | 14.1273 | 14.1273 | 14.1273 | 14.1273 | 14.1273 | 14.1273 | 14.1273 | 20% | 4282.7105 | 10.2311 | 13.2537 | 14.0452 | 13.9981 | 14.0021 | 14.0836 | 14.2981 | 14.4419 | 14.5826 | 14.7471 | 14.8997 | 15.0477 | 15.0649 | 15.2376 | 15.1071 | 15.1071 | 15.1071 | 15.1071 | 15.1071 | 15.1071 | 15.1071 | 15.1071 | 15.1071 | 15.1071 | 15.1071 | 15.1071 | 15.1071 | 15.1071 | 15.1071 | 15.1071
15% | 4152.622 | 6.8814 | 9.1438 | 9.7601 | 9.7425 | 9.7423 | 9.8128 | 9.8901 | 10.0486 | 10.1626 | 10.2245 | 10.2924 | 10.3544 | 10.4661 | 10.6048 | 10.5955 | 10.5955 | 10.5955 | 10.5955 | 10.5955 | 10.5955 | 10.5955 | 10.5955 | 10.5955 | 10.5955 | 10.5955 | 10.5955 | 10.5955 | 10.5955 | 10.5955 | 10.5955 | 15% | 4364.7722 | 7.6733 | 9.9403 | 10.5339 | 10.4986 | 10.5016 | 10.5627 | 10.7236 | 10.8315 | 10.937 | 11.0603 | 11.1748 | 11.2858 | 11.2986 | 11.4282 | 11.3303 | 11.3303 | 11.3303 | 11.3303 | 11.3303 | 11.3303 | 11.3303 | 11.3303 | 11.3303 | 11.3303 | 11.3303 | 11.3303 | 11.3303 | 11.3303 | 11.3303 | 11.3303
10% | 4248.2976 | 4.5876 | 6.0959 | 6.5067 | 6.495 | 6.4948 | 6.5418 | 6.5934 | 6.6991 | 6.775 | 6.8163 | 6.8616 | 6.9029 | 6.9774 | 7.0699 | 7.0636 | 7.0636 | 7.0636 | 7.0636 | 7.0636 | 7.0636 | 7.0636 | 7.0636 | 7.0636 | 7.0636 | 7.0636 | 7.0636 | 7.0636 | 7.0636 | 7.0636 | 7.0636 | 10% | 4391.6218 | 5.1155 | 6.6269 | 7.0226 | 6.9991 | 7.001 | 7.0418 | 7.1491 | 7.221 | 7.2913 | 7.3736 | 7.4499 | 7.5239 | 7.5324 | 7.6188 | 7.5536 | 7.5536 | 7.5536 | 7.5536 | 7.5536 | 7.5536 | 7.5536 | 7.5536 | 7.5536 | 7.5536 | 7.5536 | 7.5536 | 7.5536 | 7.5536 | 7.5536 | 7.5536
5% | 4361.7469 | 2.2938 | 3.0479 | 3.2534 | 3.2475 | 3.2474 | 3.2709 | 3.2967 | 3.3495 | 3.3875 | 3.4082 | 3.4308 | 3.4515 | 3.4887 | 3.5349 | 3.5318 | 3.5318 | 3.5318 | 3.5318 | 3.5318 | 3.5318 | 3.5318 | 3.5318 | 3.5318 | 3.5318 | 3.5318 | 3.5318 | 3.5318 | 3.5318 | 3.5318 | 3.5318 | 5% | 4391.6218 | 2.5578 | 3.3134 | 3.5113 | 3.4995 | 3.5005 | 3.5209 | 3.5745 | 3.6105 | 3.6457 | 3.6868 | 3.7249 | 3.7619 | 3.7662 | 3.8094 | 3.7768 | 3.7768 | 3.7768 | 3.7768 | 3.7768 | 3.7768 | 3.7768 | 3.7768 | 3.7768 | 3.7768 | 3.7768 | 3.7768 | 3.7768 | 3.7768 | 3.7768 | 3.7768
9.992e-14% | 4391.6218 | 4.5839e-14 | 6.091e-14 | 6.5015e-14 | 6.4898e-14 | 6.4897e-14 | 6.5366e-14 | 6.5881e-14 | 6.6937e-14 | 6.7696e-14 | 6.8109e-14 | 6.8561e-14 | 6.8974e-14 | 6.9719e-14 | 7.0642e-14 | 7.058e-14 | 7.058e-14 | 7.058e-14 | 7.058e-14 | 7.058e-14 | 7.058e-14 | 7.058e-14 | 7.058e-14 | 7.058e-14 | 7.058e-14 | 7.058e-14 | 7.058e-14 | 7.058e-14 | 7.058e-14 | 7.058e-14 | 7.058e-14 | 9.992e-14% | 4391.6218 | 5.1114e-14 | 6.6216e-14 | 7.017e-14 | 6.9935e-14 | 6.9955e-14 | 7.0362e-14 | 7.1433e-14 | 7.2152e-14 | 7.2855e-14 | 7.3677e-14 | 7.4439e-14 | 7.5178e-14 | 7.5264e-14 | 7.6127e-14 | 7.5475e-14 | 7.5475e-14 | 7.5475e-14 | 7.5475e-14 | 7.5475e-14 | 7.5475e-14 | 7.5475e-14 | 7.5475e-14 | 7.5475e-14 | 7.5475e-14 | 7.5475e-14 | 7.5475e-14 | 7.5475e-14 | 7.5475e-14 | 7.5475e-14 | 7.5475e-14
Option 4
Winter Season | [31 empty] | Winter Season
P50 | [31 empty] | P10
% of MD | Winter - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Winter - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 40.358 | 56.0239 | 60.0964 | 46.2906 | 46.8321 | 47.7643 | 49.8852 | 51.3049 | 53.1034 | 54.0369 | 54.8582 | 53.345 | 55.1185 | 57.9066 | 55.7908 | 55.7908 | 55.7908 | 55.7908 | 55.7908 | 55.7908 | 55.7908 | 55.7908 | 55.7908 | 55.7908 | 55.7908 | 55.7908 | 55.7908 | 55.7908 | 55.7908 | 55.7908 | 100% | 0 | 43.208 | 58.6763 | 62.9078 | 49.0625 | 49.4783 | 50.3903 | 52.5443 | 53.7204 | 55.9608 | 62.7709 | 57.1566 | 56.0585 | 57.5408 | 60.7827 | 58.5883 | 58.5883 | 58.5883 | 58.5883 | 58.5883 | 58.5883 | 58.5883 | 58.5883 | 58.5883 | 58.5883 | 58.5883 | 58.5883 | 58.5883 | 58.5883 | 58.5883 | 58.5883
99% | 1.486 | 39.9544 | 55.4636 | 59.4955 | 45.8277 | 46.3637 | 47.2866 | 49.3863 | 50.7918 | 52.5724 | 53.4966 | 54.3096 | 52.8115 | 54.5673 | 57.3275 | 55.2329 | 55.2329 | 55.2329 | 55.2329 | 55.2329 | 55.2329 | 55.2329 | 55.2329 | 55.2329 | 55.2329 | 55.2329 | 55.2329 | 55.2329 | 55.2329 | 55.2329 | 55.2329 | 99% | 1.486 | 42.7759 | 58.0895 | 62.2787 | 48.5719 | 48.9835 | 49.8864 | 52.0189 | 53.1832 | 55.4012 | 62.1432 | 56.5851 | 55.4979 | 56.9654 | 60.1749 | 58.0025 | 58.0025 | 58.0025 | 58.0025 | 58.0025 | 58.0025 | 58.0025 | 58.0025 | 58.0025 | 58.0025 | 58.0025 | 58.0025 | 58.0025 | 58.0025 | 58.0025 | 58.0025
98% | 3.2692 | 39.5508 | 54.9034 | 58.8945 | 45.3648 | 45.8954 | 46.809 | 48.8875 | 50.2788 | 52.0413 | 52.9562 | 53.7611 | 52.2781 | 54.0161 | 56.7484 | 54.675 | 54.675 | 54.675 | 54.675 | 54.675 | 54.675 | 54.675 | 54.675 | 54.675 | 54.675 | 54.675 | 54.675 | 54.675 | 54.675 | 54.675 | 54.675 | 98% | 3.2692 | 42.3438 | 57.5027 | 61.6497 | 48.0813 | 48.4887 | 49.3825 | 51.4934 | 52.646 | 54.8416 | 61.5155 | 56.0135 | 54.9373 | 56.39 | 59.5671 | 57.4166 | 57.4166 | 57.4166 | 57.4166 | 57.4166 | 57.4166 | 57.4166 | 57.4166 | 57.4166 | 57.4166 | 57.4166 | 57.4166 | 57.4166 | 57.4166 | 57.4166 | 57.4166
97% | 6.8356 | 39.1473 | 54.3431 | 58.2935 | 44.9019 | 45.4271 | 46.3314 | 48.3886 | 49.7657 | 51.5103 | 52.4158 | 53.2125 | 51.7446 | 53.4649 | 56.1694 | 54.1171 | 54.1171 | 54.1171 | 54.1171 | 54.1171 | 54.1171 | 54.1171 | 54.1171 | 54.1171 | 54.1171 | 54.1171 | 54.1171 | 54.1171 | 54.1171 | 54.1171 | 54.1171 | 97% | 6.8356 | 41.9118 | 56.916 | 61.0206 | 47.5907 | 47.9939 | 48.8786 | 50.968 | 52.1088 | 54.2819 | 60.8878 | 55.4419 | 54.3767 | 55.8146 | 58.9593 | 56.8307 | 56.8307 | 56.8307 | 56.8307 | 56.8307 | 56.8307 | 56.8307 | 56.8307 | 56.8307 | 56.8307 | 56.8307 | 56.8307 | 56.8307 | 56.8307 | 56.8307 | 56.8307
95% | 17.5347 | 38.3401 | 53.2227 | 57.0916 | 43.9761 | 44.4905 | 45.3761 | 47.3909 | 48.7396 | 50.4482 | 51.3351 | 52.1153 | 50.6777 | 52.3625 | 55.0112 | 53.0012 | 53.0012 | 53.0012 | 53.0012 | 53.0012 | 53.0012 | 53.0012 | 53.0012 | 53.0012 | 53.0012 | 53.0012 | 53.0012 | 53.0012 | 53.0012 | 53.0012 | 53.0012 | 95% | 17.5347 | 41.0476 | 55.7425 | 59.7624 | 46.6094 | 47.0044 | 47.8708 | 49.9171 | 51.0344 | 53.1627 | 59.6323 | 54.2988 | 53.2556 | 54.6638 | 57.7436 | 55.6589 | 55.6589 | 55.6589 | 55.6589 | 55.6589 | 55.6589 | 55.6589 | 55.6589 | 55.6589 | 55.6589 | 55.6589 | 55.6589 | 55.6589 | 55.6589 | 55.6589 | 55.6589
90% | 78.7576 | 36.3222 | 50.4215 | 54.0868 | 41.6616 | 42.1488 | 42.9879 | 44.8967 | 46.1744 | 47.7931 | 48.6333 | 49.3724 | 48.0105 | 49.6066 | 52.1159 | 50.2117 | 50.2117 | 50.2117 | 50.2117 | 50.2117 | 50.2117 | 50.2117 | 50.2117 | 50.2117 | 50.2117 | 50.2117 | 50.2117 | 50.2117 | 50.2117 | 50.2117 | 50.2117 | 90% | 78.7576 | 38.8872 | 52.8086 | 56.617 | 44.1563 | 44.5304 | 45.3513 | 47.2899 | 48.3484 | 50.3647 | 56.4938 | 51.441 | 50.4526 | 51.7868 | 54.7045 | 52.7295 | 52.7295 | 52.7295 | 52.7295 | 52.7295 | 52.7295 | 52.7295 | 52.7295 | 52.7295 | 52.7295 | 52.7295 | 52.7295 | 52.7295 | 52.7295 | 52.7295 | 52.7295
85% | 236.8672 | 34.3043 | 47.6203 | 51.082 | 39.347 | 39.8072 | 40.5996 | 42.4024 | 43.6092 | 45.1379 | 45.9314 | 46.6295 | 45.3432 | 46.8507 | 49.2206 | 47.4222 | 47.4222 | 47.4222 | 47.4222 | 47.4222 | 47.4222 | 47.4222 | 47.4222 | 47.4222 | 47.4222 | 47.4222 | 47.4222 | 47.4222 | 47.4222 | 47.4222 | 47.4222 | 85% | 236.8672 | 36.7268 | 49.8748 | 53.4716 | 41.7032 | 42.0565 | 42.8317 | 44.6627 | 45.6623 | 47.5667 | 53.3553 | 48.5831 | 47.6497 | 48.9097 | 51.6653 | 49.8001 | 49.8001 | 49.8001 | 49.8001 | 49.8001 | 49.8001 | 49.8001 | 49.8001 | 49.8001 | 49.8001 | 49.8001 | 49.8001 | 49.8001 | 49.8001 | 49.8001 | 49.8001
80% | 497.5104 | 32.2864 | 44.8191 | 48.0771 | 37.0325 | 37.4656 | 38.2114 | 39.9081 | 41.0439 | 42.4827 | 43.2296 | 43.8866 | 42.676 | 44.0948 | 46.3252 | 44.6326 | 44.6326 | 44.6326 | 44.6326 | 44.6326 | 44.6326 | 44.6326 | 44.6326 | 44.6326 | 44.6326 | 44.6326 | 44.6326 | 44.6326 | 44.6326 | 44.6326 | 44.6326 | 80% | 497.5104 | 34.5664 | 46.941 | 50.3262 | 39.25 | 39.5826 | 40.3122 | 42.0355 | 42.9763 | 44.7686 | 50.2167 | 45.7253 | 44.8468 | 46.0327 | 48.6262 | 46.8707 | 46.8707 | 46.8707 | 46.8707 | 46.8707 | 46.8707 | 46.8707 | 46.8707 | 46.8707 | 46.8707 | 46.8707 | 46.8707 | 46.8707 | 46.8707 | 46.8707 | 46.8707
75% | 803.6248 | 30.2685 | 42.0179 | 45.0723 | 34.718 | 35.124 | 35.8232 | 37.4139 | 38.4787 | 39.8276 | 40.5277 | 41.1437 | 40.0087 | 41.3388 | 43.4299 | 41.8431 | 41.8431 | 41.8431 | 41.8431 | 41.8431 | 41.8431 | 41.8431 | 41.8431 | 41.8431 | 41.8431 | 41.8431 | 41.8431 | 41.8431 | 41.8431 | 41.8431 | 41.8431 | 75% | 803.6248 | 32.406 | 44.0072 | 47.1809 | 36.7969 | 37.1087 | 37.7927 | 39.4082 | 40.2903 | 41.9706 | 47.0782 | 42.8675 | 42.0439 | 43.1556 | 45.5871 | 43.9413 | 43.9413 | 43.9413 | 43.9413 | 43.9413 | 43.9413 | 43.9413 | 43.9413 | 43.9413 | 43.9413 | 43.9413 | 43.9413 | 43.9413 | 43.9413 | 43.9413 | 43.9413
70% | 1155.2107 | 28.2506 | 39.2167 | 42.0675 | 32.4034 | 32.7824 | 33.435 | 34.9196 | 35.9134 | 37.1724 | 37.8259 | 38.4008 | 37.3415 | 38.5829 | 40.5346 | 39.0535 | 39.0535 | 39.0535 | 39.0535 | 39.0535 | 39.0535 | 39.0535 | 39.0535 | 39.0535 | 39.0535 | 39.0535 | 39.0535 | 39.0535 | 39.0535 | 39.0535 | 39.0535 | 70% | 1155.2107 | 30.2456 | 41.0734 | 44.0355 | 34.3438 | 34.6348 | 35.2732 | 36.781 | 37.6043 | 39.1725 | 43.9396 | 40.0096 | 39.2409 | 40.2786 | 42.5479 | 41.0118 | 41.0118 | 41.0118 | 41.0118 | 41.0118 | 41.0118 | 41.0118 | 41.0118 | 41.0118 | 41.0118 | 41.0118 | 41.0118 | 41.0118 | 41.0118 | 41.0118 | 41.0118
65% | 1553.1596 | 26.2327 | 36.4155 | 39.0627 | 30.0889 | 30.4408 | 31.0468 | 32.4254 | 33.3482 | 34.5172 | 35.124 | 35.6578 | 34.6742 | 35.827 | 37.6393 | 36.264 | 36.264 | 36.264 | 36.264 | 36.264 | 36.264 | 36.264 | 36.264 | 36.264 | 36.264 | 36.264 | 36.264 | 36.264 | 36.264 | 36.264 | 36.264 | 65% | 1553.1596 | 28.0852 | 38.1396 | 40.8901 | 31.8907 | 32.1609 | 32.7537 | 34.1538 | 34.9183 | 36.3745 | 40.8011 | 37.1518 | 36.438 | 37.4016 | 39.5088 | 38.0824 | 38.0824 | 38.0824 | 38.0824 | 38.0824 | 38.0824 | 38.0824 | 38.0824 | 38.0824 | 38.0824 | 38.0824 | 38.0824 | 38.0824 | 38.0824 | 38.0824 | 38.0824
60% | 2026.2996 | 24.2148 | 33.6143 | 36.0579 | 27.7744 | 28.0992 | 28.6586 | 29.9311 | 30.7829 | 31.862 | 32.4222 | 32.9149 | 32.007 | 33.0711 | 34.7439 | 33.4745 | 33.4745 | 33.4745 | 33.4745 | 33.4745 | 33.4745 | 33.4745 | 33.4745 | 33.4745 | 33.4745 | 33.4745 | 33.4745 | 33.4745 | 33.4745 | 33.4745 | 33.4745 | 60% | 2026.2996 | 25.9248 | 35.2058 | 37.7447 | 29.4375 | 29.687 | 30.2342 | 31.5266 | 32.2322 | 33.5765 | 37.6625 | 34.294 | 33.6351 | 34.5245 | 36.4696 | 35.153 | 35.153 | 35.153 | 35.153 | 35.153 | 35.153 | 35.153 | 35.153 | 35.153 | 35.153 | 35.153 | 35.153 | 35.153 | 35.153 | 35.153 | 35.153
55% | 2598.4068 | 22.1969 | 30.8131 | 33.053 | 25.4598 | 25.7576 | 26.2704 | 27.4369 | 28.2177 | 29.2069 | 29.7203 | 30.172 | 29.3397 | 30.3152 | 31.8486 | 30.6849 | 30.6849 | 30.6849 | 30.6849 | 30.6849 | 30.6849 | 30.6849 | 30.6849 | 30.6849 | 30.6849 | 30.6849 | 30.6849 | 30.6849 | 30.6849 | 30.6849 | 30.6849 | 55% | 2598.4068 | 23.7644 | 32.272 | 34.5993 | 26.9844 | 27.213 | 27.7147 | 28.8994 | 29.5462 | 30.7784 | 34.524 | 31.4361 | 30.8322 | 31.6475 | 33.4305 | 32.2236 | 32.2236 | 32.2236 | 32.2236 | 32.2236 | 32.2236 | 32.2236 | 32.2236 | 32.2236 | 32.2236 | 32.2236 | 32.2236 | 32.2236 | 32.2236 | 32.2236 | 32.2236
50% | 3233.5201 | 20.179 | 28.0119 | 30.0482 | 23.1453 | 23.416 | 23.8821 | 24.9426 | 25.6524 | 26.5517 | 27.0185 | 27.4291 | 26.6725 | 27.5592 | 28.9533 | 27.8954 | 27.8954 | 27.8954 | 27.8954 | 27.8954 | 27.8954 | 27.8954 | 27.8954 | 27.8954 | 27.8954 | 27.8954 | 27.8954 | 27.8954 | 27.8954 | 27.8954 | 27.8954 | 50% | 3233.5201 | 21.604 | 29.3381 | 31.4539 | 24.5313 | 24.7391 | 25.1951 | 26.2722 | 26.8602 | 27.9804 | 31.3854 | 28.5783 | 28.0292 | 28.7704 | 30.3914 | 29.2942 | 29.2942 | 29.2942 | 29.2942 | 29.2942 | 29.2942 | 29.2942 | 29.2942 | 29.2942 | 29.2942 | 29.2942 | 29.2942 | 29.2942 | 29.2942 | 29.2942 | 29.2942
45% | 3775.313 | 18.1611 | 25.2107 | 27.0434 | 20.8308 | 21.0744 | 21.4939 | 22.4483 | 23.0872 | 23.8965 | 24.3166 | 24.6862 | 24.0052 | 24.8033 | 26.058 | 25.1059 | 25.1059 | 25.1059 | 25.1059 | 25.1059 | 25.1059 | 25.1059 | 25.1059 | 25.1059 | 25.1059 | 25.1059 | 25.1059 | 25.1059 | 25.1059 | 25.1059 | 25.1059 | 45% | 3775.313 | 19.4436 | 26.4043 | 28.3085 | 22.0781 | 22.2652 | 22.6756 | 23.6449 | 24.1742 | 25.1823 | 28.2469 | 25.7205 | 25.2263 | 25.8934 | 27.3522 | 26.3648 | 26.3648 | 26.3648 | 26.3648 | 26.3648 | 26.3648 | 26.3648 | 26.3648 | 26.3648 | 26.3648 | 26.3648 | 26.3648 | 26.3648 | 26.3648 | 26.3648 | 26.3648
40% | 4072.8088 | 16.1432 | 22.4095 | 24.0386 | 18.5162 | 18.7328 | 19.1057 | 19.9541 | 20.522 | 21.2414 | 21.6148 | 21.9433 | 21.338 | 22.0474 | 23.1626 | 22.3163 | 22.3163 | 22.3163 | 22.3163 | 22.3163 | 22.3163 | 22.3163 | 22.3163 | 22.3163 | 22.3163 | 22.3163 | 22.3163 | 22.3163 | 22.3163 | 22.3163 | 22.3163 | 40% | 4072.8088 | 17.2832 | 23.4705 | 25.1631 | 19.625 | 19.7913 | 20.1561 | 21.0177 | 21.4882 | 22.3843 | 25.1084 | 22.8627 | 22.4234 | 23.0163 | 24.3131 | 23.4353 | 23.4353 | 23.4353 | 23.4353 | 23.4353 | 23.4353 | 23.4353 | 23.4353 | 23.4353 | 23.4353 | 23.4353 | 23.4353 | 23.4353 | 23.4353 | 23.4353 | 23.4353
35% | 4198.821 | 14.1253 | 19.6083 | 21.0337 | 16.2017 | 16.3912 | 16.7175 | 17.4598 | 17.9567 | 18.5862 | 18.9129 | 19.2004 | 18.6707 | 19.2915 | 20.2673 | 19.5268 | 19.5268 | 19.5268 | 19.5268 | 19.5268 | 19.5268 | 19.5268 | 19.5268 | 19.5268 | 19.5268 | 19.5268 | 19.5268 | 19.5268 | 19.5268 | 19.5268 | 19.5268 | 35% | 4198.821 | 15.1228 | 20.5367 | 22.0177 | 17.1719 | 17.3174 | 17.6366 | 18.3905 | 18.8021 | 19.5863 | 21.9698 | 20.0048 | 19.6205 | 20.1393 | 21.274 | 20.5059 | 20.5059 | 20.5059 | 20.5059 | 20.5059 | 20.5059 | 20.5059 | 20.5059 | 20.5059 | 20.5059 | 20.5059 | 20.5059 | 20.5059 | 20.5059 | 20.5059 | 20.5059
30% | 4271.3374 | 12.1074 | 16.8072 | 18.0289 | 13.8872 | 14.0496 | 14.3293 | 14.9656 | 15.3915 | 15.931 | 16.2111 | 16.4575 | 16.0035 | 16.5355 | 17.372 | 16.7372 | 16.7372 | 16.7372 | 16.7372 | 16.7372 | 16.7372 | 16.7372 | 16.7372 | 16.7372 | 16.7372 | 16.7372 | 16.7372 | 16.7372 | 16.7372 | 16.7372 | 16.7372 | 30% | 4271.3374 | 12.9624 | 17.6029 | 18.8723 | 14.7188 | 14.8435 | 15.1171 | 15.7633 | 16.1161 | 16.7882 | 18.8313 | 17.147 | 16.8175 | 17.2623 | 18.2348 | 17.5765 | 17.5765 | 17.5765 | 17.5765 | 17.5765 | 17.5765 | 17.5765 | 17.5765 | 17.5765 | 17.5765 | 17.5765 | 17.5765 | 17.5765 | 17.5765 | 17.5765 | 17.5765
25% | 4321.8611 | 10.0895 | 14.006 | 15.0241 | 11.5727 | 11.708 | 11.9411 | 12.4713 | 12.8262 | 13.2759 | 13.5092 | 13.7146 | 13.3362 | 13.7796 | 14.4766 | 13.9477 | 13.9477 | 13.9477 | 13.9477 | 13.9477 | 13.9477 | 13.9477 | 13.9477 | 13.9477 | 13.9477 | 13.9477 | 13.9477 | 13.9477 | 13.9477 | 13.9477 | 13.9477 | 25% | 4321.8611 | 10.802 | 14.6691 | 15.727 | 12.2656 | 12.3696 | 12.5976 | 13.1361 | 13.4301 | 13.9902 | 15.6927 | 14.2892 | 14.0146 | 14.3852 | 15.1957 | 14.6471 | 14.6471 | 14.6471 | 14.6471 | 14.6471 | 14.6471 | 14.6471 | 14.6471 | 14.6471 | 14.6471 | 14.6471 | 14.6471 | 14.6471 | 14.6471 | 14.6471 | 14.6471
20% | 4353.067 | 8.0716 | 11.2048 | 12.0193 | 9.2581 | 9.3664 | 9.5529 | 9.977 | 10.261 | 10.6207 | 10.8074 | 10.9716 | 10.669 | 11.0237 | 11.5813 | 11.1582 | 11.1582 | 11.1582 | 11.1582 | 11.1582 | 11.1582 | 11.1582 | 11.1582 | 11.1582 | 11.1582 | 11.1582 | 11.1582 | 11.1582 | 11.1582 | 11.1582 | 11.1582 | 20% | 4353.067 | 8.6416 | 11.7353 | 12.5816 | 9.8125 | 9.8957 | 10.0781 | 10.5089 | 10.7441 | 11.1922 | 12.5542 | 11.4313 | 11.2117 | 11.5082 | 12.1565 | 11.7177 | 11.7177 | 11.7177 | 11.7177 | 11.7177 | 11.7177 | 11.7177 | 11.7177 | 11.7177 | 11.7177 | 11.7177 | 11.7177 | 11.7177 | 11.7177 | 11.7177 | 11.7177
15% | 4369.4129 | 6.0537 | 8.4036 | 9.0145 | 6.9436 | 7.0248 | 7.1646 | 7.4828 | 7.6957 | 7.9655 | 8.1055 | 8.2287 | 8.0017 | 8.2678 | 8.686 | 8.3686 | 8.3686 | 8.3686 | 8.3686 | 8.3686 | 8.3686 | 8.3686 | 8.3686 | 8.3686 | 8.3686 | 8.3686 | 8.3686 | 8.3686 | 8.3686 | 8.3686 | 8.3686 | 15% | 4369.4129 | 6.4812 | 8.8014 | 9.4362 | 7.3594 | 7.4217 | 7.5585 | 7.8816 | 8.0581 | 8.3941 | 9.4156 | 8.5735 | 8.4088 | 8.6311 | 9.1174 | 8.7883 | 8.7883 | 8.7883 | 8.7883 | 8.7883 | 8.7883 | 8.7883 | 8.7883 | 8.7883 | 8.7883 | 8.7883 | 8.7883 | 8.7883 | 8.7883 | 8.7883 | 8.7883
10% | 4378.6261 | 4.0358 | 5.6024 | 6.0096 | 4.6291 | 4.6832 | 4.7764 | 4.9885 | 5.1305 | 5.3103 | 5.4037 | 5.4858 | 5.3345 | 5.5118 | 5.7907 | 5.5791 | 5.5791 | 5.5791 | 5.5791 | 5.5791 | 5.5791 | 5.5791 | 5.5791 | 5.5791 | 5.5791 | 5.5791 | 5.5791 | 5.5791 | 5.5791 | 5.5791 | 5.5791 | 10% | 4378.6261 | 4.3208 | 5.8676 | 6.2908 | 4.9063 | 4.9478 | 5.039 | 5.2544 | 5.372 | 5.5961 | 6.2771 | 5.7157 | 5.6058 | 5.7541 | 6.0783 | 5.8588 | 5.8588 | 5.8588 | 5.8588 | 5.8588 | 5.8588 | 5.8588 | 5.8588 | 5.8588 | 5.8588 | 5.8588 | 5.8588 | 5.8588 | 5.8588 | 5.8588 | 5.8588
5% | 4391.7028 | 2.0179 | 2.8012 | 3.0048 | 2.3145 | 2.3416 | 2.3882 | 2.4943 | 2.5652 | 2.6552 | 2.7018 | 2.7429 | 2.6672 | 2.7559 | 2.8953 | 2.7895 | 2.7895 | 2.7895 | 2.7895 | 2.7895 | 2.7895 | 2.7895 | 2.7895 | 2.7895 | 2.7895 | 2.7895 | 2.7895 | 2.7895 | 2.7895 | 2.7895 | 2.7895 | 5% | 4391.7028 | 2.1604 | 2.9338 | 3.1454 | 2.4531 | 2.4739 | 2.5195 | 2.6272 | 2.686 | 2.798 | 3.1385 | 2.8578 | 2.8029 | 2.877 | 3.0391 | 2.9294 | 2.9294 | 2.9294 | 2.9294 | 2.9294 | 2.9294 | 2.9294 | 2.9294 | 2.9294 | 2.9294 | 2.9294 | 2.9294 | 2.9294 | 2.9294 | 2.9294 | 2.9294
9.992e-14% | 4391.7028 | 4.0326e-14 | 5.5979e-14 | 6.0048e-14 | 4.6254e-14 | 4.6795e-14 | 4.7726e-14 | 4.9845e-14 | 5.1264e-14 | 5.3061e-14 | 5.3994e-14 | 5.4814e-14 | 5.3302e-14 | 5.5074e-14 | 5.786e-14 | 5.5746e-14 | 5.5746e-14 | 5.5746e-14 | 5.5746e-14 | 5.5746e-14 | 5.5746e-14 | 5.5746e-14 | 5.5746e-14 | 5.5746e-14 | 5.5746e-14 | 5.5746e-14 | 5.5746e-14 | 5.5746e-14 | 5.5746e-14 | 5.5746e-14 | 5.5746e-14 | 9.992e-14% | 4391.7028 | 4.3173e-14 | 5.8629e-14 | 6.2858e-14 | 4.9023e-14 | 4.9439e-14 | 5.035e-14 | 5.2502e-14 | 5.3677e-14 | 5.5916e-14 | 6.2721e-14 | 5.7111e-14 | 5.6014e-14 | 5.7495e-14 | 6.0734e-14 | 5.8542e-14 | 5.8542e-14 | 5.8542e-14 | 5.8542e-14 | 5.8542e-14 | 5.8542e-14 | 5.8542e-14 | 5.8542e-14 | 5.8542e-14 | 5.8542e-14 | 5.8542e-14 | 5.8542e-14 | 5.8542e-14 | 5.8542e-14 | 5.8542e-14 | 5.8542e-14
Summer Season | [31 empty] | Summer Season
P50 | [31 empty] | P10
% of MD | Summer - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Summer - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 45.8759 | 60.9589 | 65.0674 | 50.4499 | 50.4485 | 50.9184 | 51.4338 | 52.4909 | 53.2504 | 53.6633 | 54.1157 | 54.529 | 55.2743 | 56.1989 | 56.1364 | 56.1364 | 56.1364 | 56.1364 | 56.1364 | 56.1364 | 56.1364 | 56.1364 | 56.1364 | 56.1364 | 56.1364 | 56.1364 | 56.1364 | 56.1364 | 56.1364 | 56.1364 | 100% | 0 | 51.1554 | 66.2686 | 70.2261 | 55.4907 | 55.5105 | 55.9179 | 56.9905 | 57.7097 | 58.4132 | 59.2356 | 59.9985 | 60.7386 | 60.8243 | 61.6878 | 61.0357 | 61.0357 | 61.0357 | 61.0357 | 61.0357 | 61.0357 | 61.0357 | 61.0357 | 61.0357 | 61.0357 | 61.0357 | 61.0357 | 61.0357 | 61.0357 | 61.0357 | 61.0357
99% | 0 | 45.4171 | 60.3493 | 64.4168 | 49.9454 | 49.944 | 50.4092 | 50.9195 | 51.966 | 52.7179 | 53.1267 | 53.5745 | 53.9837 | 54.7216 | 55.6369 | 55.575 | 55.575 | 55.575 | 55.575 | 55.575 | 55.575 | 55.575 | 55.575 | 55.575 | 55.575 | 55.575 | 55.575 | 55.575 | 55.575 | 55.575 | 55.575 | 99% | 1.5127 | 50.6438 | 65.6059 | 69.5238 | 54.9358 | 54.9554 | 55.3587 | 56.4206 | 57.1326 | 57.829 | 58.6433 | 59.3985 | 60.1312 | 60.216 | 61.0709 | 60.4253 | 60.4253 | 60.4253 | 60.4253 | 60.4253 | 60.4253 | 60.4253 | 60.4253 | 60.4253 | 60.4253 | 60.4253 | 60.4253 | 60.4253 | 60.4253 | 60.4253 | 60.4253
98% | 0 | 44.9584 | 59.7397 | 63.7661 | 49.4409 | 49.4395 | 49.9 | 50.4051 | 51.4411 | 52.1854 | 52.5901 | 53.0334 | 53.4384 | 54.1688 | 55.0749 | 55.0136 | 55.0136 | 55.0136 | 55.0136 | 55.0136 | 55.0136 | 55.0136 | 55.0136 | 55.0136 | 55.0136 | 55.0136 | 55.0136 | 55.0136 | 55.0136 | 55.0136 | 55.0136 | 98% | 2.269 | 50.1322 | 64.9433 | 68.8216 | 54.3809 | 54.4003 | 54.7996 | 55.8507 | 56.5555 | 57.2449 | 58.0509 | 58.7985 | 59.5238 | 59.6078 | 60.454 | 59.8149 | 59.8149 | 59.8149 | 59.8149 | 59.8149 | 59.8149 | 59.8149 | 59.8149 | 59.8149 | 59.8149 | 59.8149 | 59.8149 | 59.8149 | 59.8149 | 59.8149 | 59.8149
97% | 0.37816 | 44.4996 | 59.1301 | 63.1154 | 48.9364 | 48.935 | 49.3908 | 49.8908 | 50.9162 | 51.6529 | 52.0534 | 52.4922 | 52.8931 | 53.6161 | 54.5129 | 54.4523 | 54.4523 | 54.4523 | 54.4523 | 54.4523 | 54.4523 | 54.4523 | 54.4523 | 54.4523 | 54.4523 | 54.4523 | 54.4523 | 54.4523 | 54.4523 | 54.4523 | 54.4523 | 97% | 3.7816 | 49.6207 | 64.2806 | 68.1193 | 53.826 | 53.8452 | 54.2404 | 55.2808 | 55.9784 | 56.6608 | 57.4586 | 58.1986 | 58.9164 | 58.9996 | 59.8372 | 59.2046 | 59.2046 | 59.2046 | 59.2046 | 59.2046 | 59.2046 | 59.2046 | 59.2046 | 59.2046 | 59.2046 | 59.2046 | 59.2046 | 59.2046 | 59.2046 | 59.2046 | 59.2046
95% | 2.269 | 43.5821 | 57.911 | 61.8141 | 47.9274 | 47.926 | 48.3724 | 48.8621 | 49.8664 | 50.5879 | 50.9802 | 51.4099 | 51.8026 | 52.5106 | 53.3889 | 53.3296 | 53.3296 | 53.3296 | 53.3296 | 53.3296 | 53.3296 | 53.3296 | 53.3296 | 53.3296 | 53.3296 | 53.3296 | 53.3296 | 53.3296 | 53.3296 | 53.3296 | 53.3296 | 95% | 6.0506 | 48.5976 | 62.9552 | 66.7148 | 52.7162 | 52.735 | 53.122 | 54.141 | 54.8242 | 55.4925 | 56.2738 | 56.9986 | 57.7016 | 57.7831 | 58.6034 | 57.9839 | 57.9839 | 57.9839 | 57.9839 | 57.9839 | 57.9839 | 57.9839 | 57.9839 | 57.9839 | 57.9839 | 57.9839 | 57.9839 | 57.9839 | 57.9839 | 57.9839 | 57.9839
90% | 5.6725 | 41.2883 | 54.863 | 58.5607 | 45.4049 | 45.4036 | 45.8265 | 46.2904 | 47.2418 | 47.9254 | 48.297 | 48.7041 | 49.0761 | 49.7469 | 50.579 | 50.5227 | 50.5227 | 50.5227 | 50.5227 | 50.5227 | 50.5227 | 50.5227 | 50.5227 | 50.5227 | 50.5227 | 50.5227 | 50.5227 | 50.5227 | 50.5227 | 50.5227 | 50.5227 | 90% | 16.2611 | 46.0398 | 59.6418 | 63.2035 | 49.9417 | 49.9594 | 50.3261 | 51.2915 | 51.9387 | 52.5718 | 53.3121 | 53.9987 | 54.6647 | 54.7419 | 55.519 | 54.9321 | 54.9321 | 54.9321 | 54.9321 | 54.9321 | 54.9321 | 54.9321 | 54.9321 | 54.9321 | 54.9321 | 54.9321 | 54.9321 | 54.9321 | 54.9321 | 54.9321 | 54.9321
85% | 15.8829 | 38.9945 | 51.8151 | 55.3073 | 42.8824 | 42.8812 | 43.2806 | 43.7187 | 44.6173 | 45.2629 | 45.6138 | 45.9983 | 46.3497 | 46.9832 | 47.769 | 47.7159 | 47.7159 | 47.7159 | 47.7159 | 47.7159 | 47.7159 | 47.7159 | 47.7159 | 47.7159 | 47.7159 | 47.7159 | 47.7159 | 47.7159 | 47.7159 | 47.7159 | 47.7159 | 85% | 26.4715 | 43.482 | 56.3283 | 59.6922 | 47.1671 | 47.1839 | 47.5302 | 48.442 | 49.0533 | 49.6512 | 50.3503 | 50.9987 | 51.6278 | 51.7006 | 52.4346 | 51.8803 | 51.8803 | 51.8803 | 51.8803 | 51.8803 | 51.8803 | 51.8803 | 51.8803 | 51.8803 | 51.8803 | 51.8803 | 51.8803 | 51.8803 | 51.8803 | 51.8803 | 51.8803
80% | 31.0095 | 36.7007 | 48.7671 | 52.0539 | 40.3599 | 40.3588 | 40.7347 | 41.147 | 41.9928 | 42.6003 | 42.9307 | 43.2925 | 43.6232 | 44.2194 | 44.9591 | 44.9091 | 44.9091 | 44.9091 | 44.9091 | 44.9091 | 44.9091 | 44.9091 | 44.9091 | 44.9091 | 44.9091 | 44.9091 | 44.9091 | 44.9091 | 44.9091 | 44.9091 | 44.9091 | 80% | 34.0348 | 40.9243 | 53.0149 | 56.1809 | 44.3926 | 44.4084 | 44.7343 | 45.5924 | 46.1678 | 46.7305 | 47.3885 | 47.9988 | 48.5908 | 48.6594 | 49.3502 | 48.8285 | 48.8285 | 48.8285 | 48.8285 | 48.8285 | 48.8285 | 48.8285 | 48.8285 | 48.8285 | 48.8285 | 48.8285 | 48.8285 | 48.8285 | 48.8285 | 48.8285 | 48.8285
75% | 72.9857 | 34.4069 | 45.7192 | 48.8006 | 37.8374 | 37.8363 | 38.1888 | 38.5754 | 39.3682 | 39.9378 | 40.2475 | 40.5868 | 40.8968 | 41.4557 | 42.1491 | 42.1023 | 42.1023 | 42.1023 | 42.1023 | 42.1023 | 42.1023 | 42.1023 | 42.1023 | 42.1023 | 42.1023 | 42.1023 | 42.1023 | 42.1023 | 42.1023 | 42.1023 | 42.1023 | 75% | 48.405 | 38.3665 | 49.7015 | 52.6696 | 41.618 | 41.6329 | 41.9384 | 42.7429 | 43.2823 | 43.8099 | 44.4267 | 44.9989 | 45.5539 | 45.6182 | 46.2658 | 45.7767 | 45.7767 | 45.7767 | 45.7767 | 45.7767 | 45.7767 | 45.7767 | 45.7767 | 45.7767 | 45.7767 | 45.7767 | 45.7767 | 45.7767 | 45.7767 | 45.7767 | 45.7767
70% | 150.5094 | 32.1131 | 42.6712 | 45.5472 | 35.3149 | 35.3139 | 35.6429 | 36.0037 | 36.7437 | 37.2753 | 37.5643 | 37.881 | 38.1703 | 38.692 | 39.3392 | 39.2955 | 39.2955 | 39.2955 | 39.2955 | 39.2955 | 39.2955 | 39.2955 | 39.2955 | 39.2955 | 39.2955 | 39.2955 | 39.2955 | 39.2955 | 39.2955 | 39.2955 | 39.2955 | 70% | 76.3892 | 35.8087 | 46.388 | 49.1583 | 38.8435 | 38.8573 | 39.1425 | 39.8934 | 40.3968 | 40.8892 | 41.4649 | 41.999 | 42.517 | 42.577 | 43.1815 | 42.725 | 42.725 | 42.725 | 42.725 | 42.725 | 42.725 | 42.725 | 42.725 | 42.725 | 42.725 | 42.725 | 42.725 | 42.725 | 42.725 | 42.725 | 42.725
65% | 359.6342 | 29.8193 | 39.6233 | 42.2938 | 32.7924 | 32.7915 | 33.0969 | 33.432 | 34.1191 | 34.6128 | 34.8812 | 35.1752 | 35.4439 | 35.9283 | 36.5293 | 36.4886 | 36.4886 | 36.4886 | 36.4886 | 36.4886 | 36.4886 | 36.4886 | 36.4886 | 36.4886 | 36.4886 | 36.4886 | 36.4886 | 36.4886 | 36.4886 | 36.4886 | 36.4886 | 65% | 114.2056 | 33.251 | 43.0746 | 45.647 | 36.069 | 36.0818 | 36.3466 | 37.0439 | 37.5113 | 37.9686 | 38.5032 | 38.999 | 39.4801 | 39.5358 | 40.0971 | 39.6732 | 39.6732 | 39.6732 | 39.6732 | 39.6732 | 39.6732 | 39.6732 | 39.6732 | 39.6732 | 39.6732 | 39.6732 | 39.6732 | 39.6732 | 39.6732 | 39.6732 | 39.6732
60% | 689.7717 | 27.5255 | 36.5753 | 39.0405 | 30.2699 | 30.2691 | 30.551 | 30.8603 | 31.4946 | 31.9503 | 32.198 | 32.4694 | 32.7174 | 33.1646 | 33.7193 | 33.6818 | 33.6818 | 33.6818 | 33.6818 | 33.6818 | 33.6818 | 33.6818 | 33.6818 | 33.6818 | 33.6818 | 33.6818 | 33.6818 | 33.6818 | 33.6818 | 33.6818 | 33.6818 | 60% | 178.1154 | 30.6932 | 39.7612 | 42.1357 | 33.2944 | 33.3063 | 33.5508 | 34.1943 | 34.6258 | 35.0479 | 35.5414 | 35.9991 | 36.4431 | 36.4946 | 37.0127 | 36.6214 | 36.6214 | 36.6214 | 36.6214 | 36.6214 | 36.6214 | 36.6214 | 36.6214 | 36.6214 | 36.6214 | 36.6214 | 36.6214 | 36.6214 | 36.6214 | 36.6214 | 36.6214
55% | 1095.5419 | 25.2317 | 33.5274 | 35.7871 | 27.7474 | 27.7467 | 28.0051 | 28.2886 | 28.87 | 29.2877 | 29.5148 | 29.7636 | 29.991 | 30.4009 | 30.9094 | 30.875 | 30.875 | 30.875 | 30.875 | 30.875 | 30.875 | 30.875 | 30.875 | 30.875 | 30.875 | 30.875 | 30.875 | 30.875 | 30.875 | 30.875 | 30.875 | 55% | 311.6074 | 28.1354 | 36.4477 | 38.6243 | 30.5199 | 30.5308 | 30.7549 | 31.3448 | 31.7403 | 32.1272 | 32.5796 | 32.9992 | 33.4062 | 33.4534 | 33.9283 | 33.5696 | 33.5696 | 33.5696 | 33.5696 | 33.5696 | 33.5696 | 33.5696 | 33.5696 | 33.5696 | 33.5696 | 33.5696 | 33.5696 | 33.5696 | 33.5696 | 33.5696 | 33.5696
50% | 1666.1918 | 22.9379 | 30.4794 | 32.5337 | 25.2249 | 25.2242 | 25.4592 | 25.7169 | 26.2455 | 26.6252 | 26.8317 | 27.0578 | 27.2645 | 27.6372 | 28.0994 | 28.0682 | 28.0682 | 28.0682 | 28.0682 | 28.0682 | 28.0682 | 28.0682 | 28.0682 | 28.0682 | 28.0682 | 28.0682 | 28.0682 | 28.0682 | 28.0682 | 28.0682 | 28.0682 | 50% | 636.0723 | 25.5777 | 33.1343 | 35.113 | 27.7454 | 27.7552 | 27.959 | 28.4953 | 28.8549 | 29.2066 | 29.6178 | 29.9993 | 30.3693 | 30.4121 | 30.8439 | 30.5178 | 30.5178 | 30.5178 | 30.5178 | 30.5178 | 30.5178 | 30.5178 | 30.5178 | 30.5178 | 30.5178 | 30.5178 | 30.5178 | 30.5178 | 30.5178 | 30.5178 | 30.5178
45% | 2506.0947 | 20.6442 | 27.4315 | 29.2803 | 22.7024 | 22.7018 | 22.9133 | 23.1452 | 23.6209 | 23.9627 | 24.1485 | 24.3521 | 24.5381 | 24.8734 | 25.2895 | 25.2614 | 25.2614 | 25.2614 | 25.2614 | 25.2614 | 25.2614 | 25.2614 | 25.2614 | 25.2614 | 25.2614 | 25.2614 | 25.2614 | 25.2614 | 25.2614 | 25.2614 | 25.2614 | 45% | 1179.4944 | 23.0199 | 29.8209 | 31.6017 | 24.9708 | 24.9797 | 25.1631 | 25.6457 | 25.9694 | 26.2859 | 26.656 | 26.9993 | 27.3323 | 27.3709 | 27.7595 | 27.466 | 27.466 | 27.466 | 27.466 | 27.466 | 27.466 | 27.466 | 27.466 | 27.466 | 27.466 | 27.466 | 27.466 | 27.466 | 27.466 | 27.466 | 27.466
40% | 3164.4787 | 18.3504 | 24.3836 | 26.027 | 20.1799 | 20.1794 | 20.3673 | 20.5735 | 20.9964 | 21.3002 | 21.4653 | 21.6463 | 21.8116 | 22.1097 | 22.4795 | 22.4546 | 22.4546 | 22.4546 | 22.4546 | 22.4546 | 22.4546 | 22.4546 | 22.4546 | 22.4546 | 22.4546 | 22.4546 | 22.4546 | 22.4546 | 22.4546 | 22.4546 | 22.4546 | 40% | 1808.3816 | 20.4621 | 26.5075 | 28.0904 | 22.1963 | 22.2042 | 22.3672 | 22.7962 | 23.0839 | 23.3653 | 23.6942 | 23.9994 | 24.2954 | 24.3297 | 24.6751 | 24.4143 | 24.4143 | 24.4143 | 24.4143 | 24.4143 | 24.4143 | 24.4143 | 24.4143 | 24.4143 | 24.4143 | 24.4143 | 24.4143 | 24.4143 | 24.4143 | 24.4143 | 24.4143
35% | 3551.3408 | 16.0566 | 21.3356 | 22.7736 | 17.6575 | 17.657 | 17.8214 | 18.0018 | 18.3718 | 18.6376 | 18.7822 | 18.9405 | 19.0852 | 19.346 | 19.6696 | 19.6477 | 19.6477 | 19.6477 | 19.6477 | 19.6477 | 19.6477 | 19.6477 | 19.6477 | 19.6477 | 19.6477 | 19.6477 | 19.6477 | 19.6477 | 19.6477 | 19.6477 | 19.6477 | 35% | 2779.1293 | 17.9044 | 23.194 | 24.5791 | 19.4218 | 19.4287 | 19.5713 | 19.9467 | 20.1984 | 20.4446 | 20.7325 | 20.9995 | 21.2585 | 21.2885 | 21.5907 | 21.3625 | 21.3625 | 21.3625 | 21.3625 | 21.3625 | 21.3625 | 21.3625 | 21.3625 | 21.3625 | 21.3625 | 21.3625 | 21.3625 | 21.3625 | 21.3625 | 21.3625 | 21.3625
30% | 3758.953 | 13.7628 | 18.2877 | 19.5202 | 15.135 | 15.1345 | 15.2755 | 15.4301 | 15.7473 | 15.9751 | 16.099 | 16.2347 | 16.3587 | 16.5823 | 16.8597 | 16.8409 | 16.8409 | 16.8409 | 16.8409 | 16.8409 | 16.8409 | 16.8409 | 16.8409 | 16.8409 | 16.8409 | 16.8409 | 16.8409 | 16.8409 | 16.8409 | 16.8409 | 16.8409 | 30% | 3814.165 | 15.3466 | 19.8806 | 21.0678 | 16.6472 | 16.6531 | 16.7754 | 17.0972 | 17.3129 | 17.5239 | 17.7707 | 17.9996 | 18.2216 | 18.2473 | 18.5063 | 18.3107 | 18.3107 | 18.3107 | 18.3107 | 18.3107 | 18.3107 | 18.3107 | 18.3107 | 18.3107 | 18.3107 | 18.3107 | 18.3107 | 18.3107 | 18.3107 | 18.3107 | 18.3107
25% | 3926.4798 | 11.469 | 15.2397 | 16.2669 | 12.6125 | 12.6121 | 12.7296 | 12.8585 | 13.1227 | 13.3126 | 13.4158 | 13.5289 | 13.6323 | 13.8186 | 14.0497 | 14.0341 | 14.0341 | 14.0341 | 14.0341 | 14.0341 | 14.0341 | 14.0341 | 14.0341 | 14.0341 | 14.0341 | 14.0341 | 14.0341 | 14.0341 | 14.0341 | 14.0341 | 14.0341 | 25% | 4166.9923 | 12.7888 | 16.5672 | 17.5565 | 13.8727 | 13.8776 | 13.9795 | 14.2476 | 14.4274 | 14.6033 | 14.8089 | 14.9996 | 15.1846 | 15.2061 | 15.4219 | 15.2589 | 15.2589 | 15.2589 | 15.2589 | 15.2589 | 15.2589 | 15.2589 | 15.2589 | 15.2589 | 15.2589 | 15.2589 | 15.2589 | 15.2589 | 15.2589 | 15.2589 | 15.2589
20% | 4050.5177 | 9.1752 | 12.1918 | 13.0135 | 10.09 | 10.0897 | 10.1837 | 10.2868 | 10.4982 | 10.6501 | 10.7327 | 10.8231 | 10.9058 | 11.0549 | 11.2398 | 11.2273 | 11.2273 | 11.2273 | 11.2273 | 11.2273 | 11.2273 | 11.2273 | 11.2273 | 11.2273 | 11.2273 | 11.2273 | 11.2273 | 11.2273 | 11.2273 | 11.2273 | 11.2273 | 20% | 4282.7105 | 10.2311 | 13.2537 | 14.0452 | 11.0981 | 11.1021 | 11.1836 | 11.3981 | 11.5419 | 11.6826 | 11.8471 | 11.9997 | 12.1477 | 12.1649 | 12.3376 | 12.2071 | 12.2071 | 12.2071 | 12.2071 | 12.2071 | 12.2071 | 12.2071 | 12.2071 | 12.2071 | 12.2071 | 12.2071 | 12.2071 | 12.2071 | 12.2071 | 12.2071 | 12.2071
15% | 4152.622 | 6.8814 | 9.1438 | 9.7601 | 7.5675 | 7.5673 | 7.6378 | 7.7151 | 7.8736 | 7.9876 | 8.0495 | 8.1174 | 8.1794 | 8.2911 | 8.4298 | 8.4205 | 8.4205 | 8.4205 | 8.4205 | 8.4205 | 8.4205 | 8.4205 | 8.4205 | 8.4205 | 8.4205 | 8.4205 | 8.4205 | 8.4205 | 8.4205 | 8.4205 | 8.4205 | 15% | 4364.7722 | 7.6733 | 9.9403 | 10.5339 | 8.3236 | 8.3266 | 8.3877 | 8.5486 | 8.6565 | 8.762 | 8.8853 | 8.9998 | 9.1108 | 9.1236 | 9.2532 | 9.1553 | 9.1553 | 9.1553 | 9.1553 | 9.1553 | 9.1553 | 9.1553 | 9.1553 | 9.1553 | 9.1553 | 9.1553 | 9.1553 | 9.1553 | 9.1553 | 9.1553 | 9.1553
10% | 4248.2976 | 4.5876 | 6.0959 | 6.5067 | 5.045 | 5.0448 | 5.0918 | 5.1434 | 5.2491 | 5.325 | 5.3663 | 5.4116 | 5.4529 | 5.5274 | 5.6199 | 5.6136 | 5.6136 | 5.6136 | 5.6136 | 5.6136 | 5.6136 | 5.6136 | 5.6136 | 5.6136 | 5.6136 | 5.6136 | 5.6136 | 5.6136 | 5.6136 | 5.6136 | 5.6136 | 10% | 4391.6218 | 5.1155 | 6.6269 | 7.0226 | 5.5491 | 5.551 | 5.5918 | 5.6991 | 5.771 | 5.8413 | 5.9236 | 5.9999 | 6.0739 | 6.0824 | 6.1688 | 6.1036 | 6.1036 | 6.1036 | 6.1036 | 6.1036 | 6.1036 | 6.1036 | 6.1036 | 6.1036 | 6.1036 | 6.1036 | 6.1036 | 6.1036 | 6.1036 | 6.1036 | 6.1036
5% | 4361.7469 | 2.2938 | 3.0479 | 3.2534 | 2.5225 | 2.5224 | 2.5459 | 2.5717 | 2.6245 | 2.6625 | 2.6832 | 2.7058 | 2.7265 | 2.7637 | 2.8099 | 2.8068 | 2.8068 | 2.8068 | 2.8068 | 2.8068 | 2.8068 | 2.8068 | 2.8068 | 2.8068 | 2.8068 | 2.8068 | 2.8068 | 2.8068 | 2.8068 | 2.8068 | 2.8068 | 5% | 4391.6218 | 2.5578 | 3.3134 | 3.5113 | 2.7745 | 2.7755 | 2.7959 | 2.8495 | 2.8855 | 2.9207 | 2.9618 | 2.9999 | 3.0369 | 3.0412 | 3.0844 | 3.0518 | 3.0518 | 3.0518 | 3.0518 | 3.0518 | 3.0518 | 3.0518 | 3.0518 | 3.0518 | 3.0518 | 3.0518 | 3.0518 | 3.0518 | 3.0518 | 3.0518 | 3.0518
9.992e-14% | 4391.6218 | 4.5839e-14 | 6.091e-14 | 6.5015e-14 | 5.041e-14 | 5.0408e-14 | 5.0878e-14 | 5.1393e-14 | 5.2449e-14 | 5.3208e-14 | 5.362e-14 | 5.4072e-14 | 5.4485e-14 | 5.523e-14 | 5.6154e-14 | 5.6092e-14 | 5.6092e-14 | 5.6092e-14 | 5.6092e-14 | 5.6092e-14 | 5.6092e-14 | 5.6092e-14 | 5.6092e-14 | 5.6092e-14 | 5.6092e-14 | 5.6092e-14 | 5.6092e-14 | 5.6092e-14 | 5.6092e-14 | 5.6092e-14 | 5.6092e-14 | 9.992e-14% | 4391.6218 | 5.1114e-14 | 6.6216e-14 | 7.017e-14 | 5.5446e-14 | 5.5466e-14 | 5.5873e-14 | 5.6945e-14 | 5.7664e-14 | 5.8366e-14 | 5.9188e-14 | 5.9951e-14 | 6.069e-14 | 6.0776e-14 | 6.1638e-14 | 6.0987e-14 | 6.0987e-14 | 6.0987e-14 | 6.0987e-14 | 6.0987e-14 | 6.0987e-14 | 6.0987e-14 | 6.0987e-14 | 6.0987e-14 | 6.0987e-14 | 6.0987e-14 | 6.0987e-14 | 6.0987e-14 | 6.0987e-14 | 6.0987e-14 | 6.0987e-14
Option 5
Winter Season | [31 empty] | Winter Season
P50 | [31 empty] | P10
% of MD | Winter - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Winter - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 40.358 | 56.0239 | 60.0964 | 31.7906 | 32.3321 | 33.2643 | 35.3852 | 36.8049 | 38.6034 | 39.5369 | 40.3582 | 38.845 | 40.6185 | 43.4066 | 41.2908 | 41.2908 | 41.2908 | 41.2908 | 41.2908 | 41.2908 | 41.2908 | 41.2908 | 41.2908 | 41.2908 | 41.2908 | 41.2908 | 41.2908 | 41.2908 | 41.2908 | 41.2908 | 100% | 0 | 43.208 | 58.6763 | 62.9078 | 34.5625 | 34.9783 | 35.8903 | 38.0443 | 39.2204 | 41.4608 | 48.2709 | 42.6566 | 41.5585 | 43.0408 | 46.2827 | 44.0883 | 44.0883 | 44.0883 | 44.0883 | 44.0883 | 44.0883 | 44.0883 | 44.0883 | 44.0883 | 44.0883 | 44.0883 | 44.0883 | 44.0883 | 44.0883 | 44.0883 | 44.0883
99% | 1.486 | 39.9544 | 55.4636 | 59.4955 | 31.4727 | 32.0087 | 32.9316 | 35.0313 | 36.4368 | 38.2174 | 39.1416 | 39.9546 | 38.4565 | 40.2123 | 42.9725 | 40.8779 | 40.8779 | 40.8779 | 40.8779 | 40.8779 | 40.8779 | 40.8779 | 40.8779 | 40.8779 | 40.8779 | 40.8779 | 40.8779 | 40.8779 | 40.8779 | 40.8779 | 40.8779 | 99% | 1.486 | 42.7759 | 58.0895 | 62.2787 | 34.2169 | 34.6285 | 35.5314 | 37.6639 | 38.8282 | 41.0462 | 47.7882 | 42.2301 | 41.1429 | 42.6104 | 45.8199 | 43.6475 | 43.6475 | 43.6475 | 43.6475 | 43.6475 | 43.6475 | 43.6475 | 43.6475 | 43.6475 | 43.6475 | 43.6475 | 43.6475 | 43.6475 | 43.6475 | 43.6475 | 43.6475
98% | 3.2692 | 39.5508 | 54.9034 | 58.8945 | 31.1548 | 31.6854 | 32.599 | 34.6775 | 36.0688 | 37.8313 | 38.7462 | 39.5511 | 38.0681 | 39.8061 | 42.5384 | 40.465 | 40.465 | 40.465 | 40.465 | 40.465 | 40.465 | 40.465 | 40.465 | 40.465 | 40.465 | 40.465 | 40.465 | 40.465 | 40.465 | 40.465 | 40.465 | 98% | 3.2692 | 42.3438 | 57.5027 | 61.6497 | 33.8713 | 34.2787 | 35.1725 | 37.2834 | 38.436 | 40.6316 | 47.3055 | 41.8035 | 40.7273 | 42.18 | 45.3571 | 43.2066 | 43.2066 | 43.2066 | 43.2066 | 43.2066 | 43.2066 | 43.2066 | 43.2066 | 43.2066 | 43.2066 | 43.2066 | 43.2066 | 43.2066 | 43.2066 | 43.2066 | 43.2066
97% | 6.8356 | 39.1473 | 54.3431 | 58.2935 | 30.8369 | 31.3621 | 32.2664 | 34.3236 | 35.7007 | 37.4453 | 38.3508 | 39.1475 | 37.6796 | 39.3999 | 42.1044 | 40.0521 | 40.0521 | 40.0521 | 40.0521 | 40.0521 | 40.0521 | 40.0521 | 40.0521 | 40.0521 | 40.0521 | 40.0521 | 40.0521 | 40.0521 | 40.0521 | 40.0521 | 40.0521 | 97% | 6.8356 | 41.9118 | 56.916 | 61.0206 | 33.5257 | 33.9289 | 34.8136 | 36.903 | 38.0438 | 40.2169 | 46.8228 | 41.3769 | 40.3117 | 41.7496 | 44.8943 | 42.7657 | 42.7657 | 42.7657 | 42.7657 | 42.7657 | 42.7657 | 42.7657 | 42.7657 | 42.7657 | 42.7657 | 42.7657 | 42.7657 | 42.7657 | 42.7657 | 42.7657 | 42.7657
95% | 17.5347 | 38.3401 | 53.2227 | 57.0916 | 30.2011 | 30.7155 | 31.6011 | 33.6159 | 34.9646 | 36.6732 | 37.5601 | 38.3403 | 36.9027 | 38.5875 | 41.2362 | 39.2262 | 39.2262 | 39.2262 | 39.2262 | 39.2262 | 39.2262 | 39.2262 | 39.2262 | 39.2262 | 39.2262 | 39.2262 | 39.2262 | 39.2262 | 39.2262 | 39.2262 | 39.2262 | 95% | 17.5347 | 41.0476 | 55.7425 | 59.7624 | 32.8344 | 33.2294 | 34.0958 | 36.1421 | 37.2594 | 39.3877 | 45.8573 | 40.5238 | 39.4806 | 40.8888 | 43.9686 | 41.8839 | 41.8839 | 41.8839 | 41.8839 | 41.8839 | 41.8839 | 41.8839 | 41.8839 | 41.8839 | 41.8839 | 41.8839 | 41.8839 | 41.8839 | 41.8839 | 41.8839 | 41.8839
90% | 78.7576 | 36.3222 | 50.4215 | 54.0868 | 28.6116 | 29.0988 | 29.9379 | 31.8467 | 33.1244 | 34.7431 | 35.5833 | 36.3224 | 34.9605 | 36.5566 | 39.0659 | 37.1617 | 37.1617 | 37.1617 | 37.1617 | 37.1617 | 37.1617 | 37.1617 | 37.1617 | 37.1617 | 37.1617 | 37.1617 | 37.1617 | 37.1617 | 37.1617 | 37.1617 | 37.1617 | 90% | 78.7576 | 38.8872 | 52.8086 | 56.617 | 31.1063 | 31.4804 | 32.3013 | 34.2399 | 35.2984 | 37.3147 | 43.4438 | 38.391 | 37.4026 | 38.7368 | 41.6545 | 39.6795 | 39.6795 | 39.6795 | 39.6795 | 39.6795 | 39.6795 | 39.6795 | 39.6795 | 39.6795 | 39.6795 | 39.6795 | 39.6795 | 39.6795 | 39.6795 | 39.6795 | 39.6795
85% | 236.8672 | 34.3043 | 47.6203 | 51.082 | 27.022 | 27.4822 | 28.2746 | 30.0774 | 31.2842 | 32.8129 | 33.6064 | 34.3045 | 33.0182 | 34.5257 | 36.8956 | 35.0972 | 35.0972 | 35.0972 | 35.0972 | 35.0972 | 35.0972 | 35.0972 | 35.0972 | 35.0972 | 35.0972 | 35.0972 | 35.0972 | 35.0972 | 35.0972 | 35.0972 | 35.0972 | 85% | 236.8672 | 36.7268 | 49.8748 | 53.4716 | 29.3782 | 29.7315 | 30.5067 | 32.3377 | 33.3373 | 35.2417 | 41.0303 | 36.2581 | 35.3247 | 36.5847 | 39.3403 | 37.4751 | 37.4751 | 37.4751 | 37.4751 | 37.4751 | 37.4751 | 37.4751 | 37.4751 | 37.4751 | 37.4751 | 37.4751 | 37.4751 | 37.4751 | 37.4751 | 37.4751 | 37.4751
80% | 497.5104 | 32.2864 | 44.8191 | 48.0771 | 25.4325 | 25.8656 | 26.6114 | 28.3081 | 29.4439 | 30.8827 | 31.6296 | 32.2866 | 31.076 | 32.4948 | 34.7252 | 33.0326 | 33.0326 | 33.0326 | 33.0326 | 33.0326 | 33.0326 | 33.0326 | 33.0326 | 33.0326 | 33.0326 | 33.0326 | 33.0326 | 33.0326 | 33.0326 | 33.0326 | 33.0326 | 80% | 497.5104 | 34.5664 | 46.941 | 50.3262 | 27.65 | 27.9826 | 28.7122 | 30.4355 | 31.3763 | 33.1686 | 38.6167 | 34.1253 | 33.2468 | 34.4327 | 37.0262 | 35.2707 | 35.2707 | 35.2707 | 35.2707 | 35.2707 | 35.2707 | 35.2707 | 35.2707 | 35.2707 | 35.2707 | 35.2707 | 35.2707 | 35.2707 | 35.2707 | 35.2707 | 35.2707
75% | 803.6248 | 30.2685 | 42.0179 | 45.0723 | 23.843 | 24.249 | 24.9482 | 26.5389 | 27.6037 | 28.9526 | 29.6527 | 30.2687 | 29.1337 | 30.4638 | 32.5549 | 30.9681 | 30.9681 | 30.9681 | 30.9681 | 30.9681 | 30.9681 | 30.9681 | 30.9681 | 30.9681 | 30.9681 | 30.9681 | 30.9681 | 30.9681 | 30.9681 | 30.9681 | 30.9681 | 75% | 803.6248 | 32.406 | 44.0072 | 47.1809 | 25.9219 | 26.2337 | 26.9177 | 28.5332 | 29.4153 | 31.0956 | 36.2032 | 31.9925 | 31.1689 | 32.2806 | 34.7121 | 33.0663 | 33.0663 | 33.0663 | 33.0663 | 33.0663 | 33.0663 | 33.0663 | 33.0663 | 33.0663 | 33.0663 | 33.0663 | 33.0663 | 33.0663 | 33.0663 | 33.0663 | 33.0663
70% | 1155.2107 | 28.2506 | 39.2167 | 42.0675 | 22.2534 | 22.6324 | 23.285 | 24.7696 | 25.7634 | 27.0224 | 27.6759 | 28.2508 | 27.1915 | 28.4329 | 30.3846 | 28.9035 | 28.9035 | 28.9035 | 28.9035 | 28.9035 | 28.9035 | 28.9035 | 28.9035 | 28.9035 | 28.9035 | 28.9035 | 28.9035 | 28.9035 | 28.9035 | 28.9035 | 28.9035 | 70% | 1155.2107 | 30.2456 | 41.0734 | 44.0355 | 24.1938 | 24.4848 | 25.1232 | 26.631 | 27.4543 | 29.0225 | 33.7896 | 29.8596 | 29.0909 | 30.1286 | 32.3979 | 30.8618 | 30.8618 | 30.8618 | 30.8618 | 30.8618 | 30.8618 | 30.8618 | 30.8618 | 30.8618 | 30.8618 | 30.8618 | 30.8618 | 30.8618 | 30.8618 | 30.8618 | 30.8618
65% | 1553.1596 | 26.2327 | 36.4155 | 39.0627 | 20.6639 | 21.0158 | 21.6218 | 23.0004 | 23.9232 | 25.0922 | 25.699 | 26.2328 | 25.2492 | 26.402 | 28.2143 | 26.839 | 26.839 | 26.839 | 26.839 | 26.839 | 26.839 | 26.839 | 26.839 | 26.839 | 26.839 | 26.839 | 26.839 | 26.839 | 26.839 | 26.839 | 26.839 | 65% | 1553.1596 | 28.0852 | 38.1396 | 40.8901 | 22.4657 | 22.7359 | 23.3287 | 24.7288 | 25.4933 | 26.9495 | 31.3761 | 27.7268 | 27.013 | 27.9766 | 30.0838 | 28.6574 | 28.6574 | 28.6574 | 28.6574 | 28.6574 | 28.6574 | 28.6574 | 28.6574 | 28.6574 | 28.6574 | 28.6574 | 28.6574 | 28.6574 | 28.6574 | 28.6574 | 28.6574
60% | 2026.2996 | 24.2148 | 33.6143 | 36.0579 | 19.0744 | 19.3992 | 19.9586 | 21.2311 | 22.0829 | 23.162 | 23.7222 | 24.2149 | 23.307 | 24.3711 | 26.0439 | 24.7745 | 24.7745 | 24.7745 | 24.7745 | 24.7745 | 24.7745 | 24.7745 | 24.7745 | 24.7745 | 24.7745 | 24.7745 | 24.7745 | 24.7745 | 24.7745 | 24.7745 | 24.7745 | 60% | 2026.2996 | 25.9248 | 35.2058 | 37.7447 | 20.7375 | 20.987 | 21.5342 | 22.8266 | 23.5322 | 24.8765 | 28.9625 | 25.594 | 24.9351 | 25.8245 | 27.7696 | 26.453 | 26.453 | 26.453 | 26.453 | 26.453 | 26.453 | 26.453 | 26.453 | 26.453 | 26.453 | 26.453 | 26.453 | 26.453 | 26.453 | 26.453 | 26.453
55% | 2598.4068 | 22.1969 | 30.8131 | 33.053 | 17.4848 | 17.7826 | 18.2954 | 19.4619 | 20.2427 | 21.2319 | 21.7453 | 22.197 | 21.3647 | 22.3402 | 23.8736 | 22.7099 | 22.7099 | 22.7099 | 22.7099 | 22.7099 | 22.7099 | 22.7099 | 22.7099 | 22.7099 | 22.7099 | 22.7099 | 22.7099 | 22.7099 | 22.7099 | 22.7099 | 22.7099 | 55% | 2598.4068 | 23.7644 | 32.272 | 34.5993 | 19.0094 | 19.238 | 19.7397 | 20.9244 | 21.5712 | 22.8034 | 26.549 | 23.4611 | 22.8572 | 23.6725 | 25.4555 | 24.2486 | 24.2486 | 24.2486 | 24.2486 | 24.2486 | 24.2486 | 24.2486 | 24.2486 | 24.2486 | 24.2486 | 24.2486 | 24.2486 | 24.2486 | 24.2486 | 24.2486 | 24.2486
50% | 3233.5201 | 20.179 | 28.0119 | 30.0482 | 15.8953 | 16.166 | 16.6321 | 17.6926 | 18.4024 | 19.3017 | 19.7685 | 20.1791 | 19.4225 | 20.3092 | 21.7033 | 20.6454 | 20.6454 | 20.6454 | 20.6454 | 20.6454 | 20.6454 | 20.6454 | 20.6454 | 20.6454 | 20.6454 | 20.6454 | 20.6454 | 20.6454 | 20.6454 | 20.6454 | 20.6454 | 50% | 3233.5201 | 21.604 | 29.3381 | 31.4539 | 17.2813 | 17.4891 | 17.9451 | 19.0222 | 19.6102 | 20.7304 | 24.1354 | 21.3283 | 20.7792 | 21.5204 | 23.1414 | 22.0442 | 22.0442 | 22.0442 | 22.0442 | 22.0442 | 22.0442 | 22.0442 | 22.0442 | 22.0442 | 22.0442 | 22.0442 | 22.0442 | 22.0442 | 22.0442 | 22.0442 | 22.0442
45% | 3775.313 | 18.1611 | 25.2107 | 27.0434 | 14.3058 | 14.5494 | 14.9689 | 15.9233 | 16.5622 | 17.3715 | 17.7916 | 18.1612 | 17.4802 | 18.2783 | 19.533 | 18.5809 | 18.5809 | 18.5809 | 18.5809 | 18.5809 | 18.5809 | 18.5809 | 18.5809 | 18.5809 | 18.5809 | 18.5809 | 18.5809 | 18.5809 | 18.5809 | 18.5809 | 18.5809 | 45% | 3775.313 | 19.4436 | 26.4043 | 28.3085 | 15.5531 | 15.7402 | 16.1506 | 17.1199 | 17.6492 | 18.6573 | 21.7219 | 19.1955 | 18.7013 | 19.3684 | 20.8272 | 19.8398 | 19.8398 | 19.8398 | 19.8398 | 19.8398 | 19.8398 | 19.8398 | 19.8398 | 19.8398 | 19.8398 | 19.8398 | 19.8398 | 19.8398 | 19.8398 | 19.8398 | 19.8398
40% | 4072.8088 | 16.1432 | 22.4095 | 24.0386 | 12.7162 | 12.9328 | 13.3057 | 14.1541 | 14.722 | 15.4414 | 15.8148 | 16.1433 | 15.538 | 16.2474 | 17.3626 | 16.5163 | 16.5163 | 16.5163 | 16.5163 | 16.5163 | 16.5163 | 16.5163 | 16.5163 | 16.5163 | 16.5163 | 16.5163 | 16.5163 | 16.5163 | 16.5163 | 16.5163 | 16.5163 | 40% | 4072.8088 | 17.2832 | 23.4705 | 25.1631 | 13.825 | 13.9913 | 14.3561 | 15.2177 | 15.6882 | 16.5843 | 19.3084 | 17.0627 | 16.6234 | 17.2163 | 18.5131 | 17.6353 | 17.6353 | 17.6353 | 17.6353 | 17.6353 | 17.6353 | 17.6353 | 17.6353 | 17.6353 | 17.6353 | 17.6353 | 17.6353 | 17.6353 | 17.6353 | 17.6353 | 17.6353
35% | 4198.821 | 14.1253 | 19.6083 | 21.0337 | 11.1267 | 11.3162 | 11.6425 | 12.3848 | 12.8817 | 13.5112 | 13.8379 | 14.1254 | 13.5957 | 14.2165 | 15.1923 | 14.4518 | 14.4518 | 14.4518 | 14.4518 | 14.4518 | 14.4518 | 14.4518 | 14.4518 | 14.4518 | 14.4518 | 14.4518 | 14.4518 | 14.4518 | 14.4518 | 14.4518 | 14.4518 | 35% | 4198.821 | 15.1228 | 20.5367 | 22.0177 | 12.0969 | 12.2424 | 12.5616 | 13.3155 | 13.7271 | 14.5113 | 16.8948 | 14.9298 | 14.5455 | 15.0643 | 16.199 | 15.4309 | 15.4309 | 15.4309 | 15.4309 | 15.4309 | 15.4309 | 15.4309 | 15.4309 | 15.4309 | 15.4309 | 15.4309 | 15.4309 | 15.4309 | 15.4309 | 15.4309 | 15.4309
30% | 4271.3374 | 12.1074 | 16.8072 | 18.0289 | 9.5372 | 9.6996 | 9.9793 | 10.6156 | 11.0415 | 11.581 | 11.8611 | 12.1075 | 11.6535 | 12.1855 | 13.022 | 12.3872 | 12.3872 | 12.3872 | 12.3872 | 12.3872 | 12.3872 | 12.3872 | 12.3872 | 12.3872 | 12.3872 | 12.3872 | 12.3872 | 12.3872 | 12.3872 | 12.3872 | 12.3872 | 30% | 4271.3374 | 12.9624 | 17.6029 | 18.8723 | 10.3688 | 10.4935 | 10.7671 | 11.4133 | 11.7661 | 12.4382 | 14.4813 | 12.797 | 12.4675 | 12.9123 | 13.8848 | 13.2265 | 13.2265 | 13.2265 | 13.2265 | 13.2265 | 13.2265 | 13.2265 | 13.2265 | 13.2265 | 13.2265 | 13.2265 | 13.2265 | 13.2265 | 13.2265 | 13.2265 | 13.2265
25% | 4321.8611 | 10.0895 | 14.006 | 15.0241 | 7.9477 | 8.083 | 8.3161 | 8.8463 | 9.2012 | 9.6509 | 9.8842 | 10.0896 | 9.7112 | 10.1546 | 10.8516 | 10.3227 | 10.3227 | 10.3227 | 10.3227 | 10.3227 | 10.3227 | 10.3227 | 10.3227 | 10.3227 | 10.3227 | 10.3227 | 10.3227 | 10.3227 | 10.3227 | 10.3227 | 10.3227 | 25% | 4321.8611 | 10.802 | 14.6691 | 15.727 | 8.6406 | 8.7446 | 8.9726 | 9.5111 | 9.8051 | 10.3652 | 12.0677 | 10.6642 | 10.3896 | 10.7602 | 11.5707 | 11.0221 | 11.0221 | 11.0221 | 11.0221 | 11.0221 | 11.0221 | 11.0221 | 11.0221 | 11.0221 | 11.0221 | 11.0221 | 11.0221 | 11.0221 | 11.0221 | 11.0221 | 11.0221
20% | 4353.067 | 8.0716 | 11.2048 | 12.0193 | 6.3581 | 6.4664 | 6.6529 | 7.077 | 7.361 | 7.7207 | 7.9074 | 8.0716 | 7.769 | 8.1237 | 8.6813 | 8.2582 | 8.2582 | 8.2582 | 8.2582 | 8.2582 | 8.2582 | 8.2582 | 8.2582 | 8.2582 | 8.2582 | 8.2582 | 8.2582 | 8.2582 | 8.2582 | 8.2582 | 8.2582 | 20% | 4353.067 | 8.6416 | 11.7353 | 12.5816 | 6.9125 | 6.9957 | 7.1781 | 7.6089 | 7.8441 | 8.2922 | 9.6542 | 8.5313 | 8.3117 | 8.6082 | 9.2565 | 8.8177 | 8.8177 | 8.8177 | 8.8177 | 8.8177 | 8.8177 | 8.8177 | 8.8177 | 8.8177 | 8.8177 | 8.8177 | 8.8177 | 8.8177 | 8.8177 | 8.8177 | 8.8177
15% | 4369.4129 | 6.0537 | 8.4036 | 9.0145 | 4.7686 | 4.8498 | 4.9896 | 5.3078 | 5.5207 | 5.7905 | 5.9305 | 6.0537 | 5.8267 | 6.0928 | 6.511 | 6.1936 | 6.1936 | 6.1936 | 6.1936 | 6.1936 | 6.1936 | 6.1936 | 6.1936 | 6.1936 | 6.1936 | 6.1936 | 6.1936 | 6.1936 | 6.1936 | 6.1936 | 6.1936 | 15% | 4369.4129 | 6.4812 | 8.8014 | 9.4362 | 5.1844 | 5.2467 | 5.3835 | 5.7066 | 5.8831 | 6.2191 | 7.2406 | 6.3985 | 6.2338 | 6.4561 | 6.9424 | 6.6133 | 6.6133 | 6.6133 | 6.6133 | 6.6133 | 6.6133 | 6.6133 | 6.6133 | 6.6133 | 6.6133 | 6.6133 | 6.6133 | 6.6133 | 6.6133 | 6.6133 | 6.6133
10% | 4378.6261 | 4.0358 | 5.6024 | 6.0096 | 3.1791 | 3.2332 | 3.3264 | 3.5385 | 3.6805 | 3.8603 | 3.9537 | 4.0358 | 3.8845 | 4.0618 | 4.3407 | 4.1291 | 4.1291 | 4.1291 | 4.1291 | 4.1291 | 4.1291 | 4.1291 | 4.1291 | 4.1291 | 4.1291 | 4.1291 | 4.1291 | 4.1291 | 4.1291 | 4.1291 | 4.1291 | 10% | 4378.6261 | 4.3208 | 5.8676 | 6.2908 | 3.4563 | 3.4978 | 3.589 | 3.8044 | 3.922 | 4.1461 | 4.8271 | 4.2657 | 4.1558 | 4.3041 | 4.6283 | 4.4088 | 4.4088 | 4.4088 | 4.4088 | 4.4088 | 4.4088 | 4.4088 | 4.4088 | 4.4088 | 4.4088 | 4.4088 | 4.4088 | 4.4088 | 4.4088 | 4.4088 | 4.4088
5% | 4391.7028 | 2.0179 | 2.8012 | 3.0048 | 1.5895 | 1.6166 | 1.6632 | 1.7693 | 1.8402 | 1.9302 | 1.9768 | 2.0179 | 1.9422 | 2.0309 | 2.1703 | 2.0645 | 2.0645 | 2.0645 | 2.0645 | 2.0645 | 2.0645 | 2.0645 | 2.0645 | 2.0645 | 2.0645 | 2.0645 | 2.0645 | 2.0645 | 2.0645 | 2.0645 | 2.0645 | 5% | 4391.7028 | 2.1604 | 2.9338 | 3.1454 | 1.7281 | 1.7489 | 1.7945 | 1.9022 | 1.961 | 2.073 | 2.4135 | 2.1328 | 2.0779 | 2.152 | 2.3141 | 2.2044 | 2.2044 | 2.2044 | 2.2044 | 2.2044 | 2.2044 | 2.2044 | 2.2044 | 2.2044 | 2.2044 | 2.2044 | 2.2044 | 2.2044 | 2.2044 | 2.2044 | 2.2044
9.992e-14% | 4391.7028 | 4.0326e-14 | 5.5979e-14 | 6.0048e-14 | 3.1765e-14 | 3.2306e-14 | 3.3238e-14 | 3.5357e-14 | 3.6775e-14 | 3.8573e-14 | 3.9505e-14 | 4.0326e-14 | 3.8814e-14 | 4.0586e-14 | 4.3372e-14 | 4.1258e-14 | 4.1258e-14 | 4.1258e-14 | 4.1258e-14 | 4.1258e-14 | 4.1258e-14 | 4.1258e-14 | 4.1258e-14 | 4.1258e-14 | 4.1258e-14 | 4.1258e-14 | 4.1258e-14 | 4.1258e-14 | 4.1258e-14 | 4.1258e-14 | 4.1258e-14 | 9.992e-14% | 4391.7028 | 4.3173e-14 | 5.8629e-14 | 6.2858e-14 | 3.4535e-14 | 3.495e-14 | 3.5862e-14 | 3.8014e-14 | 3.9189e-14 | 4.1428e-14 | 4.8232e-14 | 4.2623e-14 | 4.1525e-14 | 4.3006e-14 | 4.6246e-14 | 4.4053e-14 | 4.4053e-14 | 4.4053e-14 | 4.4053e-14 | 4.4053e-14 | 4.4053e-14 | 4.4053e-14 | 4.4053e-14 | 4.4053e-14 | 4.4053e-14 | 4.4053e-14 | 4.4053e-14 | 4.4053e-14 | 4.4053e-14 | 4.4053e-14 | 4.4053e-14
Summer Season | [31 empty] | Summer Season
P50 | [31 empty] | P10
% of MD | Summer - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Summer - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 45.8759 | 60.9589 | 65.0674 | 35.9499 | 35.9485 | 36.4184 | 36.9338 | 37.9909 | 38.7504 | 39.1633 | 39.6157 | 40.029 | 40.7743 | 41.6989 | 41.6364 | 41.6364 | 41.6364 | 41.6364 | 41.6364 | 41.6364 | 41.6364 | 41.6364 | 41.6364 | 41.6364 | 41.6364 | 41.6364 | 41.6364 | 41.6364 | 41.6364 | 41.6364 | 100% | 0 | 51.1554 | 66.2686 | 70.2261 | 40.9907 | 41.0105 | 41.4179 | 42.4905 | 43.2097 | 43.9132 | 44.7356 | 45.4985 | 46.2386 | 46.3243 | 47.1878 | 46.5357 | 46.5357 | 46.5357 | 46.5357 | 46.5357 | 46.5357 | 46.5357 | 46.5357 | 46.5357 | 46.5357 | 46.5357 | 46.5357 | 46.5357 | 46.5357 | 46.5357 | 46.5357
99% | 0 | 45.4171 | 60.3493 | 64.4168 | 35.5904 | 35.589 | 36.0542 | 36.5645 | 37.611 | 38.3629 | 38.7717 | 39.2195 | 39.6287 | 40.3666 | 41.2819 | 41.22 | 41.22 | 41.22 | 41.22 | 41.22 | 41.22 | 41.22 | 41.22 | 41.22 | 41.22 | 41.22 | 41.22 | 41.22 | 41.22 | 41.22 | 41.22 | 99% | 1.5127 | 50.6438 | 65.6059 | 69.5238 | 40.5808 | 40.6004 | 41.0037 | 42.0656 | 42.7776 | 43.474 | 44.2883 | 45.0435 | 45.7762 | 45.861 | 46.7159 | 46.0703 | 46.0703 | 46.0703 | 46.0703 | 46.0703 | 46.0703 | 46.0703 | 46.0703 | 46.0703 | 46.0703 | 46.0703 | 46.0703 | 46.0703 | 46.0703 | 46.0703 | 46.0703
98% | 0 | 44.9584 | 59.7397 | 63.7661 | 35.2309 | 35.2295 | 35.69 | 36.1951 | 37.2311 | 37.9754 | 38.3801 | 38.8234 | 39.2284 | 39.9588 | 40.8649 | 40.8036 | 40.8036 | 40.8036 | 40.8036 | 40.8036 | 40.8036 | 40.8036 | 40.8036 | 40.8036 | 40.8036 | 40.8036 | 40.8036 | 40.8036 | 40.8036 | 40.8036 | 40.8036 | 98% | 2.269 | 50.1322 | 64.9433 | 68.8216 | 40.1709 | 40.1903 | 40.5896 | 41.6407 | 42.3455 | 43.0349 | 43.8409 | 44.5885 | 45.3138 | 45.3978 | 46.244 | 45.6049 | 45.6049 | 45.6049 | 45.6049 | 45.6049 | 45.6049 | 45.6049 | 45.6049 | 45.6049 | 45.6049 | 45.6049 | 45.6049 | 45.6049 | 45.6049 | 45.6049 | 45.6049
97% | 0.37816 | 44.4996 | 59.1301 | 63.1154 | 34.8714 | 34.87 | 35.3258 | 35.8258 | 36.8512 | 37.5879 | 37.9884 | 38.4272 | 38.8281 | 39.5511 | 40.4479 | 40.3873 | 40.3873 | 40.3873 | 40.3873 | 40.3873 | 40.3873 | 40.3873 | 40.3873 | 40.3873 | 40.3873 | 40.3873 | 40.3873 | 40.3873 | 40.3873 | 40.3873 | 40.3873 | 97% | 3.7816 | 49.6207 | 64.2806 | 68.1193 | 39.761 | 39.7802 | 40.1754 | 41.2158 | 41.9134 | 42.5958 | 43.3936 | 44.1336 | 44.8514 | 44.9346 | 45.7722 | 45.1396 | 45.1396 | 45.1396 | 45.1396 | 45.1396 | 45.1396 | 45.1396 | 45.1396 | 45.1396 | 45.1396 | 45.1396 | 45.1396 | 45.1396 | 45.1396 | 45.1396 | 45.1396
95% | 2.269 | 43.5821 | 57.911 | 61.8141 | 34.1524 | 34.151 | 34.5974 | 35.0871 | 36.0914 | 36.8129 | 37.2052 | 37.6349 | 38.0276 | 38.7356 | 39.6139 | 39.5546 | 39.5546 | 39.5546 | 39.5546 | 39.5546 | 39.5546 | 39.5546 | 39.5546 | 39.5546 | 39.5546 | 39.5546 | 39.5546 | 39.5546 | 39.5546 | 39.5546 | 39.5546 | 95% | 6.0506 | 48.5976 | 62.9552 | 66.7148 | 38.9412 | 38.96 | 39.347 | 40.366 | 41.0492 | 41.7175 | 42.4988 | 43.2236 | 43.9266 | 44.0081 | 44.8284 | 44.2089 | 44.2089 | 44.2089 | 44.2089 | 44.2089 | 44.2089 | 44.2089 | 44.2089 | 44.2089 | 44.2089 | 44.2089 | 44.2089 | 44.2089 | 44.2089 | 44.2089 | 44.2089
90% | 5.6725 | 41.2883 | 54.863 | 58.5607 | 32.3549 | 32.3536 | 32.7765 | 33.2404 | 34.1918 | 34.8754 | 35.247 | 35.6541 | 36.0261 | 36.6969 | 37.529 | 37.4727 | 37.4727 | 37.4727 | 37.4727 | 37.4727 | 37.4727 | 37.4727 | 37.4727 | 37.4727 | 37.4727 | 37.4727 | 37.4727 | 37.4727 | 37.4727 | 37.4727 | 37.4727 | 90% | 16.2611 | 46.0398 | 59.6418 | 63.2035 | 36.8917 | 36.9094 | 37.2761 | 38.2415 | 38.8887 | 39.5218 | 40.2621 | 40.9487 | 41.6147 | 41.6919 | 42.469 | 41.8821 | 41.8821 | 41.8821 | 41.8821 | 41.8821 | 41.8821 | 41.8821 | 41.8821 | 41.8821 | 41.8821 | 41.8821 | 41.8821 | 41.8821 | 41.8821 | 41.8821 | 41.8821
85% | 15.8829 | 38.9945 | 51.8151 | 55.3073 | 30.5574 | 30.5562 | 30.9556 | 31.3937 | 32.2923 | 32.9379 | 33.2888 | 33.6733 | 34.0247 | 34.6582 | 35.444 | 35.3909 | 35.3909 | 35.3909 | 35.3909 | 35.3909 | 35.3909 | 35.3909 | 35.3909 | 35.3909 | 35.3909 | 35.3909 | 35.3909 | 35.3909 | 35.3909 | 35.3909 | 35.3909 | 85% | 26.4715 | 43.482 | 56.3283 | 59.6922 | 34.8421 | 34.8589 | 35.2052 | 36.117 | 36.7283 | 37.3262 | 38.0253 | 38.6737 | 39.3028 | 39.3756 | 40.1096 | 39.5553 | 39.5553 | 39.5553 | 39.5553 | 39.5553 | 39.5553 | 39.5553 | 39.5553 | 39.5553 | 39.5553 | 39.5553 | 39.5553 | 39.5553 | 39.5553 | 39.5553 | 39.5553
80% | 31.0095 | 36.7007 | 48.7671 | 52.0539 | 28.7599 | 28.7588 | 29.1347 | 29.547 | 30.3928 | 31.0003 | 31.3307 | 31.6925 | 32.0232 | 32.6194 | 33.3591 | 33.3091 | 33.3091 | 33.3091 | 33.3091 | 33.3091 | 33.3091 | 33.3091 | 33.3091 | 33.3091 | 33.3091 | 33.3091 | 33.3091 | 33.3091 | 33.3091 | 33.3091 | 33.3091 | 80% | 34.0348 | 40.9243 | 53.0149 | 56.1809 | 32.7926 | 32.8084 | 33.1343 | 33.9924 | 34.5678 | 35.1305 | 35.7885 | 36.3988 | 36.9908 | 37.0594 | 37.7502 | 37.2285 | 37.2285 | 37.2285 | 37.2285 | 37.2285 | 37.2285 | 37.2285 | 37.2285 | 37.2285 | 37.2285 | 37.2285 | 37.2285 | 37.2285 | 37.2285 | 37.2285 | 37.2285
75% | 72.9857 | 34.4069 | 45.7192 | 48.8006 | 26.9624 | 26.9613 | 27.3138 | 27.7004 | 28.4932 | 29.0628 | 29.3725 | 29.7118 | 30.0218 | 30.5807 | 31.2741 | 31.2273 | 31.2273 | 31.2273 | 31.2273 | 31.2273 | 31.2273 | 31.2273 | 31.2273 | 31.2273 | 31.2273 | 31.2273 | 31.2273 | 31.2273 | 31.2273 | 31.2273 | 31.2273 | 75% | 48.405 | 38.3665 | 49.7015 | 52.6696 | 30.743 | 30.7579 | 31.0634 | 31.8679 | 32.4073 | 32.9349 | 33.5517 | 34.1239 | 34.6789 | 34.7432 | 35.3908 | 34.9017 | 34.9017 | 34.9017 | 34.9017 | 34.9017 | 34.9017 | 34.9017 | 34.9017 | 34.9017 | 34.9017 | 34.9017 | 34.9017 | 34.9017 | 34.9017 | 34.9017 | 34.9017
70% | 150.5094 | 32.1131 | 42.6712 | 45.5472 | 25.1649 | 25.1639 | 25.4929 | 25.8537 | 26.5937 | 27.1253 | 27.4143 | 27.731 | 28.0203 | 28.542 | 29.1892 | 29.1455 | 29.1455 | 29.1455 | 29.1455 | 29.1455 | 29.1455 | 29.1455 | 29.1455 | 29.1455 | 29.1455 | 29.1455 | 29.1455 | 29.1455 | 29.1455 | 29.1455 | 29.1455 | 70% | 76.3892 | 35.8087 | 46.388 | 49.1583 | 28.6935 | 28.7073 | 28.9925 | 29.7434 | 30.2468 | 30.7392 | 31.3149 | 31.849 | 32.367 | 32.427 | 33.0315 | 32.575 | 32.575 | 32.575 | 32.575 | 32.575 | 32.575 | 32.575 | 32.575 | 32.575 | 32.575 | 32.575 | 32.575 | 32.575 | 32.575 | 32.575 | 32.575
65% | 359.6342 | 29.8193 | 39.6233 | 42.2938 | 23.3674 | 23.3665 | 23.6719 | 24.007 | 24.6941 | 25.1878 | 25.4562 | 25.7502 | 26.0189 | 26.5033 | 27.1043 | 27.0636 | 27.0636 | 27.0636 | 27.0636 | 27.0636 | 27.0636 | 27.0636 | 27.0636 | 27.0636 | 27.0636 | 27.0636 | 27.0636 | 27.0636 | 27.0636 | 27.0636 | 27.0636 | 65% | 114.2056 | 33.251 | 43.0746 | 45.647 | 26.644 | 26.6568 | 26.9216 | 27.6189 | 28.0863 | 28.5436 | 29.0782 | 29.574 | 30.0551 | 30.1108 | 30.6721 | 30.2482 | 30.2482 | 30.2482 | 30.2482 | 30.2482 | 30.2482 | 30.2482 | 30.2482 | 30.2482 | 30.2482 | 30.2482 | 30.2482 | 30.2482 | 30.2482 | 30.2482 | 30.2482
60% | 689.7717 | 27.5255 | 36.5753 | 39.0405 | 21.5699 | 21.5691 | 21.851 | 22.1603 | 22.7946 | 23.2503 | 23.498 | 23.7694 | 24.0174 | 24.4646 | 25.0193 | 24.9818 | 24.9818 | 24.9818 | 24.9818 | 24.9818 | 24.9818 | 24.9818 | 24.9818 | 24.9818 | 24.9818 | 24.9818 | 24.9818 | 24.9818 | 24.9818 | 24.9818 | 24.9818 | 60% | 178.1154 | 30.6932 | 39.7612 | 42.1357 | 24.5944 | 24.6063 | 24.8508 | 25.4943 | 25.9258 | 26.3479 | 26.8414 | 27.2991 | 27.7431 | 27.7946 | 28.3127 | 27.9214 | 27.9214 | 27.9214 | 27.9214 | 27.9214 | 27.9214 | 27.9214 | 27.9214 | 27.9214 | 27.9214 | 27.9214 | 27.9214 | 27.9214 | 27.9214 | 27.9214 | 27.9214
55% | 1095.5419 | 25.2317 | 33.5274 | 35.7871 | 19.7724 | 19.7717 | 20.0301 | 20.3136 | 20.895 | 21.3127 | 21.5398 | 21.7886 | 22.016 | 22.4259 | 22.9344 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 55% | 311.6074 | 28.1354 | 36.4477 | 38.6243 | 22.5449 | 22.5558 | 22.7799 | 23.3698 | 23.7653 | 24.1522 | 24.6046 | 25.0242 | 25.4312 | 25.4784 | 25.9533 | 25.5946 | 25.5946 | 25.5946 | 25.5946 | 25.5946 | 25.5946 | 25.5946 | 25.5946 | 25.5946 | 25.5946 | 25.5946 | 25.5946 | 25.5946 | 25.5946 | 25.5946 | 25.5946
50% | 1666.1918 | 22.9379 | 30.4794 | 32.5337 | 17.9749 | 17.9742 | 18.2092 | 18.4669 | 18.9955 | 19.3752 | 19.5817 | 19.8078 | 20.0145 | 20.3872 | 20.8494 | 20.8182 | 20.8182 | 20.8182 | 20.8182 | 20.8182 | 20.8182 | 20.8182 | 20.8182 | 20.8182 | 20.8182 | 20.8182 | 20.8182 | 20.8182 | 20.8182 | 20.8182 | 20.8182 | 50% | 636.0723 | 25.5777 | 33.1343 | 35.113 | 20.4954 | 20.5052 | 20.709 | 21.2453 | 21.6049 | 21.9566 | 22.3678 | 22.7493 | 23.1193 | 23.1621 | 23.5939 | 23.2678 | 23.2678 | 23.2678 | 23.2678 | 23.2678 | 23.2678 | 23.2678 | 23.2678 | 23.2678 | 23.2678 | 23.2678 | 23.2678 | 23.2678 | 23.2678 | 23.2678 | 23.2678
45% | 2506.0947 | 20.6442 | 27.4315 | 29.2803 | 16.1774 | 16.1768 | 16.3883 | 16.6202 | 17.0959 | 17.4377 | 17.6235 | 17.8271 | 18.0131 | 18.3484 | 18.7645 | 18.7364 | 18.7364 | 18.7364 | 18.7364 | 18.7364 | 18.7364 | 18.7364 | 18.7364 | 18.7364 | 18.7364 | 18.7364 | 18.7364 | 18.7364 | 18.7364 | 18.7364 | 18.7364 | 45% | 1179.4944 | 23.0199 | 29.8209 | 31.6017 | 18.4458 | 18.4547 | 18.6381 | 19.1207 | 19.4444 | 19.7609 | 20.131 | 20.4743 | 20.8073 | 20.8459 | 21.2345 | 20.941 | 20.941 | 20.941 | 20.941 | 20.941 | 20.941 | 20.941 | 20.941 | 20.941 | 20.941 | 20.941 | 20.941 | 20.941 | 20.941 | 20.941 | 20.941
40% | 3164.4787 | 18.3504 | 24.3836 | 26.027 | 14.3799 | 14.3794 | 14.5673 | 14.7735 | 15.1964 | 15.5002 | 15.6653 | 15.8463 | 16.0116 | 16.3097 | 16.6795 | 16.6546 | 16.6546 | 16.6546 | 16.6546 | 16.6546 | 16.6546 | 16.6546 | 16.6546 | 16.6546 | 16.6546 | 16.6546 | 16.6546 | 16.6546 | 16.6546 | 16.6546 | 16.6546 | 40% | 1808.3816 | 20.4621 | 26.5075 | 28.0904 | 16.3963 | 16.4042 | 16.5672 | 16.9962 | 17.2839 | 17.5653 | 17.8942 | 18.1994 | 18.4954 | 18.5297 | 18.8751 | 18.6143 | 18.6143 | 18.6143 | 18.6143 | 18.6143 | 18.6143 | 18.6143 | 18.6143 | 18.6143 | 18.6143 | 18.6143 | 18.6143 | 18.6143 | 18.6143 | 18.6143 | 18.6143
35% | 3551.3408 | 16.0566 | 21.3356 | 22.7736 | 12.5825 | 12.582 | 12.7464 | 12.9268 | 13.2968 | 13.5626 | 13.7072 | 13.8655 | 14.0102 | 14.271 | 14.5946 | 14.5727 | 14.5727 | 14.5727 | 14.5727 | 14.5727 | 14.5727 | 14.5727 | 14.5727 | 14.5727 | 14.5727 | 14.5727 | 14.5727 | 14.5727 | 14.5727 | 14.5727 | 14.5727 | 35% | 2779.1293 | 17.9044 | 23.194 | 24.5791 | 14.3468 | 14.3537 | 14.4963 | 14.8717 | 15.1234 | 15.3696 | 15.6575 | 15.9245 | 16.1835 | 16.2135 | 16.5157 | 16.2875 | 16.2875 | 16.2875 | 16.2875 | 16.2875 | 16.2875 | 16.2875 | 16.2875 | 16.2875 | 16.2875 | 16.2875 | 16.2875 | 16.2875 | 16.2875 | 16.2875 | 16.2875
30% | 3758.953 | 13.7628 | 18.2877 | 19.5202 | 10.785 | 10.7845 | 10.9255 | 11.0801 | 11.3973 | 11.6251 | 11.749 | 11.8847 | 12.0087 | 12.2323 | 12.5097 | 12.4909 | 12.4909 | 12.4909 | 12.4909 | 12.4909 | 12.4909 | 12.4909 | 12.4909 | 12.4909 | 12.4909 | 12.4909 | 12.4909 | 12.4909 | 12.4909 | 12.4909 | 12.4909 | 30% | 3814.165 | 15.3466 | 19.8806 | 21.0678 | 12.2972 | 12.3031 | 12.4254 | 12.7472 | 12.9629 | 13.1739 | 13.4207 | 13.6496 | 13.8716 | 13.8973 | 14.1563 | 13.9607 | 13.9607 | 13.9607 | 13.9607 | 13.9607 | 13.9607 | 13.9607 | 13.9607 | 13.9607 | 13.9607 | 13.9607 | 13.9607 | 13.9607 | 13.9607 | 13.9607 | 13.9607
25% | 3926.4798 | 11.469 | 15.2397 | 16.2669 | 8.9875 | 8.9871 | 9.1046 | 9.2335 | 9.4977 | 9.6876 | 9.7908 | 9.9039 | 10.0073 | 10.1936 | 10.4247 | 10.4091 | 10.4091 | 10.4091 | 10.4091 | 10.4091 | 10.4091 | 10.4091 | 10.4091 | 10.4091 | 10.4091 | 10.4091 | 10.4091 | 10.4091 | 10.4091 | 10.4091 | 10.4091 | 25% | 4166.9923 | 12.7888 | 16.5672 | 17.5565 | 10.2477 | 10.2526 | 10.3545 | 10.6226 | 10.8024 | 10.9783 | 11.1839 | 11.3746 | 11.5596 | 11.5811 | 11.7969 | 11.6339 | 11.6339 | 11.6339 | 11.6339 | 11.6339 | 11.6339 | 11.6339 | 11.6339 | 11.6339 | 11.6339 | 11.6339 | 11.6339 | 11.6339 | 11.6339 | 11.6339 | 11.6339
20% | 4050.5177 | 9.1752 | 12.1918 | 13.0135 | 7.19 | 7.1897 | 7.2837 | 7.3868 | 7.5982 | 7.7501 | 7.8327 | 7.9231 | 8.0058 | 8.1549 | 8.3398 | 8.3273 | 8.3273 | 8.3273 | 8.3273 | 8.3273 | 8.3273 | 8.3273 | 8.3273 | 8.3273 | 8.3273 | 8.3273 | 8.3273 | 8.3273 | 8.3273 | 8.3273 | 8.3273 | 20% | 4282.7105 | 10.2311 | 13.2537 | 14.0452 | 8.1981 | 8.2021 | 8.2836 | 8.4981 | 8.6419 | 8.7826 | 8.9471 | 9.0997 | 9.2477 | 9.2649 | 9.4376 | 9.3071 | 9.3071 | 9.3071 | 9.3071 | 9.3071 | 9.3071 | 9.3071 | 9.3071 | 9.3071 | 9.3071 | 9.3071 | 9.3071 | 9.3071 | 9.3071 | 9.3071 | 9.3071
15% | 4152.622 | 6.8814 | 9.1438 | 9.7601 | 5.3925 | 5.3923 | 5.4628 | 5.5401 | 5.6986 | 5.8126 | 5.8745 | 5.9424 | 6.0044 | 6.1161 | 6.2548 | 6.2455 | 6.2455 | 6.2455 | 6.2455 | 6.2455 | 6.2455 | 6.2455 | 6.2455 | 6.2455 | 6.2455 | 6.2455 | 6.2455 | 6.2455 | 6.2455 | 6.2455 | 6.2455 | 15% | 4364.7722 | 7.6733 | 9.9403 | 10.5339 | 6.1486 | 6.1516 | 6.2127 | 6.3736 | 6.4815 | 6.587 | 6.7103 | 6.8248 | 6.9358 | 6.9486 | 7.0782 | 6.9803 | 6.9803 | 6.9803 | 6.9803 | 6.9803 | 6.9803 | 6.9803 | 6.9803 | 6.9803 | 6.9803 | 6.9803 | 6.9803 | 6.9803 | 6.9803 | 6.9803 | 6.9803
10% | 4248.2976 | 4.5876 | 6.0959 | 6.5067 | 3.595 | 3.5948 | 3.6418 | 3.6934 | 3.7991 | 3.875 | 3.9163 | 3.9616 | 4.0029 | 4.0774 | 4.1699 | 4.1636 | 4.1636 | 4.1636 | 4.1636 | 4.1636 | 4.1636 | 4.1636 | 4.1636 | 4.1636 | 4.1636 | 4.1636 | 4.1636 | 4.1636 | 4.1636 | 4.1636 | 4.1636 | 10% | 4391.6218 | 5.1155 | 6.6269 | 7.0226 | 4.0991 | 4.101 | 4.1418 | 4.2491 | 4.321 | 4.3913 | 4.4736 | 4.5499 | 4.6239 | 4.6324 | 4.7188 | 4.6536 | 4.6536 | 4.6536 | 4.6536 | 4.6536 | 4.6536 | 4.6536 | 4.6536 | 4.6536 | 4.6536 | 4.6536 | 4.6536 | 4.6536 | 4.6536 | 4.6536 | 4.6536
5% | 4361.7469 | 2.2938 | 3.0479 | 3.2534 | 1.7975 | 1.7974 | 1.8209 | 1.8467 | 1.8995 | 1.9375 | 1.9582 | 1.9808 | 2.0015 | 2.0387 | 2.0849 | 2.0818 | 2.0818 | 2.0818 | 2.0818 | 2.0818 | 2.0818 | 2.0818 | 2.0818 | 2.0818 | 2.0818 | 2.0818 | 2.0818 | 2.0818 | 2.0818 | 2.0818 | 2.0818 | 5% | 4391.6218 | 2.5578 | 3.3134 | 3.5113 | 2.0495 | 2.0505 | 2.0709 | 2.1245 | 2.1605 | 2.1957 | 2.2368 | 2.2749 | 2.3119 | 2.3162 | 2.3594 | 2.3268 | 2.3268 | 2.3268 | 2.3268 | 2.3268 | 2.3268 | 2.3268 | 2.3268 | 2.3268 | 2.3268 | 2.3268 | 2.3268 | 2.3268 | 2.3268 | 2.3268 | 2.3268
9.992e-14% | 4391.6218 | 4.5839e-14 | 6.091e-14 | 6.5015e-14 | 3.5921e-14 | 3.592e-14 | 3.6389e-14 | 3.6904e-14 | 3.7961e-14 | 3.8719e-14 | 3.9132e-14 | 3.9584e-14 | 3.9997e-14 | 4.0742e-14 | 4.1666e-14 | 4.1603e-14 | 4.1603e-14 | 4.1603e-14 | 4.1603e-14 | 4.1603e-14 | 4.1603e-14 | 4.1603e-14 | 4.1603e-14 | 4.1603e-14 | 4.1603e-14 | 4.1603e-14 | 4.1603e-14 | 4.1603e-14 | 4.1603e-14 | 4.1603e-14 | 4.1603e-14 | 9.992e-14% | 4391.6218 | 5.1114e-14 | 6.6216e-14 | 7.017e-14 | 4.0958e-14 | 4.0978e-14 | 4.1385e-14 | 4.2457e-14 | 4.3175e-14 | 4.3878e-14 | 4.47e-14 | 4.5462e-14 | 4.6202e-14 | 4.6287e-14 | 4.715e-14 | 4.6498e-14 | 4.6498e-14 | 4.6498e-14 | 4.6498e-14 | 4.6498e-14 | 4.6498e-14 | 4.6498e-14 | 4.6498e-14 | 4.6498e-14 | 4.6498e-14 | 4.6498e-14 | 4.6498e-14 | 4.6498e-14 | 4.6498e-14 | 4.6498e-14 | 4.6498e-14
Option 6
Winter Season | [31 empty] | Winter Season
P50 | [31 empty] | P10
% of MD | Winter - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Winter - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 32.6124 | 46.0636 | 49.5606 | 50.2922 | 50.8351 | 51.7106 | 53.6772 | 54.9959 | 56.6943 | 57.5103 | 58.2241 | 56.6054 | 58.3692 | 61.0337 | 59.0164 | 59.0164 | 59.0164 | 59.0164 | 59.0164 | 59.0164 | 59.0164 | 59.0164 | 59.0164 | 59.0164 | 59.0164 | 59.0164 | 59.0164 | 59.0164 | 59.0164 | 59.0164 | 100% | 0 | 35.4624 | 48.716 | 52.372 | 53.0641 | 53.4814 | 54.3366 | 56.3364 | 57.4115 | 59.5517 | 66.2442 | 60.5225 | 59.3189 | 60.7916 | 63.9099 | 61.814 | 61.814 | 61.814 | 61.814 | 61.814 | 61.814 | 61.814 | 61.814 | 61.814 | 61.814 | 61.814 | 61.814 | 61.814 | 61.814 | 61.814 | 61.814
99% | 1.486 | 32.2863 | 45.6029 | 49.065 | 49.7893 | 50.3268 | 51.1935 | 53.1405 | 54.446 | 56.1274 | 56.9352 | 57.6419 | 56.0393 | 57.7855 | 60.4234 | 58.4263 | 58.4263 | 58.4263 | 58.4263 | 58.4263 | 58.4263 | 58.4263 | 58.4263 | 58.4263 | 58.4263 | 58.4263 | 58.4263 | 58.4263 | 58.4263 | 58.4263 | 58.4263 | 99% | 1.486 | 35.1078 | 48.2288 | 51.8482 | 52.5335 | 52.9465 | 53.7932 | 55.773 | 56.8373 | 58.9562 | 65.5818 | 59.9173 | 58.7257 | 60.1837 | 63.2708 | 61.1959 | 61.1959 | 61.1959 | 61.1959 | 61.1959 | 61.1959 | 61.1959 | 61.1959 | 61.1959 | 61.1959 | 61.1959 | 61.1959 | 61.1959 | 61.1959 | 61.1959 | 61.1959
98% | 3.2692 | 31.9602 | 45.1423 | 48.5694 | 49.2864 | 49.8184 | 50.6764 | 52.6037 | 53.896 | 55.5604 | 56.3601 | 57.0597 | 55.4733 | 57.2018 | 59.813 | 57.8361 | 57.8361 | 57.8361 | 57.8361 | 57.8361 | 57.8361 | 57.8361 | 57.8361 | 57.8361 | 57.8361 | 57.8361 | 57.8361 | 57.8361 | 57.8361 | 57.8361 | 57.8361 | 98% | 3.2692 | 34.7532 | 47.7417 | 51.3245 | 52.0028 | 52.4117 | 53.2499 | 55.2097 | 56.2632 | 58.3606 | 64.9193 | 59.3121 | 58.1325 | 59.5758 | 62.6317 | 60.5777 | 60.5777 | 60.5777 | 60.5777 | 60.5777 | 60.5777 | 60.5777 | 60.5777 | 60.5777 | 60.5777 | 60.5777 | 60.5777 | 60.5777 | 60.5777 | 60.5777 | 60.5777
97% | 6.8356 | 31.6341 | 44.6816 | 48.0738 | 48.7834 | 49.3101 | 50.1593 | 52.0669 | 53.3461 | 54.9935 | 55.7849 | 56.4774 | 54.9072 | 56.6181 | 59.2027 | 57.2459 | 57.2459 | 57.2459 | 57.2459 | 57.2459 | 57.2459 | 57.2459 | 57.2459 | 57.2459 | 57.2459 | 57.2459 | 57.2459 | 57.2459 | 57.2459 | 57.2459 | 57.2459 | 97% | 6.8356 | 34.3986 | 47.2545 | 50.8008 | 51.4722 | 51.8769 | 52.7065 | 54.6463 | 55.6891 | 57.7651 | 64.2569 | 58.7069 | 57.5393 | 58.9679 | 61.9926 | 59.9596 | 59.9596 | 59.9596 | 59.9596 | 59.9596 | 59.9596 | 59.9596 | 59.9596 | 59.9596 | 59.9596 | 59.9596 | 59.9596 | 59.9596 | 59.9596 | 59.9596 | 59.9596
95% | 17.5347 | 30.9818 | 43.7604 | 47.0826 | 47.7776 | 48.2934 | 49.1251 | 50.9934 | 52.2461 | 53.8596 | 54.6347 | 55.3129 | 53.7751 | 55.4508 | 57.982 | 56.0656 | 56.0656 | 56.0656 | 56.0656 | 56.0656 | 56.0656 | 56.0656 | 56.0656 | 56.0656 | 56.0656 | 56.0656 | 56.0656 | 56.0656 | 56.0656 | 56.0656 | 56.0656 | 95% | 17.5347 | 33.6893 | 46.2802 | 49.7534 | 50.4109 | 50.8073 | 51.6198 | 53.5196 | 54.5409 | 56.5741 | 62.932 | 57.4964 | 56.3529 | 57.752 | 60.7144 | 58.7233 | 58.7233 | 58.7233 | 58.7233 | 58.7233 | 58.7233 | 58.7233 | 58.7233 | 58.7233 | 58.7233 | 58.7233 | 58.7233 | 58.7233 | 58.7233 | 58.7233 | 58.7233
90% | 78.7576 | 29.3512 | 41.4572 | 44.6045 | 45.263 | 45.7516 | 46.5395 | 48.3095 | 49.4964 | 51.0249 | 51.7592 | 52.4017 | 50.9448 | 52.5323 | 54.9303 | 53.1148 | 53.1148 | 53.1148 | 53.1148 | 53.1148 | 53.1148 | 53.1148 | 53.1148 | 53.1148 | 53.1148 | 53.1148 | 53.1148 | 53.1148 | 53.1148 | 53.1148 | 53.1148 | 90% | 78.7576 | 31.9162 | 43.8444 | 47.1348 | 47.7577 | 48.1332 | 48.9029 | 50.7027 | 51.6703 | 53.5965 | 59.6198 | 54.4703 | 53.387 | 54.7124 | 57.5189 | 55.6326 | 55.6326 | 55.6326 | 55.6326 | 55.6326 | 55.6326 | 55.6326 | 55.6326 | 55.6326 | 55.6326 | 55.6326 | 55.6326 | 55.6326 | 55.6326 | 55.6326 | 55.6326
85% | 236.8672 | 27.7206 | 39.154 | 42.1265 | 42.7484 | 43.2099 | 43.954 | 45.6257 | 46.7466 | 48.1902 | 48.8837 | 49.4905 | 48.1146 | 49.6138 | 51.8787 | 50.164 | 50.164 | 50.164 | 50.164 | 50.164 | 50.164 | 50.164 | 50.164 | 50.164 | 50.164 | 50.164 | 50.164 | 50.164 | 50.164 | 50.164 | 50.164 | 85% | 236.8672 | 30.1431 | 41.4086 | 44.5162 | 45.1045 | 45.4592 | 46.1861 | 47.8859 | 48.7997 | 50.6189 | 56.3076 | 51.4442 | 50.421 | 51.6729 | 54.3234 | 52.5419 | 52.5419 | 52.5419 | 52.5419 | 52.5419 | 52.5419 | 52.5419 | 52.5419 | 52.5419 | 52.5419 | 52.5419 | 52.5419 | 52.5419 | 52.5419 | 52.5419 | 52.5419
80% | 497.5104 | 26.09 | 36.8508 | 39.6485 | 40.2338 | 40.6681 | 41.3685 | 42.9418 | 43.9968 | 45.3555 | 46.0082 | 46.5793 | 45.2843 | 46.6954 | 48.827 | 47.2131 | 47.2131 | 47.2131 | 47.2131 | 47.2131 | 47.2131 | 47.2131 | 47.2131 | 47.2131 | 47.2131 | 47.2131 | 47.2131 | 47.2131 | 47.2131 | 47.2131 | 47.2131 | 80% | 497.5104 | 28.37 | 38.9728 | 41.8976 | 42.4513 | 42.7851 | 43.4693 | 45.0691 | 45.9292 | 47.6413 | 52.9954 | 48.418 | 47.4551 | 48.6333 | 51.1279 | 49.4512 | 49.4512 | 49.4512 | 49.4512 | 49.4512 | 49.4512 | 49.4512 | 49.4512 | 49.4512 | 49.4512 | 49.4512 | 49.4512 | 49.4512 | 49.4512 | 49.4512 | 49.4512
75% | 803.6248 | 24.4593 | 34.5477 | 37.1704 | 37.7192 | 38.1264 | 38.7829 | 40.2579 | 41.247 | 42.5207 | 43.1327 | 43.6681 | 42.454 | 43.7769 | 45.7753 | 44.2623 | 44.2623 | 44.2623 | 44.2623 | 44.2623 | 44.2623 | 44.2623 | 44.2623 | 44.2623 | 44.2623 | 44.2623 | 44.2623 | 44.2623 | 44.2623 | 44.2623 | 44.2623 | 75% | 803.6248 | 26.5968 | 36.537 | 39.279 | 39.7981 | 40.111 | 40.7524 | 42.2523 | 43.0586 | 44.6638 | 49.6831 | 45.3919 | 44.4892 | 45.5937 | 47.9324 | 46.3605 | 46.3605 | 46.3605 | 46.3605 | 46.3605 | 46.3605 | 46.3605 | 46.3605 | 46.3605 | 46.3605 | 46.3605 | 46.3605 | 46.3605 | 46.3605 | 46.3605 | 46.3605
70% | 1155.2107 | 22.8287 | 32.2445 | 34.6924 | 35.2045 | 35.5846 | 36.1974 | 37.5741 | 38.4972 | 39.686 | 40.2572 | 40.7569 | 39.6238 | 40.8585 | 42.7236 | 41.3115 | 41.3115 | 41.3115 | 41.3115 | 41.3115 | 41.3115 | 41.3115 | 41.3115 | 41.3115 | 41.3115 | 41.3115 | 41.3115 | 41.3115 | 41.3115 | 41.3115 | 41.3115 | 70% | 1155.2107 | 24.8237 | 34.1012 | 36.6604 | 37.1449 | 37.4369 | 38.0356 | 39.4355 | 40.188 | 41.6862 | 46.3709 | 42.3658 | 41.5232 | 42.5541 | 44.7369 | 43.2698 | 43.2698 | 43.2698 | 43.2698 | 43.2698 | 43.2698 | 43.2698 | 43.2698 | 43.2698 | 43.2698 | 43.2698 | 43.2698 | 43.2698 | 43.2698 | 43.2698 | 43.2698
65% | 1553.1596 | 21.1981 | 29.9413 | 32.2144 | 32.6899 | 33.0428 | 33.6119 | 34.8902 | 35.7474 | 36.8513 | 37.3817 | 37.8457 | 36.7935 | 37.94 | 39.6719 | 38.3607 | 38.3607 | 38.3607 | 38.3607 | 38.3607 | 38.3607 | 38.3607 | 38.3607 | 38.3607 | 38.3607 | 38.3607 | 38.3607 | 38.3607 | 38.3607 | 38.3607 | 38.3607 | 65% | 1553.1596 | 23.0506 | 31.6654 | 34.0418 | 34.4917 | 34.7629 | 35.3188 | 36.6187 | 37.3174 | 38.7086 | 43.0587 | 39.3397 | 38.5573 | 39.5145 | 41.5414 | 40.1791 | 40.1791 | 40.1791 | 40.1791 | 40.1791 | 40.1791 | 40.1791 | 40.1791 | 40.1791 | 40.1791 | 40.1791 | 40.1791 | 40.1791 | 40.1791 | 40.1791 | 40.1791
60% | 2026.2996 | 19.5675 | 27.6381 | 29.7363 | 30.1753 | 30.5011 | 31.0264 | 32.2063 | 32.9976 | 34.0166 | 34.5062 | 34.9345 | 33.9632 | 35.0215 | 36.6202 | 35.4099 | 35.4099 | 35.4099 | 35.4099 | 35.4099 | 35.4099 | 35.4099 | 35.4099 | 35.4099 | 35.4099 | 35.4099 | 35.4099 | 35.4099 | 35.4099 | 35.4099 | 35.4099 | 60% | 2026.2996 | 21.2775 | 29.2296 | 31.4232 | 31.8385 | 32.0888 | 32.602 | 33.8018 | 34.4469 | 35.731 | 39.7465 | 36.3135 | 35.5913 | 36.475 | 38.3459 | 37.0884 | 37.0884 | 37.0884 | 37.0884 | 37.0884 | 37.0884 | 37.0884 | 37.0884 | 37.0884 | 37.0884 | 37.0884 | 37.0884 | 37.0884 | 37.0884 | 37.0884 | 37.0884
55% | 2598.4068 | 17.9368 | 25.335 | 27.2583 | 27.6607 | 27.9593 | 28.4408 | 29.5225 | 30.2478 | 31.1819 | 31.6306 | 32.0233 | 31.133 | 32.1031 | 33.5685 | 32.459 | 32.459 | 32.459 | 32.459 | 32.459 | 32.459 | 32.459 | 32.459 | 32.459 | 32.459 | 32.459 | 32.459 | 32.459 | 32.459 | 32.459 | 32.459 | 55% | 2598.4068 | 19.5043 | 26.7938 | 28.8046 | 29.1853 | 29.4147 | 29.8851 | 30.985 | 31.5763 | 32.7534 | 36.4343 | 33.2874 | 32.6254 | 33.4354 | 35.1504 | 33.9977 | 33.9977 | 33.9977 | 33.9977 | 33.9977 | 33.9977 | 33.9977 | 33.9977 | 33.9977 | 33.9977 | 33.9977 | 33.9977 | 33.9977 | 33.9977 | 33.9977 | 33.9977
50% | 3233.5201 | 16.3062 | 23.0318 | 24.7803 | 25.1461 | 25.4176 | 25.8553 | 26.8386 | 27.498 | 28.3472 | 28.7551 | 29.1121 | 28.3027 | 29.1846 | 30.5169 | 29.5082 | 29.5082 | 29.5082 | 29.5082 | 29.5082 | 29.5082 | 29.5082 | 29.5082 | 29.5082 | 29.5082 | 29.5082 | 29.5082 | 29.5082 | 29.5082 | 29.5082 | 29.5082 | 50% | 3233.5201 | 17.7312 | 24.358 | 26.186 | 26.5321 | 26.7407 | 27.1683 | 28.1682 | 28.7057 | 29.7758 | 33.1221 | 30.2613 | 29.6594 | 30.3958 | 31.9549 | 30.907 | 30.907 | 30.907 | 30.907 | 30.907 | 30.907 | 30.907 | 30.907 | 30.907 | 30.907 | 30.907 | 30.907 | 30.907 | 30.907 | 30.907 | 30.907
45% | 3775.313 | 14.6756 | 20.7286 | 22.3023 | 22.6315 | 22.8758 | 23.2698 | 24.1548 | 24.7482 | 25.5124 | 25.8796 | 26.2009 | 25.4724 | 26.2662 | 27.4652 | 26.5574 | 26.5574 | 26.5574 | 26.5574 | 26.5574 | 26.5574 | 26.5574 | 26.5574 | 26.5574 | 26.5574 | 26.5574 | 26.5574 | 26.5574 | 26.5574 | 26.5574 | 26.5574 | 45% | 3775.313 | 15.9581 | 21.9222 | 23.5674 | 23.8789 | 24.0666 | 24.4515 | 25.3514 | 25.8352 | 26.7983 | 29.8099 | 27.2351 | 26.6935 | 27.3562 | 28.7595 | 27.8163 | 27.8163 | 27.8163 | 27.8163 | 27.8163 | 27.8163 | 27.8163 | 27.8163 | 27.8163 | 27.8163 | 27.8163 | 27.8163 | 27.8163 | 27.8163 | 27.8163 | 27.8163
40% | 4072.8088 | 13.045 | 18.4254 | 19.8242 | 20.1169 | 20.3341 | 20.6842 | 21.4709 | 21.9984 | 22.6777 | 23.0041 | 23.2897 | 22.6422 | 23.3477 | 24.4135 | 23.6066 | 23.6066 | 23.6066 | 23.6066 | 23.6066 | 23.6066 | 23.6066 | 23.6066 | 23.6066 | 23.6066 | 23.6066 | 23.6066 | 23.6066 | 23.6066 | 23.6066 | 23.6066 | 40% | 4072.8088 | 14.185 | 19.4864 | 20.9488 | 21.2257 | 21.3925 | 21.7346 | 22.5346 | 22.9646 | 23.8207 | 26.4977 | 24.209 | 23.7276 | 24.3166 | 25.564 | 24.7256 | 24.7256 | 24.7256 | 24.7256 | 24.7256 | 24.7256 | 24.7256 | 24.7256 | 24.7256 | 24.7256 | 24.7256 | 24.7256 | 24.7256 | 24.7256 | 24.7256 | 24.7256
35% | 4198.821 | 11.4144 | 16.1222 | 17.3462 | 17.6023 | 17.7923 | 18.0987 | 18.787 | 19.2486 | 19.843 | 20.1286 | 20.3785 | 19.8119 | 20.4292 | 21.3618 | 20.6558 | 20.6558 | 20.6558 | 20.6558 | 20.6558 | 20.6558 | 20.6558 | 20.6558 | 20.6558 | 20.6558 | 20.6558 | 20.6558 | 20.6558 | 20.6558 | 20.6558 | 20.6558 | 35% | 4198.821 | 12.4119 | 17.0506 | 18.3302 | 18.5724 | 18.7185 | 19.0178 | 19.7177 | 20.094 | 20.8431 | 23.1855 | 21.1829 | 20.7616 | 21.2771 | 22.3685 | 21.6349 | 21.6349 | 21.6349 | 21.6349 | 21.6349 | 21.6349 | 21.6349 | 21.6349 | 21.6349 | 21.6349 | 21.6349 | 21.6349 | 21.6349 | 21.6349 | 21.6349 | 21.6349
30% | 4271.3374 | 9.7837 | 13.8191 | 14.8682 | 15.0877 | 15.2505 | 15.5132 | 16.1032 | 16.4988 | 17.0083 | 17.2531 | 17.4672 | 16.9816 | 17.5108 | 18.3101 | 17.7049 | 17.7049 | 17.7049 | 17.7049 | 17.7049 | 17.7049 | 17.7049 | 17.7049 | 17.7049 | 17.7049 | 17.7049 | 17.7049 | 17.7049 | 17.7049 | 17.7049 | 17.7049 | 30% | 4271.3374 | 10.6387 | 14.6148 | 15.7116 | 15.9192 | 16.0444 | 16.301 | 16.9009 | 17.2234 | 17.8655 | 19.8733 | 18.1568 | 17.7957 | 18.2375 | 19.173 | 18.5442 | 18.5442 | 18.5442 | 18.5442 | 18.5442 | 18.5442 | 18.5442 | 18.5442 | 18.5442 | 18.5442 | 18.5442 | 18.5442 | 18.5442 | 18.5442 | 18.5442 | 18.5442
25% | 4321.8611 | 8.1531 | 11.5159 | 12.3901 | 12.5731 | 12.7088 | 12.9276 | 13.4193 | 13.749 | 14.1736 | 14.3776 | 14.556 | 14.1513 | 14.5923 | 15.2584 | 14.7541 | 14.7541 | 14.7541 | 14.7541 | 14.7541 | 14.7541 | 14.7541 | 14.7541 | 14.7541 | 14.7541 | 14.7541 | 14.7541 | 14.7541 | 14.7541 | 14.7541 | 14.7541 | 25% | 4321.8611 | 8.8656 | 12.179 | 13.093 | 13.266 | 13.3703 | 13.5841 | 14.0841 | 14.3529 | 14.8879 | 16.561 | 15.1306 | 14.8297 | 15.1979 | 15.9775 | 15.4535 | 15.4535 | 15.4535 | 15.4535 | 15.4535 | 15.4535 | 15.4535 | 15.4535 | 15.4535 | 15.4535 | 15.4535 | 15.4535 | 15.4535 | 15.4535 | 15.4535 | 15.4535
20% | 4353.067 | 6.5225 | 9.2127 | 9.9121 | 10.0584 | 10.167 | 10.3421 | 10.7354 | 10.9992 | 11.3389 | 11.5021 | 11.6448 | 11.3211 | 11.6738 | 12.2067 | 11.8033 | 11.8033 | 11.8033 | 11.8033 | 11.8033 | 11.8033 | 11.8033 | 11.8033 | 11.8033 | 11.8033 | 11.8033 | 11.8033 | 11.8033 | 11.8033 | 11.8033 | 11.8033 | 20% | 4353.067 | 7.0925 | 9.7432 | 10.4744 | 10.6128 | 10.6963 | 10.8673 | 11.2673 | 11.4823 | 11.9103 | 13.2488 | 12.1045 | 11.8638 | 12.1583 | 12.782 | 12.3628 | 12.3628 | 12.3628 | 12.3628 | 12.3628 | 12.3628 | 12.3628 | 12.3628 | 12.3628 | 12.3628 | 12.3628 | 12.3628 | 12.3628 | 12.3628 | 12.3628 | 12.3628
15% | 4369.4129 | 4.8919 | 6.9095 | 7.4341 | 7.5438 | 7.6253 | 7.7566 | 8.0516 | 8.2494 | 8.5041 | 8.6265 | 8.7336 | 8.4908 | 8.7554 | 9.1551 | 8.8525 | 8.8525 | 8.8525 | 8.8525 | 8.8525 | 8.8525 | 8.8525 | 8.8525 | 8.8525 | 8.8525 | 8.8525 | 8.8525 | 8.8525 | 8.8525 | 8.8525 | 8.8525 | 15% | 4369.4129 | 5.3194 | 7.3074 | 7.8558 | 7.9596 | 8.0222 | 8.1505 | 8.4505 | 8.6117 | 8.9328 | 9.9366 | 9.0784 | 8.8978 | 9.1187 | 9.5865 | 9.2721 | 9.2721 | 9.2721 | 9.2721 | 9.2721 | 9.2721 | 9.2721 | 9.2721 | 9.2721 | 9.2721 | 9.2721 | 9.2721 | 9.2721 | 9.2721 | 9.2721 | 9.2721
10% | 4378.6261 | 3.2612 | 4.6064 | 4.9561 | 5.0292 | 5.0835 | 5.1711 | 5.3677 | 5.4996 | 5.6694 | 5.751 | 5.8224 | 5.6605 | 5.8369 | 6.1034 | 5.9016 | 5.9016 | 5.9016 | 5.9016 | 5.9016 | 5.9016 | 5.9016 | 5.9016 | 5.9016 | 5.9016 | 5.9016 | 5.9016 | 5.9016 | 5.9016 | 5.9016 | 5.9016 | 10% | 4378.6261 | 3.5462 | 4.8716 | 5.2372 | 5.3064 | 5.3481 | 5.4337 | 5.6336 | 5.7411 | 5.9552 | 6.6244 | 6.0523 | 5.9319 | 6.0792 | 6.391 | 6.1814 | 6.1814 | 6.1814 | 6.1814 | 6.1814 | 6.1814 | 6.1814 | 6.1814 | 6.1814 | 6.1814 | 6.1814 | 6.1814 | 6.1814 | 6.1814 | 6.1814 | 6.1814
5% | 4391.7028 | 1.6306 | 2.3032 | 2.478 | 2.5146 | 2.5418 | 2.5855 | 2.6839 | 2.7498 | 2.8347 | 2.8755 | 2.9112 | 2.8303 | 2.9185 | 3.0517 | 2.9508 | 2.9508 | 2.9508 | 2.9508 | 2.9508 | 2.9508 | 2.9508 | 2.9508 | 2.9508 | 2.9508 | 2.9508 | 2.9508 | 2.9508 | 2.9508 | 2.9508 | 2.9508 | 5% | 4391.7028 | 1.7731 | 2.4358 | 2.6186 | 2.6532 | 2.6741 | 2.7168 | 2.8168 | 2.8706 | 2.9776 | 3.3122 | 3.0261 | 2.9659 | 3.0396 | 3.1955 | 3.0907 | 3.0907 | 3.0907 | 3.0907 | 3.0907 | 3.0907 | 3.0907 | 3.0907 | 3.0907 | 3.0907 | 3.0907 | 3.0907 | 3.0907 | 3.0907 | 3.0907 | 3.0907
9.992e-14% | 4391.7028 | 3.2586e-14 | 4.6027e-14 | 4.9521e-14 | 5.0252e-14 | 5.0795e-14 | 5.1669e-14 | 5.3634e-14 | 5.4952e-14 | 5.6649e-14 | 5.7464e-14 | 5.8178e-14 | 5.656e-14 | 5.8323e-14 | 6.0985e-14 | 5.8969e-14 | 5.8969e-14 | 5.8969e-14 | 5.8969e-14 | 5.8969e-14 | 5.8969e-14 | 5.8969e-14 | 5.8969e-14 | 5.8969e-14 | 5.8969e-14 | 5.8969e-14 | 5.8969e-14 | 5.8969e-14 | 5.8969e-14 | 5.8969e-14 | 5.8969e-14 | 9.992e-14% | 4391.7028 | 3.5434e-14 | 4.8677e-14 | 5.233e-14 | 5.3022e-14 | 5.3439e-14 | 5.4293e-14 | 5.6291e-14 | 5.7366e-14 | 5.9504e-14 | 6.6191e-14 | 6.0474e-14 | 5.9271e-14 | 6.0743e-14 | 6.3859e-14 | 6.1765e-14 | 6.1765e-14 | 6.1765e-14 | 6.1765e-14 | 6.1765e-14 | 6.1765e-14 | 6.1765e-14 | 6.1765e-14 | 6.1765e-14 | 6.1765e-14 | 6.1765e-14 | 6.1765e-14 | 6.1765e-14 | 6.1765e-14 | 6.1765e-14 | 6.1765e-14
Summer Season | [31 empty] | Summer Season
P50 | [31 empty] | P10
% of MD | Summer - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Summer - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 38.1303 | 50.9986 | 54.5316 | 54.4514 | 54.4515 | 54.8647 | 55.2259 | 56.182 | 56.8413 | 57.1366 | 57.4816 | 57.7894 | 58.5251 | 59.326 | 59.362 | 59.362 | 59.362 | 59.362 | 59.362 | 59.362 | 59.362 | 59.362 | 59.362 | 59.362 | 59.362 | 59.362 | 59.362 | 59.362 | 59.362 | 59.362 | 100% | 0 | 43.4098 | 56.3083 | 59.6903 | 59.4923 | 59.5136 | 59.8642 | 60.7826 | 61.4008 | 62.0041 | 62.7089 | 63.3644 | 63.9989 | 64.075 | 64.8149 | 64.2613 | 64.2613 | 64.2613 | 64.2613 | 64.2613 | 64.2613 | 64.2613 | 64.2613 | 64.2613 | 64.2613 | 64.2613 | 64.2613 | 64.2613 | 64.2613 | 64.2613 | 64.2613
99% | 0 | 37.749 | 50.4886 | 53.9863 | 53.9069 | 53.907 | 54.316 | 54.6736 | 55.6202 | 56.2729 | 56.5653 | 56.9068 | 57.2115 | 57.9398 | 58.7328 | 58.7684 | 58.7684 | 58.7684 | 58.7684 | 58.7684 | 58.7684 | 58.7684 | 58.7684 | 58.7684 | 58.7684 | 58.7684 | 58.7684 | 58.7684 | 58.7684 | 58.7684 | 58.7684 | 99% | 1.5127 | 42.9757 | 55.7452 | 59.0933 | 58.8974 | 58.9184 | 59.2656 | 60.1748 | 60.7868 | 61.384 | 62.0818 | 62.7308 | 63.359 | 63.4343 | 64.1668 | 63.6187 | 63.6187 | 63.6187 | 63.6187 | 63.6187 | 63.6187 | 63.6187 | 63.6187 | 63.6187 | 63.6187 | 63.6187 | 63.6187 | 63.6187 | 63.6187 | 63.6187 | 63.6187
98% | 0 | 37.3677 | 49.9786 | 53.441 | 53.3624 | 53.3625 | 53.7674 | 54.1213 | 55.0584 | 55.7045 | 55.9939 | 56.332 | 56.6336 | 57.3546 | 58.1395 | 58.1748 | 58.1748 | 58.1748 | 58.1748 | 58.1748 | 58.1748 | 58.1748 | 58.1748 | 58.1748 | 58.1748 | 58.1748 | 58.1748 | 58.1748 | 58.1748 | 58.1748 | 58.1748 | 98% | 2.269 | 42.5416 | 55.1822 | 58.4964 | 58.3025 | 58.3233 | 58.6669 | 59.5669 | 60.1728 | 60.764 | 61.4548 | 62.0971 | 62.719 | 62.7935 | 63.5186 | 62.9761 | 62.9761 | 62.9761 | 62.9761 | 62.9761 | 62.9761 | 62.9761 | 62.9761 | 62.9761 | 62.9761 | 62.9761 | 62.9761 | 62.9761 | 62.9761 | 62.9761 | 62.9761
97% | 0.37816 | 36.9864 | 49.4686 | 52.8956 | 52.8179 | 52.818 | 53.2187 | 53.5691 | 54.4965 | 55.1361 | 55.4225 | 55.7571 | 56.0557 | 56.7693 | 57.5462 | 57.5812 | 57.5812 | 57.5812 | 57.5812 | 57.5812 | 57.5812 | 57.5812 | 57.5812 | 57.5812 | 57.5812 | 57.5812 | 57.5812 | 57.5812 | 57.5812 | 57.5812 | 57.5812 | 97% | 3.7816 | 42.1075 | 54.6191 | 57.8995 | 57.7075 | 57.7282 | 58.0683 | 58.9591 | 59.5588 | 60.1439 | 60.8277 | 61.4635 | 62.079 | 62.1528 | 62.8705 | 62.3335 | 62.3335 | 62.3335 | 62.3335 | 62.3335 | 62.3335 | 62.3335 | 62.3335 | 62.3335 | 62.3335 | 62.3335 | 62.3335 | 62.3335 | 62.3335 | 62.3335 | 62.3335
95% | 2.269 | 36.2238 | 48.4487 | 51.805 | 51.7289 | 51.729 | 52.1214 | 52.4646 | 53.3729 | 53.9993 | 54.2798 | 54.6075 | 54.8999 | 55.5988 | 56.3597 | 56.3939 | 56.3939 | 56.3939 | 56.3939 | 56.3939 | 56.3939 | 56.3939 | 56.3939 | 56.3939 | 56.3939 | 56.3939 | 56.3939 | 56.3939 | 56.3939 | 56.3939 | 56.3939 | 95% | 6.0506 | 41.2393 | 53.4929 | 56.7057 | 56.5177 | 56.5379 | 56.871 | 57.7435 | 58.3307 | 58.9039 | 59.5735 | 60.1962 | 60.799 | 60.8713 | 61.5742 | 61.0482 | 61.0482 | 61.0482 | 61.0482 | 61.0482 | 61.0482 | 61.0482 | 61.0482 | 61.0482 | 61.0482 | 61.0482 | 61.0482 | 61.0482 | 61.0482 | 61.0482 | 61.0482
90% | 5.6725 | 34.3173 | 45.8987 | 49.0784 | 49.0063 | 49.0064 | 49.3782 | 49.7033 | 50.5638 | 51.1572 | 51.423 | 51.7334 | 52.0105 | 52.6726 | 53.3934 | 53.4258 | 53.4258 | 53.4258 | 53.4258 | 53.4258 | 53.4258 | 53.4258 | 53.4258 | 53.4258 | 53.4258 | 53.4258 | 53.4258 | 53.4258 | 53.4258 | 53.4258 | 53.4258 | 90% | 16.2611 | 39.0688 | 50.6775 | 53.7212 | 53.5431 | 53.5622 | 53.8778 | 54.7043 | 55.2607 | 55.8037 | 56.438 | 57.028 | 57.5991 | 57.6675 | 58.3335 | 57.8352 | 57.8352 | 57.8352 | 57.8352 | 57.8352 | 57.8352 | 57.8352 | 57.8352 | 57.8352 | 57.8352 | 57.8352 | 57.8352 | 57.8352 | 57.8352 | 57.8352 | 57.8352
85% | 15.8829 | 32.4108 | 43.3488 | 46.3519 | 46.2837 | 46.2838 | 46.635 | 46.942 | 47.7547 | 48.3151 | 48.5662 | 48.8593 | 49.121 | 49.7463 | 50.4271 | 50.4577 | 50.4577 | 50.4577 | 50.4577 | 50.4577 | 50.4577 | 50.4577 | 50.4577 | 50.4577 | 50.4577 | 50.4577 | 50.4577 | 50.4577 | 50.4577 | 50.4577 | 50.4577 | 85% | 26.4715 | 36.8983 | 47.8621 | 50.7367 | 50.5685 | 50.5865 | 50.8846 | 51.6652 | 52.1907 | 52.7035 | 53.3026 | 53.8598 | 54.3991 | 54.4638 | 55.0927 | 54.6221 | 54.6221 | 54.6221 | 54.6221 | 54.6221 | 54.6221 | 54.6221 | 54.6221 | 54.6221 | 54.6221 | 54.6221 | 54.6221 | 54.6221 | 54.6221 | 54.6221 | 54.6221
80% | 31.0095 | 30.5043 | 40.7989 | 43.6253 | 43.5612 | 43.5612 | 43.8917 | 44.1807 | 44.9456 | 45.4731 | 45.7093 | 45.9853 | 46.2315 | 46.8201 | 47.4608 | 47.4896 | 47.4896 | 47.4896 | 47.4896 | 47.4896 | 47.4896 | 47.4896 | 47.4896 | 47.4896 | 47.4896 | 47.4896 | 47.4896 | 47.4896 | 47.4896 | 47.4896 | 47.4896 | 80% | 34.0348 | 34.7278 | 45.0467 | 47.7522 | 47.5938 | 47.6109 | 47.8914 | 48.6261 | 49.1206 | 49.6033 | 50.1671 | 50.6915 | 51.1992 | 51.26 | 51.852 | 51.409 | 51.409 | 51.409 | 51.409 | 51.409 | 51.409 | 51.409 | 51.409 | 51.409 | 51.409 | 51.409 | 51.409 | 51.409 | 51.409 | 51.409 | 51.409
75% | 72.9857 | 28.5977 | 38.249 | 40.8987 | 40.8386 | 40.8387 | 41.1485 | 41.4194 | 42.1365 | 42.631 | 42.8525 | 43.1112 | 43.3421 | 43.8938 | 44.4945 | 44.5215 | 44.5215 | 44.5215 | 44.5215 | 44.5215 | 44.5215 | 44.5215 | 44.5215 | 44.5215 | 44.5215 | 44.5215 | 44.5215 | 44.5215 | 44.5215 | 44.5215 | 44.5215 | 75% | 48.405 | 32.5573 | 42.2312 | 44.7677 | 44.6192 | 44.6352 | 44.8982 | 45.5869 | 46.0506 | 46.503 | 47.0317 | 47.5233 | 47.9992 | 48.0563 | 48.6112 | 48.196 | 48.196 | 48.196 | 48.196 | 48.196 | 48.196 | 48.196 | 48.196 | 48.196 | 48.196 | 48.196 | 48.196 | 48.196 | 48.196 | 48.196 | 48.196
70% | 150.5094 | 26.6912 | 35.699 | 38.1721 | 38.116 | 38.1161 | 38.4053 | 38.6581 | 39.3274 | 39.7889 | 39.9957 | 40.2371 | 40.4526 | 40.9675 | 41.5282 | 41.5534 | 41.5534 | 41.5534 | 41.5534 | 41.5534 | 41.5534 | 41.5534 | 41.5534 | 41.5534 | 41.5534 | 41.5534 | 41.5534 | 41.5534 | 41.5534 | 41.5534 | 41.5534 | 70% | 76.3892 | 30.3869 | 39.4158 | 41.7832 | 41.6446 | 41.6595 | 41.905 | 42.5478 | 42.9805 | 43.4028 | 43.8963 | 44.3551 | 44.7993 | 44.8525 | 45.3705 | 44.9829 | 44.9829 | 44.9829 | 44.9829 | 44.9829 | 44.9829 | 44.9829 | 44.9829 | 44.9829 | 44.9829 | 44.9829 | 44.9829 | 44.9829 | 44.9829 | 44.9829 | 44.9829
65% | 359.6342 | 24.7847 | 33.1491 | 35.4455 | 35.3934 | 35.3935 | 35.662 | 35.8968 | 36.5183 | 36.9469 | 37.1388 | 37.363 | 37.5631 | 38.0413 | 38.5619 | 38.5853 | 38.5853 | 38.5853 | 38.5853 | 38.5853 | 38.5853 | 38.5853 | 38.5853 | 38.5853 | 38.5853 | 38.5853 | 38.5853 | 38.5853 | 38.5853 | 38.5853 | 38.5853 | 65% | 114.2056 | 28.2164 | 36.6004 | 38.7987 | 38.67 | 38.6838 | 38.9117 | 39.5087 | 39.9105 | 40.3026 | 40.7608 | 41.1869 | 41.5993 | 41.6488 | 42.1297 | 41.7698 | 41.7698 | 41.7698 | 41.7698 | 41.7698 | 41.7698 | 41.7698 | 41.7698 | 41.7698 | 41.7698 | 41.7698 | 41.7698 | 41.7698 | 41.7698 | 41.7698 | 41.7698
60% | 689.7717 | 22.8782 | 30.5992 | 32.719 | 32.6709 | 32.6709 | 32.9188 | 33.1355 | 33.7092 | 34.1048 | 34.282 | 34.4889 | 34.6736 | 35.115 | 35.5956 | 35.6172 | 35.6172 | 35.6172 | 35.6172 | 35.6172 | 35.6172 | 35.6172 | 35.6172 | 35.6172 | 35.6172 | 35.6172 | 35.6172 | 35.6172 | 35.6172 | 35.6172 | 35.6172 | 60% | 178.1154 | 26.0459 | 33.785 | 35.8142 | 35.6954 | 35.7081 | 35.9185 | 36.4696 | 36.8405 | 37.2024 | 37.6254 | 38.0187 | 38.3994 | 38.445 | 38.889 | 38.5568 | 38.5568 | 38.5568 | 38.5568 | 38.5568 | 38.5568 | 38.5568 | 38.5568 | 38.5568 | 38.5568 | 38.5568 | 38.5568 | 38.5568 | 38.5568 | 38.5568 | 38.5568
55% | 1095.5419 | 20.9717 | 28.0492 | 29.9924 | 29.9483 | 29.9483 | 30.1756 | 30.3742 | 30.9001 | 31.2627 | 31.4252 | 31.6149 | 31.7842 | 32.1888 | 32.6293 | 32.6491 | 32.6491 | 32.6491 | 32.6491 | 32.6491 | 32.6491 | 32.6491 | 32.6491 | 32.6491 | 32.6491 | 32.6491 | 32.6491 | 32.6491 | 32.6491 | 32.6491 | 32.6491 | 55% | 311.6074 | 23.8754 | 30.9696 | 32.8296 | 32.7208 | 32.7325 | 32.9253 | 33.4304 | 33.7704 | 34.1022 | 34.4899 | 34.8504 | 35.1994 | 35.2413 | 35.6482 | 35.3437 | 35.3437 | 35.3437 | 35.3437 | 35.3437 | 35.3437 | 35.3437 | 35.3437 | 35.3437 | 35.3437 | 35.3437 | 35.3437 | 35.3437 | 35.3437 | 35.3437 | 35.3437
50% | 1666.1918 | 19.0652 | 25.4993 | 27.2658 | 27.2257 | 27.2258 | 27.4323 | 27.6129 | 28.091 | 28.4207 | 28.5683 | 28.7408 | 28.8947 | 29.2625 | 29.663 | 29.681 | 29.681 | 29.681 | 29.681 | 29.681 | 29.681 | 29.681 | 29.681 | 29.681 | 29.681 | 29.681 | 29.681 | 29.681 | 29.681 | 29.681 | 29.681 | 50% | 636.0723 | 21.7049 | 28.1542 | 29.8451 | 29.7462 | 29.7568 | 29.9321 | 30.3913 | 30.7004 | 31.002 | 31.3545 | 31.6822 | 31.9995 | 32.0375 | 32.4075 | 32.1307 | 32.1307 | 32.1307 | 32.1307 | 32.1307 | 32.1307 | 32.1307 | 32.1307 | 32.1307 | 32.1307 | 32.1307 | 32.1307 | 32.1307 | 32.1307 | 32.1307 | 32.1307
45% | 2506.0947 | 17.1586 | 22.9494 | 24.5392 | 24.5032 | 24.5032 | 24.6891 | 24.8516 | 25.2819 | 25.5786 | 25.7115 | 25.8667 | 26.0052 | 26.3363 | 26.6967 | 26.7129 | 26.7129 | 26.7129 | 26.7129 | 26.7129 | 26.7129 | 26.7129 | 26.7129 | 26.7129 | 26.7129 | 26.7129 | 26.7129 | 26.7129 | 26.7129 | 26.7129 | 26.7129 | 45% | 1179.4944 | 19.5344 | 25.3387 | 26.8606 | 26.7715 | 26.7811 | 26.9389 | 27.3522 | 27.6303 | 27.9018 | 28.219 | 28.514 | 28.7995 | 28.8338 | 29.1667 | 28.9176 | 28.9176 | 28.9176 | 28.9176 | 28.9176 | 28.9176 | 28.9176 | 28.9176 | 28.9176 | 28.9176 | 28.9176 | 28.9176 | 28.9176 | 28.9176 | 28.9176 | 28.9176
40% | 3164.4787 | 15.2521 | 20.3994 | 21.8126 | 21.7806 | 21.7806 | 21.9459 | 22.0903 | 22.4728 | 22.7365 | 22.8547 | 22.9926 | 23.1158 | 23.41 | 23.7304 | 23.7448 | 23.7448 | 23.7448 | 23.7448 | 23.7448 | 23.7448 | 23.7448 | 23.7448 | 23.7448 | 23.7448 | 23.7448 | 23.7448 | 23.7448 | 23.7448 | 23.7448 | 23.7448 | 40% | 1808.3816 | 17.3639 | 22.5233 | 23.8761 | 23.7969 | 23.8054 | 23.9457 | 24.313 | 24.5603 | 24.8016 | 25.0836 | 25.3458 | 25.5996 | 25.63 | 25.926 | 25.7045 | 25.7045 | 25.7045 | 25.7045 | 25.7045 | 25.7045 | 25.7045 | 25.7045 | 25.7045 | 25.7045 | 25.7045 | 25.7045 | 25.7045 | 25.7045 | 25.7045 | 25.7045
35% | 3551.3408 | 13.3456 | 17.8495 | 19.0861 | 19.058 | 19.058 | 19.2026 | 19.3291 | 19.6637 | 19.8945 | 19.9978 | 20.1186 | 20.2263 | 20.4838 | 20.7641 | 20.7767 | 20.7767 | 20.7767 | 20.7767 | 20.7767 | 20.7767 | 20.7767 | 20.7767 | 20.7767 | 20.7767 | 20.7767 | 20.7767 | 20.7767 | 20.7767 | 20.7767 | 20.7767 | 35% | 2779.1293 | 15.1934 | 19.7079 | 20.8916 | 20.8223 | 20.8297 | 20.9525 | 21.2739 | 21.4903 | 21.7014 | 21.9481 | 22.1775 | 22.3996 | 22.4263 | 22.6852 | 22.4915 | 22.4915 | 22.4915 | 22.4915 | 22.4915 | 22.4915 | 22.4915 | 22.4915 | 22.4915 | 22.4915 | 22.4915 | 22.4915 | 22.4915 | 22.4915 | 22.4915 | 22.4915
30% | 3758.953 | 11.4391 | 15.2996 | 16.3595 | 16.3354 | 16.3355 | 16.4594 | 16.5678 | 16.8546 | 17.0524 | 17.141 | 17.2445 | 17.3368 | 17.5575 | 17.7978 | 17.8086 | 17.8086 | 17.8086 | 17.8086 | 17.8086 | 17.8086 | 17.8086 | 17.8086 | 17.8086 | 17.8086 | 17.8086 | 17.8086 | 17.8086 | 17.8086 | 17.8086 | 17.8086 | 30% | 3814.165 | 13.0229 | 16.8925 | 17.9071 | 17.8477 | 17.8541 | 17.9593 | 18.2348 | 18.4202 | 18.6012 | 18.8127 | 19.0093 | 19.1997 | 19.2225 | 19.4445 | 19.2784 | 19.2784 | 19.2784 | 19.2784 | 19.2784 | 19.2784 | 19.2784 | 19.2784 | 19.2784 | 19.2784 | 19.2784 | 19.2784 | 19.2784 | 19.2784 | 19.2784 | 19.2784
25% | 3926.4798 | 9.5326 | 12.7497 | 13.6329 | 13.6129 | 13.6129 | 13.7162 | 13.8065 | 14.0455 | 14.2103 | 14.2842 | 14.3704 | 14.4474 | 14.6313 | 14.8315 | 14.8405 | 14.8405 | 14.8405 | 14.8405 | 14.8405 | 14.8405 | 14.8405 | 14.8405 | 14.8405 | 14.8405 | 14.8405 | 14.8405 | 14.8405 | 14.8405 | 14.8405 | 14.8405 | 25% | 4166.9923 | 10.8524 | 14.0771 | 14.9226 | 14.8731 | 14.8784 | 14.9661 | 15.1956 | 15.3502 | 15.501 | 15.6772 | 15.8411 | 15.9997 | 16.0188 | 16.2037 | 16.0653 | 16.0653 | 16.0653 | 16.0653 | 16.0653 | 16.0653 | 16.0653 | 16.0653 | 16.0653 | 16.0653 | 16.0653 | 16.0653 | 16.0653 | 16.0653 | 16.0653 | 16.0653
20% | 4050.5177 | 7.6261 | 10.1997 | 10.9063 | 10.8903 | 10.8903 | 10.9729 | 11.0452 | 11.2364 | 11.3683 | 11.4273 | 11.4963 | 11.5579 | 11.705 | 11.8652 | 11.8724 | 11.8724 | 11.8724 | 11.8724 | 11.8724 | 11.8724 | 11.8724 | 11.8724 | 11.8724 | 11.8724 | 11.8724 | 11.8724 | 11.8724 | 11.8724 | 11.8724 | 11.8724 | 20% | 4282.7105 | 8.682 | 11.2617 | 11.9381 | 11.8985 | 11.9027 | 11.9728 | 12.1565 | 12.2802 | 12.4008 | 12.5418 | 12.6729 | 12.7998 | 12.815 | 12.963 | 12.8523 | 12.8523 | 12.8523 | 12.8523 | 12.8523 | 12.8523 | 12.8523 | 12.8523 | 12.8523 | 12.8523 | 12.8523 | 12.8523 | 12.8523 | 12.8523 | 12.8523 | 12.8523
15% | 4152.622 | 5.7195 | 7.6498 | 8.1797 | 8.1677 | 8.1677 | 8.2297 | 8.2839 | 8.4273 | 8.5262 | 8.5705 | 8.6222 | 8.6684 | 8.7788 | 8.8989 | 8.9043 | 8.9043 | 8.9043 | 8.9043 | 8.9043 | 8.9043 | 8.9043 | 8.9043 | 8.9043 | 8.9043 | 8.9043 | 8.9043 | 8.9043 | 8.9043 | 8.9043 | 8.9043 | 15% | 4364.7722 | 6.5115 | 8.4462 | 8.9535 | 8.9238 | 8.927 | 8.9796 | 9.1174 | 9.2101 | 9.3006 | 9.4063 | 9.5047 | 9.5998 | 9.6113 | 9.7222 | 9.6392 | 9.6392 | 9.6392 | 9.6392 | 9.6392 | 9.6392 | 9.6392 | 9.6392 | 9.6392 | 9.6392 | 9.6392 | 9.6392 | 9.6392 | 9.6392 | 9.6392 | 9.6392
10% | 4248.2976 | 3.813 | 5.0999 | 5.4532 | 5.4451 | 5.4452 | 5.4865 | 5.5226 | 5.6182 | 5.6841 | 5.7137 | 5.7482 | 5.7789 | 5.8525 | 5.9326 | 5.9362 | 5.9362 | 5.9362 | 5.9362 | 5.9362 | 5.9362 | 5.9362 | 5.9362 | 5.9362 | 5.9362 | 5.9362 | 5.9362 | 5.9362 | 5.9362 | 5.9362 | 5.9362 | 10% | 4391.6218 | 4.341 | 5.6308 | 5.969 | 5.9492 | 5.9514 | 5.9864 | 6.0783 | 6.1401 | 6.2004 | 6.2709 | 6.3364 | 6.3999 | 6.4075 | 6.4815 | 6.4261 | 6.4261 | 6.4261 | 6.4261 | 6.4261 | 6.4261 | 6.4261 | 6.4261 | 6.4261 | 6.4261 | 6.4261 | 6.4261 | 6.4261 | 6.4261 | 6.4261 | 6.4261
5% | 4361.7469 | 1.9065 | 2.5499 | 2.7266 | 2.7226 | 2.7226 | 2.7432 | 2.7613 | 2.8091 | 2.8421 | 2.8568 | 2.8741 | 2.8895 | 2.9263 | 2.9663 | 2.9681 | 2.9681 | 2.9681 | 2.9681 | 2.9681 | 2.9681 | 2.9681 | 2.9681 | 2.9681 | 2.9681 | 2.9681 | 2.9681 | 2.9681 | 2.9681 | 2.9681 | 2.9681 | 5% | 4391.6218 | 2.1705 | 2.8154 | 2.9845 | 2.9746 | 2.9757 | 2.9932 | 3.0391 | 3.07 | 3.1002 | 3.1354 | 3.1682 | 3.1999 | 3.2038 | 3.2407 | 3.2131 | 3.2131 | 3.2131 | 3.2131 | 3.2131 | 3.2131 | 3.2131 | 3.2131 | 3.2131 | 3.2131 | 3.2131 | 3.2131 | 3.2131 | 3.2131 | 3.2131 | 3.2131
9.992e-14% | 4391.6218 | 3.81e-14 | 5.0958e-14 | 5.4488e-14 | 5.4408e-14 | 5.4408e-14 | 5.4821e-14 | 5.5182e-14 | 5.6137e-14 | 5.6796e-14 | 5.7091e-14 | 5.7436e-14 | 5.7743e-14 | 5.8478e-14 | 5.9279e-14 | 5.9315e-14 | 5.9315e-14 | 5.9315e-14 | 5.9315e-14 | 5.9315e-14 | 5.9315e-14 | 5.9315e-14 | 5.9315e-14 | 5.9315e-14 | 5.9315e-14 | 5.9315e-14 | 5.9315e-14 | 5.9315e-14 | 5.9315e-14 | 5.9315e-14 | 5.9315e-14 | 9.992e-14% | 4391.6218 | 4.3375e-14 | 5.6263e-14 | 5.9643e-14 | 5.9445e-14 | 5.9466e-14 | 5.9816e-14 | 6.0734e-14 | 6.1352e-14 | 6.1955e-14 | 6.2659e-14 | 6.3314e-14 | 6.3948e-14 | 6.4024e-14 | 6.4763e-14 | 6.421e-14 | 6.421e-14 | 6.421e-14 | 6.421e-14 | 6.421e-14 | 6.421e-14 | 6.421e-14 | 6.421e-14 | 6.421e-14 | 6.421e-14 | 6.421e-14 | 6.421e-14 | 6.421e-14 | 6.421e-14 | 6.421e-14 | 6.421e-14
Option 7
Winter Season | [31 empty] | Winter Season
P50 | [31 empty] | P10
% of MD | Winter - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Winter - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 40.358 | 56.0239 | 60.0964 | 60.7906 | 61.3321 | 62.2643 | 64.3852 | 65.8049 | 67.6034 | 68.5369 | 69.3582 | 67.845 | 69.6185 | 72.4066 | 70.2908 | 70.2908 | 70.2908 | 70.2908 | 70.2908 | 70.2908 | 70.2908 | 70.2908 | 70.2908 | 70.2908 | 70.2908 | 70.2908 | 70.2908 | 70.2908 | 70.2908 | 70.2908 | 100% | 0 | 43.208 | 58.6763 | 62.9078 | 63.5625 | 63.9783 | 64.8903 | 67.0443 | 68.2204 | 70.4608 | 77.2709 | 71.6566 | 70.5585 | 72.0408 | 75.2827 | 73.0883 | 73.0883 | 73.0883 | 73.0883 | 73.0883 | 73.0883 | 73.0883 | 73.0883 | 73.0883 | 73.0883 | 73.0883 | 73.0883 | 73.0883 | 73.0883 | 73.0883 | 73.0883
99% | 1.486 | 39.9544 | 55.4636 | 59.4955 | 60.1827 | 60.7187 | 61.6416 | 63.7413 | 65.1468 | 66.9274 | 67.8516 | 68.6646 | 67.1665 | 68.9223 | 71.6825 | 69.5879 | 69.5879 | 69.5879 | 69.5879 | 69.5879 | 69.5879 | 69.5879 | 69.5879 | 69.5879 | 69.5879 | 69.5879 | 69.5879 | 69.5879 | 69.5879 | 69.5879 | 69.5879 | 99% | 1.486 | 42.7759 | 58.0895 | 62.2787 | 62.9269 | 63.3385 | 64.2414 | 66.3739 | 67.5382 | 69.7562 | 76.4982 | 70.9401 | 69.8529 | 71.3204 | 74.5299 | 72.3575 | 72.3575 | 72.3575 | 72.3575 | 72.3575 | 72.3575 | 72.3575 | 72.3575 | 72.3575 | 72.3575 | 72.3575 | 72.3575 | 72.3575 | 72.3575 | 72.3575 | 72.3575
98% | 3.2692 | 39.5508 | 54.9034 | 58.8945 | 59.5748 | 60.1054 | 61.019 | 63.0975 | 64.4888 | 66.2513 | 67.1662 | 67.9711 | 66.4881 | 68.2261 | 70.9584 | 68.885 | 68.885 | 68.885 | 68.885 | 68.885 | 68.885 | 68.885 | 68.885 | 68.885 | 68.885 | 68.885 | 68.885 | 68.885 | 68.885 | 68.885 | 68.885 | 98% | 3.2692 | 42.3438 | 57.5027 | 61.6497 | 62.2913 | 62.6987 | 63.5925 | 65.7034 | 66.856 | 69.0516 | 75.7255 | 70.2235 | 69.1473 | 70.6 | 73.7771 | 71.6266 | 71.6266 | 71.6266 | 71.6266 | 71.6266 | 71.6266 | 71.6266 | 71.6266 | 71.6266 | 71.6266 | 71.6266 | 71.6266 | 71.6266 | 71.6266 | 71.6266 | 71.6266
97% | 6.8356 | 39.1473 | 54.3431 | 58.2935 | 58.9669 | 59.4921 | 60.3964 | 62.4536 | 63.8307 | 65.5753 | 66.4808 | 67.2775 | 65.8096 | 67.5299 | 70.2344 | 68.1821 | 68.1821 | 68.1821 | 68.1821 | 68.1821 | 68.1821 | 68.1821 | 68.1821 | 68.1821 | 68.1821 | 68.1821 | 68.1821 | 68.1821 | 68.1821 | 68.1821 | 68.1821 | 97% | 6.8356 | 41.9118 | 56.916 | 61.0206 | 61.6557 | 62.0589 | 62.9436 | 65.033 | 66.1738 | 68.3469 | 74.9528 | 69.5069 | 68.4417 | 69.8796 | 73.0243 | 70.8957 | 70.8957 | 70.8957 | 70.8957 | 70.8957 | 70.8957 | 70.8957 | 70.8957 | 70.8957 | 70.8957 | 70.8957 | 70.8957 | 70.8957 | 70.8957 | 70.8957 | 70.8957
95% | 17.5347 | 38.3401 | 53.2227 | 57.0916 | 57.7511 | 58.2655 | 59.1511 | 61.1659 | 62.5146 | 64.2232 | 65.1101 | 65.8903 | 64.4527 | 66.1375 | 68.7862 | 66.7762 | 66.7762 | 66.7762 | 66.7762 | 66.7762 | 66.7762 | 66.7762 | 66.7762 | 66.7762 | 66.7762 | 66.7762 | 66.7762 | 66.7762 | 66.7762 | 66.7762 | 66.7762 | 95% | 17.5347 | 41.0476 | 55.7425 | 59.7624 | 60.3844 | 60.7794 | 61.6458 | 63.6921 | 64.8094 | 66.9377 | 73.4073 | 68.0738 | 67.0306 | 68.4388 | 71.5186 | 69.4339 | 69.4339 | 69.4339 | 69.4339 | 69.4339 | 69.4339 | 69.4339 | 69.4339 | 69.4339 | 69.4339 | 69.4339 | 69.4339 | 69.4339 | 69.4339 | 69.4339 | 69.4339
90% | 78.7576 | 36.3222 | 50.4215 | 54.0868 | 54.7116 | 55.1988 | 56.0379 | 57.9467 | 59.2244 | 60.8431 | 61.6833 | 62.4224 | 61.0605 | 62.6566 | 65.1659 | 63.2617 | 63.2617 | 63.2617 | 63.2617 | 63.2617 | 63.2617 | 63.2617 | 63.2617 | 63.2617 | 63.2617 | 63.2617 | 63.2617 | 63.2617 | 63.2617 | 63.2617 | 63.2617 | 90% | 78.7576 | 38.8872 | 52.8086 | 56.617 | 57.2063 | 57.5804 | 58.4013 | 60.3399 | 61.3984 | 63.4147 | 69.5438 | 64.491 | 63.5026 | 64.8368 | 67.7545 | 65.7795 | 65.7795 | 65.7795 | 65.7795 | 65.7795 | 65.7795 | 65.7795 | 65.7795 | 65.7795 | 65.7795 | 65.7795 | 65.7795 | 65.7795 | 65.7795 | 65.7795 | 65.7795
85% | 236.8672 | 34.3043 | 47.6203 | 51.082 | 51.672 | 52.1322 | 52.9246 | 54.7274 | 55.9342 | 57.4629 | 58.2564 | 58.9545 | 57.6682 | 59.1757 | 61.5456 | 59.7472 | 59.7472 | 59.7472 | 59.7472 | 59.7472 | 59.7472 | 59.7472 | 59.7472 | 59.7472 | 59.7472 | 59.7472 | 59.7472 | 59.7472 | 59.7472 | 59.7472 | 59.7472 | 85% | 236.8672 | 36.7268 | 49.8748 | 53.4716 | 54.0282 | 54.3815 | 55.1567 | 56.9877 | 57.9873 | 59.8917 | 65.6803 | 60.9081 | 59.9747 | 61.2347 | 63.9903 | 62.1251 | 62.1251 | 62.1251 | 62.1251 | 62.1251 | 62.1251 | 62.1251 | 62.1251 | 62.1251 | 62.1251 | 62.1251 | 62.1251 | 62.1251 | 62.1251 | 62.1251 | 62.1251
80% | 497.5104 | 32.2864 | 44.8191 | 48.0771 | 48.6325 | 49.0656 | 49.8114 | 51.5081 | 52.6439 | 54.0827 | 54.8296 | 55.4866 | 54.276 | 55.6948 | 57.9252 | 56.2326 | 56.2326 | 56.2326 | 56.2326 | 56.2326 | 56.2326 | 56.2326 | 56.2326 | 56.2326 | 56.2326 | 56.2326 | 56.2326 | 56.2326 | 56.2326 | 56.2326 | 56.2326 | 80% | 497.5104 | 34.5664 | 46.941 | 50.3262 | 50.85 | 51.1826 | 51.9122 | 53.6355 | 54.5763 | 56.3686 | 61.8167 | 57.3253 | 56.4468 | 57.6327 | 60.2262 | 58.4707 | 58.4707 | 58.4707 | 58.4707 | 58.4707 | 58.4707 | 58.4707 | 58.4707 | 58.4707 | 58.4707 | 58.4707 | 58.4707 | 58.4707 | 58.4707 | 58.4707 | 58.4707
75% | 803.6248 | 30.2685 | 42.0179 | 45.0723 | 45.593 | 45.999 | 46.6982 | 48.2889 | 49.3537 | 50.7026 | 51.4027 | 52.0187 | 50.8837 | 52.2138 | 54.3049 | 52.7181 | 52.7181 | 52.7181 | 52.7181 | 52.7181 | 52.7181 | 52.7181 | 52.7181 | 52.7181 | 52.7181 | 52.7181 | 52.7181 | 52.7181 | 52.7181 | 52.7181 | 52.7181 | 75% | 803.6248 | 32.406 | 44.0072 | 47.1809 | 47.6719 | 47.9837 | 48.6677 | 50.2832 | 51.1653 | 52.8456 | 57.9532 | 53.7425 | 52.9189 | 54.0306 | 56.4621 | 54.8163 | 54.8163 | 54.8163 | 54.8163 | 54.8163 | 54.8163 | 54.8163 | 54.8163 | 54.8163 | 54.8163 | 54.8163 | 54.8163 | 54.8163 | 54.8163 | 54.8163 | 54.8163
70% | 1155.2107 | 28.2506 | 39.2167 | 42.0675 | 42.5534 | 42.9324 | 43.585 | 45.0696 | 46.0634 | 47.3224 | 47.9759 | 48.5508 | 47.4915 | 48.7329 | 50.6846 | 49.2035 | 49.2035 | 49.2035 | 49.2035 | 49.2035 | 49.2035 | 49.2035 | 49.2035 | 49.2035 | 49.2035 | 49.2035 | 49.2035 | 49.2035 | 49.2035 | 49.2035 | 49.2035 | 70% | 1155.2107 | 30.2456 | 41.0734 | 44.0355 | 44.4938 | 44.7848 | 45.4232 | 46.931 | 47.7543 | 49.3225 | 54.0896 | 50.1596 | 49.3909 | 50.4286 | 52.6979 | 51.1618 | 51.1618 | 51.1618 | 51.1618 | 51.1618 | 51.1618 | 51.1618 | 51.1618 | 51.1618 | 51.1618 | 51.1618 | 51.1618 | 51.1618 | 51.1618 | 51.1618 | 51.1618
65% | 1553.1596 | 26.2327 | 36.4155 | 39.0627 | 39.5139 | 39.8658 | 40.4718 | 41.8504 | 42.7732 | 43.9422 | 44.549 | 45.0828 | 44.0992 | 45.252 | 47.0643 | 45.689 | 45.689 | 45.689 | 45.689 | 45.689 | 45.689 | 45.689 | 45.689 | 45.689 | 45.689 | 45.689 | 45.689 | 45.689 | 45.689 | 45.689 | 45.689 | 65% | 1553.1596 | 28.0852 | 38.1396 | 40.8901 | 41.3157 | 41.5859 | 42.1787 | 43.5788 | 44.3433 | 45.7995 | 50.2261 | 46.5768 | 45.863 | 46.8266 | 48.9338 | 47.5074 | 47.5074 | 47.5074 | 47.5074 | 47.5074 | 47.5074 | 47.5074 | 47.5074 | 47.5074 | 47.5074 | 47.5074 | 47.5074 | 47.5074 | 47.5074 | 47.5074 | 47.5074
60% | 2026.2996 | 24.2148 | 33.6143 | 36.0579 | 36.4744 | 36.7992 | 37.3586 | 38.6311 | 39.4829 | 40.562 | 41.1222 | 41.6149 | 40.707 | 41.7711 | 43.4439 | 42.1745 | 42.1745 | 42.1745 | 42.1745 | 42.1745 | 42.1745 | 42.1745 | 42.1745 | 42.1745 | 42.1745 | 42.1745 | 42.1745 | 42.1745 | 42.1745 | 42.1745 | 42.1745 | 60% | 2026.2996 | 25.9248 | 35.2058 | 37.7447 | 38.1375 | 38.387 | 38.9342 | 40.2266 | 40.9322 | 42.2765 | 46.3625 | 42.994 | 42.3351 | 43.2245 | 45.1696 | 43.853 | 43.853 | 43.853 | 43.853 | 43.853 | 43.853 | 43.853 | 43.853 | 43.853 | 43.853 | 43.853 | 43.853 | 43.853 | 43.853 | 43.853 | 43.853
55% | 2598.4068 | 22.1969 | 30.8131 | 33.053 | 33.4348 | 33.7326 | 34.2454 | 35.4119 | 36.1927 | 37.1819 | 37.6953 | 38.147 | 37.3147 | 38.2902 | 39.8236 | 38.6599 | 38.6599 | 38.6599 | 38.6599 | 38.6599 | 38.6599 | 38.6599 | 38.6599 | 38.6599 | 38.6599 | 38.6599 | 38.6599 | 38.6599 | 38.6599 | 38.6599 | 38.6599 | 55% | 2598.4068 | 23.7644 | 32.272 | 34.5993 | 34.9594 | 35.188 | 35.6897 | 36.8744 | 37.5212 | 38.7534 | 42.499 | 39.4111 | 38.8072 | 39.6225 | 41.4055 | 40.1986 | 40.1986 | 40.1986 | 40.1986 | 40.1986 | 40.1986 | 40.1986 | 40.1986 | 40.1986 | 40.1986 | 40.1986 | 40.1986 | 40.1986 | 40.1986 | 40.1986 | 40.1986
50% | 3233.5201 | 20.179 | 28.0119 | 30.0482 | 30.3953 | 30.666 | 31.1321 | 32.1926 | 32.9024 | 33.8017 | 34.2685 | 34.6791 | 33.9225 | 34.8092 | 36.2033 | 35.1454 | 35.1454 | 35.1454 | 35.1454 | 35.1454 | 35.1454 | 35.1454 | 35.1454 | 35.1454 | 35.1454 | 35.1454 | 35.1454 | 35.1454 | 35.1454 | 35.1454 | 35.1454 | 50% | 3233.5201 | 21.604 | 29.3381 | 31.4539 | 31.7813 | 31.9891 | 32.4451 | 33.5222 | 34.1102 | 35.2304 | 38.6354 | 35.8283 | 35.2792 | 36.0204 | 37.6414 | 36.5442 | 36.5442 | 36.5442 | 36.5442 | 36.5442 | 36.5442 | 36.5442 | 36.5442 | 36.5442 | 36.5442 | 36.5442 | 36.5442 | 36.5442 | 36.5442 | 36.5442 | 36.5442
45% | 3775.313 | 18.1611 | 25.2107 | 27.0434 | 27.3558 | 27.5994 | 28.0189 | 28.9733 | 29.6122 | 30.4215 | 30.8416 | 31.2112 | 30.5302 | 31.3283 | 32.583 | 31.6309 | 31.6309 | 31.6309 | 31.6309 | 31.6309 | 31.6309 | 31.6309 | 31.6309 | 31.6309 | 31.6309 | 31.6309 | 31.6309 | 31.6309 | 31.6309 | 31.6309 | 31.6309 | 45% | 3775.313 | 19.4436 | 26.4043 | 28.3085 | 28.6031 | 28.7902 | 29.2006 | 30.1699 | 30.6992 | 31.7073 | 34.7719 | 32.2455 | 31.7513 | 32.4184 | 33.8772 | 32.8898 | 32.8898 | 32.8898 | 32.8898 | 32.8898 | 32.8898 | 32.8898 | 32.8898 | 32.8898 | 32.8898 | 32.8898 | 32.8898 | 32.8898 | 32.8898 | 32.8898 | 32.8898
40% | 4072.8088 | 16.1432 | 22.4095 | 24.0386 | 24.3162 | 24.5328 | 24.9057 | 25.7541 | 26.322 | 27.0414 | 27.4148 | 27.7433 | 27.138 | 27.8474 | 28.9626 | 28.1163 | 28.1163 | 28.1163 | 28.1163 | 28.1163 | 28.1163 | 28.1163 | 28.1163 | 28.1163 | 28.1163 | 28.1163 | 28.1163 | 28.1163 | 28.1163 | 28.1163 | 28.1163 | 40% | 4072.8088 | 17.2832 | 23.4705 | 25.1631 | 25.425 | 25.5913 | 25.9561 | 26.8177 | 27.2882 | 28.1843 | 30.9084 | 28.6627 | 28.2234 | 28.8163 | 30.1131 | 29.2353 | 29.2353 | 29.2353 | 29.2353 | 29.2353 | 29.2353 | 29.2353 | 29.2353 | 29.2353 | 29.2353 | 29.2353 | 29.2353 | 29.2353 | 29.2353 | 29.2353 | 29.2353
35% | 4198.821 | 14.1253 | 19.6083 | 21.0337 | 21.2767 | 21.4662 | 21.7925 | 22.5348 | 23.0317 | 23.6612 | 23.9879 | 24.2754 | 23.7457 | 24.3665 | 25.3423 | 24.6018 | 24.6018 | 24.6018 | 24.6018 | 24.6018 | 24.6018 | 24.6018 | 24.6018 | 24.6018 | 24.6018 | 24.6018 | 24.6018 | 24.6018 | 24.6018 | 24.6018 | 24.6018 | 35% | 4198.821 | 15.1228 | 20.5367 | 22.0177 | 22.2469 | 22.3924 | 22.7116 | 23.4655 | 23.8771 | 24.6613 | 27.0448 | 25.0798 | 24.6955 | 25.2143 | 26.349 | 25.5809 | 25.5809 | 25.5809 | 25.5809 | 25.5809 | 25.5809 | 25.5809 | 25.5809 | 25.5809 | 25.5809 | 25.5809 | 25.5809 | 25.5809 | 25.5809 | 25.5809 | 25.5809
30% | 4271.3374 | 12.1074 | 16.8072 | 18.0289 | 18.2372 | 18.3996 | 18.6793 | 19.3156 | 19.7415 | 20.281 | 20.5611 | 20.8075 | 20.3535 | 20.8855 | 21.722 | 21.0872 | 21.0872 | 21.0872 | 21.0872 | 21.0872 | 21.0872 | 21.0872 | 21.0872 | 21.0872 | 21.0872 | 21.0872 | 21.0872 | 21.0872 | 21.0872 | 21.0872 | 21.0872 | 30% | 4271.3374 | 12.9624 | 17.6029 | 18.8723 | 19.0688 | 19.1935 | 19.4671 | 20.1133 | 20.4661 | 21.1382 | 23.1813 | 21.497 | 21.1675 | 21.6123 | 22.5848 | 21.9265 | 21.9265 | 21.9265 | 21.9265 | 21.9265 | 21.9265 | 21.9265 | 21.9265 | 21.9265 | 21.9265 | 21.9265 | 21.9265 | 21.9265 | 21.9265 | 21.9265 | 21.9265
25% | 4321.8611 | 10.0895 | 14.006 | 15.0241 | 15.1977 | 15.333 | 15.5661 | 16.0963 | 16.4512 | 16.9009 | 17.1342 | 17.3396 | 16.9612 | 17.4046 | 18.1016 | 17.5727 | 17.5727 | 17.5727 | 17.5727 | 17.5727 | 17.5727 | 17.5727 | 17.5727 | 17.5727 | 17.5727 | 17.5727 | 17.5727 | 17.5727 | 17.5727 | 17.5727 | 17.5727 | 25% | 4321.8611 | 10.802 | 14.6691 | 15.727 | 15.8906 | 15.9946 | 16.2226 | 16.7611 | 17.0551 | 17.6152 | 19.3177 | 17.9142 | 17.6396 | 18.0102 | 18.8207 | 18.2721 | 18.2721 | 18.2721 | 18.2721 | 18.2721 | 18.2721 | 18.2721 | 18.2721 | 18.2721 | 18.2721 | 18.2721 | 18.2721 | 18.2721 | 18.2721 | 18.2721 | 18.2721
20% | 4353.067 | 8.0716 | 11.2048 | 12.0193 | 12.1581 | 12.2664 | 12.4529 | 12.877 | 13.161 | 13.5207 | 13.7074 | 13.8716 | 13.569 | 13.9237 | 14.4813 | 14.0582 | 14.0582 | 14.0582 | 14.0582 | 14.0582 | 14.0582 | 14.0582 | 14.0582 | 14.0582 | 14.0582 | 14.0582 | 14.0582 | 14.0582 | 14.0582 | 14.0582 | 14.0582 | 20% | 4353.067 | 8.6416 | 11.7353 | 12.5816 | 12.7125 | 12.7957 | 12.9781 | 13.4089 | 13.6441 | 14.0922 | 15.4542 | 14.3313 | 14.1117 | 14.4082 | 15.0565 | 14.6177 | 14.6177 | 14.6177 | 14.6177 | 14.6177 | 14.6177 | 14.6177 | 14.6177 | 14.6177 | 14.6177 | 14.6177 | 14.6177 | 14.6177 | 14.6177 | 14.6177 | 14.6177
15% | 4369.4129 | 6.0537 | 8.4036 | 9.0145 | 9.1186 | 9.1998 | 9.3396 | 9.6578 | 9.8707 | 10.1405 | 10.2805 | 10.4037 | 10.1767 | 10.4428 | 10.861 | 10.5436 | 10.5436 | 10.5436 | 10.5436 | 10.5436 | 10.5436 | 10.5436 | 10.5436 | 10.5436 | 10.5436 | 10.5436 | 10.5436 | 10.5436 | 10.5436 | 10.5436 | 10.5436 | 15% | 4369.4129 | 6.4812 | 8.8014 | 9.4362 | 9.5344 | 9.5967 | 9.7335 | 10.0566 | 10.2331 | 10.5691 | 11.5906 | 10.7485 | 10.5838 | 10.8061 | 11.2924 | 10.9633 | 10.9633 | 10.9633 | 10.9633 | 10.9633 | 10.9633 | 10.9633 | 10.9633 | 10.9633 | 10.9633 | 10.9633 | 10.9633 | 10.9633 | 10.9633 | 10.9633 | 10.9633
10% | 4378.6261 | 4.0358 | 5.6024 | 6.0096 | 6.0791 | 6.1332 | 6.2264 | 6.4385 | 6.5805 | 6.7603 | 6.8537 | 6.9358 | 6.7845 | 6.9618 | 7.2407 | 7.0291 | 7.0291 | 7.0291 | 7.0291 | 7.0291 | 7.0291 | 7.0291 | 7.0291 | 7.0291 | 7.0291 | 7.0291 | 7.0291 | 7.0291 | 7.0291 | 7.0291 | 7.0291 | 10% | 4378.6261 | 4.3208 | 5.8676 | 6.2908 | 6.3563 | 6.3978 | 6.489 | 6.7044 | 6.822 | 7.0461 | 7.7271 | 7.1657 | 7.0558 | 7.2041 | 7.5283 | 7.3088 | 7.3088 | 7.3088 | 7.3088 | 7.3088 | 7.3088 | 7.3088 | 7.3088 | 7.3088 | 7.3088 | 7.3088 | 7.3088 | 7.3088 | 7.3088 | 7.3088 | 7.3088
5% | 4391.7028 | 2.0179 | 2.8012 | 3.0048 | 3.0395 | 3.0666 | 3.1132 | 3.2193 | 3.2902 | 3.3802 | 3.4268 | 3.4679 | 3.3922 | 3.4809 | 3.6203 | 3.5145 | 3.5145 | 3.5145 | 3.5145 | 3.5145 | 3.5145 | 3.5145 | 3.5145 | 3.5145 | 3.5145 | 3.5145 | 3.5145 | 3.5145 | 3.5145 | 3.5145 | 3.5145 | 5% | 4391.7028 | 2.1604 | 2.9338 | 3.1454 | 3.1781 | 3.1989 | 3.2445 | 3.3522 | 3.411 | 3.523 | 3.8635 | 3.5828 | 3.5279 | 3.602 | 3.7641 | 3.6544 | 3.6544 | 3.6544 | 3.6544 | 3.6544 | 3.6544 | 3.6544 | 3.6544 | 3.6544 | 3.6544 | 3.6544 | 3.6544 | 3.6544 | 3.6544 | 3.6544 | 3.6544
9.992e-14% | 4391.7028 | 4.0326e-14 | 5.5979e-14 | 6.0048e-14 | 6.0742e-14 | 6.1283e-14 | 6.2215e-14 | 6.4334e-14 | 6.5752e-14 | 6.7549e-14 | 6.8482e-14 | 6.9303e-14 | 6.7791e-14 | 6.9563e-14 | 7.2349e-14 | 7.0235e-14 | 7.0235e-14 | 7.0235e-14 | 7.0235e-14 | 7.0235e-14 | 7.0235e-14 | 7.0235e-14 | 7.0235e-14 | 7.0235e-14 | 7.0235e-14 | 7.0235e-14 | 7.0235e-14 | 7.0235e-14 | 7.0235e-14 | 7.0235e-14 | 7.0235e-14 | 9.992e-14% | 4391.7028 | 4.3173e-14 | 5.8629e-14 | 6.2858e-14 | 6.3512e-14 | 6.3927e-14 | 6.4838e-14 | 6.6991e-14 | 6.8166e-14 | 7.0404e-14 | 7.7209e-14 | 7.1599e-14 | 7.0502e-14 | 7.1983e-14 | 7.5223e-14 | 7.303e-14 | 7.303e-14 | 7.303e-14 | 7.303e-14 | 7.303e-14 | 7.303e-14 | 7.303e-14 | 7.303e-14 | 7.303e-14 | 7.303e-14 | 7.303e-14 | 7.303e-14 | 7.303e-14 | 7.303e-14 | 7.303e-14 | 7.303e-14
Summer Season | [31 empty] | Summer Season
P50 | [31 empty] | P10
% of MD | Summer - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Summer - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 45.8759 | 60.9589 | 65.0674 | 64.9499 | 64.9485 | 65.4184 | 65.9338 | 66.9909 | 67.7504 | 68.1633 | 68.6157 | 69.029 | 69.7743 | 70.6989 | 70.6364 | 70.6364 | 70.6364 | 70.6364 | 70.6364 | 70.6364 | 70.6364 | 70.6364 | 70.6364 | 70.6364 | 70.6364 | 70.6364 | 70.6364 | 70.6364 | 70.6364 | 70.6364 | 100% | 0 | 51.1554 | 66.2686 | 70.2261 | 69.9907 | 70.0105 | 70.4179 | 71.4905 | 72.2097 | 72.9132 | 73.7356 | 74.4985 | 75.2386 | 75.3243 | 76.1878 | 75.5357 | 75.5357 | 75.5357 | 75.5357 | 75.5357 | 75.5357 | 75.5357 | 75.5357 | 75.5357 | 75.5357 | 75.5357 | 75.5357 | 75.5357 | 75.5357 | 75.5357 | 75.5357
99% | 0 | 45.4171 | 60.3493 | 64.4168 | 64.3004 | 64.299 | 64.7642 | 65.2745 | 66.321 | 67.0729 | 67.4817 | 67.9295 | 68.3387 | 69.0766 | 69.9919 | 69.93 | 69.93 | 69.93 | 69.93 | 69.93 | 69.93 | 69.93 | 69.93 | 69.93 | 69.93 | 69.93 | 69.93 | 69.93 | 69.93 | 69.93 | 69.93 | 99% | 1.5127 | 50.6438 | 65.6059 | 69.5238 | 69.2908 | 69.3104 | 69.7137 | 70.7756 | 71.4876 | 72.184 | 72.9983 | 73.7535 | 74.4862 | 74.571 | 75.4259 | 74.7803 | 74.7803 | 74.7803 | 74.7803 | 74.7803 | 74.7803 | 74.7803 | 74.7803 | 74.7803 | 74.7803 | 74.7803 | 74.7803 | 74.7803 | 74.7803 | 74.7803 | 74.7803
98% | 0 | 44.9584 | 59.7397 | 63.7661 | 63.6509 | 63.6495 | 64.11 | 64.6151 | 65.6511 | 66.3954 | 66.8001 | 67.2434 | 67.6484 | 68.3788 | 69.2849 | 69.2236 | 69.2236 | 69.2236 | 69.2236 | 69.2236 | 69.2236 | 69.2236 | 69.2236 | 69.2236 | 69.2236 | 69.2236 | 69.2236 | 69.2236 | 69.2236 | 69.2236 | 69.2236 | 98% | 2.269 | 50.1322 | 64.9433 | 68.8216 | 68.5909 | 68.6103 | 69.0096 | 70.0607 | 70.7655 | 71.4549 | 72.2609 | 73.0085 | 73.7338 | 73.8178 | 74.664 | 74.0249 | 74.0249 | 74.0249 | 74.0249 | 74.0249 | 74.0249 | 74.0249 | 74.0249 | 74.0249 | 74.0249 | 74.0249 | 74.0249 | 74.0249 | 74.0249 | 74.0249 | 74.0249
97% | 0.37816 | 44.4996 | 59.1301 | 63.1154 | 63.0014 | 63 | 63.4558 | 63.9558 | 64.9812 | 65.7179 | 66.1184 | 66.5572 | 66.9581 | 67.6811 | 68.5779 | 68.5173 | 68.5173 | 68.5173 | 68.5173 | 68.5173 | 68.5173 | 68.5173 | 68.5173 | 68.5173 | 68.5173 | 68.5173 | 68.5173 | 68.5173 | 68.5173 | 68.5173 | 68.5173 | 97% | 3.7816 | 49.6207 | 64.2806 | 68.1193 | 67.891 | 67.9102 | 68.3054 | 69.3458 | 70.0434 | 70.7258 | 71.5236 | 72.2636 | 72.9814 | 73.0646 | 73.9022 | 73.2696 | 73.2696 | 73.2696 | 73.2696 | 73.2696 | 73.2696 | 73.2696 | 73.2696 | 73.2696 | 73.2696 | 73.2696 | 73.2696 | 73.2696 | 73.2696 | 73.2696 | 73.2696
95% | 2.269 | 43.5821 | 57.911 | 61.8141 | 61.7024 | 61.701 | 62.1474 | 62.6371 | 63.6414 | 64.3629 | 64.7552 | 65.1849 | 65.5776 | 66.2856 | 67.1639 | 67.1046 | 67.1046 | 67.1046 | 67.1046 | 67.1046 | 67.1046 | 67.1046 | 67.1046 | 67.1046 | 67.1046 | 67.1046 | 67.1046 | 67.1046 | 67.1046 | 67.1046 | 67.1046 | 95% | 6.0506 | 48.5976 | 62.9552 | 66.7148 | 66.4912 | 66.51 | 66.897 | 67.916 | 68.5992 | 69.2675 | 70.0488 | 70.7736 | 71.4766 | 71.5581 | 72.3784 | 71.7589 | 71.7589 | 71.7589 | 71.7589 | 71.7589 | 71.7589 | 71.7589 | 71.7589 | 71.7589 | 71.7589 | 71.7589 | 71.7589 | 71.7589 | 71.7589 | 71.7589 | 71.7589
90% | 5.6725 | 41.2883 | 54.863 | 58.5607 | 58.4549 | 58.4536 | 58.8765 | 59.3404 | 60.2918 | 60.9754 | 61.347 | 61.7541 | 62.1261 | 62.7969 | 63.629 | 63.5727 | 63.5727 | 63.5727 | 63.5727 | 63.5727 | 63.5727 | 63.5727 | 63.5727 | 63.5727 | 63.5727 | 63.5727 | 63.5727 | 63.5727 | 63.5727 | 63.5727 | 63.5727 | 90% | 16.2611 | 46.0398 | 59.6418 | 63.2035 | 62.9917 | 63.0094 | 63.3761 | 64.3415 | 64.9887 | 65.6218 | 66.3621 | 67.0487 | 67.7147 | 67.7919 | 68.569 | 67.9821 | 67.9821 | 67.9821 | 67.9821 | 67.9821 | 67.9821 | 67.9821 | 67.9821 | 67.9821 | 67.9821 | 67.9821 | 67.9821 | 67.9821 | 67.9821 | 67.9821 | 67.9821
85% | 15.8829 | 38.9945 | 51.8151 | 55.3073 | 55.2074 | 55.2062 | 55.6056 | 56.0437 | 56.9423 | 57.5879 | 57.9388 | 58.3233 | 58.6747 | 59.3082 | 60.094 | 60.0409 | 60.0409 | 60.0409 | 60.0409 | 60.0409 | 60.0409 | 60.0409 | 60.0409 | 60.0409 | 60.0409 | 60.0409 | 60.0409 | 60.0409 | 60.0409 | 60.0409 | 60.0409 | 85% | 26.4715 | 43.482 | 56.3283 | 59.6922 | 59.4921 | 59.5089 | 59.8552 | 60.767 | 61.3783 | 61.9762 | 62.6753 | 63.3237 | 63.9528 | 64.0256 | 64.7596 | 64.2053 | 64.2053 | 64.2053 | 64.2053 | 64.2053 | 64.2053 | 64.2053 | 64.2053 | 64.2053 | 64.2053 | 64.2053 | 64.2053 | 64.2053 | 64.2053 | 64.2053 | 64.2053
80% | 31.0095 | 36.7007 | 48.7671 | 52.0539 | 51.9599 | 51.9588 | 52.3347 | 52.747 | 53.5928 | 54.2003 | 54.5307 | 54.8925 | 55.2232 | 55.8194 | 56.5591 | 56.5091 | 56.5091 | 56.5091 | 56.5091 | 56.5091 | 56.5091 | 56.5091 | 56.5091 | 56.5091 | 56.5091 | 56.5091 | 56.5091 | 56.5091 | 56.5091 | 56.5091 | 56.5091 | 80% | 34.0348 | 40.9243 | 53.0149 | 56.1809 | 55.9926 | 56.0084 | 56.3343 | 57.1924 | 57.7678 | 58.3305 | 58.9885 | 59.5988 | 60.1908 | 60.2594 | 60.9502 | 60.4285 | 60.4285 | 60.4285 | 60.4285 | 60.4285 | 60.4285 | 60.4285 | 60.4285 | 60.4285 | 60.4285 | 60.4285 | 60.4285 | 60.4285 | 60.4285 | 60.4285 | 60.4285
75% | 72.9857 | 34.4069 | 45.7192 | 48.8006 | 48.7124 | 48.7113 | 49.0638 | 49.4504 | 50.2432 | 50.8128 | 51.1225 | 51.4618 | 51.7718 | 52.3307 | 53.0241 | 52.9773 | 52.9773 | 52.9773 | 52.9773 | 52.9773 | 52.9773 | 52.9773 | 52.9773 | 52.9773 | 52.9773 | 52.9773 | 52.9773 | 52.9773 | 52.9773 | 52.9773 | 52.9773 | 75% | 48.405 | 38.3665 | 49.7015 | 52.6696 | 52.493 | 52.5079 | 52.8134 | 53.6179 | 54.1573 | 54.6849 | 55.3017 | 55.8739 | 56.4289 | 56.4932 | 57.1408 | 56.6517 | 56.6517 | 56.6517 | 56.6517 | 56.6517 | 56.6517 | 56.6517 | 56.6517 | 56.6517 | 56.6517 | 56.6517 | 56.6517 | 56.6517 | 56.6517 | 56.6517 | 56.6517
70% | 150.5094 | 32.1131 | 42.6712 | 45.5472 | 45.4649 | 45.4639 | 45.7929 | 46.1537 | 46.8937 | 47.4253 | 47.7143 | 48.031 | 48.3203 | 48.842 | 49.4892 | 49.4455 | 49.4455 | 49.4455 | 49.4455 | 49.4455 | 49.4455 | 49.4455 | 49.4455 | 49.4455 | 49.4455 | 49.4455 | 49.4455 | 49.4455 | 49.4455 | 49.4455 | 49.4455 | 70% | 76.3892 | 35.8087 | 46.388 | 49.1583 | 48.9935 | 49.0073 | 49.2925 | 50.0434 | 50.5468 | 51.0392 | 51.6149 | 52.149 | 52.667 | 52.727 | 53.3315 | 52.875 | 52.875 | 52.875 | 52.875 | 52.875 | 52.875 | 52.875 | 52.875 | 52.875 | 52.875 | 52.875 | 52.875 | 52.875 | 52.875 | 52.875 | 52.875
65% | 359.6342 | 29.8193 | 39.6233 | 42.2938 | 42.2174 | 42.2165 | 42.5219 | 42.857 | 43.5441 | 44.0378 | 44.3062 | 44.6002 | 44.8689 | 45.3533 | 45.9543 | 45.9136 | 45.9136 | 45.9136 | 45.9136 | 45.9136 | 45.9136 | 45.9136 | 45.9136 | 45.9136 | 45.9136 | 45.9136 | 45.9136 | 45.9136 | 45.9136 | 45.9136 | 45.9136 | 65% | 114.2056 | 33.251 | 43.0746 | 45.647 | 45.494 | 45.5068 | 45.7716 | 46.4689 | 46.9363 | 47.3936 | 47.9282 | 48.424 | 48.9051 | 48.9608 | 49.5221 | 49.0982 | 49.0982 | 49.0982 | 49.0982 | 49.0982 | 49.0982 | 49.0982 | 49.0982 | 49.0982 | 49.0982 | 49.0982 | 49.0982 | 49.0982 | 49.0982 | 49.0982 | 49.0982
60% | 689.7717 | 27.5255 | 36.5753 | 39.0405 | 38.9699 | 38.9691 | 39.251 | 39.5603 | 40.1946 | 40.6503 | 40.898 | 41.1694 | 41.4174 | 41.8646 | 42.4193 | 42.3818 | 42.3818 | 42.3818 | 42.3818 | 42.3818 | 42.3818 | 42.3818 | 42.3818 | 42.3818 | 42.3818 | 42.3818 | 42.3818 | 42.3818 | 42.3818 | 42.3818 | 42.3818 | 60% | 178.1154 | 30.6932 | 39.7612 | 42.1357 | 41.9944 | 42.0063 | 42.2508 | 42.8943 | 43.3258 | 43.7479 | 44.2414 | 44.6991 | 45.1431 | 45.1946 | 45.7127 | 45.3214 | 45.3214 | 45.3214 | 45.3214 | 45.3214 | 45.3214 | 45.3214 | 45.3214 | 45.3214 | 45.3214 | 45.3214 | 45.3214 | 45.3214 | 45.3214 | 45.3214 | 45.3214
55% | 1095.5419 | 25.2317 | 33.5274 | 35.7871 | 35.7224 | 35.7217 | 35.9801 | 36.2636 | 36.845 | 37.2627 | 37.4898 | 37.7386 | 37.966 | 38.3759 | 38.8844 | 38.85 | 38.85 | 38.85 | 38.85 | 38.85 | 38.85 | 38.85 | 38.85 | 38.85 | 38.85 | 38.85 | 38.85 | 38.85 | 38.85 | 38.85 | 38.85 | 55% | 311.6074 | 28.1354 | 36.4477 | 38.6243 | 38.4949 | 38.5058 | 38.7299 | 39.3198 | 39.7153 | 40.1022 | 40.5546 | 40.9742 | 41.3812 | 41.4284 | 41.9033 | 41.5446 | 41.5446 | 41.5446 | 41.5446 | 41.5446 | 41.5446 | 41.5446 | 41.5446 | 41.5446 | 41.5446 | 41.5446 | 41.5446 | 41.5446 | 41.5446 | 41.5446 | 41.5446
50% | 1666.1918 | 22.9379 | 30.4794 | 32.5337 | 32.4749 | 32.4742 | 32.7092 | 32.9669 | 33.4955 | 33.8752 | 34.0817 | 34.3078 | 34.5145 | 34.8872 | 35.3494 | 35.3182 | 35.3182 | 35.3182 | 35.3182 | 35.3182 | 35.3182 | 35.3182 | 35.3182 | 35.3182 | 35.3182 | 35.3182 | 35.3182 | 35.3182 | 35.3182 | 35.3182 | 35.3182 | 50% | 636.0723 | 25.5777 | 33.1343 | 35.113 | 34.9954 | 35.0052 | 35.209 | 35.7453 | 36.1049 | 36.4566 | 36.8678 | 37.2493 | 37.6193 | 37.6621 | 38.0939 | 37.7678 | 37.7678 | 37.7678 | 37.7678 | 37.7678 | 37.7678 | 37.7678 | 37.7678 | 37.7678 | 37.7678 | 37.7678 | 37.7678 | 37.7678 | 37.7678 | 37.7678 | 37.7678
45% | 2506.0947 | 20.6442 | 27.4315 | 29.2803 | 29.2274 | 29.2268 | 29.4383 | 29.6702 | 30.1459 | 30.4877 | 30.6735 | 30.8771 | 31.0631 | 31.3984 | 31.8145 | 31.7864 | 31.7864 | 31.7864 | 31.7864 | 31.7864 | 31.7864 | 31.7864 | 31.7864 | 31.7864 | 31.7864 | 31.7864 | 31.7864 | 31.7864 | 31.7864 | 31.7864 | 31.7864 | 45% | 1179.4944 | 23.0199 | 29.8209 | 31.6017 | 31.4958 | 31.5047 | 31.6881 | 32.1707 | 32.4944 | 32.8109 | 33.181 | 33.5243 | 33.8573 | 33.8959 | 34.2845 | 33.991 | 33.991 | 33.991 | 33.991 | 33.991 | 33.991 | 33.991 | 33.991 | 33.991 | 33.991 | 33.991 | 33.991 | 33.991 | 33.991 | 33.991 | 33.991
40% | 3164.4787 | 18.3504 | 24.3836 | 26.027 | 25.9799 | 25.9794 | 26.1673 | 26.3735 | 26.7964 | 27.1002 | 27.2653 | 27.4463 | 27.6116 | 27.9097 | 28.2795 | 28.2546 | 28.2546 | 28.2546 | 28.2546 | 28.2546 | 28.2546 | 28.2546 | 28.2546 | 28.2546 | 28.2546 | 28.2546 | 28.2546 | 28.2546 | 28.2546 | 28.2546 | 28.2546 | 40% | 1808.3816 | 20.4621 | 26.5075 | 28.0904 | 27.9963 | 28.0042 | 28.1672 | 28.5962 | 28.8839 | 29.1653 | 29.4942 | 29.7994 | 30.0954 | 30.1297 | 30.4751 | 30.2143 | 30.2143 | 30.2143 | 30.2143 | 30.2143 | 30.2143 | 30.2143 | 30.2143 | 30.2143 | 30.2143 | 30.2143 | 30.2143 | 30.2143 | 30.2143 | 30.2143 | 30.2143
35% | 3551.3408 | 16.0566 | 21.3356 | 22.7736 | 22.7325 | 22.732 | 22.8964 | 23.0768 | 23.4468 | 23.7126 | 23.8572 | 24.0155 | 24.1602 | 24.421 | 24.7446 | 24.7227 | 24.7227 | 24.7227 | 24.7227 | 24.7227 | 24.7227 | 24.7227 | 24.7227 | 24.7227 | 24.7227 | 24.7227 | 24.7227 | 24.7227 | 24.7227 | 24.7227 | 24.7227 | 35% | 2779.1293 | 17.9044 | 23.194 | 24.5791 | 24.4968 | 24.5037 | 24.6463 | 25.0217 | 25.2734 | 25.5196 | 25.8075 | 26.0745 | 26.3335 | 26.3635 | 26.6657 | 26.4375 | 26.4375 | 26.4375 | 26.4375 | 26.4375 | 26.4375 | 26.4375 | 26.4375 | 26.4375 | 26.4375 | 26.4375 | 26.4375 | 26.4375 | 26.4375 | 26.4375 | 26.4375
30% | 3758.953 | 13.7628 | 18.2877 | 19.5202 | 19.485 | 19.4845 | 19.6255 | 19.7801 | 20.0973 | 20.3251 | 20.449 | 20.5847 | 20.7087 | 20.9323 | 21.2097 | 21.1909 | 21.1909 | 21.1909 | 21.1909 | 21.1909 | 21.1909 | 21.1909 | 21.1909 | 21.1909 | 21.1909 | 21.1909 | 21.1909 | 21.1909 | 21.1909 | 21.1909 | 21.1909 | 30% | 3814.165 | 15.3466 | 19.8806 | 21.0678 | 20.9972 | 21.0031 | 21.1254 | 21.4472 | 21.6629 | 21.8739 | 22.1207 | 22.3496 | 22.5716 | 22.5973 | 22.8563 | 22.6607 | 22.6607 | 22.6607 | 22.6607 | 22.6607 | 22.6607 | 22.6607 | 22.6607 | 22.6607 | 22.6607 | 22.6607 | 22.6607 | 22.6607 | 22.6607 | 22.6607 | 22.6607
25% | 3926.4798 | 11.469 | 15.2397 | 16.2669 | 16.2375 | 16.2371 | 16.3546 | 16.4835 | 16.7477 | 16.9376 | 17.0408 | 17.1539 | 17.2573 | 17.4436 | 17.6747 | 17.6591 | 17.6591 | 17.6591 | 17.6591 | 17.6591 | 17.6591 | 17.6591 | 17.6591 | 17.6591 | 17.6591 | 17.6591 | 17.6591 | 17.6591 | 17.6591 | 17.6591 | 17.6591 | 25% | 4166.9923 | 12.7888 | 16.5672 | 17.5565 | 17.4977 | 17.5026 | 17.6045 | 17.8726 | 18.0524 | 18.2283 | 18.4339 | 18.6246 | 18.8096 | 18.8311 | 19.0469 | 18.8839 | 18.8839 | 18.8839 | 18.8839 | 18.8839 | 18.8839 | 18.8839 | 18.8839 | 18.8839 | 18.8839 | 18.8839 | 18.8839 | 18.8839 | 18.8839 | 18.8839 | 18.8839
20% | 4050.5177 | 9.1752 | 12.1918 | 13.0135 | 12.99 | 12.9897 | 13.0837 | 13.1868 | 13.3982 | 13.5501 | 13.6327 | 13.7231 | 13.8058 | 13.9549 | 14.1398 | 14.1273 | 14.1273 | 14.1273 | 14.1273 | 14.1273 | 14.1273 | 14.1273 | 14.1273 | 14.1273 | 14.1273 | 14.1273 | 14.1273 | 14.1273 | 14.1273 | 14.1273 | 14.1273 | 20% | 4282.7105 | 10.2311 | 13.2537 | 14.0452 | 13.9981 | 14.0021 | 14.0836 | 14.2981 | 14.4419 | 14.5826 | 14.7471 | 14.8997 | 15.0477 | 15.0649 | 15.2376 | 15.1071 | 15.1071 | 15.1071 | 15.1071 | 15.1071 | 15.1071 | 15.1071 | 15.1071 | 15.1071 | 15.1071 | 15.1071 | 15.1071 | 15.1071 | 15.1071 | 15.1071 | 15.1071
15% | 4152.622 | 6.8814 | 9.1438 | 9.7601 | 9.7425 | 9.7423 | 9.8128 | 9.8901 | 10.0486 | 10.1626 | 10.2245 | 10.2924 | 10.3544 | 10.4661 | 10.6048 | 10.5955 | 10.5955 | 10.5955 | 10.5955 | 10.5955 | 10.5955 | 10.5955 | 10.5955 | 10.5955 | 10.5955 | 10.5955 | 10.5955 | 10.5955 | 10.5955 | 10.5955 | 10.5955 | 15% | 4364.7722 | 7.6733 | 9.9403 | 10.5339 | 10.4986 | 10.5016 | 10.5627 | 10.7236 | 10.8315 | 10.937 | 11.0603 | 11.1748 | 11.2858 | 11.2986 | 11.4282 | 11.3303 | 11.3303 | 11.3303 | 11.3303 | 11.3303 | 11.3303 | 11.3303 | 11.3303 | 11.3303 | 11.3303 | 11.3303 | 11.3303 | 11.3303 | 11.3303 | 11.3303 | 11.3303
10% | 4248.2976 | 4.5876 | 6.0959 | 6.5067 | 6.495 | 6.4948 | 6.5418 | 6.5934 | 6.6991 | 6.775 | 6.8163 | 6.8616 | 6.9029 | 6.9774 | 7.0699 | 7.0636 | 7.0636 | 7.0636 | 7.0636 | 7.0636 | 7.0636 | 7.0636 | 7.0636 | 7.0636 | 7.0636 | 7.0636 | 7.0636 | 7.0636 | 7.0636 | 7.0636 | 7.0636 | 10% | 4391.6218 | 5.1155 | 6.6269 | 7.0226 | 6.9991 | 7.001 | 7.0418 | 7.1491 | 7.221 | 7.2913 | 7.3736 | 7.4499 | 7.5239 | 7.5324 | 7.6188 | 7.5536 | 7.5536 | 7.5536 | 7.5536 | 7.5536 | 7.5536 | 7.5536 | 7.5536 | 7.5536 | 7.5536 | 7.5536 | 7.5536 | 7.5536 | 7.5536 | 7.5536 | 7.5536
5% | 4361.7469 | 2.2938 | 3.0479 | 3.2534 | 3.2475 | 3.2474 | 3.2709 | 3.2967 | 3.3495 | 3.3875 | 3.4082 | 3.4308 | 3.4515 | 3.4887 | 3.5349 | 3.5318 | 3.5318 | 3.5318 | 3.5318 | 3.5318 | 3.5318 | 3.5318 | 3.5318 | 3.5318 | 3.5318 | 3.5318 | 3.5318 | 3.5318 | 3.5318 | 3.5318 | 3.5318 | 5% | 4391.6218 | 2.5578 | 3.3134 | 3.5113 | 3.4995 | 3.5005 | 3.5209 | 3.5745 | 3.6105 | 3.6457 | 3.6868 | 3.7249 | 3.7619 | 3.7662 | 3.8094 | 3.7768 | 3.7768 | 3.7768 | 3.7768 | 3.7768 | 3.7768 | 3.7768 | 3.7768 | 3.7768 | 3.7768 | 3.7768 | 3.7768 | 3.7768 | 3.7768 | 3.7768 | 3.7768
9.992e-14% | 4391.6218 | 4.5839e-14 | 6.091e-14 | 6.5015e-14 | 6.4898e-14 | 6.4897e-14 | 6.5366e-14 | 6.5881e-14 | 6.6937e-14 | 6.7696e-14 | 6.8109e-14 | 6.8561e-14 | 6.8974e-14 | 6.9719e-14 | 7.0642e-14 | 7.058e-14 | 7.058e-14 | 7.058e-14 | 7.058e-14 | 7.058e-14 | 7.058e-14 | 7.058e-14 | 7.058e-14 | 7.058e-14 | 7.058e-14 | 7.058e-14 | 7.058e-14 | 7.058e-14 | 7.058e-14 | 7.058e-14 | 7.058e-14 | 9.992e-14% | 4391.6218 | 5.1114e-14 | 6.6216e-14 | 7.017e-14 | 6.9935e-14 | 6.9955e-14 | 7.0362e-14 | 7.1433e-14 | 7.2152e-14 | 7.2855e-14 | 7.3677e-14 | 7.4439e-14 | 7.5178e-14 | 7.5264e-14 | 7.6127e-14 | 7.5475e-14 | 7.5475e-14 | 7.5475e-14 | 7.5475e-14 | 7.5475e-14 | 7.5475e-14 | 7.5475e-14 | 7.5475e-14 | 7.5475e-14 | 7.5475e-14 | 7.5475e-14 | 7.5475e-14 | 7.5475e-14 | 7.5475e-14 | 7.5475e-14 | 7.5475e-14
Option 8
Winter Season | [31 empty] | Winter Season
P50 | [31 empty] | P10
% of MD | Winter - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Winter - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 40.358 | 56.0239 | 60.0964 | 60.7906 | 61.3321 | 62.2643 | 64.3852 | 65.8049 | 67.6034 | 68.5369 | 69.3582 | 67.845 | 69.6185 | 72.4066 | 70.2908 | 70.2908 | 70.2908 | 70.2908 | 70.2908 | 70.2908 | 70.2908 | 70.2908 | 70.2908 | 70.2908 | 70.2908 | 70.2908 | 70.2908 | 70.2908 | 70.2908 | 70.2908 | 100% | 0 | 43.208 | 58.6763 | 62.9078 | 63.5625 | 63.9783 | 64.8903 | 67.0443 | 68.2204 | 70.4608 | 77.2709 | 71.6566 | 70.5585 | 72.0408 | 75.2827 | 73.0883 | 73.0883 | 73.0883 | 73.0883 | 73.0883 | 73.0883 | 73.0883 | 73.0883 | 73.0883 | 73.0883 | 73.0883 | 73.0883 | 73.0883 | 73.0883 | 73.0883 | 73.0883
99% | 1.486 | 39.9544 | 55.4636 | 59.4955 | 60.1827 | 60.7187 | 61.6416 | 63.7413 | 65.1468 | 66.9274 | 67.8516 | 68.6646 | 67.1665 | 68.9223 | 71.6825 | 69.5879 | 69.5879 | 69.5879 | 69.5879 | 69.5879 | 69.5879 | 69.5879 | 69.5879 | 69.5879 | 69.5879 | 69.5879 | 69.5879 | 69.5879 | 69.5879 | 69.5879 | 69.5879 | 99% | 1.486 | 42.7759 | 58.0895 | 62.2787 | 62.9269 | 63.3385 | 64.2414 | 66.3739 | 67.5382 | 69.7562 | 76.4982 | 70.9401 | 69.8529 | 71.3204 | 74.5299 | 72.3575 | 72.3575 | 72.3575 | 72.3575 | 72.3575 | 72.3575 | 72.3575 | 72.3575 | 72.3575 | 72.3575 | 72.3575 | 72.3575 | 72.3575 | 72.3575 | 72.3575 | 72.3575
98% | 3.2692 | 39.5508 | 54.9034 | 58.8945 | 59.5748 | 60.1054 | 61.019 | 63.0975 | 64.4888 | 66.2513 | 67.1662 | 67.9711 | 66.4881 | 68.2261 | 70.9584 | 68.885 | 68.885 | 68.885 | 68.885 | 68.885 | 68.885 | 68.885 | 68.885 | 68.885 | 68.885 | 68.885 | 68.885 | 68.885 | 68.885 | 68.885 | 68.885 | 98% | 3.2692 | 42.3438 | 57.5027 | 61.6497 | 62.2913 | 62.6987 | 63.5925 | 65.7034 | 66.856 | 69.0516 | 75.7255 | 70.2235 | 69.1473 | 70.6 | 73.7771 | 71.6266 | 71.6266 | 71.6266 | 71.6266 | 71.6266 | 71.6266 | 71.6266 | 71.6266 | 71.6266 | 71.6266 | 71.6266 | 71.6266 | 71.6266 | 71.6266 | 71.6266 | 71.6266
97% | 6.8356 | 39.1473 | 54.3431 | 58.2935 | 58.9669 | 59.4921 | 60.3964 | 62.4536 | 63.8307 | 65.5753 | 66.4808 | 67.2775 | 65.8096 | 67.5299 | 70.2344 | 68.1821 | 68.1821 | 68.1821 | 68.1821 | 68.1821 | 68.1821 | 68.1821 | 68.1821 | 68.1821 | 68.1821 | 68.1821 | 68.1821 | 68.1821 | 68.1821 | 68.1821 | 68.1821 | 97% | 6.8356 | 41.9118 | 56.916 | 61.0206 | 61.6557 | 62.0589 | 62.9436 | 65.033 | 66.1738 | 68.3469 | 74.9528 | 69.5069 | 68.4417 | 69.8796 | 73.0243 | 70.8957 | 70.8957 | 70.8957 | 70.8957 | 70.8957 | 70.8957 | 70.8957 | 70.8957 | 70.8957 | 70.8957 | 70.8957 | 70.8957 | 70.8957 | 70.8957 | 70.8957 | 70.8957
95% | 17.5347 | 38.3401 | 53.2227 | 57.0916 | 57.7511 | 58.2655 | 59.1511 | 61.1659 | 62.5146 | 64.2232 | 65.1101 | 65.8903 | 64.4527 | 66.1375 | 68.7862 | 66.7762 | 66.7762 | 66.7762 | 66.7762 | 66.7762 | 66.7762 | 66.7762 | 66.7762 | 66.7762 | 66.7762 | 66.7762 | 66.7762 | 66.7762 | 66.7762 | 66.7762 | 66.7762 | 95% | 17.5347 | 41.0476 | 55.7425 | 59.7624 | 60.3844 | 60.7794 | 61.6458 | 63.6921 | 64.8094 | 66.9377 | 73.4073 | 68.0738 | 67.0306 | 68.4388 | 71.5186 | 69.4339 | 69.4339 | 69.4339 | 69.4339 | 69.4339 | 69.4339 | 69.4339 | 69.4339 | 69.4339 | 69.4339 | 69.4339 | 69.4339 | 69.4339 | 69.4339 | 69.4339 | 69.4339
90% | 78.7576 | 36.3222 | 50.4215 | 54.0868 | 54.7116 | 55.1988 | 56.0379 | 57.9467 | 59.2244 | 60.8431 | 61.6833 | 62.4224 | 61.0605 | 62.6566 | 65.1659 | 63.2617 | 63.2617 | 63.2617 | 63.2617 | 63.2617 | 63.2617 | 63.2617 | 63.2617 | 63.2617 | 63.2617 | 63.2617 | 63.2617 | 63.2617 | 63.2617 | 63.2617 | 63.2617 | 90% | 78.7576 | 38.8872 | 52.8086 | 56.617 | 57.2063 | 57.5804 | 58.4013 | 60.3399 | 61.3984 | 63.4147 | 69.5438 | 64.491 | 63.5026 | 64.8368 | 67.7545 | 65.7795 | 65.7795 | 65.7795 | 65.7795 | 65.7795 | 65.7795 | 65.7795 | 65.7795 | 65.7795 | 65.7795 | 65.7795 | 65.7795 | 65.7795 | 65.7795 | 65.7795 | 65.7795
85% | 236.8672 | 34.3043 | 47.6203 | 51.082 | 51.672 | 52.1322 | 52.9246 | 54.7274 | 55.9342 | 57.4629 | 58.2564 | 58.9545 | 57.6682 | 59.1757 | 61.5456 | 59.7472 | 59.7472 | 59.7472 | 59.7472 | 59.7472 | 59.7472 | 59.7472 | 59.7472 | 59.7472 | 59.7472 | 59.7472 | 59.7472 | 59.7472 | 59.7472 | 59.7472 | 59.7472 | 85% | 236.8672 | 36.7268 | 49.8748 | 53.4716 | 54.0282 | 54.3815 | 55.1567 | 56.9877 | 57.9873 | 59.8917 | 65.6803 | 60.9081 | 59.9747 | 61.2347 | 63.9903 | 62.1251 | 62.1251 | 62.1251 | 62.1251 | 62.1251 | 62.1251 | 62.1251 | 62.1251 | 62.1251 | 62.1251 | 62.1251 | 62.1251 | 62.1251 | 62.1251 | 62.1251 | 62.1251
80% | 497.5104 | 32.2864 | 44.8191 | 48.0771 | 48.6325 | 49.0656 | 49.8114 | 51.5081 | 52.6439 | 54.0827 | 54.8296 | 55.4866 | 54.276 | 55.6948 | 57.9252 | 56.2326 | 56.2326 | 56.2326 | 56.2326 | 56.2326 | 56.2326 | 56.2326 | 56.2326 | 56.2326 | 56.2326 | 56.2326 | 56.2326 | 56.2326 | 56.2326 | 56.2326 | 56.2326 | 80% | 497.5104 | 34.5664 | 46.941 | 50.3262 | 50.85 | 51.1826 | 51.9122 | 53.6355 | 54.5763 | 56.3686 | 61.8167 | 57.3253 | 56.4468 | 57.6327 | 60.2262 | 58.4707 | 58.4707 | 58.4707 | 58.4707 | 58.4707 | 58.4707 | 58.4707 | 58.4707 | 58.4707 | 58.4707 | 58.4707 | 58.4707 | 58.4707 | 58.4707 | 58.4707 | 58.4707
75% | 803.6248 | 30.2685 | 42.0179 | 45.0723 | 45.593 | 45.999 | 46.6982 | 48.2889 | 49.3537 | 50.7026 | 51.4027 | 52.0187 | 50.8837 | 52.2138 | 54.3049 | 52.7181 | 52.7181 | 52.7181 | 52.7181 | 52.7181 | 52.7181 | 52.7181 | 52.7181 | 52.7181 | 52.7181 | 52.7181 | 52.7181 | 52.7181 | 52.7181 | 52.7181 | 52.7181 | 75% | 803.6248 | 32.406 | 44.0072 | 47.1809 | 47.6719 | 47.9837 | 48.6677 | 50.2832 | 51.1653 | 52.8456 | 57.9532 | 53.7425 | 52.9189 | 54.0306 | 56.4621 | 54.8163 | 54.8163 | 54.8163 | 54.8163 | 54.8163 | 54.8163 | 54.8163 | 54.8163 | 54.8163 | 54.8163 | 54.8163 | 54.8163 | 54.8163 | 54.8163 | 54.8163 | 54.8163
70% | 1155.2107 | 28.2506 | 39.2167 | 42.0675 | 42.5534 | 42.9324 | 43.585 | 45.0696 | 46.0634 | 47.3224 | 47.9759 | 48.5508 | 47.4915 | 48.7329 | 50.6846 | 49.2035 | 49.2035 | 49.2035 | 49.2035 | 49.2035 | 49.2035 | 49.2035 | 49.2035 | 49.2035 | 49.2035 | 49.2035 | 49.2035 | 49.2035 | 49.2035 | 49.2035 | 49.2035 | 70% | 1155.2107 | 30.2456 | 41.0734 | 44.0355 | 44.4938 | 44.7848 | 45.4232 | 46.931 | 47.7543 | 49.3225 | 54.0896 | 50.1596 | 49.3909 | 50.4286 | 52.6979 | 51.1618 | 51.1618 | 51.1618 | 51.1618 | 51.1618 | 51.1618 | 51.1618 | 51.1618 | 51.1618 | 51.1618 | 51.1618 | 51.1618 | 51.1618 | 51.1618 | 51.1618 | 51.1618
65% | 1553.1596 | 26.2327 | 36.4155 | 39.0627 | 39.5139 | 39.8658 | 40.4718 | 41.8504 | 42.7732 | 43.9422 | 44.549 | 45.0828 | 44.0992 | 45.252 | 47.0643 | 45.689 | 45.689 | 45.689 | 45.689 | 45.689 | 45.689 | 45.689 | 45.689 | 45.689 | 45.689 | 45.689 | 45.689 | 45.689 | 45.689 | 45.689 | 45.689 | 65% | 1553.1596 | 28.0852 | 38.1396 | 40.8901 | 41.3157 | 41.5859 | 42.1787 | 43.5788 | 44.3433 | 45.7995 | 50.2261 | 46.5768 | 45.863 | 46.8266 | 48.9338 | 47.5074 | 47.5074 | 47.5074 | 47.5074 | 47.5074 | 47.5074 | 47.5074 | 47.5074 | 47.5074 | 47.5074 | 47.5074 | 47.5074 | 47.5074 | 47.5074 | 47.5074 | 47.5074
60% | 2026.2996 | 24.2148 | 33.6143 | 36.0579 | 36.4744 | 36.7992 | 37.3586 | 38.6311 | 39.4829 | 40.562 | 41.1222 | 41.6149 | 40.707 | 41.7711 | 43.4439 | 42.1745 | 42.1745 | 42.1745 | 42.1745 | 42.1745 | 42.1745 | 42.1745 | 42.1745 | 42.1745 | 42.1745 | 42.1745 | 42.1745 | 42.1745 | 42.1745 | 42.1745 | 42.1745 | 60% | 2026.2996 | 25.9248 | 35.2058 | 37.7447 | 38.1375 | 38.387 | 38.9342 | 40.2266 | 40.9322 | 42.2765 | 46.3625 | 42.994 | 42.3351 | 43.2245 | 45.1696 | 43.853 | 43.853 | 43.853 | 43.853 | 43.853 | 43.853 | 43.853 | 43.853 | 43.853 | 43.853 | 43.853 | 43.853 | 43.853 | 43.853 | 43.853 | 43.853
55% | 2598.4068 | 22.1969 | 30.8131 | 33.053 | 33.4348 | 33.7326 | 34.2454 | 35.4119 | 36.1927 | 37.1819 | 37.6953 | 38.147 | 37.3147 | 38.2902 | 39.8236 | 38.6599 | 38.6599 | 38.6599 | 38.6599 | 38.6599 | 38.6599 | 38.6599 | 38.6599 | 38.6599 | 38.6599 | 38.6599 | 38.6599 | 38.6599 | 38.6599 | 38.6599 | 38.6599 | 55% | 2598.4068 | 23.7644 | 32.272 | 34.5993 | 34.9594 | 35.188 | 35.6897 | 36.8744 | 37.5212 | 38.7534 | 42.499 | 39.4111 | 38.8072 | 39.6225 | 41.4055 | 40.1986 | 40.1986 | 40.1986 | 40.1986 | 40.1986 | 40.1986 | 40.1986 | 40.1986 | 40.1986 | 40.1986 | 40.1986 | 40.1986 | 40.1986 | 40.1986 | 40.1986 | 40.1986
50% | 3233.5201 | 20.179 | 28.0119 | 30.0482 | 30.3953 | 30.666 | 31.1321 | 32.1926 | 32.9024 | 33.8017 | 34.2685 | 34.6791 | 33.9225 | 34.8092 | 36.2033 | 35.1454 | 35.1454 | 35.1454 | 35.1454 | 35.1454 | 35.1454 | 35.1454 | 35.1454 | 35.1454 | 35.1454 | 35.1454 | 35.1454 | 35.1454 | 35.1454 | 35.1454 | 35.1454 | 50% | 3233.5201 | 21.604 | 29.3381 | 31.4539 | 31.7813 | 31.9891 | 32.4451 | 33.5222 | 34.1102 | 35.2304 | 38.6354 | 35.8283 | 35.2792 | 36.0204 | 37.6414 | 36.5442 | 36.5442 | 36.5442 | 36.5442 | 36.5442 | 36.5442 | 36.5442 | 36.5442 | 36.5442 | 36.5442 | 36.5442 | 36.5442 | 36.5442 | 36.5442 | 36.5442 | 36.5442
45% | 3775.313 | 18.1611 | 25.2107 | 27.0434 | 27.3558 | 27.5994 | 28.0189 | 28.9733 | 29.6122 | 30.4215 | 30.8416 | 31.2112 | 30.5302 | 31.3283 | 32.583 | 31.6309 | 31.6309 | 31.6309 | 31.6309 | 31.6309 | 31.6309 | 31.6309 | 31.6309 | 31.6309 | 31.6309 | 31.6309 | 31.6309 | 31.6309 | 31.6309 | 31.6309 | 31.6309 | 45% | 3775.313 | 19.4436 | 26.4043 | 28.3085 | 28.6031 | 28.7902 | 29.2006 | 30.1699 | 30.6992 | 31.7073 | 34.7719 | 32.2455 | 31.7513 | 32.4184 | 33.8772 | 32.8898 | 32.8898 | 32.8898 | 32.8898 | 32.8898 | 32.8898 | 32.8898 | 32.8898 | 32.8898 | 32.8898 | 32.8898 | 32.8898 | 32.8898 | 32.8898 | 32.8898 | 32.8898
40% | 4072.8088 | 16.1432 | 22.4095 | 24.0386 | 24.3162 | 24.5328 | 24.9057 | 25.7541 | 26.322 | 27.0414 | 27.4148 | 27.7433 | 27.138 | 27.8474 | 28.9626 | 28.1163 | 28.1163 | 28.1163 | 28.1163 | 28.1163 | 28.1163 | 28.1163 | 28.1163 | 28.1163 | 28.1163 | 28.1163 | 28.1163 | 28.1163 | 28.1163 | 28.1163 | 28.1163 | 40% | 4072.8088 | 17.2832 | 23.4705 | 25.1631 | 25.425 | 25.5913 | 25.9561 | 26.8177 | 27.2882 | 28.1843 | 30.9084 | 28.6627 | 28.2234 | 28.8163 | 30.1131 | 29.2353 | 29.2353 | 29.2353 | 29.2353 | 29.2353 | 29.2353 | 29.2353 | 29.2353 | 29.2353 | 29.2353 | 29.2353 | 29.2353 | 29.2353 | 29.2353 | 29.2353 | 29.2353
35% | 4198.821 | 14.1253 | 19.6083 | 21.0337 | 21.2767 | 21.4662 | 21.7925 | 22.5348 | 23.0317 | 23.6612 | 23.9879 | 24.2754 | 23.7457 | 24.3665 | 25.3423 | 24.6018 | 24.6018 | 24.6018 | 24.6018 | 24.6018 | 24.6018 | 24.6018 | 24.6018 | 24.6018 | 24.6018 | 24.6018 | 24.6018 | 24.6018 | 24.6018 | 24.6018 | 24.6018 | 35% | 4198.821 | 15.1228 | 20.5367 | 22.0177 | 22.2469 | 22.3924 | 22.7116 | 23.4655 | 23.8771 | 24.6613 | 27.0448 | 25.0798 | 24.6955 | 25.2143 | 26.349 | 25.5809 | 25.5809 | 25.5809 | 25.5809 | 25.5809 | 25.5809 | 25.5809 | 25.5809 | 25.5809 | 25.5809 | 25.5809 | 25.5809 | 25.5809 | 25.5809 | 25.5809 | 25.5809
30% | 4271.3374 | 12.1074 | 16.8072 | 18.0289 | 18.2372 | 18.3996 | 18.6793 | 19.3156 | 19.7415 | 20.281 | 20.5611 | 20.8075 | 20.3535 | 20.8855 | 21.722 | 21.0872 | 21.0872 | 21.0872 | 21.0872 | 21.0872 | 21.0872 | 21.0872 | 21.0872 | 21.0872 | 21.0872 | 21.0872 | 21.0872 | 21.0872 | 21.0872 | 21.0872 | 21.0872 | 30% | 4271.3374 | 12.9624 | 17.6029 | 18.8723 | 19.0688 | 19.1935 | 19.4671 | 20.1133 | 20.4661 | 21.1382 | 23.1813 | 21.497 | 21.1675 | 21.6123 | 22.5848 | 21.9265 | 21.9265 | 21.9265 | 21.9265 | 21.9265 | 21.9265 | 21.9265 | 21.9265 | 21.9265 | 21.9265 | 21.9265 | 21.9265 | 21.9265 | 21.9265 | 21.9265 | 21.9265
25% | 4321.8611 | 10.0895 | 14.006 | 15.0241 | 15.1977 | 15.333 | 15.5661 | 16.0963 | 16.4512 | 16.9009 | 17.1342 | 17.3396 | 16.9612 | 17.4046 | 18.1016 | 17.5727 | 17.5727 | 17.5727 | 17.5727 | 17.5727 | 17.5727 | 17.5727 | 17.5727 | 17.5727 | 17.5727 | 17.5727 | 17.5727 | 17.5727 | 17.5727 | 17.5727 | 17.5727 | 25% | 4321.8611 | 10.802 | 14.6691 | 15.727 | 15.8906 | 15.9946 | 16.2226 | 16.7611 | 17.0551 | 17.6152 | 19.3177 | 17.9142 | 17.6396 | 18.0102 | 18.8207 | 18.2721 | 18.2721 | 18.2721 | 18.2721 | 18.2721 | 18.2721 | 18.2721 | 18.2721 | 18.2721 | 18.2721 | 18.2721 | 18.2721 | 18.2721 | 18.2721 | 18.2721 | 18.2721
20% | 4353.067 | 8.0716 | 11.2048 | 12.0193 | 12.1581 | 12.2664 | 12.4529 | 12.877 | 13.161 | 13.5207 | 13.7074 | 13.8716 | 13.569 | 13.9237 | 14.4813 | 14.0582 | 14.0582 | 14.0582 | 14.0582 | 14.0582 | 14.0582 | 14.0582 | 14.0582 | 14.0582 | 14.0582 | 14.0582 | 14.0582 | 14.0582 | 14.0582 | 14.0582 | 14.0582 | 20% | 4353.067 | 8.6416 | 11.7353 | 12.5816 | 12.7125 | 12.7957 | 12.9781 | 13.4089 | 13.6441 | 14.0922 | 15.4542 | 14.3313 | 14.1117 | 14.4082 | 15.0565 | 14.6177 | 14.6177 | 14.6177 | 14.6177 | 14.6177 | 14.6177 | 14.6177 | 14.6177 | 14.6177 | 14.6177 | 14.6177 | 14.6177 | 14.6177 | 14.6177 | 14.6177 | 14.6177
15% | 4369.4129 | 6.0537 | 8.4036 | 9.0145 | 9.1186 | 9.1998 | 9.3396 | 9.6578 | 9.8707 | 10.1405 | 10.2805 | 10.4037 | 10.1767 | 10.4428 | 10.861 | 10.5436 | 10.5436 | 10.5436 | 10.5436 | 10.5436 | 10.5436 | 10.5436 | 10.5436 | 10.5436 | 10.5436 | 10.5436 | 10.5436 | 10.5436 | 10.5436 | 10.5436 | 10.5436 | 15% | 4369.4129 | 6.4812 | 8.8014 | 9.4362 | 9.5344 | 9.5967 | 9.7335 | 10.0566 | 10.2331 | 10.5691 | 11.5906 | 10.7485 | 10.5838 | 10.8061 | 11.2924 | 10.9633 | 10.9633 | 10.9633 | 10.9633 | 10.9633 | 10.9633 | 10.9633 | 10.9633 | 10.9633 | 10.9633 | 10.9633 | 10.9633 | 10.9633 | 10.9633 | 10.9633 | 10.9633
10% | 4378.6261 | 4.0358 | 5.6024 | 6.0096 | 6.0791 | 6.1332 | 6.2264 | 6.4385 | 6.5805 | 6.7603 | 6.8537 | 6.9358 | 6.7845 | 6.9618 | 7.2407 | 7.0291 | 7.0291 | 7.0291 | 7.0291 | 7.0291 | 7.0291 | 7.0291 | 7.0291 | 7.0291 | 7.0291 | 7.0291 | 7.0291 | 7.0291 | 7.0291 | 7.0291 | 7.0291 | 10% | 4378.6261 | 4.3208 | 5.8676 | 6.2908 | 6.3563 | 6.3978 | 6.489 | 6.7044 | 6.822 | 7.0461 | 7.7271 | 7.1657 | 7.0558 | 7.2041 | 7.5283 | 7.3088 | 7.3088 | 7.3088 | 7.3088 | 7.3088 | 7.3088 | 7.3088 | 7.3088 | 7.3088 | 7.3088 | 7.3088 | 7.3088 | 7.3088 | 7.3088 | 7.3088 | 7.3088
5% | 4391.7028 | 2.0179 | 2.8012 | 3.0048 | 3.0395 | 3.0666 | 3.1132 | 3.2193 | 3.2902 | 3.3802 | 3.4268 | 3.4679 | 3.3922 | 3.4809 | 3.6203 | 3.5145 | 3.5145 | 3.5145 | 3.5145 | 3.5145 | 3.5145 | 3.5145 | 3.5145 | 3.5145 | 3.5145 | 3.5145 | 3.5145 | 3.5145 | 3.5145 | 3.5145 | 3.5145 | 5% | 4391.7028 | 2.1604 | 2.9338 | 3.1454 | 3.1781 | 3.1989 | 3.2445 | 3.3522 | 3.411 | 3.523 | 3.8635 | 3.5828 | 3.5279 | 3.602 | 3.7641 | 3.6544 | 3.6544 | 3.6544 | 3.6544 | 3.6544 | 3.6544 | 3.6544 | 3.6544 | 3.6544 | 3.6544 | 3.6544 | 3.6544 | 3.6544 | 3.6544 | 3.6544 | 3.6544
9.992e-14% | 4391.7028 | 4.0326e-14 | 5.5979e-14 | 6.0048e-14 | 6.0742e-14 | 6.1283e-14 | 6.2215e-14 | 6.4334e-14 | 6.5752e-14 | 6.7549e-14 | 6.8482e-14 | 6.9303e-14 | 6.7791e-14 | 6.9563e-14 | 7.2349e-14 | 7.0235e-14 | 7.0235e-14 | 7.0235e-14 | 7.0235e-14 | 7.0235e-14 | 7.0235e-14 | 7.0235e-14 | 7.0235e-14 | 7.0235e-14 | 7.0235e-14 | 7.0235e-14 | 7.0235e-14 | 7.0235e-14 | 7.0235e-14 | 7.0235e-14 | 7.0235e-14 | 9.992e-14% | 4391.7028 | 4.3173e-14 | 5.8629e-14 | 6.2858e-14 | 6.3512e-14 | 6.3927e-14 | 6.4838e-14 | 6.6991e-14 | 6.8166e-14 | 7.0404e-14 | 7.7209e-14 | 7.1599e-14 | 7.0502e-14 | 7.1983e-14 | 7.5223e-14 | 7.303e-14 | 7.303e-14 | 7.303e-14 | 7.303e-14 | 7.303e-14 | 7.303e-14 | 7.303e-14 | 7.303e-14 | 7.303e-14 | 7.303e-14 | 7.303e-14 | 7.303e-14 | 7.303e-14 | 7.303e-14 | 7.303e-14 | 7.303e-14
Summer Season | [31 empty] | Summer Season
P50 | [31 empty] | P10
% of MD | Summer - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Summer - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 45.8759 | 60.9589 | 65.0674 | 64.9499 | 64.9485 | 65.4184 | 65.9338 | 66.9909 | 67.7504 | 68.1633 | 68.6157 | 69.029 | 69.7743 | 70.6989 | 70.6364 | 70.6364 | 70.6364 | 70.6364 | 70.6364 | 70.6364 | 70.6364 | 70.6364 | 70.6364 | 70.6364 | 70.6364 | 70.6364 | 70.6364 | 70.6364 | 70.6364 | 70.6364 | 100% | 0 | 51.1554 | 66.2686 | 70.2261 | 69.9907 | 70.0105 | 70.4179 | 71.4905 | 72.2097 | 72.9132 | 73.7356 | 74.4985 | 75.2386 | 75.3243 | 76.1878 | 75.5357 | 75.5357 | 75.5357 | 75.5357 | 75.5357 | 75.5357 | 75.5357 | 75.5357 | 75.5357 | 75.5357 | 75.5357 | 75.5357 | 75.5357 | 75.5357 | 75.5357 | 75.5357
99% | 0 | 45.4171 | 60.3493 | 64.4168 | 64.3004 | 64.299 | 64.7642 | 65.2745 | 66.321 | 67.0729 | 67.4817 | 67.9295 | 68.3387 | 69.0766 | 69.9919 | 69.93 | 69.93 | 69.93 | 69.93 | 69.93 | 69.93 | 69.93 | 69.93 | 69.93 | 69.93 | 69.93 | 69.93 | 69.93 | 69.93 | 69.93 | 69.93 | 99% | 1.5127 | 50.6438 | 65.6059 | 69.5238 | 69.2908 | 69.3104 | 69.7137 | 70.7756 | 71.4876 | 72.184 | 72.9983 | 73.7535 | 74.4862 | 74.571 | 75.4259 | 74.7803 | 74.7803 | 74.7803 | 74.7803 | 74.7803 | 74.7803 | 74.7803 | 74.7803 | 74.7803 | 74.7803 | 74.7803 | 74.7803 | 74.7803 | 74.7803 | 74.7803 | 74.7803
98% | 0 | 44.9584 | 59.7397 | 63.7661 | 63.6509 | 63.6495 | 64.11 | 64.6151 | 65.6511 | 66.3954 | 66.8001 | 67.2434 | 67.6484 | 68.3788 | 69.2849 | 69.2236 | 69.2236 | 69.2236 | 69.2236 | 69.2236 | 69.2236 | 69.2236 | 69.2236 | 69.2236 | 69.2236 | 69.2236 | 69.2236 | 69.2236 | 69.2236 | 69.2236 | 69.2236 | 98% | 2.269 | 50.1322 | 64.9433 | 68.8216 | 68.5909 | 68.6103 | 69.0096 | 70.0607 | 70.7655 | 71.4549 | 72.2609 | 73.0085 | 73.7338 | 73.8178 | 74.664 | 74.0249 | 74.0249 | 74.0249 | 74.0249 | 74.0249 | 74.0249 | 74.0249 | 74.0249 | 74.0249 | 74.0249 | 74.0249 | 74.0249 | 74.0249 | 74.0249 | 74.0249 | 74.0249
97% | 0.37816 | 44.4996 | 59.1301 | 63.1154 | 63.0014 | 63 | 63.4558 | 63.9558 | 64.9812 | 65.7179 | 66.1184 | 66.5572 | 66.9581 | 67.6811 | 68.5779 | 68.5173 | 68.5173 | 68.5173 | 68.5173 | 68.5173 | 68.5173 | 68.5173 | 68.5173 | 68.5173 | 68.5173 | 68.5173 | 68.5173 | 68.5173 | 68.5173 | 68.5173 | 68.5173 | 97% | 3.7816 | 49.6207 | 64.2806 | 68.1193 | 67.891 | 67.9102 | 68.3054 | 69.3458 | 70.0434 | 70.7258 | 71.5236 | 72.2636 | 72.9814 | 73.0646 | 73.9022 | 73.2696 | 73.2696 | 73.2696 | 73.2696 | 73.2696 | 73.2696 | 73.2696 | 73.2696 | 73.2696 | 73.2696 | 73.2696 | 73.2696 | 73.2696 | 73.2696 | 73.2696 | 73.2696
95% | 2.269 | 43.5821 | 57.911 | 61.8141 | 61.7024 | 61.701 | 62.1474 | 62.6371 | 63.6414 | 64.3629 | 64.7552 | 65.1849 | 65.5776 | 66.2856 | 67.1639 | 67.1046 | 67.1046 | 67.1046 | 67.1046 | 67.1046 | 67.1046 | 67.1046 | 67.1046 | 67.1046 | 67.1046 | 67.1046 | 67.1046 | 67.1046 | 67.1046 | 67.1046 | 67.1046 | 95% | 6.0506 | 48.5976 | 62.9552 | 66.7148 | 66.4912 | 66.51 | 66.897 | 67.916 | 68.5992 | 69.2675 | 70.0488 | 70.7736 | 71.4766 | 71.5581 | 72.3784 | 71.7589 | 71.7589 | 71.7589 | 71.7589 | 71.7589 | 71.7589 | 71.7589 | 71.7589 | 71.7589 | 71.7589 | 71.7589 | 71.7589 | 71.7589 | 71.7589 | 71.7589 | 71.7589
90% | 5.6725 | 41.2883 | 54.863 | 58.5607 | 58.4549 | 58.4536 | 58.8765 | 59.3404 | 60.2918 | 60.9754 | 61.347 | 61.7541 | 62.1261 | 62.7969 | 63.629 | 63.5727 | 63.5727 | 63.5727 | 63.5727 | 63.5727 | 63.5727 | 63.5727 | 63.5727 | 63.5727 | 63.5727 | 63.5727 | 63.5727 | 63.5727 | 63.5727 | 63.5727 | 63.5727 | 90% | 16.2611 | 46.0398 | 59.6418 | 63.2035 | 62.9917 | 63.0094 | 63.3761 | 64.3415 | 64.9887 | 65.6218 | 66.3621 | 67.0487 | 67.7147 | 67.7919 | 68.569 | 67.9821 | 67.9821 | 67.9821 | 67.9821 | 67.9821 | 67.9821 | 67.9821 | 67.9821 | 67.9821 | 67.9821 | 67.9821 | 67.9821 | 67.9821 | 67.9821 | 67.9821 | 67.9821
85% | 15.8829 | 38.9945 | 51.8151 | 55.3073 | 55.2074 | 55.2062 | 55.6056 | 56.0437 | 56.9423 | 57.5879 | 57.9388 | 58.3233 | 58.6747 | 59.3082 | 60.094 | 60.0409 | 60.0409 | 60.0409 | 60.0409 | 60.0409 | 60.0409 | 60.0409 | 60.0409 | 60.0409 | 60.0409 | 60.0409 | 60.0409 | 60.0409 | 60.0409 | 60.0409 | 60.0409 | 85% | 26.4715 | 43.482 | 56.3283 | 59.6922 | 59.4921 | 59.5089 | 59.8552 | 60.767 | 61.3783 | 61.9762 | 62.6753 | 63.3237 | 63.9528 | 64.0256 | 64.7596 | 64.2053 | 64.2053 | 64.2053 | 64.2053 | 64.2053 | 64.2053 | 64.2053 | 64.2053 | 64.2053 | 64.2053 | 64.2053 | 64.2053 | 64.2053 | 64.2053 | 64.2053 | 64.2053
80% | 31.0095 | 36.7007 | 48.7671 | 52.0539 | 51.9599 | 51.9588 | 52.3347 | 52.747 | 53.5928 | 54.2003 | 54.5307 | 54.8925 | 55.2232 | 55.8194 | 56.5591 | 56.5091 | 56.5091 | 56.5091 | 56.5091 | 56.5091 | 56.5091 | 56.5091 | 56.5091 | 56.5091 | 56.5091 | 56.5091 | 56.5091 | 56.5091 | 56.5091 | 56.5091 | 56.5091 | 80% | 34.0348 | 40.9243 | 53.0149 | 56.1809 | 55.9926 | 56.0084 | 56.3343 | 57.1924 | 57.7678 | 58.3305 | 58.9885 | 59.5988 | 60.1908 | 60.2594 | 60.9502 | 60.4285 | 60.4285 | 60.4285 | 60.4285 | 60.4285 | 60.4285 | 60.4285 | 60.4285 | 60.4285 | 60.4285 | 60.4285 | 60.4285 | 60.4285 | 60.4285 | 60.4285 | 60.4285
75% | 72.9857 | 34.4069 | 45.7192 | 48.8006 | 48.7124 | 48.7113 | 49.0638 | 49.4504 | 50.2432 | 50.8128 | 51.1225 | 51.4618 | 51.7718 | 52.3307 | 53.0241 | 52.9773 | 52.9773 | 52.9773 | 52.9773 | 52.9773 | 52.9773 | 52.9773 | 52.9773 | 52.9773 | 52.9773 | 52.9773 | 52.9773 | 52.9773 | 52.9773 | 52.9773 | 52.9773 | 75% | 48.405 | 38.3665 | 49.7015 | 52.6696 | 52.493 | 52.5079 | 52.8134 | 53.6179 | 54.1573 | 54.6849 | 55.3017 | 55.8739 | 56.4289 | 56.4932 | 57.1408 | 56.6517 | 56.6517 | 56.6517 | 56.6517 | 56.6517 | 56.6517 | 56.6517 | 56.6517 | 56.6517 | 56.6517 | 56.6517 | 56.6517 | 56.6517 | 56.6517 | 56.6517 | 56.6517
70% | 150.5094 | 32.1131 | 42.6712 | 45.5472 | 45.4649 | 45.4639 | 45.7929 | 46.1537 | 46.8937 | 47.4253 | 47.7143 | 48.031 | 48.3203 | 48.842 | 49.4892 | 49.4455 | 49.4455 | 49.4455 | 49.4455 | 49.4455 | 49.4455 | 49.4455 | 49.4455 | 49.4455 | 49.4455 | 49.4455 | 49.4455 | 49.4455 | 49.4455 | 49.4455 | 49.4455 | 70% | 76.3892 | 35.8087 | 46.388 | 49.1583 | 48.9935 | 49.0073 | 49.2925 | 50.0434 | 50.5468 | 51.0392 | 51.6149 | 52.149 | 52.667 | 52.727 | 53.3315 | 52.875 | 52.875 | 52.875 | 52.875 | 52.875 | 52.875 | 52.875 | 52.875 | 52.875 | 52.875 | 52.875 | 52.875 | 52.875 | 52.875 | 52.875 | 52.875
65% | 359.6342 | 29.8193 | 39.6233 | 42.2938 | 42.2174 | 42.2165 | 42.5219 | 42.857 | 43.5441 | 44.0378 | 44.3062 | 44.6002 | 44.8689 | 45.3533 | 45.9543 | 45.9136 | 45.9136 | 45.9136 | 45.9136 | 45.9136 | 45.9136 | 45.9136 | 45.9136 | 45.9136 | 45.9136 | 45.9136 | 45.9136 | 45.9136 | 45.9136 | 45.9136 | 45.9136 | 65% | 114.2056 | 33.251 | 43.0746 | 45.647 | 45.494 | 45.5068 | 45.7716 | 46.4689 | 46.9363 | 47.3936 | 47.9282 | 48.424 | 48.9051 | 48.9608 | 49.5221 | 49.0982 | 49.0982 | 49.0982 | 49.0982 | 49.0982 | 49.0982 | 49.0982 | 49.0982 | 49.0982 | 49.0982 | 49.0982 | 49.0982 | 49.0982 | 49.0982 | 49.0982 | 49.0982
60% | 689.7717 | 27.5255 | 36.5753 | 39.0405 | 38.9699 | 38.9691 | 39.251 | 39.5603 | 40.1946 | 40.6503 | 40.898 | 41.1694 | 41.4174 | 41.8646 | 42.4193 | 42.3818 | 42.3818 | 42.3818 | 42.3818 | 42.3818 | 42.3818 | 42.3818 | 42.3818 | 42.3818 | 42.3818 | 42.3818 | 42.3818 | 42.3818 | 42.3818 | 42.3818 | 42.3818 | 60% | 178.1154 | 30.6932 | 39.7612 | 42.1357 | 41.9944 | 42.0063 | 42.2508 | 42.8943 | 43.3258 | 43.7479 | 44.2414 | 44.6991 | 45.1431 | 45.1946 | 45.7127 | 45.3214 | 45.3214 | 45.3214 | 45.3214 | 45.3214 | 45.3214 | 45.3214 | 45.3214 | 45.3214 | 45.3214 | 45.3214 | 45.3214 | 45.3214 | 45.3214 | 45.3214 | 45.3214
55% | 1095.5419 | 25.2317 | 33.5274 | 35.7871 | 35.7224 | 35.7217 | 35.9801 | 36.2636 | 36.845 | 37.2627 | 37.4898 | 37.7386 | 37.966 | 38.3759 | 38.8844 | 38.85 | 38.85 | 38.85 | 38.85 | 38.85 | 38.85 | 38.85 | 38.85 | 38.85 | 38.85 | 38.85 | 38.85 | 38.85 | 38.85 | 38.85 | 38.85 | 55% | 311.6074 | 28.1354 | 36.4477 | 38.6243 | 38.4949 | 38.5058 | 38.7299 | 39.3198 | 39.7153 | 40.1022 | 40.5546 | 40.9742 | 41.3812 | 41.4284 | 41.9033 | 41.5446 | 41.5446 | 41.5446 | 41.5446 | 41.5446 | 41.5446 | 41.5446 | 41.5446 | 41.5446 | 41.5446 | 41.5446 | 41.5446 | 41.5446 | 41.5446 | 41.5446 | 41.5446
50% | 1666.1918 | 22.9379 | 30.4794 | 32.5337 | 32.4749 | 32.4742 | 32.7092 | 32.9669 | 33.4955 | 33.8752 | 34.0817 | 34.3078 | 34.5145 | 34.8872 | 35.3494 | 35.3182 | 35.3182 | 35.3182 | 35.3182 | 35.3182 | 35.3182 | 35.3182 | 35.3182 | 35.3182 | 35.3182 | 35.3182 | 35.3182 | 35.3182 | 35.3182 | 35.3182 | 35.3182 | 50% | 636.0723 | 25.5777 | 33.1343 | 35.113 | 34.9954 | 35.0052 | 35.209 | 35.7453 | 36.1049 | 36.4566 | 36.8678 | 37.2493 | 37.6193 | 37.6621 | 38.0939 | 37.7678 | 37.7678 | 37.7678 | 37.7678 | 37.7678 | 37.7678 | 37.7678 | 37.7678 | 37.7678 | 37.7678 | 37.7678 | 37.7678 | 37.7678 | 37.7678 | 37.7678 | 37.7678
45% | 2506.0947 | 20.6442 | 27.4315 | 29.2803 | 29.2274 | 29.2268 | 29.4383 | 29.6702 | 30.1459 | 30.4877 | 30.6735 | 30.8771 | 31.0631 | 31.3984 | 31.8145 | 31.7864 | 31.7864 | 31.7864 | 31.7864 | 31.7864 | 31.7864 | 31.7864 | 31.7864 | 31.7864 | 31.7864 | 31.7864 | 31.7864 | 31.7864 | 31.7864 | 31.7864 | 31.7864 | 45% | 1179.4944 | 23.0199 | 29.8209 | 31.6017 | 31.4958 | 31.5047 | 31.6881 | 32.1707 | 32.4944 | 32.8109 | 33.181 | 33.5243 | 33.8573 | 33.8959 | 34.2845 | 33.991 | 33.991 | 33.991 | 33.991 | 33.991 | 33.991 | 33.991 | 33.991 | 33.991 | 33.991 | 33.991 | 33.991 | 33.991 | 33.991 | 33.991 | 33.991
40% | 3164.4787 | 18.3504 | 24.3836 | 26.027 | 25.9799 | 25.9794 | 26.1673 | 26.3735 | 26.7964 | 27.1002 | 27.2653 | 27.4463 | 27.6116 | 27.9097 | 28.2795 | 28.2546 | 28.2546 | 28.2546 | 28.2546 | 28.2546 | 28.2546 | 28.2546 | 28.2546 | 28.2546 | 28.2546 | 28.2546 | 28.2546 | 28.2546 | 28.2546 | 28.2546 | 28.2546 | 40% | 1808.3816 | 20.4621 | 26.5075 | 28.0904 | 27.9963 | 28.0042 | 28.1672 | 28.5962 | 28.8839 | 29.1653 | 29.4942 | 29.7994 | 30.0954 | 30.1297 | 30.4751 | 30.2143 | 30.2143 | 30.2143 | 30.2143 | 30.2143 | 30.2143 | 30.2143 | 30.2143 | 30.2143 | 30.2143 | 30.2143 | 30.2143 | 30.2143 | 30.2143 | 30.2143 | 30.2143
35% | 3551.3408 | 16.0566 | 21.3356 | 22.7736 | 22.7325 | 22.732 | 22.8964 | 23.0768 | 23.4468 | 23.7126 | 23.8572 | 24.0155 | 24.1602 | 24.421 | 24.7446 | 24.7227 | 24.7227 | 24.7227 | 24.7227 | 24.7227 | 24.7227 | 24.7227 | 24.7227 | 24.7227 | 24.7227 | 24.7227 | 24.7227 | 24.7227 | 24.7227 | 24.7227 | 24.7227 | 35% | 2779.1293 | 17.9044 | 23.194 | 24.5791 | 24.4968 | 24.5037 | 24.6463 | 25.0217 | 25.2734 | 25.5196 | 25.8075 | 26.0745 | 26.3335 | 26.3635 | 26.6657 | 26.4375 | 26.4375 | 26.4375 | 26.4375 | 26.4375 | 26.4375 | 26.4375 | 26.4375 | 26.4375 | 26.4375 | 26.4375 | 26.4375 | 26.4375 | 26.4375 | 26.4375 | 26.4375
30% | 3758.953 | 13.7628 | 18.2877 | 19.5202 | 19.485 | 19.4845 | 19.6255 | 19.7801 | 20.0973 | 20.3251 | 20.449 | 20.5847 | 20.7087 | 20.9323 | 21.2097 | 21.1909 | 21.1909 | 21.1909 | 21.1909 | 21.1909 | 21.1909 | 21.1909 | 21.1909 | 21.1909 | 21.1909 | 21.1909 | 21.1909 | 21.1909 | 21.1909 | 21.1909 | 21.1909 | 30% | 3814.165 | 15.3466 | 19.8806 | 21.0678 | 20.9972 | 21.0031 | 21.1254 | 21.4472 | 21.6629 | 21.8739 | 22.1207 | 22.3496 | 22.5716 | 22.5973 | 22.8563 | 22.6607 | 22.6607 | 22.6607 | 22.6607 | 22.6607 | 22.6607 | 22.6607 | 22.6607 | 22.6607 | 22.6607 | 22.6607 | 22.6607 | 22.6607 | 22.6607 | 22.6607 | 22.6607
25% | 3926.4798 | 11.469 | 15.2397 | 16.2669 | 16.2375 | 16.2371 | 16.3546 | 16.4835 | 16.7477 | 16.9376 | 17.0408 | 17.1539 | 17.2573 | 17.4436 | 17.6747 | 17.6591 | 17.6591 | 17.6591 | 17.6591 | 17.6591 | 17.6591 | 17.6591 | 17.6591 | 17.6591 | 17.6591 | 17.6591 | 17.6591 | 17.6591 | 17.6591 | 17.6591 | 17.6591 | 25% | 4166.9923 | 12.7888 | 16.5672 | 17.5565 | 17.4977 | 17.5026 | 17.6045 | 17.8726 | 18.0524 | 18.2283 | 18.4339 | 18.6246 | 18.8096 | 18.8311 | 19.0469 | 18.8839 | 18.8839 | 18.8839 | 18.8839 | 18.8839 | 18.8839 | 18.8839 | 18.8839 | 18.8839 | 18.8839 | 18.8839 | 18.8839 | 18.8839 | 18.8839 | 18.8839 | 18.8839
20% | 4050.5177 | 9.1752 | 12.1918 | 13.0135 | 12.99 | 12.9897 | 13.0837 | 13.1868 | 13.3982 | 13.5501 | 13.6327 | 13.7231 | 13.8058 | 13.9549 | 14.1398 | 14.1273 | 14.1273 | 14.1273 | 14.1273 | 14.1273 | 14.1273 | 14.1273 | 14.1273 | 14.1273 | 14.1273 | 14.1273 | 14.1273 | 14.1273 | 14.1273 | 14.1273 | 14.1273 | 20% | 4282.7105 | 10.2311 | 13.2537 | 14.0452 | 13.9981 | 14.0021 | 14.0836 | 14.2981 | 14.4419 | 14.5826 | 14.7471 | 14.8997 | 15.0477 | 15.0649 | 15.2376 | 15.1071 | 15.1071 | 15.1071 | 15.1071 | 15.1071 | 15.1071 | 15.1071 | 15.1071 | 15.1071 | 15.1071 | 15.1071 | 15.1071 | 15.1071 | 15.1071 | 15.1071 | 15.1071
15% | 4152.622 | 6.8814 | 9.1438 | 9.7601 | 9.7425 | 9.7423 | 9.8128 | 9.8901 | 10.0486 | 10.1626 | 10.2245 | 10.2924 | 10.3544 | 10.4661 | 10.6048 | 10.5955 | 10.5955 | 10.5955 | 10.5955 | 10.5955 | 10.5955 | 10.5955 | 10.5955 | 10.5955 | 10.5955 | 10.5955 | 10.5955 | 10.5955 | 10.5955 | 10.5955 | 10.5955 | 15% | 4364.7722 | 7.6733 | 9.9403 | 10.5339 | 10.4986 | 10.5016 | 10.5627 | 10.7236 | 10.8315 | 10.937 | 11.0603 | 11.1748 | 11.2858 | 11.2986 | 11.4282 | 11.3303 | 11.3303 | 11.3303 | 11.3303 | 11.3303 | 11.3303 | 11.3303 | 11.3303 | 11.3303 | 11.3303 | 11.3303 | 11.3303 | 11.3303 | 11.3303 | 11.3303 | 11.3303
10% | 4248.2976 | 4.5876 | 6.0959 | 6.5067 | 6.495 | 6.4948 | 6.5418 | 6.5934 | 6.6991 | 6.775 | 6.8163 | 6.8616 | 6.9029 | 6.9774 | 7.0699 | 7.0636 | 7.0636 | 7.0636 | 7.0636 | 7.0636 | 7.0636 | 7.0636 | 7.0636 | 7.0636 | 7.0636 | 7.0636 | 7.0636 | 7.0636 | 7.0636 | 7.0636 | 7.0636 | 10% | 4391.6218 | 5.1155 | 6.6269 | 7.0226 | 6.9991 | 7.001 | 7.0418 | 7.1491 | 7.221 | 7.2913 | 7.3736 | 7.4499 | 7.5239 | 7.5324 | 7.6188 | 7.5536 | 7.5536 | 7.5536 | 7.5536 | 7.5536 | 7.5536 | 7.5536 | 7.5536 | 7.5536 | 7.5536 | 7.5536 | 7.5536 | 7.5536 | 7.5536 | 7.5536 | 7.5536
5% | 4361.7469 | 2.2938 | 3.0479 | 3.2534 | 3.2475 | 3.2474 | 3.2709 | 3.2967 | 3.3495 | 3.3875 | 3.4082 | 3.4308 | 3.4515 | 3.4887 | 3.5349 | 3.5318 | 3.5318 | 3.5318 | 3.5318 | 3.5318 | 3.5318 | 3.5318 | 3.5318 | 3.5318 | 3.5318 | 3.5318 | 3.5318 | 3.5318 | 3.5318 | 3.5318 | 3.5318 | 5% | 4391.6218 | 2.5578 | 3.3134 | 3.5113 | 3.4995 | 3.5005 | 3.5209 | 3.5745 | 3.6105 | 3.6457 | 3.6868 | 3.7249 | 3.7619 | 3.7662 | 3.8094 | 3.7768 | 3.7768 | 3.7768 | 3.7768 | 3.7768 | 3.7768 | 3.7768 | 3.7768 | 3.7768 | 3.7768 | 3.7768 | 3.7768 | 3.7768 | 3.7768 | 3.7768 | 3.7768
9.992e-14% | 4391.6218 | 4.5839e-14 | 6.091e-14 | 6.5015e-14 | 6.4898e-14 | 6.4897e-14 | 6.5366e-14 | 6.5881e-14 | 6.6937e-14 | 6.7696e-14 | 6.8109e-14 | 6.8561e-14 | 6.8974e-14 | 6.9719e-14 | 7.0642e-14 | 7.058e-14 | 7.058e-14 | 7.058e-14 | 7.058e-14 | 7.058e-14 | 7.058e-14 | 7.058e-14 | 7.058e-14 | 7.058e-14 | 7.058e-14 | 7.058e-14 | 7.058e-14 | 7.058e-14 | 7.058e-14 | 7.058e-14 | 7.058e-14 | 9.992e-14% | 4391.6218 | 5.1114e-14 | 6.6216e-14 | 7.017e-14 | 6.9935e-14 | 6.9955e-14 | 7.0362e-14 | 7.1433e-14 | 7.2152e-14 | 7.2855e-14 | 7.3677e-14 | 7.4439e-14 | 7.5178e-14 | 7.5264e-14 | 7.6127e-14 | 7.5475e-14 | 7.5475e-14 | 7.5475e-14 | 7.5475e-14 | 7.5475e-14 | 7.5475e-14 | 7.5475e-14 | 7.5475e-14 | 7.5475e-14 | 7.5475e-14 | 7.5475e-14 | 7.5475e-14 | 7.5475e-14 | 7.5475e-14 | 7.5475e-14 | 7.5475e-14

## Locational VCR
Base case |  | Energy Usage (CY 2024 kWh) | Energy Usage (CY 2024 %) | Tailored VCR
Dec 24 AER VCR ($/kWh) - Res | 49.23 | 67934749.1441 | 34.06% | 16.7657
Dec 24 AER VCR ($/kWh) - Com | 34.39 | 101368150.4504 | 50.82% | 17.4756
Dec 24 AER VCR ($/kWh) - Ind | 33.49 | 17726336.2671 | 8.886% | 2.976
Dec 24 AER VCR ($/kWh) - Agr | 22.25 | 12451243.5083 | 6.242% | 1.3888
|  | 199480479.3698 |  | 38.6062 | KW/h
|  |  |  | 38606.1513 | MW/h

## E@R N
Option 1 - Do Nothing / Base Case
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99%
98%
97%
95%
90%
85%
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1 Winter POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 1 Winter POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99
98%
97%
95%
90%
85%
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1 Summer POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 1 Summer POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2 - 1A New PHS ZSS + Four new feeders
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99%
98%
97%
95%
90%
85%
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2 Winter POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 2 Winter POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99
98%
97%
95%
90%
85%
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2 Summer POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 2 Summer POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 - 2A PHM 3rd Tx + Switchroom + Three new feeders + OFR12 New Feeder
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99%
98%
97%
95%
90%
85%
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 Winter POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 3 Winter POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99
98%
97%
95%
90%
85%
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 Summer POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 3 Summer POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 - 3A OFR 3rd Tx + Switchroom + Three new feeders + OFR12 New Feeder
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99%
98%
97%
95%
90%
85%
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 Winter POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 4 Winter POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99
98%
97%
95%
90%
85%
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 Summer POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 4 Summer POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 - 4A LLG 2nd Tx + Switchroom + Three new feeders + OFR12 New Feeder
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99%
98%
97%
95%
90%
85%
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 Winter POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 5 Winter POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99
98%
97%
95%
90%
85%
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 Summer POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 5 Summer POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 6 - Non Network
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99%
98%
97%
95%
90%
85%
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 6 Winter POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 6 Winter POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99
98%
97%
95%
90%
85%
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 6 Summer POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 6 Summer POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 7 -
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99%
98%
97%
95%
90%
85%
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 7 Winter POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 7 Winter POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99
98%
97%
95%
90%
85%
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 7 Summer POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 7 Summer POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 8 -
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99%
98%
97%
95%
90%
85%
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 8 Winter POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 8 Winter POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99
98%
97%
95%
90%
85%
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 8 Summer POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 8 Summer POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## E@R N-1
Option 1 - Do Nothing / Base Case
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% |  | 9.8725 | 15.8941 | 16.9205 | 17.721 | 19.0994 | 22.2353 | 24.3344 | 26.9936 | 28.3739 | 29.5883 | 27.3508 | 29.973 | 34.0954 | 30.9671 | 30.9671 | 30.9671 | 30.9671 | 30.9671 | 30.9671 | 30.9671 | 30.9671 | 30.9671 | 30.9671 | 30.9671 | 30.9671 | 30.9671 | 30.9671 | 30.9671 | 30.9671 |  |  | 13.7943 | 20.0509 | 21.019 | 21.6336 | 22.9821 | 26.167 | 27.9059 | 31.2184 | 41.2876 | 32.9866 | 31.3629 | 33.5547 | 38.348 | 35.1035 | 35.1035 | 35.1035 | 35.1035 | 35.1035 | 35.1035 | 35.1035 | 35.1035 | 35.1035 | 35.1035 | 35.1035 | 35.1035 | 35.1035 | 35.1035 | 35.1035 | 35.1035
98% |  | 10.848 | 18.0013 | 19.2206 | 20.1716 | 21.809 | 25.5342 | 28.0279 | 31.1869 | 32.8266 | 34.2691 | 31.6112 | 34.7262 | 39.6233 | 35.9071 | 35.9071 | 35.9071 | 35.9071 | 35.9071 | 35.9071 | 35.9071 | 35.9071 | 35.9071 | 35.9071 | 35.9071 | 35.9071 | 35.9071 | 35.9071 | 35.9071 | 35.9071 |  |  | 15.5069 | 22.9393 | 24.0893 | 24.8195 | 26.4214 | 30.2049 | 32.2706 | 36.2057 | 48.1672 | 38.3061 | 36.3773 | 38.981 | 44.6752 | 40.8209 | 40.8209 | 40.8209 | 40.8209 | 40.8209 | 40.8209 | 40.8209 | 40.8209 | 40.8209 | 40.8209 | 40.8209 | 40.8209 | 40.8209 | 40.8209 | 40.8209 | 40.8209
97% |  | 19.698 | 33.8593 | 36.2732 | 38.1558 | 41.3974 | 48.7723 | 53.7089 | 59.9627 | 63.2089 | 66.0646 | 60.8028 | 66.9695 | 76.6644 | 69.3073 | 69.3073 | 69.3073 | 69.3073 | 69.3073 | 69.3073 | 69.3073 | 69.3073 | 69.3073 | 69.3073 | 69.3073 | 69.3073 | 69.3073 | 69.3073 | 69.3073 | 69.3073 |  |  | 28.9211 | 43.6351 | 45.9118 | 47.3573 | 50.5286 | 58.0187 | 62.1081 | 69.8984 | 93.5787 | 74.0567 | 70.2382 | 75.3927 | 86.6655 | 79.0351 | 79.0351 | 79.0351 | 79.0351 | 79.0351 | 79.0351 | 79.0351 | 79.0351 | 79.0351 | 79.0351 | 79.0351 | 79.0351 | 79.0351 | 79.0351 | 79.0351 | 79.0351
95% |  | 50.103 | 91.9331 | 99.0634 | 104.6245 | 114.1996 | 135.9838 | 150.5658 | 169.0387 | 178.6273 | 187.0628 | 171.5201 | 189.7357 | 218.3728 | 196.6412 | 196.6412 | 196.6412 | 196.6412 | 196.6412 | 196.6412 | 196.6412 | 196.6412 | 196.6412 | 196.6412 | 196.6412 | 196.6412 | 196.6412 | 196.6412 | 196.6412 | 196.6412 |  |  | 77.3465 | 120.8094 | 127.5343 | 131.8043 | 141.1717 | 163.2964 | 175.3759 | 198.3872 | 268.3351 | 210.6702 | 199.3908 | 214.6165 | 247.9145 | 225.3755 | 225.3755 | 225.3755 | 225.3755 | 225.3755 | 225.3755 | 225.3755 | 225.3755 | 225.3755 | 225.3755 | 225.3755 | 225.3755 | 225.3755 | 225.3755 | 225.3755 | 225.3755
90% |  | 166.6526 | 397.287 | 436.6005 | 467.2624 | 520.0555 | 640.1647 | 720.5641 | 822.4165 | 875.2838 | 921.7942 | 836.0975 | 936.5313 | 1094.4248 | 974.6055 | 974.6055 | 974.6055 | 974.6055 | 974.6055 | 974.6055 | 974.6055 | 974.6055 | 974.6055 | 974.6055 | 974.6055 | 974.6055 | 974.6055 | 974.6055 | 974.6055 | 974.6055 |  |  | 316.8623 | 556.4991 | 593.5776 | 617.1207 | 668.7691 | 790.7554 | 857.3571 | 984.2321 | 1369.8972 | 1051.9556 | 989.7659 | 1073.714 | 1257.3061 | 1133.0351 | 1133.0351 | 1133.0351 | 1133.0351 | 1133.0351 | 1133.0351 | 1133.0351 | 1133.0351 | 1133.0351 | 1133.0351 | 1133.0351 | 1133.0351 | 1133.0351 | 1133.0351 | 1133.0351 | 1133.0351
85% |  | 49.283 | 550.9121 | 646.9524 | 721.8571 | 850.8267 | 1144.2449 | 1340.6551 | 1589.473 | 1718.6242 | 1832.2457 | 1622.8948 | 1868.2474 | 2253.97 | 1961.2601 | 1961.2601 | 1961.2601 | 1961.2601 | 1961.2601 | 1961.2601 | 1961.2601 | 1961.2601 | 1961.2601 | 1961.2601 | 1961.2601 | 1961.2601 | 1961.2601 | 1961.2601 | 1961.2601 | 1961.2601 |  |  | 354.4405 | 939.8561 | 1030.4361 | 1087.9502 | 1214.1234 | 1512.1274 | 1674.8304 | 1984.7771 | 2926.9292 | 2150.2208 | 1998.2958 | 2203.3748 | 2651.8773 | 2348.2922 | 2348.2922 | 2348.2922 | 2348.2922 | 2348.2922 | 2348.2922 | 2348.2922 | 2348.2922 | 2348.2922 | 2348.2922 | 2348.2922 | 2348.2922 | 2348.2922 | 2348.2922 | 2348.2922 | 2348.2922
80% |  |  | 170.3674 | 283.6364 | 390.7399 | 591.1469 | 1047.2057 | 1352.4853 | 1739.2221 | 1939.9613 | 2116.5629 | 1791.1696 | 2172.5202 | 2772.0475 | 2317.0894 | 2317.0894 | 2317.0894 | 2317.0894 | 2317.0894 | 2317.0894 | 2317.0894 | 2317.0894 | 2317.0894 | 2317.0894 | 2317.0894 | 2317.0894 | 2317.0894 | 2317.0894 | 2317.0894 | 2317.0894 |  |  | 26.6685 | 729.5248 | 870.3131 | 959.707 | 1155.8176 | 1619.0041 | 1871.8928 | 2353.6419 | 3818.0255 | 2610.7904 | 2374.6539 | 2693.4076 | 3390.5133 | 2918.6521 | 2918.6521 | 2918.6521 | 2918.6521 | 2918.6521 | 2918.6521 | 2918.6521 | 2918.6521 | 2918.6521 | 2918.6521 | 2918.6521 | 2918.6521 | 2918.6521 | 2918.6521 | 2918.6521 | 2918.6521
75% | [5 empty] | 24.883 | 275.7172 | 581.2462 | 1007.9249 | 1229.3962 | 1424.237 | 1065.2374 | 1485.9735 | 2147.4195 | 1645.4738 | 1645.4738 | 1645.4738 | 1645.4738 | 1645.4738 | 1645.4738 | 1645.4738 | 1645.4738 | 1645.4738 | 1645.4738 | 1645.4738 | 1645.4738 | 1645.4738 | 1645.4738 | 1645.4738 | 1645.4738 |  |  |  | 73.1703 | 147.4946 | 207.5247 | 373.0825 | 875.2908 | 1154.2977 | 1685.8014 | 3301.4252 | 1969.5079 | 1708.9835 | 2060.6577 | 2829.7599 | 2309.1653 | 2309.1653 | 2309.1653 | 2309.1653 | 2309.1653 | 2309.1653 | 2309.1653 | 2309.1653 | 2309.1653 | 2309.1653 | 2309.1653 | 2309.1653 | 2309.1653 | 2309.1653 | 2309.1653 | 2309.1653
70% | [7 empty] | 3.4379 | 133.5638 | 272.0098 | 431.8215 | 164.8836 | 489.6671 | 1193.5489 | 654.2363 | 654.2363 | 654.2363 | 654.2363 | 654.2363 | 654.2363 | 654.2363 | 654.2363 | 654.2363 | 654.2363 | 654.2363 | 654.2363 | 654.2363 | 654.2363 | 654.2363 | 654.2363 | [7 empty] | 73.4213 | 219.8269 | 697.566 | 2433.4635 | 1002.3928 | 722.4739 | 1100.3282 | 1926.6855 | 1367.3357 | 1367.3357 | 1367.3357 | 1367.3357 | 1367.3357 | 1367.3357 | 1367.3357 | 1367.3357 | 1367.3357 | 1367.3357 | 1367.3357 | 1367.3357 | 1367.3357 | 1367.3357 | 1367.3357 | 1367.3357
65% | FY38: 138.0019; FY39: 0.607; FY40: 0.607; FY41: 0.607; FY42: 0.607; FY43: 0.607; FY44: 0.607; FY45: 0.607; FY46: 0.607; FY47: 0.607; FY48: 0.607; FY49: 0.607; FY50: 0.607; FY51: 0.607; FY52: 0.607; FY53: 0.607; FY54: 0.607 | [9 empty] | 2.7969 | 1216.8668 | 62.358 | 4.774 | 97.5063 | 684.2805 | 231.4677 | 231.4677 | 231.4677 | 231.4677 | 231.4677 | 231.4677 | 231.4677 | 231.4677 | 231.4677 | 231.4677 | 231.4677 | 231.4677 | 231.4677 | 231.4677 | 231.4677 | 231.4677
60% | [40 empty] | 77.6441
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 306.4572 | 1278.2542 | 1538.6669 | 1760.5324 | 2183.4175 | 3339.858 | 4255.0255 | 5579.7822 | 6338.312 | 7043.6462 | 5771.5678 | 7274.3439 | 9968.1685 | 7886.0948 | 7886.0948 | 7886.0948 | 7886.0948 | 7886.0948 | 7886.0948 | 7886.0948 | 7886.0948 | 7886.0948 | 7886.0948 | 7886.0948 | 7886.0948 | 7886.0948 | 7886.0948 | 7886.0948 | 7886.0948 | E @ R (MWh) | 0 | 833.5401 | 2506.4849 | 2860.3759 | 3097.9173 | 3652.8965 | 5148.2859 | 6075.8653 | 8044.5252 | 15595.6201 | 9203.2451 | 8136.3162 | 9591.5333 | 13158.0259 | 10688.2832 | 10688.2832 | 10688.2832 | 10688.2832 | 10688.2832 | 10688.2832 | 10688.2832 | 10688.2832 | 10688.2832 | 10688.2832 | 10688.2832 | 10688.2832 | 10688.2832 | 10688.2832 | 10688.2832 | 10688.2832
Option 1 Winter POE50 W E @ R (MWh) N 1 | 0 | 214.5201 | 894.7779 | 1077.0669 | 1232.3727 | 1528.3922 | 2337.9006 | 2978.5179 | 3905.8475 | 4436.8184 | 4930.5523 | 4040.0974 | 5092.0407 | 6977.718 | 5520.2664 | 5520.2664 | 5520.2664 | 5520.2664 | 5520.2664 | 5520.2664 | 5520.2664 | 5520.2664 | 5520.2664 | 5520.2664 | 5520.2664 | 5520.2664 | 5520.2664 | 5520.2664 | 5520.2664 | 5520.2664 | Option 1 Winter POE10 W E @ R (MWh) N 1 | 0 | 250.062 | 751.9455 | 858.1128 | 929.3752 | 1095.8689 | 1544.4858 | 1822.7596 | 2413.3575 | 4678.686 | 2760.9735 | 2440.8949 | 2877.46 | 3947.4078 | 3206.485 | 3206.485 | 3206.485 | 3206.485 | 3206.485 | 3206.485 | 3206.485 | 3206.485 | 3206.485 | 3206.485 | 3206.485 | 3206.485 | 3206.485 | 3206.485 | 3206.485 | 3206.485
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 8.924 | 31.6709 | 37.6273 | 37.273 | 37.3028 | 37.916 | 39.5304 | 40.6128 | 41.6716 | 42.9095 | 44.0577 | 45.1715 | 45.3005 | 46.6002 | 45.6187 | 45.6187 | 45.6187 | 45.6187 | 45.6187 | 45.6187 | 45.6187 | 45.6187 | 45.6187 | 45.6187 | 45.6187 | 45.6187 | 45.6187 | 45.6187 | 45.6187 | 45.6187
98% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4.0751 | 15.3343 | 18.2825 | 18.1072 | 18.1219 | 18.4254 | 19.2245 | 19.7603 | 20.2843 | 20.897 | 21.4654 | 22.0167 | 22.0806 | 22.7239 | 22.238 | 22.238 | 22.238 | 22.238 | 22.238 | 22.238 | 22.238 | 22.238 | 22.238 | 22.238 | 22.238 | 22.238 | 22.238 | 22.238 | 22.238 | 22.238
97% |  | 5.4588 | 6.9736 | 6.9303 | 6.9298 | 7.103 | 7.2931 | 7.6829 | 7.9629 | 8.1151 | 8.2819 | 8.4343 | 8.7091 | 9.05 | 9.027 | 9.027 | 9.027 | 9.027 | 9.027 | 9.027 | 9.027 | 9.027 | 9.027 | 9.027 | 9.027 | 9.027 | 9.027 | 9.027 | 9.027 | 9.027 |  | 7.3764 | 29.6661 | 35.5027 | 35.1556 | 35.1847 | 35.7856 | 37.3676 | 38.4283 | 39.4657 | 40.6787 | 41.8039 | 42.8953 | 43.0218 | 44.2953 | 43.3335 | 43.3335 | 43.3335 | 43.3335 | 43.3335 | 43.3335 | 43.3335 | 43.3335 | 43.3335 | 43.3335 | 43.3335 | 43.3335 | 43.3335 | 43.3335 | 43.3335 | 43.3335
95% |  | 25.5649 | 33.0227 | 32.8093 | 32.8067 | 33.6597 | 34.5953 | 36.5142 | 37.8928 | 38.6423 | 39.4634 | 40.2137 | 41.5666 | 43.2448 | 43.1314 | 43.1314 | 43.1314 | 43.1314 | 43.1314 | 43.1314 | 43.1314 | 43.1314 | 43.1314 | 43.1314 | 43.1314 | 43.1314 | 43.1314 | 43.1314 | 43.1314 | 43.1314 |  | 9.3236 | 42.2437 | 50.864 | 50.3513 | 50.3943 | 51.2818 | 53.6182 | 55.1847 | 56.717 | 58.5085 | 60.1702 | 61.7822 | 61.969 | 63.8499 | 62.4294 | 62.4294 | 62.4294 | 62.4294 | 62.4294 | 62.4294 | 62.4294 | 62.4294 | 62.4294 | 62.4294 | 62.4294 | 62.4294 | 62.4294 | 62.4294 | 62.4294 | 62.4294
90% |  | 38.7554 | 51.6899 | 51.3198 | 51.3153 | 52.7947 | 54.4175 | 57.7455 | 60.1366 | 61.4365 | 62.8605 | 64.1618 | 66.5082 | 69.4189 | 69.2222 | 69.2222 | 69.2222 | 69.2222 | 69.2222 | 69.2222 | 69.2222 | 69.2222 | 69.2222 | 69.2222 | 69.2222 | 69.2222 | 69.2222 | 69.2222 | 69.2222 | 69.2222 |  | 23.6749 | 166.4146 | 203.7914 | 201.5685 | 201.7552 | 205.6032 | 215.7337 | 222.5261 | 229.1699 | 236.9378 | 244.1429 | 251.1324 | 251.9421 | 260.0977 | 253.9385 | 253.9385 | 253.9385 | 253.9385 | 253.9385 | 253.9385 | 253.9385 | 253.9385 | 253.9385 | 253.9385 | 253.9385 | 253.9385 | 253.9385 | 253.9385 | 253.9385 | 253.9385
85% |  | 85.1452 | 121.8514 | 120.801 | 120.7884 | 124.9866 | 129.5917 | 139.0363 | 145.8216 | 149.5106 | 153.5518 | 157.2446 | 163.9032 | 172.1633 | 171.605 | 171.605 | 171.605 | 171.605 | 171.605 | 171.605 | 171.605 | 171.605 | 171.605 | 171.605 | 171.605 | 171.605 | 171.605 | 171.605 | 171.605 | 171.605 |  | 2.1581 | 132.583 | 167.9395 | 165.8367 | 166.0133 | 169.6533 | 179.2362 | 185.6615 | 191.9461 | 199.2941 | 206.1098 | 212.7215 | 213.4874 | 221.2021 | 215.3759 | 215.3759 | 215.3759 | 215.3759 | 215.3759 | 215.3759 | 215.3759 | 215.3759 | 215.3759 | 215.3759 | 215.3759 | 215.3759 | 215.3759 | 215.3759 | 215.3759 | 215.3759
80% |  | 80.0361 | 131.3082 | 129.841 | 129.8234 | 135.6876 | 142.1201 | 155.3125 | 164.7904 | 169.9433 | 175.5881 | 180.7464 | 190.0472 | 201.5852 | 200.8054 | 200.8054 | 200.8054 | 200.8054 | 200.8054 | 200.8054 | 200.8054 | 200.8054 | 200.8054 | 200.8054 | 200.8054 | 200.8054 | 200.8054 | 200.8054 | 200.8054 | 200.8054 |  |  | 73.1492 | 97.8426 | 96.374 | 96.4973 | 99.0396 | 105.7324 | 110.2199 | 114.6092 | 119.7411 | 124.5013 | 129.1189 | 129.6539 | 135.0419 | 130.9728 | 130.9728 | 130.9728 | 130.9728 | 130.9728 | 130.9728 | 130.9728 | 130.9728 | 130.9728 | 130.9728 | 130.9728 | 130.9728 | 130.9728 | 130.9728 | 130.9728 | 130.9728
75% |  | 94.1589 | 227.8159 | 223.9912 | 223.9454 | 239.2321 | 256.0006 | 290.3908 | 315.098 | 328.5306 | 343.2457 | 356.6924 | 380.938 | 411.0152 | 408.9825 | 408.9825 | 408.9825 | 408.9825 | 408.9825 | 408.9825 | 408.9825 | 408.9825 | 408.9825 | 408.9825 | 408.9825 | 408.9825 | 408.9825 | 408.9825 | 408.9825 | 408.9825 |  |  | 91.3687 | 135.4427 | 132.8215 | 133.0415 | 137.5791 | 149.5248 | 157.5342 | 165.3684 | 174.5281 | 183.0243 | 191.2662 | 192.221 | 201.8378 | 194.575 | 194.575 | 194.575 | 194.575 | 194.575 | 194.575 | 194.575 | 194.575 | 194.575 | 194.575 | 194.575 | 194.575 | 194.575 | 194.575 | 194.575 | 194.575
70% |  | 6.5776 | 168.5277 | 161.9198 | 161.8408 | 188.2515 | 217.2224 | 276.6382 | 319.3247 | 342.5321 | 367.9553 | 391.1871 | 433.0761 | 485.0404 | 481.5284 | 481.5284 | 481.5284 | 481.5284 | 481.5284 | 481.5284 | 481.5284 | 481.5284 | 481.5284 | 481.5284 | 481.5284 | 481.5284 | 481.5284 | 481.5284 | 481.5284 | 481.5284 |  |  | 85.2049 | 165.4959 | 160.7208 | 161.1217 | 169.3879 | 191.1497 | 205.7408 | 220.0126 | 236.6991 | 252.1769 | 267.1913 | 268.9307 | 286.45 | 273.2191 | 273.2191 | 273.2191 | 273.2191 | 273.2191 | 273.2191 | 273.2191 | 273.2191 | 273.2191 | 273.2191 | 273.2191 | 273.2191 | 273.2191 | 273.2191 | 273.2191 | 273.2191
65% |  |  | 9.6236 | 6.9591 | 6.9298 | 20.0951 | 42.2143 | 111.9423 | 181.5617 | 226.0382 | 279.9918 | 333.9879 | 438.672 | 569.1816 | 560.3612 | 560.3612 | 560.3612 | 560.3612 | 560.3612 | 560.3612 | 560.3612 | 560.3612 | 560.3612 | 560.3612 | 560.3612 | 560.3612 | 560.3612 | 560.3612 | 560.3612 | 560.3612 |  |  | 10.9945 | 90.8581 | 84.8503 | 85.3547 | 95.7548 | 123.1346 | 141.4924 | 159.4485 | 180.4428 | 199.9162 | 218.8067 | 220.9952 | 243.0371 | 226.3906 | 226.3906 | 226.3906 | 226.3906 | 226.3906 | 226.3906 | 226.3906 | 226.3906 | 226.3906 | 226.3906 | 226.3906 | 226.3906 | 226.3906 | 226.3906 | 226.3906 | 226.3906
60% | [12 empty] | 5.9059 | 42.5222 | 39.014 | 39.014 | 39.014 | 39.014 | 39.014 | 39.014 | 39.014 | 39.014 | 39.014 | 39.014 | 39.014 | 39.014 | 39.014 | 39.014 | 39.014 | 39.014 |  |  |  | 3.8091 | 2.2281 | 2.3448 | 5.4041 | 19.2874 | 33.1836 | 50.2166 | 74.3153 | 100.576 | 129.3594 | 132.7839 | 167.2756 | 141.2268 | 141.2268 | 141.2268 | 141.2268 | 141.2268 | 141.2268 | 141.2268 | 141.2268 | 141.2268 | 141.2268 | 141.2268 | 141.2268 | 141.2268 | 141.2268 | 141.2268 | 141.2268
55% | [42 empty] | 0.36348 | 0.67093 | 8.8993 | 1.8255 | 1.8255 | 1.8255 | 1.8255 | 1.8255 | 1.8255 | 1.8255 | 1.8255 | 1.8255 | 1.8255 | 1.8255 | 1.8255 | 1.8255 | 1.8255 | 1.8255 | 1.8255
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 335.6968 | 750.8128 | 734.5714 | 734.3797 | 801.8103 | 883.4549 | 1075.2627 | 1232.5888 | 1324.7487 | 1430.9386 | 1532.6682 | 1729.3262 | 2003.2214 | 1983.6771 | 1983.6771 | 1983.6771 | 1983.6771 | 1983.6771 | 1983.6771 | 1983.6771 | 1983.6771 | 1983.6771 | 1983.6771 | 1983.6771 | 1983.6771 | 1983.6771 | 1983.6771 | 1983.6771 | 1983.6771 | E @ R (MWh) | 55.5322 | 678.63 | 1007.4559 | 985.2871 | 987.1322 | 1025.8309 | 1133.5396 | 1210.3445 | 1288.9099 | 1384.9521 | 1477.9447 | 1571.8256 | 1583.0571 | 1701.3108 | 1611.1437 | 1611.1437 | 1611.1437 | 1611.1437 | 1611.1437 | 1611.1437 | 1611.1437 | 1611.1437 | 1611.1437 | 1611.1437 | 1611.1437 | 1611.1437 | 1611.1437 | 1611.1437 | 1611.1437 | 1611.1437
Option 1 Summer POE50 W E @ R (MWh) N 1 | 0 | 234.9878 | 525.569 | 514.2 | 514.0658 | 561.2672 | 618.4185 | 752.6839 | 862.8122 | 927.3241 | 1001.657 | 1072.8678 | 1210.5283 | 1402.255 | 1388.5739 | 1388.5739 | 1388.5739 | 1388.5739 | 1388.5739 | 1388.5739 | 1388.5739 | 1388.5739 | 1388.5739 | 1388.5739 | 1388.5739 | 1388.5739 | 1388.5739 | 1388.5739 | 1388.5739 | 1388.5739 | Option 1 Summer POE10 W E @ R (MWh) N 1 | 16.6597 | 203.589 | 302.2368 | 295.5861 | 296.1396 | 307.7493 | 340.0619 | 363.1034 | 386.673 | 415.4856 | 443.3834 | 471.5477 | 474.9171 | 510.3932 | 483.3431 | 483.3431 | 483.3431 | 483.3431 | 483.3431 | 483.3431 | 483.3431 | 483.3431 | 483.3431 | 483.3431 | 483.3431 | 483.3431 | 483.3431 | 483.3431 | 483.3431 | 483.3431
Option 2 - 1A New PHS ZSS + Four new feeders
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | FY26: 9.8725; FY27: 15.8941 |  |  | 13.7943 | 20.0509
98% | FY26: 10.848; FY27: 18.0013 |  |  | 15.5069 | 22.9393
97% | FY26: 19.698; FY27: 33.8593 |  |  | 28.9211 | 43.6351
95% | FY26: 50.103; FY27: 91.9331 |  |  | 77.3465 | 120.8094
90% | FY26: 166.6526; FY27: 397.287 |  |  | 316.8623 | 556.4991
85% | FY26: 49.283; FY27: 550.9121 |  |  | 354.4405 | 939.8561
80% | FY27: 170.3674 |  |  | 26.6685 | 729.5248
75% | [33 empty] | 73.1703
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 306.4572 | 1278.2542 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 833.5401 | 2506.4849 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2 Winter POE50 W E @ R (MWh) N 1 | 0 | 214.5201 | 894.7779 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 2 Winter POE10 W E @ R (MWh) N 1 | 0 | 250.062 | 751.9455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | FY25: 0; FY26: 0; FY27: 0 |  | 8.924 | 31.6709 | 37.6273 | [7 empty] | 0.40995 | 1.5238 | 1.6528 | 2.9525 | 1.971 | 1.971 | 1.971 | 1.971 | 1.971 | 1.971 | 1.971 | 1.971 | 1.971 | 1.971 | 1.971 | 1.971 | 1.971 | 1.971 | 1.971 | 1.971
98% | FY25: 0; FY26: 0; FY27: 0 |  | 4.0751 | 15.3343 | 18.2825 | [7 empty] | 0.0015743 | 0.41218 | 0.47605 | 1.1193 | 0.63352 | 0.63352 | 0.63352 | 0.63352 | 0.63352 | 0.63352 | 0.63352 | 0.63352 | 0.63352 | 0.63352 | 0.63352 | 0.63352 | 0.63352 | 0.63352 | 0.63352 | 0.63352
97% | FY26: 5.4588; FY27: 6.9736 |  | 7.3764 | 29.6661 | 35.5027 | [8 empty] | 0.16105 | 0.25836 | 1.5249 | 0.56311 | 0.56311 | 0.56311 | 0.56311 | 0.56311 | 0.56311 | 0.56311 | 0.56311 | 0.56311 | 0.56311 | 0.56311 | 0.56311 | 0.56311 | 0.56311 | 0.56311 | 0.56311
95% | FY26: 25.5649; FY27: 33.0227 |  | 9.3236 | 42.2437 | 50.864 | [10 empty] | 0.71673 | 0.02375 | 0.02375 | 0.02375 | 0.02375 | 0.02375 | 0.02375 | 0.02375 | 0.02375 | 0.02375 | 0.02375 | 0.02375 | 0.02375 | 0.02375 | 0.02375 | 0.02375 | 0.02375
90% | FY26: 38.7554; FY27: 51.6899 |  | 23.6749 | 166.4146 | 203.7914
85% | FY26: 85.1452; FY27: 121.8514 |  | 2.1581 | 132.583 | 167.9395
80% | FY26: 80.0361; FY27: 131.3082 |  |  | 73.1492 | 97.8426
75% | FY26: 94.1589; FY27: 227.8159 |  |  | 91.3687 | 135.4427
70% | FY26: 6.5776; FY27: 168.5277 |  |  | 85.2049 | 165.4959
65% | FY27: 9.6236 |  |  | 10.9945 | 90.8581
60% | [33 empty] | 3.8091
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 335.6968 | 750.8128 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 55.5322 | 678.63 | 1007.4559 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.41152 | 2.097 | 2.3872 | 6.3135 | 3.1913 | 3.1913 | 3.1913 | 3.1913 | 3.1913 | 3.1913 | 3.1913 | 3.1913 | 3.1913 | 3.1913 | 3.1913 | 3.1913 | 3.1913 | 3.1913 | 3.1913 | 3.1913
Option 2 Summer POE50 W E @ R (MWh) N 1 | 0 | 234.9878 | 525.569 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 2 Summer POE10 W E @ R (MWh) N 1 | 16.6597 | 203.589 | 302.2368 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.12346 | 0.6291 | 0.71617 | 1.894 | 0.9574 | 0.9574 | 0.9574 | 0.9574 | 0.9574 | 0.9574 | 0.9574 | 0.9574 | 0.9574 | 0.9574 | 0.9574 | 0.9574 | 0.9574 | 0.9574 | 0.9574 | 0.9574
Option 3 - 2A PHM 3rd Tx + Switchroom + Three new feeders + OFR12 New Feeder
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | FY26: 9.8725; FY27: 15.8941 |  |  | 13.7943 | 20.0509
98% | FY26: 10.848; FY27: 18.0013 |  |  | 15.5069 | 22.9393
97% | FY26: 19.698; FY27: 33.8593 |  |  | 28.9211 | 43.6351
95% | FY26: 50.103; FY27: 91.9331 |  |  | 77.3465 | 120.8094
90% | FY26: 166.6526; FY27: 397.287 |  |  | 316.8623 | 556.4991
85% | FY26: 49.283; FY27: 550.9121 |  |  | 354.4405 | 939.8561
80% | FY27: 170.3674 |  |  | 26.6685 | 729.5248
75% | [33 empty] | 73.1703
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 306.4572 | 1278.2542 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 833.5401 | 2506.4849 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 Winter POE50 W E @ R (MWh) N 1 | 0 | 214.5201 | 894.7779 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 3 Winter POE10 W E @ R (MWh) N 1 | 0 | 250.062 | 751.9455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | FY25: 0; FY26: 0; FY27: 0 |  | 8.924 | 31.6709 | 37.6273
98% | FY25: 0; FY26: 0; FY27: 0 |  | 4.0751 | 15.3343 | 18.2825
97% | FY26: 5.4588; FY27: 6.9736 |  | 7.3764 | 29.6661 | 35.5027
95% | FY26: 25.5649; FY27: 33.0227 |  | 9.3236 | 42.2437 | 50.864
90% | FY26: 38.7554; FY27: 51.6899 |  | 23.6749 | 166.4146 | 203.7914
85% | FY26: 85.1452; FY27: 121.8514 |  | 2.1581 | 132.583 | 167.9395
80% | FY26: 80.0361; FY27: 131.3082 |  |  | 73.1492 | 97.8426
75% | FY26: 94.1589; FY27: 227.8159 |  |  | 91.3687 | 135.4427
70% | FY26: 6.5776; FY27: 168.5277 |  |  | 85.2049 | 165.4959
65% | FY27: 9.6236 |  |  | 10.9945 | 90.8581
60% | [33 empty] | 3.8091
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 335.6968 | 750.8128 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 55.5322 | 678.63 | 1007.4559 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 Summer POE50 W E @ R (MWh) N 1 | 0 | 234.9878 | 525.569 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 3 Summer POE10 W E @ R (MWh) N 1 | 16.6597 | 203.589 | 302.2368 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 - 3A OFR 3rd Tx + Switchroom + Three new feeders + OFR12 New Feeder
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% |  | 9.8725 | 15.8941 |  |  |  | 0.79613 | 2.8953 | 5.5545 | 6.9348 | 8.1491 | 5.9117 | 8.5339 | 12.6562 | 9.5279 | 9.5279 | 9.5279 | 9.5279 | 9.5279 | 9.5279 | 9.5279 | 9.5279 | 9.5279 | 9.5279 | 9.5279 | 9.5279 | 9.5279 | 9.5279 | 9.5279 | 9.5279 |  |  | 13.7943 | 20.0509 |  | 0.21487 | 1.543 | 4.7279 | 6.4667 | 9.7793 | 19.8484 | 11.5474 | 9.9237 | 12.1155 | 16.9089 | 13.6643 | 13.6643 | 13.6643 | 13.6643 | 13.6643 | 13.6643 | 13.6643 | 13.6643 | 13.6643 | 13.6643 | 13.6643 | 13.6643 | 13.6643 | 13.6643 | 13.6643 | 13.6643
98% |  | 10.848 | 18.0013 |  |  |  | 0.14653 | 2.5594 | 5.7184 | 7.3581 | 8.8007 | 6.1428 | 9.2578 | 14.1549 | 10.4387 | 10.4387 | 10.4387 | 10.4387 | 10.4387 | 10.4387 | 10.4387 | 10.4387 | 10.4387 | 10.4387 | 10.4387 | 10.4387 | 10.4387 | 10.4387 | 10.4387 | 10.4387 |  |  | 15.5069 | 22.9393 |  |  | 0.95299 | 4.7365 | 6.8021 | 10.7372 | 22.6988 | 12.8377 | 10.9089 | 13.5125 | 19.2067 | 15.3524 | 15.3524 | 15.3524 | 15.3524 | 15.3524 | 15.3524 | 15.3524 | 15.3524 | 15.3524 | 15.3524 | 15.3524 | 15.3524 | 15.3524 | 15.3524 | 15.3524 | 15.3524
97% |  | 19.698 | 33.8593 |  |  |  |  | 3.2891 | 9.543 | 12.7891 | 15.6449 | 10.383 | 16.5498 | 26.2446 | 18.8876 | 18.8876 | 18.8876 | 18.8876 | 18.8876 | 18.8876 | 18.8876 | 18.8876 | 18.8876 | 18.8876 | 18.8876 | 18.8876 | 18.8876 | 18.8876 | 18.8876 | 18.8876 |  |  | 28.9211 | 43.6351 |  |  | 0.28237 | 7.599 | 11.6884 | 19.4787 | 43.159 | 23.637 | 19.8185 | 24.973 | 36.2458 | 28.6154 | 28.6154 | 28.6154 | 28.6154 | 28.6154 | 28.6154 | 28.6154 | 28.6154 | 28.6154 | 28.6154 | 28.6154 | 28.6154 | 28.6154 | 28.6154 | 28.6154 | 28.6154
95% |  | 50.103 | 91.9331 |  |  |  |  | 2.3107 | 20.1066 | 29.6951 | 38.1307 | 22.5879 | 40.8036 | 69.4407 | 47.7091 | 47.7091 | 47.7091 | 47.7091 | 47.7091 | 47.7091 | 47.7091 | 47.7091 | 47.7091 | 47.7091 | 47.7091 | 47.7091 | 47.7091 | 47.7091 | 47.7091 | 47.7091 |  |  | 77.3465 | 120.8094 |  |  |  | 14.3642 | 26.4438 | 49.4551 | 119.403 | 61.738 | 50.4587 | 65.6843 | 98.9824 | 76.4434 | 76.4434 | 76.4434 | 76.4434 | 76.4434 | 76.4434 | 76.4434 | 76.4434 | 76.4434 | 76.4434 | 76.4434 | 76.4434 | 76.4434 | 76.4434 | 76.4434 | 76.4434
90% |  | 166.6526 | 397.287 | [5 empty] | 20.9567 | 56.5999 | 100.6421 | 28.5687 | 115.3792 | 273.2727 | 153.4534 | 153.4534 | 153.4534 | 153.4534 | 153.4534 | 153.4534 | 153.4534 | 153.4534 | 153.4534 | 153.4534 | 153.4534 | 153.4534 | 153.4534 | 153.4534 | 153.4534 | 153.4534 |  |  | 316.8623 | 556.4991 |  |  |  | 7.7796 | 42.6437 | 163.08 | 548.745 | 230.8035 | 168.6138 | 252.5618 | 436.154 | 311.883 | 311.883 | 311.883 | 311.883 | 311.883 | 311.883 | 311.883 | 311.883 | 311.883 | 311.883 | 311.883 | 311.883 | 311.883 | 311.883 | 311.883 | 311.883
85% |  | 49.283 | 550.9121 | [7 empty] | 2.1387 |  | 7.3623 | 247.9542 | 35.0245 | 35.0245 | 35.0245 | 35.0245 | 35.0245 | 35.0245 | 35.0245 | 35.0245 | 35.0245 | 35.0245 | 35.0245 | 35.0245 | 35.0245 | 35.0245 | 35.0245 | 35.0245 |  |  | 354.4405 | 939.8561 | [5 empty] | 45.1901 | 920.9133 | 151.5948 | 51.6034 | 198.3539 | 645.8614 | 342.2764 | 342.2764 | 342.2764 | 342.2764 | 342.2764 | 342.2764 | 342.2764 | 342.2764 | 342.2764 | 342.2764 | 342.2764 | 342.2764 | 342.2764 | 342.2764 | 342.2764 | 342.2764
80% | FY27: 170.3674; FY38: 0.65442 |  |  | 26.6685 | 729.5248 | [6 empty] | 700.0822 |  |  |  | 282.1966 | 21.8047 | 21.8047 | 21.8047 | 21.8047 | 21.8047 | 21.8047 | 21.8047 | 21.8047 | 21.8047 | 21.8047 | 21.8047 | 21.8047 | 21.8047 | 21.8047 | 21.8047 | 21.8047
75% | [33 empty] | 73.1703 | [6 empty] | 60.8142
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 306.4572 | 1278.2542 | 0 | 0 | 0 | 0.94266 | 11.0545 | 61.8792 | 113.3771 | 173.5062 | 73.5941 | 197.8865 | 644.3778 | 275.0412 | 275.0412 | 275.0412 | 275.0412 | 275.0412 | 275.0412 | 275.0412 | 275.0412 | 275.0412 | 275.0412 | 275.0412 | 275.0412 | 275.0412 | 275.0412 | 275.0412 | 275.0412 | E @ R (MWh) | 0 | 833.5401 | 2506.4849 | 0 | 0.21487 | 2.7783 | 39.2071 | 94.0447 | 297.7203 | 2435.664 | 492.1585 | 311.327 | 567.2011 | 1535.5558 | 810.0396 | 810.0396 | 810.0396 | 810.0396 | 810.0396 | 810.0396 | 810.0396 | 810.0396 | 810.0396 | 810.0396 | 810.0396 | 810.0396 | 810.0396 | 810.0396 | 810.0396 | 810.0396
Option 4 Winter POE50 W E @ R (MWh) N 1 | 0 | 214.5201 | 894.7779 | 0 | 0 | 0 | 0.65986 | 7.7382 | 43.3155 | 79.364 | 121.4543 | 51.5159 | 138.5205 | 451.0644 | 192.5288 | 192.5288 | 192.5288 | 192.5288 | 192.5288 | 192.5288 | 192.5288 | 192.5288 | 192.5288 | 192.5288 | 192.5288 | 192.5288 | 192.5288 | 192.5288 | 192.5288 | 192.5288 | Option 4 Winter POE10 W E @ R (MWh) N 1 | 0 | 250.062 | 751.9455 | 0 | 0.064461 | 0.83349 | 11.7621 | 28.2134 | 89.3161 | 730.6992 | 147.6475 | 93.3981 | 170.1603 | 460.6667 | 243.0119 | 243.0119 | 243.0119 | 243.0119 | 243.0119 | 243.0119 | 243.0119 | 243.0119 | 243.0119 | 243.0119 | 243.0119 | 243.0119 | 243.0119 | 243.0119 | 243.0119 | 243.0119
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 8.924 | 31.6709 | 37.6273 | 15.4492 | 15.4789 | 16.0921 | 17.7065 | 18.789 | 19.8477 | 21.0856 | 22.2338 | 23.3476 | 23.4767 | 24.7763 | 23.7948 | 23.7948 | 23.7948 | 23.7948 | 23.7948 | 23.7948 | 23.7948 | 23.7948 | 23.7948 | 23.7948 | 23.7948 | 23.7948 | 23.7948 | 23.7948 | 23.7948 | 23.7948
98% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4.0751 | 15.3343 | 18.2825 | 7.3049 | 7.3196 | 7.6231 | 8.4222 | 8.958 | 9.4821 | 10.0948 | 10.6631 | 11.2144 | 11.2783 | 11.9216 | 11.4358 | 11.4358 | 11.4358 | 11.4358 | 11.4358 | 11.4358 | 11.4358 | 11.4358 | 11.4358 | 11.4358 | 11.4358 | 11.4358 | 11.4358 | 11.4358 | 11.4358 | 11.4358
97% |  | 5.4588 | 6.9736 | 1.584 | 1.5835 | 1.7567 | 1.9468 | 2.3366 | 2.6166 | 2.7688 | 2.9356 | 3.088 | 3.3628 | 3.7037 | 3.6807 | 3.6807 | 3.6807 | 3.6807 | 3.6807 | 3.6807 | 3.6807 | 3.6807 | 3.6807 | 3.6807 | 3.6807 | 3.6807 | 3.6807 | 3.6807 | 3.6807 | 3.6807 |  | 7.3764 | 29.6661 | 35.5027 | 13.7704 | 13.7996 | 14.4005 | 15.9824 | 17.0431 | 18.0805 | 19.2935 | 20.4187 | 21.5101 | 21.6366 | 22.9101 | 21.9483 | 21.9483 | 21.9483 | 21.9483 | 21.9483 | 21.9483 | 21.9483 | 21.9483 | 21.9483 | 21.9483 | 21.9483 | 21.9483 | 21.9483 | 21.9483 | 21.9483 | 21.9483
95% |  | 25.5649 | 33.0227 | 6.489 | 6.4865 | 7.3395 | 8.2751 | 10.194 | 11.5726 | 12.3221 | 13.1432 | 13.8935 | 15.2463 | 16.9246 | 16.8111 | 16.8111 | 16.8111 | 16.8111 | 16.8111 | 16.8111 | 16.8111 | 16.8111 | 16.8111 | 16.8111 | 16.8111 | 16.8111 | 16.8111 | 16.8111 | 16.8111 | 16.8111 |  | 9.3236 | 42.2437 | 50.864 | 18.767 | 18.81 | 19.6975 | 22.0339 | 23.6005 | 25.1327 | 26.9242 | 28.586 | 30.198 | 30.3847 | 32.2656 | 30.8451 | 30.8451 | 30.8451 | 30.8451 | 30.8451 | 30.8451 | 30.8451 | 30.8451 | 30.8451 | 30.8451 | 30.8451 | 30.8451 | 30.8451 | 30.8451 | 30.8451 | 30.8451
90% |  | 38.7554 | 51.6899 | 5.6706 | 5.6662 | 7.1455 | 8.7683 | 12.0964 | 14.4874 | 15.7873 | 17.2114 | 18.5127 | 20.859 | 23.7697 | 23.573 | 23.573 | 23.573 | 23.573 | 23.573 | 23.573 | 23.573 | 23.573 | 23.573 | 23.573 | 23.573 | 23.573 | 23.573 | 23.573 | 23.573 | 23.573 |  | 23.6749 | 166.4146 | 203.7914 | 64.6211 | 64.8077 | 68.6557 | 78.7863 | 85.5786 | 92.2224 | 99.9903 | 107.1955 | 114.1849 | 114.9947 | 123.1502 | 116.991 | 116.991 | 116.991 | 116.991 | 116.991 | 116.991 | 116.991 | 116.991 | 116.991 | 116.991 | 116.991 | 116.991 | 116.991 | 116.991 | 116.991 | 116.991
85% |  | 85.1452 | 121.8514 | 0.33176 | 0.3297 | 1.3699 | 3.3057 | 9.7763 | 16.2767 | 19.9657 | 24.0069 | 27.6997 | 34.3583 | 42.6184 | 42.0601 | 42.0601 | 42.0601 | 42.0601 | 42.0601 | 42.0601 | 42.0601 | 42.0601 | 42.0601 | 42.0601 | 42.0601 | 42.0601 | 42.0601 | 42.0601 | 42.0601 | 42.0601 |  | 2.1581 | 132.583 | 167.9395 | 36.2918 | 36.4684 | 40.1084 | 49.6913 | 56.1166 | 62.4012 | 69.7492 | 76.5649 | 83.1766 | 83.9425 | 91.6572 | 85.8309 | 85.8309 | 85.8309 | 85.8309 | 85.8309 | 85.8309 | 85.8309 | 85.8309 | 85.8309 | 85.8309 | 85.8309 | 85.8309 | 85.8309 | 85.8309 | 85.8309 | 85.8309
80% |  | 80.0361 | 131.3082 | [5 empty] | 0.19628 | 1.0621 | 2.7858 | 5.0531 | 10.763 | 20.6381 | 19.876 | 19.876 | 19.876 | 19.876 | 19.876 | 19.876 | 19.876 | 19.876 | 19.876 | 19.876 | 19.876 | 19.876 | 19.876 | 19.876 | 19.876 | 19.876 |  |  | 73.1492 | 97.8426 | 6.4011 | 6.4984 | 8.6592 | 15.2566 | 19.7441 | 24.1334 | 29.2653 | 34.0255 | 38.6431 | 39.1781 | 44.5661 | 40.497 | 40.497 | 40.497 | 40.497 | 40.497 | 40.497 | 40.497 | 40.497 | 40.497 | 40.497 | 40.497 | 40.497 | 40.497 | 40.497 | 40.497 | 40.497
75% | FY26: 94.1589; FY27: 227.8159 |  |  | 91.3687 | 135.4427 |  |  |  | 0.88499 | 3.3957 | 7.3673 | 13.8398 | 21.5387 | 29.7806 | 30.7354 | 40.3522 | 33.0894 | 33.0894 | 33.0894 | 33.0894 | 33.0894 | 33.0894 | 33.0894 | 33.0894 | 33.0894 | 33.0894 | 33.0894 | 33.0894 | 33.0894 | 33.0894 | 33.0894 | 33.0894
70% | FY26: 6.5776; FY27: 168.5277 |  |  | 85.2049 | 165.4959 | [8 empty] | 1.4136 | 1.7584 | 7.269 | 2.7662 | 2.7662 | 2.7662 | 2.7662 | 2.7662 | 2.7662 | 2.7662 | 2.7662 | 2.7662 | 2.7662 | 2.7662 | 2.7662 | 2.7662 | 2.7662 | 2.7662 | 2.7662
65% | FY27: 9.6236 |  |  | 10.9945 | 90.8581
60% | [33 empty] | 3.8091
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 335.6968 | 750.8128 | 14.0754 | 14.0658 | 17.6116 | 22.2959 | 34.4032 | 45.1496 | 51.906 | 60.0829 | 68.247 | 84.5894 | 107.6544 | 106.001 | 106.001 | 106.001 | 106.001 | 106.001 | 106.001 | 106.001 | 106.001 | 106.001 | 106.001 | 106.001 | 106.001 | 106.001 | 106.001 | 106.001 | 106.001 | E @ R (MWh) | 55.5322 | 678.63 | 1007.4559 | 162.6055 | 163.1826 | 175.2367 | 208.7643 | 233.2255 | 258.6673 | 290.2428 | 321.2261 | 353.469 | 357.3853 | 398.8684 | 367.1985 | 367.1985 | 367.1985 | 367.1985 | 367.1985 | 367.1985 | 367.1985 | 367.1985 | 367.1985 | 367.1985 | 367.1985 | 367.1985 | 367.1985 | 367.1985 | 367.1985 | 367.1985
Option 4 Summer POE50 W E @ R (MWh) N 1 | 0 | 234.9878 | 525.569 | 9.8528 | 9.8461 | 12.3281 | 15.6071 | 24.0822 | 31.6047 | 36.3342 | 42.058 | 47.7729 | 59.2126 | 75.3581 | 74.2007 | 74.2007 | 74.2007 | 74.2007 | 74.2007 | 74.2007 | 74.2007 | 74.2007 | 74.2007 | 74.2007 | 74.2007 | 74.2007 | 74.2007 | 74.2007 | 74.2007 | 74.2007 | Option 4 Summer POE10 W E @ R (MWh) N 1 | 16.6597 | 203.589 | 302.2368 | 48.7817 | 48.9548 | 52.571 | 62.6293 | 69.9677 | 77.6002 | 87.0728 | 96.3678 | 106.0407 | 107.2156 | 119.6605 | 110.1596 | 110.1596 | 110.1596 | 110.1596 | 110.1596 | 110.1596 | 110.1596 | 110.1596 | 110.1596 | 110.1596 | 110.1596 | 110.1596 | 110.1596 | 110.1596 | 110.1596 | 110.1596
Option 5 - 4A LLG 2nd Tx + Switchroom + Three new feeders + OFR12 New Feeder
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | FY26: 9.8725; FY27: 15.8941 |  |  | 13.7943 | 20.0509
98% | FY26: 10.848; FY27: 18.0013 |  |  | 15.5069 | 22.9393
97% | FY26: 19.698; FY27: 33.8593 |  |  | 28.9211 | 43.6351
95% | FY26: 50.103; FY27: 91.9331 |  |  | 77.3465 | 120.8094
90% | FY26: 166.6526; FY27: 397.287 |  |  | 316.8623 | 556.4991
85% | FY26: 49.283; FY27: 550.9121 |  |  | 354.4405 | 939.8561
80% | FY27: 170.3674 |  |  | 26.6685 | 729.5248
75% | [33 empty] | 73.1703
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 306.4572 | 1278.2542 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 833.5401 | 2506.4849 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 Winter POE50 W E @ R (MWh) N 1 | 0 | 214.5201 | 894.7779 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 5 Winter POE10 W E @ R (MWh) N 1 | 0 | 250.062 | 751.9455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | FY25: 0; FY26: 0; FY27: 0 |  | 8.924 | 31.6709 | 37.6273 | [7 empty] | 0.40995 | 1.5238 | 1.6528 | 2.9525 | 1.971 | 1.971 | 1.971 | 1.971 | 1.971 | 1.971 | 1.971 | 1.971 | 1.971 | 1.971 | 1.971 | 1.971 | 1.971 | 1.971 | 1.971 | 1.971
98% | FY25: 0; FY26: 0; FY27: 0 |  | 4.0751 | 15.3343 | 18.2825 | [7 empty] | 0.0015743 | 0.41218 | 0.47605 | 1.1193 | 0.63352 | 0.63352 | 0.63352 | 0.63352 | 0.63352 | 0.63352 | 0.63352 | 0.63352 | 0.63352 | 0.63352 | 0.63352 | 0.63352 | 0.63352 | 0.63352 | 0.63352 | 0.63352
97% | FY26: 5.4588; FY27: 6.9736 |  | 7.3764 | 29.6661 | 35.5027 | [8 empty] | 0.16105 | 0.25836 | 1.5249 | 0.56311 | 0.56311 | 0.56311 | 0.56311 | 0.56311 | 0.56311 | 0.56311 | 0.56311 | 0.56311 | 0.56311 | 0.56311 | 0.56311 | 0.56311 | 0.56311 | 0.56311 | 0.56311
95% | FY26: 25.5649; FY27: 33.0227 |  | 9.3236 | 42.2437 | 50.864 | [10 empty] | 0.71673 | 0.02375 | 0.02375 | 0.02375 | 0.02375 | 0.02375 | 0.02375 | 0.02375 | 0.02375 | 0.02375 | 0.02375 | 0.02375 | 0.02375 | 0.02375 | 0.02375 | 0.02375 | 0.02375
90% | FY26: 38.7554; FY27: 51.6899 |  | 23.6749 | 166.4146 | 203.7914
85% | FY26: 85.1452; FY27: 121.8514 |  | 2.1581 | 132.583 | 167.9395
80% | FY26: 80.0361; FY27: 131.3082 |  |  | 73.1492 | 97.8426
75% | FY26: 94.1589; FY27: 227.8159 |  |  | 91.3687 | 135.4427
70% | FY26: 6.5776; FY27: 168.5277 |  |  | 85.2049 | 165.4959
65% | FY27: 9.6236 |  |  | 10.9945 | 90.8581
60% | [33 empty] | 3.8091
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 335.6968 | 750.8128 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 55.5322 | 678.63 | 1007.4559 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.41152 | 2.097 | 2.3872 | 6.3135 | 3.1913 | 3.1913 | 3.1913 | 3.1913 | 3.1913 | 3.1913 | 3.1913 | 3.1913 | 3.1913 | 3.1913 | 3.1913 | 3.1913 | 3.1913 | 3.1913 | 3.1913 | 3.1913
Option 5 Summer POE50 W E @ R (MWh) N 1 | 0 | 234.9878 | 525.569 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 5 Summer POE10 W E @ R (MWh) N 1 | 16.6597 | 203.589 | 302.2368 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.12346 | 0.6291 | 0.71617 | 1.894 | 0.9574 | 0.9574 | 0.9574 | 0.9574 | 0.9574 | 0.9574 | 0.9574 | 0.9574 | 0.9574 | 0.9574 | 0.9574 | 0.9574 | 0.9574 | 0.9574 | 0.9574 | 0.9574
Option 6 - Non Network
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% |  |  | 0.31803 | 1.3979 | 2.2007 | 3.4951 | 6.4029 | 8.3527 | 10.8639 | 12.0703 | 13.1258 | 10.7324 | 13.3403 | 17.2799 | 14.2973 | 14.2973 | 14.2973 | 14.2973 | 14.2973 | 14.2973 | 14.2973 | 14.2973 | 14.2973 | 14.2973 | 14.2973 | 14.2973 | 14.2973 | 14.2973 | 14.2973 | 14.2973 |  |  |  | 4.473 | 5.4964 | 6.1133 | 7.3778 | 10.3346 | 11.9242 | 15.0886 | 24.984 | 16.5241 | 14.7444 | 16.922 | 21.5325 | 18.4336 | 18.4336 | 18.4336 | 18.4336 | 18.4336 | 18.4336 | 18.4336 | 18.4336 | 18.4336 | 18.4336 | 18.4336 | 18.4336 | 18.4336 | 18.4336 | 18.4336 | 18.4336
98% |  |  |  | 0.78072 | 1.7344 | 3.272 | 6.7263 | 9.0426 | 12.0257 | 13.4588 | 14.7127 | 11.8695 | 14.9675 | 19.6476 | 16.1043 | 16.1043 | 16.1043 | 16.1043 | 16.1043 | 16.1043 | 16.1043 | 16.1043 | 16.1043 | 16.1043 | 16.1043 | 16.1043 | 16.1043 | 16.1043 | 16.1043 | 16.1043 |  |  |  | 4.4337 | 5.6494 | 6.3823 | 7.8845 | 11.397 | 13.2853 | 17.0445 | 28.7995 | 18.7497 | 16.6356 | 19.2223 | 24.6994 | 21.0181 | 21.0181 | 21.0181 | 21.0181 | 21.0181 | 21.0181 | 21.0181 | 21.0181 | 21.0181 | 21.0181 | 21.0181 | 21.0181 | 21.0181 | 21.0181 | 21.0181 | 21.0181
97% |  |  |  | 0.12314 | 1.6557 | 4.6999 | 11.5383 | 16.1238 | 22.0294 | 24.8666 | 27.3489 | 21.7202 | 27.8534 | 37.1185 | 30.1039 | 30.1039 | 30.1039 | 30.1039 | 30.1039 | 30.1039 | 30.1039 | 30.1039 | 30.1039 | 30.1039 | 30.1039 | 30.1039 | 30.1039 | 30.1039 | 30.1039 | 30.1039 |  |  |  | 6.9996 | 9.4064 | 10.8572 | 13.8311 | 20.7848 | 24.523 | 31.9651 | 55.2365 | 35.341 | 31.1556 | 36.2766 | 47.1196 | 39.8317 | 39.8317 | 39.8317 | 39.8317 | 39.8317 | 39.8317 | 39.8317 | 39.8317 | 39.8317 | 39.8317 | 39.8317 | 39.8317 | 39.8317 | 39.8317 | 39.8317 | 39.8317
95% |  |  |  |  | 0.23223 | 5.8007 | 26.0005 | 39.5452 | 56.9895 | 65.3701 | 72.7026 | 56.076 | 74.1927 | 101.5602 | 80.8403 | 80.8403 | 80.8403 | 80.8403 | 80.8403 | 80.8403 | 80.8403 | 80.8403 | 80.8403 | 80.8403 | 80.8403 | 80.8403 | 80.8403 | 80.8403 | 80.8403 | 80.8403 |  |  |  | 12.5939 | 19.7031 | 23.9886 | 32.7729 | 53.3131 | 64.3553 | 86.3379 | 155.078 | 96.31 | 83.9468 | 99.0735 | 131.102 | 109.5747 | 109.5747 | 109.5747 | 109.5747 | 109.5747 | 109.5747 | 109.5747 | 109.5747 | 109.5747 | 109.5747 | 109.5747 | 109.5747 | 109.5747 | 109.5747 | 109.5747 | 109.5747
90% | [5 empty] | 0.007435 | 40.8881 | 108.4411 | 204.6216 | 250.8294 | 291.2577 | 199.5855 | 299.4737 | 450.3671 | 336.1258 | 336.1258 | 336.1258 | 336.1258 | 336.1258 | 336.1258 | 336.1258 | 336.1258 | 336.1258 | 336.1258 | 336.1258 | 336.1258 | 336.1258 | 336.1258 | 336.1258 | 336.1258 |  |  |  | 4.9904 | 19.8274 | 33.3675 | 71.5386 | 184.3518 | 245.2341 | 366.4373 | 745.4428 | 421.4192 | 353.2539 | 436.6564 | 613.2484 | 494.5554 | 494.5554 | 494.5554 | 494.5554 | 494.5554 | 494.5554 | 494.5554 | 494.5554 | 494.5554 | 494.5554 | 494.5554 | 494.5554 | 494.5554 | 494.5554 | 494.5554 | 494.5554
85% | [7 empty] | 4.5164 | 103.3302 | 194.4129 | 291.8903 | 95.065 | 311.9614 | 680.5831 | 401.4998 | 401.4998 | 401.4998 | 401.4998 | 401.4998 | 401.4998 | 401.4998 | 401.4998 | 401.4998 | 401.4998 | 401.4998 | 401.4998 | 401.4998 | 401.4998 | 401.4998 | 401.4998 | [7 empty] | 72.0941 | 181.9407 | 475.5487 | 1401.4319 | 609.8653 | 443.3425 | 647.0888 | 1078.4904 | 788.5319 | 788.5319 | 788.5319 | 788.5319 | 788.5319 | 788.5319 | 788.5319 | 788.5319 | 788.5319 | 788.5319 | 788.5319 | 788.5319 | 788.5319 | 788.5319 | 788.5319 | 788.5319
80% | [10 empty] | 6.8271 |  | 11.7901 | 329.7212 | 49.9952 | 49.9952 | 49.9952 | 49.9952 | 49.9952 | 49.9952 | 49.9952 | 49.9952 | 49.9952 | 49.9952 | 49.9952 | 49.9952 | 49.9952 | 49.9952 | 49.9952 | 49.9952 | [9 empty] | 100.9773 | 1446.9505 | 236.6498 | 76.6814 | 283.8167 | 945.0037 | 494.3223 | 494.3223 | 494.3223 | 494.3223 | 494.3223 | 494.3223 | 494.3223 | 494.3223 | 494.3223 | 494.3223 | 494.3223 | 494.3223 | 494.3223 | 494.3223 | 494.3223 | 494.3223
75% | [40 empty] | 685.4677 |  |  |  | 196.9767 | 6.108 | 6.108 | 6.108 | 6.108 | 6.108 | 6.108 | 6.108 | 6.108 | 6.108 | 6.108 | 6.108 | 6.108 | 6.108 | 6.108 | 6.108 | 6.108
70% | [40 empty] | 18.0485
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0.31803 | 2.3018 | 5.823 | 17.2751 | 91.5563 | 186.0218 | 409.8602 | 561.0082 | 717.8652 | 395.0486 | 753.5793 | 1636.2776 | 928.9666 | 928.9666 | 928.9666 | 928.9666 | 928.9666 | 928.9666 | 928.9666 | 928.9666 | 928.9666 | 928.9666 | 928.9666 | 928.9666 | 928.9666 | 928.9666 | 928.9666 | 928.9666 | E @ R (MWh) | 0 | 0 | 33.4906 | 60.0828 | 80.7089 | 133.4048 | 352.2755 | 541.2626 | 1093.3994 | 4561.4393 | 1434.8592 | 1019.7602 | 1539.0564 | 3058.1726 | 1972.3757 | 1972.3757 | 1972.3757 | 1972.3757 | 1972.3757 | 1972.3757 | 1972.3757 | 1972.3757 | 1972.3757 | 1972.3757 | 1972.3757 | 1972.3757 | 1972.3757 | 1972.3757 | 1972.3757 | 1972.3757
Option 6 Winter POE50 W E @ R (MWh) N 1 | 0 | 0 | 0.22262 | 1.6113 | 4.0761 | 12.0926 | 64.0894 | 130.2153 | 286.9021 | 392.7058 | 502.5056 | 276.534 | 527.5055 | 1145.3943 | 650.2766 | 650.2766 | 650.2766 | 650.2766 | 650.2766 | 650.2766 | 650.2766 | 650.2766 | 650.2766 | 650.2766 | 650.2766 | 650.2766 | 650.2766 | 650.2766 | 650.2766 | 650.2766 | Option 6 Winter POE10 W E @ R (MWh) N 1 | 0 | 0 | 10.0472 | 18.0248 | 24.2127 | 40.0214 | 105.6827 | 162.3788 | 328.0198 | 1368.4318 | 430.4578 | 305.9281 | 461.7169 | 917.4518 | 591.7127 | 591.7127 | 591.7127 | 591.7127 | 591.7127 | 591.7127 | 591.7127 | 591.7127 | 591.7127 | 591.7127 | 591.7127 | 591.7127 | 591.7127 | 591.7127 | 591.7127 | 591.7127
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 16.6798 | 21.7699 | 21.4719 | 21.5039 | 22.0317 | 23.4139 | 24.3444 | 25.2524 | 26.3133 | 27.2998 | 28.2549 | 28.3694 | 29.483 | 28.6497 | 28.6497 | 28.6497 | 28.6497 | 28.6497 | 28.6497 | 28.6497 | 28.6497 | 28.6497 | 28.6497 | 28.6497 | 28.6497 | 28.6497 | 28.6497 | 28.6497 | 28.6497
98% |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 7.914 | 10.4335 | 10.286 | 10.3019 | 10.5631 | 11.2473 | 11.7078 | 12.1572 | 12.6823 | 13.1707 | 13.6434 | 13.7001 | 14.2513 | 13.8388 | 13.8388 | 13.8388 | 13.8388 | 13.8388 | 13.8388 | 13.8388 | 13.8388 | 13.8388 | 13.8388 | 13.8388 | 13.8388 | 13.8388 | 13.8388 | 13.8388 | 13.8388
97% |  | 1.7863 | 3.089 | 3.0594 | 3.0594 | 3.2118 | 3.3449 | 3.6975 | 3.9406 | 4.0495 | 4.1767 | 4.2901 | 4.5614 | 4.8567 | 4.87 | 4.87 | 4.87 | 4.87 | 4.87 | 4.87 | 4.87 | 4.87 | 4.87 | 4.87 | 4.87 | 4.87 | 4.87 | 4.87 | 4.87 | 4.87 |  |  | 14.9762 | 19.964 | 19.6721 | 19.7035 | 20.2206 | 21.5751 | 22.4868 | 23.3765 | 24.4161 | 25.3829 | 26.3187 | 26.4309 | 27.5222 | 26.7056 | 26.7056 | 26.7056 | 26.7056 | 26.7056 | 26.7056 | 26.7056 | 26.7056 | 26.7056 | 26.7056 | 26.7056 | 26.7056 | 26.7056 | 26.7056 | 26.7056 | 26.7056
95% |  | 7.4851 | 13.8982 | 13.7527 | 13.7528 | 14.5028 | 15.1584 | 16.894 | 18.0908 | 18.6268 | 19.2529 | 19.8117 | 21.1471 | 22.6009 | 22.6663 | 22.6663 | 22.6663 | 22.6663 | 22.6663 | 22.6663 | 22.6663 | 22.6663 | 22.6663 | 22.6663 | 22.6663 | 22.6663 | 22.6663 | 22.6663 | 22.6663 | 22.6663 |  |  | 20.5479 | 27.9145 | 27.4834 | 27.5297 | 28.2935 | 30.2939 | 31.6404 | 32.9545 | 34.4899 | 35.9177 | 37.2998 | 37.4656 | 39.0773 | 37.8713 | 37.8713 | 37.8713 | 37.8713 | 37.8713 | 37.8713 | 37.8713 | 37.8713 | 37.8713 | 37.8713 | 37.8713 | 37.8713 | 37.8713 | 37.8713 | 37.8713 | 37.8713
90% |  | 7.3982 | 18.5208 | 18.2685 | 18.2688 | 19.5694 | 20.7065 | 23.7166 | 25.7924 | 26.7221 | 27.808 | 28.7771 | 31.0931 | 33.6147 | 33.728 | 33.728 | 33.728 | 33.728 | 33.728 | 33.728 | 33.728 | 33.728 | 33.728 | 33.728 | 33.728 | 33.728 | 33.728 | 33.728 | 33.728 | 33.728 |  |  | 72.343 | 104.2841 | 102.4146 | 102.6154 | 105.9273 | 114.6009 | 120.4394 | 126.1373 | 132.7945 | 138.9854 | 144.9782 | 145.697 | 152.6851 | 147.4561 | 147.4561 | 147.4561 | 147.4561 | 147.4561 | 147.4561 | 147.4561 | 147.4561 | 147.4561 | 147.4561 | 147.4561 | 147.4561 | 147.4561 | 147.4561 | 147.4561 | 147.4561
85% |  | 1.6172 | 27.7228 | 27.0067 | 27.0076 | 30.6985 | 33.9255 | 42.4678 | 48.3583 | 50.9967 | 54.0784 | 56.8285 | 63.401 | 70.5568 | 70.8785 | 70.8785 | 70.8785 | 70.8785 | 70.8785 | 70.8785 | 70.8785 | 70.8785 | 70.8785 | 70.8785 | 70.8785 | 70.8785 | 70.8785 | 70.8785 | 70.8785 | 70.8785 |  |  | 43.5964 | 73.8109 | 72.0425 | 72.2324 | 75.3653 | 83.5701 | 89.093 | 94.4829 | 100.7803 | 106.6364 | 112.3054 | 112.9853 | 119.5956 | 114.6493 | 114.6493 | 114.6493 | 114.6493 | 114.6493 | 114.6493 | 114.6493 | 114.6493 | 114.6493 | 114.6493 | 114.6493 | 114.6493 | 114.6493 | 114.6493 | 114.6493 | 114.6493
80% |  |  | 5.0693 | 4.578 | 4.5786 | 7.37 | 10.3298 | 20.4312 | 28.6513 | 32.3366 | 36.6412 | 40.4827 | 49.6633 | 59.6586 | 60.108 | 60.108 | 60.108 | 60.108 | 60.108 | 60.108 | 60.108 | 60.108 | 60.108 | 60.108 | 60.108 | 60.108 | 60.108 | 60.108 | 60.108 | 60.108 |  |  | 10.9998 | 32.102 | 30.867 | 30.9996 | 33.1876 | 38.9179 | 42.7752 | 46.5396 | 50.9378 | 55.0278 | 58.9871 | 59.4619 | 64.0787 | 60.6241 | 60.6241 | 60.6241 | 60.6241 | 60.6241 | 60.6241 | 60.6241 | 60.6241 | 60.6241 | 60.6241 | 60.6241 | 60.6241 | 60.6241 | 60.6241 | 60.6241 | 60.6241
75% | [8 empty] | 1.6527 | 3.6963 | 7.089 | 11.0165 | 23.7591 | 42.8465 | 43.829 | 43.829 | 43.829 | 43.829 | 43.829 | 43.829 | 43.829 | 43.829 | 43.829 | 43.829 | 43.829 | 43.829 | 43.829 | 43.829 | 43.829 | 43.829 |  |  | 0.0055572 | 18.2356 | 16.2515 | 16.4594 | 20.0682 | 30.2711 | 37.1557 | 43.8745 | 51.7246 | 59.0247 | 66.0914 | 66.9389 | 75.1791 | 69.0133 | 69.0133 | 69.0133 | 69.0133 | 69.0133 | 69.0133 | 69.0133 | 69.0133 | 69.0133 | 69.0133 | 69.0133 | 69.0133 | 69.0133 | 69.0133 | 69.0133 | 69.0133
70% | [37 empty] | 1.5861 | 5.0304 | 10.1962 | 18.4205 | 28.1196 | 39.3327 | 40.7954 | 55.7119 | 44.4806 | 44.4806 | 44.4806 | 44.4806 | 44.4806 | 44.4806 | 44.4806 | 44.4806 | 44.4806 | 44.4806 | 44.4806 | 44.4806 | 44.4806 | 44.4806 | 44.4806 | 44.4806
65% | [44 empty] | 0.80075
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 18.2868 | 68.3 | 66.6653 | 66.6672 | 75.3524 | 83.4651 | 107.2071 | 126.486 | 136.428 | 149.0461 | 161.2066 | 193.625 | 234.1342 | 236.0799 | 236.0799 | 236.0799 | 236.0799 | 236.0799 | 236.0799 | 236.0799 | 236.0799 | 236.0799 | 236.0799 | 236.0799 | 236.0799 | 236.0799 | 236.0799 | 236.0799 | 236.0799 | E @ R (MWh) | 0 | 187.0628 | 308.5146 | 300.489 | 301.3458 | 315.6572 | 355.4762 | 384.6731 | 414.9711 | 452.5593 | 489.5649 | 527.2115 | 531.8446 | 578.3848 | 543.2889 | 543.2889 | 543.2889 | 543.2889 | 543.2889 | 543.2889 | 543.2889 | 543.2889 | 543.2889 | 543.2889 | 543.2889 | 543.2889 | 543.2889 | 543.2889 | 543.2889 | 543.2889
Option 6 Summer POE50 W E @ R (MWh) N 1 | 0 | 12.8007 | 47.81 | 46.6657 | 46.6671 | 52.7467 | 58.4256 | 75.045 | 88.5402 | 95.4996 | 104.3323 | 112.8446 | 135.5375 | 163.8939 | 165.2559 | 165.2559 | 165.2559 | 165.2559 | 165.2559 | 165.2559 | 165.2559 | 165.2559 | 165.2559 | 165.2559 | 165.2559 | 165.2559 | 165.2559 | 165.2559 | 165.2559 | 165.2559 | Option 6 Summer POE10 W E @ R (MWh) N 1 | 0 | 56.1188 | 92.5544 | 90.1467 | 90.4037 | 94.6972 | 106.6429 | 115.4019 | 124.4913 | 135.7678 | 146.8695 | 158.1635 | 159.5534 | 173.5155 | 162.9867 | 162.9867 | 162.9867 | 162.9867 | 162.9867 | 162.9867 | 162.9867 | 162.9867 | 162.9867 | 162.9867 | 162.9867 | 162.9867 | 162.9867 | 162.9867 | 162.9867 | 162.9867
Option 7 -
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% |  | 9.8725 | 15.8941 | 16.9205 | 17.721 | 19.0994 | 22.2353 | 24.3344 | 26.9936 | 28.3739 | 29.5883 | 27.3508 | 29.973 | 34.0954 | 30.9671 | 30.9671 | 30.9671 | 30.9671 | 30.9671 | 30.9671 | 30.9671 | 30.9671 | 30.9671 | 30.9671 | 30.9671 | 30.9671 | 30.9671 | 30.9671 | 30.9671 | 30.9671 |  |  | 13.7943 | 20.0509 | 21.019 | 21.6336 | 22.9821 | 26.167 | 27.9059 | 31.2184 | 41.2876 | 32.9866 | 31.3629 | 33.5547 | 38.348 | 35.1035 | 35.1035 | 35.1035 | 35.1035 | 35.1035 | 35.1035 | 35.1035 | 35.1035 | 35.1035 | 35.1035 | 35.1035 | 35.1035 | 35.1035 | 35.1035 | 35.1035 | 35.1035
98% |  | 10.848 | 18.0013 | 19.2206 | 20.1716 | 21.809 | 25.5342 | 28.0279 | 31.1869 | 32.8266 | 34.2691 | 31.6112 | 34.7262 | 39.6233 | 35.9071 | 35.9071 | 35.9071 | 35.9071 | 35.9071 | 35.9071 | 35.9071 | 35.9071 | 35.9071 | 35.9071 | 35.9071 | 35.9071 | 35.9071 | 35.9071 | 35.9071 | 35.9071 |  |  | 15.5069 | 22.9393 | 24.0893 | 24.8195 | 26.4214 | 30.2049 | 32.2706 | 36.2057 | 48.1672 | 38.3061 | 36.3773 | 38.981 | 44.6752 | 40.8209 | 40.8209 | 40.8209 | 40.8209 | 40.8209 | 40.8209 | 40.8209 | 40.8209 | 40.8209 | 40.8209 | 40.8209 | 40.8209 | 40.8209 | 40.8209 | 40.8209 | 40.8209
97% |  | 19.698 | 33.8593 | 36.2732 | 38.1558 | 41.3974 | 48.7723 | 53.7089 | 59.9627 | 63.2089 | 66.0646 | 60.8028 | 66.9695 | 76.6644 | 69.3073 | 69.3073 | 69.3073 | 69.3073 | 69.3073 | 69.3073 | 69.3073 | 69.3073 | 69.3073 | 69.3073 | 69.3073 | 69.3073 | 69.3073 | 69.3073 | 69.3073 | 69.3073 |  |  | 28.9211 | 43.6351 | 45.9118 | 47.3573 | 50.5286 | 58.0187 | 62.1081 | 69.8984 | 93.5787 | 74.0567 | 70.2382 | 75.3927 | 86.6655 | 79.0351 | 79.0351 | 79.0351 | 79.0351 | 79.0351 | 79.0351 | 79.0351 | 79.0351 | 79.0351 | 79.0351 | 79.0351 | 79.0351 | 79.0351 | 79.0351 | 79.0351 | 79.0351
95% |  | 50.103 | 91.9331 | 99.0634 | 104.6245 | 114.1996 | 135.9838 | 150.5658 | 169.0387 | 178.6273 | 187.0628 | 171.5201 | 189.7357 | 218.3728 | 196.6412 | 196.6412 | 196.6412 | 196.6412 | 196.6412 | 196.6412 | 196.6412 | 196.6412 | 196.6412 | 196.6412 | 196.6412 | 196.6412 | 196.6412 | 196.6412 | 196.6412 | 196.6412 |  |  | 77.3465 | 120.8094 | 127.5343 | 131.8043 | 141.1717 | 163.2964 | 175.3759 | 198.3872 | 268.3351 | 210.6702 | 199.3908 | 214.6165 | 247.9145 | 225.3755 | 225.3755 | 225.3755 | 225.3755 | 225.3755 | 225.3755 | 225.3755 | 225.3755 | 225.3755 | 225.3755 | 225.3755 | 225.3755 | 225.3755 | 225.3755 | 225.3755 | 225.3755
90% |  | 166.6526 | 397.287 | 436.6005 | 467.2624 | 520.0555 | 640.1647 | 720.5641 | 822.4165 | 875.2838 | 921.7942 | 836.0975 | 936.5313 | 1094.4248 | 974.6055 | 974.6055 | 974.6055 | 974.6055 | 974.6055 | 974.6055 | 974.6055 | 974.6055 | 974.6055 | 974.6055 | 974.6055 | 974.6055 | 974.6055 | 974.6055 | 974.6055 | 974.6055 |  |  | 316.8623 | 556.4991 | 593.5776 | 617.1207 | 668.7691 | 790.7554 | 857.3571 | 984.2321 | 1369.8972 | 1051.9556 | 989.7659 | 1073.714 | 1257.3061 | 1133.0351 | 1133.0351 | 1133.0351 | 1133.0351 | 1133.0351 | 1133.0351 | 1133.0351 | 1133.0351 | 1133.0351 | 1133.0351 | 1133.0351 | 1133.0351 | 1133.0351 | 1133.0351 | 1133.0351 | 1133.0351
85% |  | 49.283 | 550.9121 | 646.9524 | 721.8571 | 850.8267 | 1144.2449 | 1340.6551 | 1589.473 | 1718.6242 | 1832.2457 | 1622.8948 | 1868.2474 | 2253.97 | 1961.2601 | 1961.2601 | 1961.2601 | 1961.2601 | 1961.2601 | 1961.2601 | 1961.2601 | 1961.2601 | 1961.2601 | 1961.2601 | 1961.2601 | 1961.2601 | 1961.2601 | 1961.2601 | 1961.2601 | 1961.2601 |  |  | 354.4405 | 939.8561 | 1030.4361 | 1087.9502 | 1214.1234 | 1512.1274 | 1674.8304 | 1984.7771 | 2926.9292 | 2150.2208 | 1998.2958 | 2203.3748 | 2651.8773 | 2348.2922 | 2348.2922 | 2348.2922 | 2348.2922 | 2348.2922 | 2348.2922 | 2348.2922 | 2348.2922 | 2348.2922 | 2348.2922 | 2348.2922 | 2348.2922 | 2348.2922 | 2348.2922 | 2348.2922 | 2348.2922
80% |  |  | 170.3674 | 283.6364 | 390.7399 | 591.1469 | 1047.2057 | 1352.4853 | 1739.2221 | 1939.9613 | 2116.5629 | 1791.1696 | 2172.5202 | 2772.0475 | 2317.0894 | 2317.0894 | 2317.0894 | 2317.0894 | 2317.0894 | 2317.0894 | 2317.0894 | 2317.0894 | 2317.0894 | 2317.0894 | 2317.0894 | 2317.0894 | 2317.0894 | 2317.0894 | 2317.0894 | 2317.0894 |  |  | 26.6685 | 729.5248 | 870.3131 | 959.707 | 1155.8176 | 1619.0041 | 1871.8928 | 2353.6419 | 3818.0255 | 2610.7904 | 2374.6539 | 2693.4076 | 3390.5133 | 2918.6521 | 2918.6521 | 2918.6521 | 2918.6521 | 2918.6521 | 2918.6521 | 2918.6521 | 2918.6521 | 2918.6521 | 2918.6521 | 2918.6521 | 2918.6521 | 2918.6521 | 2918.6521 | 2918.6521 | 2918.6521
75% | [5 empty] | 24.883 | 275.7172 | 581.2462 | 1007.9249 | 1229.3962 | 1424.237 | 1065.2374 | 1485.9735 | 2147.4195 | 1645.4738 | 1645.4738 | 1645.4738 | 1645.4738 | 1645.4738 | 1645.4738 | 1645.4738 | 1645.4738 | 1645.4738 | 1645.4738 | 1645.4738 | 1645.4738 | 1645.4738 | 1645.4738 | 1645.4738 | 1645.4738 |  |  |  | 73.1703 | 147.4946 | 207.5247 | 373.0825 | 875.2908 | 1154.2977 | 1685.8014 | 3301.4252 | 1969.5079 | 1708.9835 | 2060.6577 | 2829.7599 | 2309.1653 | 2309.1653 | 2309.1653 | 2309.1653 | 2309.1653 | 2309.1653 | 2309.1653 | 2309.1653 | 2309.1653 | 2309.1653 | 2309.1653 | 2309.1653 | 2309.1653 | 2309.1653 | 2309.1653 | 2309.1653
70% | [7 empty] | 3.4379 | 133.5638 | 272.0098 | 431.8215 | 164.8836 | 489.6671 | 1193.5489 | 654.2363 | 654.2363 | 654.2363 | 654.2363 | 654.2363 | 654.2363 | 654.2363 | 654.2363 | 654.2363 | 654.2363 | 654.2363 | 654.2363 | 654.2363 | 654.2363 | 654.2363 | 654.2363 | [7 empty] | 73.4213 | 219.8269 | 697.566 | 2433.4635 | 1002.3928 | 722.4739 | 1100.3282 | 1926.6855 | 1367.3357 | 1367.3357 | 1367.3357 | 1367.3357 | 1367.3357 | 1367.3357 | 1367.3357 | 1367.3357 | 1367.3357 | 1367.3357 | 1367.3357 | 1367.3357 | 1367.3357 | 1367.3357 | 1367.3357 | 1367.3357
65% | FY38: 138.0019; FY39: 0.607; FY40: 0.607; FY41: 0.607; FY42: 0.607; FY43: 0.607; FY44: 0.607; FY45: 0.607; FY46: 0.607; FY47: 0.607; FY48: 0.607; FY49: 0.607; FY50: 0.607; FY51: 0.607; FY52: 0.607; FY53: 0.607; FY54: 0.607 | [9 empty] | 2.7969 | 1216.8668 | 62.358 | 4.774 | 97.5063 | 684.2805 | 231.4677 | 231.4677 | 231.4677 | 231.4677 | 231.4677 | 231.4677 | 231.4677 | 231.4677 | 231.4677 | 231.4677 | 231.4677 | 231.4677 | 231.4677 | 231.4677 | 231.4677 | 231.4677
60% | [40 empty] | 77.6441
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 306.4572 | 1278.2542 | 1538.6669 | 1760.5324 | 2183.4175 | 3339.858 | 4255.0255 | 5579.7822 | 6338.312 | 7043.6462 | 5771.5678 | 7274.3439 | 9968.1685 | 7886.0948 | 7886.0948 | 7886.0948 | 7886.0948 | 7886.0948 | 7886.0948 | 7886.0948 | 7886.0948 | 7886.0948 | 7886.0948 | 7886.0948 | 7886.0948 | 7886.0948 | 7886.0948 | 7886.0948 | 7886.0948 | E @ R (MWh) | 0 | 833.5401 | 2506.4849 | 2860.3759 | 3097.9173 | 3652.8965 | 5148.2859 | 6075.8653 | 8044.5252 | 15595.6201 | 9203.2451 | 8136.3162 | 9591.5333 | 13158.0259 | 10688.2832 | 10688.2832 | 10688.2832 | 10688.2832 | 10688.2832 | 10688.2832 | 10688.2832 | 10688.2832 | 10688.2832 | 10688.2832 | 10688.2832 | 10688.2832 | 10688.2832 | 10688.2832 | 10688.2832 | 10688.2832
Option 7 Winter POE50 W E @ R (MWh) N 1 | 0 | 214.5201 | 894.7779 | 1077.0669 | 1232.3727 | 1528.3922 | 2337.9006 | 2978.5179 | 3905.8475 | 4436.8184 | 4930.5523 | 4040.0974 | 5092.0407 | 6977.718 | 5520.2664 | 5520.2664 | 5520.2664 | 5520.2664 | 5520.2664 | 5520.2664 | 5520.2664 | 5520.2664 | 5520.2664 | 5520.2664 | 5520.2664 | 5520.2664 | 5520.2664 | 5520.2664 | 5520.2664 | 5520.2664 | Option 7 Winter POE10 W E @ R (MWh) N 1 | 0 | 250.062 | 751.9455 | 858.1128 | 929.3752 | 1095.8689 | 1544.4858 | 1822.7596 | 2413.3575 | 4678.686 | 2760.9735 | 2440.8949 | 2877.46 | 3947.4078 | 3206.485 | 3206.485 | 3206.485 | 3206.485 | 3206.485 | 3206.485 | 3206.485 | 3206.485 | 3206.485 | 3206.485 | 3206.485 | 3206.485 | 3206.485 | 3206.485 | 3206.485 | 3206.485
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 8.924 | 31.6709 | 37.6273 | 37.273 | 37.3028 | 37.916 | 39.5304 | 40.6128 | 41.6716 | 42.9095 | 44.0577 | 45.1715 | 45.3005 | 46.6002 | 45.6187 | 45.6187 | 45.6187 | 45.6187 | 45.6187 | 45.6187 | 45.6187 | 45.6187 | 45.6187 | 45.6187 | 45.6187 | 45.6187 | 45.6187 | 45.6187 | 45.6187 | 45.6187
98% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4.0751 | 15.3343 | 18.2825 | 18.1072 | 18.1219 | 18.4254 | 19.2245 | 19.7603 | 20.2843 | 20.897 | 21.4654 | 22.0167 | 22.0806 | 22.7239 | 22.238 | 22.238 | 22.238 | 22.238 | 22.238 | 22.238 | 22.238 | 22.238 | 22.238 | 22.238 | 22.238 | 22.238 | 22.238 | 22.238 | 22.238 | 22.238
97% |  | 5.4588 | 6.9736 | 6.9303 | 6.9298 | 7.103 | 7.2931 | 7.6829 | 7.9629 | 8.1151 | 8.2819 | 8.4343 | 8.7091 | 9.05 | 9.027 | 9.027 | 9.027 | 9.027 | 9.027 | 9.027 | 9.027 | 9.027 | 9.027 | 9.027 | 9.027 | 9.027 | 9.027 | 9.027 | 9.027 | 9.027 |  | 7.3764 | 29.6661 | 35.5027 | 35.1556 | 35.1847 | 35.7856 | 37.3676 | 38.4283 | 39.4657 | 40.6787 | 41.8039 | 42.8953 | 43.0218 | 44.2953 | 43.3335 | 43.3335 | 43.3335 | 43.3335 | 43.3335 | 43.3335 | 43.3335 | 43.3335 | 43.3335 | 43.3335 | 43.3335 | 43.3335 | 43.3335 | 43.3335 | 43.3335 | 43.3335
95% |  | 25.5649 | 33.0227 | 32.8093 | 32.8067 | 33.6597 | 34.5953 | 36.5142 | 37.8928 | 38.6423 | 39.4634 | 40.2137 | 41.5666 | 43.2448 | 43.1314 | 43.1314 | 43.1314 | 43.1314 | 43.1314 | 43.1314 | 43.1314 | 43.1314 | 43.1314 | 43.1314 | 43.1314 | 43.1314 | 43.1314 | 43.1314 | 43.1314 | 43.1314 |  | 9.3236 | 42.2437 | 50.864 | 50.3513 | 50.3943 | 51.2818 | 53.6182 | 55.1847 | 56.717 | 58.5085 | 60.1702 | 61.7822 | 61.969 | 63.8499 | 62.4294 | 62.4294 | 62.4294 | 62.4294 | 62.4294 | 62.4294 | 62.4294 | 62.4294 | 62.4294 | 62.4294 | 62.4294 | 62.4294 | 62.4294 | 62.4294 | 62.4294 | 62.4294
90% |  | 38.7554 | 51.6899 | 51.3198 | 51.3153 | 52.7947 | 54.4175 | 57.7455 | 60.1366 | 61.4365 | 62.8605 | 64.1618 | 66.5082 | 69.4189 | 69.2222 | 69.2222 | 69.2222 | 69.2222 | 69.2222 | 69.2222 | 69.2222 | 69.2222 | 69.2222 | 69.2222 | 69.2222 | 69.2222 | 69.2222 | 69.2222 | 69.2222 | 69.2222 |  | 23.6749 | 166.4146 | 203.7914 | 201.5685 | 201.7552 | 205.6032 | 215.7337 | 222.5261 | 229.1699 | 236.9378 | 244.1429 | 251.1324 | 251.9421 | 260.0977 | 253.9385 | 253.9385 | 253.9385 | 253.9385 | 253.9385 | 253.9385 | 253.9385 | 253.9385 | 253.9385 | 253.9385 | 253.9385 | 253.9385 | 253.9385 | 253.9385 | 253.9385 | 253.9385
85% |  | 85.1452 | 121.8514 | 120.801 | 120.7884 | 124.9866 | 129.5917 | 139.0363 | 145.8216 | 149.5106 | 153.5518 | 157.2446 | 163.9032 | 172.1633 | 171.605 | 171.605 | 171.605 | 171.605 | 171.605 | 171.605 | 171.605 | 171.605 | 171.605 | 171.605 | 171.605 | 171.605 | 171.605 | 171.605 | 171.605 | 171.605 |  | 2.1581 | 132.583 | 167.9395 | 165.8367 | 166.0133 | 169.6533 | 179.2362 | 185.6615 | 191.9461 | 199.2941 | 206.1098 | 212.7215 | 213.4874 | 221.2021 | 215.3759 | 215.3759 | 215.3759 | 215.3759 | 215.3759 | 215.3759 | 215.3759 | 215.3759 | 215.3759 | 215.3759 | 215.3759 | 215.3759 | 215.3759 | 215.3759 | 215.3759 | 215.3759
80% |  | 80.0361 | 131.3082 | 129.841 | 129.8234 | 135.6876 | 142.1201 | 155.3125 | 164.7904 | 169.9433 | 175.5881 | 180.7464 | 190.0472 | 201.5852 | 200.8054 | 200.8054 | 200.8054 | 200.8054 | 200.8054 | 200.8054 | 200.8054 | 200.8054 | 200.8054 | 200.8054 | 200.8054 | 200.8054 | 200.8054 | 200.8054 | 200.8054 | 200.8054 |  |  | 73.1492 | 97.8426 | 96.374 | 96.4973 | 99.0396 | 105.7324 | 110.2199 | 114.6092 | 119.7411 | 124.5013 | 129.1189 | 129.6539 | 135.0419 | 130.9728 | 130.9728 | 130.9728 | 130.9728 | 130.9728 | 130.9728 | 130.9728 | 130.9728 | 130.9728 | 130.9728 | 130.9728 | 130.9728 | 130.9728 | 130.9728 | 130.9728 | 130.9728
75% |  | 94.1589 | 227.8159 | 223.9912 | 223.9454 | 239.2321 | 256.0006 | 290.3908 | 315.098 | 328.5306 | 343.2457 | 356.6924 | 380.938 | 411.0152 | 408.9825 | 408.9825 | 408.9825 | 408.9825 | 408.9825 | 408.9825 | 408.9825 | 408.9825 | 408.9825 | 408.9825 | 408.9825 | 408.9825 | 408.9825 | 408.9825 | 408.9825 | 408.9825 |  |  | 91.3687 | 135.4427 | 132.8215 | 133.0415 | 137.5791 | 149.5248 | 157.5342 | 165.3684 | 174.5281 | 183.0243 | 191.2662 | 192.221 | 201.8378 | 194.575 | 194.575 | 194.575 | 194.575 | 194.575 | 194.575 | 194.575 | 194.575 | 194.575 | 194.575 | 194.575 | 194.575 | 194.575 | 194.575 | 194.575 | 194.575
70% |  | 6.5776 | 168.5277 | 161.9198 | 161.8408 | 188.2515 | 217.2224 | 276.6382 | 319.3247 | 342.5321 | 367.9553 | 391.1871 | 433.0761 | 485.0404 | 481.5284 | 481.5284 | 481.5284 | 481.5284 | 481.5284 | 481.5284 | 481.5284 | 481.5284 | 481.5284 | 481.5284 | 481.5284 | 481.5284 | 481.5284 | 481.5284 | 481.5284 | 481.5284 |  |  | 85.2049 | 165.4959 | 160.7208 | 161.1217 | 169.3879 | 191.1497 | 205.7408 | 220.0126 | 236.6991 | 252.1769 | 267.1913 | 268.9307 | 286.45 | 273.2191 | 273.2191 | 273.2191 | 273.2191 | 273.2191 | 273.2191 | 273.2191 | 273.2191 | 273.2191 | 273.2191 | 273.2191 | 273.2191 | 273.2191 | 273.2191 | 273.2191 | 273.2191
65% |  |  | 9.6236 | 6.9591 | 6.9298 | 20.0951 | 42.2143 | 111.9423 | 181.5617 | 226.0382 | 279.9918 | 333.9879 | 438.672 | 569.1816 | 560.3612 | 560.3612 | 560.3612 | 560.3612 | 560.3612 | 560.3612 | 560.3612 | 560.3612 | 560.3612 | 560.3612 | 560.3612 | 560.3612 | 560.3612 | 560.3612 | 560.3612 | 560.3612 |  |  | 10.9945 | 90.8581 | 84.8503 | 85.3547 | 95.7548 | 123.1346 | 141.4924 | 159.4485 | 180.4428 | 199.9162 | 218.8067 | 220.9952 | 243.0371 | 226.3906 | 226.3906 | 226.3906 | 226.3906 | 226.3906 | 226.3906 | 226.3906 | 226.3906 | 226.3906 | 226.3906 | 226.3906 | 226.3906 | 226.3906 | 226.3906 | 226.3906 | 226.3906
60% | [12 empty] | 5.9059 | 42.5222 | 39.014 | 39.014 | 39.014 | 39.014 | 39.014 | 39.014 | 39.014 | 39.014 | 39.014 | 39.014 | 39.014 | 39.014 | 39.014 | 39.014 | 39.014 | 39.014 |  |  |  | 3.8091 | 2.2281 | 2.3448 | 5.4041 | 19.2874 | 33.1836 | 50.2166 | 74.3153 | 100.576 | 129.3594 | 132.7839 | 167.2756 | 141.2268 | 141.2268 | 141.2268 | 141.2268 | 141.2268 | 141.2268 | 141.2268 | 141.2268 | 141.2268 | 141.2268 | 141.2268 | 141.2268 | 141.2268 | 141.2268 | 141.2268 | 141.2268
55% | [42 empty] | 0.36348 | 0.67093 | 8.8993 | 1.8255 | 1.8255 | 1.8255 | 1.8255 | 1.8255 | 1.8255 | 1.8255 | 1.8255 | 1.8255 | 1.8255 | 1.8255 | 1.8255 | 1.8255 | 1.8255 | 1.8255 | 1.8255
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 335.6968 | 750.8128 | 734.5714 | 734.3797 | 801.8103 | 883.4549 | 1075.2627 | 1232.5888 | 1324.7487 | 1430.9386 | 1532.6682 | 1729.3262 | 2003.2214 | 1983.6771 | 1983.6771 | 1983.6771 | 1983.6771 | 1983.6771 | 1983.6771 | 1983.6771 | 1983.6771 | 1983.6771 | 1983.6771 | 1983.6771 | 1983.6771 | 1983.6771 | 1983.6771 | 1983.6771 | 1983.6771 | E @ R (MWh) | 55.5322 | 678.63 | 1007.4559 | 985.2871 | 987.1322 | 1025.8309 | 1133.5396 | 1210.3445 | 1288.9099 | 1384.9521 | 1477.9447 | 1571.8256 | 1583.0571 | 1701.3108 | 1611.1437 | 1611.1437 | 1611.1437 | 1611.1437 | 1611.1437 | 1611.1437 | 1611.1437 | 1611.1437 | 1611.1437 | 1611.1437 | 1611.1437 | 1611.1437 | 1611.1437 | 1611.1437 | 1611.1437 | 1611.1437
Option 7 Summer POE50 W E @ R (MWh) N 1 | 0 | 234.9878 | 525.569 | 514.2 | 514.0658 | 561.2672 | 618.4185 | 752.6839 | 862.8122 | 927.3241 | 1001.657 | 1072.8678 | 1210.5283 | 1402.255 | 1388.5739 | 1388.5739 | 1388.5739 | 1388.5739 | 1388.5739 | 1388.5739 | 1388.5739 | 1388.5739 | 1388.5739 | 1388.5739 | 1388.5739 | 1388.5739 | 1388.5739 | 1388.5739 | 1388.5739 | 1388.5739 | Option 7 Summer POE10 W E @ R (MWh) N 1 | 16.6597 | 203.589 | 302.2368 | 295.5861 | 296.1396 | 307.7493 | 340.0619 | 363.1034 | 386.673 | 415.4856 | 443.3834 | 471.5477 | 474.9171 | 510.3932 | 483.3431 | 483.3431 | 483.3431 | 483.3431 | 483.3431 | 483.3431 | 483.3431 | 483.3431 | 483.3431 | 483.3431 | 483.3431 | 483.3431 | 483.3431 | 483.3431 | 483.3431 | 483.3431
Option 8 -
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% |  | 9.8725 | 15.8941 | 16.9205 | 17.721 | 19.0994 | 22.2353 | 24.3344 | 26.9936 | 28.3739 | 29.5883 | 27.3508 | 29.973 | 34.0954 | 30.9671 | 30.9671 | 30.9671 | 30.9671 | 30.9671 | 30.9671 | 30.9671 | 30.9671 | 30.9671 | 30.9671 | 30.9671 | 30.9671 | 30.9671 | 30.9671 | 30.9671 | 30.9671 |  |  | 13.7943 | 20.0509 | 21.019 | 21.6336 | 22.9821 | 26.167 | 27.9059 | 31.2184 | 41.2876 | 32.9866 | 31.3629 | 33.5547 | 38.348 | 35.1035 | 35.1035 | 35.1035 | 35.1035 | 35.1035 | 35.1035 | 35.1035 | 35.1035 | 35.1035 | 35.1035 | 35.1035 | 35.1035 | 35.1035 | 35.1035 | 35.1035 | 35.1035
98% |  | 10.848 | 18.0013 | 19.2206 | 20.1716 | 21.809 | 25.5342 | 28.0279 | 31.1869 | 32.8266 | 34.2691 | 31.6112 | 34.7262 | 39.6233 | 35.9071 | 35.9071 | 35.9071 | 35.9071 | 35.9071 | 35.9071 | 35.9071 | 35.9071 | 35.9071 | 35.9071 | 35.9071 | 35.9071 | 35.9071 | 35.9071 | 35.9071 | 35.9071 |  |  | 15.5069 | 22.9393 | 24.0893 | 24.8195 | 26.4214 | 30.2049 | 32.2706 | 36.2057 | 48.1672 | 38.3061 | 36.3773 | 38.981 | 44.6752 | 40.8209 | 40.8209 | 40.8209 | 40.8209 | 40.8209 | 40.8209 | 40.8209 | 40.8209 | 40.8209 | 40.8209 | 40.8209 | 40.8209 | 40.8209 | 40.8209 | 40.8209 | 40.8209
97% |  | 19.698 | 33.8593 | 36.2732 | 38.1558 | 41.3974 | 48.7723 | 53.7089 | 59.9627 | 63.2089 | 66.0646 | 60.8028 | 66.9695 | 76.6644 | 69.3073 | 69.3073 | 69.3073 | 69.3073 | 69.3073 | 69.3073 | 69.3073 | 69.3073 | 69.3073 | 69.3073 | 69.3073 | 69.3073 | 69.3073 | 69.3073 | 69.3073 | 69.3073 |  |  | 28.9211 | 43.6351 | 45.9118 | 47.3573 | 50.5286 | 58.0187 | 62.1081 | 69.8984 | 93.5787 | 74.0567 | 70.2382 | 75.3927 | 86.6655 | 79.0351 | 79.0351 | 79.0351 | 79.0351 | 79.0351 | 79.0351 | 79.0351 | 79.0351 | 79.0351 | 79.0351 | 79.0351 | 79.0351 | 79.0351 | 79.0351 | 79.0351 | 79.0351
95% |  | 50.103 | 91.9331 | 99.0634 | 104.6245 | 114.1996 | 135.9838 | 150.5658 | 169.0387 | 178.6273 | 187.0628 | 171.5201 | 189.7357 | 218.3728 | 196.6412 | 196.6412 | 196.6412 | 196.6412 | 196.6412 | 196.6412 | 196.6412 | 196.6412 | 196.6412 | 196.6412 | 196.6412 | 196.6412 | 196.6412 | 196.6412 | 196.6412 | 196.6412 |  |  | 77.3465 | 120.8094 | 127.5343 | 131.8043 | 141.1717 | 163.2964 | 175.3759 | 198.3872 | 268.3351 | 210.6702 | 199.3908 | 214.6165 | 247.9145 | 225.3755 | 225.3755 | 225.3755 | 225.3755 | 225.3755 | 225.3755 | 225.3755 | 225.3755 | 225.3755 | 225.3755 | 225.3755 | 225.3755 | 225.3755 | 225.3755 | 225.3755 | 225.3755
90% |  | 166.6526 | 397.287 | 436.6005 | 467.2624 | 520.0555 | 640.1647 | 720.5641 | 822.4165 | 875.2838 | 921.7942 | 836.0975 | 936.5313 | 1094.4248 | 974.6055 | 974.6055 | 974.6055 | 974.6055 | 974.6055 | 974.6055 | 974.6055 | 974.6055 | 974.6055 | 974.6055 | 974.6055 | 974.6055 | 974.6055 | 974.6055 | 974.6055 | 974.6055 |  |  | 316.8623 | 556.4991 | 593.5776 | 617.1207 | 668.7691 | 790.7554 | 857.3571 | 984.2321 | 1369.8972 | 1051.9556 | 989.7659 | 1073.714 | 1257.3061 | 1133.0351 | 1133.0351 | 1133.0351 | 1133.0351 | 1133.0351 | 1133.0351 | 1133.0351 | 1133.0351 | 1133.0351 | 1133.0351 | 1133.0351 | 1133.0351 | 1133.0351 | 1133.0351 | 1133.0351 | 1133.0351
85% |  | 49.283 | 550.9121 | 646.9524 | 721.8571 | 850.8267 | 1144.2449 | 1340.6551 | 1589.473 | 1718.6242 | 1832.2457 | 1622.8948 | 1868.2474 | 2253.97 | 1961.2601 | 1961.2601 | 1961.2601 | 1961.2601 | 1961.2601 | 1961.2601 | 1961.2601 | 1961.2601 | 1961.2601 | 1961.2601 | 1961.2601 | 1961.2601 | 1961.2601 | 1961.2601 | 1961.2601 | 1961.2601 |  |  | 354.4405 | 939.8561 | 1030.4361 | 1087.9502 | 1214.1234 | 1512.1274 | 1674.8304 | 1984.7771 | 2926.9292 | 2150.2208 | 1998.2958 | 2203.3748 | 2651.8773 | 2348.2922 | 2348.2922 | 2348.2922 | 2348.2922 | 2348.2922 | 2348.2922 | 2348.2922 | 2348.2922 | 2348.2922 | 2348.2922 | 2348.2922 | 2348.2922 | 2348.2922 | 2348.2922 | 2348.2922 | 2348.2922
80% |  |  | 170.3674 | 283.6364 | 390.7399 | 591.1469 | 1047.2057 | 1352.4853 | 1739.2221 | 1939.9613 | 2116.5629 | 1791.1696 | 2172.5202 | 2772.0475 | 2317.0894 | 2317.0894 | 2317.0894 | 2317.0894 | 2317.0894 | 2317.0894 | 2317.0894 | 2317.0894 | 2317.0894 | 2317.0894 | 2317.0894 | 2317.0894 | 2317.0894 | 2317.0894 | 2317.0894 | 2317.0894 |  |  | 26.6685 | 729.5248 | 870.3131 | 959.707 | 1155.8176 | 1619.0041 | 1871.8928 | 2353.6419 | 3818.0255 | 2610.7904 | 2374.6539 | 2693.4076 | 3390.5133 | 2918.6521 | 2918.6521 | 2918.6521 | 2918.6521 | 2918.6521 | 2918.6521 | 2918.6521 | 2918.6521 | 2918.6521 | 2918.6521 | 2918.6521 | 2918.6521 | 2918.6521 | 2918.6521 | 2918.6521 | 2918.6521
75% | [5 empty] | 24.883 | 275.7172 | 581.2462 | 1007.9249 | 1229.3962 | 1424.237 | 1065.2374 | 1485.9735 | 2147.4195 | 1645.4738 | 1645.4738 | 1645.4738 | 1645.4738 | 1645.4738 | 1645.4738 | 1645.4738 | 1645.4738 | 1645.4738 | 1645.4738 | 1645.4738 | 1645.4738 | 1645.4738 | 1645.4738 | 1645.4738 | 1645.4738 |  |  |  | 73.1703 | 147.4946 | 207.5247 | 373.0825 | 875.2908 | 1154.2977 | 1685.8014 | 3301.4252 | 1969.5079 | 1708.9835 | 2060.6577 | 2829.7599 | 2309.1653 | 2309.1653 | 2309.1653 | 2309.1653 | 2309.1653 | 2309.1653 | 2309.1653 | 2309.1653 | 2309.1653 | 2309.1653 | 2309.1653 | 2309.1653 | 2309.1653 | 2309.1653 | 2309.1653 | 2309.1653
70% | [7 empty] | 3.4379 | 133.5638 | 272.0098 | 431.8215 | 164.8836 | 489.6671 | 1193.5489 | 654.2363 | 654.2363 | 654.2363 | 654.2363 | 654.2363 | 654.2363 | 654.2363 | 654.2363 | 654.2363 | 654.2363 | 654.2363 | 654.2363 | 654.2363 | 654.2363 | 654.2363 | 654.2363 | [7 empty] | 73.4213 | 219.8269 | 697.566 | 2433.4635 | 1002.3928 | 722.4739 | 1100.3282 | 1926.6855 | 1367.3357 | 1367.3357 | 1367.3357 | 1367.3357 | 1367.3357 | 1367.3357 | 1367.3357 | 1367.3357 | 1367.3357 | 1367.3357 | 1367.3357 | 1367.3357 | 1367.3357 | 1367.3357 | 1367.3357 | 1367.3357
65% | FY38: 138.0019; FY39: 0.607; FY40: 0.607; FY41: 0.607; FY42: 0.607; FY43: 0.607; FY44: 0.607; FY45: 0.607; FY46: 0.607; FY47: 0.607; FY48: 0.607; FY49: 0.607; FY50: 0.607; FY51: 0.607; FY52: 0.607; FY53: 0.607; FY54: 0.607 | [9 empty] | 2.7969 | 1216.8668 | 62.358 | 4.774 | 97.5063 | 684.2805 | 231.4677 | 231.4677 | 231.4677 | 231.4677 | 231.4677 | 231.4677 | 231.4677 | 231.4677 | 231.4677 | 231.4677 | 231.4677 | 231.4677 | 231.4677 | 231.4677 | 231.4677 | 231.4677
60% | [40 empty] | 77.6441
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 306.4572 | 1278.2542 | 1538.6669 | 1760.5324 | 2183.4175 | 3339.858 | 4255.0255 | 5579.7822 | 6338.312 | 7043.6462 | 5771.5678 | 7274.3439 | 9968.1685 | 7886.0948 | 7886.0948 | 7886.0948 | 7886.0948 | 7886.0948 | 7886.0948 | 7886.0948 | 7886.0948 | 7886.0948 | 7886.0948 | 7886.0948 | 7886.0948 | 7886.0948 | 7886.0948 | 7886.0948 | 7886.0948 | E @ R (MWh) | 0 | 833.5401 | 2506.4849 | 2860.3759 | 3097.9173 | 3652.8965 | 5148.2859 | 6075.8653 | 8044.5252 | 15595.6201 | 9203.2451 | 8136.3162 | 9591.5333 | 13158.0259 | 10688.2832 | 10688.2832 | 10688.2832 | 10688.2832 | 10688.2832 | 10688.2832 | 10688.2832 | 10688.2832 | 10688.2832 | 10688.2832 | 10688.2832 | 10688.2832 | 10688.2832 | 10688.2832 | 10688.2832 | 10688.2832
Option 8 Winter POE50 W E @ R (MWh) N 1 | 0 | 214.5201 | 894.7779 | 1077.0669 | 1232.3727 | 1528.3922 | 2337.9006 | 2978.5179 | 3905.8475 | 4436.8184 | 4930.5523 | 4040.0974 | 5092.0407 | 6977.718 | 5520.2664 | 5520.2664 | 5520.2664 | 5520.2664 | 5520.2664 | 5520.2664 | 5520.2664 | 5520.2664 | 5520.2664 | 5520.2664 | 5520.2664 | 5520.2664 | 5520.2664 | 5520.2664 | 5520.2664 | 5520.2664 | Option 8 Winter POE10 W E @ R (MWh) N 1 | 0 | 250.062 | 751.9455 | 858.1128 | 929.3752 | 1095.8689 | 1544.4858 | 1822.7596 | 2413.3575 | 4678.686 | 2760.9735 | 2440.8949 | 2877.46 | 3947.4078 | 3206.485 | 3206.485 | 3206.485 | 3206.485 | 3206.485 | 3206.485 | 3206.485 | 3206.485 | 3206.485 | 3206.485 | 3206.485 | 3206.485 | 3206.485 | 3206.485 | 3206.485 | 3206.485
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 8.924 | 31.6709 | 37.6273 | 37.273 | 37.3028 | 37.916 | 39.5304 | 40.6128 | 41.6716 | 42.9095 | 44.0577 | 45.1715 | 45.3005 | 46.6002 | 45.6187 | 45.6187 | 45.6187 | 45.6187 | 45.6187 | 45.6187 | 45.6187 | 45.6187 | 45.6187 | 45.6187 | 45.6187 | 45.6187 | 45.6187 | 45.6187 | 45.6187 | 45.6187
98% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4.0751 | 15.3343 | 18.2825 | 18.1072 | 18.1219 | 18.4254 | 19.2245 | 19.7603 | 20.2843 | 20.897 | 21.4654 | 22.0167 | 22.0806 | 22.7239 | 22.238 | 22.238 | 22.238 | 22.238 | 22.238 | 22.238 | 22.238 | 22.238 | 22.238 | 22.238 | 22.238 | 22.238 | 22.238 | 22.238 | 22.238 | 22.238
97% |  | 5.4588 | 6.9736 | 6.9303 | 6.9298 | 7.103 | 7.2931 | 7.6829 | 7.9629 | 8.1151 | 8.2819 | 8.4343 | 8.7091 | 9.05 | 9.027 | 9.027 | 9.027 | 9.027 | 9.027 | 9.027 | 9.027 | 9.027 | 9.027 | 9.027 | 9.027 | 9.027 | 9.027 | 9.027 | 9.027 | 9.027 |  | 7.3764 | 29.6661 | 35.5027 | 35.1556 | 35.1847 | 35.7856 | 37.3676 | 38.4283 | 39.4657 | 40.6787 | 41.8039 | 42.8953 | 43.0218 | 44.2953 | 43.3335 | 43.3335 | 43.3335 | 43.3335 | 43.3335 | 43.3335 | 43.3335 | 43.3335 | 43.3335 | 43.3335 | 43.3335 | 43.3335 | 43.3335 | 43.3335 | 43.3335 | 43.3335
95% |  | 25.5649 | 33.0227 | 32.8093 | 32.8067 | 33.6597 | 34.5953 | 36.5142 | 37.8928 | 38.6423 | 39.4634 | 40.2137 | 41.5666 | 43.2448 | 43.1314 | 43.1314 | 43.1314 | 43.1314 | 43.1314 | 43.1314 | 43.1314 | 43.1314 | 43.1314 | 43.1314 | 43.1314 | 43.1314 | 43.1314 | 43.1314 | 43.1314 | 43.1314 |  | 9.3236 | 42.2437 | 50.864 | 50.3513 | 50.3943 | 51.2818 | 53.6182 | 55.1847 | 56.717 | 58.5085 | 60.1702 | 61.7822 | 61.969 | 63.8499 | 62.4294 | 62.4294 | 62.4294 | 62.4294 | 62.4294 | 62.4294 | 62.4294 | 62.4294 | 62.4294 | 62.4294 | 62.4294 | 62.4294 | 62.4294 | 62.4294 | 62.4294 | 62.4294
90% |  | 38.7554 | 51.6899 | 51.3198 | 51.3153 | 52.7947 | 54.4175 | 57.7455 | 60.1366 | 61.4365 | 62.8605 | 64.1618 | 66.5082 | 69.4189 | 69.2222 | 69.2222 | 69.2222 | 69.2222 | 69.2222 | 69.2222 | 69.2222 | 69.2222 | 69.2222 | 69.2222 | 69.2222 | 69.2222 | 69.2222 | 69.2222 | 69.2222 | 69.2222 |  | 23.6749 | 166.4146 | 203.7914 | 201.5685 | 201.7552 | 205.6032 | 215.7337 | 222.5261 | 229.1699 | 236.9378 | 244.1429 | 251.1324 | 251.9421 | 260.0977 | 253.9385 | 253.9385 | 253.9385 | 253.9385 | 253.9385 | 253.9385 | 253.9385 | 253.9385 | 253.9385 | 253.9385 | 253.9385 | 253.9385 | 253.9385 | 253.9385 | 253.9385 | 253.9385
85% |  | 85.1452 | 121.8514 | 120.801 | 120.7884 | 124.9866 | 129.5917 | 139.0363 | 145.8216 | 149.5106 | 153.5518 | 157.2446 | 163.9032 | 172.1633 | 171.605 | 171.605 | 171.605 | 171.605 | 171.605 | 171.605 | 171.605 | 171.605 | 171.605 | 171.605 | 171.605 | 171.605 | 171.605 | 171.605 | 171.605 | 171.605 |  | 2.1581 | 132.583 | 167.9395 | 165.8367 | 166.0133 | 169.6533 | 179.2362 | 185.6615 | 191.9461 | 199.2941 | 206.1098 | 212.7215 | 213.4874 | 221.2021 | 215.3759 | 215.3759 | 215.3759 | 215.3759 | 215.3759 | 215.3759 | 215.3759 | 215.3759 | 215.3759 | 215.3759 | 215.3759 | 215.3759 | 215.3759 | 215.3759 | 215.3759 | 215.3759
80% |  | 80.0361 | 131.3082 | 129.841 | 129.8234 | 135.6876 | 142.1201 | 155.3125 | 164.7904 | 169.9433 | 175.5881 | 180.7464 | 190.0472 | 201.5852 | 200.8054 | 200.8054 | 200.8054 | 200.8054 | 200.8054 | 200.8054 | 200.8054 | 200.8054 | 200.8054 | 200.8054 | 200.8054 | 200.8054 | 200.8054 | 200.8054 | 200.8054 | 200.8054 |  |  | 73.1492 | 97.8426 | 96.374 | 96.4973 | 99.0396 | 105.7324 | 110.2199 | 114.6092 | 119.7411 | 124.5013 | 129.1189 | 129.6539 | 135.0419 | 130.9728 | 130.9728 | 130.9728 | 130.9728 | 130.9728 | 130.9728 | 130.9728 | 130.9728 | 130.9728 | 130.9728 | 130.9728 | 130.9728 | 130.9728 | 130.9728 | 130.9728 | 130.9728
75% |  | 94.1589 | 227.8159 | 223.9912 | 223.9454 | 239.2321 | 256.0006 | 290.3908 | 315.098 | 328.5306 | 343.2457 | 356.6924 | 380.938 | 411.0152 | 408.9825 | 408.9825 | 408.9825 | 408.9825 | 408.9825 | 408.9825 | 408.9825 | 408.9825 | 408.9825 | 408.9825 | 408.9825 | 408.9825 | 408.9825 | 408.9825 | 408.9825 | 408.9825 |  |  | 91.3687 | 135.4427 | 132.8215 | 133.0415 | 137.5791 | 149.5248 | 157.5342 | 165.3684 | 174.5281 | 183.0243 | 191.2662 | 192.221 | 201.8378 | 194.575 | 194.575 | 194.575 | 194.575 | 194.575 | 194.575 | 194.575 | 194.575 | 194.575 | 194.575 | 194.575 | 194.575 | 194.575 | 194.575 | 194.575 | 194.575
70% |  | 6.5776 | 168.5277 | 161.9198 | 161.8408 | 188.2515 | 217.2224 | 276.6382 | 319.3247 | 342.5321 | 367.9553 | 391.1871 | 433.0761 | 485.0404 | 481.5284 | 481.5284 | 481.5284 | 481.5284 | 481.5284 | 481.5284 | 481.5284 | 481.5284 | 481.5284 | 481.5284 | 481.5284 | 481.5284 | 481.5284 | 481.5284 | 481.5284 | 481.5284 |  |  | 85.2049 | 165.4959 | 160.7208 | 161.1217 | 169.3879 | 191.1497 | 205.7408 | 220.0126 | 236.6991 | 252.1769 | 267.1913 | 268.9307 | 286.45 | 273.2191 | 273.2191 | 273.2191 | 273.2191 | 273.2191 | 273.2191 | 273.2191 | 273.2191 | 273.2191 | 273.2191 | 273.2191 | 273.2191 | 273.2191 | 273.2191 | 273.2191 | 273.2191
65% |  |  | 9.6236 | 6.9591 | 6.9298 | 20.0951 | 42.2143 | 111.9423 | 181.5617 | 226.0382 | 279.9918 | 333.9879 | 438.672 | 569.1816 | 560.3612 | 560.3612 | 560.3612 | 560.3612 | 560.3612 | 560.3612 | 560.3612 | 560.3612 | 560.3612 | 560.3612 | 560.3612 | 560.3612 | 560.3612 | 560.3612 | 560.3612 | 560.3612 |  |  | 10.9945 | 90.8581 | 84.8503 | 85.3547 | 95.7548 | 123.1346 | 141.4924 | 159.4485 | 180.4428 | 199.9162 | 218.8067 | 220.9952 | 243.0371 | 226.3906 | 226.3906 | 226.3906 | 226.3906 | 226.3906 | 226.3906 | 226.3906 | 226.3906 | 226.3906 | 226.3906 | 226.3906 | 226.3906 | 226.3906 | 226.3906 | 226.3906 | 226.3906
60% | [12 empty] | 5.9059 | 42.5222 | 39.014 | 39.014 | 39.014 | 39.014 | 39.014 | 39.014 | 39.014 | 39.014 | 39.014 | 39.014 | 39.014 | 39.014 | 39.014 | 39.014 | 39.014 | 39.014 |  |  |  | 3.8091 | 2.2281 | 2.3448 | 5.4041 | 19.2874 | 33.1836 | 50.2166 | 74.3153 | 100.576 | 129.3594 | 132.7839 | 167.2756 | 141.2268 | 141.2268 | 141.2268 | 141.2268 | 141.2268 | 141.2268 | 141.2268 | 141.2268 | 141.2268 | 141.2268 | 141.2268 | 141.2268 | 141.2268 | 141.2268 | 141.2268 | 141.2268
55% | [42 empty] | 0.36348 | 0.67093 | 8.8993 | 1.8255 | 1.8255 | 1.8255 | 1.8255 | 1.8255 | 1.8255 | 1.8255 | 1.8255 | 1.8255 | 1.8255 | 1.8255 | 1.8255 | 1.8255 | 1.8255 | 1.8255 | 1.8255
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 335.6968 | 750.8128 | 734.5714 | 734.3797 | 801.8103 | 883.4549 | 1075.2627 | 1232.5888 | 1324.7487 | 1430.9386 | 1532.6682 | 1729.3262 | 2003.2214 | 1983.6771 | 1983.6771 | 1983.6771 | 1983.6771 | 1983.6771 | 1983.6771 | 1983.6771 | 1983.6771 | 1983.6771 | 1983.6771 | 1983.6771 | 1983.6771 | 1983.6771 | 1983.6771 | 1983.6771 | 1983.6771 | E @ R (MWh) | 55.5322 | 678.63 | 1007.4559 | 985.2871 | 987.1322 | 1025.8309 | 1133.5396 | 1210.3445 | 1288.9099 | 1384.9521 | 1477.9447 | 1571.8256 | 1583.0571 | 1701.3108 | 1611.1437 | 1611.1437 | 1611.1437 | 1611.1437 | 1611.1437 | 1611.1437 | 1611.1437 | 1611.1437 | 1611.1437 | 1611.1437 | 1611.1437 | 1611.1437 | 1611.1437 | 1611.1437 | 1611.1437 | 1611.1437
Option 8 Summer POE50 W E @ R (MWh) N 1 | 0 | 234.9878 | 525.569 | 514.2 | 514.0658 | 561.2672 | 618.4185 | 752.6839 | 862.8122 | 927.3241 | 1001.657 | 1072.8678 | 1210.5283 | 1402.255 | 1388.5739 | 1388.5739 | 1388.5739 | 1388.5739 | 1388.5739 | 1388.5739 | 1388.5739 | 1388.5739 | 1388.5739 | 1388.5739 | 1388.5739 | 1388.5739 | 1388.5739 | 1388.5739 | 1388.5739 | 1388.5739 | Option 8 Summer POE10 W E @ R (MWh) N 1 | 16.6597 | 203.589 | 302.2368 | 295.5861 | 296.1396 | 307.7493 | 340.0619 | 363.1034 | 386.673 | 415.4856 | 443.3834 | 471.5477 | 474.9171 | 510.3932 | 483.3431 | 483.3431 | 483.3431 | 483.3431 | 483.3431 | 483.3431 | 483.3431 | 483.3431 | 483.3431 | 483.3431 | 483.3431 | 483.3431 | 483.3431 | 483.3431 | 483.3431 | 483.3431

## E@R N-2
Option 1 - Do Nothing / Base Case
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | 59.6718 | 82.8348 | 88.8563 | 89.8828 | 90.6833 | 92.0616 | 95.1975 | 97.2967 | 99.9559 | 101.3362 | 102.5505 | 100.3131 | 102.9353 | 107.0576 | 103.9293 | 103.9293 | 103.9293 | 103.9293 | 103.9293 | 103.9293 | 103.9293 | 103.9293 | 103.9293 | 103.9293 | 103.9293 | 103.9293 | 103.9293 | 103.9293 | 103.9293 | 103.9293 |  | 63.8857 | 86.7566 | 93.0131 | 93.9812 | 94.5959 | 95.9444 | 99.1293 | 100.8681 | 104.1807 | 114.2499 | 105.9488 | 104.3251 | 106.5169 | 111.3103 | 108.0657 | 108.0657 | 108.0657 | 108.0657 | 108.0657 | 108.0657 | 108.0657 | 108.0657 | 108.0657 | 108.0657 | 108.0657 | 108.0657 | 108.0657 | 108.0657 | 108.0657 | 108.0657
98% | 70.8865 | 98.4027 | 105.556 | 106.7753 | 107.7263 | 109.3637 | 113.0889 | 115.5826 | 118.7416 | 120.3813 | 121.8238 | 119.1659 | 122.2809 | 127.178 | 123.4618 | 123.4618 | 123.4618 | 123.4618 | 123.4618 | 123.4618 | 123.4618 | 123.4618 | 123.4618 | 123.4618 | 123.4618 | 123.4618 | 123.4618 | 123.4618 | 123.4618 | 123.4618 |  | 75.8924 | 103.0616 | 110.494 | 111.644 | 112.3742 | 113.9761 | 117.7596 | 119.8253 | 123.7603 | 135.7219 | 125.8608 | 123.932 | 126.5357 | 132.2299 | 128.3755 | 128.3755 | 128.3755 | 128.3755 | 128.3755 | 128.3755 | 128.3755 | 128.3755 | 128.3755 | 128.3755 | 128.3755 | 128.3755 | 128.3755 | 128.3755 | 128.3755 | 128.3755
97% | 140.3338 | 194.8074 | 208.9687 | 211.3826 | 213.2652 | 216.5068 | 223.8816 | 228.8183 | 235.0721 | 238.3182 | 241.174 | 235.9121 | 242.0789 | 251.7738 | 244.4167 | 244.4167 | 244.4167 | 244.4167 | 244.4167 | 244.4167 | 244.4167 | 244.4167 | 244.4167 | 244.4167 | 244.4167 | 244.4167 | 244.4167 | 244.4167 | 244.4167 | 244.4167 |  | 150.2438 | 204.0305 | 218.7445 | 221.0211 | 222.4667 | 225.638 | 233.1281 | 237.2175 | 245.0078 | 268.6881 | 249.1661 | 245.3476 | 250.5021 | 261.7749 | 254.1445 | 254.1445 | 254.1445 | 254.1445 | 254.1445 | 254.1445 | 254.1445 | 254.1445 | 254.1445 | 254.1445 | 254.1445 | 254.1445 | 254.1445 | 254.1445 | 254.1445 | 254.1445
95% | 414.5243 | 575.4311 | 617.2612 | 624.3915 | 629.9527 | 639.5277 | 661.3119 | 675.8939 | 694.3669 | 703.9554 | 712.391 | 696.8482 | 715.0638 | 743.7009 | 721.9694 | 721.9694 | 721.9694 | 721.9694 | 721.9694 | 721.9694 | 721.9694 | 721.9694 | 721.9694 | 721.9694 | 721.9694 | 721.9694 | 721.9694 | 721.9694 | 721.9694 | 721.9694 |  | 443.7972 | 602.6746 | 646.1375 | 652.8624 | 657.1324 | 666.4999 | 688.6245 | 700.704 | 723.7153 | 793.6633 | 735.9983 | 724.719 | 739.9446 | 773.2427 | 750.7037 | 750.7037 | 750.7037 | 750.7037 | 750.7037 | 750.7037 | 750.7037 | 750.7037 | 750.7037 | 750.7037 | 750.7037 | 750.7037 | 750.7037 | 750.7037 | 750.7037 | 750.7037
90% | 2285.5212 | 3172.6969 | 3403.3313 | 3442.6449 | 3473.3067 | 3526.0998 | 3646.209 | 3726.6085 | 3828.4608 | 3881.3281 | 3927.8385 | 3842.1418 | 3942.5756 | 4100.4692 | 3980.6499 | 3980.6499 | 3980.6499 | 3980.6499 | 3980.6499 | 3980.6499 | 3980.6499 | 3980.6499 | 3980.6499 | 3980.6499 | 3980.6499 | 3980.6499 | 3980.6499 | 3980.6499 | 3980.6499 | 3980.6499 |  | 2446.9201 | 3322.9067 | 3562.5435 | 3599.622 | 3623.165 | 3674.8134 | 3796.7998 | 3863.4014 | 3990.2765 | 4375.9415 | 4058 | 3995.8103 | 4079.7583 | 4263.3504 | 4139.0795 | 4139.0795 | 4139.0795 | 4139.0795 | 4139.0795 | 4139.0795 | 4139.0795 | 4139.0795 | 4139.0795 | 4139.0795 | 4139.0795 | 4139.0795 | 4139.0795 | 4139.0795 | 4139.0795 | 4139.0795
85% | 5583.3646 | 7750.6712 | 8314.0946 | 8410.1348 | 8485.0395 | 8614.0092 | 8907.4274 | 9103.8375 | 9352.6555 | 9481.8066 | 9595.4282 | 9386.0773 | 9631.4298 | 10017.1525 | 9724.4425 | 9724.4425 | 9724.4425 | 9724.4425 | 9724.4425 | 9724.4425 | 9724.4425 | 9724.4425 | 9724.4425 | 9724.4425 | 9724.4425 | 9724.4425 | 9724.4425 | 9724.4425 | 9724.4425 | 9724.4425 |  | 5977.6505 | 8117.623 | 8703.0385 | 8793.6186 | 8851.1326 | 8977.3059 | 9275.3098 | 9438.0128 | 9747.9596 | 10690.1116 | 9913.4032 | 9761.4782 | 9966.5573 | 10415.0597 | 10111.4747 | 10111.4747 | 10111.4747 | 10111.4747 | 10111.4747 | 10111.4747 | 10111.4747 | 10111.4747 | 10111.4747 | 10111.4747 | 10111.4747 | 10111.4747 | 10111.4747 | 10111.4747 | 10111.4747 | 10111.4747
80% | 8678.2039 | 12046.8408 | 12922.5678 | 13071.8427 | 13188.2668 | 13388.724 | 13844.7828 | 14150.0624 | 14536.7992 | 14737.5384 | 14914.14 | 14588.7467 | 14970.0973 | 15569.6246 | 15114.6665 | 15114.6665 | 15114.6665 | 15114.6665 | 15114.6665 | 15114.6665 | 15114.6665 | 15114.6665 | 15114.6665 | 15114.6665 | 15114.6665 | 15114.6665 | 15114.6665 | 15114.6665 | 15114.6665 | 15114.6665 |  | 9291.041 | 12617.1926 | 13527.1019 | 13667.8902 | 13757.2841 | 13953.3947 | 14416.5812 | 14669.4699 | 15151.219 | 16615.6026 | 15408.3675 | 15172.231 | 15490.9847 | 16188.0904 | 15716.2292 | 15716.2292 | 15716.2292 | 15716.2292 | 15716.2292 | 15716.2292 | 15716.2292 | 15716.2292 | 15716.2292 | 15716.2292 | 15716.2292 | 15716.2292 | 15716.2292 | 15716.2292 | 15716.2292 | 15716.2292
75% | 9574.4808 | 13291.0275 | 14257.1987 | 14421.8907 | 14550.339 | 14771.4991 | 15274.6593 | 15611.4679 | 16038.1465 | 16259.6179 | 16454.4587 | 16095.4591 | 16516.1952 | 17177.6412 | 16675.6955 | 16675.6955 | 16675.6955 | 16675.6955 | 16675.6955 | 16675.6955 | 16675.6955 | 16675.6955 | 16675.6955 | 16675.6955 | 16675.6955 | 16675.6955 | 16675.6955 | 16675.6955 | 16675.6955 | 16675.6955 |  | 10250.6112 | 13920.2847 | 14924.1686 | 15079.4974 | 15178.1238 | 15394.4886 | 15905.5125 | 16184.5193 | 16716.023 | 18331.6468 | 16999.7296 | 16739.2052 | 17090.8794 | 17859.9816 | 17339.387 | 17339.387 | 17339.387 | 17339.387 | 17339.387 | 17339.387 | 17339.387 | 17339.387 | 17339.387 | 17339.387 | 17339.387 | 17339.387 | 17339.387 | 17339.387 | 17339.387 | 17339.387
70% | 10287.2444 | 14280.4661 | 15318.563 | 15495.5153 | 15633.5258 | 15871.15 | 16411.7675 | 16773.6495 | 17232.0919 | 17470.0505 | 17679.396 | 17293.671 | 17745.7284 | 18456.4151 | 17917.1025 | 17917.1025 | 17917.1025 | 17917.1025 | 17917.1025 | 17917.1025 | 17917.1025 | 17917.1025 | 17917.1025 | 17917.1025 | 17917.1025 | 17917.1025 | 17917.1025 | 17917.1025 | 17917.1025 | 17917.1025 |  | 11013.7087 | 14956.5677 | 16035.1849 | 16202.077 | 16308.0455 | 16540.5174 | 17089.584 | 17389.3613 | 17960.4323 | 19696.3297 | 18265.2591 | 17985.3402 | 18363.1944 | 19189.5518 | 18630.202 | 18630.202 | 18630.202 | 18630.202 | 18630.202 | 18630.202 | 18630.202 | 18630.202 | 18630.202 | 18630.202 | 18630.202 | 18630.202 | 18630.202 | 18630.202 | 18630.202 | 18630.202
65% | 10840.7831 | 15048.8731 | 16142.8282 | 16329.302 | 16474.7386 | 16725.149 | 17294.8562 | 17676.2104 | 18159.3208 | 18410.0835 | 18630.6936 | 18224.2134 | 18700.5952 | 19449.5227 | 18881.1907 | 18881.1907 | 18881.1907 | 18881.1907 | 18881.1907 | 18881.1907 | 18881.1907 | 18881.1907 | 18881.1907 | 18881.1907 | 18881.1907 | 18881.1907 | 18881.1907 | 18881.1907 | 18881.1907 | 18881.1907 |  | 11606.3372 | 15761.3546 | 16898.0103 | 17073.8826 | 17185.553 | 17430.5339 | 18009.1448 | 18325.0525 | 18926.8519 | 20756.155 | 19248.0809 | 18953.1 | 19351.286 | 20222.1082 | 19632.6608 | 19632.6608 | 19632.6608 | 19632.6608 | 19632.6608 | 19632.6608 | 19632.6608 | 19632.6608 | 19632.6608 | 19632.6608 | 19632.6608 | 19632.6608 | 19632.6608 | 19632.6608 | 19632.6608 | 19632.6608
60% | 11934.3669 | 16566.9557 | 17771.2656 | 17976.5503 | 18136.658 | 18412.329 | 19039.5064 | 19459.3305 | 19991.1755 | 20267.2344 | 20510.0989 | 20062.6142 | 20587.052 | 21411.5289 | 20785.8653 | 20785.8653 | 20785.8653 | 20785.8653 | 20785.8653 | 20785.8653 | 20785.8653 | 20785.8653 | 20785.8653 | 20785.8653 | 20785.8653 | 20785.8653 | 20785.8653 | 20785.8653 | 20785.8653 | 20785.8653 |  | 12777.1477 | 17351.3101 | 18602.628 | 18796.2417 | 18919.1771 | 19188.8708 | 19825.8502 | 20173.6257 | 20836.1327 | 22849.9701 | 21189.7663 | 20865.0287 | 21303.3824 | 22262.0503 | 21613.1413 | 21613.1413 | 21613.1413 | 21613.1413 | 21613.1413 | 21613.1413 | 21613.1413 | 21613.1413 | 21613.1413 | 21613.1413 | 21613.1413 | 21613.1413 | 21613.1413 | 21613.1413 | 21613.1413 | 21613.1413
55% | 13276.2336 | 18429.6976 | 19769.4166 | 19997.783 | 20175.8928 | 20482.5595 | 21180.255 | 21647.2828 | 22238.927 | 22546.0252 | 22816.1967 | 22318.3981 | 22901.8021 | 23818.981 | 23122.9695 | 23122.9695 | 23122.9695 | 23122.9695 | 23122.9695 | 23122.9695 | 23122.9695 | 23122.9695 | 23122.9695 | 23122.9695 | 23122.9695 | 23122.9695 | 23122.9695 | 23122.9695 | 23122.9695 | 23122.9695 |  | 14213.7742 | 19302.2426 | 20694.2551 | 20909.6382 | 21046.3962 | 21346.4135 | 22055.013 | 22441.8914 | 23178.8888 | 25419.1564 | 23572.284 | 23211.0338 | 23698.6747 | 24765.1326 | 24043.2621 | 24043.2621 | 24043.2621 | 24043.2621 | 24043.2621 | 24043.2621 | 24043.2621 | 24043.2621 | 24043.2621 | 24043.2621 | 24043.2621 | 24043.2621 | 24043.2621 | 24043.2621 | 24043.2621 | 24043.2621
50% | 13456.7484 | 18680.2832 | 20038.2182 | 20269.6896 | 20450.2212 | 20761.0575 | 21468.2395 | 21941.6174 | 22541.3061 | 22852.5798 | 23126.4248 | 22621.8577 | 23213.1942 | 24142.8438 | 23437.3688 | 23437.3688 | 23437.3688 | 23437.3688 | 23437.3688 | 23437.3688 | 23437.3688 | 23437.3688 | 23437.3688 | 23437.3688 | 23437.3688 | 23437.3688 | 23437.3688 | 23437.3688 | 23437.3688 | 23437.3688 |  | 14407.0366 | 19564.692 | 20975.6315 | 21193.9432 | 21332.5606 | 21636.6572 | 22354.8915 | 22747.0302 | 23494.0484 | 25764.7766 | 23892.7925 | 23526.6304 | 24020.9018 | 25101.8601 | 24370.1745 | 24370.1745 | 24370.1745 | 24370.1745 | 24370.1745 | 24370.1745 | 24370.1745 | 24370.1745 | 24370.1745 | 24370.1745 | 24370.1745 | 24370.1745 | 24370.1745 | 24370.1745 | 24370.1745 | 24370.1745
45% | 10386.1977 | 14417.8303 | 15465.9127 | 15644.5671 | 15783.9051 | 16023.8151 | 16569.6328 | 16934.9957 | 17397.8478 | 17638.0954 | 17849.4547 | 17460.0193 | 17916.4251 | 18633.9479 | 18089.4477 | 18089.4477 | 18089.4477 | 18089.4477 | 18089.4477 | 18089.4477 | 18089.4477 | 18089.4477 | 18089.4477 | 18089.4477 | 18089.4477 | 18089.4477 | 18089.4477 | 18089.4477 | 18089.4477 | 18089.4477 |  | 11119.6499 | 15100.4354 | 16189.4278 | 16357.9252 | 16464.913 | 16699.6211 | 17253.9692 | 17556.63 | 18133.1942 | 19885.7893 | 18440.9531 | 18158.3417 | 18539.8305 | 19374.1366 | 18809.4064 | 18809.4064 | 18809.4064 | 18809.4064 | 18809.4064 | 18809.4064 | 18809.4064 | 18809.4064 | 18809.4064 | 18809.4064 | 18809.4064 | 18809.4064 | 18809.4064 | 18809.4064 | 18809.4064 | 18809.4064
40% | 5102.6915 | 7083.4142 | 7598.3323 | 7686.1044 | 7754.5606 | 7872.4272 | 8140.5849 | 8320.0861 | 8547.4832 | 8665.5158 | 8769.3556 | 8578.0278 | 8802.2579 | 9154.7736 | 8887.2631 | 8887.2631 | 8887.2631 | 8887.2631 | 8887.2631 | 8887.2631 | 8887.2631 | 8887.2631 | 8887.2631 | 8887.2631 | 8887.2631 | 8887.2631 | 8887.2631 | 8887.2631 | 8887.2631 | 8887.2631 |  | 5463.0332 | 7418.775 | 7953.792 | 8036.574 | 8089.1366 | 8204.4476 | 8476.7963 | 8625.4922 | 8908.7555 | 9769.7975 | 9059.9561 | 8921.1104 | 9108.5341 | 9518.4249 | 9240.9755 | 9240.9755 | 9240.9755 | 9240.9755 | 9240.9755 | 9240.9755 | 9240.9755 | 9240.9755 | 9240.9755 | 9240.9755 | 9240.9755 | 9240.9755 | 9240.9755 | 9240.9755 | 9240.9755 | 9240.9755
35% | 1907.0998 | 2647.3829 | 2839.8304 | 2872.6347 | 2898.2197 | 2942.2717 | 3042.494 | 3109.5815 | 3194.5697 | 3238.6837 | 3277.4932 | 3205.9856 | 3289.7902 | 3421.5408 | 3321.5604 | 3321.5604 | 3321.5604 | 3321.5604 | 3321.5604 | 3321.5604 | 3321.5604 | 3321.5604 | 3321.5604 | 3321.5604 | 3321.5604 | 3321.5604 | 3321.5604 | 3321.5604 | 3321.5604 | 3321.5604 |  | 2041.7754 | 2772.7219 | 2972.6813 | 3003.6205 | 3023.2655 | 3066.3623 | 3168.1509 | 3223.7251 | 3329.5931 | 3651.4023 | 3386.1034 | 3334.2106 | 3404.2591 | 3557.4533 | 3453.7583 | 3453.7583 | 3453.7583 | 3453.7583 | 3453.7583 | 3453.7583 | 3453.7583 | 3453.7583 | 3453.7583 | 3453.7583 | 3453.7583 | 3453.7583 | 3453.7583 | 3453.7583 | 3453.7583 | 3453.7583
30% | 951.1511 | 1320.3614 | 1416.3431 | 1432.704 | 1445.4643 | 1467.4349 | 1517.42 | 1550.8793 | 1593.2665 | 1615.268 | 1634.624 | 1598.9601 | 1640.757 | 1706.4666 | 1656.6021 | 1656.6021 | 1656.6021 | 1656.6021 | 1656.6021 | 1656.6021 | 1656.6021 | 1656.6021 | 1656.6021 | 1656.6021 | 1656.6021 | 1656.6021 | 1656.6021 | 1656.6021 | 1656.6021 | 1656.6021 |  | 1018.3194 | 1382.8733 | 1482.6014 | 1498.0321 | 1507.8299 | 1529.3241 | 1580.0904 | 1607.8076 | 1660.6084 | 1821.1082 | 1688.7924 | 1662.9113 | 1697.8475 | 1774.2519 | 1722.5348 | 1722.5348 | 1722.5348 | 1722.5348 | 1722.5348 | 1722.5348 | 1722.5348 | 1722.5348 | 1722.5348 | 1722.5348 | 1722.5348 | 1722.5348 | 1722.5348 | 1722.5348 | 1722.5348 | 1722.5348
25% | 560.7353 | 778.3972 | 834.9816 | 844.6269 | 852.1495 | 865.1019 | 894.5698 | 914.2952 | 939.2839 | 952.2545 | 963.6655 | 942.6404 | 967.2811 | 1006.0191 | 976.6223 | 976.6223 | 976.6223 | 976.6223 | 976.6223 | 976.6223 | 976.6223 | 976.6223 | 976.6223 | 976.6223 | 976.6223 | 976.6223 | 976.6223 | 976.6223 | 976.6223 | 976.6223 |  | 600.3333 | 815.25 | 874.0431 | 883.14 | 888.9161 | 901.5876 | 931.5161 | 947.8563 | 978.9841 | 1073.6041 | 995.5996 | 980.3418 | 1000.9378 | 1045.9808 | 1015.4918 | 1015.4918 | 1015.4918 | 1015.4918 | 1015.4918 | 1015.4918 | 1015.4918 | 1015.4918 | 1015.4918 | 1015.4918 | 1015.4918 | 1015.4918 | 1015.4918 | 1015.4918 | 1015.4918 | 1015.4918
20% | 283.3663 | 393.3611 | 421.9559 | 426.8302 | 430.6317 | 437.1772 | 452.0687 | 462.0369 | 474.6648 | 481.2195 | 486.986 | 476.3611 | 488.8132 | 508.3893 | 493.5337 | 493.5337 | 493.5337 | 493.5337 | 493.5337 | 493.5337 | 493.5337 | 493.5337 | 493.5337 | 493.5337 | 493.5337 | 493.5337 | 493.5337 | 493.5337 | 493.5337 | 493.5337 |  | 303.377 | 411.9846 | 441.6956 | 446.2927 | 449.2116 | 455.6151 | 470.7394 | 478.9969 | 494.7273 | 542.5433 | 503.1238 | 495.4134 | 505.8215 | 528.5839 | 513.1763 | 513.1763 | 513.1763 | 513.1763 | 513.1763 | 513.1763 | 513.1763 | 513.1763 | 513.1763 | 513.1763 | 513.1763 | 513.1763 | 513.1763 | 513.1763 | 513.1763 | 513.1763
15% | 115.4455 | 160.2582 | 171.908 | 173.8938 | 175.4425 | 178.1092 | 184.1761 | 188.2372 | 193.382 | 196.0524 | 198.4017 | 194.073 | 199.1461 | 207.1216 | 201.0693 | 201.0693 | 201.0693 | 201.0693 | 201.0693 | 201.0693 | 201.0693 | 201.0693 | 201.0693 | 201.0693 | 201.0693 | 201.0693 | 201.0693 | 201.0693 | 201.0693 | 201.0693 |  | 123.598 | 167.8456 | 179.95 | 181.8229 | 183.0121 | 185.621 | 191.7827 | 195.1469 | 201.5556 | 221.0361 | 204.9764 | 201.8351 | 206.0754 | 215.349 | 209.0718 | 209.0718 | 209.0718 | 209.0718 | 209.0718 | 209.0718 | 209.0718 | 209.0718 | 209.0718 | 209.0718 | 209.0718 | 209.0718 | 209.0718 | 209.0718 | 209.0718 | 209.0718
10% | 46.4781 | 64.5196 | 69.2097 | 70.0092 | 70.6327 | 71.7063 | 74.1488 | 75.7838 | 77.8551 | 78.9302 | 79.876 | 78.1333 | 80.1757 | 83.3866 | 80.95 | 80.95 | 80.95 | 80.95 | 80.95 | 80.95 | 80.95 | 80.95 | 80.95 | 80.95 | 80.95 | 80.95 | 80.95 | 80.95 | 80.95 | 80.95 |  | 49.7602 | 67.5742 | 72.4474 | 73.2014 | 73.6802 | 74.7305 | 77.2112 | 78.5656 | 81.1457 | 88.9886 | 82.523 | 81.2583 | 82.9654 | 86.6989 | 84.1718 | 84.1718 | 84.1718 | 84.1718 | 84.1718 | 84.1718 | 84.1718 | 84.1718 | 84.1718 | 84.1718 | 84.1718 | 84.1718 | 84.1718 | 84.1718 | 84.1718 | 84.1718
5% | 39.5813 | 54.9457 | 58.9399 | 59.6207 | 60.1517 | 61.066 | 63.1461 | 64.5385 | 66.3024 | 67.218 | 68.0234 | 66.5393 | 68.2787 | 71.0131 | 68.938 | 68.938 | 68.938 | 68.938 | 68.938 | 68.938 | 68.938 | 68.938 | 68.938 | 68.938 | 68.938 | 68.938 | 68.938 | 68.938 | 68.938 | 68.938 |  | 42.3765 | 57.5471 | 61.6972 | 62.3393 | 62.747 | 63.6415 | 65.7541 | 66.9075 | 69.1048 | 75.7838 | 70.2776 | 69.2006 | 70.6544 | 73.8339 | 71.6818 | 71.6818 | 71.6818 | 71.6818 | 71.6818 | 71.6818 | 71.6818 | 71.6818 | 71.6818 | 71.6818 | 71.6818 | 71.6818 | 71.6818 | 71.6818 | 71.6818 | 71.6818
9.992e-14% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E @ R (MWh) | 105995.1099 | 147139.4588 | 157835.5397 | 159658.7762 | 161080.774 | 163529.1464 | 169099.4242 | 172828.0925 | 177551.675 | 180003.4929 | 182160.4948 | 178186.1586 | 182843.9537 | 190166.5478 | 184609.7151 | 184609.7151 | 184609.7151 | 184609.7151 | 184609.7151 | 184609.7151 | 184609.7151 | 184609.7151 | 184609.7151 | 184609.7151 | 184609.7151 | 184609.7151 | 184609.7151 | 184609.7151 | 184609.7151 | 184609.7151 | E @ R (MWh) | 113480.2695 | 154105.704 | 165219.287 | 166938.8679 | 168030.7193 | 170426.0046 | 176083.3386 | 179172.1077 | 185056.165 | 202942.0666 | 188196.9625 | 185312.8045 | 189206.044 | 197720.4561 | 191957.169 | 191957.169 | 191957.169 | 191957.169 | 191957.169 | 191957.169 | 191957.169 | 191957.169 | 191957.169 | 191957.169 | 191957.169 | 191957.169 | 191957.169 | 191957.169 | 191957.169 | 191957.169
Option 1 Winter POE50 W E @ R (MWh) N 2 | 74196.5769 | 102997.6211 | 110484.8778 | 111761.1434 | 112756.5418 | 114470.4025 | 118369.597 | 120979.6647 | 124286.1725 | 126002.4451 | 127512.3464 | 124730.311 | 127990.7676 | 133116.5835 | 129226.8005 | 129226.8005 | 129226.8005 | 129226.8005 | 129226.8005 | 129226.8005 | 129226.8005 | 129226.8005 | 129226.8005 | 129226.8005 | 129226.8005 | 129226.8005 | 129226.8005 | 129226.8005 | 129226.8005 | 129226.8005 | Option 1 Winter POE10 W E @ R (MWh) N 2 | 34044.0809 | 46231.7112 | 49565.7861 | 50081.6604 | 50409.2158 | 51127.8014 | 52825.0016 | 53751.6323 | 55516.8495 | 60882.62 | 56459.0887 | 55593.8414 | 56761.8132 | 59316.1368 | 57587.1507 | 57587.1507 | 57587.1507 | 57587.1507 | 57587.1507 | 57587.1507 | 57587.1507 | 57587.1507 | 57587.1507 | 57587.1507 | 57587.1507 | 57587.1507 | 57587.1507 | 57587.1507 | 57587.1507 | 57587.1507
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 76.9936 | 99.7405 | 105.6969 | 105.3426 | 105.3724 | 105.9856 | 107.6 | 108.6824 | 109.7411 | 110.979 | 112.1272 | 113.2411 | 113.3701 | 114.6698 | 113.6883 | 113.6883 | 113.6883 | 113.6883 | 113.6883 | 113.6883 | 113.6883 | 113.6883 | 113.6883 | 113.6883 | 113.6883 | 113.6883 | 113.6883 | 113.6883 | 113.6883 | 113.6883
98% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 38.1099 | 49.369 | 52.3173 | 52.1419 | 52.1567 | 52.4602 | 53.2593 | 53.7951 | 54.3191 | 54.9318 | 55.5002 | 56.0515 | 56.1154 | 56.7587 | 56.2728 | 56.2728 | 56.2728 | 56.2728 | 56.2728 | 56.2728 | 56.2728 | 56.2728 | 56.2728 | 56.2728 | 56.2728 | 56.2728 | 56.2728 | 56.2728 | 56.2728 | 56.2728
97% | 16.9149 | 22.4762 | 23.991 | 23.9477 | 23.9472 | 24.1204 | 24.3105 | 24.7002 | 24.9803 | 25.1325 | 25.2993 | 25.4517 | 25.7265 | 26.0674 | 26.0444 | 26.0444 | 26.0444 | 26.0444 | 26.0444 | 26.0444 | 26.0444 | 26.0444 | 26.0444 | 26.0444 | 26.0444 | 26.0444 | 26.0444 | 26.0444 | 26.0444 | 26.0444 |  | 75.446 | 97.7357 | 103.5723 | 103.2252 | 103.2543 | 103.8552 | 105.4372 | 106.4978 | 107.5353 | 108.7483 | 109.8734 | 110.9649 | 111.0913 | 112.3649 | 111.4031 | 111.4031 | 111.4031 | 111.4031 | 111.4031 | 111.4031 | 111.4031 | 111.4031 | 111.4031 | 111.4031 | 111.4031 | 111.4031 | 111.4031 | 111.4031 | 111.4031 | 111.4031
95% | 83.2734 | 110.6519 | 118.1097 | 117.8962 | 117.8937 | 118.7467 | 119.6823 | 121.6012 | 122.9798 | 123.7293 | 124.5504 | 125.3007 | 126.6535 | 128.3318 | 128.2183 | 128.2183 | 128.2183 | 128.2183 | 128.2183 | 128.2183 | 128.2183 | 128.2183 | 128.2183 | 128.2183 | 128.2183 | 128.2183 | 128.2183 | 128.2183 | 128.2183 | 128.2183 |  | 111.4279 | 144.3481 | 152.9683 | 152.4556 | 152.4987 | 153.3862 | 155.7226 | 157.2891 | 158.8214 | 160.6129 | 162.2746 | 163.8866 | 164.0733 | 165.9543 | 164.5337 | 164.5337 | 164.5337 | 164.5337 | 164.5337 | 164.5337 | 164.5337 | 164.5337 | 164.5337 | 164.5337 | 164.5337 | 164.5337 | 164.5337 | 164.5337 | 164.5337 | 164.5337
90% | 144.4273 | 191.9119 | 204.8464 | 204.4763 | 204.4719 | 205.9512 | 207.574 | 210.9021 | 213.2931 | 214.593 | 216.0171 | 217.3184 | 219.6647 | 222.5754 | 222.3787 | 222.3787 | 222.3787 | 222.3787 | 222.3787 | 222.3787 | 222.3787 | 222.3787 | 222.3787 | 222.3787 | 222.3787 | 222.3787 | 222.3787 | 222.3787 | 222.3787 | 222.3787 |  | 483.1446 | 625.8842 | 663.261 | 661.0381 | 661.2248 | 665.0728 | 675.2033 | 681.9957 | 688.6395 | 696.4074 | 703.6125 | 710.602 | 711.4117 | 719.5673 | 713.4081 | 713.4081 | 713.4081 | 713.4081 | 713.4081 | 713.4081 | 713.4081 | 713.4081 | 713.4081 | 713.4081 | 713.4081 | 713.4081 | 713.4081 | 713.4081 | 713.4081 | 713.4081
85% | 409.8612 | 544.6148 | 581.321 | 580.2706 | 580.258 | 584.4562 | 589.0613 | 598.5059 | 605.2912 | 608.9802 | 613.0214 | 616.7142 | 623.3728 | 631.6329 | 631.0746 | 631.0746 | 631.0746 | 631.0746 | 631.0746 | 631.0746 | 631.0746 | 631.0746 | 631.0746 | 631.0746 | 631.0746 | 631.0746 | 631.0746 | 631.0746 | 631.0746 | 631.0746 |  | 457.0286 | 592.0526 | 627.4091 | 625.3063 | 625.4829 | 629.1229 | 638.7059 | 645.1311 | 651.4157 | 658.7637 | 665.5794 | 672.1911 | 672.9571 | 680.6717 | 674.8455 | 674.8455 | 674.8455 | 674.8455 | 674.8455 | 674.8455 | 674.8455 | 674.8455 | 674.8455 | 674.8455 | 674.8455 | 674.8455 | 674.8455 | 674.8455 | 674.8455 | 674.8455
80% | 572.5046 | 760.7318 | 812.0039 | 810.5367 | 810.5191 | 816.3833 | 822.8158 | 836.0082 | 845.4861 | 850.639 | 856.2839 | 861.4421 | 870.743 | 882.2809 | 881.5011 | 881.5011 | 881.5011 | 881.5011 | 881.5011 | 881.5011 | 881.5011 | 881.5011 | 881.5011 | 881.5011 | 881.5011 | 881.5011 | 881.5011 | 881.5011 | 881.5011 | 881.5011 |  | 319.1946 | 413.4971 | 438.1905 | 436.7219 | 436.8452 | 439.3874 | 446.0803 | 450.5677 | 454.957 | 460.089 | 464.8491 | 469.4668 | 470.0018 | 475.3898 | 471.3206 | 471.3206 | 471.3206 | 471.3206 | 471.3206 | 471.3206 | 471.3206 | 471.3206 | 471.3206 | 471.3206 | 471.3206 | 471.3206 | 471.3206 | 471.3206 | 471.3206 | 471.3206
75% | 1492.4153 | 1983.0895 | 2116.7465 | 2112.9218 | 2112.876 | 2128.1627 | 2144.9312 | 2179.3214 | 2204.0286 | 2217.4612 | 2232.1763 | 2245.623 | 2269.8686 | 2299.9458 | 2297.9131 | 2297.9131 | 2297.9131 | 2297.9131 | 2297.9131 | 2297.9131 | 2297.9131 | 2297.9131 | 2297.9131 | 2297.9131 | 2297.9131 | 2297.9131 | 2297.9131 | 2297.9131 | 2297.9131 | 2297.9131 |  | 569.714 | 738.0296 | 782.1036 | 779.4824 | 779.7025 | 784.24 | 796.1857 | 804.1951 | 812.0293 | 821.1891 | 829.6853 | 837.9271 | 838.8819 | 848.4987 | 841.2359 | 841.2359 | 841.2359 | 841.2359 | 841.2359 | 841.2359 | 841.2359 | 841.2359 | 841.2359 | 841.2359 | 841.2359 | 841.2359 | 841.2359 | 841.2359 | 841.2359 | 841.2359
70% | 2578.4391 | 3426.1747 | 3657.0932 | 3650.4854 | 3650.4063 | 3676.8171 | 3705.7879 | 3765.2037 | 3807.8902 | 3831.0976 | 3856.5209 | 3879.7526 | 3921.6416 | 3973.6059 | 3970.094 | 3970.094 | 3970.094 | 3970.094 | 3970.094 | 3970.094 | 3970.094 | 3970.094 | 3970.094 | 3970.094 | 3970.094 | 3970.094 | 3970.094 | 3970.094 | 3970.094 | 3970.094 |  | 1037.8661 | 1344.492 | 1424.783 | 1420.0079 | 1420.4087 | 1428.6749 | 1450.4368 | 1465.0278 | 1479.2996 | 1495.9862 | 1511.464 | 1526.4784 | 1528.2178 | 1545.7371 | 1532.5062 | 1532.5062 | 1532.5062 | 1532.5062 | 1532.5062 | 1532.5062 | 1532.5062 | 1532.5062 | 1532.5062 | 1532.5062 | 1532.5062 | 1532.5062 | 1532.5062 | 1532.5062 | 1532.5062 | 1532.5062
65% | 6475.8072 | 8604.914 | 9184.8711 | 9168.2753 | 9168.0768 | 9234.408 | 9307.1689 | 9456.393 | 9563.6012 | 9621.887 | 9685.7381 | 9744.0851 | 9849.2903 | 9979.7998 | 9970.9794 | 9970.9794 | 9970.9794 | 9970.9794 | 9970.9794 | 9970.9794 | 9970.9794 | 9970.9794 | 9970.9794 | 9970.9794 | 9970.9794 | 9970.9794 | 9970.9794 | 9970.9794 | 9970.9794 | 9970.9794 |  | 1305.7961 | 1691.5789 | 1792.5974 | 1786.5896 | 1787.0939 | 1797.4941 | 1824.8739 | 1843.2317 | 1861.1878 | 1882.1821 | 1901.6555 | 1920.546 | 1922.7344 | 1944.7764 | 1928.1299 | 1928.1299 | 1928.1299 | 1928.1299 | 1928.1299 | 1928.1299 | 1928.1299 | 1928.1299 | 1928.1299 | 1928.1299 | 1928.1299 | 1928.1299 | 1928.1299 | 1928.1299 | 1928.1299 | 1928.1299
60% | 9465.8424 | 12578.0087 | 13425.7459 | 13401.4874 | 13401.1972 | 13498.1551 | 13604.5115 | 13822.636 | 13979.3447 | 14064.5425 | 14157.8751 | 14243.1624 | 14396.9433 | 14587.7122 | 14574.8193 | 14574.8193 | 14574.8193 | 14574.8193 | 14574.8193 | 14574.8193 | 14574.8193 | 14574.8193 | 14574.8193 | 14574.8193 | 14574.8193 | 14574.8193 | 14574.8193 | 14574.8193 | 14574.8193 | 14574.8193 |  | 2043.3291 | 2647.0078 | 2805.083 | 2795.6818 | 2796.4711 | 2812.7454 | 2855.5897 | 2884.3162 | 2912.4142 | 2945.2664 | 2975.7387 | 3005.2988 | 3008.7233 | 3043.2149 | 3017.1662 | 3017.1662 | 3017.1662 | 3017.1662 | 3017.1662 | 3017.1662 | 3017.1662 | 3017.1662 | 3017.1662 | 3017.1662 | 3017.1662 | 3017.1662 | 3017.1662 | 3017.1662 | 3017.1662 | 3017.1662
55% | 10703.6666 | 14222.8031 | 15181.3967 | 15153.966 | 15153.6378 | 15263.2747 | 15383.539 | 15630.1871 | 15807.3882 | 15903.7271 | 16009.2646 | 16105.7046 | 16279.5951 | 16495.3104 | 16480.7315 | 16480.7315 | 16480.7315 | 16480.7315 | 16480.7315 | 16480.7315 | 16480.7315 | 16480.7315 | 16480.7315 | 16480.7315 | 16480.7315 | 16480.7315 | 16480.7315 | 16480.7315 | 16480.7315 | 16480.7315 |  | 3926.5772 | 5086.6405 | 5390.4069 | 5372.341 | 5373.8577 | 5405.1313 | 5487.4633 | 5542.6658 | 5596.6606 | 5659.7913 | 5718.3486 | 5775.1529 | 5781.7337 | 5848.0147 | 5797.958 | 5797.958 | 5797.958 | 5797.958 | 5797.958 | 5797.958 | 5797.958 | 5797.958 | 5797.958 | 5797.958 | 5797.958 | 5797.958 | 5797.958 | 5797.958 | 5797.958 | 5797.958
50% | 13744.0128 | 18262.75 | 19493.6294 | 19458.4071 | 19457.9857 | 19598.7646 | 19753.1897 | 20069.8975 | 20297.432 | 20421.1357 | 20556.6509 | 20680.4844 | 20903.7679 | 21180.7565 | 21162.0366 | 21162.0366 | 21162.0366 | 21162.0366 | 21162.0366 | 21162.0366 | 21162.0366 | 21162.0366 | 21162.0366 | 21162.0366 | 21162.0366 | 21162.0366 | 21162.0366 | 21162.0366 | 21162.0366 | 21162.0366 |  | 8714.0125 | 11288.47 | 11962.6002 | 11922.5077 | 11925.8735 | 11995.2773 | 12177.9916 | 12300.4992 | 12420.3265 | 12560.4285 | 12690.3811 | 12816.4434 | 12831.0478 | 12978.1412 | 12867.0534 | 12867.0534 | 12867.0534 | 12867.0534 | 12867.0534 | 12867.0534 | 12867.0534 | 12867.0534 | 12867.0534 | 12867.0534 | 12867.0534 | 12867.0534 | 12867.0534 | 12867.0534 | 12867.0534 | 12867.0534
45% | 18302.3635 | 24319.7888 | 25958.9027 | 25911.9985 | 25911.4373 | 26098.9072 | 26304.5489 | 26726.2963 | 27029.2951 | 27194.0265 | 27374.4867 | 27539.391 | 27836.7289 | 28205.5838 | 28180.6551 | 28180.6551 | 28180.6551 | 28180.6551 | 28180.6551 | 28180.6551 | 28180.6551 | 28180.6551 | 28180.6551 | 28180.6551 | 28180.6551 | 28180.6551 | 28180.6551 | 28180.6551 | 28180.6551 | 28180.6551 |  | 13204.5002 | 17105.6219 | 18127.1435 | 18066.3908 | 18071.491 | 18176.6598 | 18453.5301 | 18639.1681 | 18820.7445 | 19033.0436 | 19229.9631 | 19420.9876 | 19443.1179 | 19666.0112 | 19497.6778 | 19497.6778 | 19497.6778 | 19497.6778 | 19497.6778 | 19497.6778 | 19497.6778 | 19497.6778 | 19497.6778 | 19497.6778 | 19497.6778 | 19497.6778 | 19497.6778 | 19497.6778 | 19497.6778 | 19497.6778
40% | 12836.6798 | 17057.1053 | 18206.7263 | 18173.8293 | 18173.4357 | 18304.9209 | 18449.1513 | 18744.9511 | 18957.4646 | 19073.0018 | 19199.5707 | 19315.2292 | 19523.7723 | 19782.475 | 19764.9909 | 19764.9909 | 19764.9909 | 19764.9909 | 19764.9909 | 19764.9909 | 19764.9909 | 19764.9909 | 19764.9909 | 19764.9909 | 19764.9909 | 19764.9909 | 19764.9909 | 19764.9909 | 19764.9909 | 19764.9909 |  | 13672.6523 | 17712.0843 | 18769.8229 | 18706.9162 | 18712.1973 | 18821.0947 | 19107.7811 | 19300.0008 | 19488.0148 | 19707.8407 | 19911.7418 | 20109.5389 | 20132.4538 | 20363.2496 | 20188.9481 | 20188.9481 | 20188.9481 | 20188.9481 | 20188.9481 | 20188.9481 | 20188.9481 | 20188.9481 | 20188.9481 | 20188.9481 | 20188.9481 | 20188.9481 | 20188.9481 | 20188.9481 | 20188.9481 | 20188.9481
35% | 6655.3655 | 8843.5072 | 9439.545 | 9422.4891 | 9422.285 | 9490.4555 | 9565.2339 | 9718.5956 | 9828.7764 | 9888.6783 | 9954.2998 | 10014.2647 | 10122.3869 | 10256.5152 | 10247.4502 | 10247.4502 | 10247.4502 | 10247.4502 | 10247.4502 | 10247.4502 | 10247.4502 | 10247.4502 | 10247.4502 | 10247.4502 | 10247.4502 | 10247.4502 | 10247.4502 | 10247.4502 | 10247.4502 | 10247.4502 |  | 18622.1031 | 24123.7949 | 25564.4311 | 25478.7524 | 25485.9452 | 25634.2631 | 26024.729 | 26286.5314 | 26542.6059 | 26842.008 | 27119.7205 | 27389.1195 | 27420.3294 | 27734.6724 | 27497.2745 | 27497.2745 | 27497.2745 | 27497.2745 | 27497.2745 | 27497.2745 | 27497.2745 | 27497.2745 | 27497.2745 | 27497.2745 | 27497.2745 | 27497.2745 | 27497.2745 | 27497.2745 | 27497.2745 | 27497.2745
30% | 3095.428 | 4113.1385 | 4390.3573 | 4382.4246 | 4382.3296 | 4414.0359 | 4448.8155 | 4520.1445 | 4571.3898 | 4599.2504 | 4629.7711 | 4657.6609 | 4707.9489 | 4770.3323 | 4766.1162 | 4766.1162 | 4766.1162 | 4766.1162 | 4766.1162 | 4766.1162 | 4766.1162 | 4766.1162 | 4766.1162 | 4766.1162 | 4766.1162 | 4766.1162 | 4766.1162 | 4766.1162 | 4766.1162 | 4766.1162 |  | 17207.9743 | 22291.8776 | 23623.1145 | 23543.942 | 23550.5887 | 23687.6435 | 24048.4582 | 24290.3798 | 24527.0085 | 24803.6745 | 25060.2981 | 25309.2393 | 25338.0792 | 25628.5516 | 25409.1812 | 25409.1812 | 25409.1812 | 25409.1812 | 25409.1812 | 25409.1812 | 25409.1812 | 25409.1812 | 25409.1812 | 25409.1812 | 25409.1812 | 25409.1812 | 25409.1812 | 25409.1812 | 25409.1812 | 25409.1812
25% | 2113.496 | 2808.3682 | 2997.6476 | 2992.2313 | 2992.1665 | 3013.8149 | 3037.5617 | 3086.2637 | 3121.253 | 3140.2756 | 3161.1146 | 3180.1572 | 3214.4928 | 3257.0869 | 3254.2082 | 3254.2082 | 3254.2082 | 3254.2082 | 3254.2082 | 3254.2082 | 3254.2082 | 3254.2082 | 3254.2082 | 3254.2082 | 3254.2082 | 3254.2082 | 3254.2082 | 3254.2082 | 3254.2082 | 3254.2082 |  | 4963.476 | 6429.8794 | 6813.862 | 6791.0255 | 6792.9426 | 6832.4748 | 6936.5483 | 7006.3283 | 7074.5816 | 7154.3833 | 7228.4039 | 7300.2086 | 7308.5272 | 7392.3112 | 7329.0359 | 7329.0359 | 7329.0359 | 7329.0359 | 7329.0359 | 7329.0359 | 7329.0359 | 7329.0359 | 7329.0359 | 7329.0359 | 7329.0359 | 7329.0359 | 7329.0359 | 7329.0359 | 7329.0359 | 7329.0359
20% | 1280.3284 | 1701.2729 | 1815.9359 | 1812.6548 | 1812.6155 | 1825.7299 | 1840.1154 | 1869.6184 | 1890.8145 | 1902.3381 | 1914.9621 | 1926.4978 | 1947.2979 | 1973.1009 | 1971.357 | 1971.357 | 1971.357 | 1971.357 | 1971.357 | 1971.357 | 1971.357 | 1971.357 | 1971.357 | 1971.357 | 1971.357 | 1971.357 | 1971.357 | 1971.357 | 1971.357 | 1971.357 |  | 1331.912 | 1725.4105 | 1828.4494 | 1822.3214 | 1822.8358 | 1833.444 | 1861.3713 | 1880.0963 | 1898.4115 | 1919.8257 | 1939.6886 | 1958.9569 | 1961.1891 | 1983.6719 | 1966.6925 | 1966.6925 | 1966.6925 | 1966.6925 | 1966.6925 | 1966.6925 | 1966.6925 | 1966.6925 | 1966.6925 | 1966.6925 | 1966.6925 | 1966.6925 | 1966.6925 | 1966.6925 | 1966.6925 | 1966.6925
15% | 819.7224 | 1089.2296 | 1162.6419 | 1160.5412 | 1160.516 | 1168.9124 | 1178.1226 | 1197.0118 | 1210.5824 | 1217.9604 | 1226.0428 | 1233.4285 | 1246.7456 | 1263.2658 | 1262.1493 | 1262.1493 | 1262.1493 | 1262.1493 | 1262.1493 | 1262.1493 | 1262.1493 | 1262.1493 | 1262.1493 | 1262.1493 | 1262.1493 | 1262.1493 | 1262.1493 | 1262.1493 | 1262.1493 | 1262.1493 |  | 734.6312 | 951.6698 | 1008.502 | 1005.1221 | 1005.4058 | 1011.2569 | 1026.6605 | 1036.9885 | 1047.0905 | 1058.9017 | 1069.8573 | 1080.4849 | 1081.7162 | 1094.1168 | 1084.7516 | 1084.7516 | 1084.7516 | 1084.7516 | 1084.7516 | 1084.7516 | 1084.7516 | 1084.7516 | 1084.7516 | 1084.7516 | 1084.7516 | 1084.7516 | 1084.7516 | 1084.7516 | 1084.7516 | 1084.7516
10% | 548.6502 | 729.0346 | 778.1704 | 776.7643 | 776.7475 | 782.3673 | 788.5318 | 801.1745 | 810.2575 | 815.1957 | 820.6054 | 825.5487 | 834.462 | 845.5192 | 844.7719 | 844.7719 | 844.7719 | 844.7719 | 844.7719 | 844.7719 | 844.7719 | 844.7719 | 844.7719 | 844.7719 | 844.7719 | 844.7719 | 844.7719 | 844.7719 | 844.7719 | 844.7719 |  | 171.688 | 222.4113 | 235.6934 | 234.9034 | 234.9698 | 236.3372 | 239.9371 | 242.3508 | 244.7117 | 247.4721 | 250.0325 | 252.5162 | 252.804 | 255.7021 | 253.5134 | 253.5134 | 253.5134 | 253.5134 | 253.5134 | 253.5134 | 253.5134 | 253.5134 | 253.5134 | 253.5134 | 253.5134 | 253.5134 | 253.5134 | 253.5134 | 253.5134 | 253.5134
5% | 390.344 | 518.6808 | 553.639 | 552.6387 | 552.6267 | 556.625 | 561.0108 | 570.0056 | 576.4678 | 579.9811 | 583.8299 | 587.3469 | 593.6884 | 601.5551 | 601.0235 | 601.0235 | 601.0235 | 601.0235 | 601.0235 | 601.0235 | 601.0235 | 601.0235 | 601.0235 | 601.0235 | 601.0235 | 601.0235 | 601.0235 | 601.0235 | 601.0235 | 601.0235 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9.992e-14% | 34.2635 | 45.5286 | 48.5972 | 48.5094 | 48.5083 | 48.8593 | 49.2443 | 50.0338 | 50.6011 | 50.9095 | 51.2473 | 51.556 | 52.1126 | 52.8032 | 52.7565 | 52.7565 | 52.7565 | 52.7565 | 52.7565 | 52.7565 | 52.7565 | 52.7565 | 52.7565 | 52.7565 | 52.7565 | 52.7565 | 52.7565 | 52.7565 | 52.7565 | 52.7565 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E @ R (MWh) | 91763.8061 | 121933.7811 | 130151.918 | 129916.7517 | 129913.938 | 130853.8682 | 131884.9083 | 133999.4516 | 135518.6175 | 136344.5424 | 137249.3282 | 138076.12 | 139566.9035 | 141416.2562 | 141291.2697 | 141291.2697 | 141291.2697 | 141291.2697 | 141291.2697 | 141291.2697 | 141291.2697 | 141291.2697 | 141291.2697 | 141291.2697 | 141291.2697 | 141291.2697 | 141291.2697 | 141291.2697 | 141291.2697 | 141291.2697 | E @ R (MWh) | 89067.5772 | 115381.5956 | 122272.0083 | 121862.2159 | 121896.6185 | 122606.0074 | 124473.5651 | 125725.7387 | 126950.5164 | 128382.5252 | 129710.7955 | 130999.3026 | 131148.5764 | 132652.0463 | 131516.5966 | 131516.5966 | 131516.5966 | 131516.5966 | 131516.5966 | 131516.5966 | 131516.5966 | 131516.5966 | 131516.5966 | 131516.5966 | 131516.5966 | 131516.5966 | 131516.5966 | 131516.5966 | 131516.5966 | 131516.5966
Option 1 Summer POE50 W E @ R (MWh) N 2 | 64234.6643 | 85353.6468 | 91106.3426 | 90941.7262 | 90939.7566 | 91597.7077 | 92319.4358 | 93799.6161 | 94863.0323 | 95441.1797 | 96074.5298 | 96653.284 | 97696.8324 | 98991.3793 | 98903.8888 | 98903.8888 | 98903.8888 | 98903.8888 | 98903.8888 | 98903.8888 | 98903.8888 | 98903.8888 | 98903.8888 | 98903.8888 | 98903.8888 | 98903.8888 | 98903.8888 | 98903.8888 | 98903.8888 | 98903.8888 | Option 1 Summer POE10 W E @ R (MWh) N 2 | 26720.2732 | 34614.4787 | 36681.6025 | 36558.6648 | 36568.9855 | 36781.8022 | 37342.0695 | 37717.7216 | 38085.1549 | 38514.7576 | 38913.2387 | 39299.7908 | 39344.5729 | 39795.6139 | 39454.979 | 39454.979 | 39454.979 | 39454.979 | 39454.979 | 39454.979 | 39454.979 | 39454.979 | 39454.979 | 39454.979 | 39454.979 | 39454.979 | 39454.979 | 39454.979 | 39454.979 | 39454.979
Option 2 - 1A New PHS ZSS + Four new feeders
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | 59.6718 | 82.8348 | 88.8563 | 47.0044 | 47.805 | 49.1833 | 52.3192 | 54.4183 | 57.0776 | 58.4579 | 59.6722 | 57.4348 | 60.0569 | 64.1793 | 61.051 | 61.051 | 61.051 | 61.051 | 61.051 | 61.051 | 61.051 | 61.051 | 61.051 | 61.051 | 61.051 | 61.051 | 61.051 | 61.051 | 61.051 | 61.051 |  | 63.8857 | 86.7566 | 93.0131 | 51.1029 | 51.7176 | 53.066 | 56.2509 | 57.9898 | 61.3023 | 71.3715 | 63.0705 | 61.4468 | 63.6386 | 68.4319 | 65.1874 | 65.1874 | 65.1874 | 65.1874 | 65.1874 | 65.1874 | 65.1874 | 65.1874 | 65.1874 | 65.1874 | 65.1874 | 65.1874 | 65.1874 | 65.1874 | 65.1874 | 65.1874
98% | 70.8865 | 98.4027 | 105.556 | 55.8384 | 56.7894 | 58.4268 | 62.1521 | 64.6457 | 67.8047 | 69.4444 | 70.8869 | 68.229 | 71.344 | 76.2412 | 72.5249 | 72.5249 | 72.5249 | 72.5249 | 72.5249 | 72.5249 | 72.5249 | 72.5249 | 72.5249 | 72.5249 | 72.5249 | 72.5249 | 72.5249 | 72.5249 | 72.5249 | 72.5249 |  | 75.8924 | 103.0616 | 110.494 | 60.7072 | 61.4374 | 63.0392 | 66.8227 | 68.8884 | 72.8235 | 84.7851 | 74.924 | 72.9951 | 75.5988 | 81.293 | 77.4387 | 77.4387 | 77.4387 | 77.4387 | 77.4387 | 77.4387 | 77.4387 | 77.4387 | 77.4387 | 77.4387 | 77.4387 | 77.4387 | 77.4387 | 77.4387 | 77.4387 | 77.4387
97% | 140.3338 | 194.8074 | 208.9687 | 110.5431 | 112.4258 | 115.6673 | 123.0422 | 127.9788 | 134.2326 | 137.4788 | 140.3346 | 135.0727 | 141.2394 | 150.9343 | 143.5772 | 143.5772 | 143.5772 | 143.5772 | 143.5772 | 143.5772 | 143.5772 | 143.5772 | 143.5772 | 143.5772 | 143.5772 | 143.5772 | 143.5772 | 143.5772 | 143.5772 | 143.5772 |  | 150.2438 | 204.0305 | 218.7445 | 120.1817 | 121.6272 | 124.7985 | 132.2886 | 136.378 | 144.1683 | 167.8486 | 148.3266 | 144.5081 | 149.6626 | 160.9354 | 153.305 | 153.305 | 153.305 | 153.305 | 153.305 | 153.305 | 153.305 | 153.305 | 153.305 | 153.305 | 153.305 | 153.305 | 153.305 | 153.305 | 153.305 | 153.305
95% | 414.5243 | 575.4311 | 617.2612 | 326.5273 | 332.0884 | 341.6635 | 363.4476 | 378.0297 | 396.5026 | 406.0911 | 414.5267 | 398.9839 | 417.1996 | 445.8367 | 424.1051 | 424.1051 | 424.1051 | 424.1051 | 424.1051 | 424.1051 | 424.1051 | 424.1051 | 424.1051 | 424.1051 | 424.1051 | 424.1051 | 424.1051 | 424.1051 | 424.1051 | 424.1051 |  | 443.7972 | 602.6746 | 646.1375 | 354.9982 | 359.2682 | 368.6356 | 390.7602 | 402.8398 | 425.8511 | 495.799 | 438.1341 | 426.8547 | 442.0804 | 475.3784 | 452.8394 | 452.8394 | 452.8394 | 452.8394 | 452.8394 | 452.8394 | 452.8394 | 452.8394 | 452.8394 | 452.8394 | 452.8394 | 452.8394 | 452.8394 | 452.8394 | 452.8394 | 452.8394
90% | 2285.5212 | 3172.6969 | 3403.3313 | 1800.3406 | 1831.0025 | 1883.7955 | 2003.9047 | 2084.3042 | 2186.1565 | 2239.0239 | 2285.5343 | 2199.8376 | 2300.2714 | 2458.1649 | 2338.3456 | 2338.3456 | 2338.3456 | 2338.3456 | 2338.3456 | 2338.3456 | 2338.3456 | 2338.3456 | 2338.3456 | 2338.3456 | 2338.3456 | 2338.3456 | 2338.3456 | 2338.3456 | 2338.3456 | 2338.3456 |  | 2446.9201 | 3322.9067 | 3562.5435 | 1957.3177 | 1980.8608 | 2032.5091 | 2154.4955 | 2221.0971 | 2347.9722 | 2733.6372 | 2415.6957 | 2353.506 | 2437.454 | 2621.0462 | 2496.7752 | 2496.7752 | 2496.7752 | 2496.7752 | 2496.7752 | 2496.7752 | 2496.7752 | 2496.7752 | 2496.7752 | 2496.7752 | 2496.7752 | 2496.7752 | 2496.7752 | 2496.7752 | 2496.7752 | 2496.7752
85% | 5583.3646 | 7750.6712 | 8314.0946 | 4398.1031 | 4473.0078 | 4601.9775 | 4895.3957 | 5091.8059 | 5340.6238 | 5469.775 | 5583.3965 | 5374.0456 | 5619.3982 | 6005.1208 | 5712.4108 | 5712.4108 | 5712.4108 | 5712.4108 | 5712.4108 | 5712.4108 | 5712.4108 | 5712.4108 | 5712.4108 | 5712.4108 | 5712.4108 | 5712.4108 | 5712.4108 | 5712.4108 | 5712.4108 | 5712.4108 |  | 5977.6505 | 8117.623 | 8703.0385 | 4781.5869 | 4839.101 | 4965.2742 | 5263.2782 | 5425.9812 | 5735.9279 | 6678.08 | 5901.3716 | 5749.4466 | 5954.5256 | 6403.0281 | 6099.443 | 6099.443 | 6099.443 | 6099.443 | 6099.443 | 6099.443 | 6099.443 | 6099.443 | 6099.443 | 6099.443 | 6099.443 | 6099.443 | 6099.443 | 6099.443 | 6099.443 | 6099.443
80% | 8678.2039 | 12046.8408 | 12922.5678 | 6835.9561 | 6952.3802 | 7152.8374 | 7608.8962 | 7914.1758 | 8300.9126 | 8501.6518 | 8678.2534 | 8352.8601 | 8734.2107 | 9333.738 | 8878.7799 | 8878.7799 | 8878.7799 | 8878.7799 | 8878.7799 | 8878.7799 | 8878.7799 | 8878.7799 | 8878.7799 | 8878.7799 | 8878.7799 | 8878.7799 | 8878.7799 | 8878.7799 | 8878.7799 | 8878.7799 |  | 9291.041 | 12617.1926 | 13527.1019 | 7432.0036 | 7521.3975 | 7717.5081 | 8180.6946 | 8433.5833 | 8915.3324 | 10379.716 | 9172.4809 | 8936.3444 | 9255.098 | 9952.2038 | 9480.3426 | 9480.3426 | 9480.3426 | 9480.3426 | 9480.3426 | 9480.3426 | 9480.3426 | 9480.3426 | 9480.3426 | 9480.3426 | 9480.3426 | 9480.3426 | 9480.3426 | 9480.3426 | 9480.3426 | 9480.3426
75% | 9574.4808 | 13291.0275 | 14257.1987 | 7541.9674 | 7670.4157 | 7891.5759 | 8394.736 | 8731.5446 | 9158.2233 | 9379.6947 | 9574.5355 | 9215.5358 | 9636.2719 | 10297.7179 | 9795.7722 | 9795.7722 | 9795.7722 | 9795.7722 | 9795.7722 | 9795.7722 | 9795.7722 | 9795.7722 | 9795.7722 | 9795.7722 | 9795.7722 | 9795.7722 | 9795.7722 | 9795.7722 | 9795.7722 | 9795.7722 |  | 10250.6112 | 13920.2847 | 14924.1686 | 8199.5742 | 8298.2005 | 8514.5653 | 9025.5892 | 9304.5961 | 9836.0998 | 11451.7236 | 10119.8063 | 9859.2819 | 10210.9561 | 10980.0583 | 10459.4637 | 10459.4637 | 10459.4637 | 10459.4637 | 10459.4637 | 10459.4637 | 10459.4637 | 10459.4637 | 10459.4637 | 10459.4637 | 10459.4637 | 10459.4637 | 10459.4637 | 10459.4637 | 10459.4637 | 10459.4637
70% | 10287.2444 | 14280.4661 | 15318.563 | 8103.4224 | 8241.4329 | 8479.0571 | 9019.6746 | 9381.5566 | 9839.9989 | 10077.9576 | 10287.3031 | 9901.5781 | 10353.6355 | 11064.3222 | 10525.0096 | 10525.0096 | 10525.0096 | 10525.0096 | 10525.0096 | 10525.0096 | 10525.0096 | 10525.0096 | 10525.0096 | 10525.0096 | 10525.0096 | 10525.0096 | 10525.0096 | 10525.0096 | 10525.0096 | 10525.0096 |  | 11013.7087 | 14956.5677 | 16035.1849 | 8809.9841 | 8915.9525 | 9148.4244 | 9697.4911 | 9997.2683 | 10568.3393 | 12304.2368 | 10873.1662 | 10593.2472 | 10971.1015 | 11797.4589 | 11238.1091 | 11238.1091 | 11238.1091 | 11238.1091 | 11238.1091 | 11238.1091 | 11238.1091 | 11238.1091 | 11238.1091 | 11238.1091 | 11238.1091 | 11238.1091 | 11238.1091 | 11238.1091 | 11238.1091 | 11238.1091
65% | 10840.7831 | 15048.8731 | 16142.8282 | 8539.4534 | 8684.89 | 8935.3004 | 9505.0076 | 9886.3618 | 10369.4722 | 10620.2349 | 10840.845 | 10434.3648 | 10910.7466 | 11659.6741 | 11091.3421 | 11091.3421 | 11091.3421 | 11091.3421 | 11091.3421 | 11091.3421 | 11091.3421 | 11091.3421 | 11091.3421 | 11091.3421 | 11091.3421 | 11091.3421 | 11091.3421 | 11091.3421 | 11091.3421 | 11091.3421 |  | 11606.3372 | 15761.3546 | 16898.0103 | 9284.034 | 9395.7044 | 9640.6853 | 10219.2962 | 10535.2039 | 11137.0033 | 12966.3064 | 11458.2323 | 11163.2514 | 11561.4374 | 12432.2596 | 11842.8122 | 11842.8122 | 11842.8122 | 11842.8122 | 11842.8122 | 11842.8122 | 11842.8122 | 11842.8122 | 11842.8122 | 11842.8122 | 11842.8122 | 11842.8122 | 11842.8122 | 11842.8122 | 11842.8122 | 11842.8122
60% | 11934.3669 | 16566.9557 | 17771.2656 | 9400.8864 | 9560.9942 | 9836.6652 | 10463.8426 | 10883.6666 | 11415.5116 | 11691.5705 | 11934.4351 | 11486.9504 | 12011.3881 | 12835.8651 | 12210.2015 | 12210.2015 | 12210.2015 | 12210.2015 | 12210.2015 | 12210.2015 | 12210.2015 | 12210.2015 | 12210.2015 | 12210.2015 | 12210.2015 | 12210.2015 | 12210.2015 | 12210.2015 | 12210.2015 | 12210.2015 |  | 12777.1477 | 17351.3101 | 18602.628 | 10220.5779 | 10343.5133 | 10613.207 | 11250.1864 | 11597.9619 | 12260.4689 | 14274.3063 | 12614.1025 | 12289.3648 | 12727.7185 | 13686.3865 | 13037.4775 | 13037.4775 | 13037.4775 | 13037.4775 | 13037.4775 | 13037.4775 | 13037.4775 | 13037.4775 | 13037.4775 | 13037.4775 | 13037.4775 | 13037.4775 | 13037.4775 | 13037.4775 | 13037.4775 | 13037.4775
55% | 13276.2336 | 18429.6976 | 19769.4166 | 10457.8956 | 10636.0055 | 10942.6721 | 11640.3676 | 12107.3955 | 12699.0396 | 13006.1378 | 13276.3094 | 12778.5108 | 13361.9148 | 14279.0936 | 13583.0822 | 13583.0822 | 13583.0822 | 13583.0822 | 13583.0822 | 13583.0822 | 13583.0822 | 13583.0822 | 13583.0822 | 13583.0822 | 13583.0822 | 13583.0822 | 13583.0822 | 13583.0822 | 13583.0822 | 13583.0822 |  | 14213.7742 | 19302.2426 | 20694.2551 | 11369.7509 | 11506.5088 | 11806.5261 | 12515.1257 | 12902.0041 | 13639.0015 | 15879.2691 | 14032.3966 | 13671.1464 | 14158.7874 | 15225.2453 | 14503.3748 | 14503.3748 | 14503.3748 | 14503.3748 | 14503.3748 | 14503.3748 | 14503.3748 | 14503.3748 | 14503.3748 | 14503.3748 | 14503.3748 | 14503.3748 | 14503.3748 | 14503.3748 | 14503.3748 | 14503.3748
50% | 13456.7484 | 18680.2832 | 20038.2182 | 10600.09 | 10780.6215 | 11091.4579 | 11798.6398 | 12272.0178 | 12871.7064 | 13182.9802 | 13456.8252 | 12952.2581 | 13543.5946 | 14473.2442 | 13767.7692 | 13767.7692 | 13767.7692 | 13767.7692 | 13767.7692 | 13767.7692 | 13767.7692 | 13767.7692 | 13767.7692 | 13767.7692 | 13767.7692 | 13767.7692 | 13767.7692 | 13767.7692 | 13767.7692 | 13767.7692 |  | 14407.0366 | 19564.692 | 20975.6315 | 11524.3436 | 11662.961 | 11967.0576 | 12685.2918 | 13077.4306 | 13824.4488 | 16095.1769 | 14223.1929 | 13857.0308 | 14351.3021 | 15432.2605 | 14700.5748 | 14700.5748 | 14700.5748 | 14700.5748 | 14700.5748 | 14700.5748 | 14700.5748 | 14700.5748 | 14700.5748 | 14700.5748 | 14700.5748 | 14700.5748 | 14700.5748 | 14700.5748 | 14700.5748 | 14700.5748
45% | 10386.1977 | 14417.8303 | 15465.9127 | 8181.3694 | 8320.7075 | 8560.6174 | 9106.4351 | 9471.798 | 9934.6502 | 10174.8977 | 10386.257 | 9996.8216 | 10453.2274 | 11170.7502 | 10626.25 | 10626.25 | 10626.25 | 10626.25 | 10626.25 | 10626.25 | 10626.25 | 10626.25 | 10626.25 | 10626.25 | 10626.25 | 10626.25 | 10626.25 | 10626.25 | 10626.25 | 10626.25 |  | 11119.6499 | 15100.4354 | 16189.4278 | 8894.7275 | 9001.7153 | 9236.4234 | 9790.7715 | 10093.4323 | 10669.9965 | 12422.5916 | 10977.7554 | 10695.144 | 11076.6328 | 11910.9389 | 11346.2087 | 11346.2087 | 11346.2087 | 11346.2087 | 11346.2087 | 11346.2087 | 11346.2087 | 11346.2087 | 11346.2087 | 11346.2087 | 11346.2087 | 11346.2087 | 11346.2087 | 11346.2087 | 11346.2087 | 11346.2087
40% | 5102.6915 | 7083.4142 | 7598.3323 | 4019.4695 | 4087.9256 | 4205.7922 | 4473.95 | 4653.4511 | 4880.8483 | 4998.8808 | 5102.7206 | 4911.3928 | 5135.6229 | 5488.1386 | 5220.6281 | 5220.6281 | 5220.6281 | 5220.6281 | 5220.6281 | 5220.6281 | 5220.6281 | 5220.6281 | 5220.6281 | 5220.6281 | 5220.6281 | 5220.6281 | 5220.6281 | 5220.6281 | 5220.6281 | 5220.6281 |  | 5463.0332 | 7418.775 | 7953.792 | 4369.939 | 4422.5017 | 4537.8127 | 4810.1614 | 4958.8572 | 5242.1206 | 6103.1625 | 5393.3211 | 5254.4754 | 5441.8992 | 5851.7899 | 5574.3406 | 5574.3406 | 5574.3406 | 5574.3406 | 5574.3406 | 5574.3406 | 5574.3406 | 5574.3406 | 5574.3406 | 5574.3406 | 5574.3406 | 5574.3406 | 5574.3406 | 5574.3406 | 5574.3406 | 5574.3406
35% | 1907.0998 | 2647.3829 | 2839.8304 | 1502.2522 | 1527.8373 | 1571.8892 | 1672.1115 | 1739.199 | 1824.1873 | 1868.3012 | 1907.1107 | 1835.6031 | 1919.4078 | 2051.1583 | 1951.1779 | 1951.1779 | 1951.1779 | 1951.1779 | 1951.1779 | 1951.1779 | 1951.1779 | 1951.1779 | 1951.1779 | 1951.1779 | 1951.1779 | 1951.1779 | 1951.1779 | 1951.1779 | 1951.1779 | 1951.1779 |  | 2041.7754 | 2772.7219 | 2972.6813 | 1633.2381 | 1652.883 | 1695.9798 | 1797.7685 | 1853.3427 | 1959.2106 | 2281.0198 | 2015.7209 | 1963.8282 | 2033.8766 | 2187.0708 | 2083.3758 | 2083.3758 | 2083.3758 | 2083.3758 | 2083.3758 | 2083.3758 | 2083.3758 | 2083.3758 | 2083.3758 | 2083.3758 | 2083.3758 | 2083.3758 | 2083.3758 | 2083.3758 | 2083.3758 | 2083.3758
30% | 951.1511 | 1320.3614 | 1416.3431 | 749.2365 | 761.9968 | 783.9674 | 833.9525 | 867.4118 | 909.7991 | 931.8005 | 951.1565 | 915.4926 | 957.2895 | 1022.9991 | 973.1347 | 973.1347 | 973.1347 | 973.1347 | 973.1347 | 973.1347 | 973.1347 | 973.1347 | 973.1347 | 973.1347 | 973.1347 | 973.1347 | 973.1347 | 973.1347 | 973.1347 | 973.1347 |  | 1018.3194 | 1382.8733 | 1482.6014 | 814.5646 | 824.3624 | 845.8566 | 896.6229 | 924.3401 | 977.1409 | 1137.6407 | 1005.3249 | 979.4439 | 1014.38 | 1090.7844 | 1039.0673 | 1039.0673 | 1039.0673 | 1039.0673 | 1039.0673 | 1039.0673 | 1039.0673 | 1039.0673 | 1039.0673 | 1039.0673 | 1039.0673 | 1039.0673 | 1039.0673 | 1039.0673 | 1039.0673 | 1039.0673
25% | 560.7353 | 778.3972 | 834.9816 | 441.6999 | 449.2226 | 462.175 | 491.6429 | 511.3683 | 536.357 | 549.3276 | 560.7385 | 539.7135 | 564.3542 | 603.0922 | 573.6954 | 573.6954 | 573.6954 | 573.6954 | 573.6954 | 573.6954 | 573.6954 | 573.6954 | 573.6954 | 573.6954 | 573.6954 | 573.6954 | 573.6954 | 573.6954 | 573.6954 | 573.6954 |  | 600.3333 | 815.25 | 874.0431 | 480.2131 | 485.9892 | 498.6607 | 528.5892 | 544.9294 | 576.0572 | 670.6772 | 592.6727 | 577.4149 | 598.0109 | 643.0538 | 612.5649 | 612.5649 | 612.5649 | 612.5649 | 612.5649 | 612.5649 | 612.5649 | 612.5649 | 612.5649 | 612.5649 | 612.5649 | 612.5649 | 612.5649 | 612.5649 | 612.5649 | 612.5649
20% | 283.3663 | 393.3611 | 421.9559 | 223.212 | 227.0136 | 233.559 | 248.4505 | 258.4187 | 271.0467 | 277.6014 | 283.3679 | 272.7429 | 285.195 | 304.7712 | 289.9156 | 289.9156 | 289.9156 | 289.9156 | 289.9156 | 289.9156 | 289.9156 | 289.9156 | 289.9156 | 289.9156 | 289.9156 | 289.9156 | 289.9156 | 289.9156 | 289.9156 | 289.9156 |  | 303.377 | 411.9846 | 441.6956 | 242.6745 | 245.5935 | 251.997 | 267.1213 | 275.3787 | 291.1091 | 338.9251 | 299.5057 | 291.7952 | 302.2034 | 324.9657 | 309.5582 | 309.5582 | 309.5582 | 309.5582 | 309.5582 | 309.5582 | 309.5582 | 309.5582 | 309.5582 | 309.5582 | 309.5582 | 309.5582 | 309.5582 | 309.5582 | 309.5582 | 309.5582
15% | 115.4455 | 160.2582 | 171.908 | 90.9382 | 92.487 | 95.1537 | 101.2206 | 105.2817 | 110.4264 | 113.0969 | 115.4462 | 111.1175 | 116.1906 | 124.166 | 118.1138 | 118.1138 | 118.1138 | 118.1138 | 118.1138 | 118.1138 | 118.1138 | 118.1138 | 118.1138 | 118.1138 | 118.1138 | 118.1138 | 118.1138 | 118.1138 | 118.1138 | 118.1138 |  | 123.598 | 167.8456 | 179.95 | 98.8674 | 100.0566 | 102.6654 | 108.8272 | 112.1913 | 118.6 | 138.0806 | 122.0208 | 118.8795 | 123.1199 | 132.3934 | 126.1163 | 126.1163 | 126.1163 | 126.1163 | 126.1163 | 126.1163 | 126.1163 | 126.1163 | 126.1163 | 126.1163 | 126.1163 | 126.1163 | 126.1163 | 126.1163 | 126.1163 | 126.1163
10% | 46.4781 | 64.5196 | 69.2097 | 36.6115 | 37.235 | 38.3086 | 40.7511 | 42.3861 | 44.4574 | 45.5325 | 46.4783 | 44.7356 | 46.778 | 49.9889 | 47.5523 | 47.5523 | 47.5523 | 47.5523 | 47.5523 | 47.5523 | 47.5523 | 47.5523 | 47.5523 | 47.5523 | 47.5523 | 47.5523 | 47.5523 | 47.5523 | 47.5523 | 47.5523 |  | 49.7602 | 67.5742 | 72.4474 | 39.8038 | 40.2825 | 41.3328 | 43.8135 | 45.1679 | 47.7481 | 55.5909 | 49.1253 | 47.8606 | 49.5677 | 53.3013 | 50.7741 | 50.7741 | 50.7741 | 50.7741 | 50.7741 | 50.7741 | 50.7741 | 50.7741 | 50.7741 | 50.7741 | 50.7741 | 50.7741 | 50.7741 | 50.7741 | 50.7741 | 50.7741
5% | 39.5813 | 54.9457 | 58.9399 | 31.1788 | 31.7098 | 32.6241 | 34.7042 | 36.0966 | 37.8605 | 38.7761 | 39.5815 | 38.0974 | 39.8368 | 42.5712 | 40.4961 | 40.4961 | 40.4961 | 40.4961 | 40.4961 | 40.4961 | 40.4961 | 40.4961 | 40.4961 | 40.4961 | 40.4961 | 40.4961 | 40.4961 | 40.4961 | 40.4961 | 40.4961 |  | 42.3765 | 57.5471 | 61.6972 | 33.8974 | 34.3051 | 35.1996 | 37.3122 | 38.4656 | 40.6629 | 47.3419 | 41.8357 | 40.7587 | 42.2125 | 45.392 | 43.2399 | 43.2399 | 43.2399 | 43.2399 | 43.2399 | 43.2399 | 43.2399 | 43.2399 | 43.2399 | 43.2399 | 43.2399 | 43.2399 | 43.2399 | 43.2399 | 43.2399 | 43.2399
9.992e-14% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E @ R (MWh) | 105995.1099 | 147139.4588 | 157835.5397 | 83493.9964 | 84915.9942 | 87364.3666 | 92934.6444 | 96663.3127 | 101386.8952 | 103838.7131 | 105995.715 | 102021.3788 | 106679.1739 | 114001.768 | 108444.9352 | 108444.9352 | 108444.9352 | 108444.9352 | 108444.9352 | 108444.9352 | 108444.9352 | 108444.9352 | 108444.9352 | 108444.9352 | 108444.9352 | 108444.9352 | 108444.9352 | 108444.9352 | 108444.9352 | 108444.9352 | E @ R (MWh) | 113480.2695 | 154105.704 | 165219.287 | 90774.0881 | 91865.9395 | 94261.2247 | 99918.5588 | 103007.3279 | 108891.3852 | 126777.2868 | 112032.1827 | 109148.0247 | 113041.2642 | 121555.6763 | 115792.3892 | 115792.3892 | 115792.3892 | 115792.3892 | 115792.3892 | 115792.3892 | 115792.3892 | 115792.3892 | 115792.3892 | 115792.3892 | 115792.3892 | 115792.3892 | 115792.3892 | 115792.3892 | 115792.3892 | 115792.3892
Option 2 Winter POE50 W E @ R (MWh) N 2 | 74196.5769 | 102997.6211 | 110484.8778 | 58445.7975 | 59441.1959 | 61155.0566 | 65054.2511 | 67664.3189 | 70970.8267 | 72687.0992 | 74197.0005 | 71414.9651 | 74675.4217 | 79801.2376 | 75911.4547 | 75911.4547 | 75911.4547 | 75911.4547 | 75911.4547 | 75911.4547 | 75911.4547 | 75911.4547 | 75911.4547 | 75911.4547 | 75911.4547 | 75911.4547 | 75911.4547 | 75911.4547 | 75911.4547 | 75911.4547 | Option 2 Winter POE10 W E @ R (MWh) N 2 | 34044.0809 | 46231.7112 | 49565.7861 | 27232.2264 | 27559.7818 | 28278.3674 | 29975.5676 | 30902.1984 | 32667.4155 | 38033.1861 | 33609.6548 | 32744.4074 | 33912.3793 | 36466.7029 | 34737.7168 | 34737.7168 | 34737.7168 | 34737.7168 | 34737.7168 | 34737.7168 | 34737.7168 | 34737.7168 | 34737.7168 | 34737.7168 | 34737.7168 | 34737.7168 | 34737.7168 | 34737.7168 | 34737.7168 | 34737.7168
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 76.9936 | 99.7405 | 105.6969 | 61.6949 | 61.7246 | 62.3379 | 63.9522 | 65.0347 | 66.0934 | 67.3313 | 68.4795 | 69.5934 | 69.7224 | 71.0221 | 70.0405 | 70.0405 | 70.0405 | 70.0405 | 70.0405 | 70.0405 | 70.0405 | 70.0405 | 70.0405 | 70.0405 | 70.0405 | 70.0405 | 70.0405 | 70.0405 | 70.0405 | 70.0405
98% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 38.1099 | 49.369 | 52.3173 | 30.5374 | 30.5521 | 30.8557 | 31.6548 | 32.1905 | 32.7146 | 33.3273 | 33.8956 | 34.447 | 34.5108 | 35.1541 | 34.6683 | 34.6683 | 34.6683 | 34.6683 | 34.6683 | 34.6683 | 34.6683 | 34.6683 | 34.6683 | 34.6683 | 34.6683 | 34.6683 | 34.6683 | 34.6683 | 34.6683 | 34.6683
97% | 16.9149 | 22.4762 | 23.991 | 13.2551 | 13.2546 | 13.4278 | 13.6179 | 14.0076 | 14.2877 | 14.4399 | 14.6067 | 14.7591 | 15.0339 | 15.3748 | 15.3518 | 15.3518 | 15.3518 | 15.3518 | 15.3518 | 15.3518 | 15.3518 | 15.3518 | 15.3518 | 15.3518 | 15.3518 | 15.3518 | 15.3518 | 15.3518 | 15.3518 | 15.3518 |  | 75.446 | 97.7357 | 103.5723 | 60.4548 | 60.4839 | 61.0848 | 62.6668 | 63.7274 | 64.7649 | 65.9779 | 67.103 | 68.1945 | 68.3209 | 69.5945 | 68.6327 | 68.6327 | 68.6327 | 68.6327 | 68.6327 | 68.6327 | 68.6327 | 68.6327 | 68.6327 | 68.6327 | 68.6327 | 68.6327 | 68.6327 | 68.6327 | 68.6327 | 68.6327
95% | 83.2734 | 110.6519 | 118.1097 | 65.2558 | 65.2532 | 66.1062 | 67.0418 | 68.9607 | 70.3393 | 71.0888 | 71.9099 | 72.6602 | 74.0131 | 75.6913 | 75.5779 | 75.5779 | 75.5779 | 75.5779 | 75.5779 | 75.5779 | 75.5779 | 75.5779 | 75.5779 | 75.5779 | 75.5779 | 75.5779 | 75.5779 | 75.5779 | 75.5779 | 75.5779 |  | 111.4279 | 144.3481 | 152.9683 | 89.2871 | 89.3301 | 90.2176 | 92.554 | 94.1205 | 95.6528 | 97.4443 | 99.106 | 100.718 | 100.9048 | 102.7857 | 101.3652 | 101.3652 | 101.3652 | 101.3652 | 101.3652 | 101.3652 | 101.3652 | 101.3652 | 101.3652 | 101.3652 | 101.3652 | 101.3652 | 101.3652 | 101.3652 | 101.3652 | 101.3652
90% | 144.4273 | 191.9119 | 204.8464 | 113.178 | 113.1736 | 114.6529 | 116.2757 | 119.6038 | 121.9948 | 123.2947 | 124.7188 | 126.02 | 128.3664 | 131.2771 | 131.0804 | 131.0804 | 131.0804 | 131.0804 | 131.0804 | 131.0804 | 131.0804 | 131.0804 | 131.0804 | 131.0804 | 131.0804 | 131.0804 | 131.0804 | 131.0804 | 131.0804 | 131.0804 |  | 483.1446 | 625.8842 | 663.261 | 387.1432 | 387.3298 | 391.1779 | 401.3084 | 408.1008 | 414.7445 | 422.5124 | 429.7176 | 436.7071 | 437.5168 | 445.6723 | 439.5131 | 439.5131 | 439.5131 | 439.5131 | 439.5131 | 439.5131 | 439.5131 | 439.5131 | 439.5131 | 439.5131 | 439.5131 | 439.5131 | 439.5131 | 439.5131 | 439.5131 | 439.5131
85% | 409.8612 | 544.6148 | 581.321 | 321.1808 | 321.1682 | 325.3664 | 329.9715 | 339.4161 | 346.2014 | 349.8904 | 353.9316 | 357.6244 | 364.283 | 372.5431 | 371.9848 | 371.9848 | 371.9848 | 371.9848 | 371.9848 | 371.9848 | 371.9848 | 371.9848 | 371.9848 | 371.9848 | 371.9848 | 371.9848 | 371.9848 | 371.9848 | 371.9848 | 371.9848 |  | 457.0286 | 592.0526 | 627.4091 | 366.2165 | 366.3931 | 370.0331 | 379.616 | 386.0413 | 392.3259 | 399.6739 | 406.4896 | 413.1013 | 413.8672 | 421.5819 | 415.7557 | 415.7557 | 415.7557 | 415.7557 | 415.7557 | 415.7557 | 415.7557 | 415.7557 | 415.7557 | 415.7557 | 415.7557 | 415.7557 | 415.7557 | 415.7557 | 415.7557 | 415.7557
80% | 572.5046 | 760.7318 | 812.0039 | 448.6335 | 448.6159 | 454.48 | 460.9126 | 474.105 | 483.5829 | 488.7358 | 494.3806 | 499.5389 | 508.8397 | 520.3777 | 519.5979 | 519.5979 | 519.5979 | 519.5979 | 519.5979 | 519.5979 | 519.5979 | 519.5979 | 519.5979 | 519.5979 | 519.5979 | 519.5979 | 519.5979 | 519.5979 | 519.5979 | 519.5979 |  | 319.1946 | 413.4971 | 438.1905 | 255.7703 | 255.8936 | 258.4358 | 265.1287 | 269.6161 | 274.0054 | 279.1373 | 283.8975 | 288.5152 | 289.0501 | 294.4382 | 290.369 | 290.369 | 290.369 | 290.369 | 290.369 | 290.369 | 290.369 | 290.369 | 290.369 | 290.369 | 290.369 | 290.369 | 290.369 | 290.369 | 290.369 | 290.369
75% | 1492.4153 | 1983.0895 | 2116.7465 | 1169.5059 | 1169.4601 | 1184.7468 | 1201.5153 | 1235.9055 | 1260.6127 | 1274.0453 | 1288.7604 | 1302.2071 | 1326.4527 | 1356.5299 | 1354.4972 | 1354.4972 | 1354.4972 | 1354.4972 | 1354.4972 | 1354.4972 | 1354.4972 | 1354.4972 | 1354.4972 | 1354.4972 | 1354.4972 | 1354.4972 | 1354.4972 | 1354.4972 | 1354.4972 | 1354.4972 |  | 569.714 | 738.0296 | 782.1036 | 456.5112 | 456.7313 | 461.2688 | 473.2145 | 481.2239 | 489.0581 | 498.2179 | 506.714 | 514.9559 | 515.9107 | 525.5275 | 518.2647 | 518.2647 | 518.2647 | 518.2647 | 518.2647 | 518.2647 | 518.2647 | 518.2647 | 518.2647 | 518.2647 | 518.2647 | 518.2647 | 518.2647 | 518.2647 | 518.2647 | 518.2647
70% | 2578.4391 | 3426.1747 | 3657.0932 | 2020.55 | 2020.471 | 2046.8817 | 2075.8526 | 2135.2684 | 2177.9549 | 2201.1623 | 2226.5855 | 2249.8173 | 2291.7063 | 2343.6706 | 2340.1586 | 2340.1586 | 2340.1586 | 2340.1586 | 2340.1586 | 2340.1586 | 2340.1586 | 2340.1586 | 2340.1586 | 2340.1586 | 2340.1586 | 2340.1586 | 2340.1586 | 2340.1586 | 2340.1586 | 2340.1586 |  | 1037.8661 | 1344.492 | 1424.783 | 831.641 | 832.0418 | 840.308 | 862.0699 | 876.6609 | 890.9327 | 907.6193 | 923.0971 | 938.1115 | 939.8509 | 957.3702 | 944.1393 | 944.1393 | 944.1393 | 944.1393 | 944.1393 | 944.1393 | 944.1393 | 944.1393 | 944.1393 | 944.1393 | 944.1393 | 944.1393 | 944.1393 | 944.1393 | 944.1393 | 944.1393
65% | 6475.8072 | 8604.914 | 9184.8711 | 5074.6564 | 5074.4578 | 5140.7891 | 5213.55 | 5362.7741 | 5469.9822 | 5528.2681 | 5592.1192 | 5650.4662 | 5755.6713 | 5886.1809 | 5877.3605 | 5877.3605 | 5877.3605 | 5877.3605 | 5877.3605 | 5877.3605 | 5877.3605 | 5877.3605 | 5877.3605 | 5877.3605 | 5877.3605 | 5877.3605 | 5877.3605 | 5877.3605 | 5877.3605 | 5877.3605 |  | 1305.7961 | 1691.5789 | 1792.5974 | 1046.333 | 1046.8374 | 1057.2375 | 1084.6173 | 1102.9751 | 1120.9312 | 1141.9255 | 1161.3989 | 1180.2894 | 1182.4778 | 1204.5198 | 1187.8733 | 1187.8733 | 1187.8733 | 1187.8733 | 1187.8733 | 1187.8733 | 1187.8733 | 1187.8733 | 1187.8733 | 1187.8733 | 1187.8733 | 1187.8733 | 1187.8733 | 1187.8733 | 1187.8733 | 1187.8733
60% | 9465.8424 | 12578.0087 | 13425.7459 | 7417.7467 | 7417.4564 | 7514.4144 | 7620.7707 | 7838.8952 | 7995.6039 | 8080.8017 | 8174.1344 | 8259.4216 | 8413.2025 | 8603.9714 | 8591.0785 | 8591.0785 | 8591.0785 | 8591.0785 | 8591.0785 | 8591.0785 | 8591.0785 | 8591.0785 | 8591.0785 | 8591.0785 | 8591.0785 | 8591.0785 | 8591.0785 | 8591.0785 | 8591.0785 | 8591.0785 |  | 2043.3291 | 2647.0078 | 2805.083 | 1637.3174 | 1638.1066 | 1654.3809 | 1697.2252 | 1725.9517 | 1754.0498 | 1786.902 | 1817.3742 | 1846.9343 | 1850.3589 | 1884.8505 | 1858.8017 | 1858.8017 | 1858.8017 | 1858.8017 | 1858.8017 | 1858.8017 | 1858.8017 | 1858.8017 | 1858.8017 | 1858.8017 | 1858.8017 | 1858.8017 | 1858.8017 | 1858.8017 | 1858.8017 | 1858.8017
55% | 10703.6666 | 14222.8031 | 15181.3967 | 8387.7466 | 8387.4184 | 8497.0553 | 8617.3196 | 8863.9677 | 9041.1688 | 9137.5077 | 9243.0452 | 9339.4853 | 9513.3757 | 9729.091 | 9714.5121 | 9714.5121 | 9714.5121 | 9714.5121 | 9714.5121 | 9714.5121 | 9714.5121 | 9714.5121 | 9714.5121 | 9714.5121 | 9714.5121 | 9714.5121 | 9714.5121 | 9714.5121 | 9714.5121 | 9714.5121 |  | 3926.5772 | 5086.6405 | 5390.4069 | 3146.362 | 3147.8787 | 3179.1524 | 3261.4843 | 3316.6869 | 3370.6816 | 3433.8123 | 3492.3696 | 3549.1739 | 3555.7547 | 3622.0357 | 3571.979 | 3571.979 | 3571.979 | 3571.979 | 3571.979 | 3571.979 | 3571.979 | 3571.979 | 3571.979 | 3571.979 | 3571.979 | 3571.979 | 3571.979 | 3571.979 | 3571.979 | 3571.979
50% | 13744.0128 | 18262.75 | 19493.6294 | 10770.2623 | 10769.8409 | 10910.6198 | 11065.0449 | 11381.7526 | 11609.2872 | 11732.9909 | 11868.5061 | 11992.3396 | 12215.6231 | 12492.6117 | 12473.8917 | 12473.8917 | 12473.8917 | 12473.8917 | 12473.8917 | 12473.8917 | 12473.8917 | 12473.8917 | 12473.8917 | 12473.8917 | 12473.8917 | 12473.8917 | 12473.8917 | 12473.8917 | 12473.8917 | 12473.8917 |  | 8714.0125 | 11288.47 | 11962.6002 | 6982.5288 | 6985.8946 | 7055.2983 | 7238.0126 | 7360.5203 | 7480.3476 | 7620.4495 | 7750.4022 | 7876.4645 | 7891.0688 | 8038.1623 | 7927.0744 | 7927.0744 | 7927.0744 | 7927.0744 | 7927.0744 | 7927.0744 | 7927.0744 | 7927.0744 | 7927.0744 | 7927.0744 | 7927.0744 | 7927.0744 | 7927.0744 | 7927.0744 | 7927.0744 | 7927.0744
45% | 18302.3635 | 24319.7888 | 25958.9027 | 14342.3364 | 14341.7752 | 14529.2451 | 14734.8868 | 15156.6342 | 15459.633 | 15624.3644 | 15804.8246 | 15969.7289 | 16267.0668 | 16635.9217 | 16610.993 | 16610.993 | 16610.993 | 16610.993 | 16610.993 | 16610.993 | 16610.993 | 16610.993 | 16610.993 | 16610.993 | 16610.993 | 16610.993 | 16610.993 | 16610.993 | 16610.993 | 16610.993 |  | 13204.5002 | 17105.6219 | 18127.1435 | 10580.7517 | 10585.8519 | 10691.0207 | 10967.891 | 11153.529 | 11335.1054 | 11547.4045 | 11744.324 | 11935.3485 | 11957.4788 | 12180.3721 | 12012.0387 | 12012.0387 | 12012.0387 | 12012.0387 | 12012.0387 | 12012.0387 | 12012.0387 | 12012.0387 | 12012.0387 | 12012.0387 | 12012.0387 | 12012.0387 | 12012.0387 | 12012.0387 | 12012.0387 | 12012.0387
40% | 12836.6798 | 17057.1053 | 18206.7263 | 10059.2462 | 10058.8526 | 10190.3378 | 10334.5682 | 10630.368 | 10842.8815 | 10958.4187 | 11084.9876 | 11200.6461 | 11409.1892 | 11667.892 | 11650.4078 | 11650.4078 | 11650.4078 | 11650.4078 | 11650.4078 | 11650.4078 | 11650.4078 | 11650.4078 | 11650.4078 | 11650.4078 | 11650.4078 | 11650.4078 | 11650.4078 | 11650.4078 | 11650.4078 | 11650.4078 |  | 13672.6523 | 17712.0843 | 18769.8229 | 10955.8814 | 10961.1625 | 11070.0599 | 11356.7463 | 11548.966 | 11736.98 | 11956.8059 | 12160.707 | 12358.5041 | 12381.419 | 12612.2148 | 12437.9133 | 12437.9133 | 12437.9133 | 12437.9133 | 12437.9133 | 12437.9133 | 12437.9133 | 12437.9133 | 12437.9133 | 12437.9133 | 12437.9133 | 12437.9133 | 12437.9133 | 12437.9133 | 12437.9133 | 12437.9133
35% | 6655.3655 | 8843.5072 | 9439.545 | 5215.3642 | 5215.1601 | 5283.3305 | 5358.1089 | 5511.4707 | 5621.6514 | 5681.5534 | 5747.1749 | 5807.1397 | 5915.262 | 6049.3902 | 6040.3253 | 6040.3253 | 6040.3253 | 6040.3253 | 6040.3253 | 6040.3253 | 6040.3253 | 6040.3253 | 6040.3253 | 6040.3253 | 6040.3253 | 6040.3253 | 6040.3253 | 6040.3253 | 6040.3253 | 6040.3253 |  | 18622.1031 | 24123.7949 | 25564.4311 | 14921.8709 | 14929.0638 | 15077.3816 | 15467.8475 | 15729.65 | 15985.7245 | 16285.1265 | 16562.8391 | 16832.2381 | 16863.448 | 17177.791 | 16940.393 | 16940.393 | 16940.393 | 16940.393 | 16940.393 | 16940.393 | 16940.393 | 16940.393 | 16940.393 | 16940.393 | 16940.393 | 16940.393 | 16940.393 | 16940.393 | 16940.393 | 16940.393
30% | 3095.428 | 4113.1385 | 4390.3573 | 2425.6796 | 2425.5847 | 2457.291 | 2492.0706 | 2563.3996 | 2614.6449 | 2642.5055 | 2673.0262 | 2700.916 | 2751.204 | 2813.5874 | 2809.3712 | 2809.3712 | 2809.3712 | 2809.3712 | 2809.3712 | 2809.3712 | 2809.3712 | 2809.3712 | 2809.3712 | 2809.3712 | 2809.3712 | 2809.3712 | 2809.3712 | 2809.3712 | 2809.3712 | 2809.3712 |  | 17207.9743 | 22291.8776 | 23623.1145 | 13788.7311 | 13795.3777 | 13932.4326 | 14293.2472 | 14535.1688 | 14771.7975 | 15048.4635 | 15305.0871 | 15554.0284 | 15582.8683 | 15873.3407 | 15653.9702 | 15653.9702 | 15653.9702 | 15653.9702 | 15653.9702 | 15653.9702 | 15653.9702 | 15653.9702 | 15653.9702 | 15653.9702 | 15653.9702 | 15653.9702 | 15653.9702 | 15653.9702 | 15653.9702 | 15653.9702
25% | 2113.496 | 2808.3682 | 2997.6476 | 1656.2053 | 1656.1404 | 1677.7888 | 1701.5357 | 1750.2376 | 1785.2269 | 1804.2496 | 1825.0885 | 1844.1311 | 1878.4667 | 1921.0608 | 1918.1822 | 1918.1822 | 1918.1822 | 1918.1822 | 1918.1822 | 1918.1822 | 1918.1822 | 1918.1822 | 1918.1822 | 1918.1822 | 1918.1822 | 1918.1822 | 1918.1822 | 1918.1822 | 1918.1822 | 1918.1822 |  | 4963.476 | 6429.8794 | 6813.862 | 3977.2279 | 3979.1451 | 4018.6773 | 4122.7508 | 4192.5308 | 4260.7841 | 4340.5857 | 4414.6064 | 4486.4111 | 4494.7297 | 4578.5137 | 4515.2384 | 4515.2384 | 4515.2384 | 4515.2384 | 4515.2384 | 4515.2384 | 4515.2384 | 4515.2384 | 4515.2384 | 4515.2384 | 4515.2384 | 4515.2384 | 4515.2384 | 4515.2384 | 4515.2384 | 4515.2384
20% | 1280.3284 | 1701.2729 | 1815.9359 | 1003.3076 | 1003.2683 | 1016.3826 | 1030.7682 | 1060.2712 | 1081.4673 | 1092.9909 | 1105.6149 | 1117.1506 | 1137.9507 | 1163.7537 | 1162.0098 | 1162.0098 | 1162.0098 | 1162.0098 | 1162.0098 | 1162.0098 | 1162.0098 | 1162.0098 | 1162.0098 | 1162.0098 | 1162.0098 | 1162.0098 | 1162.0098 | 1162.0098 | 1162.0098 | 1162.0098 |  | 1331.912 | 1725.4105 | 1828.4494 | 1067.2596 | 1067.7741 | 1078.3823 | 1106.3096 | 1125.0346 | 1143.3498 | 1164.764 | 1184.6269 | 1203.8952 | 1206.1274 | 1228.6102 | 1211.6308 | 1211.6308 | 1211.6308 | 1211.6308 | 1211.6308 | 1211.6308 | 1211.6308 | 1211.6308 | 1211.6308 | 1211.6308 | 1211.6308 | 1211.6308 | 1211.6308 | 1211.6308 | 1211.6308 | 1211.6308
15% | 819.7224 | 1089.2296 | 1162.6419 | 642.3616 | 642.3364 | 650.7328 | 659.943 | 678.8322 | 692.4028 | 699.7808 | 707.8632 | 715.2489 | 728.566 | 745.0862 | 743.9697 | 743.9697 | 743.9697 | 743.9697 | 743.9697 | 743.9697 | 743.9697 | 743.9697 | 743.9697 | 743.9697 | 743.9697 | 743.9697 | 743.9697 | 743.9697 | 743.9697 | 743.9697 |  | 734.6312 | 951.6698 | 1008.502 | 588.6592 | 588.9429 | 594.794 | 610.1976 | 620.5256 | 630.6276 | 642.4388 | 653.3944 | 664.0221 | 665.2533 | 677.6539 | 668.2887 | 668.2887 | 668.2887 | 668.2887 | 668.2887 | 668.2887 | 668.2887 | 668.2887 | 668.2887 | 668.2887 | 668.2887 | 668.2887 | 668.2887 | 668.2887 | 668.2887 | 668.2887
10% | 548.6502 | 729.0346 | 778.1704 | 429.9404 | 429.9236 | 435.5434 | 441.7079 | 454.3506 | 463.4336 | 468.3718 | 473.7814 | 478.7248 | 487.6381 | 498.6953 | 497.948 | 497.948 | 497.948 | 497.948 | 497.948 | 497.948 | 497.948 | 497.948 | 497.948 | 497.948 | 497.948 | 497.948 | 497.948 | 497.948 | 497.948 | 497.948 |  | 171.688 | 222.4113 | 235.6934 | 137.5734 | 137.6397 | 139.0072 | 142.6071 | 145.0208 | 147.3817 | 150.1421 | 152.7025 | 155.1862 | 155.4739 | 158.3721 | 156.1833 | 156.1833 | 156.1833 | 156.1833 | 156.1833 | 156.1833 | 156.1833 | 156.1833 | 156.1833 | 156.1833 | 156.1833 | 156.1833 | 156.1833 | 156.1833 | 156.1833 | 156.1833
5% | 390.344 | 518.6808 | 553.639 | 305.8865 | 305.8745 | 309.8728 | 314.2586 | 323.2534 | 329.7156 | 333.2289 | 337.0777 | 340.5947 | 346.9362 | 354.8029 | 354.2713 | 354.2713 | 354.2713 | 354.2713 | 354.2713 | 354.2713 | 354.2713 | 354.2713 | 354.2713 | 354.2713 | 354.2713 | 354.2713 | 354.2713 | 354.2713 | 354.2713 | 354.2713 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9.992e-14% | 34.2635 | 45.5286 | 48.5972 | 26.85 | 26.849 | 27.1999 | 27.5849 | 28.3745 | 28.9417 | 29.2501 | 29.5879 | 29.8966 | 30.4533 | 31.1438 | 31.0971 | 31.0971 | 31.0971 | 31.0971 | 31.0971 | 31.0971 | 31.0971 | 31.0971 | 31.0971 | 31.0971 | 31.0971 | 31.0971 | 31.0971 | 31.0971 | 31.0971 | 31.0971 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E @ R (MWh) | 91763.8061 | 121933.7811 | 130151.918 | 71909.1488 | 71906.3352 | 72846.2653 | 73877.3055 | 75991.8488 | 77511.0147 | 78336.9396 | 79241.7254 | 80068.5172 | 81559.3006 | 83408.6533 | 83283.6669 | 83283.6669 | 83283.6669 | 83283.6669 | 83283.6669 | 83283.6669 | 83283.6669 | 83283.6669 | 83283.6669 | 83283.6669 | 83283.6669 | 83283.6669 | 83283.6669 | 83283.6669 | 83283.6669 | 83283.6669 | E @ R (MWh) | 89067.5772 | 115381.5956 | 122272.0083 | 71369.7528 | 71404.1554 | 72113.5443 | 73981.1019 | 75233.2756 | 76458.0532 | 77890.0621 | 79218.3324 | 80506.8395 | 80656.1133 | 82159.5832 | 81024.1335 | 81024.1335 | 81024.1335 | 81024.1335 | 81024.1335 | 81024.1335 | 81024.1335 | 81024.1335 | 81024.1335 | 81024.1335 | 81024.1335 | 81024.1335 | 81024.1335 | 81024.1335 | 81024.1335 | 81024.1335
Option 2 Summer POE50 W E @ R (MWh) N 2 | 64234.6643 | 85353.6468 | 91106.3426 | 50336.4042 | 50334.4346 | 50992.3857 | 51714.1138 | 53194.2942 | 54257.7103 | 54835.8577 | 55469.2078 | 56047.962 | 57091.5104 | 58386.0573 | 58298.5668 | 58298.5668 | 58298.5668 | 58298.5668 | 58298.5668 | 58298.5668 | 58298.5668 | 58298.5668 | 58298.5668 | 58298.5668 | 58298.5668 | 58298.5668 | 58298.5668 | 58298.5668 | 58298.5668 | 58298.5668 | Option 2 Summer POE10 W E @ R (MWh) N 2 | 26720.2732 | 34614.4787 | 36681.6025 | 21410.9258 | 21421.2466 | 21634.0633 | 22194.3306 | 22569.9827 | 22937.416 | 23367.0186 | 23765.4997 | 24152.0518 | 24196.834 | 24647.875 | 24307.24 | 24307.24 | 24307.24 | 24307.24 | 24307.24 | 24307.24 | 24307.24 | 24307.24 | 24307.24 | 24307.24 | 24307.24 | 24307.24 | 24307.24 | 24307.24 | 24307.24 | 24307.24
Option 3 - 2A PHM 3rd Tx + Switchroom + Three new feeders + OFR12 New Feeder
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | 59.6718 | 82.8348 | 88.8563 | 23.0131 | 23.8136 | 25.192 | 28.3279 | 30.427 | 33.0862 | 34.4665 | 35.6808 | 33.4434 | 36.0656 | 40.188 | 37.0597 | 37.0597 | 37.0597 | 37.0597 | 37.0597 | 37.0597 | 37.0597 | 37.0597 | 37.0597 | 37.0597 | 37.0597 | 37.0597 | 37.0597 | 37.0597 | 37.0597 | 37.0597 |  | 63.8857 | 86.7566 | 93.0131 | 27.1115 | 27.7262 | 29.0747 | 32.2596 | 33.9985 | 37.311 | 47.3802 | 39.0792 | 37.4555 | 39.6472 | 44.4406 | 41.196 | 41.196 | 41.196 | 41.196 | 41.196 | 41.196 | 41.196 | 41.196 | 41.196 | 41.196 | 41.196 | 41.196 | 41.196 | 41.196 | 41.196 | 41.196
98% | 70.8865 | 98.4027 | 105.556 | 26.5317 | 27.4827 | 29.1201 | 32.8453 | 35.339 | 38.4979 | 40.1377 | 41.5802 | 38.9223 | 42.0373 | 46.9344 | 43.2182 | 43.2182 | 43.2182 | 43.2182 | 43.2182 | 43.2182 | 43.2182 | 43.2182 | 43.2182 | 43.2182 | 43.2182 | 43.2182 | 43.2182 | 43.2182 | 43.2182 | 43.2182 |  | 75.8924 | 103.0616 | 110.494 | 31.4004 | 32.1306 | 33.7325 | 37.516 | 39.5816 | 43.5167 | 55.4783 | 45.6172 | 43.6884 | 46.2921 | 51.9863 | 48.1319 | 48.1319 | 48.1319 | 48.1319 | 48.1319 | 48.1319 | 48.1319 | 48.1319 | 48.1319 | 48.1319 | 48.1319 | 48.1319 | 48.1319 | 48.1319 | 48.1319 | 48.1319
97% | 140.3338 | 194.8074 | 208.9687 | 50.8953 | 52.778 | 56.0196 | 63.3944 | 68.331 | 74.5849 | 77.831 | 80.6868 | 75.4249 | 81.5917 | 91.2865 | 83.9295 | 83.9295 | 83.9295 | 83.9295 | 83.9295 | 83.9295 | 83.9295 | 83.9295 | 83.9295 | 83.9295 | 83.9295 | 83.9295 | 83.9295 | 83.9295 | 83.9295 | 83.9295 |  | 150.2438 | 204.0305 | 218.7445 | 60.5339 | 61.9795 | 65.1508 | 72.6409 | 76.7303 | 84.5206 | 108.2009 | 88.6789 | 84.8604 | 90.0149 | 101.2877 | 93.6573 | 93.6573 | 93.6573 | 93.6573 | 93.6573 | 93.6573 | 93.6573 | 93.6573 | 93.6573 | 93.6573 | 93.6573 | 93.6573 | 93.6573 | 93.6573 | 93.6573 | 93.6573
95% | 414.5243 | 575.4311 | 617.2612 | 142.9299 | 148.491 | 158.0661 | 179.8503 | 194.4323 | 212.9052 | 222.4938 | 230.9293 | 215.3866 | 233.6022 | 262.2393 | 240.5077 | 240.5077 | 240.5077 | 240.5077 | 240.5077 | 240.5077 | 240.5077 | 240.5077 | 240.5077 | 240.5077 | 240.5077 | 240.5077 | 240.5077 | 240.5077 | 240.5077 | 240.5077 |  | 443.7972 | 602.6746 | 646.1375 | 171.4008 | 175.6708 | 185.0382 | 207.1629 | 219.2424 | 242.2537 | 312.2017 | 254.5367 | 243.2574 | 258.483 | 291.781 | 269.2421 | 269.2421 | 269.2421 | 269.2421 | 269.2421 | 269.2421 | 269.2421 | 269.2421 | 269.2421 | 269.2421 | 269.2421 | 269.2421 | 269.2421 | 269.2421 | 269.2421 | 269.2421
90% | 2285.5212 | 3172.6969 | 3403.3313 | 687.6144 | 718.2763 | 771.0693 | 891.1785 | 971.578 | 1073.4303 | 1126.2977 | 1172.8081 | 1087.1114 | 1187.5452 | 1345.4387 | 1225.6194 | 1225.6194 | 1225.6194 | 1225.6194 | 1225.6194 | 1225.6194 | 1225.6194 | 1225.6194 | 1225.6194 | 1225.6194 | 1225.6194 | 1225.6194 | 1225.6194 | 1225.6194 | 1225.6194 | 1225.6194 |  | 2446.9201 | 3322.9067 | 3562.5435 | 844.5915 | 868.1346 | 919.783 | 1041.7693 | 1108.3709 | 1235.246 | 1620.9111 | 1302.9695 | 1240.7798 | 1324.7279 | 1508.32 | 1384.049 | 1384.049 | 1384.049 | 1384.049 | 1384.049 | 1384.049 | 1384.049 | 1384.049 | 1384.049 | 1384.049 | 1384.049 | 1384.049 | 1384.049 | 1384.049 | 1384.049 | 1384.049
85% | 5583.3646 | 7750.6712 | 8314.0946 | 1295.2018 | 1370.1065 | 1499.0762 | 1792.4944 | 1988.9045 | 2237.7224 | 2366.8736 | 2480.4952 | 2271.1443 | 2516.4968 | 2902.2195 | 2609.5095 | 2609.5095 | 2609.5095 | 2609.5095 | 2609.5095 | 2609.5095 | 2609.5095 | 2609.5095 | 2609.5095 | 2609.5095 | 2609.5095 | 2609.5095 | 2609.5095 | 2609.5095 | 2609.5095 | 2609.5095 |  | 5977.6505 | 8117.623 | 8703.0385 | 1678.6856 | 1736.1996 | 1862.3729 | 2160.3768 | 2323.0798 | 2633.0266 | 3575.1786 | 2798.4702 | 2646.5452 | 2851.6243 | 3300.1267 | 2996.5417 | 2996.5417 | 2996.5417 | 2996.5417 | 2996.5417 | 2996.5417 | 2996.5417 | 2996.5417 | 2996.5417 | 2996.5417 | 2996.5417 | 2996.5417 | 2996.5417 | 2996.5417 | 2996.5417 | 2996.5417
80% | 8678.2039 | 12046.8408 | 12922.5678 | 1342.9024 | 1459.3265 | 1659.7836 | 2115.8425 | 2421.1221 | 2807.8589 | 3008.5981 | 3185.1997 | 2859.8064 | 3241.1569 | 3840.6843 | 3385.7262 | 3385.7262 | 3385.7262 | 3385.7262 | 3385.7262 | 3385.7262 | 3385.7262 | 3385.7262 | 3385.7262 | 3385.7262 | 3385.7262 | 3385.7262 | 3385.7262 | 3385.7262 | 3385.7262 | 3385.7262 |  | 9291.041 | 12617.1926 | 13527.1019 | 1938.9499 | 2028.3437 | 2224.4544 | 2687.6409 | 2940.5296 | 3422.2787 | 4886.6623 | 3679.4272 | 3443.2907 | 3762.0443 | 4459.1501 | 3987.2889 | 3987.2889 | 3987.2889 | 3987.2889 | 3987.2889 | 3987.2889 | 3987.2889 | 3987.2889 | 3987.2889 | 3987.2889 | 3987.2889 | 3987.2889 | 3987.2889 | 3987.2889 | 3987.2889 | 3987.2889
75% | 9574.4808 | 13291.0275 | 14257.1987 | 646.7384 | 775.1867 | 996.3469 | 1499.5071 | 1836.3156 | 2262.9943 | 2484.4657 | 2679.3065 | 2320.3068 | 2741.0429 | 3402.4889 | 2900.5432 | 2900.5432 | 2900.5432 | 2900.5432 | 2900.5432 | 2900.5432 | 2900.5432 | 2900.5432 | 2900.5432 | 2900.5432 | 2900.5432 | 2900.5432 | 2900.5432 | 2900.5432 | 2900.5432 | 2900.5432 |  | 10250.6112 | 13920.2847 | 14924.1686 | 1304.3452 | 1402.9715 | 1619.3363 | 2130.3603 | 2409.3671 | 2940.8708 | 4556.4946 | 3224.5773 | 2964.0529 | 3315.7271 | 4084.8293 | 3564.2347 | 3564.2347 | 3564.2347 | 3564.2347 | 3564.2347 | 3564.2347 | 3564.2347 | 3564.2347 | 3564.2347 | 3564.2347 | 3564.2347 | 3564.2347 | 3564.2347 | 3564.2347 | 3564.2347 | 3564.2347
70% | 10287.2444 | 14280.4661 | 15318.563 | 20.3356 | 57.2151 | 162.8454 | 590.4033 | 952.2853 | 1410.7277 | 1648.6863 | 1858.0319 | 1472.3068 | 1924.3642 | 2635.0509 | 2095.7384 | 2095.7384 | 2095.7384 | 2095.7384 | 2095.7384 | 2095.7384 | 2095.7384 | 2095.7384 | 2095.7384 | 2095.7384 | 2095.7384 | 2095.7384 | 2095.7384 | 2095.7384 | 2095.7384 | 2095.7384 |  | 11013.7087 | 14956.5677 | 16035.1849 | 394.8873 | 489.2265 | 719.1532 | 1268.2198 | 1567.9971 | 2139.0681 | 3874.9655 | 2443.8949 | 2163.976 | 2541.8303 | 3368.1876 | 2808.8378 | 2808.8378 | 2808.8378 | 2808.8378 | 2808.8378 | 2808.8378 | 2808.8378 | 2808.8378 | 2808.8378 | 2808.8378 | 2808.8378 | 2808.8378 | 2808.8378 | 2808.8378 | 2808.8378 | 2808.8378
65% | 10840.7831 | 15048.8731 | 16142.8282 |  |  |  | 0.29965 | 68.3879 | 317.4877 | 514.195 | 722.9957 | 364.1065 | 792.8973 | 1541.8248 | 973.4927 | 973.4927 | 973.4927 | 973.4927 | 973.4927 | 973.4927 | 973.4927 | 973.4927 | 973.4927 | 973.4927 | 973.4927 | 973.4927 | 973.4927 | 973.4927 | 973.4927 | 973.4927 |  | 11606.3372 | 15761.3546 | 16898.0103 |  |  | 10.9834 | 221.3321 | 442.5144 | 1019.154 | 2848.457 | 1340.383 | 1045.4021 | 1443.5881 | 2314.4103 | 1724.9628 | 1724.9628 | 1724.9628 | 1724.9628 | 1724.9628 | 1724.9628 | 1724.9628 | 1724.9628 | 1724.9628 | 1724.9628 | 1724.9628 | 1724.9628 | 1724.9628 | 1724.9628 | 1724.9628 | 1724.9628
60% | 11934.3669 | 16566.9557 | 17771.2656 | [7 empty] | 0.46825 |  | 4.3158 | 278.4473 | 31.955 | 31.955 | 31.955 | 31.955 | 31.955 | 31.955 | 31.955 | 31.955 | 31.955 | 31.955 | 31.955 | 31.955 | 31.955 | 31.955 | 31.955 | 31.955 |  | 12777.1477 | 17351.3101 | 18602.628 | [5 empty] | 42.9218 | 1558.6668 | 164.1701 | 49.9432 | 219.1162 | 970.7471 | 407.0032 | 407.0032 | 407.0032 | 407.0032 | 407.0032 | 407.0032 | 407.0032 | 407.0032 | 407.0032 | 407.0032 | 407.0032 | 407.0032 | 407.0032 | 407.0032 | 407.0032 | 407.0032
55% | FY25: 13276.2336; FY26: 18429.6976; FY27: 19769.4166 |  | 14213.7742 | 19302.2426 | 20694.2551 | [6 empty] | 137.453 |  |  |  | 2.187
50% | FY25: 13456.7484; FY26: 18680.2832; FY27: 20038.2182 |  | 14407.0366 | 19564.692 | 20975.6315
45% | FY25: 10386.1977; FY26: 14417.8303; FY27: 15465.9127 |  | 11119.6499 | 15100.4354 | 16189.4278
40% | FY25: 5102.6915; FY26: 7083.4142; FY27: 7598.3323 |  | 5463.0332 | 7418.775 | 7953.792
35% | FY25: 1907.0998; FY26: 2647.3829; FY27: 2839.8304 |  | 2041.7754 | 2772.7219 | 2972.6813
30% | FY25: 951.1511; FY26: 1320.3614; FY27: 1416.3431 |  | 1018.3194 | 1382.8733 | 1482.6014
25% | FY25: 560.7353; FY26: 778.3972; FY27: 834.9816 |  | 600.3333 | 815.25 | 874.0431
20% | FY25: 283.3663; FY26: 393.3611; FY27: 421.9559 |  | 303.377 | 411.9846 | 441.6956
15% | FY25: 115.4455; FY26: 160.2582; FY27: 171.908 |  | 123.598 | 167.8456 | 179.95
10% | FY25: 46.4781; FY26: 64.5196; FY27: 69.2097 |  | 49.7602 | 67.5742 | 72.4474
5% | FY25: 39.5813; FY26: 54.9457; FY27: 58.9399 |  | 42.3765 | 57.5471 | 61.6972
9.992e-14% | FY25: 0; FY26: 0; FY27: 0 |  | 0 | 0 | 0
E @ R (MWh) | 105995.1099 | 147139.4588 | 157835.5397 | 4236.1627 | 4632.6765 | 5357.5192 | 7194.1433 | 8567.1227 | 10469.2957 | 11524.0454 | 12488.1823 | 10737.9594 | 12801.116 | 16386.8026 | 13627.2995 | 13627.2995 | 13627.2995 | 13627.2995 | 13627.2995 | 13627.2995 | 13627.2995 | 13627.2995 | 13627.2995 | 13627.2995 | 13627.2995 | 13627.2995 | 13627.2995 | 13627.2995 | 13627.2995 | 13627.2995 | E @ R (MWh) | 113480.2695 | 154105.704 | 165219.287 | 6451.9061 | 6822.3831 | 7669.0794 | 9859.2785 | 11161.4117 | 13840.1679 | 23582.05 | 15381.8041 | 13963.2515 | 15893.0952 | 20497.4537 | 17325.1454 | 17325.1454 | 17325.1454 | 17325.1454 | 17325.1454 | 17325.1454 | 17325.1454 | 17325.1454 | 17325.1454 | 17325.1454 | 17325.1454 | 17325.1454 | 17325.1454 | 17325.1454 | 17325.1454 | 17325.1454
Option 3 Winter POE50 W E @ R (MWh) N 2 | 74196.5769 | 102997.6211 | 110484.8778 | 2965.3139 | 3242.8735 | 3750.2634 | 5035.9003 | 5996.9859 | 7328.507 | 8066.8318 | 8741.7276 | 7516.5716 | 8960.7812 | 11470.7618 | 9539.1096 | 9539.1096 | 9539.1096 | 9539.1096 | 9539.1096 | 9539.1096 | 9539.1096 | 9539.1096 | 9539.1096 | 9539.1096 | 9539.1096 | 9539.1096 | 9539.1096 | 9539.1096 | 9539.1096 | 9539.1096 | Option 3 Winter POE10 W E @ R (MWh) N 2 | 34044.0809 | 46231.7112 | 49565.7861 | 1935.5718 | 2046.7149 | 2300.7238 | 2957.7835 | 3348.4235 | 4152.0504 | 7074.615 | 4614.5412 | 4188.9754 | 4767.9286 | 6149.2361 | 5197.5436 | 5197.5436 | 5197.5436 | 5197.5436 | 5197.5436 | 5197.5436 | 5197.5436 | 5197.5436 | 5197.5436 | 5197.5436 | 5197.5436 | 5197.5436 | 5197.5436 | 5197.5436 | 5197.5436 | 5197.5436
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 76.9936 | 99.7405 | 105.6969 | 37.273 | 37.3028 | 37.916 | 39.5304 | 40.6128 | 41.6716 | 42.9095 | 44.0577 | 45.1715 | 45.3005 | 46.6002 | 45.6187 | 45.6187 | 45.6187 | 45.6187 | 45.6187 | 45.6187 | 45.6187 | 45.6187 | 45.6187 | 45.6187 | 45.6187 | 45.6187 | 45.6187 | 45.6187 | 45.6187 | 45.6187
98% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 38.1099 | 49.369 | 52.3173 | 18.1072 | 18.1219 | 18.4254 | 19.2245 | 19.7603 | 20.2843 | 20.897 | 21.4654 | 22.0167 | 22.0806 | 22.7239 | 22.238 | 22.238 | 22.238 | 22.238 | 22.238 | 22.238 | 22.238 | 22.238 | 22.238 | 22.238 | 22.238 | 22.238 | 22.238 | 22.238 | 22.238 | 22.238
97% | 16.9149 | 22.4762 | 23.991 | 6.9303 | 6.9298 | 7.103 | 7.2931 | 7.6829 | 7.9629 | 8.1151 | 8.2819 | 8.4343 | 8.7091 | 9.05 | 9.027 | 9.027 | 9.027 | 9.027 | 9.027 | 9.027 | 9.027 | 9.027 | 9.027 | 9.027 | 9.027 | 9.027 | 9.027 | 9.027 | 9.027 | 9.027 |  | 75.446 | 97.7357 | 103.5723 | 35.1556 | 35.1847 | 35.7856 | 37.3676 | 38.4283 | 39.4657 | 40.6787 | 41.8039 | 42.8953 | 43.0218 | 44.2953 | 43.3335 | 43.3335 | 43.3335 | 43.3335 | 43.3335 | 43.3335 | 43.3335 | 43.3335 | 43.3335 | 43.3335 | 43.3335 | 43.3335 | 43.3335 | 43.3335 | 43.3335 | 43.3335
95% | 83.2734 | 110.6519 | 118.1097 | 32.8093 | 32.8067 | 33.6597 | 34.5953 | 36.5142 | 37.8928 | 38.6423 | 39.4634 | 40.2137 | 41.5666 | 43.2448 | 43.1314 | 43.1314 | 43.1314 | 43.1314 | 43.1314 | 43.1314 | 43.1314 | 43.1314 | 43.1314 | 43.1314 | 43.1314 | 43.1314 | 43.1314 | 43.1314 | 43.1314 | 43.1314 |  | 111.4279 | 144.3481 | 152.9683 | 50.3513 | 50.3943 | 51.2818 | 53.6182 | 55.1847 | 56.717 | 58.5085 | 60.1702 | 61.7822 | 61.969 | 63.8499 | 62.4294 | 62.4294 | 62.4294 | 62.4294 | 62.4294 | 62.4294 | 62.4294 | 62.4294 | 62.4294 | 62.4294 | 62.4294 | 62.4294 | 62.4294 | 62.4294 | 62.4294 | 62.4294
90% | 144.4273 | 191.9119 | 204.8464 | 51.3198 | 51.3153 | 52.7947 | 54.4175 | 57.7455 | 60.1366 | 61.4365 | 62.8605 | 64.1618 | 66.5082 | 69.4189 | 69.2222 | 69.2222 | 69.2222 | 69.2222 | 69.2222 | 69.2222 | 69.2222 | 69.2222 | 69.2222 | 69.2222 | 69.2222 | 69.2222 | 69.2222 | 69.2222 | 69.2222 | 69.2222 |  | 483.1446 | 625.8842 | 663.261 | 201.5685 | 201.7552 | 205.6032 | 215.7337 | 222.5261 | 229.1699 | 236.9378 | 244.1429 | 251.1324 | 251.9421 | 260.0977 | 253.9385 | 253.9385 | 253.9385 | 253.9385 | 253.9385 | 253.9385 | 253.9385 | 253.9385 | 253.9385 | 253.9385 | 253.9385 | 253.9385 | 253.9385 | 253.9385 | 253.9385 | 253.9385
85% | 409.8612 | 544.6148 | 581.321 | 120.801 | 120.7884 | 124.9866 | 129.5917 | 139.0363 | 145.8216 | 149.5106 | 153.5518 | 157.2446 | 163.9032 | 172.1633 | 171.605 | 171.605 | 171.605 | 171.605 | 171.605 | 171.605 | 171.605 | 171.605 | 171.605 | 171.605 | 171.605 | 171.605 | 171.605 | 171.605 | 171.605 | 171.605 |  | 457.0286 | 592.0526 | 627.4091 | 165.8367 | 166.0133 | 169.6533 | 179.2362 | 185.6615 | 191.9461 | 199.2941 | 206.1098 | 212.7215 | 213.4874 | 221.2021 | 215.3759 | 215.3759 | 215.3759 | 215.3759 | 215.3759 | 215.3759 | 215.3759 | 215.3759 | 215.3759 | 215.3759 | 215.3759 | 215.3759 | 215.3759 | 215.3759 | 215.3759 | 215.3759
80% | 572.5046 | 760.7318 | 812.0039 | 129.841 | 129.8234 | 135.6876 | 142.1201 | 155.3125 | 164.7904 | 169.9433 | 175.5881 | 180.7464 | 190.0472 | 201.5852 | 200.8054 | 200.8054 | 200.8054 | 200.8054 | 200.8054 | 200.8054 | 200.8054 | 200.8054 | 200.8054 | 200.8054 | 200.8054 | 200.8054 | 200.8054 | 200.8054 | 200.8054 | 200.8054 |  | 319.1946 | 413.4971 | 438.1905 | 96.374 | 96.4973 | 99.0396 | 105.7324 | 110.2199 | 114.6092 | 119.7411 | 124.5013 | 129.1189 | 129.6539 | 135.0419 | 130.9728 | 130.9728 | 130.9728 | 130.9728 | 130.9728 | 130.9728 | 130.9728 | 130.9728 | 130.9728 | 130.9728 | 130.9728 | 130.9728 | 130.9728 | 130.9728 | 130.9728 | 130.9728
75% | 1492.4153 | 1983.0895 | 2116.7465 | 223.9912 | 223.9454 | 239.2321 | 256.0006 | 290.3908 | 315.098 | 328.5306 | 343.2457 | 356.6924 | 380.938 | 411.0152 | 408.9825 | 408.9825 | 408.9825 | 408.9825 | 408.9825 | 408.9825 | 408.9825 | 408.9825 | 408.9825 | 408.9825 | 408.9825 | 408.9825 | 408.9825 | 408.9825 | 408.9825 | 408.9825 |  | 569.714 | 738.0296 | 782.1036 | 132.8215 | 133.0415 | 137.5791 | 149.5248 | 157.5342 | 165.3684 | 174.5281 | 183.0243 | 191.2662 | 192.221 | 201.8378 | 194.575 | 194.575 | 194.575 | 194.575 | 194.575 | 194.575 | 194.575 | 194.575 | 194.575 | 194.575 | 194.575 | 194.575 | 194.575 | 194.575 | 194.575 | 194.575
70% | 2578.4391 | 3426.1747 | 3657.0932 | 161.9198 | 161.8408 | 188.2515 | 217.2224 | 276.6382 | 319.3247 | 342.5321 | 367.9553 | 391.1871 | 433.0761 | 485.0404 | 481.5284 | 481.5284 | 481.5284 | 481.5284 | 481.5284 | 481.5284 | 481.5284 | 481.5284 | 481.5284 | 481.5284 | 481.5284 | 481.5284 | 481.5284 | 481.5284 | 481.5284 | 481.5284 |  | 1037.8661 | 1344.492 | 1424.783 | 160.7208 | 161.1217 | 169.3879 | 191.1497 | 205.7408 | 220.0126 | 236.6991 | 252.1769 | 267.1913 | 268.9307 | 286.45 | 273.2191 | 273.2191 | 273.2191 | 273.2191 | 273.2191 | 273.2191 | 273.2191 | 273.2191 | 273.2191 | 273.2191 | 273.2191 | 273.2191 | 273.2191 | 273.2191 | 273.2191 | 273.2191
65% | 6475.8072 | 8604.914 | 9184.8711 | 6.9591 | 6.9298 | 20.0951 | 42.2143 | 111.9423 | 181.5617 | 226.0382 | 279.9918 | 333.9879 | 438.672 | 569.1816 | 560.3612 | 560.3612 | 560.3612 | 560.3612 | 560.3612 | 560.3612 | 560.3612 | 560.3612 | 560.3612 | 560.3612 | 560.3612 | 560.3612 | 560.3612 | 560.3612 | 560.3612 | 560.3612 |  | 1305.7961 | 1691.5789 | 1792.5974 | 84.8503 | 85.3547 | 95.7548 | 123.1346 | 141.4924 | 159.4485 | 180.4428 | 199.9162 | 218.8067 | 220.9952 | 243.0371 | 226.3906 | 226.3906 | 226.3906 | 226.3906 | 226.3906 | 226.3906 | 226.3906 | 226.3906 | 226.3906 | 226.3906 | 226.3906 | 226.3906 | 226.3906 | 226.3906 | 226.3906 | 226.3906
60% | 9465.8424 | 12578.0087 | 13425.7459 | [9 empty] | 5.9059 | 42.5222 | 39.014 | 39.014 | 39.014 | 39.014 | 39.014 | 39.014 | 39.014 | 39.014 | 39.014 | 39.014 | 39.014 | 39.014 | 39.014 | 39.014 | 39.014 | 39.014 |  | 2043.3291 | 2647.0078 | 2805.083 | 2.2281 | 2.3448 | 5.4041 | 19.2874 | 33.1836 | 50.2166 | 74.3153 | 100.576 | 129.3594 | 132.7839 | 167.2756 | 141.2268 | 141.2268 | 141.2268 | 141.2268 | 141.2268 | 141.2268 | 141.2268 | 141.2268 | 141.2268 | 141.2268 | 141.2268 | 141.2268 | 141.2268 | 141.2268 | 141.2268 | 141.2268
55% | FY25: 10703.6666; FY26: 14222.8031; FY27: 15181.3967 |  | 3926.5772 | 5086.6405 | 5390.4069 | [8 empty] | 0.36348 | 0.67093 | 8.8993 | 1.8255 | 1.8255 | 1.8255 | 1.8255 | 1.8255 | 1.8255 | 1.8255 | 1.8255 | 1.8255 | 1.8255 | 1.8255 | 1.8255 | 1.8255 | 1.8255 | 1.8255 | 1.8255
50% | FY25: 13744.0128; FY26: 18262.75; FY27: 19493.6294 |  | 8714.0125 | 11288.47 | 11962.6002
45% | FY25: 18302.3635; FY26: 24319.7888; FY27: 25958.9027 |  | 13204.5002 | 17105.6219 | 18127.1435
40% | FY25: 12836.6798; FY26: 17057.1053; FY27: 18206.7263 |  | 13672.6523 | 17712.0843 | 18769.8229
35% | FY25: 6655.3655; FY26: 8843.5072; FY27: 9439.545 |  | 18622.1031 | 24123.7949 | 25564.4311
30% | FY25: 3095.428; FY26: 4113.1385; FY27: 4390.3573 |  | 17207.9743 | 22291.8776 | 23623.1145
25% | FY25: 2113.496; FY26: 2808.3682; FY27: 2997.6476 |  | 4963.476 | 6429.8794 | 6813.862
20% | FY25: 1280.3284; FY26: 1701.2729; FY27: 1815.9359 |  | 1331.912 | 1725.4105 | 1828.4494
15% | FY25: 819.7224; FY26: 1089.2296; FY27: 1162.6419 |  | 734.6312 | 951.6698 | 1008.502
10% | FY25: 548.6502; FY26: 729.0346; FY27: 778.1704 |  | 171.688 | 222.4113 | 235.6934
5% | FY25: 390.344; FY26: 518.6808; FY27: 553.639 |  | 0 | 0 | 0
9.992e-14% | FY25: 34.2635; FY26: 45.5286; FY27: 48.5972 |  | 0 | 0 | 0
E @ R (MWh) | 91763.8061 | 121933.7811 | 130151.918 | 734.5714 | 734.3797 | 801.8103 | 883.4549 | 1075.2627 | 1232.5888 | 1324.7487 | 1430.9386 | 1532.6682 | 1729.3262 | 2003.2214 | 1983.6771 | 1983.6771 | 1983.6771 | 1983.6771 | 1983.6771 | 1983.6771 | 1983.6771 | 1983.6771 | 1983.6771 | 1983.6771 | 1983.6771 | 1983.6771 | 1983.6771 | 1983.6771 | 1983.6771 | 1983.6771 | E @ R (MWh) | 89067.5772 | 115381.5956 | 122272.0083 | 985.2871 | 987.1322 | 1025.8309 | 1133.5396 | 1210.3445 | 1288.9099 | 1384.9521 | 1477.9447 | 1571.8256 | 1583.0571 | 1701.3108 | 1611.1437 | 1611.1437 | 1611.1437 | 1611.1437 | 1611.1437 | 1611.1437 | 1611.1437 | 1611.1437 | 1611.1437 | 1611.1437 | 1611.1437 | 1611.1437 | 1611.1437 | 1611.1437 | 1611.1437 | 1611.1437
Option 3 Summer POE50 W E @ R (MWh) N 2 | 64234.6643 | 85353.6468 | 91106.3426 | 514.2 | 514.0658 | 561.2672 | 618.4185 | 752.6839 | 862.8122 | 927.3241 | 1001.657 | 1072.8678 | 1210.5283 | 1402.255 | 1388.5739 | 1388.5739 | 1388.5739 | 1388.5739 | 1388.5739 | 1388.5739 | 1388.5739 | 1388.5739 | 1388.5739 | 1388.5739 | 1388.5739 | 1388.5739 | 1388.5739 | 1388.5739 | 1388.5739 | 1388.5739 | Option 3 Summer POE10 W E @ R (MWh) N 2 | 26720.2732 | 34614.4787 | 36681.6025 | 295.5861 | 296.1396 | 307.7493 | 340.0619 | 363.1034 | 386.673 | 415.4856 | 443.3834 | 471.5477 | 474.9171 | 510.3932 | 483.3431 | 483.3431 | 483.3431 | 483.3431 | 483.3431 | 483.3431 | 483.3431 | 483.3431 | 483.3431 | 483.3431 | 483.3431 | 483.3431 | 483.3431 | 483.3431 | 483.3431 | 483.3431
Option 4 - 3A OFR 3rd Tx + Switchroom + Three new feeders + OFR12 New Feeder
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | 59.6718 | 82.8348 | 88.8563 | 68.4436 | 69.2441 | 70.6225 | 73.7584 | 75.8575 | 78.5167 | 79.897 | 81.1113 | 78.8739 | 81.4961 | 85.6185 | 82.4902 | 82.4902 | 82.4902 | 82.4902 | 82.4902 | 82.4902 | 82.4902 | 82.4902 | 82.4902 | 82.4902 | 82.4902 | 82.4902 | 82.4902 | 82.4902 | 82.4902 | 82.4902 |  | 63.8857 | 86.7566 | 93.0131 | 72.542 | 73.1567 | 74.5052 | 77.6901 | 79.429 | 82.7415 | 92.8107 | 84.5097 | 82.886 | 85.0778 | 89.8711 | 86.6265 | 86.6265 | 86.6265 | 86.6265 | 86.6265 | 86.6265 | 86.6265 | 86.6265 | 86.6265 | 86.6265 | 86.6265 | 86.6265 | 86.6265 | 86.6265 | 86.6265 | 86.6265
98% | 70.8865 | 98.4027 | 105.556 | 81.3069 | 82.2579 | 83.8953 | 87.6205 | 90.1141 | 93.2731 | 94.9128 | 96.3554 | 93.6975 | 96.8125 | 101.7096 | 97.9933 | 97.9933 | 97.9933 | 97.9933 | 97.9933 | 97.9933 | 97.9933 | 97.9933 | 97.9933 | 97.9933 | 97.9933 | 97.9933 | 97.9933 | 97.9933 | 97.9933 | 97.9933 |  | 75.8924 | 103.0616 | 110.494 | 86.1756 | 86.9058 | 88.5077 | 92.2911 | 94.3568 | 98.2919 | 110.2535 | 100.3924 | 98.4636 | 101.0672 | 106.7614 | 102.9071 | 102.9071 | 102.9071 | 102.9071 | 102.9071 | 102.9071 | 102.9071 | 102.9071 | 102.9071 | 102.9071 | 102.9071 | 102.9071 | 102.9071 | 102.9071 | 102.9071 | 102.9071
97% | 140.3338 | 194.8074 | 208.9687 | 160.9628 | 162.8455 | 166.0871 | 173.4619 | 178.3985 | 184.6524 | 187.8985 | 190.7543 | 185.4924 | 191.6592 | 201.354 | 193.997 | 193.997 | 193.997 | 193.997 | 193.997 | 193.997 | 193.997 | 193.997 | 193.997 | 193.997 | 193.997 | 193.997 | 193.997 | 193.997 | 193.997 | 193.997 |  | 150.2438 | 204.0305 | 218.7445 | 170.6014 | 172.047 | 175.2182 | 182.7084 | 186.7978 | 194.5881 | 218.2684 | 198.7464 | 194.9278 | 200.0824 | 211.3551 | 203.7247 | 203.7247 | 203.7247 | 203.7247 | 203.7247 | 203.7247 | 203.7247 | 203.7247 | 203.7247 | 203.7247 | 203.7247 | 203.7247 | 203.7247 | 203.7247 | 203.7247 | 203.7247
95% | 414.5243 | 575.4311 | 617.2612 | 475.4594 | 481.0205 | 490.5956 | 512.3798 | 526.9618 | 545.4347 | 555.0233 | 563.4588 | 547.9161 | 566.1317 | 594.7688 | 573.0372 | 573.0372 | 573.0372 | 573.0372 | 573.0372 | 573.0372 | 573.0372 | 573.0372 | 573.0372 | 573.0372 | 573.0372 | 573.0372 | 573.0372 | 573.0372 | 573.0372 | 573.0372 |  | 443.7972 | 602.6746 | 646.1375 | 503.9303 | 508.2003 | 517.5677 | 539.6924 | 551.7719 | 574.7832 | 644.7312 | 587.0662 | 575.7869 | 591.0125 | 624.3105 | 601.7716 | 601.7716 | 601.7716 | 601.7716 | 601.7716 | 601.7716 | 601.7716 | 601.7716 | 601.7716 | 601.7716 | 601.7716 | 601.7716 | 601.7716 | 601.7716 | 601.7716 | 601.7716
90% | 2285.5212 | 3172.6969 | 3403.3313 | 2621.4927 | 2652.1546 | 2704.9477 | 2825.0569 | 2905.4563 | 3007.3087 | 3060.176 | 3106.6864 | 3020.9897 | 3121.4235 | 3279.317 | 3159.4978 | 3159.4978 | 3159.4978 | 3159.4978 | 3159.4978 | 3159.4978 | 3159.4978 | 3159.4978 | 3159.4978 | 3159.4978 | 3159.4978 | 3159.4978 | 3159.4978 | 3159.4978 | 3159.4978 | 3159.4978 |  | 2446.9201 | 3322.9067 | 3562.5435 | 2778.4698 | 2802.0129 | 2853.6613 | 2975.6476 | 3042.2493 | 3169.1243 | 3554.7894 | 3236.8478 | 3174.6581 | 3258.6062 | 3442.1983 | 3317.9273 | 3317.9273 | 3317.9273 | 3317.9273 | 3317.9273 | 3317.9273 | 3317.9273 | 3317.9273 | 3317.9273 | 3317.9273 | 3317.9273 | 3317.9273 | 3317.9273 | 3317.9273 | 3317.9273 | 3317.9273
85% | 5583.3646 | 7750.6712 | 8314.0946 | 6404.119 | 6479.0237 | 6607.9934 | 6901.4115 | 7097.8217 | 7346.6396 | 7475.7908 | 7589.4123 | 7380.0615 | 7625.414 | 8011.1366 | 7718.4267 | 7718.4267 | 7718.4267 | 7718.4267 | 7718.4267 | 7718.4267 | 7718.4267 | 7718.4267 | 7718.4267 | 7718.4267 | 7718.4267 | 7718.4267 | 7718.4267 | 7718.4267 | 7718.4267 | 7718.4267 |  | 5977.6505 | 8117.623 | 8703.0385 | 6787.6028 | 6845.1168 | 6971.2901 | 7269.294 | 7431.997 | 7741.9437 | 8684.0958 | 7907.3874 | 7755.4624 | 7960.5414 | 8409.0439 | 8105.4588 | 8105.4588 | 8105.4588 | 8105.4588 | 8105.4588 | 8105.4588 | 8105.4588 | 8105.4588 | 8105.4588 | 8105.4588 | 8105.4588 | 8105.4588 | 8105.4588 | 8105.4588 | 8105.4588 | 8105.4588
80% | 8678.2039 | 12046.8408 | 12922.5678 | 9953.8994 | 10070.3235 | 10270.7807 | 10726.8395 | 11032.1191 | 11418.8559 | 11619.5951 | 11796.1967 | 11470.8034 | 11852.154 | 12451.6813 | 11996.7232 | 11996.7232 | 11996.7232 | 11996.7232 | 11996.7232 | 11996.7232 | 11996.7232 | 11996.7232 | 11996.7232 | 11996.7232 | 11996.7232 | 11996.7232 | 11996.7232 | 11996.7232 | 11996.7232 | 11996.7232 |  | 9291.041 | 12617.1926 | 13527.1019 | 10549.9469 | 10639.3408 | 10835.4514 | 11298.6379 | 11551.5266 | 12033.2757 | 13497.6593 | 12290.4242 | 12054.2877 | 12373.0414 | 13070.1471 | 12598.2859 | 12598.2859 | 12598.2859 | 12598.2859 | 12598.2859 | 12598.2859 | 12598.2859 | 12598.2859 | 12598.2859 | 12598.2859 | 12598.2859 | 12598.2859 | 12598.2859 | 12598.2859 | 12598.2859 | 12598.2859
75% | 9574.4808 | 13291.0275 | 14257.1987 | 10981.9291 | 11110.3773 | 11331.5375 | 11834.6977 | 12171.5063 | 12598.1849 | 12819.6563 | 13014.4971 | 12655.4975 | 13076.2336 | 13737.6795 | 13235.7338 | 13235.7338 | 13235.7338 | 13235.7338 | 13235.7338 | 13235.7338 | 13235.7338 | 13235.7338 | 13235.7338 | 13235.7338 | 13235.7338 | 13235.7338 | 13235.7338 | 13235.7338 | 13235.7338 | 13235.7338 |  | 10250.6112 | 13920.2847 | 14924.1686 | 11639.5358 | 11738.1621 | 11954.527 | 12465.5509 | 12744.5577 | 13276.0614 | 14891.6852 | 13559.768 | 13299.2435 | 13650.9177 | 14420.02 | 13899.4254 | 13899.4254 | 13899.4254 | 13899.4254 | 13899.4254 | 13899.4254 | 13899.4254 | 13899.4254 | 13899.4254 | 13899.4254 | 13899.4254 | 13899.4254 | 13899.4254 | 13899.4254 | 13899.4254 | 13899.4254
70% | 10287.2444 | 14280.4661 | 15318.563 | 11799.4688 | 11937.4793 | 12175.1036 | 12715.721 | 13077.603 | 13536.0454 | 13774.004 | 13983.3496 | 13597.6245 | 14049.682 | 14760.3687 | 14221.0561 | 14221.0561 | 14221.0561 | 14221.0561 | 14221.0561 | 14221.0561 | 14221.0561 | 14221.0561 | 14221.0561 | 14221.0561 | 14221.0561 | 14221.0561 | 14221.0561 | 14221.0561 | 14221.0561 | 14221.0561 |  | 11013.7087 | 14956.5677 | 16035.1849 | 12506.0305 | 12611.999 | 12844.4709 | 13393.5375 | 13693.3148 | 14264.3858 | 16000.2833 | 14569.2126 | 14289.2937 | 14667.148 | 15493.5053 | 14934.1555 | 14934.1555 | 14934.1555 | 14934.1555 | 14934.1555 | 14934.1555 | 14934.1555 | 14934.1555 | 14934.1555 | 14934.1555 | 14934.1555 | 14934.1555 | 14934.1555 | 14934.1555 | 14934.1555 | 14934.1555
65% | 10840.7831 | 15048.8731 | 16142.8282 | 12434.3777 | 12579.8143 | 12830.2247 | 13399.9319 | 13781.2861 | 14264.3965 | 14515.1592 | 14735.7693 | 14329.2891 | 14805.6709 | 15554.5984 | 14986.2664 | 14986.2664 | 14986.2664 | 14986.2664 | 14986.2664 | 14986.2664 | 14986.2664 | 14986.2664 | 14986.2664 | 14986.2664 | 14986.2664 | 14986.2664 | 14986.2664 | 14986.2664 | 14986.2664 | 14986.2664 |  | 11606.3372 | 15761.3546 | 16898.0103 | 13178.9583 | 13290.6287 | 13535.6096 | 14114.2205 | 14430.1282 | 15031.9276 | 16861.2307 | 15353.1566 | 15058.1757 | 15456.3617 | 16327.1839 | 15737.7365 | 15737.7365 | 15737.7365 | 15737.7365 | 15737.7365 | 15737.7365 | 15737.7365 | 15737.7365 | 15737.7365 | 15737.7365 | 15737.7365 | 15737.7365 | 15737.7365 | 15737.7365 | 15737.7365 | 15737.7365
60% | 11934.3669 | 16566.9557 | 17771.2656 | 13688.7183 | 13848.8261 | 14124.4971 | 14751.6745 | 15171.4986 | 15703.3435 | 15979.4025 | 16222.267 | 15774.7823 | 16299.22 | 17123.697 | 16498.0334 | 16498.0334 | 16498.0334 | 16498.0334 | 16498.0334 | 16498.0334 | 16498.0334 | 16498.0334 | 16498.0334 | 16498.0334 | 16498.0334 | 16498.0334 | 16498.0334 | 16498.0334 | 16498.0334 | 16498.0334 |  | 12777.1477 | 17351.3101 | 18602.628 | 14508.4098 | 14631.3452 | 14901.0389 | 15538.0183 | 15885.7938 | 16548.3008 | 18562.1382 | 16901.9344 | 16577.1968 | 17015.5505 | 17974.2184 | 17325.3094 | 17325.3094 | 17325.3094 | 17325.3094 | 17325.3094 | 17325.3094 | 17325.3094 | 17325.3094 | 17325.3094 | 17325.3094 | 17325.3094 | 17325.3094 | 17325.3094 | 17325.3094 | 17325.3094 | 17325.3094
55% | 13276.2336 | 18429.6976 | 19769.4166 | 15227.8393 | 15405.9492 | 15712.6158 | 16410.3113 | 16877.3392 | 17468.9833 | 17776.0815 | 18046.253 | 17548.4544 | 18131.8585 | 19049.0373 | 18353.0259 | 18353.0259 | 18353.0259 | 18353.0259 | 18353.0259 | 18353.0259 | 18353.0259 | 18353.0259 | 18353.0259 | 18353.0259 | 18353.0259 | 18353.0259 | 18353.0259 | 18353.0259 | 18353.0259 | 18353.0259 |  | 14213.7742 | 19302.2426 | 20694.2551 | 16139.6946 | 16276.4525 | 16576.4698 | 17285.0694 | 17671.9478 | 18408.9452 | 20649.2127 | 18802.3403 | 18441.0901 | 18928.7311 | 19995.189 | 19273.3184 | 19273.3184 | 19273.3184 | 19273.3184 | 19273.3184 | 19273.3184 | 19273.3184 | 19273.3184 | 19273.3184 | 19273.3184 | 19273.3184 | 19273.3184 | 19273.3184 | 19273.3184 | 19273.3184 | 19273.3184
50% | 13456.7484 | 18680.2832 | 20038.2182 | 15434.8898 | 15615.4214 | 15926.2577 | 16633.4396 | 17106.8176 | 17706.5062 | 18017.78 | 18291.625 | 17787.0579 | 18378.3944 | 19308.044 | 18602.569 | 18602.569 | 18602.569 | 18602.569 | 18602.569 | 18602.569 | 18602.569 | 18602.569 | 18602.569 | 18602.569 | 18602.569 | 18602.569 | 18602.569 | 18602.569 | 18602.569 | 18602.569 |  | 14407.0366 | 19564.692 | 20975.6315 | 16359.1434 | 16497.7608 | 16801.8574 | 17520.0917 | 17912.2304 | 18659.2486 | 20929.9767 | 19057.9927 | 18691.8306 | 19186.102 | 20267.0603 | 19535.3746 | 19535.3746 | 19535.3746 | 19535.3746 | 19535.3746 | 19535.3746 | 19535.3746 | 19535.3746 | 19535.3746 | 19535.3746 | 19535.3746 | 19535.3746 | 19535.3746 | 19535.3746 | 19535.3746 | 19535.3746
45% | 10386.1977 | 14417.8303 | 15465.9127 | 11912.9683 | 12052.3063 | 12292.2162 | 12838.0339 | 13203.3969 | 13666.249 | 13906.4966 | 14117.8558 | 13728.4205 | 14184.8262 | 14902.3491 | 14357.8488 | 14357.8488 | 14357.8488 | 14357.8488 | 14357.8488 | 14357.8488 | 14357.8488 | 14357.8488 | 14357.8488 | 14357.8488 | 14357.8488 | 14357.8488 | 14357.8488 | 14357.8488 | 14357.8488 | 14357.8488 |  | 11119.6499 | 15100.4354 | 16189.4278 | 12626.3264 | 12733.3142 | 12968.0222 | 13522.3704 | 13825.0312 | 14401.5953 | 16154.1904 | 14709.3543 | 14426.7428 | 14808.2317 | 15642.5378 | 15077.8076 | 15077.8076 | 15077.8076 | 15077.8076 | 15077.8076 | 15077.8076 | 15077.8076 | 15077.8076 | 15077.8076 | 15077.8076 | 15077.8076 | 15077.8076 | 15077.8076 | 15077.8076 | 15077.8076 | 15077.8076
40% | 5102.6915 | 7083.4142 | 7598.3323 | 5852.7869 | 5921.2431 | 6039.1097 | 6307.2675 | 6486.7686 | 6714.1658 | 6832.1983 | 6936.0381 | 6744.7103 | 6968.9404 | 7321.4561 | 7053.9456 | 7053.9456 | 7053.9456 | 7053.9456 | 7053.9456 | 7053.9456 | 7053.9456 | 7053.9456 | 7053.9456 | 7053.9456 | 7053.9456 | 7053.9456 | 7053.9456 | 7053.9456 | 7053.9456 | 7053.9456 |  | 5463.0332 | 7418.775 | 7953.792 | 6203.2565 | 6255.8191 | 6371.1301 | 6643.4788 | 6792.1747 | 7075.4381 | 7936.48 | 7226.6386 | 7087.7929 | 7275.2166 | 7685.1074 | 7407.658 | 7407.658 | 7407.658 | 7407.658 | 7407.658 | 7407.658 | 7407.658 | 7407.658 | 7407.658 | 7407.658 | 7407.658 | 7407.658 | 7407.658 | 7407.658 | 7407.658 | 7407.658
35% | 1907.0998 | 2647.3829 | 2839.8304 | 2187.4434 | 2213.0285 | 2257.0804 | 2357.3028 | 2424.3902 | 2509.3785 | 2553.4925 | 2592.302 | 2520.7944 | 2604.599 | 2736.3496 | 2636.3692 | 2636.3692 | 2636.3692 | 2636.3692 | 2636.3692 | 2636.3692 | 2636.3692 | 2636.3692 | 2636.3692 | 2636.3692 | 2636.3692 | 2636.3692 | 2636.3692 | 2636.3692 | 2636.3692 | 2636.3692 |  | 2041.7754 | 2772.7219 | 2972.6813 | 2318.4293 | 2338.0743 | 2381.171 | 2482.9597 | 2538.5339 | 2644.4018 | 2966.211 | 2700.9121 | 2649.0194 | 2719.0679 | 2872.262 | 2768.567 | 2768.567 | 2768.567 | 2768.567 | 2768.567 | 2768.567 | 2768.567 | 2768.567 | 2768.567 | 2768.567 | 2768.567 | 2768.567 | 2768.567 | 2768.567 | 2768.567 | 2768.567
30% | 951.1511 | 1320.3614 | 1416.3431 | 1090.9702 | 1103.7306 | 1125.7011 | 1175.6862 | 1209.1456 | 1251.5328 | 1273.5343 | 1292.8902 | 1257.2264 | 1299.0233 | 1364.7328 | 1314.8684 | 1314.8684 | 1314.8684 | 1314.8684 | 1314.8684 | 1314.8684 | 1314.8684 | 1314.8684 | 1314.8684 | 1314.8684 | 1314.8684 | 1314.8684 | 1314.8684 | 1314.8684 | 1314.8684 | 1314.8684 |  | 1018.3194 | 1382.8733 | 1482.6014 | 1156.2984 | 1166.0962 | 1187.5903 | 1238.3566 | 1266.0738 | 1318.8746 | 1479.3744 | 1347.0587 | 1321.1776 | 1356.1137 | 1432.5181 | 1380.801 | 1380.801 | 1380.801 | 1380.801 | 1380.801 | 1380.801 | 1380.801 | 1380.801 | 1380.801 | 1380.801 | 1380.801 | 1380.801 | 1380.801 | 1380.801 | 1380.801 | 1380.801
25% | 560.7353 | 778.3972 | 834.9816 | 643.1634 | 650.6861 | 663.6384 | 693.1063 | 712.8317 | 737.8204 | 750.791 | 762.202 | 741.177 | 765.8176 | 804.5556 | 775.1589 | 775.1589 | 775.1589 | 775.1589 | 775.1589 | 775.1589 | 775.1589 | 775.1589 | 775.1589 | 775.1589 | 775.1589 | 775.1589 | 775.1589 | 775.1589 | 775.1589 | 775.1589 |  | 600.3333 | 815.25 | 874.0431 | 681.6765 | 687.4527 | 700.1242 | 730.0526 | 746.3928 | 777.5207 | 872.1407 | 794.1361 | 778.8783 | 799.4744 | 844.5173 | 814.0284 | 814.0284 | 814.0284 | 814.0284 | 814.0284 | 814.0284 | 814.0284 | 814.0284 | 814.0284 | 814.0284 | 814.0284 | 814.0284 | 814.0284 | 814.0284 | 814.0284 | 814.0284
20% | 283.3663 | 393.3611 | 421.9559 | 325.0211 | 328.8226 | 335.3681 | 350.2596 | 360.2278 | 372.8558 | 379.4104 | 385.1769 | 374.552 | 387.0041 | 406.5802 | 391.7247 | 391.7247 | 391.7247 | 391.7247 | 391.7247 | 391.7247 | 391.7247 | 391.7247 | 391.7247 | 391.7247 | 391.7247 | 391.7247 | 391.7247 | 391.7247 | 391.7247 | 391.7247 |  | 303.377 | 411.9846 | 441.6956 | 344.4836 | 347.4025 | 353.8061 | 368.9303 | 377.1878 | 392.9182 | 440.7342 | 401.3148 | 393.6043 | 404.0124 | 426.7748 | 411.3673 | 411.3673 | 411.3673 | 411.3673 | 411.3673 | 411.3673 | 411.3673 | 411.3673 | 411.3673 | 411.3673 | 411.3673 | 411.3673 | 411.3673 | 411.3673 | 411.3673 | 411.3673
15% | 115.4455 | 160.2582 | 171.908 | 132.416 | 133.9648 | 136.6314 | 142.6984 | 146.7595 | 151.9042 | 154.5746 | 156.9239 | 152.5953 | 157.6683 | 165.6438 | 159.5915 | 159.5915 | 159.5915 | 159.5915 | 159.5915 | 159.5915 | 159.5915 | 159.5915 | 159.5915 | 159.5915 | 159.5915 | 159.5915 | 159.5915 | 159.5915 | 159.5915 | 159.5915 |  | 123.598 | 167.8456 | 179.95 | 140.3452 | 141.5344 | 144.1432 | 150.305 | 153.6691 | 160.0778 | 179.5584 | 163.4986 | 160.3573 | 164.5977 | 173.8712 | 167.5941 | 167.5941 | 167.5941 | 167.5941 | 167.5941 | 167.5941 | 167.5941 | 167.5941 | 167.5941 | 167.5941 | 167.5941 | 167.5941 | 167.5941 | 167.5941 | 167.5941 | 167.5941
10% | 46.4781 | 64.5196 | 69.2097 | 53.3103 | 53.9339 | 55.0075 | 57.45 | 59.085 | 61.1562 | 62.2313 | 63.1772 | 61.4345 | 63.4769 | 66.6878 | 64.2511 | 64.2511 | 64.2511 | 64.2511 | 64.2511 | 64.2511 | 64.2511 | 64.2511 | 64.2511 | 64.2511 | 64.2511 | 64.2511 | 64.2511 | 64.2511 | 64.2511 | 64.2511 |  | 49.7602 | 67.5742 | 72.4474 | 56.5026 | 56.9814 | 58.0317 | 60.5124 | 61.8668 | 64.4469 | 72.2897 | 65.8241 | 64.5594 | 66.2666 | 70.0001 | 67.4729 | 67.4729 | 67.4729 | 67.4729 | 67.4729 | 67.4729 | 67.4729 | 67.4729 | 67.4729 | 67.4729 | 67.4729 | 67.4729 | 67.4729 | 67.4729 | 67.4729 | 67.4729
5% | 39.5813 | 54.9457 | 58.9399 | 45.3998 | 45.9308 | 46.8451 | 48.9252 | 50.3175 | 52.0814 | 52.997 | 53.8025 | 52.3184 | 54.0577 | 56.7922 | 54.7171 | 54.7171 | 54.7171 | 54.7171 | 54.7171 | 54.7171 | 54.7171 | 54.7171 | 54.7171 | 54.7171 | 54.7171 | 54.7171 | 54.7171 | 54.7171 | 54.7171 | 54.7171 |  | 42.3765 | 57.5471 | 61.6972 | 48.1183 | 48.5261 | 49.4205 | 51.5331 | 52.6866 | 54.8838 | 61.5629 | 56.0567 | 54.9796 | 56.4335 | 59.613 | 57.4608 | 57.4608 | 57.4608 | 57.4608 | 57.4608 | 57.4608 | 57.4608 | 57.4608 | 57.4608 | 57.4608 | 57.4608 | 57.4608 | 57.4608 | 57.4608 | 57.4608 | 57.4608
9.992e-14% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E @ R (MWh) | 105995.1099 | 147139.4588 | 157835.5397 | 121576.3863 | 122998.3841 | 125446.7565 | 131017.0343 | 134745.7026 | 139469.2851 | 141921.103 | 144078.1049 | 140103.7687 | 144761.5638 | 152084.1579 | 146527.3251 | 146527.3251 | 146527.3251 | 146527.3251 | 146527.3251 | 146527.3251 | 146527.3251 | 146527.3251 | 146527.3251 | 146527.3251 | 146527.3251 | 146527.3251 | 146527.3251 | 146527.3251 | 146527.3251 | 146527.3251 | E @ R (MWh) | 113480.2695 | 154105.704 | 165219.287 | 128856.478 | 129948.3294 | 132343.6147 | 138000.9487 | 141089.7178 | 146973.7751 | 164859.6767 | 150114.5726 | 147230.4146 | 151123.6541 | 159638.0662 | 153874.7791 | 153874.7791 | 153874.7791 | 153874.7791 | 153874.7791 | 153874.7791 | 153874.7791 | 153874.7791 | 153874.7791 | 153874.7791 | 153874.7791 | 153874.7791 | 153874.7791 | 153874.7791 | 153874.7791 | 153874.7791
Option 4 Winter POE50 W E @ R (MWh) N 2 | 74196.5769 | 102997.6211 | 110484.8778 | 85103.4704 | 86098.8688 | 87812.7295 | 91711.924 | 94321.9918 | 97628.4996 | 99344.7721 | 100854.6734 | 98072.6381 | 101333.0947 | 106458.9105 | 102569.1276 | 102569.1276 | 102569.1276 | 102569.1276 | 102569.1276 | 102569.1276 | 102569.1276 | 102569.1276 | 102569.1276 | 102569.1276 | 102569.1276 | 102569.1276 | 102569.1276 | 102569.1276 | 102569.1276 | 102569.1276 | Option 4 Winter POE10 W E @ R (MWh) N 2 | 34044.0809 | 46231.7112 | 49565.7861 | 38656.9434 | 38984.4988 | 39703.0844 | 41400.2846 | 42326.9153 | 44092.1325 | 49457.903 | 45034.3718 | 44169.1244 | 45337.0962 | 47891.4199 | 46162.4337 | 46162.4337 | 46162.4337 | 46162.4337 | 46162.4337 | 46162.4337 | 46162.4337 | 46162.4337 | 46162.4337 | 46162.4337 | 46162.4337 | 46162.4337 | 46162.4337 | 46162.4337 | 46162.4337 | 46162.4337
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 76.9936 | 99.7405 | 105.6969 | 83.5188 | 83.5485 | 84.1617 | 85.7761 | 86.8585 | 87.9173 | 89.1552 | 90.3034 | 91.4172 | 91.5463 | 92.8459 | 91.8644 | 91.8644 | 91.8644 | 91.8644 | 91.8644 | 91.8644 | 91.8644 | 91.8644 | 91.8644 | 91.8644 | 91.8644 | 91.8644 | 91.8644 | 91.8644 | 91.8644 | 91.8644
98% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 38.1099 | 49.369 | 52.3173 | 41.3397 | 41.3544 | 41.6579 | 42.457 | 42.9928 | 43.5168 | 44.1296 | 44.6979 | 45.2492 | 45.3131 | 45.9564 | 45.4706 | 45.4706 | 45.4706 | 45.4706 | 45.4706 | 45.4706 | 45.4706 | 45.4706 | 45.4706 | 45.4706 | 45.4706 | 45.4706 | 45.4706 | 45.4706 | 45.4706 | 45.4706
97% | 16.9149 | 22.4762 | 23.991 | 18.6014 | 18.6009 | 18.7741 | 18.9642 | 19.3539 | 19.634 | 19.7862 | 19.953 | 20.1054 | 20.3802 | 20.7211 | 20.6981 | 20.6981 | 20.6981 | 20.6981 | 20.6981 | 20.6981 | 20.6981 | 20.6981 | 20.6981 | 20.6981 | 20.6981 | 20.6981 | 20.6981 | 20.6981 | 20.6981 | 20.6981 |  | 75.446 | 97.7357 | 103.5723 | 81.84 | 81.8691 | 82.47 | 84.052 | 85.1126 | 86.1501 | 87.3631 | 88.4882 | 89.5797 | 89.7061 | 90.9797 | 90.0179 | 90.0179 | 90.0179 | 90.0179 | 90.0179 | 90.0179 | 90.0179 | 90.0179 | 90.0179 | 90.0179 | 90.0179 | 90.0179 | 90.0179 | 90.0179 | 90.0179 | 90.0179
95% | 83.2734 | 110.6519 | 118.1097 | 91.576 | 91.5735 | 92.4264 | 93.3621 | 95.281 | 96.6596 | 97.4091 | 98.2301 | 98.9804 | 100.3333 | 102.0115 | 101.8981 | 101.8981 | 101.8981 | 101.8981 | 101.8981 | 101.8981 | 101.8981 | 101.8981 | 101.8981 | 101.8981 | 101.8981 | 101.8981 | 101.8981 | 101.8981 | 101.8981 | 101.8981 |  | 111.4279 | 144.3481 | 152.9683 | 120.8714 | 120.9144 | 121.8019 | 124.1383 | 125.7048 | 127.2371 | 129.0286 | 130.6903 | 132.3023 | 132.4891 | 134.37 | 132.9495 | 132.9495 | 132.9495 | 132.9495 | 132.9495 | 132.9495 | 132.9495 | 132.9495 | 132.9495 | 132.9495 | 132.9495 | 132.9495 | 132.9495 | 132.9495 | 132.9495 | 132.9495
90% | 144.4273 | 191.9119 | 204.8464 | 158.8271 | 158.8227 | 160.3021 | 161.9248 | 165.2529 | 167.6439 | 168.9439 | 170.3679 | 171.6692 | 174.0155 | 176.9262 | 176.7295 | 176.7295 | 176.7295 | 176.7295 | 176.7295 | 176.7295 | 176.7295 | 176.7295 | 176.7295 | 176.7295 | 176.7295 | 176.7295 | 176.7295 | 176.7295 | 176.7295 | 176.7295 |  | 483.1446 | 625.8842 | 663.261 | 524.0907 | 524.2773 | 528.1253 | 538.2559 | 545.0482 | 551.692 | 559.4599 | 566.6651 | 573.6545 | 574.4643 | 582.6198 | 576.4606 | 576.4606 | 576.4606 | 576.4606 | 576.4606 | 576.4606 | 576.4606 | 576.4606 | 576.4606 | 576.4606 | 576.4606 | 576.4606 | 576.4606 | 576.4606 | 576.4606 | 576.4606
85% | 409.8612 | 544.6148 | 581.321 | 450.7257 | 450.7131 | 454.9113 | 459.5164 | 468.961 | 475.7463 | 479.4353 | 483.4765 | 487.1693 | 493.8279 | 502.088 | 501.5297 | 501.5297 | 501.5297 | 501.5297 | 501.5297 | 501.5297 | 501.5297 | 501.5297 | 501.5297 | 501.5297 | 501.5297 | 501.5297 | 501.5297 | 501.5297 | 501.5297 | 501.5297 |  | 457.0286 | 592.0526 | 627.4091 | 495.7614 | 495.938 | 499.578 | 509.161 | 515.5862 | 521.8708 | 529.2188 | 536.0345 | 542.6462 | 543.4121 | 551.1268 | 545.3006 | 545.3006 | 545.3006 | 545.3006 | 545.3006 | 545.3006 | 545.3006 | 545.3006 | 545.3006 | 545.3006 | 545.3006 | 545.3006 | 545.3006 | 545.3006 | 545.3006 | 545.3006
80% | 572.5046 | 760.7318 | 812.0039 | 629.5851 | 629.5675 | 635.4317 | 641.8642 | 655.0566 | 664.5345 | 669.6874 | 675.3322 | 680.4905 | 689.7914 | 701.3293 | 700.5495 | 700.5495 | 700.5495 | 700.5495 | 700.5495 | 700.5495 | 700.5495 | 700.5495 | 700.5495 | 700.5495 | 700.5495 | 700.5495 | 700.5495 | 700.5495 | 700.5495 | 700.5495 |  | 319.1946 | 413.4971 | 438.1905 | 346.2461 | 346.3694 | 348.9116 | 355.6045 | 360.0919 | 364.4812 | 369.6132 | 374.3733 | 378.991 | 379.5259 | 384.914 | 380.8448 | 380.8448 | 380.8448 | 380.8448 | 380.8448 | 380.8448 | 380.8448 | 380.8448 | 380.8448 | 380.8448 | 380.8448 | 380.8448 | 380.8448 | 380.8448 | 380.8448 | 380.8448
75% | 1492.4153 | 1983.0895 | 2116.7465 | 1641.2139 | 1641.1681 | 1656.4548 | 1673.2233 | 1707.6135 | 1732.3207 | 1745.7533 | 1760.4684 | 1773.915 | 1798.1606 | 1828.2379 | 1826.2051 | 1826.2051 | 1826.2051 | 1826.2051 | 1826.2051 | 1826.2051 | 1826.2051 | 1826.2051 | 1826.2051 | 1826.2051 | 1826.2051 | 1826.2051 | 1826.2051 | 1826.2051 | 1826.2051 | 1826.2051 |  | 569.714 | 738.0296 | 782.1036 | 617.9968 | 618.2169 | 622.7544 | 634.7001 | 642.7095 | 650.5437 | 659.7035 | 668.1997 | 676.4415 | 677.3963 | 687.0131 | 679.7503 | 679.7503 | 679.7503 | 679.7503 | 679.7503 | 679.7503 | 679.7503 | 679.7503 | 679.7503 | 679.7503 | 679.7503 | 679.7503 | 679.7503 | 679.7503 | 679.7503 | 679.7503
70% | 2578.4391 | 3426.1747 | 3657.0932 | 2835.5177 | 2835.4386 | 2861.8494 | 2890.8202 | 2950.236 | 2992.9226 | 3016.1299 | 3041.5532 | 3064.7849 | 3106.6739 | 3158.6382 | 3155.1263 | 3155.1263 | 3155.1263 | 3155.1263 | 3155.1263 | 3155.1263 | 3155.1263 | 3155.1263 | 3155.1263 | 3155.1263 | 3155.1263 | 3155.1263 | 3155.1263 | 3155.1263 | 3155.1263 | 3155.1263 |  | 1037.8661 | 1344.492 | 1424.783 | 1125.8244 | 1126.2253 | 1134.4915 | 1156.2533 | 1170.8444 | 1185.1162 | 1201.8028 | 1217.2805 | 1232.2949 | 1234.0344 | 1251.5536 | 1238.3227 | 1238.3227 | 1238.3227 | 1238.3227 | 1238.3227 | 1238.3227 | 1238.3227 | 1238.3227 | 1238.3227 | 1238.3227 | 1238.3227 | 1238.3227 | 1238.3227 | 1238.3227 | 1238.3227 | 1238.3227
65% | 6475.8072 | 8604.914 | 9184.8711 | 7121.4659 | 7121.2673 | 7187.5985 | 7260.3594 | 7409.5836 | 7516.7917 | 7575.0775 | 7638.9286 | 7697.2756 | 7802.4808 | 7932.9903 | 7924.17 | 7924.17 | 7924.17 | 7924.17 | 7924.17 | 7924.17 | 7924.17 | 7924.17 | 7924.17 | 7924.17 | 7924.17 | 7924.17 | 7924.17 | 7924.17 | 7924.17 | 7924.17 |  | 1305.7961 | 1691.5789 | 1792.5974 | 1416.4613 | 1416.9656 | 1427.3658 | 1454.7456 | 1473.1034 | 1491.0595 | 1512.0538 | 1531.5272 | 1550.4177 | 1552.6061 | 1574.6481 | 1558.0016 | 1558.0016 | 1558.0016 | 1558.0016 | 1558.0016 | 1558.0016 | 1558.0016 | 1558.0016 | 1558.0016 | 1558.0016 | 1558.0016 | 1558.0016 | 1558.0016 | 1558.0016 | 1558.0016 | 1558.0016
60% | 9465.8424 | 12578.0087 | 13425.7459 | 10409.6171 | 10409.3268 | 10506.2848 | 10612.6411 | 10830.7656 | 10987.4743 | 11072.6721 | 11166.0048 | 11251.292 | 11405.0729 | 11595.8418 | 11582.9489 | 11582.9489 | 11582.9489 | 11582.9489 | 11582.9489 | 11582.9489 | 11582.9489 | 11582.9489 | 11582.9489 | 11582.9489 | 11582.9489 | 11582.9489 | 11582.9489 | 11582.9489 | 11582.9489 | 11582.9489 |  | 2043.3291 | 2647.0078 | 2805.083 | 2216.4996 | 2217.2888 | 2233.5632 | 2276.4074 | 2305.134 | 2333.232 | 2366.0842 | 2396.5565 | 2426.1166 | 2429.5411 | 2464.0327 | 2437.984 | 2437.984 | 2437.984 | 2437.984 | 2437.984 | 2437.984 | 2437.984 | 2437.984 | 2437.984 | 2437.984 | 2437.984 | 2437.984 | 2437.984 | 2437.984 | 2437.984 | 2437.984
55% | 10703.6666 | 14222.8031 | 15181.3967 | 11770.8563 | 11770.5281 | 11880.165 | 12000.4293 | 12247.0774 | 12424.2785 | 12520.6174 | 12626.1549 | 12722.595 | 12896.4854 | 13112.2007 | 13097.6218 | 13097.6218 | 13097.6218 | 13097.6218 | 13097.6218 | 13097.6218 | 13097.6218 | 13097.6218 | 13097.6218 | 13097.6218 | 13097.6218 | 13097.6218 | 13097.6218 | 13097.6218 | 13097.6218 | 13097.6218 |  | 3926.5772 | 5086.6405 | 5390.4069 | 4259.3515 | 4260.8682 | 4292.1418 | 4374.4738 | 4429.6764 | 4483.6711 | 4546.8018 | 4605.3591 | 4662.1634 | 4668.7442 | 4735.0252 | 4684.9685 | 4684.9685 | 4684.9685 | 4684.9685 | 4684.9685 | 4684.9685 | 4684.9685 | 4684.9685 | 4684.9685 | 4684.9685 | 4684.9685 | 4684.9685 | 4684.9685 | 4684.9685 | 4684.9685 | 4684.9685
50% | 13744.0128 | 18262.75 | 19493.6294 | 15114.3347 | 15113.9133 | 15254.6922 | 15409.1173 | 15725.825 | 15953.3596 | 16077.0633 | 16212.5785 | 16336.412 | 16559.6955 | 16836.6841 | 16817.9641 | 16817.9641 | 16817.9641 | 16817.9641 | 16817.9641 | 16817.9641 | 16817.9641 | 16817.9641 | 16817.9641 | 16817.9641 | 16817.9641 | 16817.9641 | 16817.9641 | 16817.9641 | 16817.9641 | 16817.9641 |  | 8714.0125 | 11288.47 | 11962.6002 | 9452.5183 | 9455.8841 | 9525.2878 | 9708.0021 | 9830.5098 | 9950.3371 | 10090.439 | 10220.3916 | 10346.454 | 10361.0583 | 10508.1518 | 10397.0639 | 10397.0639 | 10397.0639 | 10397.0639 | 10397.0639 | 10397.0639 | 10397.0639 | 10397.0639 | 10397.0639 | 10397.0639 | 10397.0639 | 10397.0639 | 10397.0639 | 10397.0639 | 10397.0639 | 10397.0639
45% | 18302.3635 | 24319.7888 | 25958.9027 | 20127.1675 | 20126.6063 | 20314.0761 | 20519.7179 | 20941.4652 | 21244.4641 | 21409.1954 | 21589.6557 | 21754.5599 | 22051.8979 | 22420.7527 | 22395.8241 | 22395.8241 | 22395.8241 | 22395.8241 | 22395.8241 | 22395.8241 | 22395.8241 | 22395.8241 | 22395.8241 | 22395.8241 | 22395.8241 | 22395.8241 | 22395.8241 | 22395.8241 | 22395.8241 | 22395.8241 |  | 13204.5002 | 17105.6219 | 18127.1435 | 14323.5712 | 14328.6715 | 14433.8402 | 14710.7105 | 14896.3485 | 15077.925 | 15290.224 | 15487.1436 | 15678.1681 | 15700.2983 | 15923.1917 | 15754.8583 | 15754.8583 | 15754.8583 | 15754.8583 | 15754.8583 | 15754.8583 | 15754.8583 | 15754.8583 | 15754.8583 | 15754.8583 | 15754.8583 | 15754.8583 | 15754.8583 | 15754.8583 | 15754.8583 | 15754.8583
40% | 12836.6798 | 17057.1053 | 18206.7263 | 14116.5377 | 14116.1441 | 14247.6293 | 14391.8598 | 14687.6596 | 14900.173 | 15015.7102 | 15142.2792 | 15257.9376 | 15466.4808 | 15725.1835 | 15707.6994 | 15707.6994 | 15707.6994 | 15707.6994 | 15707.6994 | 15707.6994 | 15707.6994 | 15707.6994 | 15707.6994 | 15707.6994 | 15707.6994 | 15707.6994 | 15707.6994 | 15707.6994 | 15707.6994 | 15707.6994 |  | 13672.6523 | 17712.0843 | 18769.8229 | 14831.3988 | 14836.6799 | 14945.5773 | 15232.2637 | 15424.4834 | 15612.4974 | 15832.3233 | 16036.2244 | 16234.0215 | 16256.9364 | 16487.7322 | 16313.4307 | 16313.4307 | 16313.4307 | 16313.4307 | 16313.4307 | 16313.4307 | 16313.4307 | 16313.4307 | 16313.4307 | 16313.4307 | 16313.4307 | 16313.4307 | 16313.4307 | 16313.4307 | 16313.4307 | 16313.4307
35% | 6655.3655 | 8843.5072 | 9439.545 | 7318.9266 | 7318.7226 | 7386.893 | 7461.6714 | 7615.0331 | 7725.2139 | 7785.1158 | 7850.7374 | 7910.7022 | 8018.8244 | 8152.9527 | 8143.8878 | 8143.8878 | 8143.8878 | 8143.8878 | 8143.8878 | 8143.8878 | 8143.8878 | 8143.8878 | 8143.8878 | 8143.8878 | 8143.8878 | 8143.8878 | 8143.8878 | 8143.8878 | 8143.8878 | 8143.8878 |  | 18622.1031 | 24123.7949 | 25564.4311 | 20200.3117 | 20207.5045 | 20355.8224 | 20746.2883 | 21008.0907 | 21264.1652 | 21563.5672 | 21841.2798 | 22110.6788 | 22141.8887 | 22456.2317 | 22218.8337 | 22218.8337 | 22218.8337 | 22218.8337 | 22218.8337 | 22218.8337 | 22218.8337 | 22218.8337 | 22218.8337 | 22218.8337 | 22218.8337 | 22218.8337 | 22218.8337 | 22218.8337 | 22218.8337 | 22218.8337
30% | 3095.428 | 4113.1385 | 4390.3573 | 3404.0521 | 3403.9572 | 3435.6634 | 3470.4431 | 3541.772 | 3593.0174 | 3620.8779 | 3651.3987 | 3679.2885 | 3729.5764 | 3791.9598 | 3787.7437 | 3787.7437 | 3787.7437 | 3787.7437 | 3787.7437 | 3787.7437 | 3787.7437 | 3787.7437 | 3787.7437 | 3787.7437 | 3787.7437 | 3787.7437 | 3787.7437 | 3787.7437 | 3787.7437 | 3787.7437 |  | 17207.9743 | 22291.8776 | 23623.1145 | 18666.3366 | 18672.9832 | 18810.0381 | 19170.8527 | 19412.7743 | 19649.403 | 19926.069 | 20182.6926 | 20431.6339 | 20460.4738 | 20750.9461 | 20531.5757 | 20531.5757 | 20531.5757 | 20531.5757 | 20531.5757 | 20531.5757 | 20531.5757 | 20531.5757 | 20531.5757 | 20531.5757 | 20531.5757 | 20531.5757 | 20531.5757 | 20531.5757 | 20531.5757 | 20531.5757
25% | 2113.496 | 2808.3682 | 2997.6476 | 2324.2183 | 2324.1535 | 2345.8019 | 2369.5487 | 2418.2507 | 2453.24 | 2472.2626 | 2493.1015 | 2512.1441 | 2546.4797 | 2589.0739 | 2586.1952 | 2586.1952 | 2586.1952 | 2586.1952 | 2586.1952 | 2586.1952 | 2586.1952 | 2586.1952 | 2586.1952 | 2586.1952 | 2586.1952 | 2586.1952 | 2586.1952 | 2586.1952 | 2586.1952 | 2586.1952 |  | 4963.476 | 6429.8794 | 6813.862 | 5384.1267 | 5386.0439 | 5425.576 | 5529.6496 | 5599.4295 | 5667.6828 | 5747.4845 | 5821.5051 | 5893.3099 | 5901.6285 | 5985.4124 | 5922.1371 | 5922.1371 | 5922.1371 | 5922.1371 | 5922.1371 | 5922.1371 | 5922.1371 | 5922.1371 | 5922.1371 | 5922.1371 | 5922.1371 | 5922.1371 | 5922.1371 | 5922.1371 | 5922.1371 | 5922.1371
20% | 1280.3284 | 1701.2729 | 1815.9359 | 1407.9812 | 1407.9419 | 1421.0562 | 1435.4418 | 1464.9448 | 1486.1409 | 1497.6645 | 1510.2885 | 1521.8242 | 1542.6243 | 1568.4273 | 1566.6834 | 1566.6834 | 1566.6834 | 1566.6834 | 1566.6834 | 1566.6834 | 1566.6834 | 1566.6834 | 1566.6834 | 1566.6834 | 1566.6834 | 1566.6834 | 1566.6834 | 1566.6834 | 1566.6834 | 1566.6834 |  | 1331.912 | 1725.4105 | 1828.4494 | 1444.7905 | 1445.305 | 1455.9131 | 1483.8405 | 1502.5654 | 1520.8807 | 1542.2949 | 1562.1578 | 1581.426 | 1583.6583 | 1606.1411 | 1589.1616 | 1589.1616 | 1589.1616 | 1589.1616 | 1589.1616 | 1589.1616 | 1589.1616 | 1589.1616 | 1589.1616 | 1589.1616 | 1589.1616 | 1589.1616 | 1589.1616 | 1589.1616 | 1589.1616 | 1589.1616
15% | 819.7224 | 1089.2296 | 1162.6419 | 901.4514 | 901.4262 | 909.8226 | 919.0328 | 937.922 | 951.4926 | 958.8706 | 966.953 | 974.3387 | 987.6558 | 1004.176 | 1003.0595 | 1003.0595 | 1003.0595 | 1003.0595 | 1003.0595 | 1003.0595 | 1003.0595 | 1003.0595 | 1003.0595 | 1003.0595 | 1003.0595 | 1003.0595 | 1003.0595 | 1003.0595 | 1003.0595 | 1003.0595 |  | 734.6312 | 951.6698 | 1008.502 | 796.8906 | 797.1744 | 803.0254 | 818.4291 | 828.757 | 838.859 | 850.6703 | 861.6259 | 872.2535 | 873.4847 | 885.8854 | 876.5202 | 876.5202 | 876.5202 | 876.5202 | 876.5202 | 876.5202 | 876.5202 | 876.5202 | 876.5202 | 876.5202 | 876.5202 | 876.5202 | 876.5202 | 876.5202 | 876.5202 | 876.5202
10% | 548.6502 | 729.0346 | 778.1704 | 603.3524 | 603.3356 | 608.9553 | 615.1199 | 627.7626 | 636.8456 | 641.7837 | 647.1934 | 652.1367 | 661.05 | 672.1072 | 671.3599 | 671.3599 | 671.3599 | 671.3599 | 671.3599 | 671.3599 | 671.3599 | 671.3599 | 671.3599 | 671.3599 | 671.3599 | 671.3599 | 671.3599 | 671.3599 | 671.3599 | 671.3599 |  | 171.688 | 222.4113 | 235.6934 | 186.2384 | 186.3047 | 187.6722 | 191.2721 | 193.6858 | 196.0467 | 198.8071 | 201.3675 | 203.8512 | 204.139 | 207.0371 | 204.8484 | 204.8484 | 204.8484 | 204.8484 | 204.8484 | 204.8484 | 204.8484 | 204.8484 | 204.8484 | 204.8484 | 204.8484 | 204.8484 | 204.8484 | 204.8484 | 204.8484 | 204.8484
5% | 390.344 | 518.6808 | 553.639 | 429.2626 | 429.2506 | 433.2489 | 437.6347 | 446.6295 | 453.0917 | 456.605 | 460.4538 | 463.9708 | 470.3123 | 478.179 | 477.6474 | 477.6474 | 477.6474 | 477.6474 | 477.6474 | 477.6474 | 477.6474 | 477.6474 | 477.6474 | 477.6474 | 477.6474 | 477.6474 | 477.6474 | 477.6474 | 477.6474 | 477.6474 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9.992e-14% | 34.2635 | 45.5286 | 48.5972 | 37.6797 | 37.6787 | 38.0296 | 38.4146 | 39.2041 | 39.7714 | 40.0798 | 40.4176 | 40.7263 | 41.283 | 41.9735 | 41.9268 | 41.9268 | 41.9268 | 41.9268 | 41.9268 | 41.9268 | 41.9268 | 41.9268 | 41.9268 | 41.9268 | 41.9268 | 41.9268 | 41.9268 | 41.9268 | 41.9268 | 41.9268 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E @ R (MWh) | 91763.8061 | 121933.7811 | 130151.918 | 100912.9503 | 100910.1366 | 101850.0668 | 102881.1069 | 104995.6502 | 106514.8161 | 107340.741 | 108245.5268 | 109072.3186 | 110563.102 | 112412.4548 | 112287.4683 | 112287.4683 | 112287.4683 | 112287.4683 | 112287.4683 | 112287.4683 | 112287.4683 | 112287.4683 | 112287.4683 | 112287.4683 | 112287.4683 | 112287.4683 | 112287.4683 | 112287.4683 | 112287.4683 | 112287.4683 | E @ R (MWh) | 89067.5772 | 115381.5956 | 122272.0083 | 96615.9844 | 96650.3869 | 97359.7758 | 99227.3335 | 100479.5072 | 101704.2848 | 103136.2937 | 104464.564 | 105753.071 | 105902.3449 | 107405.8148 | 106270.365 | 106270.365 | 106270.365 | 106270.365 | 106270.365 | 106270.365 | 106270.365 | 106270.365 | 106270.365 | 106270.365 | 106270.365 | 106270.365 | 106270.365 | 106270.365 | 106270.365 | 106270.365
Option 4 Summer POE50 W E @ R (MWh) N 2 | 64234.6643 | 85353.6468 | 91106.3426 | 70639.0652 | 70637.0956 | 71295.0467 | 72016.7748 | 73496.9552 | 74560.3713 | 75138.5187 | 75771.8688 | 76350.623 | 77394.1714 | 78688.7183 | 78601.2278 | 78601.2278 | 78601.2278 | 78601.2278 | 78601.2278 | 78601.2278 | 78601.2278 | 78601.2278 | 78601.2278 | 78601.2278 | 78601.2278 | 78601.2278 | 78601.2278 | 78601.2278 | 78601.2278 | 78601.2278 | Option 4 Summer POE10 W E @ R (MWh) N 2 | 26720.2732 | 34614.4787 | 36681.6025 | 28984.7953 | 28995.1161 | 29207.9328 | 29768.2 | 30143.8522 | 30511.2854 | 30940.8881 | 31339.3692 | 31725.9213 | 31770.7035 | 32221.7444 | 31881.1095 | 31881.1095 | 31881.1095 | 31881.1095 | 31881.1095 | 31881.1095 | 31881.1095 | 31881.1095 | 31881.1095 | 31881.1095 | 31881.1095 | 31881.1095 | 31881.1095 | 31881.1095 | 31881.1095 | 31881.1095
Option 5 - 4A LLG 2nd Tx + Switchroom + Three new feeders + OFR12 New Feeder
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | 59.6718 | 82.8348 | 88.8563 | 47.0044 | 47.805 | 49.1833 | 52.3192 | 54.4183 | 57.0776 | 58.4579 | 59.6722 | 57.4348 | 60.0569 | 64.1793 | 61.051 | 61.051 | 61.051 | 61.051 | 61.051 | 61.051 | 61.051 | 61.051 | 61.051 | 61.051 | 61.051 | 61.051 | 61.051 | 61.051 | 61.051 | 61.051 |  | 63.8857 | 86.7566 | 93.0131 | 51.1029 | 51.7176 | 53.066 | 56.2509 | 57.9898 | 61.3023 | 71.3715 | 63.0705 | 61.4468 | 63.6386 | 68.4319 | 65.1874 | 65.1874 | 65.1874 | 65.1874 | 65.1874 | 65.1874 | 65.1874 | 65.1874 | 65.1874 | 65.1874 | 65.1874 | 65.1874 | 65.1874 | 65.1874 | 65.1874 | 65.1874
98% | 70.8865 | 98.4027 | 105.556 | 55.8384 | 56.7894 | 58.4268 | 62.1521 | 64.6457 | 67.8047 | 69.4444 | 70.8869 | 68.229 | 71.344 | 76.2412 | 72.5249 | 72.5249 | 72.5249 | 72.5249 | 72.5249 | 72.5249 | 72.5249 | 72.5249 | 72.5249 | 72.5249 | 72.5249 | 72.5249 | 72.5249 | 72.5249 | 72.5249 | 72.5249 |  | 75.8924 | 103.0616 | 110.494 | 60.7072 | 61.4374 | 63.0392 | 66.8227 | 68.8884 | 72.8235 | 84.7851 | 74.924 | 72.9951 | 75.5988 | 81.293 | 77.4387 | 77.4387 | 77.4387 | 77.4387 | 77.4387 | 77.4387 | 77.4387 | 77.4387 | 77.4387 | 77.4387 | 77.4387 | 77.4387 | 77.4387 | 77.4387 | 77.4387 | 77.4387
97% | 140.3338 | 194.8074 | 208.9687 | 110.5431 | 112.4258 | 115.6673 | 123.0422 | 127.9788 | 134.2326 | 137.4788 | 140.3346 | 135.0727 | 141.2394 | 150.9343 | 143.5772 | 143.5772 | 143.5772 | 143.5772 | 143.5772 | 143.5772 | 143.5772 | 143.5772 | 143.5772 | 143.5772 | 143.5772 | 143.5772 | 143.5772 | 143.5772 | 143.5772 | 143.5772 |  | 150.2438 | 204.0305 | 218.7445 | 120.1817 | 121.6272 | 124.7985 | 132.2886 | 136.378 | 144.1683 | 167.8486 | 148.3266 | 144.5081 | 149.6626 | 160.9354 | 153.305 | 153.305 | 153.305 | 153.305 | 153.305 | 153.305 | 153.305 | 153.305 | 153.305 | 153.305 | 153.305 | 153.305 | 153.305 | 153.305 | 153.305 | 153.305
95% | 414.5243 | 575.4311 | 617.2612 | 326.5273 | 332.0884 | 341.6635 | 363.4476 | 378.0297 | 396.5026 | 406.0911 | 414.5267 | 398.9839 | 417.1996 | 445.8367 | 424.1051 | 424.1051 | 424.1051 | 424.1051 | 424.1051 | 424.1051 | 424.1051 | 424.1051 | 424.1051 | 424.1051 | 424.1051 | 424.1051 | 424.1051 | 424.1051 | 424.1051 | 424.1051 |  | 443.7972 | 602.6746 | 646.1375 | 354.9982 | 359.2682 | 368.6356 | 390.7602 | 402.8398 | 425.8511 | 495.799 | 438.1341 | 426.8547 | 442.0804 | 475.3784 | 452.8394 | 452.8394 | 452.8394 | 452.8394 | 452.8394 | 452.8394 | 452.8394 | 452.8394 | 452.8394 | 452.8394 | 452.8394 | 452.8394 | 452.8394 | 452.8394 | 452.8394 | 452.8394
90% | 2285.5212 | 3172.6969 | 3403.3313 | 1800.3406 | 1831.0025 | 1883.7955 | 2003.9047 | 2084.3042 | 2186.1565 | 2239.0239 | 2285.5343 | 2199.8376 | 2300.2714 | 2458.1649 | 2338.3456 | 2338.3456 | 2338.3456 | 2338.3456 | 2338.3456 | 2338.3456 | 2338.3456 | 2338.3456 | 2338.3456 | 2338.3456 | 2338.3456 | 2338.3456 | 2338.3456 | 2338.3456 | 2338.3456 | 2338.3456 |  | 2446.9201 | 3322.9067 | 3562.5435 | 1957.3177 | 1980.8608 | 2032.5091 | 2154.4955 | 2221.0971 | 2347.9722 | 2733.6372 | 2415.6957 | 2353.506 | 2437.454 | 2621.0462 | 2496.7752 | 2496.7752 | 2496.7752 | 2496.7752 | 2496.7752 | 2496.7752 | 2496.7752 | 2496.7752 | 2496.7752 | 2496.7752 | 2496.7752 | 2496.7752 | 2496.7752 | 2496.7752 | 2496.7752 | 2496.7752
85% | 5583.3646 | 7750.6712 | 8314.0946 | 4398.1031 | 4473.0078 | 4601.9775 | 4895.3957 | 5091.8059 | 5340.6238 | 5469.775 | 5583.3965 | 5374.0456 | 5619.3982 | 6005.1208 | 5712.4108 | 5712.4108 | 5712.4108 | 5712.4108 | 5712.4108 | 5712.4108 | 5712.4108 | 5712.4108 | 5712.4108 | 5712.4108 | 5712.4108 | 5712.4108 | 5712.4108 | 5712.4108 | 5712.4108 | 5712.4108 |  | 5977.6505 | 8117.623 | 8703.0385 | 4781.5869 | 4839.101 | 4965.2742 | 5263.2782 | 5425.9812 | 5735.9279 | 6678.08 | 5901.3716 | 5749.4466 | 5954.5256 | 6403.0281 | 6099.443 | 6099.443 | 6099.443 | 6099.443 | 6099.443 | 6099.443 | 6099.443 | 6099.443 | 6099.443 | 6099.443 | 6099.443 | 6099.443 | 6099.443 | 6099.443 | 6099.443 | 6099.443
80% | 8678.2039 | 12046.8408 | 12922.5678 | 6835.9561 | 6952.3802 | 7152.8374 | 7608.8962 | 7914.1758 | 8300.9126 | 8501.6518 | 8678.2534 | 8352.8601 | 8734.2107 | 9333.738 | 8878.7799 | 8878.7799 | 8878.7799 | 8878.7799 | 8878.7799 | 8878.7799 | 8878.7799 | 8878.7799 | 8878.7799 | 8878.7799 | 8878.7799 | 8878.7799 | 8878.7799 | 8878.7799 | 8878.7799 | 8878.7799 |  | 9291.041 | 12617.1926 | 13527.1019 | 7432.0036 | 7521.3975 | 7717.5081 | 8180.6946 | 8433.5833 | 8915.3324 | 10379.716 | 9172.4809 | 8936.3444 | 9255.098 | 9952.2038 | 9480.3426 | 9480.3426 | 9480.3426 | 9480.3426 | 9480.3426 | 9480.3426 | 9480.3426 | 9480.3426 | 9480.3426 | 9480.3426 | 9480.3426 | 9480.3426 | 9480.3426 | 9480.3426 | 9480.3426 | 9480.3426
75% | 9574.4808 | 13291.0275 | 14257.1987 | 7541.9674 | 7670.4157 | 7891.5759 | 8394.736 | 8731.5446 | 9158.2233 | 9379.6947 | 9574.5355 | 9215.5358 | 9636.2719 | 10297.7179 | 9795.7722 | 9795.7722 | 9795.7722 | 9795.7722 | 9795.7722 | 9795.7722 | 9795.7722 | 9795.7722 | 9795.7722 | 9795.7722 | 9795.7722 | 9795.7722 | 9795.7722 | 9795.7722 | 9795.7722 | 9795.7722 |  | 10250.6112 | 13920.2847 | 14924.1686 | 8199.5742 | 8298.2005 | 8514.5653 | 9025.5892 | 9304.5961 | 9836.0998 | 11451.7236 | 10119.8063 | 9859.2819 | 10210.9561 | 10980.0583 | 10459.4637 | 10459.4637 | 10459.4637 | 10459.4637 | 10459.4637 | 10459.4637 | 10459.4637 | 10459.4637 | 10459.4637 | 10459.4637 | 10459.4637 | 10459.4637 | 10459.4637 | 10459.4637 | 10459.4637 | 10459.4637
70% | 10287.2444 | 14280.4661 | 15318.563 | 8103.4224 | 8241.4329 | 8479.0571 | 9019.6746 | 9381.5566 | 9839.9989 | 10077.9576 | 10287.3031 | 9901.5781 | 10353.6355 | 11064.3222 | 10525.0096 | 10525.0096 | 10525.0096 | 10525.0096 | 10525.0096 | 10525.0096 | 10525.0096 | 10525.0096 | 10525.0096 | 10525.0096 | 10525.0096 | 10525.0096 | 10525.0096 | 10525.0096 | 10525.0096 | 10525.0096 |  | 11013.7087 | 14956.5677 | 16035.1849 | 8809.9841 | 8915.9525 | 9148.4244 | 9697.4911 | 9997.2683 | 10568.3393 | 12304.2368 | 10873.1662 | 10593.2472 | 10971.1015 | 11797.4589 | 11238.1091 | 11238.1091 | 11238.1091 | 11238.1091 | 11238.1091 | 11238.1091 | 11238.1091 | 11238.1091 | 11238.1091 | 11238.1091 | 11238.1091 | 11238.1091 | 11238.1091 | 11238.1091 | 11238.1091 | 11238.1091
65% | 10840.7831 | 15048.8731 | 16142.8282 | 8539.4534 | 8684.89 | 8935.3004 | 9505.0076 | 9886.3618 | 10369.4722 | 10620.2349 | 10840.845 | 10434.3648 | 10910.7466 | 11659.6741 | 11091.3421 | 11091.3421 | 11091.3421 | 11091.3421 | 11091.3421 | 11091.3421 | 11091.3421 | 11091.3421 | 11091.3421 | 11091.3421 | 11091.3421 | 11091.3421 | 11091.3421 | 11091.3421 | 11091.3421 | 11091.3421 |  | 11606.3372 | 15761.3546 | 16898.0103 | 9284.034 | 9395.7044 | 9640.6853 | 10219.2962 | 10535.2039 | 11137.0033 | 12966.3064 | 11458.2323 | 11163.2514 | 11561.4374 | 12432.2596 | 11842.8122 | 11842.8122 | 11842.8122 | 11842.8122 | 11842.8122 | 11842.8122 | 11842.8122 | 11842.8122 | 11842.8122 | 11842.8122 | 11842.8122 | 11842.8122 | 11842.8122 | 11842.8122 | 11842.8122 | 11842.8122
60% | 11934.3669 | 16566.9557 | 17771.2656 | 9400.8864 | 9560.9942 | 9836.6652 | 10463.8426 | 10883.6666 | 11415.5116 | 11691.5705 | 11934.4351 | 11486.9504 | 12011.3881 | 12835.8651 | 12210.2015 | 12210.2015 | 12210.2015 | 12210.2015 | 12210.2015 | 12210.2015 | 12210.2015 | 12210.2015 | 12210.2015 | 12210.2015 | 12210.2015 | 12210.2015 | 12210.2015 | 12210.2015 | 12210.2015 | 12210.2015 |  | 12777.1477 | 17351.3101 | 18602.628 | 10220.5779 | 10343.5133 | 10613.207 | 11250.1864 | 11597.9619 | 12260.4689 | 14274.3063 | 12614.1025 | 12289.3648 | 12727.7185 | 13686.3865 | 13037.4775 | 13037.4775 | 13037.4775 | 13037.4775 | 13037.4775 | 13037.4775 | 13037.4775 | 13037.4775 | 13037.4775 | 13037.4775 | 13037.4775 | 13037.4775 | 13037.4775 | 13037.4775 | 13037.4775 | 13037.4775
55% | 13276.2336 | 18429.6976 | 19769.4166 | 10457.8956 | 10636.0055 | 10942.6721 | 11640.3676 | 12107.3955 | 12699.0396 | 13006.1378 | 13276.3094 | 12778.5108 | 13361.9148 | 14279.0936 | 13583.0822 | 13583.0822 | 13583.0822 | 13583.0822 | 13583.0822 | 13583.0822 | 13583.0822 | 13583.0822 | 13583.0822 | 13583.0822 | 13583.0822 | 13583.0822 | 13583.0822 | 13583.0822 | 13583.0822 | 13583.0822 |  | 14213.7742 | 19302.2426 | 20694.2551 | 11369.7509 | 11506.5088 | 11806.5261 | 12515.1257 | 12902.0041 | 13639.0015 | 15879.2691 | 14032.3966 | 13671.1464 | 14158.7874 | 15225.2453 | 14503.3748 | 14503.3748 | 14503.3748 | 14503.3748 | 14503.3748 | 14503.3748 | 14503.3748 | 14503.3748 | 14503.3748 | 14503.3748 | 14503.3748 | 14503.3748 | 14503.3748 | 14503.3748 | 14503.3748 | 14503.3748
50% | 13456.7484 | 18680.2832 | 20038.2182 | 10600.09 | 10780.6215 | 11091.4579 | 11798.6398 | 12272.0178 | 12871.7064 | 13182.9802 | 13456.8252 | 12952.2581 | 13543.5946 | 14473.2442 | 13767.7692 | 13767.7692 | 13767.7692 | 13767.7692 | 13767.7692 | 13767.7692 | 13767.7692 | 13767.7692 | 13767.7692 | 13767.7692 | 13767.7692 | 13767.7692 | 13767.7692 | 13767.7692 | 13767.7692 | 13767.7692 |  | 14407.0366 | 19564.692 | 20975.6315 | 11524.3436 | 11662.961 | 11967.0576 | 12685.2918 | 13077.4306 | 13824.4488 | 16095.1769 | 14223.1929 | 13857.0308 | 14351.3021 | 15432.2605 | 14700.5748 | 14700.5748 | 14700.5748 | 14700.5748 | 14700.5748 | 14700.5748 | 14700.5748 | 14700.5748 | 14700.5748 | 14700.5748 | 14700.5748 | 14700.5748 | 14700.5748 | 14700.5748 | 14700.5748 | 14700.5748
45% | 10386.1977 | 14417.8303 | 15465.9127 | 8181.3694 | 8320.7075 | 8560.6174 | 9106.4351 | 9471.798 | 9934.6502 | 10174.8977 | 10386.257 | 9996.8216 | 10453.2274 | 11170.7502 | 10626.25 | 10626.25 | 10626.25 | 10626.25 | 10626.25 | 10626.25 | 10626.25 | 10626.25 | 10626.25 | 10626.25 | 10626.25 | 10626.25 | 10626.25 | 10626.25 | 10626.25 | 10626.25 |  | 11119.6499 | 15100.4354 | 16189.4278 | 8894.7275 | 9001.7153 | 9236.4234 | 9790.7715 | 10093.4323 | 10669.9965 | 12422.5916 | 10977.7554 | 10695.144 | 11076.6328 | 11910.9389 | 11346.2087 | 11346.2087 | 11346.2087 | 11346.2087 | 11346.2087 | 11346.2087 | 11346.2087 | 11346.2087 | 11346.2087 | 11346.2087 | 11346.2087 | 11346.2087 | 11346.2087 | 11346.2087 | 11346.2087 | 11346.2087
40% | 5102.6915 | 7083.4142 | 7598.3323 | 4019.4695 | 4087.9256 | 4205.7922 | 4473.95 | 4653.4511 | 4880.8483 | 4998.8808 | 5102.7206 | 4911.3928 | 5135.6229 | 5488.1386 | 5220.6281 | 5220.6281 | 5220.6281 | 5220.6281 | 5220.6281 | 5220.6281 | 5220.6281 | 5220.6281 | 5220.6281 | 5220.6281 | 5220.6281 | 5220.6281 | 5220.6281 | 5220.6281 | 5220.6281 | 5220.6281 |  | 5463.0332 | 7418.775 | 7953.792 | 4369.939 | 4422.5017 | 4537.8127 | 4810.1614 | 4958.8572 | 5242.1206 | 6103.1625 | 5393.3211 | 5254.4754 | 5441.8992 | 5851.7899 | 5574.3406 | 5574.3406 | 5574.3406 | 5574.3406 | 5574.3406 | 5574.3406 | 5574.3406 | 5574.3406 | 5574.3406 | 5574.3406 | 5574.3406 | 5574.3406 | 5574.3406 | 5574.3406 | 5574.3406 | 5574.3406
35% | 1907.0998 | 2647.3829 | 2839.8304 | 1502.2522 | 1527.8373 | 1571.8892 | 1672.1115 | 1739.199 | 1824.1873 | 1868.3012 | 1907.1107 | 1835.6031 | 1919.4078 | 2051.1583 | 1951.1779 | 1951.1779 | 1951.1779 | 1951.1779 | 1951.1779 | 1951.1779 | 1951.1779 | 1951.1779 | 1951.1779 | 1951.1779 | 1951.1779 | 1951.1779 | 1951.1779 | 1951.1779 | 1951.1779 | 1951.1779 |  | 2041.7754 | 2772.7219 | 2972.6813 | 1633.2381 | 1652.883 | 1695.9798 | 1797.7685 | 1853.3427 | 1959.2106 | 2281.0198 | 2015.7209 | 1963.8282 | 2033.8766 | 2187.0708 | 2083.3758 | 2083.3758 | 2083.3758 | 2083.3758 | 2083.3758 | 2083.3758 | 2083.3758 | 2083.3758 | 2083.3758 | 2083.3758 | 2083.3758 | 2083.3758 | 2083.3758 | 2083.3758 | 2083.3758 | 2083.3758
30% | 951.1511 | 1320.3614 | 1416.3431 | 749.2365 | 761.9968 | 783.9674 | 833.9525 | 867.4118 | 909.7991 | 931.8005 | 951.1565 | 915.4926 | 957.2895 | 1022.9991 | 973.1347 | 973.1347 | 973.1347 | 973.1347 | 973.1347 | 973.1347 | 973.1347 | 973.1347 | 973.1347 | 973.1347 | 973.1347 | 973.1347 | 973.1347 | 973.1347 | 973.1347 | 973.1347 |  | 1018.3194 | 1382.8733 | 1482.6014 | 814.5646 | 824.3624 | 845.8566 | 896.6229 | 924.3401 | 977.1409 | 1137.6407 | 1005.3249 | 979.4439 | 1014.38 | 1090.7844 | 1039.0673 | 1039.0673 | 1039.0673 | 1039.0673 | 1039.0673 | 1039.0673 | 1039.0673 | 1039.0673 | 1039.0673 | 1039.0673 | 1039.0673 | 1039.0673 | 1039.0673 | 1039.0673 | 1039.0673 | 1039.0673
25% | 560.7353 | 778.3972 | 834.9816 | 441.6999 | 449.2226 | 462.175 | 491.6429 | 511.3683 | 536.357 | 549.3276 | 560.7385 | 539.7135 | 564.3542 | 603.0922 | 573.6954 | 573.6954 | 573.6954 | 573.6954 | 573.6954 | 573.6954 | 573.6954 | 573.6954 | 573.6954 | 573.6954 | 573.6954 | 573.6954 | 573.6954 | 573.6954 | 573.6954 | 573.6954 |  | 600.3333 | 815.25 | 874.0431 | 480.2131 | 485.9892 | 498.6607 | 528.5892 | 544.9294 | 576.0572 | 670.6772 | 592.6727 | 577.4149 | 598.0109 | 643.0538 | 612.5649 | 612.5649 | 612.5649 | 612.5649 | 612.5649 | 612.5649 | 612.5649 | 612.5649 | 612.5649 | 612.5649 | 612.5649 | 612.5649 | 612.5649 | 612.5649 | 612.5649 | 612.5649
20% | 283.3663 | 393.3611 | 421.9559 | 223.212 | 227.0136 | 233.559 | 248.4505 | 258.4187 | 271.0467 | 277.6014 | 283.3679 | 272.7429 | 285.195 | 304.7712 | 289.9156 | 289.9156 | 289.9156 | 289.9156 | 289.9156 | 289.9156 | 289.9156 | 289.9156 | 289.9156 | 289.9156 | 289.9156 | 289.9156 | 289.9156 | 289.9156 | 289.9156 | 289.9156 |  | 303.377 | 411.9846 | 441.6956 | 242.6745 | 245.5935 | 251.997 | 267.1213 | 275.3787 | 291.1091 | 338.9251 | 299.5057 | 291.7952 | 302.2034 | 324.9657 | 309.5582 | 309.5582 | 309.5582 | 309.5582 | 309.5582 | 309.5582 | 309.5582 | 309.5582 | 309.5582 | 309.5582 | 309.5582 | 309.5582 | 309.5582 | 309.5582 | 309.5582 | 309.5582
15% | 115.4455 | 160.2582 | 171.908 | 90.9382 | 92.487 | 95.1537 | 101.2206 | 105.2817 | 110.4264 | 113.0969 | 115.4462 | 111.1175 | 116.1906 | 124.166 | 118.1138 | 118.1138 | 118.1138 | 118.1138 | 118.1138 | 118.1138 | 118.1138 | 118.1138 | 118.1138 | 118.1138 | 118.1138 | 118.1138 | 118.1138 | 118.1138 | 118.1138 | 118.1138 |  | 123.598 | 167.8456 | 179.95 | 98.8674 | 100.0566 | 102.6654 | 108.8272 | 112.1913 | 118.6 | 138.0806 | 122.0208 | 118.8795 | 123.1199 | 132.3934 | 126.1163 | 126.1163 | 126.1163 | 126.1163 | 126.1163 | 126.1163 | 126.1163 | 126.1163 | 126.1163 | 126.1163 | 126.1163 | 126.1163 | 126.1163 | 126.1163 | 126.1163 | 126.1163
10% | 46.4781 | 64.5196 | 69.2097 | 36.6115 | 37.235 | 38.3086 | 40.7511 | 42.3861 | 44.4574 | 45.5325 | 46.4783 | 44.7356 | 46.778 | 49.9889 | 47.5523 | 47.5523 | 47.5523 | 47.5523 | 47.5523 | 47.5523 | 47.5523 | 47.5523 | 47.5523 | 47.5523 | 47.5523 | 47.5523 | 47.5523 | 47.5523 | 47.5523 | 47.5523 |  | 49.7602 | 67.5742 | 72.4474 | 39.8038 | 40.2825 | 41.3328 | 43.8135 | 45.1679 | 47.7481 | 55.5909 | 49.1253 | 47.8606 | 49.5677 | 53.3013 | 50.7741 | 50.7741 | 50.7741 | 50.7741 | 50.7741 | 50.7741 | 50.7741 | 50.7741 | 50.7741 | 50.7741 | 50.7741 | 50.7741 | 50.7741 | 50.7741 | 50.7741 | 50.7741
5% | 39.5813 | 54.9457 | 58.9399 | 31.1788 | 31.7098 | 32.6241 | 34.7042 | 36.0966 | 37.8605 | 38.7761 | 39.5815 | 38.0974 | 39.8368 | 42.5712 | 40.4961 | 40.4961 | 40.4961 | 40.4961 | 40.4961 | 40.4961 | 40.4961 | 40.4961 | 40.4961 | 40.4961 | 40.4961 | 40.4961 | 40.4961 | 40.4961 | 40.4961 | 40.4961 |  | 42.3765 | 57.5471 | 61.6972 | 33.8974 | 34.3051 | 35.1996 | 37.3122 | 38.4656 | 40.6629 | 47.3419 | 41.8357 | 40.7587 | 42.2125 | 45.392 | 43.2399 | 43.2399 | 43.2399 | 43.2399 | 43.2399 | 43.2399 | 43.2399 | 43.2399 | 43.2399 | 43.2399 | 43.2399 | 43.2399 | 43.2399 | 43.2399 | 43.2399 | 43.2399
9.992e-14% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E @ R (MWh) | 105995.1099 | 147139.4588 | 157835.5397 | 83493.9964 | 84915.9942 | 87364.3666 | 92934.6444 | 96663.3127 | 101386.8952 | 103838.7131 | 105995.715 | 102021.3788 | 106679.1739 | 114001.768 | 108444.9352 | 108444.9352 | 108444.9352 | 108444.9352 | 108444.9352 | 108444.9352 | 108444.9352 | 108444.9352 | 108444.9352 | 108444.9352 | 108444.9352 | 108444.9352 | 108444.9352 | 108444.9352 | 108444.9352 | 108444.9352 | E @ R (MWh) | 113480.2695 | 154105.704 | 165219.287 | 90774.0881 | 91865.9395 | 94261.2247 | 99918.5588 | 103007.3279 | 108891.3852 | 126777.2868 | 112032.1827 | 109148.0247 | 113041.2642 | 121555.6763 | 115792.3892 | 115792.3892 | 115792.3892 | 115792.3892 | 115792.3892 | 115792.3892 | 115792.3892 | 115792.3892 | 115792.3892 | 115792.3892 | 115792.3892 | 115792.3892 | 115792.3892 | 115792.3892 | 115792.3892 | 115792.3892
Option 5 Winter POE50 W E @ R (MWh) N 2 | 74196.5769 | 102997.6211 | 110484.8778 | 58445.7975 | 59441.1959 | 61155.0566 | 65054.2511 | 67664.3189 | 70970.8267 | 72687.0992 | 74197.0005 | 71414.9651 | 74675.4217 | 79801.2376 | 75911.4547 | 75911.4547 | 75911.4547 | 75911.4547 | 75911.4547 | 75911.4547 | 75911.4547 | 75911.4547 | 75911.4547 | 75911.4547 | 75911.4547 | 75911.4547 | 75911.4547 | 75911.4547 | 75911.4547 | 75911.4547 | Option 5 Winter POE10 W E @ R (MWh) N 2 | 34044.0809 | 46231.7112 | 49565.7861 | 27232.2264 | 27559.7818 | 28278.3674 | 29975.5676 | 30902.1984 | 32667.4155 | 38033.1861 | 33609.6548 | 32744.4074 | 33912.3793 | 36466.7029 | 34737.7168 | 34737.7168 | 34737.7168 | 34737.7168 | 34737.7168 | 34737.7168 | 34737.7168 | 34737.7168 | 34737.7168 | 34737.7168 | 34737.7168 | 34737.7168 | 34737.7168 | 34737.7168 | 34737.7168 | 34737.7168
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 76.9936 | 99.7405 | 105.6969 | 61.6949 | 61.7246 | 62.3379 | 63.9522 | 65.0347 | 66.0934 | 67.3313 | 68.4795 | 69.5934 | 69.7224 | 71.0221 | 70.0405 | 70.0405 | 70.0405 | 70.0405 | 70.0405 | 70.0405 | 70.0405 | 70.0405 | 70.0405 | 70.0405 | 70.0405 | 70.0405 | 70.0405 | 70.0405 | 70.0405 | 70.0405
98% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 38.1099 | 49.369 | 52.3173 | 30.5374 | 30.5521 | 30.8557 | 31.6548 | 32.1905 | 32.7146 | 33.3273 | 33.8956 | 34.447 | 34.5108 | 35.1541 | 34.6683 | 34.6683 | 34.6683 | 34.6683 | 34.6683 | 34.6683 | 34.6683 | 34.6683 | 34.6683 | 34.6683 | 34.6683 | 34.6683 | 34.6683 | 34.6683 | 34.6683 | 34.6683
97% | 16.9149 | 22.4762 | 23.991 | 13.2551 | 13.2546 | 13.4278 | 13.6179 | 14.0076 | 14.2877 | 14.4399 | 14.6067 | 14.7591 | 15.0339 | 15.3748 | 15.3518 | 15.3518 | 15.3518 | 15.3518 | 15.3518 | 15.3518 | 15.3518 | 15.3518 | 15.3518 | 15.3518 | 15.3518 | 15.3518 | 15.3518 | 15.3518 | 15.3518 | 15.3518 |  | 75.446 | 97.7357 | 103.5723 | 60.4548 | 60.4839 | 61.0848 | 62.6668 | 63.7274 | 64.7649 | 65.9779 | 67.103 | 68.1945 | 68.3209 | 69.5945 | 68.6327 | 68.6327 | 68.6327 | 68.6327 | 68.6327 | 68.6327 | 68.6327 | 68.6327 | 68.6327 | 68.6327 | 68.6327 | 68.6327 | 68.6327 | 68.6327 | 68.6327 | 68.6327
95% | 83.2734 | 110.6519 | 118.1097 | 65.2558 | 65.2532 | 66.1062 | 67.0418 | 68.9607 | 70.3393 | 71.0888 | 71.9099 | 72.6602 | 74.0131 | 75.6913 | 75.5779 | 75.5779 | 75.5779 | 75.5779 | 75.5779 | 75.5779 | 75.5779 | 75.5779 | 75.5779 | 75.5779 | 75.5779 | 75.5779 | 75.5779 | 75.5779 | 75.5779 | 75.5779 |  | 111.4279 | 144.3481 | 152.9683 | 89.2871 | 89.3301 | 90.2176 | 92.554 | 94.1205 | 95.6528 | 97.4443 | 99.106 | 100.718 | 100.9048 | 102.7857 | 101.3652 | 101.3652 | 101.3652 | 101.3652 | 101.3652 | 101.3652 | 101.3652 | 101.3652 | 101.3652 | 101.3652 | 101.3652 | 101.3652 | 101.3652 | 101.3652 | 101.3652 | 101.3652
90% | 144.4273 | 191.9119 | 204.8464 | 113.178 | 113.1736 | 114.6529 | 116.2757 | 119.6038 | 121.9948 | 123.2947 | 124.7188 | 126.02 | 128.3664 | 131.2771 | 131.0804 | 131.0804 | 131.0804 | 131.0804 | 131.0804 | 131.0804 | 131.0804 | 131.0804 | 131.0804 | 131.0804 | 131.0804 | 131.0804 | 131.0804 | 131.0804 | 131.0804 | 131.0804 |  | 483.1446 | 625.8842 | 663.261 | 387.1432 | 387.3298 | 391.1779 | 401.3084 | 408.1008 | 414.7445 | 422.5124 | 429.7176 | 436.7071 | 437.5168 | 445.6723 | 439.5131 | 439.5131 | 439.5131 | 439.5131 | 439.5131 | 439.5131 | 439.5131 | 439.5131 | 439.5131 | 439.5131 | 439.5131 | 439.5131 | 439.5131 | 439.5131 | 439.5131 | 439.5131
85% | 409.8612 | 544.6148 | 581.321 | 321.1808 | 321.1682 | 325.3664 | 329.9715 | 339.4161 | 346.2014 | 349.8904 | 353.9316 | 357.6244 | 364.283 | 372.5431 | 371.9848 | 371.9848 | 371.9848 | 371.9848 | 371.9848 | 371.9848 | 371.9848 | 371.9848 | 371.9848 | 371.9848 | 371.9848 | 371.9848 | 371.9848 | 371.9848 | 371.9848 | 371.9848 |  | 457.0286 | 592.0526 | 627.4091 | 366.2165 | 366.3931 | 370.0331 | 379.616 | 386.0413 | 392.3259 | 399.6739 | 406.4896 | 413.1013 | 413.8672 | 421.5819 | 415.7557 | 415.7557 | 415.7557 | 415.7557 | 415.7557 | 415.7557 | 415.7557 | 415.7557 | 415.7557 | 415.7557 | 415.7557 | 415.7557 | 415.7557 | 415.7557 | 415.7557 | 415.7557
80% | 572.5046 | 760.7318 | 812.0039 | 448.6335 | 448.6159 | 454.48 | 460.9126 | 474.105 | 483.5829 | 488.7358 | 494.3806 | 499.5389 | 508.8397 | 520.3777 | 519.5979 | 519.5979 | 519.5979 | 519.5979 | 519.5979 | 519.5979 | 519.5979 | 519.5979 | 519.5979 | 519.5979 | 519.5979 | 519.5979 | 519.5979 | 519.5979 | 519.5979 | 519.5979 |  | 319.1946 | 413.4971 | 438.1905 | 255.7703 | 255.8936 | 258.4358 | 265.1287 | 269.6161 | 274.0054 | 279.1373 | 283.8975 | 288.5152 | 289.0501 | 294.4382 | 290.369 | 290.369 | 290.369 | 290.369 | 290.369 | 290.369 | 290.369 | 290.369 | 290.369 | 290.369 | 290.369 | 290.369 | 290.369 | 290.369 | 290.369 | 290.369
75% | 1492.4153 | 1983.0895 | 2116.7465 | 1169.5059 | 1169.4601 | 1184.7468 | 1201.5153 | 1235.9055 | 1260.6127 | 1274.0453 | 1288.7604 | 1302.2071 | 1326.4527 | 1356.5299 | 1354.4972 | 1354.4972 | 1354.4972 | 1354.4972 | 1354.4972 | 1354.4972 | 1354.4972 | 1354.4972 | 1354.4972 | 1354.4972 | 1354.4972 | 1354.4972 | 1354.4972 | 1354.4972 | 1354.4972 | 1354.4972 |  | 569.714 | 738.0296 | 782.1036 | 456.5112 | 456.7313 | 461.2688 | 473.2145 | 481.2239 | 489.0581 | 498.2179 | 506.714 | 514.9559 | 515.9107 | 525.5275 | 518.2647 | 518.2647 | 518.2647 | 518.2647 | 518.2647 | 518.2647 | 518.2647 | 518.2647 | 518.2647 | 518.2647 | 518.2647 | 518.2647 | 518.2647 | 518.2647 | 518.2647 | 518.2647
70% | 2578.4391 | 3426.1747 | 3657.0932 | 2020.55 | 2020.471 | 2046.8817 | 2075.8526 | 2135.2684 | 2177.9549 | 2201.1623 | 2226.5855 | 2249.8173 | 2291.7063 | 2343.6706 | 2340.1586 | 2340.1586 | 2340.1586 | 2340.1586 | 2340.1586 | 2340.1586 | 2340.1586 | 2340.1586 | 2340.1586 | 2340.1586 | 2340.1586 | 2340.1586 | 2340.1586 | 2340.1586 | 2340.1586 | 2340.1586 |  | 1037.8661 | 1344.492 | 1424.783 | 831.641 | 832.0418 | 840.308 | 862.0699 | 876.6609 | 890.9327 | 907.6193 | 923.0971 | 938.1115 | 939.8509 | 957.3702 | 944.1393 | 944.1393 | 944.1393 | 944.1393 | 944.1393 | 944.1393 | 944.1393 | 944.1393 | 944.1393 | 944.1393 | 944.1393 | 944.1393 | 944.1393 | 944.1393 | 944.1393 | 944.1393
65% | 6475.8072 | 8604.914 | 9184.8711 | 5074.6564 | 5074.4578 | 5140.7891 | 5213.55 | 5362.7741 | 5469.9822 | 5528.2681 | 5592.1192 | 5650.4662 | 5755.6713 | 5886.1809 | 5877.3605 | 5877.3605 | 5877.3605 | 5877.3605 | 5877.3605 | 5877.3605 | 5877.3605 | 5877.3605 | 5877.3605 | 5877.3605 | 5877.3605 | 5877.3605 | 5877.3605 | 5877.3605 | 5877.3605 | 5877.3605 |  | 1305.7961 | 1691.5789 | 1792.5974 | 1046.333 | 1046.8374 | 1057.2375 | 1084.6173 | 1102.9751 | 1120.9312 | 1141.9255 | 1161.3989 | 1180.2894 | 1182.4778 | 1204.5198 | 1187.8733 | 1187.8733 | 1187.8733 | 1187.8733 | 1187.8733 | 1187.8733 | 1187.8733 | 1187.8733 | 1187.8733 | 1187.8733 | 1187.8733 | 1187.8733 | 1187.8733 | 1187.8733 | 1187.8733 | 1187.8733
60% | 9465.8424 | 12578.0087 | 13425.7459 | 7417.7467 | 7417.4564 | 7514.4144 | 7620.7707 | 7838.8952 | 7995.6039 | 8080.8017 | 8174.1344 | 8259.4216 | 8413.2025 | 8603.9714 | 8591.0785 | 8591.0785 | 8591.0785 | 8591.0785 | 8591.0785 | 8591.0785 | 8591.0785 | 8591.0785 | 8591.0785 | 8591.0785 | 8591.0785 | 8591.0785 | 8591.0785 | 8591.0785 | 8591.0785 | 8591.0785 |  | 2043.3291 | 2647.0078 | 2805.083 | 1637.3174 | 1638.1066 | 1654.3809 | 1697.2252 | 1725.9517 | 1754.0498 | 1786.902 | 1817.3742 | 1846.9343 | 1850.3589 | 1884.8505 | 1858.8017 | 1858.8017 | 1858.8017 | 1858.8017 | 1858.8017 | 1858.8017 | 1858.8017 | 1858.8017 | 1858.8017 | 1858.8017 | 1858.8017 | 1858.8017 | 1858.8017 | 1858.8017 | 1858.8017 | 1858.8017
55% | 10703.6666 | 14222.8031 | 15181.3967 | 8387.7466 | 8387.4184 | 8497.0553 | 8617.3196 | 8863.9677 | 9041.1688 | 9137.5077 | 9243.0452 | 9339.4853 | 9513.3757 | 9729.091 | 9714.5121 | 9714.5121 | 9714.5121 | 9714.5121 | 9714.5121 | 9714.5121 | 9714.5121 | 9714.5121 | 9714.5121 | 9714.5121 | 9714.5121 | 9714.5121 | 9714.5121 | 9714.5121 | 9714.5121 | 9714.5121 |  | 3926.5772 | 5086.6405 | 5390.4069 | 3146.362 | 3147.8787 | 3179.1524 | 3261.4843 | 3316.6869 | 3370.6816 | 3433.8123 | 3492.3696 | 3549.1739 | 3555.7547 | 3622.0357 | 3571.979 | 3571.979 | 3571.979 | 3571.979 | 3571.979 | 3571.979 | 3571.979 | 3571.979 | 3571.979 | 3571.979 | 3571.979 | 3571.979 | 3571.979 | 3571.979 | 3571.979 | 3571.979
50% | 13744.0128 | 18262.75 | 19493.6294 | 10770.2623 | 10769.8409 | 10910.6198 | 11065.0449 | 11381.7526 | 11609.2872 | 11732.9909 | 11868.5061 | 11992.3396 | 12215.6231 | 12492.6117 | 12473.8917 | 12473.8917 | 12473.8917 | 12473.8917 | 12473.8917 | 12473.8917 | 12473.8917 | 12473.8917 | 12473.8917 | 12473.8917 | 12473.8917 | 12473.8917 | 12473.8917 | 12473.8917 | 12473.8917 | 12473.8917 |  | 8714.0125 | 11288.47 | 11962.6002 | 6982.5288 | 6985.8946 | 7055.2983 | 7238.0126 | 7360.5203 | 7480.3476 | 7620.4495 | 7750.4022 | 7876.4645 | 7891.0688 | 8038.1623 | 7927.0744 | 7927.0744 | 7927.0744 | 7927.0744 | 7927.0744 | 7927.0744 | 7927.0744 | 7927.0744 | 7927.0744 | 7927.0744 | 7927.0744 | 7927.0744 | 7927.0744 | 7927.0744 | 7927.0744 | 7927.0744
45% | 18302.3635 | 24319.7888 | 25958.9027 | 14342.3364 | 14341.7752 | 14529.2451 | 14734.8868 | 15156.6342 | 15459.633 | 15624.3644 | 15804.8246 | 15969.7289 | 16267.0668 | 16635.9217 | 16610.993 | 16610.993 | 16610.993 | 16610.993 | 16610.993 | 16610.993 | 16610.993 | 16610.993 | 16610.993 | 16610.993 | 16610.993 | 16610.993 | 16610.993 | 16610.993 | 16610.993 | 16610.993 |  | 13204.5002 | 17105.6219 | 18127.1435 | 10580.7517 | 10585.8519 | 10691.0207 | 10967.891 | 11153.529 | 11335.1054 | 11547.4045 | 11744.324 | 11935.3485 | 11957.4788 | 12180.3721 | 12012.0387 | 12012.0387 | 12012.0387 | 12012.0387 | 12012.0387 | 12012.0387 | 12012.0387 | 12012.0387 | 12012.0387 | 12012.0387 | 12012.0387 | 12012.0387 | 12012.0387 | 12012.0387 | 12012.0387 | 12012.0387
40% | 12836.6798 | 17057.1053 | 18206.7263 | 10059.2462 | 10058.8526 | 10190.3378 | 10334.5682 | 10630.368 | 10842.8815 | 10958.4187 | 11084.9876 | 11200.6461 | 11409.1892 | 11667.892 | 11650.4078 | 11650.4078 | 11650.4078 | 11650.4078 | 11650.4078 | 11650.4078 | 11650.4078 | 11650.4078 | 11650.4078 | 11650.4078 | 11650.4078 | 11650.4078 | 11650.4078 | 11650.4078 | 11650.4078 | 11650.4078 |  | 13672.6523 | 17712.0843 | 18769.8229 | 10955.8814 | 10961.1625 | 11070.0599 | 11356.7463 | 11548.966 | 11736.98 | 11956.8059 | 12160.707 | 12358.5041 | 12381.419 | 12612.2148 | 12437.9133 | 12437.9133 | 12437.9133 | 12437.9133 | 12437.9133 | 12437.9133 | 12437.9133 | 12437.9133 | 12437.9133 | 12437.9133 | 12437.9133 | 12437.9133 | 12437.9133 | 12437.9133 | 12437.9133 | 12437.9133
35% | 6655.3655 | 8843.5072 | 9439.545 | 5215.3642 | 5215.1601 | 5283.3305 | 5358.1089 | 5511.4707 | 5621.6514 | 5681.5534 | 5747.1749 | 5807.1397 | 5915.262 | 6049.3902 | 6040.3253 | 6040.3253 | 6040.3253 | 6040.3253 | 6040.3253 | 6040.3253 | 6040.3253 | 6040.3253 | 6040.3253 | 6040.3253 | 6040.3253 | 6040.3253 | 6040.3253 | 6040.3253 | 6040.3253 | 6040.3253 |  | 18622.1031 | 24123.7949 | 25564.4311 | 14921.8709 | 14929.0638 | 15077.3816 | 15467.8475 | 15729.65 | 15985.7245 | 16285.1265 | 16562.8391 | 16832.2381 | 16863.448 | 17177.791 | 16940.393 | 16940.393 | 16940.393 | 16940.393 | 16940.393 | 16940.393 | 16940.393 | 16940.393 | 16940.393 | 16940.393 | 16940.393 | 16940.393 | 16940.393 | 16940.393 | 16940.393 | 16940.393
30% | 3095.428 | 4113.1385 | 4390.3573 | 2425.6796 | 2425.5847 | 2457.291 | 2492.0706 | 2563.3996 | 2614.6449 | 2642.5055 | 2673.0262 | 2700.916 | 2751.204 | 2813.5874 | 2809.3712 | 2809.3712 | 2809.3712 | 2809.3712 | 2809.3712 | 2809.3712 | 2809.3712 | 2809.3712 | 2809.3712 | 2809.3712 | 2809.3712 | 2809.3712 | 2809.3712 | 2809.3712 | 2809.3712 | 2809.3712 |  | 17207.9743 | 22291.8776 | 23623.1145 | 13788.7311 | 13795.3777 | 13932.4326 | 14293.2472 | 14535.1688 | 14771.7975 | 15048.4635 | 15305.0871 | 15554.0284 | 15582.8683 | 15873.3407 | 15653.9702 | 15653.9702 | 15653.9702 | 15653.9702 | 15653.9702 | 15653.9702 | 15653.9702 | 15653.9702 | 15653.9702 | 15653.9702 | 15653.9702 | 15653.9702 | 15653.9702 | 15653.9702 | 15653.9702 | 15653.9702
25% | 2113.496 | 2808.3682 | 2997.6476 | 1656.2053 | 1656.1404 | 1677.7888 | 1701.5357 | 1750.2376 | 1785.2269 | 1804.2496 | 1825.0885 | 1844.1311 | 1878.4667 | 1921.0608 | 1918.1822 | 1918.1822 | 1918.1822 | 1918.1822 | 1918.1822 | 1918.1822 | 1918.1822 | 1918.1822 | 1918.1822 | 1918.1822 | 1918.1822 | 1918.1822 | 1918.1822 | 1918.1822 | 1918.1822 | 1918.1822 |  | 4963.476 | 6429.8794 | 6813.862 | 3977.2279 | 3979.1451 | 4018.6773 | 4122.7508 | 4192.5308 | 4260.7841 | 4340.5857 | 4414.6064 | 4486.4111 | 4494.7297 | 4578.5137 | 4515.2384 | 4515.2384 | 4515.2384 | 4515.2384 | 4515.2384 | 4515.2384 | 4515.2384 | 4515.2384 | 4515.2384 | 4515.2384 | 4515.2384 | 4515.2384 | 4515.2384 | 4515.2384 | 4515.2384 | 4515.2384
20% | 1280.3284 | 1701.2729 | 1815.9359 | 1003.3076 | 1003.2683 | 1016.3826 | 1030.7682 | 1060.2712 | 1081.4673 | 1092.9909 | 1105.6149 | 1117.1506 | 1137.9507 | 1163.7537 | 1162.0098 | 1162.0098 | 1162.0098 | 1162.0098 | 1162.0098 | 1162.0098 | 1162.0098 | 1162.0098 | 1162.0098 | 1162.0098 | 1162.0098 | 1162.0098 | 1162.0098 | 1162.0098 | 1162.0098 | 1162.0098 |  | 1331.912 | 1725.4105 | 1828.4494 | 1067.2596 | 1067.7741 | 1078.3823 | 1106.3096 | 1125.0346 | 1143.3498 | 1164.764 | 1184.6269 | 1203.8952 | 1206.1274 | 1228.6102 | 1211.6308 | 1211.6308 | 1211.6308 | 1211.6308 | 1211.6308 | 1211.6308 | 1211.6308 | 1211.6308 | 1211.6308 | 1211.6308 | 1211.6308 | 1211.6308 | 1211.6308 | 1211.6308 | 1211.6308 | 1211.6308
15% | 819.7224 | 1089.2296 | 1162.6419 | 642.3616 | 642.3364 | 650.7328 | 659.943 | 678.8322 | 692.4028 | 699.7808 | 707.8632 | 715.2489 | 728.566 | 745.0862 | 743.9697 | 743.9697 | 743.9697 | 743.9697 | 743.9697 | 743.9697 | 743.9697 | 743.9697 | 743.9697 | 743.9697 | 743.9697 | 743.9697 | 743.9697 | 743.9697 | 743.9697 | 743.9697 |  | 734.6312 | 951.6698 | 1008.502 | 588.6592 | 588.9429 | 594.794 | 610.1976 | 620.5256 | 630.6276 | 642.4388 | 653.3944 | 664.0221 | 665.2533 | 677.6539 | 668.2887 | 668.2887 | 668.2887 | 668.2887 | 668.2887 | 668.2887 | 668.2887 | 668.2887 | 668.2887 | 668.2887 | 668.2887 | 668.2887 | 668.2887 | 668.2887 | 668.2887 | 668.2887
10% | 548.6502 | 729.0346 | 778.1704 | 429.9404 | 429.9236 | 435.5434 | 441.7079 | 454.3506 | 463.4336 | 468.3718 | 473.7814 | 478.7248 | 487.6381 | 498.6953 | 497.948 | 497.948 | 497.948 | 497.948 | 497.948 | 497.948 | 497.948 | 497.948 | 497.948 | 497.948 | 497.948 | 497.948 | 497.948 | 497.948 | 497.948 | 497.948 |  | 171.688 | 222.4113 | 235.6934 | 137.5734 | 137.6397 | 139.0072 | 142.6071 | 145.0208 | 147.3817 | 150.1421 | 152.7025 | 155.1862 | 155.4739 | 158.3721 | 156.1833 | 156.1833 | 156.1833 | 156.1833 | 156.1833 | 156.1833 | 156.1833 | 156.1833 | 156.1833 | 156.1833 | 156.1833 | 156.1833 | 156.1833 | 156.1833 | 156.1833 | 156.1833
5% | 390.344 | 518.6808 | 553.639 | 305.8865 | 305.8745 | 309.8728 | 314.2586 | 323.2534 | 329.7156 | 333.2289 | 337.0777 | 340.5947 | 346.9362 | 354.8029 | 354.2713 | 354.2713 | 354.2713 | 354.2713 | 354.2713 | 354.2713 | 354.2713 | 354.2713 | 354.2713 | 354.2713 | 354.2713 | 354.2713 | 354.2713 | 354.2713 | 354.2713 | 354.2713 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9.992e-14% | 34.2635 | 45.5286 | 48.5972 | 26.85 | 26.849 | 27.1999 | 27.5849 | 28.3745 | 28.9417 | 29.2501 | 29.5879 | 29.8966 | 30.4533 | 31.1438 | 31.0971 | 31.0971 | 31.0971 | 31.0971 | 31.0971 | 31.0971 | 31.0971 | 31.0971 | 31.0971 | 31.0971 | 31.0971 | 31.0971 | 31.0971 | 31.0971 | 31.0971 | 31.0971 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E @ R (MWh) | 91763.8061 | 121933.7811 | 130151.918 | 71909.1488 | 71906.3352 | 72846.2653 | 73877.3055 | 75991.8488 | 77511.0147 | 78336.9396 | 79241.7254 | 80068.5172 | 81559.3006 | 83408.6533 | 83283.6669 | 83283.6669 | 83283.6669 | 83283.6669 | 83283.6669 | 83283.6669 | 83283.6669 | 83283.6669 | 83283.6669 | 83283.6669 | 83283.6669 | 83283.6669 | 83283.6669 | 83283.6669 | 83283.6669 | 83283.6669 | E @ R (MWh) | 89067.5772 | 115381.5956 | 122272.0083 | 71369.7528 | 71404.1554 | 72113.5443 | 73981.1019 | 75233.2756 | 76458.0532 | 77890.0621 | 79218.3324 | 80506.8395 | 80656.1133 | 82159.5832 | 81024.1335 | 81024.1335 | 81024.1335 | 81024.1335 | 81024.1335 | 81024.1335 | 81024.1335 | 81024.1335 | 81024.1335 | 81024.1335 | 81024.1335 | 81024.1335 | 81024.1335 | 81024.1335 | 81024.1335 | 81024.1335
Option 5 Summer POE50 W E @ R (MWh) N 2 | 64234.6643 | 85353.6468 | 91106.3426 | 50336.4042 | 50334.4346 | 50992.3857 | 51714.1138 | 53194.2942 | 54257.7103 | 54835.8577 | 55469.2078 | 56047.962 | 57091.5104 | 58386.0573 | 58298.5668 | 58298.5668 | 58298.5668 | 58298.5668 | 58298.5668 | 58298.5668 | 58298.5668 | 58298.5668 | 58298.5668 | 58298.5668 | 58298.5668 | 58298.5668 | 58298.5668 | 58298.5668 | 58298.5668 | 58298.5668 | Option 5 Summer POE10 W E @ R (MWh) N 2 | 26720.2732 | 34614.4787 | 36681.6025 | 21410.9258 | 21421.2466 | 21634.0633 | 22194.3306 | 22569.9827 | 22937.416 | 23367.0186 | 23765.4997 | 24152.0518 | 24196.834 | 24647.875 | 24307.24 | 24307.24 | 24307.24 | 24307.24 | 24307.24 | 24307.24 | 24307.24 | 24307.24 | 24307.24 | 24307.24 | 24307.24 | 24307.24 | 24307.24 | 24307.24 | 24307.24 | 24307.24
Option 6 - Non Network
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | 48.2195 | 68.1079 | 73.2784 | 74.3602 | 75.1629 | 76.4573 | 79.3652 | 81.315 | 83.8261 | 85.0325 | 86.088 | 83.6946 | 86.3026 | 90.2422 | 87.2595 | 87.2595 | 87.2595 | 87.2595 | 87.2595 | 87.2595 | 87.2595 | 87.2595 | 87.2595 | 87.2595 | 87.2595 | 87.2595 | 87.2595 | 87.2595 | 87.2595 | 87.2595 |  | 52.4334 | 72.0296 | 77.4352 | 78.4586 | 79.0755 | 80.3401 | 83.2969 | 84.8864 | 88.0509 | 97.9462 | 89.4864 | 87.7067 | 89.8842 | 94.4948 | 91.3959 | 91.3959 | 91.3959 | 91.3959 | 91.3959 | 91.3959 | 91.3959 | 91.3959 | 91.3959 | 91.3959 | 91.3959 | 91.3959 | 91.3959 | 91.3959 | 91.3959 | 91.3959
98% | 57.2819 | 80.908 | 87.0504 | 88.3354 | 89.289 | 90.8267 | 94.281 | 96.5973 | 99.5804 | 101.0135 | 102.2674 | 99.4242 | 102.5222 | 107.2023 | 103.659 | 103.659 | 103.659 | 103.659 | 103.659 | 103.659 | 103.659 | 103.659 | 103.659 | 103.659 | 103.659 | 103.659 | 103.659 | 103.659 | 103.659 | 103.659 |  | 62.2878 | 85.5669 | 91.9884 | 93.2041 | 93.937 | 95.4391 | 98.9517 | 100.84 | 104.5991 | 116.3542 | 106.3044 | 104.1903 | 106.777 | 112.2541 | 108.5728 | 108.5728 | 108.5728 | 108.5728 | 108.5728 | 108.5728 | 108.5728 | 108.5728 | 108.5728 | 108.5728 | 108.5728 | 108.5728 | 108.5728 | 108.5728 | 108.5728 | 108.5728
97% | 113.4007 | 160.1732 | 172.3332 | 174.8772 | 176.7651 | 179.8092 | 186.6477 | 191.2332 | 197.1388 | 199.976 | 202.4583 | 196.8295 | 202.9628 | 212.2278 | 205.2133 | 205.2133 | 205.2133 | 205.2133 | 205.2133 | 205.2133 | 205.2133 | 205.2133 | 205.2133 | 205.2133 | 205.2133 | 205.2133 | 205.2133 | 205.2133 | 205.2133 | 205.2133 |  | 123.3108 | 169.3963 | 182.109 | 184.5158 | 185.9666 | 188.9404 | 195.8942 | 199.6324 | 207.0744 | 230.3458 | 210.4504 | 206.265 | 211.386 | 222.2289 | 214.941 | 214.941 | 214.941 | 214.941 | 214.941 | 214.941 | 214.941 | 214.941 | 214.941 | 214.941 | 214.941 | 214.941 | 214.941 | 214.941 | 214.941 | 214.941
95% | 334.9683 | 473.1271 | 509.0457 | 516.5604 | 522.1369 | 531.1288 | 551.3287 | 564.8734 | 582.3176 | 590.6983 | 598.0307 | 581.4042 | 599.5209 | 626.8884 | 606.1685 | 606.1685 | 606.1685 | 606.1685 | 606.1685 | 606.1685 | 606.1685 | 606.1685 | 606.1685 | 606.1685 | 606.1685 | 606.1685 | 606.1685 | 606.1685 | 606.1685 | 606.1685 |  | 364.2412 | 500.3706 | 537.922 | 545.0313 | 549.3167 | 558.101 | 578.6413 | 589.6834 | 611.6661 | 680.4062 | 621.6381 | 609.275 | 624.4017 | 656.4301 | 634.9028 | 634.9028 | 634.9028 | 634.9028 | 634.9028 | 634.9028 | 634.9028 | 634.9028 | 634.9028 | 634.9028 | 634.9028 | 634.9028 | 634.9028 | 634.9028 | 634.9028 | 634.9028
90% | 1846.881 | 2608.6334 | 2806.6743 | 2848.1071 | 2878.8539 | 2928.4318 | 3039.8054 | 3114.4855 | 3210.666 | 3256.8738 | 3297.3021 | 3205.6298 | 3305.5181 | 3456.4115 | 3342.1701 | 3342.1701 | 3342.1701 | 3342.1701 | 3342.1701 | 3342.1701 | 3342.1701 | 3342.1701 | 3342.1701 | 3342.1701 | 3342.1701 | 3342.1701 | 3342.1701 | 3342.1701 | 3342.1701 | 3342.1701 |  | 2008.2799 | 2758.8432 | 2965.8865 | 3005.0842 | 3028.7122 | 3077.1454 | 3190.3962 | 3251.2784 | 3372.4817 | 3751.4871 | 3427.4635 | 3359.2982 | 3442.7007 | 3619.2927 | 3500.5997 | 3500.5997 | 3500.5997 | 3500.5997 | 3500.5997 | 3500.5997 | 3500.5997 | 3500.5997 | 3500.5997 | 3500.5997 | 3500.5997 | 3500.5997 | 3500.5997 | 3500.5997 | 3500.5997 | 3500.5997
85% | 4511.798 | 6372.7046 | 6856.5043 | 6957.7216 | 7032.8339 | 7153.949 | 7426.0268 | 7608.4649 | 7843.427 | 7956.3094 | 8055.0727 | 7831.124 | 8075.1438 | 8443.7656 | 8164.6823 | 8164.6823 | 8164.6823 | 8164.6823 | 8164.6823 | 8164.6823 | 8164.6823 | 8164.6823 | 8164.6823 | 8164.6823 | 8164.6823 | 8164.6823 | 8164.6823 | 8164.6823 | 8164.6823 | 8164.6823 |  | 4906.0839 | 6739.6563 | 7245.4482 | 7341.2054 | 7398.9271 | 7517.2457 | 7793.9093 | 7942.6402 | 8238.7311 | 9164.6144 | 8373.0478 | 8206.5249 | 8410.2713 | 8841.6728 | 8551.7144 | 8551.7144 | 8551.7144 | 8551.7144 | 8551.7144 | 8551.7144 | 8551.7144 | 8551.7144 | 8551.7144 | 8551.7144 | 8551.7144 | 8551.7144 | 8551.7144 | 8551.7144 | 8551.7144 | 8551.7144
80% | 7012.6717 | 9905.0722 | 10657.0403 | 10814.3621 | 10931.1089 | 11119.3576 | 11542.2472 | 11825.81 | 12191.0108 | 12366.4634 | 12519.971 | 12171.8883 | 12551.1675 | 13124.1149 | 12690.3367 | 12690.3367 | 12690.3367 | 12690.3367 | 12690.3367 | 12690.3367 | 12690.3367 | 12690.3367 | 12690.3367 | 12690.3367 | 12690.3367 | 12690.3367 | 12690.3367 | 12690.3367 | 12690.3367 | 12690.3367 |  | 7625.5088 | 10475.4239 | 11261.5745 | 11410.4096 | 11500.1261 | 11684.0283 | 12114.0456 | 12345.2175 | 12805.4306 | 14244.5276 | 13014.1985 | 12755.3726 | 13072.0549 | 13742.5808 | 13291.8994 | 13291.8994 | 13291.8994 | 13291.8994 | 13291.8994 | 13291.8994 | 13291.8994 | 13291.8994 | 13291.8994 | 13291.8994 | 13291.8994 | 13291.8994 | 13291.8994 | 13291.8994 | 13291.8994 | 13291.8994
75% | 7736.934 | 10928.059 | 11757.6897 | 11931.2595 | 12060.0638 | 12267.7546 | 12734.3199 | 13047.1688 | 13450.0872 | 13643.6605 | 13813.0222 | 13428.9897 | 13847.4406 | 14479.5615 | 14000.983 | 14000.983 | 14000.983 | 14000.983 | 14000.983 | 14000.983 | 14000.983 | 14000.983 | 14000.983 | 14000.983 | 14000.983 | 14000.983 | 14000.983 | 14000.983 | 14000.983 | 14000.983 |  | 8413.0644 | 11557.3161 | 12424.6596 | 12588.8662 | 12687.8486 | 12890.7441 | 13365.1731 | 13620.2203 | 14127.9637 | 15715.6894 | 14358.293 | 14072.7358 | 14422.1247 | 15161.9019 | 14664.6746 | 14664.6746 | 14664.6746 | 14664.6746 | 14664.6746 | 14664.6746 | 14664.6746 | 14664.6746 | 14664.6746 | 14664.6746 | 14664.6746 | 14664.6746 | 14664.6746 | 14664.6746 | 14664.6746 | 14664.6746
70% | 8312.9031 | 11741.5885 | 12632.9803 | 12819.4713 | 12957.8644 | 13181.0165 | 13682.3148 | 14018.4535 | 14451.3668 | 14659.3504 | 14841.3201 | 14428.6988 | 14878.3008 | 15557.4794 | 15043.2736 | 15043.2736 | 15043.2736 | 15043.2736 | 15043.2736 | 15043.2736 | 15043.2736 | 15043.2736 | 15043.2736 | 15043.2736 | 15043.2736 | 15043.2736 | 15043.2736 | 15043.2736 | 15043.2736 | 15043.2736 |  | 9039.3674 | 12417.6901 | 13349.6022 | 13526.033 | 13632.384 | 13850.3839 | 14360.1313 | 14634.1653 | 15179.7072 | 16885.6297 | 15427.1832 | 15120.3679 | 15495.7668 | 16290.616 | 15756.373 | 15756.373 | 15756.373 | 15756.373 | 15756.373 | 15756.373 | 15756.373 | 15756.373 | 15756.373 | 15756.373 | 15756.373 | 15756.373 | 15756.373 | 15756.373 | 15756.373 | 15756.373
65% | 8760.2059 | 12373.3829 | 13312.739 | 13509.2648 | 13655.1045 | 13890.2641 | 14418.5364 | 14772.7621 | 15228.9697 | 15448.1446 | 15639.9057 | 15205.0819 | 15678.8762 | 16394.6003 | 15852.726 | 15852.726 | 15852.726 | 15852.726 | 15852.726 | 15852.726 | 15852.726 | 15852.726 | 15852.726 | 15852.726 | 15852.726 | 15852.726 | 15852.726 | 15852.726 | 15852.726 | 15852.726 |  | 9525.76 | 13085.8644 | 14067.921 | 14253.8453 | 14365.9189 | 14595.649 | 15132.825 | 15421.6043 | 15996.5009 | 17794.216 | 16257.2931 | 15933.9686 | 16329.567 | 17167.1857 | 16604.1961 | 16604.1961 | 16604.1961 | 16604.1961 | 16604.1961 | 16604.1961 | 16604.1961 | 16604.1961 | 16604.1961 | 16604.1961 | 16604.1961 | 16604.1961 | 16604.1961 | 16604.1961 | 16604.1961 | 16604.1961
60% | 9643.9077 | 13621.5705 | 14655.6859 | 14872.0366 | 15032.5881 | 15291.4699 | 15873.0326 | 16262.9915 | 16765.2199 | 17006.5044 | 17217.6098 | 16738.9224 | 17260.5116 | 18048.4355 | 17451.8987 | 17451.8987 | 17451.8987 | 17451.8987 | 17451.8987 | 17451.8987 | 17451.8987 | 17451.8987 | 17451.8987 | 17451.8987 | 17451.8987 | 17451.8987 | 17451.8987 | 17451.8987 | 17451.8987 | 17451.8987 |  | 10486.6885 | 14405.9249 | 15487.0483 | 15691.728 | 15815.1072 | 16068.0117 | 16659.3764 | 16977.2868 | 17610.1771 | 19589.2401 | 17897.2772 | 17541.3368 | 17976.842 | 18898.957 | 18279.1747 | 18279.1747 | 18279.1747 | 18279.1747 | 18279.1747 | 18279.1747 | 18279.1747 | 18279.1747 | 18279.1747 | 18279.1747 | 18279.1747 | 18279.1747 | 18279.1747 | 18279.1747 | 18279.1747 | 18279.1747
55% | 10728.2416 | 15153.1416 | 16303.53 | 16544.2065 | 16722.81 | 17010.7998 | 17657.7518 | 18091.5565 | 18650.254 | 18918.6679 | 19153.5094 | 18620.9997 | 19201.2349 | 20077.7508 | 19414.1411 | 19414.1411 | 19414.1411 | 19414.1411 | 19414.1411 | 19414.1411 | 19414.1411 | 19414.1411 | 19414.1411 | 19414.1411 | 19414.1411 | 19414.1411 | 19414.1411 | 19414.1411 | 19414.1411 | 19414.1411 |  | 11665.7823 | 16025.6866 | 17228.3684 | 17456.0617 | 17593.3134 | 17874.6538 | 18532.5098 | 18886.1652 | 19590.2159 | 21791.7992 | 19909.5967 | 19513.6354 | 19998.1075 | 21023.9025 | 20334.4337 | 20334.4337 | 20334.4337 | 20334.4337 | 20334.4337 | 20334.4337 | 20334.4337 | 20334.4337 | 20334.4337 | 20334.4337 | 20334.4337 | 20334.4337 | 20334.4337 | 20334.4337 | 20334.4337 | 20334.4337
50% | 10874.1117 | 15359.1764 | 16525.2064 | 16769.1554 | 16950.1874 | 17242.0928 | 17897.8414 | 18337.5445 | 18903.8385 | 19175.902 | 19413.9366 | 18874.1864 | 19462.311 | 20350.7448 | 19678.112 | 19678.112 | 19678.112 | 19678.112 | 19678.112 | 19678.112 | 19678.112 | 19678.112 | 19678.112 | 19678.112 | 19678.112 | 19678.112 | 19678.112 | 19678.112 | 19678.112 | 19678.112 |  | 11824.4 | 16243.5852 | 17462.6198 | 17693.409 | 17832.5268 | 18117.6925 | 18784.4934 | 19142.9573 | 19856.5809 | 22088.0987 | 20180.3043 | 19778.9591 | 20270.0185 | 21309.7611 | 20610.9177 | 20610.9177 | 20610.9177 | 20610.9177 | 20610.9177 | 20610.9177 | 20610.9177 | 20610.9177 | 20610.9177 | 20610.9177 | 20610.9177 | 20610.9177 | 20610.9177 | 20610.9177 | 20610.9177 | 20610.9177
45% | 8392.8651 | 11854.5311 | 12754.4973 | 12942.7822 | 13082.5064 | 13307.8051 | 13813.9254 | 14153.2974 | 14590.3749 | 14800.3591 | 14984.0792 | 14567.4888 | 15021.4155 | 15707.1272 | 15187.9753 | 15187.9753 | 15187.9753 | 15187.9753 | 15187.9753 | 15187.9753 | 15187.9753 | 15187.9753 | 15187.9753 | 15187.9753 | 15187.9753 | 15187.9753 | 15187.9753 | 15187.9753 | 15187.9753 | 15187.9753 |  | 9126.3173 | 12537.1362 | 13478.0124 | 13656.1403 | 13763.5143 | 13983.6111 | 14498.2618 | 14774.9317 | 15325.7212 | 17048.053 | 15575.5777 | 15265.8112 | 15644.821 | 16447.3159 | 15907.934 | 15907.934 | 15907.934 | 15907.934 | 15907.934 | 15907.934 | 15907.934 | 15907.934 | 15907.934 | 15907.934 | 15907.934 | 15907.934 | 15907.934 | 15907.934 | 15907.934 | 15907.934
40% | 4123.3763 | 5824.077 | 6266.2263 | 6358.7298 | 6427.3757 | 6538.0639 | 6786.7185 | 6953.4504 | 7168.1846 | 7271.3489 | 7361.6097 | 7156.9408 | 7379.9529 | 7716.8399 | 7461.7829 | 7461.7829 | 7461.7829 | 7461.7829 | 7461.7829 | 7461.7829 | 7461.7829 | 7461.7829 | 7461.7829 | 7461.7829 | 7461.7829 | 7461.7829 | 7461.7829 | 7461.7829 | 7461.7829 | 7461.7829 |  | 4483.718 | 6159.4378 | 6621.686 | 6709.1994 | 6761.9518 | 6870.0843 | 7122.9299 | 7258.8565 | 7529.4569 | 8375.6306 | 7652.2102 | 7500.0233 | 7686.2291 | 8080.4912 | 7815.4954 | 7815.4954 | 7815.4954 | 7815.4954 | 7815.4954 | 7815.4954 | 7815.4954 | 7815.4954 | 7815.4954 | 7815.4954 | 7815.4954 | 7815.4954 | 7815.4954 | 7815.4954 | 7815.4954 | 7815.4954
35% | 1541.0868 | 2176.7133 | 2341.9639 | 2376.5365 | 2402.1925 | 2443.5615 | 2536.4947 | 2598.8097 | 2679.0653 | 2717.6223 | 2751.3567 | 2674.863 | 2758.2124 | 2884.1219 | 2788.7959 | 2788.7959 | 2788.7959 | 2788.7959 | 2788.7959 | 2788.7959 | 2788.7959 | 2788.7959 | 2788.7959 | 2788.7959 | 2788.7959 | 2788.7959 | 2788.7959 | 2788.7959 | 2788.7959 | 2788.7959 |  | 1675.7623 | 2302.0523 | 2474.8148 | 2507.5224 | 2527.2382 | 2567.6521 | 2662.1516 | 2712.9534 | 2814.0886 | 3130.3409 | 2859.9669 | 2803.088 | 2872.6813 | 3020.0343 | 2920.9937 | 2920.9937 | 2920.9937 | 2920.9937 | 2920.9937 | 2920.9937 | 2920.9937 | 2920.9937 | 2920.9937 | 2920.9937 | 2920.9937 | 2920.9937 | 2920.9937 | 2920.9937 | 2920.9937 | 2920.9937
30% | 768.6049 | 1085.6186 | 1168.0361 | 1185.2789 | 1198.0746 | 1218.7071 | 1265.0568 | 1296.1359 | 1336.1628 | 1355.3928 | 1372.2175 | 1334.0669 | 1375.6368 | 1438.4331 | 1390.89 | 1390.89 | 1390.89 | 1390.89 | 1390.89 | 1390.89 | 1390.89 | 1390.89 | 1390.89 | 1390.89 | 1390.89 | 1390.89 | 1390.89 | 1390.89 | 1390.89 | 1390.89 |  | 835.7733 | 1148.1305 | 1234.2944 | 1250.6071 | 1260.4402 | 1280.5963 | 1327.7272 | 1353.0642 | 1403.5046 | 1561.2329 | 1426.386 | 1398.0181 | 1432.7272 | 1506.2184 | 1456.8227 | 1456.8227 | 1456.8227 | 1456.8227 | 1456.8227 | 1456.8227 | 1456.8227 | 1456.8227 | 1456.8227 | 1456.8227 | 1456.8227 | 1456.8227 | 1456.8227 | 1456.8227 | 1456.8227 | 1456.8227
25% | 453.1183 | 640.0085 | 688.5963 | 698.7615 | 706.305 | 718.4686 | 745.7932 | 764.1154 | 787.7126 | 799.0493 | 808.9681 | 786.477 | 810.9838 | 848.0044 | 819.9761 | 819.9761 | 819.9761 | 819.9761 | 819.9761 | 819.9761 | 819.9761 | 819.9761 | 819.9761 | 819.9761 | 819.9761 | 819.9761 | 819.9761 | 819.9761 | 819.9761 | 819.9761 |  | 492.7163 | 676.8613 | 727.6578 | 737.2747 | 743.0716 | 754.9543 | 782.7395 | 797.6765 | 827.4128 | 920.399 | 840.9022 | 824.1784 | 844.6406 | 887.9661 | 858.8456 | 858.8456 | 858.8456 | 858.8456 | 858.8456 | 858.8456 | 858.8456 | 858.8456 | 858.8456 | 858.8456 | 858.8456 | 858.8456 | 858.8456 | 858.8456 | 858.8456 | 858.8456
20% | 228.9822 | 323.4267 | 347.9805 | 353.1175 | 356.9295 | 363.0764 | 376.8848 | 386.1439 | 398.0687 | 403.7977 | 408.8101 | 397.4443 | 409.8287 | 428.537 | 414.373 | 414.373 | 414.373 | 414.373 | 414.373 | 414.373 | 414.373 | 414.373 | 414.373 | 414.373 | 414.373 | 414.373 | 414.373 | 414.373 | 414.373 | 414.373 |  | 248.993 | 342.0502 | 367.7201 | 372.58 | 375.5095 | 381.5143 | 395.5555 | 403.1039 | 418.1311 | 465.1214 | 424.9479 | 416.4966 | 426.8371 | 448.7315 | 434.0156 | 434.0156 | 434.0156 | 434.0156 | 434.0156 | 434.0156 | 434.0156 | 434.0156 | 434.0156 | 434.0156 | 434.0156 | 434.0156 | 434.0156 | 434.0156 | 434.0156 | 434.0156
15% | 93.2891 | 131.7664 | 141.7698 | 143.8627 | 145.4157 | 147.92 | 153.5457 | 157.3179 | 162.1761 | 164.5102 | 166.5523 | 161.9217 | 166.9673 | 174.5891 | 168.8186 | 168.8186 | 168.8186 | 168.8186 | 168.8186 | 168.8186 | 168.8186 | 168.8186 | 168.8186 | 168.8186 | 168.8186 | 168.8186 | 168.8186 | 168.8186 | 168.8186 | 168.8186 |  | 101.4416 | 139.3538 | 149.8119 | 151.7918 | 152.9853 | 155.4318 | 161.1523 | 164.2275 | 170.3497 | 189.4939 | 173.1269 | 169.6838 | 173.8966 | 182.8165 | 176.8212 | 176.8212 | 176.8212 | 176.8212 | 176.8212 | 176.8212 | 176.8212 | 176.8212 | 176.8212 | 176.8212 | 176.8212 | 176.8212 | 176.8212 | 176.8212 | 176.8212 | 176.8212
10% | 37.5579 | 53.0488 | 57.0762 | 57.9187 | 58.544 | 59.5522 | 61.8171 | 63.3358 | 65.2917 | 66.2314 | 67.0535 | 65.1893 | 67.2206 | 70.2891 | 67.9659 | 67.9659 | 67.9659 | 67.9659 | 67.9659 | 67.9659 | 67.9659 | 67.9659 | 67.9659 | 67.9659 | 67.9659 | 67.9659 | 67.9659 | 67.9659 | 67.9659 | 67.9659 |  | 40.8401 | 56.1035 | 60.3139 | 61.111 | 61.5915 | 62.5764 | 64.8795 | 66.1176 | 68.5823 | 76.2898 | 69.7005 | 68.3143 | 70.0103 | 73.6015 | 71.1877 | 71.1877 | 71.1877 | 71.1877 | 71.1877 | 71.1877 | 71.1877 | 71.1877 | 71.1877 | 71.1877 | 71.1877 | 71.1877 | 71.1877 | 71.1877 | 71.1877 | 71.1877
5% | 31.9848 | 45.1771 | 48.6068 | 49.3243 | 49.8568 | 50.7154 | 52.6442 | 53.9376 | 55.6032 | 56.4035 | 57.1036 | 55.516 | 57.2459 | 59.8591 | 57.8807 | 57.8807 | 57.8807 | 57.8807 | 57.8807 | 57.8807 | 57.8807 | 57.8807 | 57.8807 | 57.8807 | 57.8807 | 57.8807 | 57.8807 | 57.8807 | 57.8807 | 57.8807 |  | 34.78 | 47.7784 | 51.3641 | 52.0429 | 52.4521 | 53.2909 | 55.2522 | 56.3066 | 58.4056 | 64.9693 | 59.3578 | 58.1773 | 59.6217 | 62.68 | 60.6244 | 60.6244 | 60.6244 | 60.6244 | 60.6244 | 60.6244 | 60.6244 | 60.6244 | 60.6244 | 60.6244 | 60.6244 | 60.6244 | 60.6244 | 60.6244 | 60.6244 | 60.6244
9.992e-14% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E @ R (MWh) | 85652.3907 | 120980.013 | 130164.5112 | 132086.03 | 133511.9693 | 135811.2284 | 140976.3793 | 144439.8002 | 148900.3426 | 151043.3117 | 152918.245 | 148666.7812 | 153299.2768 | 160297.2257 | 154999.0821 | 154999.0821 | 154999.0821 | 154999.0821 | 154999.0821 | 154999.0821 | 154999.0821 | 154999.0821 | 154999.0821 | 154999.0821 | 154999.0821 | 154999.0821 | 154999.0821 | 154999.0821 | 154999.0821 | 154999.0821 | E @ R (MWh) | 93137.5503 | 127946.2583 | 137548.2585 | 139366.1217 | 140461.9146 | 142708.0866 | 147960.2936 | 150783.8154 | 156404.8325 | 173981.8854 | 158954.7127 | 155793.4272 | 159661.3671 | 167851.1339 | 162346.536 | 162346.536 | 162346.536 | 162346.536 | 162346.536 | 162346.536 | 162346.536 | 162346.536 | 162346.536 | 162346.536 | 162346.536 | 162346.536 | 162346.536 | 162346.536 | 162346.536 | 162346.536
Option 6 Winter POE50 W E @ R (MWh) N 2 | 59956.6735 | 84686.0091 | 91115.1578 | 92460.221 | 93458.3785 | 95067.8599 | 98683.4655 | 101107.8601 | 104230.2398 | 105730.3182 | 107042.7715 | 104066.7469 | 107309.4937 | 112208.058 | 108499.3575 | 108499.3575 | 108499.3575 | 108499.3575 | 108499.3575 | 108499.3575 | 108499.3575 | 108499.3575 | 108499.3575 | 108499.3575 | 108499.3575 | 108499.3575 | 108499.3575 | 108499.3575 | 108499.3575 | 108499.3575 | Option 6 Winter POE10 W E @ R (MWh) N 2 | 27941.2651 | 38383.8775 | 41264.4775 | 41809.8365 | 42138.5744 | 42812.426 | 44388.0881 | 45235.1446 | 46921.4497 | 52194.5656 | 47686.4138 | 46738.0281 | 47898.4101 | 50355.3402 | 48703.9608 | 48703.9608 | 48703.9608 | 48703.9608 | 48703.9608 | 48703.9608 | 48703.9608 | 48703.9608 | 48703.9608 | 48703.9608 | 48703.9608 | 48703.9608 | 48703.9608 | 48703.9608 | 48703.9608 | 48703.9608
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 65.3358 | 84.7493 | 89.8394 | 89.5415 | 89.5735 | 90.1013 | 91.4835 | 92.4139 | 93.3219 | 94.3828 | 95.3694 | 96.3244 | 96.439 | 97.5526 | 96.7193 | 96.7193 | 96.7193 | 96.7193 | 96.7193 | 96.7193 | 96.7193 | 96.7193 | 96.7193 | 96.7193 | 96.7193 | 96.7193 | 96.7193 | 96.7193 | 96.7193 | 96.7193
98% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 32.3396 | 41.9488 | 44.4683 | 44.3208 | 44.3366 | 44.5979 | 45.282 | 45.7426 | 46.192 | 46.7171 | 47.2055 | 47.6782 | 47.7349 | 48.2861 | 47.8736 | 47.8736 | 47.8736 | 47.8736 | 47.8736 | 47.8736 | 47.8736 | 47.8736 | 47.8736 | 47.8736 | 47.8736 | 47.8736 | 47.8736 | 47.8736 | 47.8736 | 47.8736
97% | 14.059 | 18.8037 | 20.1064 | 20.0768 | 20.0768 | 20.2292 | 20.3623 | 20.7149 | 20.958 | 21.0669 | 21.194 | 21.3075 | 21.5788 | 21.8741 | 21.8874 | 21.8874 | 21.8874 | 21.8874 | 21.8874 | 21.8874 | 21.8874 | 21.8874 | 21.8874 | 21.8874 | 21.8874 | 21.8874 | 21.8874 | 21.8874 | 21.8874 | 21.8874 |  | 64.0225 | 83.0458 | 88.0336 | 87.7417 | 87.773 | 88.2902 | 89.6446 | 90.5564 | 91.4461 | 92.4857 | 93.4524 | 94.3883 | 94.5005 | 95.5917 | 94.7752 | 94.7752 | 94.7752 | 94.7752 | 94.7752 | 94.7752 | 94.7752 | 94.7752 | 94.7752 | 94.7752 | 94.7752 | 94.7752 | 94.7752 | 94.7752 | 94.7752 | 94.7752
95% | 69.2137 | 92.5721 | 98.9851 | 98.8396 | 98.8398 | 99.5897 | 100.2454 | 101.9809 | 103.1777 | 103.7138 | 104.3399 | 104.8987 | 106.234 | 107.6879 | 107.7533 | 107.7533 | 107.7533 | 107.7533 | 107.7533 | 107.7533 | 107.7533 | 107.7533 | 107.7533 | 107.7533 | 107.7533 | 107.7533 | 107.7533 | 107.7533 | 107.7533 | 107.7533 |  | 94.5564 | 122.6523 | 130.0189 | 129.5877 | 129.634 | 130.3978 | 132.3982 | 133.7448 | 135.0589 | 136.5943 | 138.022 | 139.4042 | 139.57 | 141.1816 | 139.9757 | 139.9757 | 139.9757 | 139.9757 | 139.9757 | 139.9757 | 139.9757 | 139.9757 | 139.9757 | 139.9757 | 139.9757 | 139.9757 | 139.9757 | 139.9757 | 139.9757 | 139.9757
90% | 120.0426 | 160.5547 | 171.6773 | 171.425 | 171.4253 | 172.7259 | 173.863 | 176.8732 | 178.9489 | 179.8786 | 180.9645 | 181.9336 | 184.2497 | 186.7712 | 186.8846 | 186.8846 | 186.8846 | 186.8846 | 186.8846 | 186.8846 | 186.8846 | 186.8846 | 186.8846 | 186.8846 | 186.8846 | 186.8846 | 186.8846 | 186.8846 | 186.8846 | 186.8846 |  | 409.9904 | 531.8126 | 563.7537 | 561.8842 | 562.085 | 565.3969 | 574.0705 | 579.909 | 585.6069 | 592.2641 | 598.455 | 604.4479 | 605.1666 | 612.1547 | 606.9257 | 606.9257 | 606.9257 | 606.9257 | 606.9257 | 606.9257 | 606.9257 | 606.9257 | 606.9257 | 606.9257 | 606.9257 | 606.9257 | 606.9257 | 606.9257 | 606.9257 | 606.9257
85% | 340.6614 | 455.6282 | 487.1924 | 486.4764 | 486.4772 | 490.1681 | 493.3951 | 501.9374 | 507.8279 | 510.4663 | 513.548 | 516.2982 | 522.8706 | 530.0264 | 530.3481 | 530.3481 | 530.3481 | 530.3481 | 530.3481 | 530.3481 | 530.3481 | 530.3481 | 530.3481 | 530.3481 | 530.3481 | 530.3481 | 530.3481 | 530.3481 | 530.3481 | 530.3481 |  | 387.8288 | 503.066 | 533.2805 | 531.5121 | 531.702 | 534.8349 | 543.0397 | 548.5626 | 553.9525 | 560.2499 | 566.106 | 571.775 | 572.4549 | 579.0652 | 574.1189 | 574.1189 | 574.1189 | 574.1189 | 574.1189 | 574.1189 | 574.1189 | 574.1189 | 574.1189 | 574.1189 | 574.1189 | 574.1189 | 574.1189 | 574.1189 | 574.1189 | 574.1189
80% | 475.8445 | 636.433 | 680.5227 | 679.5225 | 679.5237 | 684.6793 | 689.1869 | 701.1189 | 709.347 | 713.0323 | 717.3369 | 721.1784 | 730.359 | 740.3543 | 740.8037 | 740.8037 | 740.8037 | 740.8037 | 740.8037 | 740.8037 | 740.8037 | 740.8037 | 740.8037 | 740.8037 | 740.8037 | 740.8037 | 740.8037 | 740.8037 | 740.8037 | 740.8037 |  | 270.8645 | 351.3477 | 372.4499 | 371.2148 | 371.3475 | 373.5355 | 379.2658 | 383.1231 | 386.8874 | 391.2856 | 395.3756 | 399.3349 | 399.8098 | 404.4265 | 400.972 | 400.972 | 400.972 | 400.972 | 400.972 | 400.972 | 400.972 | 400.972 | 400.972 | 400.972 | 400.972 | 400.972 | 400.972 | 400.972 | 400.972 | 400.972
75% | 1240.44 | 1659.0652 | 1773.999 | 1771.3917 | 1771.3947 | 1784.8344 | 1796.5848 | 1827.6895 | 1849.1386 | 1858.7456 | 1869.9669 | 1879.9809 | 1903.9131 | 1929.9691 | 1931.1407 | 1931.1407 | 1931.1407 | 1931.1407 | 1931.1407 | 1931.1407 | 1931.1407 | 1931.1407 | 1931.1407 | 1931.1407 | 1931.1407 | 1931.1407 | 1931.1407 | 1931.1407 | 1931.1407 | 1931.1407 |  | 483.4522 | 627.1024 | 664.7666 | 662.5622 | 662.799 | 666.7042 | 676.932 | 683.8167 | 690.5354 | 698.3855 | 705.6856 | 712.7523 | 713.5999 | 721.8401 | 715.6742 | 715.6742 | 715.6742 | 715.6742 | 715.6742 | 715.6742 | 715.6742 | 715.6742 | 715.6742 | 715.6742 | 715.6742 | 715.6742 | 715.6742 | 715.6742 | 715.6742 | 715.6742
70% | 2143.1025 | 2866.3594 | 3064.9299 | 3060.4253 | 3060.4306 | 3083.6503 | 3103.9514 | 3157.6909 | 3194.7483 | 3211.3463 | 3230.7332 | 3248.0344 | 3289.382 | 3334.3989 | 3336.4229 | 3336.4229 | 3336.4229 | 3336.4229 | 3336.4229 | 3336.4229 | 3336.4229 | 3336.4229 | 3336.4229 | 3336.4229 | 3336.4229 | 3336.4229 | 3336.4229 | 3336.4229 | 3336.4229 | 3336.4229 |  | 880.7202 | 1142.4123 | 1211.0265 | 1207.0106 | 1207.4419 | 1214.5562 | 1233.1885 | 1245.7305 | 1257.9704 | 1272.2711 | 1285.5699 | 1298.4435 | 1299.9875 | 1314.9989 | 1303.7664 | 1303.7664 | 1303.7664 | 1303.7664 | 1303.7664 | 1303.7664 | 1303.7664 | 1303.7664 | 1303.7664 | 1303.7664 | 1303.7664 | 1303.7664 | 1303.7664 | 1303.7664 | 1303.7664 | 1303.7664
65% | 5382.4496 | 7198.9255 | 7697.6398 | 7686.3264 | 7686.3396 | 7744.6565 | 7795.6431 | 7930.611 | 8023.6816 | 8065.3677 | 8114.0585 | 8157.5108 | 8261.3562 | 8374.4171 | 8379.5005 | 8379.5005 | 8379.5005 | 8379.5005 | 8379.5005 | 8379.5005 | 8379.5005 | 8379.5005 | 8379.5005 | 8379.5005 | 8379.5005 | 8379.5005 | 8379.5005 | 8379.5005 | 8379.5005 | 8379.5005 |  | 1108.0822 | 1437.3315 | 1523.6587 | 1518.606 | 1519.1487 | 1528.0996 | 1551.5419 | 1567.3217 | 1582.7213 | 1600.7139 | 1617.4458 | 1633.6428 | 1635.5854 | 1654.4721 | 1640.3398 | 1640.3398 | 1640.3398 | 1640.3398 | 1640.3398 | 1640.3398 | 1640.3398 | 1640.3398 | 1640.3398 | 1640.3398 | 1640.3398 | 1640.3398 | 1640.3398 | 1640.3398 | 1640.3398 | 1640.3398
60% | 7867.6554 | 10522.8417 | 11251.8243 | 11235.2872 | 11235.3066 | 11320.5498 | 11395.0781 | 11592.3639 | 11728.4073 | 11789.341 | 11860.5135 | 11924.0287 | 12075.822 | 12241.0858 | 12248.5163 | 12248.5163 | 12248.5163 | 12248.5163 | 12248.5163 | 12248.5163 | 12248.5163 | 12248.5163 | 12248.5163 | 12248.5163 | 12248.5163 | 12248.5163 | 12248.5163 | 12248.5163 | 12248.5163 | 12248.5163 |  | 1733.9435 | 2249.1576 | 2384.2437 | 2376.3372 | 2377.1864 | 2391.1929 | 2427.8757 | 2452.5682 | 2476.6658 | 2504.8208 | 2531.0032 | 2556.3485 | 2559.3883 | 2588.9425 | 2566.8281 | 2566.8281 | 2566.8281 | 2566.8281 | 2566.8281 | 2566.8281 | 2566.8281 | 2566.8281 | 2566.8281 | 2566.8281 | 2566.8281 | 2566.8281 | 2566.8281 | 2566.8281 | 2566.8281 | 2566.8281
55% | 8896.4888 | 11898.8871 | 12723.1968 | 12704.4972 | 12704.5192 | 12800.9094 | 12885.1836 | 13108.268 | 13262.1015 | 13331.0033 | 13411.4828 | 13483.3038 | 13654.9467 | 13841.8216 | 13850.2238 | 13850.2238 | 13850.2238 | 13850.2238 | 13850.2238 | 13850.2238 | 13850.2238 | 13850.2238 | 13850.2238 | 13850.2238 | 13850.2238 | 13850.2238 | 13850.2238 | 13850.2238 | 13850.2238 | 13850.2238 |  | 3332.0443 | 4322.1089 | 4581.6981 | 4566.5046 | 4568.1364 | 4595.0522 | 4665.544 | 4712.9944 | 4759.3016 | 4813.4059 | 4863.7195 | 4912.4245 | 4918.2659 | 4975.0589 | 4932.5626 | 4932.5626 | 4932.5626 | 4932.5626 | 4932.5626 | 4932.5626 | 4932.5626 | 4932.5626 | 4932.5626 | 4932.5626 | 4932.5626 | 4932.5626 | 4932.5626 | 4932.5626 | 4932.5626 | 4932.5626
50% | 11423.5112 | 15278.7323 | 16337.1848 | 16313.1737 | 16313.2019 | 16436.9714 | 16545.1835 | 16831.6344 | 17029.1638 | 17117.637 | 17220.9765 | 17313.198 | 17533.5956 | 17773.5518 | 17784.3406 | 17784.3406 | 17784.3406 | 17784.3406 | 17784.3406 | 17784.3406 | 17784.3406 | 17784.3406 | 17784.3406 | 17784.3406 | 17784.3406 | 17784.3406 | 17784.3406 | 17784.3406 | 17784.3406 | 17784.3406 |  | 7394.6021 | 9591.7919 | 10167.8822 | 10134.1643 | 10137.7857 | 10197.5181 | 10353.9563 | 10459.2602 | 10562.0269 | 10682.0973 | 10793.7552 | 10901.8432 | 10914.8067 | 11040.8439 | 10946.5344 | 10946.5344 | 10946.5344 | 10946.5344 | 10946.5344 | 10946.5344 | 10946.5344 | 10946.5344 | 10946.5344 | 10946.5344 | 10946.5344 | 10946.5344 | 10946.5344 | 10946.5344 | 10946.5344 | 10946.5344
45% | 15212.2424 | 20346.0893 | 21755.5891 | 21723.6144 | 21723.6519 | 21888.471 | 22032.5727 | 22414.0282 | 22677.0704 | 22794.8867 | 22932.4999 | 23055.3076 | 23348.8025 | 23668.3427 | 23682.7098 | 23682.7098 | 23682.7098 | 23682.7098 | 23682.7098 | 23682.7098 | 23682.7098 | 23682.7098 | 23682.7098 | 23682.7098 | 23682.7098 | 23682.7098 | 23682.7098 | 23682.7098 | 23682.7098 | 23682.7098 |  | 11205.1738 | 14534.6151 | 15407.5751 | 15356.4817 | 15361.9693 | 15452.4829 | 15689.5365 | 15849.1054 | 16004.8297 | 16186.7744 | 16355.9716 | 16519.7595 | 16539.4032 | 16730.3897 | 16587.4809 | 16587.4809 | 16587.4809 | 16587.4809 | 16587.4809 | 16587.4809 | 16587.4809 | 16587.4809 | 16587.4809 | 16587.4809 | 16587.4809 | 16587.4809 | 16587.4809 | 16587.4809 | 16587.4809 | 16587.4809
40% | 10669.3699 | 14270.0823 | 15258.6595 | 15236.2334 | 15236.2598 | 15351.8585 | 15452.9267 | 15720.4671 | 15904.9563 | 15987.5889 | 16084.1062 | 16170.2396 | 16376.0873 | 16600.2024 | 16610.2789 | 16610.2789 | 16610.2789 | 16610.2789 | 16610.2789 | 16610.2789 | 16610.2789 | 16610.2789 | 16610.2789 | 16610.2789 | 16610.2789 | 16610.2789 | 16610.2789 | 16610.2789 | 16610.2789 | 16610.2789 |  | 11602.4418 | 15049.925 | 15953.8349 | 15900.9301 | 15906.6123 | 16000.3349 | 16245.793 | 16411.0192 | 16572.2646 | 16760.66 | 16935.8559 | 17105.4507 | 17125.7909 | 17323.5486 | 17175.5731 | 17175.5731 | 17175.5731 | 17175.5731 | 17175.5731 | 17175.5731 | 17175.5731 | 17175.5731 | 17175.5731 | 17175.5731 | 17175.5731 | 17175.5731 | 17175.5731 | 17175.5731 | 17175.5731 | 17175.5731
35% | 5531.6918 | 7398.5341 | 7911.0764 | 7899.4493 | 7899.463 | 7959.3968 | 8011.7972 | 8150.5074 | 8246.1586 | 8289.0006 | 8339.0415 | 8383.6986 | 8490.4233 | 8606.6191 | 8611.8434 | 8611.8434 | 8611.8434 | 8611.8434 | 8611.8434 | 8611.8434 | 8611.8434 | 8611.8434 | 8611.8434 | 8611.8434 | 8611.8434 | 8611.8434 | 8611.8434 | 8611.8434 | 8611.8434 | 8611.8434 |  | 15802.4839 | 20497.9436 | 21729.0656 | 21657.0094 | 21664.7486 | 21792.3985 | 22126.7114 | 22351.749 | 22571.3646 | 22827.9584 | 23066.5747 | 23297.5621 | 23325.2654 | 23594.6107 | 23393.0685 | 23393.0685 | 23393.0685 | 23393.0685 | 23393.0685 | 23393.0685 | 23393.0685 | 23393.0685 | 23393.0685 | 23393.0685 | 23393.0685 | 23393.0685 | 23393.0685 | 23393.0685 | 23393.0685 | 23393.0685
30% | 2572.8044 | 3441.0777 | 3679.4625 | 3674.0547 | 3674.0611 | 3701.9365 | 3726.308 | 3790.8225 | 3835.3101 | 3855.2361 | 3878.5102 | 3899.2803 | 3948.9183 | 4002.9613 | 4005.3911 | 4005.3911 | 4005.3911 | 4005.3911 | 4005.3911 | 4005.3911 | 4005.3911 | 4005.3911 | 4005.3911 | 4005.3911 | 4005.3911 | 4005.3911 | 4005.3911 | 4005.3911 | 4005.3911 | 4005.3911 |  | 14602.4719 | 18941.3669 | 20078.9997 | 20012.4153 | 20019.5668 | 20137.5232 | 20446.449 | 20654.3976 | 20857.336 | 21094.4446 | 21314.9407 | 21528.3874 | 21553.9869 | 21802.8787 | 21616.6413 | 21616.6413 | 21616.6413 | 21616.6413 | 21616.6413 | 21616.6413 | 21616.6413 | 21616.6413 | 21616.6413 | 21616.6413 | 21616.6413 | 21616.6413 | 21616.6413 | 21616.6413 | 21616.6413 | 21616.6413
25% | 1756.6591 | 2349.4986 | 2512.263 | 2508.5707 | 2508.575 | 2527.6077 | 2544.2481 | 2588.2973 | 2618.6726 | 2632.2776 | 2648.1687 | 2662.3502 | 2696.242 | 2733.1414 | 2734.8005 | 2734.8005 | 2734.8005 | 2734.8005 | 2734.8005 | 2734.8005 | 2734.8005 | 2734.8005 | 2734.8005 | 2734.8005 | 2734.8005 | 2734.8005 | 2734.8005 | 2734.8005 | 2734.8005 | 2734.8005 |  | 4211.9437 | 5463.4566 | 5791.5959 | 5772.3903 | 5774.453 | 5808.4764 | 5897.5831 | 5957.564 | 6016.0996 | 6084.4913 | 6148.0913 | 6209.658 | 6217.0419 | 6288.8323 | 6235.1139 | 6235.1139 | 6235.1139 | 6235.1139 | 6235.1139 | 6235.1139 | 6235.1139 | 6235.1139 | 6235.1139 | 6235.1139 | 6235.1139 | 6235.1139 | 6235.1139 | 6235.1139 | 6235.1139 | 6235.1139
20% | 1064.1612 | 1423.2957 | 1521.8962 | 1519.6595 | 1519.6621 | 1531.1919 | 1541.2724 | 1567.9569 | 1586.3578 | 1594.5995 | 1604.2262 | 1612.8171 | 1633.3483 | 1655.7015 | 1656.7065 | 1656.7065 | 1656.7065 | 1656.7065 | 1656.7065 | 1656.7065 | 1656.7065 | 1656.7065 | 1656.7065 | 1656.7065 | 1656.7065 | 1656.7065 | 1656.7065 | 1656.7065 | 1656.7065 | 1656.7065 |  | 1130.2439 | 1466.0781 | 1554.1318 | 1548.9782 | 1549.5317 | 1558.6616 | 1582.5727 | 1598.6681 | 1614.3757 | 1632.7282 | 1649.7947 | 1666.3157 | 1668.2971 | 1687.5616 | 1673.1466 | 1673.1466 | 1673.1466 | 1673.1466 | 1673.1466 | 1673.1466 | 1673.1466 | 1673.1466 | 1673.1466 | 1673.1466 | 1673.1466 | 1673.1466 | 1673.1466 | 1673.1466 | 1673.1466 | 1673.1466
15% | 681.3227 | 911.2564 | 974.3848 | 972.9527 | 972.9544 | 980.3363 | 986.7903 | 1003.8748 | 1015.6559 | 1020.9326 | 1027.096 | 1032.5963 | 1045.7413 | 1060.0528 | 1060.6963 | 1060.6963 | 1060.6963 | 1060.6963 | 1060.6963 | 1060.6963 | 1060.6963 | 1060.6963 | 1060.6963 | 1060.6963 | 1060.6963 | 1060.6963 | 1060.6963 | 1060.6963 | 1060.6963 | 1060.6963 |  | 623.3989 | 808.632 | 857.1991 | 854.3565 | 854.6618 | 859.6975 | 872.886 | 881.7636 | 890.4273 | 900.5498 | 909.963 | 919.0754 | 920.1682 | 930.7938 | 922.843 | 922.843 | 922.843 | 922.843 | 922.843 | 922.843 | 922.843 | 922.843 | 922.843 | 922.843 | 922.843 | 922.843 | 922.843 | 922.843 | 922.843 | 922.843
10% | 456.0176 | 609.915 | 652.1676 | 651.2091 | 651.2102 | 656.151 | 660.4707 | 671.9056 | 679.7908 | 683.3226 | 687.4479 | 691.1293 | 699.9274 | 709.5062 | 709.9369 | 709.9369 | 709.9369 | 709.9369 | 709.9369 | 709.9369 | 709.9369 | 709.9369 | 709.9369 | 709.9369 | 709.9369 | 709.9369 | 709.9369 | 709.9369 | 709.9369 | 709.9369 |  | 145.6923 | 188.9825 | 200.3329 | 199.6686 | 199.7399 | 200.9168 | 203.999 | 206.0738 | 208.0985 | 210.4642 | 212.6642 | 214.7938 | 215.0492 | 217.5324 | 215.6743 | 215.6743 | 215.6743 | 215.6743 | 215.6743 | 215.6743 | 215.6743 | 215.6743 | 215.6743 | 215.6743 | 215.6743 | 215.6743 | 215.6743 | 215.6743 | 215.6743 | 215.6743
5% | 324.4394 | 433.9316 | 463.9928 | 463.3108 | 463.3116 | 466.8268 | 469.9001 | 478.0356 | 483.6457 | 486.1584 | 489.0933 | 491.7125 | 497.972 | 504.787 | 505.0935 | 505.0935 | 505.0935 | 505.0935 | 505.0935 | 505.0935 | 505.0935 | 505.0935 | 505.0935 | 505.0935 | 505.0935 | 505.0935 | 505.0935 | 505.0935 | 505.0935 | 505.0935 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9.992e-14% | 28.4786 | 38.0896 | 40.7283 | 40.6684 | 40.6685 | 40.977 | 41.2468 | 41.9609 | 42.4533 | 42.6739 | 42.9315 | 43.1614 | 43.7109 | 44.3091 | 44.336 | 44.336 | 44.336 | 44.336 | 44.336 | 44.336 | 44.336 | 44.336 | 44.336 | 44.336 | 44.336 | 44.336 | 44.336 | 44.336 | 44.336 | 44.336 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E @ R (MWh) | 76270.6559 | 102010.5733 | 109077.4787 | 108917.1648 | 108917.353 | 109743.7175 | 110466.2102 | 112378.7394 | 113697.5722 | 114288.2758 | 114978.2363 | 115593.9659 | 117065.481 | 118667.5818 | 118739.6147 | 118739.6147 | 118739.6147 | 118739.6147 | 118739.6147 | 118739.6147 | 118739.6147 | 118739.6147 | 118739.6147 | 118739.6147 | 118739.6147 | 118739.6147 | 118739.6147 | 118739.6147 | 118739.6147 | 118739.6147 | E @ R (MWh) | 75581.6326 | 98039.5268 | 103927.8551 | 103583.2177 | 103620.2333 | 104230.7695 | 105829.7534 | 106906.0848 | 107956.4833 | 109183.7448 | 110325.0214 | 111429.8103 | 111562.3121 | 112850.5626 | 111886.6076 | 111886.6076 | 111886.6076 | 111886.6076 | 111886.6076 | 111886.6076 | 111886.6076 | 111886.6076 | 111886.6076 | 111886.6076 | 111886.6076 | 111886.6076 | 111886.6076 | 111886.6076 | 111886.6076 | 111886.6076
Option 6 Summer POE50 W E @ R (MWh) N 2 | 53389.4591 | 71407.4013 | 76354.2351 | 76242.0153 | 76242.1471 | 76820.6023 | 77326.3472 | 78665.1176 | 79588.3005 | 80001.7931 | 80484.7654 | 80915.7761 | 81945.8367 | 83067.3072 | 83117.7303 | 83117.7303 | 83117.7303 | 83117.7303 | 83117.7303 | 83117.7303 | 83117.7303 | 83117.7303 | 83117.7303 | 83117.7303 | 83117.7303 | 83117.7303 | 83117.7303 | 83117.7303 | 83117.7303 | 83117.7303 | Option 6 Summer POE10 W E @ R (MWh) N 2 | 22674.4898 | 29411.8581 | 31178.3565 | 31074.9653 | 31086.07 | 31269.2308 | 31748.926 | 32071.8254 | 32386.945 | 32755.1234 | 33097.5064 | 33428.9431 | 33468.6936 | 33855.1688 | 33565.9823 | 33565.9823 | 33565.9823 | 33565.9823 | 33565.9823 | 33565.9823 | 33565.9823 | 33565.9823 | 33565.9823 | 33565.9823 | 33565.9823 | 33565.9823 | 33565.9823 | 33565.9823 | 33565.9823 | 33565.9823
Option 7 -
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | 59.6718 | 82.8348 | 88.8563 | 89.8828 | 90.6833 | 92.0616 | 95.1975 | 97.2967 | 99.9559 | 101.3362 | 102.5505 | 100.3131 | 102.9353 | 107.0576 | 103.9293 | 103.9293 | 103.9293 | 103.9293 | 103.9293 | 103.9293 | 103.9293 | 103.9293 | 103.9293 | 103.9293 | 103.9293 | 103.9293 | 103.9293 | 103.9293 | 103.9293 | 103.9293 |  | 63.8857 | 86.7566 | 93.0131 | 93.9812 | 94.5959 | 95.9444 | 99.1293 | 100.8681 | 104.1807 | 114.2499 | 105.9488 | 104.3251 | 106.5169 | 111.3103 | 108.0657 | 108.0657 | 108.0657 | 108.0657 | 108.0657 | 108.0657 | 108.0657 | 108.0657 | 108.0657 | 108.0657 | 108.0657 | 108.0657 | 108.0657 | 108.0657 | 108.0657 | 108.0657
98% | 70.8865 | 98.4027 | 105.556 | 106.7753 | 107.7263 | 109.3637 | 113.0889 | 115.5826 | 118.7416 | 120.3813 | 121.8238 | 119.1659 | 122.2809 | 127.178 | 123.4618 | 123.4618 | 123.4618 | 123.4618 | 123.4618 | 123.4618 | 123.4618 | 123.4618 | 123.4618 | 123.4618 | 123.4618 | 123.4618 | 123.4618 | 123.4618 | 123.4618 | 123.4618 |  | 75.8924 | 103.0616 | 110.494 | 111.644 | 112.3742 | 113.9761 | 117.7596 | 119.8253 | 123.7603 | 135.7219 | 125.8608 | 123.932 | 126.5357 | 132.2299 | 128.3755 | 128.3755 | 128.3755 | 128.3755 | 128.3755 | 128.3755 | 128.3755 | 128.3755 | 128.3755 | 128.3755 | 128.3755 | 128.3755 | 128.3755 | 128.3755 | 128.3755 | 128.3755
97% | 140.3338 | 194.8074 | 208.9687 | 211.3826 | 213.2652 | 216.5068 | 223.8816 | 228.8183 | 235.0721 | 238.3182 | 241.174 | 235.9121 | 242.0789 | 251.7738 | 244.4167 | 244.4167 | 244.4167 | 244.4167 | 244.4167 | 244.4167 | 244.4167 | 244.4167 | 244.4167 | 244.4167 | 244.4167 | 244.4167 | 244.4167 | 244.4167 | 244.4167 | 244.4167 |  | 150.2438 | 204.0305 | 218.7445 | 221.0211 | 222.4667 | 225.638 | 233.1281 | 237.2175 | 245.0078 | 268.6881 | 249.1661 | 245.3476 | 250.5021 | 261.7749 | 254.1445 | 254.1445 | 254.1445 | 254.1445 | 254.1445 | 254.1445 | 254.1445 | 254.1445 | 254.1445 | 254.1445 | 254.1445 | 254.1445 | 254.1445 | 254.1445 | 254.1445 | 254.1445
95% | 414.5243 | 575.4311 | 617.2612 | 624.3915 | 629.9527 | 639.5277 | 661.3119 | 675.8939 | 694.3669 | 703.9554 | 712.391 | 696.8482 | 715.0638 | 743.7009 | 721.9694 | 721.9694 | 721.9694 | 721.9694 | 721.9694 | 721.9694 | 721.9694 | 721.9694 | 721.9694 | 721.9694 | 721.9694 | 721.9694 | 721.9694 | 721.9694 | 721.9694 | 721.9694 |  | 443.7972 | 602.6746 | 646.1375 | 652.8624 | 657.1324 | 666.4999 | 688.6245 | 700.704 | 723.7153 | 793.6633 | 735.9983 | 724.719 | 739.9446 | 773.2427 | 750.7037 | 750.7037 | 750.7037 | 750.7037 | 750.7037 | 750.7037 | 750.7037 | 750.7037 | 750.7037 | 750.7037 | 750.7037 | 750.7037 | 750.7037 | 750.7037 | 750.7037 | 750.7037
90% | 2285.5212 | 3172.6969 | 3403.3313 | 3442.6449 | 3473.3067 | 3526.0998 | 3646.209 | 3726.6085 | 3828.4608 | 3881.3281 | 3927.8385 | 3842.1418 | 3942.5756 | 4100.4692 | 3980.6499 | 3980.6499 | 3980.6499 | 3980.6499 | 3980.6499 | 3980.6499 | 3980.6499 | 3980.6499 | 3980.6499 | 3980.6499 | 3980.6499 | 3980.6499 | 3980.6499 | 3980.6499 | 3980.6499 | 3980.6499 |  | 2446.9201 | 3322.9067 | 3562.5435 | 3599.622 | 3623.165 | 3674.8134 | 3796.7998 | 3863.4014 | 3990.2765 | 4375.9415 | 4058 | 3995.8103 | 4079.7583 | 4263.3504 | 4139.0795 | 4139.0795 | 4139.0795 | 4139.0795 | 4139.0795 | 4139.0795 | 4139.0795 | 4139.0795 | 4139.0795 | 4139.0795 | 4139.0795 | 4139.0795 | 4139.0795 | 4139.0795 | 4139.0795 | 4139.0795
85% | 5583.3646 | 7750.6712 | 8314.0946 | 8410.1348 | 8485.0395 | 8614.0092 | 8907.4274 | 9103.8375 | 9352.6555 | 9481.8066 | 9595.4282 | 9386.0773 | 9631.4298 | 10017.1525 | 9724.4425 | 9724.4425 | 9724.4425 | 9724.4425 | 9724.4425 | 9724.4425 | 9724.4425 | 9724.4425 | 9724.4425 | 9724.4425 | 9724.4425 | 9724.4425 | 9724.4425 | 9724.4425 | 9724.4425 | 9724.4425 |  | 5977.6505 | 8117.623 | 8703.0385 | 8793.6186 | 8851.1326 | 8977.3059 | 9275.3098 | 9438.0128 | 9747.9596 | 10690.1116 | 9913.4032 | 9761.4782 | 9966.5573 | 10415.0597 | 10111.4747 | 10111.4747 | 10111.4747 | 10111.4747 | 10111.4747 | 10111.4747 | 10111.4747 | 10111.4747 | 10111.4747 | 10111.4747 | 10111.4747 | 10111.4747 | 10111.4747 | 10111.4747 | 10111.4747 | 10111.4747
80% | 8678.2039 | 12046.8408 | 12922.5678 | 13071.8427 | 13188.2668 | 13388.724 | 13844.7828 | 14150.0624 | 14536.7992 | 14737.5384 | 14914.14 | 14588.7467 | 14970.0973 | 15569.6246 | 15114.6665 | 15114.6665 | 15114.6665 | 15114.6665 | 15114.6665 | 15114.6665 | 15114.6665 | 15114.6665 | 15114.6665 | 15114.6665 | 15114.6665 | 15114.6665 | 15114.6665 | 15114.6665 | 15114.6665 | 15114.6665 |  | 9291.041 | 12617.1926 | 13527.1019 | 13667.8902 | 13757.2841 | 13953.3947 | 14416.5812 | 14669.4699 | 15151.219 | 16615.6026 | 15408.3675 | 15172.231 | 15490.9847 | 16188.0904 | 15716.2292 | 15716.2292 | 15716.2292 | 15716.2292 | 15716.2292 | 15716.2292 | 15716.2292 | 15716.2292 | 15716.2292 | 15716.2292 | 15716.2292 | 15716.2292 | 15716.2292 | 15716.2292 | 15716.2292 | 15716.2292
75% | 9574.4808 | 13291.0275 | 14257.1987 | 14421.8907 | 14550.339 | 14771.4991 | 15274.6593 | 15611.4679 | 16038.1465 | 16259.6179 | 16454.4587 | 16095.4591 | 16516.1952 | 17177.6412 | 16675.6955 | 16675.6955 | 16675.6955 | 16675.6955 | 16675.6955 | 16675.6955 | 16675.6955 | 16675.6955 | 16675.6955 | 16675.6955 | 16675.6955 | 16675.6955 | 16675.6955 | 16675.6955 | 16675.6955 | 16675.6955 |  | 10250.6112 | 13920.2847 | 14924.1686 | 15079.4974 | 15178.1238 | 15394.4886 | 15905.5125 | 16184.5193 | 16716.023 | 18331.6468 | 16999.7296 | 16739.2052 | 17090.8794 | 17859.9816 | 17339.387 | 17339.387 | 17339.387 | 17339.387 | 17339.387 | 17339.387 | 17339.387 | 17339.387 | 17339.387 | 17339.387 | 17339.387 | 17339.387 | 17339.387 | 17339.387 | 17339.387 | 17339.387
70% | 10287.2444 | 14280.4661 | 15318.563 | 15495.5153 | 15633.5258 | 15871.15 | 16411.7675 | 16773.6495 | 17232.0919 | 17470.0505 | 17679.396 | 17293.671 | 17745.7284 | 18456.4151 | 17917.1025 | 17917.1025 | 17917.1025 | 17917.1025 | 17917.1025 | 17917.1025 | 17917.1025 | 17917.1025 | 17917.1025 | 17917.1025 | 17917.1025 | 17917.1025 | 17917.1025 | 17917.1025 | 17917.1025 | 17917.1025 |  | 11013.7087 | 14956.5677 | 16035.1849 | 16202.077 | 16308.0455 | 16540.5174 | 17089.584 | 17389.3613 | 17960.4323 | 19696.3297 | 18265.2591 | 17985.3402 | 18363.1944 | 19189.5518 | 18630.202 | 18630.202 | 18630.202 | 18630.202 | 18630.202 | 18630.202 | 18630.202 | 18630.202 | 18630.202 | 18630.202 | 18630.202 | 18630.202 | 18630.202 | 18630.202 | 18630.202 | 18630.202
65% | 10840.7831 | 15048.8731 | 16142.8282 | 16329.302 | 16474.7386 | 16725.149 | 17294.8562 | 17676.2104 | 18159.3208 | 18410.0835 | 18630.6936 | 18224.2134 | 18700.5952 | 19449.5227 | 18881.1907 | 18881.1907 | 18881.1907 | 18881.1907 | 18881.1907 | 18881.1907 | 18881.1907 | 18881.1907 | 18881.1907 | 18881.1907 | 18881.1907 | 18881.1907 | 18881.1907 | 18881.1907 | 18881.1907 | 18881.1907 |  | 11606.3372 | 15761.3546 | 16898.0103 | 17073.8826 | 17185.553 | 17430.5339 | 18009.1448 | 18325.0525 | 18926.8519 | 20756.155 | 19248.0809 | 18953.1 | 19351.286 | 20222.1082 | 19632.6608 | 19632.6608 | 19632.6608 | 19632.6608 | 19632.6608 | 19632.6608 | 19632.6608 | 19632.6608 | 19632.6608 | 19632.6608 | 19632.6608 | 19632.6608 | 19632.6608 | 19632.6608 | 19632.6608 | 19632.6608
60% | 11934.3669 | 16566.9557 | 17771.2656 | 17976.5503 | 18136.658 | 18412.329 | 19039.5064 | 19459.3305 | 19991.1755 | 20267.2344 | 20510.0989 | 20062.6142 | 20587.052 | 21411.5289 | 20785.8653 | 20785.8653 | 20785.8653 | 20785.8653 | 20785.8653 | 20785.8653 | 20785.8653 | 20785.8653 | 20785.8653 | 20785.8653 | 20785.8653 | 20785.8653 | 20785.8653 | 20785.8653 | 20785.8653 | 20785.8653 |  | 12777.1477 | 17351.3101 | 18602.628 | 18796.2417 | 18919.1771 | 19188.8708 | 19825.8502 | 20173.6257 | 20836.1327 | 22849.9701 | 21189.7663 | 20865.0287 | 21303.3824 | 22262.0503 | 21613.1413 | 21613.1413 | 21613.1413 | 21613.1413 | 21613.1413 | 21613.1413 | 21613.1413 | 21613.1413 | 21613.1413 | 21613.1413 | 21613.1413 | 21613.1413 | 21613.1413 | 21613.1413 | 21613.1413 | 21613.1413
55% | 13276.2336 | 18429.6976 | 19769.4166 | 19997.783 | 20175.8928 | 20482.5595 | 21180.255 | 21647.2828 | 22238.927 | 22546.0252 | 22816.1967 | 22318.3981 | 22901.8021 | 23818.981 | 23122.9695 | 23122.9695 | 23122.9695 | 23122.9695 | 23122.9695 | 23122.9695 | 23122.9695 | 23122.9695 | 23122.9695 | 23122.9695 | 23122.9695 | 23122.9695 | 23122.9695 | 23122.9695 | 23122.9695 | 23122.9695 |  | 14213.7742 | 19302.2426 | 20694.2551 | 20909.6382 | 21046.3962 | 21346.4135 | 22055.013 | 22441.8914 | 23178.8888 | 25419.1564 | 23572.284 | 23211.0338 | 23698.6747 | 24765.1326 | 24043.2621 | 24043.2621 | 24043.2621 | 24043.2621 | 24043.2621 | 24043.2621 | 24043.2621 | 24043.2621 | 24043.2621 | 24043.2621 | 24043.2621 | 24043.2621 | 24043.2621 | 24043.2621 | 24043.2621 | 24043.2621
50% | 13456.7484 | 18680.2832 | 20038.2182 | 20269.6896 | 20450.2212 | 20761.0575 | 21468.2395 | 21941.6174 | 22541.3061 | 22852.5798 | 23126.4248 | 22621.8577 | 23213.1942 | 24142.8438 | 23437.3688 | 23437.3688 | 23437.3688 | 23437.3688 | 23437.3688 | 23437.3688 | 23437.3688 | 23437.3688 | 23437.3688 | 23437.3688 | 23437.3688 | 23437.3688 | 23437.3688 | 23437.3688 | 23437.3688 | 23437.3688 |  | 14407.0366 | 19564.692 | 20975.6315 | 21193.9432 | 21332.5606 | 21636.6572 | 22354.8915 | 22747.0302 | 23494.0484 | 25764.7766 | 23892.7925 | 23526.6304 | 24020.9018 | 25101.8601 | 24370.1745 | 24370.1745 | 24370.1745 | 24370.1745 | 24370.1745 | 24370.1745 | 24370.1745 | 24370.1745 | 24370.1745 | 24370.1745 | 24370.1745 | 24370.1745 | 24370.1745 | 24370.1745 | 24370.1745 | 24370.1745
45% | 10386.1977 | 14417.8303 | 15465.9127 | 15644.5671 | 15783.9051 | 16023.8151 | 16569.6328 | 16934.9957 | 17397.8478 | 17638.0954 | 17849.4547 | 17460.0193 | 17916.4251 | 18633.9479 | 18089.4477 | 18089.4477 | 18089.4477 | 18089.4477 | 18089.4477 | 18089.4477 | 18089.4477 | 18089.4477 | 18089.4477 | 18089.4477 | 18089.4477 | 18089.4477 | 18089.4477 | 18089.4477 | 18089.4477 | 18089.4477 |  | 11119.6499 | 15100.4354 | 16189.4278 | 16357.9252 | 16464.913 | 16699.6211 | 17253.9692 | 17556.63 | 18133.1942 | 19885.7893 | 18440.9531 | 18158.3417 | 18539.8305 | 19374.1366 | 18809.4064 | 18809.4064 | 18809.4064 | 18809.4064 | 18809.4064 | 18809.4064 | 18809.4064 | 18809.4064 | 18809.4064 | 18809.4064 | 18809.4064 | 18809.4064 | 18809.4064 | 18809.4064 | 18809.4064 | 18809.4064
40% | 5102.6915 | 7083.4142 | 7598.3323 | 7686.1044 | 7754.5606 | 7872.4272 | 8140.5849 | 8320.0861 | 8547.4832 | 8665.5158 | 8769.3556 | 8578.0278 | 8802.2579 | 9154.7736 | 8887.2631 | 8887.2631 | 8887.2631 | 8887.2631 | 8887.2631 | 8887.2631 | 8887.2631 | 8887.2631 | 8887.2631 | 8887.2631 | 8887.2631 | 8887.2631 | 8887.2631 | 8887.2631 | 8887.2631 | 8887.2631 |  | 5463.0332 | 7418.775 | 7953.792 | 8036.574 | 8089.1366 | 8204.4476 | 8476.7963 | 8625.4922 | 8908.7555 | 9769.7975 | 9059.9561 | 8921.1104 | 9108.5341 | 9518.4249 | 9240.9755 | 9240.9755 | 9240.9755 | 9240.9755 | 9240.9755 | 9240.9755 | 9240.9755 | 9240.9755 | 9240.9755 | 9240.9755 | 9240.9755 | 9240.9755 | 9240.9755 | 9240.9755 | 9240.9755 | 9240.9755
35% | 1907.0998 | 2647.3829 | 2839.8304 | 2872.6347 | 2898.2197 | 2942.2717 | 3042.494 | 3109.5815 | 3194.5697 | 3238.6837 | 3277.4932 | 3205.9856 | 3289.7902 | 3421.5408 | 3321.5604 | 3321.5604 | 3321.5604 | 3321.5604 | 3321.5604 | 3321.5604 | 3321.5604 | 3321.5604 | 3321.5604 | 3321.5604 | 3321.5604 | 3321.5604 | 3321.5604 | 3321.5604 | 3321.5604 | 3321.5604 |  | 2041.7754 | 2772.7219 | 2972.6813 | 3003.6205 | 3023.2655 | 3066.3623 | 3168.1509 | 3223.7251 | 3329.5931 | 3651.4023 | 3386.1034 | 3334.2106 | 3404.2591 | 3557.4533 | 3453.7583 | 3453.7583 | 3453.7583 | 3453.7583 | 3453.7583 | 3453.7583 | 3453.7583 | 3453.7583 | 3453.7583 | 3453.7583 | 3453.7583 | 3453.7583 | 3453.7583 | 3453.7583 | 3453.7583 | 3453.7583
30% | 951.1511 | 1320.3614 | 1416.3431 | 1432.704 | 1445.4643 | 1467.4349 | 1517.42 | 1550.8793 | 1593.2665 | 1615.268 | 1634.624 | 1598.9601 | 1640.757 | 1706.4666 | 1656.6021 | 1656.6021 | 1656.6021 | 1656.6021 | 1656.6021 | 1656.6021 | 1656.6021 | 1656.6021 | 1656.6021 | 1656.6021 | 1656.6021 | 1656.6021 | 1656.6021 | 1656.6021 | 1656.6021 | 1656.6021 |  | 1018.3194 | 1382.8733 | 1482.6014 | 1498.0321 | 1507.8299 | 1529.3241 | 1580.0904 | 1607.8076 | 1660.6084 | 1821.1082 | 1688.7924 | 1662.9113 | 1697.8475 | 1774.2519 | 1722.5348 | 1722.5348 | 1722.5348 | 1722.5348 | 1722.5348 | 1722.5348 | 1722.5348 | 1722.5348 | 1722.5348 | 1722.5348 | 1722.5348 | 1722.5348 | 1722.5348 | 1722.5348 | 1722.5348 | 1722.5348
25% | 560.7353 | 778.3972 | 834.9816 | 844.6269 | 852.1495 | 865.1019 | 894.5698 | 914.2952 | 939.2839 | 952.2545 | 963.6655 | 942.6404 | 967.2811 | 1006.0191 | 976.6223 | 976.6223 | 976.6223 | 976.6223 | 976.6223 | 976.6223 | 976.6223 | 976.6223 | 976.6223 | 976.6223 | 976.6223 | 976.6223 | 976.6223 | 976.6223 | 976.6223 | 976.6223 |  | 600.3333 | 815.25 | 874.0431 | 883.14 | 888.9161 | 901.5876 | 931.5161 | 947.8563 | 978.9841 | 1073.6041 | 995.5996 | 980.3418 | 1000.9378 | 1045.9808 | 1015.4918 | 1015.4918 | 1015.4918 | 1015.4918 | 1015.4918 | 1015.4918 | 1015.4918 | 1015.4918 | 1015.4918 | 1015.4918 | 1015.4918 | 1015.4918 | 1015.4918 | 1015.4918 | 1015.4918 | 1015.4918
20% | 283.3663 | 393.3611 | 421.9559 | 426.8302 | 430.6317 | 437.1772 | 452.0687 | 462.0369 | 474.6648 | 481.2195 | 486.986 | 476.3611 | 488.8132 | 508.3893 | 493.5337 | 493.5337 | 493.5337 | 493.5337 | 493.5337 | 493.5337 | 493.5337 | 493.5337 | 493.5337 | 493.5337 | 493.5337 | 493.5337 | 493.5337 | 493.5337 | 493.5337 | 493.5337 |  | 303.377 | 411.9846 | 441.6956 | 446.2927 | 449.2116 | 455.6151 | 470.7394 | 478.9969 | 494.7273 | 542.5433 | 503.1238 | 495.4134 | 505.8215 | 528.5839 | 513.1763 | 513.1763 | 513.1763 | 513.1763 | 513.1763 | 513.1763 | 513.1763 | 513.1763 | 513.1763 | 513.1763 | 513.1763 | 513.1763 | 513.1763 | 513.1763 | 513.1763 | 513.1763
15% | 115.4455 | 160.2582 | 171.908 | 173.8938 | 175.4425 | 178.1092 | 184.1761 | 188.2372 | 193.382 | 196.0524 | 198.4017 | 194.073 | 199.1461 | 207.1216 | 201.0693 | 201.0693 | 201.0693 | 201.0693 | 201.0693 | 201.0693 | 201.0693 | 201.0693 | 201.0693 | 201.0693 | 201.0693 | 201.0693 | 201.0693 | 201.0693 | 201.0693 | 201.0693 |  | 123.598 | 167.8456 | 179.95 | 181.8229 | 183.0121 | 185.621 | 191.7827 | 195.1469 | 201.5556 | 221.0361 | 204.9764 | 201.8351 | 206.0754 | 215.349 | 209.0718 | 209.0718 | 209.0718 | 209.0718 | 209.0718 | 209.0718 | 209.0718 | 209.0718 | 209.0718 | 209.0718 | 209.0718 | 209.0718 | 209.0718 | 209.0718 | 209.0718 | 209.0718
10% | 46.4781 | 64.5196 | 69.2097 | 70.0092 | 70.6327 | 71.7063 | 74.1488 | 75.7838 | 77.8551 | 78.9302 | 79.876 | 78.1333 | 80.1757 | 83.3866 | 80.95 | 80.95 | 80.95 | 80.95 | 80.95 | 80.95 | 80.95 | 80.95 | 80.95 | 80.95 | 80.95 | 80.95 | 80.95 | 80.95 | 80.95 | 80.95 |  | 49.7602 | 67.5742 | 72.4474 | 73.2014 | 73.6802 | 74.7305 | 77.2112 | 78.5656 | 81.1457 | 88.9886 | 82.523 | 81.2583 | 82.9654 | 86.6989 | 84.1718 | 84.1718 | 84.1718 | 84.1718 | 84.1718 | 84.1718 | 84.1718 | 84.1718 | 84.1718 | 84.1718 | 84.1718 | 84.1718 | 84.1718 | 84.1718 | 84.1718 | 84.1718
5% | 39.5813 | 54.9457 | 58.9399 | 59.6207 | 60.1517 | 61.066 | 63.1461 | 64.5385 | 66.3024 | 67.218 | 68.0234 | 66.5393 | 68.2787 | 71.0131 | 68.938 | 68.938 | 68.938 | 68.938 | 68.938 | 68.938 | 68.938 | 68.938 | 68.938 | 68.938 | 68.938 | 68.938 | 68.938 | 68.938 | 68.938 | 68.938 |  | 42.3765 | 57.5471 | 61.6972 | 62.3393 | 62.747 | 63.6415 | 65.7541 | 66.9075 | 69.1048 | 75.7838 | 70.2776 | 69.2006 | 70.6544 | 73.8339 | 71.6818 | 71.6818 | 71.6818 | 71.6818 | 71.6818 | 71.6818 | 71.6818 | 71.6818 | 71.6818 | 71.6818 | 71.6818 | 71.6818 | 71.6818 | 71.6818 | 71.6818 | 71.6818
9.992e-14% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E @ R (MWh) | 105995.1099 | 147139.4588 | 157835.5397 | 159658.7762 | 161080.774 | 163529.1464 | 169099.4242 | 172828.0925 | 177551.675 | 180003.4929 | 182160.4948 | 178186.1586 | 182843.9537 | 190166.5478 | 184609.7151 | 184609.7151 | 184609.7151 | 184609.7151 | 184609.7151 | 184609.7151 | 184609.7151 | 184609.7151 | 184609.7151 | 184609.7151 | 184609.7151 | 184609.7151 | 184609.7151 | 184609.7151 | 184609.7151 | 184609.7151 | E @ R (MWh) | 113480.2695 | 154105.704 | 165219.287 | 166938.8679 | 168030.7193 | 170426.0046 | 176083.3386 | 179172.1077 | 185056.165 | 202942.0666 | 188196.9625 | 185312.8045 | 189206.044 | 197720.4561 | 191957.169 | 191957.169 | 191957.169 | 191957.169 | 191957.169 | 191957.169 | 191957.169 | 191957.169 | 191957.169 | 191957.169 | 191957.169 | 191957.169 | 191957.169 | 191957.169 | 191957.169 | 191957.169
Option 7 Winter POE50 W E @ R (MWh) N 2 | 74196.5769 | 102997.6211 | 110484.8778 | 111761.1434 | 112756.5418 | 114470.4025 | 118369.597 | 120979.6647 | 124286.1725 | 126002.4451 | 127512.3464 | 124730.311 | 127990.7676 | 133116.5835 | 129226.8005 | 129226.8005 | 129226.8005 | 129226.8005 | 129226.8005 | 129226.8005 | 129226.8005 | 129226.8005 | 129226.8005 | 129226.8005 | 129226.8005 | 129226.8005 | 129226.8005 | 129226.8005 | 129226.8005 | 129226.8005 | Option 7 Winter POE10 W E @ R (MWh) N 2 | 34044.0809 | 46231.7112 | 49565.7861 | 50081.6604 | 50409.2158 | 51127.8014 | 52825.0016 | 53751.6323 | 55516.8495 | 60882.62 | 56459.0887 | 55593.8414 | 56761.8132 | 59316.1368 | 57587.1507 | 57587.1507 | 57587.1507 | 57587.1507 | 57587.1507 | 57587.1507 | 57587.1507 | 57587.1507 | 57587.1507 | 57587.1507 | 57587.1507 | 57587.1507 | 57587.1507 | 57587.1507 | 57587.1507 | 57587.1507
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 76.9936 | 99.7405 | 105.6969 | 105.3426 | 105.3724 | 105.9856 | 107.6 | 108.6824 | 109.7411 | 110.979 | 112.1272 | 113.2411 | 113.3701 | 114.6698 | 113.6883 | 113.6883 | 113.6883 | 113.6883 | 113.6883 | 113.6883 | 113.6883 | 113.6883 | 113.6883 | 113.6883 | 113.6883 | 113.6883 | 113.6883 | 113.6883 | 113.6883 | 113.6883
98% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 38.1099 | 49.369 | 52.3173 | 52.1419 | 52.1567 | 52.4602 | 53.2593 | 53.7951 | 54.3191 | 54.9318 | 55.5002 | 56.0515 | 56.1154 | 56.7587 | 56.2728 | 56.2728 | 56.2728 | 56.2728 | 56.2728 | 56.2728 | 56.2728 | 56.2728 | 56.2728 | 56.2728 | 56.2728 | 56.2728 | 56.2728 | 56.2728 | 56.2728 | 56.2728
97% | 16.9149 | 22.4762 | 23.991 | 23.9477 | 23.9472 | 24.1204 | 24.3105 | 24.7002 | 24.9803 | 25.1325 | 25.2993 | 25.4517 | 25.7265 | 26.0674 | 26.0444 | 26.0444 | 26.0444 | 26.0444 | 26.0444 | 26.0444 | 26.0444 | 26.0444 | 26.0444 | 26.0444 | 26.0444 | 26.0444 | 26.0444 | 26.0444 | 26.0444 | 26.0444 |  | 75.446 | 97.7357 | 103.5723 | 103.2252 | 103.2543 | 103.8552 | 105.4372 | 106.4978 | 107.5353 | 108.7483 | 109.8734 | 110.9649 | 111.0913 | 112.3649 | 111.4031 | 111.4031 | 111.4031 | 111.4031 | 111.4031 | 111.4031 | 111.4031 | 111.4031 | 111.4031 | 111.4031 | 111.4031 | 111.4031 | 111.4031 | 111.4031 | 111.4031 | 111.4031
95% | 83.2734 | 110.6519 | 118.1097 | 117.8962 | 117.8937 | 118.7467 | 119.6823 | 121.6012 | 122.9798 | 123.7293 | 124.5504 | 125.3007 | 126.6535 | 128.3318 | 128.2183 | 128.2183 | 128.2183 | 128.2183 | 128.2183 | 128.2183 | 128.2183 | 128.2183 | 128.2183 | 128.2183 | 128.2183 | 128.2183 | 128.2183 | 128.2183 | 128.2183 | 128.2183 |  | 111.4279 | 144.3481 | 152.9683 | 152.4556 | 152.4987 | 153.3862 | 155.7226 | 157.2891 | 158.8214 | 160.6129 | 162.2746 | 163.8866 | 164.0733 | 165.9543 | 164.5337 | 164.5337 | 164.5337 | 164.5337 | 164.5337 | 164.5337 | 164.5337 | 164.5337 | 164.5337 | 164.5337 | 164.5337 | 164.5337 | 164.5337 | 164.5337 | 164.5337 | 164.5337
90% | 144.4273 | 191.9119 | 204.8464 | 204.4763 | 204.4719 | 205.9512 | 207.574 | 210.9021 | 213.2931 | 214.593 | 216.0171 | 217.3184 | 219.6647 | 222.5754 | 222.3787 | 222.3787 | 222.3787 | 222.3787 | 222.3787 | 222.3787 | 222.3787 | 222.3787 | 222.3787 | 222.3787 | 222.3787 | 222.3787 | 222.3787 | 222.3787 | 222.3787 | 222.3787 |  | 483.1446 | 625.8842 | 663.261 | 661.0381 | 661.2248 | 665.0728 | 675.2033 | 681.9957 | 688.6395 | 696.4074 | 703.6125 | 710.602 | 711.4117 | 719.5673 | 713.4081 | 713.4081 | 713.4081 | 713.4081 | 713.4081 | 713.4081 | 713.4081 | 713.4081 | 713.4081 | 713.4081 | 713.4081 | 713.4081 | 713.4081 | 713.4081 | 713.4081 | 713.4081
85% | 409.8612 | 544.6148 | 581.321 | 580.2706 | 580.258 | 584.4562 | 589.0613 | 598.5059 | 605.2912 | 608.9802 | 613.0214 | 616.7142 | 623.3728 | 631.6329 | 631.0746 | 631.0746 | 631.0746 | 631.0746 | 631.0746 | 631.0746 | 631.0746 | 631.0746 | 631.0746 | 631.0746 | 631.0746 | 631.0746 | 631.0746 | 631.0746 | 631.0746 | 631.0746 |  | 457.0286 | 592.0526 | 627.4091 | 625.3063 | 625.4829 | 629.1229 | 638.7059 | 645.1311 | 651.4157 | 658.7637 | 665.5794 | 672.1911 | 672.9571 | 680.6717 | 674.8455 | 674.8455 | 674.8455 | 674.8455 | 674.8455 | 674.8455 | 674.8455 | 674.8455 | 674.8455 | 674.8455 | 674.8455 | 674.8455 | 674.8455 | 674.8455 | 674.8455 | 674.8455
80% | 572.5046 | 760.7318 | 812.0039 | 810.5367 | 810.5191 | 816.3833 | 822.8158 | 836.0082 | 845.4861 | 850.639 | 856.2839 | 861.4421 | 870.743 | 882.2809 | 881.5011 | 881.5011 | 881.5011 | 881.5011 | 881.5011 | 881.5011 | 881.5011 | 881.5011 | 881.5011 | 881.5011 | 881.5011 | 881.5011 | 881.5011 | 881.5011 | 881.5011 | 881.5011 |  | 319.1946 | 413.4971 | 438.1905 | 436.7219 | 436.8452 | 439.3874 | 446.0803 | 450.5677 | 454.957 | 460.089 | 464.8491 | 469.4668 | 470.0018 | 475.3898 | 471.3206 | 471.3206 | 471.3206 | 471.3206 | 471.3206 | 471.3206 | 471.3206 | 471.3206 | 471.3206 | 471.3206 | 471.3206 | 471.3206 | 471.3206 | 471.3206 | 471.3206 | 471.3206
75% | 1492.4153 | 1983.0895 | 2116.7465 | 2112.9218 | 2112.876 | 2128.1627 | 2144.9312 | 2179.3214 | 2204.0286 | 2217.4612 | 2232.1763 | 2245.623 | 2269.8686 | 2299.9458 | 2297.9131 | 2297.9131 | 2297.9131 | 2297.9131 | 2297.9131 | 2297.9131 | 2297.9131 | 2297.9131 | 2297.9131 | 2297.9131 | 2297.9131 | 2297.9131 | 2297.9131 | 2297.9131 | 2297.9131 | 2297.9131 |  | 569.714 | 738.0296 | 782.1036 | 779.4824 | 779.7025 | 784.24 | 796.1857 | 804.1951 | 812.0293 | 821.1891 | 829.6853 | 837.9271 | 838.8819 | 848.4987 | 841.2359 | 841.2359 | 841.2359 | 841.2359 | 841.2359 | 841.2359 | 841.2359 | 841.2359 | 841.2359 | 841.2359 | 841.2359 | 841.2359 | 841.2359 | 841.2359 | 841.2359 | 841.2359
70% | 2578.4391 | 3426.1747 | 3657.0932 | 3650.4854 | 3650.4063 | 3676.8171 | 3705.7879 | 3765.2037 | 3807.8902 | 3831.0976 | 3856.5209 | 3879.7526 | 3921.6416 | 3973.6059 | 3970.094 | 3970.094 | 3970.094 | 3970.094 | 3970.094 | 3970.094 | 3970.094 | 3970.094 | 3970.094 | 3970.094 | 3970.094 | 3970.094 | 3970.094 | 3970.094 | 3970.094 | 3970.094 |  | 1037.8661 | 1344.492 | 1424.783 | 1420.0079 | 1420.4087 | 1428.6749 | 1450.4368 | 1465.0278 | 1479.2996 | 1495.9862 | 1511.464 | 1526.4784 | 1528.2178 | 1545.7371 | 1532.5062 | 1532.5062 | 1532.5062 | 1532.5062 | 1532.5062 | 1532.5062 | 1532.5062 | 1532.5062 | 1532.5062 | 1532.5062 | 1532.5062 | 1532.5062 | 1532.5062 | 1532.5062 | 1532.5062 | 1532.5062
65% | 6475.8072 | 8604.914 | 9184.8711 | 9168.2753 | 9168.0768 | 9234.408 | 9307.1689 | 9456.393 | 9563.6012 | 9621.887 | 9685.7381 | 9744.0851 | 9849.2903 | 9979.7998 | 9970.9794 | 9970.9794 | 9970.9794 | 9970.9794 | 9970.9794 | 9970.9794 | 9970.9794 | 9970.9794 | 9970.9794 | 9970.9794 | 9970.9794 | 9970.9794 | 9970.9794 | 9970.9794 | 9970.9794 | 9970.9794 |  | 1305.7961 | 1691.5789 | 1792.5974 | 1786.5896 | 1787.0939 | 1797.4941 | 1824.8739 | 1843.2317 | 1861.1878 | 1882.1821 | 1901.6555 | 1920.546 | 1922.7344 | 1944.7764 | 1928.1299 | 1928.1299 | 1928.1299 | 1928.1299 | 1928.1299 | 1928.1299 | 1928.1299 | 1928.1299 | 1928.1299 | 1928.1299 | 1928.1299 | 1928.1299 | 1928.1299 | 1928.1299 | 1928.1299 | 1928.1299
60% | 9465.8424 | 12578.0087 | 13425.7459 | 13401.4874 | 13401.1972 | 13498.1551 | 13604.5115 | 13822.636 | 13979.3447 | 14064.5425 | 14157.8751 | 14243.1624 | 14396.9433 | 14587.7122 | 14574.8193 | 14574.8193 | 14574.8193 | 14574.8193 | 14574.8193 | 14574.8193 | 14574.8193 | 14574.8193 | 14574.8193 | 14574.8193 | 14574.8193 | 14574.8193 | 14574.8193 | 14574.8193 | 14574.8193 | 14574.8193 |  | 2043.3291 | 2647.0078 | 2805.083 | 2795.6818 | 2796.4711 | 2812.7454 | 2855.5897 | 2884.3162 | 2912.4142 | 2945.2664 | 2975.7387 | 3005.2988 | 3008.7233 | 3043.2149 | 3017.1662 | 3017.1662 | 3017.1662 | 3017.1662 | 3017.1662 | 3017.1662 | 3017.1662 | 3017.1662 | 3017.1662 | 3017.1662 | 3017.1662 | 3017.1662 | 3017.1662 | 3017.1662 | 3017.1662 | 3017.1662
55% | 10703.6666 | 14222.8031 | 15181.3967 | 15153.966 | 15153.6378 | 15263.2747 | 15383.539 | 15630.1871 | 15807.3882 | 15903.7271 | 16009.2646 | 16105.7046 | 16279.5951 | 16495.3104 | 16480.7315 | 16480.7315 | 16480.7315 | 16480.7315 | 16480.7315 | 16480.7315 | 16480.7315 | 16480.7315 | 16480.7315 | 16480.7315 | 16480.7315 | 16480.7315 | 16480.7315 | 16480.7315 | 16480.7315 | 16480.7315 |  | 3926.5772 | 5086.6405 | 5390.4069 | 5372.341 | 5373.8577 | 5405.1313 | 5487.4633 | 5542.6658 | 5596.6606 | 5659.7913 | 5718.3486 | 5775.1529 | 5781.7337 | 5848.0147 | 5797.958 | 5797.958 | 5797.958 | 5797.958 | 5797.958 | 5797.958 | 5797.958 | 5797.958 | 5797.958 | 5797.958 | 5797.958 | 5797.958 | 5797.958 | 5797.958 | 5797.958 | 5797.958
50% | 13744.0128 | 18262.75 | 19493.6294 | 19458.4071 | 19457.9857 | 19598.7646 | 19753.1897 | 20069.8975 | 20297.432 | 20421.1357 | 20556.6509 | 20680.4844 | 20903.7679 | 21180.7565 | 21162.0366 | 21162.0366 | 21162.0366 | 21162.0366 | 21162.0366 | 21162.0366 | 21162.0366 | 21162.0366 | 21162.0366 | 21162.0366 | 21162.0366 | 21162.0366 | 21162.0366 | 21162.0366 | 21162.0366 | 21162.0366 |  | 8714.0125 | 11288.47 | 11962.6002 | 11922.5077 | 11925.8735 | 11995.2773 | 12177.9916 | 12300.4992 | 12420.3265 | 12560.4285 | 12690.3811 | 12816.4434 | 12831.0478 | 12978.1412 | 12867.0534 | 12867.0534 | 12867.0534 | 12867.0534 | 12867.0534 | 12867.0534 | 12867.0534 | 12867.0534 | 12867.0534 | 12867.0534 | 12867.0534 | 12867.0534 | 12867.0534 | 12867.0534 | 12867.0534 | 12867.0534
45% | 18302.3635 | 24319.7888 | 25958.9027 | 25911.9985 | 25911.4373 | 26098.9072 | 26304.5489 | 26726.2963 | 27029.2951 | 27194.0265 | 27374.4867 | 27539.391 | 27836.7289 | 28205.5838 | 28180.6551 | 28180.6551 | 28180.6551 | 28180.6551 | 28180.6551 | 28180.6551 | 28180.6551 | 28180.6551 | 28180.6551 | 28180.6551 | 28180.6551 | 28180.6551 | 28180.6551 | 28180.6551 | 28180.6551 | 28180.6551 |  | 13204.5002 | 17105.6219 | 18127.1435 | 18066.3908 | 18071.491 | 18176.6598 | 18453.5301 | 18639.1681 | 18820.7445 | 19033.0436 | 19229.9631 | 19420.9876 | 19443.1179 | 19666.0112 | 19497.6778 | 19497.6778 | 19497.6778 | 19497.6778 | 19497.6778 | 19497.6778 | 19497.6778 | 19497.6778 | 19497.6778 | 19497.6778 | 19497.6778 | 19497.6778 | 19497.6778 | 19497.6778 | 19497.6778 | 19497.6778
40% | 12836.6798 | 17057.1053 | 18206.7263 | 18173.8293 | 18173.4357 | 18304.9209 | 18449.1513 | 18744.9511 | 18957.4646 | 19073.0018 | 19199.5707 | 19315.2292 | 19523.7723 | 19782.475 | 19764.9909 | 19764.9909 | 19764.9909 | 19764.9909 | 19764.9909 | 19764.9909 | 19764.9909 | 19764.9909 | 19764.9909 | 19764.9909 | 19764.9909 | 19764.9909 | 19764.9909 | 19764.9909 | 19764.9909 | 19764.9909 |  | 13672.6523 | 17712.0843 | 18769.8229 | 18706.9162 | 18712.1973 | 18821.0947 | 19107.7811 | 19300.0008 | 19488.0148 | 19707.8407 | 19911.7418 | 20109.5389 | 20132.4538 | 20363.2496 | 20188.9481 | 20188.9481 | 20188.9481 | 20188.9481 | 20188.9481 | 20188.9481 | 20188.9481 | 20188.9481 | 20188.9481 | 20188.9481 | 20188.9481 | 20188.9481 | 20188.9481 | 20188.9481 | 20188.9481 | 20188.9481
35% | 6655.3655 | 8843.5072 | 9439.545 | 9422.4891 | 9422.285 | 9490.4555 | 9565.2339 | 9718.5956 | 9828.7764 | 9888.6783 | 9954.2998 | 10014.2647 | 10122.3869 | 10256.5152 | 10247.4502 | 10247.4502 | 10247.4502 | 10247.4502 | 10247.4502 | 10247.4502 | 10247.4502 | 10247.4502 | 10247.4502 | 10247.4502 | 10247.4502 | 10247.4502 | 10247.4502 | 10247.4502 | 10247.4502 | 10247.4502 |  | 18622.1031 | 24123.7949 | 25564.4311 | 25478.7524 | 25485.9452 | 25634.2631 | 26024.729 | 26286.5314 | 26542.6059 | 26842.008 | 27119.7205 | 27389.1195 | 27420.3294 | 27734.6724 | 27497.2745 | 27497.2745 | 27497.2745 | 27497.2745 | 27497.2745 | 27497.2745 | 27497.2745 | 27497.2745 | 27497.2745 | 27497.2745 | 27497.2745 | 27497.2745 | 27497.2745 | 27497.2745 | 27497.2745 | 27497.2745
30% | 3095.428 | 4113.1385 | 4390.3573 | 4382.4246 | 4382.3296 | 4414.0359 | 4448.8155 | 4520.1445 | 4571.3898 | 4599.2504 | 4629.7711 | 4657.6609 | 4707.9489 | 4770.3323 | 4766.1162 | 4766.1162 | 4766.1162 | 4766.1162 | 4766.1162 | 4766.1162 | 4766.1162 | 4766.1162 | 4766.1162 | 4766.1162 | 4766.1162 | 4766.1162 | 4766.1162 | 4766.1162 | 4766.1162 | 4766.1162 |  | 17207.9743 | 22291.8776 | 23623.1145 | 23543.942 | 23550.5887 | 23687.6435 | 24048.4582 | 24290.3798 | 24527.0085 | 24803.6745 | 25060.2981 | 25309.2393 | 25338.0792 | 25628.5516 | 25409.1812 | 25409.1812 | 25409.1812 | 25409.1812 | 25409.1812 | 25409.1812 | 25409.1812 | 25409.1812 | 25409.1812 | 25409.1812 | 25409.1812 | 25409.1812 | 25409.1812 | 25409.1812 | 25409.1812 | 25409.1812
25% | 2113.496 | 2808.3682 | 2997.6476 | 2992.2313 | 2992.1665 | 3013.8149 | 3037.5617 | 3086.2637 | 3121.253 | 3140.2756 | 3161.1146 | 3180.1572 | 3214.4928 | 3257.0869 | 3254.2082 | 3254.2082 | 3254.2082 | 3254.2082 | 3254.2082 | 3254.2082 | 3254.2082 | 3254.2082 | 3254.2082 | 3254.2082 | 3254.2082 | 3254.2082 | 3254.2082 | 3254.2082 | 3254.2082 | 3254.2082 |  | 4963.476 | 6429.8794 | 6813.862 | 6791.0255 | 6792.9426 | 6832.4748 | 6936.5483 | 7006.3283 | 7074.5816 | 7154.3833 | 7228.4039 | 7300.2086 | 7308.5272 | 7392.3112 | 7329.0359 | 7329.0359 | 7329.0359 | 7329.0359 | 7329.0359 | 7329.0359 | 7329.0359 | 7329.0359 | 7329.0359 | 7329.0359 | 7329.0359 | 7329.0359 | 7329.0359 | 7329.0359 | 7329.0359 | 7329.0359
20% | 1280.3284 | 1701.2729 | 1815.9359 | 1812.6548 | 1812.6155 | 1825.7299 | 1840.1154 | 1869.6184 | 1890.8145 | 1902.3381 | 1914.9621 | 1926.4978 | 1947.2979 | 1973.1009 | 1971.357 | 1971.357 | 1971.357 | 1971.357 | 1971.357 | 1971.357 | 1971.357 | 1971.357 | 1971.357 | 1971.357 | 1971.357 | 1971.357 | 1971.357 | 1971.357 | 1971.357 | 1971.357 |  | 1331.912 | 1725.4105 | 1828.4494 | 1822.3214 | 1822.8358 | 1833.444 | 1861.3713 | 1880.0963 | 1898.4115 | 1919.8257 | 1939.6886 | 1958.9569 | 1961.1891 | 1983.6719 | 1966.6925 | 1966.6925 | 1966.6925 | 1966.6925 | 1966.6925 | 1966.6925 | 1966.6925 | 1966.6925 | 1966.6925 | 1966.6925 | 1966.6925 | 1966.6925 | 1966.6925 | 1966.6925 | 1966.6925 | 1966.6925
15% | 819.7224 | 1089.2296 | 1162.6419 | 1160.5412 | 1160.516 | 1168.9124 | 1178.1226 | 1197.0118 | 1210.5824 | 1217.9604 | 1226.0428 | 1233.4285 | 1246.7456 | 1263.2658 | 1262.1493 | 1262.1493 | 1262.1493 | 1262.1493 | 1262.1493 | 1262.1493 | 1262.1493 | 1262.1493 | 1262.1493 | 1262.1493 | 1262.1493 | 1262.1493 | 1262.1493 | 1262.1493 | 1262.1493 | 1262.1493 |  | 734.6312 | 951.6698 | 1008.502 | 1005.1221 | 1005.4058 | 1011.2569 | 1026.6605 | 1036.9885 | 1047.0905 | 1058.9017 | 1069.8573 | 1080.4849 | 1081.7162 | 1094.1168 | 1084.7516 | 1084.7516 | 1084.7516 | 1084.7516 | 1084.7516 | 1084.7516 | 1084.7516 | 1084.7516 | 1084.7516 | 1084.7516 | 1084.7516 | 1084.7516 | 1084.7516 | 1084.7516 | 1084.7516 | 1084.7516
10% | 548.6502 | 729.0346 | 778.1704 | 776.7643 | 776.7475 | 782.3673 | 788.5318 | 801.1745 | 810.2575 | 815.1957 | 820.6054 | 825.5487 | 834.462 | 845.5192 | 844.7719 | 844.7719 | 844.7719 | 844.7719 | 844.7719 | 844.7719 | 844.7719 | 844.7719 | 844.7719 | 844.7719 | 844.7719 | 844.7719 | 844.7719 | 844.7719 | 844.7719 | 844.7719 |  | 171.688 | 222.4113 | 235.6934 | 234.9034 | 234.9698 | 236.3372 | 239.9371 | 242.3508 | 244.7117 | 247.4721 | 250.0325 | 252.5162 | 252.804 | 255.7021 | 253.5134 | 253.5134 | 253.5134 | 253.5134 | 253.5134 | 253.5134 | 253.5134 | 253.5134 | 253.5134 | 253.5134 | 253.5134 | 253.5134 | 253.5134 | 253.5134 | 253.5134 | 253.5134
5% | 390.344 | 518.6808 | 553.639 | 552.6387 | 552.6267 | 556.625 | 561.0108 | 570.0056 | 576.4678 | 579.9811 | 583.8299 | 587.3469 | 593.6884 | 601.5551 | 601.0235 | 601.0235 | 601.0235 | 601.0235 | 601.0235 | 601.0235 | 601.0235 | 601.0235 | 601.0235 | 601.0235 | 601.0235 | 601.0235 | 601.0235 | 601.0235 | 601.0235 | 601.0235 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9.992e-14% | 34.2635 | 45.5286 | 48.5972 | 48.5094 | 48.5083 | 48.8593 | 49.2443 | 50.0338 | 50.6011 | 50.9095 | 51.2473 | 51.556 | 52.1126 | 52.8032 | 52.7565 | 52.7565 | 52.7565 | 52.7565 | 52.7565 | 52.7565 | 52.7565 | 52.7565 | 52.7565 | 52.7565 | 52.7565 | 52.7565 | 52.7565 | 52.7565 | 52.7565 | 52.7565 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E @ R (MWh) | 91763.8061 | 121933.7811 | 130151.918 | 129916.7517 | 129913.938 | 130853.8682 | 131884.9083 | 133999.4516 | 135518.6175 | 136344.5424 | 137249.3282 | 138076.12 | 139566.9035 | 141416.2562 | 141291.2697 | 141291.2697 | 141291.2697 | 141291.2697 | 141291.2697 | 141291.2697 | 141291.2697 | 141291.2697 | 141291.2697 | 141291.2697 | 141291.2697 | 141291.2697 | 141291.2697 | 141291.2697 | 141291.2697 | 141291.2697 | E @ R (MWh) | 89067.5772 | 115381.5956 | 122272.0083 | 121862.2159 | 121896.6185 | 122606.0074 | 124473.5651 | 125725.7387 | 126950.5164 | 128382.5252 | 129710.7955 | 130999.3026 | 131148.5764 | 132652.0463 | 131516.5966 | 131516.5966 | 131516.5966 | 131516.5966 | 131516.5966 | 131516.5966 | 131516.5966 | 131516.5966 | 131516.5966 | 131516.5966 | 131516.5966 | 131516.5966 | 131516.5966 | 131516.5966 | 131516.5966 | 131516.5966
Option 7 Summer POE50 W E @ R (MWh) N 2 | 64234.6643 | 85353.6468 | 91106.3426 | 90941.7262 | 90939.7566 | 91597.7077 | 92319.4358 | 93799.6161 | 94863.0323 | 95441.1797 | 96074.5298 | 96653.284 | 97696.8324 | 98991.3793 | 98903.8888 | 98903.8888 | 98903.8888 | 98903.8888 | 98903.8888 | 98903.8888 | 98903.8888 | 98903.8888 | 98903.8888 | 98903.8888 | 98903.8888 | 98903.8888 | 98903.8888 | 98903.8888 | 98903.8888 | 98903.8888 | Option 7 Summer POE10 W E @ R (MWh) N 2 | 26720.2732 | 34614.4787 | 36681.6025 | 36558.6648 | 36568.9855 | 36781.8022 | 37342.0695 | 37717.7216 | 38085.1549 | 38514.7576 | 38913.2387 | 39299.7908 | 39344.5729 | 39795.6139 | 39454.979 | 39454.979 | 39454.979 | 39454.979 | 39454.979 | 39454.979 | 39454.979 | 39454.979 | 39454.979 | 39454.979 | 39454.979 | 39454.979 | 39454.979 | 39454.979 | 39454.979 | 39454.979
Option 8 -
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | 59.6718 | 82.8348 | 88.8563 | 89.8828 | 90.6833 | 92.0616 | 95.1975 | 97.2967 | 99.9559 | 101.3362 | 102.5505 | 100.3131 | 102.9353 | 107.0576 | 103.9293 | 103.9293 | 103.9293 | 103.9293 | 103.9293 | 103.9293 | 103.9293 | 103.9293 | 103.9293 | 103.9293 | 103.9293 | 103.9293 | 103.9293 | 103.9293 | 103.9293 | 103.9293 |  | 63.8857 | 86.7566 | 93.0131 | 93.9812 | 94.5959 | 95.9444 | 99.1293 | 100.8681 | 104.1807 | 114.2499 | 105.9488 | 104.3251 | 106.5169 | 111.3103 | 108.0657 | 108.0657 | 108.0657 | 108.0657 | 108.0657 | 108.0657 | 108.0657 | 108.0657 | 108.0657 | 108.0657 | 108.0657 | 108.0657 | 108.0657 | 108.0657 | 108.0657 | 108.0657
98% | 70.8865 | 98.4027 | 105.556 | 106.7753 | 107.7263 | 109.3637 | 113.0889 | 115.5826 | 118.7416 | 120.3813 | 121.8238 | 119.1659 | 122.2809 | 127.178 | 123.4618 | 123.4618 | 123.4618 | 123.4618 | 123.4618 | 123.4618 | 123.4618 | 123.4618 | 123.4618 | 123.4618 | 123.4618 | 123.4618 | 123.4618 | 123.4618 | 123.4618 | 123.4618 |  | 75.8924 | 103.0616 | 110.494 | 111.644 | 112.3742 | 113.9761 | 117.7596 | 119.8253 | 123.7603 | 135.7219 | 125.8608 | 123.932 | 126.5357 | 132.2299 | 128.3755 | 128.3755 | 128.3755 | 128.3755 | 128.3755 | 128.3755 | 128.3755 | 128.3755 | 128.3755 | 128.3755 | 128.3755 | 128.3755 | 128.3755 | 128.3755 | 128.3755 | 128.3755
97% | 140.3338 | 194.8074 | 208.9687 | 211.3826 | 213.2652 | 216.5068 | 223.8816 | 228.8183 | 235.0721 | 238.3182 | 241.174 | 235.9121 | 242.0789 | 251.7738 | 244.4167 | 244.4167 | 244.4167 | 244.4167 | 244.4167 | 244.4167 | 244.4167 | 244.4167 | 244.4167 | 244.4167 | 244.4167 | 244.4167 | 244.4167 | 244.4167 | 244.4167 | 244.4167 |  | 150.2438 | 204.0305 | 218.7445 | 221.0211 | 222.4667 | 225.638 | 233.1281 | 237.2175 | 245.0078 | 268.6881 | 249.1661 | 245.3476 | 250.5021 | 261.7749 | 254.1445 | 254.1445 | 254.1445 | 254.1445 | 254.1445 | 254.1445 | 254.1445 | 254.1445 | 254.1445 | 254.1445 | 254.1445 | 254.1445 | 254.1445 | 254.1445 | 254.1445 | 254.1445
95% | 414.5243 | 575.4311 | 617.2612 | 624.3915 | 629.9527 | 639.5277 | 661.3119 | 675.8939 | 694.3669 | 703.9554 | 712.391 | 696.8482 | 715.0638 | 743.7009 | 721.9694 | 721.9694 | 721.9694 | 721.9694 | 721.9694 | 721.9694 | 721.9694 | 721.9694 | 721.9694 | 721.9694 | 721.9694 | 721.9694 | 721.9694 | 721.9694 | 721.9694 | 721.9694 |  | 443.7972 | 602.6746 | 646.1375 | 652.8624 | 657.1324 | 666.4999 | 688.6245 | 700.704 | 723.7153 | 793.6633 | 735.9983 | 724.719 | 739.9446 | 773.2427 | 750.7037 | 750.7037 | 750.7037 | 750.7037 | 750.7037 | 750.7037 | 750.7037 | 750.7037 | 750.7037 | 750.7037 | 750.7037 | 750.7037 | 750.7037 | 750.7037 | 750.7037 | 750.7037
90% | 2285.5212 | 3172.6969 | 3403.3313 | 3442.6449 | 3473.3067 | 3526.0998 | 3646.209 | 3726.6085 | 3828.4608 | 3881.3281 | 3927.8385 | 3842.1418 | 3942.5756 | 4100.4692 | 3980.6499 | 3980.6499 | 3980.6499 | 3980.6499 | 3980.6499 | 3980.6499 | 3980.6499 | 3980.6499 | 3980.6499 | 3980.6499 | 3980.6499 | 3980.6499 | 3980.6499 | 3980.6499 | 3980.6499 | 3980.6499 |  | 2446.9201 | 3322.9067 | 3562.5435 | 3599.622 | 3623.165 | 3674.8134 | 3796.7998 | 3863.4014 | 3990.2765 | 4375.9415 | 4058 | 3995.8103 | 4079.7583 | 4263.3504 | 4139.0795 | 4139.0795 | 4139.0795 | 4139.0795 | 4139.0795 | 4139.0795 | 4139.0795 | 4139.0795 | 4139.0795 | 4139.0795 | 4139.0795 | 4139.0795 | 4139.0795 | 4139.0795 | 4139.0795 | 4139.0795
85% | 5583.3646 | 7750.6712 | 8314.0946 | 8410.1348 | 8485.0395 | 8614.0092 | 8907.4274 | 9103.8375 | 9352.6555 | 9481.8066 | 9595.4282 | 9386.0773 | 9631.4298 | 10017.1525 | 9724.4425 | 9724.4425 | 9724.4425 | 9724.4425 | 9724.4425 | 9724.4425 | 9724.4425 | 9724.4425 | 9724.4425 | 9724.4425 | 9724.4425 | 9724.4425 | 9724.4425 | 9724.4425 | 9724.4425 | 9724.4425 |  | 5977.6505 | 8117.623 | 8703.0385 | 8793.6186 | 8851.1326 | 8977.3059 | 9275.3098 | 9438.0128 | 9747.9596 | 10690.1116 | 9913.4032 | 9761.4782 | 9966.5573 | 10415.0597 | 10111.4747 | 10111.4747 | 10111.4747 | 10111.4747 | 10111.4747 | 10111.4747 | 10111.4747 | 10111.4747 | 10111.4747 | 10111.4747 | 10111.4747 | 10111.4747 | 10111.4747 | 10111.4747 | 10111.4747 | 10111.4747
80% | 8678.2039 | 12046.8408 | 12922.5678 | 13071.8427 | 13188.2668 | 13388.724 | 13844.7828 | 14150.0624 | 14536.7992 | 14737.5384 | 14914.14 | 14588.7467 | 14970.0973 | 15569.6246 | 15114.6665 | 15114.6665 | 15114.6665 | 15114.6665 | 15114.6665 | 15114.6665 | 15114.6665 | 15114.6665 | 15114.6665 | 15114.6665 | 15114.6665 | 15114.6665 | 15114.6665 | 15114.6665 | 15114.6665 | 15114.6665 |  | 9291.041 | 12617.1926 | 13527.1019 | 13667.8902 | 13757.2841 | 13953.3947 | 14416.5812 | 14669.4699 | 15151.219 | 16615.6026 | 15408.3675 | 15172.231 | 15490.9847 | 16188.0904 | 15716.2292 | 15716.2292 | 15716.2292 | 15716.2292 | 15716.2292 | 15716.2292 | 15716.2292 | 15716.2292 | 15716.2292 | 15716.2292 | 15716.2292 | 15716.2292 | 15716.2292 | 15716.2292 | 15716.2292 | 15716.2292
75% | 9574.4808 | 13291.0275 | 14257.1987 | 14421.8907 | 14550.339 | 14771.4991 | 15274.6593 | 15611.4679 | 16038.1465 | 16259.6179 | 16454.4587 | 16095.4591 | 16516.1952 | 17177.6412 | 16675.6955 | 16675.6955 | 16675.6955 | 16675.6955 | 16675.6955 | 16675.6955 | 16675.6955 | 16675.6955 | 16675.6955 | 16675.6955 | 16675.6955 | 16675.6955 | 16675.6955 | 16675.6955 | 16675.6955 | 16675.6955 |  | 10250.6112 | 13920.2847 | 14924.1686 | 15079.4974 | 15178.1238 | 15394.4886 | 15905.5125 | 16184.5193 | 16716.023 | 18331.6468 | 16999.7296 | 16739.2052 | 17090.8794 | 17859.9816 | 17339.387 | 17339.387 | 17339.387 | 17339.387 | 17339.387 | 17339.387 | 17339.387 | 17339.387 | 17339.387 | 17339.387 | 17339.387 | 17339.387 | 17339.387 | 17339.387 | 17339.387 | 17339.387
70% | 10287.2444 | 14280.4661 | 15318.563 | 15495.5153 | 15633.5258 | 15871.15 | 16411.7675 | 16773.6495 | 17232.0919 | 17470.0505 | 17679.396 | 17293.671 | 17745.7284 | 18456.4151 | 17917.1025 | 17917.1025 | 17917.1025 | 17917.1025 | 17917.1025 | 17917.1025 | 17917.1025 | 17917.1025 | 17917.1025 | 17917.1025 | 17917.1025 | 17917.1025 | 17917.1025 | 17917.1025 | 17917.1025 | 17917.1025 |  | 11013.7087 | 14956.5677 | 16035.1849 | 16202.077 | 16308.0455 | 16540.5174 | 17089.584 | 17389.3613 | 17960.4323 | 19696.3297 | 18265.2591 | 17985.3402 | 18363.1944 | 19189.5518 | 18630.202 | 18630.202 | 18630.202 | 18630.202 | 18630.202 | 18630.202 | 18630.202 | 18630.202 | 18630.202 | 18630.202 | 18630.202 | 18630.202 | 18630.202 | 18630.202 | 18630.202 | 18630.202
65% | 10840.7831 | 15048.8731 | 16142.8282 | 16329.302 | 16474.7386 | 16725.149 | 17294.8562 | 17676.2104 | 18159.3208 | 18410.0835 | 18630.6936 | 18224.2134 | 18700.5952 | 19449.5227 | 18881.1907 | 18881.1907 | 18881.1907 | 18881.1907 | 18881.1907 | 18881.1907 | 18881.1907 | 18881.1907 | 18881.1907 | 18881.1907 | 18881.1907 | 18881.1907 | 18881.1907 | 18881.1907 | 18881.1907 | 18881.1907 |  | 11606.3372 | 15761.3546 | 16898.0103 | 17073.8826 | 17185.553 | 17430.5339 | 18009.1448 | 18325.0525 | 18926.8519 | 20756.155 | 19248.0809 | 18953.1 | 19351.286 | 20222.1082 | 19632.6608 | 19632.6608 | 19632.6608 | 19632.6608 | 19632.6608 | 19632.6608 | 19632.6608 | 19632.6608 | 19632.6608 | 19632.6608 | 19632.6608 | 19632.6608 | 19632.6608 | 19632.6608 | 19632.6608 | 19632.6608
60% | 11934.3669 | 16566.9557 | 17771.2656 | 17976.5503 | 18136.658 | 18412.329 | 19039.5064 | 19459.3305 | 19991.1755 | 20267.2344 | 20510.0989 | 20062.6142 | 20587.052 | 21411.5289 | 20785.8653 | 20785.8653 | 20785.8653 | 20785.8653 | 20785.8653 | 20785.8653 | 20785.8653 | 20785.8653 | 20785.8653 | 20785.8653 | 20785.8653 | 20785.8653 | 20785.8653 | 20785.8653 | 20785.8653 | 20785.8653 |  | 12777.1477 | 17351.3101 | 18602.628 | 18796.2417 | 18919.1771 | 19188.8708 | 19825.8502 | 20173.6257 | 20836.1327 | 22849.9701 | 21189.7663 | 20865.0287 | 21303.3824 | 22262.0503 | 21613.1413 | 21613.1413 | 21613.1413 | 21613.1413 | 21613.1413 | 21613.1413 | 21613.1413 | 21613.1413 | 21613.1413 | 21613.1413 | 21613.1413 | 21613.1413 | 21613.1413 | 21613.1413 | 21613.1413 | 21613.1413
55% | 13276.2336 | 18429.6976 | 19769.4166 | 19997.783 | 20175.8928 | 20482.5595 | 21180.255 | 21647.2828 | 22238.927 | 22546.0252 | 22816.1967 | 22318.3981 | 22901.8021 | 23818.981 | 23122.9695 | 23122.9695 | 23122.9695 | 23122.9695 | 23122.9695 | 23122.9695 | 23122.9695 | 23122.9695 | 23122.9695 | 23122.9695 | 23122.9695 | 23122.9695 | 23122.9695 | 23122.9695 | 23122.9695 | 23122.9695 |  | 14213.7742 | 19302.2426 | 20694.2551 | 20909.6382 | 21046.3962 | 21346.4135 | 22055.013 | 22441.8914 | 23178.8888 | 25419.1564 | 23572.284 | 23211.0338 | 23698.6747 | 24765.1326 | 24043.2621 | 24043.2621 | 24043.2621 | 24043.2621 | 24043.2621 | 24043.2621 | 24043.2621 | 24043.2621 | 24043.2621 | 24043.2621 | 24043.2621 | 24043.2621 | 24043.2621 | 24043.2621 | 24043.2621 | 24043.2621
50% | 13456.7484 | 18680.2832 | 20038.2182 | 20269.6896 | 20450.2212 | 20761.0575 | 21468.2395 | 21941.6174 | 22541.3061 | 22852.5798 | 23126.4248 | 22621.8577 | 23213.1942 | 24142.8438 | 23437.3688 | 23437.3688 | 23437.3688 | 23437.3688 | 23437.3688 | 23437.3688 | 23437.3688 | 23437.3688 | 23437.3688 | 23437.3688 | 23437.3688 | 23437.3688 | 23437.3688 | 23437.3688 | 23437.3688 | 23437.3688 |  | 14407.0366 | 19564.692 | 20975.6315 | 21193.9432 | 21332.5606 | 21636.6572 | 22354.8915 | 22747.0302 | 23494.0484 | 25764.7766 | 23892.7925 | 23526.6304 | 24020.9018 | 25101.8601 | 24370.1745 | 24370.1745 | 24370.1745 | 24370.1745 | 24370.1745 | 24370.1745 | 24370.1745 | 24370.1745 | 24370.1745 | 24370.1745 | 24370.1745 | 24370.1745 | 24370.1745 | 24370.1745 | 24370.1745 | 24370.1745
45% | 10386.1977 | 14417.8303 | 15465.9127 | 15644.5671 | 15783.9051 | 16023.8151 | 16569.6328 | 16934.9957 | 17397.8478 | 17638.0954 | 17849.4547 | 17460.0193 | 17916.4251 | 18633.9479 | 18089.4477 | 18089.4477 | 18089.4477 | 18089.4477 | 18089.4477 | 18089.4477 | 18089.4477 | 18089.4477 | 18089.4477 | 18089.4477 | 18089.4477 | 18089.4477 | 18089.4477 | 18089.4477 | 18089.4477 | 18089.4477 |  | 11119.6499 | 15100.4354 | 16189.4278 | 16357.9252 | 16464.913 | 16699.6211 | 17253.9692 | 17556.63 | 18133.1942 | 19885.7893 | 18440.9531 | 18158.3417 | 18539.8305 | 19374.1366 | 18809.4064 | 18809.4064 | 18809.4064 | 18809.4064 | 18809.4064 | 18809.4064 | 18809.4064 | 18809.4064 | 18809.4064 | 18809.4064 | 18809.4064 | 18809.4064 | 18809.4064 | 18809.4064 | 18809.4064 | 18809.4064
40% | 5102.6915 | 7083.4142 | 7598.3323 | 7686.1044 | 7754.5606 | 7872.4272 | 8140.5849 | 8320.0861 | 8547.4832 | 8665.5158 | 8769.3556 | 8578.0278 | 8802.2579 | 9154.7736 | 8887.2631 | 8887.2631 | 8887.2631 | 8887.2631 | 8887.2631 | 8887.2631 | 8887.2631 | 8887.2631 | 8887.2631 | 8887.2631 | 8887.2631 | 8887.2631 | 8887.2631 | 8887.2631 | 8887.2631 | 8887.2631 |  | 5463.0332 | 7418.775 | 7953.792 | 8036.574 | 8089.1366 | 8204.4476 | 8476.7963 | 8625.4922 | 8908.7555 | 9769.7975 | 9059.9561 | 8921.1104 | 9108.5341 | 9518.4249 | 9240.9755 | 9240.9755 | 9240.9755 | 9240.9755 | 9240.9755 | 9240.9755 | 9240.9755 | 9240.9755 | 9240.9755 | 9240.9755 | 9240.9755 | 9240.9755 | 9240.9755 | 9240.9755 | 9240.9755 | 9240.9755
35% | 1907.0998 | 2647.3829 | 2839.8304 | 2872.6347 | 2898.2197 | 2942.2717 | 3042.494 | 3109.5815 | 3194.5697 | 3238.6837 | 3277.4932 | 3205.9856 | 3289.7902 | 3421.5408 | 3321.5604 | 3321.5604 | 3321.5604 | 3321.5604 | 3321.5604 | 3321.5604 | 3321.5604 | 3321.5604 | 3321.5604 | 3321.5604 | 3321.5604 | 3321.5604 | 3321.5604 | 3321.5604 | 3321.5604 | 3321.5604 |  | 2041.7754 | 2772.7219 | 2972.6813 | 3003.6205 | 3023.2655 | 3066.3623 | 3168.1509 | 3223.7251 | 3329.5931 | 3651.4023 | 3386.1034 | 3334.2106 | 3404.2591 | 3557.4533 | 3453.7583 | 3453.7583 | 3453.7583 | 3453.7583 | 3453.7583 | 3453.7583 | 3453.7583 | 3453.7583 | 3453.7583 | 3453.7583 | 3453.7583 | 3453.7583 | 3453.7583 | 3453.7583 | 3453.7583 | 3453.7583
30% | 951.1511 | 1320.3614 | 1416.3431 | 1432.704 | 1445.4643 | 1467.4349 | 1517.42 | 1550.8793 | 1593.2665 | 1615.268 | 1634.624 | 1598.9601 | 1640.757 | 1706.4666 | 1656.6021 | 1656.6021 | 1656.6021 | 1656.6021 | 1656.6021 | 1656.6021 | 1656.6021 | 1656.6021 | 1656.6021 | 1656.6021 | 1656.6021 | 1656.6021 | 1656.6021 | 1656.6021 | 1656.6021 | 1656.6021 |  | 1018.3194 | 1382.8733 | 1482.6014 | 1498.0321 | 1507.8299 | 1529.3241 | 1580.0904 | 1607.8076 | 1660.6084 | 1821.1082 | 1688.7924 | 1662.9113 | 1697.8475 | 1774.2519 | 1722.5348 | 1722.5348 | 1722.5348 | 1722.5348 | 1722.5348 | 1722.5348 | 1722.5348 | 1722.5348 | 1722.5348 | 1722.5348 | 1722.5348 | 1722.5348 | 1722.5348 | 1722.5348 | 1722.5348 | 1722.5348
25% | 560.7353 | 778.3972 | 834.9816 | 844.6269 | 852.1495 | 865.1019 | 894.5698 | 914.2952 | 939.2839 | 952.2545 | 963.6655 | 942.6404 | 967.2811 | 1006.0191 | 976.6223 | 976.6223 | 976.6223 | 976.6223 | 976.6223 | 976.6223 | 976.6223 | 976.6223 | 976.6223 | 976.6223 | 976.6223 | 976.6223 | 976.6223 | 976.6223 | 976.6223 | 976.6223 |  | 600.3333 | 815.25 | 874.0431 | 883.14 | 888.9161 | 901.5876 | 931.5161 | 947.8563 | 978.9841 | 1073.6041 | 995.5996 | 980.3418 | 1000.9378 | 1045.9808 | 1015.4918 | 1015.4918 | 1015.4918 | 1015.4918 | 1015.4918 | 1015.4918 | 1015.4918 | 1015.4918 | 1015.4918 | 1015.4918 | 1015.4918 | 1015.4918 | 1015.4918 | 1015.4918 | 1015.4918 | 1015.4918
20% | 283.3663 | 393.3611 | 421.9559 | 426.8302 | 430.6317 | 437.1772 | 452.0687 | 462.0369 | 474.6648 | 481.2195 | 486.986 | 476.3611 | 488.8132 | 508.3893 | 493.5337 | 493.5337 | 493.5337 | 493.5337 | 493.5337 | 493.5337 | 493.5337 | 493.5337 | 493.5337 | 493.5337 | 493.5337 | 493.5337 | 493.5337 | 493.5337 | 493.5337 | 493.5337 |  | 303.377 | 411.9846 | 441.6956 | 446.2927 | 449.2116 | 455.6151 | 470.7394 | 478.9969 | 494.7273 | 542.5433 | 503.1238 | 495.4134 | 505.8215 | 528.5839 | 513.1763 | 513.1763 | 513.1763 | 513.1763 | 513.1763 | 513.1763 | 513.1763 | 513.1763 | 513.1763 | 513.1763 | 513.1763 | 513.1763 | 513.1763 | 513.1763 | 513.1763 | 513.1763
15% | 115.4455 | 160.2582 | 171.908 | 173.8938 | 175.4425 | 178.1092 | 184.1761 | 188.2372 | 193.382 | 196.0524 | 198.4017 | 194.073 | 199.1461 | 207.1216 | 201.0693 | 201.0693 | 201.0693 | 201.0693 | 201.0693 | 201.0693 | 201.0693 | 201.0693 | 201.0693 | 201.0693 | 201.0693 | 201.0693 | 201.0693 | 201.0693 | 201.0693 | 201.0693 |  | 123.598 | 167.8456 | 179.95 | 181.8229 | 183.0121 | 185.621 | 191.7827 | 195.1469 | 201.5556 | 221.0361 | 204.9764 | 201.8351 | 206.0754 | 215.349 | 209.0718 | 209.0718 | 209.0718 | 209.0718 | 209.0718 | 209.0718 | 209.0718 | 209.0718 | 209.0718 | 209.0718 | 209.0718 | 209.0718 | 209.0718 | 209.0718 | 209.0718 | 209.0718
10% | 46.4781 | 64.5196 | 69.2097 | 70.0092 | 70.6327 | 71.7063 | 74.1488 | 75.7838 | 77.8551 | 78.9302 | 79.876 | 78.1333 | 80.1757 | 83.3866 | 80.95 | 80.95 | 80.95 | 80.95 | 80.95 | 80.95 | 80.95 | 80.95 | 80.95 | 80.95 | 80.95 | 80.95 | 80.95 | 80.95 | 80.95 | 80.95 |  | 49.7602 | 67.5742 | 72.4474 | 73.2014 | 73.6802 | 74.7305 | 77.2112 | 78.5656 | 81.1457 | 88.9886 | 82.523 | 81.2583 | 82.9654 | 86.6989 | 84.1718 | 84.1718 | 84.1718 | 84.1718 | 84.1718 | 84.1718 | 84.1718 | 84.1718 | 84.1718 | 84.1718 | 84.1718 | 84.1718 | 84.1718 | 84.1718 | 84.1718 | 84.1718
5% | 39.5813 | 54.9457 | 58.9399 | 59.6207 | 60.1517 | 61.066 | 63.1461 | 64.5385 | 66.3024 | 67.218 | 68.0234 | 66.5393 | 68.2787 | 71.0131 | 68.938 | 68.938 | 68.938 | 68.938 | 68.938 | 68.938 | 68.938 | 68.938 | 68.938 | 68.938 | 68.938 | 68.938 | 68.938 | 68.938 | 68.938 | 68.938 |  | 42.3765 | 57.5471 | 61.6972 | 62.3393 | 62.747 | 63.6415 | 65.7541 | 66.9075 | 69.1048 | 75.7838 | 70.2776 | 69.2006 | 70.6544 | 73.8339 | 71.6818 | 71.6818 | 71.6818 | 71.6818 | 71.6818 | 71.6818 | 71.6818 | 71.6818 | 71.6818 | 71.6818 | 71.6818 | 71.6818 | 71.6818 | 71.6818 | 71.6818 | 71.6818
9.992e-14% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E @ R (MWh) | 105995.1099 | 147139.4588 | 157835.5397 | 159658.7762 | 161080.774 | 163529.1464 | 169099.4242 | 172828.0925 | 177551.675 | 180003.4929 | 182160.4948 | 178186.1586 | 182843.9537 | 190166.5478 | 184609.7151 | 184609.7151 | 184609.7151 | 184609.7151 | 184609.7151 | 184609.7151 | 184609.7151 | 184609.7151 | 184609.7151 | 184609.7151 | 184609.7151 | 184609.7151 | 184609.7151 | 184609.7151 | 184609.7151 | 184609.7151 | E @ R (MWh) | 113480.2695 | 154105.704 | 165219.287 | 166938.8679 | 168030.7193 | 170426.0046 | 176083.3386 | 179172.1077 | 185056.165 | 202942.0666 | 188196.9625 | 185312.8045 | 189206.044 | 197720.4561 | 191957.169 | 191957.169 | 191957.169 | 191957.169 | 191957.169 | 191957.169 | 191957.169 | 191957.169 | 191957.169 | 191957.169 | 191957.169 | 191957.169 | 191957.169 | 191957.169 | 191957.169 | 191957.169
Option 8 Winter POE50 W E @ R (MWh) N 2 | 74196.5769 | 102997.6211 | 110484.8778 | 111761.1434 | 112756.5418 | 114470.4025 | 118369.597 | 120979.6647 | 124286.1725 | 126002.4451 | 127512.3464 | 124730.311 | 127990.7676 | 133116.5835 | 129226.8005 | 129226.8005 | 129226.8005 | 129226.8005 | 129226.8005 | 129226.8005 | 129226.8005 | 129226.8005 | 129226.8005 | 129226.8005 | 129226.8005 | 129226.8005 | 129226.8005 | 129226.8005 | 129226.8005 | 129226.8005 | Option 8 Winter POE10 W E @ R (MWh) N 2 | 34044.0809 | 46231.7112 | 49565.7861 | 50081.6604 | 50409.2158 | 51127.8014 | 52825.0016 | 53751.6323 | 55516.8495 | 60882.62 | 56459.0887 | 55593.8414 | 56761.8132 | 59316.1368 | 57587.1507 | 57587.1507 | 57587.1507 | 57587.1507 | 57587.1507 | 57587.1507 | 57587.1507 | 57587.1507 | 57587.1507 | 57587.1507 | 57587.1507 | 57587.1507 | 57587.1507 | 57587.1507 | 57587.1507 | 57587.1507
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 76.9936 | 99.7405 | 105.6969 | 105.3426 | 105.3724 | 105.9856 | 107.6 | 108.6824 | 109.7411 | 110.979 | 112.1272 | 113.2411 | 113.3701 | 114.6698 | 113.6883 | 113.6883 | 113.6883 | 113.6883 | 113.6883 | 113.6883 | 113.6883 | 113.6883 | 113.6883 | 113.6883 | 113.6883 | 113.6883 | 113.6883 | 113.6883 | 113.6883 | 113.6883
98% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 38.1099 | 49.369 | 52.3173 | 52.1419 | 52.1567 | 52.4602 | 53.2593 | 53.7951 | 54.3191 | 54.9318 | 55.5002 | 56.0515 | 56.1154 | 56.7587 | 56.2728 | 56.2728 | 56.2728 | 56.2728 | 56.2728 | 56.2728 | 56.2728 | 56.2728 | 56.2728 | 56.2728 | 56.2728 | 56.2728 | 56.2728 | 56.2728 | 56.2728 | 56.2728
97% | 16.9149 | 22.4762 | 23.991 | 23.9477 | 23.9472 | 24.1204 | 24.3105 | 24.7002 | 24.9803 | 25.1325 | 25.2993 | 25.4517 | 25.7265 | 26.0674 | 26.0444 | 26.0444 | 26.0444 | 26.0444 | 26.0444 | 26.0444 | 26.0444 | 26.0444 | 26.0444 | 26.0444 | 26.0444 | 26.0444 | 26.0444 | 26.0444 | 26.0444 | 26.0444 |  | 75.446 | 97.7357 | 103.5723 | 103.2252 | 103.2543 | 103.8552 | 105.4372 | 106.4978 | 107.5353 | 108.7483 | 109.8734 | 110.9649 | 111.0913 | 112.3649 | 111.4031 | 111.4031 | 111.4031 | 111.4031 | 111.4031 | 111.4031 | 111.4031 | 111.4031 | 111.4031 | 111.4031 | 111.4031 | 111.4031 | 111.4031 | 111.4031 | 111.4031 | 111.4031
95% | 83.2734 | 110.6519 | 118.1097 | 117.8962 | 117.8937 | 118.7467 | 119.6823 | 121.6012 | 122.9798 | 123.7293 | 124.5504 | 125.3007 | 126.6535 | 128.3318 | 128.2183 | 128.2183 | 128.2183 | 128.2183 | 128.2183 | 128.2183 | 128.2183 | 128.2183 | 128.2183 | 128.2183 | 128.2183 | 128.2183 | 128.2183 | 128.2183 | 128.2183 | 128.2183 |  | 111.4279 | 144.3481 | 152.9683 | 152.4556 | 152.4987 | 153.3862 | 155.7226 | 157.2891 | 158.8214 | 160.6129 | 162.2746 | 163.8866 | 164.0733 | 165.9543 | 164.5337 | 164.5337 | 164.5337 | 164.5337 | 164.5337 | 164.5337 | 164.5337 | 164.5337 | 164.5337 | 164.5337 | 164.5337 | 164.5337 | 164.5337 | 164.5337 | 164.5337 | 164.5337
90% | 144.4273 | 191.9119 | 204.8464 | 204.4763 | 204.4719 | 205.9512 | 207.574 | 210.9021 | 213.2931 | 214.593 | 216.0171 | 217.3184 | 219.6647 | 222.5754 | 222.3787 | 222.3787 | 222.3787 | 222.3787 | 222.3787 | 222.3787 | 222.3787 | 222.3787 | 222.3787 | 222.3787 | 222.3787 | 222.3787 | 222.3787 | 222.3787 | 222.3787 | 222.3787 |  | 483.1446 | 625.8842 | 663.261 | 661.0381 | 661.2248 | 665.0728 | 675.2033 | 681.9957 | 688.6395 | 696.4074 | 703.6125 | 710.602 | 711.4117 | 719.5673 | 713.4081 | 713.4081 | 713.4081 | 713.4081 | 713.4081 | 713.4081 | 713.4081 | 713.4081 | 713.4081 | 713.4081 | 713.4081 | 713.4081 | 713.4081 | 713.4081 | 713.4081 | 713.4081
85% | 409.8612 | 544.6148 | 581.321 | 580.2706 | 580.258 | 584.4562 | 589.0613 | 598.5059 | 605.2912 | 608.9802 | 613.0214 | 616.7142 | 623.3728 | 631.6329 | 631.0746 | 631.0746 | 631.0746 | 631.0746 | 631.0746 | 631.0746 | 631.0746 | 631.0746 | 631.0746 | 631.0746 | 631.0746 | 631.0746 | 631.0746 | 631.0746 | 631.0746 | 631.0746 |  | 457.0286 | 592.0526 | 627.4091 | 625.3063 | 625.4829 | 629.1229 | 638.7059 | 645.1311 | 651.4157 | 658.7637 | 665.5794 | 672.1911 | 672.9571 | 680.6717 | 674.8455 | 674.8455 | 674.8455 | 674.8455 | 674.8455 | 674.8455 | 674.8455 | 674.8455 | 674.8455 | 674.8455 | 674.8455 | 674.8455 | 674.8455 | 674.8455 | 674.8455 | 674.8455
80% | 572.5046 | 760.7318 | 812.0039 | 810.5367 | 810.5191 | 816.3833 | 822.8158 | 836.0082 | 845.4861 | 850.639 | 856.2839 | 861.4421 | 870.743 | 882.2809 | 881.5011 | 881.5011 | 881.5011 | 881.5011 | 881.5011 | 881.5011 | 881.5011 | 881.5011 | 881.5011 | 881.5011 | 881.5011 | 881.5011 | 881.5011 | 881.5011 | 881.5011 | 881.5011 |  | 319.1946 | 413.4971 | 438.1905 | 436.7219 | 436.8452 | 439.3874 | 446.0803 | 450.5677 | 454.957 | 460.089 | 464.8491 | 469.4668 | 470.0018 | 475.3898 | 471.3206 | 471.3206 | 471.3206 | 471.3206 | 471.3206 | 471.3206 | 471.3206 | 471.3206 | 471.3206 | 471.3206 | 471.3206 | 471.3206 | 471.3206 | 471.3206 | 471.3206 | 471.3206
75% | 1492.4153 | 1983.0895 | 2116.7465 | 2112.9218 | 2112.876 | 2128.1627 | 2144.9312 | 2179.3214 | 2204.0286 | 2217.4612 | 2232.1763 | 2245.623 | 2269.8686 | 2299.9458 | 2297.9131 | 2297.9131 | 2297.9131 | 2297.9131 | 2297.9131 | 2297.9131 | 2297.9131 | 2297.9131 | 2297.9131 | 2297.9131 | 2297.9131 | 2297.9131 | 2297.9131 | 2297.9131 | 2297.9131 | 2297.9131 |  | 569.714 | 738.0296 | 782.1036 | 779.4824 | 779.7025 | 784.24 | 796.1857 | 804.1951 | 812.0293 | 821.1891 | 829.6853 | 837.9271 | 838.8819 | 848.4987 | 841.2359 | 841.2359 | 841.2359 | 841.2359 | 841.2359 | 841.2359 | 841.2359 | 841.2359 | 841.2359 | 841.2359 | 841.2359 | 841.2359 | 841.2359 | 841.2359 | 841.2359 | 841.2359
70% | 2578.4391 | 3426.1747 | 3657.0932 | 3650.4854 | 3650.4063 | 3676.8171 | 3705.7879 | 3765.2037 | 3807.8902 | 3831.0976 | 3856.5209 | 3879.7526 | 3921.6416 | 3973.6059 | 3970.094 | 3970.094 | 3970.094 | 3970.094 | 3970.094 | 3970.094 | 3970.094 | 3970.094 | 3970.094 | 3970.094 | 3970.094 | 3970.094 | 3970.094 | 3970.094 | 3970.094 | 3970.094 |  | 1037.8661 | 1344.492 | 1424.783 | 1420.0079 | 1420.4087 | 1428.6749 | 1450.4368 | 1465.0278 | 1479.2996 | 1495.9862 | 1511.464 | 1526.4784 | 1528.2178 | 1545.7371 | 1532.5062 | 1532.5062 | 1532.5062 | 1532.5062 | 1532.5062 | 1532.5062 | 1532.5062 | 1532.5062 | 1532.5062 | 1532.5062 | 1532.5062 | 1532.5062 | 1532.5062 | 1532.5062 | 1532.5062 | 1532.5062
65% | 6475.8072 | 8604.914 | 9184.8711 | 9168.2753 | 9168.0768 | 9234.408 | 9307.1689 | 9456.393 | 9563.6012 | 9621.887 | 9685.7381 | 9744.0851 | 9849.2903 | 9979.7998 | 9970.9794 | 9970.9794 | 9970.9794 | 9970.9794 | 9970.9794 | 9970.9794 | 9970.9794 | 9970.9794 | 9970.9794 | 9970.9794 | 9970.9794 | 9970.9794 | 9970.9794 | 9970.9794 | 9970.9794 | 9970.9794 |  | 1305.7961 | 1691.5789 | 1792.5974 | 1786.5896 | 1787.0939 | 1797.4941 | 1824.8739 | 1843.2317 | 1861.1878 | 1882.1821 | 1901.6555 | 1920.546 | 1922.7344 | 1944.7764 | 1928.1299 | 1928.1299 | 1928.1299 | 1928.1299 | 1928.1299 | 1928.1299 | 1928.1299 | 1928.1299 | 1928.1299 | 1928.1299 | 1928.1299 | 1928.1299 | 1928.1299 | 1928.1299 | 1928.1299 | 1928.1299
60% | 9465.8424 | 12578.0087 | 13425.7459 | 13401.4874 | 13401.1972 | 13498.1551 | 13604.5115 | 13822.636 | 13979.3447 | 14064.5425 | 14157.8751 | 14243.1624 | 14396.9433 | 14587.7122 | 14574.8193 | 14574.8193 | 14574.8193 | 14574.8193 | 14574.8193 | 14574.8193 | 14574.8193 | 14574.8193 | 14574.8193 | 14574.8193 | 14574.8193 | 14574.8193 | 14574.8193 | 14574.8193 | 14574.8193 | 14574.8193 |  | 2043.3291 | 2647.0078 | 2805.083 | 2795.6818 | 2796.4711 | 2812.7454 | 2855.5897 | 2884.3162 | 2912.4142 | 2945.2664 | 2975.7387 | 3005.2988 | 3008.7233 | 3043.2149 | 3017.1662 | 3017.1662 | 3017.1662 | 3017.1662 | 3017.1662 | 3017.1662 | 3017.1662 | 3017.1662 | 3017.1662 | 3017.1662 | 3017.1662 | 3017.1662 | 3017.1662 | 3017.1662 | 3017.1662 | 3017.1662
55% | 10703.6666 | 14222.8031 | 15181.3967 | 15153.966 | 15153.6378 | 15263.2747 | 15383.539 | 15630.1871 | 15807.3882 | 15903.7271 | 16009.2646 | 16105.7046 | 16279.5951 | 16495.3104 | 16480.7315 | 16480.7315 | 16480.7315 | 16480.7315 | 16480.7315 | 16480.7315 | 16480.7315 | 16480.7315 | 16480.7315 | 16480.7315 | 16480.7315 | 16480.7315 | 16480.7315 | 16480.7315 | 16480.7315 | 16480.7315 |  | 3926.5772 | 5086.6405 | 5390.4069 | 5372.341 | 5373.8577 | 5405.1313 | 5487.4633 | 5542.6658 | 5596.6606 | 5659.7913 | 5718.3486 | 5775.1529 | 5781.7337 | 5848.0147 | 5797.958 | 5797.958 | 5797.958 | 5797.958 | 5797.958 | 5797.958 | 5797.958 | 5797.958 | 5797.958 | 5797.958 | 5797.958 | 5797.958 | 5797.958 | 5797.958 | 5797.958 | 5797.958
50% | 13744.0128 | 18262.75 | 19493.6294 | 19458.4071 | 19457.9857 | 19598.7646 | 19753.1897 | 20069.8975 | 20297.432 | 20421.1357 | 20556.6509 | 20680.4844 | 20903.7679 | 21180.7565 | 21162.0366 | 21162.0366 | 21162.0366 | 21162.0366 | 21162.0366 | 21162.0366 | 21162.0366 | 21162.0366 | 21162.0366 | 21162.0366 | 21162.0366 | 21162.0366 | 21162.0366 | 21162.0366 | 21162.0366 | 21162.0366 |  | 8714.0125 | 11288.47 | 11962.6002 | 11922.5077 | 11925.8735 | 11995.2773 | 12177.9916 | 12300.4992 | 12420.3265 | 12560.4285 | 12690.3811 | 12816.4434 | 12831.0478 | 12978.1412 | 12867.0534 | 12867.0534 | 12867.0534 | 12867.0534 | 12867.0534 | 12867.0534 | 12867.0534 | 12867.0534 | 12867.0534 | 12867.0534 | 12867.0534 | 12867.0534 | 12867.0534 | 12867.0534 | 12867.0534 | 12867.0534
45% | 18302.3635 | 24319.7888 | 25958.9027 | 25911.9985 | 25911.4373 | 26098.9072 | 26304.5489 | 26726.2963 | 27029.2951 | 27194.0265 | 27374.4867 | 27539.391 | 27836.7289 | 28205.5838 | 28180.6551 | 28180.6551 | 28180.6551 | 28180.6551 | 28180.6551 | 28180.6551 | 28180.6551 | 28180.6551 | 28180.6551 | 28180.6551 | 28180.6551 | 28180.6551 | 28180.6551 | 28180.6551 | 28180.6551 | 28180.6551 |  | 13204.5002 | 17105.6219 | 18127.1435 | 18066.3908 | 18071.491 | 18176.6598 | 18453.5301 | 18639.1681 | 18820.7445 | 19033.0436 | 19229.9631 | 19420.9876 | 19443.1179 | 19666.0112 | 19497.6778 | 19497.6778 | 19497.6778 | 19497.6778 | 19497.6778 | 19497.6778 | 19497.6778 | 19497.6778 | 19497.6778 | 19497.6778 | 19497.6778 | 19497.6778 | 19497.6778 | 19497.6778 | 19497.6778 | 19497.6778
40% | 12836.6798 | 17057.1053 | 18206.7263 | 18173.8293 | 18173.4357 | 18304.9209 | 18449.1513 | 18744.9511 | 18957.4646 | 19073.0018 | 19199.5707 | 19315.2292 | 19523.7723 | 19782.475 | 19764.9909 | 19764.9909 | 19764.9909 | 19764.9909 | 19764.9909 | 19764.9909 | 19764.9909 | 19764.9909 | 19764.9909 | 19764.9909 | 19764.9909 | 19764.9909 | 19764.9909 | 19764.9909 | 19764.9909 | 19764.9909 |  | 13672.6523 | 17712.0843 | 18769.8229 | 18706.9162 | 18712.1973 | 18821.0947 | 19107.7811 | 19300.0008 | 19488.0148 | 19707.8407 | 19911.7418 | 20109.5389 | 20132.4538 | 20363.2496 | 20188.9481 | 20188.9481 | 20188.9481 | 20188.9481 | 20188.9481 | 20188.9481 | 20188.9481 | 20188.9481 | 20188.9481 | 20188.9481 | 20188.9481 | 20188.9481 | 20188.9481 | 20188.9481 | 20188.9481 | 20188.9481
35% | 6655.3655 | 8843.5072 | 9439.545 | 9422.4891 | 9422.285 | 9490.4555 | 9565.2339 | 9718.5956 | 9828.7764 | 9888.6783 | 9954.2998 | 10014.2647 | 10122.3869 | 10256.5152 | 10247.4502 | 10247.4502 | 10247.4502 | 10247.4502 | 10247.4502 | 10247.4502 | 10247.4502 | 10247.4502 | 10247.4502 | 10247.4502 | 10247.4502 | 10247.4502 | 10247.4502 | 10247.4502 | 10247.4502 | 10247.4502 |  | 18622.1031 | 24123.7949 | 25564.4311 | 25478.7524 | 25485.9452 | 25634.2631 | 26024.729 | 26286.5314 | 26542.6059 | 26842.008 | 27119.7205 | 27389.1195 | 27420.3294 | 27734.6724 | 27497.2745 | 27497.2745 | 27497.2745 | 27497.2745 | 27497.2745 | 27497.2745 | 27497.2745 | 27497.2745 | 27497.2745 | 27497.2745 | 27497.2745 | 27497.2745 | 27497.2745 | 27497.2745 | 27497.2745 | 27497.2745
30% | 3095.428 | 4113.1385 | 4390.3573 | 4382.4246 | 4382.3296 | 4414.0359 | 4448.8155 | 4520.1445 | 4571.3898 | 4599.2504 | 4629.7711 | 4657.6609 | 4707.9489 | 4770.3323 | 4766.1162 | 4766.1162 | 4766.1162 | 4766.1162 | 4766.1162 | 4766.1162 | 4766.1162 | 4766.1162 | 4766.1162 | 4766.1162 | 4766.1162 | 4766.1162 | 4766.1162 | 4766.1162 | 4766.1162 | 4766.1162 |  | 17207.9743 | 22291.8776 | 23623.1145 | 23543.942 | 23550.5887 | 23687.6435 | 24048.4582 | 24290.3798 | 24527.0085 | 24803.6745 | 25060.2981 | 25309.2393 | 25338.0792 | 25628.5516 | 25409.1812 | 25409.1812 | 25409.1812 | 25409.1812 | 25409.1812 | 25409.1812 | 25409.1812 | 25409.1812 | 25409.1812 | 25409.1812 | 25409.1812 | 25409.1812 | 25409.1812 | 25409.1812 | 25409.1812 | 25409.1812
25% | 2113.496 | 2808.3682 | 2997.6476 | 2992.2313 | 2992.1665 | 3013.8149 | 3037.5617 | 3086.2637 | 3121.253 | 3140.2756 | 3161.1146 | 3180.1572 | 3214.4928 | 3257.0869 | 3254.2082 | 3254.2082 | 3254.2082 | 3254.2082 | 3254.2082 | 3254.2082 | 3254.2082 | 3254.2082 | 3254.2082 | 3254.2082 | 3254.2082 | 3254.2082 | 3254.2082 | 3254.2082 | 3254.2082 | 3254.2082 |  | 4963.476 | 6429.8794 | 6813.862 | 6791.0255 | 6792.9426 | 6832.4748 | 6936.5483 | 7006.3283 | 7074.5816 | 7154.3833 | 7228.4039 | 7300.2086 | 7308.5272 | 7392.3112 | 7329.0359 | 7329.0359 | 7329.0359 | 7329.0359 | 7329.0359 | 7329.0359 | 7329.0359 | 7329.0359 | 7329.0359 | 7329.0359 | 7329.0359 | 7329.0359 | 7329.0359 | 7329.0359 | 7329.0359 | 7329.0359
20% | 1280.3284 | 1701.2729 | 1815.9359 | 1812.6548 | 1812.6155 | 1825.7299 | 1840.1154 | 1869.6184 | 1890.8145 | 1902.3381 | 1914.9621 | 1926.4978 | 1947.2979 | 1973.1009 | 1971.357 | 1971.357 | 1971.357 | 1971.357 | 1971.357 | 1971.357 | 1971.357 | 1971.357 | 1971.357 | 1971.357 | 1971.357 | 1971.357 | 1971.357 | 1971.357 | 1971.357 | 1971.357 |  | 1331.912 | 1725.4105 | 1828.4494 | 1822.3214 | 1822.8358 | 1833.444 | 1861.3713 | 1880.0963 | 1898.4115 | 1919.8257 | 1939.6886 | 1958.9569 | 1961.1891 | 1983.6719 | 1966.6925 | 1966.6925 | 1966.6925 | 1966.6925 | 1966.6925 | 1966.6925 | 1966.6925 | 1966.6925 | 1966.6925 | 1966.6925 | 1966.6925 | 1966.6925 | 1966.6925 | 1966.6925 | 1966.6925 | 1966.6925
15% | 819.7224 | 1089.2296 | 1162.6419 | 1160.5412 | 1160.516 | 1168.9124 | 1178.1226 | 1197.0118 | 1210.5824 | 1217.9604 | 1226.0428 | 1233.4285 | 1246.7456 | 1263.2658 | 1262.1493 | 1262.1493 | 1262.1493 | 1262.1493 | 1262.1493 | 1262.1493 | 1262.1493 | 1262.1493 | 1262.1493 | 1262.1493 | 1262.1493 | 1262.1493 | 1262.1493 | 1262.1493 | 1262.1493 | 1262.1493 |  | 734.6312 | 951.6698 | 1008.502 | 1005.1221 | 1005.4058 | 1011.2569 | 1026.6605 | 1036.9885 | 1047.0905 | 1058.9017 | 1069.8573 | 1080.4849 | 1081.7162 | 1094.1168 | 1084.7516 | 1084.7516 | 1084.7516 | 1084.7516 | 1084.7516 | 1084.7516 | 1084.7516 | 1084.7516 | 1084.7516 | 1084.7516 | 1084.7516 | 1084.7516 | 1084.7516 | 1084.7516 | 1084.7516 | 1084.7516
10% | 548.6502 | 729.0346 | 778.1704 | 776.7643 | 776.7475 | 782.3673 | 788.5318 | 801.1745 | 810.2575 | 815.1957 | 820.6054 | 825.5487 | 834.462 | 845.5192 | 844.7719 | 844.7719 | 844.7719 | 844.7719 | 844.7719 | 844.7719 | 844.7719 | 844.7719 | 844.7719 | 844.7719 | 844.7719 | 844.7719 | 844.7719 | 844.7719 | 844.7719 | 844.7719 |  | 171.688 | 222.4113 | 235.6934 | 234.9034 | 234.9698 | 236.3372 | 239.9371 | 242.3508 | 244.7117 | 247.4721 | 250.0325 | 252.5162 | 252.804 | 255.7021 | 253.5134 | 253.5134 | 253.5134 | 253.5134 | 253.5134 | 253.5134 | 253.5134 | 253.5134 | 253.5134 | 253.5134 | 253.5134 | 253.5134 | 253.5134 | 253.5134 | 253.5134 | 253.5134
5% | 390.344 | 518.6808 | 553.639 | 552.6387 | 552.6267 | 556.625 | 561.0108 | 570.0056 | 576.4678 | 579.9811 | 583.8299 | 587.3469 | 593.6884 | 601.5551 | 601.0235 | 601.0235 | 601.0235 | 601.0235 | 601.0235 | 601.0235 | 601.0235 | 601.0235 | 601.0235 | 601.0235 | 601.0235 | 601.0235 | 601.0235 | 601.0235 | 601.0235 | 601.0235 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9.992e-14% | 34.2635 | 45.5286 | 48.5972 | 48.5094 | 48.5083 | 48.8593 | 49.2443 | 50.0338 | 50.6011 | 50.9095 | 51.2473 | 51.556 | 52.1126 | 52.8032 | 52.7565 | 52.7565 | 52.7565 | 52.7565 | 52.7565 | 52.7565 | 52.7565 | 52.7565 | 52.7565 | 52.7565 | 52.7565 | 52.7565 | 52.7565 | 52.7565 | 52.7565 | 52.7565 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E @ R (MWh) | 91763.8061 | 121933.7811 | 130151.918 | 129916.7517 | 129913.938 | 130853.8682 | 131884.9083 | 133999.4516 | 135518.6175 | 136344.5424 | 137249.3282 | 138076.12 | 139566.9035 | 141416.2562 | 141291.2697 | 141291.2697 | 141291.2697 | 141291.2697 | 141291.2697 | 141291.2697 | 141291.2697 | 141291.2697 | 141291.2697 | 141291.2697 | 141291.2697 | 141291.2697 | 141291.2697 | 141291.2697 | 141291.2697 | 141291.2697 | E @ R (MWh) | 89067.5772 | 115381.5956 | 122272.0083 | 121862.2159 | 121896.6185 | 122606.0074 | 124473.5651 | 125725.7387 | 126950.5164 | 128382.5252 | 129710.7955 | 130999.3026 | 131148.5764 | 132652.0463 | 131516.5966 | 131516.5966 | 131516.5966 | 131516.5966 | 131516.5966 | 131516.5966 | 131516.5966 | 131516.5966 | 131516.5966 | 131516.5966 | 131516.5966 | 131516.5966 | 131516.5966 | 131516.5966 | 131516.5966 | 131516.5966
Option 8 Summer POE50 W E @ R (MWh) N 2 | 64234.6643 | 85353.6468 | 91106.3426 | 90941.7262 | 90939.7566 | 91597.7077 | 92319.4358 | 93799.6161 | 94863.0323 | 95441.1797 | 96074.5298 | 96653.284 | 97696.8324 | 98991.3793 | 98903.8888 | 98903.8888 | 98903.8888 | 98903.8888 | 98903.8888 | 98903.8888 | 98903.8888 | 98903.8888 | 98903.8888 | 98903.8888 | 98903.8888 | 98903.8888 | 98903.8888 | 98903.8888 | 98903.8888 | 98903.8888 | Option 8 Summer POE10 W E @ R (MWh) N 2 | 26720.2732 | 34614.4787 | 36681.6025 | 36558.6648 | 36568.9855 | 36781.8022 | 37342.0695 | 37717.7216 | 38085.1549 | 38514.7576 | 38913.2387 | 39299.7908 | 39344.5729 | 39795.6139 | 39454.979 | 39454.979 | 39454.979 | 39454.979 | 39454.979 | 39454.979 | 39454.979 | 39454.979 | 39454.979 | 39454.979 | 39454.979 | 39454.979 | 39454.979 | 39454.979 | 39454.979 | 39454.979

## POF N,N-1 & N-2 Risk
N-2 Method 1
| Asset name | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Tx 1 Pof | DS-PHM-TRNFMR-9000004393 | 0.01357% | 0.01357% | 0.01791% | 0.023% | 0.02887% | 0.03555% | 0.04308% | 0.0515% | 0.06084% | 0.07112% | 0.08238% | 0.09465% | 0.1079% | 0.1223% | 0.1378% | 0.1378% | 0.1378% | 0.1378% | 0.1378% | 0.1378% | 0.1378% | 0.1378% | 0.1378% | 0.1378% | 0.1378% | 0.1378% | 0.1378% | 0.1378% | 0.1378% | 0.1378%
Tx 2 Pof | DS-PHM-TRNFMR-9000007050 | 0.01357% | 0.01357% | 0.01791% | 0.023% | 0.02887% | 0.03555% | 0.04308% | 0.0515% | 0.06084% | 0.07112% | 0.08238% | 0.09465% | 0.1079% | 0.1223% | 0.1378% | 0.1378% | 0.1378% | 0.1378% | 0.1378% | 0.1378% | 0.1378% | 0.1378% | 0.1378% | 0.1378% | 0.1378% | 0.1378% | 0.1378% | 0.1378% | 0.1378% | 0.1378%
Tx 3 Pof | bar: FY25 to FY54
Tx 4 Pof
Tx 5 Pof
Total Tx Pof |  | 0.02714% | 0.02714% | 0.03583% | 0.046% | 0.05773% | 0.0711% | 0.08616% | 0.103% | 0.1217% | 0.1422% | 0.1648% | 0.1893% | 0.2159% | 0.2446% | 0.2755% | 0.2755% | 0.2755% | 0.2755% | 0.2755% | 0.2755% | 0.2755% | 0.2755% | 0.2755% | 0.2755% | 0.2755% | 0.2755% | 0.2755% | 0.2755% | 0.2755% | 0.2755%
N-1 Risk |  | 0.01047% | 0.01047% | 0.01382% | 0.01775% | 0.02227% | 0.02743% | 0.03324% | 0.03974% | 0.04694% | 0.05488% | 0.06356% | 0.07303% | 0.08329% | 0.09438% | 0.1063% | 0.1063% | 0.1063% | 0.1063% | 0.1063% | 0.1063% | 0.1063% | 0.1063% | 0.1063% | 0.1063% | 0.1063% | 0.1063% | 0.1063% | 0.1063% | 0.1063% | 0.1063%
N-2 Risk |  | 4.318e-07% | 4.318e-07% | 7.523e-07% | 1.24e-06% | 1.953e-06% | 2.962e-06% | 4.351e-06% | 6.217e-06% | 8.675e-06% | 1.186e-05% | 1.591e-05% | 2.1e-05% | 2.731e-05% | 3.507e-05% | 4.449e-05% | 4.449e-05% | 4.449e-05% | 4.449e-05% | 4.449e-05% | 4.449e-05% | 4.449e-05% | 4.449e-05% | 4.449e-05% | 4.449e-05% | 4.449e-05% | 4.449e-05% | 4.449e-05% | 4.449e-05% | 4.449e-05% | 4.449e-05%
N Risk |  | 99.99% | 99.99% | 99.99% | 99.98% | 99.98% | 99.97% | 99.97% | 99.96% | 99.95% | 99.95% | 99.94% | 99.93% | 99.92% | 99.91% | 99.89% | 99.89% | 99.89% | 99.89% | 99.89% | 99.89% | 99.89% | 99.89% | 99.89% | 99.89% | 99.89% | 99.89% | 99.89% | 99.89% | 99.89% | 99.89%

## Summary
Involuntary load shedding (NER 5.17.1(c)(4)(ii))
Option 1 - Do Nothing / Base Case | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Weighted Energy @ Risk (MWh) under N Conditions | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Weighted Energy @ Risk (MWh) under N-1 Conditions | 0.0023203 | 0.11606 | 0.4094 | 0.57921 | 0.78408 | 1.1304 | 1.8821 | 2.7457 | 4.132 | 6.6326 | 6.7463 | 6.8484 | 9.3681 | 14.0517 | 13.1286 | 13.1286 | 13.1286 | 13.1286 | 13.1286 | 13.1286 | 13.1286 | 13.1286 | 13.1286 | 13.1286 | 13.1286 | 13.1286 | 13.1286 | 13.1286 | 13.1286 | 13.1286
Weighted Energy @ Risk (MWh) under N-2 Conditions | 0.0010504 | 0.001417 | 0.0026391 | 0.0043703 | 0.0069132 | 0.0106 | 0.015919 | 0.02315 | 0.032966 | 0.04616 | 0.06163 | 0.080754 | 0.10681 | 0.14098 | 0.17577 | 0.17577 | 0.17577 | 0.17577 | 0.17577 | 0.17577 | 0.17577 | 0.17577 | 0.17577 | 0.17577 | 0.17577 | 0.17577 | 0.17577 | 0.17577 | 0.17577 | 0.17577
Total EUE (MWh) - Option 1 | 0.0033707 | 0.11748 | 0.41204 | 0.58358 | 0.79099 | 1.141 | 1.8981 | 2.7688 | 4.165 | 6.6787 | 6.808 | 6.9292 | 9.4749 | 14.1927 | 13.3044 | 13.3044 | 13.3044 | 13.3044 | 13.3044 | 13.3044 | 13.3044 | 13.3044 | 13.3044 | 13.3044 | 13.3044 | 13.3044 | 13.3044 | 13.3044 | 13.3044 | 13.3044
Cost of EUE ($) - Option 1 | 130.1311 | 4535.3658 | 15907.403 | 22529.7846 | 30537.0779 | 44049.876 | 73276.699 | 106894.3736 | 160794.8873 | 257840.0603 | 262829.0846 | 267509.4891 | 365790.3822 | 547926.623 | 513632.0021 | 513632.0021 | 513632.0021 | 513632.0021 | 513632.0021 | 513632.0021 | 513632.0021 | 513632.0021 | 513632.0021 | 513632.0021 | 513632.0021 | 513632.0021 | 513632.0021 | 513632.0021 | 513632.0021 | 513632.0021
Hours at Risk pA. (Hrs) (N) | 1.486 | 1.486 | 1.486 | 1.486 | 1.486 | 1.486 | 1.486 | 1.486 | 1.486 | 1.486 | 1.486 | 1.486 | 1.486 | 1.486 | 1.486 | 1.486 | 1.486 | 1.486 | 1.486 | 1.486 | 1.486 | 1.486 | 1.486 | 1.486 | 1.486 | 1.486 | 1.486 | 1.486 | 1.486 | 1.486
Option 2 - 1A New PHS ZSS + Four new feeders | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Weighted Energy @ Risk (MWh) under N Conditions | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Weighted Energy @ Risk (MWh) under N-1 Conditions | 0.0023203 | 0.11606 | 0.4094 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00010437 | 0.00061105 | 0.00079337 | 0.0023774 | 0.0013535 | 0.0013535 | 0.0013535 | 0.0013535 | 0.0013535 | 0.0013535 | 0.0013535 | 0.0013535 | 0.0013535 | 0.0013535 | 0.0013535 | 0.0013535 | 0.0013535 | 0.0013535 | 0.0013535 | 0.0013535
Weighted Energy @ Risk (MWh) under N-2 Conditions | 0.0010504 | 0.001417 | 0.0026391 | 0.0023837 | 0.003784 | 0.0058546 | 0.0089485 | 0.013189 | 0.019067 | 0.027165 | 0.036143 | 0.047112 | 0.063046 | 0.084797 | 0.1045 | 0.1045 | 0.1045 | 0.1045 | 0.1045 | 0.1045 | 0.1045 | 0.1045 | 0.1045 | 0.1045 | 0.1045 | 0.1045 | 0.1045 | 0.1045 | 0.1045 | 0.1045
Total EUE (MWh) - Option 2 | 0.0033707 | 0.11748 | 0.41204 | 0.0023837 | 0.003784 | 0.0058546 | 0.0089485 | 0.013189 | 0.019067 | 0.027165 | 0.036247 | 0.047723 | 0.06384 | 0.087174 | 0.10585 | 0.10585 | 0.10585 | 0.10585 | 0.10585 | 0.10585 | 0.10585 | 0.10585 | 0.10585 | 0.10585 | 0.10585 | 0.10585 | 0.10585 | 0.10585 | 0.10585 | 0.10585
Cost of EUE ($) - Option 2 | 130.1311 | 4535.3658 | 15907.403 | 92.0252 | 146.086 | 226.0233 | 345.4684 | 509.1947 | 736.0964 | 1048.7341 | 1399.3594 | 1842.4001 | 2464.6045 | 3365.4552 | 4086.4328 | 4086.4328 | 4086.4328 | 4086.4328 | 4086.4328 | 4086.4328 | 4086.4328 | 4086.4328 | 4086.4328 | 4086.4328 | 4086.4328 | 4086.4328 | 4086.4328 | 4086.4328 | 4086.4328 | 4086.4328
Option 3 - 2A PHM 3rd Tx + Switchroom + Three new feeders + OFR12 New Feeder | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Weighted Energy @ Risk (MWh) under N Conditions | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Weighted Energy @ Risk (MWh) under N-1 Conditions | 0.0023203 | 0.11606 | 0.4094 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Weighted Energy @ Risk (MWh) under N-2 Conditions | 0.0010504 | 0.001417 | 0.0026391 | 8.2023e-05 | 0.00013779 | 0.00023677 | 0.00044845 | 0.00074881 | 0.0012696 | 0.0022403 | 0.0027066 | 0.0032087 | 0.0048497 | 0.0078739 | 0.0085154 | 0.0085154 | 0.0085154 | 0.0085154 | 0.0085154 | 0.0085154 | 0.0085154 | 0.0085154 | 0.0085154 | 0.0085154 | 0.0085154 | 0.0085154 | 0.0085154 | 0.0085154 | 0.0085154 | 0.0085154
Total EUE (MWh) - Option 3 | 0.0033707 | 0.11748 | 0.41204 | 8.2023e-05 | 0.00013779 | 0.00023677 | 0.00044845 | 0.00074881 | 0.0012696 | 0.0022403 | 0.0027066 | 0.0032087 | 0.0048497 | 0.0078739 | 0.0085154 | 0.0085154 | 0.0085154 | 0.0085154 | 0.0085154 | 0.0085154 | 0.0085154 | 0.0085154 | 0.0085154 | 0.0085154 | 0.0085154 | 0.0085154 | 0.0085154 | 0.0085154 | 0.0085154 | 0.0085154
Cost of EUE ($) - Option 3 | 130.1311 | 4535.3658 | 15907.403 | 3.1666 | 5.3194 | 9.1408 | 17.313 | 28.9088 | 49.0155 | 86.4888 | 104.4914 | 123.8772 | 187.2276 | 303.9826 | 328.7473 | 328.7473 | 328.7473 | 328.7473 | 328.7473 | 328.7473 | 328.7473 | 328.7473 | 328.7473 | 328.7473 | 328.7473 | 328.7473 | 328.7473 | 328.7473 | 328.7473 | 328.7473
Option 4 - 3A OFR 3rd Tx + Switchroom + Three new feeders + OFR12 New Feeder | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Weighted Energy @ Risk (MWh) under N Conditions | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Weighted Energy @ Risk (MWh) under N-1 Conditions | 0.0023203 | 0.11606 | 0.4094 | 0.01384 | 0.017435 | 0.023934 | 0.039256 | 0.065851 | 0.13853 | 0.59239 | 0.31032 | 0.26899 | 0.4749 | 1.2171 | 0.78379 | 0.78379 | 0.78379 | 0.78379 | 0.78379 | 0.78379 | 0.78379 | 0.78379 | 0.78379 | 0.78379 | 0.78379 | 0.78379 | 0.78379 | 0.78379 | 0.78379 | 0.78379
Weighted Energy @ Risk (MWh) under N-2 Conditions | 0.0010504 | 0.001417 | 0.0026391 | 0.003377 | 0.0053486 | 0.0082275 | 0.012434 | 0.01817 | 0.026017 | 0.036663 | 0.048886 | 0.063933 | 0.084928 | 0.11289 | 0.14013 | 0.14013 | 0.14013 | 0.14013 | 0.14013 | 0.14013 | 0.14013 | 0.14013 | 0.14013 | 0.14013 | 0.14013 | 0.14013 | 0.14013 | 0.14013 | 0.14013 | 0.14013
Total EUE (MWh) - Option 4 | 0.0033707 | 0.11748 | 0.41204 | 0.017217 | 0.022783 | 0.032161 | 0.05169 | 0.084021 | 0.16455 | 0.62905 | 0.3592 | 0.33292 | 0.55983 | 1.33 | 0.92393 | 0.92393 | 0.92393 | 0.92393 | 0.92393 | 0.92393 | 0.92393 | 0.92393 | 0.92393 | 0.92393 | 0.92393 | 0.92393 | 0.92393 | 0.92393 | 0.92393 | 0.92393
Cost of EUE ($) - Option 4 | 130.1311 | 4535.3658 | 15907.403 | 664.6639 | 879.5726 | 1241.6273 | 1995.555 | 3243.7239 | 6352.5946 | 24285.2429 | 13867.4657 | 12852.7592 | 21612.8866 | 51345.4792 | 35669.2138 | 35669.2138 | 35669.2138 | 35669.2138 | 35669.2138 | 35669.2138 | 35669.2138 | 35669.2138 | 35669.2138 | 35669.2138 | 35669.2138 | 35669.2138 | 35669.2138 | 35669.2138 | 35669.2138 | 35669.2138
Option 5 - 4A LLG 2nd Tx + Switchroom + Three new feeders + OFR12 New Feeder | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Weighted Energy @ Risk (MWh) under N Conditions | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Weighted Energy @ Risk (MWh) under N-1 Conditions | 0.0023203 | 0.11606 | 0.4094 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00010437 | 0.00061105 | 0.00079337 | 0.0023774 | 0.0013535 | 0.0013535 | 0.0013535 | 0.0013535 | 0.0013535 | 0.0013535 | 0.0013535 | 0.0013535 | 0.0013535 | 0.0013535 | 0.0013535 | 0.0013535 | 0.0013535 | 0.0013535 | 0.0013535 | 0.0013535
Weighted Energy @ Risk (MWh) under N-2 Conditions | 0.0010504 | 0.001417 | 0.0026391 | 0.0023837 | 0.003784 | 0.0058546 | 0.0089485 | 0.013189 | 0.019067 | 0.027165 | 0.036143 | 0.047112 | 0.063046 | 0.084797 | 0.1045 | 0.1045 | 0.1045 | 0.1045 | 0.1045 | 0.1045 | 0.1045 | 0.1045 | 0.1045 | 0.1045 | 0.1045 | 0.1045 | 0.1045 | 0.1045 | 0.1045 | 0.1045
Total EUE (MWh) - Option 5 | 0.0033707 | 0.11748 | 0.41204 | 0.0023837 | 0.003784 | 0.0058546 | 0.0089485 | 0.013189 | 0.019067 | 0.027165 | 0.036247 | 0.047723 | 0.06384 | 0.087174 | 0.10585 | 0.10585 | 0.10585 | 0.10585 | 0.10585 | 0.10585 | 0.10585 | 0.10585 | 0.10585 | 0.10585 | 0.10585 | 0.10585 | 0.10585 | 0.10585 | 0.10585 | 0.10585
Cost of EUE ($) - Option 5 | 130.1311 | 4535.3658 | 15907.403 | 92.0252 | 146.086 | 226.0233 | 345.4684 | 509.1947 | 736.0964 | 1048.7341 | 1399.3594 | 1842.4001 | 2464.6045 | 3365.4552 | 4086.4328 | 4086.4328 | 4086.4328 | 4086.4328 | 4086.4328 | 4086.4328 | 4086.4328 | 4086.4328 | 4086.4328 | 4086.4328 | 4086.4328 | 4086.4328 | 4086.4328 | 4086.4328 | 4086.4328 | 4086.4328
Option 6 - Non Network | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Weighted Energy @ Risk (MWh) under N Conditions | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Weighted Energy @ Risk (MWh) under N-1 Conditions | 0 | 0.0095991 | 0.027409 | 0.03623 | 0.047724 | 0.069941 | 0.13675 | 0.23204 | 0.45918 | 1.2609 | 0.8825 | 0.7439 | 1.258 | 2.6234 | 1.9559 | 1.9559 | 1.9559 | 1.9559 | 1.9559 | 1.9559 | 1.9559 | 1.9559 | 1.9559 | 1.9559 | 1.9559 | 1.9559 | 1.9559 | 1.9559 | 1.9559 | 1.9559
Weighted Energy @ Risk (MWh) under N-2 Conditions | 0.00086563 | 0.0011794 | 0.0022012 | 0.0036511 | 0.0057805 | 0.0088733 | 0.013345 | 0.019438 | 0.027738 | 0.038938 | 0.051844 | 0.067715 | 0.089833 | 0.11895 | 0.14806 | 0.14806 | 0.14806 | 0.14806 | 0.14806 | 0.14806 | 0.14806 | 0.14806 | 0.14806 | 0.14806 | 0.14806 | 0.14806 | 0.14806 | 0.14806 | 0.14806 | 0.14806
Total EUE (MWh) - Option 6 | 0.00086563 | 0.010778 | 0.029611 | 0.039881 | 0.053504 | 0.078814 | 0.1501 | 0.25148 | 0.48692 | 1.2998 | 0.93434 | 0.81161 | 1.3478 | 2.7424 | 2.1039 | 2.1039 | 2.1039 | 2.1039 | 2.1039 | 2.1039 | 2.1039 | 2.1039 | 2.1039 | 2.1039 | 2.1039 | 2.1039 | 2.1039 | 2.1039 | 2.1039 | 2.1039
Cost of EUE ($) - Option 6 | 33.4188 | 416.1141 | 1143.1504 | 1539.6448 | 2065.5976 | 3042.7156 | 5794.7316 | 9708.6653 | 18798.0019 | 50180.6141 | 36071.3773 | 31333.2819 | 52033.4205 | 105872.1468 | 81225.0262 | 81225.0262 | 81225.0262 | 81225.0262 | 81225.0262 | 81225.0262 | 81225.0262 | 81225.0262 | 81225.0262 | 81225.0262 | 81225.0262 | 81225.0262 | 81225.0262 | 81225.0262 | 81225.0262 | 81225.0262
Option 7 - | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Weighted Energy @ Risk (MWh) under N Conditions | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Weighted Energy @ Risk (MWh) under N-1 Conditions | 0.0023203 | 0.11606 | 0.4094 | 0.57921 | 0.78408 | 1.1304 | 1.8821 | 2.7457 | 4.132 | 6.6326 | 6.7463 | 6.8484 | 9.3681 | 14.0517 | 13.1286 | 13.1286 | 13.1286 | 13.1286 | 13.1286 | 13.1286 | 13.1286 | 13.1286 | 13.1286 | 13.1286 | 13.1286 | 13.1286 | 13.1286 | 13.1286 | 13.1286 | 13.1286
Weighted Energy @ Risk (MWh) under N-2 Conditions | 0.0010504 | 0.001417 | 0.0026391 | 0.0043703 | 0.0069132 | 0.0106 | 0.015919 | 0.02315 | 0.032966 | 0.04616 | 0.06163 | 0.080754 | 0.10681 | 0.14098 | 0.17577 | 0.17577 | 0.17577 | 0.17577 | 0.17577 | 0.17577 | 0.17577 | 0.17577 | 0.17577 | 0.17577 | 0.17577 | 0.17577 | 0.17577 | 0.17577 | 0.17577 | 0.17577
Total EUE (MWh) - Option 7 | 0.0033707 | 0.11748 | 0.41204 | 0.58358 | 0.79099 | 1.141 | 1.8981 | 2.7688 | 4.165 | 6.6787 | 6.808 | 6.9292 | 9.4749 | 14.1927 | 13.3044 | 13.3044 | 13.3044 | 13.3044 | 13.3044 | 13.3044 | 13.3044 | 13.3044 | 13.3044 | 13.3044 | 13.3044 | 13.3044 | 13.3044 | 13.3044 | 13.3044 | 13.3044
Cost of EUE ($) - Option 7 | 130.1311 | 4535.3658 | 15907.403 | 22529.7846 | 30537.0779 | 44049.876 | 73276.699 | 106894.3736 | 160794.8873 | 257840.0603 | 262829.0846 | 267509.4891 | 365790.3822 | 547926.623 | 513632.0021 | 513632.0021 | 513632.0021 | 513632.0021 | 513632.0021 | 513632.0021 | 513632.0021 | 513632.0021 | 513632.0021 | 513632.0021 | 513632.0021 | 513632.0021 | 513632.0021 | 513632.0021 | 513632.0021 | 513632.0021
Option 8 - | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Weighted Energy @ Risk (MWh) under N Conditions | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Weighted Energy @ Risk (MWh) under N-1 Conditions | 0.0023203 | 0.11606 | 0.4094 | 0.57921 | 0.78408 | 1.1304 | 1.8821 | 2.7457 | 4.132 | 6.6326 | 6.7463 | 6.8484 | 9.3681 | 14.0517 | 13.1286 | 13.1286 | 13.1286 | 13.1286 | 13.1286 | 13.1286 | 13.1286 | 13.1286 | 13.1286 | 13.1286 | 13.1286 | 13.1286 | 13.1286 | 13.1286 | 13.1286 | 13.1286
Weighted Energy @ Risk (MWh) under N-2 Conditions | 0.0010504 | 0.001417 | 0.0026391 | 0.0043703 | 0.0069132 | 0.0106 | 0.015919 | 0.02315 | 0.032966 | 0.04616 | 0.06163 | 0.080754 | 0.10681 | 0.14098 | 0.17577 | 0.17577 | 0.17577 | 0.17577 | 0.17577 | 0.17577 | 0.17577 | 0.17577 | 0.17577 | 0.17577 | 0.17577 | 0.17577 | 0.17577 | 0.17577 | 0.17577 | 0.17577
Total EUE (MWh) - Option 8 | 0.0033707 | 0.11748 | 0.41204 | 0.58358 | 0.79099 | 1.141 | 1.8981 | 2.7688 | 4.165 | 6.6787 | 6.808 | 6.9292 | 9.4749 | 14.1927 | 13.3044 | 13.3044 | 13.3044 | 13.3044 | 13.3044 | 13.3044 | 13.3044 | 13.3044 | 13.3044 | 13.3044 | 13.3044 | 13.3044 | 13.3044 | 13.3044 | 13.3044 | 13.3044
Cost of EUE ($) - Option 8 | 130.1311 | 4535.3658 | 15907.403 | 22529.7846 | 30537.0779 | 44049.876 | 73276.699 | 106894.3736 | 160794.8873 | 257840.0603 | 262829.0846 | 267509.4891 | 365790.3822 | 547926.623 | 513632.0021 | 513632.0021 | 513632.0021 | 513632.0021 | 513632.0021 | 513632.0021 | 513632.0021 | 513632.0021 | 513632.0021 | 513632.0021 | 513632.0021 | 513632.0021 | 513632.0021 | 513632.0021 | 513632.0021 | 513632.0021