## Info
Document description
This model Energy at Risk model has been developed to calculated Energy at Risk (EaR) in terms of Expected Unsureved Energy (EUE) and the cost of EUE. The modelling inputs, calculation steps and outputs are described in the 'Modelling Steps' tab. Further detail on EaR/EUE calculations can be found in AusNet's Network Planning Policy and Guidelines.
Tab # | Tab Name | Description | Source/ Inputs
0.1 | Modelling Steps | E@R model process flowchart and underlying equations | N/A
0.2 | Modelling Example & QA | Example E@R model calculations and data flow; also used to validate base case | N/A
0.3 | QA | Quality assurance and data validation | Entire workbook
1.1 | Output for AusNet's NPV Model | Aggregates Supply Risk ($M) and EUE (MWh) for input into AusNet’s NPV model | Summary tab
2.1 | Key Model Assumptions & Inputs | E@R model inputs and asset selection | Augmentation plans from RPs/EPCs, Embedded Generation DB, Demand Management DB
2.2 | Tx PoF | Transformer Probabilities of Failure | Provided by Asset Management Team
2.3 | Customer No. and Volume per Feeder | Customer consumption data | Provided by Finance Team
2.4 | AER VCR Rates (2024) | AER 2024 VCR rates | AER VCR Factsheet
2.5 | Forecast - Summer | Summer Forecast Data | Extract from Forecasting Toolbox
2.6 | Forecast- Winter | Winter Forecast Data | Extract from Forecasting Toolbox
2.7 | Ratings | Station Rating Data | AMS 20-101 / Provided by Asset mangement Team
2.8 | FT (Forecast & Transfers) | Forecast, transfer & PF inputs | Forecast Summer , Forecast Winter , NP Transfer Sheet, PF = avg. max demand PF across stations
2.9 | Load Duration Curves | Load duration curve data | LDC Tool; data sourced from PI SCADA Historian and AEMO
3.1 | Capacity N | Option N capacity calculated | FT Sheet, Ratings & Key Model Assumptions
3.2 | Capacity N-1 | Option N-1 capacity calculated | FT Sheet, Ratings & Key Model Assumptions
3.3 | Capacity N-1 | Option N-2 capacity calculated | FT Sheet, Ratings & Key Model Assumptions
3.4 | Demand | Calculates maximum demand | FT Sheet & Key Model Assumptions
3.5 | MD Weighted LDC | Maps maximum demand forecast to load duration curve | Demand Sheet & Load Duration Curve Sheet
3.6 | Locational VCR | Calculates tailored VCR by location using feeder energy mix and AER rates | AER VCR Rates (2024) & Customer No./Volume per Feeder
3.7 | E@R N | Calculates N EUE using capacity and demand inputs | MD Weighted LDC & Capacity N
3.8 | E@R N-1 | Calculates N-1 EUE using capacity and demand inputs | MD Weighted LDC & Capacity N-1
3.9 | E@R N-2 | Calculates N-2 EUE using capacity and demand inputs | MD Weighted LDC & Capacity N-2
4 | POF N,N-1 & N-2 Risk | Calculates Station N , N-1 & N-2 PoF's from Tx PoF Data & MTTR | TX PoF & Key Model Assumptions
4.1 | Summary | Collates weighted EUE and calculates supply risk | E@R & Locational VCR
Revision table
Date | Editted by | Change
2025-10-14 | HT | Draft Version 2.1
2025-10-20 | HT | Version 2.2
2025-11-10 | HT | Version 2.3 Example Page Update and General Refinements

## Modelling Steps
Eq1. Locational VCR |  | Data Inputs |  |  | Calculations |  |  |  |  | Outputs
|  |  | Customer No. and Vol per Feeder |  | Eq1.
Locational VCR
Eq2. Maximum Demand
AER Latetst VCR Rates
Eq3. Options & Do nothing Capacity
Eq6. & Eq7.
Load Forecast
[9 empty] | Summary Sheet | Output for AusNet's NPV Model
Eq4. Help Sheet | Re Name Forecasted LDC add Forecast MD to eq
Transfer Capacity
Eq2.
Eq5. Energy at Risk ( Option/ Do Nothing Capacity) |  |  |  |  | Options & Do Nothing Max Demand
Embeded Generation
Eq6. Weighted Expected Unserved Energy
[6 empty] | Eq.4 | Eq.5
Demand Mangement Capacity
[6 empty] | Forecasted LDC |  | Energy @ Risk Sheet
Eq7. Supply Risk
Load Duration Curves
|  |  | Asset Ratings |  | Eq3.
Options & Do Nothing Capacity
Planned & Proposed Works

## Modelling Steps Example & QA
End of Sheet
Data Inputs |  |  | Calculations | [12 empty] | Outputs
AER VCR Rates(2024 |  |  | Locational (Tailored VCR)
Category | Rate |  | Base case |  | Energy Usage (CY 2024 kWh) | Energy Usage (CY 2024 %) | Tailored VCR
Dec 24 AER VCR ($/kWh) - Res | 49.23 |  | Dec 24 AER VCR ($/kWh) - Res | 49.23 | 67934749.1441 | 34.06% | 16.7657
Dec 24 AER VCR ($/kWh) - Com | 34.39 |  | Dec 24 AER VCR ($/kWh) - Com | 34.39 | 101368150.4504 | 50.82% | 17.4756
Dec 24 AER VCR ($/kWh) - Ind | 33.49 |  | Dec 24 AER VCR ($/kWh) - Ind | 33.49 | 17726336.2671 | 8.886% | 2.976
Dec 24 AER VCR ($/kWh) - Agr | 22.25 |  | Dec 24 AER VCR ($/kWh) - Agr | 22.25 | 12451243.5083 | 6.242% | 1.3888
[5 empty] | 199480479.3698 |  | 38.6062
Customer No. and Vol per Feeder | [6 empty] | 38606.1513 | [8 empty] | Summary |  | Outputs for NPV model
COMMERCIAL | 101368150.4504 | [14 empty] | Year | 2031 | Year | 2031
[16 empty] | E@R MWh | 2.537 | E@R MWh | 2.537
RESIDENTL | 67934749.1441 | [14 empty] | cost of EUE ($) | 97942.7747 | cost of EUE ($M) | 0.097943
FARM | 12451243.5083
INDUSTRIAL | 17726336.2671
Forecast (FCT)
Forecast | 2031
Summer POE50 | 75.0153
Summer POE10 | 81.1895
Winter POE50 | 73.2946
Winter POE10 | 76.2493
Transfer Capacity |  |  | Option Max Demand |  |  |  | MD Weighted LDC |  |  | E@R (N) |  | E@R (N-1) |  | E@R (N-2)
Year | 2031 |  | Forecast | 2031 |  |  | % of MD | Summer - AD - Hours | FY31 | % of MD | FY31 | % of MD | FY31 | % of MD | FY31
Capacity | 1.58 |  | Summer POE50 | 73.4353 |  |  | 100% | 0 | 73.4353 | 100% |  | 100% |  | 100%
|  |  | Summer POE10 | 79.6095 |  |  | 99% | 0 | 72.701 | 99% |  | 99% | 0 | 99% | 0
Embedded Generation |  |  | Winter POE50 | 71.7146 |  |  | 98% | 0 | 71.9666 | 98% |  | 98% | 0 | 98% | 0
|  |  | Winter POE10 | 74.6693 |  |  | 97% | 0.37816 | 71.2323 | 97% |  | 97% | 10.059 | 97% | 27.0764
Year | 2031 | [5 empty] | 95% | 2.269 | 69.7636 | 95% |  | 95% | 48.212 | 95% | 133.299
Capacity | 0 | [5 empty] | 90% | 5.6725 | 66.0918 | 90% |  | 90% | 78.0339 | 90% | 231.1905
[7 empty] | 85% | 15.8829 | 62.42 | 85% |  | 85% | 196.6114 | 85% | 656.081
Demand Mangement | [6 empty] | 80% | 31.0095 | 58.7483 | 80% |  | 80% | 235.7349 | 80% | 916.4306
[7 empty] | 75% | 72.9857 | 55.0765 | 75% |  | 75% | 500.0374 | 75% | 2388.968
Year | 2031 | [5 empty] | 70% | 150.5094 | 51.4047 | 70% |  | 70% | 638.8436 | 70% | 4127.4091
Capacity | 0 | [5 empty] | 65% | 359.6342 | 47.733 | 65% |  | 65% | 955.4618 | 65% | 10366.0801
[7 empty] | 60% | 689.7717 | 44.0612 | 60% |  | 60% | 335.7847 | 60% | 15152.3473
LDC | [6 empty] | 55% | 1095.5419 | 40.3894 | 55% |  | 55% |  | 55% | 17133.7814
[7 empty] | 50% | 1666.1918 | 36.7177 | 50% |  | 50% |  | 50% | 22000.5834
% of MD | Summer - AD - Duration % | Summer - AD - Hours |  |  |  |  | 45% | 2506.0947 | 33.0459 | 45% |  | 45% |  | 45% | 29297.3152
100% | 0% | 0 |  |  |  |  | 40% | 3164.4787 | 29.3741 | 40% |  | 40% |  | 40% | 20548.1797
99% | 0% | 0 |  |  |  |  | 35% | 3551.3408 | 25.7024 | 35% |  | 35% |  | 35% | 10653.506
98% | 0% | 0 |  |  |  |  | 30% | 3758.953 | 22.0306 | 30% |  | 30% |  | 30% | 4954.9738
97% | 0.00861% | 0.37816 |  |  |  |  | 25% | 3926.4798 | 18.3588 | 25% |  | 25% |  | 25% | 3383.1564
95% | 0.05166% | 2.269 |  |  |  |  | 20% | 4050.5177 | 14.6871 | 20% |  | 20% |  | 20% | 2049.4721
90% | 0.1292% | 5.6725 |  |  |  |  | 15% | 4152.622 | 11.0153 | 15% |  | 15% |  | 15% | 1312.162
85% | 0.3616% | 15.8829 |  |  |  |  | 10% | 4248.2976 | 7.3435 | 10% |  | 10% |  | 10% | 878.246
80% | 0.706% | 31.0095 |  |  |  |  | 5% | 4361.7469 | 3.6718 | 5% |  | 5% |  | 5% | 624.8391
75% | 1.662% | 72.9857 |  |  |  |  | 9.992e-14% | 4391.6218 | 7.3377e-14 | 9.992e-14% |  | 9.992e-14% |  | 9.992e-14% | 54.847
70% | 3.427% | 150.5094 | [7 empty] | Total E@R | 0 | Total E@R | 2998.7788 | Total E@R | 146889.9441
65% | 8.188% | 359.6342 | [7 empty] | Total WE@R | 0 | Total WE@R | 0.46404 | Total WE@R | 0.0014874
60% | 15.71% | 689.7717 |  |  |  |  | MD Weighted LDC
55% | 24.94% | 1095.5419
50% | 37.94% | 1666.1918 |  |  |  |  | % of MD | Summer - MD - Hours | FY31
45% | 57.06% | 2506.0947 |  |  |  |  | 100% | 0 | 79.6095 | E@R (N) |  | E@R (N-1) |  | E@R (N-2)
40% | 72.05% | 3164.4787 |  |  |  |  | 99% | 1.5127 | 78.8134
35% | 80.86% | 3551.3408 |  |  |  |  | 98% | 2.269 | 78.0173 | % of MD | FY31 | % of MD | FY31 | % of MD | FY31
30% | 85.59% | 3758.953 |  |  |  |  | 97% | 3.7816 | 77.2212 | 100% |  | 100% |  | 100%
25% | 89.4% | 3926.4798 |  |  |  |  | 95% | 6.0506 | 75.629 | 99% |  | 99% | 51.7502 | 99% | 119.8198
20% | 92.22% | 4050.5177 |  |  |  |  | 90% | 16.2611 | 71.6485 | 98% |  | 98% | 25.273 | 98% | 59.3078
15% | 94.55% | 4152.622 |  |  |  |  | 85% | 26.4715 | 67.6681 | 97% |  | 97% | 49.3417 | 97% | 117.4113
10% | 96.73% | 4248.2976 |  |  |  |  | 80% | 34.0348 | 63.6876 | 95% |  | 95% | 71.3031 | 95% | 173.4075
5% | 99.31% | 4361.7469 |  |  |  |  | 75% | 48.405 | 59.7071 | 90% |  | 90% | 292.4144 | 90% | 751.884
9.992e-14% | 99.99% | 4391.6218 |  |  |  |  | 70% | 76.3892 | 55.7266 | 85% |  | 85% | 251.772 | 85% | 711.2416
[7 empty] | 65% | 114.2056 | 51.7462 | 80% |  | 80% | 156.3923 | 80% | 496.7402
[7 empty] | 60% | 178.1154 | 47.7657 | 75% |  | 75% | 239.945 | 75% | 886.6059
[7 empty] | 55% | 311.6074 | 43.7852 | 70% |  | 70% | 355.8711 | 70% | 1615.1582
LDC | [6 empty] | 50% | 636.0723 | 39.8047 | 65% |  | 65% | 330.3796 | 65% | 2032.1189
[7 empty] | 45% | 1179.4944 | 35.8243 | 60% |  | 60% | 303.9503 | 60% | 3179.8897
% of MD | Summer - MD - Duration % | Summer - MD - Hours |  |  |  |  | 40% | 1808.3816 | 31.8438 | 55% |  | 55% | 128.262 | 55% | 6110.6567
100% | 0% | 0 |  |  |  |  | 35% | 2779.1293 | 27.8633 | 50% |  | 50% |  | 50% | 13561.0066
99% | 0.03444% | 1.5127 |  |  |  |  | 30% | 3814.165 | 23.8828 | 45% |  | 45% |  | 45% | 20549.2377
98% | 0.05166% | 2.269 |  |  |  |  | 25% | 4166.9923 | 19.9024 | 40% |  | 40% |  | 40% | 21277.7899
97% | 0.0861% | 3.7816 |  |  |  |  | 20% | 4282.7105 | 15.9219 | 35% |  | 35% |  | 35% | 28980.2731
95% | 0.1378% | 6.0506 |  |  |  |  | 15% | 4364.7722 | 11.9414 | 30% |  | 30% |  | 30% | 26779.5636
90% | 0.3702% | 16.2611 |  |  |  |  | 10% | 4391.6218 | 7.9609 | 25% |  | 25% |  | 25% | 7724.3096
85% | 0.6027% | 26.4715 |  |  |  |  | 5% | 4391.6218 | 3.9805 | 20% |  | 20% |  | 20% | 2072.7613
80% | 0.7749% | 34.0348 |  |  |  |  | 9.992e-14% | 4391.6218 | 7.9546e-14 | 15% |  | 15% |  | 15% | 1143.255
75% | 1.102% | 48.405 | [7 empty] | 10% |  | 10% |  | 10% | 267.186
70% | 1.739% | 76.3892 | [7 empty] | 5% |  | 5% |  | 5% | 0
65% | 2.6% | 114.2056 | [7 empty] | 9.992e-14% |  | 9.992e-14% |  | 9.992e-14% | 0
60% | 4.055% | 178.1154 | [7 empty] | Total E@R | 0 | Total E@R | 2256.6548 | Total E@R | 138609.6244
55% | 7.095% | 311.6074 |  |  |  |  | MD Weighted LDC |  |  | Total WE@R | 0 | Total WE@R | 0.14966 | Total WE@R | 0.00060154
50% | 14.48% | 636.0723
45% | 26.86% | 1179.4944 |  |  |  |  | % of MD | Winter - AD - Hours | FY31
40% | 41.17% | 1808.3816 |  |  |  |  | 100% | 0 | 71.7146
35% | 63.28% | 2779.1293 |  |  |  |  | 99% | 1.486 | 70.9975 | E@R (N) |  | E@R (N-1) |  | E@R (N-2)
30% | 86.84% | 3814.165 |  |  |  |  | 98% | 3.2692 | 70.2804
25% | 94.88% | 4166.9923 |  |  |  |  | 97% | 6.8356 | 69.5632 | % of MD | FY31 | % of MD | FY31 | % of MD | FY31
20% | 97.51% | 4282.7105 |  |  |  |  | 95% | 17.5347 | 68.1289 | 100% |  | 100% |  | 100%
15% | 99.38% | 4364.7722 |  |  |  |  | 90% | 78.7576 | 64.5432 | 99% |  | 99% | 33.0724 | 99% | 106.0346
10% | 99.99% | 4391.6218 |  |  |  |  | 85% | 236.8672 | 60.9575 | 98% |  | 98% | 38.408 | 98% | 125.9627
5% | 99.99% | 4391.6218 |  |  |  |  | 80% | 497.5104 | 57.3717 | 97% |  | 97% | 74.2584 | 97% | 249.3678
9.992e-14% | 99.99% | 4391.6218 |  |  |  |  | 75% | 803.6248 | 53.786 | 95% |  | 95% | 211.266 | 95% | 736.5942
[7 empty] | 70% | 1155.2107 | 50.2003 | 90% |  | 90% | 1055.2409 | 90% | 4061.2852
[7 empty] | 65% | 1553.1596 | 46.6145 | 85% |  | 85% | 2158.2465 | 85% | 9921.4289
[7 empty] | 60% | 2026.2996 | 43.0288 | 80% |  | 80% | 2623.2647 | 80% | 15420.8418
LDC | [6 empty] | 55% | 2598.4068 | 39.4431 | 75% |  | 75% | 1983.2706 | 75% | 17013.4923
[7 empty] | 50% | 3233.5201 | 35.8573 | 70% |  | 70% | 1017.18 | 70% | 18280.0463
% of MD | Winter - AD (P50) - Duration % | Winter - AD - Hours |  |  |  |  | 45% | 3775.313 | 32.2716 | 65% |  | 65% | 67.1746 | 65% | 19263.6638
100% | 0% | 0 |  |  |  |  | 40% | 4072.8088 | 28.6859 | 60% |  | 60% |  | 60% | 21206.9211
99% | 0.03383% | 1.486 |  |  |  |  | 35% | 4198.821 | 25.1001 | 55% |  | 55% |  | 55% | 23591.3677
98% | 0.07443% | 3.2692 |  |  |  |  | 30% | 4271.3374 | 21.5144 | 50% |  | 50% |  | 50% | 23912.1357
97% | 0.1556% | 6.8356 |  |  |  |  | 25% | 4321.8611 | 17.9287 | 45% |  | 45% |  | 45% | 18455.8826
95% | 0.3992% | 17.5347 |  |  |  |  | 20% | 4353.067 | 14.3429 | 40% |  | 40% |  | 40% | 9067.2909
90% | 1.793% | 78.7576 |  |  |  |  | 15% | 4369.4129 | 10.7572 | 35% |  | 35% |  | 35% | 3388.8447
85% | 5.393% | 236.8672 |  |  |  |  | 10% | 4378.6261 | 7.1715 | 30% |  | 30% |  | 30% | 1690.1596
80% | 11.33% | 497.5104 |  |  |  |  | 5% | 4391.7028 | 3.5857 | 25% |  | 25% |  | 25% | 996.4056
75% | 18.3% | 803.6248 |  |  |  |  | 9.992e-14% | 4391.7028 | 7.1657e-14 | 20% |  | 20% |  | 20% | 503.5312
70% | 26.3% | 1155.2107 | [7 empty] | 15% |  | 15% |  | 15% | 205.1423
65% | 35.36% | 1553.1596 | [7 empty] | 10% |  | 10% |  | 10% | 82.5898
60% | 46.14% | 2026.2996 | [7 empty] | 5% |  | 5% |  | 5% | 70.3345
55% | 59.16% | 2598.4068 | [7 empty] | 9.992e-14% |  | 9.992e-14% |  | 9.992e-14% | 0
50% | 73.62% | 3233.5201 |  |  |  |  | MD Weighted LDC |  |  | Total E@R | 0 | Total E@R | 9261.3822 | Total E@R | 188349.3233
45% | 85.96% | 3775.313 | [7 empty] | Total WE@R | 0 | Total WE@R | 1.2176 | Total WE@R | 0.0016205
40% | 92.73% | 4072.8088 |  |  |  |  | % of MD | Winter - MD - Hours | FY31
35% | 95.6% | 4198.821 |  |  |  |  | 100% | 0 | 74.6693 | E@R (N) |  | E@R (N) |  | E@R (N)
30% | 97.25% | 4271.3374 |  |  |  |  | 99% | 1.486 | 73.9226
25% | 98.4% | 4321.8611 |  |  |  |  | 98% | 3.2692 | 73.1759 | % of MD | FY31 | % of MD | FY31 | % of MD | FY31
20% | 99.11% | 4353.067 |  |  |  |  | 97% | 6.8356 | 72.4292 | 100% |  | 100% |  | 100%
15% | 99.49% | 4369.4129 |  |  |  |  | 95% | 17.5347 | 70.9358 | 99% |  | 99% | 37.4409 | 99% | 110.4032
10% | 99.7% | 4378.6261 |  |  |  |  | 90% | 78.7576 | 67.2023 | 98% |  | 98% | 43.5976 | 98% | 131.1523
5% | 99.99% | 4391.7028 |  |  |  |  | 85% | 236.8672 | 63.4689 | 97% |  | 97% | 84.5323 | 97% | 259.6417
9.992e-14% | 99.99% | 4391.7028 |  |  |  |  | 80% | 497.5104 | 59.7354 | 95% |  | 95% | 241.6134 | 95% | 766.9415
[7 empty] | 75% | 803.6248 | 56.0019 | 90% |  | 90% | 1222.564 | 90% | 4228.6083
[7 empty] | 70% | 1155.2107 | 52.2685 | 85% |  | 85% | 2567.0047 | 85% | 10330.1872
[7 empty] | 65% | 1553.1596 | 48.535 | 80% |  | 80% | 3258.5963 | 80% | 16056.1734
LDC | [6 empty] | 60% | 2026.2996 | 44.8016 | 75% |  | 75% | 2684.2186 | 75% | 17714.4402
[7 empty] | 55% | 2598.4068 | 41.0681 | 70% |  | 70% | 1770.3095 | 70% | 19033.1757
% of MD | Winter - MD (P10) - Duration % | Winter - MD - Hours |  |  |  |  | 50% | 3233.5201 | 37.3346 | 65% |  | 65% | 535.0416 | 65% | 20057.3178
100% | 0% | 0 |  |  |  |  | 45% | 3775.313 | 33.6012 | 60% |  | 60% |  | 60% | 22080.6365
99% | 0.03383% | 1.486 |  |  |  |  | 40% | 4072.8088 | 29.8677 | 55% |  | 55% |  | 55% | 24563.3211
98% | 0.07443% | 3.2692 |  |  |  |  | 35% | 4198.821 | 26.1342 | 50% |  | 50% |  | 50% | 24897.3046
97% | 0.1556% | 6.8356 |  |  |  |  | 30% | 4271.3374 | 22.4008 | 45% |  | 45% |  | 45% | 19216.2564
95% | 0.3992% | 17.5347 |  |  |  |  | 25% | 4321.8611 | 18.6673 | 40% |  | 40% |  | 40% | 9440.8591
90% | 1.793% | 78.7576 |  |  |  |  | 20% | 4353.067 | 14.9339 | 35% |  | 35% |  | 35% | 3528.4635
85% | 5.393% | 236.8672 |  |  |  |  | 15% | 4369.4129 | 11.2004 | 30% |  | 30% |  | 30% | 1759.7934
80% | 11.33% | 497.5104 |  |  |  |  | 10% | 4378.6261 | 7.4669 | 25% |  | 25% |  | 25% | 1037.457
75% | 18.3% | 803.6248 |  |  |  |  | 5% | 4391.7028 | 3.7335 | 20% |  | 20% |  | 20% | 524.2764
70% | 26.3% | 1155.2107 |  |  |  |  | 9.992e-14% | 4391.7028 | 7.461e-14 | 15% |  | 15% |  | 15% | 213.5941
65% | 35.36% | 1553.1596 | [7 empty] | 10% |  | 10% |  | 10% | 85.9924
60% | 46.14% | 2026.2996 | [7 empty] | 5% |  | 5% |  | 5% | 73.2323
55% | 59.16% | 2598.4068 | [7 empty] | 9.992e-14% |  | 9.992e-14% | 0 | 9.992e-14% | 0
50% | 73.62% | 3233.5201 | [7 empty] | Total E@R | 0 | Total E@R | 12444.9189 | Total E@R | 196109.2281
45% | 85.96% | 3775.313 | [7 empty] | Total WE@R | 0 | Total WE@R | 0.70122 | Total WE@R | 0.00072309
40% | 92.73% | 4072.8088
35% | 95.6% | 4198.821
30% | 97.25% | 4271.3374
25% | 98.4% | 4321.8611
20% | 99.11% | 4353.067
15% | 99.49% | 4369.4129
10% | 99.7% | 4378.6261
5% | 99.99% | 4391.7028
9.992e-14% | 99.99% | 4391.7028
Ratings (MVA) |  |  |  | Option Capacity
SCR (N) | 91.9 |  |  | Year | 2031
SCR (N-1) | 45 |  |  | SCR (N) | 91.9
SCR (N-2) | 0 |  |  | SCR (N-1) | 45
WCR (N) | 95.7 |  |  | SCR (N-2) | 0
WCR (N-1) | 49.1 |  |  | WCR (N) | 95.7
WCR (N-2) | 0 |  |  | WCR (N-1) | 49.1
|  |  |  | WCR (N-2) | 0
Planned Works
Year | 2031
Capacity (N) | 0
Capacity (N-1) | 0
Capacity (N-2) | 0
Power Factor
Value | 1
End of Sheet

## QA
Overall Status
Good
Number | Check Name | Status | Info
1 | Forecast | Good | Confirms POE10 forecast is higher than POE50
2 | Option Maximum Demand | Good | Confirms whether transfers, embedded generation, and demand management contribute to demand reduction when present
3 | EUE Base Case | Good | Confirms Do Nothing/Base Case EUE for FY31 is the same as the example / checks model in Modelling Steps Example Sheet
4 | Feeder Consumption | Good | Confirms if aggregated feeder energy consumption by customer category matches with total feeder energy consumption (excluding uncategorised consumption)

## Output for AusNet's NPV model
Involuntary load shedding (NER 5.17.1(c)(4)(ii))
Base Case
Cost
Option 1 - Do Nothing / Base Case | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Cost of EUE ($M) | 0.00021781 | 0.0098795 | 0.026377 | 0.036055 | 0.047559 | 0.065252 | 0.097943 | 0.13515 | 0.18945 | 0.27588 | 0.29461 | 0.31173 | 0.40597 | 0.56605 | 0.55688 | 0.55688 | 0.55688 | 0.55688 | 0.55688 | 0.55688 | 0.55688 | 0.55688 | 0.55688 | 0.55688 | 0.55688 | 0.55688 | 0.55688 | 0.55688 | 0.55688 | 0.55688
Total EUE (MWh) | 0.0056418 | 0.25591 | 0.68323 | 0.93391 | 1.2319 | 1.6902 | 2.537 | 3.5007 | 4.9073 | 7.146 | 7.6311 | 8.0746 | 10.5156 | 14.6621 | 14.4247 | 14.4247 | 14.4247 | 14.4247 | 14.4247 | 14.4247 | 14.4247 | 14.4247 | 14.4247 | 14.4247 | 14.4247 | 14.4247 | 14.4247 | 14.4247 | 14.4247 | 14.4247
Residual Values
Option 2 - 1A New PHS ZSS + Four new feeders | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Cost of Avoided EUE ($M) | 0.00021781 | 0.0098795 | 0.026377 | 5.7063e-05 | 8.1208e-05 | 0.00012583 | 0.0002206 | 0.00033752 | 0.00049913 | 0.002412 | 0.0010403 | 0.0013759 | 0.0017845 | 0.0036579 | 0.0028495 | 0.0028495 | 0.0028495 | 0.0028495 | 0.0028495 | 0.0028495 | 0.0028495 | 0.0028495 | 0.0028495 | 0.0028495 | 0.0028495 | 0.0028495 | 0.0028495 | 0.0028495 | 0.0028495 | 0.0028495
Total EUE (MWh) | 0.0056418 | 0.25591 | 0.68323 | 0.0014781 | 0.0021035 | 0.0032594 | 0.0057142 | 0.0087425 | 0.012929 | 0.062477 | 0.026947 | 0.035639 | 0.046222 | 0.09475 | 0.073809 | 0.073809 | 0.073809 | 0.073809 | 0.073809 | 0.073809 | 0.073809 | 0.073809 | 0.073809 | 0.073809 | 0.073809 | 0.073809 | 0.073809 | 0.073809 | 0.073809 | 0.073809
Option 3 - 2A PHM 3rd Tx + Switchroom + Three new feeders + OFR12 New Feeder | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Cost of Avoided EUE ($M) | 0.00021781 | 0.0098795 | 0.026377 | 1.9642e-06 | 3.2321e-06 | 5.3666e-06 | 9.4732e-06 | 1.5272e-05 | 2.4712e-05 | 4.09e-05 | 5.1049e-05 | 6.2368e-05 | 9.1192e-05 | 0.00014081 | 0.00015793 | 0.00015793 | 0.00015793 | 0.00015793 | 0.00015793 | 0.00015793 | 0.00015793 | 0.00015793 | 0.00015793 | 0.00015793 | 0.00015793 | 0.00015793 | 0.00015793 | 0.00015793 | 0.00015793 | 0.00015793
Total EUE (MWh) | 0.0056418 | 0.25591 | 0.68323 | 5.0878e-05 | 8.372e-05 | 0.00013901 | 0.00024538 | 0.00039558 | 0.00064011 | 0.0010594 | 0.0013223 | 0.0016155 | 0.0023621 | 0.0036473 | 0.0040907 | 0.0040907 | 0.0040907 | 0.0040907 | 0.0040907 | 0.0040907 | 0.0040907 | 0.0040907 | 0.0040907 | 0.0040907 | 0.0040907 | 0.0040907 | 0.0040907 | 0.0040907 | 0.0040907 | 0.0040907
Option 4 - 3A OFR 3rd Tx + Switchroom + Three new feeders + OFR12 New Feeder | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Cost of Avoided EUE ($M) | 0.00021781 | 0.0098795 | 0.026377 | 0.0018233 | 0.0025205 | 0.0039464 | 0.0083354 | 0.014167 | 0.026172 | 0.056469 | 0.049065 | 0.045132 | 0.070245 | 0.12709 | 0.1045 | 0.1045 | 0.1045 | 0.1045 | 0.1045 | 0.1045 | 0.1045 | 0.1045 | 0.1045 | 0.1045 | 0.1045 | 0.1045 | 0.1045 | 0.1045 | 0.1045 | 0.1045
Total EUE (MWh) | 0.0056418 | 0.25591 | 0.68323 | 0.047229 | 0.065286 | 0.10222 | 0.21591 | 0.36696 | 0.67793 | 1.4627 | 1.2709 | 1.169 | 1.8195 | 3.292 | 2.7067 | 2.7067 | 2.7067 | 2.7067 | 2.7067 | 2.7067 | 2.7067 | 2.7067 | 2.7067 | 2.7067 | 2.7067 | 2.7067 | 2.7067 | 2.7067 | 2.7067 | 2.7067
Option 5 - 4A LLG 2nd Tx + Switchroom + Three new feeders + OFR12 New Feeder | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Cost of Avoided EUE ($M) | 0.00021781 | 0.0098795 | 0.026377 | 5.7063e-05 | 8.1208e-05 | 0.00012583 | 0.0002206 | 0.00033752 | 0.00049913 | 0.002412 | 0.0010403 | 0.0013759 | 0.0017845 | 0.0036579 | 0.0028495 | 0.0028495 | 0.0028495 | 0.0028495 | 0.0028495 | 0.0028495 | 0.0028495 | 0.0028495 | 0.0028495 | 0.0028495 | 0.0028495 | 0.0028495 | 0.0028495 | 0.0028495 | 0.0028495 | 0.0028495
Total EUE (MWh) | 0.0056418 | 0.25591 | 0.68323 | 0.0014781 | 0.0021035 | 0.0032594 | 0.0057142 | 0.0087425 | 0.012929 | 0.062477 | 0.026947 | 0.035639 | 0.046222 | 0.09475 | 0.073809 | 0.073809 | 0.073809 | 0.073809 | 0.073809 | 0.073809 | 0.073809 | 0.073809 | 0.073809 | 0.073809 | 0.073809 | 0.073809 | 0.073809 | 0.073809 | 0.073809 | 0.073809
Option 6 - Non Network | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Cost of Avoided EUE ($M) | 3.0088e-05 | 0.00096519 | 0.0036506 | 0.0053312 | 0.0073742 | 0.0111 | 0.020288 | 0.031216 | 0.050619 | 0.091018 | 0.085193 | 0.080997 | 0.11824 | 0.19223 | 0.17043 | 0.17043 | 0.17043 | 0.17043 | 0.17043 | 0.17043 | 0.17043 | 0.17043 | 0.17043 | 0.17043 | 0.17043 | 0.17043 | 0.17043 | 0.17043 | 0.17043 | 0.17043
Total EUE (MWh) | 0.00077936 | 0.025001 | 0.09456 | 0.13809 | 0.19101 | 0.28753 | 0.52551 | 0.80858 | 1.3112 | 2.3576 | 2.2067 | 2.098 | 3.0628 | 4.9792 | 4.4146 | 4.4146 | 4.4146 | 4.4146 | 4.4146 | 4.4146 | 4.4146 | 4.4146 | 4.4146 | 4.4146 | 4.4146 | 4.4146 | 4.4146 | 4.4146 | 4.4146 | 4.4146
Option 7 - | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Cost of Avoided EUE ($M) | 0.00021781 | 0.0098795 | 0.026377 | 0.036055 | 0.047559 | 0.065252 | 0.097943 | 0.13515 | 0.18945 | 0.27588 | 0.29461 | 0.31173 | 0.40597 | 0.56605 | 0.55688 | 0.55688 | 0.55688 | 0.55688 | 0.55688 | 0.55688 | 0.55688 | 0.55688 | 0.55688 | 0.55688 | 0.55688 | 0.55688 | 0.55688 | 0.55688 | 0.55688 | 0.55688
Total EUE (MWh) | 0.0056418 | 0.25591 | 0.68323 | 0.93391 | 1.2319 | 1.6902 | 2.537 | 3.5007 | 4.9073 | 7.146 | 7.6311 | 8.0746 | 10.5156 | 14.6621 | 14.4247 | 14.4247 | 14.4247 | 14.4247 | 14.4247 | 14.4247 | 14.4247 | 14.4247 | 14.4247 | 14.4247 | 14.4247 | 14.4247 | 14.4247 | 14.4247 | 14.4247 | 14.4247
Option 8 - | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Cost of Avoided EUE ($M) | 0.00021781 | 0.0098795 | 0.026377 | 0.036055 | 0.047559 | 0.065252 | 0.097943 | 0.13515 | 0.18945 | 0.27588 | 0.29461 | 0.31173 | 0.40597 | 0.56605 | 0.55688 | 0.55688 | 0.55688 | 0.55688 | 0.55688 | 0.55688 | 0.55688 | 0.55688 | 0.55688 | 0.55688 | 0.55688 | 0.55688 | 0.55688 | 0.55688 | 0.55688 | 0.55688
Total EUE (MWh) | 0.0056418 | 0.25591 | 0.68323 | 0.93391 | 1.2319 | 1.6902 | 2.537 | 3.5007 | 4.9073 | 7.146 | 7.6311 | 8.0746 | 10.5156 | 14.6621 | 14.4247 | 14.4247 | 14.4247 | 14.4247 | 14.4247 | 14.4247 | 14.4247 | 14.4247 | 14.4247 | 14.4247 | 14.4247 | 14.4247 | 14.4247 | 14.4247 | 14.4247 | 14.4247

## Key Model Assumption & Inputs
Select ZSS & Region | PHM | Central | MTTR
Probability Weighting for 10% POE MDs | 30% |  |  | Central | North | East | For Analysis
Probability Weighting for 50% POE MDs | 70% |  | N-1 MTTR (years) | 0.3858 | 0.1418 | 0.3858 | 0.3858
First year of analysis | FY25 |  | N-2 MTTR (years) | 0.2344 | 0.049 | 0.2344 | 0.2344
Select Sensitivity Variant | Forecast Sensitivity
Base | 100% |  | PV Factor's |  |  | PoF Sensitvity
Options | Name |  | Summer | 1.33 |  | Varaint
Option 1 - Do Nothing / Base Case | Do Nothing / Base Case |  | Winter | 1.13 |  | Low | 50%
Option 2 - 1A New PHS ZSS + Four new feeders | 1A New PHS ZSS + Four new feeders
Option 3 - 2A PHM 3rd Tx + Switchroom + Three new feeders + OFR12 New Feeder | 2A PHM 3rd Tx + Switchroom + Three new feeders + OFR12 New Feeder |  | Demand Response
Option 4 - 3A OFR 3rd Tx + Switchroom + Three new feeders + OFR12 New Feeder | 3A OFR 3rd Tx + Switchroom + Three new feeders + OFR12 New Feeder |  | Average Rate % | 20%
Option 5 - 4A LLG 2nd Tx + Switchroom + Three new feeders + OFR12 New Feeder | 4A LLG 2nd Tx + Switchroom + Three new feeders + OFR12 New Feeder
Option 6 - Non Network | Non Network
Option 7 -
Option 8 -
Added Capacity (MVA) | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39
Added Capacity (MVA) Option 1 N | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 1 N-1 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 1 N-2 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 2 N | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 2 N-1 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 2 N-2 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 3 N |  |  |  | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45
Added Capacity (MVA) Option 3 N-1 |  |  |  | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45
Added Capacity (MVA) Option 3 N-2 |  |  |  | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45
Added Capacity (MVA) Option 4 N | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 4 N-1 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 4 N-2 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 5 N | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 5 N-1 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 5 N-2 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 6 N | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 6 N-1 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 6 N-2 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 7 N | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 7 N-1 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 7 N-2 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 8 N | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 8 N-1 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 8 N-2 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Embedded Generation (MVA) | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39
Avaliable Embedded Generation (MVA) Option 1 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Embedded Generation (MVA) Option 2 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Embedded Generation (MVA) Option 3 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Embedded Generation (MVA) Option 4 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Embedded Generation (MVA) Option 5 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Embedded Generation (MVA) Option 6 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Embedded Generation (MVA) Option 7 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Embedded Generation (MVA) Option 8 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Demand Management (MVA) | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39
Avaliable Demand Management (MVA) Option 1 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Demand Management (MVA) Option 2 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Demand Management (MVA) Option 3 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Demand Management (MVA) Option 4 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Demand Management (MVA) Option 5 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Demand Management (MVA) Option 6 | 7.7456 | 9.9603 | 10.5358 | 10.4984 | 10.4969 | 10.5537 | 10.7079 | 10.8089 | 10.9091 | 11.0267 | 11.1341 | 11.2396 | 11.2492 | 11.3728 | 11.2743
Added Demand Management (MVA) Option 7 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Demand Management (MVA) Option 8 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Transfers (MVA) | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39
Planned Transfers (MVA) Option 1 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Transfers (MVA) Option 2 |  |  |  | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29
Added Transfers (MVA) Option 3 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Transfers (MVA) Option 4 |  |  |  | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5
Added Transfers (MVA) Option 5 |  |  |  | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29
Added Transfers (MVA) Option 6 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Transfers (MVA) Option 7 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Transfers (MVA) Option 8 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Block Loads Not in Forecast (MVA) | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39
Block Loads (MVA) | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Base | FY25: 100%
High | FY25: 110%
Low | FY25: 90%

## Tx PoF
Transformer Failure Rates for individual Transformers
[5 empty] | 10 | 8 | 10 | 6 | 8 | 6 | 6 | 10 | 6
Zone | arm_asset_id | floc | user_status | Age | Major Winding insulation | Accelerated cellulose Aging | Winding insulating liquid | Hot metal fault covered by paper | Chemical contamination, degradation | Physical & chemical contamination, degradation | Physical contamination | Short Circuit Concern | OLTC | WMA Health Score | WMA CS | WMA effective age | WMA Beta | WMA Eta | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WGI | 30192717 | DS-WGI-TRNFMR-9000004493 |  | 59 | 5 | 3 | 1 | 5 | 2 | 1 | 5 | 5 | 5 | 351.4286 | 4 | 60 | 3.5 | 82 | 1.976% | 1.976% | 2.058% | 2.142% | 2.227% | 2.315% | 2.405% | 2.496% | 2.59% | 2.686% | 2.783% | 2.883% | 2.985% | 3.089% | 3.195% | 3.303% | 3.413% | 3.525% | 3.639% | 3.755% | 3.873% | 3.994% | 4.116% | 4.241% | 4.368% | 4.497% | 4.628% | 4.761% | 4.897% | 5.034%
WGI | 30111322 | DS-WGI-TRNFMR-9000003147 |  | 59 | 5 | 5 | 1 | 3 | 2 | 1 | 4 | 5 | 5 | 348.5714 | 3 | 44 | 3.5 | 82 | 0.9218% | 0.9218% | 0.9742% | 1.028% | 1.084% | 1.142% | 1.201% | 1.262% | 1.325% | 1.39% | 1.457% | 1.525% | 1.596% | 1.668% | 1.742% | 1.818% | 1.896% | 1.976% | 2.058% | 2.142% | 2.227% | 2.315% | 2.405% | 2.496% | 2.59% | 2.686% | 2.783% | 2.883% | 2.985% | 3.089%
EPG | 30026486 | DS-EPG-TRNFMR-9000010175 |  | 45 | 5 | 3 | 2 | 1 | 2 | 1 | 4 | 5 | 5 | 322.8571 | 3 | 44 | 3.5 | 84.05 | 0.8458% | 0.8458% | 0.8939% | 0.9436% | 0.9949% | 1.048% | 1.102% | 1.159% | 1.216% | 1.276% | 1.337% | 1.4% | 1.465% | 1.531% | 1.599% | 1.669% | 1.741% | 1.814% | 1.889% | 1.966% | 2.045% | 2.125% | 2.208% | 2.292% | 2.378% | 2.466% | 2.556% | 2.648% | 2.741% | 2.837%
EPG | 30058367 | DS-EPG-TRNFMR-9000010174 |  | 45 | 5 | 3 | 2 | 1 | 2 | 1 | 4 | 5 | 5 | 322.8571 | 3 | 44 | 3.5 | 84.05 | 0.8458% | 0.8458% | 0.8939% | 0.9436% | 0.9949% | 1.048% | 1.102% | 1.159% | 1.216% | 1.276% | 1.337% | 1.4% | 1.465% | 1.531% | 1.599% | 1.669% | 1.741% | 1.814% | 1.889% | 1.966% | 2.045% | 2.125% | 2.208% | 2.292% | 2.378% | 2.466% | 2.556% | 2.648% | 2.741% | 2.837%
WGI | 30475971 | DS-WGI-TRNFMR-9000007146 |  | 49 | 5 | 5 | 1 | 1 | 1 | 1 | 2 | 5 | 1 | 268.5714 | 3 | 44 | 3.5 | 82 | 0.9218% | 0.9218% | 0.9742% | 1.028% | 1.084% | 1.142% | 1.201% | 1.262% | 1.325% | 1.39% | 1.457% | 1.525% | 1.596% | 1.668% | 1.742% | 1.818% | 1.896% | 1.976% | 2.058% | 2.142% | 2.227% | 2.315% | 2.405% | 2.496% | 2.59% | 2.686% | 2.783% | 2.883% | 2.985% | 3.089%
EPG | 30209984 | DS-EPG-TRNFMR-9000007095 |  | 24 | 3 | 3 | 1 | 3 | 2 | 1 | 4 | 3 | 3 | 251.4286 | 3 | 44 | 3.5 | 84.05 | 0.8458% | 0.8458% | 0.8939% | 0.9436% | 0.9949% | 1.048% | 1.102% | 1.159% | 1.216% | 1.276% | 1.337% | 1.4% | 1.465% | 1.531% | 1.599% | 1.669% | 1.741% | 1.814% | 1.889% | 1.966% | 2.045% | 2.125% | 2.208% | 2.292% | 2.378% | 2.466% | 2.556% | 2.648% | 2.741% | 2.837%
CLN | 30338702 | DS-CLN-TRNFMR-9000006730 |  | 21 | 3 | 2 | 2 | 3 | 1 | 1 | 3 | 3 | 2 | 225.7143 | 2 | 24 | 3.5 | 84.05 | 0.1909% | 0.1909% | 0.211% | 0.2322% | 0.2547% | 0.2785% | 0.3035% | 0.3298% | 0.3575% | 0.3865% | 0.4168% | 0.4486% | 0.4817% | 0.5162% | 0.5522% | 0.5897% | 0.6286% | 0.669% | 0.7109% | 0.7543% | 0.7993% | 0.8458% | 0.8939% | 0.9436% | 0.9949% | 1.048% | 1.102% | 1.159% | 1.216% | 1.276%
CRE | 30165029 | DS-CRE-TRNFMR-9000525811 |  | 13 | 3 | 2 | 1 | 3 | 2 | 1 | 4 | 2 | 2 | 217.1429 | 2 | 24 | 3.5 | 84.05 | 0.1909% | 0.1909% | 0.211% | 0.2322% | 0.2547% | 0.2785% | 0.3035% | 0.3298% | 0.3575% | 0.3865% | 0.4168% | 0.4486% | 0.4817% | 0.5162% | 0.5522% | 0.5897% | 0.6286% | 0.669% | 0.7109% | 0.7543% | 0.7993% | 0.8458% | 0.8939% | 0.9436% | 0.9949% | 1.048% | 1.102% | 1.159% | 1.216% | 1.276%
LLG | 30359074 | DS-LLG-TRNFMR-9000007796 |  | 20 | 1 | 2 | 1 | 2 | 1 | 1 | 5 | 3 | 2 | 191.4286 | 2 | 24 | 3.5 | 84.05 | 0.1909% | 0.1909% | 0.211% | 0.2322% | 0.2547% | 0.2785% | 0.3035% | 0.3298% | 0.3575% | 0.3865% | 0.4168% | 0.4486% | 0.4817% | 0.5162% | 0.5522% | 0.5897% | 0.6286% | 0.669% | 0.7109% | 0.7543% | 0.7993% | 0.8458% | 0.8939% | 0.9436% | 0.9949% | 1.048% | 1.102% | 1.159% | 1.216% | 1.276%
CRE | 30380287 | DS-CRE-TRNFMR-9000525810 |  | 13 | 2 | 2 | 1 | 1 | 2 | 1 | 3 | 2 | 2 | 177.1429 | 2 | 24 | 3.5 | 84.05 | 0.1909% | 0.1909% | 0.211% | 0.2322% | 0.2547% | 0.2785% | 0.3035% | 0.3298% | 0.3575% | 0.3865% | 0.4168% | 0.4486% | 0.4817% | 0.5162% | 0.5522% | 0.5897% | 0.6286% | 0.669% | 0.7109% | 0.7543% | 0.7993% | 0.8458% | 0.8939% | 0.9436% | 0.9949% | 1.048% | 1.102% | 1.159% | 1.216% | 1.276%
CLN | 30000439 | DS-CLN-TRNFMR-9000001306 |  | 19 | 2 | 2 | 1 | 1 | 1 | 1 | 3 | 2 | 2 | 165.7143 | 2 | 24 | 3.5 | 84.05 | 0.1909% | 0.1909% | 0.211% | 0.2322% | 0.2547% | 0.2785% | 0.3035% | 0.3298% | 0.3575% | 0.3865% | 0.4168% | 0.4486% | 0.4817% | 0.5162% | 0.5522% | 0.5897% | 0.6286% | 0.669% | 0.7109% | 0.7543% | 0.7993% | 0.8458% | 0.8939% | 0.9436% | 0.9949% | 1.048% | 1.102% | 1.159% | 1.216% | 1.276%
OFR | 30035965 | DS-OFR-TRNFMR-9000014181 |  | 16 | 2 | 2 | 1 | 1 | 1 | 1 | 3 | 2 | 2 | 165.7143 | 2 | 24 | 3.5 | 84.05 | 0.1909% | 0.1909% | 0.211% | 0.2322% | 0.2547% | 0.2785% | 0.3035% | 0.3298% | 0.3575% | 0.3865% | 0.4168% | 0.4486% | 0.4817% | 0.5162% | 0.5522% | 0.5897% | 0.6286% | 0.669% | 0.7109% | 0.7543% | 0.7993% | 0.8458% | 0.8939% | 0.9436% | 0.9949% | 1.048% | 1.102% | 1.159% | 1.216% | 1.276%
KLO | 30002764 | DS-KLO-TRNFMR-9000412348 |  | 15 | 1 | 2 | 1 | 1 | 1 | 1 | 4 | 2 | 2 | 160 | 2 | 24 | 3.5 | 84.05 | 0.1909% | 0.1909% | 0.211% | 0.2322% | 0.2547% | 0.2785% | 0.3035% | 0.3298% | 0.3575% | 0.3865% | 0.4168% | 0.4486% | 0.4817% | 0.5162% | 0.5522% | 0.5897% | 0.6286% | 0.669% | 0.7109% | 0.7543% | 0.7993% | 0.8458% | 0.8939% | 0.9436% | 0.9949% | 1.048% | 1.102% | 1.159% | 1.216% | 1.276%
OFR | 30221642 | DS-OFR-TRNFMR-9000016122 |  | 16 | 1 | 2 | 1 | 1 | 1 | 1 | 3 | 2 | 2 | 151.4286 | 2 | 24 | 3.5 | 84.05 | 0.1909% | 0.1909% | 0.211% | 0.2322% | 0.2547% | 0.2785% | 0.3035% | 0.3298% | 0.3575% | 0.3865% | 0.4168% | 0.4486% | 0.4817% | 0.5162% | 0.5522% | 0.5897% | 0.6286% | 0.669% | 0.7109% | 0.7543% | 0.7993% | 0.8458% | 0.8939% | 0.9436% | 0.9949% | 1.048% | 1.102% | 1.159% | 1.216% | 1.276%
KLO | 30208816 | DS-KLO-TRNFMR-9000412347 |  | 15 | 1 | 2 | 1 | 1 | 1 | 1 | 3 | 2 | 2 | 151.4286 | 2 | 24 | 3.5 | 84.05 | 0.1909% | 0.1909% | 0.211% | 0.2322% | 0.2547% | 0.2785% | 0.3035% | 0.3298% | 0.3575% | 0.3865% | 0.4168% | 0.4486% | 0.4817% | 0.5162% | 0.5522% | 0.5897% | 0.6286% | 0.669% | 0.7109% | 0.7543% | 0.7993% | 0.8458% | 0.8939% | 0.9436% | 0.9949% | 1.048% | 1.102% | 1.159% | 1.216% | 1.276%
PHM | 32944656 | DS-PHM-TRNFMR-9000004393 |  | 8 | 2 | 2 | 1 | 1 | 1 | 1 | 3 | 1 | 1 | 142.8571 | 1 | 8 | 3.5 | 84.05 | 0.01357% | 0.01357% | 0.01791% | 0.023% | 0.02887% | 0.03555% | 0.04308% | 0.0515% | 0.06084% | 0.07112% | 0.08238% | 0.09465% | 0.1079% | 0.1223% | 0.1378% | 0.1543% | 0.172% | 0.1909% | 0.211% | 0.2322% | 0.2547% | 0.2785% | 0.3035% | 0.3298% | 0.3575% | 0.3865% | 0.4168% | 0.4486% | 0.4817% | 0.5162%
PHM | 32944654 | DS-PHM-TRNFMR-9000007050 |  | 8 | 2 | 2 | 1 | 1 | 1 | 1 | 3 | 1 | 1 | 142.8571 | 1 | 8 | 3.5 | 84.05 | 0.01357% | 0.01357% | 0.01791% | 0.023% | 0.02887% | 0.03555% | 0.04308% | 0.0515% | 0.06084% | 0.07112% | 0.08238% | 0.09465% | 0.1079% | 0.1223% | 0.1378% | 0.1543% | 0.172% | 0.1909% | 0.211% | 0.2322% | 0.2547% | 0.2785% | 0.3035% | 0.3298% | 0.3575% | 0.3865% | 0.4168% | 0.4486% | 0.4817% | 0.5162%

## AER VCR Rates(2024)
Category | Rate | Notes
Dec 24 AER VCR ($/kWh) - Res | 49.23 | Vic Av Res
Dec 24 AER VCR ($/kWh) - Com | 34.39 | Vic Av Com
Dec 24 AER VCR ($/kWh) - Ind | 33.49 | Vic Av Ind
Dec 24 AER VCR ($/kWh) - Agr | 22.25 | Vic Av Agr

## Customer No. and Vol per Feeder
CUSTOMER_CLASS | Feeder | VOL | CUST_NO | ZSS | Customer mix received from AusNet Financial Planning & Strategy on 25/7/2025
COMMERCIAL | bra11 | 9860526.7854 | 168 | bra
COMMERCIAL | bge13 | 654988.62 | 45 | bge
COMMERCIAL | phi11 | 1878610.03 | 37 | phi
NCONUML | moe11 | 47447.48 | 18 | moe
NCONUML | drn13 | 27414.73 | 17 | drn
COMMERCIAL | smg34 | 5224461.8 | 1 | smg
FARM | wgl13 | 901266.5312 | 97 | wgl
FARM | msd2 | 2808295.5668 | 471 | msd
NCONUML | elm34 | 86758.8 | 34 | elm
| rwt36 | 703.54 | 2 | rwt
COMMERCIAL | lga41 | 1099100.22 | 2 | lga
| bdl33 | 4298.82 | 8 | bdl
NCONUML | smr14 | 27225.34 | 18 | smr
COMMERCIAL | cln24 | 4484028.8333 | 290 | cln
RESIDENTL | ofr14 | 13024383.6958 | 3554 | ofr
NCONUML | bdl43 | 100361.9983 | 38 | bdl
| ofr22 | 16469.09 | 22 | ofr
NCONUML | rwn33 | 8721.79 | 7 | rwn
LIGHTING | hpk12 | 342838 | 1 | hpk
COMMERCIAL | bra23 | 6262297.01 | 84 | bra
FARM | tt1 | 1865.76 | 1 | tt
LIGHTING | mfa14 | 787800.53 | 1 | mfa
RESIDENTL | brt22 | 9968534.1043 | 1376 | brt
RESIDENTL | mwl25 | 4092575.372 | 493 | mwl
NCONUML | wgi22 | 83961.44 | 23 | wgi
INDUSTRIAL | ldl22 | 4379901.5885 | 45 | ldl
RESIDENTL | phm22 | 3628742.5283 | 796 | phm
FARM | mfa23 | 2691321.6324 | 201 | mfa
NCONUML | rwn32 | 60415.37 | 23 | rwn
FARM | cre22 | 55644.16 | 17 | cre
RESIDENTL | elm24 | 17367685.5307 | 2999 | elm
COMMERCIAL | tt9 | 7181168.3052 | 213 | tt
COMMERCIAL | kms12 | 15257134.8455 | 395 | kms
NCONUML | cyn31 | 24759.23 | 14 | cyn
| llg12 | 26420.7189 | 15 | llg
LIGHTING | ruba22 | 247422.69 | 1 | ruba
RESIDENTL | wt12 | 10803758.701 | 2579 | wt
COMMERCIAL | bwn14 | 6975240.1 | 156 | bwn
NCONUML | bge12 | 37366.03 | 11 | bge
NCONUML | rwn24 | 30489.76 | 21 | rwn
FARM | sfs1 | 113380.09 | 9 | sfs
| bwr13 | 80076.52 | 46 | bwr
FARM | wt13 | 37228.86 | 3 | wt
FARM | cre23 | 226478.55 | 9 | cre
COMMERCIAL | rwn22 | 1886562.0146 | 72 | rwn
| tgn23 | 13898.1302 | 15 | tgn
FARM | ldl22 | 7887.95 | 1 | ldl
RESIDENTL | fgy21 | 7153989.4877 | 1047 | fgy
FARM | mjg11 | 735019.886 | 74 | mjg
| ldl14 | 17432.2687 | 11 | ldl
INDUSTRIAL | ldl24 | 64751.4 | 12 | ldl
| sle13 | 253.3245 | 2 | sle
FARM | moe21 | 6301170.9744 | 504 | moe
FARM | bge23 | 671977.1074 | 66 | bge
RESIDENTL | elm32 | 19949095.4752 | 2463 | elm
COMMERCIAL | ftr12 | 1975462.7263 | 113 | ftr
RESIDENTL | lyd12 | 6657897.88 | 1592 | lyd
RESIDENTL | epg31 | 11862355.3417 | 3027 | epg
NCONUML | ofr11 | 57102.89 | 18 | ofr
FARM | moe11 | 65350.2807 | 7 | moe
FARM | nla32 | 1181128.1259 | 84 | nla
FARM | smr24 | 4141783.4574 | 392 | smr
RESIDENTL | fgy13 | 7970231.1446 | 1518 | fgy
FARM | bdl41 | 1305847.5951 | 258 | bdl
NCONUML | elm23 | 62172.37 | 40 | elm
| elm22 | 20617.5429 | 26 | elm
NCONUML | cre21 | 58240.1 | 18 | cre
FARM | phm32 | 50851.13 | 8 | phm
INDUSTRIAL | lga21 | 208132.02 | 16 | lga
INDUSTRIAL | nrn13 | 39703.59 | 6 | nrn
RESIDENTL | hpk22 | 18949862.0449 | 4569 | hpk
NCONUML | cyn13 | 17637.49 | 6 | cyn
COMMERCIAL | cre31 | 14851829.6913 | 363 | cre
COMMERCIAL | epg32 | 5001490.9226 | 156 | epg
| phm32 | 41386.12 | 47 | phm
NCONUML | wo33 | 6875.31 | 2 | wo
FARM | wgl21 | 5056187.7677 | 366 | wgl
INDUSTRIAL | cre22 | 240829.25 | 4 | cre
RESIDENTL | wgi34 | 3671110.7601 | 570 | wgi
INDUSTRIAL | ldl12 | 10352583.7 | 7 | ldl
INDUSTRIAL | wyk12 | 149433.7 | 6 | wyk
INDUSTRIAL | cyn14 | 23200.151 | 3 | cyn
| wo11 | 4136.2425 | 3 | wo
| msd4 | 20521.76 | 37 | msd
FARM | mby12 | 52034.88 | 19 | mby
COMMERCIAL | rwt22 | 7145877.6761 | 143 | rwt
COMMERCIAL | wo12 | 23719023.8 | 1 | wo
RESIDENTL | wn2 | 17414453.5902 | 3500 | wn
COMMERCIAL | wots25 | 3483725.2811 | 72 | wots
RESIDENTL | bwr33 | 46024.67 | 2 | bwr
RESIDENTL | wn3 | 12349888.6736 | 2099 | wn
RESIDENTL | bn24 | 2992797.8263 | 559 | bn
| bra21 | 41455.7142 | 65 | bra
INDUSTRIAL | hpk14 | 16381.88 | 4 | hpk
RESIDENTL | epg32 | 14811809.1158 | 3829 | epg
COMMERCIAL | cln14 | 10141314.5039 | 129 | cln
FARM | smg31 | 14995.46 | 5 | smg
INDUSTRIAL | drn22 | 2117102.6666 | 12 | drn
NCONUML | drn12 | 43785.8374 | 16 | drn
INDUSTRIAL | fgy34 | 128392.6893 | 5 | fgy
NCONUML | fgy31 | 6707.46 | 4 | fgy
| wt8 | 7059.0655 | 13 | wt
| bwn12 | 6521.57 | 6 | bwn
COMMERCIAL | myt12 | 10774273.2986 | 307 | myt
COMMERCIAL | ldl21 | 5339830.9491 | 117 | ldl
| cln21 | 32425.72 | 66 | cln
INDUSTRIAL | fgy14 | 162921.94 | 7 | fgy
| tgn12 | 22490.11 | 3 | tgn
COMMERCIAL | epg12 | 8214339.5389 | 163 | epg
NCONUML | moe23 | 69334.91 | 17 | moe
FARM | cyn14 | 7715.15 | 1 | cyn
RESIDENTL | lyd14 | 10580841.4317 | 1203 | lyd
COMMERCIAL | smg23 | 21963007.1063 | 434 | smg
INDUSTRIAL | bra33 | 2076536.62 | 34 | bra
INDUSTRIAL | rwt14 | 2271244.55 | 44 | rwt
COMMERCIAL | lga14 | 2174194.9787 | 115 | lga
INDUSTRIAL | myt22 | 3176.32 | 3 | myt
FARM | cyn21 | 10230.57 | 2 | cyn
| klo24 | 65411.35 | 119 | klo
COMMERCIAL | brt21 | 6571769.7252 | 216 | brt
FARM | kms11 | 665243.0597 | 75 | kms
| elm34 | 25999.6869 | 33 | elm
INDUSTRIAL | mwl11 | 366139.79 | 15 | mwl
INDUSTRIAL | lyd14 | 80895.88 | 12 | lyd
LIGHTING | cpk11 | 1086.88 | 1 | cpk
NCONUML | fgy23 | 34402.31 | 12 | fgy
| bra32 | 15753.982 | 22 | bra
RESIDENTL | epg12 | 26391788.5687 | 6905 | epg
COMMERCIAL | cyn24 | 15647575.1097 | 304 | cyn
INDUSTRIAL | phm21 | 511727.73 | 19 | phm
NCONUML | ftr12 | 5424.58 | 5 | ftr
| bwa23 | 5447.575 | 8 | bwa
NCONUML | llg12 | 4182.92 | 3 | llg
COMMERCIAL | drn13 | 5299129.684 | 96 | drn
INDUSTRIAL | hpk21 | 31624.71 | 8 | hpk
INDUSTRIAL | wyk23 | 1500537.4334 | 28 | wyk
RESIDENTL | lga12 | 4152631.2896 | 644 | lga
RESIDENTL | cyn11 | 6009338.551 | 1440 | cyn
NCONUML | fgy24 | 70027.41 | 43 | fgy
| moe23 | 74726.3012 | 22 | moe
COMMERCIAL | elm24 | 3531802.26 | 46 | elm
LIGHTING | elm33 | 1000.47 | 1 | elm
RESIDENTL | smg23 | 6500499.5996 | 1411 | smg
FARM | msd4 | 1851245.0012 | 252 | msd
COMMERCIAL | lga24 | 21693950.3379 | 92 | lga
COMMERCIAL | ldl11 | 7360578.73 | 74 | ldl
NCONUML | rve13 | 29515.6981 | 24 | rve
COMMERCIAL | trc01 | 365242.5067 | 42 | trc
COMMERCIAL | wt15 | 1164715.6471 | 30 | wt
COMMERCIAL | bra14 | 811059.401 | 59 | bra
| ftr21 | 17034.7542 | 20 | ftr
RESIDENTL | bra23 | 7643359.408 | 1736 | bra
INDUSTRIAL | cpk11 | 59065.36 | 14 | cpk
INDUSTRIAL | hpk12 | 531460.54 | 46 | hpk
FARM | fgy23 | 137430.23 | 3 | fgy
INDUSTRIAL | tt4 | 77015.1997 | 16 | tt
FARM | cpk22 | 45399.86 | 6 | cpk
INDUSTRIAL | yn31 | 1004932.7745 | 6 | yn
FARM | myt22 | 1873055.6433 | 191 | myt
| cpk12 | 20188.43 | 32 | cpk
RESIDENTL | bwa22 | 6606654.3694 | 1106 | bwa
| mfa34 | 1434.55 | 6 | mfa
| nla31 | 4780.58 | 5 | nla
FARM | mdg1 | 36782.2 | 6 | mdg
RESIDENTL | mwl21 | 3605605.4081 | 859 | mwl
COMMERCIAL | phm33 | 14452041.4603 | 180 | phm
INDUSTRIAL | ofr23 | 154535.41 | 17 | ofr
INDUSTRIAL | elm21 | 177435.466 | 7 | elm
INDUSTRIAL | wt5 | 89.11 | 1 | wt
FARM | llg13 | 1917532.2118 | 152 | llg
INDUSTRIAL | klk21 | 41156.68 | 10 | klk
NCONUML | wt9 | 48247.64 | 17 | wt
FARM | mdi1 | 153288.2952 | 21 | mdi
INDUSTRIAL | nrn14 | 19245.31 | 5 | nrn
INDUSTRIAL | wgl12 | 500659.11 | 16 | wgl
FARM | fgy13 | 80534.51 | 6 | fgy
INDUSTRIAL | bwr14 | 1597974.48 | 1 | bwr
LIGHTING | bn11 | 103048.5 | 1 | bn
RESIDENTL | klo14 | 40411755.0117 | 10946 | klo
RESIDENTL | fgy33 | 9101921.8028 | 1763 | fgy
LIGHTING | cre31 | 2308168.51 | 1 | cre
RESIDENTL | wn5 | 8555201.9981 | 1156 | wn
COMMERCIAL | mfa22 | 5299491.9938 | 179 | mfa
COMMERCIAL | lyd11 | 3798691.89 | 62 | lyd
LIGHTING | bn24 | 2014.81 | 1 | bn
COMMERCIAL | cf1 | 9360587.4941 | 189 | cf
FARM | lga11 | 4665290.6529 | 555 | lga
RESIDENTL | lyd13 | 10895753.2364 | 2051 | lyd
NCONUML | cre33 | 35388.67 | 19 | cre
| smg32 | 685.05 | 3 | smg
INDUSTRIAL | cyn11 | 1966971.1028 | 55 | cyn
COMMERCIAL | wn2 | 10157994.9798 | 156 | wn
| phm21 | 32464.7212 | 22 | phm
| sfs1 | 13890.635 | 10 | sfs
NCONUML | tt12 | 15011.94 | 8 | tt
FARM | lga21 | 1065599.6961 | 147 | lga
| ldl12 | 52350.63 | 6 | ldl
INDUSTRIAL | smg31 | 231921 | 9 | smg
LIGHTING | myt12 | 813470.88 | 6 | myt
| smr24 | 66801.9 | 34 | smr
NCONUML | cre32 | 49453.4427 | 23 | cre
INDUSTRIAL | bdl44 | 2337630.2078 | 41 | bdl
| rve11 | 302066.1 | 12 | rve
FARM | wo31 | 3245.01 | 1 | wo
LIGHTING | ofr13 | 171706.2 | 2 | ofr
RESIDENTL | tt9 | 13181645.445 | 3553 | tt
COMMERCIAL | wgl11 | 13522117.9742 | 216 | wgl
COMMERCIAL | hpk24 | 15242696.9791 | 271 | hpk
COMMERCIAL | bwr34 | 12222544.1423 | 437 | bwr
NCONUML | nla34 | 19980.17 | 11 | nla
FARM | bwr24 | 9303.26 | 1 | bwr
| wgi23 | 15962.8799 | 36 | wgi
RESIDENTL | cln13 | 18593732.5659 | 6830 | cln
RESIDENTL | lga13 | 1879247.7046 | 295 | lga
RESIDENTL | cnr3 | 108696.4186 | 22 | cnr
| wgl12 | 112644.3661 | 43 | wgl
COMMERCIAL | cln12 | 8203266.5202 | 86 | cln
NCONUML | ofr21 | 100427.35 | 34 | ofr
RESIDENTL | drn24 | 10021102.8231 | 2473 | drn
COMMERCIAL | cyn31 | 1940881.6507 | 53 | cyn
NCONUML | ldl24 | 34534.3 | 19 | ldl
COMMERCIAL | ofr13 | 9302944.2987 | 197 | ofr
| wots13 | 58538.6484 | 32 | wots
| cpk23 | 23360.0808 | 24 | cpk
NCONUML | cln11 | 4587.8606 | 9 | cln
| wt15 | 51811.4 | 11 | wt
COMMERCIAL | epg24 | 26841528 | 1 | epg
FARM | drn22 | 329138.5031 | 52 | drn
| mfa31 | 16838.31 | 22 | mfa
COMMERCIAL | bra32 | 4055727.3404 | 158 | bra
COMMERCIAL | cpk21 | 14974774.5549 | 258 | cpk
INDUSTRIAL | myt21 | 335981.9667 | 19 | myt
FARM | nrn14 | 139044.47 | 14 | nrn
| wt5 | 22324.85 | 13 | wt
INDUSTRIAL | mfa23 | 139940.33 | 14 | mfa
FARM | wyk12 | 2634438.6357 | 233 | wyk
RESIDENTL | epg23 | 3653084.6682 | 932 | epg
COMMERCIAL | tgn11 | 2525258.71 | 85 | tgn
| wt13 | 22551.0062 | 37 | wt
| cyn13 | 10533.28 | 7 | cyn
INDUSTRIAL | fgy13 | 259435.94 | 2 | fgy
RESIDENTL | cln12 | 23908773.0216 | 6775 | cln
COMMERCIAL | brt22 | 9042592.2197 | 210 | brt
COMMERCIAL | rwt25 | 7526054.6961 | 146 | rwt
FARM | mfa31 | 218040.8355 | 21 | mfa
COMMERCIAL | cln22 | 3248277.4443 | 37 | cln
NCONUML | bdl33 | 22970.8 | 8 | bdl
COMMERCIAL | fgy12 | 74427.591 | 4 | fgy
RESIDENTL | mwl16 | 8188909.2298 | 1700 | mwl
INDUSTRIAL | moe25 | 612177.9824 | 16 | moe
COMMERCIAL | tt7 | 24970154.3491 | 341 | tt
INDUSTRIAL | bwr24 | 4118148.7987 | 125 | bwr
RESIDENTL | moe13 | 2791200.4315 | 357 | moe
FARM | wyk24 | 694188.3378 | 94 | wyk
NCONUML | wo14 | 36996.26 | 12 | wo
RESIDENTL | bra13 | 6470560.8911 | 1572 | bra
RESIDENTL | tt7 | 39398.92 | 9 | tt
FARM | epg34 | 15821.91 | 5 | epg
INDUSTRIAL | yn35 | 6582.38 | 2 | yn
NCONUML | bwa23 | 749.23 | 1 | bwa
FARM | sle13 | 1461316.56 | 213 | sle
COMMERCIAL | cpk13 | 4127340.5971 | 198 | cpk
INDUSTRIAL | ldl14 | 1064067.7426 | 16 | ldl
| rwt14 | 62105.3312 | 18 | rwt
LIGHTING | hpk13 | 14513.85 | 1 | hpk
RESIDENTL | klk22 | 940238.19 | 128 | klk
COMMERCIAL | mwl25 | 259300.06 | 16 | mwl
| mjg11 | 96977.3135 | 7 | mjg
RESIDENTL | hpk24 | 4867180.3451 | 1284 | hpk
FARM | ftr21 | 6703423.0704 | 705 | ftr
FARM | smr12 | 441800.25 | 44 | smr
FARM | bwr13 | 73574.54 | 13 | bwr
| ldl22 | 9241.11 | 9 | ldl
FARM | wo22 | 35676.335 | 7 | wo
NCONUML | moe12 | 9318.9 | 3 | moe
INDUSTRIAL | bdl31 | 1561951.6978 | 44 | bdl
COMMERCIAL | ofr14 | 8393968.2568 | 77 | ofr
NCONUML | tgn23 | 48562.71 | 16 | tgn
NCONUML | cyn21 | 25127.29 | 5 | cyn
FARM | phm34 | 22945.58 | 3 | phm
INDUSTRIAL | cyn33 | 36519.92 | 4 | cyn
LIGHTING | bm8b32 | 1070.04 | 1 | bmb
FARM | llg12 | 5311057.9488 | 488 | llg
NCONUML | rwt32 | 94072.85 | 46 | rwt
COMMERCIAL | myt11 | 912988.53 | 42 | myt
INDUSTRIAL | cpk22 | 129954.91 | 11 | cpk
| cre22 | 20388.051 | 33 | cre
RESIDENTL | ldl21 | 5451727.7741 | 1502 | ldl
FARM | bdl44 | 8189534.7866 | 736 | bdl
INDUSTRIAL | bn11 | 1899511.3657 | 45 | bn
INDUSTRIAL | wgi31 | 152399.6 | 19 | wgi
INDUSTRIAL | mdi1 | 16.0426 | 1 | mdi
| ofr11 | 90492.4817 | 79 | ofr
LIGHTING | kms11 | 547479.19 | 1 | kms
RESIDENTL | phi12 | 18738852.0082 | 4967 | phi
COMMERCIAL | bwr12 | 7897915.6022 | 287 | bwr
FARM | msd1 | 2520603.4144 | 354 | msd
COMMERCIAL | tgn44 | 4662112.18 | 89 | tgn
NCONUML | uwy1 | 29815.85 | 15 | uwy
NCONUML | lga22 | 54192.29 | 17 | lga
NCONUML | lga23 | 17186.13 | 6 | lga
INDUSTRIAL | hpk13 | 1952010.47 | 3 | hpk
FARM | drn23 | 391232.6382 | 58 | drn
FARM | ldl23 | 5910515.5529 | 453 | ldl
FARM | bdl31 | 55336.85 | 12 | bdl
RESIDENTL | bwr34 | 11176240.016 | 2984 | bwr
RESIDENTL | ofr13 | 5689359.8131 | 1445 | ofr
NCONUML | bra21 | 145563.002 | 72 | bra
COMMERCIAL | cf2 | 1114027.3697 | 138 | cf
RESIDENTL | bdl32 | 16368580.902 | 3124 | bdl
COMMERCIAL | smr22 | 10240657.5236 | 95 | smr
NCONUML | rve12 | 34563.18 | 21 | rve
COMMERCIAL | cnr3 | 208527.63 | 11 | cnr
| elm25 | 9741.0155 | 15 | elm
INDUSTRIAL | lyd13 | 30651.21 | 5 | lyd
INDUSTRIAL | mby12 | 279353.09 | 7 | mby
INDUSTRIAL | epg21 | 31298.6803 | 2 | epg
FARM | wgl12 | 7817936.5802 | 624 | wgl
COMMERCIAL | moe13 | 1401894.0174 | 82 | moe
RESIDENTL | lga14 | 7239522.4699 | 1158 | lga
RESIDENTL | epg35 | 308209.78 | 22 | epg
FARM | hpk14 | 29274.39 | 5 | hpk
LIGHTING | bn22 | 341591.58 | 1 | bn
NCONUML | bge11 | 85890.46 | 45 | bge
NCONUML | wt7 | 26985.19 | 18 | wt
| wo31 | 27869.149 | 41 | wo
INDUSTRIAL | elm32 | 759094.4258 | 68 | elm
NCONUML | cre23 | 95638.5 | 25 | cre
RESIDENTL | cln23 | 19292170.1488 | 4992 | cln
| lga21 | 17263.28 | 18 | lga
NCONUML | bwn12 | 35975.24 | 12 | bwn
| fgy31 | 1671.76 | 6 | fgy
NCONUML | ftr23 | 39743.6852 | 30 | ftr
NCONUML | smg21 | 9405.11 | 5 | smg
RESIDENTL | epg13 | 24819451.0174 | 7299 | epg
RESIDENTL | ruba22 | 5955886.59 | 1080 | ruba
INDUSTRIAL | bwr23 | 1917390.4058 | 110 | bwr
COMMERCIAL | bn23 | 4585306.9 | 117 | bn
| fgy24 | 60212.15 | 95 | fgy
LIGHTING | brt21 | 27441.26 | 1 | brt
COMMERCIAL | mby14 | 13812.56 | 3 | mby
RESIDENTL | drn21 | 15235611.8074 | 3585 | drn
RESIDENTL | nrn11 | 3368324.1063 | 703 | nrn
NCONUML | cln21 | 97183.1897 | 28 | cln
NCONUML | tgn12 | 26909.78 | 9 | tgn
FARM | moe22 | 48531.59 | 7 | moe
RESIDENTL | bra14 | 17287022.2386 | 4193 | bra
RESIDENTL | brt21 | 8587133.8204 | 1368 | brt
INDUSTRIAL | ldl23 | 2181365.61 | 45 | ldl
NCONUML | klo24 | 121410.57 | 41 | klo
INDUSTRIAL | wt8 | 22231.36 | 5 | wt
| bdl41 | 27628.4721 | 32 | bdl
COMMERCIAL | sle14 | 13227565.7623 | 343 | sle
| smr14 | 17300.3116 | 19 | smr
INDUSTRIAL | llg11 | 439641.21 | 9 | llg
| wgi22 | 13903.1 | 35 | wgi
NCONUML | moe22 | 34069.45 | 10 | moe
| ftr12 | 15921.46 | 17 | ftr
COMMERCIAL | epg11 | 902129.45 | 16 | epg
RESIDENTL | cpk13 | 21255549.7429 | 4974 | cpk
| fgy23 | 9273.25 | 10 | fgy
FARM | cyn12 | 9105.46 | 2 | cyn
INDUSTRIAL | rwn31 | 527467.66 | 22 | rwn
RESIDENTL | bm8b32 | 357081.227 | 62 | bmb
FARM | ruba22 | 1060033.1321 | 158 | ruba
INDUSTRIAL | cnr1 | 88077.93 | 3 | cnr
FARM | cpk12 | 972803.9358 | 91 | cpk
COMMERCIAL | wo14 | 14658340.7796 | 304 | wo
COMMERCIAL | tt5 | 6134357.4395 | 224 | tt
INDUSTRIAL | wo11 | 18559582.74 | 7 | wo
| wgl23 | 17798.7289 | 12 | wgl
NCONUML | cyn12 | 64730.9 | 21 | cyn
COMMERCIAL | bwr33 | 3515549.759 | 83 | bwr
COMMERCIAL | cyn22 | 10287381.4837 | 183 | cyn
COMMERCIAL | rwt32 | 5482054.6843 | 198 | rwt
INDUSTRIAL | nrn12 | 7260.73 | 2 | nrn
RESIDENTL | cln22 | 8137131.1146 | 3340 | cln
| kms12 | 36774.1343 | 44 | kms
| cyn24 | 12784.0842 | 11 | cyn
| smg33 | 11524.64 | 21 | smg
COMMERCIAL | rve11 | 18192998.0721 | 274 | rve
FARM | wt5 | 8146.48 | 2 | wt
INDUSTRIAL | bge23 | 983662.8538 | 7 | bge
| msd2 | 9983.6 | 13 | msd
| bra12 | 98134.87 | 2 | bra
RESIDENTL | hpk23 | 13762355.5073 | 3377 | hpk
COMMERCIAL | smr13 | 15057236.7589 | 394 | smr
INDUSTRIAL | rwt21 | 372221.49 | 45 | rwt
FARM | rve12 | 22362.86 | 5 | rve
NCONUML | fgy32 | 32042.28 | 18 | fgy
INDUSTRIAL | smr12 | 37387308.69 | 3 | smr
NCONUML | mfa34 | 19451.19 | 8 | mfa
FARM | wots13 | 4844280.0942 | 510 | wots
COMMERCIAL | drn21 | 3220798.94 | 52 | drn
INDUSTRIAL | wo31 | 765.77 | 1 | wo
| fgy32 | 8528.5063 | 10 | fgy
INDUSTRIAL | bwr32 | 3058614 | 72 | bwr
| elm23 | 20831.6 | 30 | elm
INDUSTRIAL | mwl12 | 574569.29 | 12 | mwl
RESIDENTL | cpk21 | 7771248.352 | 1679 | cpk
COMMERCIAL | wots11 | 6621581.9604 | 243 | wots
INDUSTRIAL | ftr21 | 313604.8 | 24 | ftr
NCONUML | lyd11 | 43059.75 | 9 | lyd
FARM | phm21 | 25361.56 | 3 | phm
INDUSTRIAL | wyk13 | 453974.55 | 15 | wyk
INDUSTRIAL | mdg1 | 21781.42 | 1 | mdg
INDUSTRIAL | tt1 | 7434378.9861 | 77 | tt
INDUSTRIAL | wgi34 | 1206209.57 | 8 | wgi
LIGHTING | wgi33 | 1050486.0487 | 2 | wgi
COMMERCIAL | wgl15 | 27996457.3831 | 596 | wgl
RESIDENTL | bge23 | 16900476.9279 | 2094 | bge
INDUSTRIAL | bwr13 | 2417661.2776 | 147 | bwr
NCONUML | epg23 | 28250.73 | 7 | epg
INDUSTRIAL | drn14 | 25996.95 | 2 | drn
RESIDENTL | drn14 | 23831050.9741 | 4399 | drn
RESIDENTL | rwt31 | 5842296.4371 | 1436 | rwt
COMMERCIAL | drn24 | 1717660.9 | 35 | drn
FARM | epg14 | 3614.72 | 1 | epg
RESIDENTL | smr13 | 11225814.5464 | 2447 | smr
COMMERCIAL | wots12 | 14359758.4732 | 371 | wots
COMMERCIAL | klk11 | 3080934.4269 | 114 | klk
NCONUML | mwl14 | 31252.61 | 13 | mwl
INDUSTRIAL | sle11 | 266690.1 | 32 | sle
NCONUML | epg31 | 41319.36 | 24 | epg
RESIDENTL | cf1 | 4176161.3871 | 493 | cf
INDUSTRIAL | phm34 | 816155.12 | 6 | phm
FARM | rwn34 | 20402.21 | 4 | rwn
| mby12 | 1524.95 | 3 | mby
RESIDENTL | wgi31 | 14866992.8529 | 3617 | wgi
RESIDENTL | wots25 | 16858284.9544 | 3532 | wots
RESIDENTL | cre33 | 21876811.5892 | 4235 | cre
RESIDENTL | fgy34 | 4606270.9018 | 975 | fgy
RESIDENTL | cyn32 | 15011504.2579 | 3573 | cyn
RESIDENTL | klk11 | 9194980.7775 | 1227 | klk
INDUSTRIAL | fgy33 | 1452360.19 | 13 | fgy
INDUSTRIAL | wgl13 | 6688610.4344 | 14 | wgl
| tgn41 | 12751.16 | 13 | tgn
COMMERCIAL | klk22 | 85830.78 | 8 | klk
| mby11 | 4292.69 | 12 | mby
FARM | drn12 | 9939.61 | 1 | drn
RESIDENTL | rwn24 | 15617115.6722 | 2794 | rwn
RESIDENTL | cre32 | 8053371.5554 | 2218 | cre
COMMERCIAL | bwn11 | 5920812.2037 | 76 | bwn
NCONUML | smg33 | 19709.42 | 12 | smg
INDUSTRIAL | mby11 | 90387.22 | 16 | mby
COMMERCIAL | tgn41 | 8173213.7745 | 338 | tgn
INDUSTRIAL | wn7 | 3582803.57 | 9 | wn
FARM | bwr23 | 29264.76 | 8 | bwr
RESIDENTL | bwn13 | 8026926.4045 | 1629 | bwn
FARM | wgi24 | 1757204.2906 | 142 | wgi
| rve13 | 21148.03 | 29 | rve
RESIDENTL | wgl21 | 23764201.6622 | 4642 | wgl
COMMERCIAL | wn1 | 22168293.2818 | 620 | wn
INDUSTRIAL | cyn32 | 738566.1077 | 85 | cyn
| hpk21 | 27858.58 | 57 | hpk
COMMERCIAL | klo11 | 2030116.61 | 11 | klo
INDUSTRIAL | bn22 | 260832.7234 | 23 | bn
| ofr24 | 25053.77 | 43 | ofr
| drn12 | 30292.1138 | 29 | drn
COMMERCIAL | smg22 | 18806077.0677 | 136 | smg
COMMERCIAL | bwa22 | 4509592.2057 | 144 | bwa
COMMERCIAL | drn12 | 15118769.4919 | 112 | drn
| ldl23 | 80304.9161 | 48 | ldl
| rwn32 | 14306.27 | 22 | rwn
| drn23 | 12868.4314 | 15 | drn
RESIDENTL | mwl22 | 12904194.2639 | 2809 | mwl
COMMERCIAL | tt6 | 3682930.1298 | 115 | tt
COMMERCIAL | bra24 | 3429037.1414 | 127 | bra
NCONUML | hpk11 | 112614.82 | 31 | hpk
RESIDENTL | mfa21 | 12551518.2306 | 1921 | mfa
RESIDENTL | bge22 | 19945240.9452 | 3164 | bge
| tt4 | 9710.0483 | 41 | tt
NCONUML | phm22 | 22255.8232 | 9 | phm
COMMERCIAL | fgy21 | 1241019.6707 | 34 | fgy
INDUSTRIAL | nla31 | 516137.35 | 16 | nla
FARM | wyk13 | 707273.0378 | 84 | wyk
NCONUML | elm25 | 44655.33 | 20 | elm
| ofr23 | 28214.1089 | 26 | ofr
INDUSTRIAL | ruba22 | 167892.49 | 8 | ruba
FARM | hpk21 | 3124.97 | 1 | hpk
FARM | wn4 | 999664.927 | 129 | wn
COMMERCIAL | wn6 | 8795190.5545 | 246 | wn
| cre23 | 50195.43 | 25 | cre
COMMERCIAL | bwr22 | 15914202.1636 | 269 | bwr
INDUSTRIAL | elm22 | 545216.4127 | 27 | elm
NCONUML | bwr32 | 46210.27 | 31 | bwr
COMMERCIAL | moe12 | 4799517.76 | 51 | moe
| drn22 | 43438.5 | 28 | drn
FARM | bn22 | 13032.09 | 3 | bn
FARM | ldl24 | 222231.4641 | 11 | ldl
| bdl31 | 24144.6762 | 16 | bdl
FARM | cpk11 | 227979.0877 | 18 | cpk
FARM | elm33 | 50441.5205 | 4 | elm
INDUSTRIAL | rve13 | 147824.4003 | 10 | rve
COMMERCIAL | uwy1 | 603856.89 | 33 | uwy
FARM | mfa21 | 13347321.3386 | 701 | mfa
RESIDENTL | wo14 | 1446838.665 | 266 | wo
NCONUML | rwt14 | 102266.96 | 37 | rwt
| kms11 | 9612.23 | 20 | kms
RESIDENTL | phi11 | 5828644.3864 | 1391 | phi
COMMERCIAL | tgn12 | 10174331.2835 | 242 | tgn
LIGHTING | drn21 | 522455.53 | 1 | drn
INDUSTRIAL | smr22 | 2060432.23 | 13 | smr
| moe21 | 19173.8011 | 29 | moe
NCONUML | fgy12 | 1668.8419 | 4 | fgy
COMMERCIAL | elm25 | 2590499.6378 | 73 | elm
| epg34 | 11737.1961 | 27 | epg
COMMERCIAL | cpk23 | 2022573.8223 | 44 | cpk
COMMERCIAL | sle31 | 4198591.4215 | 178 | sle
FARM | nrn13 | 23844.37 | 5 | nrn
FARM | elm26 | 83060.0495 | 12 | elm
INDUSTRIAL | rve12 | 67014.5 | 12 | rve
INDUSTRIAL | moe21 | 304282.5341 | 37 | moe
COMMERCIAL | ofr21 | 9424773.56 | 126 | ofr
FARM | wn3 | 4385381.9629 | 585 | wn
FARM | klk21 | 574949.1868 | 82 | klk
NCONUML | wyk13 | 97422.66 | 49 | wyk
FARM | bwn12 | 14573.05 | 3 | bwn
NCONUML | msd2 | 8161.26 | 6 | msd
COMMERCIAL | elm31 | 474386.1613 | 1 | elm
RESIDENTL | rwt35 | 12065.95 | 2 | rwt
RESIDENTL | wt6 | 15702930.1084 | 3397 | wt
RESIDENTL | cln24 | 3991370.9732 | 1090 | cln
COMMERCIAL | smg21 | 2744632.8687 | 43 | smg
| myt21 | 64545.94 | 22 | myt
RESIDENTL | lga22 | 9862202.3617 | 1608 | lga
INDUSTRIAL | cyn13 | 4447831.06 | 67 | cyn
COMMERCIAL | ruba12 | 6703349.3664 | 290 | ruba
| smr23 | 7378.7014 | 9 | smr
FARM | phi13 | 230339.12 | 15 | phi
RESIDENTL | wt11 | 8665012.8839 | 2213 | wt
RESIDENTL | bge13 | 9255563.8982 | 1458 | bge
COMMERCIAL | bge11 | 11367890.3817 | 330 | bge
COMMERCIAL | wgi23 | 2290528.82 | 95 | wgi
COMMERCIAL | epg35 | 29855241.8371 | 304 | epg
NCONUML | mwl23 | 55631.52 | 20 | mwl
RESIDENTL | tgn11 | 18615536.7391 | 4196 | tgn
RESIDENTL | klo24 | 35150523.3753 | 8219 | klo
| wgi32 | 32777.55 | 36 | wgi
| uwy1 | 1895.86 | 6 | uwy
COMMERCIAL | wots24 | 5008654.6646 | 265 | wots
INDUSTRIAL | phi13 | 601326.64 | 38 | phi
LIGHTING | cf1 | 76883.018 | 3 | cf
RESIDENTL | cre21 | 18876617.5647 | 4715 | cre
INDUSTRIAL | wo32 | 73086.25 | 1 | wo
COMMERCIAL | lga13 | 621321.4861 | 47 | lga
FARM | cnr2 | 245915.51 | 48 | cnr
COMMERCIAL | bge22 | 4521687.9575 | 100 | bge
INDUSTRIAL | cyn12 | 101425.5 | 5 | cyn
FARM | drn11 | 51881.33 | 8 | drn
INDUSTRIAL | wo23 | 212041.78 | 1 | wo
RESIDENTL | lga23 | 5064870.5947 | 821 | lga
RESIDENTL | bn12 | 3438265.7182 | 625 | bn
RESIDENTL | bra21 | 23268334.8963 | 5707 | bra
| bdl42 | 11198.42 | 14 | bdl
FARM | cnr1 | 2440.03 | 2 | cnr
| phm34 | 68320.3174 | 32 | phm
FARM | rwt31 | 12148.87 | 1 | rwt
| smg31 | 8879.89 | 17 | smg
LIGHTING | tgn11 | 1064655.8 | 1 | tgn
FARM | llg14 | 4195351.6172 | 347 | llg
FARM | mwl11 | 2401732.236 | 295 | mwl
INDUSTRIAL | brt22 | 103539.39 | 15 | brt
COMMERCIAL | mwl14 | 15268408.4249 | 139 | mwl
RESIDENTL | wn1 | 4757807.4084 | 1039 | wn
COMMERCIAL | wo33 | 4706642.85 | 27 | wo
| nrn14 | 10562.91 | 10 | nrn
RESIDENTL | wgl15 | 10836827.2608 | 2158 | wgl
RESIDENTL | mfa22 | 4069843.249 | 701 | mfa
NCONUML | wyk24 | 96009.71 | 32 | wyk
NCONUML | rwn34 | 17137.95 | 21 | rwn
NCONUML | rve11 | 32578.28 | 16 | rve
INDUSTRIAL | klk11 | 54511.69 | 7 | klk
RESIDENTL | tt2 | 73044.37 | 7 | tt
COMMERCIAL | rwn32 | 3002784.6794 | 97 | rwn
NCONUML | tt1 | 9612.49 | 4 | tt
NCONUML | bwr23 | 79898.93 | 30 | bwr
NCONUML | epg14 | 19866.64 | 14 | epg
| elm26 | 27328.755 | 32 | elm
INDUSTRIAL | bdl32 | 418697.92 | 34 | bdl
FARM | wt11 | 3746.97 | 1 | wt
NCONUML | ofr23 | 50364.93 | 30 | ofr
INDUSTRIAL | smg23 | 412547.84 | 9 | smg
LIGHTING | klo14 | 3058096.87 | 1 | klo
| nrn13 | 13473.67 | 22 | nrn
FARM | bra12 | 12444.91 | 1 | bra
COMMERCIAL | cre21 | 15222170.3645 | 489 | cre
INDUSTRIAL | wgi32 | 984365.53 | 33 | wgi
NCONUML | rwt25 | 118451.05 | 54 | rwt
INDUSTRIAL | mwe236 | 280541.09 | 16 | mwe
RESIDENTL | epg33 | 183201.2006 | 6 | epg
INDUSTRIAL | elm33 | 243571.284 | 12 | elm
RESIDENTL | ldl11 | 13512975.3636 | 2241 | ldl
| mwl12 | 15850.97 | 9 | mwl
INDUSTRIAL | fgy21 | 6595081.67 | 18 | fgy
LIGHTING | smr24 | 109914.08 | 1 | smr
RESIDENTL | rwt25 | 10768082.8154 | 2324 | rwt
INDUSTRIAL | rwt15 | 3409961.2906 | 83 | rwt
INDUSTRIAL | phi12 | 3418741.3516 | 25 | phi
INDUSTRIAL | bwa22 | 1592049.74 | 9 | bwa
NCONUML | wo22 | 90587.46 | 26 | wo
INDUSTRIAL | ldl21 | 599666.7 | 44 | ldl
INDUSTRIAL | wt6 | 1814.16 | 1 | wt
NCONUML | ofr22 | 9198.59 | 2 | ofr
INDUSTRIAL | bra13 | 1860337.5903 | 47 | bra
COMMERCIAL | fgy24 | 2616699.5517 | 109 | fgy
RESIDENTL | epg11 | 6094828.0666 | 1503 | epg
NCONUML | rwt36 | 1279.88 | 1 | rwt
RESIDENTL | bwn14 | 23184606.5946 | 3016 | bwn
COMMERCIAL | bra31 | 7996775.7312 | 141 | bra
| nla32 | 13550.62 | 15 | nla
FARM | brt11 | 223967.42 | 33 | brt
| hpk12 | 10433.13 | 13 | hpk
INDUSTRIAL | llg13 | 899195.7591 | 21 | llg
INDUSTRIAL | wgl21 | 1687828.17 | 29 | wgl
INDUSTRIAL | cnr2 | 615523.18 | 19 | cnr
INDUSTRIAL | mfa14 | 499885.98 | 5 | mfa
RESIDENTL | drn13 | 15714620.5428 | 2698 | drn
FARM | kms12 | 1180373.8068 | 156 | kms
COMMERCIAL | rwn24 | 15303994.2605 | 63 | rwn
NCONUML | wn4 | 65357.11 | 21 | wn
COMMERCIAL | rwn33 | 562037.42 | 22 | rwn
| moe22 | 3614.75 | 12 | moe
| wgl13 | 39374.2 | 44 | wgl
| moe11 | 8193.3901 | 21 | moe
COMMERCIAL | wt7 | 4475658.5866 | 198 | wt
NCONUML | bwr13 | 106489.72 | 46 | bwr
NCONUML | kms12 | 115620.45 | 45 | kms
NCONUML | cyn24 | 41312.6858 | 21 | cyn
COMMERCIAL | mwl13 | 8520395.3383 | 232 | mwl
COMMERCIAL | cyn32 | 10902527.7138 | 351 | cyn
INDUSTRIAL | tgn31 | 3050316.88 | 29 | tgn
| wo13 | 12961.22 | 9 | wo
NCONUML | bra12 | 30121.15 | 6 | bra
| mwl24 | 4141.68 | 3 | mwl
RESIDENTL | ftr22 | 5196242.6186 | 1010 | ftr
| cyn12 | 33132.831 | 28 | cyn
| mwl11 | 4217.9 | 11 | mwl
NCONUML | sle13 | 9744.3474 | 7 | sle
RESIDENTL | sle14 | 16027394.2978 | 4223 | sle
RESIDENTL | wgl23 | 5362246.1099 | 739 | wgl
COMMERCIAL | cre23 | 25513720.5265 | 132 | cre
RESIDENTL | bdl43 | 5886157.096 | 1122 | bdl
RESIDENTL | bge21 | 100743.92 | 11 | bge
RESIDENTL | smg22 | 10427736.14 | 2476 | smg
FARM | rwn31 | 347566.14 | 21 | rwn
INDUSTRIAL | bn12 | 8173831.79 | 6 | bn
| wgi24 | 27543.5394 | 32 | wgi
| mfa23 | 2828.28 | 3 | mfa
NCONUML | elm22 | 93887.89 | 42 | elm
INDUSTRIAL | wots13 | 2426481.9937 | 28 | wots
RESIDENTL | mwl13 | 9372820.2657 | 1896 | mwl
COMMERCIAL | epg31 | 8736205.1691 | 170 | epg
| bdl44 | 43009.9658 | 33 | bdl
COMMERCIAL | wgl24 | 14484234.4559 | 200 | wgl
INDUSTRIAL | wn3 | 1104797.78 | 30 | wn
| wgi33 | 38017.7186 | 28 | wgi
NCONUML | wo31 | 91536.41 | 24 | wo
FARM | ldl14 | 3990495.203 | 142 | ldl
NCONUML | wyk12 | 43139.17 | 24 | wyk
INDUSTRIAL | mwl15 | 15961047.4 | 1 | mwl
LIGHTING | bdl32 | 23514.52 | 1 | bdl
| rve12 | 15159.19 | 33 | rve
NCONUML | phm34 | 55440.25 | 17 | phm
COMMERCIAL | phm22 | 18761180.3018 | 732 | phm
RESIDENTL | cyn22 | 8715945.6121 | 2142 | cyn
FARM | fgy31 | 3345.68 | 2 | fgy
RESIDENTL | smr22 | 8159798.5324 | 1327 | smr
RESIDENTL | cyn23 | 7298806.6664 | 1621 | cyn
FARM | bdl42 | 2407309.4815 | 483 | bdl
| wyk23 | 31976.68 | 33 | wyk
INDUSTRIAL | rwn26 | 257525.5397 | 10 | rwn
NCONUML | bwn11 | 91006.47 | 23 | bwn
COMMERCIAL | cyn23 | 7883296.3431 | 299 | cyn
| moe15 | 19145.0797 | 16 | moe
| drn11 | 44271.4909 | 65 | drn
INDUSTRIAL | moe22 | 88009.47 | 4 | moe
NCONUML | mdg1 | 4146.1 | 9 | mdg
FARM | bra33 | 5568.67 | 1 | bra
LIGHTING | bwa22 | 75542.46 | 1 | bwa
NCONUML | hpk14 | 64164.68 | 20 | hpk
NCONUML |  | 262.3928 | 5 | #REF!
INDUSTRIAL | cln13 | 2016187.9013 | 2 | cln
FARM | ofr11 | 1184021.9516 | 51 | ofr
FARM | phm31 | 2011038.4476 | 90 | phm
NCONUML | elm21 | 62554.36 | 23 | elm
NCONUML | wt8 | 36862.33 | 14 | wt
NCONUML | cnr1 | 1922.85 | 2 | cnr
INDUSTRIAL | cre31 | 212230.18 | 2 | cre
COMMERCIAL | mfa34 | 8313764.4144 | 170 | mfa
INDUSTRIAL | tt5 | 637183.9506 | 23 | tt
INDUSTRIAL | llg14 | 1201432.9268 | 29 | llg
RESIDENTL | wo23 | 1549813.7708 | 361 | wo
| bwr23 | 25383.1703 | 47 | bwr
| sle11 | 3997.21 | 10 | sle
NCONUML | epg22 | 8538.04 | 7 | epg
NCONUML | bwr24 | 20744.02 | 14 | bwr
INDUSTRIAL | myt12 | 952524.23 | 20 | myt
| ftr23 | 53453.1274 | 33 | ftr
RESIDENTL | bra11 | 9331476.9371 | 2277 | bra
FARM | ldl13 | 3504918.0126 | 302 | ldl
| brt11 | 8693.81 | 14 | brt
INDUSTRIAL | phm31 | 91642.7039 | 2 | phm
COMMERCIAL | bdl43 | 22280533.2345 | 523 | bdl
FARM | moe23 | 4928404.5033 | 365 | moe
| klk21 | 7164.56 | 8 | klk
| wt7 | 8483.27 | 17 | wt
FARM | llg11 | 4501914.1562 | 365 | llg
LIGHTING | cf2 | 13221.322 | 1 | cf
| tgn31 | 23134.1673 | 13 | tgn
RESIDENTL | nla31 | 3471883.5329 | 742 | nla
COMMERCIAL | bdl31 | 6479518.62 | 206 | bdl
COMMERCIAL | smr23 | 799486.21 | 26 | smr
INDUSTRIAL | rve11 | 154936.16 | 21 | rve
RESIDENTL | bm8b33 | 130717.0048 | 17 | bmb
FARM | phi12 | 364625.9 | 40 | phi
INDUSTRIAL | klk22 | 5518.6 | 1 | klk
RESIDENTL | llg12 | 7619865.2998 | 1210 | llg
RESIDENTL | cln21 | 24090170.4832 | 5877 | cln
NCONUML | cpk11 | 17830.25 | 17 | cpk
COMMERCIAL | ruba22 | 3463594.5603 | 120 | ruba
NCONUML | brt22 | 9306.55 | 7 | brt
INDUSTRIAL | epg32 | 7635590.16 | 5 | epg
INDUSTRIAL | cln12 | 360384.55 | 1 | cln
COMMERCIAL | bwr13 | 10101102.0366 | 288 | bwr
COMMERCIAL | wo22 | 9017310.64 | 153 | wo
INDUSTRIAL | hpk24 | 9439809.63 | 31 | hpk
COMMERCIAL | cpk12 | 5057421.24 | 115 | cpk
| lyd14 | 55928.8081 | 17 | lyd
INDUSTRIAL | klo11 | 67703.26 | 1 | klo
RESIDENTL | ldl14 | 11349760.1474 | 1905 | ldl
LIGHTING | myt21 | 2294.9 | 1 | myt
RESIDENTL | rwn22 | 13452598.5118 | 2640 | rwn
COMMERCIAL | bm8b32 | 168652.4116 | 16 | bmb
INDUSTRIAL | bdl34 | 328519.77 | 31 | bdl
| tt12 | 16952.1045 | 5 | tt
RESIDENTL | wots24 | 6979604.5034 | 1172 | wots
INDUSTRIAL | wyk24 | 160679.33 | 16 | wyk
COMMERCIAL | klo12 | 12237846.22 | 9 | klo
RESIDENTL | wo33 | 232024.16 | 58 | wo
COMMERCIAL | bn24 | 3468313.5774 | 163 | bn
COMMERCIAL | lga12 | 9341312.33 | 61 | lga
| msd1 | 16071.3636 | 20 | msd
INDUSTRIAL | ofr24 | 300622.14 | 4 | ofr
INDUSTRIAL | bwn13 | 24333.45 | 4 | bwn
| tt1 | 26786.62 | 3 | tt
INDUSTRIAL | rwt31 | 22449174.23 | 3 | rwt
FARM | mfa14 | 28798.91 | 1 | mfa
| bwr32 | 10607.4826 | 52 | bwr
INDUSTRIAL | wn4 | 1120535.2101 | 54 | wn
RESIDENTL | bwr12 | 975012.274 | 199 | bwr
INDUSTRIAL | wgi24 | 1432383.73 | 33 | wgi
| llg13 | 135285.4952 | 24 | llg
| rwn34 | 10950.9 | 10 | rwn
FARM | elm34 | 16399.68 | 6 | elm
RESIDENTL | ruba12 | 12797333.4035 | 1890 | ruba
COMMERCIAL | hpk22 | 5875279.82 | 181 | hpk
| cln11 | 262675.9461 | 229 | cln
RESIDENTL | cf2 | 494427.3912 | 409 | cf
FARM | elm22 | 15544.2323 | 4 | elm
INDUSTRIAL | smg32 | 67645.78 | 1 | smg
FARM | bwa23 | 3495492.525 | 169 | bwa
NCONUML | phm24 | 66511.6 | 15 | phm
NCONUML | wgi23 | 35701.3 | 15 | wgi
NCONUML | epg35 | 18576.68 | 9 | epg
NCONUML | llg13 | 26801.83 | 12 | llg
LIGHTING | phi13 | 74566.47 | 1 | phi
| ldl24 | 28689.7774 | 48 | ldl
| bge11 | 41147.6131 | 30 | bge
RESIDENTL | ofr21 | 18456788.2346 | 4412 | ofr
INDUSTRIAL | ofr11 | 52339.71 | 6 | ofr
COMMERCIAL | nrn11 | 8254682.48 | 13 | nrn
FARM | moe15 | 1053275.4428 | 126 | moe
INDUSTRIAL | lyd12 | 15947.41 | 3 | lyd
INDUSTRIAL | wt10 | 5540.7 | 1 | wt
RESIDENTL | rwt21 | 965731.93 | 282 | rwt
FARM | wo13 | 51683.13 | 6 | wo
INDUSTRIAL | epg34 | 25722.81 | 2 | epg
COMMERCIAL | lys36 | 31611.41 | 1 | lys
RESIDENTL | wn6 | 17451542.0984 | 3750 | wn
NCONUML | hpk12 | 23613.79 | 7 | hpk
INDUSTRIAL | ruba24 | 189283.4035 | 13 | ruba
| nrn12 | 36108.6 | 9 | nrn
NCONUML | nla32 | 30069.03 | 18 | nla
COMMERCIAL | bm8b31 | 174913.9253 | 14 | bmb
| wo22 | 26321.2427 | 38 | wo
INDUSTRIAL | fgy31 | 4952.61 | 1 | fgy
RESIDENTL | cln14 | 25051991.2109 | 8311 | cln
RESIDENTL | lga24 | 3807672.9803 | 653 | lga
RESIDENTL | bra31 | 2624204.8049 | 649 | bra
COMMERCIAL | cln21 | 7282112.3749 | 104 | cln
COMMERCIAL | ftr23 | 8984637.4811 | 336 | ftr
RESIDENTL | klo13 | 97850.5847 | 89 | klo
INDUSTRIAL | ofr14 | 250.62 | 1 | ofr
FARM | mwl24 | 966080.4815 | 75 | mwl
NCONUML | bdl41 | 86032.0652 | 28 | bdl
INDUSTRIAL | epg13 | 201122.3196 | 20 | epg
COMMERCIAL | tgn23 | 6173474.1124 | 95 | tgn
| moe12 | 11374.0239 | 16 | moe
INDUSTRIAL | drn11 | 8297.91 | 2 | drn
| wn4 | 46461.2191 | 29 | wn
NCONUML | wgl13 | 85005.64 | 23 | wgl
INDUSTRIAL | ftr22 | 264831.3749 | 23 | ftr
NCONUML | mjg11 | 5653.43 | 3 | mjg
RESIDENTL | klo12 | 526.2 | 1 | klo
COMMERCIAL | cln11 | 18408618.7138 | 182 | cln
NCONUML | wo13 | 11132.69 | 4 | wo
COMMERCIAL | yn38 | 28127.08 | 5 | yn
NCONUML | mwl24 | 19701.6 | 5 | mwl
RESIDENTL | wots12 | 7880580.6899 | 1786 | wots
COMMERCIAL | tgn43 | 5598797.62 | 126 | tgn
NCONUML | mfa23 | 6277.17 | 3 | mfa
NCONUML | bra32 | 63005.82 | 38 | bra
FARM | bdl34 | 247623.03 | 51 | bdl
INDUSTRIAL | wn5 | 6299826.69 | 33 | wn
| mby13 | 155.9226 | 1 | mby
FARM | ofr23 | 2419763.5413 | 305 | ofr
NCONUML | cre22 | 86458.6773 | 42 | cre
NCONUML | hpk23 | 84001.53 | 23 | hpk
RESIDENTL | bra24 | 8260262.5707 | 1824 | bra
| cyn14 | 12637.7523 | 26 | cyn
LIGHTING | wgl11 | 2443513.25 | 2 | wgl
NCONUML | wgi24 | 69610.83 | 24 | wgi
COMMERCIAL | klo14 | 11961206.944 | 269 | klo
FARM | drn14 | 379625.3327 | 36 | drn
RESIDENTL | bwr22 | 1941843.629 | 510 | bwr
| llg14 | 42684.6726 | 22 | llg
INDUSTRIAL | drn21 | 709809.96 | 3 | drn
INDUSTRIAL | tgn42 | 199383.97 | 5 | tgn
RESIDENTL | sle32 | 6677118.757 | 1350 | sle
RESIDENTL | myt12 | 14552002.0991 | 2380 | myt
FARM | myt21 | 821475.54 | 124 | myt
| bn11 | 39921.12 | 40 | bn
NCONUML | mby12 | 15769.2 | 4 | mby
NCONUML | bdl44 | 1602.59 | 5 | bdl
COMMERCIAL | tt12 | 10810239.5174 | 467 | tt
NCONUML | wn7 | 7884.6 | 2 | wn
| bdl34 | 14430.17 | 36 | bdl
RESIDENTL | lyd11 | 11014119.7855 | 2574 | lyd
FARM | wyk23 | 2329152.6841 | 202 | wyk
| epg23 | 66262.7623 | 20 | epg
RESIDENTL | rwt32 | 15157646.1346 | 3808 | rwt
RESIDENTL | cre31 | 23125994.5084 | 5990 | cre
FARM | bn11 | 9012293.1298 | 1372 | bn
COMMERCIAL |  | 2470964.7554 | 79 | #REF!
INDUSTRIAL | kms11 | 3849512.37 | 9 | kms
RESIDENTL | sle31 | 15232222.0022 | 4728 | sle
RESIDENTL | myt11 | 3230941.4261 | 365 | myt
| wyk12 | 33744.4845 | 17 | wyk
| lga11 | 13750.1489 | 25 | lga
COMMERCIAL | cre33 | 14716025.8299 | 132 | cre
RESIDENTL | trc01 | 404888.8876 | 85 | trc
| moe25 | 10579.3743 | 23 | moe
NCONUML | msd1 | 8725.66 | 9 | msd
RESIDENTL | mwl14 | 1637810.9082 | 178 | mwl
FARM | wn5 | 10157746.9699 | 1090 | wn
INDUSTRIAL | bwr33 | 13101695.07 | 41 | bwr
NCONUML | ofr24 | 72292.73 | 18 | ofr
| mdg1 | 5594.13 | 4 | mdg
FARM | wgi33 | 86057.74 | 7 | wgi
RESIDENTL | rwt22 | 12512450.4989 | 3066 | rwt
RESIDENTL | cnr2 | 3844076.3719 | 1054 | cnr
| hpk14 | 17565.23 | 35 | hpk
NCONUML | drn23 | 37389.78 | 20 | drn
RESIDENTL | tgn44 | 11943542.7304 | 2804 | tgn
| tgn42 | 0 | 1 | tgn
NCONUML | rwt22 | 27503.296 | 22 | rwt
FARM | mwl16 | 172184.54 | 14 | mwl
COMMERCIAL | nla34 | 1413700.5844 | 93 | nla
| epg22 | 2049.9261 | 2 | epg
FARM | tgn41 | 3728231.4432 | 423 | tgn
COMMERCIAL | lga23 | 3382991.9134 | 119 | lga
NCONUML | sle31 | 61055.23 | 20 | sle
NCONUML | tgn44 | 66469.79 | 20 | tgn
| phm24 | 18272.6834 | 34 | phm
RESIDENTL | hpk11 | 16523367.4098 | 4141 | hpk
| hpk13 | 40054.7485 | 22 | hpk
| bwr24 | 10180.34 | 28 | bwr
COMMERCIAL | bdl33 | 34051046.7333 | 257 | bdl
COMMERCIAL | wt9 | 7035668.1433 | 128 | wt
NCONUML | wt15 | 16005.53 | 14 | wt
FARM | ruba24 | 730484.142 | 55 | ruba
NCONUML | cpk23 | 20021.69 | 18 | cpk
INDUSTRIAL | mwl21 | 320021.87 | 5 | mwl
COMMERCIAL | hpk23 | 12064171.7331 | 206 | hpk
INDUSTRIAL | wt11 | 2563605.84 | 2 | wt
RESIDENTL | wt15 | 8580853.2399 | 1947 | wt
| elm21 | 24345.52 | 16 | elm
INDUSTRIAL | mwl16 | 183545.9668 | 9 | mwl
FARM | rve13 | 9637.99 | 1 | rve
NCONUML | drn22 | 69938.3 | 27 | drn
NCONUML | bdl31 | 70697.58 | 29 | bdl
NCONUML | bwa24 | 1320.25 | 1 | bwa
COMMERCIAL | mwl23 | 10773058.8537 | 154 | mwl
COMMERCIAL | elm23 | 5093994.3825 | 95 | elm
FARM | smr23 | 1078615.6398 | 156 | smr
| cpk11 | 37835.6667 | 47 | cpk
INDUSTRIAL | bra14 | 14750.52 | 4 | bra
RESIDENTL | rwn33 | 5693275.4596 | 1153 | rwn
| bn22 | 41634.09 | 21 | bn
INDUSTRIAL | tt2 | 11531135.8238 | 100 | tt
INDUSTRIAL | wt12 | 3871876.0911 | 67 | wt
INDUSTRIAL | mwl22 | 292678.42 | 8 | mwl
RESIDENTL | bn23 | 8695284.412 | 1665 | bn
COMMERCIAL | cyn11 | 9621618.8569 | 233 | cyn
| cyn21 | 22400.14 | 28 | cyn
INDUSTRIAL | mjg11 | 1321804.29 | 13 | mjg
INDUSTRIAL | cf2 | 1970.494 | 2 | cf
RESIDENTL | tt5 | 6560032.4165 | 1633 | tt
COMMERCIAL | smr14 | 6818307.6657 | 239 | smr
COMMERCIAL | smg33 | 1348313.99 | 14 | smg
RESIDENTL | rwt15 | 11066767.0768 | 2454 | rwt
COMMERCIAL | cre32 | 14440881.1645 | 427 | cre
INDUSTRIAL | smr24 | 4639865.5557 | 45 | smr
COMMERCIAL | fgy23 | 10185283.97 | 98 | fgy
COMMERCIAL | hpk11 | 3476478.711 | 53 | hpk
| cre32 | 19011.64 | 13 | cre
NCONUML | wgl23 | 12760.41 | 6 | wgl
COMMERCIAL | nrn15 | 84419.81 | 3 | nrn
NCONUML | moe15 | 22748.39 | 11 | moe
RESIDENTL | tt12 | 86039.86 | 6 | tt
RESIDENTL | cyn31 | 8632445.7043 | 2077 | cyn
RESIDENTL | wgl24 | 16633542.8094 | 2715 | wgl
COMMERCIAL | wgi22 | 6881286.006 | 159 | wgi
INDUSTRIAL | smr13 | 992080.85 | 26 | smr
NCONUML | cpk12 | 17033.61 | 10 | cpk
NCONUML | ftr21 | 16597.26 | 11 | ftr
FARM | mwl12 | 18529.37 | 2 | mwl
INDUSTRIAL | epg33 | 1129768.4897 | 4 | epg
| wyk13 | 9658.4809 | 15 | wyk
LIGHTING | trc01 | 669938.2281 | 2 | trc
FARM | hpk13 | 2305.94 | 1 | hpk
RESIDENTL | tt6 | 19150788.3328 | 4695 | tt
FARM | tgn31 | 5369095.0164 | 562 | tgn
NCONUML | wgl24 | 11028.97 | 10 | wgl
INDUSTRIAL | brt11 | 82545.9018 | 12 | brt
LIGHTING | mby11 | 10728.24 | 1 | mby
NCONUML | myt21 | 24178.1 | 12 | myt
| wt10 | 6115.9374 | 5 | wt
RESIDENTL | bge12 | 9796026.1467 | 1789 | bge
FARM | myt11 | 2640136.7565 | 257 | myt
NCONUML | cyn11 | 21168.08 | 13 | cyn
INDUSTRIAL |  | 942329979.1078 | 12 | #REF!
INDUSTRIAL | elm34 | 168803.0667 | 15 | elm
| brt22 | 30486.3216 | 18 | brt
INDUSTRIAL | epg11 | 6777.42 | 2 | epg
RESIDENTL | elm34 | 19825611.7814 | 4189 | elm
COMMERCIAL | sle13 | 974523.8832 | 109 | sle
INDUSTRIAL | lga13 | 207007.5439 | 9 | lga
RESIDENTL | mwl23 | 3618535.6291 | 812 | mwl
| fgy14 | 28887.99 | 26 | fgy
COMMERCIAL | mby13 | 2521770.2974 | 71 | mby
| lga12 | 14720.56 | 12 | lga
RESIDENTL | cpk12 | 17343162.547 | 2927 | cpk
COMMERCIAL | wt5 | 19785711.5258 | 118 | wt
INDUSTRIAL | drn24 | 4643890.64 | 3 | drn
FARM | drn21 | 13254.24 | 1 | drn
NCONUML | mwl11 | 360.93 | 3 | mwl
RESIDENTL | epg34 | 15669683.4078 | 3862 | epg
NCONUML | wt10 | 27658.61 | 16 | wt
LIGHTING | rwt14 | 962126.36 | 3 | rwt
COMMERCIAL | drn23 | 5472888.3558 | 161 | drn
LIGHTING | bwn11 | 6340546.01 | 1 | bwn
INDUSTRIAL | sfs1 | 80102.39 | 5 | sfs
COMMERCIAL | phm34 | 4610839.9937 | 66 | phm
COMMERCIAL | mfa31 | 3803351.87 | 100 | mfa
INDUSTRIAL | rwt25 | 2203508.65 | 42 | rwt
| bwa22 | 41045.3074 | 24 | bwa
FARM | smr13 | 139441.5096 | 27 | smr
NCONUML | phi12 | 84007.84 | 24 | phi
| fgy21 | 10377.87 | 9 | fgy
NCONUML | rwt15 | 44056.974 | 28 | rwt
LIGHTING | nla34 | 5187.52 | 1 | nla
RESIDENTL | sfs1 | 6449039.4989 | 958 | sfs
RESIDENTL | msd4 | 16354350.3097 | 2395 | msd
INDUSTRIAL | phm33 | 724516.58 | 21 | phm
COMMERCIAL | wgl14 | 59932538.6 | 1 | wgl
COMMERCIAL | rwt31 | 3904134.109 | 54 | rwt
RESIDENTL | wt5 | 5466545.168 | 1335 | wt
FARM | ftr22 | 3872176.8459 | 271 | ftr
| wn5 | 51237.831 | 23 | wn
INDUSTRIAL | kms12 | 880994.04 | 26 | kms
NCONUML | rwt31 | 27889.28 | 18 | rwt
RESIDENTL | elm22 | 20622579.4478 | 3120 | elm
| bn24 | 7126.586 | 9 | bn
FARM | wots11 | 7572710.4051 | 689 | wots
INDUSTRIAL | myt11 | 122662.09 | 11 | myt
NCONUML | bdl32 | 81716.25 | 38 | bdl
NCONUML | cyn33 | 39860.39 | 20 | cyn
| lga13 | 7900.07 | 12 | lga
COMMERCIAL | wn7 | 705796.26 | 31 | wn
RESIDENTL | tgn23 | 12995258.1614 | 2157 | tgn
RESIDENTL | wgl12 | 18309192.1093 | 3011 | wgl
NCONUML | drn14 | 58816.42 | 20 | drn
INDUSTRIAL | tt9 | 1853761.73 | 4 | tt
RESIDENTL | kms12 | 23913269.0041 | 4277 | kms
COMMERCIAL | wgi33 | 13737748.8552 | 364 | wgi
COMMERCIAL | phm21 | 28428865.0993 | 838 | phm
FARM | sle32 | 5441049.7096 | 310 | sle
NCONUML | cyn32 | 58907.16 | 38 | cyn
INDUSTRIAL | msd2 | 165834.72 | 18 | msd
COMMERCIAL | bwr23 | 26845428.111 | 233 | bwr
RESIDENTL | msd2 | 5810770.2828 | 1153 | msd
FARM | klk11 | 2014936.8264 | 177 | klk
| wots12 | 13459.1171 | 22 | wots
INDUSTRIAL | rwn24 | 4339629.96 | 13 | rwn
INDUSTRIAL | tgn41 | 1853911.3546 | 62 | tgn
COMMERCIAL | smg32 | 6595824.87 | 22 | smg
| wgi34 | 86239.94 | 15 | wgi
RESIDENTL | bn22 | 13286130.4589 | 3118 | bn
RESIDENTL | mfa31 | 9237847.4317 | 2206 | mfa
COMMERCIAL | wgi34 | 9571334.08 | 60 | wgi
RESIDENTL | mdi1 | 176577.17 | 31 | mdi
NCONUML | rwn31 | 16738.19 | 15 | rwn
INDUSTRIAL | drn13 | 239296.9 | 11 | drn
INDUSTRIAL | bdl43 | 306419.52 | 21 | bdl
NCONUML | wo23 | 56204.51 | 16 | wo
COMMERCIAL | ftr21 | 2804675.8206 | 100 | ftr
COMMERCIAL | bwa23 | 206762.2501 | 23 | bwa
NCONUML | mfa21 | 28416.84 | 12 | mfa
| cln23 | 52144.7804 | 85 | cln
RESIDENTL | rve11 | 2276471.0008 | 508 | rve
COMMERCIAL | ofr24 | 6649904.8426 | 113 | ofr
NCONUML | phi13 | 105028.33 | 33 | phi
FARM | smg22 | 25054.15 | 4 | smg
FARM | bwn11 | 18419.1 | 1 | bwn
INDUSTRIAL | epg31 | 360181.3871 | 31 | epg
COMMERCIAL | fgy14 | 7872993.2117 | 231 | fgy
| ldl11 | 24480.7 | 22 | ldl
INDUSTRIAL | wgl24 | 939120.3004 | 39 | wgl
| phm22 | 31542.7748 | 10 | phm
COMMERCIAL | moe15 | 2469270.3666 | 172 | moe
| cnr3 | 100.0469 | 1 | cnr
RESIDENTL | bwn12 | 4456239.3509 | 1013 | bwn
COMMERCIAL | mwl24 | 5791496.4979 | 78 | mwl
COMMERCIAL | wo13 | 2493976.37 | 46 | wo
RESIDENTL | elm25 | 10534980.5572 | 2009 | elm
RESIDENTL | phm32 | 14466986.7977 | 3288 | phm
COMMERCIAL | ofr11 | 14130002.2904 | 224 | ofr
INDUSTRIAL | bge13 | 1057475.88 | 11 | bge
RESIDENTL | ofr22 | 7907197.5875 | 2174 | ofr
INDUSTRIAL | lga22 | 745287.81 | 44 | lga
FARM | hpk22 | 33600.65 | 5 | hpk
COMMERCIAL | epg23 | 63543126.9632 | 711 | epg
NCONUML | epg34 | 29379.47 | 21 | epg
| mwl23 | 14018.9088 | 10 | mwl
FARM | lyd14 | 350081.37 | 31 | lyd
| elm33 | 18371.0537 | 30 | elm
RESIDENTL | bwn11 | 14758921.2622 | 2984 | bwn
| cyn33 | 33636.86 | 37 | cyn
INDUSTRIAL | ldl13 | 1566146.5513 | 31 | ldl
NCONUML | smg32 | 19512.15 | 10 | smg
NCONUML | lga21 | 24931.49 | 9 | lga
RESIDENTL | mfa34 | 6438005.323 | 995 | mfa
COMMERCIAL | lga22 | 10229963.6597 | 340 | lga
COMMERCIAL | wgi31 | 4363035.5887 | 128 | wgi
| wt9 | 17175.83 | 21 | wt
INDUSTRIAL | mfa21 | 1292894.4886 | 57 | mfa
FARM | wgi32 | 343056.5273 | 19 | wgi
COMMERCIAL | bge21 | 44944.8 | 1 | bge
INDUSTRIAL | elm26 | 46289.86 | 5 | elm
NCONUML | msd4 | 12187.83 | 6 | msd
COMMERCIAL | bra21 | 14789918.5926 | 289 | bra
| cpk22 | 7305.07 | 12 | cpk
NCONUML | phm32 | 76324.09 | 20 | phm
NCONUML | sfs1 | 44865.78 | 10 | sfs
COMMERCIAL | lyd13 | 6072257.17 | 42 | lyd
FARM | cyn33 | 36456.98 | 4 | cyn
NCONUML | phm21 | 71428.0533 | 24 | phm
COMMERCIAL | sle32 | 5434267.6149 | 190 | sle
NCONUML | smg31 | 21751.86 | 17 | smg
NCONUML | wots11 | 25057.91 | 11 | wots
RESIDENTL | tgn43 | 15724147.9465 | 3608 | tgn
INDUSTRIAL | cyn21 | 9259443.95 | 23 | cyn
INDUSTRIAL | bn23 | 1923467.13 | 19 | bn
NCONUML | nrn14 | 79150.17 | 17 | nrn
NCONUML | cyn22 | 32483.16 | 10 | cyn
NCONUML | wgl12 | 47271.49 | 20 | wgl
COMMERCIAL | phm24 | 600129.57 | 25 | phm
NCONUML | lga11 | 25837.14 | 8 | lga
NCONUML | tgn41 | 7415.11 | 5 | tgn
RESIDENTL | wgl11 | 17118670.1537 | 3818 | wgl
RESIDENTL | wots11 | 15871220.8415 | 2910 | wots
| rwn31 | 40233.5106 | 27 | rwn
COMMERCIAL | elm32 | 8171019.0636 | 263 | elm
FARM | mby11 | 1335559.7721 | 187 | mby
INDUSTRIAL | mwl25 | 33119.15 | 8 | mwl
FARM | rwn26 | 5055.63 | 2 | rwn
| nla34 | 8234.98 | 10 | nla
RESIDENTL |  | 349105.8277 | 492 | #REF!
FARM | epg13 | 82815.8863 | 12 | epg
| wyk24 | 32167.14 | 30 | wyk
FARM | sle11 | 16862.17 | 6 | sle
COMMERCIAL | bm8b33 | 3349.12 | 2 | bmb
RESIDENTL | smg21 | 17914575.4009 | 3718 | smg
INDUSTRIAL | bdl42 | 622534.62 | 24 | bdl
| yn38 | 7519.7419 | 1 | yn
| phi13 | 28221.5917 | 27 | phi
| epg14 | 9258.9052 | 38 | epg
FARM | nla31 | 1791184.5035 | 140 | nla
INDUSTRIAL | wgi33 | 1188063.8119 | 37 | wgi
LIGHTING | phm33 | 4303153.65 | 2 | phm
RESIDENTL | phm33 | 12878778.4238 | 2134 | phm
COMMERCIAL | wgl23 | 3870974.8784 | 252 | wgl
NCONUML | wt5 | 58508.56 | 14 | wt
NCONUML | bwn14 | 81385.02 | 37 | bwn
NCONUML | mfa31 | 49958.93 | 14 | mfa
COMMERCIAL | bra12 | 23355928.37 | 122 | bra
NCONUML | wt13 | 98966.19 | 41 | wt
COMMERCIAL | klo24 | 13267963.2484 | 244 | klo
COMMERCIAL | bge12 | 6262328.83 | 64 | bge
COMMERCIAL | wn4 | 10511680.2174 | 332 | wn
INDUSTRIAL | tt6 | 2940006.87 | 14 | tt
FARM | cln13 | 4519.0334 | 1 | cln
RESIDENTL | bwa23 | 1839261.5711 | 259 | bwa
RESIDENTL | smr12 | 601661.7559 | 102 | smr
NCONUML | bra31 | 17155.48 | 11 | bra
FARM | cln22 | 84599.56 | 6 | cln
RESIDENTL | moe23 | 10757204.18 | 1872 | moe
FARM | bn23 | 4995698.9571 | 709 | bn
INDUSTRIAL | bwr12 | 7576207.2428 | 317 | bwr
COMMERCIAL | elm33 | 8652520.7547 | 229 | elm
RESIDENTL | tgn12 | 769554.192 | 239 | tgn
NCONUML | bn23 | 5729.17 | 9 | bn
| cyn11 | 35169.6447 | 13 | cyn
INDUSTRIAL | wots12 | 5742170.47 | 22 | wots
INDUSTRIAL | llg12 | 8080777.31 | 18 | llg
NCONUML | ofr14 | 11958.45 | 3 | ofr
RESIDENTL | rwn34 | 11161403.5989 | 1490 | rwn
RESIDENTL | fgy12 | 975691.3435 | 398 | fgy
COMMERCIAL | wyk24 | 11852940.7836 | 290 | wyk
COMMERCIAL | smr12 | 1199230.8 | 20 | smr
INDUSTRIAL | wgl11 | 590499.13 | 17 | wgl
INDUSTRIAL | moe13 | 8896507.14 | 13 | moe
INDUSTRIAL | wots11 | 14616083.73 | 22 | wots
NCONUML | epg13 | 4325.18 | 2 | epg
NCONUML | bn22 | 72789.04 | 38 | bn
RESIDENTL | bwr23 | 15381612.1105 | 3589 | bwr
NCONUML | cln13 | 19538.3161 | 10 | cln
COMMERCIAL | bwa24 | 4350900.07 | 4 | bwa
COMMERCIAL | bwr32 | 11258727.4704 | 251 | bwr
RESIDENTL | bra32 | 8710928.5985 | 2041 | bra
FARM | klo14 | 681766.459 | 92 | klo
INDUSTRIAL | tt7 | 9353368.9205 | 125 | tt
RESIDENTL | wo11 | 815896.564 | 156 | wo
LIGHTING | mwl24 | 803944.3 | 2 | mwl
COMMERCIAL | bwr24 | 7860784.794 | 262 | bwr
COMMERCIAL | drn14 | 5284276.4061 | 147 | drn
NCONUML | hpk24 | 27055.52 | 10 | hpk
| cyn32 | 34865.18 | 48 | cyn
| bra23 | 7974.72 | 25 | bra
RESIDENTL | rve13 | 16767421.4281 | 3587 | rve
COMMERCIAL | bwn13 | 11531398.8601 | 263 | bwn
FARM | cln23 | 76487.94 | 5 | cln
NCONUML | ruba24 | 1482.28 | 4 | ruba
COMMERCIAL | msd1 | 4448954.738 | 126 | msd
| phm31 | 2299.25 | 4 | phm
LIGHTING | wn1 | 677520.74 | 1 | wn
COMMERCIAL | wt8 | 2125517.5597 | 71 | wt
RESIDENTL | bdl33 | 5101200.3632 | 906 | bdl
COMMERCIAL | rwt21 | 33203170.5825 | 281 | rwt
FARM |  | 15223.9488 | 53 | #REF!
| fgy13 | 16173.63 | 19 | fgy
| wt11 | 14907.843 | 20 | wt
RESIDENTL | mwl24 | 4259131.5949 | 729 | mwl
INDUSTRIAL | bwn12 | 375603.57 | 33 | bwn
| lyd12 | 10355.6 | 16 | lyd
| lyd13 | 31235.27 | 24 | lyd
| elm32 | 28931.8643 | 22 | elm
RESIDENTL | ldl13 | 20183081.1078 | 3515 | ldl
COMMERCIAL | epg14 | 4722560.1631 | 66 | epg
FARM | epg32 | 616929.8369 | 16 | epg
| smg23 | 6841.4304 | 12 | smg
NCONUML | mwl16 | 31954.29 | 10 | mwl
COMMERCIAL | ofr22 | 3955299.41 | 63 | ofr
FARM | wgl24 | 9990463.449 | 886 | wgl
COMMERCIAL | llg14 | 8402501.0583 | 280 | llg
COMMERCIAL | wgi24 | 3234685.3433 | 136 | wgi
FARM | cnr3 | 47812.597 | 17 | cnr
| epg33 | 55263.0616 | 6 | epg
INDUSTRIAL | bra24 | 1115020.317 | 14 | bra
NCONUML | wgi33 | 84992.31 | 23 | wgi
FARM | rwt15 | 1849.17 | 1 | rwt
RESIDENTL | ldl12 | 620798.3677 | 119 | ldl
INDUSTRIAL | bwr22 | 8606432.4227 | 334 | bwr
FARM | cf2 | 2033.193 | 1 | cf
NCONUML | klo14 | 36515.49 | 28 | klo
INDUSTRIAL | trc01 | 31629.57 | 2 | trc
RESIDENTL | lga21 | 9412760.8279 | 1623 | lga
RESIDENTL | wt13 | 15834142.0313 | 3223 | wt
RESIDENTL | cyn13 | 3260017.5153 | 858 | cyn
INDUSTRIAL | ofr21 | 138382.59 | 9 | ofr
NCONUML | sle32 | 22407.43 | 13 | sle
COMMERCIAL | lyd12 | 210380 | 9 | lyd
NCONUML | wyk23 | 87622.06 | 45 | wyk
| fgy33 | 11652.67 | 18 | fgy
INDUSTRIAL | hpk22 | 98414.21 | 14 | hpk
NCONUML | sle11 | 59204.61 | 19 | sle
RESIDENTL | bwr13 | 20902397.8318 | 4170 | bwr
COMMERCIAL | rwn34 | 3999387.7688 | 144 | rwn
| hpk22 | 19671.58 | 41 | hpk
FARM | klk22 | 332413.14 | 10 | klk
INDUSTRIAL | wn1 | 2988984.92 | 20 | wn
NCONUML | rwn26 | 27156.61 | 25 | rwn
| bwr33 | 13120.641 | 3 | bwr
NCONUML | mby11 | 20114.34 | 7 | mby
RESIDENTL | smg33 | 11198068.0634 | 2626 | smg
FARM | bn12 | 813334.585 | 146 | bn
FARM | bdl32 | 1026406.0127 | 170 | bdl
FARM | drn24 | 15422429 | 2 | drn
LIGHTING | cre21 | 378603.77 | 3 | cre
RESIDENTL | smg32 | 834640.09 | 219 | smg
| wt12 | 39199.7023 | 19 | wt
FARM | bwn14 | 804408.7 | 76 | bwn
NCONUML | bwr33 | 16865.43 | 3 | bwr
INDUSTRIAL | rwn22 | 12871.85 | 4 | rwn
NCONUML | drn11 | 63307.01 | 20 | drn
INDUSTRIAL | mwl13 | 228128.43 | 11 | mwl
COMMERCIAL | elm22 | 6567142.5918 | 154 | elm
FARM | trc01 | 521142.3328 | 100 | trc
COMMERCIAL | rwt14 | 11855990.576 | 301 | rwt
INDUSTRIAL | sle14 | 1780526.4437 | 64 | sle
RESIDENTL | smr24 | 17064871.7804 | 2952 | smr
FARM | bwa22 | 1586063.9755 | 254 | bwa
NCONUML | tt4 | 37478.54 | 17 | tt
| tt9 | 28146.8116 | 74 | tt
COMMERCIAL | epg34 | 4040655.8363 | 65 | epg
FARM | nrn11 | 7816.07 | 2 | nrn
LIGHTING | cpk23 | 1632459.3 | 1 | cpk
RESIDENTL | fgy31 | 4476808.4262 | 913 | fgy
COMMERCIAL | fgy33 | 6399813.6929 | 132 | fgy
| cnr2 | 20535.9245 | 15 | cnr
INDUSTRIAL | sle32 | 10933678.58 | 25 | sle
| bra13 | 120577.89 | 18 | bra
RESIDENTL | wgi23 | 12118480.0079 | 2685 | wgi
INDUSTRIAL | wn6 | 922850.6842 | 19 | wn
LIGHTING | tgn44 | 752.53 | 1 | tgn
RESIDENTL | wt8 | 8250779.9392 | 1851 | wt
COMMERCIAL | moe25 | 5695010.3572 | 176 | moe
FARM | wgi34 | 4315044.5216 | 374 | wgi
INDUSTRIAL | fgy32 | 667572.7217 | 61 | fgy
NCONUML | wo32 | 55386.46 | 14 | wo
INDUSTRIAL | lys36 | 1267258.48 | 1 | lys
| bn12 | 10728.35 | 13 | bn
NCONUML | brt11 | 10828.27 | 7 | brt
| drn21 | 27694.76 | 39 | drn
| drn24 | 16030.7 | 26 | drn
RESIDENTL | cpk23 | 11646034.7633 | 2466 | cpk
RESIDENTL | wots13 | 7948103.7952 | 1344 | wots
FARM | wgl23 | 3908847.1376 | 390 | wgl
COMMERCIAL | wyk13 | 4417313.7071 | 191 | wyk
NCONUML | klk21 | 10664.54 | 6 | klk
INDUSTRIAL | smg22 | 31514.93 | 2 | smg
RESIDENTL | wgi22 | 12719214.8315 | 3088 | wgi
| cpk13 | 49314.0333 | 41 | cpk
COMMERCIAL | bdl41 | 11311068.2286 | 367 | bdl
NCONUML | nrn12 | 43208.48 | 18 | nrn
RESIDENTL | fgy23 | 5177398.3937 | 1023 | fgy
NCONUML | brt21 | 3240.29 | 5 | brt
NCONUML | tgn31 | 2100.01 | 7 | tgn
RESIDENTL | mjg11 | 6256821.3625 | 1064 | mjg
INDUSTRIAL | lga24 | 175905.212 | 21 | lga
COMMERCIAL | moe21 | 6644337.36 | 291 | moe
INDUSTRIAL | bwn14 | 326743.47 | 17 | bwn
INDUSTRIAL | phm22 | 15545673.5732 | 29 | phm
LIGHTING | klo24 | 2201282.63 | 3 | klo
FARM | epg12 | 13782.33 | 2 | epg
INDUSTRIAL | cln14 | 247.5387 | 1 | cln
FARM | bge13 | 383352.554 | 75 | bge
NCONUML | bra14 | 25509.54 | 26 | bra
RESIDENTL | fgy24 | 17189073.2659 | 3574 | fgy
NCONUML | lyd14 | 37348.84 | 18 | lyd
FARM | fgy21 | 91303 | 9 | fgy
INDUSTRIAL | elm24 | 6476.78 | 2 | elm
FARM | bra24 | 985.88 | 1 | bra
COMMERCIAL | ldl24 | 1420329.0926 | 55 | ldl
INDUSTRIAL | wots24 | 329358.8434 | 32 | wots
| moe13 | 6325.43 | 5 | moe
COMMERCIAL | cyn14 | 5422735.5047 | 221 | cyn
LIGHTING | smg21 | 4640189.26 | 4 | smg
COMMERCIAL | tgn42 | 24454733.755 | 420 | tgn
INDUSTRIAL | lga14 | 502652.15 | 16 | lga
INDUSTRIAL | cre33 | 377497.19 | 17 | cre
FARM | ldl11 | 223383.36 | 16 | ldl
INDUSTRIAL | bn24 | 28582582.13 | 34 | bn
COMMERCIAL | tt1 | 14308038.8686 | 155 | tt
| wn3 | 30735.58 | 33 | wn
NCONUML | ldl21 | 10778.31 | 7 | ldl
NCONUML | wt6 | 188781.23 | 35 | wt
RESIDENTL | elm23 | 20356024.4153 | 3325 | elm
COMMERCIAL | drn11 | 4003224.2127 | 79 | drn
COMMERCIAL | bra34 | 7850026.49 | 9 | bra
FARM | cyn32 | 3133.97 | 2 | cyn
FARM | cpk23 | 18946.87 | 2 | cpk
FARM | wt15 | 5251.96 | 1 | wt
NCONUML | wgi32 | 95036.63 | 31 | wgi
COMMERCIAL | phm32 | 13343791.1884 | 221 | phm
COMMERCIAL | epg22 | 38007492.3668 | 89 | epg
INDUSTRIAL | wgl15 | 1553419.6108 | 26 | wgl
FARM | phm33 | 7138587.5126 | 545 | phm
LIGHTING | bra32 | 1301740.84 | 1 | bra
COMMERCIAL | bra22 | 30448240 | 1 | bra
COMMERCIAL | msd4 | 11090376.2999 | 395 | msd
COMMERCIAL | lyd14 | 7038791.6959 | 51 | lyd
| phi12 | 701365.4285 | 34 | phi
| nrn11 | 5120.38 | 9 | nrn
INDUSTRIAL | smg21 | 777155.28 | 5 | smg
NCONUML | nla31 | 5002.08 | 5 | nla
RESIDENTL | wyk13 | 19583843.7522 | 3346 | wyk
RESIDENTL | tgn41 | 6800482.2089 | 1104 | tgn
COMMERCIAL | fgy34 | 7285642.6158 | 201 | fgy
FARM | wgl11 | 5210774.8775 | 355 | wgl
FARM | tgn11 | 616949.6887 | 82 | tgn
NCONUML | wn5 | 5268.61 | 9 | wn
NCONUML | bdl42 | 6088.6 | 9 | bdl
INDUSTRIAL | hpk23 | 515987.93 | 6 | hpk
FARM | tgn44 | 47621.17 | 6 | tgn
| smr13 | 35140.976 | 19 | smr
| wgi31 | 18377.08 | 37 | wgi
NCONUML | bwr34 | 85519.21 | 30 | bwr
| bdl32 | 24365.9844 | 40 | bdl
COMMERCIAL | fgy13 | 5672167.28 | 57 | fgy
INDUSTRIAL | sle31 | 621920.2305 | 85 | sle
NCONUML | cyn23 | 72679.67 | 24 | cyn
NCONUML | hpk22 | 92149.17 | 38 | hpk
RESIDENTL | cre23 | 13902510.3441 | 3180 | cre
COMMERCIAL | lga21 | 4415159.211 | 179 | lga
| cre33 | 51988.0123 | 70 | cre
INDUSTRIAL | bra32 | 800790.5812 | 33 | bra
| rwn26 | 43959.1499 | 36 | rwn
NCONUML | ftr22 | 27457.1971 | 11 | ftr
FARM | cyn23 | 28738.28 | 3 | cyn
FARM | wn2 | 2722540.844 | 262 | wn
FARM | wots25 | 1192605.1156 | 155 | wots
COMMERCIAL | lga11 | 2601951.4442 | 115 | lga
COMMERCIAL | cnr1 | 836269.15 | 40 | cnr
RESIDENTL | cre22 | 15737441.9951 | 3931 | cre
RESIDENTL | cyn24 | 3227627.7482 | 729 | cyn
| drn14 | 42739.5968 | 43 | drn
NCONUML | wgi34 | 240.62 | 2 | wgi
COMMERCIAL | mdi1 | 200221.43 | 4 | mdi
LIGHTING | lga22 | 290997.27 | 1 | lga
RESIDENTL | sle13 | 2426821.6594 | 1643 | sle
RESIDENTL | mby12 | 3267894.3821 | 609 | mby
FARM | wgi31 | 368672.79 | 43 | wgi
INDUSTRIAL | cyn24 | 15644182.2427 | 207 | cyn
| fgy34 | 3433.61 | 11 | fgy
RESIDENTL | bge11 | 15368827.4604 | 2654 | bge
RESIDENTL | ftr12 | 3825364.7454 | 636 | ftr
| mfa21 | 17049.39 | 26 | mfa
COMMERCIAL | wgi21 | 45541.7604 | 2 | wgi
INDUSTRIAL | wo14 | 2975508 | 24 | wo
COMMERCIAL | wgl12 | 5759083.9004 | 210 | wgl
INDUSTRIAL | moe23 | 765740.5661 | 26 | moe
COMMERCIAL | hpk14 | 5487941.7 | 85 | hpk
NCONUML | tt2 | 10017.24 | 3 | tt
INDUSTRIAL | cpk13 | 1507420.269 | 6 | cpk
INDUSTRIAL | lga41 | 52440142.6 | 1 | lga
NCONUML | elm26 | 60173.53 | 25 | elm
FARM | cf1 | 12492.747 | 1 | cf
RESIDENTL | bwr32 | 11435795.4629 | 2903 | bwr
NCONUML | cln23 | 19017.15 | 5 | cln
RESIDENTL | bdl41 | 18711766.0554 | 3582 | bdl
RESIDENTL | tt4 | 9918702.5206 | 2673 | tt
NCONUML | nrn13 | 44749.68 | 14 | nrn
NCONUML | mwl12 | 43601.75 | 11 | mwl
FARM | cln12 | 30466.72 | 1 | cln
INDUSTRIAL | cpk21 | 122110.94 | 5 | cpk
NCONUML | epg11 | 2275 | 2 | epg
FARM | brt22 | 1064314.9433 | 146 | brt
NCONUML | moe21 | 60919.67 | 15 | moe
RESIDENTL | ldl22 | 4948357.507 | 1104 | ldl
INDUSTRIAL | epg22 | 206880.17 | 13 | epg
NCONUML | cln12 | 55224.6632 | 17 | cln
| wo14 | 16653.0726 | 14 | wo
INDUSTRIAL | wo13 | 14774006.15 | 3 | wo
INDUSTRIAL | wgi22 | 729700.7 | 28 | wgi
COMMERCIAL | msd2 | 2629949.014 | 87 | msd
NCONUML | ldl22 | 11421.24 | 5 | ldl
RESIDENTL | wo22 | 17812297.6729 | 4125 | wo
FARM | mwl25 | 2028215.2676 | 224 | mwl
| cln14 | 46492.03 | 68 | cln
INDUSTRIAL | smr14 | 413387.45 | 34 | smr
FARM | rwn33 | 39914.72 | 5 | rwn
NCONUML | tt7 | 28203.83 | 11 | tt
INDUSTRIAL | lga11 | 317451.8284 | 16 | lga
INDUSTRIAL | tt12 | 6074893.6495 | 86 | tt
INDUSTRIAL | rwn32 | 87972.96 | 1 | rwn
RESIDENTL | myt21 | 10899844.0445 | 1487 | myt
RESIDENTL | cyn14 | 9596207.6734 | 2758 | cyn
RESIDENTL | kms11 | 9874885.3712 | 1972 | kms
COMMERCIAL | wo32 | 9961950.2687 | 147 | wo
NCONUML | hpk21 | 96497.83 | 40 | hpk
FARM | mwl13 | 248036.6173 | 7 | mwl
RESIDENTL | smr23 | 3447913.5369 | 523 | smr
INDUSTRIAL | nla32 | 1443086.18 | 25 | nla
| rwt32 | 35174.87 | 36 | rwt
INDUSTRIAL | moe11 | 65970.59 | 6 | moe
INDUSTRIAL | wo33 | 33298223.9508 | 7 | wo
INDUSTRIAL | bra31 | 2919.84 | 1 | bra
RESIDENTL | moe15 | 9740983.6859 | 1552 | moe
RESIDENTL | moe12 | 4538532.291 | 887 | moe
INDUSTRIAL | bdl41 | 1328921.5447 | 34 | bdl
NCONUML | tt6 | 36560.52 | 20 | tt
RESIDENTL | uwy1 | 6496143.3356 | 1032 | uwy
RESIDENTL | wgi32 | 16438958.2366 | 3917 | wgi
COMMERCIAL | rwn31 | 2125446.8547 | 72 | rwn
| ldl13 | 45979.2126 | 34 | ldl
LIGHTING | hpk23 | 2010173.36 | 1 | hpk
RESIDENTL | fgy14 | 9703108.5669 | 2483 | fgy
FARM | rwn24 | 30208.83 | 4 | rwn
COMMERCIAL | wo23 | 11409957.4027 | 304 | wo
| myt12 | 115131.3847 | 34 | myt
| bge13 | 13458.3255 | 19 | bge
| sle32 | 15918.6359 | 20 | sle
FARM | epg11 | 14625.27 | 2 | epg
NCONUML | mwl21 | 34561.25 | 17 | mwl
COMMERCIAL | nrn12 | 21654160.6835 | 271 | nrn
COMMERCIAL | llg13 | 15983000.2277 | 99 | llg
| lga22 | 14116.8478 | 12 | lga
FARM | hpk11 | 14620.89 | 5 | hpk
RESIDENTL | ofr11 | 25072251.243 | 5672 | ofr
FARM | ftr12 | 9732520.1395 | 879 | ftr
RESIDENTL | epg21 | 580054.4394 | 151 | epg
FARM | bge22 | 343097.1961 | 60 | bge
COMMERCIAL | sfs1 | 1879673.1771 | 124 | sfs
| cln24 | 61460.6675 | 37 | cln
NCONUML | smg22 | 48204.28 | 25 | smg
RESIDENTL | phm34 | 11301839.7716 | 2904 | phm
RESIDENTL | phm31 | 2762476.4376 | 550 | phm
NCONUML | smr13 | 69764.68 | 26 | smr
RESIDENTL | wyk12 | 12357178.5976 | 1789 | wyk
INDUSTRIAL | sle13 | 125251.914 | 47 | sle
FARM | phm24 | 689286.43 | 52 | phm
| cre31 | 63798.4484 | 85 | cre
INDUSTRIAL | bge12 | 121322.77 | 7 | bge
FARM | wots12 | 5076.62 | 1 | wots
NCONUML | cf1 | 1922.85 | 2 | cf
RESIDENTL | wo31 | 20016820.444 | 4554 | wo
FARM | smr22 | 1275801.32 | 154 | smr
FARM | lga22 | 1443457.6222 | 105 | lga
COMMERCIAL | mwl22 | 10003347.9587 | 192 | mwl
FARM | bn24 | 2239563.0749 | 370 | bn
NCONUML | wots25 | 45798.68 | 13 | wots
NCONUML | wgi31 | 79233.36 | 21 | wgi
FARM | epg23 | 30049.96 | 2 | epg
NCONUML | klk11 | 24723.1 | 13 | klk
| mwl14 | 3593.32 | 2 | mwl
RESIDENTL | mdg1 | 4384126.608 | 684 | mdg
RESIDENTL | nrn14 | 9562152.1887 | 1877 | nrn
LIGHTING | msd4 | 139319.89 | 1 | msd
LIGHTING | sfs1 | 1558457.9 | 1 | sfs
| klo14 | 120043.1087 | 185 | klo
RESIDENTL | hpk14 | 17025183.7337 | 3944 | hpk
FARM | lga12 | 4046898.7707 | 351 | lga
COMMERCIAL | ldl14 | 12475957.7156 | 266 | ldl
RESIDENTL | bn11 | 14382992.5485 | 2912 | bn
COMMERCIAL | bdl34 | 6213094.4744 | 204 | bdl
FARM | lyd11 | 23799.7 | 3 | lyd
| mwl22 | 10189.434 | 23 | mwl
NCONUML | cf2 | 120.31 | 1 | cf
| epg32 | 18473.04 | 31 | epg
RESIDENTL | bdl34 | 21922135.2151 | 5106 | bdl
COMMERCIAL | rwn26 | 3719056.4225 | 81 | rwn
INDUSTRIAL | mby13 | 219583.33 | 2 | mby
NCONUML | fgy33 | 40029.49 | 14 | fgy
| ftr22 | 13372.1897 | 14 | ftr
NCONUML | mwl13 | 53127.87 | 17 | mwl
INDUSTRIAL | rwt32 | 132361.99 | 4 | rwt
COMMERCIAL | phm23 | 17053480.4 | 2 | phm
COMMERCIAL | bra13 | 19208526.3529 | 181 | bra
FARM | wn1 | 37241.96 | 7 | wn
FARM | bm8b33 | 1540.9 | 2 | bmb
COMMERCIAL | wt10 | 13883699.3972 | 155 | wt
INDUSTRIAL | uwy1 | 90405.23 | 3 | uwy
RESIDENTL | ldl23 | 26005181.5029 | 4084 | ldl
FARM | klo24 | 194259.84 | 22 | klo
| hpk11 | 33718.6052 | 42 | hpk
NCONUML | phm33 | 47915.862 | 19 | phm
FARM | wn6 | 4543418.3442 | 605 | wn
COMMERCIAL | cyn21 | 3633643.5973 | 195 | cyn
INDUSTRIAL | wo22 | 393144.5 | 11 | wo
RESIDENTL | tgn42 | 795534.2193 | 223 | tgn
INDUSTRIAL | mwl23 | 715134.0252 | 54 | mwl
| rwt22 | 26934.55 | 52 | rwt
COMMERCIAL | phm31 | 4117822.4369 | 32 | phm
RESIDENTL | epg22 | 39578.43 | 14 | epg
RESIDENTL | nla32 | 6559402.1513 | 1220 | nla
RESIDENTL | myt22 | 1017937.6841 | 120 | myt
| wgl15 | 30619.4 | 19 | wgl
LIGHTING | mjg11 | 68938.73 | 1 | mjg
COMMERCIAL | phi12 | 2400712.314 | 73 | phi
COMMERCIAL | rwt36 | 2264519.95 | 43 | rwt
INDUSTRIAL | wgi23 | 157973.74 | 15 | wgi
NCONUML | elm24 | 74942.52 | 25 | elm
RESIDENTL | wt10 | 3332972.5881 | 860 | wt
NCONUML | ruba22 | 360.93 | 3 | ruba
FARM | phi11 | 82538.05 | 19 | phi
| bra11 | 11169.2884 | 32 | bra
INDUSTRIAL | moe15 | 1465208.8927 | 46 | moe
| tt5 | 13084.5535 | 33 | tt
LIGHTING | elm34 | 2971413.79 | 6 | elm
FARM | rwt25 | 33966.32 | 4 | rwt
RESIDENTL | moe11 | 9711471.9521 | 1967 | moe
INDUSTRIAL | rwt22 | 12240.297 | 2 | rwt
FARM | tgn23 | 1979366.6929 | 215 | tgn
COMMERCIAL | elm34 | 4840398.0166 | 153 | elm
NCONUML | phi11 | 19831.48 | 5 | phi
NCONUML | bra13 | 31922.03 | 14 | bra
RESIDENTL | mwl11 | 7113484.1589 | 1047 | mwl
| sle14 | 9929.5555 | 28 | sle
COMMERCIAL | cpk11 | 7316179.79 | 51 | cpk
| cyn31 | 5192.9 | 11 | cyn
NCONUML | epg12 | 1563.57 | 9 | epg
| epg11 | 4794.77 | 9 | epg
INDUSTRIAL | bwa23 | 17470876.21 | 8 | bwa
FARM | cln21 | 792.83 | 1 | cln
COMMERCIAL | wn3 | 8489705.5245 | 275 | wn
COMMERCIAL | bwn12 | 29123057.9665 | 274 | bwn
NCONUML | bra23 | 28962.5293 | 21 | bra
| bge12 | 5967.8256 | 14 | bge
INDUSTRIAL | tgn12 | 464065.58 | 15 | tgn
LIGHTING | fgy31 | 1047083.29 | 1 | fgy
NCONUML | moe25 | 63582.44 | 18 | moe
NCONUML | fgy21 | 30728.13 | 12 | fgy
INDUSTRIAL | lyd11 | 151654.68 | 9 | lyd
FARM | bwn13 | 5960.02 | 1 | bwn
RESIDENTL | lga11 | 6965787.8425 | 1044 | lga
NCONUML | bwr22 | 31744.79 | 14 | bwr
COMMERCIAL | llg12 | 3977405.3306 | 115 | llg
COMMERCIAL | mfa21 | 3716072.0048 | 197 | mfa
INDUSTRIAL | phm32 | 1008.48 | 1 | phm
COMMERCIAL | nrn13 | 3605622.38 | 41 | nrn
FARM | cyn22 | 1131.4275 | 1 | cyn
INDUSTRIAL | ftr23 | 1828762.8842 | 76 | ftr
INDUSTRIAL | mfa31 | 463955.39 | 14 | mfa
INDUSTRIAL | bge11 | 395339.98 | 10 | bge
RESIDENTL | wo13 | 2691801.805 | 586 | wo
RESIDENTL | llg11 | 4969161.4408 | 709 | llg
| cpk21 | 8908.612 | 12 | cpk
INDUSTRIAL | cre23 | 238715.04 | 8 | cre
COMMERCIAL | epg33 | 43303826.6612 | 357 | epg
FARM | ofr21 | 60907.55 | 6 | ofr
COMMERCIAL | cpk22 | 8802072.7366 | 32 | cpk
NCONUML | bra24 | 34184.91 | 27 | bra
NCONUML | wn6 | 84222.69 | 35 | wn
FARM | mfa22 | 15017348.1505 | 702 | mfa
FARM | lga24 | 2675198.7919 | 323 | lga
COMMERCIAL | phi13 | 13565764.588 | 480 | phi
FARM | lga13 | 6142984.8245 | 572 | lga
NCONUML | wn2 | 74469.51 | 25 | wn
COMMERCIAL | wyk23 | 9043742.9219 | 306 | wyk
INDUSTRIAL | cyn31 | 110897.03 | 2 | cyn
RESIDENTL | wt7 | 9398293.9689 | 2293 | wt
COMMERCIAL | rwt15 | 2407529.701 | 118 | rwt
| wots11 | 29868.01 | 43 | wots
COMMERCIAL | wt12 | 9788397.4198 | 246 | wt
FARM | wots24 | 5049980.8194 | 706 | wots
COMMERCIAL | ftr22 | 3919173.7529 | 139 | ftr
INDUSTRIAL | ruba12 | 859698.6565 | 35 | ruba
| wots25 | 37134.4365 | 43 | wots
RESIDENTL | ofr24 | 14317680.0438 | 3420 | ofr
COMMERCIAL | bdl32 | 9327480.3168 | 349 | bdl
NCONUML | trc01 | 2600.11 | 1 | trc
RESIDENTL | wgi33 | 15074294.4922 | 2906 | wgi
RESIDENTL | wyk24 | 16651462.561 | 3130 | wyk
NCONUML | wn1 | 109135.95 | 32 | wn
NCONUML | fgy34 | 69468.4 | 26 | fgy
| tgn43 | 23585.3 | 37 | tgn
| bwn11 | 22540.96 | 33 | bwn
COMMERCIAL | bn11 | 11469939.8143 | 448 | bn
RESIDENTL | wn7 | 334597.06 | 81 | wn
FARM | lga23 | 6580772.0568 | 604 | lga
RESIDENTL | mby13 | 1114988.13 | 129 | mby
INDUSTRIAL | moe12 | 309363.05 | 10 | moe
NCONUML | wgl21 | 72341.71 | 26 | wgl
| rwn22 | 13422.17 | 20 | rwn
FARM | ofr13 | 1726.88 | 2 | ofr
INDUSTRIAL | smg33 | 3791.86 | 1 | smg
COMMERCIAL | cnr2 | 2241662.7301 | 123 | cnr
NCONUML | bwn13 | 114734.08 | 27 | bwn
INDUSTRIAL | tgn43 | 8336.37 | 2 | tgn
NCONUML | bra33 | 54640.5039 | 38 | bra
LIGHTING | drn23 | 137376.82 | 1 | drn
COMMERCIAL | wt11 | 6045415.4763 | 137 | wt
| wo23 | 3425.76 | 13 | wo
RESIDENTL | drn11 | 23689909.4015 | 5897 | drn
RESIDENTL | bra33 | 17227071.6094 | 3920 | bra
FARM | cre21 | 1165190.53 | 9 | cre
| wo32 | 20472.5797 | 26 | wo
NCONUML | mfa22 | 12133.93 | 8 | mfa
COMMERCIAL | fgy32 | 10874129.2215 | 316 | fgy
INDUSTRIAL | bdl33 | 6444229.03 | 34 | bdl
NCONUML | cnr3 | 880.96 | 3 | cnr
COMMERCIAL | bwr14 | 64319.73 | 1 | bwr
NCONUML | ldl11 | 15379.88 | 9 | ldl
FARM | bdl33 | 333127.23 | 48 | bdl
INDUSTRIAL | elm23 | 351538.3612 | 12 | elm
NCONUML | lga14 | 16509.29 | 6 | lga
NCONUML | rwt21 | 45520.76 | 13 | rwt
INDUSTRIAL | mwl24 | 3823292.43 | 15 | mwl
RESIDENTL | epg14 | 8906284.5994 | 2218 | epg
NCONUML | drn21 | 11559.57 | 6 | drn
FARM | ldl21 | 4274.77 | 1 | ldl
| lga14 | 13272.15 | 11 | lga
LIGHTING | wo22 | 1145144.2306 | 3 | wo
LIGHTING | bdl33 | 755365.47 | 1 | bdl
INDUSTRIAL | lga12 | 340570.559 | 7 | lga
RESIDENTL | ofr23 | 20573594.8025 | 3065 | ofr
LIGHTING | tgn12 | 393.8997 | 1 | tgn
RESIDENTL | fgy32 | 4718000.0914 | 1180 | fgy
COMMERCIAL | moe11 | 6876107.6583 | 169 | moe
COMMERCIAL | wgl13 | 16726185.3211 | 289 | wgl
COMMERCIAL | cre22 | 19152716.1468 | 212 | cre
RESIDENTL | drn12 | 16081122.8597 | 3986 | drn
COMMERCIAL | mfa23 | 8005013.26 | 78 | mfa
| cln13 | 39224.5517 | 61 | cln
INDUSTRIAL | mfa22 | 1793714.26 | 36 | mfa
LIGHTING | smr23 | 37560.88 | 1 | smr
RESIDENTL | rwn32 | 6727398.7344 | 1603 | rwn
FARM | lga14 | 4550189.1065 | 436 | lga
| cln12 | 24735.6225 | 51 | cln
COMMERCIAL | kms11 | 4936701.5866 | 120 | kms
RESIDENTL | smr14 | 10997106.9114 | 1697 | smr
| epg13 | 194183.3358 | 102 | epg
| brt21 | 9723.1397 | 7 | brt
INDUSTRIAL | drn12 | 10032.09 | 2 | drn
| tt7 | 34871.95 | 3 | tt
INDUSTRIAL | wots25 | 7153785.931 | 7 | wots
FARM | tgn43 | 14451.81 | 2 | tgn
NCONUML | ldl14 | 38917.21 | 26 | ldl
INDUSTRIAL | brt21 | 238786.6 | 10 | brt
| llg11 | 8477.8 | 10 | llg
RESIDENTL | wgi24 | 12721878.952 | 3596 | wgi
RESIDENTL | cyn21 | 10508542.767 | 2257 | cyn
INDUSTRIAL | bra11 | 3982632.29 | 3 | bra
INDUSTRIAL | phi11 | 184139.3994 | 13 | phi
| hpk24 | 8609.4373 | 14 | hpk
NCONUML | ldl13 | 24965.12 | 22 | ldl
RESIDENTL | hpk21 | 20637351.8958 | 5254 | hpk
RESIDENTL | wgl13 | 19626090.0794 | 4751 | wgl
COMMERCIAL | elm21 | 12124007.57 | 258 | elm
COMMERCIAL | wt13 | 23168272.4303 | 498 | wt
| hpk23 | 55023.71 | 41 | hpk
COMMERCIAL | mdg1 | 1157212.0402 | 52 | mdg
NCONUML | wt11 | 64055.27 | 25 | wt
NCONUML | phm31 | 9383.328 | 4 | phm
COMMERCIAL | bge23 | 4904566.2339 | 176 | bge
NCONUML | smg23 | 17942.69 | 11 | smg
| mwl16 | 4764.4783 | 12 | mwl
COMMERCIAL | hpk12 | 20352329.5415 | 361 | hpk
RESIDENTL | ruba24 | 4395729.6843 | 894 | ruba
COMMERCIAL | nla32 | 3390681.6399 | 175 | nla
NCONUML | lyd12 | 44439.84 | 9 | lyd
| cln22 | 289385.5413 | 85 | cln
NCONUML | cpk21 | 53769.1 | 26 | cpk
| ruba22 | 8482.6526 | 15 | ruba
COMMERCIAL | myt22 | 191990.12 | 18 | myt
RESIDENTL | mby11 | 5261006.6685 | 922 | mby
RESIDENTL | rwn26 | 21195116.3973 | 2454 | rwn
| rwt31 | 14608.62 | 19 | rwt
INDUSTRIAL | epg35 | 1615230.05 | 4 | epg
| bge23 | 30837.693 | 28 | bge
NCONUML | bdl34 | 70291.97 | 25 | bdl
NCONUML | ofr13 | 30258.73 | 11 | ofr
| klk11 | 25230.2094 | 21 | klk
NCONUML | bn12 | 1241.66 | 2 | bn
COMMERCIAL | wgi32 | 5461052.6827 | 195 | wgi
NCONUML | ldl12 | 45990.38 | 14 | ldl
INDUSTRIAL | bra23 | 3394433.4433 | 42 | bra
| wo33 | 4138.8 | 1 | wo
NCONUML | myt12 | 33269.22 | 16 | myt
INDUSTRIAL | ldl11 | 1468879.69 | 10 | ldl
RESIDENTL | msd1 | 8481569.4252 | 1750 | msd
NCONUML | bn11 | 57126.91 | 28 | bn
INDUSTRIAL | ftr12 | 2824402.5 | 31 | ftr
INDUSTRIAL | hpk11 | 29483.41 | 8 | hpk
NCONUML | epg33 | 5589.26 | 2 | epg
COMMERCIAL | wo31 | 10532525.1457 | 139 | wo
| wgl21 | 38182.04 | 53 | wgl
| bge22 | 25062.3495 | 31 | bge
RESIDENTL | tt1 | 171030.69 | 8 | tt
INDUSTRIAL | bwr34 | 134229.36 | 26 | bwr
COMMERCIAL | bra33 | 14409139.6368 | 303 | bra
COMMERCIAL | bdl44 | 4495186.894 | 197 | bdl
| bwn13 | 12482.8878 | 14 | bwn
NCONUML | wn3 | 40552.61 | 16 | wn
NCONUML | smr24 | 41055.27 | 16 | smr
INDUSTRIAL | mwl14 | 4499194.0326 | 50 | mwl
| wots24 | 36833.8626 | 36 | wots
NCONUML | wt12 | 74491.29 | 36 | wt
COMMERCIAL | smg31 | 17181337.4 | 81 | smg
FARM | lyd13 | 146611.14 | 18 | lyd
NCONUML | wots12 | 53576.05 | 15 | wots
INDUSTRIAL | fgy12 | 30820.7097 | 2 | fgy
FARM | myt12 | 4025860.4278 | 600 | myt
INDUSTRIAL | cyn22 | 204983.76 | 12 | cyn
COMMERCIAL | cyn33 | 3196035.4476 | 122 | cyn
COMMERCIAL | mby12 | 1853426.4391 | 89 | mby
NCONUML | tgn43 | 111938.06 | 34 | tgn
NCONUML | wo11 | 17571.55 | 5 | wo
INDUSTRIAL | epg12 | 1405424.52 | 3 | epg
| cf2 | 30699.57 | 2 | cf
COMMERCIAL | llg11 | 3213282.749 | 85 | llg
LIGHTING | rwn24 | 1936572.72 | 3 | rwn
INDUSTRIAL | cln24 | 15633.29 | 3 | cln
FARM | sle31 | 4999785.6618 | 315 | sle
INDUSTRIAL | cf1 | 129164.746 | 4 | cf
| ruba12 | 126134.0367 | 24 | ruba
| bwr12 | 18318.3952 | 15 | bwr
FARM | elm32 | 382389.8968 | 32 | elm
| ofr21 | 113717.1 | 52 | ofr
INDUSTRIAL | wn2 | 282430.54 | 13 | wn
NCONUML | bge22 | 82280.88 | 49 | bge
NCONUML | cnr2 | 33661.17 | 17 | cnr
NCONUML | wots13 | 10386.18 | 6 | wots
FARM | elm24 | 39172.3194 | 4 | elm
COMMERCIAL | nrn14 | 6896476.1265 | 116 | nrn
NCONUML | ruba12 | 27603.68 | 16 | ruba
NCONUML | hpk13 | 50290.3 | 16 | hpk
NCONUML | bra11 | 44798.92 | 35 | bra
| rwt21 | 23376.2409 | 6 | rwt
RESIDENTL | drn23 | 20613814.4846 | 2434 | drn
RESIDENTL | rwt36 | 2676215.9999 | 821 | rwt
RESIDENTL | llg13 | 6857833.0372 | 1230 | llg
COMMERCIAL | wyk12 | 4295149.2844 | 131 | wyk
INDUSTRIAL | ofr13 | 1622296.11 | 21 | ofr
| bra14 | 30334.7783 | 42 | bra
INDUSTRIAL | tgn11 | 3321263.75 | 18 | tgn
LIGHTING | mby13 | 9944.78 | 1 | mby
RESIDENTL | cln11 | 39284605.9906 | 12154 | cln
COMMERCIAL | drn22 | 10741065.2473 | 246 | drn
RESIDENTL | wo32 | 11244170.0715 | 2343 | wo
| bra33 | 27895.4569 | 47 | bra
COMMERCIAL | epg21 | 21867278.1603 | 75 | epg
INDUSTRIAL | cre21 | 293542.6 | 2 | cre
RESIDENTL | bwr24 | 1834966.95 | 415 | bwr
RESIDENTL | hpk13 | 8888406.848 | 2283 | hpk
NCONUML | moe13 | 240.62 | 2 | moe
RESIDENTL | mwl12 | 3605926.3697 | 887 | mwl
| elm24 | 29520.3106 | 27 | elm
COMMERCIAL | tgn31 | 5251765.7474 | 163 | tgn
| rwt25 | 17882.0217 | 23 | rwt
RESIDENTL | moe21 | 9438147.1697 | 1978 | moe
COMMERCIAL | mjg11 | 16973320.0649 | 258 | mjg
COMMERCIAL | moe22 | 1619971.835 | 34 | moe
NCONUML | cpk13 | 44472.2623 | 32 | cpk
| phi11 | 13149.9006 | 9 | phi
FARM | cyn11 | 2814.65 | 1 | cyn
FARM | cyn24 | 25049.8 | 2 | cyn
FARM | drn13 | 379220.8035 | 25 | drn
COMMERCIAL | mwe236 | 663523.2 | 21 | mwe
INDUSTRIAL | phm24 | 35612.08 | 4 | phm
INDUSTRIAL | bge22 | 36211.2493 | 9 | bge
RESIDENTL | cnr1 | 478523.9112 | 104 | cnr
| lga24 | 10918.35 | 11 | lga
NCONUML | sle14 | 98131.7526 | 34 | sle
NCONUML | tt5 | 14462.54 | 12 | tt
| epg12 | 53720.6497 | 70 | epg
NCONUML | kms11 | 42647.24 | 13 | kms
FARM | elm23 | 38507.8 | 8 | elm
COMMERCIAL | cyn12 | 12045879.7132 | 241 | cyn
INDUSTRIAL | fgy23 | 1420677.79 | 11 | fgy
COMMERCIAL | mfa14 | 259168.13 | 17 | mfa
| bra31 | 49797.7422 | 13 | bra
COMMERCIAL | mwl12 | 1780079.4127 | 78 | mwl
| bwr22 | 2405.71 | 25 | bwr
INDUSTRIAL | fgy24 | 415478.9 | 15 | fgy
COMMERCIAL | hpk13 | 9763023.5697 | 134 | hpk
| cyn22 | 22272.33 | 22 | cyn
| ldl21 | 13369.5383 | 42 | ldl
| wt6 | 17591.4373 | 23 | wt
RESIDENTL | wn4 | 11276854.4814 | 2349 | wn
FARM | mwl14 | 451834.7532 | 54 | mwl
RESIDENTL | bm8b31 | 357131.6719 | 111 | bmb
NCONUML | cyn14 | 48577.9677 | 22 | cyn
FARM | cre32 | 5136.47 | 1 | cre
FARM | bwr34 | 4550.33 | 1 | bwr
RESIDENTL | llg14 | 14855712.1657 | 2170 | llg
FARM | smg33 | 29400.19 | 7 | smg
RESIDENTL | drn22 | 21996972.8148 | 3999 | drn
NCONUML | elm32 | 42948.38 | 25 | elm
INDUSTRIAL | klo14 | 587332.99 | 17 | klo
| tgn11 | 22256.53 | 32 | tgn
INDUSTRIAL | tgn44 | 4536032.57 | 9 | tgn
COMMERCIAL | ldl23 | 15994398.5627 | 272 | ldl
| wn6 | 146062.0009 | 59 | wn
COMMERCIAL | tt2 | 18806104.6367 | 399 | tt
COMMERCIAL | brt11 | 4047117.81 | 129 | brt
NCONUML | llg14 | 65195.01 | 40 | llg
FARM | fgy24 | 95940.3 | 9 | fgy
NCONUML | fgy14 | 61562.37 | 33 | fgy
COMMERCIAL | rve12 | 3272242.91 | 54 | rve
INDUSTRIAL | cpk23 | 208291.634 | 5 | cpk
| lga23 | 41697.3391 | 21 | lga
INDUSTRIAL | yn38 | 642769.3081 | 6 | yn
COMMERCIAL | bwa21 | 7920817.52 | 6 | bwa
INDUSTRIAL | elm25 | 2097.04 | 1 | elm
COMMERCIAL | wots13 | 3416108.1488 | 213 | wots
FARM | wgi22 | 191494.2501 | 24 | wgi
NCONUML | fgy13 | 27847.71 | 7 | fgy
| bra24 | 9840.15 | 27 | bra
FARM | ofr14 | 100163.6258 | 21 | ofr
NCONUML | nrn11 | 16820.36 | 5 | nrn
RESIDENTL | smg31 | 12434679.8443 | 2879 | smg
COMMERCIAL | smr24 | 15083854.4686 | 348 | smr
| lyd11 | 12152.66 | 25 | lyd
INDUSTRIAL | bra12 | 1282907.1727 | 55 | bra
FARM | wgl15 | 3297105.6723 | 233 | wgl
INDUSTRIAL | msd1 | 544058.7154 | 15 | msd
| epg31 | 13971.3347 | 31 | epg
INDUSTRIAL | wgl23 | 572354.5027 | 44 | wgl
INDUSTRIAL | cpk12 | 343353.79 | 14 | cpk
INDUSTRIAL | mfa34 | 4790944.63 | 37 | mfa
| wn2 | 65478.1843 | 60 | wn
INDUSTRIAL | drn23 | 222019.33 | 21 | drn
| klo11 | 24997.4 | 1 | klo
COMMERCIAL | cyn13 | 11562540.4133 | 213 | cyn
| tgn44 | 15598.29 | 27 | tgn
| wn1 | 5093 | 9 | wn
NCONUML | wots24 | 22958.48 | 11 | wots
RESIDENTL | ftr21 | 5974099.1685 | 1654 | ftr
NCONUML | wgl11 | 116770.29 | 32 | wgl
FARM | phm22 | 2513172.8482 | 159 | phm
| mfa22 | 25912.0235 | 15 | mfa
| tt2 | 5693.01 | 1 | tt
RESIDENTL | cyn12 | 11384819.6049 | 2642 | cyn
COMMERCIAL | mby11 | 1920906.95 | 83 | mby
RESIDENTL | bdl42 | 7579399.6648 | 1528 | bdl
COMMERCIAL | sle11 | 16789466.3124 | 430 | sle
COMMERCIAL | bdl42 | 3935066.2305 | 228 | bdl
NCONUML | rwn22 | 25304.89 | 19 | rwn
INDUSTRIAL | cre32 | 1414910.91 | 33 | cre
INDUSTRIAL | bwn11 | 121807.37 | 8 | bwn
NCONUML | smr22 | 29006.3 | 13 | smr
RESIDENTL | phm24 | 12991887.5254 | 2975 | phm
RESIDENTL | phm21 | 5600884.0097 | 1319 | phm
NCONUML | ldl23 | 93357.12 | 44 | ldl
RESIDENTL | ldl24 | 19255310.9766 | 3964 | ldl
INDUSTRIAL | bra21 | 9682528.358 | 10 | bra
| sle31 | 21276.5675 | 34 | sle
| myt11 | 11671.01 | 10 | myt
RESIDENTL | elm21 | 10927220.6891 | 2208 | elm
COMMERCIAL | epg13 | 13081700.0195 | 121 | epg
COMMERCIAL | hpk21 | 6771211.022 | 80 | hpk
NCONUML | bwr12 | 55323.1848 | 22 | bwr
| trc01 | 7370.1419 | 1 | trc
| epg35 | 12733.43 | 3 | epg
INDUSTRIAL | bge21 | 30163.23 | 3 | bge
RESIDENTL | tgn31 | 10330935.5842 | 1504 | tgn
COMMERCIAL | moe23 | 8180066.6029 | 204 | moe
FARM | bra21 | 5211.11 | 2 | bra
LIGHTING | llg12 | 9573.66 | 1 | llg
RESIDENTL | bdl31 | 18828777.9984 | 3534 | bdl
COMMERCIAL | nla31 | 1365542.8767 | 73 | nla
INDUSTRIAL | klo24 | 421040.3606 | 14 | klo
FARM | bdl43 | 35833.9 | 4 | bdl
FARM | cyn31 | 3324.08 | 1 | cyn
FARM | sle14 | 508528.62 | 59 | sle
FARM | fgy34 | 3609.3 | 1 | fgy
RESIDENTL | elm26 | 19204314.084 | 3128 | elm
COMMERCIAL | ldl13 | 4974121.0157 | 271 | ldl
NCONUML | tgn42 | 32526.3 | 9 | tgn
RESIDENTL | nrn13 | 11128338.9236 | 2708 | nrn
| drn13 | 33230.29 | 35 | drn
RESIDENTL | mfa14 | 15628.16 | 8 | mfa
RESIDENTL | rwt14 | 5266292.5405 | 1232 | rwt
FARM | ftr23 | 7584335.745 | 587 | ftr
FARM | moe12 | 2890738.1544 | 266 | moe
RESIDENTL | klk21 | 6022162.144 | 692 | klk
COMMERCIAL | bn22 | 11917129.8815 | 407 | bn
COMMERCIAL | cln13 | 10498926.3291 | 102 | cln
INDUSTRIAL | cln11 | 955300.36 | 11 | cln
FARM | bge11 | 1450445.3683 | 132 | bge
| mwl25 | 368.2898 | 2 | mwl
| rwn33 | 13688.96 | 19 | rwn
| bdl43 | 33766.9817 | 15 | bdl
NCONUML | cln14 | 95979.5703 | 31 | cln
NCONUML | lga24 | 7306.35 | 4 | lga
| bn23 | 36133.4118 | 23 | bn
| ofr14 | 18460.3638 | 32 | ofr
FARM | wo14 | 29381.84 | 3 | wo
FARM | cln24 | 15169.45 | 1 | cln
FARM | smg21 | 2813.13 | 1 | smg
FARM | uwy1 | 50419.26 | 6 | uwy
RESIDENTL | cpk11 | 18255270.9798 | 3705 | cpk
INDUSTRIAL | rwn34 | 151721.8975 | 12 | rwn
FARM | mfa34 | 8352796.4311 | 398 | mfa
INDUSTRIAL | cyn23 | 283668.3977 | 39 | cyn
COMMERCIAL | cln23 | 7919442.4187 | 94 | cln
| rwn24 | 145239.1574 | 36 | rwn
INDUSTRIAL | cln21 | 91173.7471 | 8 | cln
INDUSTRIAL | wots23 | 9771996.01 | 2 | wots
COMMERCIAL | ofr23 | 7962081.4442 | 137 | ofr
FARM | cln11 | 5358747.3528 | 175 | cln
INDUSTRIAL | epg23 | 1603069.098 | 49 | epg
NCONUML | elm33 | 106570.09 | 33 | elm
| tt6 | 16214.4725 | 50 | tt
NCONUML | lga12 | 120.31 | 1 | lga
RESIDENTL | moe25 | 15202048.016 | 3044 | moe
RESIDENTL | moe22 | 6183768.6959 | 1343 | moe
RESIDENTL | mfa23 | 1535883.9368 | 206 | mfa
FARM | rwn22 | 76017.25 | 13 | rwn
COMMERCIAL | fgy31 | 26687.08 | 5 | fgy
RESIDENTL | elm33 | 17751529.9107 | 3238 | elm
COMMERCIAL | ldl22 | 7642772.3181 | 272 | ldl
NCONUML | llg11 | 13058.17 | 7 | llg
| ruba24 | 72607.09 | 10 | ruba
FARM | rwt32 | 21924.18 | 3 | rwt
FARM | ruba12 | 5735958.293 | 534 | ruba
FARM | brt21 | 526055.8565 | 65 | brt
| rwt15 | 24735.76 | 50 | rwt
NCONUML | bge13 | 40077 | 45 | bge
COMMERCIAL | klk21 | 1344972.0506 | 75 | klk
INDUSTRIAL | msd4 | 532825.24 | 27 | msd
| mwl21 | 2371.576 | 7 | mwl
RESIDENTL | wt9 | 13126762.7947 | 2901 | wt
FARM | wgi23 | 957555.9102 | 143 | wgi
| wgl24 | 12928.4076 | 27 | wgl
NCONUML | tgn11 | 50804.93 | 14 | tgn
LIGHTING | hpk22 | 402155.12 | 2 | hpk
INDUSTRIAL | wt13 | 198794.34 | 24 | wt
LIGHTING | wots24 | 69082.45 | 1 | wots
| ofr13 | 25120.5182 | 29 | ofr
| cre21 | 98632.2224 | 69 | cre
| smg22 | 13378.71 | 23 | smg
COMMERCIAL | tt4 | 4770691.1401 | 169 | tt
COMMERCIAL | elm26 | 2765254.86 | 47 | elm
NCONUML | bwa22 | 120.31 | 1 | bwa
| cyn23 | 386495.78 | 52 | cyn
INDUSTRIAL | nla34 | 227255.6563 | 13 | nla
FARM | mwl22 | 63.01 | 1 | mwl
| cf1 | 5771.13 | 3 | cf
NCONUML | cpk22 | 15413.02 | 10 | cpk
NCONUML | lyd13 | 28195.47 | 10 | lyd
NCONUML | cre31 | 35482.06 | 18 | cre
COMMERCIAL | wo11 | 6006584.4175 | 54 | wo
INDUSTRIAL | wt7 | 2382042.5333 | 25 | wt
| bwr34 | 19530.96 | 64 | bwr
NCONUML | bge23 | 57838.96 | 34 | bge
INDUSTRIAL | tgn23 | 187420.5 | 24 | tgn
RESIDENTL | cyn33 | 17836008.3498 | 3662 | cyn
RESIDENTL | nla34 | 7124747.0562 | 1408 | nla
| wgl11 | 21820.8596 | 38 | wgl
COMMERCIAL | bn12 | 3658135.6563 | 31 | bn
| mwl13 | 7054.2121 | 17 | mwl
COMMERCIAL | rwt26 | 65754589.65 | 1 | rwt
FARM | wt9 | 2789.4 | 1 | wt
RESIDENTL | bdl44 | 10906570.4152 | 1766 | bdl
FARM | cre33 | 2156267.3416 | 81 | cre
COMMERCIAL | wgl21 | 7364849.9167 | 150 | wgl
COMMERCIAL | wn5 | 3727109.367 | 208 | wn
NCONUML | mwl22 | 81020 | 27 | mwl
NCONUML | bn24 | 14677.57 | 9 | bn
| smr22 | 9887.67 | 15 | smr
|  | 8782.36 | 2 | #REF!
RESIDENTL | sle11 | 5311421.2716 | 1344 | sle
RESIDENTL | nw13 | 126364.0108 | 18 | nw
RESIDENTL | ftr23 | 12909653.9148 | 2620 | ftr
COMMERCIAL | mwl11 | 1278518.3133 | 72 | mwl
LIGHTING | llg13 | 66328.6913 | 1 | llg
NCONUML | klk22 | 2600.11 | 1 | klk
RESIDENTL | wyk23 | 22445865.182 | 3391 | wyk
COMMERCIAL | wt6 | 6354339.6482 | 191 | wt
RESIDENTL | brt11 | 6592458.6386 | 1001 | brt
NCONUML | tt9 | 66916.75 | 41 | tt
FARM | smr14 | 4406259.38 | 487 | smr
NCONUML | epg32 | 55568.91 | 13 | epg
RESIDENTL | rwn31 | 17135173.2235 | 2210 | rwn
| phm33 | 20993.1171 | 27 | phm
NCONUML | myt11 | 6079.5 | 6 | myt
RESIDENTL | nrn12 | 2807836.1314 | 591 | nrn
COMMERCIAL | mwl16 | 411566.3345 | 42 | mwl
INDUSTRIAL | lga23 | 1068068.6578 | 23 | lga
COMMERCIAL | ldl12 | 15390056.6509 | 380 | ldl
FARM | nla34 | 624678.3932 | 78 | nla
COMMERCIAL | rve13 | 1685040.429 | 44 | rve
NCONUML | drn24 | 11009.3526 | 4 | drn
COMMERCIAL | myt21 | 6919383.7104 | 251 | myt
FARM | moe13 | 3478506.4958 | 306 | moe
COMMERCIAL | mwl21 | 9182796.6603 | 240 | mwl
NCONUML | wgl15 | 97647.0301 | 36 | wgl
| bwn14 | 31300.22 | 31 | bwn
RESIDENTL | cpk22 | 8203984.593 | 1482 | cpk
RESIDENTL | rve12 | 17634581.2748 | 3656 | rve
RESIDENTL | phi13 | 17016004.0328 | 4317 | phi
RESIDENTL | hpk12 | 5058413.1519 | 1238 | hpk
COMMERCIAL | ruba24 | 4555190.3466 | 105 | ruba
FARM | cln14 | 51639.06 | 13 | cln
INDUSTRIAL | wt9 | 148098.11 | 5 | wt
| smg21 | 44014.37 | 27 | smg
INDUSTRIAL | smr23 | 883845.12 | 6 | smr

## Forecast - Summer
Forecasting Application - 13/10/2025
asset_type | asset | extremum | scenario | demand_year | season | poe | customer_count | pv_capacity | value | forecast_round | unit | region
zone_sub | cln | maximum |  | 2022 | Summer | 50 | 38619 | 72.2578 | 77.9086 | 202503 | MVA | central
zone_sub | cln | maximum |  | 2022 | Summer | 10 | 38619 | 72.2578 | 91.3183 | 202503 | MVA | central
zone_sub | cln | maximum |  | 2023 | Summer | 10 | 41429 | 81.3604 | 97.5884 | 202503 | MVA | central
zone_sub | cln | maximum |  | 2023 | Summer | 50 | 41429 | 81.3604 | 83.3369 | 202503 | MVA | central
zone_sub | cln | maximum |  | 2024 | Summer | 10 | 44846 | 94.6588 | 104.9463 | 202503 | MVA | central
zone_sub | cln | maximum |  | 2024 | Summer | 50 | 44846 | 94.6588 | 89.7351 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2025 | Summer | 10 |  |  | 119.6766 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2025 | Summer | 50 |  |  | 104.3341 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2026 | Summer | 10 |  |  | 124.2514 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2026 | Summer | 50 |  |  | 108.3435 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2027 | Summer | 10 |  |  | 128.0364 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2027 | Summer | 50 |  |  | 111.4611 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2028 | Summer | 10 |  |  | 131.3686 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2028 | Summer | 50 |  |  | 115.2173 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2029 | Summer | 10 |  |  | 136.7682 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2029 | Summer | 50 |  |  | 119.0984 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2030 | Summer | 10 |  |  | 141.634 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2030 | Summer | 50 |  |  | 123.2461 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2031 | Summer | 10 |  |  | 148.4809 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2031 | Summer | 50 |  |  | 128.0275 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2032 | Summer | 10 |  |  | 155.6302 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2032 | Summer | 50 |  |  | 133.6994 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2033 | Summer | 10 |  |  | 161.4365 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2033 | Summer | 50 |  |  | 139.0092 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2034 | Summer | 10 |  |  | 166.8996 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2034 | Summer | 50 |  |  | 144.6013 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2035 | Summer | 10 |  |  | 175.1342 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2035 | Summer | 50 |  |  | 154.2938 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2036 | Summer | 10 |  |  | 181.0486 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2036 | Summer | 50 |  |  | 157.43 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2037 | Summer | 10 |  |  | 187.0195 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2037 | Summer | 50 |  |  | 163.5566 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2038 | Summer | 10 |  |  | 193.3671 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2038 | Summer | 50 |  |  | 168.1999 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2039 | Summer | 10 |  |  | 192.0421 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2039 | Summer | 50 |  |  | 167.0472 | 202503 | MVA | central
zone_sub | cre | maximum |  | 2022 | Summer | 10 | 24937 | 39.5122 | 71.3044 | 202503 | MVA | central
zone_sub | cre | maximum |  | 2022 | Summer | 50 | 24937 | 39.5122 | 64.1683 | 202503 | MVA | central
zone_sub | cre | maximum |  | 2023 | Summer | 10 | 25835 | 43.8704 | 73.6781 | 202503 | MVA | central
zone_sub | cre | maximum |  | 2023 | Summer | 50 | 25835 | 43.8704 | 65.8328 | 202503 | MVA | central
zone_sub | cre | maximum |  | 2024 | Summer | 10 | 26314 | 48.9572 | 74.7994 | 202503 | MVA | central
zone_sub | cre | maximum |  | 2024 | Summer | 50 | 26314 | 48.9572 | 66.0879 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2025 | Summer | 10 |  |  | 89.8342 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2025 | Summer | 50 |  |  | 80.6612 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2026 | Summer | 10 |  |  | 90.653 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2026 | Summer | 50 |  |  | 81.4056 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2027 | Summer | 10 |  |  | 89.7773 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2027 | Summer | 50 |  |  | 80.6131 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2028 | Summer | 10 |  |  | 94.9573 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2028 | Summer | 50 |  |  | 85.9509 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2029 | Summer | 10 |  |  | 94.8385 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2029 | Summer | 50 |  |  | 85.6114 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2030 | Summer | 10 |  |  | 96.1186 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2030 | Summer | 50 |  |  | 85.7941 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2031 | Summer | 10 |  |  | 97.2062 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2031 | Summer | 50 |  |  | 86.4866 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2032 | Summer | 10 |  |  | 98.0786 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2032 | Summer | 50 |  |  | 87.2925 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2033 | Summer | 10 |  |  | 98.8781 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2033 | Summer | 50 |  |  | 88.2343 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2034 | Summer | 10 |  |  | 99.6475 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2034 | Summer | 50 |  |  | 88.9575 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2035 | Summer | 10 |  |  | 99.2707 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2035 | Summer | 50 |  |  | 89.8044 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2036 | Summer | 10 |  |  | 99.9981 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2036 | Summer | 50 |  |  | 89.5675 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2037 | Summer | 10 |  |  | 101.1509 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2037 | Summer | 50 |  |  | 90.5821 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2038 | Summer | 10 |  |  | 101.3208 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2038 | Summer | 50 |  |  | 90.3196 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2039 | Summer | 10 |  |  | 99.6095 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2039 | Summer | 50 |  |  | 88.5146 | 202503 | MVA | central
zone_sub | epg | maximum |  | 2022 | Summer | 10 | 29371 | 40.0067 | 87.2498 | 202503 | MVA | central
zone_sub | epg | maximum |  | 2022 | Summer | 50 | 29371 | 40.0067 | 72.9666 | 202503 | MVA | central
zone_sub | epg | maximum |  | 2023 | Summer | 10 | 30422 | 45.1511 | 90.3071 | 202503 | MVA | central
zone_sub | epg | maximum |  | 2023 | Summer | 50 | 30422 | 45.1511 | 75.7012 | 202503 | MVA | central
zone_sub | epg | maximum |  | 2024 | Summer | 10 | 32118 | 51.557 | 95.8895 | 202503 | MVA | central
zone_sub | epg | maximum |  | 2024 | Summer | 50 | 32118 | 51.557 | 79.9844 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2025 | Summer | 10 |  |  | 109.0669 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2025 | Summer | 50 |  |  | 92.5622 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2026 | Summer | 10 |  |  | 118.5447 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2026 | Summer | 50 |  |  | 101.6723 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2027 | Summer | 10 |  |  | 121.4869 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2027 | Summer | 50 |  |  | 104.4042 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2028 | Summer | 10 |  |  | 119.8786 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2028 | Summer | 50 |  |  | 102.6031 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2029 | Summer | 10 |  |  | 121.9204 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2029 | Summer | 50 |  |  | 105.5757 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2030 | Summer | 10 |  |  | 124.6444 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2030 | Summer | 50 |  |  | 106.371 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2031 | Summer | 10 |  |  | 127.5507 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2031 | Summer | 50 |  |  | 110.1341 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2032 | Summer | 10 |  |  | 131.8742 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2032 | Summer | 50 |  |  | 112.2581 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2033 | Summer | 10 |  |  | 136.3355 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2033 | Summer | 50 |  |  | 113.9316 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2034 | Summer | 10 |  |  | 140.9437 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2034 | Summer | 50 |  |  | 117.5793 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2035 | Summer | 10 |  |  | 144.5914 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2035 | Summer | 50 |  |  | 120.4726 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2036 | Summer | 50 |  |  | 128.0797 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2036 | Summer | 10 |  |  | 149.6115 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2037 | Summer | 10 |  |  | 152.9797 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2037 | Summer | 50 |  |  | 129.922 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2038 | Summer | 10 |  |  | 155.1715 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2038 | Summer | 50 |  |  | 132.5568 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2039 | Summer | 10 |  |  | 152.1644 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2039 | Summer | 50 |  |  | 125.7761 | 202503 | MVA | central
zone_sub | klo | maximum |  | 2022 | Summer | 10 | 14879 | 23.0226 | 53.5677 | 202503 | MVA | central
zone_sub | klo | maximum |  | 2022 | Summer | 50 | 14879 | 23.0226 | 41.9423 | 202503 | MVA | central
zone_sub | klo | maximum |  | 2023 | Summer | 10 | 17175 | 27.7177 | 61.121 | 202503 | MVA | central
zone_sub | klo | maximum |  | 2023 | Summer | 50 | 17175 | 27.7177 | 48.3019 | 202503 | MVA | central
zone_sub | klo | maximum |  | 2024 | Summer | 10 | 19951 | 34.2052 | 70.1897 | 202503 | MVA | central
zone_sub | klo | maximum |  | 2024 | Summer | 50 | 19951 | 34.2052 | 55.7613 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2025 | Summer | 10 |  |  | 83.6879 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2025 | Summer | 50 |  |  | 68.2523 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2026 | Summer | 10 |  |  | 94.1984 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2026 | Summer | 50 |  |  | 77.9353 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2027 | Summer | 10 |  |  | 102.4436 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2027 | Summer | 50 |  |  | 84.7194 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2028 | Summer | 10 |  |  | 118.3247 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2028 | Summer | 50 |  |  | 99.6669 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2029 | Summer | 10 |  |  | 126.3487 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2029 | Summer | 50 |  |  | 106.8624 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2030 | Summer | 10 |  |  | 135.5692 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2030 | Summer | 50 |  |  | 115.5707 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2031 | Summer | 10 |  |  | 148.561 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2031 | Summer | 50 |  |  | 127.0156 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2032 | Summer | 10 |  |  | 164.8827 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2032 | Summer | 50 |  |  | 137.8179 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2033 | Summer | 10 |  |  | 180.5841 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2033 | Summer | 50 |  |  | 151.2391 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2034 | Summer | 10 |  |  | 196.9964 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2034 | Summer | 50 |  |  | 164.8814 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2035 | Summer | 10 |  |  | 212.9758 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2035 | Summer | 50 |  |  | 181.5355 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2036 | Summer | 10 |  |  | 230.0573 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2036 | Summer | 50 |  |  | 195.8954 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2037 | Summer | 10 |  |  | 248.4456 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2037 | Summer | 50 |  |  | 212.2991 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2038 | Summer | 10 |  |  | 266.5409 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2038 | Summer | 50 |  |  | 225.6959 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2039 | Summer | 10 |  |  | 272.6357 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2039 | Summer | 50 |  |  | 228.9049 | 202503 | MVA | central
zone_sub | ofr | maximum |  | 2022 | Summer | 10 | 23246 | 35.5119 | 59.9776 | 202503 | MVA | central
zone_sub | ofr | maximum |  | 2022 | Summer | 50 | 23246 | 35.5119 | 53.856 | 202503 | MVA | central
zone_sub | ofr | maximum |  | 2023 | Summer | 10 | 24109 | 39.5748 | 62.0639 | 202503 | MVA | central
zone_sub | ofr | maximum |  | 2023 | Summer | 50 | 24109 | 39.5748 | 55.451 | 202503 | MVA | central
zone_sub | ofr | maximum |  | 2024 | Summer | 10 | 24997 | 44.4669 | 64.073 | 202503 | MVA | central
zone_sub | ofr | maximum |  | 2024 | Summer | 50 | 24997 | 44.4669 | 56.9594 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2025 | Summer | 10 |  |  | 69.589 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2025 | Summer | 50 |  |  | 61.9907 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2026 | Summer | 10 |  |  | 76.597 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2026 | Summer | 50 |  |  | 68.9791 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2027 | Summer | 10 |  |  | 81.5678 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2027 | Summer | 50 |  |  | 74.0072 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2028 | Summer | 10 |  |  | 84.5283 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2028 | Summer | 50 |  |  | 76.6284 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2029 | Summer | 10 |  |  | 86.8984 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2029 | Summer | 50 |  |  | 78.9811 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2030 | Summer | 10 |  |  | 88.8048 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2030 | Summer | 50 |  |  | 80.4506 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2031 | Summer | 10 |  |  | 90.6365 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2031 | Summer | 50 |  |  | 82.1352 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2032 | Summer | 10 |  |  | 92.2256 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2032 | Summer | 50 |  |  | 83.4813 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2033 | Summer | 10 |  |  | 92.9929 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2033 | Summer | 50 |  |  | 84.3346 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2034 | Summer | 10 |  |  | 94.1573 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2034 | Summer | 50 |  |  | 86.446 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2035 | Summer | 10 |  |  | 95.4952 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2035 | Summer | 50 |  |  | 87.894 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2036 | Summer | 10 |  |  | 96.8516 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2036 | Summer | 50 |  |  | 88.627 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2037 | Summer | 10 |  |  | 98.5806 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2037 | Summer | 50 |  |  | 90.0391 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2038 | Summer | 10 |  |  | 98.8168 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2038 | Summer | 50 |  |  | 89.5765 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2039 | Summer | 10 |  |  | 97.8239 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2039 | Summer | 50 |  |  | 88.3981 | 202503 | MVA | central
zone_sub | phm | maximum |  | 2022 | Summer | 50 | 16270 | 23.521 | 51.4174 | 202503 | MVA | central
zone_sub | phm | maximum |  | 2022 | Summer | 10 | 16270 | 23.521 | 56.9097 | 202503 | MVA | central
zone_sub | phm | maximum |  | 2023 | Summer | 10 | 16562 | 25.5412 | 57.758 | 202503 | MVA | central
zone_sub | phm | maximum |  | 2023 | Summer | 50 | 16562 | 25.5412 | 52.1386 | 202503 | MVA | central
zone_sub | phm | maximum |  | 2024 | Summer | 10 | 16854 | 27.7496 | 58.7282 | 202503 | MVA | central
zone_sub | phm | maximum |  | 2024 | Summer | 50 | 16854 | 27.7496 | 52.8621 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2025 | Summer | 10 |  |  | 75.5207 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2025 | Summer | 50 |  |  | 69.621 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2026 | Summer | 10 |  |  | 79.8845 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2026 | Summer | 50 |  |  | 74.1527 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2027 | Summer | 10 |  |  | 79.6008 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2027 | Summer | 50 |  |  | 73.9998 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2028 | Summer | 10 |  |  | 79.5894 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2028 | Summer | 50 |  |  | 73.965 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2029 | Summer | 10 |  |  | 80.0199 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2029 | Summer | 50 |  |  | 74.4648 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2030 | Summer | 10 |  |  | 81.1895 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2030 | Summer | 50 |  |  | 75.0153 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2031 | Summer | 10 |  |  | 81.9552 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2031 | Summer | 50 |  |  | 76.1566 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2032 | Summer | 10 |  |  | 82.7146 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2032 | Summer | 50 |  |  | 76.9783 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2033 | Summer | 10 |  |  | 83.6062 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2033 | Summer | 50 |  |  | 77.4148 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2034 | Summer | 10 |  |  | 84.4206 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2034 | Summer | 50 |  |  | 77.8841 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2035 | Summer | 10 |  |  | 85.2206 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2035 | Summer | 50 |  |  | 78.3211 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2036 | Summer | 10 |  |  | 85.2937 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2036 | Summer | 50 |  |  | 79.127 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2037 | Summer | 10 |  |  | 86.2309 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2037 | Summer | 50 |  |  | 80.1321 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2038 | Summer | 10 |  |  | 85.4841 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2038 | Summer | 50 |  |  | 80.0404 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2039 | Summer | 10 |  |  | 79.3417 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2039 | Summer | 50 |  |  | 73.3195 | 202503 | MVA | central
zone_sub | llg | maximum |  | 2022 | Summer | 10 | 7174 | 11.5134 | 25.3928 | 202503 | MVA | central
zone_sub | llg | maximum |  | 2022 | Summer | 50 | 7174 | 11.5134 | 23.4346 | 202503 | MVA | central
zone_sub | llg | maximum |  | 2023 | Summer | 10 | 7235 | 12.7349 | 25.4543 | 202503 | MVA | central
zone_sub | llg | maximum |  | 2023 | Summer | 50 | 7235 | 12.7349 | 23.4406 | 202503 | MVA | central
zone_sub | llg | maximum |  | 2024 | Summer | 10 | 7295 | 13.7538 | 25.544 | 202503 | MVA | central
zone_sub | llg | maximum |  | 2024 | Summer | 50 | 7295 | 13.7538 | 23.5081 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2025 | Summer | 10 |  |  | 28.7312 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2025 | Summer | 50 |  |  | 26.0976 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2026 | Summer | 10 |  |  | 33.0834 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2026 | Summer | 50 |  |  | 30.4575 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2027 | Summer | 10 |  |  | 33.0249 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2027 | Summer | 50 |  |  | 30.4247 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2028 | Summer | 10 |  |  | 33.0633 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2028 | Summer | 50 |  |  | 30.3952 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2029 | Summer | 10 |  |  | 33.1822 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2029 | Summer | 50 |  |  | 30.8677 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2030 | Summer | 10 |  |  | 33.5865 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2030 | Summer | 50 |  |  | 31.5616 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2031 | Summer | 10 |  |  | 33.8573 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2031 | Summer | 50 |  |  | 32.037 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2032 | Summer | 10 |  |  | 34.0794 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2032 | Summer | 50 |  |  | 31.4591 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2033 | Summer | 10 |  |  | 34.1121 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2033 | Summer | 50 |  |  | 31.5166 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2034 | Summer | 10 |  |  | 34.3124 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2034 | Summer | 50 |  |  | 31.792 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2035 | Summer | 10 |  |  | 34.3834 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2035 | Summer | 50 |  |  | 32.8827 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2036 | Summer | 10 |  |  | 34.3832 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2036 | Summer | 50 |  |  | 31.8492 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2037 | Summer | 10 |  |  | 34.3374 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2037 | Summer | 50 |  |  | 31.7885 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2038 | Summer | 10 |  |  | 34.3276 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2038 | Summer | 50 |  |  | 31.7234 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2039 | Summer | 10 |  |  | 32.6827 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2039 | Summer | 50 |  |  | 30.3101 | 202503 | MVA | central
zone_sub | wgi | maximum |  | 2022 | Summer | 10 | 21696 | 27.3902 | 50.299 | 202503 | MVA | east
zone_sub | wgi | maximum |  | 2022 | Summer | 50 | 21696 | 27.3902 | 41.2414 | 202503 | MVA | east
zone_sub | wgi | maximum |  | 2023 | Summer | 10 | 22045 | 30.4273 | 50.6919 | 202503 | MVA | east
zone_sub | wgi | maximum |  | 2023 | Summer | 50 | 22045 | 30.4273 | 41.4384 | 202503 | MVA | east
zone_sub | wgi | maximum |  | 2024 | Summer | 10 | 22388 | 33.5461 | 51.0465 | 202503 | MVA | east
zone_sub | wgi | maximum |  | 2024 | Summer | 50 | 22388 | 33.5461 | 41.5121 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2025 | Summer | 10 |  |  | 54.5057 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2025 | Summer | 50 |  |  | 44.6075 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2026 | Summer | 10 |  |  | 54.6012 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2026 | Summer | 50 |  |  | 44.9185 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2027 | Summer | 10 |  |  | 54.4983 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2027 | Summer | 50 |  |  | 44.7661 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2028 | Summer | 10 |  |  | 54.5247 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2028 | Summer | 50 |  |  | 44.911 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2029 | Summer | 10 |  |  | 54.7136 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2029 | Summer | 50 |  |  | 44.9706 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2030 | Summer | 10 |  |  | 55.0965 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2030 | Summer | 50 |  |  | 45.1615 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2031 | Summer | 10 |  |  | 55.7707 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2031 | Summer | 50 |  |  | 45.5541 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2032 | Summer | 50 |  |  | 45.8843 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2032 | Summer | 10 |  |  | 56.122 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2033 | Summer | 10 |  |  | 56.3761 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2033 | Summer | 50 |  |  | 46.0363 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2034 | Summer | 10 |  |  | 56.7608 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2034 | Summer | 50 |  |  | 45.9008 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2035 | Summer | 10 |  |  | 57.2519 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2035 | Summer | 50 |  |  | 46.4689 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2036 | Summer | 10 |  |  | 57.8457 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2036 | Summer | 50 |  |  | 46.559 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2037 | Summer | 10 |  |  | 58.1569 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2037 | Summer | 50 |  |  | 46.4523 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2038 | Summer | 10 |  |  | 58.056 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2038 | Summer | 50 |  |  | 46.6661 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2039 | Summer | 10 |  |  | 56.811 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2039 | Summer | 50 |  |  | 45.5652 | 202503 | MVA | east

## Forecast- Winter
Forecasting Application - 13/10/2025
asset_type | asset | extremum | scenario | demand_year | season | poe | customer_count | pv_capacity | value | forecast_round | unit | region
zone_sub | cln | maximum |  | 2022 | Winter | 10 | 38619 | 72.2578 | 63.0362 | 202503 | MVA | central
zone_sub | cln | maximum |  | 2022 | Winter | 50 | 38619 | 72.2578 | 58.8161 | 202503 | MVA | central
zone_sub | cln | maximum |  | 2023 | Winter | 10 | 41429 | 81.3604 | 67.9918 | 202503 | MVA | central
zone_sub | cln | maximum |  | 2023 | Winter | 50 | 41429 | 81.3604 | 63.4647 | 202503 | MVA | central
zone_sub | cln | maximum |  | 2024 | Winter | 10 | 44846 | 94.6588 | 74.018 | 202503 | MVA | central
zone_sub | cln | maximum |  | 2024 | Winter | 50 | 44846 | 94.6588 | 69.1182 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2025 | Winter | 10 |  |  | 89.4372 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2025 | Winter | 50 |  |  | 84.5179 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2026 | Winter | 10 |  |  | 93.2911 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2026 | Winter | 50 |  |  | 88.1502 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2027 | Winter | 10 |  |  | 98.0701 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2027 | Winter | 50 |  |  | 92.8679 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2028 | Winter | 10 |  |  | 102.5171 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2028 | Winter | 50 |  |  | 97.437 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2029 | Winter | 10 |  |  | 107.2692 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2029 | Winter | 50 |  |  | 101.4753 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2030 | Winter | 10 |  |  | 112.2902 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2030 | Winter | 50 |  |  | 107.1286 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2031 | Winter | 10 |  |  | 119.5588 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2031 | Winter | 50 |  |  | 113.3315 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2032 | Winter | 10 |  |  | 125.8642 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2032 | Winter | 50 |  |  | 119.6901 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2033 | Winter | 10 |  |  | 131.807 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2033 | Winter | 50 |  |  | 125.9989 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2034 | Winter | 10 |  |  | 137.993 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2034 | Winter | 50 |  |  | 131.579 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2035 | Winter | 10 |  |  | 145.465 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2035 | Winter | 50 |  |  | 137.6925 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2036 | Winter | 10 |  |  | 147.8036 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2036 | Winter | 50 |  |  | 139.8743 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2037 | Winter | 10 |  |  | 155.8793 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2037 | Winter | 50 |  |  | 147.8441 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2038 | Winter | 10 |  |  | 163.4009 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2038 | Winter | 50 |  |  | 156.1056 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2039 | Winter | 10 |  |  | 133.5693 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2039 | Winter | 50 |  |  | 127.2077 | 202503 | MVA | central
zone_sub | cre | maximum |  | 2022 | Winter | 10 | 24937 | 39.5122 | 50.635 | 202503 | MVA | central
zone_sub | cre | maximum |  | 2022 | Winter | 50 | 24937 | 39.5122 | 48.3881 | 202503 | MVA | central
zone_sub | cre | maximum |  | 2023 | Winter | 10 | 25835 | 43.8704 | 52.4586 | 202503 | MVA | central
zone_sub | cre | maximum |  | 2023 | Winter | 50 | 25835 | 43.8704 | 50.1308 | 202503 | MVA | central
zone_sub | cre | maximum |  | 2024 | Winter | 10 | 26314 | 48.9572 | 53.4328 | 202503 | MVA | central
zone_sub | cre | maximum |  | 2024 | Winter | 50 | 26314 | 48.9572 | 51.0617 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2025 | Winter | 10 |  |  | 68.4471 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2025 | Winter | 50 |  |  | 65.7336 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2026 | Winter | 10 |  |  | 69.4459 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2026 | Winter | 50 |  |  | 66.605 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2027 | Winter | 10 |  |  | 69.249 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2027 | Winter | 50 |  |  | 66.728 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2028 | Winter | 10 |  |  | 74.3386 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2028 | Winter | 50 |  |  | 72.0847 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2029 | Winter | 10 |  |  | 74.5773 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2029 | Winter | 50 |  |  | 72.2361 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2030 | Winter | 10 |  |  | 76.3193 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2030 | Winter | 50 |  |  | 74.0669 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2031 | Winter | 10 |  |  | 77.7248 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2031 | Winter | 50 |  |  | 75.6012 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2032 | Winter | 10 |  |  | 79.2116 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2032 | Winter | 50 |  |  | 76.7507 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2033 | Winter | 10 |  |  | 79.7367 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2033 | Winter | 50 |  |  | 77.8762 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2034 | Winter | 10 |  |  | 80.3545 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2034 | Winter | 50 |  |  | 78.6625 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2035 | Winter | 10 |  |  | 81.081 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2035 | Winter | 50 |  |  | 79.0014 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2036 | Winter | 10 |  |  | 80.0375 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2036 | Winter | 50 |  |  | 78.1499 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2037 | Winter | 10 |  |  | 83.4116 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2037 | Winter | 50 |  |  | 80.9567 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2038 | Winter | 10 |  |  | 84.3767 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2038 | Winter | 50 |  |  | 81.4995 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2039 | Winter | 10 |  |  | 72.4681 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2039 | Winter | 50 |  |  | 69.0004 | 202503 | MVA | central
zone_sub | epg | maximum |  | 2022 | Winter | 10 | 29371 | 40.0067 | 65.9271 | 202503 | MVA | central
zone_sub | epg | maximum |  | 2022 | Winter | 50 | 29371 | 40.0067 | 59.4269 | 202503 | MVA | central
zone_sub | epg | maximum |  | 2023 | Winter | 10 | 30422 | 45.1511 | 68.3101 | 202503 | MVA | central
zone_sub | epg | maximum |  | 2023 | Winter | 50 | 30422 | 45.1511 | 61.7598 | 202503 | MVA | central
zone_sub | epg | maximum |  | 2024 | Winter | 50 | 32118 | 51.557 | 65.5719 | 202503 | MVA | central
zone_sub | epg | maximum |  | 2024 | Winter | 10 | 32118 | 51.557 | 72.1952 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2025 | Winter | 10 |  |  | 85.9871 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2025 | Winter | 50 |  |  | 79.3939 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2026 | Winter | 10 |  |  | 95.0802 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2026 | Winter | 50 |  |  | 89.3565 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2027 | Winter | 10 |  |  | 100.5082 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2027 | Winter | 50 |  |  | 92.7492 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2028 | Winter | 10 |  |  | 99.8778 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2028 | Winter | 50 |  |  | 93.3308 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2029 | Winter | 10 |  |  | 103.1049 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2029 | Winter | 50 |  |  | 96.5577 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2030 | Winter | 10 |  |  | 109.1359 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2030 | Winter | 50 |  |  | 102.3455 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2031 | Winter | 10 |  |  | 112.51 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2031 | Winter | 50 |  |  | 104.2867 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2032 | Winter | 10 |  |  | 121.7799 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2032 | Winter | 50 |  |  | 114.0182 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2033 | Winter | 10 |  |  | 127.6696 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2033 | Winter | 50 |  |  | 119.7255 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2034 | Winter | 10 |  |  | 133.3287 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2034 | Winter | 50 |  |  | 125.5482 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2035 | Winter | 10 |  |  | 135.1129 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2035 | Winter | 50 |  |  | 126.6853 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2036 | Winter | 10 |  |  | 142.2751 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2036 | Winter | 50 |  |  | 134.3407 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2037 | Winter | 10 |  |  | 149.629 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2037 | Winter | 50 |  |  | 142.1357 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2038 | Winter | 10 |  |  | 150.109 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2038 | Winter | 50 |  |  | 141.9626 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2039 | Winter | 10 |  |  | 116.0207 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2039 | Winter | 50 |  |  | 101.3122 | 202503 | MVA | central
zone_sub | klo | maximum |  | 2022 | Winter | 10 | 14879 | 23.0226 | 48.7862 | 202503 | MVA | central
zone_sub | klo | maximum |  | 2022 | Winter | 50 | 14879 | 23.0226 | 43.3886 | 202503 | MVA | central
zone_sub | klo | maximum |  | 2023 | Winter | 10 | 17175 | 27.7177 | 56.3067 | 202503 | MVA | central
zone_sub | klo | maximum |  | 2023 | Winter | 50 | 17175 | 27.7177 | 50.077 | 202503 | MVA | central
zone_sub | klo | maximum |  | 2024 | Winter | 10 | 19951 | 34.2052 | 65.4015 | 202503 | MVA | central
zone_sub | klo | maximum |  | 2024 | Winter | 50 | 19951 | 34.2052 | 58.1655 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2025 | Winter | 10 |  |  | 79.8942 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2025 | Winter | 50 |  |  | 72.3119 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2026 | Winter | 10 |  |  | 92.3723 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2026 | Winter | 50 |  |  | 83.7626 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2027 | Winter | 10 |  |  | 102.9502 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2027 | Winter | 50 |  |  | 93.3778 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2028 | Winter | 10 |  |  | 120.3965 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2028 | Winter | 50 |  |  | 109.8362 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2029 | Winter | 10 |  |  | 129.7211 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2029 | Winter | 50 |  |  | 118.6301 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2030 | Winter | 10 |  |  | 142.5707 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2030 | Winter | 50 |  |  | 129.8167 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2031 | Winter | 10 |  |  | 159.4027 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2031 | Winter | 50 |  |  | 143.8497 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2032 | Winter | 10 |  |  | 178.8568 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2032 | Winter | 50 |  |  | 161.743 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2033 | Winter | 10 |  |  | 196.8658 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2033 | Winter | 50 |  |  | 178.8635 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2034 | Winter | 10 |  |  | 214.3536 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2034 | Winter | 50 |  |  | 194.8729 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2035 | Winter | 10 |  |  | 235.0946 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2035 | Winter | 50 |  |  | 213.0243 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2036 | Winter | 10 |  |  | 246.5584 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2036 | Winter | 50 |  |  | 225.0657 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2037 | Winter | 10 |  |  | 273.2503 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2037 | Winter | 50 |  |  | 249.8153 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2038 | Winter | 10 |  |  | 298.8878 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2038 | Winter | 50 |  |  | 271.7276 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2039 | Winter | 10 |  |  | 252.4111 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2039 | Winter | 50 |  |  | 227.0702 | 202503 | MVA | central
zone_sub | llg | maximum |  | 2022 | Winter | 10 | 7174 | 11.5134 | 22.426 | 202503 | MVA | central
zone_sub | llg | maximum |  | 2022 | Winter | 50 | 7174 | 11.5134 | 20.2322 | 202503 | MVA | central
zone_sub | llg | maximum |  | 2023 | Winter | 10 | 7235 | 12.7349 | 22.5982 | 202503 | MVA | central
zone_sub | llg | maximum |  | 2023 | Winter | 50 | 7235 | 12.7349 | 20.4035 | 202503 | MVA | central
zone_sub | llg | maximum |  | 2024 | Winter | 10 | 7295 | 13.7538 | 22.7705 | 202503 | MVA | central
zone_sub | llg | maximum |  | 2024 | Winter | 50 | 7295 | 13.7538 | 20.5738 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2025 | Winter | 10 |  |  | 26.1225 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2025 | Winter | 50 |  |  | 23.9159 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2026 | Winter | 10 |  |  | 30.6829 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2026 | Winter | 50 |  |  | 28.4398 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2027 | Winter | 10 |  |  | 31.049 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2027 | Winter | 50 |  |  | 28.8402 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2028 | Winter | 10 |  |  | 31.3064 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2028 | Winter | 50 |  |  | 29.108 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2029 | Winter | 10 |  |  | 31.5714 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2029 | Winter | 50 |  |  | 29.4846 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2030 | Winter | 10 |  |  | 32.5932 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2030 | Winter | 50 |  |  | 30.3426 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2031 | Winter | 10 |  |  | 33.1905 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2031 | Winter | 50 |  |  | 31.0163 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2032 | Winter | 10 |  |  | 33.8014 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2032 | Winter | 50 |  |  | 31.6154 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2033 | Winter | 10 |  |  | 34.0793 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2033 | Winter | 50 |  |  | 31.8255 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2034 | Winter | 10 |  |  | 34.2253 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2034 | Winter | 50 |  |  | 32.0656 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2035 | Winter | 10 |  |  | 33.7185 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2035 | Winter | 50 |  |  | 31.7299 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2036 | Winter | 10 |  |  | 33.9832 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2036 | Winter | 50 |  |  | 31.9069 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2037 | Winter | 10 |  |  | 34.9987 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2037 | Winter | 50 |  |  | 32.7389 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2038 | Winter | 10 |  |  | 34.5209 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2038 | Winter | 50 |  |  | 32.3709 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2039 | Winter | 10 |  |  | 28.3277 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2039 | Winter | 50 |  |  | 26.2847 | 202503 | MVA | central
zone_sub | ofr | maximum |  | 2022 | Winter | 10 | 23246 | 35.5119 | 49.8939 | 202503 | MVA | central
zone_sub | ofr | maximum |  | 2022 | Winter | 50 | 23246 | 35.5119 | 46.8764 | 202503 | MVA | central
zone_sub | ofr | maximum |  | 2023 | Winter | 10 | 24109 | 39.5748 | 51.7437 | 202503 | MVA | central
zone_sub | ofr | maximum |  | 2023 | Winter | 50 | 24109 | 39.5748 | 48.6149 | 202503 | MVA | central
zone_sub | ofr | maximum |  | 2024 | Winter | 10 | 24997 | 44.4669 | 53.6497 | 202503 | MVA | central
zone_sub | ofr | maximum |  | 2024 | Winter | 50 | 24997 | 44.4669 | 50.4065 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2025 | Winter | 10 |  |  | 59.4536 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2025 | Winter | 50 |  |  | 56.1183 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2026 | Winter | 10 |  |  | 66.5595 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2026 | Winter | 50 |  |  | 63.2802 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2027 | Winter | 10 |  |  | 72.8129 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2027 | Winter | 50 |  |  | 69.3039 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2028 | Winter | 10 |  |  | 76.0509 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2028 | Winter | 50 |  |  | 72.5305 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2029 | Winter | 10 |  |  | 78.6773 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2029 | Winter | 50 |  |  | 74.8582 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2030 | Winter | 10 |  |  | 81.1629 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2030 | Winter | 50 |  |  | 77.5373 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2031 | Winter | 10 |  |  | 83.2732 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2031 | Winter | 50 |  |  | 79.5294 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2032 | Winter | 10 |  |  | 85.4834 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2032 | Winter | 50 |  |  | 81.7407 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2033 | Winter | 10 |  |  | 86.4197 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2033 | Winter | 50 |  |  | 82.8706 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2034 | Winter | 10 |  |  | 87.7259 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2034 | Winter | 50 |  |  | 83.8526 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2035 | Winter | 10 |  |  | 90.1815 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2035 | Winter | 50 |  |  | 86.3425 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2036 | Winter | 10 |  |  | 89.3155 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2036 | Winter | 50 |  |  | 84.7668 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2037 | Winter | 10 |  |  | 92.5351 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2037 | Winter | 50 |  |  | 88.8524 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2038 | Winter | 10 |  |  | 94.3753 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2038 | Winter | 50 |  |  | 94.1939 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2039 | Winter | 10 |  |  | 80.6717 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2039 | Winter | 50 |  |  | 77.1549 | 202503 | MVA | central
zone_sub | phm | maximum |  | 2022 | Winter | 10 | 16270 | 23.521 | 48.1658 | 202503 | MVA | central
zone_sub | phm | maximum |  | 2022 | Winter | 50 | 16270 | 23.521 | 45.1092 | 202503 | MVA | central
zone_sub | phm | maximum |  | 2023 | Winter | 10 | 16562 | 25.5412 | 49.0318 | 202503 | MVA | central
zone_sub | phm | maximum |  | 2023 | Winter | 50 | 16562 | 25.5412 | 45.9202 | 202503 | MVA | central
zone_sub | phm | maximum |  | 2024 | Winter | 10 | 16854 | 27.7496 | 49.8978 | 202503 | MVA | central
zone_sub | phm | maximum |  | 2024 | Winter | 50 | 16854 | 27.7496 | 46.7311 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2025 | Winter | 10 |  |  | 67.0847 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2025 | Winter | 50 |  |  | 64.1376 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2026 | Winter | 10 |  |  | 71.7531 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2026 | Winter | 50 |  |  | 68.6294 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2027 | Winter | 10 |  |  | 72.4584 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2027 | Winter | 50 |  |  | 69.3785 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2028 | Winter | 10 |  |  | 72.887 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2028 | Winter | 50 |  |  | 69.9467 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2029 | Winter | 10 |  |  | 73.8781 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2029 | Winter | 50 |  |  | 70.9603 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2030 | Winter | 10 |  |  | 76.2493 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2030 | Winter | 50 |  |  | 73.2946 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2031 | Winter | 10 |  |  | 77.5227 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2031 | Winter | 50 |  |  | 74.8388 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2032 | Winter | 10 |  |  | 79.9897 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2032 | Winter | 50 |  |  | 76.8149 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2033 | Winter | 10 |  |  | 87.5343 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2033 | Winter | 50 |  |  | 77.8299 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2034 | Winter | 10 |  |  | 81.2629 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2034 | Winter | 50 |  |  | 78.7091 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2035 | Winter | 10 |  |  | 80.0205 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2035 | Winter | 50 |  |  | 77.0055 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2036 | Winter | 10 |  |  | 81.6454 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2036 | Winter | 50 |  |  | 78.9538 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2037 | Winter | 10 |  |  | 85.2253 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2037 | Winter | 50 |  |  | 82.0295 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2038 | Winter | 10 |  |  | 82.7648 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2038 | Winter | 50 |  |  | 79.6564 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2039 | Winter | 10 |  |  | 67.0558 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2039 | Winter | 50 |  |  | 63.9852 | 202503 | MVA | central
zone_sub | wgi | maximum |  | 2022 | Winter | 10 | 21696 | 27.3902 | 41.941 | 202503 | MVA | east
zone_sub | wgi | maximum |  | 2022 | Winter | 50 | 21696 | 27.3902 | 38.234 | 202503 | MVA | east
zone_sub | wgi | maximum |  | 2023 | Winter | 10 | 22045 | 30.4273 | 42.6315 | 202503 | MVA | east
zone_sub | wgi | maximum |  | 2023 | Winter | 50 | 22045 | 30.4273 | 38.883 | 202503 | MVA | east
zone_sub | wgi | maximum |  | 2024 | Winter | 10 | 22388 | 33.5461 | 43.3126 | 202503 | MVA | east
zone_sub | wgi | maximum |  | 2024 | Winter | 50 | 22388 | 33.5461 | 39.5207 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2025 | Winter | 10 |  |  | 47.2482 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2025 | Winter | 50 |  |  | 43.6466 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2026 | Winter | 10 |  |  | 47.6557 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2026 | Winter | 50 |  |  | 44.0841 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2027 | Winter | 10 |  |  | 49.0622 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2027 | Winter | 50 |  |  | 44.625 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2028 | Winter | 10 |  |  | 49.028 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2028 | Winter | 50 |  |  | 45.3431 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2029 | Winter | 10 |  |  | 49.3373 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2029 | Winter | 50 |  |  | 46.0239 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2030 | Winter | 10 |  |  | 50.5469 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2030 | Winter | 50 |  |  | 47.2137 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2031 | Winter | 10 |  |  | 54.0224 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2031 | Winter | 50 |  |  | 50.206 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2032 | Winter | 10 |  |  | 55.4565 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2032 | Winter | 50 |  |  | 51.8155 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2033 | Winter | 10 |  |  | 54.099 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2033 | Winter | 50 |  |  | 50.6413 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2034 | Winter | 10 |  |  | 57.8491 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2034 | Winter | 50 |  |  | 54.2764 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2035 | Winter | 10 |  |  | 56.2746 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2035 | Winter | 50 |  |  | 54.9313 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2036 | Winter | 10 |  |  | 57.6913 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2036 | Winter | 50 |  |  | 55.4021 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2037 | Winter | 10 |  |  | 58.7122 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2037 | Winter | 50 |  |  | 57.6212 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2038 | Winter | 10 |  |  | 58.2928 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2038 | Winter | 50 |  |  | 57.9824 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2039 | Winter | 10 |  |  | 49.2493 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2039 | Winter | 50 |  |  | 45.4578 | 202503 | MVA | east

## Ratings
STATION OUTPUT RATING (TRANSFORMER SUMMATION) SUMMARY
|  |  | Station N Rating |  | Station N-1 Rating |  | Station N-2 Rating
|  |  | SCR | WCR | SCR | WCR | SCR | WCR | Remarks | Remarks | Bus Target | Station Cap Bank
S/S Name | No. TX | Name Plate MVA | MVA | MVA | MVA | MVA | MVA | MVA | For N-1 Ratings | N-2 | Voltage kV | MVAr
CLN | 3 | 99 | 130.95 | 142.95 | 89.2 | 97.8 | 44.6 | 48.9
LLG | 1 | 33 | 47.4 | 48.3 | 0 | 0 | 0 | 0 | N rating only |  | 22 | 4
OFR | 2 | 66 | 93.2 | 93.2 | 45.2 | 48 | 0 | 0 | Loss of T1 or T2 |  | 22 | 6
PHM | 2 | 66 | 91.9 | 95.7 | 45 | 49.1 | 0 | 0 | Loss of T1 or T2 |  | 22 | 12

## Power Factor
asset_type | asset | PF
zone_sub | cln | 1
zone_sub | llg | 0.99
zone_sub | ofr | 1
zone_sub | phm | 1

## FT
Forecast tool (MVA) |  | Forecast Capacity & Transfers
ZSS |  | PHM
Summer
[5 empty] | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads
DY (Apr 1 to Mar 30) |  | 2022/23 | 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2028/29 | 2029/30 | 2030/31 | 2031/32 | 2032/33 | 2033/34 | 2034/35 | 2035/36 | 2036/37 | 2037/38 | 2038/39
DY (Apr 1 to Mar 30) |  | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038
FY (Jul 1 to Jun 30) |  | 2022/23 | 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2028/29 | 2029/30 | 2030/31 | 2031/32 | 2032/33 | 2033/34 | 2034/35 | 2035/36 | 2036/37 | 2037/38 | 2038/39
FY (Jul 1 to Jun 30) |  |  |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39
Summer POE50 | 50 |  |  | 52.8621 | 69.621 | 74.1527 | 73.9998 | 73.965 | 74.4648 | 75.0153 | 76.1566 | 76.9783 | 77.4148 | 77.8841 | 78.3211 | 79.127 | 80.1321 | 80.0404
Summer POE10 | 10 |  |  | 58.7282 | 75.5207 | 79.8845 | 79.6008 | 79.5894 | 80.0199 | 81.1895 | 81.9552 | 82.7146 | 83.6062 | 84.4206 | 85.2206 | 85.2937 | 86.2309 | 85.4841
Winter
[5 empty] | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads
DM (Apr 1 to Mar 30) |  |  |  | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2028/29 | 2029/30 | 2030/31 | 2031/32 | 2032/33 | 2033/34 | 2034/35 | 2035/36 | 2036/37 | 2037/38 | 2038/39
DY (Apr 1 to Mar 30) |  |  |  | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038
FY (Jul 1 to Jun 30) |  |  |  | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2028/29 | 2029/30 | 2030/31 | 2031/32 | 2032/33 | 2033/34 | 2034/35 | 2035/36 | 2036/37 | 2037/38 | 2038/39
FY (Jul 1 to Jun 30) |  |  |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39
Winter POE50 | 50 |  |  | 46.7311 | 64.1376 | 68.6294 | 69.3785 | 69.9467 | 70.9603 | 73.2946 | 74.8388 | 76.8149 | 77.8299 | 78.7091 | 77.0055 | 78.9538 | 82.0295 | 79.6564
Winter POE10 | 10 |  |  | 49.8978 | 67.0847 | 71.7531 | 72.4584 | 72.887 | 73.8781 | 76.2493 | 77.5227 | 79.9897 | 87.5343 | 81.2629 | 80.0205 | 81.6454 | 85.2253 | 82.7648
Transfers (MVA)
|  | Feeder | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39
|  | PHM | 1.7 | 1.7 | 1.67 | 1.65 | 1.62 | 1.6 | 1.58 | 1.55 | 1.53 | 1.51 | 1.48 | 1.46 | 1.44 | 1.42 | 1.4
|  | PowerFactor | 1

## Load Duration Curves
Station
PHM
POE10
[6 empty] | Stations | KLO |  | EPG |  | CRE |  | CLN |  | PHM |  | OFR |  | LLG |  | WGI
| % of MD | Winter - MD (P10) - Duration % | Winter - MD - Hours | Summer - MD - Duration % | Summer - MD - Hours | %MD | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration %
| 100% | 0% | 0 | 0% | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| 99% | 0.03383% | 1.486 | 0.03444% | 1.5127 | 99% | 0.01722% | 0.02707% | 0% | 0.04737% | 0% | 0% | 0.00861% | 0.01353% | 0.03444% | 0.03383% | 0.01722% | 0.0203% | 0.02583% | 0.006767% | 0% | 0.006767%
| 98% | 0.07443% | 3.2692 | 0.05166% | 2.269 | 98% | 0.01722% | 0.07443% | 0.00861% | 0.08797% | 0.02583% | 0.01353% | 0.02583% | 0.0203% | 0.05166% | 0.07443% | 0.02583% | 0.0812% | 0.04305% | 0.0203% | 0% | 0.006767%
| 97% | 0.1556% | 6.8356 | 0.0861% | 3.7816 | 97% | 0.02583% | 0.09474% | 0.02583% | 0.1421% | 0.04305% | 0.02707% | 0.05166% | 0.03383% | 0.0861% | 0.1556% | 0.04305% | 0.1083% | 0.05166% | 0.04737% | 0.00861% | 0.006767%
| 95% | 0.3992% | 17.5347 | 0.1378% | 6.0506 | 95% | 0.05166% | 0.1895% | 0.09471% | 0.3519% | 0.0861% | 0.08797% | 0.1033% | 0.05413% | 0.1378% | 0.3992% | 0.07749% | 0.1759% | 0.09471% | 0.09474% | 0.00861% | 0.03383%
| 90% | 1.793% | 78.7576 | 0.3702% | 16.2611 | 90% | 0.0861% | 0.9135% | 0.1894% | 1.786% | 0.1894% | 0.7579% | 0.1808% | 0.07443% | 0.3702% | 1.793% | 0.2066% | 0.8932% | 0.353% | 0.2639% | 0.01722% | 0.1962%
| 85% | 5.393% | 236.8672 | 0.6027% | 26.4715 | 85% | 0.1205% | 2.355% | 0.353% | 4.588% | 0.2669% | 2.761% | 0.3272% | 0.318% | 0.6027% | 5.393% | 0.3702% | 2.68% | 0.7147% | 0.7443% | 0.02583% | 0.9135%
| 80% | 11.33% | 497.5104 | 0.7749% | 34.0348 | 80% | 0.31% | 5.616% | 0.6458% | 8.885% | 0.4219% | 6.787% | 0.4477% | 0.9406% | 0.7749% | 11.33% | 0.5683% | 6.11% | 1.317% | 1.915% | 0.06027% | 2.118%
| 75% | 18.3% | 803.6248 | 1.102% | 48.405 | 75% | 0.4822% | 9.995% | 0.9988% | 14.05% | 0.5338% | 11.76% | 0.5855% | 2.876% | 1.102% | 18.3% | 0.7491% | 10.38% | 2.764% | 4.601% | 0.07749% | 4.486%
| 70% | 26.3% | 1155.2107 | 1.739% | 76.3892 | 70% | 0.7491% | 14.12% | 1.498% | 19.88% | 0.8438% | 17.56% | 0.7921% | 7.376% | 1.739% | 26.3% | 0.9557% | 15.73% | 6.225% | 8.837% | 0.1292% | 8.607%
| 65% | 35.36% | 1553.1596 | 2.6% | 114.2056 | 65% | 1.154% | 18.84% | 2.265% | 27.11% | 1.102% | 25.21% | 1.05% | 12.51% | 2.6% | 35.36% | 1.541% | 22.03% | 12.05% | 15.25% | 0.1464% | 14.03%
| 60% | 46.14% | 2026.2996 | 4.055% | 178.1154 | 60% | 1.602% | 25.14% | 3.203% | 35.21% | 1.627% | 33.62% | 1.748% | 18.2% | 4.055% | 46.14% | 2.247% | 29.44% | 20.92% | 25.15% | 0.2583% | 21.29%
| 55% | 59.16% | 2598.4068 | 7.095% | 311.6074 | 55% | 2.411% | 33.56% | 4.357% | 45.33% | 2.48% | 42.68% | 2.419% | 25.42% | 7.095% | 59.16% | 3.496% | 37.5% | 33.11% | 37.15% | 0.8094% | 29.85%
| 50% | 73.62% | 3233.5201 | 14.48% | 636.0723 | 50% | 4.598% | 44.25% | 6.303% | 58.26% | 3.84% | 54.87% | 4.064% | 34.04% | 14.48% | 73.62% | 5.881% | 47.91% | 47.93% | 51.32% | 2.17% | 39.4%
| 45% | 85.96% | 3775.313 | 26.86% | 1179.4944 | 45% | 9.592% | 58.98% | 10.8% | 69.36% | 6.535% | 71.48% | 8.378% | 45.63% | 26.86% | 85.96% | 11.13% | 62.3% | 62.8% | 65.85% | 4.753% | 49.36%
| 40% | 92.73% | 4072.8088 | 41.17% | 1808.3816 | 40% | 19.83% | 71.65% | 21.2% | 75.98% | 14.01% | 84.31% | 16.88% | 65.51% | 41.17% | 92.73% | 21.13% | 79.32% | 76.24% | 79.08% | 8.662% | 59.42%
| 35% | 95.6% | 4198.821 | 63.28% | 2779.1293 | 35% | 37.74% | 78.94% | 37.58% | 85.16% | 27.53% | 88.52% | 26.59% | 78.66% | 63.28% | 95.6% | 34.85% | 87.21% | 86.9% | 88.41% | 15.86% | 68.26%
| 30% | 97.25% | 4271.3374 | 86.84% | 3814.165 | 30% | 66.82% | 83.24% | 57.09% | 93.38% | 49.73% | 90.98% | 45.59% | 83.41% | 86.84% | 97.25% | 59.02% | 90.02% | 92.6% | 93.97% | 28.71% | 75.35%
| 25% | 98.4% | 4321.8611 | 94.88% | 4166.9923 | 25% | 77.33% | 87.43% | 77.75% | 96.1% | 81.07% | 93.44% | 72.26% | 87.95% | 94.88% | 98.4% | 83.32% | 92.46% | 96.47% | 96.66% | 44.75% | 80.55%
| 20% | 99.11% | 4353.067 | 97.51% | 4282.7105 | 20% | 85.59% | 92.06% | 96.84% | 97.65% | 89.22% | 95.65% | 79.18% | 93.87% | 97.51% | 99.11% | 91.2% | 94.84% | 98.65% | 98.41% | 56.7% | 84.95%
| 15% | 99.49% | 4369.4129 | 99.38% | 4364.7722 | 15% | 96.14% | 98.9% | 99.64% | 98.65% | 96.11% | 97.43% | 86.26% | 99.55% | 99.38% | 99.49% | 97.48% | 97.23% | 99.31% | 99.14% | 68.25% | 89.03%
| 10% | 99.7% | 4378.6261 | 99.99% | 4391.6218 | 10% | 99.99% | 99.99% | 99.99% | 99.16% | 99.9% | 98.78% | 98.3% | 99.6% | 99.99% | 99.7% | 99.99% | 99.59% | 99.63% | 99.41% | 79.5% | 92.79%
| 5% | 99.99% | 4391.7028 | 99.99% | 4391.6218 | 5% | 99.99% | 99.99% | 99.99% | 99.49% | 99.99% | 99.76% | 99.99% | 99.61% | 99.99% | 99.99% | 99.99% | 99.99% | 99.68% | 99.6% | 90.07% | 96.81%
| 9.992e-14% | 99.99% | 4391.7028 | 99.99% | 4391.6218 | 0% | 99.99% | 99.99% | 99.99% | 99.99% | 99.99% | 99.99% | 99.99% | 99.63% | 99.99% | 99.99% | 99.99% | 99.99% | 99.71% | 99.63% | 99.99% | 99.99%
POE 50
[6 empty] | Stations | KLO |  | EPG |  | CRE |  | CLN |  | PHM |  | OFR |  | LLG |  | WGI
| % of MD | Winter - AD (P50) - Duration % | Winter - AD - Hours | Summer - AD - Duration % | Summer - AD - Hours | %MD | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration %
| 100% | 0% | 0 | 0% | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| 99% | 0.03383% | 1.486 | 0% | 0 | 99% | 0.03444% | 0.02707% | 0.04305% | 0.04737% | 0% | 0% | 0% | 0.01353% | 0% | 0.03383% | 0% | 0.0203% | 0.00861% | 0.006767% | 0.00861% | 0.006767%
| 98% | 0.07443% | 3.2692 | 0% | 0 | 98% | 0.05166% | 0.07443% | 0.07749% | 0.08797% | 0% | 0.01353% | 0.00861% | 0.0203% | 0% | 0.07443% | 0.00861% | 0.0812% | 0.00861% | 0.0203% | 0.00861% | 0.006767%
| 97% | 0.1556% | 6.8356 | 0.00861% | 0.37816 | 97% | 0.06888% | 0.09474% | 0.07749% | 0.1421% | 0.02583% | 0.02707% | 0.01722% | 0.03383% | 0.00861% | 0.1556% | 0.01722% | 0.1083% | 0.01722% | 0.0406% | 0.00861% | 0.006767%
| 95% | 0.3992% | 17.5347 | 0.05166% | 2.269 | 95% | 0.0861% | 0.1895% | 0.1378% | 0.3519% | 0.04305% | 0.08797% | 0.02583% | 0.05413% | 0.05166% | 0.3992% | 0.04305% | 0.1759% | 0.01722% | 0.1015% | 0.01722% | 0.03383%
| 90% | 1.793% | 78.7576 | 0.1292% | 5.6725 | 90% | 0.1292% | 0.9135% | 0.2583% | 1.786% | 0.1119% | 0.7579% | 0.1033% | 0.07443% | 0.1292% | 1.793% | 0.1033% | 0.8932% | 0.0861% | 0.3451% | 0.2066% | 0.1962%
| 85% | 5.393% | 236.8672 | 0.3616% | 15.8829 | 85% | 0.2497% | 2.355% | 0.465% | 4.588% | 0.2755% | 2.761% | 0.1808% | 0.318% | 0.3616% | 5.393% | 0.2066% | 2.68% | 0.31% | 0.9% | 0.9213% | 0.9135%
| 80% | 11.33% | 497.5104 | 0.706% | 31.0095 | 80% | 0.4133% | 5.616% | 0.7835% | 8.885% | 0.6113% | 6.787% | 0.2669% | 0.9406% | 0.706% | 11.33% | 0.6286% | 6.11% | 0.8008% | 2.517% | 2.153% | 2.118%
| 75% | 18.3% | 803.6248 | 1.662% | 72.9857 | 75% | 0.8352% | 9.995% | 1.257% | 14.05% | 0.9902% | 11.76% | 0.4047% | 2.876% | 1.662% | 18.3% | 1.309% | 10.38% | 1.834% | 5.562% | 4.486% | 4.486%
| 70% | 26.3% | 1155.2107 | 3.427% | 150.5094 | 70% | 1.619% | 14.12% | 2.101% | 19.88% | 1.911% | 17.56% | 0.8008% | 7.376% | 3.427% | 26.3% | 2.419% | 15.73% | 4.374% | 10.11% | 7.672% | 8.607%
| 65% | 35.36% | 1553.1596 | 8.188% | 359.6342 | 65% | 3.057% | 18.84% | 4.288% | 27.11% | 3.504% | 25.21% | 1.352% | 12.51% | 8.188% | 35.36% | 4.598% | 22.03% | 9.179% | 17.54% | 11.87% | 14.03%
| 60% | 46.14% | 2026.2996 | 15.71% | 689.7717 | 60% | 5.528% | 25.14% | 9.342% | 35.21% | 7.758% | 33.62% | 3.573% | 18.2% | 15.71% | 46.14% | 9.17% | 29.44% | 16.83% | 27.53% | 18.5% | 21.29%
| 55% | 59.16% | 2598.4068 | 24.94% | 1095.5419 | 55% | 11.8% | 33.56% | 17.61% | 45.33% | 16.05% | 42.68% | 8.283% | 25.42% | 24.94% | 59.16% | 14.93% | 37.5% | 27.43% | 40.02% | 27.37% | 29.85%
| 50% | 73.62% | 3233.5201 | 37.94% | 1666.1918 | 50% | 21.47% | 44.25% | 28.46% | 58.26% | 24.85% | 54.87% | 17.57% | 34.04% | 37.94% | 73.62% | 22.35% | 47.91% | 40.6% | 54.15% | 38.39% | 39.4%
| 45% | 85.96% | 3775.313 | 57.06% | 2506.0947 | 45% | 35.07% | 58.98% | 42.44% | 69.36% | 37.15% | 71.48% | 28.59% | 45.63% | 57.06% | 85.96% | 36.95% | 62.3% | 53.97% | 68.39% | 48.48% | 49.36%
| 40% | 92.73% | 4072.8088 | 72.05% | 3164.4787 | 40% | 60.78% | 71.65% | 63.35% | 75.98% | 61.17% | 84.31% | 46.88% | 65.51% | 72.05% | 92.73% | 55.62% | 79.32% | 65.21% | 80.79% | 56.57% | 59.42%
| 35% | 95.6% | 4198.821 | 80.86% | 3551.3408 | 35% | 70.59% | 78.94% | 76.04% | 85.16% | 71.05% | 88.52% | 69.68% | 78.66% | 80.86% | 95.6% | 68.46% | 87.21% | 75.09% | 89.43% | 63.94% | 68.26%
| 30% | 97.25% | 4271.3374 | 85.59% | 3758.953 | 30% | 76.73% | 83.24% | 80.97% | 93.38% | 75.06% | 90.98% | 76.64% | 83.41% | 85.59% | 97.25% | 74.6% | 90.02% | 81.51% | 94.17% | 70.48% | 75.35%
| 25% | 98.4% | 4321.8611 | 89.4% | 3926.4798 | 25% | 83.08% | 87.43% | 85.41% | 96.1% | 78.56% | 93.44% | 83.93% | 87.95% | 89.4% | 98.4% | 78.93% | 92.46% | 86.44% | 96.81% | 76.48% | 80.55%
| 20% | 99.11% | 4353.067 | 92.22% | 4050.5177 | 20% | 91.12% | 92.06% | 89.28% | 97.65% | 81.79% | 95.65% | 91.73% | 93.87% | 92.22% | 99.11% | 84.56% | 94.84% | 90.52% | 98.48% | 81.71% | 84.95%
| 15% | 99.49% | 4369.4129 | 94.55% | 4152.622 | 15% | 99.18% | 98.9% | 92.61% | 98.65% | 86.18% | 97.43% | 98.93% | 99.55% | 94.55% | 99.49% | 92.06% | 97.23% | 93.75% | 99.28% | 86.58% | 89.03%
| 10% | 99.7% | 4378.6261 | 96.73% | 4248.2976 | 10% | 99.99% | 99.99% | 95.16% | 99.16% | 91.73% | 98.78% | 99.75% | 99.6% | 96.73% | 99.7% | 99.06% | 99.59% | 96.19% | 99.59% | 91.64% | 92.79%
| 5% | 99.99% | 4391.7028 | 99.31% | 4361.7469 | 5% | 99.99% | 99.99% | 97.15% | 99.49% | 97.84% | 99.76% | 99.99% | 99.61% | 99.31% | 99.99% | 99.99% | 99.99% | 98.14% | 99.77% | 96.54% | 96.81%
| 9.992e-14% | 99.99% | 4391.7028 | 99.99% | 4391.6218 | 0% | 99.99% | 99.99% | 99.99% | 99.99% | 99.99% | 99.99% | 99.99% | 99.63% | 99.99% | 99.99% | 99.99% | 99.99% | 99.78% | 99.99% | 99.99% | 99.99%
POE10
|  | Summer | Winter
| Year | 2019/2020 | 2023
| Start | 2024-10-01 | 2024-04-01
| End | 2025-04-01 | 2024-10-01
| Days | 183 | 183
| Hours | 4392 | 4392
POE50
|  | Summer | Winter
| Year | 2023/2024 | 2023
| Start | 2023-10-01 | 2024-04-01
| End | 2024-04-01 | 2024-10-01
| Days | 183 | 183
| Hours | 4392 | 4392

## Capacity N
Option 1 - Do Nothing / Base Case - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N Rating (MVA) - Option 1 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7
SCR N Rating (MVA) - Option 1 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9
Planned Additional Capacity (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2 - 1A New PHS ZSS + Four new feeders - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N Rating (MVA) - Option 2 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7
SCR N Rating (MVA) - Option 2 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 - 2A PHM 3rd Tx + Switchroom + Three new feeders + OFR12 New Feeder - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N Rating (MVA) - Option 3 | 95.7 | 95.7 | 95.7 | 140.7 | 140.7 | 140.7 | 140.7 | 140.7 | 140.7 | 140.7 | 140.7 | 140.7 | 140.7 | 140.7 | 140.7 | 140.7 | 140.7 | 140.7 | 140.7 | 140.7 | 140.7 | 140.7 | 140.7 | 140.7 | 140.7 | 140.7 | 140.7 | 140.7 | 140.7 | 140.7
SCR N Rating (MVA) - Option 3 | 91.9 | 91.9 | 91.9 | 136.9 | 136.9 | 136.9 | 136.9 | 136.9 | 136.9 | 136.9 | 136.9 | 136.9 | 136.9 | 136.9 | 136.9 | 136.9 | 136.9 | 136.9 | 136.9 | 136.9 | 136.9 | 136.9 | 136.9 | 136.9 | 136.9 | 136.9 | 136.9 | 136.9 | 136.9 | 136.9
Capacity Added (MVA) | 0 | 0 | 0 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45
Option 4 - 3A OFR 3rd Tx + Switchroom + Three new feeders + OFR12 New Feeder - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N Rating (MVA) - Option 4 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7
SCR N Rating (MVA) - Option 4 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 - 4A LLG 2nd Tx + Switchroom + Three new feeders + OFR12 New Feeder - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N Rating (MVA) - Option 5 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7
SCR N Rating (MVA) - Option 5 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 6 - Non Network - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N Rating (MVA) - Option 6 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7
SCR N Rating (MVA) - Option 6 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 7 - - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N Rating (MVA) - Option 7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7
SCR N Rating (MVA) - Option 7 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 8 - - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N Rating (MVA) - Option 8 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7
SCR N Rating (MVA) - Option 8 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Capacity N-1
Option 1 - Do Nothing / Base Case - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-1 Rating (MVA) - Option 1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1
SCR N-1 Rating (MVA) - Option 1 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45
Planned Additional Capacity (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2 - 1A New PHS ZSS + Four new feeders - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-1 Rating (MVA) - Option 2 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1
SCR N-1 Rating (MVA) - Option 2 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 - 2A PHM 3rd Tx + Switchroom + Three new feeders + OFR12 New Feeder - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-1 Rating (MVA) - Option 3 | 49.1 | 49.1 | 49.1 | 94.1 | 94.1 | 94.1 | 94.1 | 94.1 | 94.1 | 94.1 | 94.1 | 94.1 | 94.1 | 94.1 | 94.1 | 94.1 | 94.1 | 94.1 | 94.1 | 94.1 | 94.1 | 94.1 | 94.1 | 94.1 | 94.1 | 94.1 | 94.1 | 94.1 | 94.1 | 94.1
SCR N-1 Rating (MVA) - Option 3 | 45 | 45 | 45 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90
Capacity Added (MVA) | 0 | 0 | 0 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45
Option 4 - 3A OFR 3rd Tx + Switchroom + Three new feeders + OFR12 New Feeder - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-1 Rating (MVA) - Option 4 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1
SCR N-1 Rating (MVA) - Option 4 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 - 4A LLG 2nd Tx + Switchroom + Three new feeders + OFR12 New Feeder - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-1 Rating (MVA) - Option 5 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1
SCR N-1 Rating (MVA) - Option 5 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 6 - Non Network - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-1 Rating (MVA) - Option 6 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1
SCR N-1 Rating (MVA) - Option 6 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 7 - - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-1 Rating (MVA) - Option 7 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1
SCR N-1 Rating (MVA) - Option 7 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 8 - - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-1 Rating (MVA) - Option 8 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1
SCR N-1 Rating (MVA) - Option 8 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Capacity N-2
Option 1 - Do Nothing / Base Case - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-2 Rating (MVA) - Option 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCR N-2 Rating (MVA) - Option 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Planned Additional Capacity (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2 - 1A New PHS ZSS + Four new feeders - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-2 Rating (MVA) - Option 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCR N-2 Rating (MVA) - Option 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 - 2A PHM 3rd Tx + Switchroom + Three new feeders + OFR12 New Feeder - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-2 Rating (MVA) - Option 3 | 0 | 0 | 0 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45
SCR N-2 Rating (MVA) - Option 3 | 0 | 0 | 0 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45
Capacity Added (MVA) | 0 | 0 | 0 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45
Option 4 - 3A OFR 3rd Tx + Switchroom + Three new feeders + OFR12 New Feeder - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-2 Rating (MVA) - Option 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCR N-2 Rating (MVA) - Option 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 - 4A LLG 2nd Tx + Switchroom + Three new feeders + OFR12 New Feeder - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-2 Rating (MVA) - Option 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCR N-2 Rating (MVA) - Option 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 6 - Non Network - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-2 Rating (MVA) - Option 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCR N-2 Rating (MVA) - Option 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 7 - - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-2 Rating (MVA) - Option 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCR N-2 Rating (MVA) - Option 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 8 - - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-2 Rating (MVA) - Option 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCR N-2 Rating (MVA) - Option 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Demand
Option 1 - Do Nothing / Base Case
Winter Season | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Maximum Demand (MVA) - P50 | 46.7311 | 64.1376 | 68.6294 | 69.3785 | 69.9467 | 70.9603 | 73.2946 | 74.8388 | 76.8149 | 77.8299 | 78.7091 | 77.0055 | 78.9538 | 82.0295 | 79.6564 | 79.6564 | 79.6564 | 79.6564 | 79.6564 | 79.6564 | 79.6564 | 79.6564 | 79.6564 | 79.6564 | 79.6564 | 79.6564 | 79.6564 | 79.6564 | 79.6564 | 79.6564
Maximum Demand (MVA) - P10 | 49.8978 | 67.0847 | 71.7531 | 72.4584 | 72.887 | 73.8781 | 76.2493 | 77.5227 | 79.9897 | 87.5343 | 81.2629 | 80.0205 | 81.6454 | 85.2253 | 82.7648 | 82.7648 | 82.7648 | 82.7648 | 82.7648 | 82.7648 | 82.7648 | 82.7648 | 82.7648 | 82.7648 | 82.7648 | 82.7648 | 82.7648 | 82.7648 | 82.7648 | 82.7648
Block loads (MVA) not in the forecast | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Available Transfers (MVA) | 1.7 | 1.7 | 1.67 | 1.65 | 1.62 | 1.6 | 1.58 | 1.55 | 1.53 | 1.51 | 1.48 | 1.46 | 1.44 | 1.42 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4
Demand management (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Embedded generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Maximum Demand (MVA) - Option 1 Winter POE50 | 45.0311 | 62.4376 | 66.9594 | 67.7285 | 68.3267 | 69.3603 | 71.7146 | 73.2888 | 75.2849 | 76.3199 | 77.2291 | 75.5455 | 77.5138 | 80.6095 | 78.2564 | 78.2564 | 78.2564 | 78.2564 | 78.2564 | 78.2564 | 78.2564 | 78.2564 | 78.2564 | 78.2564 | 78.2564 | 78.2564 | 78.2564 | 78.2564 | 78.2564 | 78.2564
Total Maximum Demand (MVA) - Option 1 Winter POE10 | 48.1978 | 65.3847 | 70.0831 | 70.8084 | 71.267 | 72.2781 | 74.6693 | 75.9727 | 78.4597 | 86.0243 | 79.7829 | 78.5605 | 80.2054 | 83.8053 | 81.3648 | 81.3648 | 81.3648 | 81.3648 | 81.3648 | 81.3648 | 81.3648 | 81.3648 | 81.3648 | 81.3648 | 81.3648 | 81.3648 | 81.3648 | 81.3648 | 81.3648 | 81.3648
Summer Season | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Maximum Demand (MVA) - P50 | 52.8621 | 69.621 | 74.1527 | 73.9998 | 73.965 | 74.4648 | 75.0153 | 76.1566 | 76.9783 | 77.4148 | 77.8841 | 78.3211 | 79.127 | 80.1321 | 80.0404 | 80.0404 | 80.0404 | 80.0404 | 80.0404 | 80.0404 | 80.0404 | 80.0404 | 80.0404 | 80.0404 | 80.0404 | 80.0404 | 80.0404 | 80.0404 | 80.0404 | 80.0404
Maximum Demand (MVA) - P10 | 58.7282 | 75.5207 | 79.8845 | 79.6008 | 79.5894 | 80.0199 | 81.1895 | 81.9552 | 82.7146 | 83.6062 | 84.4206 | 85.2206 | 85.2937 | 86.2309 | 85.4841 | 85.4841 | 85.4841 | 85.4841 | 85.4841 | 85.4841 | 85.4841 | 85.4841 | 85.4841 | 85.4841 | 85.4841 | 85.4841 | 85.4841 | 85.4841 | 85.4841 | 85.4841
Block loads (MVA) not in the forecast | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Available Transfers (MVA) | 1.7 | 1.7 | 1.67 | 1.65 | 1.62 | 1.6 | 1.58 | 1.55 | 1.53 | 1.51 | 1.48 | 1.46 | 1.44 | 1.42 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4
Demand management (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Embedded generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Maximum Demand (MVA) - Option 1 Summer POE50 | 51.1621 | 67.921 | 72.4827 | 72.3498 | 72.345 | 72.8648 | 73.4353 | 74.6066 | 75.4483 | 75.9048 | 76.4041 | 76.8611 | 77.687 | 78.7121 | 78.6404 | 78.6404 | 78.6404 | 78.6404 | 78.6404 | 78.6404 | 78.6404 | 78.6404 | 78.6404 | 78.6404 | 78.6404 | 78.6404 | 78.6404 | 78.6404 | 78.6404 | 78.6404
Total Maximum Demand (MVA) - Option 1 Summer POE10 | 57.0282 | 73.8207 | 78.2145 | 77.9508 | 77.9694 | 78.4199 | 79.6095 | 80.4052 | 81.1846 | 82.0962 | 82.9406 | 83.7606 | 83.8537 | 84.8109 | 84.0841 | 84.0841 | 84.0841 | 84.0841 | 84.0841 | 84.0841 | 84.0841 | 84.0841 | 84.0841 | 84.0841 | 84.0841 | 84.0841 | 84.0841 | 84.0841 | 84.0841 | 84.0841
Option 2 - 1A New PHS ZSS + Four new feeders
Year | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Added Transfers (MVA) | 0 | 0 | 0 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29
Added Demand management (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Added Embedded generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Maximum Demand (MVA) - Option 2 Winter POE50 | 45.0311 | 62.4376 | 66.9594 | 38.7285 | 39.3267 | 40.3603 | 42.7146 | 44.2888 | 46.2849 | 47.3199 | 48.2291 | 46.5455 | 48.5138 | 51.6095 | 49.2564 | 49.2564 | 49.2564 | 49.2564 | 49.2564 | 49.2564 | 49.2564 | 49.2564 | 49.2564 | 49.2564 | 49.2564 | 49.2564 | 49.2564 | 49.2564 | 49.2564 | 49.2564
Total Maximum Demand (MVA) - Option 2 Winter POE10 | 48.1978 | 65.3847 | 70.0831 | 41.8084 | 42.267 | 43.2781 | 45.6693 | 46.9727 | 49.4597 | 57.0243 | 50.7829 | 49.5605 | 51.2054 | 54.8053 | 52.3648 | 52.3648 | 52.3648 | 52.3648 | 52.3648 | 52.3648 | 52.3648 | 52.3648 | 52.3648 | 52.3648 | 52.3648 | 52.3648 | 52.3648 | 52.3648 | 52.3648 | 52.3648
Total Maximum Demand (MVA) - Option 2 Summer POE50 | 51.1621 | 67.921 | 72.4827 | 43.3498 | 43.345 | 43.8648 | 44.4353 | 45.6066 | 46.4483 | 46.9048 | 47.4041 | 47.8611 | 48.687 | 49.7121 | 49.6404 | 49.6404 | 49.6404 | 49.6404 | 49.6404 | 49.6404 | 49.6404 | 49.6404 | 49.6404 | 49.6404 | 49.6404 | 49.6404 | 49.6404 | 49.6404 | 49.6404 | 49.6404
Total Maximum Demand (MVA) - Option 2 Summer POE10 | 57.0282 | 73.8207 | 78.2145 | 48.9508 | 48.9694 | 49.4199 | 50.6095 | 51.4052 | 52.1846 | 53.0962 | 53.9406 | 54.7606 | 54.8537 | 55.8109 | 55.0841 | 55.0841 | 55.0841 | 55.0841 | 55.0841 | 55.0841 | 55.0841 | 55.0841 | 55.0841 | 55.0841 | 55.0841 | 55.0841 | 55.0841 | 55.0841 | 55.0841 | 55.0841
Option 3 - 2A PHM 3rd Tx + Switchroom + Three new feeders + OFR12 New Feeder
Year | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Added Transfers (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Added Demand management (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Added Embedded generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Maximum Demand (MVA) - Option 3 Winter POE50 | 45.0311 | 62.4376 | 66.9594 | 67.7285 | 68.3267 | 69.3603 | 71.7146 | 73.2888 | 75.2849 | 76.3199 | 77.2291 | 75.5455 | 77.5138 | 80.6095 | 78.2564 | 78.2564 | 78.2564 | 78.2564 | 78.2564 | 78.2564 | 78.2564 | 78.2564 | 78.2564 | 78.2564 | 78.2564 | 78.2564 | 78.2564 | 78.2564 | 78.2564 | 78.2564
Total Maximum Demand (MVA) - Option 3 Winter POE10 | 48.1978 | 65.3847 | 70.0831 | 70.8084 | 71.267 | 72.2781 | 74.6693 | 75.9727 | 78.4597 | 86.0243 | 79.7829 | 78.5605 | 80.2054 | 83.8053 | 81.3648 | 81.3648 | 81.3648 | 81.3648 | 81.3648 | 81.3648 | 81.3648 | 81.3648 | 81.3648 | 81.3648 | 81.3648 | 81.3648 | 81.3648 | 81.3648 | 81.3648 | 81.3648
Total Maximum Demand (MVA) - Option 3 Summer POE50 | 51.1621 | 67.921 | 72.4827 | 72.3498 | 72.345 | 72.8648 | 73.4353 | 74.6066 | 75.4483 | 75.9048 | 76.4041 | 76.8611 | 77.687 | 78.7121 | 78.6404 | 78.6404 | 78.6404 | 78.6404 | 78.6404 | 78.6404 | 78.6404 | 78.6404 | 78.6404 | 78.6404 | 78.6404 | 78.6404 | 78.6404 | 78.6404 | 78.6404 | 78.6404
Total Maximum Demand (MVA) - Option 3 Summer POE10 | 57.0282 | 73.8207 | 78.2145 | 77.9508 | 77.9694 | 78.4199 | 79.6095 | 80.4052 | 81.1846 | 82.0962 | 82.9406 | 83.7606 | 83.8537 | 84.8109 | 84.0841 | 84.0841 | 84.0841 | 84.0841 | 84.0841 | 84.0841 | 84.0841 | 84.0841 | 84.0841 | 84.0841 | 84.0841 | 84.0841 | 84.0841 | 84.0841 | 84.0841 | 84.0841
Option 4 - 3A OFR 3rd Tx + Switchroom + Three new feeders + OFR12 New Feeder
Year | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Added Transfers (MVA) | 0 | 0 | 0 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5
Added Demand management (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Added Embedded generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Maximum Demand (MVA) - Option 4 Winter POE50 | 45.0311 | 62.4376 | 66.9594 | 53.2285 | 53.8267 | 54.8603 | 57.2146 | 58.7888 | 60.7849 | 61.8199 | 62.7291 | 61.0455 | 63.0138 | 66.1095 | 63.7564 | 63.7564 | 63.7564 | 63.7564 | 63.7564 | 63.7564 | 63.7564 | 63.7564 | 63.7564 | 63.7564 | 63.7564 | 63.7564 | 63.7564 | 63.7564 | 63.7564 | 63.7564
Total Maximum Demand (MVA) - Option 4 Winter POE10 | 48.1978 | 65.3847 | 70.0831 | 56.3084 | 56.767 | 57.7781 | 60.1693 | 61.4727 | 63.9597 | 71.5243 | 65.2829 | 64.0605 | 65.7054 | 69.3053 | 66.8648 | 66.8648 | 66.8648 | 66.8648 | 66.8648 | 66.8648 | 66.8648 | 66.8648 | 66.8648 | 66.8648 | 66.8648 | 66.8648 | 66.8648 | 66.8648 | 66.8648 | 66.8648
Total Maximum Demand (MVA) - Option 4 Summer POE50 | 51.1621 | 67.921 | 72.4827 | 57.8498 | 57.845 | 58.3648 | 58.9353 | 60.1066 | 60.9483 | 61.4048 | 61.9041 | 62.3611 | 63.187 | 64.2121 | 64.1404 | 64.1404 | 64.1404 | 64.1404 | 64.1404 | 64.1404 | 64.1404 | 64.1404 | 64.1404 | 64.1404 | 64.1404 | 64.1404 | 64.1404 | 64.1404 | 64.1404 | 64.1404
Total Maximum Demand (MVA) - Option 4 Summer POE10 | 57.0282 | 73.8207 | 78.2145 | 63.4508 | 63.4694 | 63.9199 | 65.1095 | 65.9052 | 66.6846 | 67.5962 | 68.4406 | 69.2606 | 69.3537 | 70.3109 | 69.5841 | 69.5841 | 69.5841 | 69.5841 | 69.5841 | 69.5841 | 69.5841 | 69.5841 | 69.5841 | 69.5841 | 69.5841 | 69.5841 | 69.5841 | 69.5841 | 69.5841 | 69.5841
Option 5 - 4A LLG 2nd Tx + Switchroom + Three new feeders + OFR12 New Feeder
Year | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Added Transfers (MVA) | 0 | 0 | 0 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29
Added Demand management (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Added Embedded generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Maximum Demand (MVA) - Option 5 Winter POE50 | 45.0311 | 62.4376 | 66.9594 | 38.7285 | 39.3267 | 40.3603 | 42.7146 | 44.2888 | 46.2849 | 47.3199 | 48.2291 | 46.5455 | 48.5138 | 51.6095 | 49.2564 | 49.2564 | 49.2564 | 49.2564 | 49.2564 | 49.2564 | 49.2564 | 49.2564 | 49.2564 | 49.2564 | 49.2564 | 49.2564 | 49.2564 | 49.2564 | 49.2564 | 49.2564
Total Maximum Demand (MVA) - Option 5 Winter POE10 | 48.1978 | 65.3847 | 70.0831 | 41.8084 | 42.267 | 43.2781 | 45.6693 | 46.9727 | 49.4597 | 57.0243 | 50.7829 | 49.5605 | 51.2054 | 54.8053 | 52.3648 | 52.3648 | 52.3648 | 52.3648 | 52.3648 | 52.3648 | 52.3648 | 52.3648 | 52.3648 | 52.3648 | 52.3648 | 52.3648 | 52.3648 | 52.3648 | 52.3648 | 52.3648
Total Maximum Demand (MVA) - Option 5 Summer POE50 | 51.1621 | 67.921 | 72.4827 | 43.3498 | 43.345 | 43.8648 | 44.4353 | 45.6066 | 46.4483 | 46.9048 | 47.4041 | 47.8611 | 48.687 | 49.7121 | 49.6404 | 49.6404 | 49.6404 | 49.6404 | 49.6404 | 49.6404 | 49.6404 | 49.6404 | 49.6404 | 49.6404 | 49.6404 | 49.6404 | 49.6404 | 49.6404 | 49.6404 | 49.6404
Total Maximum Demand (MVA) - Option 5 Summer POE10 | 57.0282 | 73.8207 | 78.2145 | 48.9508 | 48.9694 | 49.4199 | 50.6095 | 51.4052 | 52.1846 | 53.0962 | 53.9406 | 54.7606 | 54.8537 | 55.8109 | 55.0841 | 55.0841 | 55.0841 | 55.0841 | 55.0841 | 55.0841 | 55.0841 | 55.0841 | 55.0841 | 55.0841 | 55.0841 | 55.0841 | 55.0841 | 55.0841 | 55.0841 | 55.0841
Option 6 - Non Network
Year | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Added Transfers (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Added Demand management (MVA) | 7.7456 | 9.9603 | 10.5358 | 10.4984 | 10.4969 | 10.5537 | 10.7079 | 10.8089 | 10.9091 | 11.0267 | 11.1341 | 11.2396 | 11.2492 | 11.3728 | 11.2743 | 11.2743 | 11.2743 | 11.2743 | 11.2743 | 11.2743 | 11.2743 | 11.2743 | 11.2743 | 11.2743 | 11.2743 | 11.2743 | 11.2743 | 11.2743 | 11.2743 | 11.2743
Added Embedded generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Maximum Demand (MVA) - Option 6 Winter POE50 | 37.2856 | 52.4773 | 56.4235 | 57.2301 | 57.8298 | 58.8066 | 61.0067 | 62.4798 | 64.3758 | 65.2933 | 66.0951 | 64.3059 | 66.2646 | 69.2367 | 66.9821 | 66.9821 | 66.9821 | 66.9821 | 66.9821 | 66.9821 | 66.9821 | 66.9821 | 66.9821 | 66.9821 | 66.9821 | 66.9821 | 66.9821 | 66.9821 | 66.9821 | 66.9821
Total Maximum Demand (MVA) - Option 6 Winter POE10 | 40.4522 | 55.4244 | 59.5473 | 60.31 | 60.7701 | 61.7244 | 63.9613 | 65.1637 | 67.5506 | 74.9976 | 68.6488 | 67.3209 | 68.9561 | 72.4324 | 70.0905 | 70.0905 | 70.0905 | 70.0905 | 70.0905 | 70.0905 | 70.0905 | 70.0905 | 70.0905 | 70.0905 | 70.0905 | 70.0905 | 70.0905 | 70.0905 | 70.0905 | 70.0905
Total Maximum Demand (MVA) - Option 6 Summer POE50 | 43.4165 | 57.9607 | 61.9469 | 61.8514 | 61.848 | 62.3112 | 62.7274 | 63.7977 | 64.5392 | 64.8781 | 65.27 | 65.6215 | 66.4378 | 67.3392 | 67.3661 | 67.3661 | 67.3661 | 67.3661 | 67.3661 | 67.3661 | 67.3661 | 67.3661 | 67.3661 | 67.3661 | 67.3661 | 67.3661 | 67.3661 | 67.3661 | 67.3661 | 67.3661
Total Maximum Demand (MVA) - Option 6 Summer POE10 | 49.2826 | 63.8604 | 67.6787 | 67.4524 | 67.4725 | 67.8662 | 68.9015 | 69.5963 | 70.2755 | 71.0696 | 71.8065 | 72.521 | 72.6044 | 73.438 | 72.8097 | 72.8097 | 72.8097 | 72.8097 | 72.8097 | 72.8097 | 72.8097 | 72.8097 | 72.8097 | 72.8097 | 72.8097 | 72.8097 | 72.8097 | 72.8097 | 72.8097 | 72.8097
Option 7 -
Year | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Added Transfers (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Added Demand management (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Added Embedded generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Maximum Demand (MVA) - Option 7 Winter POE50 | 45.0311 | 62.4376 | 66.9594 | 67.7285 | 68.3267 | 69.3603 | 71.7146 | 73.2888 | 75.2849 | 76.3199 | 77.2291 | 75.5455 | 77.5138 | 80.6095 | 78.2564 | 78.2564 | 78.2564 | 78.2564 | 78.2564 | 78.2564 | 78.2564 | 78.2564 | 78.2564 | 78.2564 | 78.2564 | 78.2564 | 78.2564 | 78.2564 | 78.2564 | 78.2564
Total Maximum Demand (MVA) - Option 7 Winter POE10 | 48.1978 | 65.3847 | 70.0831 | 70.8084 | 71.267 | 72.2781 | 74.6693 | 75.9727 | 78.4597 | 86.0243 | 79.7829 | 78.5605 | 80.2054 | 83.8053 | 81.3648 | 81.3648 | 81.3648 | 81.3648 | 81.3648 | 81.3648 | 81.3648 | 81.3648 | 81.3648 | 81.3648 | 81.3648 | 81.3648 | 81.3648 | 81.3648 | 81.3648 | 81.3648
Total Maximum Demand (MVA) - Option 7 Summer POE50 | 51.1621 | 67.921 | 72.4827 | 72.3498 | 72.345 | 72.8648 | 73.4353 | 74.6066 | 75.4483 | 75.9048 | 76.4041 | 76.8611 | 77.687 | 78.7121 | 78.6404 | 78.6404 | 78.6404 | 78.6404 | 78.6404 | 78.6404 | 78.6404 | 78.6404 | 78.6404 | 78.6404 | 78.6404 | 78.6404 | 78.6404 | 78.6404 | 78.6404 | 78.6404
Total Maximum Demand (MVA) - Option 7 Summer POE10 | 57.0282 | 73.8207 | 78.2145 | 77.9508 | 77.9694 | 78.4199 | 79.6095 | 80.4052 | 81.1846 | 82.0962 | 82.9406 | 83.7606 | 83.8537 | 84.8109 | 84.0841 | 84.0841 | 84.0841 | 84.0841 | 84.0841 | 84.0841 | 84.0841 | 84.0841 | 84.0841 | 84.0841 | 84.0841 | 84.0841 | 84.0841 | 84.0841 | 84.0841 | 84.0841
Option 8 -
Year | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Added Transfers (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Added Demand management (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Added Embedded generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Maximum Demand (MVA) - Option 8 Winter POE50 | 45.0311 | 62.4376 | 66.9594 | 67.7285 | 68.3267 | 69.3603 | 71.7146 | 73.2888 | 75.2849 | 76.3199 | 77.2291 | 75.5455 | 77.5138 | 80.6095 | 78.2564 | 78.2564 | 78.2564 | 78.2564 | 78.2564 | 78.2564 | 78.2564 | 78.2564 | 78.2564 | 78.2564 | 78.2564 | 78.2564 | 78.2564 | 78.2564 | 78.2564 | 78.2564
Total Maximum Demand (MVA) - Option 8 Winter POE10 | 48.1978 | 65.3847 | 70.0831 | 70.8084 | 71.267 | 72.2781 | 74.6693 | 75.9727 | 78.4597 | 86.0243 | 79.7829 | 78.5605 | 80.2054 | 83.8053 | 81.3648 | 81.3648 | 81.3648 | 81.3648 | 81.3648 | 81.3648 | 81.3648 | 81.3648 | 81.3648 | 81.3648 | 81.3648 | 81.3648 | 81.3648 | 81.3648 | 81.3648 | 81.3648
Total Maximum Demand (MVA) - Option 8 Summer POE50 | 51.1621 | 67.921 | 72.4827 | 72.3498 | 72.345 | 72.8648 | 73.4353 | 74.6066 | 75.4483 | 75.9048 | 76.4041 | 76.8611 | 77.687 | 78.7121 | 78.6404 | 78.6404 | 78.6404 | 78.6404 | 78.6404 | 78.6404 | 78.6404 | 78.6404 | 78.6404 | 78.6404 | 78.6404 | 78.6404 | 78.6404 | 78.6404 | 78.6404 | 78.6404
Total Maximum Demand (MVA) - Option 8 Summer POE10 | 57.0282 | 73.8207 | 78.2145 | 77.9508 | 77.9694 | 78.4199 | 79.6095 | 80.4052 | 81.1846 | 82.0962 | 82.9406 | 83.7606 | 83.8537 | 84.8109 | 84.0841 | 84.0841 | 84.0841 | 84.0841 | 84.0841 | 84.0841 | 84.0841 | 84.0841 | 84.0841 | 84.0841 | 84.0841 | 84.0841 | 84.0841 | 84.0841 | 84.0841 | 84.0841

## Forecasted LDC
Option 1 - Do Nothing / Base Case
Winter Season | [31 empty] | Winter Season
P50 | [31 empty] | P10
% of MD | Winter - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Winter - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 45.0311 | 62.4376 | 66.9594 | 67.7285 | 68.3267 | 69.3603 | 71.7146 | 73.2888 | 75.2849 | 76.3199 | 77.2291 | 75.5455 | 77.5138 | 80.6095 | 78.2564 | 78.2564 | 78.2564 | 78.2564 | 78.2564 | 78.2564 | 78.2564 | 78.2564 | 78.2564 | 78.2564 | 78.2564 | 78.2564 | 78.2564 | 78.2564 | 78.2564 | 78.2564 | 100% | 0 | 48.1978 | 65.3847 | 70.0831 | 70.8084 | 71.267 | 72.2781 | 74.6693 | 75.9727 | 78.4597 | 86.0243 | 79.7829 | 78.5605 | 80.2054 | 83.8053 | 81.3648 | 81.3648 | 81.3648 | 81.3648 | 81.3648 | 81.3648 | 81.3648 | 81.3648 | 81.3648 | 81.3648 | 81.3648 | 81.3648 | 81.3648 | 81.3648 | 81.3648 | 81.3648
99% | 1.486 | 44.5808 | 61.8132 | 66.2898 | 67.0512 | 67.6435 | 68.6667 | 70.9975 | 72.5559 | 74.532 | 75.5567 | 76.4569 | 74.7901 | 76.7387 | 79.8034 | 77.4739 | 77.4739 | 77.4739 | 77.4739 | 77.4739 | 77.4739 | 77.4739 | 77.4739 | 77.4739 | 77.4739 | 77.4739 | 77.4739 | 77.4739 | 77.4739 | 77.4739 | 77.4739 | 99% | 1.486 | 47.7158 | 64.7309 | 69.3823 | 70.1003 | 70.5543 | 71.5553 | 73.9226 | 75.2129 | 77.6751 | 85.1641 | 78.9851 | 77.7749 | 79.4033 | 82.9672 | 80.5512 | 80.5512 | 80.5512 | 80.5512 | 80.5512 | 80.5512 | 80.5512 | 80.5512 | 80.5512 | 80.5512 | 80.5512 | 80.5512 | 80.5512 | 80.5512 | 80.5512 | 80.5512
98% | 3.2692 | 44.1305 | 61.1889 | 65.6202 | 66.3739 | 66.9602 | 67.9731 | 70.2804 | 71.823 | 73.7792 | 74.7935 | 75.6846 | 74.0346 | 75.9636 | 78.9973 | 76.6913 | 76.6913 | 76.6913 | 76.6913 | 76.6913 | 76.6913 | 76.6913 | 76.6913 | 76.6913 | 76.6913 | 76.6913 | 76.6913 | 76.6913 | 76.6913 | 76.6913 | 76.6913 | 98% | 3.2692 | 47.2338 | 64.0771 | 68.6815 | 69.3922 | 69.8416 | 70.8325 | 73.1759 | 74.4532 | 76.8905 | 84.3038 | 78.1873 | 76.9893 | 78.6013 | 82.1292 | 79.7375 | 79.7375 | 79.7375 | 79.7375 | 79.7375 | 79.7375 | 79.7375 | 79.7375 | 79.7375 | 79.7375 | 79.7375 | 79.7375 | 79.7375 | 79.7375 | 79.7375 | 79.7375
97% | 6.8356 | 43.6802 | 60.5645 | 64.9506 | 65.6966 | 66.2769 | 67.2795 | 69.5632 | 71.0901 | 73.0263 | 74.0303 | 74.9123 | 73.2792 | 75.1884 | 78.1912 | 75.9087 | 75.9087 | 75.9087 | 75.9087 | 75.9087 | 75.9087 | 75.9087 | 75.9087 | 75.9087 | 75.9087 | 75.9087 | 75.9087 | 75.9087 | 75.9087 | 75.9087 | 75.9087 | 97% | 6.8356 | 46.7518 | 63.4232 | 67.9806 | 68.6841 | 69.129 | 70.1097 | 72.4292 | 73.6935 | 76.1059 | 83.4436 | 77.3894 | 76.2037 | 77.7992 | 81.2911 | 78.9239 | 78.9239 | 78.9239 | 78.9239 | 78.9239 | 78.9239 | 78.9239 | 78.9239 | 78.9239 | 78.9239 | 78.9239 | 78.9239 | 78.9239 | 78.9239 | 78.9239 | 78.9239
95% | 17.5347 | 42.7796 | 59.3157 | 63.6114 | 64.342 | 64.9104 | 65.8923 | 68.1289 | 69.6243 | 71.5207 | 72.5039 | 73.3677 | 71.7683 | 73.6382 | 76.579 | 74.3436 | 74.3436 | 74.3436 | 74.3436 | 74.3436 | 74.3436 | 74.3436 | 74.3436 | 74.3436 | 74.3436 | 74.3436 | 74.3436 | 74.3436 | 74.3436 | 74.3436 | 74.3436 | 95% | 17.5347 | 45.7879 | 62.1155 | 66.579 | 67.268 | 67.7036 | 68.6642 | 70.9358 | 72.174 | 74.5368 | 81.7231 | 75.7938 | 74.6325 | 76.1951 | 79.615 | 77.2966 | 77.2966 | 77.2966 | 77.2966 | 77.2966 | 77.2966 | 77.2966 | 77.2966 | 77.2966 | 77.2966 | 77.2966 | 77.2966 | 77.2966 | 77.2966 | 77.2966 | 77.2966
90% | 78.7576 | 40.528 | 56.1939 | 60.2634 | 60.9556 | 61.4941 | 62.4243 | 64.5432 | 65.9599 | 67.7564 | 68.6879 | 69.5062 | 67.991 | 69.7625 | 72.5486 | 70.4308 | 70.4308 | 70.4308 | 70.4308 | 70.4308 | 70.4308 | 70.4308 | 70.4308 | 70.4308 | 70.4308 | 70.4308 | 70.4308 | 70.4308 | 70.4308 | 70.4308 | 70.4308 | 90% | 78.7576 | 43.378 | 58.8463 | 63.0748 | 63.7275 | 64.1403 | 65.0503 | 67.2023 | 68.3754 | 70.6138 | 77.4219 | 71.8046 | 70.7045 | 72.1848 | 75.4247 | 73.2283 | 73.2283 | 73.2283 | 73.2283 | 73.2283 | 73.2283 | 73.2283 | 73.2283 | 73.2283 | 73.2283 | 73.2283 | 73.2283 | 73.2283 | 73.2283 | 73.2283 | 73.2283
85% | 236.8672 | 38.2764 | 53.072 | 56.9155 | 57.5692 | 58.0777 | 58.9563 | 60.9575 | 62.2954 | 63.9922 | 64.8719 | 65.6448 | 64.2137 | 65.8868 | 68.5181 | 66.518 | 66.518 | 66.518 | 66.518 | 66.518 | 66.518 | 66.518 | 66.518 | 66.518 | 66.518 | 66.518 | 66.518 | 66.518 | 66.518 | 66.518 | 66.518 | 85% | 236.8672 | 40.9681 | 55.577 | 59.5707 | 60.1871 | 60.5769 | 61.4364 | 63.4689 | 64.5768 | 66.6908 | 73.1207 | 67.8155 | 66.7765 | 68.1746 | 71.2345 | 69.1601 | 69.1601 | 69.1601 | 69.1601 | 69.1601 | 69.1601 | 69.1601 | 69.1601 | 69.1601 | 69.1601 | 69.1601 | 69.1601 | 69.1601 | 69.1601 | 69.1601 | 69.1601
80% | 497.5104 | 36.0249 | 49.9501 | 53.5675 | 54.1828 | 54.6614 | 55.4882 | 57.3717 | 58.631 | 60.2279 | 61.056 | 61.7833 | 60.4364 | 62.0111 | 64.4876 | 62.6051 | 62.6051 | 62.6051 | 62.6051 | 62.6051 | 62.6051 | 62.6051 | 62.6051 | 62.6051 | 62.6051 | 62.6051 | 62.6051 | 62.6051 | 62.6051 | 62.6051 | 62.6051 | 80% | 497.5104 | 38.5582 | 52.3078 | 56.0665 | 56.6467 | 57.0136 | 57.8225 | 59.7354 | 60.7781 | 62.7678 | 68.8195 | 63.8263 | 62.8484 | 64.1643 | 67.0442 | 65.0919 | 65.0919 | 65.0919 | 65.0919 | 65.0919 | 65.0919 | 65.0919 | 65.0919 | 65.0919 | 65.0919 | 65.0919 | 65.0919 | 65.0919 | 65.0919 | 65.0919 | 65.0919
75% | 803.6248 | 33.7733 | 46.8282 | 50.2195 | 50.7964 | 51.245 | 52.0202 | 53.786 | 54.9666 | 56.4637 | 57.24 | 57.9219 | 56.6592 | 58.1354 | 60.4571 | 58.6923 | 58.6923 | 58.6923 | 58.6923 | 58.6923 | 58.6923 | 58.6923 | 58.6923 | 58.6923 | 58.6923 | 58.6923 | 58.6923 | 58.6923 | 58.6923 | 58.6923 | 58.6923 | 75% | 803.6248 | 36.1483 | 49.0386 | 52.5623 | 53.1063 | 53.4502 | 54.2086 | 56.0019 | 56.9795 | 58.8448 | 64.5182 | 59.8372 | 58.9204 | 60.154 | 62.8539 | 61.0236 | 61.0236 | 61.0236 | 61.0236 | 61.0236 | 61.0236 | 61.0236 | 61.0236 | 61.0236 | 61.0236 | 61.0236 | 61.0236 | 61.0236 | 61.0236 | 61.0236 | 61.0236
70% | 1155.2107 | 31.5218 | 43.7063 | 46.8715 | 47.4099 | 47.8287 | 48.5522 | 50.2003 | 51.3021 | 52.6994 | 53.424 | 54.0604 | 52.8819 | 54.2597 | 56.4267 | 54.7795 | 54.7795 | 54.7795 | 54.7795 | 54.7795 | 54.7795 | 54.7795 | 54.7795 | 54.7795 | 54.7795 | 54.7795 | 54.7795 | 54.7795 | 54.7795 | 54.7795 | 54.7795 | 70% | 1155.2107 | 33.7384 | 45.7693 | 49.0582 | 49.5659 | 49.8869 | 50.5947 | 52.2685 | 53.1809 | 54.9218 | 60.217 | 55.8481 | 54.9924 | 56.1438 | 58.6637 | 56.9554 | 56.9554 | 56.9554 | 56.9554 | 56.9554 | 56.9554 | 56.9554 | 56.9554 | 56.9554 | 56.9554 | 56.9554 | 56.9554 | 56.9554 | 56.9554 | 56.9554 | 56.9554
65% | 1553.1596 | 29.2702 | 40.5844 | 43.5236 | 44.0235 | 44.4124 | 45.0842 | 46.6145 | 47.6377 | 48.9352 | 49.608 | 50.1989 | 49.1046 | 50.384 | 52.3962 | 50.8667 | 50.8667 | 50.8667 | 50.8667 | 50.8667 | 50.8667 | 50.8667 | 50.8667 | 50.8667 | 50.8667 | 50.8667 | 50.8667 | 50.8667 | 50.8667 | 50.8667 | 50.8667 | 65% | 1553.1596 | 31.3286 | 42.5001 | 45.554 | 46.0254 | 46.3235 | 46.9808 | 48.535 | 49.3822 | 50.9988 | 55.9158 | 51.8589 | 51.0643 | 52.1335 | 54.4734 | 52.8871 | 52.8871 | 52.8871 | 52.8871 | 52.8871 | 52.8871 | 52.8871 | 52.8871 | 52.8871 | 52.8871 | 52.8871 | 52.8871 | 52.8871 | 52.8871 | 52.8871 | 52.8871
60% | 2026.2996 | 27.0187 | 37.4626 | 40.1756 | 40.6371 | 40.996 | 41.6162 | 43.0288 | 43.9733 | 45.1709 | 45.792 | 46.3375 | 45.3273 | 46.5083 | 48.3657 | 46.9539 | 46.9539 | 46.9539 | 46.9539 | 46.9539 | 46.9539 | 46.9539 | 46.9539 | 46.9539 | 46.9539 | 46.9539 | 46.9539 | 46.9539 | 46.9539 | 46.9539 | 46.9539 | 60% | 2026.2996 | 28.9187 | 39.2308 | 42.0499 | 42.485 | 42.7602 | 43.3669 | 44.8016 | 45.5836 | 47.0758 | 51.6146 | 47.8698 | 47.1363 | 48.1232 | 50.2832 | 48.8189 | 48.8189 | 48.8189 | 48.8189 | 48.8189 | 48.8189 | 48.8189 | 48.8189 | 48.8189 | 48.8189 | 48.8189 | 48.8189 | 48.8189 | 48.8189 | 48.8189 | 48.8189
55% | 2598.4068 | 24.7671 | 34.3407 | 36.8276 | 37.2507 | 37.5797 | 38.1482 | 39.4431 | 40.3088 | 41.4067 | 41.976 | 42.476 | 41.55 | 42.6326 | 44.3352 | 43.041 | 43.041 | 43.041 | 43.041 | 43.041 | 43.041 | 43.041 | 43.041 | 43.041 | 43.041 | 43.041 | 43.041 | 43.041 | 43.041 | 43.041 | 43.041 | 55% | 2598.4068 | 26.5088 | 35.9616 | 38.5457 | 38.9446 | 39.1968 | 39.753 | 41.0681 | 41.785 | 43.1529 | 47.3134 | 43.8806 | 43.2083 | 44.113 | 46.0929 | 44.7507 | 44.7507 | 44.7507 | 44.7507 | 44.7507 | 44.7507 | 44.7507 | 44.7507 | 44.7507 | 44.7507 | 44.7507 | 44.7507 | 44.7507 | 44.7507 | 44.7507 | 44.7507
50% | 3233.5201 | 22.5156 | 31.2188 | 33.4797 | 33.8642 | 34.1634 | 34.6802 | 35.8573 | 36.6444 | 37.6424 | 38.16 | 38.6146 | 37.7728 | 38.7569 | 40.3048 | 39.1282 | 39.1282 | 39.1282 | 39.1282 | 39.1282 | 39.1282 | 39.1282 | 39.1282 | 39.1282 | 39.1282 | 39.1282 | 39.1282 | 39.1282 | 39.1282 | 39.1282 | 39.1282 | 50% | 3233.5201 | 24.0989 | 32.6924 | 35.0416 | 35.4042 | 35.6335 | 36.139 | 37.3346 | 37.9863 | 39.2299 | 43.0122 | 39.8915 | 39.2803 | 40.1027 | 41.9026 | 40.6824 | 40.6824 | 40.6824 | 40.6824 | 40.6824 | 40.6824 | 40.6824 | 40.6824 | 40.6824 | 40.6824 | 40.6824 | 40.6824 | 40.6824 | 40.6824 | 40.6824 | 40.6824
45% | 3775.313 | 20.264 | 28.0969 | 30.1317 | 30.4778 | 30.747 | 31.2121 | 32.2716 | 32.9799 | 33.8782 | 34.344 | 34.7531 | 33.9955 | 34.8812 | 36.2743 | 35.2154 | 35.2154 | 35.2154 | 35.2154 | 35.2154 | 35.2154 | 35.2154 | 35.2154 | 35.2154 | 35.2154 | 35.2154 | 35.2154 | 35.2154 | 35.2154 | 35.2154 | 35.2154 | 45% | 3775.313 | 21.689 | 29.4231 | 31.5374 | 31.8638 | 32.0701 | 32.5251 | 33.6012 | 34.1877 | 35.3069 | 38.7109 | 35.9023 | 35.3522 | 36.0924 | 37.7124 | 36.6142 | 36.6142 | 36.6142 | 36.6142 | 36.6142 | 36.6142 | 36.6142 | 36.6142 | 36.6142 | 36.6142 | 36.6142 | 36.6142 | 36.6142 | 36.6142 | 36.6142 | 36.6142
40% | 4072.8088 | 18.0124 | 24.975 | 26.7837 | 27.0914 | 27.3307 | 27.7441 | 28.6859 | 29.3155 | 30.114 | 30.528 | 30.8917 | 30.2182 | 31.0055 | 32.2438 | 31.3026 | 31.3026 | 31.3026 | 31.3026 | 31.3026 | 31.3026 | 31.3026 | 31.3026 | 31.3026 | 31.3026 | 31.3026 | 31.3026 | 31.3026 | 31.3026 | 31.3026 | 31.3026 | 40% | 4072.8088 | 19.2791 | 26.1539 | 28.0332 | 28.3234 | 28.5068 | 28.9112 | 29.8677 | 30.3891 | 31.3839 | 34.4097 | 31.9132 | 31.4242 | 32.0822 | 33.5221 | 32.5459 | 32.5459 | 32.5459 | 32.5459 | 32.5459 | 32.5459 | 32.5459 | 32.5459 | 32.5459 | 32.5459 | 32.5459 | 32.5459 | 32.5459 | 32.5459 | 32.5459 | 32.5459
35% | 4198.821 | 15.7609 | 21.8532 | 23.4358 | 23.705 | 23.9144 | 24.2761 | 25.1001 | 25.6511 | 26.3497 | 26.712 | 27.0302 | 26.4409 | 27.1298 | 28.2133 | 27.3897 | 27.3897 | 27.3897 | 27.3897 | 27.3897 | 27.3897 | 27.3897 | 27.3897 | 27.3897 | 27.3897 | 27.3897 | 27.3897 | 27.3897 | 27.3897 | 27.3897 | 27.3897 | 35% | 4198.821 | 16.8692 | 22.8847 | 24.5291 | 24.7829 | 24.9434 | 25.2973 | 26.1342 | 26.5904 | 27.4609 | 30.1085 | 27.924 | 27.4962 | 28.0719 | 29.3318 | 28.4777 | 28.4777 | 28.4777 | 28.4777 | 28.4777 | 28.4777 | 28.4777 | 28.4777 | 28.4777 | 28.4777 | 28.4777 | 28.4777 | 28.4777 | 28.4777 | 28.4777 | 28.4777
30% | 4271.3374 | 13.5093 | 18.7313 | 20.0878 | 20.3185 | 20.498 | 20.8081 | 21.5144 | 21.9866 | 22.5855 | 22.896 | 23.1687 | 22.6637 | 23.2542 | 24.1829 | 23.4769 | 23.4769 | 23.4769 | 23.4769 | 23.4769 | 23.4769 | 23.4769 | 23.4769 | 23.4769 | 23.4769 | 23.4769 | 23.4769 | 23.4769 | 23.4769 | 23.4769 | 23.4769 | 30% | 4271.3374 | 14.4593 | 19.6154 | 21.0249 | 21.2425 | 21.3801 | 21.6834 | 22.4008 | 22.7918 | 23.5379 | 25.8073 | 23.9349 | 23.5682 | 24.0616 | 25.1416 | 24.4094 | 24.4094 | 24.4094 | 24.4094 | 24.4094 | 24.4094 | 24.4094 | 24.4094 | 24.4094 | 24.4094 | 24.4094 | 24.4094 | 24.4094 | 24.4094 | 24.4094 | 24.4094
25% | 4321.8611 | 11.2578 | 15.6094 | 16.7398 | 16.9321 | 17.0817 | 17.3401 | 17.9287 | 18.3222 | 18.8212 | 19.08 | 19.3073 | 18.8864 | 19.3785 | 20.1524 | 19.5641 | 19.5641 | 19.5641 | 19.5641 | 19.5641 | 19.5641 | 19.5641 | 19.5641 | 19.5641 | 19.5641 | 19.5641 | 19.5641 | 19.5641 | 19.5641 | 19.5641 | 19.5641 | 25% | 4321.8611 | 12.0494 | 16.3462 | 17.5208 | 17.7021 | 17.8167 | 18.0695 | 18.6673 | 18.9932 | 19.6149 | 21.5061 | 19.9457 | 19.6401 | 20.0513 | 20.9513 | 20.3412 | 20.3412 | 20.3412 | 20.3412 | 20.3412 | 20.3412 | 20.3412 | 20.3412 | 20.3412 | 20.3412 | 20.3412 | 20.3412 | 20.3412 | 20.3412 | 20.3412 | 20.3412
20% | 4353.067 | 9.0062 | 12.4875 | 13.3919 | 13.5457 | 13.6653 | 13.8721 | 14.3429 | 14.6578 | 15.057 | 15.264 | 15.4458 | 15.1091 | 15.5028 | 16.1219 | 15.6513 | 15.6513 | 15.6513 | 15.6513 | 15.6513 | 15.6513 | 15.6513 | 15.6513 | 15.6513 | 15.6513 | 15.6513 | 15.6513 | 15.6513 | 15.6513 | 15.6513 | 15.6513 | 20% | 4353.067 | 9.6396 | 13.0769 | 14.0166 | 14.1617 | 14.2534 | 14.4556 | 14.9339 | 15.1945 | 15.6919 | 17.2049 | 15.9566 | 15.7121 | 16.0411 | 16.7611 | 16.273 | 16.273 | 16.273 | 16.273 | 16.273 | 16.273 | 16.273 | 16.273 | 16.273 | 16.273 | 16.273 | 16.273 | 16.273 | 16.273 | 16.273 | 16.273
15% | 4369.4129 | 6.7547 | 9.3656 | 10.0439 | 10.1593 | 10.249 | 10.404 | 10.7572 | 10.9933 | 11.2927 | 11.448 | 11.5844 | 11.3318 | 11.6271 | 12.0914 | 11.7385 | 11.7385 | 11.7385 | 11.7385 | 11.7385 | 11.7385 | 11.7385 | 11.7385 | 11.7385 | 11.7385 | 11.7385 | 11.7385 | 11.7385 | 11.7385 | 11.7385 | 11.7385 | 15% | 4369.4129 | 7.2297 | 9.8077 | 10.5125 | 10.6213 | 10.69 | 10.8417 | 11.2004 | 11.3959 | 11.769 | 12.9036 | 11.9674 | 11.7841 | 12.0308 | 12.5708 | 12.2047 | 12.2047 | 12.2047 | 12.2047 | 12.2047 | 12.2047 | 12.2047 | 12.2047 | 12.2047 | 12.2047 | 12.2047 | 12.2047 | 12.2047 | 12.2047 | 12.2047 | 12.2047
10% | 4378.6261 | 4.5031 | 6.2438 | 6.6959 | 6.7728 | 6.8327 | 6.936 | 7.1715 | 7.3289 | 7.5285 | 7.632 | 7.7229 | 7.5546 | 7.7514 | 8.061 | 7.8256 | 7.8256 | 7.8256 | 7.8256 | 7.8256 | 7.8256 | 7.8256 | 7.8256 | 7.8256 | 7.8256 | 7.8256 | 7.8256 | 7.8256 | 7.8256 | 7.8256 | 7.8256 | 10% | 4378.6261 | 4.8198 | 6.5385 | 7.0083 | 7.0808 | 7.1267 | 7.2278 | 7.4669 | 7.5973 | 7.846 | 8.6024 | 7.9783 | 7.8561 | 8.0205 | 8.3805 | 8.1365 | 8.1365 | 8.1365 | 8.1365 | 8.1365 | 8.1365 | 8.1365 | 8.1365 | 8.1365 | 8.1365 | 8.1365 | 8.1365 | 8.1365 | 8.1365 | 8.1365 | 8.1365
5% | 4391.7028 | 2.2516 | 3.1219 | 3.348 | 3.3864 | 3.4163 | 3.468 | 3.5857 | 3.6644 | 3.7642 | 3.816 | 3.8615 | 3.7773 | 3.8757 | 4.0305 | 3.9128 | 3.9128 | 3.9128 | 3.9128 | 3.9128 | 3.9128 | 3.9128 | 3.9128 | 3.9128 | 3.9128 | 3.9128 | 3.9128 | 3.9128 | 3.9128 | 3.9128 | 3.9128 | 5% | 4391.7028 | 2.4099 | 3.2692 | 3.5042 | 3.5404 | 3.5633 | 3.6139 | 3.7335 | 3.7986 | 3.923 | 4.3012 | 3.9891 | 3.928 | 4.0103 | 4.1903 | 4.0682 | 4.0682 | 4.0682 | 4.0682 | 4.0682 | 4.0682 | 4.0682 | 4.0682 | 4.0682 | 4.0682 | 4.0682 | 4.0682 | 4.0682 | 4.0682 | 4.0682 | 4.0682
9.992e-14% | 4391.7028 | 4.4995e-14 | 6.2388e-14 | 6.6906e-14 | 6.7674e-14 | 6.8272e-14 | 6.9305e-14 | 7.1657e-14 | 7.323e-14 | 7.5225e-14 | 7.6259e-14 | 7.7167e-14 | 7.5485e-14 | 7.7452e-14 | 8.0545e-14 | 7.8194e-14 | 7.8194e-14 | 7.8194e-14 | 7.8194e-14 | 7.8194e-14 | 7.8194e-14 | 7.8194e-14 | 7.8194e-14 | 7.8194e-14 | 7.8194e-14 | 7.8194e-14 | 7.8194e-14 | 7.8194e-14 | 7.8194e-14 | 7.8194e-14 | 7.8194e-14 | 9.992e-14% | 4391.7028 | 4.8159e-14 | 6.5332e-14 | 7.0027e-14 | 7.0752e-14 | 7.121e-14 | 7.222e-14 | 7.461e-14 | 7.5912e-14 | 7.8397e-14 | 8.5956e-14 | 7.9719e-14 | 7.8498e-14 | 8.0141e-14 | 8.3738e-14 | 8.13e-14 | 8.13e-14 | 8.13e-14 | 8.13e-14 | 8.13e-14 | 8.13e-14 | 8.13e-14 | 8.13e-14 | 8.13e-14 | 8.13e-14 | 8.13e-14 | 8.13e-14 | 8.13e-14 | 8.13e-14 | 8.13e-14 | 8.13e-14
Summer Season | [31 empty] | Summer Season
P50 | [31 empty] | P10
% of MD | Summer - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Summer - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 51.1621 | 67.921 | 72.4827 | 72.3498 | 72.345 | 72.8648 | 73.4353 | 74.6066 | 75.4483 | 75.9048 | 76.4041 | 76.8611 | 77.687 | 78.7121 | 78.6404 | 78.6404 | 78.6404 | 78.6404 | 78.6404 | 78.6404 | 78.6404 | 78.6404 | 78.6404 | 78.6404 | 78.6404 | 78.6404 | 78.6404 | 78.6404 | 78.6404 | 78.6404 | 100% | 0 | 57.0282 | 73.8207 | 78.2145 | 77.9508 | 77.9694 | 78.4199 | 79.6095 | 80.4052 | 81.1846 | 82.0962 | 82.9406 | 83.7606 | 83.8537 | 84.8109 | 84.0841 | 84.0841 | 84.0841 | 84.0841 | 84.0841 | 84.0841 | 84.0841 | 84.0841 | 84.0841 | 84.0841 | 84.0841 | 84.0841 | 84.0841 | 84.0841 | 84.0841 | 84.0841
99% | 0 | 50.6505 | 67.2418 | 71.7579 | 71.6263 | 71.6215 | 72.1362 | 72.701 | 73.8605 | 74.6938 | 75.1458 | 75.64 | 76.0925 | 76.9101 | 77.9249 | 77.854 | 77.854 | 77.854 | 77.854 | 77.854 | 77.854 | 77.854 | 77.854 | 77.854 | 77.854 | 77.854 | 77.854 | 77.854 | 77.854 | 77.854 | 77.854 | 99% | 1.5127 | 56.4579 | 73.0825 | 77.4324 | 77.1713 | 77.1897 | 77.6357 | 78.8134 | 79.6012 | 80.3728 | 81.2753 | 82.1112 | 82.923 | 83.0151 | 83.9628 | 83.2432 | 83.2432 | 83.2432 | 83.2432 | 83.2432 | 83.2432 | 83.2432 | 83.2432 | 83.2432 | 83.2432 | 83.2432 | 83.2432 | 83.2432 | 83.2432 | 83.2432 | 83.2432
98% | 0 | 50.1389 | 66.5626 | 71.033 | 70.9028 | 70.8981 | 71.4075 | 71.9666 | 73.1145 | 73.9393 | 74.3867 | 74.876 | 75.3239 | 76.1333 | 77.1378 | 77.0676 | 77.0676 | 77.0676 | 77.0676 | 77.0676 | 77.0676 | 77.0676 | 77.0676 | 77.0676 | 77.0676 | 77.0676 | 77.0676 | 77.0676 | 77.0676 | 77.0676 | 77.0676 | 98% | 2.269 | 55.8876 | 72.3443 | 76.6503 | 76.3918 | 76.41 | 76.8515 | 78.0173 | 78.7971 | 79.5609 | 80.4543 | 81.2818 | 82.0854 | 82.1766 | 83.1147 | 82.4024 | 82.4024 | 82.4024 | 82.4024 | 82.4024 | 82.4024 | 82.4024 | 82.4024 | 82.4024 | 82.4024 | 82.4024 | 82.4024 | 82.4024 | 82.4024 | 82.4024 | 82.4024
97% | 0.37816 | 49.6272 | 65.8834 | 70.3082 | 70.1794 | 70.1746 | 70.6789 | 71.2323 | 72.3684 | 73.1848 | 73.6277 | 74.112 | 74.5553 | 75.3564 | 76.3507 | 76.2812 | 76.2812 | 76.2812 | 76.2812 | 76.2812 | 76.2812 | 76.2812 | 76.2812 | 76.2812 | 76.2812 | 76.2812 | 76.2812 | 76.2812 | 76.2812 | 76.2812 | 76.2812 | 97% | 3.7816 | 55.3173 | 71.6061 | 75.8681 | 75.6123 | 75.6303 | 76.0673 | 77.2212 | 77.9931 | 78.7491 | 79.6334 | 80.4523 | 81.2478 | 81.338 | 82.2666 | 81.5615 | 81.5615 | 81.5615 | 81.5615 | 81.5615 | 81.5615 | 81.5615 | 81.5615 | 81.5615 | 81.5615 | 81.5615 | 81.5615 | 81.5615 | 81.5615 | 81.5615 | 81.5615
95% | 2.269 | 48.604 | 64.5249 | 68.8586 | 68.7324 | 68.7277 | 69.2216 | 69.7636 | 70.8763 | 71.6758 | 72.1096 | 72.5839 | 73.0181 | 73.8027 | 74.7765 | 74.7084 | 74.7084 | 74.7084 | 74.7084 | 74.7084 | 74.7084 | 74.7084 | 74.7084 | 74.7084 | 74.7084 | 74.7084 | 74.7084 | 74.7084 | 74.7084 | 74.7084 | 74.7084 | 95% | 6.0506 | 54.1768 | 70.1297 | 74.3038 | 74.0533 | 74.071 | 74.4989 | 75.629 | 76.385 | 77.1254 | 77.9914 | 78.7935 | 79.5726 | 79.661 | 80.5703 | 79.8799 | 79.8799 | 79.8799 | 79.8799 | 79.8799 | 79.8799 | 79.8799 | 79.8799 | 79.8799 | 79.8799 | 79.8799 | 79.8799 | 79.8799 | 79.8799 | 79.8799 | 79.8799
90% | 5.6725 | 46.0459 | 61.1289 | 65.2344 | 65.1149 | 65.1105 | 65.5784 | 66.0918 | 67.1459 | 67.9034 | 68.3143 | 68.7637 | 69.175 | 69.9183 | 70.8409 | 70.7764 | 70.7764 | 70.7764 | 70.7764 | 70.7764 | 70.7764 | 70.7764 | 70.7764 | 70.7764 | 70.7764 | 70.7764 | 70.7764 | 70.7764 | 70.7764 | 70.7764 | 70.7764 | 90% | 16.2611 | 51.3254 | 66.4386 | 70.3931 | 70.1557 | 70.1725 | 70.5779 | 71.6485 | 72.3647 | 73.0662 | 73.8866 | 74.6465 | 75.3846 | 75.4683 | 76.3298 | 75.6757 | 75.6757 | 75.6757 | 75.6757 | 75.6757 | 75.6757 | 75.6757 | 75.6757 | 75.6757 | 75.6757 | 75.6757 | 75.6757 | 75.6757 | 75.6757 | 75.6757 | 75.6757
85% | 15.8829 | 43.4878 | 57.7328 | 61.6103 | 61.4974 | 61.4932 | 61.9351 | 62.42 | 63.4156 | 64.131 | 64.5191 | 64.9435 | 65.332 | 66.034 | 66.9053 | 66.8444 | 66.8444 | 66.8444 | 66.8444 | 66.8444 | 66.8444 | 66.8444 | 66.8444 | 66.8444 | 66.8444 | 66.8444 | 66.8444 | 66.8444 | 66.8444 | 66.8444 | 66.8444 | 85% | 26.4715 | 48.4739 | 62.7476 | 66.4824 | 66.2582 | 66.274 | 66.6569 | 67.6681 | 68.3445 | 69.0069 | 69.7818 | 70.4995 | 71.1965 | 71.2756 | 72.0892 | 71.4715 | 71.4715 | 71.4715 | 71.4715 | 71.4715 | 71.4715 | 71.4715 | 71.4715 | 71.4715 | 71.4715 | 71.4715 | 71.4715 | 71.4715 | 71.4715 | 71.4715 | 71.4715
80% | 31.0095 | 40.9297 | 54.3368 | 57.9862 | 57.8799 | 57.876 | 58.2919 | 58.7483 | 59.6853 | 60.3586 | 60.7239 | 61.1233 | 61.4889 | 62.1496 | 62.9697 | 62.9123 | 62.9123 | 62.9123 | 62.9123 | 62.9123 | 62.9123 | 62.9123 | 62.9123 | 62.9123 | 62.9123 | 62.9123 | 62.9123 | 62.9123 | 62.9123 | 62.9123 | 62.9123 | 80% | 34.0348 | 45.6225 | 59.0566 | 62.5716 | 62.3606 | 62.3755 | 62.7359 | 63.6876 | 64.3242 | 64.9477 | 65.677 | 66.3524 | 67.0085 | 67.0829 | 67.8487 | 67.2672 | 67.2672 | 67.2672 | 67.2672 | 67.2672 | 67.2672 | 67.2672 | 67.2672 | 67.2672 | 67.2672 | 67.2672 | 67.2672 | 67.2672 | 67.2672 | 67.2672 | 67.2672
75% | 72.9857 | 38.3716 | 50.9407 | 54.362 | 54.2624 | 54.2587 | 54.6486 | 55.0765 | 55.955 | 56.5862 | 56.9286 | 57.3031 | 57.6458 | 58.2653 | 59.0341 | 58.9803 | 58.9803 | 58.9803 | 58.9803 | 58.9803 | 58.9803 | 58.9803 | 58.9803 | 58.9803 | 58.9803 | 58.9803 | 58.9803 | 58.9803 | 58.9803 | 58.9803 | 58.9803 | 75% | 48.405 | 42.7711 | 55.3655 | 58.6609 | 58.4631 | 58.4771 | 58.8149 | 59.7071 | 60.3039 | 60.8885 | 61.5722 | 62.2054 | 62.8205 | 62.8902 | 63.6082 | 63.063 | 63.063 | 63.063 | 63.063 | 63.063 | 63.063 | 63.063 | 63.063 | 63.063 | 63.063 | 63.063 | 63.063 | 63.063 | 63.063 | 63.063 | 63.063
70% | 150.5094 | 35.8135 | 47.5447 | 50.7379 | 50.6449 | 50.6415 | 51.0054 | 51.4047 | 52.2246 | 52.8138 | 53.1334 | 53.4829 | 53.8028 | 54.3809 | 55.0984 | 55.0483 | 55.0483 | 55.0483 | 55.0483 | 55.0483 | 55.0483 | 55.0483 | 55.0483 | 55.0483 | 55.0483 | 55.0483 | 55.0483 | 55.0483 | 55.0483 | 55.0483 | 55.0483 | 70% | 76.3892 | 39.9197 | 51.6745 | 54.7502 | 54.5656 | 54.5786 | 54.8939 | 55.7266 | 56.2837 | 56.8292 | 57.4674 | 58.0584 | 58.6324 | 58.6976 | 59.3676 | 58.8588 | 58.8588 | 58.8588 | 58.8588 | 58.8588 | 58.8588 | 58.8588 | 58.8588 | 58.8588 | 58.8588 | 58.8588 | 58.8588 | 58.8588 | 58.8588 | 58.8588 | 58.8588
65% | 359.6342 | 33.2554 | 44.1486 | 47.1138 | 47.0274 | 47.0242 | 47.3621 | 47.733 | 48.4943 | 49.0414 | 49.3381 | 49.6627 | 49.9597 | 50.4966 | 51.1628 | 51.1163 | 51.1163 | 51.1163 | 51.1163 | 51.1163 | 51.1163 | 51.1163 | 51.1163 | 51.1163 | 51.1163 | 51.1163 | 51.1163 | 51.1163 | 51.1163 | 51.1163 | 51.1163 | 65% | 114.2056 | 37.0683 | 47.9835 | 50.8395 | 50.668 | 50.6801 | 50.9729 | 51.7462 | 52.2634 | 52.77 | 53.3626 | 53.9114 | 54.4444 | 54.5049 | 55.1271 | 54.6546 | 54.6546 | 54.6546 | 54.6546 | 54.6546 | 54.6546 | 54.6546 | 54.6546 | 54.6546 | 54.6546 | 54.6546 | 54.6546 | 54.6546 | 54.6546 | 54.6546 | 54.6546
60% | 689.7717 | 30.6973 | 40.7526 | 43.4896 | 43.4099 | 43.407 | 43.7189 | 44.0612 | 44.764 | 45.269 | 45.5429 | 45.8424 | 46.1167 | 46.6122 | 47.2272 | 47.1843 | 47.1843 | 47.1843 | 47.1843 | 47.1843 | 47.1843 | 47.1843 | 47.1843 | 47.1843 | 47.1843 | 47.1843 | 47.1843 | 47.1843 | 47.1843 | 47.1843 | 47.1843 | 60% | 178.1154 | 34.2169 | 44.2924 | 46.9287 | 46.7705 | 46.7817 | 47.0519 | 47.7657 | 48.2431 | 48.7108 | 49.2577 | 49.7643 | 50.2564 | 50.3122 | 50.8865 | 50.4504 | 50.4504 | 50.4504 | 50.4504 | 50.4504 | 50.4504 | 50.4504 | 50.4504 | 50.4504 | 50.4504 | 50.4504 | 50.4504 | 50.4504 | 50.4504 | 50.4504 | 50.4504
55% | 1095.5419 | 28.1392 | 37.3565 | 39.8655 | 39.7924 | 39.7897 | 40.0757 | 40.3894 | 41.0336 | 41.4965 | 41.7476 | 42.0222 | 42.2736 | 42.7279 | 43.2916 | 43.2522 | 43.2522 | 43.2522 | 43.2522 | 43.2522 | 43.2522 | 43.2522 | 43.2522 | 43.2522 | 43.2522 | 43.2522 | 43.2522 | 43.2522 | 43.2522 | 43.2522 | 43.2522 | 55% | 311.6074 | 31.3655 | 40.6014 | 43.018 | 42.8729 | 42.8832 | 43.131 | 43.7852 | 44.2229 | 44.6515 | 45.1529 | 45.6173 | 46.0683 | 46.1195 | 46.646 | 46.2462 | 46.2462 | 46.2462 | 46.2462 | 46.2462 | 46.2462 | 46.2462 | 46.2462 | 46.2462 | 46.2462 | 46.2462 | 46.2462 | 46.2462 | 46.2462 | 46.2462 | 46.2462
50% | 1666.1918 | 25.581 | 33.9605 | 36.2413 | 36.1749 | 36.1725 | 36.4324 | 36.7177 | 37.3033 | 37.7241 | 37.9524 | 38.202 | 38.4306 | 38.8435 | 39.356 | 39.3202 | 39.3202 | 39.3202 | 39.3202 | 39.3202 | 39.3202 | 39.3202 | 39.3202 | 39.3202 | 39.3202 | 39.3202 | 39.3202 | 39.3202 | 39.3202 | 39.3202 | 39.3202 | 50% | 636.0723 | 28.5141 | 36.9103 | 39.1073 | 38.9754 | 38.9847 | 39.21 | 39.8047 | 40.2026 | 40.5923 | 41.0481 | 41.4703 | 41.8803 | 41.9268 | 42.4054 | 42.042 | 42.042 | 42.042 | 42.042 | 42.042 | 42.042 | 42.042 | 42.042 | 42.042 | 42.042 | 42.042 | 42.042 | 42.042 | 42.042 | 42.042 | 42.042
45% | 2506.0947 | 23.0229 | 30.5644 | 32.6172 | 32.5574 | 32.5552 | 32.7892 | 33.0459 | 33.573 | 33.9517 | 34.1572 | 34.3818 | 34.5875 | 34.9592 | 35.4204 | 35.3882 | 35.3882 | 35.3882 | 35.3882 | 35.3882 | 35.3882 | 35.3882 | 35.3882 | 35.3882 | 35.3882 | 35.3882 | 35.3882 | 35.3882 | 35.3882 | 35.3882 | 35.3882 | 45% | 1179.4944 | 25.6627 | 33.2193 | 35.1965 | 35.0779 | 35.0862 | 35.289 | 35.8243 | 36.1824 | 36.5331 | 36.9433 | 37.3233 | 37.6923 | 37.7341 | 38.1649 | 37.8378 | 37.8378 | 37.8378 | 37.8378 | 37.8378 | 37.8378 | 37.8378 | 37.8378 | 37.8378 | 37.8378 | 37.8378 | 37.8378 | 37.8378 | 37.8378 | 37.8378 | 37.8378
40% | 3164.4787 | 20.4648 | 27.1684 | 28.9931 | 28.9399 | 28.938 | 29.1459 | 29.3741 | 29.8426 | 30.1793 | 30.3619 | 30.5616 | 30.7444 | 31.0748 | 31.4848 | 31.4562 | 31.4562 | 31.4562 | 31.4562 | 31.4562 | 31.4562 | 31.4562 | 31.4562 | 31.4562 | 31.4562 | 31.4562 | 31.4562 | 31.4562 | 31.4562 | 31.4562 | 31.4562 | 40% | 1808.3816 | 22.8113 | 29.5283 | 31.2858 | 31.1803 | 31.1878 | 31.368 | 31.8438 | 32.1621 | 32.4738 | 32.8385 | 33.1762 | 33.5042 | 33.5415 | 33.9244 | 33.6336 | 33.6336 | 33.6336 | 33.6336 | 33.6336 | 33.6336 | 33.6336 | 33.6336 | 33.6336 | 33.6336 | 33.6336 | 33.6336 | 33.6336 | 33.6336 | 33.6336 | 33.6336
35% | 3551.3408 | 17.9067 | 23.7723 | 25.3689 | 25.3224 | 25.3207 | 25.5027 | 25.7024 | 26.1123 | 26.4069 | 26.5667 | 26.7414 | 26.9014 | 27.1905 | 27.5492 | 27.5241 | 27.5241 | 27.5241 | 27.5241 | 27.5241 | 27.5241 | 27.5241 | 27.5241 | 27.5241 | 27.5241 | 27.5241 | 27.5241 | 27.5241 | 27.5241 | 27.5241 | 27.5241 | 35% | 2779.1293 | 19.9599 | 25.8372 | 27.3751 | 27.2828 | 27.2893 | 27.447 | 27.8633 | 28.1418 | 28.4146 | 28.7337 | 29.0292 | 29.3162 | 29.3488 | 29.6838 | 29.4294 | 29.4294 | 29.4294 | 29.4294 | 29.4294 | 29.4294 | 29.4294 | 29.4294 | 29.4294 | 29.4294 | 29.4294 | 29.4294 | 29.4294 | 29.4294 | 29.4294 | 29.4294
30% | 3758.953 | 15.3486 | 20.3763 | 21.7448 | 21.705 | 21.7035 | 21.8595 | 22.0306 | 22.382 | 22.6345 | 22.7714 | 22.9212 | 23.0583 | 23.3061 | 23.6136 | 23.5921 | 23.5921 | 23.5921 | 23.5921 | 23.5921 | 23.5921 | 23.5921 | 23.5921 | 23.5921 | 23.5921 | 23.5921 | 23.5921 | 23.5921 | 23.5921 | 23.5921 | 23.5921 | 30% | 3814.165 | 17.1085 | 22.1462 | 23.4644 | 23.3852 | 23.3908 | 23.526 | 23.8828 | 24.1216 | 24.3554 | 24.6289 | 24.8822 | 25.1282 | 25.1561 | 25.4433 | 25.2252 | 25.2252 | 25.2252 | 25.2252 | 25.2252 | 25.2252 | 25.2252 | 25.2252 | 25.2252 | 25.2252 | 25.2252 | 25.2252 | 25.2252 | 25.2252 | 25.2252 | 25.2252
25% | 3926.4798 | 12.7905 | 16.9802 | 18.1207 | 18.0875 | 18.0862 | 18.2162 | 18.3588 | 18.6517 | 18.8621 | 18.9762 | 19.101 | 19.2153 | 19.4218 | 19.678 | 19.6601 | 19.6601 | 19.6601 | 19.6601 | 19.6601 | 19.6601 | 19.6601 | 19.6601 | 19.6601 | 19.6601 | 19.6601 | 19.6601 | 19.6601 | 19.6601 | 19.6601 | 19.6601 | 25% | 4166.9923 | 14.257 | 18.4552 | 19.5536 | 19.4877 | 19.4924 | 19.605 | 19.9024 | 20.1013 | 20.2962 | 20.5241 | 20.7351 | 20.9402 | 20.9634 | 21.2027 | 21.021 | 21.021 | 21.021 | 21.021 | 21.021 | 21.021 | 21.021 | 21.021 | 21.021 | 21.021 | 21.021 | 21.021 | 21.021 | 21.021 | 21.021 | 21.021
20% | 4050.5177 | 10.2324 | 13.5842 | 14.4965 | 14.47 | 14.469 | 14.573 | 14.6871 | 14.9213 | 15.0897 | 15.181 | 15.2808 | 15.3722 | 15.5374 | 15.7424 | 15.7281 | 15.7281 | 15.7281 | 15.7281 | 15.7281 | 15.7281 | 15.7281 | 15.7281 | 15.7281 | 15.7281 | 15.7281 | 15.7281 | 15.7281 | 15.7281 | 15.7281 | 15.7281 | 20% | 4282.7105 | 11.4056 | 14.7641 | 15.6429 | 15.5902 | 15.5939 | 15.684 | 15.9219 | 16.081 | 16.2369 | 16.4192 | 16.5881 | 16.7521 | 16.7707 | 16.9622 | 16.8168 | 16.8168 | 16.8168 | 16.8168 | 16.8168 | 16.8168 | 16.8168 | 16.8168 | 16.8168 | 16.8168 | 16.8168 | 16.8168 | 16.8168 | 16.8168 | 16.8168 | 16.8168
15% | 4152.622 | 7.6743 | 10.1881 | 10.8724 | 10.8525 | 10.8517 | 10.9297 | 11.0153 | 11.191 | 11.3172 | 11.3857 | 11.4606 | 11.5292 | 11.6531 | 11.8068 | 11.7961 | 11.7961 | 11.7961 | 11.7961 | 11.7961 | 11.7961 | 11.7961 | 11.7961 | 11.7961 | 11.7961 | 11.7961 | 11.7961 | 11.7961 | 11.7961 | 11.7961 | 11.7961 | 15% | 4364.7722 | 8.5542 | 11.0731 | 11.7322 | 11.6926 | 11.6954 | 11.763 | 11.9414 | 12.0608 | 12.1777 | 12.3144 | 12.4411 | 12.5641 | 12.578 | 12.7216 | 12.6126 | 12.6126 | 12.6126 | 12.6126 | 12.6126 | 12.6126 | 12.6126 | 12.6126 | 12.6126 | 12.6126 | 12.6126 | 12.6126 | 12.6126 | 12.6126 | 12.6126 | 12.6126
10% | 4248.2976 | 5.1162 | 6.7921 | 7.2483 | 7.235 | 7.2345 | 7.2865 | 7.3435 | 7.4607 | 7.5448 | 7.5905 | 7.6404 | 7.6861 | 7.7687 | 7.8712 | 7.864 | 7.864 | 7.864 | 7.864 | 7.864 | 7.864 | 7.864 | 7.864 | 7.864 | 7.864 | 7.864 | 7.864 | 7.864 | 7.864 | 7.864 | 7.864 | 10% | 4391.6218 | 5.7028 | 7.3821 | 7.8215 | 7.7951 | 7.7969 | 7.842 | 7.9609 | 8.0405 | 8.1185 | 8.2096 | 8.2941 | 8.3761 | 8.3854 | 8.4811 | 8.4084 | 8.4084 | 8.4084 | 8.4084 | 8.4084 | 8.4084 | 8.4084 | 8.4084 | 8.4084 | 8.4084 | 8.4084 | 8.4084 | 8.4084 | 8.4084 | 8.4084 | 8.4084
5% | 4361.7469 | 2.5581 | 3.396 | 3.6241 | 3.6175 | 3.6172 | 3.6432 | 3.6718 | 3.7303 | 3.7724 | 3.7952 | 3.8202 | 3.8431 | 3.8844 | 3.9356 | 3.932 | 3.932 | 3.932 | 3.932 | 3.932 | 3.932 | 3.932 | 3.932 | 3.932 | 3.932 | 3.932 | 3.932 | 3.932 | 3.932 | 3.932 | 3.932 | 5% | 4391.6218 | 2.8514 | 3.691 | 3.9107 | 3.8975 | 3.8985 | 3.921 | 3.9805 | 4.0203 | 4.0592 | 4.1048 | 4.147 | 4.188 | 4.1927 | 4.2405 | 4.2042 | 4.2042 | 4.2042 | 4.2042 | 4.2042 | 4.2042 | 4.2042 | 4.2042 | 4.2042 | 4.2042 | 4.2042 | 4.2042 | 4.2042 | 4.2042 | 4.2042 | 4.2042
9.992e-14% | 4391.6218 | 5.1121e-14 | 6.7867e-14 | 7.2425e-14 | 7.2292e-14 | 7.2287e-14 | 7.2807e-14 | 7.3377e-14 | 7.4547e-14 | 7.5388e-14 | 7.5844e-14 | 7.6343e-14 | 7.68e-14 | 7.7625e-14 | 7.8649e-14 | 7.8578e-14 | 7.8578e-14 | 7.8578e-14 | 7.8578e-14 | 7.8578e-14 | 7.8578e-14 | 7.8578e-14 | 7.8578e-14 | 7.8578e-14 | 7.8578e-14 | 7.8578e-14 | 7.8578e-14 | 7.8578e-14 | 7.8578e-14 | 7.8578e-14 | 7.8578e-14 | 9.992e-14% | 4391.6218 | 5.6983e-14 | 7.3762e-14 | 7.8152e-14 | 7.7889e-14 | 7.7907e-14 | 7.8357e-14 | 7.9546e-14 | 8.0341e-14 | 8.112e-14 | 8.2031e-14 | 8.2874e-14 | 8.3694e-14 | 8.3787e-14 | 8.4743e-14 | 8.4017e-14 | 8.4017e-14 | 8.4017e-14 | 8.4017e-14 | 8.4017e-14 | 8.4017e-14 | 8.4017e-14 | 8.4017e-14 | 8.4017e-14 | 8.4017e-14 | 8.4017e-14 | 8.4017e-14 | 8.4017e-14 | 8.4017e-14 | 8.4017e-14 | 8.4017e-14
Option 2
Winter Season | [31 empty] | Winter Season
P50 | [31 empty] | P10
% of MD | Winter - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Winter - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 45.0311 | 62.4376 | 66.9594 | 38.7285 | 39.3267 | 40.3603 | 42.7146 | 44.2888 | 46.2849 | 47.3199 | 48.2291 | 46.5455 | 48.5138 | 51.6095 | 49.2564 | 49.2564 | 49.2564 | 49.2564 | 49.2564 | 49.2564 | 49.2564 | 49.2564 | 49.2564 | 49.2564 | 49.2564 | 49.2564 | 49.2564 | 49.2564 | 49.2564 | 49.2564 | 100% | 0 | 48.1978 | 65.3847 | 70.0831 | 41.8084 | 42.267 | 43.2781 | 45.6693 | 46.9727 | 49.4597 | 57.0243 | 50.7829 | 49.5605 | 51.2054 | 54.8053 | 52.3648 | 52.3648 | 52.3648 | 52.3648 | 52.3648 | 52.3648 | 52.3648 | 52.3648 | 52.3648 | 52.3648 | 52.3648 | 52.3648 | 52.3648 | 52.3648 | 52.3648 | 52.3648
99% | 1.486 | 44.5808 | 61.8132 | 66.2898 | 38.3412 | 38.9335 | 39.9567 | 42.2875 | 43.8459 | 45.822 | 46.8467 | 47.7469 | 46.0801 | 48.0287 | 51.0934 | 48.7639 | 48.7639 | 48.7639 | 48.7639 | 48.7639 | 48.7639 | 48.7639 | 48.7639 | 48.7639 | 48.7639 | 48.7639 | 48.7639 | 48.7639 | 48.7639 | 48.7639 | 48.7639 | 99% | 1.486 | 47.7158 | 64.7309 | 69.3823 | 41.3903 | 41.8443 | 42.8453 | 45.2126 | 46.5029 | 48.9651 | 56.4541 | 50.2751 | 49.0649 | 50.6933 | 54.2572 | 51.8412 | 51.8412 | 51.8412 | 51.8412 | 51.8412 | 51.8412 | 51.8412 | 51.8412 | 51.8412 | 51.8412 | 51.8412 | 51.8412 | 51.8412 | 51.8412 | 51.8412 | 51.8412
98% | 3.2692 | 44.1305 | 61.1889 | 65.6202 | 37.9539 | 38.5402 | 39.5531 | 41.8604 | 43.403 | 45.3592 | 46.3735 | 47.2646 | 45.6146 | 47.5436 | 50.5773 | 48.2713 | 48.2713 | 48.2713 | 48.2713 | 48.2713 | 48.2713 | 48.2713 | 48.2713 | 48.2713 | 48.2713 | 48.2713 | 48.2713 | 48.2713 | 48.2713 | 48.2713 | 48.2713 | 98% | 3.2692 | 47.2338 | 64.0771 | 68.6815 | 40.9722 | 41.4216 | 42.4125 | 44.7559 | 46.0332 | 48.4705 | 55.8838 | 49.7673 | 48.5693 | 50.1813 | 53.7092 | 51.3175 | 51.3175 | 51.3175 | 51.3175 | 51.3175 | 51.3175 | 51.3175 | 51.3175 | 51.3175 | 51.3175 | 51.3175 | 51.3175 | 51.3175 | 51.3175 | 51.3175 | 51.3175
97% | 6.8356 | 43.6802 | 60.5645 | 64.9506 | 37.5666 | 38.1469 | 39.1495 | 41.4332 | 42.9601 | 44.8963 | 45.9003 | 46.7823 | 45.1492 | 47.0584 | 50.0612 | 47.7787 | 47.7787 | 47.7787 | 47.7787 | 47.7787 | 47.7787 | 47.7787 | 47.7787 | 47.7787 | 47.7787 | 47.7787 | 47.7787 | 47.7787 | 47.7787 | 47.7787 | 47.7787 | 97% | 6.8356 | 46.7518 | 63.4232 | 67.9806 | 40.5541 | 40.999 | 41.9797 | 44.2992 | 45.5635 | 47.9759 | 55.3136 | 49.2594 | 48.0737 | 49.6692 | 53.1611 | 50.7939 | 50.7939 | 50.7939 | 50.7939 | 50.7939 | 50.7939 | 50.7939 | 50.7939 | 50.7939 | 50.7939 | 50.7939 | 50.7939 | 50.7939 | 50.7939 | 50.7939 | 50.7939
95% | 17.5347 | 42.7796 | 59.3157 | 63.6114 | 36.792 | 37.3604 | 38.3423 | 40.5789 | 42.0743 | 43.9707 | 44.9539 | 45.8177 | 44.2183 | 46.0882 | 49.029 | 46.7936 | 46.7936 | 46.7936 | 46.7936 | 46.7936 | 46.7936 | 46.7936 | 46.7936 | 46.7936 | 46.7936 | 46.7936 | 46.7936 | 46.7936 | 46.7936 | 46.7936 | 46.7936 | 95% | 17.5347 | 45.7879 | 62.1155 | 66.579 | 39.718 | 40.1536 | 41.1142 | 43.3858 | 44.624 | 46.9868 | 54.1731 | 48.2438 | 47.0825 | 48.6451 | 52.065 | 49.7466 | 49.7466 | 49.7466 | 49.7466 | 49.7466 | 49.7466 | 49.7466 | 49.7466 | 49.7466 | 49.7466 | 49.7466 | 49.7466 | 49.7466 | 49.7466 | 49.7466 | 49.7466
90% | 78.7576 | 40.528 | 56.1939 | 60.2634 | 34.8556 | 35.3941 | 36.3243 | 38.4432 | 39.8599 | 41.6564 | 42.5879 | 43.4062 | 41.891 | 43.6625 | 46.4486 | 44.3308 | 44.3308 | 44.3308 | 44.3308 | 44.3308 | 44.3308 | 44.3308 | 44.3308 | 44.3308 | 44.3308 | 44.3308 | 44.3308 | 44.3308 | 44.3308 | 44.3308 | 44.3308 | 90% | 78.7576 | 43.378 | 58.8463 | 63.0748 | 37.6275 | 38.0403 | 38.9503 | 41.1023 | 42.2754 | 44.5138 | 51.3219 | 45.7046 | 44.6045 | 46.0848 | 49.3247 | 47.1283 | 47.1283 | 47.1283 | 47.1283 | 47.1283 | 47.1283 | 47.1283 | 47.1283 | 47.1283 | 47.1283 | 47.1283 | 47.1283 | 47.1283 | 47.1283 | 47.1283 | 47.1283
85% | 236.8672 | 38.2764 | 53.072 | 56.9155 | 32.9192 | 33.4277 | 34.3063 | 36.3075 | 37.6454 | 39.3422 | 40.2219 | 40.9948 | 39.5637 | 41.2368 | 43.8681 | 41.868 | 41.868 | 41.868 | 41.868 | 41.868 | 41.868 | 41.868 | 41.868 | 41.868 | 41.868 | 41.868 | 41.868 | 41.868 | 41.868 | 41.868 | 41.868 | 85% | 236.8672 | 40.9681 | 55.577 | 59.5707 | 35.5371 | 35.9269 | 36.7864 | 38.8189 | 39.9268 | 42.0408 | 48.4707 | 43.1655 | 42.1265 | 43.5246 | 46.5845 | 44.5101 | 44.5101 | 44.5101 | 44.5101 | 44.5101 | 44.5101 | 44.5101 | 44.5101 | 44.5101 | 44.5101 | 44.5101 | 44.5101 | 44.5101 | 44.5101 | 44.5101 | 44.5101
80% | 497.5104 | 36.0249 | 49.9501 | 53.5675 | 30.9828 | 31.4614 | 32.2882 | 34.1717 | 35.431 | 37.0279 | 37.856 | 38.5833 | 37.2364 | 38.8111 | 41.2876 | 39.4051 | 39.4051 | 39.4051 | 39.4051 | 39.4051 | 39.4051 | 39.4051 | 39.4051 | 39.4051 | 39.4051 | 39.4051 | 39.4051 | 39.4051 | 39.4051 | 39.4051 | 39.4051 | 80% | 497.5104 | 38.5582 | 52.3078 | 56.0665 | 33.4467 | 33.8136 | 34.6225 | 36.5354 | 37.5781 | 39.5678 | 45.6195 | 40.6263 | 39.6484 | 40.9643 | 43.8442 | 41.8919 | 41.8919 | 41.8919 | 41.8919 | 41.8919 | 41.8919 | 41.8919 | 41.8919 | 41.8919 | 41.8919 | 41.8919 | 41.8919 | 41.8919 | 41.8919 | 41.8919 | 41.8919
75% | 803.6248 | 33.7733 | 46.8282 | 50.2195 | 29.0464 | 29.495 | 30.2702 | 32.036 | 33.2166 | 34.7137 | 35.49 | 36.1719 | 34.9092 | 36.3854 | 38.7071 | 36.9423 | 36.9423 | 36.9423 | 36.9423 | 36.9423 | 36.9423 | 36.9423 | 36.9423 | 36.9423 | 36.9423 | 36.9423 | 36.9423 | 36.9423 | 36.9423 | 36.9423 | 36.9423 | 75% | 803.6248 | 36.1483 | 49.0386 | 52.5623 | 31.3563 | 31.7002 | 32.4586 | 34.2519 | 35.2295 | 37.0948 | 42.7682 | 38.0872 | 37.1704 | 38.404 | 41.1039 | 39.2736 | 39.2736 | 39.2736 | 39.2736 | 39.2736 | 39.2736 | 39.2736 | 39.2736 | 39.2736 | 39.2736 | 39.2736 | 39.2736 | 39.2736 | 39.2736 | 39.2736 | 39.2736
70% | 1155.2107 | 31.5218 | 43.7063 | 46.8715 | 27.1099 | 27.5287 | 28.2522 | 29.9003 | 31.0021 | 32.3994 | 33.124 | 33.7604 | 32.5819 | 33.9597 | 36.1267 | 34.4795 | 34.4795 | 34.4795 | 34.4795 | 34.4795 | 34.4795 | 34.4795 | 34.4795 | 34.4795 | 34.4795 | 34.4795 | 34.4795 | 34.4795 | 34.4795 | 34.4795 | 34.4795 | 70% | 1155.2107 | 33.7384 | 45.7693 | 49.0582 | 29.2659 | 29.5869 | 30.2947 | 31.9685 | 32.8809 | 34.6218 | 39.917 | 35.5481 | 34.6924 | 35.8438 | 38.3637 | 36.6554 | 36.6554 | 36.6554 | 36.6554 | 36.6554 | 36.6554 | 36.6554 | 36.6554 | 36.6554 | 36.6554 | 36.6554 | 36.6554 | 36.6554 | 36.6554 | 36.6554 | 36.6554
65% | 1553.1596 | 29.2702 | 40.5844 | 43.5236 | 25.1735 | 25.5624 | 26.2342 | 27.7645 | 28.7877 | 30.0852 | 30.758 | 31.3489 | 30.2546 | 31.534 | 33.5462 | 32.0167 | 32.0167 | 32.0167 | 32.0167 | 32.0167 | 32.0167 | 32.0167 | 32.0167 | 32.0167 | 32.0167 | 32.0167 | 32.0167 | 32.0167 | 32.0167 | 32.0167 | 32.0167 | 65% | 1553.1596 | 31.3286 | 42.5001 | 45.554 | 27.1754 | 27.4735 | 28.1308 | 29.685 | 30.5322 | 32.1488 | 37.0658 | 33.0089 | 32.2143 | 33.2835 | 35.6234 | 34.0371 | 34.0371 | 34.0371 | 34.0371 | 34.0371 | 34.0371 | 34.0371 | 34.0371 | 34.0371 | 34.0371 | 34.0371 | 34.0371 | 34.0371 | 34.0371 | 34.0371 | 34.0371
60% | 2026.2996 | 27.0187 | 37.4626 | 40.1756 | 23.2371 | 23.596 | 24.2162 | 25.6288 | 26.5733 | 27.7709 | 28.392 | 28.9375 | 27.9273 | 29.1083 | 30.9657 | 29.5539 | 29.5539 | 29.5539 | 29.5539 | 29.5539 | 29.5539 | 29.5539 | 29.5539 | 29.5539 | 29.5539 | 29.5539 | 29.5539 | 29.5539 | 29.5539 | 29.5539 | 29.5539 | 60% | 2026.2996 | 28.9187 | 39.2308 | 42.0499 | 25.085 | 25.3602 | 25.9669 | 27.4016 | 28.1836 | 29.6758 | 34.2146 | 30.4698 | 29.7363 | 30.7232 | 32.8832 | 31.4189 | 31.4189 | 31.4189 | 31.4189 | 31.4189 | 31.4189 | 31.4189 | 31.4189 | 31.4189 | 31.4189 | 31.4189 | 31.4189 | 31.4189 | 31.4189 | 31.4189 | 31.4189
55% | 2598.4068 | 24.7671 | 34.3407 | 36.8276 | 21.3007 | 21.6297 | 22.1982 | 23.4931 | 24.3588 | 25.4567 | 26.026 | 26.526 | 25.6 | 26.6826 | 28.3852 | 27.091 | 27.091 | 27.091 | 27.091 | 27.091 | 27.091 | 27.091 | 27.091 | 27.091 | 27.091 | 27.091 | 27.091 | 27.091 | 27.091 | 27.091 | 27.091 | 55% | 2598.4068 | 26.5088 | 35.9616 | 38.5457 | 22.9946 | 23.2468 | 23.803 | 25.1181 | 25.835 | 27.2029 | 31.3634 | 27.9306 | 27.2583 | 28.163 | 30.1429 | 28.8007 | 28.8007 | 28.8007 | 28.8007 | 28.8007 | 28.8007 | 28.8007 | 28.8007 | 28.8007 | 28.8007 | 28.8007 | 28.8007 | 28.8007 | 28.8007 | 28.8007 | 28.8007
50% | 3233.5201 | 22.5156 | 31.2188 | 33.4797 | 19.3642 | 19.6634 | 20.1802 | 21.3573 | 22.1444 | 23.1424 | 23.66 | 24.1146 | 23.2728 | 24.2569 | 25.8048 | 24.6282 | 24.6282 | 24.6282 | 24.6282 | 24.6282 | 24.6282 | 24.6282 | 24.6282 | 24.6282 | 24.6282 | 24.6282 | 24.6282 | 24.6282 | 24.6282 | 24.6282 | 24.6282 | 50% | 3233.5201 | 24.0989 | 32.6924 | 35.0416 | 20.9042 | 21.1335 | 21.639 | 22.8346 | 23.4863 | 24.7299 | 28.5122 | 25.3915 | 24.7803 | 25.6027 | 27.4026 | 26.1824 | 26.1824 | 26.1824 | 26.1824 | 26.1824 | 26.1824 | 26.1824 | 26.1824 | 26.1824 | 26.1824 | 26.1824 | 26.1824 | 26.1824 | 26.1824 | 26.1824 | 26.1824
45% | 3775.313 | 20.264 | 28.0969 | 30.1317 | 17.4278 | 17.697 | 18.1621 | 19.2216 | 19.9299 | 20.8282 | 21.294 | 21.7031 | 20.9455 | 21.8312 | 23.2243 | 22.1654 | 22.1654 | 22.1654 | 22.1654 | 22.1654 | 22.1654 | 22.1654 | 22.1654 | 22.1654 | 22.1654 | 22.1654 | 22.1654 | 22.1654 | 22.1654 | 22.1654 | 22.1654 | 45% | 3775.313 | 21.689 | 29.4231 | 31.5374 | 18.8138 | 19.0201 | 19.4751 | 20.5512 | 21.1377 | 22.2569 | 25.6609 | 22.8523 | 22.3022 | 23.0424 | 24.6624 | 23.5642 | 23.5642 | 23.5642 | 23.5642 | 23.5642 | 23.5642 | 23.5642 | 23.5642 | 23.5642 | 23.5642 | 23.5642 | 23.5642 | 23.5642 | 23.5642 | 23.5642 | 23.5642
40% | 4072.8088 | 18.0124 | 24.975 | 26.7837 | 15.4914 | 15.7307 | 16.1441 | 17.0859 | 17.7155 | 18.514 | 18.928 | 19.2917 | 18.6182 | 19.4055 | 20.6438 | 19.7026 | 19.7026 | 19.7026 | 19.7026 | 19.7026 | 19.7026 | 19.7026 | 19.7026 | 19.7026 | 19.7026 | 19.7026 | 19.7026 | 19.7026 | 19.7026 | 19.7026 | 19.7026 | 40% | 4072.8088 | 19.2791 | 26.1539 | 28.0332 | 16.7234 | 16.9068 | 17.3112 | 18.2677 | 18.7891 | 19.7839 | 22.8097 | 20.3132 | 19.8242 | 20.4822 | 21.9221 | 20.9459 | 20.9459 | 20.9459 | 20.9459 | 20.9459 | 20.9459 | 20.9459 | 20.9459 | 20.9459 | 20.9459 | 20.9459 | 20.9459 | 20.9459 | 20.9459 | 20.9459 | 20.9459
35% | 4198.821 | 15.7609 | 21.8532 | 23.4358 | 13.555 | 13.7644 | 14.1261 | 14.9501 | 15.5011 | 16.1997 | 16.562 | 16.8802 | 16.2909 | 16.9798 | 18.0633 | 17.2397 | 17.2397 | 17.2397 | 17.2397 | 17.2397 | 17.2397 | 17.2397 | 17.2397 | 17.2397 | 17.2397 | 17.2397 | 17.2397 | 17.2397 | 17.2397 | 17.2397 | 17.2397 | 35% | 4198.821 | 16.8692 | 22.8847 | 24.5291 | 14.6329 | 14.7934 | 15.1473 | 15.9842 | 16.4404 | 17.3109 | 19.9585 | 17.774 | 17.3462 | 17.9219 | 19.1818 | 18.3277 | 18.3277 | 18.3277 | 18.3277 | 18.3277 | 18.3277 | 18.3277 | 18.3277 | 18.3277 | 18.3277 | 18.3277 | 18.3277 | 18.3277 | 18.3277 | 18.3277 | 18.3277
30% | 4271.3374 | 13.5093 | 18.7313 | 20.0878 | 11.6185 | 11.798 | 12.1081 | 12.8144 | 13.2866 | 13.8855 | 14.196 | 14.4687 | 13.9637 | 14.5542 | 15.4829 | 14.7769 | 14.7769 | 14.7769 | 14.7769 | 14.7769 | 14.7769 | 14.7769 | 14.7769 | 14.7769 | 14.7769 | 14.7769 | 14.7769 | 14.7769 | 14.7769 | 14.7769 | 14.7769 | 30% | 4271.3374 | 14.4593 | 19.6154 | 21.0249 | 12.5425 | 12.6801 | 12.9834 | 13.7008 | 14.0918 | 14.8379 | 17.1073 | 15.2349 | 14.8682 | 15.3616 | 16.4416 | 15.7094 | 15.7094 | 15.7094 | 15.7094 | 15.7094 | 15.7094 | 15.7094 | 15.7094 | 15.7094 | 15.7094 | 15.7094 | 15.7094 | 15.7094 | 15.7094 | 15.7094 | 15.7094
25% | 4321.8611 | 11.2578 | 15.6094 | 16.7398 | 9.6821 | 9.8317 | 10.0901 | 10.6787 | 11.0722 | 11.5712 | 11.83 | 12.0573 | 11.6364 | 12.1285 | 12.9024 | 12.3141 | 12.3141 | 12.3141 | 12.3141 | 12.3141 | 12.3141 | 12.3141 | 12.3141 | 12.3141 | 12.3141 | 12.3141 | 12.3141 | 12.3141 | 12.3141 | 12.3141 | 12.3141 | 25% | 4321.8611 | 12.0494 | 16.3462 | 17.5208 | 10.4521 | 10.5667 | 10.8195 | 11.4173 | 11.7432 | 12.3649 | 14.2561 | 12.6957 | 12.3901 | 12.8013 | 13.7013 | 13.0912 | 13.0912 | 13.0912 | 13.0912 | 13.0912 | 13.0912 | 13.0912 | 13.0912 | 13.0912 | 13.0912 | 13.0912 | 13.0912 | 13.0912 | 13.0912 | 13.0912 | 13.0912
20% | 4353.067 | 9.0062 | 12.4875 | 13.3919 | 7.7457 | 7.8653 | 8.0721 | 8.5429 | 8.8578 | 9.257 | 9.464 | 9.6458 | 9.3091 | 9.7028 | 10.3219 | 9.8513 | 9.8513 | 9.8513 | 9.8513 | 9.8513 | 9.8513 | 9.8513 | 9.8513 | 9.8513 | 9.8513 | 9.8513 | 9.8513 | 9.8513 | 9.8513 | 9.8513 | 9.8513 | 20% | 4353.067 | 9.6396 | 13.0769 | 14.0166 | 8.3617 | 8.4534 | 8.6556 | 9.1339 | 9.3945 | 9.8919 | 11.4049 | 10.1566 | 9.9121 | 10.2411 | 10.9611 | 10.473 | 10.473 | 10.473 | 10.473 | 10.473 | 10.473 | 10.473 | 10.473 | 10.473 | 10.473 | 10.473 | 10.473 | 10.473 | 10.473 | 10.473 | 10.473
15% | 4369.4129 | 6.7547 | 9.3656 | 10.0439 | 5.8093 | 5.899 | 6.054 | 6.4072 | 6.6433 | 6.9427 | 7.098 | 7.2344 | 6.9818 | 7.2771 | 7.7414 | 7.3885 | 7.3885 | 7.3885 | 7.3885 | 7.3885 | 7.3885 | 7.3885 | 7.3885 | 7.3885 | 7.3885 | 7.3885 | 7.3885 | 7.3885 | 7.3885 | 7.3885 | 7.3885 | 15% | 4369.4129 | 7.2297 | 9.8077 | 10.5125 | 6.2713 | 6.34 | 6.4917 | 6.8504 | 7.0459 | 7.419 | 8.5536 | 7.6174 | 7.4341 | 7.6808 | 8.2208 | 7.8547 | 7.8547 | 7.8547 | 7.8547 | 7.8547 | 7.8547 | 7.8547 | 7.8547 | 7.8547 | 7.8547 | 7.8547 | 7.8547 | 7.8547 | 7.8547 | 7.8547 | 7.8547
10% | 4378.6261 | 4.5031 | 6.2438 | 6.6959 | 3.8728 | 3.9327 | 4.036 | 4.2715 | 4.4289 | 4.6285 | 4.732 | 4.8229 | 4.6546 | 4.8514 | 5.161 | 4.9256 | 4.9256 | 4.9256 | 4.9256 | 4.9256 | 4.9256 | 4.9256 | 4.9256 | 4.9256 | 4.9256 | 4.9256 | 4.9256 | 4.9256 | 4.9256 | 4.9256 | 4.9256 | 10% | 4378.6261 | 4.8198 | 6.5385 | 7.0083 | 4.1808 | 4.2267 | 4.3278 | 4.5669 | 4.6973 | 4.946 | 5.7024 | 5.0783 | 4.9561 | 5.1205 | 5.4805 | 5.2365 | 5.2365 | 5.2365 | 5.2365 | 5.2365 | 5.2365 | 5.2365 | 5.2365 | 5.2365 | 5.2365 | 5.2365 | 5.2365 | 5.2365 | 5.2365 | 5.2365 | 5.2365
5% | 4391.7028 | 2.2516 | 3.1219 | 3.348 | 1.9364 | 1.9663 | 2.018 | 2.1357 | 2.2144 | 2.3142 | 2.366 | 2.4115 | 2.3273 | 2.4257 | 2.5805 | 2.4628 | 2.4628 | 2.4628 | 2.4628 | 2.4628 | 2.4628 | 2.4628 | 2.4628 | 2.4628 | 2.4628 | 2.4628 | 2.4628 | 2.4628 | 2.4628 | 2.4628 | 2.4628 | 5% | 4391.7028 | 2.4099 | 3.2692 | 3.5042 | 2.0904 | 2.1133 | 2.1639 | 2.2835 | 2.3486 | 2.473 | 2.8512 | 2.5391 | 2.478 | 2.5603 | 2.7403 | 2.6182 | 2.6182 | 2.6182 | 2.6182 | 2.6182 | 2.6182 | 2.6182 | 2.6182 | 2.6182 | 2.6182 | 2.6182 | 2.6182 | 2.6182 | 2.6182 | 2.6182 | 2.6182
9.992e-14% | 4391.7028 | 4.4995e-14 | 6.2388e-14 | 6.6906e-14 | 3.8698e-14 | 3.9295e-14 | 4.0328e-14 | 4.2681e-14 | 4.4253e-14 | 4.6248e-14 | 4.7282e-14 | 4.8191e-14 | 4.6508e-14 | 4.8475e-14 | 5.1568e-14 | 4.9217e-14 | 4.9217e-14 | 4.9217e-14 | 4.9217e-14 | 4.9217e-14 | 4.9217e-14 | 4.9217e-14 | 4.9217e-14 | 4.9217e-14 | 4.9217e-14 | 4.9217e-14 | 4.9217e-14 | 4.9217e-14 | 4.9217e-14 | 4.9217e-14 | 4.9217e-14 | 9.992e-14% | 4391.7028 | 4.8159e-14 | 6.5332e-14 | 7.0027e-14 | 4.1775e-14 | 4.2233e-14 | 4.3244e-14 | 4.5633e-14 | 4.6935e-14 | 4.942e-14 | 5.6979e-14 | 5.0742e-14 | 4.9521e-14 | 5.1164e-14 | 5.4761e-14 | 5.2323e-14 | 5.2323e-14 | 5.2323e-14 | 5.2323e-14 | 5.2323e-14 | 5.2323e-14 | 5.2323e-14 | 5.2323e-14 | 5.2323e-14 | 5.2323e-14 | 5.2323e-14 | 5.2323e-14 | 5.2323e-14 | 5.2323e-14 | 5.2323e-14 | 5.2323e-14
Summer Season | [31 empty] | Summer Season
P50 | [31 empty] | P10
% of MD | Summer - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Summer - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 51.1621 | 67.921 | 72.4827 | 43.3498 | 43.345 | 43.8648 | 44.4353 | 45.6066 | 46.4483 | 46.9048 | 47.4041 | 47.8611 | 48.687 | 49.7121 | 49.6404 | 49.6404 | 49.6404 | 49.6404 | 49.6404 | 49.6404 | 49.6404 | 49.6404 | 49.6404 | 49.6404 | 49.6404 | 49.6404 | 49.6404 | 49.6404 | 49.6404 | 49.6404 | 100% | 0 | 57.0282 | 73.8207 | 78.2145 | 48.9508 | 48.9694 | 49.4199 | 50.6095 | 51.4052 | 52.1846 | 53.0962 | 53.9406 | 54.7606 | 54.8537 | 55.8109 | 55.0841 | 55.0841 | 55.0841 | 55.0841 | 55.0841 | 55.0841 | 55.0841 | 55.0841 | 55.0841 | 55.0841 | 55.0841 | 55.0841 | 55.0841 | 55.0841 | 55.0841 | 55.0841
99% | 0 | 50.6505 | 67.2418 | 71.7579 | 42.9163 | 42.9115 | 43.4262 | 43.991 | 45.1505 | 45.9838 | 46.4358 | 46.93 | 47.3825 | 48.2001 | 49.2149 | 49.144 | 49.144 | 49.144 | 49.144 | 49.144 | 49.144 | 49.144 | 49.144 | 49.144 | 49.144 | 49.144 | 49.144 | 49.144 | 49.144 | 49.144 | 49.144 | 99% | 1.5127 | 56.4579 | 73.0825 | 77.4324 | 48.4613 | 48.4797 | 48.9257 | 50.1034 | 50.8912 | 51.6628 | 52.5653 | 53.4012 | 54.213 | 54.3051 | 55.2528 | 54.5332 | 54.5332 | 54.5332 | 54.5332 | 54.5332 | 54.5332 | 54.5332 | 54.5332 | 54.5332 | 54.5332 | 54.5332 | 54.5332 | 54.5332 | 54.5332 | 54.5332 | 54.5332
98% | 0 | 50.1389 | 66.5626 | 71.033 | 42.4828 | 42.4781 | 42.9875 | 43.5466 | 44.6945 | 45.5193 | 45.9667 | 46.456 | 46.9039 | 47.7133 | 48.7178 | 48.6476 | 48.6476 | 48.6476 | 48.6476 | 48.6476 | 48.6476 | 48.6476 | 48.6476 | 48.6476 | 48.6476 | 48.6476 | 48.6476 | 48.6476 | 48.6476 | 48.6476 | 48.6476 | 98% | 2.269 | 55.8876 | 72.3443 | 76.6503 | 47.9718 | 47.99 | 48.4315 | 49.5973 | 50.3771 | 51.1409 | 52.0343 | 52.8618 | 53.6654 | 53.7566 | 54.6947 | 53.9824 | 53.9824 | 53.9824 | 53.9824 | 53.9824 | 53.9824 | 53.9824 | 53.9824 | 53.9824 | 53.9824 | 53.9824 | 53.9824 | 53.9824 | 53.9824 | 53.9824 | 53.9824
97% | 0.37816 | 49.6272 | 65.8834 | 70.3082 | 42.0494 | 42.0446 | 42.5489 | 43.1023 | 44.2384 | 45.0548 | 45.4977 | 45.982 | 46.4253 | 47.2264 | 48.2207 | 48.1512 | 48.1512 | 48.1512 | 48.1512 | 48.1512 | 48.1512 | 48.1512 | 48.1512 | 48.1512 | 48.1512 | 48.1512 | 48.1512 | 48.1512 | 48.1512 | 48.1512 | 48.1512 | 97% | 3.7816 | 55.3173 | 71.6061 | 75.8681 | 47.4823 | 47.5003 | 47.9373 | 49.0912 | 49.8631 | 50.6191 | 51.5034 | 52.3223 | 53.1178 | 53.208 | 54.1366 | 53.4315 | 53.4315 | 53.4315 | 53.4315 | 53.4315 | 53.4315 | 53.4315 | 53.4315 | 53.4315 | 53.4315 | 53.4315 | 53.4315 | 53.4315 | 53.4315 | 53.4315 | 53.4315
95% | 2.269 | 48.604 | 64.5249 | 68.8586 | 41.1824 | 41.1777 | 41.6716 | 42.2136 | 43.3263 | 44.1258 | 44.5596 | 45.0339 | 45.4681 | 46.2527 | 47.2265 | 47.1584 | 47.1584 | 47.1584 | 47.1584 | 47.1584 | 47.1584 | 47.1584 | 47.1584 | 47.1584 | 47.1584 | 47.1584 | 47.1584 | 47.1584 | 47.1584 | 47.1584 | 47.1584 | 95% | 6.0506 | 54.1768 | 70.1297 | 74.3038 | 46.5033 | 46.521 | 46.9489 | 48.079 | 48.835 | 49.5754 | 50.4414 | 51.2435 | 52.0226 | 52.111 | 53.0203 | 52.3299 | 52.3299 | 52.3299 | 52.3299 | 52.3299 | 52.3299 | 52.3299 | 52.3299 | 52.3299 | 52.3299 | 52.3299 | 52.3299 | 52.3299 | 52.3299 | 52.3299 | 52.3299
90% | 5.6725 | 46.0459 | 61.1289 | 65.2344 | 39.0149 | 39.0105 | 39.4784 | 39.9918 | 41.0459 | 41.8034 | 42.2143 | 42.6637 | 43.075 | 43.8183 | 44.7409 | 44.6764 | 44.6764 | 44.6764 | 44.6764 | 44.6764 | 44.6764 | 44.6764 | 44.6764 | 44.6764 | 44.6764 | 44.6764 | 44.6764 | 44.6764 | 44.6764 | 44.6764 | 44.6764 | 90% | 16.2611 | 51.3254 | 66.4386 | 70.3931 | 44.0557 | 44.0725 | 44.4779 | 45.5485 | 46.2647 | 46.9662 | 47.7866 | 48.5465 | 49.2846 | 49.3683 | 50.2298 | 49.5757 | 49.5757 | 49.5757 | 49.5757 | 49.5757 | 49.5757 | 49.5757 | 49.5757 | 49.5757 | 49.5757 | 49.5757 | 49.5757 | 49.5757 | 49.5757 | 49.5757 | 49.5757
85% | 15.8829 | 43.4878 | 57.7328 | 61.6103 | 36.8474 | 36.8432 | 37.2851 | 37.77 | 38.7656 | 39.481 | 39.8691 | 40.2935 | 40.682 | 41.384 | 42.2553 | 42.1944 | 42.1944 | 42.1944 | 42.1944 | 42.1944 | 42.1944 | 42.1944 | 42.1944 | 42.1944 | 42.1944 | 42.1944 | 42.1944 | 42.1944 | 42.1944 | 42.1944 | 42.1944 | 85% | 26.4715 | 48.4739 | 62.7476 | 66.4824 | 41.6082 | 41.624 | 42.0069 | 43.0181 | 43.6945 | 44.3569 | 45.1318 | 45.8495 | 46.5465 | 46.6256 | 47.4392 | 46.8215 | 46.8215 | 46.8215 | 46.8215 | 46.8215 | 46.8215 | 46.8215 | 46.8215 | 46.8215 | 46.8215 | 46.8215 | 46.8215 | 46.8215 | 46.8215 | 46.8215 | 46.8215
80% | 31.0095 | 40.9297 | 54.3368 | 57.9862 | 34.6799 | 34.676 | 35.0919 | 35.5483 | 36.4853 | 37.1586 | 37.5239 | 37.9233 | 38.2889 | 38.9496 | 39.7697 | 39.7123 | 39.7123 | 39.7123 | 39.7123 | 39.7123 | 39.7123 | 39.7123 | 39.7123 | 39.7123 | 39.7123 | 39.7123 | 39.7123 | 39.7123 | 39.7123 | 39.7123 | 39.7123 | 80% | 34.0348 | 45.6225 | 59.0566 | 62.5716 | 39.1606 | 39.1755 | 39.5359 | 40.4876 | 41.1242 | 41.7477 | 42.477 | 43.1524 | 43.8085 | 43.8829 | 44.6487 | 44.0672 | 44.0672 | 44.0672 | 44.0672 | 44.0672 | 44.0672 | 44.0672 | 44.0672 | 44.0672 | 44.0672 | 44.0672 | 44.0672 | 44.0672 | 44.0672 | 44.0672 | 44.0672
75% | 72.9857 | 38.3716 | 50.9407 | 54.362 | 32.5124 | 32.5087 | 32.8986 | 33.3265 | 34.205 | 34.8362 | 35.1786 | 35.5531 | 35.8958 | 36.5153 | 37.2841 | 37.2303 | 37.2303 | 37.2303 | 37.2303 | 37.2303 | 37.2303 | 37.2303 | 37.2303 | 37.2303 | 37.2303 | 37.2303 | 37.2303 | 37.2303 | 37.2303 | 37.2303 | 37.2303 | 75% | 48.405 | 42.7711 | 55.3655 | 58.6609 | 36.7131 | 36.7271 | 37.0649 | 37.9571 | 38.5539 | 39.1385 | 39.8222 | 40.4554 | 41.0705 | 41.1402 | 41.8582 | 41.313 | 41.313 | 41.313 | 41.313 | 41.313 | 41.313 | 41.313 | 41.313 | 41.313 | 41.313 | 41.313 | 41.313 | 41.313 | 41.313 | 41.313 | 41.313
70% | 150.5094 | 35.8135 | 47.5447 | 50.7379 | 30.3449 | 30.3415 | 30.7054 | 31.1047 | 31.9246 | 32.5138 | 32.8334 | 33.1829 | 33.5028 | 34.0809 | 34.7984 | 34.7483 | 34.7483 | 34.7483 | 34.7483 | 34.7483 | 34.7483 | 34.7483 | 34.7483 | 34.7483 | 34.7483 | 34.7483 | 34.7483 | 34.7483 | 34.7483 | 34.7483 | 34.7483 | 70% | 76.3892 | 39.9197 | 51.6745 | 54.7502 | 34.2656 | 34.2786 | 34.5939 | 35.4266 | 35.9837 | 36.5292 | 37.1674 | 37.7584 | 38.3324 | 38.3976 | 39.0676 | 38.5588 | 38.5588 | 38.5588 | 38.5588 | 38.5588 | 38.5588 | 38.5588 | 38.5588 | 38.5588 | 38.5588 | 38.5588 | 38.5588 | 38.5588 | 38.5588 | 38.5588 | 38.5588
65% | 359.6342 | 33.2554 | 44.1486 | 47.1138 | 28.1774 | 28.1742 | 28.5121 | 28.883 | 29.6443 | 30.1914 | 30.4881 | 30.8127 | 31.1097 | 31.6466 | 32.3128 | 32.2663 | 32.2663 | 32.2663 | 32.2663 | 32.2663 | 32.2663 | 32.2663 | 32.2663 | 32.2663 | 32.2663 | 32.2663 | 32.2663 | 32.2663 | 32.2663 | 32.2663 | 32.2663 | 65% | 114.2056 | 37.0683 | 47.9835 | 50.8395 | 31.818 | 31.8301 | 32.1229 | 32.8962 | 33.4134 | 33.92 | 34.5126 | 35.0614 | 35.5944 | 35.6549 | 36.2771 | 35.8046 | 35.8046 | 35.8046 | 35.8046 | 35.8046 | 35.8046 | 35.8046 | 35.8046 | 35.8046 | 35.8046 | 35.8046 | 35.8046 | 35.8046 | 35.8046 | 35.8046 | 35.8046
60% | 689.7717 | 30.6973 | 40.7526 | 43.4896 | 26.0099 | 26.007 | 26.3189 | 26.6612 | 27.364 | 27.869 | 28.1429 | 28.4424 | 28.7167 | 29.2122 | 29.8272 | 29.7843 | 29.7843 | 29.7843 | 29.7843 | 29.7843 | 29.7843 | 29.7843 | 29.7843 | 29.7843 | 29.7843 | 29.7843 | 29.7843 | 29.7843 | 29.7843 | 29.7843 | 29.7843 | 60% | 178.1154 | 34.2169 | 44.2924 | 46.9287 | 29.3705 | 29.3817 | 29.6519 | 30.3657 | 30.8431 | 31.3108 | 31.8577 | 32.3643 | 32.8564 | 32.9122 | 33.4865 | 33.0504 | 33.0504 | 33.0504 | 33.0504 | 33.0504 | 33.0504 | 33.0504 | 33.0504 | 33.0504 | 33.0504 | 33.0504 | 33.0504 | 33.0504 | 33.0504 | 33.0504 | 33.0504
55% | 1095.5419 | 28.1392 | 37.3565 | 39.8655 | 23.8424 | 23.8397 | 24.1257 | 24.4394 | 25.0836 | 25.5465 | 25.7976 | 26.0722 | 26.3236 | 26.7779 | 27.3416 | 27.3022 | 27.3022 | 27.3022 | 27.3022 | 27.3022 | 27.3022 | 27.3022 | 27.3022 | 27.3022 | 27.3022 | 27.3022 | 27.3022 | 27.3022 | 27.3022 | 27.3022 | 27.3022 | 55% | 311.6074 | 31.3655 | 40.6014 | 43.018 | 26.9229 | 26.9332 | 27.181 | 27.8352 | 28.2729 | 28.7015 | 29.2029 | 29.6673 | 30.1183 | 30.1695 | 30.696 | 30.2962 | 30.2962 | 30.2962 | 30.2962 | 30.2962 | 30.2962 | 30.2962 | 30.2962 | 30.2962 | 30.2962 | 30.2962 | 30.2962 | 30.2962 | 30.2962 | 30.2962 | 30.2962
50% | 1666.1918 | 25.581 | 33.9605 | 36.2413 | 21.6749 | 21.6725 | 21.9324 | 22.2177 | 22.8033 | 23.2241 | 23.4524 | 23.702 | 23.9306 | 24.3435 | 24.856 | 24.8202 | 24.8202 | 24.8202 | 24.8202 | 24.8202 | 24.8202 | 24.8202 | 24.8202 | 24.8202 | 24.8202 | 24.8202 | 24.8202 | 24.8202 | 24.8202 | 24.8202 | 24.8202 | 50% | 636.0723 | 28.5141 | 36.9103 | 39.1073 | 24.4754 | 24.4847 | 24.71 | 25.3047 | 25.7026 | 26.0923 | 26.5481 | 26.9703 | 27.3803 | 27.4268 | 27.9054 | 27.542 | 27.542 | 27.542 | 27.542 | 27.542 | 27.542 | 27.542 | 27.542 | 27.542 | 27.542 | 27.542 | 27.542 | 27.542 | 27.542 | 27.542 | 27.542
45% | 2506.0947 | 23.0229 | 30.5644 | 32.6172 | 19.5074 | 19.5052 | 19.7392 | 19.9959 | 20.523 | 20.9017 | 21.1072 | 21.3318 | 21.5375 | 21.9092 | 22.3704 | 22.3382 | 22.3382 | 22.3382 | 22.3382 | 22.3382 | 22.3382 | 22.3382 | 22.3382 | 22.3382 | 22.3382 | 22.3382 | 22.3382 | 22.3382 | 22.3382 | 22.3382 | 22.3382 | 45% | 1179.4944 | 25.6627 | 33.2193 | 35.1965 | 22.0279 | 22.0362 | 22.239 | 22.7743 | 23.1324 | 23.4831 | 23.8933 | 24.2733 | 24.6423 | 24.6841 | 25.1149 | 24.7878 | 24.7878 | 24.7878 | 24.7878 | 24.7878 | 24.7878 | 24.7878 | 24.7878 | 24.7878 | 24.7878 | 24.7878 | 24.7878 | 24.7878 | 24.7878 | 24.7878 | 24.7878
40% | 3164.4787 | 20.4648 | 27.1684 | 28.9931 | 17.3399 | 17.338 | 17.5459 | 17.7741 | 18.2426 | 18.5793 | 18.7619 | 18.9616 | 19.1444 | 19.4748 | 19.8848 | 19.8562 | 19.8562 | 19.8562 | 19.8562 | 19.8562 | 19.8562 | 19.8562 | 19.8562 | 19.8562 | 19.8562 | 19.8562 | 19.8562 | 19.8562 | 19.8562 | 19.8562 | 19.8562 | 40% | 1808.3816 | 22.8113 | 29.5283 | 31.2858 | 19.5803 | 19.5878 | 19.768 | 20.2438 | 20.5621 | 20.8738 | 21.2385 | 21.5762 | 21.9042 | 21.9415 | 22.3244 | 22.0336 | 22.0336 | 22.0336 | 22.0336 | 22.0336 | 22.0336 | 22.0336 | 22.0336 | 22.0336 | 22.0336 | 22.0336 | 22.0336 | 22.0336 | 22.0336 | 22.0336 | 22.0336
35% | 3551.3408 | 17.9067 | 23.7723 | 25.3689 | 15.1724 | 15.1707 | 15.3527 | 15.5524 | 15.9623 | 16.2569 | 16.4167 | 16.5914 | 16.7514 | 17.0405 | 17.3992 | 17.3741 | 17.3741 | 17.3741 | 17.3741 | 17.3741 | 17.3741 | 17.3741 | 17.3741 | 17.3741 | 17.3741 | 17.3741 | 17.3741 | 17.3741 | 17.3741 | 17.3741 | 17.3741 | 35% | 2779.1293 | 19.9599 | 25.8372 | 27.3751 | 17.1328 | 17.1393 | 17.297 | 17.7133 | 17.9918 | 18.2646 | 18.5837 | 18.8792 | 19.1662 | 19.1988 | 19.5338 | 19.2794 | 19.2794 | 19.2794 | 19.2794 | 19.2794 | 19.2794 | 19.2794 | 19.2794 | 19.2794 | 19.2794 | 19.2794 | 19.2794 | 19.2794 | 19.2794 | 19.2794 | 19.2794
30% | 3758.953 | 15.3486 | 20.3763 | 21.7448 | 13.005 | 13.0035 | 13.1595 | 13.3306 | 13.682 | 13.9345 | 14.0714 | 14.2212 | 14.3583 | 14.6061 | 14.9136 | 14.8921 | 14.8921 | 14.8921 | 14.8921 | 14.8921 | 14.8921 | 14.8921 | 14.8921 | 14.8921 | 14.8921 | 14.8921 | 14.8921 | 14.8921 | 14.8921 | 14.8921 | 14.8921 | 30% | 3814.165 | 17.1085 | 22.1462 | 23.4644 | 14.6852 | 14.6908 | 14.826 | 15.1828 | 15.4216 | 15.6554 | 15.9289 | 16.1822 | 16.4282 | 16.4561 | 16.7433 | 16.5252 | 16.5252 | 16.5252 | 16.5252 | 16.5252 | 16.5252 | 16.5252 | 16.5252 | 16.5252 | 16.5252 | 16.5252 | 16.5252 | 16.5252 | 16.5252 | 16.5252 | 16.5252
25% | 3926.4798 | 12.7905 | 16.9802 | 18.1207 | 10.8375 | 10.8362 | 10.9662 | 11.1088 | 11.4017 | 11.6121 | 11.7262 | 11.851 | 11.9653 | 12.1718 | 12.428 | 12.4101 | 12.4101 | 12.4101 | 12.4101 | 12.4101 | 12.4101 | 12.4101 | 12.4101 | 12.4101 | 12.4101 | 12.4101 | 12.4101 | 12.4101 | 12.4101 | 12.4101 | 12.4101 | 25% | 4166.9923 | 14.257 | 18.4552 | 19.5536 | 12.2377 | 12.2424 | 12.355 | 12.6524 | 12.8513 | 13.0462 | 13.2741 | 13.4851 | 13.6902 | 13.7134 | 13.9527 | 13.771 | 13.771 | 13.771 | 13.771 | 13.771 | 13.771 | 13.771 | 13.771 | 13.771 | 13.771 | 13.771 | 13.771 | 13.771 | 13.771 | 13.771 | 13.771
20% | 4050.5177 | 10.2324 | 13.5842 | 14.4965 | 8.67 | 8.669 | 8.773 | 8.8871 | 9.1213 | 9.2897 | 9.381 | 9.4808 | 9.5722 | 9.7374 | 9.9424 | 9.9281 | 9.9281 | 9.9281 | 9.9281 | 9.9281 | 9.9281 | 9.9281 | 9.9281 | 9.9281 | 9.9281 | 9.9281 | 9.9281 | 9.9281 | 9.9281 | 9.9281 | 9.9281 | 20% | 4282.7105 | 11.4056 | 14.7641 | 15.6429 | 9.7902 | 9.7939 | 9.884 | 10.1219 | 10.281 | 10.4369 | 10.6192 | 10.7881 | 10.9521 | 10.9707 | 11.1622 | 11.0168 | 11.0168 | 11.0168 | 11.0168 | 11.0168 | 11.0168 | 11.0168 | 11.0168 | 11.0168 | 11.0168 | 11.0168 | 11.0168 | 11.0168 | 11.0168 | 11.0168 | 11.0168
15% | 4152.622 | 7.6743 | 10.1881 | 10.8724 | 6.5025 | 6.5017 | 6.5797 | 6.6653 | 6.841 | 6.9672 | 7.0357 | 7.1106 | 7.1792 | 7.3031 | 7.4568 | 7.4461 | 7.4461 | 7.4461 | 7.4461 | 7.4461 | 7.4461 | 7.4461 | 7.4461 | 7.4461 | 7.4461 | 7.4461 | 7.4461 | 7.4461 | 7.4461 | 7.4461 | 7.4461 | 15% | 4364.7722 | 8.5542 | 11.0731 | 11.7322 | 7.3426 | 7.3454 | 7.413 | 7.5914 | 7.7108 | 7.8277 | 7.9644 | 8.0911 | 8.2141 | 8.228 | 8.3716 | 8.2626 | 8.2626 | 8.2626 | 8.2626 | 8.2626 | 8.2626 | 8.2626 | 8.2626 | 8.2626 | 8.2626 | 8.2626 | 8.2626 | 8.2626 | 8.2626 | 8.2626 | 8.2626
10% | 4248.2976 | 5.1162 | 6.7921 | 7.2483 | 4.335 | 4.3345 | 4.3865 | 4.4435 | 4.5607 | 4.6448 | 4.6905 | 4.7404 | 4.7861 | 4.8687 | 4.9712 | 4.964 | 4.964 | 4.964 | 4.964 | 4.964 | 4.964 | 4.964 | 4.964 | 4.964 | 4.964 | 4.964 | 4.964 | 4.964 | 4.964 | 4.964 | 4.964 | 10% | 4391.6218 | 5.7028 | 7.3821 | 7.8215 | 4.8951 | 4.8969 | 4.942 | 5.0609 | 5.1405 | 5.2185 | 5.3096 | 5.3941 | 5.4761 | 5.4854 | 5.5811 | 5.5084 | 5.5084 | 5.5084 | 5.5084 | 5.5084 | 5.5084 | 5.5084 | 5.5084 | 5.5084 | 5.5084 | 5.5084 | 5.5084 | 5.5084 | 5.5084 | 5.5084 | 5.5084
5% | 4361.7469 | 2.5581 | 3.396 | 3.6241 | 2.1675 | 2.1672 | 2.1932 | 2.2218 | 2.2803 | 2.3224 | 2.3452 | 2.3702 | 2.3931 | 2.4344 | 2.4856 | 2.482 | 2.482 | 2.482 | 2.482 | 2.482 | 2.482 | 2.482 | 2.482 | 2.482 | 2.482 | 2.482 | 2.482 | 2.482 | 2.482 | 2.482 | 2.482 | 5% | 4391.6218 | 2.8514 | 3.691 | 3.9107 | 2.4475 | 2.4485 | 2.471 | 2.5305 | 2.5703 | 2.6092 | 2.6548 | 2.697 | 2.738 | 2.7427 | 2.7905 | 2.7542 | 2.7542 | 2.7542 | 2.7542 | 2.7542 | 2.7542 | 2.7542 | 2.7542 | 2.7542 | 2.7542 | 2.7542 | 2.7542 | 2.7542 | 2.7542 | 2.7542 | 2.7542
9.992e-14% | 4391.6218 | 5.1121e-14 | 6.7867e-14 | 7.2425e-14 | 4.3315e-14 | 4.331e-14 | 4.383e-14 | 4.44e-14 | 4.557e-14 | 4.6411e-14 | 4.6867e-14 | 4.7366e-14 | 4.7823e-14 | 4.8648e-14 | 4.9672e-14 | 4.9601e-14 | 4.9601e-14 | 4.9601e-14 | 4.9601e-14 | 4.9601e-14 | 4.9601e-14 | 4.9601e-14 | 4.9601e-14 | 4.9601e-14 | 4.9601e-14 | 4.9601e-14 | 4.9601e-14 | 4.9601e-14 | 4.9601e-14 | 4.9601e-14 | 4.9601e-14 | 9.992e-14% | 4391.6218 | 5.6983e-14 | 7.3762e-14 | 7.8152e-14 | 4.8912e-14 | 4.893e-14 | 4.938e-14 | 5.0569e-14 | 5.1364e-14 | 5.2143e-14 | 5.3054e-14 | 5.3897e-14 | 5.4717e-14 | 5.481e-14 | 5.5766e-14 | 5.504e-14 | 5.504e-14 | 5.504e-14 | 5.504e-14 | 5.504e-14 | 5.504e-14 | 5.504e-14 | 5.504e-14 | 5.504e-14 | 5.504e-14 | 5.504e-14 | 5.504e-14 | 5.504e-14 | 5.504e-14 | 5.504e-14 | 5.504e-14
Option 3
Winter Season | [31 empty] | Winter Season
P50 | [31 empty] | P10
% of MD | Winter - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Winter - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 45.0311 | 62.4376 | 66.9594 | 67.7285 | 68.3267 | 69.3603 | 71.7146 | 73.2888 | 75.2849 | 76.3199 | 77.2291 | 75.5455 | 77.5138 | 80.6095 | 78.2564 | 78.2564 | 78.2564 | 78.2564 | 78.2564 | 78.2564 | 78.2564 | 78.2564 | 78.2564 | 78.2564 | 78.2564 | 78.2564 | 78.2564 | 78.2564 | 78.2564 | 78.2564 | 100% | 0 | 48.1978 | 65.3847 | 70.0831 | 70.8084 | 71.267 | 72.2781 | 74.6693 | 75.9727 | 78.4597 | 86.0243 | 79.7829 | 78.5605 | 80.2054 | 83.8053 | 81.3648 | 81.3648 | 81.3648 | 81.3648 | 81.3648 | 81.3648 | 81.3648 | 81.3648 | 81.3648 | 81.3648 | 81.3648 | 81.3648 | 81.3648 | 81.3648 | 81.3648 | 81.3648
99% | 1.486 | 44.5808 | 61.8132 | 66.2898 | 67.0512 | 67.6435 | 68.6667 | 70.9975 | 72.5559 | 74.532 | 75.5567 | 76.4569 | 74.7901 | 76.7387 | 79.8034 | 77.4739 | 77.4739 | 77.4739 | 77.4739 | 77.4739 | 77.4739 | 77.4739 | 77.4739 | 77.4739 | 77.4739 | 77.4739 | 77.4739 | 77.4739 | 77.4739 | 77.4739 | 77.4739 | 99% | 1.486 | 47.7158 | 64.7309 | 69.3823 | 70.1003 | 70.5543 | 71.5553 | 73.9226 | 75.2129 | 77.6751 | 85.1641 | 78.9851 | 77.7749 | 79.4033 | 82.9672 | 80.5512 | 80.5512 | 80.5512 | 80.5512 | 80.5512 | 80.5512 | 80.5512 | 80.5512 | 80.5512 | 80.5512 | 80.5512 | 80.5512 | 80.5512 | 80.5512 | 80.5512 | 80.5512
98% | 3.2692 | 44.1305 | 61.1889 | 65.6202 | 66.3739 | 66.9602 | 67.9731 | 70.2804 | 71.823 | 73.7792 | 74.7935 | 75.6846 | 74.0346 | 75.9636 | 78.9973 | 76.6913 | 76.6913 | 76.6913 | 76.6913 | 76.6913 | 76.6913 | 76.6913 | 76.6913 | 76.6913 | 76.6913 | 76.6913 | 76.6913 | 76.6913 | 76.6913 | 76.6913 | 76.6913 | 98% | 3.2692 | 47.2338 | 64.0771 | 68.6815 | 69.3922 | 69.8416 | 70.8325 | 73.1759 | 74.4532 | 76.8905 | 84.3038 | 78.1873 | 76.9893 | 78.6013 | 82.1292 | 79.7375 | 79.7375 | 79.7375 | 79.7375 | 79.7375 | 79.7375 | 79.7375 | 79.7375 | 79.7375 | 79.7375 | 79.7375 | 79.7375 | 79.7375 | 79.7375 | 79.7375 | 79.7375
97% | 6.8356 | 43.6802 | 60.5645 | 64.9506 | 65.6966 | 66.2769 | 67.2795 | 69.5632 | 71.0901 | 73.0263 | 74.0303 | 74.9123 | 73.2792 | 75.1884 | 78.1912 | 75.9087 | 75.9087 | 75.9087 | 75.9087 | 75.9087 | 75.9087 | 75.9087 | 75.9087 | 75.9087 | 75.9087 | 75.9087 | 75.9087 | 75.9087 | 75.9087 | 75.9087 | 75.9087 | 97% | 6.8356 | 46.7518 | 63.4232 | 67.9806 | 68.6841 | 69.129 | 70.1097 | 72.4292 | 73.6935 | 76.1059 | 83.4436 | 77.3894 | 76.2037 | 77.7992 | 81.2911 | 78.9239 | 78.9239 | 78.9239 | 78.9239 | 78.9239 | 78.9239 | 78.9239 | 78.9239 | 78.9239 | 78.9239 | 78.9239 | 78.9239 | 78.9239 | 78.9239 | 78.9239 | 78.9239
95% | 17.5347 | 42.7796 | 59.3157 | 63.6114 | 64.342 | 64.9104 | 65.8923 | 68.1289 | 69.6243 | 71.5207 | 72.5039 | 73.3677 | 71.7683 | 73.6382 | 76.579 | 74.3436 | 74.3436 | 74.3436 | 74.3436 | 74.3436 | 74.3436 | 74.3436 | 74.3436 | 74.3436 | 74.3436 | 74.3436 | 74.3436 | 74.3436 | 74.3436 | 74.3436 | 74.3436 | 95% | 17.5347 | 45.7879 | 62.1155 | 66.579 | 67.268 | 67.7036 | 68.6642 | 70.9358 | 72.174 | 74.5368 | 81.7231 | 75.7938 | 74.6325 | 76.1951 | 79.615 | 77.2966 | 77.2966 | 77.2966 | 77.2966 | 77.2966 | 77.2966 | 77.2966 | 77.2966 | 77.2966 | 77.2966 | 77.2966 | 77.2966 | 77.2966 | 77.2966 | 77.2966 | 77.2966
90% | 78.7576 | 40.528 | 56.1939 | 60.2634 | 60.9556 | 61.4941 | 62.4243 | 64.5432 | 65.9599 | 67.7564 | 68.6879 | 69.5062 | 67.991 | 69.7625 | 72.5486 | 70.4308 | 70.4308 | 70.4308 | 70.4308 | 70.4308 | 70.4308 | 70.4308 | 70.4308 | 70.4308 | 70.4308 | 70.4308 | 70.4308 | 70.4308 | 70.4308 | 70.4308 | 70.4308 | 90% | 78.7576 | 43.378 | 58.8463 | 63.0748 | 63.7275 | 64.1403 | 65.0503 | 67.2023 | 68.3754 | 70.6138 | 77.4219 | 71.8046 | 70.7045 | 72.1848 | 75.4247 | 73.2283 | 73.2283 | 73.2283 | 73.2283 | 73.2283 | 73.2283 | 73.2283 | 73.2283 | 73.2283 | 73.2283 | 73.2283 | 73.2283 | 73.2283 | 73.2283 | 73.2283 | 73.2283
85% | 236.8672 | 38.2764 | 53.072 | 56.9155 | 57.5692 | 58.0777 | 58.9563 | 60.9575 | 62.2954 | 63.9922 | 64.8719 | 65.6448 | 64.2137 | 65.8868 | 68.5181 | 66.518 | 66.518 | 66.518 | 66.518 | 66.518 | 66.518 | 66.518 | 66.518 | 66.518 | 66.518 | 66.518 | 66.518 | 66.518 | 66.518 | 66.518 | 66.518 | 85% | 236.8672 | 40.9681 | 55.577 | 59.5707 | 60.1871 | 60.5769 | 61.4364 | 63.4689 | 64.5768 | 66.6908 | 73.1207 | 67.8155 | 66.7765 | 68.1746 | 71.2345 | 69.1601 | 69.1601 | 69.1601 | 69.1601 | 69.1601 | 69.1601 | 69.1601 | 69.1601 | 69.1601 | 69.1601 | 69.1601 | 69.1601 | 69.1601 | 69.1601 | 69.1601 | 69.1601
80% | 497.5104 | 36.0249 | 49.9501 | 53.5675 | 54.1828 | 54.6614 | 55.4882 | 57.3717 | 58.631 | 60.2279 | 61.056 | 61.7833 | 60.4364 | 62.0111 | 64.4876 | 62.6051 | 62.6051 | 62.6051 | 62.6051 | 62.6051 | 62.6051 | 62.6051 | 62.6051 | 62.6051 | 62.6051 | 62.6051 | 62.6051 | 62.6051 | 62.6051 | 62.6051 | 62.6051 | 80% | 497.5104 | 38.5582 | 52.3078 | 56.0665 | 56.6467 | 57.0136 | 57.8225 | 59.7354 | 60.7781 | 62.7678 | 68.8195 | 63.8263 | 62.8484 | 64.1643 | 67.0442 | 65.0919 | 65.0919 | 65.0919 | 65.0919 | 65.0919 | 65.0919 | 65.0919 | 65.0919 | 65.0919 | 65.0919 | 65.0919 | 65.0919 | 65.0919 | 65.0919 | 65.0919 | 65.0919
75% | 803.6248 | 33.7733 | 46.8282 | 50.2195 | 50.7964 | 51.245 | 52.0202 | 53.786 | 54.9666 | 56.4637 | 57.24 | 57.9219 | 56.6592 | 58.1354 | 60.4571 | 58.6923 | 58.6923 | 58.6923 | 58.6923 | 58.6923 | 58.6923 | 58.6923 | 58.6923 | 58.6923 | 58.6923 | 58.6923 | 58.6923 | 58.6923 | 58.6923 | 58.6923 | 58.6923 | 75% | 803.6248 | 36.1483 | 49.0386 | 52.5623 | 53.1063 | 53.4502 | 54.2086 | 56.0019 | 56.9795 | 58.8448 | 64.5182 | 59.8372 | 58.9204 | 60.154 | 62.8539 | 61.0236 | 61.0236 | 61.0236 | 61.0236 | 61.0236 | 61.0236 | 61.0236 | 61.0236 | 61.0236 | 61.0236 | 61.0236 | 61.0236 | 61.0236 | 61.0236 | 61.0236 | 61.0236
70% | 1155.2107 | 31.5218 | 43.7063 | 46.8715 | 47.4099 | 47.8287 | 48.5522 | 50.2003 | 51.3021 | 52.6994 | 53.424 | 54.0604 | 52.8819 | 54.2597 | 56.4267 | 54.7795 | 54.7795 | 54.7795 | 54.7795 | 54.7795 | 54.7795 | 54.7795 | 54.7795 | 54.7795 | 54.7795 | 54.7795 | 54.7795 | 54.7795 | 54.7795 | 54.7795 | 54.7795 | 70% | 1155.2107 | 33.7384 | 45.7693 | 49.0582 | 49.5659 | 49.8869 | 50.5947 | 52.2685 | 53.1809 | 54.9218 | 60.217 | 55.8481 | 54.9924 | 56.1438 | 58.6637 | 56.9554 | 56.9554 | 56.9554 | 56.9554 | 56.9554 | 56.9554 | 56.9554 | 56.9554 | 56.9554 | 56.9554 | 56.9554 | 56.9554 | 56.9554 | 56.9554 | 56.9554 | 56.9554
65% | 1553.1596 | 29.2702 | 40.5844 | 43.5236 | 44.0235 | 44.4124 | 45.0842 | 46.6145 | 47.6377 | 48.9352 | 49.608 | 50.1989 | 49.1046 | 50.384 | 52.3962 | 50.8667 | 50.8667 | 50.8667 | 50.8667 | 50.8667 | 50.8667 | 50.8667 | 50.8667 | 50.8667 | 50.8667 | 50.8667 | 50.8667 | 50.8667 | 50.8667 | 50.8667 | 50.8667 | 65% | 1553.1596 | 31.3286 | 42.5001 | 45.554 | 46.0254 | 46.3235 | 46.9808 | 48.535 | 49.3822 | 50.9988 | 55.9158 | 51.8589 | 51.0643 | 52.1335 | 54.4734 | 52.8871 | 52.8871 | 52.8871 | 52.8871 | 52.8871 | 52.8871 | 52.8871 | 52.8871 | 52.8871 | 52.8871 | 52.8871 | 52.8871 | 52.8871 | 52.8871 | 52.8871 | 52.8871
60% | 2026.2996 | 27.0187 | 37.4626 | 40.1756 | 40.6371 | 40.996 | 41.6162 | 43.0288 | 43.9733 | 45.1709 | 45.792 | 46.3375 | 45.3273 | 46.5083 | 48.3657 | 46.9539 | 46.9539 | 46.9539 | 46.9539 | 46.9539 | 46.9539 | 46.9539 | 46.9539 | 46.9539 | 46.9539 | 46.9539 | 46.9539 | 46.9539 | 46.9539 | 46.9539 | 46.9539 | 60% | 2026.2996 | 28.9187 | 39.2308 | 42.0499 | 42.485 | 42.7602 | 43.3669 | 44.8016 | 45.5836 | 47.0758 | 51.6146 | 47.8698 | 47.1363 | 48.1232 | 50.2832 | 48.8189 | 48.8189 | 48.8189 | 48.8189 | 48.8189 | 48.8189 | 48.8189 | 48.8189 | 48.8189 | 48.8189 | 48.8189 | 48.8189 | 48.8189 | 48.8189 | 48.8189 | 48.8189
55% | 2598.4068 | 24.7671 | 34.3407 | 36.8276 | 37.2507 | 37.5797 | 38.1482 | 39.4431 | 40.3088 | 41.4067 | 41.976 | 42.476 | 41.55 | 42.6326 | 44.3352 | 43.041 | 43.041 | 43.041 | 43.041 | 43.041 | 43.041 | 43.041 | 43.041 | 43.041 | 43.041 | 43.041 | 43.041 | 43.041 | 43.041 | 43.041 | 43.041 | 55% | 2598.4068 | 26.5088 | 35.9616 | 38.5457 | 38.9446 | 39.1968 | 39.753 | 41.0681 | 41.785 | 43.1529 | 47.3134 | 43.8806 | 43.2083 | 44.113 | 46.0929 | 44.7507 | 44.7507 | 44.7507 | 44.7507 | 44.7507 | 44.7507 | 44.7507 | 44.7507 | 44.7507 | 44.7507 | 44.7507 | 44.7507 | 44.7507 | 44.7507 | 44.7507 | 44.7507
50% | 3233.5201 | 22.5156 | 31.2188 | 33.4797 | 33.8642 | 34.1634 | 34.6802 | 35.8573 | 36.6444 | 37.6424 | 38.16 | 38.6146 | 37.7728 | 38.7569 | 40.3048 | 39.1282 | 39.1282 | 39.1282 | 39.1282 | 39.1282 | 39.1282 | 39.1282 | 39.1282 | 39.1282 | 39.1282 | 39.1282 | 39.1282 | 39.1282 | 39.1282 | 39.1282 | 39.1282 | 50% | 3233.5201 | 24.0989 | 32.6924 | 35.0416 | 35.4042 | 35.6335 | 36.139 | 37.3346 | 37.9863 | 39.2299 | 43.0122 | 39.8915 | 39.2803 | 40.1027 | 41.9026 | 40.6824 | 40.6824 | 40.6824 | 40.6824 | 40.6824 | 40.6824 | 40.6824 | 40.6824 | 40.6824 | 40.6824 | 40.6824 | 40.6824 | 40.6824 | 40.6824 | 40.6824 | 40.6824
45% | 3775.313 | 20.264 | 28.0969 | 30.1317 | 30.4778 | 30.747 | 31.2121 | 32.2716 | 32.9799 | 33.8782 | 34.344 | 34.7531 | 33.9955 | 34.8812 | 36.2743 | 35.2154 | 35.2154 | 35.2154 | 35.2154 | 35.2154 | 35.2154 | 35.2154 | 35.2154 | 35.2154 | 35.2154 | 35.2154 | 35.2154 | 35.2154 | 35.2154 | 35.2154 | 35.2154 | 45% | 3775.313 | 21.689 | 29.4231 | 31.5374 | 31.8638 | 32.0701 | 32.5251 | 33.6012 | 34.1877 | 35.3069 | 38.7109 | 35.9023 | 35.3522 | 36.0924 | 37.7124 | 36.6142 | 36.6142 | 36.6142 | 36.6142 | 36.6142 | 36.6142 | 36.6142 | 36.6142 | 36.6142 | 36.6142 | 36.6142 | 36.6142 | 36.6142 | 36.6142 | 36.6142 | 36.6142
40% | 4072.8088 | 18.0124 | 24.975 | 26.7837 | 27.0914 | 27.3307 | 27.7441 | 28.6859 | 29.3155 | 30.114 | 30.528 | 30.8917 | 30.2182 | 31.0055 | 32.2438 | 31.3026 | 31.3026 | 31.3026 | 31.3026 | 31.3026 | 31.3026 | 31.3026 | 31.3026 | 31.3026 | 31.3026 | 31.3026 | 31.3026 | 31.3026 | 31.3026 | 31.3026 | 31.3026 | 40% | 4072.8088 | 19.2791 | 26.1539 | 28.0332 | 28.3234 | 28.5068 | 28.9112 | 29.8677 | 30.3891 | 31.3839 | 34.4097 | 31.9132 | 31.4242 | 32.0822 | 33.5221 | 32.5459 | 32.5459 | 32.5459 | 32.5459 | 32.5459 | 32.5459 | 32.5459 | 32.5459 | 32.5459 | 32.5459 | 32.5459 | 32.5459 | 32.5459 | 32.5459 | 32.5459 | 32.5459
35% | 4198.821 | 15.7609 | 21.8532 | 23.4358 | 23.705 | 23.9144 | 24.2761 | 25.1001 | 25.6511 | 26.3497 | 26.712 | 27.0302 | 26.4409 | 27.1298 | 28.2133 | 27.3897 | 27.3897 | 27.3897 | 27.3897 | 27.3897 | 27.3897 | 27.3897 | 27.3897 | 27.3897 | 27.3897 | 27.3897 | 27.3897 | 27.3897 | 27.3897 | 27.3897 | 27.3897 | 35% | 4198.821 | 16.8692 | 22.8847 | 24.5291 | 24.7829 | 24.9434 | 25.2973 | 26.1342 | 26.5904 | 27.4609 | 30.1085 | 27.924 | 27.4962 | 28.0719 | 29.3318 | 28.4777 | 28.4777 | 28.4777 | 28.4777 | 28.4777 | 28.4777 | 28.4777 | 28.4777 | 28.4777 | 28.4777 | 28.4777 | 28.4777 | 28.4777 | 28.4777 | 28.4777 | 28.4777
30% | 4271.3374 | 13.5093 | 18.7313 | 20.0878 | 20.3185 | 20.498 | 20.8081 | 21.5144 | 21.9866 | 22.5855 | 22.896 | 23.1687 | 22.6637 | 23.2542 | 24.1829 | 23.4769 | 23.4769 | 23.4769 | 23.4769 | 23.4769 | 23.4769 | 23.4769 | 23.4769 | 23.4769 | 23.4769 | 23.4769 | 23.4769 | 23.4769 | 23.4769 | 23.4769 | 23.4769 | 30% | 4271.3374 | 14.4593 | 19.6154 | 21.0249 | 21.2425 | 21.3801 | 21.6834 | 22.4008 | 22.7918 | 23.5379 | 25.8073 | 23.9349 | 23.5682 | 24.0616 | 25.1416 | 24.4094 | 24.4094 | 24.4094 | 24.4094 | 24.4094 | 24.4094 | 24.4094 | 24.4094 | 24.4094 | 24.4094 | 24.4094 | 24.4094 | 24.4094 | 24.4094 | 24.4094 | 24.4094
25% | 4321.8611 | 11.2578 | 15.6094 | 16.7398 | 16.9321 | 17.0817 | 17.3401 | 17.9287 | 18.3222 | 18.8212 | 19.08 | 19.3073 | 18.8864 | 19.3785 | 20.1524 | 19.5641 | 19.5641 | 19.5641 | 19.5641 | 19.5641 | 19.5641 | 19.5641 | 19.5641 | 19.5641 | 19.5641 | 19.5641 | 19.5641 | 19.5641 | 19.5641 | 19.5641 | 19.5641 | 25% | 4321.8611 | 12.0494 | 16.3462 | 17.5208 | 17.7021 | 17.8167 | 18.0695 | 18.6673 | 18.9932 | 19.6149 | 21.5061 | 19.9457 | 19.6401 | 20.0513 | 20.9513 | 20.3412 | 20.3412 | 20.3412 | 20.3412 | 20.3412 | 20.3412 | 20.3412 | 20.3412 | 20.3412 | 20.3412 | 20.3412 | 20.3412 | 20.3412 | 20.3412 | 20.3412 | 20.3412
20% | 4353.067 | 9.0062 | 12.4875 | 13.3919 | 13.5457 | 13.6653 | 13.8721 | 14.3429 | 14.6578 | 15.057 | 15.264 | 15.4458 | 15.1091 | 15.5028 | 16.1219 | 15.6513 | 15.6513 | 15.6513 | 15.6513 | 15.6513 | 15.6513 | 15.6513 | 15.6513 | 15.6513 | 15.6513 | 15.6513 | 15.6513 | 15.6513 | 15.6513 | 15.6513 | 15.6513 | 20% | 4353.067 | 9.6396 | 13.0769 | 14.0166 | 14.1617 | 14.2534 | 14.4556 | 14.9339 | 15.1945 | 15.6919 | 17.2049 | 15.9566 | 15.7121 | 16.0411 | 16.7611 | 16.273 | 16.273 | 16.273 | 16.273 | 16.273 | 16.273 | 16.273 | 16.273 | 16.273 | 16.273 | 16.273 | 16.273 | 16.273 | 16.273 | 16.273 | 16.273
15% | 4369.4129 | 6.7547 | 9.3656 | 10.0439 | 10.1593 | 10.249 | 10.404 | 10.7572 | 10.9933 | 11.2927 | 11.448 | 11.5844 | 11.3318 | 11.6271 | 12.0914 | 11.7385 | 11.7385 | 11.7385 | 11.7385 | 11.7385 | 11.7385 | 11.7385 | 11.7385 | 11.7385 | 11.7385 | 11.7385 | 11.7385 | 11.7385 | 11.7385 | 11.7385 | 11.7385 | 15% | 4369.4129 | 7.2297 | 9.8077 | 10.5125 | 10.6213 | 10.69 | 10.8417 | 11.2004 | 11.3959 | 11.769 | 12.9036 | 11.9674 | 11.7841 | 12.0308 | 12.5708 | 12.2047 | 12.2047 | 12.2047 | 12.2047 | 12.2047 | 12.2047 | 12.2047 | 12.2047 | 12.2047 | 12.2047 | 12.2047 | 12.2047 | 12.2047 | 12.2047 | 12.2047 | 12.2047
10% | 4378.6261 | 4.5031 | 6.2438 | 6.6959 | 6.7728 | 6.8327 | 6.936 | 7.1715 | 7.3289 | 7.5285 | 7.632 | 7.7229 | 7.5546 | 7.7514 | 8.061 | 7.8256 | 7.8256 | 7.8256 | 7.8256 | 7.8256 | 7.8256 | 7.8256 | 7.8256 | 7.8256 | 7.8256 | 7.8256 | 7.8256 | 7.8256 | 7.8256 | 7.8256 | 7.8256 | 10% | 4378.6261 | 4.8198 | 6.5385 | 7.0083 | 7.0808 | 7.1267 | 7.2278 | 7.4669 | 7.5973 | 7.846 | 8.6024 | 7.9783 | 7.8561 | 8.0205 | 8.3805 | 8.1365 | 8.1365 | 8.1365 | 8.1365 | 8.1365 | 8.1365 | 8.1365 | 8.1365 | 8.1365 | 8.1365 | 8.1365 | 8.1365 | 8.1365 | 8.1365 | 8.1365 | 8.1365
5% | 4391.7028 | 2.2516 | 3.1219 | 3.348 | 3.3864 | 3.4163 | 3.468 | 3.5857 | 3.6644 | 3.7642 | 3.816 | 3.8615 | 3.7773 | 3.8757 | 4.0305 | 3.9128 | 3.9128 | 3.9128 | 3.9128 | 3.9128 | 3.9128 | 3.9128 | 3.9128 | 3.9128 | 3.9128 | 3.9128 | 3.9128 | 3.9128 | 3.9128 | 3.9128 | 3.9128 | 5% | 4391.7028 | 2.4099 | 3.2692 | 3.5042 | 3.5404 | 3.5633 | 3.6139 | 3.7335 | 3.7986 | 3.923 | 4.3012 | 3.9891 | 3.928 | 4.0103 | 4.1903 | 4.0682 | 4.0682 | 4.0682 | 4.0682 | 4.0682 | 4.0682 | 4.0682 | 4.0682 | 4.0682 | 4.0682 | 4.0682 | 4.0682 | 4.0682 | 4.0682 | 4.0682 | 4.0682
9.992e-14% | 4391.7028 | 4.4995e-14 | 6.2388e-14 | 6.6906e-14 | 6.7674e-14 | 6.8272e-14 | 6.9305e-14 | 7.1657e-14 | 7.323e-14 | 7.5225e-14 | 7.6259e-14 | 7.7167e-14 | 7.5485e-14 | 7.7452e-14 | 8.0545e-14 | 7.8194e-14 | 7.8194e-14 | 7.8194e-14 | 7.8194e-14 | 7.8194e-14 | 7.8194e-14 | 7.8194e-14 | 7.8194e-14 | 7.8194e-14 | 7.8194e-14 | 7.8194e-14 | 7.8194e-14 | 7.8194e-14 | 7.8194e-14 | 7.8194e-14 | 7.8194e-14 | 9.992e-14% | 4391.7028 | 4.8159e-14 | 6.5332e-14 | 7.0027e-14 | 7.0752e-14 | 7.121e-14 | 7.222e-14 | 7.461e-14 | 7.5912e-14 | 7.8397e-14 | 8.5956e-14 | 7.9719e-14 | 7.8498e-14 | 8.0141e-14 | 8.3738e-14 | 8.13e-14 | 8.13e-14 | 8.13e-14 | 8.13e-14 | 8.13e-14 | 8.13e-14 | 8.13e-14 | 8.13e-14 | 8.13e-14 | 8.13e-14 | 8.13e-14 | 8.13e-14 | 8.13e-14 | 8.13e-14 | 8.13e-14 | 8.13e-14
Summer Season | [31 empty] | Summer Season
P50 | [31 empty] | P10
% of MD | Summer - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Summer - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 51.1621 | 67.921 | 72.4827 | 72.3498 | 72.345 | 72.8648 | 73.4353 | 74.6066 | 75.4483 | 75.9048 | 76.4041 | 76.8611 | 77.687 | 78.7121 | 78.6404 | 78.6404 | 78.6404 | 78.6404 | 78.6404 | 78.6404 | 78.6404 | 78.6404 | 78.6404 | 78.6404 | 78.6404 | 78.6404 | 78.6404 | 78.6404 | 78.6404 | 78.6404 | 100% | 0 | 57.0282 | 73.8207 | 78.2145 | 77.9508 | 77.9694 | 78.4199 | 79.6095 | 80.4052 | 81.1846 | 82.0962 | 82.9406 | 83.7606 | 83.8537 | 84.8109 | 84.0841 | 84.0841 | 84.0841 | 84.0841 | 84.0841 | 84.0841 | 84.0841 | 84.0841 | 84.0841 | 84.0841 | 84.0841 | 84.0841 | 84.0841 | 84.0841 | 84.0841 | 84.0841
99% | 0 | 50.6505 | 67.2418 | 71.7579 | 71.6263 | 71.6215 | 72.1362 | 72.701 | 73.8605 | 74.6938 | 75.1458 | 75.64 | 76.0925 | 76.9101 | 77.9249 | 77.854 | 77.854 | 77.854 | 77.854 | 77.854 | 77.854 | 77.854 | 77.854 | 77.854 | 77.854 | 77.854 | 77.854 | 77.854 | 77.854 | 77.854 | 77.854 | 99% | 1.5127 | 56.4579 | 73.0825 | 77.4324 | 77.1713 | 77.1897 | 77.6357 | 78.8134 | 79.6012 | 80.3728 | 81.2753 | 82.1112 | 82.923 | 83.0151 | 83.9628 | 83.2432 | 83.2432 | 83.2432 | 83.2432 | 83.2432 | 83.2432 | 83.2432 | 83.2432 | 83.2432 | 83.2432 | 83.2432 | 83.2432 | 83.2432 | 83.2432 | 83.2432 | 83.2432
98% | 0 | 50.1389 | 66.5626 | 71.033 | 70.9028 | 70.8981 | 71.4075 | 71.9666 | 73.1145 | 73.9393 | 74.3867 | 74.876 | 75.3239 | 76.1333 | 77.1378 | 77.0676 | 77.0676 | 77.0676 | 77.0676 | 77.0676 | 77.0676 | 77.0676 | 77.0676 | 77.0676 | 77.0676 | 77.0676 | 77.0676 | 77.0676 | 77.0676 | 77.0676 | 77.0676 | 98% | 2.269 | 55.8876 | 72.3443 | 76.6503 | 76.3918 | 76.41 | 76.8515 | 78.0173 | 78.7971 | 79.5609 | 80.4543 | 81.2818 | 82.0854 | 82.1766 | 83.1147 | 82.4024 | 82.4024 | 82.4024 | 82.4024 | 82.4024 | 82.4024 | 82.4024 | 82.4024 | 82.4024 | 82.4024 | 82.4024 | 82.4024 | 82.4024 | 82.4024 | 82.4024 | 82.4024
97% | 0.37816 | 49.6272 | 65.8834 | 70.3082 | 70.1794 | 70.1746 | 70.6789 | 71.2323 | 72.3684 | 73.1848 | 73.6277 | 74.112 | 74.5553 | 75.3564 | 76.3507 | 76.2812 | 76.2812 | 76.2812 | 76.2812 | 76.2812 | 76.2812 | 76.2812 | 76.2812 | 76.2812 | 76.2812 | 76.2812 | 76.2812 | 76.2812 | 76.2812 | 76.2812 | 76.2812 | 97% | 3.7816 | 55.3173 | 71.6061 | 75.8681 | 75.6123 | 75.6303 | 76.0673 | 77.2212 | 77.9931 | 78.7491 | 79.6334 | 80.4523 | 81.2478 | 81.338 | 82.2666 | 81.5615 | 81.5615 | 81.5615 | 81.5615 | 81.5615 | 81.5615 | 81.5615 | 81.5615 | 81.5615 | 81.5615 | 81.5615 | 81.5615 | 81.5615 | 81.5615 | 81.5615 | 81.5615
95% | 2.269 | 48.604 | 64.5249 | 68.8586 | 68.7324 | 68.7277 | 69.2216 | 69.7636 | 70.8763 | 71.6758 | 72.1096 | 72.5839 | 73.0181 | 73.8027 | 74.7765 | 74.7084 | 74.7084 | 74.7084 | 74.7084 | 74.7084 | 74.7084 | 74.7084 | 74.7084 | 74.7084 | 74.7084 | 74.7084 | 74.7084 | 74.7084 | 74.7084 | 74.7084 | 74.7084 | 95% | 6.0506 | 54.1768 | 70.1297 | 74.3038 | 74.0533 | 74.071 | 74.4989 | 75.629 | 76.385 | 77.1254 | 77.9914 | 78.7935 | 79.5726 | 79.661 | 80.5703 | 79.8799 | 79.8799 | 79.8799 | 79.8799 | 79.8799 | 79.8799 | 79.8799 | 79.8799 | 79.8799 | 79.8799 | 79.8799 | 79.8799 | 79.8799 | 79.8799 | 79.8799 | 79.8799
90% | 5.6725 | 46.0459 | 61.1289 | 65.2344 | 65.1149 | 65.1105 | 65.5784 | 66.0918 | 67.1459 | 67.9034 | 68.3143 | 68.7637 | 69.175 | 69.9183 | 70.8409 | 70.7764 | 70.7764 | 70.7764 | 70.7764 | 70.7764 | 70.7764 | 70.7764 | 70.7764 | 70.7764 | 70.7764 | 70.7764 | 70.7764 | 70.7764 | 70.7764 | 70.7764 | 70.7764 | 90% | 16.2611 | 51.3254 | 66.4386 | 70.3931 | 70.1557 | 70.1725 | 70.5779 | 71.6485 | 72.3647 | 73.0662 | 73.8866 | 74.6465 | 75.3846 | 75.4683 | 76.3298 | 75.6757 | 75.6757 | 75.6757 | 75.6757 | 75.6757 | 75.6757 | 75.6757 | 75.6757 | 75.6757 | 75.6757 | 75.6757 | 75.6757 | 75.6757 | 75.6757 | 75.6757 | 75.6757
85% | 15.8829 | 43.4878 | 57.7328 | 61.6103 | 61.4974 | 61.4932 | 61.9351 | 62.42 | 63.4156 | 64.131 | 64.5191 | 64.9435 | 65.332 | 66.034 | 66.9053 | 66.8444 | 66.8444 | 66.8444 | 66.8444 | 66.8444 | 66.8444 | 66.8444 | 66.8444 | 66.8444 | 66.8444 | 66.8444 | 66.8444 | 66.8444 | 66.8444 | 66.8444 | 66.8444 | 85% | 26.4715 | 48.4739 | 62.7476 | 66.4824 | 66.2582 | 66.274 | 66.6569 | 67.6681 | 68.3445 | 69.0069 | 69.7818 | 70.4995 | 71.1965 | 71.2756 | 72.0892 | 71.4715 | 71.4715 | 71.4715 | 71.4715 | 71.4715 | 71.4715 | 71.4715 | 71.4715 | 71.4715 | 71.4715 | 71.4715 | 71.4715 | 71.4715 | 71.4715 | 71.4715 | 71.4715
80% | 31.0095 | 40.9297 | 54.3368 | 57.9862 | 57.8799 | 57.876 | 58.2919 | 58.7483 | 59.6853 | 60.3586 | 60.7239 | 61.1233 | 61.4889 | 62.1496 | 62.9697 | 62.9123 | 62.9123 | 62.9123 | 62.9123 | 62.9123 | 62.9123 | 62.9123 | 62.9123 | 62.9123 | 62.9123 | 62.9123 | 62.9123 | 62.9123 | 62.9123 | 62.9123 | 62.9123 | 80% | 34.0348 | 45.6225 | 59.0566 | 62.5716 | 62.3606 | 62.3755 | 62.7359 | 63.6876 | 64.3242 | 64.9477 | 65.677 | 66.3524 | 67.0085 | 67.0829 | 67.8487 | 67.2672 | 67.2672 | 67.2672 | 67.2672 | 67.2672 | 67.2672 | 67.2672 | 67.2672 | 67.2672 | 67.2672 | 67.2672 | 67.2672 | 67.2672 | 67.2672 | 67.2672 | 67.2672
75% | 72.9857 | 38.3716 | 50.9407 | 54.362 | 54.2624 | 54.2587 | 54.6486 | 55.0765 | 55.955 | 56.5862 | 56.9286 | 57.3031 | 57.6458 | 58.2653 | 59.0341 | 58.9803 | 58.9803 | 58.9803 | 58.9803 | 58.9803 | 58.9803 | 58.9803 | 58.9803 | 58.9803 | 58.9803 | 58.9803 | 58.9803 | 58.9803 | 58.9803 | 58.9803 | 58.9803 | 75% | 48.405 | 42.7711 | 55.3655 | 58.6609 | 58.4631 | 58.4771 | 58.8149 | 59.7071 | 60.3039 | 60.8885 | 61.5722 | 62.2054 | 62.8205 | 62.8902 | 63.6082 | 63.063 | 63.063 | 63.063 | 63.063 | 63.063 | 63.063 | 63.063 | 63.063 | 63.063 | 63.063 | 63.063 | 63.063 | 63.063 | 63.063 | 63.063 | 63.063
70% | 150.5094 | 35.8135 | 47.5447 | 50.7379 | 50.6449 | 50.6415 | 51.0054 | 51.4047 | 52.2246 | 52.8138 | 53.1334 | 53.4829 | 53.8028 | 54.3809 | 55.0984 | 55.0483 | 55.0483 | 55.0483 | 55.0483 | 55.0483 | 55.0483 | 55.0483 | 55.0483 | 55.0483 | 55.0483 | 55.0483 | 55.0483 | 55.0483 | 55.0483 | 55.0483 | 55.0483 | 70% | 76.3892 | 39.9197 | 51.6745 | 54.7502 | 54.5656 | 54.5786 | 54.8939 | 55.7266 | 56.2837 | 56.8292 | 57.4674 | 58.0584 | 58.6324 | 58.6976 | 59.3676 | 58.8588 | 58.8588 | 58.8588 | 58.8588 | 58.8588 | 58.8588 | 58.8588 | 58.8588 | 58.8588 | 58.8588 | 58.8588 | 58.8588 | 58.8588 | 58.8588 | 58.8588 | 58.8588
65% | 359.6342 | 33.2554 | 44.1486 | 47.1138 | 47.0274 | 47.0242 | 47.3621 | 47.733 | 48.4943 | 49.0414 | 49.3381 | 49.6627 | 49.9597 | 50.4966 | 51.1628 | 51.1163 | 51.1163 | 51.1163 | 51.1163 | 51.1163 | 51.1163 | 51.1163 | 51.1163 | 51.1163 | 51.1163 | 51.1163 | 51.1163 | 51.1163 | 51.1163 | 51.1163 | 51.1163 | 65% | 114.2056 | 37.0683 | 47.9835 | 50.8395 | 50.668 | 50.6801 | 50.9729 | 51.7462 | 52.2634 | 52.77 | 53.3626 | 53.9114 | 54.4444 | 54.5049 | 55.1271 | 54.6546 | 54.6546 | 54.6546 | 54.6546 | 54.6546 | 54.6546 | 54.6546 | 54.6546 | 54.6546 | 54.6546 | 54.6546 | 54.6546 | 54.6546 | 54.6546 | 54.6546 | 54.6546
60% | 689.7717 | 30.6973 | 40.7526 | 43.4896 | 43.4099 | 43.407 | 43.7189 | 44.0612 | 44.764 | 45.269 | 45.5429 | 45.8424 | 46.1167 | 46.6122 | 47.2272 | 47.1843 | 47.1843 | 47.1843 | 47.1843 | 47.1843 | 47.1843 | 47.1843 | 47.1843 | 47.1843 | 47.1843 | 47.1843 | 47.1843 | 47.1843 | 47.1843 | 47.1843 | 47.1843 | 60% | 178.1154 | 34.2169 | 44.2924 | 46.9287 | 46.7705 | 46.7817 | 47.0519 | 47.7657 | 48.2431 | 48.7108 | 49.2577 | 49.7643 | 50.2564 | 50.3122 | 50.8865 | 50.4504 | 50.4504 | 50.4504 | 50.4504 | 50.4504 | 50.4504 | 50.4504 | 50.4504 | 50.4504 | 50.4504 | 50.4504 | 50.4504 | 50.4504 | 50.4504 | 50.4504 | 50.4504
55% | 1095.5419 | 28.1392 | 37.3565 | 39.8655 | 39.7924 | 39.7897 | 40.0757 | 40.3894 | 41.0336 | 41.4965 | 41.7476 | 42.0222 | 42.2736 | 42.7279 | 43.2916 | 43.2522 | 43.2522 | 43.2522 | 43.2522 | 43.2522 | 43.2522 | 43.2522 | 43.2522 | 43.2522 | 43.2522 | 43.2522 | 43.2522 | 43.2522 | 43.2522 | 43.2522 | 43.2522 | 55% | 311.6074 | 31.3655 | 40.6014 | 43.018 | 42.8729 | 42.8832 | 43.131 | 43.7852 | 44.2229 | 44.6515 | 45.1529 | 45.6173 | 46.0683 | 46.1195 | 46.646 | 46.2462 | 46.2462 | 46.2462 | 46.2462 | 46.2462 | 46.2462 | 46.2462 | 46.2462 | 46.2462 | 46.2462 | 46.2462 | 46.2462 | 46.2462 | 46.2462 | 46.2462 | 46.2462
50% | 1666.1918 | 25.581 | 33.9605 | 36.2413 | 36.1749 | 36.1725 | 36.4324 | 36.7177 | 37.3033 | 37.7241 | 37.9524 | 38.202 | 38.4306 | 38.8435 | 39.356 | 39.3202 | 39.3202 | 39.3202 | 39.3202 | 39.3202 | 39.3202 | 39.3202 | 39.3202 | 39.3202 | 39.3202 | 39.3202 | 39.3202 | 39.3202 | 39.3202 | 39.3202 | 39.3202 | 50% | 636.0723 | 28.5141 | 36.9103 | 39.1073 | 38.9754 | 38.9847 | 39.21 | 39.8047 | 40.2026 | 40.5923 | 41.0481 | 41.4703 | 41.8803 | 41.9268 | 42.4054 | 42.042 | 42.042 | 42.042 | 42.042 | 42.042 | 42.042 | 42.042 | 42.042 | 42.042 | 42.042 | 42.042 | 42.042 | 42.042 | 42.042 | 42.042 | 42.042
45% | 2506.0947 | 23.0229 | 30.5644 | 32.6172 | 32.5574 | 32.5552 | 32.7892 | 33.0459 | 33.573 | 33.9517 | 34.1572 | 34.3818 | 34.5875 | 34.9592 | 35.4204 | 35.3882 | 35.3882 | 35.3882 | 35.3882 | 35.3882 | 35.3882 | 35.3882 | 35.3882 | 35.3882 | 35.3882 | 35.3882 | 35.3882 | 35.3882 | 35.3882 | 35.3882 | 35.3882 | 45% | 1179.4944 | 25.6627 | 33.2193 | 35.1965 | 35.0779 | 35.0862 | 35.289 | 35.8243 | 36.1824 | 36.5331 | 36.9433 | 37.3233 | 37.6923 | 37.7341 | 38.1649 | 37.8378 | 37.8378 | 37.8378 | 37.8378 | 37.8378 | 37.8378 | 37.8378 | 37.8378 | 37.8378 | 37.8378 | 37.8378 | 37.8378 | 37.8378 | 37.8378 | 37.8378 | 37.8378
40% | 3164.4787 | 20.4648 | 27.1684 | 28.9931 | 28.9399 | 28.938 | 29.1459 | 29.3741 | 29.8426 | 30.1793 | 30.3619 | 30.5616 | 30.7444 | 31.0748 | 31.4848 | 31.4562 | 31.4562 | 31.4562 | 31.4562 | 31.4562 | 31.4562 | 31.4562 | 31.4562 | 31.4562 | 31.4562 | 31.4562 | 31.4562 | 31.4562 | 31.4562 | 31.4562 | 31.4562 | 40% | 1808.3816 | 22.8113 | 29.5283 | 31.2858 | 31.1803 | 31.1878 | 31.368 | 31.8438 | 32.1621 | 32.4738 | 32.8385 | 33.1762 | 33.5042 | 33.5415 | 33.9244 | 33.6336 | 33.6336 | 33.6336 | 33.6336 | 33.6336 | 33.6336 | 33.6336 | 33.6336 | 33.6336 | 33.6336 | 33.6336 | 33.6336 | 33.6336 | 33.6336 | 33.6336 | 33.6336
35% | 3551.3408 | 17.9067 | 23.7723 | 25.3689 | 25.3224 | 25.3207 | 25.5027 | 25.7024 | 26.1123 | 26.4069 | 26.5667 | 26.7414 | 26.9014 | 27.1905 | 27.5492 | 27.5241 | 27.5241 | 27.5241 | 27.5241 | 27.5241 | 27.5241 | 27.5241 | 27.5241 | 27.5241 | 27.5241 | 27.5241 | 27.5241 | 27.5241 | 27.5241 | 27.5241 | 27.5241 | 35% | 2779.1293 | 19.9599 | 25.8372 | 27.3751 | 27.2828 | 27.2893 | 27.447 | 27.8633 | 28.1418 | 28.4146 | 28.7337 | 29.0292 | 29.3162 | 29.3488 | 29.6838 | 29.4294 | 29.4294 | 29.4294 | 29.4294 | 29.4294 | 29.4294 | 29.4294 | 29.4294 | 29.4294 | 29.4294 | 29.4294 | 29.4294 | 29.4294 | 29.4294 | 29.4294 | 29.4294
30% | 3758.953 | 15.3486 | 20.3763 | 21.7448 | 21.705 | 21.7035 | 21.8595 | 22.0306 | 22.382 | 22.6345 | 22.7714 | 22.9212 | 23.0583 | 23.3061 | 23.6136 | 23.5921 | 23.5921 | 23.5921 | 23.5921 | 23.5921 | 23.5921 | 23.5921 | 23.5921 | 23.5921 | 23.5921 | 23.5921 | 23.5921 | 23.5921 | 23.5921 | 23.5921 | 23.5921 | 30% | 3814.165 | 17.1085 | 22.1462 | 23.4644 | 23.3852 | 23.3908 | 23.526 | 23.8828 | 24.1216 | 24.3554 | 24.6289 | 24.8822 | 25.1282 | 25.1561 | 25.4433 | 25.2252 | 25.2252 | 25.2252 | 25.2252 | 25.2252 | 25.2252 | 25.2252 | 25.2252 | 25.2252 | 25.2252 | 25.2252 | 25.2252 | 25.2252 | 25.2252 | 25.2252 | 25.2252
25% | 3926.4798 | 12.7905 | 16.9802 | 18.1207 | 18.0875 | 18.0862 | 18.2162 | 18.3588 | 18.6517 | 18.8621 | 18.9762 | 19.101 | 19.2153 | 19.4218 | 19.678 | 19.6601 | 19.6601 | 19.6601 | 19.6601 | 19.6601 | 19.6601 | 19.6601 | 19.6601 | 19.6601 | 19.6601 | 19.6601 | 19.6601 | 19.6601 | 19.6601 | 19.6601 | 19.6601 | 25% | 4166.9923 | 14.257 | 18.4552 | 19.5536 | 19.4877 | 19.4924 | 19.605 | 19.9024 | 20.1013 | 20.2962 | 20.5241 | 20.7351 | 20.9402 | 20.9634 | 21.2027 | 21.021 | 21.021 | 21.021 | 21.021 | 21.021 | 21.021 | 21.021 | 21.021 | 21.021 | 21.021 | 21.021 | 21.021 | 21.021 | 21.021 | 21.021 | 21.021
20% | 4050.5177 | 10.2324 | 13.5842 | 14.4965 | 14.47 | 14.469 | 14.573 | 14.6871 | 14.9213 | 15.0897 | 15.181 | 15.2808 | 15.3722 | 15.5374 | 15.7424 | 15.7281 | 15.7281 | 15.7281 | 15.7281 | 15.7281 | 15.7281 | 15.7281 | 15.7281 | 15.7281 | 15.7281 | 15.7281 | 15.7281 | 15.7281 | 15.7281 | 15.7281 | 15.7281 | 20% | 4282.7105 | 11.4056 | 14.7641 | 15.6429 | 15.5902 | 15.5939 | 15.684 | 15.9219 | 16.081 | 16.2369 | 16.4192 | 16.5881 | 16.7521 | 16.7707 | 16.9622 | 16.8168 | 16.8168 | 16.8168 | 16.8168 | 16.8168 | 16.8168 | 16.8168 | 16.8168 | 16.8168 | 16.8168 | 16.8168 | 16.8168 | 16.8168 | 16.8168 | 16.8168 | 16.8168
15% | 4152.622 | 7.6743 | 10.1881 | 10.8724 | 10.8525 | 10.8517 | 10.9297 | 11.0153 | 11.191 | 11.3172 | 11.3857 | 11.4606 | 11.5292 | 11.6531 | 11.8068 | 11.7961 | 11.7961 | 11.7961 | 11.7961 | 11.7961 | 11.7961 | 11.7961 | 11.7961 | 11.7961 | 11.7961 | 11.7961 | 11.7961 | 11.7961 | 11.7961 | 11.7961 | 11.7961 | 15% | 4364.7722 | 8.5542 | 11.0731 | 11.7322 | 11.6926 | 11.6954 | 11.763 | 11.9414 | 12.0608 | 12.1777 | 12.3144 | 12.4411 | 12.5641 | 12.578 | 12.7216 | 12.6126 | 12.6126 | 12.6126 | 12.6126 | 12.6126 | 12.6126 | 12.6126 | 12.6126 | 12.6126 | 12.6126 | 12.6126 | 12.6126 | 12.6126 | 12.6126 | 12.6126 | 12.6126
10% | 4248.2976 | 5.1162 | 6.7921 | 7.2483 | 7.235 | 7.2345 | 7.2865 | 7.3435 | 7.4607 | 7.5448 | 7.5905 | 7.6404 | 7.6861 | 7.7687 | 7.8712 | 7.864 | 7.864 | 7.864 | 7.864 | 7.864 | 7.864 | 7.864 | 7.864 | 7.864 | 7.864 | 7.864 | 7.864 | 7.864 | 7.864 | 7.864 | 7.864 | 10% | 4391.6218 | 5.7028 | 7.3821 | 7.8215 | 7.7951 | 7.7969 | 7.842 | 7.9609 | 8.0405 | 8.1185 | 8.2096 | 8.2941 | 8.3761 | 8.3854 | 8.4811 | 8.4084 | 8.4084 | 8.4084 | 8.4084 | 8.4084 | 8.4084 | 8.4084 | 8.4084 | 8.4084 | 8.4084 | 8.4084 | 8.4084 | 8.4084 | 8.4084 | 8.4084 | 8.4084
5% | 4361.7469 | 2.5581 | 3.396 | 3.6241 | 3.6175 | 3.6172 | 3.6432 | 3.6718 | 3.7303 | 3.7724 | 3.7952 | 3.8202 | 3.8431 | 3.8844 | 3.9356 | 3.932 | 3.932 | 3.932 | 3.932 | 3.932 | 3.932 | 3.932 | 3.932 | 3.932 | 3.932 | 3.932 | 3.932 | 3.932 | 3.932 | 3.932 | 3.932 | 5% | 4391.6218 | 2.8514 | 3.691 | 3.9107 | 3.8975 | 3.8985 | 3.921 | 3.9805 | 4.0203 | 4.0592 | 4.1048 | 4.147 | 4.188 | 4.1927 | 4.2405 | 4.2042 | 4.2042 | 4.2042 | 4.2042 | 4.2042 | 4.2042 | 4.2042 | 4.2042 | 4.2042 | 4.2042 | 4.2042 | 4.2042 | 4.2042 | 4.2042 | 4.2042 | 4.2042
9.992e-14% | 4391.6218 | 5.1121e-14 | 6.7867e-14 | 7.2425e-14 | 7.2292e-14 | 7.2287e-14 | 7.2807e-14 | 7.3377e-14 | 7.4547e-14 | 7.5388e-14 | 7.5844e-14 | 7.6343e-14 | 7.68e-14 | 7.7625e-14 | 7.8649e-14 | 7.8578e-14 | 7.8578e-14 | 7.8578e-14 | 7.8578e-14 | 7.8578e-14 | 7.8578e-14 | 7.8578e-14 | 7.8578e-14 | 7.8578e-14 | 7.8578e-14 | 7.8578e-14 | 7.8578e-14 | 7.8578e-14 | 7.8578e-14 | 7.8578e-14 | 7.8578e-14 | 9.992e-14% | 4391.6218 | 5.6983e-14 | 7.3762e-14 | 7.8152e-14 | 7.7889e-14 | 7.7907e-14 | 7.8357e-14 | 7.9546e-14 | 8.0341e-14 | 8.112e-14 | 8.2031e-14 | 8.2874e-14 | 8.3694e-14 | 8.3787e-14 | 8.4743e-14 | 8.4017e-14 | 8.4017e-14 | 8.4017e-14 | 8.4017e-14 | 8.4017e-14 | 8.4017e-14 | 8.4017e-14 | 8.4017e-14 | 8.4017e-14 | 8.4017e-14 | 8.4017e-14 | 8.4017e-14 | 8.4017e-14 | 8.4017e-14 | 8.4017e-14 | 8.4017e-14
Option 4
Winter Season | [31 empty] | Winter Season
P50 | [31 empty] | P10
% of MD | Winter - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Winter - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 45.0311 | 62.4376 | 66.9594 | 53.2285 | 53.8267 | 54.8603 | 57.2146 | 58.7888 | 60.7849 | 61.8199 | 62.7291 | 61.0455 | 63.0138 | 66.1095 | 63.7564 | 63.7564 | 63.7564 | 63.7564 | 63.7564 | 63.7564 | 63.7564 | 63.7564 | 63.7564 | 63.7564 | 63.7564 | 63.7564 | 63.7564 | 63.7564 | 63.7564 | 63.7564 | 100% | 0 | 48.1978 | 65.3847 | 70.0831 | 56.3084 | 56.767 | 57.7781 | 60.1693 | 61.4727 | 63.9597 | 71.5243 | 65.2829 | 64.0605 | 65.7054 | 69.3053 | 66.8648 | 66.8648 | 66.8648 | 66.8648 | 66.8648 | 66.8648 | 66.8648 | 66.8648 | 66.8648 | 66.8648 | 66.8648 | 66.8648 | 66.8648 | 66.8648 | 66.8648 | 66.8648
99% | 1.486 | 44.5808 | 61.8132 | 66.2898 | 52.6962 | 53.2885 | 54.3117 | 56.6425 | 58.2009 | 60.177 | 61.2017 | 62.1019 | 60.4351 | 62.3837 | 65.4484 | 63.1189 | 63.1189 | 63.1189 | 63.1189 | 63.1189 | 63.1189 | 63.1189 | 63.1189 | 63.1189 | 63.1189 | 63.1189 | 63.1189 | 63.1189 | 63.1189 | 63.1189 | 63.1189 | 99% | 1.486 | 47.7158 | 64.7309 | 69.3823 | 55.7453 | 56.1993 | 57.2003 | 59.5676 | 60.8579 | 63.3201 | 70.8091 | 64.6301 | 63.4199 | 65.0483 | 68.6122 | 66.1962 | 66.1962 | 66.1962 | 66.1962 | 66.1962 | 66.1962 | 66.1962 | 66.1962 | 66.1962 | 66.1962 | 66.1962 | 66.1962 | 66.1962 | 66.1962 | 66.1962 | 66.1962
98% | 3.2692 | 44.1305 | 61.1889 | 65.6202 | 52.1639 | 52.7502 | 53.7631 | 56.0704 | 57.613 | 59.5692 | 60.5835 | 61.4746 | 59.8246 | 61.7536 | 64.7873 | 62.4813 | 62.4813 | 62.4813 | 62.4813 | 62.4813 | 62.4813 | 62.4813 | 62.4813 | 62.4813 | 62.4813 | 62.4813 | 62.4813 | 62.4813 | 62.4813 | 62.4813 | 62.4813 | 98% | 3.2692 | 47.2338 | 64.0771 | 68.6815 | 55.1822 | 55.6316 | 56.6225 | 58.9659 | 60.2432 | 62.6805 | 70.0938 | 63.9773 | 62.7793 | 64.3913 | 67.9192 | 65.5275 | 65.5275 | 65.5275 | 65.5275 | 65.5275 | 65.5275 | 65.5275 | 65.5275 | 65.5275 | 65.5275 | 65.5275 | 65.5275 | 65.5275 | 65.5275 | 65.5275 | 65.5275
97% | 6.8356 | 43.6802 | 60.5645 | 64.9506 | 51.6316 | 52.2119 | 53.2145 | 55.4982 | 57.0251 | 58.9613 | 59.9653 | 60.8473 | 59.2142 | 61.1234 | 64.1262 | 61.8437 | 61.8437 | 61.8437 | 61.8437 | 61.8437 | 61.8437 | 61.8437 | 61.8437 | 61.8437 | 61.8437 | 61.8437 | 61.8437 | 61.8437 | 61.8437 | 61.8437 | 61.8437 | 97% | 6.8356 | 46.7518 | 63.4232 | 67.9806 | 54.6191 | 55.064 | 56.0447 | 58.3642 | 59.6285 | 62.0409 | 69.3786 | 63.3244 | 62.1387 | 63.7342 | 67.2261 | 64.8589 | 64.8589 | 64.8589 | 64.8589 | 64.8589 | 64.8589 | 64.8589 | 64.8589 | 64.8589 | 64.8589 | 64.8589 | 64.8589 | 64.8589 | 64.8589 | 64.8589 | 64.8589
95% | 17.5347 | 42.7796 | 59.3157 | 63.6114 | 50.567 | 51.1354 | 52.1173 | 54.3539 | 55.8493 | 57.7457 | 58.7289 | 59.5927 | 57.9933 | 59.8632 | 62.804 | 60.5686 | 60.5686 | 60.5686 | 60.5686 | 60.5686 | 60.5686 | 60.5686 | 60.5686 | 60.5686 | 60.5686 | 60.5686 | 60.5686 | 60.5686 | 60.5686 | 60.5686 | 60.5686 | 95% | 17.5347 | 45.7879 | 62.1155 | 66.579 | 53.493 | 53.9286 | 54.8892 | 57.1608 | 58.399 | 60.7618 | 67.9481 | 62.0188 | 60.8575 | 62.4201 | 65.84 | 63.5216 | 63.5216 | 63.5216 | 63.5216 | 63.5216 | 63.5216 | 63.5216 | 63.5216 | 63.5216 | 63.5216 | 63.5216 | 63.5216 | 63.5216 | 63.5216 | 63.5216 | 63.5216
90% | 78.7576 | 40.528 | 56.1939 | 60.2634 | 47.9056 | 48.4441 | 49.3743 | 51.4932 | 52.9099 | 54.7064 | 55.6379 | 56.4562 | 54.941 | 56.7125 | 59.4986 | 57.3808 | 57.3808 | 57.3808 | 57.3808 | 57.3808 | 57.3808 | 57.3808 | 57.3808 | 57.3808 | 57.3808 | 57.3808 | 57.3808 | 57.3808 | 57.3808 | 57.3808 | 57.3808 | 90% | 78.7576 | 43.378 | 58.8463 | 63.0748 | 50.6775 | 51.0903 | 52.0003 | 54.1523 | 55.3254 | 57.5638 | 64.3719 | 58.7546 | 57.6545 | 59.1348 | 62.3747 | 60.1783 | 60.1783 | 60.1783 | 60.1783 | 60.1783 | 60.1783 | 60.1783 | 60.1783 | 60.1783 | 60.1783 | 60.1783 | 60.1783 | 60.1783 | 60.1783 | 60.1783 | 60.1783
85% | 236.8672 | 38.2764 | 53.072 | 56.9155 | 45.2442 | 45.7527 | 46.6313 | 48.6325 | 49.9704 | 51.6672 | 52.5469 | 53.3198 | 51.8887 | 53.5618 | 56.1931 | 54.193 | 54.193 | 54.193 | 54.193 | 54.193 | 54.193 | 54.193 | 54.193 | 54.193 | 54.193 | 54.193 | 54.193 | 54.193 | 54.193 | 54.193 | 54.193 | 85% | 236.8672 | 40.9681 | 55.577 | 59.5707 | 47.8621 | 48.2519 | 49.1114 | 51.1439 | 52.2518 | 54.3658 | 60.7957 | 55.4905 | 54.4515 | 55.8496 | 58.9095 | 56.8351 | 56.8351 | 56.8351 | 56.8351 | 56.8351 | 56.8351 | 56.8351 | 56.8351 | 56.8351 | 56.8351 | 56.8351 | 56.8351 | 56.8351 | 56.8351 | 56.8351 | 56.8351
80% | 497.5104 | 36.0249 | 49.9501 | 53.5675 | 42.5828 | 43.0614 | 43.8882 | 45.7717 | 47.031 | 48.6279 | 49.456 | 50.1833 | 48.8364 | 50.4111 | 52.8876 | 51.0051 | 51.0051 | 51.0051 | 51.0051 | 51.0051 | 51.0051 | 51.0051 | 51.0051 | 51.0051 | 51.0051 | 51.0051 | 51.0051 | 51.0051 | 51.0051 | 51.0051 | 51.0051 | 80% | 497.5104 | 38.5582 | 52.3078 | 56.0665 | 45.0467 | 45.4136 | 46.2225 | 48.1354 | 49.1781 | 51.1678 | 57.2195 | 52.2263 | 51.2484 | 52.5643 | 55.4442 | 53.4919 | 53.4919 | 53.4919 | 53.4919 | 53.4919 | 53.4919 | 53.4919 | 53.4919 | 53.4919 | 53.4919 | 53.4919 | 53.4919 | 53.4919 | 53.4919 | 53.4919 | 53.4919
75% | 803.6248 | 33.7733 | 46.8282 | 50.2195 | 39.9214 | 40.37 | 41.1452 | 42.911 | 44.0916 | 45.5887 | 46.365 | 47.0469 | 45.7842 | 47.2604 | 49.5821 | 47.8173 | 47.8173 | 47.8173 | 47.8173 | 47.8173 | 47.8173 | 47.8173 | 47.8173 | 47.8173 | 47.8173 | 47.8173 | 47.8173 | 47.8173 | 47.8173 | 47.8173 | 47.8173 | 75% | 803.6248 | 36.1483 | 49.0386 | 52.5623 | 42.2313 | 42.5752 | 43.3336 | 45.1269 | 46.1045 | 47.9698 | 53.6432 | 48.9622 | 48.0454 | 49.279 | 51.9789 | 50.1486 | 50.1486 | 50.1486 | 50.1486 | 50.1486 | 50.1486 | 50.1486 | 50.1486 | 50.1486 | 50.1486 | 50.1486 | 50.1486 | 50.1486 | 50.1486 | 50.1486 | 50.1486
70% | 1155.2107 | 31.5218 | 43.7063 | 46.8715 | 37.2599 | 37.6787 | 38.4022 | 40.0503 | 41.1521 | 42.5494 | 43.274 | 43.9104 | 42.7319 | 44.1097 | 46.2767 | 44.6295 | 44.6295 | 44.6295 | 44.6295 | 44.6295 | 44.6295 | 44.6295 | 44.6295 | 44.6295 | 44.6295 | 44.6295 | 44.6295 | 44.6295 | 44.6295 | 44.6295 | 44.6295 | 70% | 1155.2107 | 33.7384 | 45.7693 | 49.0582 | 39.4159 | 39.7369 | 40.4447 | 42.1185 | 43.0309 | 44.7718 | 50.067 | 45.6981 | 44.8424 | 45.9938 | 48.5137 | 46.8054 | 46.8054 | 46.8054 | 46.8054 | 46.8054 | 46.8054 | 46.8054 | 46.8054 | 46.8054 | 46.8054 | 46.8054 | 46.8054 | 46.8054 | 46.8054 | 46.8054 | 46.8054
65% | 1553.1596 | 29.2702 | 40.5844 | 43.5236 | 34.5985 | 34.9874 | 35.6592 | 37.1895 | 38.2127 | 39.5102 | 40.183 | 40.7739 | 39.6796 | 40.959 | 42.9712 | 41.4417 | 41.4417 | 41.4417 | 41.4417 | 41.4417 | 41.4417 | 41.4417 | 41.4417 | 41.4417 | 41.4417 | 41.4417 | 41.4417 | 41.4417 | 41.4417 | 41.4417 | 41.4417 | 65% | 1553.1596 | 31.3286 | 42.5001 | 45.554 | 36.6004 | 36.8985 | 37.5558 | 39.11 | 39.9572 | 41.5738 | 46.4908 | 42.4339 | 41.6393 | 42.7085 | 45.0484 | 43.4621 | 43.4621 | 43.4621 | 43.4621 | 43.4621 | 43.4621 | 43.4621 | 43.4621 | 43.4621 | 43.4621 | 43.4621 | 43.4621 | 43.4621 | 43.4621 | 43.4621 | 43.4621
60% | 2026.2996 | 27.0187 | 37.4626 | 40.1756 | 31.9371 | 32.296 | 32.9162 | 34.3288 | 35.2733 | 36.4709 | 37.092 | 37.6375 | 36.6273 | 37.8083 | 39.6657 | 38.2539 | 38.2539 | 38.2539 | 38.2539 | 38.2539 | 38.2539 | 38.2539 | 38.2539 | 38.2539 | 38.2539 | 38.2539 | 38.2539 | 38.2539 | 38.2539 | 38.2539 | 38.2539 | 60% | 2026.2996 | 28.9187 | 39.2308 | 42.0499 | 33.785 | 34.0602 | 34.6669 | 36.1016 | 36.8836 | 38.3758 | 42.9146 | 39.1698 | 38.4363 | 39.4232 | 41.5832 | 40.1189 | 40.1189 | 40.1189 | 40.1189 | 40.1189 | 40.1189 | 40.1189 | 40.1189 | 40.1189 | 40.1189 | 40.1189 | 40.1189 | 40.1189 | 40.1189 | 40.1189 | 40.1189
55% | 2598.4068 | 24.7671 | 34.3407 | 36.8276 | 29.2757 | 29.6047 | 30.1732 | 31.4681 | 32.3338 | 33.4317 | 34.001 | 34.501 | 33.575 | 34.6576 | 36.3602 | 35.066 | 35.066 | 35.066 | 35.066 | 35.066 | 35.066 | 35.066 | 35.066 | 35.066 | 35.066 | 35.066 | 35.066 | 35.066 | 35.066 | 35.066 | 35.066 | 55% | 2598.4068 | 26.5088 | 35.9616 | 38.5457 | 30.9696 | 31.2218 | 31.778 | 33.0931 | 33.81 | 35.1779 | 39.3384 | 35.9056 | 35.2333 | 36.138 | 38.1179 | 36.7757 | 36.7757 | 36.7757 | 36.7757 | 36.7757 | 36.7757 | 36.7757 | 36.7757 | 36.7757 | 36.7757 | 36.7757 | 36.7757 | 36.7757 | 36.7757 | 36.7757 | 36.7757
50% | 3233.5201 | 22.5156 | 31.2188 | 33.4797 | 26.6142 | 26.9134 | 27.4302 | 28.6073 | 29.3944 | 30.3924 | 30.91 | 31.3646 | 30.5228 | 31.5069 | 33.0548 | 31.8782 | 31.8782 | 31.8782 | 31.8782 | 31.8782 | 31.8782 | 31.8782 | 31.8782 | 31.8782 | 31.8782 | 31.8782 | 31.8782 | 31.8782 | 31.8782 | 31.8782 | 31.8782 | 50% | 3233.5201 | 24.0989 | 32.6924 | 35.0416 | 28.1542 | 28.3835 | 28.889 | 30.0846 | 30.7363 | 31.9799 | 35.7622 | 32.6415 | 32.0303 | 32.8527 | 34.6526 | 33.4324 | 33.4324 | 33.4324 | 33.4324 | 33.4324 | 33.4324 | 33.4324 | 33.4324 | 33.4324 | 33.4324 | 33.4324 | 33.4324 | 33.4324 | 33.4324 | 33.4324 | 33.4324
45% | 3775.313 | 20.264 | 28.0969 | 30.1317 | 23.9528 | 24.222 | 24.6871 | 25.7466 | 26.4549 | 27.3532 | 27.819 | 28.2281 | 27.4705 | 28.3562 | 29.7493 | 28.6904 | 28.6904 | 28.6904 | 28.6904 | 28.6904 | 28.6904 | 28.6904 | 28.6904 | 28.6904 | 28.6904 | 28.6904 | 28.6904 | 28.6904 | 28.6904 | 28.6904 | 28.6904 | 45% | 3775.313 | 21.689 | 29.4231 | 31.5374 | 25.3388 | 25.5451 | 26.0001 | 27.0762 | 27.6627 | 28.7819 | 32.1859 | 29.3773 | 28.8272 | 29.5674 | 31.1874 | 30.0892 | 30.0892 | 30.0892 | 30.0892 | 30.0892 | 30.0892 | 30.0892 | 30.0892 | 30.0892 | 30.0892 | 30.0892 | 30.0892 | 30.0892 | 30.0892 | 30.0892 | 30.0892
40% | 4072.8088 | 18.0124 | 24.975 | 26.7837 | 21.2914 | 21.5307 | 21.9441 | 22.8859 | 23.5155 | 24.314 | 24.728 | 25.0917 | 24.4182 | 25.2055 | 26.4438 | 25.5026 | 25.5026 | 25.5026 | 25.5026 | 25.5026 | 25.5026 | 25.5026 | 25.5026 | 25.5026 | 25.5026 | 25.5026 | 25.5026 | 25.5026 | 25.5026 | 25.5026 | 25.5026 | 40% | 4072.8088 | 19.2791 | 26.1539 | 28.0332 | 22.5234 | 22.7068 | 23.1112 | 24.0677 | 24.5891 | 25.5839 | 28.6097 | 26.1132 | 25.6242 | 26.2822 | 27.7221 | 26.7459 | 26.7459 | 26.7459 | 26.7459 | 26.7459 | 26.7459 | 26.7459 | 26.7459 | 26.7459 | 26.7459 | 26.7459 | 26.7459 | 26.7459 | 26.7459 | 26.7459 | 26.7459
35% | 4198.821 | 15.7609 | 21.8532 | 23.4358 | 18.63 | 18.8394 | 19.2011 | 20.0251 | 20.5761 | 21.2747 | 21.637 | 21.9552 | 21.3659 | 22.0548 | 23.1383 | 22.3147 | 22.3147 | 22.3147 | 22.3147 | 22.3147 | 22.3147 | 22.3147 | 22.3147 | 22.3147 | 22.3147 | 22.3147 | 22.3147 | 22.3147 | 22.3147 | 22.3147 | 22.3147 | 35% | 4198.821 | 16.8692 | 22.8847 | 24.5291 | 19.7079 | 19.8684 | 20.2223 | 21.0592 | 21.5154 | 22.3859 | 25.0335 | 22.849 | 22.4212 | 22.9969 | 24.2568 | 23.4027 | 23.4027 | 23.4027 | 23.4027 | 23.4027 | 23.4027 | 23.4027 | 23.4027 | 23.4027 | 23.4027 | 23.4027 | 23.4027 | 23.4027 | 23.4027 | 23.4027 | 23.4027
30% | 4271.3374 | 13.5093 | 18.7313 | 20.0878 | 15.9685 | 16.148 | 16.4581 | 17.1644 | 17.6366 | 18.2355 | 18.546 | 18.8187 | 18.3137 | 18.9042 | 19.8329 | 19.1269 | 19.1269 | 19.1269 | 19.1269 | 19.1269 | 19.1269 | 19.1269 | 19.1269 | 19.1269 | 19.1269 | 19.1269 | 19.1269 | 19.1269 | 19.1269 | 19.1269 | 19.1269 | 30% | 4271.3374 | 14.4593 | 19.6154 | 21.0249 | 16.8925 | 17.0301 | 17.3334 | 18.0508 | 18.4418 | 19.1879 | 21.4573 | 19.5849 | 19.2182 | 19.7116 | 20.7916 | 20.0594 | 20.0594 | 20.0594 | 20.0594 | 20.0594 | 20.0594 | 20.0594 | 20.0594 | 20.0594 | 20.0594 | 20.0594 | 20.0594 | 20.0594 | 20.0594 | 20.0594 | 20.0594
25% | 4321.8611 | 11.2578 | 15.6094 | 16.7398 | 13.3071 | 13.4567 | 13.7151 | 14.3037 | 14.6972 | 15.1962 | 15.455 | 15.6823 | 15.2614 | 15.7535 | 16.5274 | 15.9391 | 15.9391 | 15.9391 | 15.9391 | 15.9391 | 15.9391 | 15.9391 | 15.9391 | 15.9391 | 15.9391 | 15.9391 | 15.9391 | 15.9391 | 15.9391 | 15.9391 | 15.9391 | 25% | 4321.8611 | 12.0494 | 16.3462 | 17.5208 | 14.0771 | 14.1917 | 14.4445 | 15.0423 | 15.3682 | 15.9899 | 17.8811 | 16.3207 | 16.0151 | 16.4263 | 17.3263 | 16.7162 | 16.7162 | 16.7162 | 16.7162 | 16.7162 | 16.7162 | 16.7162 | 16.7162 | 16.7162 | 16.7162 | 16.7162 | 16.7162 | 16.7162 | 16.7162 | 16.7162 | 16.7162
20% | 4353.067 | 9.0062 | 12.4875 | 13.3919 | 10.6457 | 10.7653 | 10.9721 | 11.4429 | 11.7578 | 12.157 | 12.364 | 12.5458 | 12.2091 | 12.6028 | 13.2219 | 12.7513 | 12.7513 | 12.7513 | 12.7513 | 12.7513 | 12.7513 | 12.7513 | 12.7513 | 12.7513 | 12.7513 | 12.7513 | 12.7513 | 12.7513 | 12.7513 | 12.7513 | 12.7513 | 20% | 4353.067 | 9.6396 | 13.0769 | 14.0166 | 11.2617 | 11.3534 | 11.5556 | 12.0339 | 12.2945 | 12.7919 | 14.3049 | 13.0566 | 12.8121 | 13.1411 | 13.8611 | 13.373 | 13.373 | 13.373 | 13.373 | 13.373 | 13.373 | 13.373 | 13.373 | 13.373 | 13.373 | 13.373 | 13.373 | 13.373 | 13.373 | 13.373 | 13.373
15% | 4369.4129 | 6.7547 | 9.3656 | 10.0439 | 7.9843 | 8.074 | 8.229 | 8.5822 | 8.8183 | 9.1177 | 9.273 | 9.4094 | 9.1568 | 9.4521 | 9.9164 | 9.5635 | 9.5635 | 9.5635 | 9.5635 | 9.5635 | 9.5635 | 9.5635 | 9.5635 | 9.5635 | 9.5635 | 9.5635 | 9.5635 | 9.5635 | 9.5635 | 9.5635 | 9.5635 | 15% | 4369.4129 | 7.2297 | 9.8077 | 10.5125 | 8.4463 | 8.515 | 8.6667 | 9.0254 | 9.2209 | 9.594 | 10.7286 | 9.7924 | 9.6091 | 9.8558 | 10.3958 | 10.0297 | 10.0297 | 10.0297 | 10.0297 | 10.0297 | 10.0297 | 10.0297 | 10.0297 | 10.0297 | 10.0297 | 10.0297 | 10.0297 | 10.0297 | 10.0297 | 10.0297 | 10.0297
10% | 4378.6261 | 4.5031 | 6.2438 | 6.6959 | 5.3228 | 5.3827 | 5.486 | 5.7215 | 5.8789 | 6.0785 | 6.182 | 6.2729 | 6.1046 | 6.3014 | 6.611 | 6.3756 | 6.3756 | 6.3756 | 6.3756 | 6.3756 | 6.3756 | 6.3756 | 6.3756 | 6.3756 | 6.3756 | 6.3756 | 6.3756 | 6.3756 | 6.3756 | 6.3756 | 6.3756 | 10% | 4378.6261 | 4.8198 | 6.5385 | 7.0083 | 5.6308 | 5.6767 | 5.7778 | 6.0169 | 6.1473 | 6.396 | 7.1524 | 6.5283 | 6.4061 | 6.5705 | 6.9305 | 6.6865 | 6.6865 | 6.6865 | 6.6865 | 6.6865 | 6.6865 | 6.6865 | 6.6865 | 6.6865 | 6.6865 | 6.6865 | 6.6865 | 6.6865 | 6.6865 | 6.6865 | 6.6865
5% | 4391.7028 | 2.2516 | 3.1219 | 3.348 | 2.6614 | 2.6913 | 2.743 | 2.8607 | 2.9394 | 3.0392 | 3.091 | 3.1365 | 3.0523 | 3.1507 | 3.3055 | 3.1878 | 3.1878 | 3.1878 | 3.1878 | 3.1878 | 3.1878 | 3.1878 | 3.1878 | 3.1878 | 3.1878 | 3.1878 | 3.1878 | 3.1878 | 3.1878 | 3.1878 | 3.1878 | 5% | 4391.7028 | 2.4099 | 3.2692 | 3.5042 | 2.8154 | 2.8383 | 2.8889 | 3.0085 | 3.0736 | 3.198 | 3.5762 | 3.2641 | 3.203 | 3.2853 | 3.4653 | 3.3432 | 3.3432 | 3.3432 | 3.3432 | 3.3432 | 3.3432 | 3.3432 | 3.3432 | 3.3432 | 3.3432 | 3.3432 | 3.3432 | 3.3432 | 3.3432 | 3.3432 | 3.3432
9.992e-14% | 4391.7028 | 4.4995e-14 | 6.2388e-14 | 6.6906e-14 | 5.3186e-14 | 5.3784e-14 | 5.4816e-14 | 5.7169e-14 | 5.8742e-14 | 6.0736e-14 | 6.1771e-14 | 6.2679e-14 | 6.0997e-14 | 6.2963e-14 | 6.6057e-14 | 6.3705e-14 | 6.3705e-14 | 6.3705e-14 | 6.3705e-14 | 6.3705e-14 | 6.3705e-14 | 6.3705e-14 | 6.3705e-14 | 6.3705e-14 | 6.3705e-14 | 6.3705e-14 | 6.3705e-14 | 6.3705e-14 | 6.3705e-14 | 6.3705e-14 | 6.3705e-14 | 9.992e-14% | 4391.7028 | 4.8159e-14 | 6.5332e-14 | 7.0027e-14 | 5.6263e-14 | 5.6722e-14 | 5.7732e-14 | 6.0121e-14 | 6.1424e-14 | 6.3909e-14 | 7.1467e-14 | 6.5231e-14 | 6.4009e-14 | 6.5653e-14 | 6.925e-14 | 6.6811e-14 | 6.6811e-14 | 6.6811e-14 | 6.6811e-14 | 6.6811e-14 | 6.6811e-14 | 6.6811e-14 | 6.6811e-14 | 6.6811e-14 | 6.6811e-14 | 6.6811e-14 | 6.6811e-14 | 6.6811e-14 | 6.6811e-14 | 6.6811e-14 | 6.6811e-14
Summer Season | [31 empty] | Summer Season
P50 | [31 empty] | P10
% of MD | Summer - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Summer - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 51.1621 | 67.921 | 72.4827 | 57.8498 | 57.845 | 58.3648 | 58.9353 | 60.1066 | 60.9483 | 61.4048 | 61.9041 | 62.3611 | 63.187 | 64.2121 | 64.1404 | 64.1404 | 64.1404 | 64.1404 | 64.1404 | 64.1404 | 64.1404 | 64.1404 | 64.1404 | 64.1404 | 64.1404 | 64.1404 | 64.1404 | 64.1404 | 64.1404 | 64.1404 | 100% | 0 | 57.0282 | 73.8207 | 78.2145 | 63.4508 | 63.4694 | 63.9199 | 65.1095 | 65.9052 | 66.6846 | 67.5962 | 68.4406 | 69.2606 | 69.3537 | 70.3109 | 69.5841 | 69.5841 | 69.5841 | 69.5841 | 69.5841 | 69.5841 | 69.5841 | 69.5841 | 69.5841 | 69.5841 | 69.5841 | 69.5841 | 69.5841 | 69.5841 | 69.5841 | 69.5841
99% | 0 | 50.6505 | 67.2418 | 71.7579 | 57.2713 | 57.2665 | 57.7812 | 58.346 | 59.5055 | 60.3388 | 60.7908 | 61.285 | 61.7375 | 62.5551 | 63.5699 | 63.499 | 63.499 | 63.499 | 63.499 | 63.499 | 63.499 | 63.499 | 63.499 | 63.499 | 63.499 | 63.499 | 63.499 | 63.499 | 63.499 | 63.499 | 63.499 | 99% | 1.5127 | 56.4579 | 73.0825 | 77.4324 | 62.8163 | 62.8347 | 63.2807 | 64.4584 | 65.2462 | 66.0178 | 66.9203 | 67.7562 | 68.568 | 68.6601 | 69.6078 | 68.8882 | 68.8882 | 68.8882 | 68.8882 | 68.8882 | 68.8882 | 68.8882 | 68.8882 | 68.8882 | 68.8882 | 68.8882 | 68.8882 | 68.8882 | 68.8882 | 68.8882 | 68.8882
98% | 0 | 50.1389 | 66.5626 | 71.033 | 56.6928 | 56.6881 | 57.1975 | 57.7566 | 58.9045 | 59.7293 | 60.1767 | 60.666 | 61.1139 | 61.9233 | 62.9278 | 62.8576 | 62.8576 | 62.8576 | 62.8576 | 62.8576 | 62.8576 | 62.8576 | 62.8576 | 62.8576 | 62.8576 | 62.8576 | 62.8576 | 62.8576 | 62.8576 | 62.8576 | 62.8576 | 98% | 2.269 | 55.8876 | 72.3443 | 76.6503 | 62.1818 | 62.2 | 62.6415 | 63.8073 | 64.5871 | 65.3509 | 66.2443 | 67.0718 | 67.8754 | 67.9666 | 68.9047 | 68.1924 | 68.1924 | 68.1924 | 68.1924 | 68.1924 | 68.1924 | 68.1924 | 68.1924 | 68.1924 | 68.1924 | 68.1924 | 68.1924 | 68.1924 | 68.1924 | 68.1924 | 68.1924
97% | 0.37816 | 49.6272 | 65.8834 | 70.3082 | 56.1144 | 56.1096 | 56.6139 | 57.1673 | 58.3034 | 59.1198 | 59.5627 | 60.047 | 60.4903 | 61.2914 | 62.2857 | 62.2162 | 62.2162 | 62.2162 | 62.2162 | 62.2162 | 62.2162 | 62.2162 | 62.2162 | 62.2162 | 62.2162 | 62.2162 | 62.2162 | 62.2162 | 62.2162 | 62.2162 | 62.2162 | 97% | 3.7816 | 55.3173 | 71.6061 | 75.8681 | 61.5473 | 61.5653 | 62.0023 | 63.1562 | 63.9281 | 64.6841 | 65.5684 | 66.3873 | 67.1828 | 67.273 | 68.2016 | 67.4965 | 67.4965 | 67.4965 | 67.4965 | 67.4965 | 67.4965 | 67.4965 | 67.4965 | 67.4965 | 67.4965 | 67.4965 | 67.4965 | 67.4965 | 67.4965 | 67.4965 | 67.4965
95% | 2.269 | 48.604 | 64.5249 | 68.8586 | 54.9574 | 54.9527 | 55.4466 | 55.9886 | 57.1013 | 57.9008 | 58.3346 | 58.8089 | 59.2431 | 60.0277 | 61.0015 | 60.9334 | 60.9334 | 60.9334 | 60.9334 | 60.9334 | 60.9334 | 60.9334 | 60.9334 | 60.9334 | 60.9334 | 60.9334 | 60.9334 | 60.9334 | 60.9334 | 60.9334 | 60.9334 | 95% | 6.0506 | 54.1768 | 70.1297 | 74.3038 | 60.2783 | 60.296 | 60.7239 | 61.854 | 62.61 | 63.3504 | 64.2164 | 65.0185 | 65.7976 | 65.886 | 66.7953 | 66.1049 | 66.1049 | 66.1049 | 66.1049 | 66.1049 | 66.1049 | 66.1049 | 66.1049 | 66.1049 | 66.1049 | 66.1049 | 66.1049 | 66.1049 | 66.1049 | 66.1049 | 66.1049
90% | 5.6725 | 46.0459 | 61.1289 | 65.2344 | 52.0649 | 52.0605 | 52.5284 | 53.0418 | 54.0959 | 54.8534 | 55.2643 | 55.7137 | 56.125 | 56.8683 | 57.7909 | 57.7264 | 57.7264 | 57.7264 | 57.7264 | 57.7264 | 57.7264 | 57.7264 | 57.7264 | 57.7264 | 57.7264 | 57.7264 | 57.7264 | 57.7264 | 57.7264 | 57.7264 | 57.7264 | 90% | 16.2611 | 51.3254 | 66.4386 | 70.3931 | 57.1057 | 57.1225 | 57.5279 | 58.5985 | 59.3147 | 60.0162 | 60.8366 | 61.5965 | 62.3346 | 62.4183 | 63.2798 | 62.6257 | 62.6257 | 62.6257 | 62.6257 | 62.6257 | 62.6257 | 62.6257 | 62.6257 | 62.6257 | 62.6257 | 62.6257 | 62.6257 | 62.6257 | 62.6257 | 62.6257 | 62.6257
85% | 15.8829 | 43.4878 | 57.7328 | 61.6103 | 49.1724 | 49.1682 | 49.6101 | 50.095 | 51.0906 | 51.806 | 52.1941 | 52.6185 | 53.007 | 53.709 | 54.5803 | 54.5194 | 54.5194 | 54.5194 | 54.5194 | 54.5194 | 54.5194 | 54.5194 | 54.5194 | 54.5194 | 54.5194 | 54.5194 | 54.5194 | 54.5194 | 54.5194 | 54.5194 | 54.5194 | 85% | 26.4715 | 48.4739 | 62.7476 | 66.4824 | 53.9332 | 53.949 | 54.3319 | 55.3431 | 56.0195 | 56.6819 | 57.4568 | 58.1745 | 58.8715 | 58.9506 | 59.7642 | 59.1465 | 59.1465 | 59.1465 | 59.1465 | 59.1465 | 59.1465 | 59.1465 | 59.1465 | 59.1465 | 59.1465 | 59.1465 | 59.1465 | 59.1465 | 59.1465 | 59.1465 | 59.1465
80% | 31.0095 | 40.9297 | 54.3368 | 57.9862 | 46.2799 | 46.276 | 46.6919 | 47.1483 | 48.0853 | 48.7586 | 49.1239 | 49.5233 | 49.8889 | 50.5496 | 51.3697 | 51.3123 | 51.3123 | 51.3123 | 51.3123 | 51.3123 | 51.3123 | 51.3123 | 51.3123 | 51.3123 | 51.3123 | 51.3123 | 51.3123 | 51.3123 | 51.3123 | 51.3123 | 51.3123 | 80% | 34.0348 | 45.6225 | 59.0566 | 62.5716 | 50.7606 | 50.7755 | 51.1359 | 52.0876 | 52.7242 | 53.3477 | 54.077 | 54.7524 | 55.4085 | 55.4829 | 56.2487 | 55.6672 | 55.6672 | 55.6672 | 55.6672 | 55.6672 | 55.6672 | 55.6672 | 55.6672 | 55.6672 | 55.6672 | 55.6672 | 55.6672 | 55.6672 | 55.6672 | 55.6672 | 55.6672
75% | 72.9857 | 38.3716 | 50.9407 | 54.362 | 43.3874 | 43.3837 | 43.7736 | 44.2015 | 45.08 | 45.7112 | 46.0536 | 46.4281 | 46.7708 | 47.3903 | 48.1591 | 48.1053 | 48.1053 | 48.1053 | 48.1053 | 48.1053 | 48.1053 | 48.1053 | 48.1053 | 48.1053 | 48.1053 | 48.1053 | 48.1053 | 48.1053 | 48.1053 | 48.1053 | 48.1053 | 75% | 48.405 | 42.7711 | 55.3655 | 58.6609 | 47.5881 | 47.6021 | 47.9399 | 48.8321 | 49.4289 | 50.0135 | 50.6972 | 51.3304 | 51.9455 | 52.0152 | 52.7332 | 52.188 | 52.188 | 52.188 | 52.188 | 52.188 | 52.188 | 52.188 | 52.188 | 52.188 | 52.188 | 52.188 | 52.188 | 52.188 | 52.188 | 52.188 | 52.188
70% | 150.5094 | 35.8135 | 47.5447 | 50.7379 | 40.4949 | 40.4915 | 40.8554 | 41.2547 | 42.0746 | 42.6638 | 42.9834 | 43.3329 | 43.6528 | 44.2309 | 44.9484 | 44.8983 | 44.8983 | 44.8983 | 44.8983 | 44.8983 | 44.8983 | 44.8983 | 44.8983 | 44.8983 | 44.8983 | 44.8983 | 44.8983 | 44.8983 | 44.8983 | 44.8983 | 44.8983 | 70% | 76.3892 | 39.9197 | 51.6745 | 54.7502 | 44.4156 | 44.4286 | 44.7439 | 45.5766 | 46.1337 | 46.6792 | 47.3174 | 47.9084 | 48.4824 | 48.5476 | 49.2176 | 48.7088 | 48.7088 | 48.7088 | 48.7088 | 48.7088 | 48.7088 | 48.7088 | 48.7088 | 48.7088 | 48.7088 | 48.7088 | 48.7088 | 48.7088 | 48.7088 | 48.7088 | 48.7088
65% | 359.6342 | 33.2554 | 44.1486 | 47.1138 | 37.6024 | 37.5992 | 37.9371 | 38.308 | 39.0693 | 39.6164 | 39.9131 | 40.2377 | 40.5347 | 41.0716 | 41.7378 | 41.6913 | 41.6913 | 41.6913 | 41.6913 | 41.6913 | 41.6913 | 41.6913 | 41.6913 | 41.6913 | 41.6913 | 41.6913 | 41.6913 | 41.6913 | 41.6913 | 41.6913 | 41.6913 | 65% | 114.2056 | 37.0683 | 47.9835 | 50.8395 | 41.243 | 41.2551 | 41.5479 | 42.3212 | 42.8384 | 43.345 | 43.9376 | 44.4864 | 45.0194 | 45.0799 | 45.7021 | 45.2296 | 45.2296 | 45.2296 | 45.2296 | 45.2296 | 45.2296 | 45.2296 | 45.2296 | 45.2296 | 45.2296 | 45.2296 | 45.2296 | 45.2296 | 45.2296 | 45.2296 | 45.2296
60% | 689.7717 | 30.6973 | 40.7526 | 43.4896 | 34.7099 | 34.707 | 35.0189 | 35.3612 | 36.064 | 36.569 | 36.8429 | 37.1424 | 37.4167 | 37.9122 | 38.5272 | 38.4843 | 38.4843 | 38.4843 | 38.4843 | 38.4843 | 38.4843 | 38.4843 | 38.4843 | 38.4843 | 38.4843 | 38.4843 | 38.4843 | 38.4843 | 38.4843 | 38.4843 | 38.4843 | 60% | 178.1154 | 34.2169 | 44.2924 | 46.9287 | 38.0705 | 38.0817 | 38.3519 | 39.0657 | 39.5431 | 40.0108 | 40.5577 | 41.0643 | 41.5564 | 41.6122 | 42.1865 | 41.7504 | 41.7504 | 41.7504 | 41.7504 | 41.7504 | 41.7504 | 41.7504 | 41.7504 | 41.7504 | 41.7504 | 41.7504 | 41.7504 | 41.7504 | 41.7504 | 41.7504 | 41.7504
55% | 1095.5419 | 28.1392 | 37.3565 | 39.8655 | 31.8174 | 31.8147 | 32.1007 | 32.4144 | 33.0586 | 33.5215 | 33.7726 | 34.0472 | 34.2986 | 34.7529 | 35.3166 | 35.2772 | 35.2772 | 35.2772 | 35.2772 | 35.2772 | 35.2772 | 35.2772 | 35.2772 | 35.2772 | 35.2772 | 35.2772 | 35.2772 | 35.2772 | 35.2772 | 35.2772 | 35.2772 | 55% | 311.6074 | 31.3655 | 40.6014 | 43.018 | 34.8979 | 34.9082 | 35.156 | 35.8102 | 36.2479 | 36.6765 | 37.1779 | 37.6423 | 38.0933 | 38.1445 | 38.671 | 38.2712 | 38.2712 | 38.2712 | 38.2712 | 38.2712 | 38.2712 | 38.2712 | 38.2712 | 38.2712 | 38.2712 | 38.2712 | 38.2712 | 38.2712 | 38.2712 | 38.2712 | 38.2712
50% | 1666.1918 | 25.581 | 33.9605 | 36.2413 | 28.9249 | 28.9225 | 29.1824 | 29.4677 | 30.0533 | 30.4741 | 30.7024 | 30.952 | 31.1806 | 31.5935 | 32.106 | 32.0702 | 32.0702 | 32.0702 | 32.0702 | 32.0702 | 32.0702 | 32.0702 | 32.0702 | 32.0702 | 32.0702 | 32.0702 | 32.0702 | 32.0702 | 32.0702 | 32.0702 | 32.0702 | 50% | 636.0723 | 28.5141 | 36.9103 | 39.1073 | 31.7254 | 31.7347 | 31.96 | 32.5547 | 32.9526 | 33.3423 | 33.7981 | 34.2203 | 34.6303 | 34.6768 | 35.1554 | 34.792 | 34.792 | 34.792 | 34.792 | 34.792 | 34.792 | 34.792 | 34.792 | 34.792 | 34.792 | 34.792 | 34.792 | 34.792 | 34.792 | 34.792 | 34.792
45% | 2506.0947 | 23.0229 | 30.5644 | 32.6172 | 26.0324 | 26.0302 | 26.2642 | 26.5209 | 27.048 | 27.4267 | 27.6322 | 27.8568 | 28.0625 | 28.4342 | 28.8954 | 28.8632 | 28.8632 | 28.8632 | 28.8632 | 28.8632 | 28.8632 | 28.8632 | 28.8632 | 28.8632 | 28.8632 | 28.8632 | 28.8632 | 28.8632 | 28.8632 | 28.8632 | 28.8632 | 45% | 1179.4944 | 25.6627 | 33.2193 | 35.1965 | 28.5529 | 28.5612 | 28.764 | 29.2993 | 29.6574 | 30.0081 | 30.4183 | 30.7983 | 31.1673 | 31.2091 | 31.6399 | 31.3128 | 31.3128 | 31.3128 | 31.3128 | 31.3128 | 31.3128 | 31.3128 | 31.3128 | 31.3128 | 31.3128 | 31.3128 | 31.3128 | 31.3128 | 31.3128 | 31.3128 | 31.3128
40% | 3164.4787 | 20.4648 | 27.1684 | 28.9931 | 23.1399 | 23.138 | 23.3459 | 23.5741 | 24.0426 | 24.3793 | 24.5619 | 24.7616 | 24.9444 | 25.2748 | 25.6848 | 25.6562 | 25.6562 | 25.6562 | 25.6562 | 25.6562 | 25.6562 | 25.6562 | 25.6562 | 25.6562 | 25.6562 | 25.6562 | 25.6562 | 25.6562 | 25.6562 | 25.6562 | 25.6562 | 40% | 1808.3816 | 22.8113 | 29.5283 | 31.2858 | 25.3803 | 25.3878 | 25.568 | 26.0438 | 26.3621 | 26.6738 | 27.0385 | 27.3762 | 27.7042 | 27.7415 | 28.1244 | 27.8336 | 27.8336 | 27.8336 | 27.8336 | 27.8336 | 27.8336 | 27.8336 | 27.8336 | 27.8336 | 27.8336 | 27.8336 | 27.8336 | 27.8336 | 27.8336 | 27.8336 | 27.8336
35% | 3551.3408 | 17.9067 | 23.7723 | 25.3689 | 20.2474 | 20.2457 | 20.4277 | 20.6274 | 21.0373 | 21.3319 | 21.4917 | 21.6664 | 21.8264 | 22.1155 | 22.4742 | 22.4491 | 22.4491 | 22.4491 | 22.4491 | 22.4491 | 22.4491 | 22.4491 | 22.4491 | 22.4491 | 22.4491 | 22.4491 | 22.4491 | 22.4491 | 22.4491 | 22.4491 | 22.4491 | 35% | 2779.1293 | 19.9599 | 25.8372 | 27.3751 | 22.2078 | 22.2143 | 22.372 | 22.7883 | 23.0668 | 23.3396 | 23.6587 | 23.9542 | 24.2412 | 24.2738 | 24.6088 | 24.3544 | 24.3544 | 24.3544 | 24.3544 | 24.3544 | 24.3544 | 24.3544 | 24.3544 | 24.3544 | 24.3544 | 24.3544 | 24.3544 | 24.3544 | 24.3544 | 24.3544 | 24.3544
30% | 3758.953 | 15.3486 | 20.3763 | 21.7448 | 17.355 | 17.3535 | 17.5095 | 17.6806 | 18.032 | 18.2845 | 18.4214 | 18.5712 | 18.7083 | 18.9561 | 19.2636 | 19.2421 | 19.2421 | 19.2421 | 19.2421 | 19.2421 | 19.2421 | 19.2421 | 19.2421 | 19.2421 | 19.2421 | 19.2421 | 19.2421 | 19.2421 | 19.2421 | 19.2421 | 19.2421 | 30% | 3814.165 | 17.1085 | 22.1462 | 23.4644 | 19.0352 | 19.0408 | 19.176 | 19.5328 | 19.7716 | 20.0054 | 20.2789 | 20.5322 | 20.7782 | 20.8061 | 21.0933 | 20.8752 | 20.8752 | 20.8752 | 20.8752 | 20.8752 | 20.8752 | 20.8752 | 20.8752 | 20.8752 | 20.8752 | 20.8752 | 20.8752 | 20.8752 | 20.8752 | 20.8752 | 20.8752
25% | 3926.4798 | 12.7905 | 16.9802 | 18.1207 | 14.4625 | 14.4612 | 14.5912 | 14.7338 | 15.0267 | 15.2371 | 15.3512 | 15.476 | 15.5903 | 15.7968 | 16.053 | 16.0351 | 16.0351 | 16.0351 | 16.0351 | 16.0351 | 16.0351 | 16.0351 | 16.0351 | 16.0351 | 16.0351 | 16.0351 | 16.0351 | 16.0351 | 16.0351 | 16.0351 | 16.0351 | 25% | 4166.9923 | 14.257 | 18.4552 | 19.5536 | 15.8627 | 15.8674 | 15.98 | 16.2774 | 16.4763 | 16.6712 | 16.8991 | 17.1101 | 17.3152 | 17.3384 | 17.5777 | 17.396 | 17.396 | 17.396 | 17.396 | 17.396 | 17.396 | 17.396 | 17.396 | 17.396 | 17.396 | 17.396 | 17.396 | 17.396 | 17.396 | 17.396 | 17.396
20% | 4050.5177 | 10.2324 | 13.5842 | 14.4965 | 11.57 | 11.569 | 11.673 | 11.7871 | 12.0213 | 12.1897 | 12.281 | 12.3808 | 12.4722 | 12.6374 | 12.8424 | 12.8281 | 12.8281 | 12.8281 | 12.8281 | 12.8281 | 12.8281 | 12.8281 | 12.8281 | 12.8281 | 12.8281 | 12.8281 | 12.8281 | 12.8281 | 12.8281 | 12.8281 | 12.8281 | 20% | 4282.7105 | 11.4056 | 14.7641 | 15.6429 | 12.6902 | 12.6939 | 12.784 | 13.0219 | 13.181 | 13.3369 | 13.5192 | 13.6881 | 13.8521 | 13.8707 | 14.0622 | 13.9168 | 13.9168 | 13.9168 | 13.9168 | 13.9168 | 13.9168 | 13.9168 | 13.9168 | 13.9168 | 13.9168 | 13.9168 | 13.9168 | 13.9168 | 13.9168 | 13.9168 | 13.9168
15% | 4152.622 | 7.6743 | 10.1881 | 10.8724 | 8.6775 | 8.6767 | 8.7547 | 8.8403 | 9.016 | 9.1422 | 9.2107 | 9.2856 | 9.3542 | 9.4781 | 9.6318 | 9.6211 | 9.6211 | 9.6211 | 9.6211 | 9.6211 | 9.6211 | 9.6211 | 9.6211 | 9.6211 | 9.6211 | 9.6211 | 9.6211 | 9.6211 | 9.6211 | 9.6211 | 9.6211 | 15% | 4364.7722 | 8.5542 | 11.0731 | 11.7322 | 9.5176 | 9.5204 | 9.588 | 9.7664 | 9.8858 | 10.0027 | 10.1394 | 10.2661 | 10.3891 | 10.403 | 10.5466 | 10.4376 | 10.4376 | 10.4376 | 10.4376 | 10.4376 | 10.4376 | 10.4376 | 10.4376 | 10.4376 | 10.4376 | 10.4376 | 10.4376 | 10.4376 | 10.4376 | 10.4376 | 10.4376
10% | 4248.2976 | 5.1162 | 6.7921 | 7.2483 | 5.785 | 5.7845 | 5.8365 | 5.8935 | 6.0107 | 6.0948 | 6.1405 | 6.1904 | 6.2361 | 6.3187 | 6.4212 | 6.414 | 6.414 | 6.414 | 6.414 | 6.414 | 6.414 | 6.414 | 6.414 | 6.414 | 6.414 | 6.414 | 6.414 | 6.414 | 6.414 | 6.414 | 6.414 | 10% | 4391.6218 | 5.7028 | 7.3821 | 7.8215 | 6.3451 | 6.3469 | 6.392 | 6.5109 | 6.5905 | 6.6685 | 6.7596 | 6.8441 | 6.9261 | 6.9354 | 7.0311 | 6.9584 | 6.9584 | 6.9584 | 6.9584 | 6.9584 | 6.9584 | 6.9584 | 6.9584 | 6.9584 | 6.9584 | 6.9584 | 6.9584 | 6.9584 | 6.9584 | 6.9584 | 6.9584
5% | 4361.7469 | 2.5581 | 3.396 | 3.6241 | 2.8925 | 2.8922 | 2.9182 | 2.9468 | 3.0053 | 3.0474 | 3.0702 | 3.0952 | 3.1181 | 3.1594 | 3.2106 | 3.207 | 3.207 | 3.207 | 3.207 | 3.207 | 3.207 | 3.207 | 3.207 | 3.207 | 3.207 | 3.207 | 3.207 | 3.207 | 3.207 | 3.207 | 3.207 | 5% | 4391.6218 | 2.8514 | 3.691 | 3.9107 | 3.1725 | 3.1735 | 3.196 | 3.2555 | 3.2953 | 3.3342 | 3.3798 | 3.422 | 3.463 | 3.4677 | 3.5155 | 3.4792 | 3.4792 | 3.4792 | 3.4792 | 3.4792 | 3.4792 | 3.4792 | 3.4792 | 3.4792 | 3.4792 | 3.4792 | 3.4792 | 3.4792 | 3.4792 | 3.4792 | 3.4792
9.992e-14% | 4391.6218 | 5.1121e-14 | 6.7867e-14 | 7.2425e-14 | 5.7804e-14 | 5.7799e-14 | 5.8318e-14 | 5.8888e-14 | 6.0059e-14 | 6.09e-14 | 6.1356e-14 | 6.1855e-14 | 6.2311e-14 | 6.3137e-14 | 6.4161e-14 | 6.4089e-14 | 6.4089e-14 | 6.4089e-14 | 6.4089e-14 | 6.4089e-14 | 6.4089e-14 | 6.4089e-14 | 6.4089e-14 | 6.4089e-14 | 6.4089e-14 | 6.4089e-14 | 6.4089e-14 | 6.4089e-14 | 6.4089e-14 | 6.4089e-14 | 6.4089e-14 | 9.992e-14% | 4391.6218 | 5.6983e-14 | 7.3762e-14 | 7.8152e-14 | 6.34e-14 | 6.3419e-14 | 6.3869e-14 | 6.5057e-14 | 6.5853e-14 | 6.6631e-14 | 6.7542e-14 | 6.8386e-14 | 6.9205e-14 | 6.9298e-14 | 7.0255e-14 | 6.9528e-14 | 6.9528e-14 | 6.9528e-14 | 6.9528e-14 | 6.9528e-14 | 6.9528e-14 | 6.9528e-14 | 6.9528e-14 | 6.9528e-14 | 6.9528e-14 | 6.9528e-14 | 6.9528e-14 | 6.9528e-14 | 6.9528e-14 | 6.9528e-14 | 6.9528e-14
Option 5
Winter Season | [31 empty] | Winter Season
P50 | [31 empty] | P10
% of MD | Winter - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Winter - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 45.0311 | 62.4376 | 66.9594 | 38.7285 | 39.3267 | 40.3603 | 42.7146 | 44.2888 | 46.2849 | 47.3199 | 48.2291 | 46.5455 | 48.5138 | 51.6095 | 49.2564 | 49.2564 | 49.2564 | 49.2564 | 49.2564 | 49.2564 | 49.2564 | 49.2564 | 49.2564 | 49.2564 | 49.2564 | 49.2564 | 49.2564 | 49.2564 | 49.2564 | 49.2564 | 100% | 0 | 48.1978 | 65.3847 | 70.0831 | 41.8084 | 42.267 | 43.2781 | 45.6693 | 46.9727 | 49.4597 | 57.0243 | 50.7829 | 49.5605 | 51.2054 | 54.8053 | 52.3648 | 52.3648 | 52.3648 | 52.3648 | 52.3648 | 52.3648 | 52.3648 | 52.3648 | 52.3648 | 52.3648 | 52.3648 | 52.3648 | 52.3648 | 52.3648 | 52.3648 | 52.3648
99% | 1.486 | 44.5808 | 61.8132 | 66.2898 | 38.3412 | 38.9335 | 39.9567 | 42.2875 | 43.8459 | 45.822 | 46.8467 | 47.7469 | 46.0801 | 48.0287 | 51.0934 | 48.7639 | 48.7639 | 48.7639 | 48.7639 | 48.7639 | 48.7639 | 48.7639 | 48.7639 | 48.7639 | 48.7639 | 48.7639 | 48.7639 | 48.7639 | 48.7639 | 48.7639 | 48.7639 | 99% | 1.486 | 47.7158 | 64.7309 | 69.3823 | 41.3903 | 41.8443 | 42.8453 | 45.2126 | 46.5029 | 48.9651 | 56.4541 | 50.2751 | 49.0649 | 50.6933 | 54.2572 | 51.8412 | 51.8412 | 51.8412 | 51.8412 | 51.8412 | 51.8412 | 51.8412 | 51.8412 | 51.8412 | 51.8412 | 51.8412 | 51.8412 | 51.8412 | 51.8412 | 51.8412 | 51.8412
98% | 3.2692 | 44.1305 | 61.1889 | 65.6202 | 37.9539 | 38.5402 | 39.5531 | 41.8604 | 43.403 | 45.3592 | 46.3735 | 47.2646 | 45.6146 | 47.5436 | 50.5773 | 48.2713 | 48.2713 | 48.2713 | 48.2713 | 48.2713 | 48.2713 | 48.2713 | 48.2713 | 48.2713 | 48.2713 | 48.2713 | 48.2713 | 48.2713 | 48.2713 | 48.2713 | 48.2713 | 98% | 3.2692 | 47.2338 | 64.0771 | 68.6815 | 40.9722 | 41.4216 | 42.4125 | 44.7559 | 46.0332 | 48.4705 | 55.8838 | 49.7673 | 48.5693 | 50.1813 | 53.7092 | 51.3175 | 51.3175 | 51.3175 | 51.3175 | 51.3175 | 51.3175 | 51.3175 | 51.3175 | 51.3175 | 51.3175 | 51.3175 | 51.3175 | 51.3175 | 51.3175 | 51.3175 | 51.3175
97% | 6.8356 | 43.6802 | 60.5645 | 64.9506 | 37.5666 | 38.1469 | 39.1495 | 41.4332 | 42.9601 | 44.8963 | 45.9003 | 46.7823 | 45.1492 | 47.0584 | 50.0612 | 47.7787 | 47.7787 | 47.7787 | 47.7787 | 47.7787 | 47.7787 | 47.7787 | 47.7787 | 47.7787 | 47.7787 | 47.7787 | 47.7787 | 47.7787 | 47.7787 | 47.7787 | 47.7787 | 97% | 6.8356 | 46.7518 | 63.4232 | 67.9806 | 40.5541 | 40.999 | 41.9797 | 44.2992 | 45.5635 | 47.9759 | 55.3136 | 49.2594 | 48.0737 | 49.6692 | 53.1611 | 50.7939 | 50.7939 | 50.7939 | 50.7939 | 50.7939 | 50.7939 | 50.7939 | 50.7939 | 50.7939 | 50.7939 | 50.7939 | 50.7939 | 50.7939 | 50.7939 | 50.7939 | 50.7939
95% | 17.5347 | 42.7796 | 59.3157 | 63.6114 | 36.792 | 37.3604 | 38.3423 | 40.5789 | 42.0743 | 43.9707 | 44.9539 | 45.8177 | 44.2183 | 46.0882 | 49.029 | 46.7936 | 46.7936 | 46.7936 | 46.7936 | 46.7936 | 46.7936 | 46.7936 | 46.7936 | 46.7936 | 46.7936 | 46.7936 | 46.7936 | 46.7936 | 46.7936 | 46.7936 | 46.7936 | 95% | 17.5347 | 45.7879 | 62.1155 | 66.579 | 39.718 | 40.1536 | 41.1142 | 43.3858 | 44.624 | 46.9868 | 54.1731 | 48.2438 | 47.0825 | 48.6451 | 52.065 | 49.7466 | 49.7466 | 49.7466 | 49.7466 | 49.7466 | 49.7466 | 49.7466 | 49.7466 | 49.7466 | 49.7466 | 49.7466 | 49.7466 | 49.7466 | 49.7466 | 49.7466 | 49.7466
90% | 78.7576 | 40.528 | 56.1939 | 60.2634 | 34.8556 | 35.3941 | 36.3243 | 38.4432 | 39.8599 | 41.6564 | 42.5879 | 43.4062 | 41.891 | 43.6625 | 46.4486 | 44.3308 | 44.3308 | 44.3308 | 44.3308 | 44.3308 | 44.3308 | 44.3308 | 44.3308 | 44.3308 | 44.3308 | 44.3308 | 44.3308 | 44.3308 | 44.3308 | 44.3308 | 44.3308 | 90% | 78.7576 | 43.378 | 58.8463 | 63.0748 | 37.6275 | 38.0403 | 38.9503 | 41.1023 | 42.2754 | 44.5138 | 51.3219 | 45.7046 | 44.6045 | 46.0848 | 49.3247 | 47.1283 | 47.1283 | 47.1283 | 47.1283 | 47.1283 | 47.1283 | 47.1283 | 47.1283 | 47.1283 | 47.1283 | 47.1283 | 47.1283 | 47.1283 | 47.1283 | 47.1283 | 47.1283
85% | 236.8672 | 38.2764 | 53.072 | 56.9155 | 32.9192 | 33.4277 | 34.3063 | 36.3075 | 37.6454 | 39.3422 | 40.2219 | 40.9948 | 39.5637 | 41.2368 | 43.8681 | 41.868 | 41.868 | 41.868 | 41.868 | 41.868 | 41.868 | 41.868 | 41.868 | 41.868 | 41.868 | 41.868 | 41.868 | 41.868 | 41.868 | 41.868 | 41.868 | 85% | 236.8672 | 40.9681 | 55.577 | 59.5707 | 35.5371 | 35.9269 | 36.7864 | 38.8189 | 39.9268 | 42.0408 | 48.4707 | 43.1655 | 42.1265 | 43.5246 | 46.5845 | 44.5101 | 44.5101 | 44.5101 | 44.5101 | 44.5101 | 44.5101 | 44.5101 | 44.5101 | 44.5101 | 44.5101 | 44.5101 | 44.5101 | 44.5101 | 44.5101 | 44.5101 | 44.5101
80% | 497.5104 | 36.0249 | 49.9501 | 53.5675 | 30.9828 | 31.4614 | 32.2882 | 34.1717 | 35.431 | 37.0279 | 37.856 | 38.5833 | 37.2364 | 38.8111 | 41.2876 | 39.4051 | 39.4051 | 39.4051 | 39.4051 | 39.4051 | 39.4051 | 39.4051 | 39.4051 | 39.4051 | 39.4051 | 39.4051 | 39.4051 | 39.4051 | 39.4051 | 39.4051 | 39.4051 | 80% | 497.5104 | 38.5582 | 52.3078 | 56.0665 | 33.4467 | 33.8136 | 34.6225 | 36.5354 | 37.5781 | 39.5678 | 45.6195 | 40.6263 | 39.6484 | 40.9643 | 43.8442 | 41.8919 | 41.8919 | 41.8919 | 41.8919 | 41.8919 | 41.8919 | 41.8919 | 41.8919 | 41.8919 | 41.8919 | 41.8919 | 41.8919 | 41.8919 | 41.8919 | 41.8919 | 41.8919
75% | 803.6248 | 33.7733 | 46.8282 | 50.2195 | 29.0464 | 29.495 | 30.2702 | 32.036 | 33.2166 | 34.7137 | 35.49 | 36.1719 | 34.9092 | 36.3854 | 38.7071 | 36.9423 | 36.9423 | 36.9423 | 36.9423 | 36.9423 | 36.9423 | 36.9423 | 36.9423 | 36.9423 | 36.9423 | 36.9423 | 36.9423 | 36.9423 | 36.9423 | 36.9423 | 36.9423 | 75% | 803.6248 | 36.1483 | 49.0386 | 52.5623 | 31.3563 | 31.7002 | 32.4586 | 34.2519 | 35.2295 | 37.0948 | 42.7682 | 38.0872 | 37.1704 | 38.404 | 41.1039 | 39.2736 | 39.2736 | 39.2736 | 39.2736 | 39.2736 | 39.2736 | 39.2736 | 39.2736 | 39.2736 | 39.2736 | 39.2736 | 39.2736 | 39.2736 | 39.2736 | 39.2736 | 39.2736
70% | 1155.2107 | 31.5218 | 43.7063 | 46.8715 | 27.1099 | 27.5287 | 28.2522 | 29.9003 | 31.0021 | 32.3994 | 33.124 | 33.7604 | 32.5819 | 33.9597 | 36.1267 | 34.4795 | 34.4795 | 34.4795 | 34.4795 | 34.4795 | 34.4795 | 34.4795 | 34.4795 | 34.4795 | 34.4795 | 34.4795 | 34.4795 | 34.4795 | 34.4795 | 34.4795 | 34.4795 | 70% | 1155.2107 | 33.7384 | 45.7693 | 49.0582 | 29.2659 | 29.5869 | 30.2947 | 31.9685 | 32.8809 | 34.6218 | 39.917 | 35.5481 | 34.6924 | 35.8438 | 38.3637 | 36.6554 | 36.6554 | 36.6554 | 36.6554 | 36.6554 | 36.6554 | 36.6554 | 36.6554 | 36.6554 | 36.6554 | 36.6554 | 36.6554 | 36.6554 | 36.6554 | 36.6554 | 36.6554
65% | 1553.1596 | 29.2702 | 40.5844 | 43.5236 | 25.1735 | 25.5624 | 26.2342 | 27.7645 | 28.7877 | 30.0852 | 30.758 | 31.3489 | 30.2546 | 31.534 | 33.5462 | 32.0167 | 32.0167 | 32.0167 | 32.0167 | 32.0167 | 32.0167 | 32.0167 | 32.0167 | 32.0167 | 32.0167 | 32.0167 | 32.0167 | 32.0167 | 32.0167 | 32.0167 | 32.0167 | 65% | 1553.1596 | 31.3286 | 42.5001 | 45.554 | 27.1754 | 27.4735 | 28.1308 | 29.685 | 30.5322 | 32.1488 | 37.0658 | 33.0089 | 32.2143 | 33.2835 | 35.6234 | 34.0371 | 34.0371 | 34.0371 | 34.0371 | 34.0371 | 34.0371 | 34.0371 | 34.0371 | 34.0371 | 34.0371 | 34.0371 | 34.0371 | 34.0371 | 34.0371 | 34.0371 | 34.0371
60% | 2026.2996 | 27.0187 | 37.4626 | 40.1756 | 23.2371 | 23.596 | 24.2162 | 25.6288 | 26.5733 | 27.7709 | 28.392 | 28.9375 | 27.9273 | 29.1083 | 30.9657 | 29.5539 | 29.5539 | 29.5539 | 29.5539 | 29.5539 | 29.5539 | 29.5539 | 29.5539 | 29.5539 | 29.5539 | 29.5539 | 29.5539 | 29.5539 | 29.5539 | 29.5539 | 29.5539 | 60% | 2026.2996 | 28.9187 | 39.2308 | 42.0499 | 25.085 | 25.3602 | 25.9669 | 27.4016 | 28.1836 | 29.6758 | 34.2146 | 30.4698 | 29.7363 | 30.7232 | 32.8832 | 31.4189 | 31.4189 | 31.4189 | 31.4189 | 31.4189 | 31.4189 | 31.4189 | 31.4189 | 31.4189 | 31.4189 | 31.4189 | 31.4189 | 31.4189 | 31.4189 | 31.4189 | 31.4189
55% | 2598.4068 | 24.7671 | 34.3407 | 36.8276 | 21.3007 | 21.6297 | 22.1982 | 23.4931 | 24.3588 | 25.4567 | 26.026 | 26.526 | 25.6 | 26.6826 | 28.3852 | 27.091 | 27.091 | 27.091 | 27.091 | 27.091 | 27.091 | 27.091 | 27.091 | 27.091 | 27.091 | 27.091 | 27.091 | 27.091 | 27.091 | 27.091 | 27.091 | 55% | 2598.4068 | 26.5088 | 35.9616 | 38.5457 | 22.9946 | 23.2468 | 23.803 | 25.1181 | 25.835 | 27.2029 | 31.3634 | 27.9306 | 27.2583 | 28.163 | 30.1429 | 28.8007 | 28.8007 | 28.8007 | 28.8007 | 28.8007 | 28.8007 | 28.8007 | 28.8007 | 28.8007 | 28.8007 | 28.8007 | 28.8007 | 28.8007 | 28.8007 | 28.8007 | 28.8007
50% | 3233.5201 | 22.5156 | 31.2188 | 33.4797 | 19.3642 | 19.6634 | 20.1802 | 21.3573 | 22.1444 | 23.1424 | 23.66 | 24.1146 | 23.2728 | 24.2569 | 25.8048 | 24.6282 | 24.6282 | 24.6282 | 24.6282 | 24.6282 | 24.6282 | 24.6282 | 24.6282 | 24.6282 | 24.6282 | 24.6282 | 24.6282 | 24.6282 | 24.6282 | 24.6282 | 24.6282 | 50% | 3233.5201 | 24.0989 | 32.6924 | 35.0416 | 20.9042 | 21.1335 | 21.639 | 22.8346 | 23.4863 | 24.7299 | 28.5122 | 25.3915 | 24.7803 | 25.6027 | 27.4026 | 26.1824 | 26.1824 | 26.1824 | 26.1824 | 26.1824 | 26.1824 | 26.1824 | 26.1824 | 26.1824 | 26.1824 | 26.1824 | 26.1824 | 26.1824 | 26.1824 | 26.1824 | 26.1824
45% | 3775.313 | 20.264 | 28.0969 | 30.1317 | 17.4278 | 17.697 | 18.1621 | 19.2216 | 19.9299 | 20.8282 | 21.294 | 21.7031 | 20.9455 | 21.8312 | 23.2243 | 22.1654 | 22.1654 | 22.1654 | 22.1654 | 22.1654 | 22.1654 | 22.1654 | 22.1654 | 22.1654 | 22.1654 | 22.1654 | 22.1654 | 22.1654 | 22.1654 | 22.1654 | 22.1654 | 45% | 3775.313 | 21.689 | 29.4231 | 31.5374 | 18.8138 | 19.0201 | 19.4751 | 20.5512 | 21.1377 | 22.2569 | 25.6609 | 22.8523 | 22.3022 | 23.0424 | 24.6624 | 23.5642 | 23.5642 | 23.5642 | 23.5642 | 23.5642 | 23.5642 | 23.5642 | 23.5642 | 23.5642 | 23.5642 | 23.5642 | 23.5642 | 23.5642 | 23.5642 | 23.5642 | 23.5642
40% | 4072.8088 | 18.0124 | 24.975 | 26.7837 | 15.4914 | 15.7307 | 16.1441 | 17.0859 | 17.7155 | 18.514 | 18.928 | 19.2917 | 18.6182 | 19.4055 | 20.6438 | 19.7026 | 19.7026 | 19.7026 | 19.7026 | 19.7026 | 19.7026 | 19.7026 | 19.7026 | 19.7026 | 19.7026 | 19.7026 | 19.7026 | 19.7026 | 19.7026 | 19.7026 | 19.7026 | 40% | 4072.8088 | 19.2791 | 26.1539 | 28.0332 | 16.7234 | 16.9068 | 17.3112 | 18.2677 | 18.7891 | 19.7839 | 22.8097 | 20.3132 | 19.8242 | 20.4822 | 21.9221 | 20.9459 | 20.9459 | 20.9459 | 20.9459 | 20.9459 | 20.9459 | 20.9459 | 20.9459 | 20.9459 | 20.9459 | 20.9459 | 20.9459 | 20.9459 | 20.9459 | 20.9459 | 20.9459
35% | 4198.821 | 15.7609 | 21.8532 | 23.4358 | 13.555 | 13.7644 | 14.1261 | 14.9501 | 15.5011 | 16.1997 | 16.562 | 16.8802 | 16.2909 | 16.9798 | 18.0633 | 17.2397 | 17.2397 | 17.2397 | 17.2397 | 17.2397 | 17.2397 | 17.2397 | 17.2397 | 17.2397 | 17.2397 | 17.2397 | 17.2397 | 17.2397 | 17.2397 | 17.2397 | 17.2397 | 35% | 4198.821 | 16.8692 | 22.8847 | 24.5291 | 14.6329 | 14.7934 | 15.1473 | 15.9842 | 16.4404 | 17.3109 | 19.9585 | 17.774 | 17.3462 | 17.9219 | 19.1818 | 18.3277 | 18.3277 | 18.3277 | 18.3277 | 18.3277 | 18.3277 | 18.3277 | 18.3277 | 18.3277 | 18.3277 | 18.3277 | 18.3277 | 18.3277 | 18.3277 | 18.3277 | 18.3277
30% | 4271.3374 | 13.5093 | 18.7313 | 20.0878 | 11.6185 | 11.798 | 12.1081 | 12.8144 | 13.2866 | 13.8855 | 14.196 | 14.4687 | 13.9637 | 14.5542 | 15.4829 | 14.7769 | 14.7769 | 14.7769 | 14.7769 | 14.7769 | 14.7769 | 14.7769 | 14.7769 | 14.7769 | 14.7769 | 14.7769 | 14.7769 | 14.7769 | 14.7769 | 14.7769 | 14.7769 | 30% | 4271.3374 | 14.4593 | 19.6154 | 21.0249 | 12.5425 | 12.6801 | 12.9834 | 13.7008 | 14.0918 | 14.8379 | 17.1073 | 15.2349 | 14.8682 | 15.3616 | 16.4416 | 15.7094 | 15.7094 | 15.7094 | 15.7094 | 15.7094 | 15.7094 | 15.7094 | 15.7094 | 15.7094 | 15.7094 | 15.7094 | 15.7094 | 15.7094 | 15.7094 | 15.7094 | 15.7094
25% | 4321.8611 | 11.2578 | 15.6094 | 16.7398 | 9.6821 | 9.8317 | 10.0901 | 10.6787 | 11.0722 | 11.5712 | 11.83 | 12.0573 | 11.6364 | 12.1285 | 12.9024 | 12.3141 | 12.3141 | 12.3141 | 12.3141 | 12.3141 | 12.3141 | 12.3141 | 12.3141 | 12.3141 | 12.3141 | 12.3141 | 12.3141 | 12.3141 | 12.3141 | 12.3141 | 12.3141 | 25% | 4321.8611 | 12.0494 | 16.3462 | 17.5208 | 10.4521 | 10.5667 | 10.8195 | 11.4173 | 11.7432 | 12.3649 | 14.2561 | 12.6957 | 12.3901 | 12.8013 | 13.7013 | 13.0912 | 13.0912 | 13.0912 | 13.0912 | 13.0912 | 13.0912 | 13.0912 | 13.0912 | 13.0912 | 13.0912 | 13.0912 | 13.0912 | 13.0912 | 13.0912 | 13.0912 | 13.0912
20% | 4353.067 | 9.0062 | 12.4875 | 13.3919 | 7.7457 | 7.8653 | 8.0721 | 8.5429 | 8.8578 | 9.257 | 9.464 | 9.6458 | 9.3091 | 9.7028 | 10.3219 | 9.8513 | 9.8513 | 9.8513 | 9.8513 | 9.8513 | 9.8513 | 9.8513 | 9.8513 | 9.8513 | 9.8513 | 9.8513 | 9.8513 | 9.8513 | 9.8513 | 9.8513 | 9.8513 | 20% | 4353.067 | 9.6396 | 13.0769 | 14.0166 | 8.3617 | 8.4534 | 8.6556 | 9.1339 | 9.3945 | 9.8919 | 11.4049 | 10.1566 | 9.9121 | 10.2411 | 10.9611 | 10.473 | 10.473 | 10.473 | 10.473 | 10.473 | 10.473 | 10.473 | 10.473 | 10.473 | 10.473 | 10.473 | 10.473 | 10.473 | 10.473 | 10.473 | 10.473
15% | 4369.4129 | 6.7547 | 9.3656 | 10.0439 | 5.8093 | 5.899 | 6.054 | 6.4072 | 6.6433 | 6.9427 | 7.098 | 7.2344 | 6.9818 | 7.2771 | 7.7414 | 7.3885 | 7.3885 | 7.3885 | 7.3885 | 7.3885 | 7.3885 | 7.3885 | 7.3885 | 7.3885 | 7.3885 | 7.3885 | 7.3885 | 7.3885 | 7.3885 | 7.3885 | 7.3885 | 15% | 4369.4129 | 7.2297 | 9.8077 | 10.5125 | 6.2713 | 6.34 | 6.4917 | 6.8504 | 7.0459 | 7.419 | 8.5536 | 7.6174 | 7.4341 | 7.6808 | 8.2208 | 7.8547 | 7.8547 | 7.8547 | 7.8547 | 7.8547 | 7.8547 | 7.8547 | 7.8547 | 7.8547 | 7.8547 | 7.8547 | 7.8547 | 7.8547 | 7.8547 | 7.8547 | 7.8547
10% | 4378.6261 | 4.5031 | 6.2438 | 6.6959 | 3.8728 | 3.9327 | 4.036 | 4.2715 | 4.4289 | 4.6285 | 4.732 | 4.8229 | 4.6546 | 4.8514 | 5.161 | 4.9256 | 4.9256 | 4.9256 | 4.9256 | 4.9256 | 4.9256 | 4.9256 | 4.9256 | 4.9256 | 4.9256 | 4.9256 | 4.9256 | 4.9256 | 4.9256 | 4.9256 | 4.9256 | 10% | 4378.6261 | 4.8198 | 6.5385 | 7.0083 | 4.1808 | 4.2267 | 4.3278 | 4.5669 | 4.6973 | 4.946 | 5.7024 | 5.0783 | 4.9561 | 5.1205 | 5.4805 | 5.2365 | 5.2365 | 5.2365 | 5.2365 | 5.2365 | 5.2365 | 5.2365 | 5.2365 | 5.2365 | 5.2365 | 5.2365 | 5.2365 | 5.2365 | 5.2365 | 5.2365 | 5.2365
5% | 4391.7028 | 2.2516 | 3.1219 | 3.348 | 1.9364 | 1.9663 | 2.018 | 2.1357 | 2.2144 | 2.3142 | 2.366 | 2.4115 | 2.3273 | 2.4257 | 2.5805 | 2.4628 | 2.4628 | 2.4628 | 2.4628 | 2.4628 | 2.4628 | 2.4628 | 2.4628 | 2.4628 | 2.4628 | 2.4628 | 2.4628 | 2.4628 | 2.4628 | 2.4628 | 2.4628 | 5% | 4391.7028 | 2.4099 | 3.2692 | 3.5042 | 2.0904 | 2.1133 | 2.1639 | 2.2835 | 2.3486 | 2.473 | 2.8512 | 2.5391 | 2.478 | 2.5603 | 2.7403 | 2.6182 | 2.6182 | 2.6182 | 2.6182 | 2.6182 | 2.6182 | 2.6182 | 2.6182 | 2.6182 | 2.6182 | 2.6182 | 2.6182 | 2.6182 | 2.6182 | 2.6182 | 2.6182
9.992e-14% | 4391.7028 | 4.4995e-14 | 6.2388e-14 | 6.6906e-14 | 3.8698e-14 | 3.9295e-14 | 4.0328e-14 | 4.2681e-14 | 4.4253e-14 | 4.6248e-14 | 4.7282e-14 | 4.8191e-14 | 4.6508e-14 | 4.8475e-14 | 5.1568e-14 | 4.9217e-14 | 4.9217e-14 | 4.9217e-14 | 4.9217e-14 | 4.9217e-14 | 4.9217e-14 | 4.9217e-14 | 4.9217e-14 | 4.9217e-14 | 4.9217e-14 | 4.9217e-14 | 4.9217e-14 | 4.9217e-14 | 4.9217e-14 | 4.9217e-14 | 4.9217e-14 | 9.992e-14% | 4391.7028 | 4.8159e-14 | 6.5332e-14 | 7.0027e-14 | 4.1775e-14 | 4.2233e-14 | 4.3244e-14 | 4.5633e-14 | 4.6935e-14 | 4.942e-14 | 5.6979e-14 | 5.0742e-14 | 4.9521e-14 | 5.1164e-14 | 5.4761e-14 | 5.2323e-14 | 5.2323e-14 | 5.2323e-14 | 5.2323e-14 | 5.2323e-14 | 5.2323e-14 | 5.2323e-14 | 5.2323e-14 | 5.2323e-14 | 5.2323e-14 | 5.2323e-14 | 5.2323e-14 | 5.2323e-14 | 5.2323e-14 | 5.2323e-14 | 5.2323e-14
Summer Season | [31 empty] | Summer Season
P50 | [31 empty] | P10
% of MD | Summer - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Summer - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 51.1621 | 67.921 | 72.4827 | 43.3498 | 43.345 | 43.8648 | 44.4353 | 45.6066 | 46.4483 | 46.9048 | 47.4041 | 47.8611 | 48.687 | 49.7121 | 49.6404 | 49.6404 | 49.6404 | 49.6404 | 49.6404 | 49.6404 | 49.6404 | 49.6404 | 49.6404 | 49.6404 | 49.6404 | 49.6404 | 49.6404 | 49.6404 | 49.6404 | 49.6404 | 100% | 0 | 57.0282 | 73.8207 | 78.2145 | 48.9508 | 48.9694 | 49.4199 | 50.6095 | 51.4052 | 52.1846 | 53.0962 | 53.9406 | 54.7606 | 54.8537 | 55.8109 | 55.0841 | 55.0841 | 55.0841 | 55.0841 | 55.0841 | 55.0841 | 55.0841 | 55.0841 | 55.0841 | 55.0841 | 55.0841 | 55.0841 | 55.0841 | 55.0841 | 55.0841 | 55.0841
99% | 0 | 50.6505 | 67.2418 | 71.7579 | 42.9163 | 42.9115 | 43.4262 | 43.991 | 45.1505 | 45.9838 | 46.4358 | 46.93 | 47.3825 | 48.2001 | 49.2149 | 49.144 | 49.144 | 49.144 | 49.144 | 49.144 | 49.144 | 49.144 | 49.144 | 49.144 | 49.144 | 49.144 | 49.144 | 49.144 | 49.144 | 49.144 | 49.144 | 99% | 1.5127 | 56.4579 | 73.0825 | 77.4324 | 48.4613 | 48.4797 | 48.9257 | 50.1034 | 50.8912 | 51.6628 | 52.5653 | 53.4012 | 54.213 | 54.3051 | 55.2528 | 54.5332 | 54.5332 | 54.5332 | 54.5332 | 54.5332 | 54.5332 | 54.5332 | 54.5332 | 54.5332 | 54.5332 | 54.5332 | 54.5332 | 54.5332 | 54.5332 | 54.5332 | 54.5332
98% | 0 | 50.1389 | 66.5626 | 71.033 | 42.4828 | 42.4781 | 42.9875 | 43.5466 | 44.6945 | 45.5193 | 45.9667 | 46.456 | 46.9039 | 47.7133 | 48.7178 | 48.6476 | 48.6476 | 48.6476 | 48.6476 | 48.6476 | 48.6476 | 48.6476 | 48.6476 | 48.6476 | 48.6476 | 48.6476 | 48.6476 | 48.6476 | 48.6476 | 48.6476 | 48.6476 | 98% | 2.269 | 55.8876 | 72.3443 | 76.6503 | 47.9718 | 47.99 | 48.4315 | 49.5973 | 50.3771 | 51.1409 | 52.0343 | 52.8618 | 53.6654 | 53.7566 | 54.6947 | 53.9824 | 53.9824 | 53.9824 | 53.9824 | 53.9824 | 53.9824 | 53.9824 | 53.9824 | 53.9824 | 53.9824 | 53.9824 | 53.9824 | 53.9824 | 53.9824 | 53.9824 | 53.9824
97% | 0.37816 | 49.6272 | 65.8834 | 70.3082 | 42.0494 | 42.0446 | 42.5489 | 43.1023 | 44.2384 | 45.0548 | 45.4977 | 45.982 | 46.4253 | 47.2264 | 48.2207 | 48.1512 | 48.1512 | 48.1512 | 48.1512 | 48.1512 | 48.1512 | 48.1512 | 48.1512 | 48.1512 | 48.1512 | 48.1512 | 48.1512 | 48.1512 | 48.1512 | 48.1512 | 48.1512 | 97% | 3.7816 | 55.3173 | 71.6061 | 75.8681 | 47.4823 | 47.5003 | 47.9373 | 49.0912 | 49.8631 | 50.6191 | 51.5034 | 52.3223 | 53.1178 | 53.208 | 54.1366 | 53.4315 | 53.4315 | 53.4315 | 53.4315 | 53.4315 | 53.4315 | 53.4315 | 53.4315 | 53.4315 | 53.4315 | 53.4315 | 53.4315 | 53.4315 | 53.4315 | 53.4315 | 53.4315
95% | 2.269 | 48.604 | 64.5249 | 68.8586 | 41.1824 | 41.1777 | 41.6716 | 42.2136 | 43.3263 | 44.1258 | 44.5596 | 45.0339 | 45.4681 | 46.2527 | 47.2265 | 47.1584 | 47.1584 | 47.1584 | 47.1584 | 47.1584 | 47.1584 | 47.1584 | 47.1584 | 47.1584 | 47.1584 | 47.1584 | 47.1584 | 47.1584 | 47.1584 | 47.1584 | 47.1584 | 95% | 6.0506 | 54.1768 | 70.1297 | 74.3038 | 46.5033 | 46.521 | 46.9489 | 48.079 | 48.835 | 49.5754 | 50.4414 | 51.2435 | 52.0226 | 52.111 | 53.0203 | 52.3299 | 52.3299 | 52.3299 | 52.3299 | 52.3299 | 52.3299 | 52.3299 | 52.3299 | 52.3299 | 52.3299 | 52.3299 | 52.3299 | 52.3299 | 52.3299 | 52.3299 | 52.3299
90% | 5.6725 | 46.0459 | 61.1289 | 65.2344 | 39.0149 | 39.0105 | 39.4784 | 39.9918 | 41.0459 | 41.8034 | 42.2143 | 42.6637 | 43.075 | 43.8183 | 44.7409 | 44.6764 | 44.6764 | 44.6764 | 44.6764 | 44.6764 | 44.6764 | 44.6764 | 44.6764 | 44.6764 | 44.6764 | 44.6764 | 44.6764 | 44.6764 | 44.6764 | 44.6764 | 44.6764 | 90% | 16.2611 | 51.3254 | 66.4386 | 70.3931 | 44.0557 | 44.0725 | 44.4779 | 45.5485 | 46.2647 | 46.9662 | 47.7866 | 48.5465 | 49.2846 | 49.3683 | 50.2298 | 49.5757 | 49.5757 | 49.5757 | 49.5757 | 49.5757 | 49.5757 | 49.5757 | 49.5757 | 49.5757 | 49.5757 | 49.5757 | 49.5757 | 49.5757 | 49.5757 | 49.5757 | 49.5757
85% | 15.8829 | 43.4878 | 57.7328 | 61.6103 | 36.8474 | 36.8432 | 37.2851 | 37.77 | 38.7656 | 39.481 | 39.8691 | 40.2935 | 40.682 | 41.384 | 42.2553 | 42.1944 | 42.1944 | 42.1944 | 42.1944 | 42.1944 | 42.1944 | 42.1944 | 42.1944 | 42.1944 | 42.1944 | 42.1944 | 42.1944 | 42.1944 | 42.1944 | 42.1944 | 42.1944 | 85% | 26.4715 | 48.4739 | 62.7476 | 66.4824 | 41.6082 | 41.624 | 42.0069 | 43.0181 | 43.6945 | 44.3569 | 45.1318 | 45.8495 | 46.5465 | 46.6256 | 47.4392 | 46.8215 | 46.8215 | 46.8215 | 46.8215 | 46.8215 | 46.8215 | 46.8215 | 46.8215 | 46.8215 | 46.8215 | 46.8215 | 46.8215 | 46.8215 | 46.8215 | 46.8215 | 46.8215
80% | 31.0095 | 40.9297 | 54.3368 | 57.9862 | 34.6799 | 34.676 | 35.0919 | 35.5483 | 36.4853 | 37.1586 | 37.5239 | 37.9233 | 38.2889 | 38.9496 | 39.7697 | 39.7123 | 39.7123 | 39.7123 | 39.7123 | 39.7123 | 39.7123 | 39.7123 | 39.7123 | 39.7123 | 39.7123 | 39.7123 | 39.7123 | 39.7123 | 39.7123 | 39.7123 | 39.7123 | 80% | 34.0348 | 45.6225 | 59.0566 | 62.5716 | 39.1606 | 39.1755 | 39.5359 | 40.4876 | 41.1242 | 41.7477 | 42.477 | 43.1524 | 43.8085 | 43.8829 | 44.6487 | 44.0672 | 44.0672 | 44.0672 | 44.0672 | 44.0672 | 44.0672 | 44.0672 | 44.0672 | 44.0672 | 44.0672 | 44.0672 | 44.0672 | 44.0672 | 44.0672 | 44.0672 | 44.0672
75% | 72.9857 | 38.3716 | 50.9407 | 54.362 | 32.5124 | 32.5087 | 32.8986 | 33.3265 | 34.205 | 34.8362 | 35.1786 | 35.5531 | 35.8958 | 36.5153 | 37.2841 | 37.2303 | 37.2303 | 37.2303 | 37.2303 | 37.2303 | 37.2303 | 37.2303 | 37.2303 | 37.2303 | 37.2303 | 37.2303 | 37.2303 | 37.2303 | 37.2303 | 37.2303 | 37.2303 | 75% | 48.405 | 42.7711 | 55.3655 | 58.6609 | 36.7131 | 36.7271 | 37.0649 | 37.9571 | 38.5539 | 39.1385 | 39.8222 | 40.4554 | 41.0705 | 41.1402 | 41.8582 | 41.313 | 41.313 | 41.313 | 41.313 | 41.313 | 41.313 | 41.313 | 41.313 | 41.313 | 41.313 | 41.313 | 41.313 | 41.313 | 41.313 | 41.313 | 41.313
70% | 150.5094 | 35.8135 | 47.5447 | 50.7379 | 30.3449 | 30.3415 | 30.7054 | 31.1047 | 31.9246 | 32.5138 | 32.8334 | 33.1829 | 33.5028 | 34.0809 | 34.7984 | 34.7483 | 34.7483 | 34.7483 | 34.7483 | 34.7483 | 34.7483 | 34.7483 | 34.7483 | 34.7483 | 34.7483 | 34.7483 | 34.7483 | 34.7483 | 34.7483 | 34.7483 | 34.7483 | 70% | 76.3892 | 39.9197 | 51.6745 | 54.7502 | 34.2656 | 34.2786 | 34.5939 | 35.4266 | 35.9837 | 36.5292 | 37.1674 | 37.7584 | 38.3324 | 38.3976 | 39.0676 | 38.5588 | 38.5588 | 38.5588 | 38.5588 | 38.5588 | 38.5588 | 38.5588 | 38.5588 | 38.5588 | 38.5588 | 38.5588 | 38.5588 | 38.5588 | 38.5588 | 38.5588 | 38.5588
65% | 359.6342 | 33.2554 | 44.1486 | 47.1138 | 28.1774 | 28.1742 | 28.5121 | 28.883 | 29.6443 | 30.1914 | 30.4881 | 30.8127 | 31.1097 | 31.6466 | 32.3128 | 32.2663 | 32.2663 | 32.2663 | 32.2663 | 32.2663 | 32.2663 | 32.2663 | 32.2663 | 32.2663 | 32.2663 | 32.2663 | 32.2663 | 32.2663 | 32.2663 | 32.2663 | 32.2663 | 65% | 114.2056 | 37.0683 | 47.9835 | 50.8395 | 31.818 | 31.8301 | 32.1229 | 32.8962 | 33.4134 | 33.92 | 34.5126 | 35.0614 | 35.5944 | 35.6549 | 36.2771 | 35.8046 | 35.8046 | 35.8046 | 35.8046 | 35.8046 | 35.8046 | 35.8046 | 35.8046 | 35.8046 | 35.8046 | 35.8046 | 35.8046 | 35.8046 | 35.8046 | 35.8046 | 35.8046
60% | 689.7717 | 30.6973 | 40.7526 | 43.4896 | 26.0099 | 26.007 | 26.3189 | 26.6612 | 27.364 | 27.869 | 28.1429 | 28.4424 | 28.7167 | 29.2122 | 29.8272 | 29.7843 | 29.7843 | 29.7843 | 29.7843 | 29.7843 | 29.7843 | 29.7843 | 29.7843 | 29.7843 | 29.7843 | 29.7843 | 29.7843 | 29.7843 | 29.7843 | 29.7843 | 29.7843 | 60% | 178.1154 | 34.2169 | 44.2924 | 46.9287 | 29.3705 | 29.3817 | 29.6519 | 30.3657 | 30.8431 | 31.3108 | 31.8577 | 32.3643 | 32.8564 | 32.9122 | 33.4865 | 33.0504 | 33.0504 | 33.0504 | 33.0504 | 33.0504 | 33.0504 | 33.0504 | 33.0504 | 33.0504 | 33.0504 | 33.0504 | 33.0504 | 33.0504 | 33.0504 | 33.0504 | 33.0504
55% | 1095.5419 | 28.1392 | 37.3565 | 39.8655 | 23.8424 | 23.8397 | 24.1257 | 24.4394 | 25.0836 | 25.5465 | 25.7976 | 26.0722 | 26.3236 | 26.7779 | 27.3416 | 27.3022 | 27.3022 | 27.3022 | 27.3022 | 27.3022 | 27.3022 | 27.3022 | 27.3022 | 27.3022 | 27.3022 | 27.3022 | 27.3022 | 27.3022 | 27.3022 | 27.3022 | 27.3022 | 55% | 311.6074 | 31.3655 | 40.6014 | 43.018 | 26.9229 | 26.9332 | 27.181 | 27.8352 | 28.2729 | 28.7015 | 29.2029 | 29.6673 | 30.1183 | 30.1695 | 30.696 | 30.2962 | 30.2962 | 30.2962 | 30.2962 | 30.2962 | 30.2962 | 30.2962 | 30.2962 | 30.2962 | 30.2962 | 30.2962 | 30.2962 | 30.2962 | 30.2962 | 30.2962 | 30.2962
50% | 1666.1918 | 25.581 | 33.9605 | 36.2413 | 21.6749 | 21.6725 | 21.9324 | 22.2177 | 22.8033 | 23.2241 | 23.4524 | 23.702 | 23.9306 | 24.3435 | 24.856 | 24.8202 | 24.8202 | 24.8202 | 24.8202 | 24.8202 | 24.8202 | 24.8202 | 24.8202 | 24.8202 | 24.8202 | 24.8202 | 24.8202 | 24.8202 | 24.8202 | 24.8202 | 24.8202 | 50% | 636.0723 | 28.5141 | 36.9103 | 39.1073 | 24.4754 | 24.4847 | 24.71 | 25.3047 | 25.7026 | 26.0923 | 26.5481 | 26.9703 | 27.3803 | 27.4268 | 27.9054 | 27.542 | 27.542 | 27.542 | 27.542 | 27.542 | 27.542 | 27.542 | 27.542 | 27.542 | 27.542 | 27.542 | 27.542 | 27.542 | 27.542 | 27.542 | 27.542
45% | 2506.0947 | 23.0229 | 30.5644 | 32.6172 | 19.5074 | 19.5052 | 19.7392 | 19.9959 | 20.523 | 20.9017 | 21.1072 | 21.3318 | 21.5375 | 21.9092 | 22.3704 | 22.3382 | 22.3382 | 22.3382 | 22.3382 | 22.3382 | 22.3382 | 22.3382 | 22.3382 | 22.3382 | 22.3382 | 22.3382 | 22.3382 | 22.3382 | 22.3382 | 22.3382 | 22.3382 | 45% | 1179.4944 | 25.6627 | 33.2193 | 35.1965 | 22.0279 | 22.0362 | 22.239 | 22.7743 | 23.1324 | 23.4831 | 23.8933 | 24.2733 | 24.6423 | 24.6841 | 25.1149 | 24.7878 | 24.7878 | 24.7878 | 24.7878 | 24.7878 | 24.7878 | 24.7878 | 24.7878 | 24.7878 | 24.7878 | 24.7878 | 24.7878 | 24.7878 | 24.7878 | 24.7878 | 24.7878
40% | 3164.4787 | 20.4648 | 27.1684 | 28.9931 | 17.3399 | 17.338 | 17.5459 | 17.7741 | 18.2426 | 18.5793 | 18.7619 | 18.9616 | 19.1444 | 19.4748 | 19.8848 | 19.8562 | 19.8562 | 19.8562 | 19.8562 | 19.8562 | 19.8562 | 19.8562 | 19.8562 | 19.8562 | 19.8562 | 19.8562 | 19.8562 | 19.8562 | 19.8562 | 19.8562 | 19.8562 | 40% | 1808.3816 | 22.8113 | 29.5283 | 31.2858 | 19.5803 | 19.5878 | 19.768 | 20.2438 | 20.5621 | 20.8738 | 21.2385 | 21.5762 | 21.9042 | 21.9415 | 22.3244 | 22.0336 | 22.0336 | 22.0336 | 22.0336 | 22.0336 | 22.0336 | 22.0336 | 22.0336 | 22.0336 | 22.0336 | 22.0336 | 22.0336 | 22.0336 | 22.0336 | 22.0336 | 22.0336
35% | 3551.3408 | 17.9067 | 23.7723 | 25.3689 | 15.1724 | 15.1707 | 15.3527 | 15.5524 | 15.9623 | 16.2569 | 16.4167 | 16.5914 | 16.7514 | 17.0405 | 17.3992 | 17.3741 | 17.3741 | 17.3741 | 17.3741 | 17.3741 | 17.3741 | 17.3741 | 17.3741 | 17.3741 | 17.3741 | 17.3741 | 17.3741 | 17.3741 | 17.3741 | 17.3741 | 17.3741 | 35% | 2779.1293 | 19.9599 | 25.8372 | 27.3751 | 17.1328 | 17.1393 | 17.297 | 17.7133 | 17.9918 | 18.2646 | 18.5837 | 18.8792 | 19.1662 | 19.1988 | 19.5338 | 19.2794 | 19.2794 | 19.2794 | 19.2794 | 19.2794 | 19.2794 | 19.2794 | 19.2794 | 19.2794 | 19.2794 | 19.2794 | 19.2794 | 19.2794 | 19.2794 | 19.2794 | 19.2794
30% | 3758.953 | 15.3486 | 20.3763 | 21.7448 | 13.005 | 13.0035 | 13.1595 | 13.3306 | 13.682 | 13.9345 | 14.0714 | 14.2212 | 14.3583 | 14.6061 | 14.9136 | 14.8921 | 14.8921 | 14.8921 | 14.8921 | 14.8921 | 14.8921 | 14.8921 | 14.8921 | 14.8921 | 14.8921 | 14.8921 | 14.8921 | 14.8921 | 14.8921 | 14.8921 | 14.8921 | 30% | 3814.165 | 17.1085 | 22.1462 | 23.4644 | 14.6852 | 14.6908 | 14.826 | 15.1828 | 15.4216 | 15.6554 | 15.9289 | 16.1822 | 16.4282 | 16.4561 | 16.7433 | 16.5252 | 16.5252 | 16.5252 | 16.5252 | 16.5252 | 16.5252 | 16.5252 | 16.5252 | 16.5252 | 16.5252 | 16.5252 | 16.5252 | 16.5252 | 16.5252 | 16.5252 | 16.5252
25% | 3926.4798 | 12.7905 | 16.9802 | 18.1207 | 10.8375 | 10.8362 | 10.9662 | 11.1088 | 11.4017 | 11.6121 | 11.7262 | 11.851 | 11.9653 | 12.1718 | 12.428 | 12.4101 | 12.4101 | 12.4101 | 12.4101 | 12.4101 | 12.4101 | 12.4101 | 12.4101 | 12.4101 | 12.4101 | 12.4101 | 12.4101 | 12.4101 | 12.4101 | 12.4101 | 12.4101 | 25% | 4166.9923 | 14.257 | 18.4552 | 19.5536 | 12.2377 | 12.2424 | 12.355 | 12.6524 | 12.8513 | 13.0462 | 13.2741 | 13.4851 | 13.6902 | 13.7134 | 13.9527 | 13.771 | 13.771 | 13.771 | 13.771 | 13.771 | 13.771 | 13.771 | 13.771 | 13.771 | 13.771 | 13.771 | 13.771 | 13.771 | 13.771 | 13.771 | 13.771
20% | 4050.5177 | 10.2324 | 13.5842 | 14.4965 | 8.67 | 8.669 | 8.773 | 8.8871 | 9.1213 | 9.2897 | 9.381 | 9.4808 | 9.5722 | 9.7374 | 9.9424 | 9.9281 | 9.9281 | 9.9281 | 9.9281 | 9.9281 | 9.9281 | 9.9281 | 9.9281 | 9.9281 | 9.9281 | 9.9281 | 9.9281 | 9.9281 | 9.9281 | 9.9281 | 9.9281 | 20% | 4282.7105 | 11.4056 | 14.7641 | 15.6429 | 9.7902 | 9.7939 | 9.884 | 10.1219 | 10.281 | 10.4369 | 10.6192 | 10.7881 | 10.9521 | 10.9707 | 11.1622 | 11.0168 | 11.0168 | 11.0168 | 11.0168 | 11.0168 | 11.0168 | 11.0168 | 11.0168 | 11.0168 | 11.0168 | 11.0168 | 11.0168 | 11.0168 | 11.0168 | 11.0168 | 11.0168
15% | 4152.622 | 7.6743 | 10.1881 | 10.8724 | 6.5025 | 6.5017 | 6.5797 | 6.6653 | 6.841 | 6.9672 | 7.0357 | 7.1106 | 7.1792 | 7.3031 | 7.4568 | 7.4461 | 7.4461 | 7.4461 | 7.4461 | 7.4461 | 7.4461 | 7.4461 | 7.4461 | 7.4461 | 7.4461 | 7.4461 | 7.4461 | 7.4461 | 7.4461 | 7.4461 | 7.4461 | 15% | 4364.7722 | 8.5542 | 11.0731 | 11.7322 | 7.3426 | 7.3454 | 7.413 | 7.5914 | 7.7108 | 7.8277 | 7.9644 | 8.0911 | 8.2141 | 8.228 | 8.3716 | 8.2626 | 8.2626 | 8.2626 | 8.2626 | 8.2626 | 8.2626 | 8.2626 | 8.2626 | 8.2626 | 8.2626 | 8.2626 | 8.2626 | 8.2626 | 8.2626 | 8.2626 | 8.2626
10% | 4248.2976 | 5.1162 | 6.7921 | 7.2483 | 4.335 | 4.3345 | 4.3865 | 4.4435 | 4.5607 | 4.6448 | 4.6905 | 4.7404 | 4.7861 | 4.8687 | 4.9712 | 4.964 | 4.964 | 4.964 | 4.964 | 4.964 | 4.964 | 4.964 | 4.964 | 4.964 | 4.964 | 4.964 | 4.964 | 4.964 | 4.964 | 4.964 | 4.964 | 10% | 4391.6218 | 5.7028 | 7.3821 | 7.8215 | 4.8951 | 4.8969 | 4.942 | 5.0609 | 5.1405 | 5.2185 | 5.3096 | 5.3941 | 5.4761 | 5.4854 | 5.5811 | 5.5084 | 5.5084 | 5.5084 | 5.5084 | 5.5084 | 5.5084 | 5.5084 | 5.5084 | 5.5084 | 5.5084 | 5.5084 | 5.5084 | 5.5084 | 5.5084 | 5.5084 | 5.5084
5% | 4361.7469 | 2.5581 | 3.396 | 3.6241 | 2.1675 | 2.1672 | 2.1932 | 2.2218 | 2.2803 | 2.3224 | 2.3452 | 2.3702 | 2.3931 | 2.4344 | 2.4856 | 2.482 | 2.482 | 2.482 | 2.482 | 2.482 | 2.482 | 2.482 | 2.482 | 2.482 | 2.482 | 2.482 | 2.482 | 2.482 | 2.482 | 2.482 | 2.482 | 5% | 4391.6218 | 2.8514 | 3.691 | 3.9107 | 2.4475 | 2.4485 | 2.471 | 2.5305 | 2.5703 | 2.6092 | 2.6548 | 2.697 | 2.738 | 2.7427 | 2.7905 | 2.7542 | 2.7542 | 2.7542 | 2.7542 | 2.7542 | 2.7542 | 2.7542 | 2.7542 | 2.7542 | 2.7542 | 2.7542 | 2.7542 | 2.7542 | 2.7542 | 2.7542 | 2.7542
9.992e-14% | 4391.6218 | 5.1121e-14 | 6.7867e-14 | 7.2425e-14 | 4.3315e-14 | 4.331e-14 | 4.383e-14 | 4.44e-14 | 4.557e-14 | 4.6411e-14 | 4.6867e-14 | 4.7366e-14 | 4.7823e-14 | 4.8648e-14 | 4.9672e-14 | 4.9601e-14 | 4.9601e-14 | 4.9601e-14 | 4.9601e-14 | 4.9601e-14 | 4.9601e-14 | 4.9601e-14 | 4.9601e-14 | 4.9601e-14 | 4.9601e-14 | 4.9601e-14 | 4.9601e-14 | 4.9601e-14 | 4.9601e-14 | 4.9601e-14 | 4.9601e-14 | 9.992e-14% | 4391.6218 | 5.6983e-14 | 7.3762e-14 | 7.8152e-14 | 4.8912e-14 | 4.893e-14 | 4.938e-14 | 5.0569e-14 | 5.1364e-14 | 5.2143e-14 | 5.3054e-14 | 5.3897e-14 | 5.4717e-14 | 5.481e-14 | 5.5766e-14 | 5.504e-14 | 5.504e-14 | 5.504e-14 | 5.504e-14 | 5.504e-14 | 5.504e-14 | 5.504e-14 | 5.504e-14 | 5.504e-14 | 5.504e-14 | 5.504e-14 | 5.504e-14 | 5.504e-14 | 5.504e-14 | 5.504e-14 | 5.504e-14
Option 6
Winter Season | [31 empty] | Winter Season
P50 | [31 empty] | P10
% of MD | Winter - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Winter - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 37.2856 | 52.4773 | 56.4235 | 57.2301 | 57.8298 | 58.8066 | 61.0067 | 62.4798 | 64.3758 | 65.2933 | 66.0951 | 64.3059 | 66.2646 | 69.2367 | 66.9821 | 66.9821 | 66.9821 | 66.9821 | 66.9821 | 66.9821 | 66.9821 | 66.9821 | 66.9821 | 66.9821 | 66.9821 | 66.9821 | 66.9821 | 66.9821 | 66.9821 | 66.9821 | 100% | 0 | 40.4522 | 55.4244 | 59.5473 | 60.31 | 60.7701 | 61.7244 | 63.9613 | 65.1637 | 67.5506 | 74.9976 | 68.6488 | 67.3209 | 68.9561 | 72.4324 | 70.0905 | 70.0905 | 70.0905 | 70.0905 | 70.0905 | 70.0905 | 70.0905 | 70.0905 | 70.0905 | 70.0905 | 70.0905 | 70.0905 | 70.0905 | 70.0905 | 70.0905 | 70.0905
99% | 1.486 | 36.9127 | 51.9525 | 55.8593 | 56.6578 | 57.2515 | 58.2186 | 60.3966 | 61.855 | 63.732 | 64.6403 | 65.4341 | 63.6629 | 65.602 | 68.5443 | 66.3123 | 66.3123 | 66.3123 | 66.3123 | 66.3123 | 66.3123 | 66.3123 | 66.3123 | 66.3123 | 66.3123 | 66.3123 | 66.3123 | 66.3123 | 66.3123 | 66.3123 | 66.3123 | 99% | 1.486 | 40.0477 | 54.8702 | 58.9518 | 59.7069 | 60.1623 | 61.1072 | 63.3217 | 64.5121 | 66.8751 | 74.2477 | 67.9624 | 66.6477 | 68.2666 | 71.7081 | 69.3896 | 69.3896 | 69.3896 | 69.3896 | 69.3896 | 69.3896 | 69.3896 | 69.3896 | 69.3896 | 69.3896 | 69.3896 | 69.3896 | 69.3896 | 69.3896 | 69.3896 | 69.3896
98% | 3.2692 | 36.5398 | 51.4278 | 55.295 | 56.0855 | 56.6732 | 57.6305 | 59.7866 | 61.2302 | 63.0883 | 63.9874 | 64.7732 | 63.0198 | 64.9393 | 67.8519 | 65.6424 | 65.6424 | 65.6424 | 65.6424 | 65.6424 | 65.6424 | 65.6424 | 65.6424 | 65.6424 | 65.6424 | 65.6424 | 65.6424 | 65.6424 | 65.6424 | 65.6424 | 65.6424 | 98% | 3.2692 | 39.6432 | 54.316 | 58.3563 | 59.1038 | 59.5546 | 60.4899 | 62.6821 | 63.8604 | 66.1996 | 73.4977 | 67.2759 | 65.9745 | 67.577 | 70.9838 | 68.6887 | 68.6887 | 68.6887 | 68.6887 | 68.6887 | 68.6887 | 68.6887 | 68.6887 | 68.6887 | 68.6887 | 68.6887 | 68.6887 | 68.6887 | 68.6887 | 68.6887 | 68.6887
97% | 6.8356 | 36.167 | 50.903 | 54.7308 | 55.5132 | 56.0949 | 57.0424 | 59.1765 | 60.6054 | 62.4445 | 63.3345 | 64.1122 | 62.3768 | 64.2767 | 67.1596 | 64.9726 | 64.9726 | 64.9726 | 64.9726 | 64.9726 | 64.9726 | 64.9726 | 64.9726 | 64.9726 | 64.9726 | 64.9726 | 64.9726 | 64.9726 | 64.9726 | 64.9726 | 64.9726 | 97% | 6.8356 | 39.2387 | 53.7617 | 57.7609 | 58.5007 | 58.9469 | 59.8727 | 62.0425 | 63.2088 | 65.5241 | 72.7477 | 66.5894 | 65.3013 | 66.8875 | 70.2594 | 67.9878 | 67.9878 | 67.9878 | 67.9878 | 67.9878 | 67.9878 | 67.9878 | 67.9878 | 67.9878 | 67.9878 | 67.9878 | 67.9878 | 67.9878 | 67.9878 | 67.9878 | 67.9878
95% | 17.5347 | 35.4213 | 49.8534 | 53.6023 | 54.3686 | 54.9383 | 55.8663 | 57.9564 | 59.3558 | 61.157 | 62.0286 | 62.7903 | 61.0906 | 62.9514 | 65.7748 | 63.633 | 63.633 | 63.633 | 63.633 | 63.633 | 63.633 | 63.633 | 63.633 | 63.633 | 63.633 | 63.633 | 63.633 | 63.633 | 63.633 | 63.633 | 63.633 | 95% | 17.5347 | 38.4296 | 52.6532 | 56.5699 | 57.2945 | 57.7315 | 58.6382 | 60.7632 | 61.9055 | 64.1731 | 71.2477 | 65.2164 | 63.9549 | 65.5083 | 68.8108 | 66.586 | 66.586 | 66.586 | 66.586 | 66.586 | 66.586 | 66.586 | 66.586 | 66.586 | 66.586 | 66.586 | 66.586 | 66.586 | 66.586 | 66.586 | 66.586
90% | 78.7576 | 33.557 | 47.2296 | 50.7812 | 51.507 | 52.0468 | 52.926 | 54.906 | 56.2318 | 57.9382 | 58.7639 | 59.4856 | 57.8753 | 59.6381 | 62.313 | 60.2839 | 60.2839 | 60.2839 | 60.2839 | 60.2839 | 60.2839 | 60.2839 | 60.2839 | 60.2839 | 60.2839 | 60.2839 | 60.2839 | 60.2839 | 60.2839 | 60.2839 | 60.2839 | 90% | 78.7576 | 36.407 | 49.882 | 53.5926 | 54.279 | 54.693 | 55.552 | 57.5652 | 58.6473 | 60.7956 | 67.4979 | 61.784 | 60.5888 | 62.0605 | 65.1892 | 63.0814 | 63.0814 | 63.0814 | 63.0814 | 63.0814 | 63.0814 | 63.0814 | 63.0814 | 63.0814 | 63.0814 | 63.0814 | 63.0814 | 63.0814 | 63.0814 | 63.0814 | 63.0814
85% | 236.8672 | 31.6927 | 44.6057 | 47.96 | 48.6455 | 49.1553 | 49.9856 | 51.8557 | 53.1078 | 54.7194 | 55.4993 | 56.1808 | 54.66 | 56.3249 | 58.8512 | 56.9348 | 56.9348 | 56.9348 | 56.9348 | 56.9348 | 56.9348 | 56.9348 | 56.9348 | 56.9348 | 56.9348 | 56.9348 | 56.9348 | 56.9348 | 56.9348 | 56.9348 | 56.9348 | 85% | 236.8672 | 34.3844 | 47.1108 | 50.6152 | 51.2635 | 51.6545 | 52.4657 | 54.3671 | 55.3892 | 57.4181 | 63.748 | 58.3515 | 57.2228 | 58.6127 | 61.5676 | 59.5769 | 59.5769 | 59.5769 | 59.5769 | 59.5769 | 59.5769 | 59.5769 | 59.5769 | 59.5769 | 59.5769 | 59.5769 | 59.5769 | 59.5769 | 59.5769 | 59.5769 | 59.5769
80% | 497.5104 | 29.8284 | 41.9819 | 45.1388 | 45.784 | 46.2638 | 47.0453 | 48.8054 | 49.9839 | 51.5006 | 52.2346 | 52.876 | 51.4448 | 53.0117 | 55.3893 | 53.5857 | 53.5857 | 53.5857 | 53.5857 | 53.5857 | 53.5857 | 53.5857 | 53.5857 | 53.5857 | 53.5857 | 53.5857 | 53.5857 | 53.5857 | 53.5857 | 53.5857 | 53.5857 | 80% | 497.5104 | 32.3618 | 44.3396 | 47.6378 | 48.248 | 48.616 | 49.3795 | 51.1691 | 52.131 | 54.0405 | 59.9981 | 54.9191 | 53.8567 | 55.1649 | 57.9459 | 56.0724 | 56.0724 | 56.0724 | 56.0724 | 56.0724 | 56.0724 | 56.0724 | 56.0724 | 56.0724 | 56.0724 | 56.0724 | 56.0724 | 56.0724 | 56.0724 | 56.0724 | 56.0724
75% | 803.6248 | 27.9642 | 39.358 | 42.3176 | 42.9225 | 43.3724 | 44.105 | 45.755 | 46.8599 | 48.2819 | 48.9699 | 49.5713 | 48.2295 | 49.6985 | 51.9275 | 50.2366 | 50.2366 | 50.2366 | 50.2366 | 50.2366 | 50.2366 | 50.2366 | 50.2366 | 50.2366 | 50.2366 | 50.2366 | 50.2366 | 50.2366 | 50.2366 | 50.2366 | 50.2366 | 75% | 803.6248 | 30.3392 | 41.5683 | 44.6605 | 45.2325 | 45.5775 | 46.2933 | 47.971 | 48.8728 | 50.663 | 56.2482 | 51.4866 | 50.4907 | 51.7171 | 54.3243 | 52.5679 | 52.5679 | 52.5679 | 52.5679 | 52.5679 | 52.5679 | 52.5679 | 52.5679 | 52.5679 | 52.5679 | 52.5679 | 52.5679 | 52.5679 | 52.5679 | 52.5679 | 52.5679
70% | 1155.2107 | 26.0999 | 36.7341 | 39.4965 | 40.061 | 40.4809 | 41.1646 | 42.7047 | 43.7359 | 45.0631 | 45.7053 | 46.2665 | 45.0142 | 46.3852 | 48.4657 | 46.8875 | 46.8875 | 46.8875 | 46.8875 | 46.8875 | 46.8875 | 46.8875 | 46.8875 | 46.8875 | 46.8875 | 46.8875 | 46.8875 | 46.8875 | 46.8875 | 46.8875 | 46.8875 | 70% | 1155.2107 | 28.3166 | 38.7971 | 41.6831 | 42.217 | 42.539 | 43.2071 | 44.7729 | 45.6146 | 47.2855 | 52.4983 | 48.0542 | 47.1247 | 48.2693 | 50.7027 | 49.0633 | 49.0633 | 49.0633 | 49.0633 | 49.0633 | 49.0633 | 49.0633 | 49.0633 | 49.0633 | 49.0633 | 49.0633 | 49.0633 | 49.0633 | 49.0633 | 49.0633 | 49.0633
65% | 1553.1596 | 24.2356 | 34.1103 | 36.6753 | 37.1995 | 37.5894 | 38.2243 | 39.6544 | 40.6119 | 41.8443 | 42.4406 | 42.9618 | 41.7989 | 43.072 | 45.0038 | 43.5383 | 43.5383 | 43.5383 | 43.5383 | 43.5383 | 43.5383 | 43.5383 | 43.5383 | 43.5383 | 43.5383 | 43.5383 | 43.5383 | 43.5383 | 43.5383 | 43.5383 | 43.5383 | 65% | 1553.1596 | 26.2939 | 36.0259 | 38.7057 | 39.2015 | 39.5005 | 40.1209 | 41.5749 | 42.3564 | 43.9079 | 48.7485 | 44.6217 | 43.7586 | 44.8215 | 47.0811 | 45.5588 | 45.5588 | 45.5588 | 45.5588 | 45.5588 | 45.5588 | 45.5588 | 45.5588 | 45.5588 | 45.5588 | 45.5588 | 45.5588 | 45.5588 | 45.5588 | 45.5588 | 45.5588
60% | 2026.2996 | 22.3713 | 31.4864 | 33.8541 | 34.338 | 34.6979 | 35.284 | 36.604 | 37.4879 | 38.6255 | 39.176 | 39.657 | 38.5836 | 39.7588 | 41.542 | 40.1892 | 40.1892 | 40.1892 | 40.1892 | 40.1892 | 40.1892 | 40.1892 | 40.1892 | 40.1892 | 40.1892 | 40.1892 | 40.1892 | 40.1892 | 40.1892 | 40.1892 | 40.1892 | 60% | 2026.2996 | 24.2713 | 33.2547 | 35.7284 | 36.186 | 36.462 | 37.0346 | 38.3768 | 39.0982 | 40.5304 | 44.9986 | 41.1893 | 40.3926 | 41.3737 | 43.4595 | 42.0543 | 42.0543 | 42.0543 | 42.0543 | 42.0543 | 42.0543 | 42.0543 | 42.0543 | 42.0543 | 42.0543 | 42.0543 | 42.0543 | 42.0543 | 42.0543 | 42.0543 | 42.0543
55% | 2598.4068 | 20.5071 | 28.8625 | 31.0329 | 31.4765 | 31.8064 | 32.3436 | 33.5537 | 34.3639 | 35.4067 | 35.9113 | 36.3523 | 35.3683 | 36.4455 | 38.0802 | 36.8401 | 36.8401 | 36.8401 | 36.8401 | 36.8401 | 36.8401 | 36.8401 | 36.8401 | 36.8401 | 36.8401 | 36.8401 | 36.8401 | 36.8401 | 36.8401 | 36.8401 | 36.8401 | 55% | 2598.4068 | 22.2487 | 30.4834 | 32.751 | 33.1705 | 33.4235 | 33.9484 | 35.1787 | 35.84 | 37.1529 | 41.2487 | 37.7569 | 37.0265 | 37.9259 | 39.8378 | 38.5498 | 38.5498 | 38.5498 | 38.5498 | 38.5498 | 38.5498 | 38.5498 | 38.5498 | 38.5498 | 38.5498 | 38.5498 | 38.5498 | 38.5498 | 38.5498 | 38.5498 | 38.5498
50% | 3233.5201 | 18.6428 | 26.2387 | 28.2118 | 28.615 | 28.9149 | 29.4033 | 30.5034 | 31.2399 | 32.1879 | 32.6466 | 33.0475 | 32.153 | 33.1323 | 34.6183 | 33.491 | 33.491 | 33.491 | 33.491 | 33.491 | 33.491 | 33.491 | 33.491 | 33.491 | 33.491 | 33.491 | 33.491 | 33.491 | 33.491 | 33.491 | 33.491 | 50% | 3233.5201 | 20.2261 | 27.7122 | 29.7736 | 30.155 | 30.385 | 30.8622 | 31.9807 | 32.5819 | 33.7753 | 37.4988 | 34.3244 | 33.6605 | 34.4781 | 36.2162 | 35.0452 | 35.0452 | 35.0452 | 35.0452 | 35.0452 | 35.0452 | 35.0452 | 35.0452 | 35.0452 | 35.0452 | 35.0452 | 35.0452 | 35.0452 | 35.0452 | 35.0452 | 35.0452
45% | 3775.313 | 16.7785 | 23.6148 | 25.3906 | 25.7535 | 26.0234 | 26.463 | 27.453 | 28.1159 | 28.9691 | 29.382 | 29.7428 | 28.9377 | 29.8191 | 31.1565 | 30.1419 | 30.1419 | 30.1419 | 30.1419 | 30.1419 | 30.1419 | 30.1419 | 30.1419 | 30.1419 | 30.1419 | 30.1419 | 30.1419 | 30.1419 | 30.1419 | 30.1419 | 30.1419 | 45% | 3775.313 | 18.2035 | 24.941 | 26.7963 | 27.1395 | 27.3465 | 27.776 | 28.7826 | 29.3237 | 30.3978 | 33.7489 | 30.892 | 30.2944 | 31.0303 | 32.5946 | 31.5407 | 31.5407 | 31.5407 | 31.5407 | 31.5407 | 31.5407 | 31.5407 | 31.5407 | 31.5407 | 31.5407 | 31.5407 | 31.5407 | 31.5407 | 31.5407 | 31.5407 | 31.5407
40% | 4072.8088 | 14.9142 | 20.9909 | 22.5694 | 22.892 | 23.1319 | 23.5226 | 24.4027 | 24.9919 | 25.7503 | 26.1173 | 26.438 | 25.7224 | 26.5058 | 27.6947 | 26.7928 | 26.7928 | 26.7928 | 26.7928 | 26.7928 | 26.7928 | 26.7928 | 26.7928 | 26.7928 | 26.7928 | 26.7928 | 26.7928 | 26.7928 | 26.7928 | 26.7928 | 26.7928 | 40% | 4072.8088 | 16.1809 | 22.1698 | 23.8189 | 24.124 | 24.308 | 24.6898 | 25.5845 | 26.0655 | 27.0203 | 29.9991 | 27.4595 | 26.9284 | 27.5825 | 28.973 | 28.0362 | 28.0362 | 28.0362 | 28.0362 | 28.0362 | 28.0362 | 28.0362 | 28.0362 | 28.0362 | 28.0362 | 28.0362 | 28.0362 | 28.0362 | 28.0362 | 28.0362 | 28.0362
35% | 4198.821 | 13.0499 | 18.3671 | 19.7482 | 20.0305 | 20.2404 | 20.5823 | 21.3523 | 21.8679 | 22.5315 | 22.8526 | 23.1333 | 22.5071 | 23.1926 | 24.2328 | 23.4437 | 23.4437 | 23.4437 | 23.4437 | 23.4437 | 23.4437 | 23.4437 | 23.4437 | 23.4437 | 23.4437 | 23.4437 | 23.4437 | 23.4437 | 23.4437 | 23.4437 | 23.4437 | 35% | 4198.821 | 14.1583 | 19.3986 | 20.8415 | 21.1085 | 21.2695 | 21.6035 | 22.3865 | 22.8073 | 23.6427 | 26.2492 | 24.0271 | 23.5623 | 24.1347 | 25.3513 | 24.5317 | 24.5317 | 24.5317 | 24.5317 | 24.5317 | 24.5317 | 24.5317 | 24.5317 | 24.5317 | 24.5317 | 24.5317 | 24.5317 | 24.5317 | 24.5317 | 24.5317 | 24.5317
30% | 4271.3374 | 11.1857 | 15.7432 | 16.9271 | 17.169 | 17.3489 | 17.642 | 18.302 | 18.7439 | 19.3127 | 19.588 | 19.8285 | 19.2918 | 19.8794 | 20.771 | 20.0946 | 20.0946 | 20.0946 | 20.0946 | 20.0946 | 20.0946 | 20.0946 | 20.0946 | 20.0946 | 20.0946 | 20.0946 | 20.0946 | 20.0946 | 20.0946 | 20.0946 | 20.0946 | 30% | 4271.3374 | 12.1357 | 16.6273 | 17.8642 | 18.093 | 18.231 | 18.5173 | 19.1884 | 19.5491 | 20.2652 | 22.4993 | 20.5947 | 20.1963 | 20.6868 | 21.7297 | 21.0271 | 21.0271 | 21.0271 | 21.0271 | 21.0271 | 21.0271 | 21.0271 | 21.0271 | 21.0271 | 21.0271 | 21.0271 | 21.0271 | 21.0271 | 21.0271 | 21.0271 | 21.0271
25% | 4321.8611 | 9.3214 | 13.1193 | 14.1059 | 14.3075 | 14.4575 | 14.7017 | 15.2517 | 15.62 | 16.094 | 16.3233 | 16.5238 | 16.0765 | 16.5662 | 17.3092 | 16.7455 | 16.7455 | 16.7455 | 16.7455 | 16.7455 | 16.7455 | 16.7455 | 16.7455 | 16.7455 | 16.7455 | 16.7455 | 16.7455 | 16.7455 | 16.7455 | 16.7455 | 16.7455 | 25% | 4321.8611 | 10.1131 | 13.8561 | 14.8868 | 15.0775 | 15.1925 | 15.4311 | 15.9903 | 16.2909 | 16.8877 | 18.7494 | 17.1622 | 16.8302 | 17.239 | 18.1081 | 17.5226 | 17.5226 | 17.5226 | 17.5226 | 17.5226 | 17.5226 | 17.5226 | 17.5226 | 17.5226 | 17.5226 | 17.5226 | 17.5226 | 17.5226 | 17.5226 | 17.5226 | 17.5226
20% | 4353.067 | 7.4571 | 10.4955 | 11.2847 | 11.446 | 11.566 | 11.7613 | 12.2013 | 12.496 | 12.8752 | 13.0587 | 13.219 | 12.8612 | 13.2529 | 13.8473 | 13.3964 | 13.3964 | 13.3964 | 13.3964 | 13.3964 | 13.3964 | 13.3964 | 13.3964 | 13.3964 | 13.3964 | 13.3964 | 13.3964 | 13.3964 | 13.3964 | 13.3964 | 13.3964 | 20% | 4353.067 | 8.0904 | 11.0849 | 11.9095 | 12.062 | 12.154 | 12.3449 | 12.7923 | 13.0327 | 13.5101 | 14.9995 | 13.7298 | 13.4642 | 13.7912 | 14.4865 | 14.0181 | 14.0181 | 14.0181 | 14.0181 | 14.0181 | 14.0181 | 14.0181 | 14.0181 | 14.0181 | 14.0181 | 14.0181 | 14.0181 | 14.0181 | 14.0181 | 14.0181 | 14.0181
15% | 4369.4129 | 5.5928 | 7.8716 | 8.4635 | 8.5845 | 8.6745 | 8.821 | 9.151 | 9.372 | 9.6564 | 9.794 | 9.9143 | 9.6459 | 9.9397 | 10.3855 | 10.0473 | 10.0473 | 10.0473 | 10.0473 | 10.0473 | 10.0473 | 10.0473 | 10.0473 | 10.0473 | 10.0473 | 10.0473 | 10.0473 | 10.0473 | 10.0473 | 10.0473 | 10.0473 | 15% | 4369.4129 | 6.0678 | 8.3137 | 8.9321 | 9.0465 | 9.1155 | 9.2587 | 9.5942 | 9.7746 | 10.1326 | 11.2496 | 10.2973 | 10.0981 | 10.3434 | 10.8649 | 10.5136 | 10.5136 | 10.5136 | 10.5136 | 10.5136 | 10.5136 | 10.5136 | 10.5136 | 10.5136 | 10.5136 | 10.5136 | 10.5136 | 10.5136 | 10.5136 | 10.5136 | 10.5136
10% | 4378.6261 | 3.7286 | 5.2477 | 5.6424 | 5.723 | 5.783 | 5.8807 | 6.1007 | 6.248 | 6.4376 | 6.5293 | 6.6095 | 6.4306 | 6.6265 | 6.9237 | 6.6982 | 6.6982 | 6.6982 | 6.6982 | 6.6982 | 6.6982 | 6.6982 | 6.6982 | 6.6982 | 6.6982 | 6.6982 | 6.6982 | 6.6982 | 6.6982 | 6.6982 | 6.6982 | 10% | 4378.6261 | 4.0452 | 5.5424 | 5.9547 | 6.031 | 6.077 | 6.1724 | 6.3961 | 6.5164 | 6.7551 | 7.4998 | 6.8649 | 6.7321 | 6.8956 | 7.2432 | 7.009 | 7.009 | 7.009 | 7.009 | 7.009 | 7.009 | 7.009 | 7.009 | 7.009 | 7.009 | 7.009 | 7.009 | 7.009 | 7.009 | 7.009 | 7.009
5% | 4391.7028 | 1.8643 | 2.6239 | 2.8212 | 2.8615 | 2.8915 | 2.9403 | 3.0503 | 3.124 | 3.2188 | 3.2647 | 3.3048 | 3.2153 | 3.3132 | 3.4618 | 3.3491 | 3.3491 | 3.3491 | 3.3491 | 3.3491 | 3.3491 | 3.3491 | 3.3491 | 3.3491 | 3.3491 | 3.3491 | 3.3491 | 3.3491 | 3.3491 | 3.3491 | 3.3491 | 5% | 4391.7028 | 2.0226 | 2.7712 | 2.9774 | 3.0155 | 3.0385 | 3.0862 | 3.1981 | 3.2582 | 3.3775 | 3.7499 | 3.4324 | 3.366 | 3.4478 | 3.6216 | 3.5045 | 3.5045 | 3.5045 | 3.5045 | 3.5045 | 3.5045 | 3.5045 | 3.5045 | 3.5045 | 3.5045 | 3.5045 | 3.5045 | 3.5045 | 3.5045 | 3.5045 | 3.5045
9.992e-14% | 4391.7028 | 3.7256e-14 | 5.2435e-14 | 5.6378e-14 | 5.7184e-14 | 5.7784e-14 | 5.876e-14 | 6.0958e-14 | 6.243e-14 | 6.4324e-14 | 6.5241e-14 | 6.6042e-14 | 6.4255e-14 | 6.6212e-14 | 6.9181e-14 | 6.6929e-14 | 6.6929e-14 | 6.6929e-14 | 6.6929e-14 | 6.6929e-14 | 6.6929e-14 | 6.6929e-14 | 6.6929e-14 | 6.6929e-14 | 6.6929e-14 | 6.6929e-14 | 6.6929e-14 | 6.6929e-14 | 6.6929e-14 | 6.6929e-14 | 6.6929e-14 | 9.992e-14% | 4391.7028 | 4.042e-14 | 5.538e-14 | 5.95e-14 | 6.0262e-14 | 6.0721e-14 | 6.1675e-14 | 6.391e-14 | 6.5112e-14 | 6.7497e-14 | 7.4938e-14 | 6.8594e-14 | 6.7267e-14 | 6.8901e-14 | 7.2375e-14 | 7.0034e-14 | 7.0034e-14 | 7.0034e-14 | 7.0034e-14 | 7.0034e-14 | 7.0034e-14 | 7.0034e-14 | 7.0034e-14 | 7.0034e-14 | 7.0034e-14 | 7.0034e-14 | 7.0034e-14 | 7.0034e-14 | 7.0034e-14 | 7.0034e-14 | 7.0034e-14
Summer Season | [31 empty] | Summer Season
P50 | [31 empty] | P10
% of MD | Summer - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Summer - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 43.4165 | 57.9607 | 61.9469 | 61.8514 | 61.848 | 62.3112 | 62.7274 | 63.7977 | 64.5392 | 64.8781 | 65.27 | 65.6215 | 66.4378 | 67.3392 | 67.3661 | 67.3661 | 67.3661 | 67.3661 | 67.3661 | 67.3661 | 67.3661 | 67.3661 | 67.3661 | 67.3661 | 67.3661 | 67.3661 | 67.3661 | 67.3661 | 67.3661 | 67.3661 | 100% | 0 | 49.2826 | 63.8604 | 67.6787 | 67.4524 | 67.4725 | 67.8662 | 68.9015 | 69.5963 | 70.2755 | 71.0696 | 71.8065 | 72.521 | 72.6044 | 73.438 | 72.8097 | 72.8097 | 72.8097 | 72.8097 | 72.8097 | 72.8097 | 72.8097 | 72.8097 | 72.8097 | 72.8097 | 72.8097 | 72.8097 | 72.8097 | 72.8097 | 72.8097 | 72.8097
99% | 0 | 42.9824 | 57.3811 | 61.3274 | 61.2329 | 61.2296 | 61.688 | 62.1001 | 63.1597 | 63.8938 | 64.2293 | 64.6173 | 64.9653 | 65.7734 | 66.6658 | 66.6924 | 66.6924 | 66.6924 | 66.6924 | 66.6924 | 66.6924 | 66.6924 | 66.6924 | 66.6924 | 66.6924 | 66.6924 | 66.6924 | 66.6924 | 66.6924 | 66.6924 | 66.6924 | 99% | 1.5127 | 48.7898 | 63.2218 | 67.0019 | 66.7779 | 66.7978 | 67.1876 | 68.2125 | 68.9003 | 69.5728 | 70.3589 | 71.0884 | 71.7958 | 71.8784 | 72.7037 | 72.0816 | 72.0816 | 72.0816 | 72.0816 | 72.0816 | 72.0816 | 72.0816 | 72.0816 | 72.0816 | 72.0816 | 72.0816 | 72.0816 | 72.0816 | 72.0816 | 72.0816 | 72.0816
98% | 0 | 42.5482 | 56.8015 | 60.7079 | 60.6144 | 60.6111 | 61.0649 | 61.4729 | 62.5217 | 63.2484 | 63.5806 | 63.9646 | 64.3091 | 65.109 | 65.9924 | 66.0187 | 66.0187 | 66.0187 | 66.0187 | 66.0187 | 66.0187 | 66.0187 | 66.0187 | 66.0187 | 66.0187 | 66.0187 | 66.0187 | 66.0187 | 66.0187 | 66.0187 | 66.0187 | 98% | 2.269 | 48.297 | 62.5832 | 66.3251 | 66.1033 | 66.1231 | 66.5089 | 67.5235 | 68.2044 | 68.87 | 69.6482 | 70.3703 | 71.0706 | 71.1523 | 71.9693 | 71.3535 | 71.3535 | 71.3535 | 71.3535 | 71.3535 | 71.3535 | 71.3535 | 71.3535 | 71.3535 | 71.3535 | 71.3535 | 71.3535 | 71.3535 | 71.3535 | 71.3535 | 71.3535
97% | 0.37816 | 42.114 | 56.2219 | 60.0885 | 59.9959 | 59.9926 | 60.4418 | 60.8456 | 61.8837 | 62.603 | 62.9318 | 63.3119 | 63.6529 | 64.4446 | 65.319 | 65.3451 | 65.3451 | 65.3451 | 65.3451 | 65.3451 | 65.3451 | 65.3451 | 65.3451 | 65.3451 | 65.3451 | 65.3451 | 65.3451 | 65.3451 | 65.3451 | 65.3451 | 65.3451 | 97% | 3.7816 | 47.8041 | 61.9446 | 65.6483 | 65.4288 | 65.4483 | 65.8302 | 66.8345 | 67.5084 | 68.1673 | 68.9375 | 69.6523 | 70.3454 | 70.4263 | 71.2349 | 70.6254 | 70.6254 | 70.6254 | 70.6254 | 70.6254 | 70.6254 | 70.6254 | 70.6254 | 70.6254 | 70.6254 | 70.6254 | 70.6254 | 70.6254 | 70.6254 | 70.6254 | 70.6254
95% | 2.269 | 41.2457 | 55.0627 | 58.8495 | 58.7589 | 58.7556 | 59.1956 | 59.591 | 60.6078 | 61.3122 | 61.6342 | 62.0065 | 62.3404 | 63.1159 | 63.9723 | 63.9978 | 63.9978 | 63.9978 | 63.9978 | 63.9978 | 63.9978 | 63.9978 | 63.9978 | 63.9978 | 63.9978 | 63.9978 | 63.9978 | 63.9978 | 63.9978 | 63.9978 | 63.9978 | 95% | 6.0506 | 46.8185 | 60.6674 | 64.2948 | 64.0798 | 64.0989 | 64.4729 | 65.4565 | 66.1165 | 66.7618 | 67.5161 | 68.2162 | 68.895 | 68.9742 | 69.7661 | 69.1692 | 69.1692 | 69.1692 | 69.1692 | 69.1692 | 69.1692 | 69.1692 | 69.1692 | 69.1692 | 69.1692 | 69.1692 | 69.1692 | 69.1692 | 69.1692 | 69.1692 | 69.1692
90% | 5.6725 | 39.0749 | 52.1646 | 55.7522 | 55.6663 | 55.6632 | 56.08 | 56.4547 | 57.4179 | 58.0852 | 58.3903 | 58.743 | 59.0594 | 59.794 | 60.6053 | 60.6295 | 60.6295 | 60.6295 | 60.6295 | 60.6295 | 60.6295 | 60.6295 | 60.6295 | 60.6295 | 60.6295 | 60.6295 | 60.6295 | 60.6295 | 60.6295 | 60.6295 | 60.6295 | 90% | 16.2611 | 44.3543 | 57.4744 | 60.9108 | 60.7072 | 60.7253 | 61.0796 | 62.0114 | 62.6367 | 63.248 | 63.9626 | 64.6258 | 65.2689 | 65.344 | 66.0942 | 65.5287 | 65.5287 | 65.5287 | 65.5287 | 65.5287 | 65.5287 | 65.5287 | 65.5287 | 65.5287 | 65.5287 | 65.5287 | 65.5287 | 65.5287 | 65.5287 | 65.5287 | 65.5287
85% | 15.8829 | 36.9041 | 49.2666 | 52.6548 | 52.5737 | 52.5708 | 52.9645 | 53.3183 | 54.228 | 54.8583 | 55.1464 | 55.4795 | 55.7783 | 56.4721 | 57.2383 | 57.2612 | 57.2612 | 57.2612 | 57.2612 | 57.2612 | 57.2612 | 57.2612 | 57.2612 | 57.2612 | 57.2612 | 57.2612 | 57.2612 | 57.2612 | 57.2612 | 57.2612 | 57.2612 | 85% | 26.4715 | 41.8902 | 54.2813 | 57.5269 | 57.3345 | 57.3516 | 57.6863 | 58.5663 | 59.1569 | 59.7342 | 60.4091 | 61.0355 | 61.6429 | 61.7138 | 62.4223 | 61.8883 | 61.8883 | 61.8883 | 61.8883 | 61.8883 | 61.8883 | 61.8883 | 61.8883 | 61.8883 | 61.8883 | 61.8883 | 61.8883 | 61.8883 | 61.8883 | 61.8883 | 61.8883
80% | 31.0095 | 34.7332 | 46.3686 | 49.5575 | 49.4811 | 49.4784 | 49.8489 | 50.1819 | 51.0381 | 51.6313 | 51.9025 | 52.216 | 52.4972 | 53.1502 | 53.8714 | 53.8929 | 53.8929 | 53.8929 | 53.8929 | 53.8929 | 53.8929 | 53.8929 | 53.8929 | 53.8929 | 53.8929 | 53.8929 | 53.8929 | 53.8929 | 53.8929 | 53.8929 | 53.8929 | 80% | 34.0348 | 39.4261 | 51.0883 | 54.143 | 53.9619 | 53.978 | 54.293 | 55.1212 | 55.677 | 56.2204 | 56.8556 | 57.4452 | 58.0168 | 58.0835 | 58.7504 | 58.2478 | 58.2478 | 58.2478 | 58.2478 | 58.2478 | 58.2478 | 58.2478 | 58.2478 | 58.2478 | 58.2478 | 58.2478 | 58.2478 | 58.2478 | 58.2478 | 58.2478 | 58.2478
75% | 72.9857 | 32.5624 | 43.4705 | 46.4601 | 46.3886 | 46.386 | 46.7334 | 47.0456 | 47.8482 | 48.4044 | 48.6586 | 48.9525 | 49.2161 | 49.8283 | 50.5044 | 50.5246 | 50.5246 | 50.5246 | 50.5246 | 50.5246 | 50.5246 | 50.5246 | 50.5246 | 50.5246 | 50.5246 | 50.5246 | 50.5246 | 50.5246 | 50.5246 | 50.5246 | 50.5246 | 75% | 48.405 | 36.962 | 47.8953 | 50.759 | 50.5893 | 50.6044 | 50.8997 | 51.6762 | 52.1972 | 52.7066 | 53.3022 | 53.8549 | 54.3908 | 54.4533 | 55.0785 | 54.6073 | 54.6073 | 54.6073 | 54.6073 | 54.6073 | 54.6073 | 54.6073 | 54.6073 | 54.6073 | 54.6073 | 54.6073 | 54.6073 | 54.6073 | 54.6073 | 54.6073 | 54.6073
70% | 150.5094 | 30.3916 | 40.5725 | 43.3628 | 43.296 | 43.2936 | 43.6178 | 43.9092 | 44.6584 | 45.1774 | 45.4147 | 45.689 | 45.9351 | 46.5064 | 47.1375 | 47.1562 | 47.1562 | 47.1562 | 47.1562 | 47.1562 | 47.1562 | 47.1562 | 47.1562 | 47.1562 | 47.1562 | 47.1562 | 47.1562 | 47.1562 | 47.1562 | 47.1562 | 47.1562 | 70% | 76.3892 | 34.4978 | 44.7023 | 47.3751 | 47.2167 | 47.2308 | 47.5064 | 48.2311 | 48.7174 | 49.1929 | 49.7487 | 50.2645 | 50.7647 | 50.8231 | 51.4066 | 50.9668 | 50.9668 | 50.9668 | 50.9668 | 50.9668 | 50.9668 | 50.9668 | 50.9668 | 50.9668 | 50.9668 | 50.9668 | 50.9668 | 50.9668 | 50.9668 | 50.9668 | 50.9668
65% | 359.6342 | 28.2208 | 37.6745 | 40.2655 | 40.2034 | 40.2012 | 40.5022 | 40.7728 | 41.4685 | 41.9505 | 42.1708 | 42.4255 | 42.654 | 43.1846 | 43.7705 | 43.7879 | 43.7879 | 43.7879 | 43.7879 | 43.7879 | 43.7879 | 43.7879 | 43.7879 | 43.7879 | 43.7879 | 43.7879 | 43.7879 | 43.7879 | 43.7879 | 43.7879 | 43.7879 | 65% | 114.2056 | 32.0337 | 41.5093 | 43.9912 | 43.8441 | 43.8571 | 44.113 | 44.786 | 45.2376 | 45.6791 | 46.1952 | 46.6742 | 47.1387 | 47.1929 | 47.7347 | 47.3263 | 47.3263 | 47.3263 | 47.3263 | 47.3263 | 47.3263 | 47.3263 | 47.3263 | 47.3263 | 47.3263 | 47.3263 | 47.3263 | 47.3263 | 47.3263 | 47.3263 | 47.3263
60% | 689.7717 | 26.0499 | 34.7764 | 37.1681 | 37.1109 | 37.1088 | 37.3867 | 37.6364 | 38.2786 | 38.7235 | 38.9269 | 39.162 | 39.3729 | 39.8627 | 40.4035 | 40.4196 | 40.4196 | 40.4196 | 40.4196 | 40.4196 | 40.4196 | 40.4196 | 40.4196 | 40.4196 | 40.4196 | 40.4196 | 40.4196 | 40.4196 | 40.4196 | 40.4196 | 40.4196 | 60% | 178.1154 | 29.5696 | 38.3162 | 40.6072 | 40.4714 | 40.4835 | 40.7197 | 41.3409 | 41.7578 | 42.1653 | 42.6417 | 43.0839 | 43.5126 | 43.5626 | 44.0628 | 43.6858 | 43.6858 | 43.6858 | 43.6858 | 43.6858 | 43.6858 | 43.6858 | 43.6858 | 43.6858 | 43.6858 | 43.6858 | 43.6858 | 43.6858 | 43.6858 | 43.6858 | 43.6858
55% | 1095.5419 | 23.8791 | 31.8784 | 34.0708 | 34.0183 | 34.0164 | 34.2711 | 34.5001 | 35.0887 | 35.4965 | 35.683 | 35.8985 | 36.0918 | 36.5408 | 37.0366 | 37.0513 | 37.0513 | 37.0513 | 37.0513 | 37.0513 | 37.0513 | 37.0513 | 37.0513 | 37.0513 | 37.0513 | 37.0513 | 37.0513 | 37.0513 | 37.0513 | 37.0513 | 37.0513 | 55% | 311.6074 | 27.1054 | 35.1232 | 37.2233 | 37.0988 | 37.1099 | 37.3264 | 37.8958 | 38.278 | 38.6515 | 39.0883 | 39.4936 | 39.8866 | 39.9324 | 40.3909 | 40.0453 | 40.0453 | 40.0453 | 40.0453 | 40.0453 | 40.0453 | 40.0453 | 40.0453 | 40.0453 | 40.0453 | 40.0453 | 40.0453 | 40.0453 | 40.0453 | 40.0453 | 40.0453
50% | 1666.1918 | 21.7083 | 28.9804 | 30.9734 | 30.9257 | 30.924 | 31.1556 | 31.3637 | 31.8988 | 32.2696 | 32.4391 | 32.635 | 32.8108 | 33.2189 | 33.6696 | 33.683 | 33.683 | 33.683 | 33.683 | 33.683 | 33.683 | 33.683 | 33.683 | 33.683 | 33.683 | 33.683 | 33.683 | 33.683 | 33.683 | 33.683 | 33.683 | 50% | 636.0723 | 24.6413 | 31.9302 | 33.8394 | 33.7262 | 33.7363 | 33.9331 | 34.4508 | 34.7982 | 35.1378 | 35.5348 | 35.9032 | 36.2605 | 36.3022 | 36.719 | 36.4049 | 36.4049 | 36.4049 | 36.4049 | 36.4049 | 36.4049 | 36.4049 | 36.4049 | 36.4049 | 36.4049 | 36.4049 | 36.4049 | 36.4049 | 36.4049 | 36.4049 | 36.4049
45% | 2506.0947 | 19.5374 | 26.0823 | 27.8761 | 27.8331 | 27.8316 | 28.04 | 28.2273 | 28.7089 | 29.0426 | 29.1952 | 29.3715 | 29.5297 | 29.897 | 30.3026 | 30.3147 | 30.3147 | 30.3147 | 30.3147 | 30.3147 | 30.3147 | 30.3147 | 30.3147 | 30.3147 | 30.3147 | 30.3147 | 30.3147 | 30.3147 | 30.3147 | 30.3147 | 30.3147 | 45% | 1179.4944 | 22.1772 | 28.7372 | 30.4554 | 30.3536 | 30.3626 | 30.5398 | 31.0057 | 31.3183 | 31.624 | 31.9813 | 32.3129 | 32.6345 | 32.672 | 33.0471 | 32.7644 | 32.7644 | 32.7644 | 32.7644 | 32.7644 | 32.7644 | 32.7644 | 32.7644 | 32.7644 | 32.7644 | 32.7644 | 32.7644 | 32.7644 | 32.7644 | 32.7644 | 32.7644
40% | 3164.4787 | 17.3666 | 23.1843 | 24.7787 | 24.7406 | 24.7392 | 24.9245 | 25.091 | 25.5191 | 25.8157 | 25.9513 | 26.108 | 26.2486 | 26.5751 | 26.9357 | 26.9464 | 26.9464 | 26.9464 | 26.9464 | 26.9464 | 26.9464 | 26.9464 | 26.9464 | 26.9464 | 26.9464 | 26.9464 | 26.9464 | 26.9464 | 26.9464 | 26.9464 | 26.9464 | 40% | 1808.3816 | 19.713 | 25.5442 | 27.0715 | 26.981 | 26.989 | 27.1465 | 27.5606 | 27.8385 | 28.1102 | 28.4278 | 28.7226 | 29.0084 | 29.0418 | 29.3752 | 29.1239 | 29.1239 | 29.1239 | 29.1239 | 29.1239 | 29.1239 | 29.1239 | 29.1239 | 29.1239 | 29.1239 | 29.1239 | 29.1239 | 29.1239 | 29.1239 | 29.1239 | 29.1239
35% | 3551.3408 | 15.1958 | 20.2862 | 21.6814 | 21.648 | 21.6468 | 21.8089 | 21.9546 | 22.3292 | 22.5887 | 22.7073 | 22.8445 | 22.9675 | 23.2532 | 23.5687 | 23.5781 | 23.5781 | 23.5781 | 23.5781 | 23.5781 | 23.5781 | 23.5781 | 23.5781 | 23.5781 | 23.5781 | 23.5781 | 23.5781 | 23.5781 | 23.5781 | 23.5781 | 23.5781 | 35% | 2779.1293 | 17.2489 | 22.3511 | 23.6875 | 23.6083 | 23.6154 | 23.7532 | 24.1155 | 24.3587 | 24.5964 | 24.8743 | 25.1323 | 25.3824 | 25.4115 | 25.7033 | 25.4834 | 25.4834 | 25.4834 | 25.4834 | 25.4834 | 25.4834 | 25.4834 | 25.4834 | 25.4834 | 25.4834 | 25.4834 | 25.4834 | 25.4834 | 25.4834 | 25.4834 | 25.4834
30% | 3758.953 | 13.025 | 17.3882 | 18.5841 | 18.5554 | 18.5544 | 18.6933 | 18.8182 | 19.1393 | 19.3617 | 19.4634 | 19.581 | 19.6865 | 19.9313 | 20.2018 | 20.2098 | 20.2098 | 20.2098 | 20.2098 | 20.2098 | 20.2098 | 20.2098 | 20.2098 | 20.2098 | 20.2098 | 20.2098 | 20.2098 | 20.2098 | 20.2098 | 20.2098 | 20.2098 | 30% | 3814.165 | 14.7848 | 19.1581 | 20.3036 | 20.2357 | 20.2418 | 20.3599 | 20.6705 | 20.8789 | 21.0827 | 21.3209 | 21.5419 | 21.7563 | 21.7813 | 22.0314 | 21.8429 | 21.8429 | 21.8429 | 21.8429 | 21.8429 | 21.8429 | 21.8429 | 21.8429 | 21.8429 | 21.8429 | 21.8429 | 21.8429 | 21.8429 | 21.8429 | 21.8429 | 21.8429
25% | 3926.4798 | 10.8541 | 14.4902 | 15.4867 | 15.4629 | 15.462 | 15.5778 | 15.6819 | 15.9494 | 16.1348 | 16.2195 | 16.3175 | 16.4054 | 16.6094 | 16.8348 | 16.8415 | 16.8415 | 16.8415 | 16.8415 | 16.8415 | 16.8415 | 16.8415 | 16.8415 | 16.8415 | 16.8415 | 16.8415 | 16.8415 | 16.8415 | 16.8415 | 16.8415 | 16.8415 | 25% | 4166.9923 | 12.3207 | 15.9651 | 16.9197 | 16.8631 | 16.8681 | 16.9666 | 17.2254 | 17.3991 | 17.5689 | 17.7674 | 17.9516 | 18.1303 | 18.1511 | 18.3595 | 18.2024 | 18.2024 | 18.2024 | 18.2024 | 18.2024 | 18.2024 | 18.2024 | 18.2024 | 18.2024 | 18.2024 | 18.2024 | 18.2024 | 18.2024 | 18.2024 | 18.2024 | 18.2024
20% | 4050.5177 | 8.6833 | 11.5921 | 12.3894 | 12.3703 | 12.3696 | 12.4622 | 12.5455 | 12.7595 | 12.9078 | 12.9756 | 13.054 | 13.1243 | 13.2876 | 13.4678 | 13.4732 | 13.4732 | 13.4732 | 13.4732 | 13.4732 | 13.4732 | 13.4732 | 13.4732 | 13.4732 | 13.4732 | 13.4732 | 13.4732 | 13.4732 | 13.4732 | 13.4732 | 13.4732 | 20% | 4282.7105 | 9.8565 | 12.7721 | 13.5357 | 13.4905 | 13.4945 | 13.5732 | 13.7803 | 13.9193 | 14.0551 | 14.2139 | 14.3613 | 14.5042 | 14.5209 | 14.6876 | 14.5619 | 14.5619 | 14.5619 | 14.5619 | 14.5619 | 14.5619 | 14.5619 | 14.5619 | 14.5619 | 14.5619 | 14.5619 | 14.5619 | 14.5619 | 14.5619 | 14.5619 | 14.5619
15% | 4152.622 | 6.5125 | 8.6941 | 9.292 | 9.2777 | 9.2772 | 9.3467 | 9.4091 | 9.5696 | 9.6809 | 9.7317 | 9.7905 | 9.8432 | 9.9657 | 10.1009 | 10.1049 | 10.1049 | 10.1049 | 10.1049 | 10.1049 | 10.1049 | 10.1049 | 10.1049 | 10.1049 | 10.1049 | 10.1049 | 10.1049 | 10.1049 | 10.1049 | 10.1049 | 10.1049 | 15% | 4364.7722 | 7.3924 | 9.5791 | 10.1518 | 10.1179 | 10.1209 | 10.1799 | 10.3352 | 10.4394 | 10.5413 | 10.6604 | 10.771 | 10.8782 | 10.8907 | 11.0157 | 10.9215 | 10.9215 | 10.9215 | 10.9215 | 10.9215 | 10.9215 | 10.9215 | 10.9215 | 10.9215 | 10.9215 | 10.9215 | 10.9215 | 10.9215 | 10.9215 | 10.9215 | 10.9215
10% | 4248.2976 | 4.3417 | 5.7961 | 6.1947 | 6.1851 | 6.1848 | 6.2311 | 6.2727 | 6.3798 | 6.4539 | 6.4878 | 6.527 | 6.5622 | 6.6438 | 6.7339 | 6.7366 | 6.7366 | 6.7366 | 6.7366 | 6.7366 | 6.7366 | 6.7366 | 6.7366 | 6.7366 | 6.7366 | 6.7366 | 6.7366 | 6.7366 | 6.7366 | 6.7366 | 6.7366 | 10% | 4391.6218 | 4.9283 | 6.386 | 6.7679 | 6.7452 | 6.7473 | 6.7866 | 6.8902 | 6.9596 | 7.0276 | 7.107 | 7.1806 | 7.2521 | 7.2604 | 7.3438 | 7.281 | 7.281 | 7.281 | 7.281 | 7.281 | 7.281 | 7.281 | 7.281 | 7.281 | 7.281 | 7.281 | 7.281 | 7.281 | 7.281 | 7.281 | 7.281
5% | 4361.7469 | 2.1708 | 2.898 | 3.0973 | 3.0926 | 3.0924 | 3.1156 | 3.1364 | 3.1899 | 3.227 | 3.2439 | 3.2635 | 3.2811 | 3.3219 | 3.367 | 3.3683 | 3.3683 | 3.3683 | 3.3683 | 3.3683 | 3.3683 | 3.3683 | 3.3683 | 3.3683 | 3.3683 | 3.3683 | 3.3683 | 3.3683 | 3.3683 | 3.3683 | 3.3683 | 5% | 4391.6218 | 2.4641 | 3.193 | 3.3839 | 3.3726 | 3.3736 | 3.3933 | 3.4451 | 3.4798 | 3.5138 | 3.5535 | 3.5903 | 3.6261 | 3.6302 | 3.6719 | 3.6405 | 3.6405 | 3.6405 | 3.6405 | 3.6405 | 3.6405 | 3.6405 | 3.6405 | 3.6405 | 3.6405 | 3.6405 | 3.6405 | 3.6405 | 3.6405 | 3.6405 | 3.6405
9.992e-14% | 4391.6218 | 4.3382e-14 | 5.7914e-14 | 6.1897e-14 | 6.1802e-14 | 6.1799e-14 | 6.2261e-14 | 6.2677e-14 | 6.3747e-14 | 6.4488e-14 | 6.4826e-14 | 6.5218e-14 | 6.5569e-14 | 6.6385e-14 | 6.7285e-14 | 6.7312e-14 | 6.7312e-14 | 6.7312e-14 | 6.7312e-14 | 6.7312e-14 | 6.7312e-14 | 6.7312e-14 | 6.7312e-14 | 6.7312e-14 | 6.7312e-14 | 6.7312e-14 | 6.7312e-14 | 6.7312e-14 | 6.7312e-14 | 6.7312e-14 | 6.7312e-14 | 9.992e-14% | 4391.6218 | 4.9243e-14 | 6.3809e-14 | 6.7625e-14 | 6.7398e-14 | 6.7419e-14 | 6.7812e-14 | 6.8846e-14 | 6.9541e-14 | 7.0219e-14 | 7.1013e-14 | 7.1749e-14 | 7.2463e-14 | 7.2546e-14 | 7.3379e-14 | 7.2752e-14 | 7.2752e-14 | 7.2752e-14 | 7.2752e-14 | 7.2752e-14 | 7.2752e-14 | 7.2752e-14 | 7.2752e-14 | 7.2752e-14 | 7.2752e-14 | 7.2752e-14 | 7.2752e-14 | 7.2752e-14 | 7.2752e-14 | 7.2752e-14 | 7.2752e-14
Option 7
Winter Season | [31 empty] | Winter Season
P50 | [31 empty] | P10
% of MD | Winter - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Winter - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 45.0311 | 62.4376 | 66.9594 | 67.7285 | 68.3267 | 69.3603 | 71.7146 | 73.2888 | 75.2849 | 76.3199 | 77.2291 | 75.5455 | 77.5138 | 80.6095 | 78.2564 | 78.2564 | 78.2564 | 78.2564 | 78.2564 | 78.2564 | 78.2564 | 78.2564 | 78.2564 | 78.2564 | 78.2564 | 78.2564 | 78.2564 | 78.2564 | 78.2564 | 78.2564 | 100% | 0 | 48.1978 | 65.3847 | 70.0831 | 70.8084 | 71.267 | 72.2781 | 74.6693 | 75.9727 | 78.4597 | 86.0243 | 79.7829 | 78.5605 | 80.2054 | 83.8053 | 81.3648 | 81.3648 | 81.3648 | 81.3648 | 81.3648 | 81.3648 | 81.3648 | 81.3648 | 81.3648 | 81.3648 | 81.3648 | 81.3648 | 81.3648 | 81.3648 | 81.3648 | 81.3648
99% | 1.486 | 44.5808 | 61.8132 | 66.2898 | 67.0512 | 67.6435 | 68.6667 | 70.9975 | 72.5559 | 74.532 | 75.5567 | 76.4569 | 74.7901 | 76.7387 | 79.8034 | 77.4739 | 77.4739 | 77.4739 | 77.4739 | 77.4739 | 77.4739 | 77.4739 | 77.4739 | 77.4739 | 77.4739 | 77.4739 | 77.4739 | 77.4739 | 77.4739 | 77.4739 | 77.4739 | 99% | 1.486 | 47.7158 | 64.7309 | 69.3823 | 70.1003 | 70.5543 | 71.5553 | 73.9226 | 75.2129 | 77.6751 | 85.1641 | 78.9851 | 77.7749 | 79.4033 | 82.9672 | 80.5512 | 80.5512 | 80.5512 | 80.5512 | 80.5512 | 80.5512 | 80.5512 | 80.5512 | 80.5512 | 80.5512 | 80.5512 | 80.5512 | 80.5512 | 80.5512 | 80.5512 | 80.5512
98% | 3.2692 | 44.1305 | 61.1889 | 65.6202 | 66.3739 | 66.9602 | 67.9731 | 70.2804 | 71.823 | 73.7792 | 74.7935 | 75.6846 | 74.0346 | 75.9636 | 78.9973 | 76.6913 | 76.6913 | 76.6913 | 76.6913 | 76.6913 | 76.6913 | 76.6913 | 76.6913 | 76.6913 | 76.6913 | 76.6913 | 76.6913 | 76.6913 | 76.6913 | 76.6913 | 76.6913 | 98% | 3.2692 | 47.2338 | 64.0771 | 68.6815 | 69.3922 | 69.8416 | 70.8325 | 73.1759 | 74.4532 | 76.8905 | 84.3038 | 78.1873 | 76.9893 | 78.6013 | 82.1292 | 79.7375 | 79.7375 | 79.7375 | 79.7375 | 79.7375 | 79.7375 | 79.7375 | 79.7375 | 79.7375 | 79.7375 | 79.7375 | 79.7375 | 79.7375 | 79.7375 | 79.7375 | 79.7375
97% | 6.8356 | 43.6802 | 60.5645 | 64.9506 | 65.6966 | 66.2769 | 67.2795 | 69.5632 | 71.0901 | 73.0263 | 74.0303 | 74.9123 | 73.2792 | 75.1884 | 78.1912 | 75.9087 | 75.9087 | 75.9087 | 75.9087 | 75.9087 | 75.9087 | 75.9087 | 75.9087 | 75.9087 | 75.9087 | 75.9087 | 75.9087 | 75.9087 | 75.9087 | 75.9087 | 75.9087 | 97% | 6.8356 | 46.7518 | 63.4232 | 67.9806 | 68.6841 | 69.129 | 70.1097 | 72.4292 | 73.6935 | 76.1059 | 83.4436 | 77.3894 | 76.2037 | 77.7992 | 81.2911 | 78.9239 | 78.9239 | 78.9239 | 78.9239 | 78.9239 | 78.9239 | 78.9239 | 78.9239 | 78.9239 | 78.9239 | 78.9239 | 78.9239 | 78.9239 | 78.9239 | 78.9239 | 78.9239
95% | 17.5347 | 42.7796 | 59.3157 | 63.6114 | 64.342 | 64.9104 | 65.8923 | 68.1289 | 69.6243 | 71.5207 | 72.5039 | 73.3677 | 71.7683 | 73.6382 | 76.579 | 74.3436 | 74.3436 | 74.3436 | 74.3436 | 74.3436 | 74.3436 | 74.3436 | 74.3436 | 74.3436 | 74.3436 | 74.3436 | 74.3436 | 74.3436 | 74.3436 | 74.3436 | 74.3436 | 95% | 17.5347 | 45.7879 | 62.1155 | 66.579 | 67.268 | 67.7036 | 68.6642 | 70.9358 | 72.174 | 74.5368 | 81.7231 | 75.7938 | 74.6325 | 76.1951 | 79.615 | 77.2966 | 77.2966 | 77.2966 | 77.2966 | 77.2966 | 77.2966 | 77.2966 | 77.2966 | 77.2966 | 77.2966 | 77.2966 | 77.2966 | 77.2966 | 77.2966 | 77.2966 | 77.2966
90% | 78.7576 | 40.528 | 56.1939 | 60.2634 | 60.9556 | 61.4941 | 62.4243 | 64.5432 | 65.9599 | 67.7564 | 68.6879 | 69.5062 | 67.991 | 69.7625 | 72.5486 | 70.4308 | 70.4308 | 70.4308 | 70.4308 | 70.4308 | 70.4308 | 70.4308 | 70.4308 | 70.4308 | 70.4308 | 70.4308 | 70.4308 | 70.4308 | 70.4308 | 70.4308 | 70.4308 | 90% | 78.7576 | 43.378 | 58.8463 | 63.0748 | 63.7275 | 64.1403 | 65.0503 | 67.2023 | 68.3754 | 70.6138 | 77.4219 | 71.8046 | 70.7045 | 72.1848 | 75.4247 | 73.2283 | 73.2283 | 73.2283 | 73.2283 | 73.2283 | 73.2283 | 73.2283 | 73.2283 | 73.2283 | 73.2283 | 73.2283 | 73.2283 | 73.2283 | 73.2283 | 73.2283 | 73.2283
85% | 236.8672 | 38.2764 | 53.072 | 56.9155 | 57.5692 | 58.0777 | 58.9563 | 60.9575 | 62.2954 | 63.9922 | 64.8719 | 65.6448 | 64.2137 | 65.8868 | 68.5181 | 66.518 | 66.518 | 66.518 | 66.518 | 66.518 | 66.518 | 66.518 | 66.518 | 66.518 | 66.518 | 66.518 | 66.518 | 66.518 | 66.518 | 66.518 | 66.518 | 85% | 236.8672 | 40.9681 | 55.577 | 59.5707 | 60.1871 | 60.5769 | 61.4364 | 63.4689 | 64.5768 | 66.6908 | 73.1207 | 67.8155 | 66.7765 | 68.1746 | 71.2345 | 69.1601 | 69.1601 | 69.1601 | 69.1601 | 69.1601 | 69.1601 | 69.1601 | 69.1601 | 69.1601 | 69.1601 | 69.1601 | 69.1601 | 69.1601 | 69.1601 | 69.1601 | 69.1601
80% | 497.5104 | 36.0249 | 49.9501 | 53.5675 | 54.1828 | 54.6614 | 55.4882 | 57.3717 | 58.631 | 60.2279 | 61.056 | 61.7833 | 60.4364 | 62.0111 | 64.4876 | 62.6051 | 62.6051 | 62.6051 | 62.6051 | 62.6051 | 62.6051 | 62.6051 | 62.6051 | 62.6051 | 62.6051 | 62.6051 | 62.6051 | 62.6051 | 62.6051 | 62.6051 | 62.6051 | 80% | 497.5104 | 38.5582 | 52.3078 | 56.0665 | 56.6467 | 57.0136 | 57.8225 | 59.7354 | 60.7781 | 62.7678 | 68.8195 | 63.8263 | 62.8484 | 64.1643 | 67.0442 | 65.0919 | 65.0919 | 65.0919 | 65.0919 | 65.0919 | 65.0919 | 65.0919 | 65.0919 | 65.0919 | 65.0919 | 65.0919 | 65.0919 | 65.0919 | 65.0919 | 65.0919 | 65.0919
75% | 803.6248 | 33.7733 | 46.8282 | 50.2195 | 50.7964 | 51.245 | 52.0202 | 53.786 | 54.9666 | 56.4637 | 57.24 | 57.9219 | 56.6592 | 58.1354 | 60.4571 | 58.6923 | 58.6923 | 58.6923 | 58.6923 | 58.6923 | 58.6923 | 58.6923 | 58.6923 | 58.6923 | 58.6923 | 58.6923 | 58.6923 | 58.6923 | 58.6923 | 58.6923 | 58.6923 | 75% | 803.6248 | 36.1483 | 49.0386 | 52.5623 | 53.1063 | 53.4502 | 54.2086 | 56.0019 | 56.9795 | 58.8448 | 64.5182 | 59.8372 | 58.9204 | 60.154 | 62.8539 | 61.0236 | 61.0236 | 61.0236 | 61.0236 | 61.0236 | 61.0236 | 61.0236 | 61.0236 | 61.0236 | 61.0236 | 61.0236 | 61.0236 | 61.0236 | 61.0236 | 61.0236 | 61.0236
70% | 1155.2107 | 31.5218 | 43.7063 | 46.8715 | 47.4099 | 47.8287 | 48.5522 | 50.2003 | 51.3021 | 52.6994 | 53.424 | 54.0604 | 52.8819 | 54.2597 | 56.4267 | 54.7795 | 54.7795 | 54.7795 | 54.7795 | 54.7795 | 54.7795 | 54.7795 | 54.7795 | 54.7795 | 54.7795 | 54.7795 | 54.7795 | 54.7795 | 54.7795 | 54.7795 | 54.7795 | 70% | 1155.2107 | 33.7384 | 45.7693 | 49.0582 | 49.5659 | 49.8869 | 50.5947 | 52.2685 | 53.1809 | 54.9218 | 60.217 | 55.8481 | 54.9924 | 56.1438 | 58.6637 | 56.9554 | 56.9554 | 56.9554 | 56.9554 | 56.9554 | 56.9554 | 56.9554 | 56.9554 | 56.9554 | 56.9554 | 56.9554 | 56.9554 | 56.9554 | 56.9554 | 56.9554 | 56.9554
65% | 1553.1596 | 29.2702 | 40.5844 | 43.5236 | 44.0235 | 44.4124 | 45.0842 | 46.6145 | 47.6377 | 48.9352 | 49.608 | 50.1989 | 49.1046 | 50.384 | 52.3962 | 50.8667 | 50.8667 | 50.8667 | 50.8667 | 50.8667 | 50.8667 | 50.8667 | 50.8667 | 50.8667 | 50.8667 | 50.8667 | 50.8667 | 50.8667 | 50.8667 | 50.8667 | 50.8667 | 65% | 1553.1596 | 31.3286 | 42.5001 | 45.554 | 46.0254 | 46.3235 | 46.9808 | 48.535 | 49.3822 | 50.9988 | 55.9158 | 51.8589 | 51.0643 | 52.1335 | 54.4734 | 52.8871 | 52.8871 | 52.8871 | 52.8871 | 52.8871 | 52.8871 | 52.8871 | 52.8871 | 52.8871 | 52.8871 | 52.8871 | 52.8871 | 52.8871 | 52.8871 | 52.8871 | 52.8871
60% | 2026.2996 | 27.0187 | 37.4626 | 40.1756 | 40.6371 | 40.996 | 41.6162 | 43.0288 | 43.9733 | 45.1709 | 45.792 | 46.3375 | 45.3273 | 46.5083 | 48.3657 | 46.9539 | 46.9539 | 46.9539 | 46.9539 | 46.9539 | 46.9539 | 46.9539 | 46.9539 | 46.9539 | 46.9539 | 46.9539 | 46.9539 | 46.9539 | 46.9539 | 46.9539 | 46.9539 | 60% | 2026.2996 | 28.9187 | 39.2308 | 42.0499 | 42.485 | 42.7602 | 43.3669 | 44.8016 | 45.5836 | 47.0758 | 51.6146 | 47.8698 | 47.1363 | 48.1232 | 50.2832 | 48.8189 | 48.8189 | 48.8189 | 48.8189 | 48.8189 | 48.8189 | 48.8189 | 48.8189 | 48.8189 | 48.8189 | 48.8189 | 48.8189 | 48.8189 | 48.8189 | 48.8189 | 48.8189
55% | 2598.4068 | 24.7671 | 34.3407 | 36.8276 | 37.2507 | 37.5797 | 38.1482 | 39.4431 | 40.3088 | 41.4067 | 41.976 | 42.476 | 41.55 | 42.6326 | 44.3352 | 43.041 | 43.041 | 43.041 | 43.041 | 43.041 | 43.041 | 43.041 | 43.041 | 43.041 | 43.041 | 43.041 | 43.041 | 43.041 | 43.041 | 43.041 | 43.041 | 55% | 2598.4068 | 26.5088 | 35.9616 | 38.5457 | 38.9446 | 39.1968 | 39.753 | 41.0681 | 41.785 | 43.1529 | 47.3134 | 43.8806 | 43.2083 | 44.113 | 46.0929 | 44.7507 | 44.7507 | 44.7507 | 44.7507 | 44.7507 | 44.7507 | 44.7507 | 44.7507 | 44.7507 | 44.7507 | 44.7507 | 44.7507 | 44.7507 | 44.7507 | 44.7507 | 44.7507
50% | 3233.5201 | 22.5156 | 31.2188 | 33.4797 | 33.8642 | 34.1634 | 34.6802 | 35.8573 | 36.6444 | 37.6424 | 38.16 | 38.6146 | 37.7728 | 38.7569 | 40.3048 | 39.1282 | 39.1282 | 39.1282 | 39.1282 | 39.1282 | 39.1282 | 39.1282 | 39.1282 | 39.1282 | 39.1282 | 39.1282 | 39.1282 | 39.1282 | 39.1282 | 39.1282 | 39.1282 | 50% | 3233.5201 | 24.0989 | 32.6924 | 35.0416 | 35.4042 | 35.6335 | 36.139 | 37.3346 | 37.9863 | 39.2299 | 43.0122 | 39.8915 | 39.2803 | 40.1027 | 41.9026 | 40.6824 | 40.6824 | 40.6824 | 40.6824 | 40.6824 | 40.6824 | 40.6824 | 40.6824 | 40.6824 | 40.6824 | 40.6824 | 40.6824 | 40.6824 | 40.6824 | 40.6824 | 40.6824
45% | 3775.313 | 20.264 | 28.0969 | 30.1317 | 30.4778 | 30.747 | 31.2121 | 32.2716 | 32.9799 | 33.8782 | 34.344 | 34.7531 | 33.9955 | 34.8812 | 36.2743 | 35.2154 | 35.2154 | 35.2154 | 35.2154 | 35.2154 | 35.2154 | 35.2154 | 35.2154 | 35.2154 | 35.2154 | 35.2154 | 35.2154 | 35.2154 | 35.2154 | 35.2154 | 35.2154 | 45% | 3775.313 | 21.689 | 29.4231 | 31.5374 | 31.8638 | 32.0701 | 32.5251 | 33.6012 | 34.1877 | 35.3069 | 38.7109 | 35.9023 | 35.3522 | 36.0924 | 37.7124 | 36.6142 | 36.6142 | 36.6142 | 36.6142 | 36.6142 | 36.6142 | 36.6142 | 36.6142 | 36.6142 | 36.6142 | 36.6142 | 36.6142 | 36.6142 | 36.6142 | 36.6142 | 36.6142
40% | 4072.8088 | 18.0124 | 24.975 | 26.7837 | 27.0914 | 27.3307 | 27.7441 | 28.6859 | 29.3155 | 30.114 | 30.528 | 30.8917 | 30.2182 | 31.0055 | 32.2438 | 31.3026 | 31.3026 | 31.3026 | 31.3026 | 31.3026 | 31.3026 | 31.3026 | 31.3026 | 31.3026 | 31.3026 | 31.3026 | 31.3026 | 31.3026 | 31.3026 | 31.3026 | 31.3026 | 40% | 4072.8088 | 19.2791 | 26.1539 | 28.0332 | 28.3234 | 28.5068 | 28.9112 | 29.8677 | 30.3891 | 31.3839 | 34.4097 | 31.9132 | 31.4242 | 32.0822 | 33.5221 | 32.5459 | 32.5459 | 32.5459 | 32.5459 | 32.5459 | 32.5459 | 32.5459 | 32.5459 | 32.5459 | 32.5459 | 32.5459 | 32.5459 | 32.5459 | 32.5459 | 32.5459 | 32.5459
35% | 4198.821 | 15.7609 | 21.8532 | 23.4358 | 23.705 | 23.9144 | 24.2761 | 25.1001 | 25.6511 | 26.3497 | 26.712 | 27.0302 | 26.4409 | 27.1298 | 28.2133 | 27.3897 | 27.3897 | 27.3897 | 27.3897 | 27.3897 | 27.3897 | 27.3897 | 27.3897 | 27.3897 | 27.3897 | 27.3897 | 27.3897 | 27.3897 | 27.3897 | 27.3897 | 27.3897 | 35% | 4198.821 | 16.8692 | 22.8847 | 24.5291 | 24.7829 | 24.9434 | 25.2973 | 26.1342 | 26.5904 | 27.4609 | 30.1085 | 27.924 | 27.4962 | 28.0719 | 29.3318 | 28.4777 | 28.4777 | 28.4777 | 28.4777 | 28.4777 | 28.4777 | 28.4777 | 28.4777 | 28.4777 | 28.4777 | 28.4777 | 28.4777 | 28.4777 | 28.4777 | 28.4777 | 28.4777
30% | 4271.3374 | 13.5093 | 18.7313 | 20.0878 | 20.3185 | 20.498 | 20.8081 | 21.5144 | 21.9866 | 22.5855 | 22.896 | 23.1687 | 22.6637 | 23.2542 | 24.1829 | 23.4769 | 23.4769 | 23.4769 | 23.4769 | 23.4769 | 23.4769 | 23.4769 | 23.4769 | 23.4769 | 23.4769 | 23.4769 | 23.4769 | 23.4769 | 23.4769 | 23.4769 | 23.4769 | 30% | 4271.3374 | 14.4593 | 19.6154 | 21.0249 | 21.2425 | 21.3801 | 21.6834 | 22.4008 | 22.7918 | 23.5379 | 25.8073 | 23.9349 | 23.5682 | 24.0616 | 25.1416 | 24.4094 | 24.4094 | 24.4094 | 24.4094 | 24.4094 | 24.4094 | 24.4094 | 24.4094 | 24.4094 | 24.4094 | 24.4094 | 24.4094 | 24.4094 | 24.4094 | 24.4094 | 24.4094
25% | 4321.8611 | 11.2578 | 15.6094 | 16.7398 | 16.9321 | 17.0817 | 17.3401 | 17.9287 | 18.3222 | 18.8212 | 19.08 | 19.3073 | 18.8864 | 19.3785 | 20.1524 | 19.5641 | 19.5641 | 19.5641 | 19.5641 | 19.5641 | 19.5641 | 19.5641 | 19.5641 | 19.5641 | 19.5641 | 19.5641 | 19.5641 | 19.5641 | 19.5641 | 19.5641 | 19.5641 | 25% | 4321.8611 | 12.0494 | 16.3462 | 17.5208 | 17.7021 | 17.8167 | 18.0695 | 18.6673 | 18.9932 | 19.6149 | 21.5061 | 19.9457 | 19.6401 | 20.0513 | 20.9513 | 20.3412 | 20.3412 | 20.3412 | 20.3412 | 20.3412 | 20.3412 | 20.3412 | 20.3412 | 20.3412 | 20.3412 | 20.3412 | 20.3412 | 20.3412 | 20.3412 | 20.3412 | 20.3412
20% | 4353.067 | 9.0062 | 12.4875 | 13.3919 | 13.5457 | 13.6653 | 13.8721 | 14.3429 | 14.6578 | 15.057 | 15.264 | 15.4458 | 15.1091 | 15.5028 | 16.1219 | 15.6513 | 15.6513 | 15.6513 | 15.6513 | 15.6513 | 15.6513 | 15.6513 | 15.6513 | 15.6513 | 15.6513 | 15.6513 | 15.6513 | 15.6513 | 15.6513 | 15.6513 | 15.6513 | 20% | 4353.067 | 9.6396 | 13.0769 | 14.0166 | 14.1617 | 14.2534 | 14.4556 | 14.9339 | 15.1945 | 15.6919 | 17.2049 | 15.9566 | 15.7121 | 16.0411 | 16.7611 | 16.273 | 16.273 | 16.273 | 16.273 | 16.273 | 16.273 | 16.273 | 16.273 | 16.273 | 16.273 | 16.273 | 16.273 | 16.273 | 16.273 | 16.273 | 16.273
15% | 4369.4129 | 6.7547 | 9.3656 | 10.0439 | 10.1593 | 10.249 | 10.404 | 10.7572 | 10.9933 | 11.2927 | 11.448 | 11.5844 | 11.3318 | 11.6271 | 12.0914 | 11.7385 | 11.7385 | 11.7385 | 11.7385 | 11.7385 | 11.7385 | 11.7385 | 11.7385 | 11.7385 | 11.7385 | 11.7385 | 11.7385 | 11.7385 | 11.7385 | 11.7385 | 11.7385 | 15% | 4369.4129 | 7.2297 | 9.8077 | 10.5125 | 10.6213 | 10.69 | 10.8417 | 11.2004 | 11.3959 | 11.769 | 12.9036 | 11.9674 | 11.7841 | 12.0308 | 12.5708 | 12.2047 | 12.2047 | 12.2047 | 12.2047 | 12.2047 | 12.2047 | 12.2047 | 12.2047 | 12.2047 | 12.2047 | 12.2047 | 12.2047 | 12.2047 | 12.2047 | 12.2047 | 12.2047
10% | 4378.6261 | 4.5031 | 6.2438 | 6.6959 | 6.7728 | 6.8327 | 6.936 | 7.1715 | 7.3289 | 7.5285 | 7.632 | 7.7229 | 7.5546 | 7.7514 | 8.061 | 7.8256 | 7.8256 | 7.8256 | 7.8256 | 7.8256 | 7.8256 | 7.8256 | 7.8256 | 7.8256 | 7.8256 | 7.8256 | 7.8256 | 7.8256 | 7.8256 | 7.8256 | 7.8256 | 10% | 4378.6261 | 4.8198 | 6.5385 | 7.0083 | 7.0808 | 7.1267 | 7.2278 | 7.4669 | 7.5973 | 7.846 | 8.6024 | 7.9783 | 7.8561 | 8.0205 | 8.3805 | 8.1365 | 8.1365 | 8.1365 | 8.1365 | 8.1365 | 8.1365 | 8.1365 | 8.1365 | 8.1365 | 8.1365 | 8.1365 | 8.1365 | 8.1365 | 8.1365 | 8.1365 | 8.1365
5% | 4391.7028 | 2.2516 | 3.1219 | 3.348 | 3.3864 | 3.4163 | 3.468 | 3.5857 | 3.6644 | 3.7642 | 3.816 | 3.8615 | 3.7773 | 3.8757 | 4.0305 | 3.9128 | 3.9128 | 3.9128 | 3.9128 | 3.9128 | 3.9128 | 3.9128 | 3.9128 | 3.9128 | 3.9128 | 3.9128 | 3.9128 | 3.9128 | 3.9128 | 3.9128 | 3.9128 | 5% | 4391.7028 | 2.4099 | 3.2692 | 3.5042 | 3.5404 | 3.5633 | 3.6139 | 3.7335 | 3.7986 | 3.923 | 4.3012 | 3.9891 | 3.928 | 4.0103 | 4.1903 | 4.0682 | 4.0682 | 4.0682 | 4.0682 | 4.0682 | 4.0682 | 4.0682 | 4.0682 | 4.0682 | 4.0682 | 4.0682 | 4.0682 | 4.0682 | 4.0682 | 4.0682 | 4.0682
9.992e-14% | 4391.7028 | 4.4995e-14 | 6.2388e-14 | 6.6906e-14 | 6.7674e-14 | 6.8272e-14 | 6.9305e-14 | 7.1657e-14 | 7.323e-14 | 7.5225e-14 | 7.6259e-14 | 7.7167e-14 | 7.5485e-14 | 7.7452e-14 | 8.0545e-14 | 7.8194e-14 | 7.8194e-14 | 7.8194e-14 | 7.8194e-14 | 7.8194e-14 | 7.8194e-14 | 7.8194e-14 | 7.8194e-14 | 7.8194e-14 | 7.8194e-14 | 7.8194e-14 | 7.8194e-14 | 7.8194e-14 | 7.8194e-14 | 7.8194e-14 | 7.8194e-14 | 9.992e-14% | 4391.7028 | 4.8159e-14 | 6.5332e-14 | 7.0027e-14 | 7.0752e-14 | 7.121e-14 | 7.222e-14 | 7.461e-14 | 7.5912e-14 | 7.8397e-14 | 8.5956e-14 | 7.9719e-14 | 7.8498e-14 | 8.0141e-14 | 8.3738e-14 | 8.13e-14 | 8.13e-14 | 8.13e-14 | 8.13e-14 | 8.13e-14 | 8.13e-14 | 8.13e-14 | 8.13e-14 | 8.13e-14 | 8.13e-14 | 8.13e-14 | 8.13e-14 | 8.13e-14 | 8.13e-14 | 8.13e-14 | 8.13e-14
Summer Season | [31 empty] | Summer Season
P50 | [31 empty] | P10
% of MD | Summer - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Summer - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 51.1621 | 67.921 | 72.4827 | 72.3498 | 72.345 | 72.8648 | 73.4353 | 74.6066 | 75.4483 | 75.9048 | 76.4041 | 76.8611 | 77.687 | 78.7121 | 78.6404 | 78.6404 | 78.6404 | 78.6404 | 78.6404 | 78.6404 | 78.6404 | 78.6404 | 78.6404 | 78.6404 | 78.6404 | 78.6404 | 78.6404 | 78.6404 | 78.6404 | 78.6404 | 100% | 0 | 57.0282 | 73.8207 | 78.2145 | 77.9508 | 77.9694 | 78.4199 | 79.6095 | 80.4052 | 81.1846 | 82.0962 | 82.9406 | 83.7606 | 83.8537 | 84.8109 | 84.0841 | 84.0841 | 84.0841 | 84.0841 | 84.0841 | 84.0841 | 84.0841 | 84.0841 | 84.0841 | 84.0841 | 84.0841 | 84.0841 | 84.0841 | 84.0841 | 84.0841 | 84.0841
99% | 0 | 50.6505 | 67.2418 | 71.7579 | 71.6263 | 71.6215 | 72.1362 | 72.701 | 73.8605 | 74.6938 | 75.1458 | 75.64 | 76.0925 | 76.9101 | 77.9249 | 77.854 | 77.854 | 77.854 | 77.854 | 77.854 | 77.854 | 77.854 | 77.854 | 77.854 | 77.854 | 77.854 | 77.854 | 77.854 | 77.854 | 77.854 | 77.854 | 99% | 1.5127 | 56.4579 | 73.0825 | 77.4324 | 77.1713 | 77.1897 | 77.6357 | 78.8134 | 79.6012 | 80.3728 | 81.2753 | 82.1112 | 82.923 | 83.0151 | 83.9628 | 83.2432 | 83.2432 | 83.2432 | 83.2432 | 83.2432 | 83.2432 | 83.2432 | 83.2432 | 83.2432 | 83.2432 | 83.2432 | 83.2432 | 83.2432 | 83.2432 | 83.2432 | 83.2432
98% | 0 | 50.1389 | 66.5626 | 71.033 | 70.9028 | 70.8981 | 71.4075 | 71.9666 | 73.1145 | 73.9393 | 74.3867 | 74.876 | 75.3239 | 76.1333 | 77.1378 | 77.0676 | 77.0676 | 77.0676 | 77.0676 | 77.0676 | 77.0676 | 77.0676 | 77.0676 | 77.0676 | 77.0676 | 77.0676 | 77.0676 | 77.0676 | 77.0676 | 77.0676 | 77.0676 | 98% | 2.269 | 55.8876 | 72.3443 | 76.6503 | 76.3918 | 76.41 | 76.8515 | 78.0173 | 78.7971 | 79.5609 | 80.4543 | 81.2818 | 82.0854 | 82.1766 | 83.1147 | 82.4024 | 82.4024 | 82.4024 | 82.4024 | 82.4024 | 82.4024 | 82.4024 | 82.4024 | 82.4024 | 82.4024 | 82.4024 | 82.4024 | 82.4024 | 82.4024 | 82.4024 | 82.4024
97% | 0.37816 | 49.6272 | 65.8834 | 70.3082 | 70.1794 | 70.1746 | 70.6789 | 71.2323 | 72.3684 | 73.1848 | 73.6277 | 74.112 | 74.5553 | 75.3564 | 76.3507 | 76.2812 | 76.2812 | 76.2812 | 76.2812 | 76.2812 | 76.2812 | 76.2812 | 76.2812 | 76.2812 | 76.2812 | 76.2812 | 76.2812 | 76.2812 | 76.2812 | 76.2812 | 76.2812 | 97% | 3.7816 | 55.3173 | 71.6061 | 75.8681 | 75.6123 | 75.6303 | 76.0673 | 77.2212 | 77.9931 | 78.7491 | 79.6334 | 80.4523 | 81.2478 | 81.338 | 82.2666 | 81.5615 | 81.5615 | 81.5615 | 81.5615 | 81.5615 | 81.5615 | 81.5615 | 81.5615 | 81.5615 | 81.5615 | 81.5615 | 81.5615 | 81.5615 | 81.5615 | 81.5615 | 81.5615
95% | 2.269 | 48.604 | 64.5249 | 68.8586 | 68.7324 | 68.7277 | 69.2216 | 69.7636 | 70.8763 | 71.6758 | 72.1096 | 72.5839 | 73.0181 | 73.8027 | 74.7765 | 74.7084 | 74.7084 | 74.7084 | 74.7084 | 74.7084 | 74.7084 | 74.7084 | 74.7084 | 74.7084 | 74.7084 | 74.7084 | 74.7084 | 74.7084 | 74.7084 | 74.7084 | 74.7084 | 95% | 6.0506 | 54.1768 | 70.1297 | 74.3038 | 74.0533 | 74.071 | 74.4989 | 75.629 | 76.385 | 77.1254 | 77.9914 | 78.7935 | 79.5726 | 79.661 | 80.5703 | 79.8799 | 79.8799 | 79.8799 | 79.8799 | 79.8799 | 79.8799 | 79.8799 | 79.8799 | 79.8799 | 79.8799 | 79.8799 | 79.8799 | 79.8799 | 79.8799 | 79.8799 | 79.8799
90% | 5.6725 | 46.0459 | 61.1289 | 65.2344 | 65.1149 | 65.1105 | 65.5784 | 66.0918 | 67.1459 | 67.9034 | 68.3143 | 68.7637 | 69.175 | 69.9183 | 70.8409 | 70.7764 | 70.7764 | 70.7764 | 70.7764 | 70.7764 | 70.7764 | 70.7764 | 70.7764 | 70.7764 | 70.7764 | 70.7764 | 70.7764 | 70.7764 | 70.7764 | 70.7764 | 70.7764 | 90% | 16.2611 | 51.3254 | 66.4386 | 70.3931 | 70.1557 | 70.1725 | 70.5779 | 71.6485 | 72.3647 | 73.0662 | 73.8866 | 74.6465 | 75.3846 | 75.4683 | 76.3298 | 75.6757 | 75.6757 | 75.6757 | 75.6757 | 75.6757 | 75.6757 | 75.6757 | 75.6757 | 75.6757 | 75.6757 | 75.6757 | 75.6757 | 75.6757 | 75.6757 | 75.6757 | 75.6757
85% | 15.8829 | 43.4878 | 57.7328 | 61.6103 | 61.4974 | 61.4932 | 61.9351 | 62.42 | 63.4156 | 64.131 | 64.5191 | 64.9435 | 65.332 | 66.034 | 66.9053 | 66.8444 | 66.8444 | 66.8444 | 66.8444 | 66.8444 | 66.8444 | 66.8444 | 66.8444 | 66.8444 | 66.8444 | 66.8444 | 66.8444 | 66.8444 | 66.8444 | 66.8444 | 66.8444 | 85% | 26.4715 | 48.4739 | 62.7476 | 66.4824 | 66.2582 | 66.274 | 66.6569 | 67.6681 | 68.3445 | 69.0069 | 69.7818 | 70.4995 | 71.1965 | 71.2756 | 72.0892 | 71.4715 | 71.4715 | 71.4715 | 71.4715 | 71.4715 | 71.4715 | 71.4715 | 71.4715 | 71.4715 | 71.4715 | 71.4715 | 71.4715 | 71.4715 | 71.4715 | 71.4715 | 71.4715
80% | 31.0095 | 40.9297 | 54.3368 | 57.9862 | 57.8799 | 57.876 | 58.2919 | 58.7483 | 59.6853 | 60.3586 | 60.7239 | 61.1233 | 61.4889 | 62.1496 | 62.9697 | 62.9123 | 62.9123 | 62.9123 | 62.9123 | 62.9123 | 62.9123 | 62.9123 | 62.9123 | 62.9123 | 62.9123 | 62.9123 | 62.9123 | 62.9123 | 62.9123 | 62.9123 | 62.9123 | 80% | 34.0348 | 45.6225 | 59.0566 | 62.5716 | 62.3606 | 62.3755 | 62.7359 | 63.6876 | 64.3242 | 64.9477 | 65.677 | 66.3524 | 67.0085 | 67.0829 | 67.8487 | 67.2672 | 67.2672 | 67.2672 | 67.2672 | 67.2672 | 67.2672 | 67.2672 | 67.2672 | 67.2672 | 67.2672 | 67.2672 | 67.2672 | 67.2672 | 67.2672 | 67.2672 | 67.2672
75% | 72.9857 | 38.3716 | 50.9407 | 54.362 | 54.2624 | 54.2587 | 54.6486 | 55.0765 | 55.955 | 56.5862 | 56.9286 | 57.3031 | 57.6458 | 58.2653 | 59.0341 | 58.9803 | 58.9803 | 58.9803 | 58.9803 | 58.9803 | 58.9803 | 58.9803 | 58.9803 | 58.9803 | 58.9803 | 58.9803 | 58.9803 | 58.9803 | 58.9803 | 58.9803 | 58.9803 | 75% | 48.405 | 42.7711 | 55.3655 | 58.6609 | 58.4631 | 58.4771 | 58.8149 | 59.7071 | 60.3039 | 60.8885 | 61.5722 | 62.2054 | 62.8205 | 62.8902 | 63.6082 | 63.063 | 63.063 | 63.063 | 63.063 | 63.063 | 63.063 | 63.063 | 63.063 | 63.063 | 63.063 | 63.063 | 63.063 | 63.063 | 63.063 | 63.063 | 63.063
70% | 150.5094 | 35.8135 | 47.5447 | 50.7379 | 50.6449 | 50.6415 | 51.0054 | 51.4047 | 52.2246 | 52.8138 | 53.1334 | 53.4829 | 53.8028 | 54.3809 | 55.0984 | 55.0483 | 55.0483 | 55.0483 | 55.0483 | 55.0483 | 55.0483 | 55.0483 | 55.0483 | 55.0483 | 55.0483 | 55.0483 | 55.0483 | 55.0483 | 55.0483 | 55.0483 | 55.0483 | 70% | 76.3892 | 39.9197 | 51.6745 | 54.7502 | 54.5656 | 54.5786 | 54.8939 | 55.7266 | 56.2837 | 56.8292 | 57.4674 | 58.0584 | 58.6324 | 58.6976 | 59.3676 | 58.8588 | 58.8588 | 58.8588 | 58.8588 | 58.8588 | 58.8588 | 58.8588 | 58.8588 | 58.8588 | 58.8588 | 58.8588 | 58.8588 | 58.8588 | 58.8588 | 58.8588 | 58.8588
65% | 359.6342 | 33.2554 | 44.1486 | 47.1138 | 47.0274 | 47.0242 | 47.3621 | 47.733 | 48.4943 | 49.0414 | 49.3381 | 49.6627 | 49.9597 | 50.4966 | 51.1628 | 51.1163 | 51.1163 | 51.1163 | 51.1163 | 51.1163 | 51.1163 | 51.1163 | 51.1163 | 51.1163 | 51.1163 | 51.1163 | 51.1163 | 51.1163 | 51.1163 | 51.1163 | 51.1163 | 65% | 114.2056 | 37.0683 | 47.9835 | 50.8395 | 50.668 | 50.6801 | 50.9729 | 51.7462 | 52.2634 | 52.77 | 53.3626 | 53.9114 | 54.4444 | 54.5049 | 55.1271 | 54.6546 | 54.6546 | 54.6546 | 54.6546 | 54.6546 | 54.6546 | 54.6546 | 54.6546 | 54.6546 | 54.6546 | 54.6546 | 54.6546 | 54.6546 | 54.6546 | 54.6546 | 54.6546
60% | 689.7717 | 30.6973 | 40.7526 | 43.4896 | 43.4099 | 43.407 | 43.7189 | 44.0612 | 44.764 | 45.269 | 45.5429 | 45.8424 | 46.1167 | 46.6122 | 47.2272 | 47.1843 | 47.1843 | 47.1843 | 47.1843 | 47.1843 | 47.1843 | 47.1843 | 47.1843 | 47.1843 | 47.1843 | 47.1843 | 47.1843 | 47.1843 | 47.1843 | 47.1843 | 47.1843 | 60% | 178.1154 | 34.2169 | 44.2924 | 46.9287 | 46.7705 | 46.7817 | 47.0519 | 47.7657 | 48.2431 | 48.7108 | 49.2577 | 49.7643 | 50.2564 | 50.3122 | 50.8865 | 50.4504 | 50.4504 | 50.4504 | 50.4504 | 50.4504 | 50.4504 | 50.4504 | 50.4504 | 50.4504 | 50.4504 | 50.4504 | 50.4504 | 50.4504 | 50.4504 | 50.4504 | 50.4504
55% | 1095.5419 | 28.1392 | 37.3565 | 39.8655 | 39.7924 | 39.7897 | 40.0757 | 40.3894 | 41.0336 | 41.4965 | 41.7476 | 42.0222 | 42.2736 | 42.7279 | 43.2916 | 43.2522 | 43.2522 | 43.2522 | 43.2522 | 43.2522 | 43.2522 | 43.2522 | 43.2522 | 43.2522 | 43.2522 | 43.2522 | 43.2522 | 43.2522 | 43.2522 | 43.2522 | 43.2522 | 55% | 311.6074 | 31.3655 | 40.6014 | 43.018 | 42.8729 | 42.8832 | 43.131 | 43.7852 | 44.2229 | 44.6515 | 45.1529 | 45.6173 | 46.0683 | 46.1195 | 46.646 | 46.2462 | 46.2462 | 46.2462 | 46.2462 | 46.2462 | 46.2462 | 46.2462 | 46.2462 | 46.2462 | 46.2462 | 46.2462 | 46.2462 | 46.2462 | 46.2462 | 46.2462 | 46.2462
50% | 1666.1918 | 25.581 | 33.9605 | 36.2413 | 36.1749 | 36.1725 | 36.4324 | 36.7177 | 37.3033 | 37.7241 | 37.9524 | 38.202 | 38.4306 | 38.8435 | 39.356 | 39.3202 | 39.3202 | 39.3202 | 39.3202 | 39.3202 | 39.3202 | 39.3202 | 39.3202 | 39.3202 | 39.3202 | 39.3202 | 39.3202 | 39.3202 | 39.3202 | 39.3202 | 39.3202 | 50% | 636.0723 | 28.5141 | 36.9103 | 39.1073 | 38.9754 | 38.9847 | 39.21 | 39.8047 | 40.2026 | 40.5923 | 41.0481 | 41.4703 | 41.8803 | 41.9268 | 42.4054 | 42.042 | 42.042 | 42.042 | 42.042 | 42.042 | 42.042 | 42.042 | 42.042 | 42.042 | 42.042 | 42.042 | 42.042 | 42.042 | 42.042 | 42.042 | 42.042
45% | 2506.0947 | 23.0229 | 30.5644 | 32.6172 | 32.5574 | 32.5552 | 32.7892 | 33.0459 | 33.573 | 33.9517 | 34.1572 | 34.3818 | 34.5875 | 34.9592 | 35.4204 | 35.3882 | 35.3882 | 35.3882 | 35.3882 | 35.3882 | 35.3882 | 35.3882 | 35.3882 | 35.3882 | 35.3882 | 35.3882 | 35.3882 | 35.3882 | 35.3882 | 35.3882 | 35.3882 | 45% | 1179.4944 | 25.6627 | 33.2193 | 35.1965 | 35.0779 | 35.0862 | 35.289 | 35.8243 | 36.1824 | 36.5331 | 36.9433 | 37.3233 | 37.6923 | 37.7341 | 38.1649 | 37.8378 | 37.8378 | 37.8378 | 37.8378 | 37.8378 | 37.8378 | 37.8378 | 37.8378 | 37.8378 | 37.8378 | 37.8378 | 37.8378 | 37.8378 | 37.8378 | 37.8378 | 37.8378
40% | 3164.4787 | 20.4648 | 27.1684 | 28.9931 | 28.9399 | 28.938 | 29.1459 | 29.3741 | 29.8426 | 30.1793 | 30.3619 | 30.5616 | 30.7444 | 31.0748 | 31.4848 | 31.4562 | 31.4562 | 31.4562 | 31.4562 | 31.4562 | 31.4562 | 31.4562 | 31.4562 | 31.4562 | 31.4562 | 31.4562 | 31.4562 | 31.4562 | 31.4562 | 31.4562 | 31.4562 | 40% | 1808.3816 | 22.8113 | 29.5283 | 31.2858 | 31.1803 | 31.1878 | 31.368 | 31.8438 | 32.1621 | 32.4738 | 32.8385 | 33.1762 | 33.5042 | 33.5415 | 33.9244 | 33.6336 | 33.6336 | 33.6336 | 33.6336 | 33.6336 | 33.6336 | 33.6336 | 33.6336 | 33.6336 | 33.6336 | 33.6336 | 33.6336 | 33.6336 | 33.6336 | 33.6336 | 33.6336
35% | 3551.3408 | 17.9067 | 23.7723 | 25.3689 | 25.3224 | 25.3207 | 25.5027 | 25.7024 | 26.1123 | 26.4069 | 26.5667 | 26.7414 | 26.9014 | 27.1905 | 27.5492 | 27.5241 | 27.5241 | 27.5241 | 27.5241 | 27.5241 | 27.5241 | 27.5241 | 27.5241 | 27.5241 | 27.5241 | 27.5241 | 27.5241 | 27.5241 | 27.5241 | 27.5241 | 27.5241 | 35% | 2779.1293 | 19.9599 | 25.8372 | 27.3751 | 27.2828 | 27.2893 | 27.447 | 27.8633 | 28.1418 | 28.4146 | 28.7337 | 29.0292 | 29.3162 | 29.3488 | 29.6838 | 29.4294 | 29.4294 | 29.4294 | 29.4294 | 29.4294 | 29.4294 | 29.4294 | 29.4294 | 29.4294 | 29.4294 | 29.4294 | 29.4294 | 29.4294 | 29.4294 | 29.4294 | 29.4294
30% | 3758.953 | 15.3486 | 20.3763 | 21.7448 | 21.705 | 21.7035 | 21.8595 | 22.0306 | 22.382 | 22.6345 | 22.7714 | 22.9212 | 23.0583 | 23.3061 | 23.6136 | 23.5921 | 23.5921 | 23.5921 | 23.5921 | 23.5921 | 23.5921 | 23.5921 | 23.5921 | 23.5921 | 23.5921 | 23.5921 | 23.5921 | 23.5921 | 23.5921 | 23.5921 | 23.5921 | 30% | 3814.165 | 17.1085 | 22.1462 | 23.4644 | 23.3852 | 23.3908 | 23.526 | 23.8828 | 24.1216 | 24.3554 | 24.6289 | 24.8822 | 25.1282 | 25.1561 | 25.4433 | 25.2252 | 25.2252 | 25.2252 | 25.2252 | 25.2252 | 25.2252 | 25.2252 | 25.2252 | 25.2252 | 25.2252 | 25.2252 | 25.2252 | 25.2252 | 25.2252 | 25.2252 | 25.2252
25% | 3926.4798 | 12.7905 | 16.9802 | 18.1207 | 18.0875 | 18.0862 | 18.2162 | 18.3588 | 18.6517 | 18.8621 | 18.9762 | 19.101 | 19.2153 | 19.4218 | 19.678 | 19.6601 | 19.6601 | 19.6601 | 19.6601 | 19.6601 | 19.6601 | 19.6601 | 19.6601 | 19.6601 | 19.6601 | 19.6601 | 19.6601 | 19.6601 | 19.6601 | 19.6601 | 19.6601 | 25% | 4166.9923 | 14.257 | 18.4552 | 19.5536 | 19.4877 | 19.4924 | 19.605 | 19.9024 | 20.1013 | 20.2962 | 20.5241 | 20.7351 | 20.9402 | 20.9634 | 21.2027 | 21.021 | 21.021 | 21.021 | 21.021 | 21.021 | 21.021 | 21.021 | 21.021 | 21.021 | 21.021 | 21.021 | 21.021 | 21.021 | 21.021 | 21.021 | 21.021
20% | 4050.5177 | 10.2324 | 13.5842 | 14.4965 | 14.47 | 14.469 | 14.573 | 14.6871 | 14.9213 | 15.0897 | 15.181 | 15.2808 | 15.3722 | 15.5374 | 15.7424 | 15.7281 | 15.7281 | 15.7281 | 15.7281 | 15.7281 | 15.7281 | 15.7281 | 15.7281 | 15.7281 | 15.7281 | 15.7281 | 15.7281 | 15.7281 | 15.7281 | 15.7281 | 15.7281 | 20% | 4282.7105 | 11.4056 | 14.7641 | 15.6429 | 15.5902 | 15.5939 | 15.684 | 15.9219 | 16.081 | 16.2369 | 16.4192 | 16.5881 | 16.7521 | 16.7707 | 16.9622 | 16.8168 | 16.8168 | 16.8168 | 16.8168 | 16.8168 | 16.8168 | 16.8168 | 16.8168 | 16.8168 | 16.8168 | 16.8168 | 16.8168 | 16.8168 | 16.8168 | 16.8168 | 16.8168
15% | 4152.622 | 7.6743 | 10.1881 | 10.8724 | 10.8525 | 10.8517 | 10.9297 | 11.0153 | 11.191 | 11.3172 | 11.3857 | 11.4606 | 11.5292 | 11.6531 | 11.8068 | 11.7961 | 11.7961 | 11.7961 | 11.7961 | 11.7961 | 11.7961 | 11.7961 | 11.7961 | 11.7961 | 11.7961 | 11.7961 | 11.7961 | 11.7961 | 11.7961 | 11.7961 | 11.7961 | 15% | 4364.7722 | 8.5542 | 11.0731 | 11.7322 | 11.6926 | 11.6954 | 11.763 | 11.9414 | 12.0608 | 12.1777 | 12.3144 | 12.4411 | 12.5641 | 12.578 | 12.7216 | 12.6126 | 12.6126 | 12.6126 | 12.6126 | 12.6126 | 12.6126 | 12.6126 | 12.6126 | 12.6126 | 12.6126 | 12.6126 | 12.6126 | 12.6126 | 12.6126 | 12.6126 | 12.6126
10% | 4248.2976 | 5.1162 | 6.7921 | 7.2483 | 7.235 | 7.2345 | 7.2865 | 7.3435 | 7.4607 | 7.5448 | 7.5905 | 7.6404 | 7.6861 | 7.7687 | 7.8712 | 7.864 | 7.864 | 7.864 | 7.864 | 7.864 | 7.864 | 7.864 | 7.864 | 7.864 | 7.864 | 7.864 | 7.864 | 7.864 | 7.864 | 7.864 | 7.864 | 10% | 4391.6218 | 5.7028 | 7.3821 | 7.8215 | 7.7951 | 7.7969 | 7.842 | 7.9609 | 8.0405 | 8.1185 | 8.2096 | 8.2941 | 8.3761 | 8.3854 | 8.4811 | 8.4084 | 8.4084 | 8.4084 | 8.4084 | 8.4084 | 8.4084 | 8.4084 | 8.4084 | 8.4084 | 8.4084 | 8.4084 | 8.4084 | 8.4084 | 8.4084 | 8.4084 | 8.4084
5% | 4361.7469 | 2.5581 | 3.396 | 3.6241 | 3.6175 | 3.6172 | 3.6432 | 3.6718 | 3.7303 | 3.7724 | 3.7952 | 3.8202 | 3.8431 | 3.8844 | 3.9356 | 3.932 | 3.932 | 3.932 | 3.932 | 3.932 | 3.932 | 3.932 | 3.932 | 3.932 | 3.932 | 3.932 | 3.932 | 3.932 | 3.932 | 3.932 | 3.932 | 5% | 4391.6218 | 2.8514 | 3.691 | 3.9107 | 3.8975 | 3.8985 | 3.921 | 3.9805 | 4.0203 | 4.0592 | 4.1048 | 4.147 | 4.188 | 4.1927 | 4.2405 | 4.2042 | 4.2042 | 4.2042 | 4.2042 | 4.2042 | 4.2042 | 4.2042 | 4.2042 | 4.2042 | 4.2042 | 4.2042 | 4.2042 | 4.2042 | 4.2042 | 4.2042 | 4.2042
9.992e-14% | 4391.6218 | 5.1121e-14 | 6.7867e-14 | 7.2425e-14 | 7.2292e-14 | 7.2287e-14 | 7.2807e-14 | 7.3377e-14 | 7.4547e-14 | 7.5388e-14 | 7.5844e-14 | 7.6343e-14 | 7.68e-14 | 7.7625e-14 | 7.8649e-14 | 7.8578e-14 | 7.8578e-14 | 7.8578e-14 | 7.8578e-14 | 7.8578e-14 | 7.8578e-14 | 7.8578e-14 | 7.8578e-14 | 7.8578e-14 | 7.8578e-14 | 7.8578e-14 | 7.8578e-14 | 7.8578e-14 | 7.8578e-14 | 7.8578e-14 | 7.8578e-14 | 9.992e-14% | 4391.6218 | 5.6983e-14 | 7.3762e-14 | 7.8152e-14 | 7.7889e-14 | 7.7907e-14 | 7.8357e-14 | 7.9546e-14 | 8.0341e-14 | 8.112e-14 | 8.2031e-14 | 8.2874e-14 | 8.3694e-14 | 8.3787e-14 | 8.4743e-14 | 8.4017e-14 | 8.4017e-14 | 8.4017e-14 | 8.4017e-14 | 8.4017e-14 | 8.4017e-14 | 8.4017e-14 | 8.4017e-14 | 8.4017e-14 | 8.4017e-14 | 8.4017e-14 | 8.4017e-14 | 8.4017e-14 | 8.4017e-14 | 8.4017e-14 | 8.4017e-14
Option 8
Winter Season | [31 empty] | Winter Season
P50 | [31 empty] | P10
% of MD | Winter - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Winter - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 45.0311 | 62.4376 | 66.9594 | 67.7285 | 68.3267 | 69.3603 | 71.7146 | 73.2888 | 75.2849 | 76.3199 | 77.2291 | 75.5455 | 77.5138 | 80.6095 | 78.2564 | 78.2564 | 78.2564 | 78.2564 | 78.2564 | 78.2564 | 78.2564 | 78.2564 | 78.2564 | 78.2564 | 78.2564 | 78.2564 | 78.2564 | 78.2564 | 78.2564 | 78.2564 | 100% | 0 | 48.1978 | 65.3847 | 70.0831 | 70.8084 | 71.267 | 72.2781 | 74.6693 | 75.9727 | 78.4597 | 86.0243 | 79.7829 | 78.5605 | 80.2054 | 83.8053 | 81.3648 | 81.3648 | 81.3648 | 81.3648 | 81.3648 | 81.3648 | 81.3648 | 81.3648 | 81.3648 | 81.3648 | 81.3648 | 81.3648 | 81.3648 | 81.3648 | 81.3648 | 81.3648
99% | 1.486 | 44.5808 | 61.8132 | 66.2898 | 67.0512 | 67.6435 | 68.6667 | 70.9975 | 72.5559 | 74.532 | 75.5567 | 76.4569 | 74.7901 | 76.7387 | 79.8034 | 77.4739 | 77.4739 | 77.4739 | 77.4739 | 77.4739 | 77.4739 | 77.4739 | 77.4739 | 77.4739 | 77.4739 | 77.4739 | 77.4739 | 77.4739 | 77.4739 | 77.4739 | 77.4739 | 99% | 1.486 | 47.7158 | 64.7309 | 69.3823 | 70.1003 | 70.5543 | 71.5553 | 73.9226 | 75.2129 | 77.6751 | 85.1641 | 78.9851 | 77.7749 | 79.4033 | 82.9672 | 80.5512 | 80.5512 | 80.5512 | 80.5512 | 80.5512 | 80.5512 | 80.5512 | 80.5512 | 80.5512 | 80.5512 | 80.5512 | 80.5512 | 80.5512 | 80.5512 | 80.5512 | 80.5512
98% | 3.2692 | 44.1305 | 61.1889 | 65.6202 | 66.3739 | 66.9602 | 67.9731 | 70.2804 | 71.823 | 73.7792 | 74.7935 | 75.6846 | 74.0346 | 75.9636 | 78.9973 | 76.6913 | 76.6913 | 76.6913 | 76.6913 | 76.6913 | 76.6913 | 76.6913 | 76.6913 | 76.6913 | 76.6913 | 76.6913 | 76.6913 | 76.6913 | 76.6913 | 76.6913 | 76.6913 | 98% | 3.2692 | 47.2338 | 64.0771 | 68.6815 | 69.3922 | 69.8416 | 70.8325 | 73.1759 | 74.4532 | 76.8905 | 84.3038 | 78.1873 | 76.9893 | 78.6013 | 82.1292 | 79.7375 | 79.7375 | 79.7375 | 79.7375 | 79.7375 | 79.7375 | 79.7375 | 79.7375 | 79.7375 | 79.7375 | 79.7375 | 79.7375 | 79.7375 | 79.7375 | 79.7375 | 79.7375
97% | 6.8356 | 43.6802 | 60.5645 | 64.9506 | 65.6966 | 66.2769 | 67.2795 | 69.5632 | 71.0901 | 73.0263 | 74.0303 | 74.9123 | 73.2792 | 75.1884 | 78.1912 | 75.9087 | 75.9087 | 75.9087 | 75.9087 | 75.9087 | 75.9087 | 75.9087 | 75.9087 | 75.9087 | 75.9087 | 75.9087 | 75.9087 | 75.9087 | 75.9087 | 75.9087 | 75.9087 | 97% | 6.8356 | 46.7518 | 63.4232 | 67.9806 | 68.6841 | 69.129 | 70.1097 | 72.4292 | 73.6935 | 76.1059 | 83.4436 | 77.3894 | 76.2037 | 77.7992 | 81.2911 | 78.9239 | 78.9239 | 78.9239 | 78.9239 | 78.9239 | 78.9239 | 78.9239 | 78.9239 | 78.9239 | 78.9239 | 78.9239 | 78.9239 | 78.9239 | 78.9239 | 78.9239 | 78.9239
95% | 17.5347 | 42.7796 | 59.3157 | 63.6114 | 64.342 | 64.9104 | 65.8923 | 68.1289 | 69.6243 | 71.5207 | 72.5039 | 73.3677 | 71.7683 | 73.6382 | 76.579 | 74.3436 | 74.3436 | 74.3436 | 74.3436 | 74.3436 | 74.3436 | 74.3436 | 74.3436 | 74.3436 | 74.3436 | 74.3436 | 74.3436 | 74.3436 | 74.3436 | 74.3436 | 74.3436 | 95% | 17.5347 | 45.7879 | 62.1155 | 66.579 | 67.268 | 67.7036 | 68.6642 | 70.9358 | 72.174 | 74.5368 | 81.7231 | 75.7938 | 74.6325 | 76.1951 | 79.615 | 77.2966 | 77.2966 | 77.2966 | 77.2966 | 77.2966 | 77.2966 | 77.2966 | 77.2966 | 77.2966 | 77.2966 | 77.2966 | 77.2966 | 77.2966 | 77.2966 | 77.2966 | 77.2966
90% | 78.7576 | 40.528 | 56.1939 | 60.2634 | 60.9556 | 61.4941 | 62.4243 | 64.5432 | 65.9599 | 67.7564 | 68.6879 | 69.5062 | 67.991 | 69.7625 | 72.5486 | 70.4308 | 70.4308 | 70.4308 | 70.4308 | 70.4308 | 70.4308 | 70.4308 | 70.4308 | 70.4308 | 70.4308 | 70.4308 | 70.4308 | 70.4308 | 70.4308 | 70.4308 | 70.4308 | 90% | 78.7576 | 43.378 | 58.8463 | 63.0748 | 63.7275 | 64.1403 | 65.0503 | 67.2023 | 68.3754 | 70.6138 | 77.4219 | 71.8046 | 70.7045 | 72.1848 | 75.4247 | 73.2283 | 73.2283 | 73.2283 | 73.2283 | 73.2283 | 73.2283 | 73.2283 | 73.2283 | 73.2283 | 73.2283 | 73.2283 | 73.2283 | 73.2283 | 73.2283 | 73.2283 | 73.2283
85% | 236.8672 | 38.2764 | 53.072 | 56.9155 | 57.5692 | 58.0777 | 58.9563 | 60.9575 | 62.2954 | 63.9922 | 64.8719 | 65.6448 | 64.2137 | 65.8868 | 68.5181 | 66.518 | 66.518 | 66.518 | 66.518 | 66.518 | 66.518 | 66.518 | 66.518 | 66.518 | 66.518 | 66.518 | 66.518 | 66.518 | 66.518 | 66.518 | 66.518 | 85% | 236.8672 | 40.9681 | 55.577 | 59.5707 | 60.1871 | 60.5769 | 61.4364 | 63.4689 | 64.5768 | 66.6908 | 73.1207 | 67.8155 | 66.7765 | 68.1746 | 71.2345 | 69.1601 | 69.1601 | 69.1601 | 69.1601 | 69.1601 | 69.1601 | 69.1601 | 69.1601 | 69.1601 | 69.1601 | 69.1601 | 69.1601 | 69.1601 | 69.1601 | 69.1601 | 69.1601
80% | 497.5104 | 36.0249 | 49.9501 | 53.5675 | 54.1828 | 54.6614 | 55.4882 | 57.3717 | 58.631 | 60.2279 | 61.056 | 61.7833 | 60.4364 | 62.0111 | 64.4876 | 62.6051 | 62.6051 | 62.6051 | 62.6051 | 62.6051 | 62.6051 | 62.6051 | 62.6051 | 62.6051 | 62.6051 | 62.6051 | 62.6051 | 62.6051 | 62.6051 | 62.6051 | 62.6051 | 80% | 497.5104 | 38.5582 | 52.3078 | 56.0665 | 56.6467 | 57.0136 | 57.8225 | 59.7354 | 60.7781 | 62.7678 | 68.8195 | 63.8263 | 62.8484 | 64.1643 | 67.0442 | 65.0919 | 65.0919 | 65.0919 | 65.0919 | 65.0919 | 65.0919 | 65.0919 | 65.0919 | 65.0919 | 65.0919 | 65.0919 | 65.0919 | 65.0919 | 65.0919 | 65.0919 | 65.0919
75% | 803.6248 | 33.7733 | 46.8282 | 50.2195 | 50.7964 | 51.245 | 52.0202 | 53.786 | 54.9666 | 56.4637 | 57.24 | 57.9219 | 56.6592 | 58.1354 | 60.4571 | 58.6923 | 58.6923 | 58.6923 | 58.6923 | 58.6923 | 58.6923 | 58.6923 | 58.6923 | 58.6923 | 58.6923 | 58.6923 | 58.6923 | 58.6923 | 58.6923 | 58.6923 | 58.6923 | 75% | 803.6248 | 36.1483 | 49.0386 | 52.5623 | 53.1063 | 53.4502 | 54.2086 | 56.0019 | 56.9795 | 58.8448 | 64.5182 | 59.8372 | 58.9204 | 60.154 | 62.8539 | 61.0236 | 61.0236 | 61.0236 | 61.0236 | 61.0236 | 61.0236 | 61.0236 | 61.0236 | 61.0236 | 61.0236 | 61.0236 | 61.0236 | 61.0236 | 61.0236 | 61.0236 | 61.0236
70% | 1155.2107 | 31.5218 | 43.7063 | 46.8715 | 47.4099 | 47.8287 | 48.5522 | 50.2003 | 51.3021 | 52.6994 | 53.424 | 54.0604 | 52.8819 | 54.2597 | 56.4267 | 54.7795 | 54.7795 | 54.7795 | 54.7795 | 54.7795 | 54.7795 | 54.7795 | 54.7795 | 54.7795 | 54.7795 | 54.7795 | 54.7795 | 54.7795 | 54.7795 | 54.7795 | 54.7795 | 70% | 1155.2107 | 33.7384 | 45.7693 | 49.0582 | 49.5659 | 49.8869 | 50.5947 | 52.2685 | 53.1809 | 54.9218 | 60.217 | 55.8481 | 54.9924 | 56.1438 | 58.6637 | 56.9554 | 56.9554 | 56.9554 | 56.9554 | 56.9554 | 56.9554 | 56.9554 | 56.9554 | 56.9554 | 56.9554 | 56.9554 | 56.9554 | 56.9554 | 56.9554 | 56.9554 | 56.9554
65% | 1553.1596 | 29.2702 | 40.5844 | 43.5236 | 44.0235 | 44.4124 | 45.0842 | 46.6145 | 47.6377 | 48.9352 | 49.608 | 50.1989 | 49.1046 | 50.384 | 52.3962 | 50.8667 | 50.8667 | 50.8667 | 50.8667 | 50.8667 | 50.8667 | 50.8667 | 50.8667 | 50.8667 | 50.8667 | 50.8667 | 50.8667 | 50.8667 | 50.8667 | 50.8667 | 50.8667 | 65% | 1553.1596 | 31.3286 | 42.5001 | 45.554 | 46.0254 | 46.3235 | 46.9808 | 48.535 | 49.3822 | 50.9988 | 55.9158 | 51.8589 | 51.0643 | 52.1335 | 54.4734 | 52.8871 | 52.8871 | 52.8871 | 52.8871 | 52.8871 | 52.8871 | 52.8871 | 52.8871 | 52.8871 | 52.8871 | 52.8871 | 52.8871 | 52.8871 | 52.8871 | 52.8871 | 52.8871
60% | 2026.2996 | 27.0187 | 37.4626 | 40.1756 | 40.6371 | 40.996 | 41.6162 | 43.0288 | 43.9733 | 45.1709 | 45.792 | 46.3375 | 45.3273 | 46.5083 | 48.3657 | 46.9539 | 46.9539 | 46.9539 | 46.9539 | 46.9539 | 46.9539 | 46.9539 | 46.9539 | 46.9539 | 46.9539 | 46.9539 | 46.9539 | 46.9539 | 46.9539 | 46.9539 | 46.9539 | 60% | 2026.2996 | 28.9187 | 39.2308 | 42.0499 | 42.485 | 42.7602 | 43.3669 | 44.8016 | 45.5836 | 47.0758 | 51.6146 | 47.8698 | 47.1363 | 48.1232 | 50.2832 | 48.8189 | 48.8189 | 48.8189 | 48.8189 | 48.8189 | 48.8189 | 48.8189 | 48.8189 | 48.8189 | 48.8189 | 48.8189 | 48.8189 | 48.8189 | 48.8189 | 48.8189 | 48.8189
55% | 2598.4068 | 24.7671 | 34.3407 | 36.8276 | 37.2507 | 37.5797 | 38.1482 | 39.4431 | 40.3088 | 41.4067 | 41.976 | 42.476 | 41.55 | 42.6326 | 44.3352 | 43.041 | 43.041 | 43.041 | 43.041 | 43.041 | 43.041 | 43.041 | 43.041 | 43.041 | 43.041 | 43.041 | 43.041 | 43.041 | 43.041 | 43.041 | 43.041 | 55% | 2598.4068 | 26.5088 | 35.9616 | 38.5457 | 38.9446 | 39.1968 | 39.753 | 41.0681 | 41.785 | 43.1529 | 47.3134 | 43.8806 | 43.2083 | 44.113 | 46.0929 | 44.7507 | 44.7507 | 44.7507 | 44.7507 | 44.7507 | 44.7507 | 44.7507 | 44.7507 | 44.7507 | 44.7507 | 44.7507 | 44.7507 | 44.7507 | 44.7507 | 44.7507 | 44.7507
50% | 3233.5201 | 22.5156 | 31.2188 | 33.4797 | 33.8642 | 34.1634 | 34.6802 | 35.8573 | 36.6444 | 37.6424 | 38.16 | 38.6146 | 37.7728 | 38.7569 | 40.3048 | 39.1282 | 39.1282 | 39.1282 | 39.1282 | 39.1282 | 39.1282 | 39.1282 | 39.1282 | 39.1282 | 39.1282 | 39.1282 | 39.1282 | 39.1282 | 39.1282 | 39.1282 | 39.1282 | 50% | 3233.5201 | 24.0989 | 32.6924 | 35.0416 | 35.4042 | 35.6335 | 36.139 | 37.3346 | 37.9863 | 39.2299 | 43.0122 | 39.8915 | 39.2803 | 40.1027 | 41.9026 | 40.6824 | 40.6824 | 40.6824 | 40.6824 | 40.6824 | 40.6824 | 40.6824 | 40.6824 | 40.6824 | 40.6824 | 40.6824 | 40.6824 | 40.6824 | 40.6824 | 40.6824 | 40.6824
45% | 3775.313 | 20.264 | 28.0969 | 30.1317 | 30.4778 | 30.747 | 31.2121 | 32.2716 | 32.9799 | 33.8782 | 34.344 | 34.7531 | 33.9955 | 34.8812 | 36.2743 | 35.2154 | 35.2154 | 35.2154 | 35.2154 | 35.2154 | 35.2154 | 35.2154 | 35.2154 | 35.2154 | 35.2154 | 35.2154 | 35.2154 | 35.2154 | 35.2154 | 35.2154 | 35.2154 | 45% | 3775.313 | 21.689 | 29.4231 | 31.5374 | 31.8638 | 32.0701 | 32.5251 | 33.6012 | 34.1877 | 35.3069 | 38.7109 | 35.9023 | 35.3522 | 36.0924 | 37.7124 | 36.6142 | 36.6142 | 36.6142 | 36.6142 | 36.6142 | 36.6142 | 36.6142 | 36.6142 | 36.6142 | 36.6142 | 36.6142 | 36.6142 | 36.6142 | 36.6142 | 36.6142 | 36.6142
40% | 4072.8088 | 18.0124 | 24.975 | 26.7837 | 27.0914 | 27.3307 | 27.7441 | 28.6859 | 29.3155 | 30.114 | 30.528 | 30.8917 | 30.2182 | 31.0055 | 32.2438 | 31.3026 | 31.3026 | 31.3026 | 31.3026 | 31.3026 | 31.3026 | 31.3026 | 31.3026 | 31.3026 | 31.3026 | 31.3026 | 31.3026 | 31.3026 | 31.3026 | 31.3026 | 31.3026 | 40% | 4072.8088 | 19.2791 | 26.1539 | 28.0332 | 28.3234 | 28.5068 | 28.9112 | 29.8677 | 30.3891 | 31.3839 | 34.4097 | 31.9132 | 31.4242 | 32.0822 | 33.5221 | 32.5459 | 32.5459 | 32.5459 | 32.5459 | 32.5459 | 32.5459 | 32.5459 | 32.5459 | 32.5459 | 32.5459 | 32.5459 | 32.5459 | 32.5459 | 32.5459 | 32.5459 | 32.5459
35% | 4198.821 | 15.7609 | 21.8532 | 23.4358 | 23.705 | 23.9144 | 24.2761 | 25.1001 | 25.6511 | 26.3497 | 26.712 | 27.0302 | 26.4409 | 27.1298 | 28.2133 | 27.3897 | 27.3897 | 27.3897 | 27.3897 | 27.3897 | 27.3897 | 27.3897 | 27.3897 | 27.3897 | 27.3897 | 27.3897 | 27.3897 | 27.3897 | 27.3897 | 27.3897 | 27.3897 | 35% | 4198.821 | 16.8692 | 22.8847 | 24.5291 | 24.7829 | 24.9434 | 25.2973 | 26.1342 | 26.5904 | 27.4609 | 30.1085 | 27.924 | 27.4962 | 28.0719 | 29.3318 | 28.4777 | 28.4777 | 28.4777 | 28.4777 | 28.4777 | 28.4777 | 28.4777 | 28.4777 | 28.4777 | 28.4777 | 28.4777 | 28.4777 | 28.4777 | 28.4777 | 28.4777 | 28.4777
30% | 4271.3374 | 13.5093 | 18.7313 | 20.0878 | 20.3185 | 20.498 | 20.8081 | 21.5144 | 21.9866 | 22.5855 | 22.896 | 23.1687 | 22.6637 | 23.2542 | 24.1829 | 23.4769 | 23.4769 | 23.4769 | 23.4769 | 23.4769 | 23.4769 | 23.4769 | 23.4769 | 23.4769 | 23.4769 | 23.4769 | 23.4769 | 23.4769 | 23.4769 | 23.4769 | 23.4769 | 30% | 4271.3374 | 14.4593 | 19.6154 | 21.0249 | 21.2425 | 21.3801 | 21.6834 | 22.4008 | 22.7918 | 23.5379 | 25.8073 | 23.9349 | 23.5682 | 24.0616 | 25.1416 | 24.4094 | 24.4094 | 24.4094 | 24.4094 | 24.4094 | 24.4094 | 24.4094 | 24.4094 | 24.4094 | 24.4094 | 24.4094 | 24.4094 | 24.4094 | 24.4094 | 24.4094 | 24.4094
25% | 4321.8611 | 11.2578 | 15.6094 | 16.7398 | 16.9321 | 17.0817 | 17.3401 | 17.9287 | 18.3222 | 18.8212 | 19.08 | 19.3073 | 18.8864 | 19.3785 | 20.1524 | 19.5641 | 19.5641 | 19.5641 | 19.5641 | 19.5641 | 19.5641 | 19.5641 | 19.5641 | 19.5641 | 19.5641 | 19.5641 | 19.5641 | 19.5641 | 19.5641 | 19.5641 | 19.5641 | 25% | 4321.8611 | 12.0494 | 16.3462 | 17.5208 | 17.7021 | 17.8167 | 18.0695 | 18.6673 | 18.9932 | 19.6149 | 21.5061 | 19.9457 | 19.6401 | 20.0513 | 20.9513 | 20.3412 | 20.3412 | 20.3412 | 20.3412 | 20.3412 | 20.3412 | 20.3412 | 20.3412 | 20.3412 | 20.3412 | 20.3412 | 20.3412 | 20.3412 | 20.3412 | 20.3412 | 20.3412
20% | 4353.067 | 9.0062 | 12.4875 | 13.3919 | 13.5457 | 13.6653 | 13.8721 | 14.3429 | 14.6578 | 15.057 | 15.264 | 15.4458 | 15.1091 | 15.5028 | 16.1219 | 15.6513 | 15.6513 | 15.6513 | 15.6513 | 15.6513 | 15.6513 | 15.6513 | 15.6513 | 15.6513 | 15.6513 | 15.6513 | 15.6513 | 15.6513 | 15.6513 | 15.6513 | 15.6513 | 20% | 4353.067 | 9.6396 | 13.0769 | 14.0166 | 14.1617 | 14.2534 | 14.4556 | 14.9339 | 15.1945 | 15.6919 | 17.2049 | 15.9566 | 15.7121 | 16.0411 | 16.7611 | 16.273 | 16.273 | 16.273 | 16.273 | 16.273 | 16.273 | 16.273 | 16.273 | 16.273 | 16.273 | 16.273 | 16.273 | 16.273 | 16.273 | 16.273 | 16.273
15% | 4369.4129 | 6.7547 | 9.3656 | 10.0439 | 10.1593 | 10.249 | 10.404 | 10.7572 | 10.9933 | 11.2927 | 11.448 | 11.5844 | 11.3318 | 11.6271 | 12.0914 | 11.7385 | 11.7385 | 11.7385 | 11.7385 | 11.7385 | 11.7385 | 11.7385 | 11.7385 | 11.7385 | 11.7385 | 11.7385 | 11.7385 | 11.7385 | 11.7385 | 11.7385 | 11.7385 | 15% | 4369.4129 | 7.2297 | 9.8077 | 10.5125 | 10.6213 | 10.69 | 10.8417 | 11.2004 | 11.3959 | 11.769 | 12.9036 | 11.9674 | 11.7841 | 12.0308 | 12.5708 | 12.2047 | 12.2047 | 12.2047 | 12.2047 | 12.2047 | 12.2047 | 12.2047 | 12.2047 | 12.2047 | 12.2047 | 12.2047 | 12.2047 | 12.2047 | 12.2047 | 12.2047 | 12.2047
10% | 4378.6261 | 4.5031 | 6.2438 | 6.6959 | 6.7728 | 6.8327 | 6.936 | 7.1715 | 7.3289 | 7.5285 | 7.632 | 7.7229 | 7.5546 | 7.7514 | 8.061 | 7.8256 | 7.8256 | 7.8256 | 7.8256 | 7.8256 | 7.8256 | 7.8256 | 7.8256 | 7.8256 | 7.8256 | 7.8256 | 7.8256 | 7.8256 | 7.8256 | 7.8256 | 7.8256 | 10% | 4378.6261 | 4.8198 | 6.5385 | 7.0083 | 7.0808 | 7.1267 | 7.2278 | 7.4669 | 7.5973 | 7.846 | 8.6024 | 7.9783 | 7.8561 | 8.0205 | 8.3805 | 8.1365 | 8.1365 | 8.1365 | 8.1365 | 8.1365 | 8.1365 | 8.1365 | 8.1365 | 8.1365 | 8.1365 | 8.1365 | 8.1365 | 8.1365 | 8.1365 | 8.1365 | 8.1365
5% | 4391.7028 | 2.2516 | 3.1219 | 3.348 | 3.3864 | 3.4163 | 3.468 | 3.5857 | 3.6644 | 3.7642 | 3.816 | 3.8615 | 3.7773 | 3.8757 | 4.0305 | 3.9128 | 3.9128 | 3.9128 | 3.9128 | 3.9128 | 3.9128 | 3.9128 | 3.9128 | 3.9128 | 3.9128 | 3.9128 | 3.9128 | 3.9128 | 3.9128 | 3.9128 | 3.9128 | 5% | 4391.7028 | 2.4099 | 3.2692 | 3.5042 | 3.5404 | 3.5633 | 3.6139 | 3.7335 | 3.7986 | 3.923 | 4.3012 | 3.9891 | 3.928 | 4.0103 | 4.1903 | 4.0682 | 4.0682 | 4.0682 | 4.0682 | 4.0682 | 4.0682 | 4.0682 | 4.0682 | 4.0682 | 4.0682 | 4.0682 | 4.0682 | 4.0682 | 4.0682 | 4.0682 | 4.0682
9.992e-14% | 4391.7028 | 4.4995e-14 | 6.2388e-14 | 6.6906e-14 | 6.7674e-14 | 6.8272e-14 | 6.9305e-14 | 7.1657e-14 | 7.323e-14 | 7.5225e-14 | 7.6259e-14 | 7.7167e-14 | 7.5485e-14 | 7.7452e-14 | 8.0545e-14 | 7.8194e-14 | 7.8194e-14 | 7.8194e-14 | 7.8194e-14 | 7.8194e-14 | 7.8194e-14 | 7.8194e-14 | 7.8194e-14 | 7.8194e-14 | 7.8194e-14 | 7.8194e-14 | 7.8194e-14 | 7.8194e-14 | 7.8194e-14 | 7.8194e-14 | 7.8194e-14 | 9.992e-14% | 4391.7028 | 4.8159e-14 | 6.5332e-14 | 7.0027e-14 | 7.0752e-14 | 7.121e-14 | 7.222e-14 | 7.461e-14 | 7.5912e-14 | 7.8397e-14 | 8.5956e-14 | 7.9719e-14 | 7.8498e-14 | 8.0141e-14 | 8.3738e-14 | 8.13e-14 | 8.13e-14 | 8.13e-14 | 8.13e-14 | 8.13e-14 | 8.13e-14 | 8.13e-14 | 8.13e-14 | 8.13e-14 | 8.13e-14 | 8.13e-14 | 8.13e-14 | 8.13e-14 | 8.13e-14 | 8.13e-14 | 8.13e-14
Summer Season | [31 empty] | Summer Season
P50 | [31 empty] | P10
% of MD | Summer - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Summer - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 51.1621 | 67.921 | 72.4827 | 72.3498 | 72.345 | 72.8648 | 73.4353 | 74.6066 | 75.4483 | 75.9048 | 76.4041 | 76.8611 | 77.687 | 78.7121 | 78.6404 | 78.6404 | 78.6404 | 78.6404 | 78.6404 | 78.6404 | 78.6404 | 78.6404 | 78.6404 | 78.6404 | 78.6404 | 78.6404 | 78.6404 | 78.6404 | 78.6404 | 78.6404 | 100% | 0 | 57.0282 | 73.8207 | 78.2145 | 77.9508 | 77.9694 | 78.4199 | 79.6095 | 80.4052 | 81.1846 | 82.0962 | 82.9406 | 83.7606 | 83.8537 | 84.8109 | 84.0841 | 84.0841 | 84.0841 | 84.0841 | 84.0841 | 84.0841 | 84.0841 | 84.0841 | 84.0841 | 84.0841 | 84.0841 | 84.0841 | 84.0841 | 84.0841 | 84.0841 | 84.0841
99% | 0 | 50.6505 | 67.2418 | 71.7579 | 71.6263 | 71.6215 | 72.1362 | 72.701 | 73.8605 | 74.6938 | 75.1458 | 75.64 | 76.0925 | 76.9101 | 77.9249 | 77.854 | 77.854 | 77.854 | 77.854 | 77.854 | 77.854 | 77.854 | 77.854 | 77.854 | 77.854 | 77.854 | 77.854 | 77.854 | 77.854 | 77.854 | 77.854 | 99% | 1.5127 | 56.4579 | 73.0825 | 77.4324 | 77.1713 | 77.1897 | 77.6357 | 78.8134 | 79.6012 | 80.3728 | 81.2753 | 82.1112 | 82.923 | 83.0151 | 83.9628 | 83.2432 | 83.2432 | 83.2432 | 83.2432 | 83.2432 | 83.2432 | 83.2432 | 83.2432 | 83.2432 | 83.2432 | 83.2432 | 83.2432 | 83.2432 | 83.2432 | 83.2432 | 83.2432
98% | 0 | 50.1389 | 66.5626 | 71.033 | 70.9028 | 70.8981 | 71.4075 | 71.9666 | 73.1145 | 73.9393 | 74.3867 | 74.876 | 75.3239 | 76.1333 | 77.1378 | 77.0676 | 77.0676 | 77.0676 | 77.0676 | 77.0676 | 77.0676 | 77.0676 | 77.0676 | 77.0676 | 77.0676 | 77.0676 | 77.0676 | 77.0676 | 77.0676 | 77.0676 | 77.0676 | 98% | 2.269 | 55.8876 | 72.3443 | 76.6503 | 76.3918 | 76.41 | 76.8515 | 78.0173 | 78.7971 | 79.5609 | 80.4543 | 81.2818 | 82.0854 | 82.1766 | 83.1147 | 82.4024 | 82.4024 | 82.4024 | 82.4024 | 82.4024 | 82.4024 | 82.4024 | 82.4024 | 82.4024 | 82.4024 | 82.4024 | 82.4024 | 82.4024 | 82.4024 | 82.4024 | 82.4024
97% | 0.37816 | 49.6272 | 65.8834 | 70.3082 | 70.1794 | 70.1746 | 70.6789 | 71.2323 | 72.3684 | 73.1848 | 73.6277 | 74.112 | 74.5553 | 75.3564 | 76.3507 | 76.2812 | 76.2812 | 76.2812 | 76.2812 | 76.2812 | 76.2812 | 76.2812 | 76.2812 | 76.2812 | 76.2812 | 76.2812 | 76.2812 | 76.2812 | 76.2812 | 76.2812 | 76.2812 | 97% | 3.7816 | 55.3173 | 71.6061 | 75.8681 | 75.6123 | 75.6303 | 76.0673 | 77.2212 | 77.9931 | 78.7491 | 79.6334 | 80.4523 | 81.2478 | 81.338 | 82.2666 | 81.5615 | 81.5615 | 81.5615 | 81.5615 | 81.5615 | 81.5615 | 81.5615 | 81.5615 | 81.5615 | 81.5615 | 81.5615 | 81.5615 | 81.5615 | 81.5615 | 81.5615 | 81.5615
95% | 2.269 | 48.604 | 64.5249 | 68.8586 | 68.7324 | 68.7277 | 69.2216 | 69.7636 | 70.8763 | 71.6758 | 72.1096 | 72.5839 | 73.0181 | 73.8027 | 74.7765 | 74.7084 | 74.7084 | 74.7084 | 74.7084 | 74.7084 | 74.7084 | 74.7084 | 74.7084 | 74.7084 | 74.7084 | 74.7084 | 74.7084 | 74.7084 | 74.7084 | 74.7084 | 74.7084 | 95% | 6.0506 | 54.1768 | 70.1297 | 74.3038 | 74.0533 | 74.071 | 74.4989 | 75.629 | 76.385 | 77.1254 | 77.9914 | 78.7935 | 79.5726 | 79.661 | 80.5703 | 79.8799 | 79.8799 | 79.8799 | 79.8799 | 79.8799 | 79.8799 | 79.8799 | 79.8799 | 79.8799 | 79.8799 | 79.8799 | 79.8799 | 79.8799 | 79.8799 | 79.8799 | 79.8799
90% | 5.6725 | 46.0459 | 61.1289 | 65.2344 | 65.1149 | 65.1105 | 65.5784 | 66.0918 | 67.1459 | 67.9034 | 68.3143 | 68.7637 | 69.175 | 69.9183 | 70.8409 | 70.7764 | 70.7764 | 70.7764 | 70.7764 | 70.7764 | 70.7764 | 70.7764 | 70.7764 | 70.7764 | 70.7764 | 70.7764 | 70.7764 | 70.7764 | 70.7764 | 70.7764 | 70.7764 | 90% | 16.2611 | 51.3254 | 66.4386 | 70.3931 | 70.1557 | 70.1725 | 70.5779 | 71.6485 | 72.3647 | 73.0662 | 73.8866 | 74.6465 | 75.3846 | 75.4683 | 76.3298 | 75.6757 | 75.6757 | 75.6757 | 75.6757 | 75.6757 | 75.6757 | 75.6757 | 75.6757 | 75.6757 | 75.6757 | 75.6757 | 75.6757 | 75.6757 | 75.6757 | 75.6757 | 75.6757
85% | 15.8829 | 43.4878 | 57.7328 | 61.6103 | 61.4974 | 61.4932 | 61.9351 | 62.42 | 63.4156 | 64.131 | 64.5191 | 64.9435 | 65.332 | 66.034 | 66.9053 | 66.8444 | 66.8444 | 66.8444 | 66.8444 | 66.8444 | 66.8444 | 66.8444 | 66.8444 | 66.8444 | 66.8444 | 66.8444 | 66.8444 | 66.8444 | 66.8444 | 66.8444 | 66.8444 | 85% | 26.4715 | 48.4739 | 62.7476 | 66.4824 | 66.2582 | 66.274 | 66.6569 | 67.6681 | 68.3445 | 69.0069 | 69.7818 | 70.4995 | 71.1965 | 71.2756 | 72.0892 | 71.4715 | 71.4715 | 71.4715 | 71.4715 | 71.4715 | 71.4715 | 71.4715 | 71.4715 | 71.4715 | 71.4715 | 71.4715 | 71.4715 | 71.4715 | 71.4715 | 71.4715 | 71.4715
80% | 31.0095 | 40.9297 | 54.3368 | 57.9862 | 57.8799 | 57.876 | 58.2919 | 58.7483 | 59.6853 | 60.3586 | 60.7239 | 61.1233 | 61.4889 | 62.1496 | 62.9697 | 62.9123 | 62.9123 | 62.9123 | 62.9123 | 62.9123 | 62.9123 | 62.9123 | 62.9123 | 62.9123 | 62.9123 | 62.9123 | 62.9123 | 62.9123 | 62.9123 | 62.9123 | 62.9123 | 80% | 34.0348 | 45.6225 | 59.0566 | 62.5716 | 62.3606 | 62.3755 | 62.7359 | 63.6876 | 64.3242 | 64.9477 | 65.677 | 66.3524 | 67.0085 | 67.0829 | 67.8487 | 67.2672 | 67.2672 | 67.2672 | 67.2672 | 67.2672 | 67.2672 | 67.2672 | 67.2672 | 67.2672 | 67.2672 | 67.2672 | 67.2672 | 67.2672 | 67.2672 | 67.2672 | 67.2672
75% | 72.9857 | 38.3716 | 50.9407 | 54.362 | 54.2624 | 54.2587 | 54.6486 | 55.0765 | 55.955 | 56.5862 | 56.9286 | 57.3031 | 57.6458 | 58.2653 | 59.0341 | 58.9803 | 58.9803 | 58.9803 | 58.9803 | 58.9803 | 58.9803 | 58.9803 | 58.9803 | 58.9803 | 58.9803 | 58.9803 | 58.9803 | 58.9803 | 58.9803 | 58.9803 | 58.9803 | 75% | 48.405 | 42.7711 | 55.3655 | 58.6609 | 58.4631 | 58.4771 | 58.8149 | 59.7071 | 60.3039 | 60.8885 | 61.5722 | 62.2054 | 62.8205 | 62.8902 | 63.6082 | 63.063 | 63.063 | 63.063 | 63.063 | 63.063 | 63.063 | 63.063 | 63.063 | 63.063 | 63.063 | 63.063 | 63.063 | 63.063 | 63.063 | 63.063 | 63.063
70% | 150.5094 | 35.8135 | 47.5447 | 50.7379 | 50.6449 | 50.6415 | 51.0054 | 51.4047 | 52.2246 | 52.8138 | 53.1334 | 53.4829 | 53.8028 | 54.3809 | 55.0984 | 55.0483 | 55.0483 | 55.0483 | 55.0483 | 55.0483 | 55.0483 | 55.0483 | 55.0483 | 55.0483 | 55.0483 | 55.0483 | 55.0483 | 55.0483 | 55.0483 | 55.0483 | 55.0483 | 70% | 76.3892 | 39.9197 | 51.6745 | 54.7502 | 54.5656 | 54.5786 | 54.8939 | 55.7266 | 56.2837 | 56.8292 | 57.4674 | 58.0584 | 58.6324 | 58.6976 | 59.3676 | 58.8588 | 58.8588 | 58.8588 | 58.8588 | 58.8588 | 58.8588 | 58.8588 | 58.8588 | 58.8588 | 58.8588 | 58.8588 | 58.8588 | 58.8588 | 58.8588 | 58.8588 | 58.8588
65% | 359.6342 | 33.2554 | 44.1486 | 47.1138 | 47.0274 | 47.0242 | 47.3621 | 47.733 | 48.4943 | 49.0414 | 49.3381 | 49.6627 | 49.9597 | 50.4966 | 51.1628 | 51.1163 | 51.1163 | 51.1163 | 51.1163 | 51.1163 | 51.1163 | 51.1163 | 51.1163 | 51.1163 | 51.1163 | 51.1163 | 51.1163 | 51.1163 | 51.1163 | 51.1163 | 51.1163 | 65% | 114.2056 | 37.0683 | 47.9835 | 50.8395 | 50.668 | 50.6801 | 50.9729 | 51.7462 | 52.2634 | 52.77 | 53.3626 | 53.9114 | 54.4444 | 54.5049 | 55.1271 | 54.6546 | 54.6546 | 54.6546 | 54.6546 | 54.6546 | 54.6546 | 54.6546 | 54.6546 | 54.6546 | 54.6546 | 54.6546 | 54.6546 | 54.6546 | 54.6546 | 54.6546 | 54.6546
60% | 689.7717 | 30.6973 | 40.7526 | 43.4896 | 43.4099 | 43.407 | 43.7189 | 44.0612 | 44.764 | 45.269 | 45.5429 | 45.8424 | 46.1167 | 46.6122 | 47.2272 | 47.1843 | 47.1843 | 47.1843 | 47.1843 | 47.1843 | 47.1843 | 47.1843 | 47.1843 | 47.1843 | 47.1843 | 47.1843 | 47.1843 | 47.1843 | 47.1843 | 47.1843 | 47.1843 | 60% | 178.1154 | 34.2169 | 44.2924 | 46.9287 | 46.7705 | 46.7817 | 47.0519 | 47.7657 | 48.2431 | 48.7108 | 49.2577 | 49.7643 | 50.2564 | 50.3122 | 50.8865 | 50.4504 | 50.4504 | 50.4504 | 50.4504 | 50.4504 | 50.4504 | 50.4504 | 50.4504 | 50.4504 | 50.4504 | 50.4504 | 50.4504 | 50.4504 | 50.4504 | 50.4504 | 50.4504
55% | 1095.5419 | 28.1392 | 37.3565 | 39.8655 | 39.7924 | 39.7897 | 40.0757 | 40.3894 | 41.0336 | 41.4965 | 41.7476 | 42.0222 | 42.2736 | 42.7279 | 43.2916 | 43.2522 | 43.2522 | 43.2522 | 43.2522 | 43.2522 | 43.2522 | 43.2522 | 43.2522 | 43.2522 | 43.2522 | 43.2522 | 43.2522 | 43.2522 | 43.2522 | 43.2522 | 43.2522 | 55% | 311.6074 | 31.3655 | 40.6014 | 43.018 | 42.8729 | 42.8832 | 43.131 | 43.7852 | 44.2229 | 44.6515 | 45.1529 | 45.6173 | 46.0683 | 46.1195 | 46.646 | 46.2462 | 46.2462 | 46.2462 | 46.2462 | 46.2462 | 46.2462 | 46.2462 | 46.2462 | 46.2462 | 46.2462 | 46.2462 | 46.2462 | 46.2462 | 46.2462 | 46.2462 | 46.2462
50% | 1666.1918 | 25.581 | 33.9605 | 36.2413 | 36.1749 | 36.1725 | 36.4324 | 36.7177 | 37.3033 | 37.7241 | 37.9524 | 38.202 | 38.4306 | 38.8435 | 39.356 | 39.3202 | 39.3202 | 39.3202 | 39.3202 | 39.3202 | 39.3202 | 39.3202 | 39.3202 | 39.3202 | 39.3202 | 39.3202 | 39.3202 | 39.3202 | 39.3202 | 39.3202 | 39.3202 | 50% | 636.0723 | 28.5141 | 36.9103 | 39.1073 | 38.9754 | 38.9847 | 39.21 | 39.8047 | 40.2026 | 40.5923 | 41.0481 | 41.4703 | 41.8803 | 41.9268 | 42.4054 | 42.042 | 42.042 | 42.042 | 42.042 | 42.042 | 42.042 | 42.042 | 42.042 | 42.042 | 42.042 | 42.042 | 42.042 | 42.042 | 42.042 | 42.042 | 42.042
45% | 2506.0947 | 23.0229 | 30.5644 | 32.6172 | 32.5574 | 32.5552 | 32.7892 | 33.0459 | 33.573 | 33.9517 | 34.1572 | 34.3818 | 34.5875 | 34.9592 | 35.4204 | 35.3882 | 35.3882 | 35.3882 | 35.3882 | 35.3882 | 35.3882 | 35.3882 | 35.3882 | 35.3882 | 35.3882 | 35.3882 | 35.3882 | 35.3882 | 35.3882 | 35.3882 | 35.3882 | 45% | 1179.4944 | 25.6627 | 33.2193 | 35.1965 | 35.0779 | 35.0862 | 35.289 | 35.8243 | 36.1824 | 36.5331 | 36.9433 | 37.3233 | 37.6923 | 37.7341 | 38.1649 | 37.8378 | 37.8378 | 37.8378 | 37.8378 | 37.8378 | 37.8378 | 37.8378 | 37.8378 | 37.8378 | 37.8378 | 37.8378 | 37.8378 | 37.8378 | 37.8378 | 37.8378 | 37.8378
40% | 3164.4787 | 20.4648 | 27.1684 | 28.9931 | 28.9399 | 28.938 | 29.1459 | 29.3741 | 29.8426 | 30.1793 | 30.3619 | 30.5616 | 30.7444 | 31.0748 | 31.4848 | 31.4562 | 31.4562 | 31.4562 | 31.4562 | 31.4562 | 31.4562 | 31.4562 | 31.4562 | 31.4562 | 31.4562 | 31.4562 | 31.4562 | 31.4562 | 31.4562 | 31.4562 | 31.4562 | 40% | 1808.3816 | 22.8113 | 29.5283 | 31.2858 | 31.1803 | 31.1878 | 31.368 | 31.8438 | 32.1621 | 32.4738 | 32.8385 | 33.1762 | 33.5042 | 33.5415 | 33.9244 | 33.6336 | 33.6336 | 33.6336 | 33.6336 | 33.6336 | 33.6336 | 33.6336 | 33.6336 | 33.6336 | 33.6336 | 33.6336 | 33.6336 | 33.6336 | 33.6336 | 33.6336 | 33.6336
35% | 3551.3408 | 17.9067 | 23.7723 | 25.3689 | 25.3224 | 25.3207 | 25.5027 | 25.7024 | 26.1123 | 26.4069 | 26.5667 | 26.7414 | 26.9014 | 27.1905 | 27.5492 | 27.5241 | 27.5241 | 27.5241 | 27.5241 | 27.5241 | 27.5241 | 27.5241 | 27.5241 | 27.5241 | 27.5241 | 27.5241 | 27.5241 | 27.5241 | 27.5241 | 27.5241 | 27.5241 | 35% | 2779.1293 | 19.9599 | 25.8372 | 27.3751 | 27.2828 | 27.2893 | 27.447 | 27.8633 | 28.1418 | 28.4146 | 28.7337 | 29.0292 | 29.3162 | 29.3488 | 29.6838 | 29.4294 | 29.4294 | 29.4294 | 29.4294 | 29.4294 | 29.4294 | 29.4294 | 29.4294 | 29.4294 | 29.4294 | 29.4294 | 29.4294 | 29.4294 | 29.4294 | 29.4294 | 29.4294
30% | 3758.953 | 15.3486 | 20.3763 | 21.7448 | 21.705 | 21.7035 | 21.8595 | 22.0306 | 22.382 | 22.6345 | 22.7714 | 22.9212 | 23.0583 | 23.3061 | 23.6136 | 23.5921 | 23.5921 | 23.5921 | 23.5921 | 23.5921 | 23.5921 | 23.5921 | 23.5921 | 23.5921 | 23.5921 | 23.5921 | 23.5921 | 23.5921 | 23.5921 | 23.5921 | 23.5921 | 30% | 3814.165 | 17.1085 | 22.1462 | 23.4644 | 23.3852 | 23.3908 | 23.526 | 23.8828 | 24.1216 | 24.3554 | 24.6289 | 24.8822 | 25.1282 | 25.1561 | 25.4433 | 25.2252 | 25.2252 | 25.2252 | 25.2252 | 25.2252 | 25.2252 | 25.2252 | 25.2252 | 25.2252 | 25.2252 | 25.2252 | 25.2252 | 25.2252 | 25.2252 | 25.2252 | 25.2252
25% | 3926.4798 | 12.7905 | 16.9802 | 18.1207 | 18.0875 | 18.0862 | 18.2162 | 18.3588 | 18.6517 | 18.8621 | 18.9762 | 19.101 | 19.2153 | 19.4218 | 19.678 | 19.6601 | 19.6601 | 19.6601 | 19.6601 | 19.6601 | 19.6601 | 19.6601 | 19.6601 | 19.6601 | 19.6601 | 19.6601 | 19.6601 | 19.6601 | 19.6601 | 19.6601 | 19.6601 | 25% | 4166.9923 | 14.257 | 18.4552 | 19.5536 | 19.4877 | 19.4924 | 19.605 | 19.9024 | 20.1013 | 20.2962 | 20.5241 | 20.7351 | 20.9402 | 20.9634 | 21.2027 | 21.021 | 21.021 | 21.021 | 21.021 | 21.021 | 21.021 | 21.021 | 21.021 | 21.021 | 21.021 | 21.021 | 21.021 | 21.021 | 21.021 | 21.021 | 21.021
20% | 4050.5177 | 10.2324 | 13.5842 | 14.4965 | 14.47 | 14.469 | 14.573 | 14.6871 | 14.9213 | 15.0897 | 15.181 | 15.2808 | 15.3722 | 15.5374 | 15.7424 | 15.7281 | 15.7281 | 15.7281 | 15.7281 | 15.7281 | 15.7281 | 15.7281 | 15.7281 | 15.7281 | 15.7281 | 15.7281 | 15.7281 | 15.7281 | 15.7281 | 15.7281 | 15.7281 | 20% | 4282.7105 | 11.4056 | 14.7641 | 15.6429 | 15.5902 | 15.5939 | 15.684 | 15.9219 | 16.081 | 16.2369 | 16.4192 | 16.5881 | 16.7521 | 16.7707 | 16.9622 | 16.8168 | 16.8168 | 16.8168 | 16.8168 | 16.8168 | 16.8168 | 16.8168 | 16.8168 | 16.8168 | 16.8168 | 16.8168 | 16.8168 | 16.8168 | 16.8168 | 16.8168 | 16.8168
15% | 4152.622 | 7.6743 | 10.1881 | 10.8724 | 10.8525 | 10.8517 | 10.9297 | 11.0153 | 11.191 | 11.3172 | 11.3857 | 11.4606 | 11.5292 | 11.6531 | 11.8068 | 11.7961 | 11.7961 | 11.7961 | 11.7961 | 11.7961 | 11.7961 | 11.7961 | 11.7961 | 11.7961 | 11.7961 | 11.7961 | 11.7961 | 11.7961 | 11.7961 | 11.7961 | 11.7961 | 15% | 4364.7722 | 8.5542 | 11.0731 | 11.7322 | 11.6926 | 11.6954 | 11.763 | 11.9414 | 12.0608 | 12.1777 | 12.3144 | 12.4411 | 12.5641 | 12.578 | 12.7216 | 12.6126 | 12.6126 | 12.6126 | 12.6126 | 12.6126 | 12.6126 | 12.6126 | 12.6126 | 12.6126 | 12.6126 | 12.6126 | 12.6126 | 12.6126 | 12.6126 | 12.6126 | 12.6126
10% | 4248.2976 | 5.1162 | 6.7921 | 7.2483 | 7.235 | 7.2345 | 7.2865 | 7.3435 | 7.4607 | 7.5448 | 7.5905 | 7.6404 | 7.6861 | 7.7687 | 7.8712 | 7.864 | 7.864 | 7.864 | 7.864 | 7.864 | 7.864 | 7.864 | 7.864 | 7.864 | 7.864 | 7.864 | 7.864 | 7.864 | 7.864 | 7.864 | 7.864 | 10% | 4391.6218 | 5.7028 | 7.3821 | 7.8215 | 7.7951 | 7.7969 | 7.842 | 7.9609 | 8.0405 | 8.1185 | 8.2096 | 8.2941 | 8.3761 | 8.3854 | 8.4811 | 8.4084 | 8.4084 | 8.4084 | 8.4084 | 8.4084 | 8.4084 | 8.4084 | 8.4084 | 8.4084 | 8.4084 | 8.4084 | 8.4084 | 8.4084 | 8.4084 | 8.4084 | 8.4084
5% | 4361.7469 | 2.5581 | 3.396 | 3.6241 | 3.6175 | 3.6172 | 3.6432 | 3.6718 | 3.7303 | 3.7724 | 3.7952 | 3.8202 | 3.8431 | 3.8844 | 3.9356 | 3.932 | 3.932 | 3.932 | 3.932 | 3.932 | 3.932 | 3.932 | 3.932 | 3.932 | 3.932 | 3.932 | 3.932 | 3.932 | 3.932 | 3.932 | 3.932 | 5% | 4391.6218 | 2.8514 | 3.691 | 3.9107 | 3.8975 | 3.8985 | 3.921 | 3.9805 | 4.0203 | 4.0592 | 4.1048 | 4.147 | 4.188 | 4.1927 | 4.2405 | 4.2042 | 4.2042 | 4.2042 | 4.2042 | 4.2042 | 4.2042 | 4.2042 | 4.2042 | 4.2042 | 4.2042 | 4.2042 | 4.2042 | 4.2042 | 4.2042 | 4.2042 | 4.2042
9.992e-14% | 4391.6218 | 5.1121e-14 | 6.7867e-14 | 7.2425e-14 | 7.2292e-14 | 7.2287e-14 | 7.2807e-14 | 7.3377e-14 | 7.4547e-14 | 7.5388e-14 | 7.5844e-14 | 7.6343e-14 | 7.68e-14 | 7.7625e-14 | 7.8649e-14 | 7.8578e-14 | 7.8578e-14 | 7.8578e-14 | 7.8578e-14 | 7.8578e-14 | 7.8578e-14 | 7.8578e-14 | 7.8578e-14 | 7.8578e-14 | 7.8578e-14 | 7.8578e-14 | 7.8578e-14 | 7.8578e-14 | 7.8578e-14 | 7.8578e-14 | 7.8578e-14 | 9.992e-14% | 4391.6218 | 5.6983e-14 | 7.3762e-14 | 7.8152e-14 | 7.7889e-14 | 7.7907e-14 | 7.8357e-14 | 7.9546e-14 | 8.0341e-14 | 8.112e-14 | 8.2031e-14 | 8.2874e-14 | 8.3694e-14 | 8.3787e-14 | 8.4743e-14 | 8.4017e-14 | 8.4017e-14 | 8.4017e-14 | 8.4017e-14 | 8.4017e-14 | 8.4017e-14 | 8.4017e-14 | 8.4017e-14 | 8.4017e-14 | 8.4017e-14 | 8.4017e-14 | 8.4017e-14 | 8.4017e-14 | 8.4017e-14 | 8.4017e-14 | 8.4017e-14

## Locational VCR
Base case |  | Energy Usage (CY 2024 kWh) | Energy Usage (CY 2024 %) | Tailored VCR
Dec 24 AER VCR ($/kWh) - Res | 49.23 | 67934749.1441 | 34.06% | 16.7657
Dec 24 AER VCR ($/kWh) - Com | 34.39 | 101368150.4504 | 50.82% | 17.4756
Dec 24 AER VCR ($/kWh) - Ind | 33.49 | 17726336.2671 | 8.886% | 2.976
Dec 24 AER VCR ($/kWh) - Agr | 22.25 | 12451243.5083 | 6.242% | 1.3888
|  | 199480479.3698 |  | 38.6062 | KW/h
|  |  |  | 38606.1513 | MW/h

## E@R N
Option 1 - Do Nothing / Base Case
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99%
98%
97%
95%
90%
85%
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1 Winter POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 1 Winter POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99
98%
97%
95%
90%
85%
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1 Summer POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 1 Summer POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2 - 1A New PHS ZSS + Four new feeders
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99%
98%
97%
95%
90%
85%
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2 Winter POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 2 Winter POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99
98%
97%
95%
90%
85%
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2 Summer POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 2 Summer POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 - 2A PHM 3rd Tx + Switchroom + Three new feeders + OFR12 New Feeder
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99%
98%
97%
95%
90%
85%
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 Winter POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 3 Winter POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99
98%
97%
95%
90%
85%
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 Summer POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 3 Summer POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 - 3A OFR 3rd Tx + Switchroom + Three new feeders + OFR12 New Feeder
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99%
98%
97%
95%
90%
85%
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 Winter POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 4 Winter POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99
98%
97%
95%
90%
85%
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 Summer POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 4 Summer POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 - 4A LLG 2nd Tx + Switchroom + Three new feeders + OFR12 New Feeder
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99%
98%
97%
95%
90%
85%
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 Winter POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 5 Winter POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99
98%
97%
95%
90%
85%
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 Summer POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 5 Summer POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 6 - Non Network
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99%
98%
97%
95%
90%
85%
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 6 Winter POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 6 Winter POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99
98%
97%
95%
90%
85%
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 6 Summer POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 6 Summer POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 7 -
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99%
98%
97%
95%
90%
85%
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 7 Winter POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 7 Winter POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99
98%
97%
95%
90%
85%
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 7 Summer POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 7 Summer POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 8 -
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99%
98%
97%
95%
90%
85%
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 8 Winter POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 8 Winter POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99
98%
97%
95%
90%
85%
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 8 Summer POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 8 Summer POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## E@R N-1
Option 1 - Do Nothing / Base Case
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% |  | 19.3557 | 26.0414 | 27.1786 | 28.0631 | 29.5913 | 33.0724 | 35.3998 | 38.3512 | 39.8816 | 41.2259 | 38.7366 | 41.6468 | 46.224 | 42.7448 | 42.7448 | 42.7448 | 42.7448 | 42.7448 | 42.7448 | 42.7448 | 42.7448 | 42.7448 | 42.7448 | 42.7448 | 42.7448 | 42.7448 | 42.7448 | 42.7448 | 42.7448 |  |  | 23.7132 | 30.66 | 31.7324 | 32.4104 | 33.9055 | 37.4409 | 39.3681 | 43.0454 | 54.2301 | 45.0018 | 43.1944 | 45.6265 | 50.9491 | 47.3408 | 47.3408 | 47.3408 | 47.3408 | 47.3408 | 47.3408 | 47.3408 | 47.3408 | 47.3408 | 47.3408 | 47.3408 | 47.3408 | 47.3408 | 47.3408 | 47.3408 | 47.3408
98% |  | 22.1134 | 30.0556 | 31.4065 | 32.4573 | 34.2728 | 38.408 | 41.1729 | 44.679 | 46.497 | 48.0939 | 45.1368 | 48.594 | 54.0314 | 49.8983 | 49.8983 | 49.8983 | 49.8983 | 49.8983 | 49.8983 | 49.8983 | 49.8983 | 49.8983 | 49.8983 | 49.8983 | 49.8983 | 49.8983 | 49.8983 | 49.8983 | 49.8983 |  |  | 27.2899 | 35.5423 | 36.8162 | 37.6217 | 39.3977 | 43.5976 | 45.887 | 50.2554 | 63.5422 | 52.5795 | 50.4324 | 53.3215 | 59.6445 | 55.358 | 55.358 | 55.358 | 55.358 | 55.358 | 55.358 | 55.358 | 55.358 | 55.358 | 55.358 | 55.358 | 55.358 | 55.358 | 55.358 | 55.358 | 55.358
97% |  | 42.0001 | 57.7232 | 60.3976 | 62.4779 | 66.0719 | 74.2584 | 79.732 | 86.673 | 90.2721 | 93.4336 | 87.5793 | 94.4235 | 105.1879 | 97.0056 | 97.0056 | 97.0056 | 97.0056 | 97.0056 | 97.0056 | 97.0056 | 97.0056 | 97.0056 | 97.0056 | 97.0056 | 97.0056 | 97.0056 | 97.0056 | 97.0056 | 97.0056 |  |  | 52.248 | 68.5852 | 71.1071 | 72.7018 | 76.2177 | 84.5323 | 89.0645 | 97.7126 | 124.0163 | 102.3136 | 98.0631 | 103.7826 | 116.3002 | 107.8143 | 107.8143 | 107.8143 | 107.8143 | 107.8143 | 107.8143 | 107.8143 | 107.8143 | 107.8143 | 107.8143 | 107.8143 | 107.8143 | 107.8143 | 107.8143 | 107.8143 | 107.8143
95% |  | 115.9799 | 162.4236 | 170.3233 | 176.4681 | 187.0842 | 211.266 | 227.434 | 247.9367 | 258.5678 | 267.9064 | 250.6138 | 270.8306 | 302.6268 | 278.4578 | 278.4578 | 278.4578 | 278.4578 | 278.4578 | 278.4578 | 278.4578 | 278.4578 | 278.4578 | 278.4578 | 278.4578 | 278.4578 | 278.4578 | 278.4578 | 278.4578 | 278.4578 |  |  | 146.2505 | 194.5083 | 201.9576 | 206.6678 | 217.0533 | 241.6134 | 255.0008 | 280.5461 | 358.2432 | 294.1368 | 281.5814 | 298.4759 | 335.451 | 310.3848 | 310.3848 | 310.3848 | 310.3848 | 310.3848 | 310.3848 | 310.3848 | 310.3848 | 310.3848 | 310.3848 | 310.3848 | 310.3848 | 310.3848 | 310.3848 | 310.3848 | 310.3848
90% |  | 529.8714 | 785.9431 | 829.499 | 863.379 | 921.9121 | 1055.2409 | 1144.3849 | 1257.4283 | 1316.044 | 1367.5334 | 1272.189 | 1383.6562 | 1558.9677 | 1425.7093 | 1425.7093 | 1425.7093 | 1425.7093 | 1425.7093 | 1425.7093 | 1425.7093 | 1425.7093 | 1425.7093 | 1425.7093 | 1425.7093 | 1425.7093 | 1425.7093 | 1425.7093 | 1425.7093 | 1425.7093 |  |  | 696.7712 | 962.8455 | 1003.918 | 1029.8882 | 1087.1494 | 1222.564 | 1296.377 | 1437.2235 | 1865.6143 | 1512.1572 | 1442.9317 | 1536.0814 | 1739.9469 | 1601.7422 | 1601.7422 | 1601.7422 | 1601.7422 | 1601.7422 | 1601.7422 | 1601.7422 | 1601.7422 | 1601.7422 | 1601.7422 | 1601.7422 | 1601.7422 | 1601.7422 | 1601.7422 | 1601.7422 | 1601.7422
85% |  | 874.8065 | 1500.3713 | 1606.7752 | 1689.5415 | 1832.5337 | 2158.2465 | 2376.0188 | 2652.1757 | 2795.3696 | 2921.1546 | 2688.2351 | 2960.5416 | 3388.8149 | 3063.2741 | 3063.2741 | 3063.2741 | 3063.2741 | 3063.2741 | 3063.2741 | 3063.2741 | 3063.2741 | 3063.2741 | 3063.2741 | 3063.2741 | 3063.2741 | 3063.2741 | 3063.2741 | 3063.2741 | 3063.2741 |  |  | 1282.5306 | 1932.5312 | 2032.8683 | 2096.3116 | 2236.1967 | 2567.0047 | 2747.3247 | 3091.4025 | 4137.9307 | 3274.4602 | 3105.3472 | 3332.9054 | 3830.934 | 3493.3099 | 3493.3099 | 3493.3099 | 3493.3099 | 3493.3099 | 3493.3099 | 3493.3099 | 3493.3099 | 3493.3099 | 3493.3099 | 3493.3099 | 3493.3099 | 3493.3099 | 3493.3099 | 3493.3099 | 3493.3099
80% |  | 628.4185 | 1600.7316 | 1766.1149 | 1894.7582 | 2117.0105 | 2623.2647 | 2961.7475 | 3390.9772 | 3613.543 | 3809.0501 | 3447.0242 | 3870.2692 | 4535.9328 | 4029.946 | 4029.946 | 4029.946 | 4029.946 | 4029.946 | 4029.946 | 4029.946 | 4029.946 | 4029.946 | 4029.946 | 4029.946 | 4029.946 | 4029.946 | 4029.946 | 4029.946 | 4029.946 |  |  | 1262.1427 | 2272.4362 | 2428.3899 | 2526.9996 | 2744.4225 | 3258.5963 | 3538.867 | 4073.6659 | 5700.2809 | 4358.1918 | 4095.3401 | 4449.033 | 5223.1171 | 4698.349 | 4698.349 | 4698.349 | 4698.349 | 4698.349 | 4698.349 | 4698.349 | 4698.349 | 4698.349 | 4698.349 | 4698.349 | 4698.349 | 4698.349 | 4698.349 | 4698.349 | 4698.349
75% |  | 35.4297 | 855.1312 | 1037.5951 | 1179.5246 | 1424.7309 | 1983.2706 | 2356.7115 | 2830.2717 | 3075.8238 | 3291.5228 | 2892.1072 | 3359.0645 | 4093.4773 | 3535.2326 | 3535.2326 | 3535.2326 | 3535.2326 | 3535.2326 | 3535.2326 | 3535.2326 | 3535.2326 | 3535.2326 | 3535.2326 | 3535.2326 | 3535.2326 | 3535.2326 | 3535.2326 | 3535.2326 | 3535.2326 |  |  | 481.7498 | 1596.2089 | 1768.2692 | 1877.0633 | 2116.9414 | 2684.2186 | 2993.4354 | 3583.4678 | 5378.0782 | 3897.3793 | 3607.3806 | 3997.6025 | 4851.6333 | 4272.6677 | 4272.6677 | 4272.6677 | 4272.6677 | 4272.6677 | 4272.6677 | 4272.6677 | 4272.6677 | 4272.6677 | 4272.6677 | 4272.6677 | 4272.6677 | 4272.6677 | 4272.6677 | 4272.6677 | 4272.6677
70% |  |  | 65.8085 | 149.3801 | 236.763 | 432.2706 | 1017.18 | 1418.4215 | 1927.2354 | 2191.0675 | 2422.824 | 1993.6741 | 2495.3937 | 3284.4792 | 2684.6765 | 2684.6765 | 2684.6765 | 2684.6765 | 2684.6765 | 2684.6765 | 2684.6765 | 2684.6765 | 2684.6765 | 2684.6765 | 2684.6765 | 2684.6765 | 2684.6765 | 2684.6765 | 2684.6765 | 2684.6765 |  |  |  | 601.3916 | 786.1731 | 903.0662 | 1160.8019 | 1770.3095 | 2102.5457 | 2736.5026 | 4664.7111 | 3073.7829 | 2762.1954 | 3181.4671 | 4099.0755 | 3477.0093 | 3477.0093 | 3477.0093 | 3477.0093 | 3477.0093 | 3477.0093 | 3477.0093 | 3477.0093 | 3477.0093 | 3477.0093 | 3477.0093 | 3477.0093 | 3477.0093 | 3477.0093 | 3477.0093 | 3477.0093
65% | [6 empty] | 67.1746 | 263.316 | 684.8354 | 961.4279 | 1205.6548 | 753.4132 | 1282.1294 | 2113.6742 | 1481.5972 | 1481.5972 | 1481.5972 | 1481.5972 | 1481.5972 | 1481.5972 | 1481.5972 | 1481.5972 | 1481.5972 | 1481.5972 | 1481.5972 | 1481.5972 | 1481.5972 | 1481.5972 | 1481.5972 | 1481.5972 |  |  |  |  | 12.1974 | 34.5742 | 123.0009 | 535.0416 | 868.1429 | 1536.2119 | 3568.1739 | 1891.6407 | 1563.2873 | 2005.1192 | 2972.1025 | 2316.564 | 2316.564 | 2316.564 | 2316.564 | 2316.564 | 2316.564 | 2316.564 | 2316.564 | 2316.564 | 2316.564 | 2316.564 | 2316.564 | 2316.564 | 2316.564 | 2316.564 | 2316.564
60% | [9 empty] | 15.996 | 73.9877 | 0.0013268 | 100.6328 | 637.7145 | 188.7046 | 188.7046 | 188.7046 | 188.7046 | 188.7046 | 188.7046 | 188.7046 | 188.7046 | 188.7046 | 188.7046 | 188.7046 | 188.7046 | 188.7046 | 188.7046 | 188.7046 | 188.7046 | [8 empty] | 4.9606 | 217.4281 | 2207.292 | 451.391 | 232.3927 | 542.8433 | 1551.0908 | 834.0186 | 834.0186 | 834.0186 | 834.0186 | 834.0186 | 834.0186 | 834.0186 | 834.0186 | 834.0186 | 834.0186 | 834.0186 | 834.0186 | 834.0186 | 834.0186 | 834.0186 | 834.0186
55% | [40 empty] | 420.5237 |  |  |  | 95.5636
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 2267.9753 | 5084.2295 | 5678.6703 | 6163.4327 | 7045.478 | 9261.3822 | 10904.3389 | 13160.5637 | 14404.4901 | 15542.3873 | 13468.7106 | 15907.1825 | 20121.1305 | 16877.247 | 16877.247 | 16877.247 | 16877.247 | 16877.247 | 16877.247 | 16877.247 | 16877.247 | 16877.247 | 16877.247 | 16877.247 | 16877.247 | 16877.247 | 16877.247 | 16877.247 | 16877.247 | E @ R (MWh) | 0 | 3972.6958 | 7694.7094 | 8373.4293 | 8817.3048 | 9835.0869 | 12444.9189 | 13980.9735 | 17147.4619 | 28542.6368 | 18953.035 | 17282.1464 | 19546.2584 | 24925.8084 | 21214.5583 | 21214.5583 | 21214.5583 | 21214.5583 | 21214.5583 | 21214.5583 | 21214.5583 | 21214.5583 | 21214.5583 | 21214.5583 | 21214.5583 | 21214.5583 | 21214.5583 | 21214.5583 | 21214.5583 | 21214.5583
Option 1 Winter POE50 W E @ R (MWh) N 1 | 0 | 1587.5827 | 3558.9606 | 3975.0692 | 4314.4029 | 4931.8346 | 6482.9675 | 7633.0372 | 9212.3946 | 10083.1431 | 10879.6711 | 9428.0974 | 11135.0277 | 14084.7914 | 11814.0729 | 11814.0729 | 11814.0729 | 11814.0729 | 11814.0729 | 11814.0729 | 11814.0729 | 11814.0729 | 11814.0729 | 11814.0729 | 11814.0729 | 11814.0729 | 11814.0729 | 11814.0729 | 11814.0729 | 11814.0729 | Option 1 Winter POE10 W E @ R (MWh) N 1 | 0 | 1191.8087 | 2308.4128 | 2512.0288 | 2645.1914 | 2950.5261 | 3733.4757 | 4194.2921 | 5144.2386 | 8562.791 | 5685.9105 | 5184.6439 | 5863.8775 | 7477.7425 | 6364.3675 | 6364.3675 | 6364.3675 | 6364.3675 | 6364.3675 | 6364.3675 | 6364.3675 | 6364.3675 | 6364.3675 | 6364.3675 | 6364.3675 | 6364.3675 | 6364.3675 | 6364.3675 | 6364.3675 | 6364.3675
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 17.7632 | 43.0375 | 49.6507 | 49.2537 | 49.2817 | 49.9598 | 51.7502 | 52.9479 | 54.1209 | 55.493 | 56.7638 | 57.998 | 58.138 | 59.5788 | 58.4848 | 58.4848 | 58.4848 | 58.4848 | 58.4848 | 58.4848 | 58.4848 | 58.4848 | 58.4848 | 58.4848 | 58.4848 | 58.4848 | 58.4848 | 58.4848 | 58.4848 | 58.4848
98% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 8.4503 | 20.9604 | 24.2338 | 24.0373 | 24.0512 | 24.3868 | 25.273 | 25.8658 | 26.4464 | 27.1256 | 27.7546 | 28.3655 | 28.4348 | 29.1479 | 28.6065 | 28.6065 | 28.6065 | 28.6065 | 28.6065 | 28.6065 | 28.6065 | 28.6065 | 28.6065 | 28.6065 | 28.6065 | 28.6065 | 28.6065 | 28.6065 | 28.6065 | 28.6065
97% | 1.8466 | 8.0258 | 9.7077 | 9.6587 | 9.6569 | 9.8486 | 10.059 | 10.4908 | 10.8011 | 10.9695 | 11.1536 | 11.3221 | 11.6266 | 12.0045 | 11.9781 | 11.9781 | 11.9781 | 11.9781 | 11.9781 | 11.9781 | 11.9781 | 11.9781 | 11.9781 | 11.9781 | 11.9781 | 11.9781 | 11.9781 | 11.9781 | 11.9781 | 11.9781 |  | 16.0379 | 40.8042 | 47.2844 | 46.8955 | 46.9229 | 47.5873 | 49.3417 | 50.5154 | 51.6648 | 53.0093 | 54.2545 | 55.464 | 55.6012 | 57.013 | 55.941 | 55.941 | 55.941 | 55.941 | 55.941 | 55.941 | 55.941 | 55.941 | 55.941 | 55.941 | 55.941 | 55.941 | 55.941 | 55.941 | 55.941 | 55.941
95% | 7.7819 | 38.2025 | 46.4828 | 46.2417 | 46.2328 | 47.1765 | 48.212 | 50.3381 | 51.8658 | 52.6946 | 53.6008 | 54.4305 | 55.9296 | 57.7903 | 57.6602 | 57.6602 | 57.6602 | 57.6602 | 57.6602 | 57.6602 | 57.6602 | 57.6602 | 57.6602 | 57.6602 | 57.6602 | 57.6602 | 57.6602 | 57.6602 | 57.6602 | 57.6602 |  | 22.1159 | 58.6938 | 68.2646 | 67.6901 | 67.7307 | 68.712 | 71.3031 | 73.0364 | 74.7341 | 76.7198 | 78.559 | 80.3452 | 80.5479 | 82.6329 | 81.0498 | 81.0498 | 81.0498 | 81.0498 | 81.0498 | 81.0498 | 81.0498 | 81.0498 | 81.0498 | 81.0498 | 81.0498 | 81.0498 | 81.0498 | 81.0498 | 81.0498 | 81.0498
90% | 7.9129 | 60.6736 | 75.0348 | 74.6165 | 74.6011 | 76.2379 | 78.0339 | 81.7213 | 84.371 | 85.8084 | 87.3801 | 88.819 | 91.4191 | 94.6462 | 94.4206 | 94.4206 | 94.4206 | 94.4206 | 94.4206 | 94.4206 | 94.4206 | 94.4206 | 94.4206 | 94.4206 | 94.4206 | 94.4206 | 94.4206 | 94.4206 | 94.4206 | 94.4206 |  | 79.1417 | 237.7413 | 279.2396 | 276.7487 | 276.9246 | 281.1792 | 292.4144 | 299.93 | 307.291 | 315.901 | 323.8752 | 331.6203 | 332.499 | 341.5397 | 334.6752 | 334.6752 | 334.6752 | 334.6752 | 334.6752 | 334.6752 | 334.6752 | 334.6752 | 334.6752 | 334.6752 | 334.6752 | 334.6752 | 334.6752 | 334.6752 | 334.6752 | 334.6752
85% | 2.1831 | 147.3455 | 188.1003 | 186.9134 | 186.8697 | 191.5145 | 196.6114 | 207.0756 | 214.595 | 218.674 | 223.1344 | 227.2178 | 234.5963 | 243.7543 | 243.1142 | 243.1142 | 243.1142 | 243.1142 | 243.1142 | 243.1142 | 243.1142 | 243.1142 | 243.1142 | 243.1142 | 243.1142 | 243.1142 | 243.1142 | 243.1142 | 243.1142 | 243.1142 |  | 50.0275 | 200.0542 | 239.3094 | 236.9532 | 237.1195 | 241.1442 | 251.772 | 258.8814 | 265.8444 | 273.989 | 281.5323 | 288.8587 | 289.6899 | 298.2419 | 291.7484 | 291.7484 | 291.7484 | 291.7484 | 291.7484 | 291.7484 | 291.7484 | 291.7484 | 291.7484 | 291.7484 | 291.7484 | 291.7484 | 291.7484 | 291.7484 | 291.7484 | 291.7484
80% |  | 166.9191 | 223.8464 | 222.1885 | 222.1274 | 228.6154 | 235.7349 | 250.3515 | 260.8548 | 266.5525 | 272.783 | 278.4866 | 288.7932 | 301.5853 | 300.6912 | 300.6912 | 300.6912 | 300.6912 | 300.6912 | 300.6912 | 300.6912 | 300.6912 | 300.6912 | 300.6912 | 300.6912 | 300.6912 | 300.6912 | 300.6912 | 300.6912 | 300.6912 |  | 15.4914 | 120.2719 | 147.6883 | 146.0426 | 146.1588 | 148.9697 | 156.3923 | 161.3576 | 166.2207 | 171.909 | 177.1773 | 182.2941 | 182.8747 | 188.8475 | 184.3124 | 184.3124 | 184.3124 | 184.3124 | 184.3124 | 184.3124 | 184.3124 | 184.3124 | 184.3124 | 184.3124 | 184.3124 | 184.3124 | 184.3124 | 184.3124 | 184.3124 | 184.3124
75% |  | 320.647 | 469.0463 | 464.7244 | 464.5651 | 481.4781 | 500.0374 | 538.1403 | 565.5205 | 580.3733 | 596.615 | 611.4834 | 638.3507 | 671.6975 | 669.3666 | 669.3666 | 669.3666 | 669.3666 | 669.3666 | 669.3666 | 669.3666 | 669.3666 | 669.3666 | 669.3666 | 669.3666 | 669.3666 | 669.3666 | 669.3666 | 669.3666 | 669.3666 |  | 0.97657 | 175.4756 | 224.4096 | 221.4724 | 221.6798 | 226.6968 | 239.945 | 248.8073 | 257.4872 | 267.6399 | 277.043 | 286.1758 | 287.212 | 297.8726 | 289.7781 | 289.7781 | 289.7781 | 289.7781 | 289.7781 | 289.7781 | 289.7781 | 289.7781 | 289.7781 | 289.7781 | 289.7781 | 289.7781 | 289.7781 | 289.7781 | 289.7781 | 289.7781
70% |  | 328.9116 | 585.3005 | 577.8335 | 577.5583 | 606.7787 | 638.8436 | 704.6738 | 751.9784 | 777.6395 | 805.7002 | 831.3883 | 877.8068 | 935.42 | 931.3929 | 931.3929 | 931.3929 | 931.3929 | 931.3929 | 931.3929 | 931.3929 | 931.3929 | 931.3929 | 931.3929 | 931.3929 | 931.3929 | 931.3929 | 931.3929 | 931.3929 | 931.3929 |  |  | 238.4252 | 327.5698 | 322.219 | 322.5968 | 331.7364 | 355.8711 | 372.0158 | 387.8282 | 406.3238 | 423.4537 | 440.0913 | 441.9789 | 461.3997 | 446.6536 | 446.6536 | 446.6536 | 446.6536 | 446.6536 | 446.6536 | 446.6536 | 446.6536 | 446.6536 | 446.6536 | 446.6536 | 446.6536 | 446.6536 | 446.6536 | 446.6536 | 446.6536
65% |  | 199.3768 | 820.987 | 802.2336 | 801.5424 | 874.9301 | 955.4618 | 1120.7959 | 1239.6024 | 1304.0507 | 1374.5258 | 1439.0422 | 1555.6231 | 1700.32 | 1690.2059 | 1690.2059 | 1690.2059 | 1690.2059 | 1690.2059 | 1690.2059 | 1690.2059 | 1690.2059 | 1690.2059 | 1690.2059 | 1690.2059 | 1690.2059 | 1690.2059 | 1690.2059 | 1690.2059 | 1690.2059 |  |  | 182.6144 | 294.7721 | 288.04 | 288.5153 | 300.0144 | 330.3796 | 350.692 | 370.5866 | 393.8569 | 415.4089 | 436.3416 | 438.7165 | 463.1508 | 444.598 | 444.598 | 444.598 | 444.598 | 444.598 | 444.598 | 444.598 | 444.598 | 444.598 | 444.598 | 444.598 | 444.598 | 444.598 | 444.598 | 444.598 | 444.598
60% |  |  | 203.5024 | 187.5582 | 186.9825 | 252.8081 | 335.7847 | 540.3015 | 711.4984 | 805.7041 | 908.7192 | 1003.0243 | 1173.4335 | 1384.9404 | 1370.1564 | 1370.1564 | 1370.1564 | 1370.1564 | 1370.1564 | 1370.1564 | 1370.1564 | 1370.1564 | 1370.1564 | 1370.1564 | 1370.1564 | 1370.1564 | 1370.1564 | 1370.1564 | 1370.1564 | 1370.1564 |  |  | 77.0598 | 248.2313 | 237.6968 | 238.4405 | 256.4344 | 303.9503 | 335.7356 | 366.8668 | 403.2805 | 437.0055 | 469.7612 | 473.4775 | 511.7128 | 482.681 | 482.681 | 482.681 | 482.681 | 482.681 | 482.681 | 482.681 | 482.681 | 482.681 | 482.681 | 482.681 | 482.681 | 482.681 | 482.681 | 482.681 | 482.681
55% | [8 empty] | 3.8903 | 15.7556 | 37.6919 | 65.8304 | 135.7599 | 255.725 | 246.1724 | 246.1724 | 246.1724 | 246.1724 | 246.1724 | 246.1724 | 246.1724 | 246.1724 | 246.1724 | 246.1724 | 246.1724 | 246.1724 | 246.1724 | 246.1724 | 246.1724 | 246.1724 |  |  |  | 63.4905 | 53.6808 | 54.3475 | 71.6739 | 128.262 | 174.6238 | 226.4176 | 294.3956 | 359.2034 | 422.1487 | 429.2901 | 502.7651 | 446.976 | 446.976 | 446.976 | 446.976 | 446.976 | 446.976 | 446.976 | 446.976 | 446.976 | 446.976 | 446.976 | 446.976 | 446.976 | 446.976 | 446.976 | 446.976
50% | [40 empty] | 0.92441 | 14.9076 | 44.2124 | 48.4954 | 103.6497 | 59.9312 | 59.9312 | 59.9312 | 59.9312 | 59.9312 | 59.9312 | 59.9312 | 59.9312 | 59.9312 | 59.9312 | 59.9312 | 59.9312 | 59.9312 | 59.9312 | 59.9312 | 59.9312
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 19.7244 | 1270.1019 | 2622.0083 | 2571.9686 | 2570.1362 | 2769.3877 | 2998.7788 | 3503.8889 | 3894.9777 | 4118.2221 | 4371.3041 | 4611.0446 | 5063.3387 | 5657.8836 | 5615.1586 | 5615.1586 | 5615.1586 | 5615.1586 | 5615.1586 | 5615.1586 | 5615.1586 | 5615.1586 | 5615.1586 | 5615.1586 | 5615.1586 | 5615.1586 | 5615.1586 | 5615.1586 | 5615.1586 | 5615.1586 | E @ R (MWh) | 210.0044 | 1395.1384 | 2014.1441 | 1970.7302 | 1973.7695 | 2048.4946 | 2256.6548 | 2404.4088 | 2555.5088 | 2740.5678 | 2926.9386 | 3123.6769 | 3146.9559 | 3397.5525 | 3205.4359 | 3205.4359 | 3205.4359 | 3205.4359 | 3205.4359 | 3205.4359 | 3205.4359 | 3205.4359 | 3205.4359 | 3205.4359 | 3205.4359 | 3205.4359 | 3205.4359 | 3205.4359 | 3205.4359 | 3205.4359
Option 1 Summer POE50 W E @ R (MWh) N 1 | 13.8071 | 889.0713 | 1835.4058 | 1800.378 | 1799.0954 | 1938.5714 | 2099.1452 | 2452.7222 | 2726.4844 | 2882.7555 | 3059.9129 | 3227.7312 | 3544.3371 | 3960.5185 | 3930.611 | 3930.611 | 3930.611 | 3930.611 | 3930.611 | 3930.611 | 3930.611 | 3930.611 | 3930.611 | 3930.611 | 3930.611 | 3930.611 | 3930.611 | 3930.611 | 3930.611 | 3930.611 | Option 1 Summer POE10 W E @ R (MWh) N 1 | 63.0013 | 418.5415 | 604.2432 | 591.2191 | 592.1308 | 614.5484 | 676.9964 | 721.3226 | 766.6526 | 822.1703 | 878.0816 | 937.1031 | 944.0868 | 1019.2657 | 961.6308 | 961.6308 | 961.6308 | 961.6308 | 961.6308 | 961.6308 | 961.6308 | 961.6308 | 961.6308 | 961.6308 | 961.6308 | 961.6308 | 961.6308 | 961.6308 | 961.6308 | 961.6308
Option 2 - 1A New PHS ZSS + Four new feeders
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% |  | 19.3557 | 26.0414 | [10 empty] | 3.3457 | 0.036908 | 0.036908 | 0.036908 | 0.036908 | 0.036908 | 0.036908 | 0.036908 | 0.036908 | 0.036908 | 0.036908 | 0.036908 | 0.036908 | 0.036908 | 0.036908 | 0.036908 | 0.036908 |  |  | 23.7132 | 30.66 | [5 empty] | 0.19441 | 11.3518 | 2.1235 | 0.31797 | 2.7481 | 8.0708 | 4.4624 | 4.4624 | 4.4624 | 4.4624 | 4.4624 | 4.4624 | 4.4624 | 4.4624 | 4.4624 | 4.4624 | 4.4624 | 4.4624 | 4.4624 | 4.4624 | 4.4624 | 4.4624
98% | FY26: 22.1134; FY27: 30.0556; FY38: 3.0945 |  |  | 27.2899 | 35.5423 | [6 empty] | 12.6053 | 1.6426 |  | 2.3847 | 8.7077 | 4.4212 | 4.4212 | 4.4212 | 4.4212 | 4.4212 | 4.4212 | 4.4212 | 4.4212 | 4.4212 | 4.4212 | 4.4212 | 4.4212 | 4.4212 | 4.4212 | 4.4212 | 4.4212
97% | FY26: 42.0001; FY27: 57.7232; FY38: 4.3484 |  |  | 52.248 | 68.5852 | [6 empty] | 23.1769 | 1.4742 |  | 2.9432 | 15.4607 | 6.9748 | 6.9748 | 6.9748 | 6.9748 | 6.9748 | 6.9748 | 6.9748 | 6.9748 | 6.9748 | 6.9748 | 6.9748 | 6.9748 | 6.9748 | 6.9748 | 6.9748 | 6.9748
95% | FY26: 115.9799; FY27: 162.4236; FY38: 4.7886 |  |  | 146.2505 | 194.5083 | [6 empty] | 60.379 | 0.1339 |  | 1.6925 | 37.5867 | 12.5205 | 12.5205 | 12.5205 | 12.5205 | 12.5205 | 12.5205 | 12.5205 | 12.5205 | 12.5205 | 12.5205 | 12.5205 | 12.5205 | 12.5205 | 12.5205 | 12.5205 | 12.5205
90% | FY26: 529.8714; FY27: 785.9431 |  |  | 696.7712 | 962.8455 | [6 empty] | 223.3101 |  |  |  | 97.6426 | 4.888 | 4.888 | 4.888 | 4.888 | 4.888 | 4.888 | 4.888 | 4.888 | 4.888 | 4.888 | 4.888 | 4.888 | 4.888 | 4.888 | 4.888 | 4.888
85% | FY26: 874.8065; FY27: 1500.3713 |  |  | 1282.5306 | 1932.5312 | [6 empty] | 136.8804 |  |  |  | 1.4571
80% | FY26: 628.4185; FY27: 1600.7316 |  |  | 1262.1427 | 2272.4362
75% | FY26: 35.4297; FY27: 855.1312 |  |  | 481.7498 | 1596.2089
70% | FY27: 65.8085 |  |  |  | 601.3916
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 2267.9753 | 5084.2295 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.5772 | 0.036908 | 0.036908 | 0.036908 | 0.036908 | 0.036908 | 0.036908 | 0.036908 | 0.036908 | 0.036908 | 0.036908 | 0.036908 | 0.036908 | 0.036908 | 0.036908 | 0.036908 | 0.036908 | E @ R (MWh) | 0 | 3972.6958 | 7694.7094 | 0 | 0 | 0 | 0 | 0 | 0.19441 | 467.7034 | 5.3742 | 0.31797 | 9.7685 | 168.9256 | 33.267 | 33.267 | 33.267 | 33.267 | 33.267 | 33.267 | 33.267 | 33.267 | 33.267 | 33.267 | 33.267 | 33.267 | 33.267 | 33.267 | 33.267 | 33.267
Option 2 Winter POE50 W E @ R (MWh) N 1 | 0 | 1587.5827 | 3558.9606 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.904 | 0.025835 | 0.025835 | 0.025835 | 0.025835 | 0.025835 | 0.025835 | 0.025835 | 0.025835 | 0.025835 | 0.025835 | 0.025835 | 0.025835 | 0.025835 | 0.025835 | 0.025835 | 0.025835 | Option 2 Winter POE10 W E @ R (MWh) N 1 | 0 | 1191.8087 | 2308.4128 | 0 | 0 | 0 | 0 | 0 | 0.058322 | 140.311 | 1.6123 | 0.09539 | 2.9306 | 50.6777 | 9.9801 | 9.9801 | 9.9801 | 9.9801 | 9.9801 | 9.9801 | 9.9801 | 9.9801 | 9.9801 | 9.9801 | 9.9801 | 9.9801 | 9.9801 | 9.9801 | 9.9801 | 9.9801
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | 0 | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 17.7632 | 43.0375 | 49.6507 | 5.606 | 5.634 | 6.312 | 8.1025 | 9.3001 | 10.4732 | 11.8453 | 13.116 | 14.3503 | 14.4903 | 15.931 | 14.8371 | 14.8371 | 14.8371 | 14.8371 | 14.8371 | 14.8371 | 14.8371 | 14.8371 | 14.8371 | 14.8371 | 14.8371 | 14.8371 | 14.8371 | 14.8371 | 14.8371 | 14.8371
98% | 0 | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 8.4503 | 20.9604 | 24.2338 | 2.4328 | 2.4466 | 2.7822 | 3.6685 | 4.2613 | 4.8419 | 5.5211 | 6.1501 | 6.761 | 6.8303 | 7.5434 | 7.0019 | 7.0019 | 7.0019 | 7.0019 | 7.0019 | 7.0019 | 7.0019 | 7.0019 | 7.0019 | 7.0019 | 7.0019 | 7.0019 | 7.0019 | 7.0019 | 7.0019 | 7.0019
97% | 1.8466 | 8.0258 | 9.7077 | [5 empty] | 0.10855 | 0.27689 | 0.46097 | 0.62949 | 0.934 | 1.312 | 1.2855 | 1.2855 | 1.2855 | 1.2855 | 1.2855 | 1.2855 | 1.2855 | 1.2855 | 1.2855 | 1.2855 | 1.2855 | 1.2855 | 1.2855 | 1.2855 | 1.2855 | 1.2855 |  | 16.0379 | 40.8042 | 47.2844 | 4.1251 | 4.1525 | 4.8169 | 6.5714 | 7.745 | 8.8944 | 10.2389 | 11.4842 | 12.6936 | 12.8308 | 14.2426 | 13.1706 | 13.1706 | 13.1706 | 13.1706 | 13.1706 | 13.1706 | 13.1706 | 13.1706 | 13.1706 | 13.1706 | 13.1706 | 13.1706 | 13.1706 | 13.1706 | 13.1706 | 13.1706
95% | 7.7819 | 38.2025 | 46.4828 | [5 empty] | 0.0030568 | 0.24961 | 0.96038 | 1.79 | 3.2891 | 5.1498 | 5.0198 | 5.0198 | 5.0198 | 5.0198 | 5.0198 | 5.0198 | 5.0198 | 5.0198 | 5.0198 | 5.0198 | 5.0198 | 5.0198 | 5.0198 | 5.0198 | 5.0198 | 5.0198 |  | 22.1159 | 58.6938 | 68.2646 | 4.5216 | 4.5621 | 5.5434 | 8.1346 | 9.8679 | 11.5656 | 13.5513 | 15.3904 | 17.1766 | 17.3793 | 19.4644 | 17.8812 | 17.8812 | 17.8812 | 17.8812 | 17.8812 | 17.8812 | 17.8812 | 17.8812 | 17.8812 | 17.8812 | 17.8812 | 17.8812 | 17.8812 | 17.8812 | 17.8812 | 17.8812
90% | 7.9129 | 60.6736 | 75.0348 | [7 empty] | 0.00082382 | 0.1558 | 1.0969 | 3.3938 | 3.1941 | 3.1941 | 3.1941 | 3.1941 | 3.1941 | 3.1941 | 3.1941 | 3.1941 | 3.1941 | 3.1941 | 3.1941 | 3.1941 | 3.1941 | 3.1941 | 3.1941 | 3.1941 |  | 79.1417 | 237.7413 | 279.2396 | 4.7137 | 4.8234 | 7.8474 | 18.5194 | 26.035 | 33.396 | 42.006 | 49.9803 | 57.7254 | 58.6041 | 67.6448 | 60.7802 | 60.7802 | 60.7802 | 60.7802 | 60.7802 | 60.7802 | 60.7802 | 60.7802 | 60.7802 | 60.7802 | 60.7802 | 60.7802 | 60.7802 | 60.7802 | 60.7802 | 60.7802
85% | FY25: 2.1831; FY26: 147.3455; FY27: 188.1003 |  | 50.0275 | 200.0542 | 239.3094 |  |  |  | 0.60705 | 3.177 | 7.5638 | 14.8992 | 22.4425 | 29.7689 | 30.6001 | 39.1521 | 32.6586 | 32.6586 | 32.6586 | 32.6586 | 32.6586 | 32.6586 | 32.6586 | 32.6586 | 32.6586 | 32.6586 | 32.6586 | 32.6586 | 32.6586 | 32.6586 | 32.6586 | 32.6586
80% | FY26: 166.9191; FY27: 223.8464 |  | 15.4914 | 120.2719 | 147.6883 | [6 empty] | 0.024748 | 1.0118 | 3.3033 | 3.6436 | 8.0631 | 4.5553 | 4.5553 | 4.5553 | 4.5553 | 4.5553 | 4.5553 | 4.5553 | 4.5553 | 4.5553 | 4.5553 | 4.5553 | 4.5553 | 4.5553 | 4.5553 | 4.5553 | 4.5553
75% | FY26: 320.647; FY27: 469.0463 |  | 0.97657 | 175.4756 | 224.4096
70% | FY26: 328.9116; FY27: 585.3005 |  |  | 238.4252 | 327.5698
65% | FY26: 199.3768; FY27: 820.987 |  |  | 182.6144 | 294.7721
60% | FY27: 203.5024 |  |  | 77.0598 | 248.2313
55% | [33 empty] | 63.4905
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 19.7244 | 1270.1019 | 2622.0083 | 0 | 0 | 0 | 0 | 0 | 0.11161 | 0.5265 | 1.4222 | 2.5753 | 5.3201 | 9.8556 | 9.4994 | 9.4994 | 9.4994 | 9.4994 | 9.4994 | 9.4994 | 9.4994 | 9.4994 | 9.4994 | 9.4994 | 9.4994 | 9.4994 | 9.4994 | 9.4994 | 9.4994 | 9.4994 | E @ R (MWh) | 210.0044 | 1395.1384 | 2014.1441 | 21.3991 | 21.6187 | 27.302 | 45.6033 | 60.3864 | 76.7349 | 98.0866 | 119.5752 | 141.7791 | 144.3786 | 172.0415 | 150.8851 | 150.8851 | 150.8851 | 150.8851 | 150.8851 | 150.8851 | 150.8851 | 150.8851 | 150.8851 | 150.8851 | 150.8851 | 150.8851 | 150.8851 | 150.8851 | 150.8851 | 150.8851
Option 2 Summer POE50 W E @ R (MWh) N 1 | 13.8071 | 889.0713 | 1835.4058 | 0 | 0 | 0 | 0 | 0 | 0.078125 | 0.36855 | 0.99552 | 1.8027 | 3.724 | 6.8989 | 6.6496 | 6.6496 | 6.6496 | 6.6496 | 6.6496 | 6.6496 | 6.6496 | 6.6496 | 6.6496 | 6.6496 | 6.6496 | 6.6496 | 6.6496 | 6.6496 | 6.6496 | 6.6496 | Option 2 Summer POE10 W E @ R (MWh) N 1 | 63.0013 | 418.5415 | 604.2432 | 6.4197 | 6.4856 | 8.1906 | 13.681 | 18.1159 | 23.0205 | 29.426 | 35.8726 | 42.5337 | 43.3136 | 51.6124 | 45.2655 | 45.2655 | 45.2655 | 45.2655 | 45.2655 | 45.2655 | 45.2655 | 45.2655 | 45.2655 | 45.2655 | 45.2655 | 45.2655 | 45.2655 | 45.2655 | 45.2655 | 45.2655
Option 3 - 2A PHM 3rd Tx + Switchroom + Three new feeders + OFR12 New Feeder
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | FY26: 19.3557; FY27: 26.0414 |  |  | 23.7132 | 30.66
98% | FY26: 22.1134; FY27: 30.0556 |  |  | 27.2899 | 35.5423
97% | FY26: 42.0001; FY27: 57.7232 |  |  | 52.248 | 68.5852
95% | FY26: 115.9799; FY27: 162.4236 |  |  | 146.2505 | 194.5083
90% | FY26: 529.8714; FY27: 785.9431 |  |  | 696.7712 | 962.8455
85% | FY26: 874.8065; FY27: 1500.3713 |  |  | 1282.5306 | 1932.5312
80% | FY26: 628.4185; FY27: 1600.7316 |  |  | 1262.1427 | 2272.4362
75% | FY26: 35.4297; FY27: 855.1312 |  |  | 481.7498 | 1596.2089
70% | FY27: 65.8085 |  |  |  | 601.3916
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 2267.9753 | 5084.2295 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 3972.6958 | 7694.7094 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 Winter POE50 W E @ R (MWh) N 1 | 0 | 1587.5827 | 3558.9606 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 3 Winter POE10 W E @ R (MWh) N 1 | 0 | 1191.8087 | 2308.4128 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | FY25: 0; FY26: 0; FY27: 0 |  | 17.7632 | 43.0375 | 49.6507
98% | FY25: 0; FY26: 0; FY27: 0 |  | 8.4503 | 20.9604 | 24.2338
97% | FY25: 1.8466; FY26: 8.0258; FY27: 9.7077 |  | 16.0379 | 40.8042 | 47.2844
95% | FY25: 7.7819; FY26: 38.2025; FY27: 46.4828 |  | 22.1159 | 58.6938 | 68.2646
90% | FY25: 7.9129; FY26: 60.6736; FY27: 75.0348 |  | 79.1417 | 237.7413 | 279.2396
85% | FY25: 2.1831; FY26: 147.3455; FY27: 188.1003 |  | 50.0275 | 200.0542 | 239.3094
80% | FY26: 166.9191; FY27: 223.8464 |  | 15.4914 | 120.2719 | 147.6883
75% | FY26: 320.647; FY27: 469.0463 |  | 0.97657 | 175.4756 | 224.4096
70% | FY26: 328.9116; FY27: 585.3005 |  |  | 238.4252 | 327.5698
65% | FY26: 199.3768; FY27: 820.987 |  |  | 182.6144 | 294.7721
60% | FY27: 203.5024 |  |  | 77.0598 | 248.2313
55% | [33 empty] | 63.4905
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 19.7244 | 1270.1019 | 2622.0083 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 210.0044 | 1395.1384 | 2014.1441 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 Summer POE50 W E @ R (MWh) N 1 | 13.8071 | 889.0713 | 1835.4058 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 3 Summer POE10 W E @ R (MWh) N 1 | 63.0013 | 418.5415 | 604.2432 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 - 3A OFR 3rd Tx + Switchroom + Three new feeders + OFR12 New Feeder
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% |  | 19.3557 | 26.0414 | 5.7394 | 6.624 | 8.1522 | 11.6332 | 13.9606 | 16.912 | 18.4424 | 19.7867 | 17.2974 | 20.2077 | 24.7848 | 21.3056 | 21.3056 | 21.3056 | 21.3056 | 21.3056 | 21.3056 | 21.3056 | 21.3056 | 21.3056 | 21.3056 | 21.3056 | 21.3056 | 21.3056 | 21.3056 | 21.3056 | 21.3056 |  |  | 23.7132 | 30.66 | 10.2932 | 10.9713 | 12.4663 | 16.0018 | 17.9289 | 21.6062 | 32.7909 | 23.5627 | 21.7553 | 24.1873 | 29.5099 | 25.9016 | 25.9016 | 25.9016 | 25.9016 | 25.9016 | 25.9016 | 25.9016 | 25.9016 | 25.9016 | 25.9016 | 25.9016 | 25.9016 | 25.9016 | 25.9016 | 25.9016 | 25.9016
98% |  | 22.1134 | 30.0556 | 5.9381 | 6.9889 | 8.8043 | 12.9396 | 15.7044 | 19.2105 | 21.0285 | 22.6255 | 19.6683 | 23.1256 | 28.5629 | 24.4299 | 24.4299 | 24.4299 | 24.4299 | 24.4299 | 24.4299 | 24.4299 | 24.4299 | 24.4299 | 24.4299 | 24.4299 | 24.4299 | 24.4299 | 24.4299 | 24.4299 | 24.4299 |  |  | 27.2899 | 35.5423 | 11.3478 | 12.1533 | 13.9293 | 18.1292 | 20.4186 | 24.787 | 38.0737 | 27.1111 | 24.964 | 27.8531 | 34.1761 | 29.8896 | 29.8896 | 29.8896 | 29.8896 | 29.8896 | 29.8896 | 29.8896 | 29.8896 | 29.8896 | 29.8896 | 29.8896 | 29.8896 | 29.8896 | 29.8896 | 29.8896 | 29.8896
97% |  | 42.0001 | 57.7232 | 9.9779 | 12.0582 | 15.6522 | 23.8387 | 29.3123 | 36.2533 | 39.8523 | 43.0138 | 37.1596 | 44.0038 | 54.7681 | 46.5859 | 46.5859 | 46.5859 | 46.5859 | 46.5859 | 46.5859 | 46.5859 | 46.5859 | 46.5859 | 46.5859 | 46.5859 | 46.5859 | 46.5859 | 46.5859 | 46.5859 | 46.5859 |  |  | 52.248 | 68.5852 | 20.6874 | 22.282 | 25.7979 | 34.1125 | 38.6448 | 47.2929 | 73.5966 | 51.8939 | 47.6434 | 53.3629 | 65.8805 | 57.3945 | 57.3945 | 57.3945 | 57.3945 | 57.3945 | 57.3945 | 57.3945 | 57.3945 | 57.3945 | 57.3945 | 57.3945 | 57.3945 | 57.3945 | 57.3945 | 57.3945 | 57.3945
95% |  | 115.9799 | 162.4236 | 21.3912 | 27.536 | 38.1521 | 62.3339 | 78.5019 | 99.0046 | 109.6357 | 118.9743 | 101.6817 | 121.8985 | 153.6947 | 129.5256 | 129.5256 | 129.5256 | 129.5256 | 129.5256 | 129.5256 | 129.5256 | 129.5256 | 129.5256 | 129.5256 | 129.5256 | 129.5256 | 129.5256 | 129.5256 | 129.5256 | 129.5256 |  |  | 146.2505 | 194.5083 | 53.0255 | 57.7357 | 68.1211 | 92.6812 | 106.0687 | 131.614 | 209.3111 | 145.2047 | 132.6493 | 149.5438 | 186.5188 | 161.4527 | 161.4527 | 161.4527 | 161.4527 | 161.4527 | 161.4527 | 161.4527 | 161.4527 | 161.4527 | 161.4527 | 161.4527 | 161.4527 | 161.4527 | 161.4527 | 161.4527 | 161.4527
90% |  | 529.8714 | 785.9431 | 24.7547 | 47.1207 | 100.76 | 234.0888 | 323.2328 | 436.2762 | 494.8918 | 546.3813 | 451.0369 | 562.5041 | 737.8155 | 604.5571 | 604.5571 | 604.5571 | 604.5571 | 604.5571 | 604.5571 | 604.5571 | 604.5571 | 604.5571 | 604.5571 | 604.5571 | 604.5571 | 604.5571 | 604.5571 | 604.5571 | 604.5571 |  |  | 696.7712 | 962.8455 | 182.7659 | 208.7361 | 265.9973 | 401.4118 | 475.2249 | 616.0714 | 1044.4622 | 691.0051 | 621.7796 | 714.9293 | 918.7947 | 780.59 | 780.59 | 780.59 | 780.59 | 780.59 | 780.59 | 780.59 | 780.59 | 780.59 | 780.59 | 780.59 | 780.59 | 780.59 | 780.59 | 780.59 | 780.59
85% |  | 874.8065 | 1500.3713 |  |  | 2.1682 | 158.2716 | 370.003 | 646.1599 | 789.3538 | 915.1388 | 682.2193 | 954.5258 | 1382.799 | 1057.2583 | 1057.2583 | 1057.2583 | 1057.2583 | 1057.2583 | 1057.2583 | 1057.2583 | 1057.2583 | 1057.2583 | 1057.2583 | 1057.2583 | 1057.2583 | 1057.2583 | 1057.2583 | 1057.2583 | 1057.2583 |  |  | 1282.5306 | 1932.5312 | 69.8792 | 110.3282 | 230.1809 | 560.9889 | 741.3089 | 1085.3867 | 2131.9149 | 1268.4444 | 1099.3314 | 1326.8896 | 1824.9182 | 1487.294 | 1487.294 | 1487.294 | 1487.294 | 1487.294 | 1487.294 | 1487.294 | 1487.294 | 1487.294 | 1487.294 | 1487.294 | 1487.294 | 1487.294 | 1487.294 | 1487.294 | 1487.294
80% |  | 628.4185 | 1600.7316 |  |  |  |  | 33.5922 | 282.5902 | 495.5997 | 691.1068 | 332.0469 | 752.3259 | 1417.9895 | 912.0027 | 912.0027 | 912.0027 | 912.0027 | 912.0027 | 912.0027 | 912.0027 | 912.0027 | 912.0027 | 912.0027 | 912.0027 | 912.0027 | 912.0027 | 912.0027 | 912.0027 | 912.0027 |  |  | 1262.1427 | 2272.4362 |  |  | 0.0058406 | 180.9581 | 420.9237 | 955.7226 | 2582.3376 | 1240.2485 | 977.3968 | 1331.0897 | 2105.1738 | 1580.4057 | 1580.4057 | 1580.4057 | 1580.4057 | 1580.4057 | 1580.4057 | 1580.4057 | 1580.4057 | 1580.4057 | 1580.4057 | 1580.4057 | 1580.4057 | 1580.4057 | 1580.4057 | 1580.4057 | 1580.4057
75% |  | 35.4297 | 855.1312 | [6 empty] | 6.2739 | 57.2697 |  | 83.5032 | 653.5156 | 174.2659 | 174.2659 | 174.2659 | 174.2659 | 174.2659 | 174.2659 | 174.2659 | 174.2659 | 174.2659 | 174.2659 | 174.2659 | 174.2659 | 174.2659 | 174.2659 | 174.2659 | 174.2659 |  |  | 481.7498 | 1596.2089 |  |  |  |  | 0.30394 | 204.6403 | 1938.1166 | 458.3081 | 220.5644 | 557.6409 | 1411.6717 | 832.706 | 832.706 | 832.706 | 832.706 | 832.706 | 832.706 | 832.706 | 832.706 | 832.706 | 832.706 | 832.706 | 832.706 | 832.706 | 832.706 | 832.706 | 832.706
70% | FY27: 65.8085; FY38: 12.3625 |  |  |  | 601.3916 | [6 empty] | 968.6646 |  |  | 1.7153 | 420.4682 | 57.8192 | 57.8192 | 57.8192 | 57.8192 | 57.8192 | 57.8192 | 57.8192 | 57.8192 | 57.8192 | 57.8192 | 57.8192 | 57.8192 | 57.8192 | 57.8192 | 57.8192 | 57.8192
65% | [40 empty] | 52.029
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 2267.9753 | 5084.2295 | 67.8013 | 100.3277 | 173.6889 | 503.1058 | 864.3071 | 1536.4066 | 1975.0781 | 2414.2969 | 1641.1101 | 2562.0945 | 4466.2928 | 2969.9312 | 2969.9312 | 2969.9312 | 2969.9312 | 2969.9312 | 2969.9312 | 2969.9312 | 2969.9312 | 2969.9312 | 2969.9312 | 2969.9312 | 2969.9312 | 2969.9312 | 2969.9312 | 2969.9312 | 2969.9312 | E @ R (MWh) | 0 | 3972.6958 | 7694.7094 | 347.9991 | 422.2066 | 616.4986 | 1304.2836 | 1820.8223 | 3087.121 | 9071.2973 | 3905.7784 | 3146.0842 | 4187.2117 | 6997.1119 | 5013.4535 | 5013.4535 | 5013.4535 | 5013.4535 | 5013.4535 | 5013.4535 | 5013.4535 | 5013.4535 | 5013.4535 | 5013.4535 | 5013.4535 | 5013.4535 | 5013.4535 | 5013.4535 | 5013.4535 | 5013.4535
Option 4 Winter POE50 W E @ R (MWh) N 1 | 0 | 1587.5827 | 3558.9606 | 47.4609 | 70.2294 | 121.5822 | 352.174 | 605.015 | 1075.4846 | 1382.5546 | 1690.0079 | 1148.7771 | 1793.4662 | 3126.4049 | 2078.9518 | 2078.9518 | 2078.9518 | 2078.9518 | 2078.9518 | 2078.9518 | 2078.9518 | 2078.9518 | 2078.9518 | 2078.9518 | 2078.9518 | 2078.9518 | 2078.9518 | 2078.9518 | 2078.9518 | 2078.9518 | Option 4 Winter POE10 W E @ R (MWh) N 1 | 0 | 1191.8087 | 2308.4128 | 104.3997 | 126.662 | 184.9496 | 391.2851 | 546.2467 | 926.1363 | 2721.3892 | 1171.7335 | 943.8252 | 1256.1635 | 2099.1336 | 1504.036 | 1504.036 | 1504.036 | 1504.036 | 1504.036 | 1504.036 | 1504.036 | 1504.036 | 1504.036 | 1504.036 | 1504.036 | 1504.036 | 1504.036 | 1504.036 | 1504.036 | 1504.036
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 17.7632 | 43.0375 | 49.6507 | 27.4299 | 27.4579 | 28.1359 | 29.9263 | 31.124 | 32.297 | 33.6691 | 34.9399 | 36.1742 | 36.3142 | 37.7549 | 36.661 | 36.661 | 36.661 | 36.661 | 36.661 | 36.661 | 36.661 | 36.661 | 36.661 | 36.661 | 36.661 | 36.661 | 36.661 | 36.661 | 36.661 | 36.661
98% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 8.4503 | 20.9604 | 24.2338 | 13.235 | 13.2489 | 13.5845 | 14.4707 | 15.0635 | 15.6442 | 16.3233 | 16.9523 | 17.5632 | 17.6325 | 18.3457 | 17.8042 | 17.8042 | 17.8042 | 17.8042 | 17.8042 | 17.8042 | 17.8042 | 17.8042 | 17.8042 | 17.8042 | 17.8042 | 17.8042 | 17.8042 | 17.8042 | 17.8042 | 17.8042
97% | 1.8466 | 8.0258 | 9.7077 | 4.3124 | 4.3106 | 4.5023 | 4.7127 | 5.1445 | 5.4548 | 5.6232 | 5.8073 | 5.9758 | 6.2803 | 6.6582 | 6.6318 | 6.6318 | 6.6318 | 6.6318 | 6.6318 | 6.6318 | 6.6318 | 6.6318 | 6.6318 | 6.6318 | 6.6318 | 6.6318 | 6.6318 | 6.6318 | 6.6318 | 6.6318 |  | 16.0379 | 40.8042 | 47.2844 | 25.5103 | 25.5377 | 26.2021 | 27.9566 | 29.1302 | 30.2796 | 31.6241 | 32.8694 | 34.0788 | 34.216 | 35.6278 | 34.5558 | 34.5558 | 34.5558 | 34.5558 | 34.5558 | 34.5558 | 34.5558 | 34.5558 | 34.5558 | 34.5558 | 34.5558 | 34.5558 | 34.5558 | 34.5558 | 34.5558 | 34.5558
95% | 7.7819 | 38.2025 | 46.4828 | 19.9214 | 19.9125 | 20.8562 | 21.8918 | 24.0179 | 25.5456 | 26.3744 | 27.2806 | 28.1102 | 29.6094 | 31.47 | 31.34 | 31.34 | 31.34 | 31.34 | 31.34 | 31.34 | 31.34 | 31.34 | 31.34 | 31.34 | 31.34 | 31.34 | 31.34 | 31.34 | 31.34 | 31.34 |  | 22.1159 | 58.6938 | 68.2646 | 36.1059 | 36.1464 | 37.1277 | 39.7188 | 41.4522 | 43.1498 | 45.1356 | 46.9747 | 48.7609 | 48.9636 | 51.0487 | 49.4655 | 49.4655 | 49.4655 | 49.4655 | 49.4655 | 49.4655 | 49.4655 | 49.4655 | 49.4655 | 49.4655 | 49.4655 | 49.4655 | 49.4655 | 49.4655 | 49.4655 | 49.4655
90% | 7.9129 | 60.6736 | 75.0348 | 28.9674 | 28.952 | 30.5887 | 32.3848 | 36.0721 | 38.7218 | 40.1592 | 41.731 | 43.1699 | 45.7699 | 48.997 | 48.7715 | 48.7715 | 48.7715 | 48.7715 | 48.7715 | 48.7715 | 48.7715 | 48.7715 | 48.7715 | 48.7715 | 48.7715 | 48.7715 | 48.7715 | 48.7715 | 48.7715 | 48.7715 |  | 79.1417 | 237.7413 | 279.2396 | 139.8013 | 139.9771 | 144.2318 | 155.4669 | 162.9825 | 170.3435 | 178.9535 | 186.9278 | 194.6728 | 195.5516 | 204.5923 | 197.7277 | 197.7277 | 197.7277 | 197.7277 | 197.7277 | 197.7277 | 197.7277 | 197.7277 | 197.7277 | 197.7277 | 197.7277 | 197.7277 | 197.7277 | 197.7277 | 197.7277 | 197.7277
85% | 2.1831 | 147.3455 | 188.1003 | 57.3685 | 57.3248 | 61.9696 | 67.0665 | 77.5307 | 85.0501 | 89.1291 | 93.5895 | 97.6729 | 105.0514 | 114.2094 | 113.5693 | 113.5693 | 113.5693 | 113.5693 | 113.5693 | 113.5693 | 113.5693 | 113.5693 | 113.5693 | 113.5693 | 113.5693 | 113.5693 | 113.5693 | 113.5693 | 113.5693 | 113.5693 |  | 50.0275 | 200.0542 | 239.3094 | 107.4082 | 107.5746 | 111.5993 | 122.2271 | 129.3365 | 136.2995 | 144.4441 | 151.9874 | 159.3138 | 160.145 | 168.697 | 162.2035 | 162.2035 | 162.2035 | 162.2035 | 162.2035 | 162.2035 | 162.2035 | 162.2035 | 162.2035 | 162.2035 | 162.2035 | 162.2035 | 162.2035 | 162.2035 | 162.2035 | 162.2035
80% |  | 166.9191 | 223.8464 | 41.2369 | 41.1758 | 47.6638 | 54.7833 | 69.3999 | 79.9032 | 85.6009 | 91.8314 | 97.535 | 107.8416 | 120.6337 | 119.7396 | 119.7396 | 119.7396 | 119.7396 | 119.7396 | 119.7396 | 119.7396 | 119.7396 | 119.7396 | 119.7396 | 119.7396 | 119.7396 | 119.7396 | 119.7396 | 119.7396 | 119.7396 |  | 15.4914 | 120.2719 | 147.6883 | 55.5668 | 55.683 | 58.4939 | 65.9165 | 70.8818 | 75.7449 | 81.4332 | 86.7015 | 91.8183 | 92.3989 | 98.3717 | 93.8366 | 93.8366 | 93.8366 | 93.8366 | 93.8366 | 93.8366 | 93.8366 | 93.8366 | 93.8366 | 93.8366 | 93.8366 | 93.8366 | 93.8366 | 93.8366 | 93.8366 | 93.8366
75% |  | 320.647 | 469.0463 | 11.8861 | 11.8144 | 20.5868 | 32.8706 | 66.4324 | 93.8125 | 108.6653 | 124.907 | 139.7754 | 166.6427 | 199.9896 | 197.6587 | 197.6587 | 197.6587 | 197.6587 | 197.6587 | 197.6587 | 197.6587 | 197.6587 | 197.6587 | 197.6587 | 197.6587 | 197.6587 | 197.6587 | 197.6587 | 197.6587 | 197.6587 |  | 0.97657 | 175.4756 | 224.4096 | 59.9868 | 60.1942 | 65.2112 | 78.4594 | 87.3217 | 96.0016 | 106.1543 | 115.5574 | 124.6902 | 125.7264 | 136.387 | 128.2925 | 128.2925 | 128.2925 | 128.2925 | 128.2925 | 128.2925 | 128.2925 | 128.2925 | 128.2925 | 128.2925 | 128.2925 | 128.2925 | 128.2925 | 128.2925 | 128.2925 | 128.2925
70% |  | 328.9116 | 585.3005 |  |  |  |  | 0.08245 | 6.4335 | 14.015 | 25.5392 | 38.9835 | 70.0963 | 120.4844 | 116.5503 | 116.5503 | 116.5503 | 116.5503 | 116.5503 | 116.5503 | 116.5503 | 116.5503 | 116.5503 | 116.5503 | 116.5503 | 116.5503 | 116.5503 | 116.5503 | 116.5503 | 116.5503 |  |  | 238.4252 | 327.5698 | 29.542 | 29.8529 | 37.84 | 61.6877 | 77.8323 | 93.6448 | 112.1403 | 129.2702 | 145.9078 | 147.7954 | 167.2162 | 152.4701 | 152.4701 | 152.4701 | 152.4701 | 152.4701 | 152.4701 | 152.4701 | 152.4701 | 152.4701 | 152.4701 | 152.4701 | 152.4701 | 152.4701 | 152.4701 | 152.4701 | 152.4701
65% | FY26: 199.3768; FY27: 820.987 |  |  | 182.6144 | 294.7721 |  |  |  | 1.9313 | 7.3745 | 15.9911 | 30.0435 | 46.7383 | 66.2133 | 68.5882 | 93.0226 | 74.4697 | 74.4697 | 74.4697 | 74.4697 | 74.4697 | 74.4697 | 74.4697 | 74.4697 | 74.4697 | 74.4697 | 74.4697 | 74.4697 | 74.4697 | 74.4697 | 74.4697 | 74.4697
60% | FY27: 203.5024 |  |  | 77.0598 | 248.2313 | [8 empty] | 0.0034722 | 0.058789 | 4.4803 | 0.48434 | 0.48434 | 0.48434 | 0.48434 | 0.48434 | 0.48434 | 0.48434 | 0.48434 | 0.48434 | 0.48434 | 0.48434 | 0.48434 | 0.48434 | 0.48434 | 0.48434 | 0.48434
55% | [33 empty] | 63.4905
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 19.7244 | 1270.1019 | 2622.0083 | 163.6927 | 163.4901 | 186.1673 | 213.7097 | 278.68 | 334.9216 | 369.5671 | 410.6859 | 451.2227 | 531.2915 | 642.4425 | 634.2611 | 634.2611 | 634.2611 | 634.2611 | 634.2611 | 634.2611 | 634.2611 | 634.2611 | 634.2611 | 634.2611 | 634.2611 | 634.2611 | 634.2611 | 634.2611 | 634.2611 | 634.2611 | E @ R (MWh) | 210.0044 | 1395.1384 | 2014.1441 | 494.5861 | 495.6728 | 522.4263 | 597.7613 | 652.4991 | 709.396 | 779.9211 | 848.9188 | 919.1969 | 927.3906 | 1015.5441 | 947.9709 | 947.9709 | 947.9709 | 947.9709 | 947.9709 | 947.9709 | 947.9709 | 947.9709 | 947.9709 | 947.9709 | 947.9709 | 947.9709 | 947.9709 | 947.9709 | 947.9709 | 947.9709
Option 4 Summer POE50 W E @ R (MWh) N 1 | 13.8071 | 889.0713 | 1835.4058 | 114.5849 | 114.4431 | 130.3171 | 149.5968 | 195.076 | 234.4451 | 258.697 | 287.4802 | 315.8559 | 371.9041 | 449.7097 | 443.9828 | 443.9828 | 443.9828 | 443.9828 | 443.9828 | 443.9828 | 443.9828 | 443.9828 | 443.9828 | 443.9828 | 443.9828 | 443.9828 | 443.9828 | 443.9828 | 443.9828 | 443.9828 | Option 4 Summer POE10 W E @ R (MWh) N 1 | 63.0013 | 418.5415 | 604.2432 | 148.3758 | 148.7018 | 156.7279 | 179.3284 | 195.7497 | 212.8188 | 233.9763 | 254.6756 | 275.7591 | 278.2172 | 304.6632 | 284.3913 | 284.3913 | 284.3913 | 284.3913 | 284.3913 | 284.3913 | 284.3913 | 284.3913 | 284.3913 | 284.3913 | 284.3913 | 284.3913 | 284.3913 | 284.3913 | 284.3913 | 284.3913
Option 5 - 4A LLG 2nd Tx + Switchroom + Three new feeders + OFR12 New Feeder
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% |  | 19.3557 | 26.0414 | [10 empty] | 3.3457 | 0.036908 | 0.036908 | 0.036908 | 0.036908 | 0.036908 | 0.036908 | 0.036908 | 0.036908 | 0.036908 | 0.036908 | 0.036908 | 0.036908 | 0.036908 | 0.036908 | 0.036908 | 0.036908 |  |  | 23.7132 | 30.66 | [5 empty] | 0.19441 | 11.3518 | 2.1235 | 0.31797 | 2.7481 | 8.0708 | 4.4624 | 4.4624 | 4.4624 | 4.4624 | 4.4624 | 4.4624 | 4.4624 | 4.4624 | 4.4624 | 4.4624 | 4.4624 | 4.4624 | 4.4624 | 4.4624 | 4.4624 | 4.4624
98% | FY26: 22.1134; FY27: 30.0556; FY38: 3.0945 |  |  | 27.2899 | 35.5423 | [6 empty] | 12.6053 | 1.6426 |  | 2.3847 | 8.7077 | 4.4212 | 4.4212 | 4.4212 | 4.4212 | 4.4212 | 4.4212 | 4.4212 | 4.4212 | 4.4212 | 4.4212 | 4.4212 | 4.4212 | 4.4212 | 4.4212 | 4.4212 | 4.4212
97% | FY26: 42.0001; FY27: 57.7232; FY38: 4.3484 |  |  | 52.248 | 68.5852 | [6 empty] | 23.1769 | 1.4742 |  | 2.9432 | 15.4607 | 6.9748 | 6.9748 | 6.9748 | 6.9748 | 6.9748 | 6.9748 | 6.9748 | 6.9748 | 6.9748 | 6.9748 | 6.9748 | 6.9748 | 6.9748 | 6.9748 | 6.9748 | 6.9748
95% | FY26: 115.9799; FY27: 162.4236; FY38: 4.7886 |  |  | 146.2505 | 194.5083 | [6 empty] | 60.379 | 0.1339 |  | 1.6925 | 37.5867 | 12.5205 | 12.5205 | 12.5205 | 12.5205 | 12.5205 | 12.5205 | 12.5205 | 12.5205 | 12.5205 | 12.5205 | 12.5205 | 12.5205 | 12.5205 | 12.5205 | 12.5205 | 12.5205
90% | FY26: 529.8714; FY27: 785.9431 |  |  | 696.7712 | 962.8455 | [6 empty] | 223.3101 |  |  |  | 97.6426 | 4.888 | 4.888 | 4.888 | 4.888 | 4.888 | 4.888 | 4.888 | 4.888 | 4.888 | 4.888 | 4.888 | 4.888 | 4.888 | 4.888 | 4.888 | 4.888
85% | FY26: 874.8065; FY27: 1500.3713 |  |  | 1282.5306 | 1932.5312 | [6 empty] | 136.8804 |  |  |  | 1.4571
80% | FY26: 628.4185; FY27: 1600.7316 |  |  | 1262.1427 | 2272.4362
75% | FY26: 35.4297; FY27: 855.1312 |  |  | 481.7498 | 1596.2089
70% | FY27: 65.8085 |  |  |  | 601.3916
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 2267.9753 | 5084.2295 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.5772 | 0.036908 | 0.036908 | 0.036908 | 0.036908 | 0.036908 | 0.036908 | 0.036908 | 0.036908 | 0.036908 | 0.036908 | 0.036908 | 0.036908 | 0.036908 | 0.036908 | 0.036908 | 0.036908 | E @ R (MWh) | 0 | 3972.6958 | 7694.7094 | 0 | 0 | 0 | 0 | 0 | 0.19441 | 467.7034 | 5.3742 | 0.31797 | 9.7685 | 168.9256 | 33.267 | 33.267 | 33.267 | 33.267 | 33.267 | 33.267 | 33.267 | 33.267 | 33.267 | 33.267 | 33.267 | 33.267 | 33.267 | 33.267 | 33.267 | 33.267
Option 5 Winter POE50 W E @ R (MWh) N 1 | 0 | 1587.5827 | 3558.9606 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.904 | 0.025835 | 0.025835 | 0.025835 | 0.025835 | 0.025835 | 0.025835 | 0.025835 | 0.025835 | 0.025835 | 0.025835 | 0.025835 | 0.025835 | 0.025835 | 0.025835 | 0.025835 | 0.025835 | Option 5 Winter POE10 W E @ R (MWh) N 1 | 0 | 1191.8087 | 2308.4128 | 0 | 0 | 0 | 0 | 0 | 0.058322 | 140.311 | 1.6123 | 0.09539 | 2.9306 | 50.6777 | 9.9801 | 9.9801 | 9.9801 | 9.9801 | 9.9801 | 9.9801 | 9.9801 | 9.9801 | 9.9801 | 9.9801 | 9.9801 | 9.9801 | 9.9801 | 9.9801 | 9.9801 | 9.9801
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | 0 | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 17.7632 | 43.0375 | 49.6507 | 5.606 | 5.634 | 6.312 | 8.1025 | 9.3001 | 10.4732 | 11.8453 | 13.116 | 14.3503 | 14.4903 | 15.931 | 14.8371 | 14.8371 | 14.8371 | 14.8371 | 14.8371 | 14.8371 | 14.8371 | 14.8371 | 14.8371 | 14.8371 | 14.8371 | 14.8371 | 14.8371 | 14.8371 | 14.8371 | 14.8371
98% | 0 | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 8.4503 | 20.9604 | 24.2338 | 2.4328 | 2.4466 | 2.7822 | 3.6685 | 4.2613 | 4.8419 | 5.5211 | 6.1501 | 6.761 | 6.8303 | 7.5434 | 7.0019 | 7.0019 | 7.0019 | 7.0019 | 7.0019 | 7.0019 | 7.0019 | 7.0019 | 7.0019 | 7.0019 | 7.0019 | 7.0019 | 7.0019 | 7.0019 | 7.0019 | 7.0019
97% | 1.8466 | 8.0258 | 9.7077 | [5 empty] | 0.10855 | 0.27689 | 0.46097 | 0.62949 | 0.934 | 1.312 | 1.2855 | 1.2855 | 1.2855 | 1.2855 | 1.2855 | 1.2855 | 1.2855 | 1.2855 | 1.2855 | 1.2855 | 1.2855 | 1.2855 | 1.2855 | 1.2855 | 1.2855 | 1.2855 |  | 16.0379 | 40.8042 | 47.2844 | 4.1251 | 4.1525 | 4.8169 | 6.5714 | 7.745 | 8.8944 | 10.2389 | 11.4842 | 12.6936 | 12.8308 | 14.2426 | 13.1706 | 13.1706 | 13.1706 | 13.1706 | 13.1706 | 13.1706 | 13.1706 | 13.1706 | 13.1706 | 13.1706 | 13.1706 | 13.1706 | 13.1706 | 13.1706 | 13.1706 | 13.1706
95% | 7.7819 | 38.2025 | 46.4828 | [5 empty] | 0.0030568 | 0.24961 | 0.96038 | 1.79 | 3.2891 | 5.1498 | 5.0198 | 5.0198 | 5.0198 | 5.0198 | 5.0198 | 5.0198 | 5.0198 | 5.0198 | 5.0198 | 5.0198 | 5.0198 | 5.0198 | 5.0198 | 5.0198 | 5.0198 | 5.0198 |  | 22.1159 | 58.6938 | 68.2646 | 4.5216 | 4.5621 | 5.5434 | 8.1346 | 9.8679 | 11.5656 | 13.5513 | 15.3904 | 17.1766 | 17.3793 | 19.4644 | 17.8812 | 17.8812 | 17.8812 | 17.8812 | 17.8812 | 17.8812 | 17.8812 | 17.8812 | 17.8812 | 17.8812 | 17.8812 | 17.8812 | 17.8812 | 17.8812 | 17.8812 | 17.8812
90% | 7.9129 | 60.6736 | 75.0348 | [7 empty] | 0.00082382 | 0.1558 | 1.0969 | 3.3938 | 3.1941 | 3.1941 | 3.1941 | 3.1941 | 3.1941 | 3.1941 | 3.1941 | 3.1941 | 3.1941 | 3.1941 | 3.1941 | 3.1941 | 3.1941 | 3.1941 | 3.1941 | 3.1941 |  | 79.1417 | 237.7413 | 279.2396 | 4.7137 | 4.8234 | 7.8474 | 18.5194 | 26.035 | 33.396 | 42.006 | 49.9803 | 57.7254 | 58.6041 | 67.6448 | 60.7802 | 60.7802 | 60.7802 | 60.7802 | 60.7802 | 60.7802 | 60.7802 | 60.7802 | 60.7802 | 60.7802 | 60.7802 | 60.7802 | 60.7802 | 60.7802 | 60.7802 | 60.7802
85% | FY25: 2.1831; FY26: 147.3455; FY27: 188.1003 |  | 50.0275 | 200.0542 | 239.3094 |  |  |  | 0.60705 | 3.177 | 7.5638 | 14.8992 | 22.4425 | 29.7689 | 30.6001 | 39.1521 | 32.6586 | 32.6586 | 32.6586 | 32.6586 | 32.6586 | 32.6586 | 32.6586 | 32.6586 | 32.6586 | 32.6586 | 32.6586 | 32.6586 | 32.6586 | 32.6586 | 32.6586 | 32.6586
80% | FY26: 166.9191; FY27: 223.8464 |  | 15.4914 | 120.2719 | 147.6883 | [6 empty] | 0.024748 | 1.0118 | 3.3033 | 3.6436 | 8.0631 | 4.5553 | 4.5553 | 4.5553 | 4.5553 | 4.5553 | 4.5553 | 4.5553 | 4.5553 | 4.5553 | 4.5553 | 4.5553 | 4.5553 | 4.5553 | 4.5553 | 4.5553 | 4.5553
75% | FY26: 320.647; FY27: 469.0463 |  | 0.97657 | 175.4756 | 224.4096
70% | FY26: 328.9116; FY27: 585.3005 |  |  | 238.4252 | 327.5698
65% | FY26: 199.3768; FY27: 820.987 |  |  | 182.6144 | 294.7721
60% | FY27: 203.5024 |  |  | 77.0598 | 248.2313
55% | [33 empty] | 63.4905
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 19.7244 | 1270.1019 | 2622.0083 | 0 | 0 | 0 | 0 | 0 | 0.11161 | 0.5265 | 1.4222 | 2.5753 | 5.3201 | 9.8556 | 9.4994 | 9.4994 | 9.4994 | 9.4994 | 9.4994 | 9.4994 | 9.4994 | 9.4994 | 9.4994 | 9.4994 | 9.4994 | 9.4994 | 9.4994 | 9.4994 | 9.4994 | 9.4994 | E @ R (MWh) | 210.0044 | 1395.1384 | 2014.1441 | 21.3991 | 21.6187 | 27.302 | 45.6033 | 60.3864 | 76.7349 | 98.0866 | 119.5752 | 141.7791 | 144.3786 | 172.0415 | 150.8851 | 150.8851 | 150.8851 | 150.8851 | 150.8851 | 150.8851 | 150.8851 | 150.8851 | 150.8851 | 150.8851 | 150.8851 | 150.8851 | 150.8851 | 150.8851 | 150.8851 | 150.8851
Option 5 Summer POE50 W E @ R (MWh) N 1 | 13.8071 | 889.0713 | 1835.4058 | 0 | 0 | 0 | 0 | 0 | 0.078125 | 0.36855 | 0.99552 | 1.8027 | 3.724 | 6.8989 | 6.6496 | 6.6496 | 6.6496 | 6.6496 | 6.6496 | 6.6496 | 6.6496 | 6.6496 | 6.6496 | 6.6496 | 6.6496 | 6.6496 | 6.6496 | 6.6496 | 6.6496 | 6.6496 | Option 5 Summer POE10 W E @ R (MWh) N 1 | 63.0013 | 418.5415 | 604.2432 | 6.4197 | 6.4856 | 8.1906 | 13.681 | 18.1159 | 23.0205 | 29.426 | 35.8726 | 42.5337 | 43.3136 | 51.6124 | 45.2655 | 45.2655 | 45.2655 | 45.2655 | 45.2655 | 45.2655 | 45.2655 | 45.2655 | 45.2655 | 45.2655 | 45.2655 | 45.2655 | 45.2655 | 45.2655 | 45.2655 | 45.2655
Option 6 - Non Network
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% |  | 4.6288 | 10.4635 | 11.656 | 12.5428 | 13.987 | 17.24 | 19.4181 | 22.2214 | 23.5779 | 24.7634 | 22.1181 | 25.0141 | 29.4085 | 26.075 | 26.075 | 26.075 | 26.075 | 26.075 | 26.075 | 26.075 | 26.075 | 26.075 | 26.075 | 26.075 | 26.075 | 26.075 | 26.075 | 26.075 | 26.075 |  |  | 8.9863 | 15.0821 | 16.2098 | 16.8901 | 18.3012 | 21.6086 | 23.3864 | 26.9156 | 37.9265 | 28.5394 | 26.576 | 28.9938 | 34.1336 | 30.6709 | 30.6709 | 30.6709 | 30.6709 | 30.6709 | 30.6709 | 30.6709 | 30.6709 | 30.6709 | 30.6709 | 30.6709 | 30.6709 | 30.6709 | 30.6709 | 30.6709 | 30.6709
98% |  | 4.6187 | 11.55 | 12.9667 | 14.0201 | 15.7358 | 19.6001 | 22.1876 | 25.5178 | 27.1292 | 28.5375 | 25.3951 | 28.8353 | 34.0556 | 30.0955 | 30.0955 | 30.0955 | 30.0955 | 30.0955 | 30.0955 | 30.0955 | 30.0955 | 30.0955 | 30.0955 | 30.0955 | 30.0955 | 30.0955 | 30.0955 | 30.0955 | 30.0955 |  |  | 9.7952 | 17.0367 | 18.3763 | 19.1845 | 20.8607 | 24.7897 | 26.9017 | 31.0942 | 44.1744 | 33.0231 | 30.6907 | 33.5629 | 39.6688 | 35.5553 | 35.5553 | 35.5553 | 35.5553 | 35.5553 | 35.5553 | 35.5553 | 35.5553 | 35.5553 | 35.5553 | 35.5553 | 35.5553 | 35.5553 | 35.5553 | 35.5553 | 35.5553
97% |  | 7.3659 | 21.0878 | 23.8923 | 25.9778 | 29.3743 | 37.0245 | 42.1469 | 48.7396 | 51.9298 | 54.7179 | 48.4967 | 55.3074 | 65.6419 | 57.8022 | 57.8022 | 57.8022 | 57.8022 | 57.8022 | 57.8022 | 57.8022 | 57.8022 | 57.8022 | 57.8022 | 57.8022 | 57.8022 | 57.8022 | 57.8022 | 57.8022 | 57.8022 |  |  | 17.6138 | 31.9498 | 34.6018 | 36.2016 | 39.5201 | 47.2984 | 51.4794 | 59.7793 | 85.6741 | 63.5979 | 58.9805 | 64.6665 | 76.7543 | 68.6108 | 68.6108 | 68.6108 | 68.6108 | 68.6108 | 68.6108 | 68.6108 | 68.6108 | 68.6108 | 68.6108 | 68.6108 | 68.6108 | 68.6108 | 68.6108 | 68.6108 | 68.6108
95% |  | 13.6759 | 54.2081 | 62.4921 | 68.6523 | 78.6853 | 101.2828 | 116.4135 | 135.8874 | 145.3107 | 153.5462 | 135.1698 | 155.2877 | 185.8142 | 162.6569 | 162.6569 | 162.6569 | 162.6569 | 162.6569 | 162.6569 | 162.6569 | 162.6569 | 162.6569 | 162.6569 | 162.6569 | 162.6569 | 162.6569 | 162.6569 | 162.6569 | 162.6569 |  |  | 43.9464 | 86.2928 | 94.1265 | 98.8521 | 108.6544 | 131.6301 | 143.9802 | 168.4968 | 244.9861 | 179.7766 | 166.1374 | 182.933 | 218.6384 | 194.5839 | 194.5839 | 194.5839 | 194.5839 | 194.5839 | 194.5839 | 194.5839 | 194.5839 | 194.5839 | 194.5839 | 194.5839 | 194.5839 | 194.5839 | 194.5839 | 194.5839 | 194.5839
90% |  | 6.6229 | 189.2861 | 234.9612 | 268.9262 | 324.244 | 448.8373 | 532.2619 | 639.6335 | 691.5896 | 736.9969 | 635.677 | 746.5987 | 914.9099 | 787.2295 | 787.2295 | 787.2295 | 787.2295 | 787.2295 | 787.2295 | 787.2295 | 787.2295 | 787.2295 | 787.2295 | 787.2295 | 787.2295 | 787.2295 | 787.2295 | 787.2295 | 787.2295 |  |  | 132.7077 | 366.1885 | 409.3802 | 435.4354 | 489.4814 | 616.1604 | 684.254 | 819.4287 | 1241.16 | 881.6207 | 806.4196 | 899.0239 | 1095.8891 | 963.2624 | 963.2624 | 963.2624 | 963.2624 | 963.2624 | 963.2624 | 963.2624 | 963.2624 | 963.2624 | 963.2624 | 963.2624 | 963.2624 | 963.2624 | 963.2624 | 963.2624 | 963.2624
85% |  |  | 79.1989 | 160.0678 | 237.3359 | 372.4735 | 676.8459 | 880.6462 | 1142.9473 | 1269.8723 | 1380.7992 | 1133.2818 | 1404.2556 | 1815.428 | 1503.5139 | 1503.5139 | 1503.5139 | 1503.5139 | 1503.5139 | 1503.5139 | 1503.5139 | 1503.5139 | 1503.5139 | 1503.5139 | 1503.5139 | 1503.5139 | 1503.5139 | 1503.5139 | 1503.5139 | 1503.5139 |  |  | 17.4452 | 474.9409 | 580.4551 | 644.106 | 776.1365 | 1085.6042 | 1251.9521 | 1582.1741 | 2612.4334 | 1734.1048 | 1550.3939 | 1776.6194 | 2257.5472 | 1933.5496 | 1933.5496 | 1933.5496 | 1933.5496 | 1933.5496 | 1933.5496 | 1933.5496 | 1933.5496 | 1933.5496 | 1933.5496 | 1933.5496 | 1933.5496 | 1933.5496 | 1933.5496 | 1933.5496 | 1933.5496
80% |  |  |  |  | 0.13803 | 34.7634 | 324.438 | 637.4951 | 1045.1888 | 1242.4679 | 1414.8812 | 1030.1658 | 1451.3394 | 2090.4231 | 1605.6162 | 1605.6162 | 1605.6162 | 1605.6162 | 1605.6162 | 1605.6162 | 1605.6162 | 1605.6162 | 1605.6162 | 1605.6162 | 1605.6162 | 1605.6162 | 1605.6162 | 1605.6162 | 1605.6162 | 1605.6162 |  |  |  | 100.4889 | 202.2828 | 279.8872 | 475.0561 | 956.0606 | 1214.6146 | 1727.8774 | 3329.2059 | 1964.0228 | 1678.4817 | 2030.1032 | 2777.6074 | 2274.0192 | 2274.0192 | 2274.0192 | 2274.0192 | 2274.0192 | 2274.0192 | 2274.0192 | 2274.0192 | 2274.0192 | 2274.0192 | 2274.0192 | 2274.0192 | 2274.0192 | 2274.0192 | 2274.0192 | 2274.0192
75% | [7 empty] | 38.2745 | 274.0415 | 460.6595 | 650.0863 | 261.7136 | 690.3099 | 1395.3976 | 860.5202 | 860.5202 | 860.5202 | 860.5202 | 860.5202 | 860.5202 | 860.5202 | 860.5202 | 860.5202 | 860.5202 | 860.5202 | 860.5202 | 860.5202 | 860.5202 | 860.5202 | 860.5202 | [6 empty] | 3.8748 | 204.8843 | 431.5615 | 995.4085 | 2762.1207 | 1255.9428 | 940.9112 | 1328.8478 | 2153.5536 | 1597.9553 | 1597.9553 | 1597.9553 | 1597.9553 | 1597.9553 | 1597.9553 | 1597.9553 | 1597.9553 | 1597.9553 | 1597.9553 | 1597.9553 | 1597.9553 | 1597.9553 | 1597.9553 | 1597.9553 | 1597.9553
70% | [10 empty] | 11.8153 |  | 19.0026 | 405.9763 | 67.8036 | 67.8036 | 67.8036 | 67.8036 | 67.8036 | 67.8036 | 67.8036 | 67.8036 | 67.8036 | 67.8036 | 67.8036 | 67.8036 | 67.8036 | 67.8036 | 67.8036 | 67.8036 | [9 empty] | 127.1488 | 1854.011 | 291.7219 | 101.0062 | 349.2232 | 1200.1397 | 603.2477 | 603.2477 | 603.2477 | 603.2477 | 603.2477 | 603.2477 | 603.2477 | 603.2477 | 603.2477 | 603.2477 | 603.2477 | 603.2477 | 603.2477 | 603.2477 | 603.2477 | 603.2477
65% | [40 empty] | 612.7924 |  |  |  | 141.1221
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 36.9122 | 365.7944 | 506.0361 | 627.5931 | 869.2634 | 1625.2686 | 2288.8437 | 3334.1773 | 3912.537 | 4456.1439 | 3292.0178 | 4575.9508 | 6937.0552 | 5101.313 | 5101.313 | 5101.313 | 5101.313 | 5101.313 | 5101.313 | 5101.313 | 5101.313 | 5101.313 | 5101.313 | 5101.313 | 5101.313 | 5101.313 | 5101.313 | 5101.313 | 5101.313 | E @ R (MWh) | 0 | 230.4946 | 1091.9798 | 1355.4326 | 1530.5569 | 1931.8852 | 3088.0363 | 3828.1299 | 5538.3234 | 12824.4846 | 6432.3501 | 5359.5973 | 6693.9736 | 9995.0542 | 7701.4551 | 7701.4551 | 7701.4551 | 7701.4551 | 7701.4551 | 7701.4551 | 7701.4551 | 7701.4551 | 7701.4551 | 7701.4551 | 7701.4551 | 7701.4551 | 7701.4551 | 7701.4551 | 7701.4551 | 7701.4551
Option 6 Winter POE50 W E @ R (MWh) N 1 | 0 | 25.8386 | 256.0561 | 354.2252 | 439.3152 | 608.4844 | 1137.6881 | 1602.1906 | 2333.9241 | 2738.7759 | 3119.3007 | 2304.4125 | 3203.1655 | 4855.9387 | 3570.9191 | 3570.9191 | 3570.9191 | 3570.9191 | 3570.9191 | 3570.9191 | 3570.9191 | 3570.9191 | 3570.9191 | 3570.9191 | 3570.9191 | 3570.9191 | 3570.9191 | 3570.9191 | 3570.9191 | 3570.9191 | Option 6 Winter POE10 W E @ R (MWh) N 1 | 0 | 69.1484 | 327.5939 | 406.6298 | 459.1671 | 579.5656 | 926.4109 | 1148.439 | 1661.497 | 3847.3454 | 1929.705 | 1607.8792 | 2008.1921 | 2998.5163 | 2310.4365 | 2310.4365 | 2310.4365 | 2310.4365 | 2310.4365 | 2310.4365 | 2310.4365 | 2310.4365 | 2310.4365 | 2310.4365 | 2310.4365 | 2310.4365 | 2310.4365 | 2310.4365 | 2310.4365 | 2310.4365
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 6.1054 | 28.0463 | 33.7932 | 33.4526 | 33.4829 | 34.0755 | 35.6337 | 36.6794 | 37.7017 | 38.8968 | 40.0059 | 41.0814 | 41.2069 | 42.4616 | 41.5159 | 41.5159 | 41.5159 | 41.5159 | 41.5159 | 41.5159 | 41.5159 | 41.5159 | 41.5159 | 41.5159 | 41.5159 | 41.5159 | 41.5159 | 41.5159 | 41.5159 | 41.5159
98% |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2.68 | 13.5402 | 16.3847 | 16.2161 | 16.2311 | 16.5244 | 17.2957 | 17.8133 | 18.3193 | 18.9109 | 19.4599 | 19.9922 | 20.0543 | 20.6753 | 20.2073 | 20.2073 | 20.2073 | 20.2073 | 20.2073 | 20.2073 | 20.2073 | 20.2073 | 20.2073 | 20.2073 | 20.2073 | 20.2073 | 20.2073 | 20.2073 | 20.2073 | 20.2073
97% |  | 4.3533 | 5.823 | 5.7879 | 5.7866 | 5.9574 | 6.1108 | 6.5055 | 6.7789 | 6.9038 | 7.0483 | 7.1779 | 7.4789 | 7.8113 | 7.8212 | 7.8212 | 7.8212 | 7.8212 | 7.8212 | 7.8212 | 7.8212 | 7.8212 | 7.8212 | 7.8212 | 7.8212 | 7.8212 | 7.8212 | 7.8212 | 7.8212 | 7.8212 |  | 4.6144 | 26.1143 | 31.7457 | 31.412 | 31.4416 | 32.0223 | 33.5492 | 34.5739 | 35.5756 | 36.7467 | 37.8335 | 38.8874 | 39.0104 | 40.2398 | 39.3132 | 39.3132 | 39.3132 | 39.3132 | 39.3132 | 39.3132 | 39.3132 | 39.3132 | 39.3132 | 39.3132 | 39.3132 | 39.3132 | 39.3132 | 39.3132 | 39.3132 | 39.3132
95% |  | 20.1226 | 27.3583 | 27.185 | 27.1789 | 28.0195 | 28.7751 | 30.7178 | 32.0638 | 32.6791 | 33.3904 | 34.0285 | 35.5101 | 37.1464 | 37.1952 | 37.1952 | 37.1952 | 37.1952 | 37.1952 | 37.1952 | 37.1952 | 37.1952 | 37.1952 | 37.1952 | 37.1952 | 37.1952 | 37.1952 | 37.1952 | 37.1952 | 37.1952 |  | 5.2443 | 36.998 | 45.3152 | 44.8222 | 44.866 | 45.7236 | 47.9788 | 49.4921 | 50.9716 | 52.7012 | 54.3064 | 55.8628 | 56.0445 | 57.8603 | 56.4917 | 56.4917 | 56.4917 | 56.4917 | 56.4917 | 56.4917 | 56.4917 | 56.4917 | 56.4917 | 56.4917 | 56.4917 | 56.4917 | 56.4917 | 56.4917 | 56.4917 | 56.4917
90% |  | 29.3164 | 41.8657 | 41.5652 | 41.5545 | 43.0125 | 44.323 | 47.6924 | 50.0268 | 51.0939 | 52.3276 | 53.4343 | 56.004 | 58.842 | 58.9265 | 58.9265 | 58.9265 | 58.9265 | 58.9265 | 58.9265 | 58.9265 | 58.9265 | 58.9265 | 58.9265 | 58.9265 | 58.9265 | 58.9265 | 58.9265 | 58.9265 | 58.9265 |  | 6.8512 | 143.6697 | 179.7323 | 177.5948 | 177.7849 | 181.5033 | 191.2816 | 197.8433 | 204.2584 | 211.7577 | 218.7176 | 225.4662 | 226.2539 | 234.1272 | 228.1929 | 228.1929 | 228.1929 | 228.1929 | 228.1929 | 228.1929 | 228.1929 | 228.1929 | 228.1929 | 228.1929 | 228.1929 | 228.1929 | 228.1929 | 228.1929 | 228.1929 | 228.1929
85% |  | 58.3589 | 93.9718 | 93.1192 | 93.0888 | 97.2264 | 100.9452 | 110.5071 | 117.1317 | 120.1601 | 123.6611 | 126.8017 | 134.0941 | 142.1478 | 142.3877 | 142.3877 | 142.3877 | 142.3877 | 142.3877 | 142.3877 | 142.3877 | 142.3877 | 142.3877 | 142.3877 | 142.3877 | 142.3877 | 142.3877 | 142.3877 | 142.3877 | 142.3877 |  |  | 111.0676 | 145.1808 | 143.1589 | 143.3387 | 146.8561 | 156.1058 | 162.3129 | 168.3812 | 175.4752 | 182.0589 | 188.4426 | 189.1878 | 196.6354 | 191.0219 | 191.0219 | 191.0219 | 191.0219 | 191.0219 | 191.0219 | 191.0219 | 191.0219 | 191.0219 | 191.0219 | 191.0219 | 191.0219 | 191.0219 | 191.0219 | 191.0219 | 191.0219
80% |  | 42.6203 | 92.3653 | 91.1743 | 91.132 | 96.9114 | 102.106 | 115.4622 | 124.7157 | 128.9458 | 133.836 | 138.2229 | 148.4092 | 159.6588 | 159.9938 | 159.9938 | 159.9938 | 159.9938 | 159.9938 | 159.9938 | 159.9938 | 159.9938 | 159.9938 | 159.9938 | 159.9938 | 159.9938 | 159.9938 | 159.9938 | 159.9938 | 159.9938 |  |  | 58.1226 | 81.9477 | 80.5356 | 80.6611 | 83.1177 | 89.5778 | 93.9129 | 98.1511 | 103.1056 | 107.7038 | 112.1623 | 112.6827 | 117.8842 | 113.9637 | 113.9637 | 113.9637 | 113.9637 | 113.9637 | 113.9637 | 113.9637 | 113.9637 | 113.9637 | 113.9637 | 113.9637 | 113.9637 | 113.9637 | 113.9637 | 113.9637 | 113.9637
75% |  | 13.5643 | 126.2988 | 123.1943 | 123.0838 | 138.1498 | 151.691 | 186.5084 | 210.6304 | 221.6576 | 234.4055 | 245.8413 | 272.3952 | 301.7208 | 302.5942 | 302.5942 | 302.5942 | 302.5942 | 302.5942 | 302.5942 | 302.5942 | 302.5942 | 302.5942 | 302.5942 | 302.5942 | 302.5942 | 302.5942 | 302.5942 | 302.5942 | 302.5942 |  |  | 64.5484 | 107.0726 | 104.5522 | 104.7763 | 109.161 | 120.6913 | 128.4288 | 135.9933 | 144.8364 | 153.0434 | 161.0011 | 161.9299 | 171.2139 | 164.2163 | 164.2163 | 164.2163 | 164.2163 | 164.2163 | 164.2163 | 164.2163 | 164.2163 | 164.2163 | 164.2163 | 164.2163 | 164.2163 | 164.2163 | 164.2163 | 164.2163 | 164.2163
70% |  |  | 26.6813 | 24.1669 | 24.0797 | 37.3807 | 51.7127 | 98.5793 | 138.8365 | 157.8882 | 179.9126 | 199.6701 | 245.5472 | 296.213 | 297.7219 | 297.7219 | 297.7219 | 297.7219 | 297.7219 | 297.7219 | 297.7219 | 297.7219 | 297.7219 | 297.7219 | 297.7219 | 297.7219 | 297.7219 | 297.7219 | 297.7219 | 297.7219 |  |  | 36.734 | 113.8133 | 109.2217 | 109.63 | 117.6177 | 138.6228 | 152.7184 | 166.499 | 182.6087 | 197.5596 | 212.0564 | 213.7486 | 230.6615 | 217.9138 | 217.9138 | 217.9138 | 217.9138 | 217.9138 | 217.9138 | 217.9138 | 217.9138 | 217.9138 | 217.9138 | 217.9138 | 217.9138 | 217.9138 | 217.9138 | 217.9138 | 217.9138
65% | [8 empty] | 1.0199 | 5.5431 | 15.2098 | 27.8639 | 71.4321 | 141.8833 | 144.3317 | 144.3317 | 144.3317 | 144.3317 | 144.3317 | 144.3317 | 144.3317 | 144.3317 | 144.3317 | 144.3317 | 144.3317 | 144.3317 | 144.3317 | 144.3317 | 144.3317 | 144.3317 |  |  |  | 31.5203 | 27.5478 | 27.8907 | 35.0035 | 57.299 | 74.7821 | 92.1201 | 112.3886 | 131.1992 | 149.4385 | 151.5675 | 172.8466 | 156.8079 | 156.8079 | 156.8079 | 156.8079 | 156.8079 | 156.8079 | 156.8079 | 156.8079 | 156.8079 | 156.8079 | 156.8079 | 156.8079 | 156.8079 | 156.8079 | 156.8079 | 156.8079
60% | [38 empty] | 0.51839 | 4.1939 | 12.8462 | 24.9473 | 40.3074 | 42.3282 | 65.0838 | 47.5022 | 47.5022 | 47.5022 | 47.5022 | 47.5022 | 47.5022 | 47.5022 | 47.5022 | 47.5022 | 47.5022 | 47.5022 | 47.5022 | 47.5022 | 47.5022 | 47.5022 | 47.5022
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 168.3359 | 414.3642 | 406.1929 | 405.9043 | 446.6577 | 485.6638 | 595.9727 | 681.2036 | 724.8717 | 779.7912 | 833.0406 | 970.8708 | 1145.4234 | 1150.9721 | 1150.9721 | 1150.9721 | 1150.9721 | 1150.9721 | 1150.9721 | 1150.9721 | 1150.9721 | 1150.9721 | 1150.9721 | 1150.9721 | 1150.9721 | 1150.9721 | 1150.9721 | 1150.9721 | 1150.9721 | E @ R (MWh) | 25.4953 | 518.8411 | 786.5059 | 768.5139 | 770.1033 | 801.605 | 888.0357 | 949.0756 | 1012.1653 | 1090.274 | 1166.8355 | 1244.6981 | 1254.0146 | 1349.6897 | 1277.1467 | 1277.1467 | 1277.1467 | 1277.1467 | 1277.1467 | 1277.1467 | 1277.1467 | 1277.1467 | 1277.1467 | 1277.1467 | 1277.1467 | 1277.1467 | 1277.1467 | 1277.1467 | 1277.1467 | 1277.1467
Option 6 Summer POE50 W E @ R (MWh) N 1 | 0 | 117.8351 | 290.0549 | 284.335 | 284.133 | 312.6604 | 339.9647 | 417.1809 | 476.8425 | 507.4102 | 545.8538 | 583.1284 | 679.6096 | 801.7964 | 805.6804 | 805.6804 | 805.6804 | 805.6804 | 805.6804 | 805.6804 | 805.6804 | 805.6804 | 805.6804 | 805.6804 | 805.6804 | 805.6804 | 805.6804 | 805.6804 | 805.6804 | 805.6804 | Option 6 Summer POE10 W E @ R (MWh) N 1 | 7.6486 | 155.6523 | 235.9518 | 230.5542 | 231.031 | 240.4815 | 266.4107 | 284.7227 | 303.6496 | 327.0822 | 350.0506 | 373.4094 | 376.2044 | 404.9069 | 383.144 | 383.144 | 383.144 | 383.144 | 383.144 | 383.144 | 383.144 | 383.144 | 383.144 | 383.144 | 383.144 | 383.144 | 383.144 | 383.144 | 383.144 | 383.144
Option 7 -
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% |  | 19.3557 | 26.0414 | 27.1786 | 28.0631 | 29.5913 | 33.0724 | 35.3998 | 38.3512 | 39.8816 | 41.2259 | 38.7366 | 41.6468 | 46.224 | 42.7448 | 42.7448 | 42.7448 | 42.7448 | 42.7448 | 42.7448 | 42.7448 | 42.7448 | 42.7448 | 42.7448 | 42.7448 | 42.7448 | 42.7448 | 42.7448 | 42.7448 | 42.7448 |  |  | 23.7132 | 30.66 | 31.7324 | 32.4104 | 33.9055 | 37.4409 | 39.3681 | 43.0454 | 54.2301 | 45.0018 | 43.1944 | 45.6265 | 50.9491 | 47.3408 | 47.3408 | 47.3408 | 47.3408 | 47.3408 | 47.3408 | 47.3408 | 47.3408 | 47.3408 | 47.3408 | 47.3408 | 47.3408 | 47.3408 | 47.3408 | 47.3408 | 47.3408
98% |  | 22.1134 | 30.0556 | 31.4065 | 32.4573 | 34.2728 | 38.408 | 41.1729 | 44.679 | 46.497 | 48.0939 | 45.1368 | 48.594 | 54.0314 | 49.8983 | 49.8983 | 49.8983 | 49.8983 | 49.8983 | 49.8983 | 49.8983 | 49.8983 | 49.8983 | 49.8983 | 49.8983 | 49.8983 | 49.8983 | 49.8983 | 49.8983 | 49.8983 |  |  | 27.2899 | 35.5423 | 36.8162 | 37.6217 | 39.3977 | 43.5976 | 45.887 | 50.2554 | 63.5422 | 52.5795 | 50.4324 | 53.3215 | 59.6445 | 55.358 | 55.358 | 55.358 | 55.358 | 55.358 | 55.358 | 55.358 | 55.358 | 55.358 | 55.358 | 55.358 | 55.358 | 55.358 | 55.358 | 55.358 | 55.358
97% |  | 42.0001 | 57.7232 | 60.3976 | 62.4779 | 66.0719 | 74.2584 | 79.732 | 86.673 | 90.2721 | 93.4336 | 87.5793 | 94.4235 | 105.1879 | 97.0056 | 97.0056 | 97.0056 | 97.0056 | 97.0056 | 97.0056 | 97.0056 | 97.0056 | 97.0056 | 97.0056 | 97.0056 | 97.0056 | 97.0056 | 97.0056 | 97.0056 | 97.0056 |  |  | 52.248 | 68.5852 | 71.1071 | 72.7018 | 76.2177 | 84.5323 | 89.0645 | 97.7126 | 124.0163 | 102.3136 | 98.0631 | 103.7826 | 116.3002 | 107.8143 | 107.8143 | 107.8143 | 107.8143 | 107.8143 | 107.8143 | 107.8143 | 107.8143 | 107.8143 | 107.8143 | 107.8143 | 107.8143 | 107.8143 | 107.8143 | 107.8143 | 107.8143
95% |  | 115.9799 | 162.4236 | 170.3233 | 176.4681 | 187.0842 | 211.266 | 227.434 | 247.9367 | 258.5678 | 267.9064 | 250.6138 | 270.8306 | 302.6268 | 278.4578 | 278.4578 | 278.4578 | 278.4578 | 278.4578 | 278.4578 | 278.4578 | 278.4578 | 278.4578 | 278.4578 | 278.4578 | 278.4578 | 278.4578 | 278.4578 | 278.4578 | 278.4578 |  |  | 146.2505 | 194.5083 | 201.9576 | 206.6678 | 217.0533 | 241.6134 | 255.0008 | 280.5461 | 358.2432 | 294.1368 | 281.5814 | 298.4759 | 335.451 | 310.3848 | 310.3848 | 310.3848 | 310.3848 | 310.3848 | 310.3848 | 310.3848 | 310.3848 | 310.3848 | 310.3848 | 310.3848 | 310.3848 | 310.3848 | 310.3848 | 310.3848 | 310.3848
90% |  | 529.8714 | 785.9431 | 829.499 | 863.379 | 921.9121 | 1055.2409 | 1144.3849 | 1257.4283 | 1316.044 | 1367.5334 | 1272.189 | 1383.6562 | 1558.9677 | 1425.7093 | 1425.7093 | 1425.7093 | 1425.7093 | 1425.7093 | 1425.7093 | 1425.7093 | 1425.7093 | 1425.7093 | 1425.7093 | 1425.7093 | 1425.7093 | 1425.7093 | 1425.7093 | 1425.7093 | 1425.7093 |  |  | 696.7712 | 962.8455 | 1003.918 | 1029.8882 | 1087.1494 | 1222.564 | 1296.377 | 1437.2235 | 1865.6143 | 1512.1572 | 1442.9317 | 1536.0814 | 1739.9469 | 1601.7422 | 1601.7422 | 1601.7422 | 1601.7422 | 1601.7422 | 1601.7422 | 1601.7422 | 1601.7422 | 1601.7422 | 1601.7422 | 1601.7422 | 1601.7422 | 1601.7422 | 1601.7422 | 1601.7422 | 1601.7422
85% |  | 874.8065 | 1500.3713 | 1606.7752 | 1689.5415 | 1832.5337 | 2158.2465 | 2376.0188 | 2652.1757 | 2795.3696 | 2921.1546 | 2688.2351 | 2960.5416 | 3388.8149 | 3063.2741 | 3063.2741 | 3063.2741 | 3063.2741 | 3063.2741 | 3063.2741 | 3063.2741 | 3063.2741 | 3063.2741 | 3063.2741 | 3063.2741 | 3063.2741 | 3063.2741 | 3063.2741 | 3063.2741 | 3063.2741 |  |  | 1282.5306 | 1932.5312 | 2032.8683 | 2096.3116 | 2236.1967 | 2567.0047 | 2747.3247 | 3091.4025 | 4137.9307 | 3274.4602 | 3105.3472 | 3332.9054 | 3830.934 | 3493.3099 | 3493.3099 | 3493.3099 | 3493.3099 | 3493.3099 | 3493.3099 | 3493.3099 | 3493.3099 | 3493.3099 | 3493.3099 | 3493.3099 | 3493.3099 | 3493.3099 | 3493.3099 | 3493.3099 | 3493.3099
80% |  | 628.4185 | 1600.7316 | 1766.1149 | 1894.7582 | 2117.0105 | 2623.2647 | 2961.7475 | 3390.9772 | 3613.543 | 3809.0501 | 3447.0242 | 3870.2692 | 4535.9328 | 4029.946 | 4029.946 | 4029.946 | 4029.946 | 4029.946 | 4029.946 | 4029.946 | 4029.946 | 4029.946 | 4029.946 | 4029.946 | 4029.946 | 4029.946 | 4029.946 | 4029.946 | 4029.946 |  |  | 1262.1427 | 2272.4362 | 2428.3899 | 2526.9996 | 2744.4225 | 3258.5963 | 3538.867 | 4073.6659 | 5700.2809 | 4358.1918 | 4095.3401 | 4449.033 | 5223.1171 | 4698.349 | 4698.349 | 4698.349 | 4698.349 | 4698.349 | 4698.349 | 4698.349 | 4698.349 | 4698.349 | 4698.349 | 4698.349 | 4698.349 | 4698.349 | 4698.349 | 4698.349 | 4698.349
75% |  | 35.4297 | 855.1312 | 1037.5951 | 1179.5246 | 1424.7309 | 1983.2706 | 2356.7115 | 2830.2717 | 3075.8238 | 3291.5228 | 2892.1072 | 3359.0645 | 4093.4773 | 3535.2326 | 3535.2326 | 3535.2326 | 3535.2326 | 3535.2326 | 3535.2326 | 3535.2326 | 3535.2326 | 3535.2326 | 3535.2326 | 3535.2326 | 3535.2326 | 3535.2326 | 3535.2326 | 3535.2326 | 3535.2326 |  |  | 481.7498 | 1596.2089 | 1768.2692 | 1877.0633 | 2116.9414 | 2684.2186 | 2993.4354 | 3583.4678 | 5378.0782 | 3897.3793 | 3607.3806 | 3997.6025 | 4851.6333 | 4272.6677 | 4272.6677 | 4272.6677 | 4272.6677 | 4272.6677 | 4272.6677 | 4272.6677 | 4272.6677 | 4272.6677 | 4272.6677 | 4272.6677 | 4272.6677 | 4272.6677 | 4272.6677 | 4272.6677 | 4272.6677
70% |  |  | 65.8085 | 149.3801 | 236.763 | 432.2706 | 1017.18 | 1418.4215 | 1927.2354 | 2191.0675 | 2422.824 | 1993.6741 | 2495.3937 | 3284.4792 | 2684.6765 | 2684.6765 | 2684.6765 | 2684.6765 | 2684.6765 | 2684.6765 | 2684.6765 | 2684.6765 | 2684.6765 | 2684.6765 | 2684.6765 | 2684.6765 | 2684.6765 | 2684.6765 | 2684.6765 | 2684.6765 |  |  |  | 601.3916 | 786.1731 | 903.0662 | 1160.8019 | 1770.3095 | 2102.5457 | 2736.5026 | 4664.7111 | 3073.7829 | 2762.1954 | 3181.4671 | 4099.0755 | 3477.0093 | 3477.0093 | 3477.0093 | 3477.0093 | 3477.0093 | 3477.0093 | 3477.0093 | 3477.0093 | 3477.0093 | 3477.0093 | 3477.0093 | 3477.0093 | 3477.0093 | 3477.0093 | 3477.0093 | 3477.0093
65% | [6 empty] | 67.1746 | 263.316 | 684.8354 | 961.4279 | 1205.6548 | 753.4132 | 1282.1294 | 2113.6742 | 1481.5972 | 1481.5972 | 1481.5972 | 1481.5972 | 1481.5972 | 1481.5972 | 1481.5972 | 1481.5972 | 1481.5972 | 1481.5972 | 1481.5972 | 1481.5972 | 1481.5972 | 1481.5972 | 1481.5972 | 1481.5972 |  |  |  |  | 12.1974 | 34.5742 | 123.0009 | 535.0416 | 868.1429 | 1536.2119 | 3568.1739 | 1891.6407 | 1563.2873 | 2005.1192 | 2972.1025 | 2316.564 | 2316.564 | 2316.564 | 2316.564 | 2316.564 | 2316.564 | 2316.564 | 2316.564 | 2316.564 | 2316.564 | 2316.564 | 2316.564 | 2316.564 | 2316.564 | 2316.564 | 2316.564
60% | [9 empty] | 15.996 | 73.9877 | 0.0013268 | 100.6328 | 637.7145 | 188.7046 | 188.7046 | 188.7046 | 188.7046 | 188.7046 | 188.7046 | 188.7046 | 188.7046 | 188.7046 | 188.7046 | 188.7046 | 188.7046 | 188.7046 | 188.7046 | 188.7046 | 188.7046 | [8 empty] | 4.9606 | 217.4281 | 2207.292 | 451.391 | 232.3927 | 542.8433 | 1551.0908 | 834.0186 | 834.0186 | 834.0186 | 834.0186 | 834.0186 | 834.0186 | 834.0186 | 834.0186 | 834.0186 | 834.0186 | 834.0186 | 834.0186 | 834.0186 | 834.0186 | 834.0186 | 834.0186
55% | [40 empty] | 420.5237 |  |  |  | 95.5636
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 2267.9753 | 5084.2295 | 5678.6703 | 6163.4327 | 7045.478 | 9261.3822 | 10904.3389 | 13160.5637 | 14404.4901 | 15542.3873 | 13468.7106 | 15907.1825 | 20121.1305 | 16877.247 | 16877.247 | 16877.247 | 16877.247 | 16877.247 | 16877.247 | 16877.247 | 16877.247 | 16877.247 | 16877.247 | 16877.247 | 16877.247 | 16877.247 | 16877.247 | 16877.247 | 16877.247 | E @ R (MWh) | 0 | 3972.6958 | 7694.7094 | 8373.4293 | 8817.3048 | 9835.0869 | 12444.9189 | 13980.9735 | 17147.4619 | 28542.6368 | 18953.035 | 17282.1464 | 19546.2584 | 24925.8084 | 21214.5583 | 21214.5583 | 21214.5583 | 21214.5583 | 21214.5583 | 21214.5583 | 21214.5583 | 21214.5583 | 21214.5583 | 21214.5583 | 21214.5583 | 21214.5583 | 21214.5583 | 21214.5583 | 21214.5583 | 21214.5583
Option 7 Winter POE50 W E @ R (MWh) N 1 | 0 | 1587.5827 | 3558.9606 | 3975.0692 | 4314.4029 | 4931.8346 | 6482.9675 | 7633.0372 | 9212.3946 | 10083.1431 | 10879.6711 | 9428.0974 | 11135.0277 | 14084.7914 | 11814.0729 | 11814.0729 | 11814.0729 | 11814.0729 | 11814.0729 | 11814.0729 | 11814.0729 | 11814.0729 | 11814.0729 | 11814.0729 | 11814.0729 | 11814.0729 | 11814.0729 | 11814.0729 | 11814.0729 | 11814.0729 | Option 7 Winter POE10 W E @ R (MWh) N 1 | 0 | 1191.8087 | 2308.4128 | 2512.0288 | 2645.1914 | 2950.5261 | 3733.4757 | 4194.2921 | 5144.2386 | 8562.791 | 5685.9105 | 5184.6439 | 5863.8775 | 7477.7425 | 6364.3675 | 6364.3675 | 6364.3675 | 6364.3675 | 6364.3675 | 6364.3675 | 6364.3675 | 6364.3675 | 6364.3675 | 6364.3675 | 6364.3675 | 6364.3675 | 6364.3675 | 6364.3675 | 6364.3675 | 6364.3675
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 17.7632 | 43.0375 | 49.6507 | 49.2537 | 49.2817 | 49.9598 | 51.7502 | 52.9479 | 54.1209 | 55.493 | 56.7638 | 57.998 | 58.138 | 59.5788 | 58.4848 | 58.4848 | 58.4848 | 58.4848 | 58.4848 | 58.4848 | 58.4848 | 58.4848 | 58.4848 | 58.4848 | 58.4848 | 58.4848 | 58.4848 | 58.4848 | 58.4848 | 58.4848
98% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 8.4503 | 20.9604 | 24.2338 | 24.0373 | 24.0512 | 24.3868 | 25.273 | 25.8658 | 26.4464 | 27.1256 | 27.7546 | 28.3655 | 28.4348 | 29.1479 | 28.6065 | 28.6065 | 28.6065 | 28.6065 | 28.6065 | 28.6065 | 28.6065 | 28.6065 | 28.6065 | 28.6065 | 28.6065 | 28.6065 | 28.6065 | 28.6065 | 28.6065 | 28.6065
97% | 1.8466 | 8.0258 | 9.7077 | 9.6587 | 9.6569 | 9.8486 | 10.059 | 10.4908 | 10.8011 | 10.9695 | 11.1536 | 11.3221 | 11.6266 | 12.0045 | 11.9781 | 11.9781 | 11.9781 | 11.9781 | 11.9781 | 11.9781 | 11.9781 | 11.9781 | 11.9781 | 11.9781 | 11.9781 | 11.9781 | 11.9781 | 11.9781 | 11.9781 | 11.9781 |  | 16.0379 | 40.8042 | 47.2844 | 46.8955 | 46.9229 | 47.5873 | 49.3417 | 50.5154 | 51.6648 | 53.0093 | 54.2545 | 55.464 | 55.6012 | 57.013 | 55.941 | 55.941 | 55.941 | 55.941 | 55.941 | 55.941 | 55.941 | 55.941 | 55.941 | 55.941 | 55.941 | 55.941 | 55.941 | 55.941 | 55.941 | 55.941
95% | 7.7819 | 38.2025 | 46.4828 | 46.2417 | 46.2328 | 47.1765 | 48.212 | 50.3381 | 51.8658 | 52.6946 | 53.6008 | 54.4305 | 55.9296 | 57.7903 | 57.6602 | 57.6602 | 57.6602 | 57.6602 | 57.6602 | 57.6602 | 57.6602 | 57.6602 | 57.6602 | 57.6602 | 57.6602 | 57.6602 | 57.6602 | 57.6602 | 57.6602 | 57.6602 |  | 22.1159 | 58.6938 | 68.2646 | 67.6901 | 67.7307 | 68.712 | 71.3031 | 73.0364 | 74.7341 | 76.7198 | 78.559 | 80.3452 | 80.5479 | 82.6329 | 81.0498 | 81.0498 | 81.0498 | 81.0498 | 81.0498 | 81.0498 | 81.0498 | 81.0498 | 81.0498 | 81.0498 | 81.0498 | 81.0498 | 81.0498 | 81.0498 | 81.0498 | 81.0498
90% | 7.9129 | 60.6736 | 75.0348 | 74.6165 | 74.6011 | 76.2379 | 78.0339 | 81.7213 | 84.371 | 85.8084 | 87.3801 | 88.819 | 91.4191 | 94.6462 | 94.4206 | 94.4206 | 94.4206 | 94.4206 | 94.4206 | 94.4206 | 94.4206 | 94.4206 | 94.4206 | 94.4206 | 94.4206 | 94.4206 | 94.4206 | 94.4206 | 94.4206 | 94.4206 |  | 79.1417 | 237.7413 | 279.2396 | 276.7487 | 276.9246 | 281.1792 | 292.4144 | 299.93 | 307.291 | 315.901 | 323.8752 | 331.6203 | 332.499 | 341.5397 | 334.6752 | 334.6752 | 334.6752 | 334.6752 | 334.6752 | 334.6752 | 334.6752 | 334.6752 | 334.6752 | 334.6752 | 334.6752 | 334.6752 | 334.6752 | 334.6752 | 334.6752 | 334.6752
85% | 2.1831 | 147.3455 | 188.1003 | 186.9134 | 186.8697 | 191.5145 | 196.6114 | 207.0756 | 214.595 | 218.674 | 223.1344 | 227.2178 | 234.5963 | 243.7543 | 243.1142 | 243.1142 | 243.1142 | 243.1142 | 243.1142 | 243.1142 | 243.1142 | 243.1142 | 243.1142 | 243.1142 | 243.1142 | 243.1142 | 243.1142 | 243.1142 | 243.1142 | 243.1142 |  | 50.0275 | 200.0542 | 239.3094 | 236.9532 | 237.1195 | 241.1442 | 251.772 | 258.8814 | 265.8444 | 273.989 | 281.5323 | 288.8587 | 289.6899 | 298.2419 | 291.7484 | 291.7484 | 291.7484 | 291.7484 | 291.7484 | 291.7484 | 291.7484 | 291.7484 | 291.7484 | 291.7484 | 291.7484 | 291.7484 | 291.7484 | 291.7484 | 291.7484 | 291.7484
80% |  | 166.9191 | 223.8464 | 222.1885 | 222.1274 | 228.6154 | 235.7349 | 250.3515 | 260.8548 | 266.5525 | 272.783 | 278.4866 | 288.7932 | 301.5853 | 300.6912 | 300.6912 | 300.6912 | 300.6912 | 300.6912 | 300.6912 | 300.6912 | 300.6912 | 300.6912 | 300.6912 | 300.6912 | 300.6912 | 300.6912 | 300.6912 | 300.6912 | 300.6912 |  | 15.4914 | 120.2719 | 147.6883 | 146.0426 | 146.1588 | 148.9697 | 156.3923 | 161.3576 | 166.2207 | 171.909 | 177.1773 | 182.2941 | 182.8747 | 188.8475 | 184.3124 | 184.3124 | 184.3124 | 184.3124 | 184.3124 | 184.3124 | 184.3124 | 184.3124 | 184.3124 | 184.3124 | 184.3124 | 184.3124 | 184.3124 | 184.3124 | 184.3124 | 184.3124
75% |  | 320.647 | 469.0463 | 464.7244 | 464.5651 | 481.4781 | 500.0374 | 538.1403 | 565.5205 | 580.3733 | 596.615 | 611.4834 | 638.3507 | 671.6975 | 669.3666 | 669.3666 | 669.3666 | 669.3666 | 669.3666 | 669.3666 | 669.3666 | 669.3666 | 669.3666 | 669.3666 | 669.3666 | 669.3666 | 669.3666 | 669.3666 | 669.3666 | 669.3666 |  | 0.97657 | 175.4756 | 224.4096 | 221.4724 | 221.6798 | 226.6968 | 239.945 | 248.8073 | 257.4872 | 267.6399 | 277.043 | 286.1758 | 287.212 | 297.8726 | 289.7781 | 289.7781 | 289.7781 | 289.7781 | 289.7781 | 289.7781 | 289.7781 | 289.7781 | 289.7781 | 289.7781 | 289.7781 | 289.7781 | 289.7781 | 289.7781 | 289.7781 | 289.7781
70% |  | 328.9116 | 585.3005 | 577.8335 | 577.5583 | 606.7787 | 638.8436 | 704.6738 | 751.9784 | 777.6395 | 805.7002 | 831.3883 | 877.8068 | 935.42 | 931.3929 | 931.3929 | 931.3929 | 931.3929 | 931.3929 | 931.3929 | 931.3929 | 931.3929 | 931.3929 | 931.3929 | 931.3929 | 931.3929 | 931.3929 | 931.3929 | 931.3929 | 931.3929 |  |  | 238.4252 | 327.5698 | 322.219 | 322.5968 | 331.7364 | 355.8711 | 372.0158 | 387.8282 | 406.3238 | 423.4537 | 440.0913 | 441.9789 | 461.3997 | 446.6536 | 446.6536 | 446.6536 | 446.6536 | 446.6536 | 446.6536 | 446.6536 | 446.6536 | 446.6536 | 446.6536 | 446.6536 | 446.6536 | 446.6536 | 446.6536 | 446.6536 | 446.6536
65% |  | 199.3768 | 820.987 | 802.2336 | 801.5424 | 874.9301 | 955.4618 | 1120.7959 | 1239.6024 | 1304.0507 | 1374.5258 | 1439.0422 | 1555.6231 | 1700.32 | 1690.2059 | 1690.2059 | 1690.2059 | 1690.2059 | 1690.2059 | 1690.2059 | 1690.2059 | 1690.2059 | 1690.2059 | 1690.2059 | 1690.2059 | 1690.2059 | 1690.2059 | 1690.2059 | 1690.2059 | 1690.2059 |  |  | 182.6144 | 294.7721 | 288.04 | 288.5153 | 300.0144 | 330.3796 | 350.692 | 370.5866 | 393.8569 | 415.4089 | 436.3416 | 438.7165 | 463.1508 | 444.598 | 444.598 | 444.598 | 444.598 | 444.598 | 444.598 | 444.598 | 444.598 | 444.598 | 444.598 | 444.598 | 444.598 | 444.598 | 444.598 | 444.598 | 444.598
60% |  |  | 203.5024 | 187.5582 | 186.9825 | 252.8081 | 335.7847 | 540.3015 | 711.4984 | 805.7041 | 908.7192 | 1003.0243 | 1173.4335 | 1384.9404 | 1370.1564 | 1370.1564 | 1370.1564 | 1370.1564 | 1370.1564 | 1370.1564 | 1370.1564 | 1370.1564 | 1370.1564 | 1370.1564 | 1370.1564 | 1370.1564 | 1370.1564 | 1370.1564 | 1370.1564 | 1370.1564 |  |  | 77.0598 | 248.2313 | 237.6968 | 238.4405 | 256.4344 | 303.9503 | 335.7356 | 366.8668 | 403.2805 | 437.0055 | 469.7612 | 473.4775 | 511.7128 | 482.681 | 482.681 | 482.681 | 482.681 | 482.681 | 482.681 | 482.681 | 482.681 | 482.681 | 482.681 | 482.681 | 482.681 | 482.681 | 482.681 | 482.681 | 482.681
55% | [8 empty] | 3.8903 | 15.7556 | 37.6919 | 65.8304 | 135.7599 | 255.725 | 246.1724 | 246.1724 | 246.1724 | 246.1724 | 246.1724 | 246.1724 | 246.1724 | 246.1724 | 246.1724 | 246.1724 | 246.1724 | 246.1724 | 246.1724 | 246.1724 | 246.1724 | 246.1724 |  |  |  | 63.4905 | 53.6808 | 54.3475 | 71.6739 | 128.262 | 174.6238 | 226.4176 | 294.3956 | 359.2034 | 422.1487 | 429.2901 | 502.7651 | 446.976 | 446.976 | 446.976 | 446.976 | 446.976 | 446.976 | 446.976 | 446.976 | 446.976 | 446.976 | 446.976 | 446.976 | 446.976 | 446.976 | 446.976 | 446.976
50% | [40 empty] | 0.92441 | 14.9076 | 44.2124 | 48.4954 | 103.6497 | 59.9312 | 59.9312 | 59.9312 | 59.9312 | 59.9312 | 59.9312 | 59.9312 | 59.9312 | 59.9312 | 59.9312 | 59.9312 | 59.9312 | 59.9312 | 59.9312 | 59.9312 | 59.9312
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 19.7244 | 1270.1019 | 2622.0083 | 2571.9686 | 2570.1362 | 2769.3877 | 2998.7788 | 3503.8889 | 3894.9777 | 4118.2221 | 4371.3041 | 4611.0446 | 5063.3387 | 5657.8836 | 5615.1586 | 5615.1586 | 5615.1586 | 5615.1586 | 5615.1586 | 5615.1586 | 5615.1586 | 5615.1586 | 5615.1586 | 5615.1586 | 5615.1586 | 5615.1586 | 5615.1586 | 5615.1586 | 5615.1586 | 5615.1586 | E @ R (MWh) | 210.0044 | 1395.1384 | 2014.1441 | 1970.7302 | 1973.7695 | 2048.4946 | 2256.6548 | 2404.4088 | 2555.5088 | 2740.5678 | 2926.9386 | 3123.6769 | 3146.9559 | 3397.5525 | 3205.4359 | 3205.4359 | 3205.4359 | 3205.4359 | 3205.4359 | 3205.4359 | 3205.4359 | 3205.4359 | 3205.4359 | 3205.4359 | 3205.4359 | 3205.4359 | 3205.4359 | 3205.4359 | 3205.4359 | 3205.4359
Option 7 Summer POE50 W E @ R (MWh) N 1 | 13.8071 | 889.0713 | 1835.4058 | 1800.378 | 1799.0954 | 1938.5714 | 2099.1452 | 2452.7222 | 2726.4844 | 2882.7555 | 3059.9129 | 3227.7312 | 3544.3371 | 3960.5185 | 3930.611 | 3930.611 | 3930.611 | 3930.611 | 3930.611 | 3930.611 | 3930.611 | 3930.611 | 3930.611 | 3930.611 | 3930.611 | 3930.611 | 3930.611 | 3930.611 | 3930.611 | 3930.611 | Option 7 Summer POE10 W E @ R (MWh) N 1 | 63.0013 | 418.5415 | 604.2432 | 591.2191 | 592.1308 | 614.5484 | 676.9964 | 721.3226 | 766.6526 | 822.1703 | 878.0816 | 937.1031 | 944.0868 | 1019.2657 | 961.6308 | 961.6308 | 961.6308 | 961.6308 | 961.6308 | 961.6308 | 961.6308 | 961.6308 | 961.6308 | 961.6308 | 961.6308 | 961.6308 | 961.6308 | 961.6308 | 961.6308 | 961.6308
Option 8 -
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% |  | 19.3557 | 26.0414 | 27.1786 | 28.0631 | 29.5913 | 33.0724 | 35.3998 | 38.3512 | 39.8816 | 41.2259 | 38.7366 | 41.6468 | 46.224 | 42.7448 | 42.7448 | 42.7448 | 42.7448 | 42.7448 | 42.7448 | 42.7448 | 42.7448 | 42.7448 | 42.7448 | 42.7448 | 42.7448 | 42.7448 | 42.7448 | 42.7448 | 42.7448 |  |  | 23.7132 | 30.66 | 31.7324 | 32.4104 | 33.9055 | 37.4409 | 39.3681 | 43.0454 | 54.2301 | 45.0018 | 43.1944 | 45.6265 | 50.9491 | 47.3408 | 47.3408 | 47.3408 | 47.3408 | 47.3408 | 47.3408 | 47.3408 | 47.3408 | 47.3408 | 47.3408 | 47.3408 | 47.3408 | 47.3408 | 47.3408 | 47.3408 | 47.3408
98% |  | 22.1134 | 30.0556 | 31.4065 | 32.4573 | 34.2728 | 38.408 | 41.1729 | 44.679 | 46.497 | 48.0939 | 45.1368 | 48.594 | 54.0314 | 49.8983 | 49.8983 | 49.8983 | 49.8983 | 49.8983 | 49.8983 | 49.8983 | 49.8983 | 49.8983 | 49.8983 | 49.8983 | 49.8983 | 49.8983 | 49.8983 | 49.8983 | 49.8983 |  |  | 27.2899 | 35.5423 | 36.8162 | 37.6217 | 39.3977 | 43.5976 | 45.887 | 50.2554 | 63.5422 | 52.5795 | 50.4324 | 53.3215 | 59.6445 | 55.358 | 55.358 | 55.358 | 55.358 | 55.358 | 55.358 | 55.358 | 55.358 | 55.358 | 55.358 | 55.358 | 55.358 | 55.358 | 55.358 | 55.358 | 55.358
97% |  | 42.0001 | 57.7232 | 60.3976 | 62.4779 | 66.0719 | 74.2584 | 79.732 | 86.673 | 90.2721 | 93.4336 | 87.5793 | 94.4235 | 105.1879 | 97.0056 | 97.0056 | 97.0056 | 97.0056 | 97.0056 | 97.0056 | 97.0056 | 97.0056 | 97.0056 | 97.0056 | 97.0056 | 97.0056 | 97.0056 | 97.0056 | 97.0056 | 97.0056 |  |  | 52.248 | 68.5852 | 71.1071 | 72.7018 | 76.2177 | 84.5323 | 89.0645 | 97.7126 | 124.0163 | 102.3136 | 98.0631 | 103.7826 | 116.3002 | 107.8143 | 107.8143 | 107.8143 | 107.8143 | 107.8143 | 107.8143 | 107.8143 | 107.8143 | 107.8143 | 107.8143 | 107.8143 | 107.8143 | 107.8143 | 107.8143 | 107.8143 | 107.8143
95% |  | 115.9799 | 162.4236 | 170.3233 | 176.4681 | 187.0842 | 211.266 | 227.434 | 247.9367 | 258.5678 | 267.9064 | 250.6138 | 270.8306 | 302.6268 | 278.4578 | 278.4578 | 278.4578 | 278.4578 | 278.4578 | 278.4578 | 278.4578 | 278.4578 | 278.4578 | 278.4578 | 278.4578 | 278.4578 | 278.4578 | 278.4578 | 278.4578 | 278.4578 |  |  | 146.2505 | 194.5083 | 201.9576 | 206.6678 | 217.0533 | 241.6134 | 255.0008 | 280.5461 | 358.2432 | 294.1368 | 281.5814 | 298.4759 | 335.451 | 310.3848 | 310.3848 | 310.3848 | 310.3848 | 310.3848 | 310.3848 | 310.3848 | 310.3848 | 310.3848 | 310.3848 | 310.3848 | 310.3848 | 310.3848 | 310.3848 | 310.3848 | 310.3848
90% |  | 529.8714 | 785.9431 | 829.499 | 863.379 | 921.9121 | 1055.2409 | 1144.3849 | 1257.4283 | 1316.044 | 1367.5334 | 1272.189 | 1383.6562 | 1558.9677 | 1425.7093 | 1425.7093 | 1425.7093 | 1425.7093 | 1425.7093 | 1425.7093 | 1425.7093 | 1425.7093 | 1425.7093 | 1425.7093 | 1425.7093 | 1425.7093 | 1425.7093 | 1425.7093 | 1425.7093 | 1425.7093 |  |  | 696.7712 | 962.8455 | 1003.918 | 1029.8882 | 1087.1494 | 1222.564 | 1296.377 | 1437.2235 | 1865.6143 | 1512.1572 | 1442.9317 | 1536.0814 | 1739.9469 | 1601.7422 | 1601.7422 | 1601.7422 | 1601.7422 | 1601.7422 | 1601.7422 | 1601.7422 | 1601.7422 | 1601.7422 | 1601.7422 | 1601.7422 | 1601.7422 | 1601.7422 | 1601.7422 | 1601.7422 | 1601.7422
85% |  | 874.8065 | 1500.3713 | 1606.7752 | 1689.5415 | 1832.5337 | 2158.2465 | 2376.0188 | 2652.1757 | 2795.3696 | 2921.1546 | 2688.2351 | 2960.5416 | 3388.8149 | 3063.2741 | 3063.2741 | 3063.2741 | 3063.2741 | 3063.2741 | 3063.2741 | 3063.2741 | 3063.2741 | 3063.2741 | 3063.2741 | 3063.2741 | 3063.2741 | 3063.2741 | 3063.2741 | 3063.2741 | 3063.2741 |  |  | 1282.5306 | 1932.5312 | 2032.8683 | 2096.3116 | 2236.1967 | 2567.0047 | 2747.3247 | 3091.4025 | 4137.9307 | 3274.4602 | 3105.3472 | 3332.9054 | 3830.934 | 3493.3099 | 3493.3099 | 3493.3099 | 3493.3099 | 3493.3099 | 3493.3099 | 3493.3099 | 3493.3099 | 3493.3099 | 3493.3099 | 3493.3099 | 3493.3099 | 3493.3099 | 3493.3099 | 3493.3099 | 3493.3099
80% |  | 628.4185 | 1600.7316 | 1766.1149 | 1894.7582 | 2117.0105 | 2623.2647 | 2961.7475 | 3390.9772 | 3613.543 | 3809.0501 | 3447.0242 | 3870.2692 | 4535.9328 | 4029.946 | 4029.946 | 4029.946 | 4029.946 | 4029.946 | 4029.946 | 4029.946 | 4029.946 | 4029.946 | 4029.946 | 4029.946 | 4029.946 | 4029.946 | 4029.946 | 4029.946 | 4029.946 |  |  | 1262.1427 | 2272.4362 | 2428.3899 | 2526.9996 | 2744.4225 | 3258.5963 | 3538.867 | 4073.6659 | 5700.2809 | 4358.1918 | 4095.3401 | 4449.033 | 5223.1171 | 4698.349 | 4698.349 | 4698.349 | 4698.349 | 4698.349 | 4698.349 | 4698.349 | 4698.349 | 4698.349 | 4698.349 | 4698.349 | 4698.349 | 4698.349 | 4698.349 | 4698.349 | 4698.349
75% |  | 35.4297 | 855.1312 | 1037.5951 | 1179.5246 | 1424.7309 | 1983.2706 | 2356.7115 | 2830.2717 | 3075.8238 | 3291.5228 | 2892.1072 | 3359.0645 | 4093.4773 | 3535.2326 | 3535.2326 | 3535.2326 | 3535.2326 | 3535.2326 | 3535.2326 | 3535.2326 | 3535.2326 | 3535.2326 | 3535.2326 | 3535.2326 | 3535.2326 | 3535.2326 | 3535.2326 | 3535.2326 | 3535.2326 |  |  | 481.7498 | 1596.2089 | 1768.2692 | 1877.0633 | 2116.9414 | 2684.2186 | 2993.4354 | 3583.4678 | 5378.0782 | 3897.3793 | 3607.3806 | 3997.6025 | 4851.6333 | 4272.6677 | 4272.6677 | 4272.6677 | 4272.6677 | 4272.6677 | 4272.6677 | 4272.6677 | 4272.6677 | 4272.6677 | 4272.6677 | 4272.6677 | 4272.6677 | 4272.6677 | 4272.6677 | 4272.6677 | 4272.6677
70% |  |  | 65.8085 | 149.3801 | 236.763 | 432.2706 | 1017.18 | 1418.4215 | 1927.2354 | 2191.0675 | 2422.824 | 1993.6741 | 2495.3937 | 3284.4792 | 2684.6765 | 2684.6765 | 2684.6765 | 2684.6765 | 2684.6765 | 2684.6765 | 2684.6765 | 2684.6765 | 2684.6765 | 2684.6765 | 2684.6765 | 2684.6765 | 2684.6765 | 2684.6765 | 2684.6765 | 2684.6765 |  |  |  | 601.3916 | 786.1731 | 903.0662 | 1160.8019 | 1770.3095 | 2102.5457 | 2736.5026 | 4664.7111 | 3073.7829 | 2762.1954 | 3181.4671 | 4099.0755 | 3477.0093 | 3477.0093 | 3477.0093 | 3477.0093 | 3477.0093 | 3477.0093 | 3477.0093 | 3477.0093 | 3477.0093 | 3477.0093 | 3477.0093 | 3477.0093 | 3477.0093 | 3477.0093 | 3477.0093 | 3477.0093
65% | [6 empty] | 67.1746 | 263.316 | 684.8354 | 961.4279 | 1205.6548 | 753.4132 | 1282.1294 | 2113.6742 | 1481.5972 | 1481.5972 | 1481.5972 | 1481.5972 | 1481.5972 | 1481.5972 | 1481.5972 | 1481.5972 | 1481.5972 | 1481.5972 | 1481.5972 | 1481.5972 | 1481.5972 | 1481.5972 | 1481.5972 | 1481.5972 |  |  |  |  | 12.1974 | 34.5742 | 123.0009 | 535.0416 | 868.1429 | 1536.2119 | 3568.1739 | 1891.6407 | 1563.2873 | 2005.1192 | 2972.1025 | 2316.564 | 2316.564 | 2316.564 | 2316.564 | 2316.564 | 2316.564 | 2316.564 | 2316.564 | 2316.564 | 2316.564 | 2316.564 | 2316.564 | 2316.564 | 2316.564 | 2316.564 | 2316.564
60% | [9 empty] | 15.996 | 73.9877 | 0.0013268 | 100.6328 | 637.7145 | 188.7046 | 188.7046 | 188.7046 | 188.7046 | 188.7046 | 188.7046 | 188.7046 | 188.7046 | 188.7046 | 188.7046 | 188.7046 | 188.7046 | 188.7046 | 188.7046 | 188.7046 | 188.7046 | [8 empty] | 4.9606 | 217.4281 | 2207.292 | 451.391 | 232.3927 | 542.8433 | 1551.0908 | 834.0186 | 834.0186 | 834.0186 | 834.0186 | 834.0186 | 834.0186 | 834.0186 | 834.0186 | 834.0186 | 834.0186 | 834.0186 | 834.0186 | 834.0186 | 834.0186 | 834.0186 | 834.0186
55% | [40 empty] | 420.5237 |  |  |  | 95.5636
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 2267.9753 | 5084.2295 | 5678.6703 | 6163.4327 | 7045.478 | 9261.3822 | 10904.3389 | 13160.5637 | 14404.4901 | 15542.3873 | 13468.7106 | 15907.1825 | 20121.1305 | 16877.247 | 16877.247 | 16877.247 | 16877.247 | 16877.247 | 16877.247 | 16877.247 | 16877.247 | 16877.247 | 16877.247 | 16877.247 | 16877.247 | 16877.247 | 16877.247 | 16877.247 | 16877.247 | E @ R (MWh) | 0 | 3972.6958 | 7694.7094 | 8373.4293 | 8817.3048 | 9835.0869 | 12444.9189 | 13980.9735 | 17147.4619 | 28542.6368 | 18953.035 | 17282.1464 | 19546.2584 | 24925.8084 | 21214.5583 | 21214.5583 | 21214.5583 | 21214.5583 | 21214.5583 | 21214.5583 | 21214.5583 | 21214.5583 | 21214.5583 | 21214.5583 | 21214.5583 | 21214.5583 | 21214.5583 | 21214.5583 | 21214.5583 | 21214.5583
Option 8 Winter POE50 W E @ R (MWh) N 1 | 0 | 1587.5827 | 3558.9606 | 3975.0692 | 4314.4029 | 4931.8346 | 6482.9675 | 7633.0372 | 9212.3946 | 10083.1431 | 10879.6711 | 9428.0974 | 11135.0277 | 14084.7914 | 11814.0729 | 11814.0729 | 11814.0729 | 11814.0729 | 11814.0729 | 11814.0729 | 11814.0729 | 11814.0729 | 11814.0729 | 11814.0729 | 11814.0729 | 11814.0729 | 11814.0729 | 11814.0729 | 11814.0729 | 11814.0729 | Option 8 Winter POE10 W E @ R (MWh) N 1 | 0 | 1191.8087 | 2308.4128 | 2512.0288 | 2645.1914 | 2950.5261 | 3733.4757 | 4194.2921 | 5144.2386 | 8562.791 | 5685.9105 | 5184.6439 | 5863.8775 | 7477.7425 | 6364.3675 | 6364.3675 | 6364.3675 | 6364.3675 | 6364.3675 | 6364.3675 | 6364.3675 | 6364.3675 | 6364.3675 | 6364.3675 | 6364.3675 | 6364.3675 | 6364.3675 | 6364.3675 | 6364.3675 | 6364.3675
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 17.7632 | 43.0375 | 49.6507 | 49.2537 | 49.2817 | 49.9598 | 51.7502 | 52.9479 | 54.1209 | 55.493 | 56.7638 | 57.998 | 58.138 | 59.5788 | 58.4848 | 58.4848 | 58.4848 | 58.4848 | 58.4848 | 58.4848 | 58.4848 | 58.4848 | 58.4848 | 58.4848 | 58.4848 | 58.4848 | 58.4848 | 58.4848 | 58.4848 | 58.4848
98% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 8.4503 | 20.9604 | 24.2338 | 24.0373 | 24.0512 | 24.3868 | 25.273 | 25.8658 | 26.4464 | 27.1256 | 27.7546 | 28.3655 | 28.4348 | 29.1479 | 28.6065 | 28.6065 | 28.6065 | 28.6065 | 28.6065 | 28.6065 | 28.6065 | 28.6065 | 28.6065 | 28.6065 | 28.6065 | 28.6065 | 28.6065 | 28.6065 | 28.6065 | 28.6065
97% | 1.8466 | 8.0258 | 9.7077 | 9.6587 | 9.6569 | 9.8486 | 10.059 | 10.4908 | 10.8011 | 10.9695 | 11.1536 | 11.3221 | 11.6266 | 12.0045 | 11.9781 | 11.9781 | 11.9781 | 11.9781 | 11.9781 | 11.9781 | 11.9781 | 11.9781 | 11.9781 | 11.9781 | 11.9781 | 11.9781 | 11.9781 | 11.9781 | 11.9781 | 11.9781 |  | 16.0379 | 40.8042 | 47.2844 | 46.8955 | 46.9229 | 47.5873 | 49.3417 | 50.5154 | 51.6648 | 53.0093 | 54.2545 | 55.464 | 55.6012 | 57.013 | 55.941 | 55.941 | 55.941 | 55.941 | 55.941 | 55.941 | 55.941 | 55.941 | 55.941 | 55.941 | 55.941 | 55.941 | 55.941 | 55.941 | 55.941 | 55.941
95% | 7.7819 | 38.2025 | 46.4828 | 46.2417 | 46.2328 | 47.1765 | 48.212 | 50.3381 | 51.8658 | 52.6946 | 53.6008 | 54.4305 | 55.9296 | 57.7903 | 57.6602 | 57.6602 | 57.6602 | 57.6602 | 57.6602 | 57.6602 | 57.6602 | 57.6602 | 57.6602 | 57.6602 | 57.6602 | 57.6602 | 57.6602 | 57.6602 | 57.6602 | 57.6602 |  | 22.1159 | 58.6938 | 68.2646 | 67.6901 | 67.7307 | 68.712 | 71.3031 | 73.0364 | 74.7341 | 76.7198 | 78.559 | 80.3452 | 80.5479 | 82.6329 | 81.0498 | 81.0498 | 81.0498 | 81.0498 | 81.0498 | 81.0498 | 81.0498 | 81.0498 | 81.0498 | 81.0498 | 81.0498 | 81.0498 | 81.0498 | 81.0498 | 81.0498 | 81.0498
90% | 7.9129 | 60.6736 | 75.0348 | 74.6165 | 74.6011 | 76.2379 | 78.0339 | 81.7213 | 84.371 | 85.8084 | 87.3801 | 88.819 | 91.4191 | 94.6462 | 94.4206 | 94.4206 | 94.4206 | 94.4206 | 94.4206 | 94.4206 | 94.4206 | 94.4206 | 94.4206 | 94.4206 | 94.4206 | 94.4206 | 94.4206 | 94.4206 | 94.4206 | 94.4206 |  | 79.1417 | 237.7413 | 279.2396 | 276.7487 | 276.9246 | 281.1792 | 292.4144 | 299.93 | 307.291 | 315.901 | 323.8752 | 331.6203 | 332.499 | 341.5397 | 334.6752 | 334.6752 | 334.6752 | 334.6752 | 334.6752 | 334.6752 | 334.6752 | 334.6752 | 334.6752 | 334.6752 | 334.6752 | 334.6752 | 334.6752 | 334.6752 | 334.6752 | 334.6752
85% | 2.1831 | 147.3455 | 188.1003 | 186.9134 | 186.8697 | 191.5145 | 196.6114 | 207.0756 | 214.595 | 218.674 | 223.1344 | 227.2178 | 234.5963 | 243.7543 | 243.1142 | 243.1142 | 243.1142 | 243.1142 | 243.1142 | 243.1142 | 243.1142 | 243.1142 | 243.1142 | 243.1142 | 243.1142 | 243.1142 | 243.1142 | 243.1142 | 243.1142 | 243.1142 |  | 50.0275 | 200.0542 | 239.3094 | 236.9532 | 237.1195 | 241.1442 | 251.772 | 258.8814 | 265.8444 | 273.989 | 281.5323 | 288.8587 | 289.6899 | 298.2419 | 291.7484 | 291.7484 | 291.7484 | 291.7484 | 291.7484 | 291.7484 | 291.7484 | 291.7484 | 291.7484 | 291.7484 | 291.7484 | 291.7484 | 291.7484 | 291.7484 | 291.7484 | 291.7484
80% |  | 166.9191 | 223.8464 | 222.1885 | 222.1274 | 228.6154 | 235.7349 | 250.3515 | 260.8548 | 266.5525 | 272.783 | 278.4866 | 288.7932 | 301.5853 | 300.6912 | 300.6912 | 300.6912 | 300.6912 | 300.6912 | 300.6912 | 300.6912 | 300.6912 | 300.6912 | 300.6912 | 300.6912 | 300.6912 | 300.6912 | 300.6912 | 300.6912 | 300.6912 |  | 15.4914 | 120.2719 | 147.6883 | 146.0426 | 146.1588 | 148.9697 | 156.3923 | 161.3576 | 166.2207 | 171.909 | 177.1773 | 182.2941 | 182.8747 | 188.8475 | 184.3124 | 184.3124 | 184.3124 | 184.3124 | 184.3124 | 184.3124 | 184.3124 | 184.3124 | 184.3124 | 184.3124 | 184.3124 | 184.3124 | 184.3124 | 184.3124 | 184.3124 | 184.3124
75% |  | 320.647 | 469.0463 | 464.7244 | 464.5651 | 481.4781 | 500.0374 | 538.1403 | 565.5205 | 580.3733 | 596.615 | 611.4834 | 638.3507 | 671.6975 | 669.3666 | 669.3666 | 669.3666 | 669.3666 | 669.3666 | 669.3666 | 669.3666 | 669.3666 | 669.3666 | 669.3666 | 669.3666 | 669.3666 | 669.3666 | 669.3666 | 669.3666 | 669.3666 |  | 0.97657 | 175.4756 | 224.4096 | 221.4724 | 221.6798 | 226.6968 | 239.945 | 248.8073 | 257.4872 | 267.6399 | 277.043 | 286.1758 | 287.212 | 297.8726 | 289.7781 | 289.7781 | 289.7781 | 289.7781 | 289.7781 | 289.7781 | 289.7781 | 289.7781 | 289.7781 | 289.7781 | 289.7781 | 289.7781 | 289.7781 | 289.7781 | 289.7781 | 289.7781
70% |  | 328.9116 | 585.3005 | 577.8335 | 577.5583 | 606.7787 | 638.8436 | 704.6738 | 751.9784 | 777.6395 | 805.7002 | 831.3883 | 877.8068 | 935.42 | 931.3929 | 931.3929 | 931.3929 | 931.3929 | 931.3929 | 931.3929 | 931.3929 | 931.3929 | 931.3929 | 931.3929 | 931.3929 | 931.3929 | 931.3929 | 931.3929 | 931.3929 | 931.3929 |  |  | 238.4252 | 327.5698 | 322.219 | 322.5968 | 331.7364 | 355.8711 | 372.0158 | 387.8282 | 406.3238 | 423.4537 | 440.0913 | 441.9789 | 461.3997 | 446.6536 | 446.6536 | 446.6536 | 446.6536 | 446.6536 | 446.6536 | 446.6536 | 446.6536 | 446.6536 | 446.6536 | 446.6536 | 446.6536 | 446.6536 | 446.6536 | 446.6536 | 446.6536
65% |  | 199.3768 | 820.987 | 802.2336 | 801.5424 | 874.9301 | 955.4618 | 1120.7959 | 1239.6024 | 1304.0507 | 1374.5258 | 1439.0422 | 1555.6231 | 1700.32 | 1690.2059 | 1690.2059 | 1690.2059 | 1690.2059 | 1690.2059 | 1690.2059 | 1690.2059 | 1690.2059 | 1690.2059 | 1690.2059 | 1690.2059 | 1690.2059 | 1690.2059 | 1690.2059 | 1690.2059 | 1690.2059 |  |  | 182.6144 | 294.7721 | 288.04 | 288.5153 | 300.0144 | 330.3796 | 350.692 | 370.5866 | 393.8569 | 415.4089 | 436.3416 | 438.7165 | 463.1508 | 444.598 | 444.598 | 444.598 | 444.598 | 444.598 | 444.598 | 444.598 | 444.598 | 444.598 | 444.598 | 444.598 | 444.598 | 444.598 | 444.598 | 444.598 | 444.598
60% |  |  | 203.5024 | 187.5582 | 186.9825 | 252.8081 | 335.7847 | 540.3015 | 711.4984 | 805.7041 | 908.7192 | 1003.0243 | 1173.4335 | 1384.9404 | 1370.1564 | 1370.1564 | 1370.1564 | 1370.1564 | 1370.1564 | 1370.1564 | 1370.1564 | 1370.1564 | 1370.1564 | 1370.1564 | 1370.1564 | 1370.1564 | 1370.1564 | 1370.1564 | 1370.1564 | 1370.1564 |  |  | 77.0598 | 248.2313 | 237.6968 | 238.4405 | 256.4344 | 303.9503 | 335.7356 | 366.8668 | 403.2805 | 437.0055 | 469.7612 | 473.4775 | 511.7128 | 482.681 | 482.681 | 482.681 | 482.681 | 482.681 | 482.681 | 482.681 | 482.681 | 482.681 | 482.681 | 482.681 | 482.681 | 482.681 | 482.681 | 482.681 | 482.681
55% | [8 empty] | 3.8903 | 15.7556 | 37.6919 | 65.8304 | 135.7599 | 255.725 | 246.1724 | 246.1724 | 246.1724 | 246.1724 | 246.1724 | 246.1724 | 246.1724 | 246.1724 | 246.1724 | 246.1724 | 246.1724 | 246.1724 | 246.1724 | 246.1724 | 246.1724 | 246.1724 |  |  |  | 63.4905 | 53.6808 | 54.3475 | 71.6739 | 128.262 | 174.6238 | 226.4176 | 294.3956 | 359.2034 | 422.1487 | 429.2901 | 502.7651 | 446.976 | 446.976 | 446.976 | 446.976 | 446.976 | 446.976 | 446.976 | 446.976 | 446.976 | 446.976 | 446.976 | 446.976 | 446.976 | 446.976 | 446.976 | 446.976
50% | [40 empty] | 0.92441 | 14.9076 | 44.2124 | 48.4954 | 103.6497 | 59.9312 | 59.9312 | 59.9312 | 59.9312 | 59.9312 | 59.9312 | 59.9312 | 59.9312 | 59.9312 | 59.9312 | 59.9312 | 59.9312 | 59.9312 | 59.9312 | 59.9312 | 59.9312
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 19.7244 | 1270.1019 | 2622.0083 | 2571.9686 | 2570.1362 | 2769.3877 | 2998.7788 | 3503.8889 | 3894.9777 | 4118.2221 | 4371.3041 | 4611.0446 | 5063.3387 | 5657.8836 | 5615.1586 | 5615.1586 | 5615.1586 | 5615.1586 | 5615.1586 | 5615.1586 | 5615.1586 | 5615.1586 | 5615.1586 | 5615.1586 | 5615.1586 | 5615.1586 | 5615.1586 | 5615.1586 | 5615.1586 | 5615.1586 | E @ R (MWh) | 210.0044 | 1395.1384 | 2014.1441 | 1970.7302 | 1973.7695 | 2048.4946 | 2256.6548 | 2404.4088 | 2555.5088 | 2740.5678 | 2926.9386 | 3123.6769 | 3146.9559 | 3397.5525 | 3205.4359 | 3205.4359 | 3205.4359 | 3205.4359 | 3205.4359 | 3205.4359 | 3205.4359 | 3205.4359 | 3205.4359 | 3205.4359 | 3205.4359 | 3205.4359 | 3205.4359 | 3205.4359 | 3205.4359 | 3205.4359
Option 8 Summer POE50 W E @ R (MWh) N 1 | 13.8071 | 889.0713 | 1835.4058 | 1800.378 | 1799.0954 | 1938.5714 | 2099.1452 | 2452.7222 | 2726.4844 | 2882.7555 | 3059.9129 | 3227.7312 | 3544.3371 | 3960.5185 | 3930.611 | 3930.611 | 3930.611 | 3930.611 | 3930.611 | 3930.611 | 3930.611 | 3930.611 | 3930.611 | 3930.611 | 3930.611 | 3930.611 | 3930.611 | 3930.611 | 3930.611 | 3930.611 | Option 8 Summer POE10 W E @ R (MWh) N 1 | 63.0013 | 418.5415 | 604.2432 | 591.2191 | 592.1308 | 614.5484 | 676.9964 | 721.3226 | 766.6526 | 822.1703 | 878.0816 | 937.1031 | 944.0868 | 1019.2657 | 961.6308 | 961.6308 | 961.6308 | 961.6308 | 961.6308 | 961.6308 | 961.6308 | 961.6308 | 961.6308 | 961.6308 | 961.6308 | 961.6308 | 961.6308 | 961.6308 | 961.6308 | 961.6308

## E@R N-2
Option 1 - Do Nothing / Base Case
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | 66.5813 | 92.3179 | 99.0036 | 100.1408 | 101.0254 | 102.5536 | 106.0346 | 108.362 | 111.3134 | 112.8438 | 114.1881 | 111.6988 | 114.6091 | 119.1862 | 115.707 | 115.707 | 115.707 | 115.707 | 115.707 | 115.707 | 115.707 | 115.707 | 115.707 | 115.707 | 115.707 | 115.707 | 115.707 | 115.707 | 115.707 | 115.707 |  | 71.2634 | 96.6755 | 103.6223 | 104.6946 | 105.3727 | 106.8677 | 110.4032 | 112.3303 | 116.0076 | 127.1923 | 117.9641 | 116.1567 | 118.5887 | 123.9113 | 120.303 | 120.303 | 120.303 | 120.303 | 120.303 | 120.303 | 120.303 | 120.303 | 120.303 | 120.303 | 120.303 | 120.303 | 120.303 | 120.303 | 120.303 | 120.303
98% | 79.0946 | 109.6681 | 117.6103 | 118.9612 | 120.012 | 121.8275 | 125.9627 | 128.7276 | 132.2337 | 134.0516 | 135.6486 | 132.6915 | 136.1487 | 141.586 | 137.453 | 137.453 | 137.453 | 137.453 | 137.453 | 137.453 | 137.453 | 137.453 | 137.453 | 137.453 | 137.453 | 137.453 | 137.453 | 137.453 | 137.453 | 137.453 |  | 84.6567 | 114.8446 | 123.097 | 124.3709 | 125.1764 | 126.9524 | 131.1523 | 133.4417 | 137.8101 | 151.0968 | 140.1342 | 137.9871 | 140.8762 | 147.1992 | 142.9127 | 142.9127 | 142.9127 | 142.9127 | 142.9127 | 142.9127 | 142.9127 | 142.9127 | 142.9127 | 142.9127 | 142.9127 | 142.9127 | 142.9127 | 142.9127 | 142.9127 | 142.9127
97% | 156.5832 | 217.1095 | 232.8326 | 235.507 | 237.5873 | 241.1813 | 249.3678 | 254.8414 | 261.7824 | 265.3814 | 268.543 | 262.6887 | 269.5329 | 280.2972 | 272.115 | 272.115 | 272.115 | 272.115 | 272.115 | 272.115 | 272.115 | 272.115 | 272.115 | 272.115 | 272.115 | 272.115 | 272.115 | 272.115 | 272.115 | 272.115 |  | 167.5944 | 227.3573 | 243.6946 | 246.2165 | 247.8111 | 251.327 | 259.6417 | 264.1739 | 272.822 | 299.1257 | 277.423 | 273.1725 | 278.892 | 291.4096 | 282.9237 | 282.9237 | 282.9237 | 282.9237 | 282.9237 | 282.9237 | 282.9237 | 282.9237 | 282.9237 | 282.9237 | 282.9237 | 282.9237 | 282.9237 | 282.9237 | 282.9237 | 282.9237
95% | 462.5227 | 641.3081 | 687.7517 | 695.6514 | 701.7962 | 712.4124 | 736.5942 | 752.7622 | 773.2648 | 783.8959 | 793.2346 | 775.942 | 796.1588 | 827.9549 | 803.7859 | 803.7859 | 803.7859 | 803.7859 | 803.7859 | 803.7859 | 803.7859 | 803.7859 | 803.7859 | 803.7859 | 803.7859 | 803.7859 | 803.7859 | 803.7859 | 803.7859 | 803.7859 |  | 495.0481 | 671.5786 | 719.8364 | 727.2857 | 731.996 | 742.3814 | 766.9415 | 780.329 | 805.8742 | 883.5714 | 819.4649 | 806.9095 | 823.8041 | 860.7791 | 835.7129 | 835.7129 | 835.7129 | 835.7129 | 835.7129 | 835.7129 | 835.7129 | 835.7129 | 835.7129 | 835.7129 | 835.7129 | 835.7129 | 835.7129 | 835.7129 | 835.7129 | 835.7129
90% | 2550.165 | 3535.9158 | 3791.9875 | 3835.5434 | 3869.4233 | 3927.9564 | 4061.2852 | 4150.4292 | 4263.4726 | 4322.0883 | 4373.5777 | 4278.2333 | 4389.7006 | 4565.012 | 4431.7536 | 4431.7536 | 4431.7536 | 4431.7536 | 4431.7536 | 4431.7536 | 4431.7536 | 4431.7536 | 4431.7536 | 4431.7536 | 4431.7536 | 4431.7536 | 4431.7536 | 4431.7536 | 4431.7536 | 4431.7536 |  | 2729.4971 | 3702.8155 | 3968.8899 | 4009.9623 | 4035.9325 | 4093.1938 | 4228.6083 | 4302.4214 | 4443.2678 | 4871.6587 | 4518.2015 | 4448.976 | 4542.1258 | 4745.9912 | 4607.7865 | 4607.7865 | 4607.7865 | 4607.7865 | 4607.7865 | 4607.7865 | 4607.7865 | 4607.7865 | 4607.7865 | 4607.7865 | 4607.7865 | 4607.7865 | 4607.7865 | 4607.7865 | 4607.7865 | 4607.7865
85% | 6229.8705 | 8637.9889 | 9263.5537 | 9369.9577 | 9452.724 | 9595.7162 | 9921.4289 | 10139.2013 | 10415.3582 | 10558.5521 | 10684.3371 | 10451.4176 | 10723.7241 | 11151.9973 | 10826.4566 | 10826.4566 | 10826.4566 | 10826.4566 | 10826.4566 | 10826.4566 | 10826.4566 | 10826.4566 | 10826.4566 | 10826.4566 | 10826.4566 | 10826.4566 | 10826.4566 | 10826.4566 | 10826.4566 | 10826.4566 |  | 6667.9659 | 9045.7131 | 9695.7136 | 9796.0508 | 9859.4941 | 9999.3792 | 10330.1872 | 10510.5072 | 10854.585 | 11901.1132 | 11037.6427 | 10868.5297 | 11096.0879 | 11594.1165 | 11256.4923 | 11256.4923 | 11256.4923 | 11256.4923 | 11256.4923 | 11256.4923 | 11256.4923 | 11256.4923 | 11256.4923 | 11256.4923 | 11256.4923 | 11256.4923 | 11256.4923 | 11256.4923 | 11256.4923 | 11256.4923
80% | 9683.0656 | 13425.9956 | 14398.3087 | 14563.692 | 14692.3353 | 14914.5876 | 15420.8418 | 15759.3246 | 16188.5543 | 16411.1201 | 16606.6272 | 16244.6013 | 16667.8463 | 17333.5099 | 16827.5231 | 16827.5231 | 16827.5231 | 16827.5231 | 16827.5231 | 16827.5231 | 16827.5231 | 16827.5231 | 16827.5231 | 16827.5231 | 16827.5231 | 16827.5231 | 16827.5231 | 16827.5231 | 16827.5231 | 16827.5231 |  | 10363.9958 | 14059.7198 | 15070.0133 | 15225.967 | 15324.5767 | 15541.9996 | 16056.1734 | 16336.4441 | 16871.243 | 18497.858 | 17155.7689 | 16892.9172 | 17246.6101 | 18020.6942 | 17495.9261 | 17495.9261 | 17495.9261 | 17495.9261 | 17495.9261 | 17495.9261 | 17495.9261 | 17495.9261 | 17495.9261 | 17495.9261 | 17495.9261 | 17495.9261 | 17495.9261 | 17495.9261 | 17495.9261 | 17495.9261
75% | 10683.1238 | 14812.6201 | 15885.3529 | 16067.8168 | 16209.7463 | 16454.9526 | 17013.4923 | 17386.9332 | 17860.4934 | 18106.0455 | 18321.7445 | 17922.3288 | 18389.2862 | 19123.699 | 18565.4543 | 18565.4543 | 18565.4543 | 18565.4543 | 18565.4543 | 18565.4543 | 18565.4543 | 18565.4543 | 18565.4543 | 18565.4543 | 18565.4543 | 18565.4543 | 18565.4543 | 18565.4543 | 18565.4543 | 18565.4543 |  | 11434.3798 | 15511.7948 | 16626.4305 | 16798.4909 | 16907.2849 | 17147.1631 | 17714.4402 | 18023.6571 | 18613.6895 | 20408.2999 | 18927.601 | 18637.6022 | 19027.8242 | 19881.855 | 19302.8894 | 19302.8894 | 19302.8894 | 19302.8894 | 19302.8894 | 19302.8894 | 19302.8894 | 19302.8894 | 19302.8894 | 19302.8894 | 19302.8894 | 19302.8894 | 19302.8894 | 19302.8894 | 19302.8894 | 19302.8894
70% | 11478.4193 | 15915.3323 | 17067.9236 | 17263.9709 | 17416.4662 | 17679.9267 | 18280.0463 | 18681.2877 | 19190.1017 | 19453.9337 | 19685.6902 | 19256.5404 | 19758.26 | 20547.3454 | 19947.5428 | 19947.5428 | 19947.5428 | 19947.5428 | 19947.5428 | 19947.5428 | 19947.5428 | 19947.5428 | 19947.5428 | 19947.5428 | 19947.5428 | 19947.5428 | 19947.5428 | 19947.5428 | 19947.5428 | 19947.5428 |  | 12285.6019 | 16666.5563 | 17864.1701 | 18049.0394 | 18165.9325 | 18423.6682 | 19033.1757 | 19365.4119 | 19999.3688 | 21927.5773 | 20336.6492 | 20025.0617 | 20444.3333 | 21361.9417 | 20739.8755 | 20739.8755 | 20739.8755 | 20739.8755 | 20739.8755 | 20739.8755 | 20739.8755 | 20739.8755 | 20739.8755 | 20739.8755 | 20739.8755 | 20739.8755 | 20739.8755 | 20739.8755 | 20739.8755 | 20739.8755
65% | 12096.053 | 16771.7086 | 17986.3189 | 18192.9151 | 18353.6159 | 18631.2528 | 19263.6638 | 19686.4953 | 20222.6877 | 20500.7161 | 20744.943 | 20292.7014 | 20821.4176 | 21652.9624 | 21020.8854 | 21020.8854 | 21020.8854 | 21020.8854 | 21020.8854 | 21020.8854 | 21020.8854 | 21020.8854 | 21020.8854 | 21020.8854 | 21020.8854 | 21020.8854 | 21020.8854 | 21020.8854 | 21020.8854 | 21020.8854 |  | 12946.6687 | 17563.3547 | 18825.4101 | 19020.2268 | 19143.4097 | 19415.0137 | 20057.3178 | 20407.431 | 21075.5001 | 23107.4621 | 21430.9289 | 21102.5754 | 21544.4074 | 22511.3907 | 21855.8521 | 21855.8521 | 21855.8521 | 21855.8521 | 21855.8521 | 21855.8521 | 21855.8521 | 21855.8521 | 21855.8521 | 21855.8521 | 21855.8521 | 21855.8521 | 21855.8521 | 21855.8521 | 21855.8521 | 21855.8521
60% | 13316.2645 | 18463.5854 | 19800.7217 | 20028.1587 | 20205.0705 | 20510.7145 | 21206.9211 | 21672.4066 | 22262.6883 | 22568.7633 | 22837.627 | 22339.7647 | 22921.8162 | 23837.2445 | 23141.4056 | 23141.4056 | 23141.4056 | 23141.4056 | 23141.4056 | 23141.4056 | 23141.4056 | 23141.4056 | 23141.4056 | 23141.4056 | 23141.4056 | 23141.4056 | 23141.4056 | 23141.4056 | 23141.4056 | 23141.4056 |  | 14252.6876 | 19335.0902 | 20724.4577 | 20938.927 | 21074.5362 | 21373.5387 | 22080.6365 | 22466.068 | 23201.5297 | 25438.4696 | 23592.813 | 23231.3363 | 23717.7389 | 24782.2684 | 24060.6012 | 24060.6012 | 24060.6012 | 24060.6012 | 24060.6012 | 24060.6012 | 24060.6012 | 24060.6012 | 24060.6012 | 24060.6012 | 24060.6012 | 24060.6012 | 24060.6012 | 24060.6012 | 24060.6012 | 24060.6012
55% | 14813.5078 | 20539.579 | 22027.0592 | 22280.0685 | 22476.8718 | 22816.8815 | 23591.3677 | 24109.191 | 24765.8423 | 25106.3315 | 25405.4256 | 24851.585 | 25499.0807 | 26517.4372 | 25743.3602 | 25743.3602 | 25743.3602 | 25743.3602 | 25743.3602 | 25743.3602 | 25743.3602 | 25743.3602 | 25743.3602 | 25743.3602 | 25743.3602 | 25743.3602 | 25743.3602 | 25743.3602 | 25743.3602 | 25743.3602 |  | 15855.2197 | 21509.0734 | 23054.6574 | 23293.241 | 23444.0977 | 23776.7193 | 24563.3211 | 24992.0894 | 25810.2444 | 28298.6996 | 26245.5225 | 25843.4024 | 26384.4947 | 27568.7169 | 26765.9075 | 26765.9075 | 26765.9075 | 26765.9075 | 26765.9075 | 26765.9075 | 26765.9075 | 26765.9075 | 26765.9075 | 26765.9075 | 26765.9075 | 26765.9075 | 26765.9075 | 26765.9075 | 26765.9075 | 26765.9075
50% | 15014.9247 | 20818.8523 | 22326.5575 | 22583.007 | 22782.4862 | 23127.1189 | 23912.1357 | 24436.9997 | 25102.5795 | 25447.6982 | 25750.859 | 25189.488 | 25845.7876 | 26877.9905 | 26093.3885 | 26093.3885 | 26093.3885 | 26093.3885 | 26093.3885 | 26093.3885 | 26093.3885 | 26093.3885 | 26093.3885 | 26093.3885 | 26093.3885 | 26093.3885 | 26093.3885 | 26093.3885 | 26093.3885 | 26093.3885 |  | 16070.8005 | 21801.5288 | 23368.1279 | 23609.9554 | 23762.8633 | 24100.0075 | 24897.3046 | 25331.9028 | 26161.1821 | 28683.4724 | 26602.3787 | 26194.791 | 26743.2404 | 27943.5643 | 27129.8392 | 27129.8392 | 27129.8392 | 27129.8392 | 27129.8392 | 27129.8392 | 27129.8392 | 27129.8392 | 27129.8392 | 27129.8392 | 27129.8392 | 27129.8392 | 27129.8392 | 27129.8392 | 27129.8392 | 27129.8392
45% | 11588.8305 | 16068.4223 | 17232.1005 | 17430.0335 | 17583.9957 | 17849.9904 | 18455.8826 | 18860.9836 | 19374.6918 | 19641.0617 | 19875.0474 | 19441.7696 | 19948.3153 | 20744.9909 | 20139.4188 | 20139.4188 | 20139.4188 | 20139.4188 | 20139.4188 | 20139.4188 | 20139.4188 | 20139.4188 | 20139.4188 | 20139.4188 | 20139.4188 | 20139.4188 | 20139.4188 | 20139.4188 | 20139.4188 | 20139.4188 |  | 12403.7774 | 16826.8724 | 18036.0061 | 18222.6536 | 18340.6711 | 18600.8859 | 19216.2564 | 19551.6884 | 20191.7433 | 22138.4993 | 20532.268 | 20217.6833 | 20640.988 | 21567.4228 | 20939.373 | 20939.373 | 20939.373 | 20939.373 | 20939.373 | 20939.373 | 20939.373 | 20939.373 | 20939.373 | 20939.373 | 20939.373 | 20939.373 | 20939.373 | 20939.373 | 20939.373 | 20939.373
40% | 5693.5395 | 7894.3425 | 8466.0523 | 8563.2959 | 8638.9368 | 8769.6188 | 9067.2909 | 9266.3151 | 9518.6977 | 9649.5639 | 9764.5201 | 9551.6527 | 9800.5162 | 10191.9194 | 9894.4045 | 9894.4045 | 9894.4045 | 9894.4045 | 9894.4045 | 9894.4045 | 9894.4045 | 9894.4045 | 9894.4045 | 9894.4045 | 9894.4045 | 9894.4045 | 9894.4045 | 9894.4045 | 9894.4045 | 9894.4045 |  | 6093.9192 | 8266.9656 | 8861.0075 | 8952.7065 | 9010.688 | 9138.5304 | 9440.8591 | 9605.6552 | 9920.1113 | 10876.5437 | 10087.4095 | 9932.8555 | 10140.8232 | 10595.9764 | 10287.4184 | 10287.4184 | 10287.4184 | 10287.4184 | 10287.4184 | 10287.4184 | 10287.4184 | 10287.4184 | 10287.4184 | 10287.4184 | 10287.4184 | 10287.4184 | 10287.4184 | 10287.4184 | 10287.4184 | 10287.4184
35% | 2127.9257 | 2950.4624 | 3164.1354 | 3200.4796 | 3228.75 | 3277.5916 | 3388.8447 | 3463.2288 | 3557.5552 | 3606.4657 | 3649.4298 | 3569.872 | 3662.8832 | 3809.1677 | 3697.9734 | 3697.9734 | 3697.9734 | 3697.9734 | 3697.9734 | 3697.9734 | 3697.9734 | 3697.9734 | 3697.9734 | 3697.9734 | 3697.9734 | 3697.9734 | 3697.9734 | 3697.9734 | 3697.9734 | 3697.9734 |  | 2277.5652 | 3089.728 | 3311.7475 | 3346.0195 | 3367.6897 | 3415.47 | 3528.4635 | 3590.0551 | 3707.5811 | 4065.0419 | 3770.1078 | 3712.3442 | 3790.0708 | 3960.1816 | 3844.8599 | 3844.8599 | 3844.8599 | 3844.8599 | 3844.8599 | 3844.8599 | 3844.8599 | 3844.8599 | 3844.8599 | 3844.8599 | 3844.8599 | 3844.8599 | 3844.8599 | 3844.8599 | 3844.8599 | 3844.8599
30% | 1061.2862 | 1471.5199 | 1578.0877 | 1596.2141 | 1610.3137 | 1634.673 | 1690.1596 | 1727.2581 | 1774.3027 | 1798.6964 | 1820.1244 | 1780.4456 | 1826.8342 | 1899.7925 | 1844.3351 | 1844.3351 | 1844.3351 | 1844.3351 | 1844.3351 | 1844.3351 | 1844.3351 | 1844.3351 | 1844.3351 | 1844.3351 | 1844.3351 | 1844.3351 | 1844.3351 | 1844.3351 | 1844.3351 | 1844.3351 |  | 1135.9177 | 1540.9775 | 1651.708 | 1668.8009 | 1679.6088 | 1703.4388 | 1759.7934 | 1790.5117 | 1849.1269 | 2027.4077 | 1880.3116 | 1851.5025 | 1890.268 | 1975.1094 | 1917.5936 | 1917.5936 | 1917.5936 | 1917.5936 | 1917.5936 | 1917.5936 | 1917.5936 | 1917.5936 | 1917.5936 | 1917.5936 | 1917.5936 | 1917.5936 | 1917.5936 | 1917.5936 | 1917.5936 | 1917.5936
25% | 625.6637 | 867.5102 | 930.3354 | 941.0215 | 949.3337 | 963.6944 | 996.4056 | 1018.2764 | 1046.0107 | 1060.3916 | 1073.0242 | 1049.6322 | 1076.9798 | 1119.9911 | 1087.2972 | 1087.2972 | 1087.2972 | 1087.2972 | 1087.2972 | 1087.2972 | 1087.2972 | 1087.2972 | 1087.2972 | 1087.2972 | 1087.2972 | 1087.2972 | 1087.2972 | 1087.2972 | 1087.2972 | 1087.2972 |  | 669.6615 | 908.4578 | 973.7371 | 983.8139 | 990.1855 | 1004.2341 | 1037.457 | 1055.5665 | 1090.1221 | 1195.2246 | 1108.5065 | 1091.5226 | 1114.3762 | 1164.393 | 1130.4855 | 1130.4855 | 1130.4855 | 1130.4855 | 1130.4855 | 1130.4855 | 1130.4855 | 1130.4855 | 1130.4855 | 1130.4855 | 1130.4855 | 1130.4855 | 1130.4855 | 1130.4855 | 1130.4855 | 1130.4855
20% | 316.1776 | 438.3942 | 470.1428 | 475.543 | 479.7435 | 487.0006 | 503.5312 | 514.5835 | 528.599 | 535.8664 | 542.2502 | 530.4291 | 544.2492 | 565.9848 | 549.463 | 549.463 | 549.463 | 549.463 | 549.463 | 549.463 | 549.463 | 549.463 | 549.463 | 549.463 | 549.463 | 549.463 | 549.463 | 549.463 | 549.463 | 549.463 |  | 338.4118 | 459.0869 | 492.0757 | 497.168 | 500.3879 | 507.4873 | 524.2764 | 533.428 | 550.8906 | 604.0039 | 560.1811 | 551.5983 | 563.1473 | 588.4232 | 571.2881 | 571.2881 | 571.2881 | 571.2881 | 571.2881 | 571.2881 | 571.2881 | 571.2881 | 571.2881 | 571.2881 | 571.2881 | 571.2881 | 571.2881 | 571.2881 | 571.2881 | 571.2881
15% | 128.8131 | 178.605 | 191.5396 | 193.7397 | 195.4511 | 198.4077 | 205.1423 | 209.6451 | 215.3552 | 218.3159 | 220.9167 | 216.1007 | 221.7311 | 230.5864 | 223.8553 | 223.8553 | 223.8553 | 223.8553 | 223.8553 | 223.8553 | 223.8553 | 223.8553 | 223.8553 | 223.8553 | 223.8553 | 223.8553 | 223.8553 | 223.8553 | 223.8553 | 223.8553 |  | 137.8715 | 187.0354 | 200.4753 | 202.5499 | 203.8617 | 206.7541 | 213.5941 | 217.3225 | 224.4369 | 246.0756 | 228.2219 | 224.7252 | 229.4304 | 239.728 | 232.747 | 232.747 | 232.747 | 232.747 | 232.747 | 232.747 | 232.747 | 232.747 | 232.747 | 232.747 | 232.747 | 232.747 | 232.747 | 232.747 | 232.747 | 232.747
10% | 51.8598 | 71.9059 | 77.1134 | 77.9991 | 78.6881 | 79.8784 | 82.5898 | 84.4026 | 86.7014 | 87.8934 | 88.9405 | 87.0016 | 89.2684 | 92.8335 | 90.1236 | 90.1236 | 90.1236 | 90.1236 | 90.1236 | 90.1236 | 90.1236 | 90.1236 | 90.1236 | 90.1236 | 90.1236 | 90.1236 | 90.1236 | 90.1236 | 90.1236 | 90.1236 |  | 55.5067 | 75.3 | 80.7108 | 81.5461 | 82.0742 | 83.2387 | 85.9924 | 87.4935 | 90.3577 | 99.0694 | 91.8816 | 90.4738 | 92.3681 | 96.5139 | 93.7033 | 93.7033 | 93.7033 | 93.7033 | 93.7033 | 93.7033 | 93.7033 | 93.7033 | 93.7033 | 93.7033 | 93.7033 | 93.7033 | 93.7033 | 93.7033 | 93.7033 | 93.7033
5% | 44.1645 | 61.236 | 65.6707 | 66.425 | 67.0118 | 68.0255 | 70.3345 | 71.8783 | 73.8361 | 74.8512 | 75.7429 | 74.0917 | 76.0221 | 79.0582 | 76.7504 | 76.7504 | 76.7504 | 76.7504 | 76.7504 | 76.7504 | 76.7504 | 76.7504 | 76.7504 | 76.7504 | 76.7504 | 76.7504 | 76.7504 | 76.7504 | 76.7504 | 76.7504 |  | 47.2702 | 64.1264 | 68.7344 | 69.4457 | 69.8954 | 70.8871 | 73.2323 | 74.5106 | 76.9498 | 84.3688 | 78.2475 | 77.0487 | 78.6618 | 82.1924 | 79.799 | 79.799 | 79.799 | 79.799 | 79.799 | 79.799 | 79.799 | 79.799 | 79.799 | 79.799 | 79.799 | 79.799 | 79.799 | 79.799 | 79.799 | 79.799
9.992e-14% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E @ R (MWh) | 118268.4368 | 163984.3799 | 175860.1598 | 177880.1417 | 179451.3847 | 182165.962 | 188349.3233 | 192483.5334 | 197726.1221 | 200444.5279 | 202832.442 | 198410.6765 | 203580.168 | 211710.5473 | 205530.4523 | 205530.4523 | 205530.4523 | 205530.4523 | 205530.4523 | 205530.4523 | 205530.4523 | 205530.4523 | 205530.4523 | 205530.4523 | 205530.4523 | 205530.4523 | 205530.4523 | 205530.4523 | 205530.4523 | 205530.4523 | E @ R (MWh) | 126585.2808 | 171724.6525 | 184064.3234 | 185969.1325 | 187173.5461 | 189829.1378 | 196109.2281 | 199532.4392 | 206064.4443 | 225931.832 | 209539.6283 | 206329.172 | 210649.1573 | 220103.7788 | 213694.29 | 213694.29 | 213694.29 | 213694.29 | 213694.29 | 213694.29 | 213694.29 | 213694.29 | 213694.29 | 213694.29 | 213694.29 | 213694.29 | 213694.29 | 213694.29 | 213694.29 | 213694.29
Option 1 Winter POE50 W E @ R (MWh) N 2 | 82787.9057 | 114789.066 | 123102.1118 | 124516.0992 | 125615.9693 | 127516.1734 | 131844.5263 | 134738.4734 | 138408.2855 | 140311.1695 | 141982.7094 | 138887.4736 | 142506.1176 | 148197.3831 | 143871.3166 | 143871.3166 | 143871.3166 | 143871.3166 | 143871.3166 | 143871.3166 | 143871.3166 | 143871.3166 | 143871.3166 | 143871.3166 | 143871.3166 | 143871.3166 | 143871.3166 | 143871.3166 | 143871.3166 | 143871.3166 | Option 1 Winter POE10 W E @ R (MWh) N 2 | 37975.5842 | 51517.3957 | 55219.297 | 55790.7397 | 56152.0638 | 56948.7413 | 58832.7684 | 59859.7318 | 61819.3333 | 67779.5496 | 62861.8885 | 61898.7516 | 63194.7472 | 66031.1336 | 64108.287 | 64108.287 | 64108.287 | 64108.287 | 64108.287 | 64108.287 | 64108.287 | 64108.287 | 64108.287 | 64108.287 | 64108.287 | 64108.287 | 64108.287 | 64108.287 | 64108.287 | 64108.287
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 85.8327 | 111.1071 | 117.7202 | 117.3233 | 117.3513 | 118.0293 | 119.8198 | 121.0174 | 122.1905 | 123.5626 | 124.8333 | 126.0676 | 126.2076 | 127.6483 | 126.5544 | 126.5544 | 126.5544 | 126.5544 | 126.5544 | 126.5544 | 126.5544 | 126.5544 | 126.5544 | 126.5544 | 126.5544 | 126.5544 | 126.5544 | 126.5544 | 126.5544 | 126.5544
98% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 42.4851 | 54.9952 | 58.2686 | 58.0721 | 58.0859 | 58.4216 | 59.3078 | 59.9006 | 60.4812 | 61.1604 | 61.7894 | 62.4003 | 62.4696 | 63.1827 | 62.6413 | 62.6413 | 62.6413 | 62.6413 | 62.6413 | 62.6413 | 62.6413 | 62.6413 | 62.6413 | 62.6413 | 62.6413 | 62.6413 | 62.6413 | 62.6413 | 62.6413 | 62.6413
97% | 18.864 | 25.0432 | 26.7251 | 26.6761 | 26.6743 | 26.866 | 27.0764 | 27.5082 | 27.8185 | 27.9869 | 28.171 | 28.3395 | 28.644 | 29.0219 | 28.9955 | 28.9955 | 28.9955 | 28.9955 | 28.9955 | 28.9955 | 28.9955 | 28.9955 | 28.9955 | 28.9955 | 28.9955 | 28.9955 | 28.9955 | 28.9955 | 28.9955 | 28.9955 |  | 84.1075 | 108.8738 | 115.354 | 114.965 | 114.9925 | 115.6569 | 117.4113 | 118.5849 | 119.7344 | 121.0789 | 122.3241 | 123.5336 | 123.6708 | 125.0825 | 124.0106 | 124.0106 | 124.0106 | 124.0106 | 124.0106 | 124.0106 | 124.0106 | 124.0106 | 124.0106 | 124.0106 | 124.0106 | 124.0106 | 124.0106 | 124.0106 | 124.0106 | 124.0106
95% | 92.8689 | 123.2894 | 131.5698 | 131.3286 | 131.3197 | 132.2634 | 133.299 | 135.4251 | 136.9528 | 137.7816 | 138.6878 | 139.5174 | 141.0166 | 142.8772 | 142.7472 | 142.7472 | 142.7472 | 142.7472 | 142.7472 | 142.7472 | 142.7472 | 142.7472 | 142.7472 | 142.7472 | 142.7472 | 142.7472 | 142.7472 | 142.7472 | 142.7472 | 142.7472 |  | 124.2203 | 160.7982 | 170.369 | 169.7945 | 169.8351 | 170.8163 | 173.4075 | 175.1408 | 176.8385 | 178.8242 | 180.6633 | 182.4496 | 182.6522 | 184.7373 | 183.1541 | 183.1541 | 183.1541 | 183.1541 | 183.1541 | 183.1541 | 183.1541 | 183.1541 | 183.1541 | 183.1541 | 183.1541 | 183.1541 | 183.1541 | 183.1541 | 183.1541 | 183.1541
90% | 161.0694 | 213.8301 | 228.1913 | 227.7731 | 227.7577 | 229.3944 | 231.1905 | 234.8778 | 237.5275 | 238.9649 | 240.5367 | 241.9755 | 244.5756 | 247.8027 | 247.5772 | 247.5772 | 247.5772 | 247.5772 | 247.5772 | 247.5772 | 247.5772 | 247.5772 | 247.5772 | 247.5772 | 247.5772 | 247.5772 | 247.5772 | 247.5772 | 247.5772 | 247.5772 |  | 538.6113 | 697.2109 | 738.7092 | 736.2183 | 736.3942 | 740.6488 | 751.884 | 759.3996 | 766.7606 | 775.3706 | 783.3448 | 791.0899 | 791.9686 | 801.0093 | 794.1448 | 794.1448 | 794.1448 | 794.1448 | 794.1448 | 794.1448 | 794.1448 | 794.1448 | 794.1448 | 794.1448 | 794.1448 | 794.1448 | 794.1448 | 794.1448 | 794.1448 | 794.1448
85% | 457.0889 | 606.8151 | 647.57 | 646.383 | 646.3393 | 650.9841 | 656.081 | 666.5452 | 674.0646 | 678.1436 | 682.6041 | 686.6874 | 694.0659 | 703.2239 | 702.5838 | 702.5838 | 702.5838 | 702.5838 | 702.5838 | 702.5838 | 702.5838 | 702.5838 | 702.5838 | 702.5838 | 702.5838 | 702.5838 | 702.5838 | 702.5838 | 702.5838 | 702.5838 |  | 509.4971 | 659.5238 | 698.779 | 696.4228 | 696.5891 | 700.6138 | 711.2416 | 718.351 | 725.3141 | 733.4587 | 741.0019 | 748.3283 | 749.1595 | 757.7115 | 751.218 | 751.218 | 751.218 | 751.218 | 751.218 | 751.218 | 751.218 | 751.218 | 751.218 | 751.218 | 751.218 | 751.218 | 751.218 | 751.218 | 751.218 | 751.218
80% | 638.4734 | 847.6148 | 904.5422 | 902.8842 | 902.8231 | 909.3111 | 916.4306 | 931.0473 | 941.5505 | 947.2482 | 953.4787 | 959.1824 | 969.4889 | 982.2811 | 981.3869 | 981.3869 | 981.3869 | 981.3869 | 981.3869 | 981.3869 | 981.3869 | 981.3869 | 981.3869 | 981.3869 | 981.3869 | 981.3869 | 981.3869 | 981.3869 | 981.3869 | 981.3869 |  | 355.8393 | 460.6198 | 488.0361 | 486.3905 | 486.5067 | 489.3176 | 496.7402 | 501.7054 | 506.5685 | 512.2568 | 517.5251 | 522.642 | 523.2225 | 529.1954 | 524.6602 | 524.6602 | 524.6602 | 524.6602 | 524.6602 | 524.6602 | 524.6602 | 524.6602 | 524.6602 | 524.6602 | 524.6602 | 524.6602 | 524.6602 | 524.6602 | 524.6602 | 524.6602
75% | 1664.3841 | 2209.5776 | 2357.9769 | 2353.655 | 2353.4957 | 2370.4087 | 2388.968 | 2427.0709 | 2454.4511 | 2469.3039 | 2485.5456 | 2500.414 | 2527.2813 | 2560.6281 | 2558.2972 | 2558.2972 | 2558.2972 | 2558.2972 | 2558.2972 | 2558.2972 | 2558.2972 | 2558.2972 | 2558.2972 | 2558.2972 | 2558.2972 | 2558.2972 | 2558.2972 | 2558.2972 | 2558.2972 | 2558.2972 |  | 635.1192 | 822.1366 | 871.0705 | 868.1333 | 868.3407 | 873.3577 | 886.6059 | 895.4682 | 904.1481 | 914.3008 | 923.7039 | 932.8368 | 933.8729 | 944.5335 | 936.439 | 936.439 | 936.439 | 936.439 | 936.439 | 936.439 | 936.439 | 936.439 | 936.439 | 936.439 | 936.439 | 936.439 | 936.439 | 936.439 | 936.439 | 936.439
70% | 2875.5487 | 3817.4772 | 4073.866 | 4066.399 | 4066.1238 | 4095.3442 | 4127.4091 | 4193.2394 | 4240.5439 | 4266.205 | 4294.2657 | 4319.9539 | 4366.3723 | 4423.9855 | 4419.9585 | 4419.9585 | 4419.9585 | 4419.9585 | 4419.9585 | 4419.9585 | 4419.9585 | 4419.9585 | 4419.9585 | 4419.9585 | 4419.9585 | 4419.9585 | 4419.9585 | 4419.9585 | 4419.9585 | 4419.9585 |  | 1157.0168 | 1497.7123 | 1586.8569 | 1581.5061 | 1581.8839 | 1591.0234 | 1615.1582 | 1631.3028 | 1647.1153 | 1665.6109 | 1682.7407 | 1699.3783 | 1701.266 | 1720.6867 | 1705.9407 | 1705.9407 | 1705.9407 | 1705.9407 | 1705.9407 | 1705.9407 | 1705.9407 | 1705.9407 | 1705.9407 | 1705.9407 | 1705.9407 | 1705.9407 | 1705.9407 | 1705.9407 | 1705.9407 | 1705.9407
65% | 7222.0048 | 9587.679 | 10231.6052 | 10212.8518 | 10212.1606 | 10285.5483 | 10366.0801 | 10531.4141 | 10650.2206 | 10714.6689 | 10785.1441 | 10849.6604 | 10966.2413 | 11110.9382 | 11100.8242 | 11100.8242 | 11100.8242 | 11100.8242 | 11100.8242 | 11100.8242 | 11100.8242 | 11100.8242 | 11100.8242 | 11100.8242 | 11100.8242 | 11100.8242 | 11100.8242 | 11100.8242 | 11100.8242 | 11100.8242 |  | 1455.7061 | 1884.3537 | 1996.5114 | 1989.7793 | 1990.2546 | 2001.7536 | 2032.1189 | 2052.4313 | 2072.3259 | 2095.5961 | 2117.1482 | 2138.0809 | 2140.4558 | 2164.8901 | 2146.3373 | 2146.3373 | 2146.3373 | 2146.3373 | 2146.3373 | 2146.3373 | 2146.3373 | 2146.3373 | 2146.3373 | 2146.3373 | 2146.3373 | 2146.3373 | 2146.3373 | 2146.3373 | 2146.3373 | 2146.3373
60% | 10556.5772 | 14014.5398 | 14955.7822 | 14928.3698 | 14927.3596 | 15034.6321 | 15152.3473 | 15394.0201 | 15567.6823 | 15661.888 | 15764.9032 | 15859.2082 | 16029.6174 | 16241.1243 | 16226.3403 | 16226.3403 | 16226.3403 | 16226.3403 | 16226.3403 | 16226.3403 | 16226.3403 | 16226.3403 | 16226.3403 | 16226.3403 | 16226.3403 | 16226.3403 | 16226.3403 | 16226.3403 | 16226.3403 | 16226.3403 |  | 2277.9105 | 2948.6646 | 3124.1707 | 3113.6361 | 3114.3799 | 3132.3737 | 3179.8897 | 3211.675 | 3242.8062 | 3279.2199 | 3312.9449 | 3345.7006 | 3349.4169 | 3387.6521 | 3358.6203 | 3358.6203 | 3358.6203 | 3358.6203 | 3358.6203 | 3358.6203 | 3358.6203 | 3358.6203 | 3358.6203 | 3358.6203 | 3358.6203 | 3358.6203 | 3358.6203 | 3358.6203 | 3358.6203 | 3358.6203
55% | 11937.0341 | 15847.1857 | 16911.512 | 16880.515 | 16879.3726 | 17000.6729 | 17133.7814 | 17407.0571 | 17603.4287 | 17709.9534 | 17826.4396 | 17933.0767 | 18125.7699 | 18364.935 | 18348.2178 | 18348.2178 | 18348.2178 | 18348.2178 | 18348.2178 | 18348.2178 | 18348.2178 | 18348.2178 | 18348.2178 | 18348.2178 | 18348.2178 | 18348.2178 | 18348.2178 | 18348.2178 | 18348.2178 | 18348.2178 |  | 4377.3623 | 5666.3214 | 6003.5838 | 5983.3401 | 5984.7694 | 6019.3473 | 6110.6567 | 6171.737 | 6231.5606 | 6301.5352 | 6366.343 | 6429.2884 | 6436.4298 | 6509.9048 | 6454.1156 | 6454.1156 | 6454.1156 | 6454.1156 | 6454.1156 | 6454.1156 | 6454.1156 | 6454.1156 | 6454.1156 | 6454.1156 | 6454.1156 | 6454.1156 | 6454.1156 | 6454.1156 | 6454.1156 | 6454.1156
50% | 15327.7148 | 20348.5339 | 21715.179 | 21675.3774 | 21673.9105 | 21829.6658 | 22000.5834 | 22351.4823 | 22603.6327 | 22740.4155 | 22889.9893 | 23026.9163 | 23274.3434 | 23581.4427 | 23559.977 | 23559.977 | 23559.977 | 23559.977 | 23559.977 | 23559.977 | 23559.977 | 23559.977 | 23559.977 | 23559.977 | 23559.977 | 23559.977 | 23559.977 | 23559.977 | 23559.977 | 23559.977 |  | 9714.4123 | 12574.9205 | 13323.3863 | 13278.4606 | 13281.6325 | 13358.3693 | 13561.0066 | 13696.5584 | 13829.3213 | 13984.6116 | 14128.4356 | 14268.1263 | 14283.9748 | 14447.0334 | 14323.224 | 14323.224 | 14323.224 | 14323.224 | 14323.224 | 14323.224 | 14323.224 | 14323.224 | 14323.224 | 14323.224 | 14323.224 | 14323.224 | 14323.224 | 14323.224 | 14323.224 | 14323.224
45% | 20411.3174 | 27097.3455 | 28917.2533 | 28864.251 | 28862.2976 | 29069.7109 | 29297.3152 | 29764.5935 | 30100.3723 | 30282.5206 | 30481.7021 | 30664.0425 | 30993.5314 | 31402.4836 | 31373.8985 | 31373.8985 | 31373.8985 | 31373.8985 | 31373.8985 | 31373.8985 | 31373.8985 | 31373.8985 | 31373.8985 | 31373.8985 | 31373.8985 | 31373.8985 | 31373.8985 | 31373.8985 | 31373.8985 | 31373.8985 |  | 14720.4239 | 19055.0036 | 20189.1672 | 20121.0905 | 20125.8971 | 20242.1776 | 20549.2377 | 20754.6417 | 20955.8197 | 21191.1339 | 21409.073 | 21620.7489 | 21644.7644 | 21891.85 | 21704.2393 | 21704.2393 | 21704.2393 | 21704.2393 | 21704.2393 | 21704.2393 | 21704.2393 | 21704.2393 | 21704.2393 | 21704.2393 | 21704.2393 | 21704.2393 | 21704.2393 | 21704.2393 | 21704.2393 | 21704.2393
40% | 14315.8312 | 19005.1929 | 20281.6168 | 20244.4427 | 20243.0727 | 20388.5455 | 20548.1797 | 20875.9135 | 21111.4178 | 21239.1706 | 21378.87 | 21506.7576 | 21737.8504 | 22024.6761 | 22004.6275 | 22004.6275 | 22004.6275 | 22004.6275 | 22004.6275 | 22004.6275 | 22004.6275 | 22004.6275 | 22004.6275 | 22004.6275 | 22004.6275 | 22004.6275 | 22004.6275 | 22004.6275 | 22004.6275 | 22004.6275 |  | 15242.3215 | 19730.5793 | 20904.9535 | 20834.4632 | 20839.4402 | 20959.8434 | 21277.7899 | 21490.4763 | 21698.7869 | 21942.444 | 22168.1098 | 22387.2904 | 22412.1574 | 22668.0032 | 22473.741 | 22473.741 | 22473.741 | 22473.741 | 22473.741 | 22473.741 | 22473.741 | 22473.741 | 22473.741 | 22473.741 | 22473.741 | 22473.741 | 22473.741 | 22473.741 | 22473.741 | 22473.741
35% | 7422.2532 | 9853.5218 | 10515.3025 | 10496.0291 | 10495.3188 | 10570.7413 | 10653.506 | 10823.4244 | 10945.5251 | 11011.7604 | 11084.1896 | 11150.4949 | 11270.3083 | 11419.0173 | 11408.6228 | 11408.6228 | 11408.6228 | 11408.6228 | 11408.6228 | 11408.6228 | 11408.6228 | 11408.6228 | 11408.6228 | 11408.6228 | 11408.6228 | 11408.6228 | 11408.6228 | 11408.6228 | 11408.6228 | 11408.6228 |  | 20759.9869 | 26872.9779 | 28472.4713 | 28376.4638 | 28383.2424 | 28547.2311 | 28980.2731 | 29269.9512 | 29553.6695 | 29885.5295 | 30192.8856 | 30491.4088 | 30525.2776 | 30873.7386 | 30609.1541 | 30609.1541 | 30609.1541 | 30609.1541 | 30609.1541 | 30609.1541 | 30609.1541 | 30609.1541 | 30609.1541 | 30609.1541 | 30609.1541 | 30609.1541 | 30609.1541 | 30609.1541 | 30609.1541 | 30609.1541
30% | 3452.1096 | 4582.899 | 4890.695 | 4881.7308 | 4881.4005 | 4916.4797 | 4954.9738 | 5034.0033 | 5090.7926 | 5121.5988 | 5155.2859 | 5186.1246 | 5241.8501 | 5311.0151 | 5306.1806 | 5306.1806 | 5306.1806 | 5306.1806 | 5306.1806 | 5306.1806 | 5306.1806 | 5306.1806 | 5306.1806 | 5306.1806 | 5306.1806 | 5306.1806 | 5306.1806 | 5306.1806 | 5306.1806 | 5306.1806 |  | 19183.5111 | 24832.2926 | 26310.3234 | 26221.6065 | 26227.8703 | 26379.406 | 26779.5636 | 27047.2441 | 27309.4173 | 27616.0765 | 27900.0925 | 28175.9464 | 28207.2432 | 28529.2428 | 28284.7504 | 28284.7504 | 28284.7504 | 28284.7504 | 28284.7504 | 28284.7504 | 28284.7504 | 28284.7504 | 28284.7504 | 28284.7504 | 28284.7504 | 28284.7504 | 28284.7504 | 28284.7504 | 28284.7504 | 28284.7504
25% | 2357.031 | 3129.1112 | 3339.2681 | 3333.1476 | 3332.922 | 3356.8734 | 3383.1564 | 3437.1161 | 3475.8908 | 3496.9246 | 3519.9255 | 3540.9815 | 3579.0298 | 3626.2542 | 3622.9533 | 3622.9533 | 3622.9533 | 3622.9533 | 3622.9533 | 3622.9533 | 3622.9533 | 3622.9533 | 3622.9533 | 3622.9533 | 3622.9533 | 3622.9533 | 3622.9533 | 3622.9533 | 3622.9533 | 3622.9533 |  | 5533.3008 | 7162.6379 | 7588.9618 | 7563.3722 | 7565.179 | 7608.888 | 7724.3096 | 7801.5195 | 7877.1409 | 7965.5938 | 8047.5155 | 8127.0829 | 8136.1102 | 8228.9879 | 8158.4664 | 8158.4664 | 8158.4664 | 8158.4664 | 8158.4664 | 8158.4664 | 8158.4664 | 8158.4664 | 8158.4664 | 8158.4664 | 8158.4664 | 8158.4664 | 8158.4664 | 8158.4664 | 8158.4664 | 8158.4664
20% | 1427.8587 | 1895.5749 | 2022.8852 | 2019.1774 | 2019.0408 | 2033.5502 | 2049.4721 | 2082.1602 | 2105.6494 | 2118.3914 | 2132.325 | 2145.0805 | 2168.1297 | 2196.7376 | 2194.738 | 2194.738 | 2194.738 | 2194.738 | 2194.738 | 2194.738 | 2194.738 | 2194.738 | 2194.738 | 2194.738 | 2194.738 | 2194.738 | 2194.738 | 2194.738 | 2194.738 | 2194.738 |  | 1484.8203 | 1922.0408 | 2036.4417 | 2029.5749 | 2030.0597 | 2041.7887 | 2072.7613 | 2093.48 | 2113.7724 | 2137.5081 | 2159.4912 | 2180.8425 | 2183.2649 | 2208.1879 | 2189.264 | 2189.264 | 2189.264 | 2189.264 | 2189.264 | 2189.264 | 2189.264 | 2189.264 | 2189.264 | 2189.264 | 2189.264 | 2189.264 | 2189.264 | 2189.264 | 2189.264 | 2189.264
15% | 914.1778 | 1213.6303 | 1295.1399 | 1292.766 | 1292.6786 | 1301.9681 | 1312.162 | 1333.0904 | 1348.1292 | 1356.2872 | 1365.2081 | 1373.3747 | 1388.1318 | 1406.4479 | 1405.1676 | 1405.1676 | 1405.1676 | 1405.1676 | 1405.1676 | 1405.1676 | 1405.1676 | 1405.1676 | 1405.1676 | 1405.1676 | 1405.1676 | 1405.1676 | 1405.1676 | 1405.1676 | 1405.1676 | 1405.1676 |  | 818.9695 | 1060.1234 | 1123.2225 | 1119.4351 | 1119.7025 | 1126.1718 | 1143.255 | 1154.6827 | 1165.8752 | 1178.9669 | 1191.0919 | 1202.8685 | 1204.2046 | 1217.9511 | 1207.5134 | 1207.5134 | 1207.5134 | 1207.5134 | 1207.5134 | 1207.5134 | 1207.5134 | 1207.5134 | 1207.5134 | 1207.5134 | 1207.5134 | 1207.5134 | 1207.5134 | 1207.5134 | 1207.5134 | 1207.5134
10% | 611.8703 | 812.2975 | 866.8529 | 865.264 | 865.2055 | 871.4231 | 878.246 | 892.2536 | 902.3193 | 907.7795 | 913.7504 | 919.2164 | 929.0935 | 941.3527 | 940.4958 | 940.4958 | 940.4958 | 940.4958 | 940.4958 | 940.4958 | 940.4958 | 940.4958 | 940.4958 | 940.4958 | 940.4958 | 940.4958 | 940.4958 | 940.4958 | 940.4958 | 940.4958 |  | 191.3984 | 247.7576 | 262.5043 | 261.6191 | 261.6816 | 263.1935 | 267.186 | 269.8567 | 272.4725 | 275.5321 | 278.3658 | 281.118 | 281.4303 | 284.643 | 282.2036 | 282.2036 | 282.2036 | 282.2036 | 282.2036 | 282.2036 | 282.2036 | 282.2036 | 282.2036 | 282.2036 | 282.2036 | 282.2036 | 282.2036 | 282.2036 | 282.2036 | 282.2036
5% | 435.3228 | 577.9192 | 616.7333 | 615.6029 | 615.5612 | 619.9848 | 624.8391 | 634.805 | 641.9663 | 645.8511 | 650.0991 | 653.988 | 661.0151 | 669.7371 | 669.1274 | 669.1274 | 669.1274 | 669.1274 | 669.1274 | 669.1274 | 669.1274 | 669.1274 | 669.1274 | 669.1274 | 669.1274 | 669.1274 | 669.1274 | 669.1274 | 669.1274 | 669.1274 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9.992e-14% | 38.2117 | 50.7285 | 54.1355 | 54.0363 | 54.0326 | 54.4209 | 54.847 | 55.7218 | 56.3504 | 56.6914 | 57.0643 | 57.4056 | 58.0224 | 58.788 | 58.7345 | 58.7345 | 58.7345 | 58.7345 | 58.7345 | 58.7345 | 58.7345 | 58.7345 | 58.7345 | 58.7345 | 58.7345 | 58.7345 | 58.7345 | 58.7345 | 58.7345 | 58.7345 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E @ R (MWh) | 102337.6118 | 135859.8063 | 144984.402 | 144718.661 | 144708.8672 | 145748.789 | 146889.9441 | 149232.7692 | 150916.2863 | 151829.5355 | 152828.1856 | 153742.3981 | 155394.3791 | 157444.7704 | 157301.4516 | 157301.4516 | 157301.4516 | 157301.4516 | 157301.4516 | 157301.4516 | 157301.4516 | 157301.4516 | 157301.4516 | 157301.4516 | 157301.4516 | 157301.4516 | 157301.4516 | 157301.4516 | 157301.4516 | 157301.4516 | E @ R (MWh) | 99292.8528 | 128530.651 | 136180.8614 | 135721.6674 | 135754.0887 | 136538.4294 | 138609.6244 | 139995.1247 | 141352.1196 | 142939.3714 | 144409.4236 | 145837.2289 | 145999.2196 | 147665.8725 | 146400.3925 | 146400.3925 | 146400.3925 | 146400.3925 | 146400.3925 | 146400.3925 | 146400.3925 | 146400.3925 | 146400.3925 | 146400.3925 | 146400.3925 | 146400.3925 | 146400.3925 | 146400.3925 | 146400.3925 | 146400.3925
Option 1 Summer POE50 W E @ R (MWh) N 2 | 71636.3283 | 95101.8644 | 101489.0814 | 101303.0627 | 101296.207 | 102024.1523 | 102822.9609 | 104462.9384 | 105641.4004 | 106280.6749 | 106979.7299 | 107619.6787 | 108776.0654 | 110211.3393 | 110111.0161 | 110111.0161 | 110111.0161 | 110111.0161 | 110111.0161 | 110111.0161 | 110111.0161 | 110111.0161 | 110111.0161 | 110111.0161 | 110111.0161 | 110111.0161 | 110111.0161 | 110111.0161 | 110111.0161 | 110111.0161 | Option 1 Summer POE10 W E @ R (MWh) N 2 | 29787.8558 | 38559.1953 | 40854.2584 | 40716.5002 | 40726.2266 | 40961.5288 | 41582.8873 | 41998.5374 | 42405.6359 | 42881.8114 | 43322.8271 | 43751.1687 | 43799.7659 | 44299.7618 | 43920.1178 | 43920.1178 | 43920.1178 | 43920.1178 | 43920.1178 | 43920.1178 | 43920.1178 | 43920.1178 | 43920.1178 | 43920.1178 | 43920.1178 | 43920.1178 | 43920.1178 | 43920.1178 | 43920.1178 | 43920.1178
Option 2 - 1A New PHS ZSS + Four new feeders
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | 66.5813 | 92.3179 | 99.0036 | 57.2625 | 58.147 | 59.6753 | 63.1563 | 65.4837 | 68.4351 | 69.9655 | 71.3098 | 68.8205 | 71.7308 | 76.3079 | 72.8287 | 72.8287 | 72.8287 | 72.8287 | 72.8287 | 72.8287 | 72.8287 | 72.8287 | 72.8287 | 72.8287 | 72.8287 | 72.8287 | 72.8287 | 72.8287 | 72.8287 | 72.8287 |  | 71.2634 | 96.6755 | 103.6223 | 61.8163 | 62.4944 | 63.9894 | 67.5249 | 69.452 | 73.1293 | 84.314 | 75.0857 | 73.2784 | 75.7104 | 81.033 | 77.4247 | 77.4247 | 77.4247 | 77.4247 | 77.4247 | 77.4247 | 77.4247 | 77.4247 | 77.4247 | 77.4247 | 77.4247 | 77.4247 | 77.4247 | 77.4247 | 77.4247 | 77.4247
98% | 79.0946 | 109.6681 | 117.6103 | 68.0244 | 69.0752 | 70.8906 | 75.0259 | 77.7907 | 81.2968 | 83.1148 | 84.7118 | 81.7546 | 85.2118 | 90.6492 | 86.5161 | 86.5161 | 86.5161 | 86.5161 | 86.5161 | 86.5161 | 86.5161 | 86.5161 | 86.5161 | 86.5161 | 86.5161 | 86.5161 | 86.5161 | 86.5161 | 86.5161 | 86.5161 |  | 84.6567 | 114.8446 | 123.097 | 73.4341 | 74.2395 | 76.0155 | 80.2155 | 82.5048 | 86.8732 | 100.16 | 89.1973 | 87.0503 | 89.9394 | 96.2623 | 91.9759 | 91.9759 | 91.9759 | 91.9759 | 91.9759 | 91.9759 | 91.9759 | 91.9759 | 91.9759 | 91.9759 | 91.9759 | 91.9759 | 91.9759 | 91.9759 | 91.9759 | 91.9759
97% | 156.5832 | 217.1095 | 232.8326 | 134.6675 | 136.7478 | 140.3418 | 148.5284 | 154.0019 | 160.9429 | 164.542 | 167.7035 | 161.8492 | 168.6934 | 179.4578 | 171.2756 | 171.2756 | 171.2756 | 171.2756 | 171.2756 | 171.2756 | 171.2756 | 171.2756 | 171.2756 | 171.2756 | 171.2756 | 171.2756 | 171.2756 | 171.2756 | 171.2756 | 171.2756 |  | 167.5944 | 227.3573 | 243.6946 | 145.3771 | 146.9717 | 150.4876 | 158.8022 | 163.3344 | 171.9825 | 198.2863 | 176.5836 | 172.333 | 178.0525 | 190.5701 | 182.0842 | 182.0842 | 182.0842 | 182.0842 | 182.0842 | 182.0842 | 182.0842 | 182.0842 | 182.0842 | 182.0842 | 182.0842 | 182.0842 | 182.0842 | 182.0842 | 182.0842 | 182.0842
95% | 462.5227 | 641.3081 | 687.7517 | 397.7872 | 403.932 | 414.5481 | 438.7299 | 454.8979 | 475.4006 | 486.0317 | 495.3703 | 478.0777 | 498.2945 | 530.0907 | 505.9216 | 505.9216 | 505.9216 | 505.9216 | 505.9216 | 505.9216 | 505.9216 | 505.9216 | 505.9216 | 505.9216 | 505.9216 | 505.9216 | 505.9216 | 505.9216 | 505.9216 | 505.9216 |  | 495.0481 | 671.5786 | 719.8364 | 429.4215 | 434.1317 | 444.5171 | 469.0772 | 482.4647 | 508.01 | 585.7071 | 521.6007 | 509.0453 | 525.9398 | 562.9148 | 537.8487 | 537.8487 | 537.8487 | 537.8487 | 537.8487 | 537.8487 | 537.8487 | 537.8487 | 537.8487 | 537.8487 | 537.8487 | 537.8487 | 537.8487 | 537.8487 | 537.8487 | 537.8487
90% | 2550.165 | 3535.9158 | 3791.9875 | 2193.2391 | 2227.119 | 2285.6522 | 2418.981 | 2508.125 | 2621.1684 | 2679.784 | 2731.2735 | 2635.9291 | 2747.3963 | 2922.7077 | 2789.4493 | 2789.4493 | 2789.4493 | 2789.4493 | 2789.4493 | 2789.4493 | 2789.4493 | 2789.4493 | 2789.4493 | 2789.4493 | 2789.4493 | 2789.4493 | 2789.4493 | 2789.4493 | 2789.4493 | 2789.4493 |  | 2729.4971 | 3702.8155 | 3968.8899 | 2367.6581 | 2393.6283 | 2450.8895 | 2586.3041 | 2660.1171 | 2800.9636 | 3229.3544 | 2875.8973 | 2806.6718 | 2899.8215 | 3103.6869 | 2965.4822 | 2965.4822 | 2965.4822 | 2965.4822 | 2965.4822 | 2965.4822 | 2965.4822 | 2965.4822 | 2965.4822 | 2965.4822 | 2965.4822 | 2965.4822 | 2965.4822 | 2965.4822 | 2965.4822 | 2965.4822
85% | 6229.8705 | 8637.9889 | 9263.5537 | 5357.926 | 5440.6923 | 5583.6845 | 5909.3973 | 6127.1696 | 6403.3265 | 6546.5204 | 6672.3054 | 6439.3859 | 6711.6924 | 7139.9657 | 6814.4249 | 6814.4249 | 6814.4249 | 6814.4249 | 6814.4249 | 6814.4249 | 6814.4249 | 6814.4249 | 6814.4249 | 6814.4249 | 6814.4249 | 6814.4249 | 6814.4249 | 6814.4249 | 6814.4249 | 6814.4249 |  | 6667.9659 | 9045.7131 | 9695.7136 | 5784.0191 | 5847.4624 | 5987.3475 | 6318.1555 | 6498.4755 | 6842.5533 | 7889.0815 | 7025.611 | 6856.498 | 7084.0562 | 7582.0848 | 7244.4607 | 7244.4607 | 7244.4607 | 7244.4607 | 7244.4607 | 7244.4607 | 7244.4607 | 7244.4607 | 7244.4607 | 7244.4607 | 7244.4607 | 7244.4607 | 7244.4607 | 7244.4607 | 7244.4607 | 7244.4607
80% | 9683.0656 | 13425.9956 | 14398.3087 | 8327.8054 | 8456.4487 | 8678.701 | 9184.9552 | 9523.438 | 9952.6677 | 10175.2335 | 10370.7406 | 10008.7147 | 10431.9597 | 11097.6233 | 10591.6365 | 10591.6365 | 10591.6365 | 10591.6365 | 10591.6365 | 10591.6365 | 10591.6365 | 10591.6365 | 10591.6365 | 10591.6365 | 10591.6365 | 10591.6365 | 10591.6365 | 10591.6365 | 10591.6365 | 10591.6365 |  | 10363.9958 | 14059.7198 | 15070.0133 | 8990.0804 | 9088.6901 | 9306.113 | 9820.2868 | 10100.5575 | 10635.3564 | 12261.9714 | 10919.8823 | 10657.0306 | 11010.7235 | 11784.8076 | 11260.0395 | 11260.0395 | 11260.0395 | 11260.0395 | 11260.0395 | 11260.0395 | 11260.0395 | 11260.0395 | 11260.0395 | 11260.0395 | 11260.0395 | 11260.0395 | 11260.0395 | 11260.0395 | 11260.0395 | 11260.0395
75% | 10683.1238 | 14812.6201 | 15885.3529 | 9187.8935 | 9329.823 | 9575.0293 | 10133.569 | 10507.0099 | 10980.5701 | 11226.1223 | 11441.8212 | 11042.4056 | 11509.3629 | 12243.7757 | 11685.5311 | 11685.5311 | 11685.5311 | 11685.5311 | 11685.5311 | 11685.5311 | 11685.5311 | 11685.5311 | 11685.5311 | 11685.5311 | 11685.5311 | 11685.5311 | 11685.5311 | 11685.5311 | 11685.5311 | 11685.5311 |  | 11434.3798 | 15511.7948 | 16626.4305 | 9918.5676 | 10027.3617 | 10267.2398 | 10834.517 | 11143.7338 | 11733.7663 | 13528.3766 | 12047.6778 | 11757.679 | 12147.9009 | 13001.9317 | 12422.9661 | 12422.9661 | 12422.9661 | 12422.9661 | 12422.9661 | 12422.9661 | 12422.9661 | 12422.9661 | 12422.9661 | 12422.9661 | 12422.9661 | 12422.9661 | 12422.9661 | 12422.9661 | 12422.9661 | 12422.9661
70% | 11478.4193 | 15915.3323 | 17067.9236 | 9871.8779 | 10024.3733 | 10287.8337 | 10887.9534 | 11289.1948 | 11798.0088 | 12061.8408 | 12293.5973 | 11864.4475 | 12366.1671 | 13155.2525 | 12555.4499 | 12555.4499 | 12555.4499 | 12555.4499 | 12555.4499 | 12555.4499 | 12555.4499 | 12555.4499 | 12555.4499 | 12555.4499 | 12555.4499 | 12555.4499 | 12555.4499 | 12555.4499 | 12555.4499 | 12555.4499 |  | 12285.6019 | 16666.5563 | 17864.1701 | 10656.9465 | 10773.8396 | 11031.5752 | 11641.0828 | 11973.319 | 12607.2759 | 14535.4844 | 12944.5562 | 12632.9688 | 13052.2404 | 13969.8488 | 13347.7826 | 13347.7826 | 13347.7826 | 13347.7826 | 13347.7826 | 13347.7826 | 13347.7826 | 13347.7826 | 13347.7826 | 13347.7826 | 13347.7826 | 13347.7826 | 13347.7826 | 13347.7826 | 13347.7826 | 13347.7826
65% | 12096.053 | 16771.7086 | 17986.3189 | 10403.0665 | 10563.7673 | 10841.4042 | 11473.8152 | 11896.6467 | 12432.8391 | 12710.8675 | 12955.0944 | 12502.8528 | 13031.569 | 13863.1138 | 13231.0368 | 13231.0368 | 13231.0368 | 13231.0368 | 13231.0368 | 13231.0368 | 13231.0368 | 13231.0368 | 13231.0368 | 13231.0368 | 13231.0368 | 13231.0368 | 13231.0368 | 13231.0368 | 13231.0368 | 13231.0368 |  | 12946.6687 | 17563.3547 | 18825.4101 | 11230.3782 | 11353.5611 | 11625.1651 | 12267.4692 | 12617.5824 | 13285.6515 | 15317.6135 | 13641.0803 | 13312.7268 | 13754.5588 | 14721.5421 | 14066.0035 | 14066.0035 | 14066.0035 | 14066.0035 | 14066.0035 | 14066.0035 | 14066.0035 | 14066.0035 | 14066.0035 | 14066.0035 | 14066.0035 | 14066.0035 | 14066.0035 | 14066.0035 | 14066.0035 | 14066.0035
60% | 13316.2645 | 18463.5854 | 19800.7217 | 11452.4949 | 11629.4067 | 11935.0506 | 12631.2573 | 13096.7427 | 13687.0245 | 13993.0995 | 14261.9632 | 13764.1009 | 14346.1524 | 15261.5807 | 14565.7418 | 14565.7418 | 14565.7418 | 14565.7418 | 14565.7418 | 14565.7418 | 14565.7418 | 14565.7418 | 14565.7418 | 14565.7418 | 14565.7418 | 14565.7418 | 14565.7418 | 14565.7418 | 14565.7418 | 14565.7418 |  | 14252.6876 | 19335.0902 | 20724.4577 | 12363.2631 | 12498.8724 | 12797.8749 | 13504.9726 | 13890.4042 | 14625.8659 | 16862.8058 | 15017.1492 | 14655.6725 | 15142.075 | 16206.6045 | 15484.9374 | 15484.9374 | 15484.9374 | 15484.9374 | 15484.9374 | 15484.9374 | 15484.9374 | 15484.9374 | 15484.9374 | 15484.9374 | 15484.9374 | 15484.9374 | 15484.9374 | 15484.9374 | 15484.9374 | 15484.9374
55% | 14813.5078 | 20539.579 | 22027.0592 | 12740.1812 | 12936.9845 | 13276.9941 | 14051.4803 | 14569.3036 | 15225.955 | 15566.4442 | 15865.5382 | 15311.6977 | 15959.1934 | 16977.5499 | 16203.4728 | 16203.4728 | 16203.4728 | 16203.4728 | 16203.4728 | 16203.4728 | 16203.4728 | 16203.4728 | 16203.4728 | 16203.4728 | 16203.4728 | 16203.4728 | 16203.4728 | 16203.4728 | 16203.4728 | 16203.4728 |  | 15855.2197 | 21509.0734 | 23054.6574 | 13753.3537 | 13904.2104 | 14236.8319 | 15023.4337 | 15452.2021 | 16270.3571 | 18758.8122 | 16705.6352 | 16303.5151 | 16844.6073 | 18028.8295 | 17226.0202 | 17226.0202 | 17226.0202 | 17226.0202 | 17226.0202 | 17226.0202 | 17226.0202 | 17226.0202 | 17226.0202 | 17226.0202 | 17226.0202 | 17226.0202 | 17226.0202 | 17226.0202 | 17226.0202 | 17226.0202
50% | 15014.9247 | 20818.8523 | 22326.5575 | 12913.4073 | 13112.8865 | 13457.5193 | 14242.536 | 14767.4001 | 15432.9798 | 15778.0986 | 16081.2594 | 15519.8883 | 16176.1879 | 17208.3909 | 16423.7888 | 16423.7888 | 16423.7888 | 16423.7888 | 16423.7888 | 16423.7888 | 16423.7888 | 16423.7888 | 16423.7888 | 16423.7888 | 16423.7888 | 16423.7888 | 16423.7888 | 16423.7888 | 16423.7888 | 16423.7888 |  | 16070.8005 | 21801.5288 | 23368.1279 | 13940.3558 | 14093.2637 | 14430.4078 | 15227.7049 | 15662.3032 | 16491.5825 | 19013.8728 | 16932.779 | 16525.1913 | 17073.6407 | 18273.9646 | 17460.2396 | 17460.2396 | 17460.2396 | 17460.2396 | 17460.2396 | 17460.2396 | 17460.2396 | 17460.2396 | 17460.2396 | 17460.2396 | 17460.2396 | 17460.2396 | 17460.2396 | 17460.2396 | 17460.2396 | 17460.2396
45% | 11588.8305 | 16068.4223 | 17232.1005 | 9966.8358 | 10120.798 | 10386.7927 | 10992.6849 | 11397.7859 | 11911.4941 | 12177.864 | 12411.8498 | 11978.5719 | 12485.1176 | 13281.7933 | 12676.2211 | 12676.2211 | 12676.2211 | 12676.2211 | 12676.2211 | 12676.2211 | 12676.2211 | 12676.2211 | 12676.2211 | 12676.2211 | 12676.2211 | 12676.2211 | 12676.2211 | 12676.2211 | 12676.2211 | 12676.2211 |  | 12403.7774 | 16826.8724 | 18036.0061 | 10759.4559 | 10877.4734 | 11137.6883 | 11753.0587 | 12088.4907 | 12728.5456 | 14675.3016 | 13069.0703 | 12754.4856 | 13177.7903 | 14104.2252 | 13476.1753 | 13476.1753 | 13476.1753 | 13476.1753 | 13476.1753 | 13476.1753 | 13476.1753 | 13476.1753 | 13476.1753 | 13476.1753 | 13476.1753 | 13476.1753 | 13476.1753 | 13476.1753 | 13476.1753 | 13476.1753
40% | 5693.5395 | 7894.3425 | 8466.0523 | 4896.6609 | 4972.3019 | 5102.9838 | 5400.6559 | 5599.6802 | 5852.0627 | 5982.929 | 6097.8851 | 5885.0177 | 6133.8813 | 6525.2844 | 6227.7696 | 6227.7696 | 6227.7696 | 6227.7696 | 6227.7696 | 6227.7696 | 6227.7696 | 6227.7696 | 6227.7696 | 6227.7696 | 6227.7696 | 6227.7696 | 6227.7696 | 6227.7696 | 6227.7696 | 6227.7696 |  | 6093.9192 | 8266.9656 | 8861.0075 | 5286.0716 | 5344.053 | 5471.8954 | 5774.2241 | 5939.0203 | 6253.4764 | 7209.9087 | 6420.7746 | 6266.2206 | 6474.1882 | 6929.3414 | 6620.7834 | 6620.7834 | 6620.7834 | 6620.7834 | 6620.7834 | 6620.7834 | 6620.7834 | 6620.7834 | 6620.7834 | 6620.7834 | 6620.7834 | 6620.7834 | 6620.7834 | 6620.7834 | 6620.7834 | 6620.7834
35% | 2127.9257 | 2950.4624 | 3164.1354 | 1830.0972 | 1858.3675 | 1907.2091 | 2018.4622 | 2092.8463 | 2187.1728 | 2236.0832 | 2279.0474 | 2199.4895 | 2292.5007 | 2438.7853 | 2327.5909 | 2327.5909 | 2327.5909 | 2327.5909 | 2327.5909 | 2327.5909 | 2327.5909 | 2327.5909 | 2327.5909 | 2327.5909 | 2327.5909 | 2327.5909 | 2327.5909 | 2327.5909 | 2327.5909 | 2327.5909 |  | 2277.5652 | 3089.728 | 3311.7475 | 1975.637 | 1997.3072 | 2045.0875 | 2158.0811 | 2219.6726 | 2337.1987 | 2694.6594 | 2399.7254 | 2341.9617 | 2419.6884 | 2589.7991 | 2474.4774 | 2474.4774 | 2474.4774 | 2474.4774 | 2474.4774 | 2474.4774 | 2474.4774 | 2474.4774 | 2474.4774 | 2474.4774 | 2474.4774 | 2474.4774 | 2474.4774 | 2474.4774 | 2474.4774 | 2474.4774
30% | 1061.2862 | 1471.5199 | 1578.0877 | 912.7466 | 926.8462 | 951.2055 | 1006.6922 | 1043.7907 | 1090.8352 | 1115.2289 | 1136.657 | 1096.9781 | 1143.3667 | 1216.325 | 1160.8677 | 1160.8677 | 1160.8677 | 1160.8677 | 1160.8677 | 1160.8677 | 1160.8677 | 1160.8677 | 1160.8677 | 1160.8677 | 1160.8677 | 1160.8677 | 1160.8677 | 1160.8677 | 1160.8677 | 1160.8677 |  | 1135.9177 | 1540.9775 | 1651.708 | 985.3334 | 996.1413 | 1019.9713 | 1076.326 | 1107.0443 | 1165.6595 | 1343.9402 | 1196.8442 | 1168.035 | 1206.8006 | 1291.6419 | 1234.1262 | 1234.1262 | 1234.1262 | 1234.1262 | 1234.1262 | 1234.1262 | 1234.1262 | 1234.1262 | 1234.1262 | 1234.1262 | 1234.1262 | 1234.1262 | 1234.1262 | 1234.1262 | 1234.1262 | 1234.1262
25% | 625.6637 | 867.5102 | 930.3354 | 538.0946 | 546.4068 | 560.7675 | 593.4787 | 615.3495 | 643.0838 | 657.4647 | 670.0973 | 646.7052 | 674.0529 | 717.0642 | 684.3703 | 684.3703 | 684.3703 | 684.3703 | 684.3703 | 684.3703 | 684.3703 | 684.3703 | 684.3703 | 684.3703 | 684.3703 | 684.3703 | 684.3703 | 684.3703 | 684.3703 | 684.3703 |  | 669.6615 | 908.4578 | 973.7371 | 580.887 | 587.2586 | 601.3072 | 634.5301 | 652.6396 | 687.1952 | 792.2977 | 705.5796 | 688.5957 | 711.4493 | 761.4661 | 727.5586 | 727.5586 | 727.5586 | 727.5586 | 727.5586 | 727.5586 | 727.5586 | 727.5586 | 727.5586 | 727.5586 | 727.5586 | 727.5586 | 727.5586 | 727.5586 | 727.5586 | 727.5586
20% | 316.1776 | 438.3942 | 470.1428 | 271.9248 | 276.1254 | 283.3825 | 299.913 | 310.9654 | 324.9809 | 332.2482 | 338.632 | 326.8109 | 340.631 | 362.3667 | 345.8449 | 345.8449 | 345.8449 | 345.8449 | 345.8449 | 345.8449 | 345.8449 | 345.8449 | 345.8449 | 345.8449 | 345.8449 | 345.8449 | 345.8449 | 345.8449 | 345.8449 | 345.8449 |  | 338.4118 | 459.0869 | 492.0757 | 293.5498 | 296.7697 | 303.8691 | 320.6583 | 329.8098 | 347.2724 | 400.3857 | 356.563 | 347.9802 | 359.5292 | 384.8051 | 367.67 | 367.67 | 367.67 | 367.67 | 367.67 | 367.67 | 367.67 | 367.67 | 367.67 | 367.67 | 367.67 | 367.67 | 367.67 | 367.67 | 367.67 | 367.67
15% | 128.8131 | 178.605 | 191.5396 | 110.7842 | 112.4955 | 115.4521 | 122.1868 | 126.6896 | 132.3996 | 135.3604 | 137.9612 | 133.1452 | 138.7756 | 147.6309 | 140.8998 | 140.8998 | 140.8998 | 140.8998 | 140.8998 | 140.8998 | 140.8998 | 140.8998 | 140.8998 | 140.8998 | 140.8998 | 140.8998 | 140.8998 | 140.8998 | 140.8998 | 140.8998 |  | 137.8715 | 187.0354 | 200.4753 | 119.5944 | 120.9062 | 123.7985 | 130.6386 | 134.367 | 141.4814 | 163.1201 | 145.2664 | 141.7697 | 146.4748 | 156.7724 | 149.7915 | 149.7915 | 149.7915 | 149.7915 | 149.7915 | 149.7915 | 149.7915 | 149.7915 | 149.7915 | 149.7915 | 149.7915 | 149.7915 | 149.7915 | 149.7915 | 149.7915 | 149.7915
10% | 51.8598 | 71.9059 | 77.1134 | 44.6014 | 45.2904 | 46.4807 | 49.1921 | 51.0049 | 53.3037 | 54.4957 | 55.5428 | 53.6039 | 55.8707 | 59.4358 | 56.7259 | 56.7259 | 56.7259 | 56.7259 | 56.7259 | 56.7259 | 56.7259 | 56.7259 | 56.7259 | 56.7259 | 56.7259 | 56.7259 | 56.7259 | 56.7259 | 56.7259 | 56.7259 |  | 55.5067 | 75.3 | 80.7108 | 48.1484 | 48.6765 | 49.841 | 52.5947 | 54.0958 | 56.96 | 65.6717 | 58.4839 | 57.0761 | 58.9704 | 63.1162 | 60.3057 | 60.3057 | 60.3057 | 60.3057 | 60.3057 | 60.3057 | 60.3057 | 60.3057 | 60.3057 | 60.3057 | 60.3057 | 60.3057 | 60.3057 | 60.3057 | 60.3057 | 60.3057
5% | 44.1645 | 61.236 | 65.6707 | 37.9831 | 38.5699 | 39.5836 | 41.8926 | 43.4364 | 45.3942 | 46.4093 | 47.301 | 45.6498 | 47.5802 | 50.6163 | 48.3085 | 48.3085 | 48.3085 | 48.3085 | 48.3085 | 48.3085 | 48.3085 | 48.3085 | 48.3085 | 48.3085 | 48.3085 | 48.3085 | 48.3085 | 48.3085 | 48.3085 | 48.3085 |  | 47.2702 | 64.1264 | 68.7344 | 41.0038 | 41.4535 | 42.4452 | 44.7904 | 46.0687 | 48.5079 | 55.9269 | 49.8056 | 48.6068 | 50.2199 | 53.7505 | 51.3571 | 51.3571 | 51.3571 | 51.3571 | 51.3571 | 51.3571 | 51.3571 | 51.3571 | 51.3571 | 51.3571 | 51.3571 | 51.3571 | 51.3571 | 51.3571 | 51.3571 | 51.3571
9.992e-14% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E @ R (MWh) | 118268.4368 | 163984.3799 | 175860.1598 | 101715.3619 | 103286.6048 | 106001.1822 | 112184.5435 | 116318.7536 | 121561.3423 | 124279.7481 | 126667.6622 | 122245.8967 | 127415.3882 | 135545.7675 | 129365.6725 | 129365.6725 | 129365.6725 | 129365.6725 | 129365.6725 | 129365.6725 | 129365.6725 | 129365.6725 | 129365.6725 | 129365.6725 | 129365.6725 | 129365.6725 | 129365.6725 | 129365.6725 | 129365.6725 | 129365.6725 | E @ R (MWh) | 126585.2808 | 171724.6525 | 184064.3234 | 109804.3527 | 111008.7663 | 113664.358 | 119944.4483 | 123367.6594 | 129899.6645 | 149767.0522 | 133374.8485 | 130164.3922 | 134484.3775 | 143938.999 | 137529.5102 | 137529.5102 | 137529.5102 | 137529.5102 | 137529.5102 | 137529.5102 | 137529.5102 | 137529.5102 | 137529.5102 | 137529.5102 | 137529.5102 | 137529.5102 | 137529.5102 | 137529.5102 | 137529.5102 | 137529.5102
Option 2 Winter POE50 W E @ R (MWh) N 2 | 82787.9057 | 114789.066 | 123102.1118 | 71200.7533 | 72300.6234 | 74200.8276 | 78529.1804 | 81423.1275 | 85092.9396 | 86995.8236 | 88667.3635 | 85572.1277 | 89190.7717 | 94882.0373 | 90555.9708 | 90555.9708 | 90555.9708 | 90555.9708 | 90555.9708 | 90555.9708 | 90555.9708 | 90555.9708 | 90555.9708 | 90555.9708 | 90555.9708 | 90555.9708 | 90555.9708 | 90555.9708 | 90555.9708 | 90555.9708 | Option 2 Winter POE10 W E @ R (MWh) N 2 | 37975.5842 | 51517.3957 | 55219.297 | 32941.3058 | 33302.6299 | 34099.3074 | 35983.3345 | 37010.2978 | 38969.8993 | 44930.1157 | 40012.4546 | 39049.3177 | 40345.3132 | 43181.6997 | 41258.8531 | 41258.8531 | 41258.8531 | 41258.8531 | 41258.8531 | 41258.8531 | 41258.8531 | 41258.8531 | 41258.8531 | 41258.8531 | 41258.8531 | 41258.8531 | 41258.8531 | 41258.8531 | 41258.8531 | 41258.8531
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 85.8327 | 111.1071 | 117.7202 | 73.6756 | 73.7036 | 74.3816 | 76.172 | 77.3697 | 78.5428 | 79.9148 | 81.1856 | 82.4199 | 82.5599 | 84.0006 | 82.9067 | 82.9067 | 82.9067 | 82.9067 | 82.9067 | 82.9067 | 82.9067 | 82.9067 | 82.9067 | 82.9067 | 82.9067 | 82.9067 | 82.9067 | 82.9067 | 82.9067 | 82.9067
98% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 42.4851 | 54.9952 | 58.2686 | 36.4676 | 36.4814 | 36.817 | 37.7032 | 38.2961 | 38.8767 | 39.5558 | 40.1848 | 40.7958 | 40.8651 | 41.5782 | 41.0367 | 41.0367 | 41.0367 | 41.0367 | 41.0367 | 41.0367 | 41.0367 | 41.0367 | 41.0367 | 41.0367 | 41.0367 | 41.0367 | 41.0367 | 41.0367 | 41.0367 | 41.0367
97% | 18.864 | 25.0432 | 26.7251 | 15.9835 | 15.9817 | 16.1734 | 16.3838 | 16.8156 | 17.1259 | 17.2943 | 17.4784 | 17.6469 | 17.9514 | 18.3293 | 18.3029 | 18.3029 | 18.3029 | 18.3029 | 18.3029 | 18.3029 | 18.3029 | 18.3029 | 18.3029 | 18.3029 | 18.3029 | 18.3029 | 18.3029 | 18.3029 | 18.3029 | 18.3029 |  | 84.1075 | 108.8738 | 115.354 | 72.1946 | 72.2221 | 72.8865 | 74.6409 | 75.8145 | 76.964 | 78.3085 | 79.5537 | 80.7632 | 80.9004 | 82.3122 | 81.2402 | 81.2402 | 81.2402 | 81.2402 | 81.2402 | 81.2402 | 81.2402 | 81.2402 | 81.2402 | 81.2402 | 81.2402 | 81.2402 | 81.2402 | 81.2402 | 81.2402 | 81.2402
95% | 92.8689 | 123.2894 | 131.5698 | 78.6881 | 78.6793 | 79.623 | 80.6585 | 82.7846 | 84.3123 | 85.1411 | 86.0473 | 86.877 | 88.3761 | 90.2368 | 90.1067 | 90.1067 | 90.1067 | 90.1067 | 90.1067 | 90.1067 | 90.1067 | 90.1067 | 90.1067 | 90.1067 | 90.1067 | 90.1067 | 90.1067 | 90.1067 | 90.1067 | 90.1067 |  | 124.2203 | 160.7982 | 170.369 | 106.6259 | 106.6665 | 107.6477 | 110.2389 | 111.9722 | 113.6699 | 115.6556 | 117.4948 | 119.281 | 119.4837 | 121.5687 | 119.9856 | 119.9856 | 119.9856 | 119.9856 | 119.9856 | 119.9856 | 119.9856 | 119.9856 | 119.9856 | 119.9856 | 119.9856 | 119.9856 | 119.9856 | 119.9856 | 119.9856 | 119.9856
90% | 161.0694 | 213.8301 | 228.1913 | 136.4748 | 136.4593 | 138.0961 | 139.8921 | 143.5795 | 146.2292 | 147.6666 | 149.2384 | 150.6772 | 153.2773 | 156.5044 | 156.2788 | 156.2788 | 156.2788 | 156.2788 | 156.2788 | 156.2788 | 156.2788 | 156.2788 | 156.2788 | 156.2788 | 156.2788 | 156.2788 | 156.2788 | 156.2788 | 156.2788 | 156.2788 |  | 538.6113 | 697.2109 | 738.7092 | 462.3234 | 462.4993 | 466.7539 | 477.989 | 485.5047 | 492.8656 | 501.4756 | 509.4499 | 517.195 | 518.0737 | 527.1144 | 520.2498 | 520.2498 | 520.2498 | 520.2498 | 520.2498 | 520.2498 | 520.2498 | 520.2498 | 520.2498 | 520.2498 | 520.2498 | 520.2498 | 520.2498 | 520.2498 | 520.2498 | 520.2498
85% | 457.0889 | 606.8151 | 647.57 | 387.2932 | 387.2495 | 391.8943 | 396.9912 | 407.4554 | 414.9748 | 419.0538 | 423.5142 | 427.5976 | 434.9761 | 444.1341 | 443.494 | 443.494 | 443.494 | 443.494 | 443.494 | 443.494 | 443.494 | 443.494 | 443.494 | 443.494 | 443.494 | 443.494 | 443.494 | 443.494 | 443.494 | 443.494 |  | 509.4971 | 659.5238 | 698.779 | 437.333 | 437.4993 | 441.524 | 452.1518 | 459.2612 | 466.2242 | 474.3688 | 481.9121 | 489.2385 | 490.0697 | 498.6217 | 492.1282 | 492.1282 | 492.1282 | 492.1282 | 492.1282 | 492.1282 | 492.1282 | 492.1282 | 492.1282 | 492.1282 | 492.1282 | 492.1282 | 492.1282 | 492.1282 | 492.1282 | 492.1282
80% | 638.4734 | 847.6148 | 904.5422 | 540.981 | 540.9199 | 547.4079 | 554.5274 | 569.144 | 579.6473 | 585.345 | 591.5755 | 597.2791 | 607.5857 | 620.3778 | 619.4837 | 619.4837 | 619.4837 | 619.4837 | 619.4837 | 619.4837 | 619.4837 | 619.4837 | 619.4837 | 619.4837 | 619.4837 | 619.4837 | 619.4837 | 619.4837 | 619.4837 | 619.4837 |  | 355.8393 | 460.6198 | 488.0361 | 305.4389 | 305.5551 | 308.3659 | 315.7886 | 320.7538 | 325.6169 | 331.3052 | 336.5735 | 341.6904 | 342.2709 | 348.2438 | 343.7086 | 343.7086 | 343.7086 | 343.7086 | 343.7086 | 343.7086 | 343.7086 | 343.7086 | 343.7086 | 343.7086 | 343.7086 | 343.7086 | 343.7086 | 343.7086 | 343.7086 | 343.7086
75% | 1664.3841 | 2209.5776 | 2357.9769 | 1410.2391 | 1410.0798 | 1426.9928 | 1445.5521 | 1483.655 | 1511.0352 | 1525.888 | 1542.1297 | 1556.9981 | 1583.8654 | 1617.2122 | 1614.8813 | 1614.8813 | 1614.8813 | 1614.8813 | 1614.8813 | 1614.8813 | 1614.8813 | 1614.8813 | 1614.8813 | 1614.8813 | 1614.8813 | 1614.8813 | 1614.8813 | 1614.8813 | 1614.8813 | 1614.8813 |  | 635.1192 | 822.1366 | 871.0705 | 545.1621 | 545.3695 | 550.3865 | 563.6347 | 572.497 | 581.1769 | 591.3296 | 600.7327 | 609.8656 | 610.9017 | 621.5623 | 613.4678 | 613.4678 | 613.4678 | 613.4678 | 613.4678 | 613.4678 | 613.4678 | 613.4678 | 613.4678 | 613.4678 | 613.4678 | 613.4678 | 613.4678 | 613.4678 | 613.4678 | 613.4678
70% | 2875.5487 | 3817.4772 | 4073.866 | 2436.4637 | 2436.1885 | 2465.4089 | 2497.4738 | 2563.304 | 2610.6086 | 2636.2697 | 2664.3304 | 2690.0185 | 2736.437 | 2794.0502 | 2790.0231 | 2790.0231 | 2790.0231 | 2790.0231 | 2790.0231 | 2790.0231 | 2790.0231 | 2790.0231 | 2790.0231 | 2790.0231 | 2790.0231 | 2790.0231 | 2790.0231 | 2790.0231 | 2790.0231 | 2790.0231 |  | 1157.0168 | 1497.7123 | 1586.8569 | 993.1392 | 993.517 | 1002.6565 | 1026.7913 | 1042.9359 | 1058.7484 | 1077.244 | 1094.3738 | 1111.0114 | 1112.8991 | 1132.3198 | 1117.5737 | 1117.5737 | 1117.5737 | 1117.5737 | 1117.5737 | 1117.5737 | 1117.5737 | 1117.5737 | 1117.5737 | 1117.5737 | 1117.5737 | 1117.5737 | 1117.5737 | 1117.5737 | 1117.5737 | 1117.5737
65% | 7222.0048 | 9587.679 | 10231.6052 | 6119.2329 | 6118.5417 | 6191.9294 | 6272.4611 | 6437.7952 | 6556.6017 | 6621.05 | 6691.5251 | 6756.0415 | 6872.6224 | 7017.3193 | 7007.2052 | 7007.2052 | 7007.2052 | 7007.2052 | 7007.2052 | 7007.2052 | 7007.2052 | 7007.2052 | 7007.2052 | 7007.2052 | 7007.2052 | 7007.2052 | 7007.2052 | 7007.2052 | 7007.2052 | 7007.2052 |  | 1455.7061 | 1884.3537 | 1996.5114 | 1249.5227 | 1249.998 | 1261.4971 | 1291.8623 | 1312.1747 | 1332.0693 | 1355.3396 | 1376.8916 | 1397.8243 | 1400.1992 | 1424.6335 | 1406.0807 | 1406.0807 | 1406.0807 | 1406.0807 | 1406.0807 | 1406.0807 | 1406.0807 | 1406.0807 | 1406.0807 | 1406.0807 | 1406.0807 | 1406.0807 | 1406.0807 | 1406.0807 | 1406.0807 | 1406.0807
60% | 10556.5772 | 14014.5398 | 14955.7822 | 8944.6291 | 8943.6188 | 9050.8914 | 9168.6065 | 9410.2793 | 9583.9415 | 9678.1472 | 9781.1624 | 9875.4675 | 10045.8766 | 10257.3836 | 10242.5996 | 10242.5996 | 10242.5996 | 10242.5996 | 10242.5996 | 10242.5996 | 10242.5996 | 10242.5996 | 10242.5996 | 10242.5996 | 10242.5996 | 10242.5996 | 10242.5996 | 10242.5996 | 10242.5996 | 10242.5996 |  | 2277.9105 | 2948.6646 | 3124.1707 | 1955.2717 | 1956.0155 | 1974.0093 | 2021.5252 | 2053.3105 | 2084.4417 | 2120.8554 | 2154.5804 | 2187.3361 | 2191.0524 | 2229.2877 | 2200.2559 | 2200.2559 | 2200.2559 | 2200.2559 | 2200.2559 | 2200.2559 | 2200.2559 | 2200.2559 | 2200.2559 | 2200.2559 | 2200.2559 | 2200.2559 | 2200.2559 | 2200.2559 | 2200.2559 | 2200.2559
55% | 11937.0341 | 15847.1857 | 16911.512 | 10114.2956 | 10113.1532 | 10234.4535 | 10367.562 | 10640.8377 | 10837.2093 | 10943.7341 | 11060.2203 | 11166.8574 | 11359.5505 | 11598.7156 | 11581.9984 | 11581.9984 | 11581.9984 | 11581.9984 | 11581.9984 | 11581.9984 | 11581.9984 | 11581.9984 | 11581.9984 | 11581.9984 | 11581.9984 | 11581.9984 | 11581.9984 | 11581.9984 | 11581.9984 | 11581.9984 |  | 4377.3623 | 5666.3214 | 6003.5838 | 3757.3611 | 3758.7904 | 3793.3684 | 3884.6778 | 3945.758 | 4005.5817 | 4075.5563 | 4140.3641 | 4203.3094 | 4210.4508 | 4283.9258 | 4228.1367 | 4228.1367 | 4228.1367 | 4228.1367 | 4228.1367 | 4228.1367 | 4228.1367 | 4228.1367 | 4228.1367 | 4228.1367 | 4228.1367 | 4228.1367 | 4228.1367 | 4228.1367 | 4228.1367 | 4228.1367
50% | 15327.7148 | 20348.5339 | 21715.179 | 12987.2326 | 12985.7657 | 13141.521 | 13312.4386 | 13663.3375 | 13915.4879 | 14052.2707 | 14201.8445 | 14338.7715 | 14586.1986 | 14893.2979 | 14871.8322 | 14871.8322 | 14871.8322 | 14871.8322 | 14871.8322 | 14871.8322 | 14871.8322 | 14871.8322 | 14871.8322 | 14871.8322 | 14871.8322 | 14871.8322 | 14871.8322 | 14871.8322 | 14871.8322 | 14871.8322 |  | 9714.4123 | 12574.9205 | 13323.3863 | 8338.4816 | 8341.6536 | 8418.3903 | 8621.0277 | 8756.5794 | 8889.3424 | 9044.6327 | 9188.4566 | 9328.1474 | 9343.9959 | 9507.0545 | 9383.245 | 9383.245 | 9383.245 | 9383.245 | 9383.245 | 9383.245 | 9383.245 | 9383.245 | 9383.245 | 9383.245 | 9383.245 | 9383.245 | 9383.245 | 9383.245 | 9383.245 | 9383.245
45% | 20411.3174 | 27097.3455 | 28917.2533 | 17294.5889 | 17292.6355 | 17500.0488 | 17727.653 | 18194.9314 | 18530.7102 | 18712.8584 | 18912.04 | 19094.3804 | 19423.8693 | 19832.8215 | 19804.2364 | 19804.2364 | 19804.2364 | 19804.2364 | 19804.2364 | 19804.2364 | 19804.2364 | 19804.2364 | 19804.2364 | 19804.2364 | 19804.2364 | 19804.2364 | 19804.2364 | 19804.2364 | 19804.2364 | 19804.2364 |  | 14720.4239 | 19055.0036 | 20189.1672 | 12635.4514 | 12640.258 | 12756.5385 | 13063.5986 | 13269.0026 | 13470.1806 | 13705.4948 | 13923.4339 | 14135.1097 | 14159.1253 | 14406.2109 | 14218.6002 | 14218.6002 | 14218.6002 | 14218.6002 | 14218.6002 | 14218.6002 | 14218.6002 | 14218.6002 | 14218.6002 | 14218.6002 | 14218.6002 | 14218.6002 | 14218.6002 | 14218.6002 | 14218.6002 | 14218.6002
40% | 14315.8312 | 19005.1929 | 20281.6168 | 12129.8597 | 12128.4896 | 12273.9625 | 12433.5967 | 12761.3304 | 12996.8347 | 13124.5876 | 13264.287 | 13392.1746 | 13623.2674 | 13910.0931 | 13890.0444 | 13890.0444 | 13890.0444 | 13890.0444 | 13890.0444 | 13890.0444 | 13890.0444 | 13890.0444 | 13890.0444 | 13890.0444 | 13890.0444 | 13890.0444 | 13890.0444 | 13890.0444 | 13890.0444 | 13890.0444 |  | 15242.3215 | 19730.5793 | 20904.9535 | 13083.4284 | 13088.4054 | 13208.8086 | 13526.7551 | 13739.4415 | 13947.7521 | 14191.4092 | 14417.075 | 14636.2556 | 14661.1226 | 14916.9684 | 14722.7062 | 14722.7062 | 14722.7062 | 14722.7062 | 14722.7062 | 14722.7062 | 14722.7062 | 14722.7062 | 14722.7062 | 14722.7062 | 14722.7062 | 14722.7062 | 14722.7062 | 14722.7062 | 14722.7062 | 14722.7062
35% | 7422.2532 | 9853.5218 | 10515.3025 | 6288.9042 | 6288.1938 | 6363.6164 | 6446.3811 | 6616.2995 | 6738.4001 | 6804.6355 | 6877.0647 | 6943.3699 | 7063.1834 | 7211.8924 | 7201.4978 | 7201.4978 | 7201.4978 | 7201.4978 | 7201.4978 | 7201.4978 | 7201.4978 | 7201.4978 | 7201.4978 | 7201.4978 | 7201.4978 | 7201.4978 | 7201.4978 | 7201.4978 | 7201.4978 | 7201.4978 |  | 20759.9869 | 26872.9779 | 28472.4713 | 17819.5823 | 17826.3609 | 17990.3496 | 18423.3917 | 18713.0698 | 18996.7881 | 19328.6481 | 19636.0042 | 19934.5274 | 19968.3961 | 20316.8572 | 20052.2727 | 20052.2727 | 20052.2727 | 20052.2727 | 20052.2727 | 20052.2727 | 20052.2727 | 20052.2727 | 20052.2727 | 20052.2727 | 20052.2727 | 20052.2727 | 20052.2727 | 20052.2727 | 20052.2727 | 20052.2727
30% | 3452.1096 | 4582.899 | 4890.695 | 2924.9859 | 2924.6556 | 2959.7348 | 2998.2289 | 3077.2583 | 3134.0477 | 3164.8539 | 3198.5409 | 3229.3797 | 3285.1052 | 3354.2702 | 3349.4357 | 3349.4357 | 3349.4357 | 3349.4357 | 3349.4357 | 3349.4357 | 3349.4357 | 3349.4357 | 3349.4357 | 3349.4357 | 3349.4357 | 3349.4357 | 3349.4357 | 3349.4357 | 3349.4357 | 3349.4357 |  | 19183.5111 | 24832.2926 | 26310.3234 | 16466.3955 | 16472.6594 | 16624.195 | 17024.3526 | 17292.0332 | 17554.2064 | 17860.8655 | 18144.8816 | 18420.7354 | 18452.0323 | 18774.0318 | 18529.5394 | 18529.5394 | 18529.5394 | 18529.5394 | 18529.5394 | 18529.5394 | 18529.5394 | 18529.5394 | 18529.5394 | 18529.5394 | 18529.5394 | 18529.5394 | 18529.5394 | 18529.5394 | 18529.5394 | 18529.5394
25% | 2357.031 | 3129.1112 | 3339.2681 | 1997.1215 | 1996.896 | 2020.8474 | 2047.1303 | 2101.0901 | 2139.8647 | 2160.8986 | 2183.8994 | 2204.9555 | 2243.0037 | 2290.2282 | 2286.9273 | 2286.9273 | 2286.9273 | 2286.9273 | 2286.9273 | 2286.9273 | 2286.9273 | 2286.9273 | 2286.9273 | 2286.9273 | 2286.9273 | 2286.9273 | 2286.9273 | 2286.9273 | 2286.9273 | 2286.9273 |  | 5533.3008 | 7162.6379 | 7588.9618 | 4749.5747 | 4751.3814 | 4795.0905 | 4910.5121 | 4987.722 | 5063.3434 | 5151.7963 | 5233.718 | 5313.2854 | 5322.3127 | 5415.1904 | 5344.6689 | 5344.6689 | 5344.6689 | 5344.6689 | 5344.6689 | 5344.6689 | 5344.6689 | 5344.6689 | 5344.6689 | 5344.6689 | 5344.6689 | 5344.6689 | 5344.6689 | 5344.6689 | 5344.6689 | 5344.6689
20% | 1427.8587 | 1895.5749 | 2022.8852 | 1209.8302 | 1209.6936 | 1224.203 | 1240.1249 | 1272.813 | 1296.3022 | 1309.0442 | 1322.9778 | 1335.7333 | 1358.7825 | 1387.3904 | 1385.3908 | 1385.3908 | 1385.3908 | 1385.3908 | 1385.3908 | 1385.3908 | 1385.3908 | 1385.3908 | 1385.3908 | 1385.3908 | 1385.3908 | 1385.3908 | 1385.3908 | 1385.3908 | 1385.3908 | 1385.3908 |  | 1484.8203 | 1922.0408 | 2036.4417 | 1274.5132 | 1274.998 | 1286.727 | 1317.6995 | 1338.4182 | 1358.7107 | 1382.4464 | 1404.4294 | 1425.7808 | 1428.2032 | 1453.1262 | 1434.2023 | 1434.2023 | 1434.2023 | 1434.2023 | 1434.2023 | 1434.2023 | 1434.2023 | 1434.2023 | 1434.2023 | 1434.2023 | 1434.2023 | 1434.2023 | 1434.2023 | 1434.2023 | 1434.2023 | 1434.2023
15% | 914.1778 | 1213.6303 | 1295.1399 | 774.5864 | 774.4989 | 783.7885 | 793.9824 | 814.9108 | 829.9496 | 838.1076 | 847.0285 | 855.1951 | 869.9522 | 888.2683 | 886.988 | 886.988 | 886.988 | 886.988 | 886.988 | 886.988 | 886.988 | 886.988 | 886.988 | 886.988 | 886.988 | 886.988 | 886.988 | 886.988 | 886.988 | 886.988 |  | 818.9695 | 1060.1234 | 1123.2225 | 702.9722 | 703.2396 | 709.7089 | 726.7922 | 738.2198 | 749.4123 | 762.504 | 774.629 | 786.4056 | 787.7417 | 801.4883 | 791.0506 | 791.0506 | 791.0506 | 791.0506 | 791.0506 | 791.0506 | 791.0506 | 791.0506 | 791.0506 | 791.0506 | 791.0506 | 791.0506 | 791.0506 | 791.0506 | 791.0506 | 791.0506
10% | 611.8703 | 812.2975 | 866.8529 | 518.4401 | 518.3816 | 524.5992 | 531.4221 | 545.4297 | 555.4954 | 560.9556 | 566.9265 | 572.3925 | 582.2696 | 594.5288 | 593.6719 | 593.6719 | 593.6719 | 593.6719 | 593.6719 | 593.6719 | 593.6719 | 593.6719 | 593.6719 | 593.6719 | 593.6719 | 593.6719 | 593.6719 | 593.6719 | 593.6719 | 593.6719 |  | 191.3984 | 247.7576 | 262.5043 | 164.2891 | 164.3516 | 165.8635 | 169.856 | 172.5267 | 175.1424 | 178.2021 | 181.0357 | 183.788 | 184.1003 | 187.3129 | 184.8736 | 184.8736 | 184.8736 | 184.8736 | 184.8736 | 184.8736 | 184.8736 | 184.8736 | 184.8736 | 184.8736 | 184.8736 | 184.8736 | 184.8736 | 184.8736 | 184.8736 | 184.8736
5% | 435.3228 | 577.9192 | 616.7333 | 368.8507 | 368.809 | 373.2326 | 378.0869 | 388.0528 | 395.2141 | 399.0989 | 403.3469 | 407.2358 | 414.263 | 422.9849 | 422.3752 | 422.3752 | 422.3752 | 422.3752 | 422.3752 | 422.3752 | 422.3752 | 422.3752 | 422.3752 | 422.3752 | 422.3752 | 422.3752 | 422.3752 | 422.3752 | 422.3752 | 422.3752 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9.992e-14% | 38.2117 | 50.7285 | 54.1355 | 32.3769 | 32.3732 | 32.7615 | 33.1876 | 34.0624 | 34.691 | 35.032 | 35.4049 | 35.7463 | 36.3631 | 37.1287 | 37.0752 | 37.0752 | 37.0752 | 37.0752 | 37.0752 | 37.0752 | 37.0752 | 37.0752 | 37.0752 | 37.0752 | 37.0752 | 37.0752 | 37.0752 | 37.0752 | 37.0752 | 37.0752 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E @ R (MWh) | 102337.6118 | 135859.8063 | 144984.402 | 86711.0582 | 86701.2643 | 87741.1862 | 88882.3413 | 91225.1664 | 92908.6835 | 93821.9327 | 94820.5828 | 95734.7953 | 97386.7763 | 99437.1676 | 99293.8487 | 99293.8487 | 99293.8487 | 99293.8487 | 99293.8487 | 99293.8487 | 99293.8487 | 99293.8487 | 99293.8487 | 99293.8487 | 99293.8487 | 99293.8487 | 99293.8487 | 99293.8487 | 99293.8487 | 99293.8487 | E @ R (MWh) | 99292.8528 | 128530.651 | 136180.8614 | 85229.2042 | 85261.6256 | 86045.9663 | 88117.1612 | 89502.6616 | 90859.6565 | 92446.9083 | 93916.9604 | 95344.7658 | 95506.7565 | 97173.4094 | 95907.9294 | 95907.9294 | 95907.9294 | 95907.9294 | 95907.9294 | 95907.9294 | 95907.9294 | 95907.9294 | 95907.9294 | 95907.9294 | 95907.9294 | 95907.9294 | 95907.9294 | 95907.9294 | 95907.9294 | 95907.9294
Option 2 Summer POE50 W E @ R (MWh) N 2 | 71636.3283 | 95101.8644 | 101489.0814 | 60697.7407 | 60690.885 | 61418.8303 | 62217.6389 | 63857.6165 | 65036.0784 | 65675.3529 | 66374.4079 | 67014.3567 | 68170.7434 | 69606.0173 | 69505.6941 | 69505.6941 | 69505.6941 | 69505.6941 | 69505.6941 | 69505.6941 | 69505.6941 | 69505.6941 | 69505.6941 | 69505.6941 | 69505.6941 | 69505.6941 | 69505.6941 | 69505.6941 | 69505.6941 | 69505.6941 | Option 2 Summer POE10 W E @ R (MWh) N 2 | 29787.8558 | 38559.1953 | 40854.2584 | 25568.7613 | 25578.4877 | 25813.7899 | 26435.1484 | 26850.7985 | 27257.8969 | 27734.0725 | 28175.0881 | 28603.4297 | 28652.0269 | 29152.0228 | 28772.3788 | 28772.3788 | 28772.3788 | 28772.3788 | 28772.3788 | 28772.3788 | 28772.3788 | 28772.3788 | 28772.3788 | 28772.3788 | 28772.3788 | 28772.3788 | 28772.3788 | 28772.3788 | 28772.3788 | 28772.3788
Option 3 - 2A PHM 3rd Tx + Switchroom + Three new feeders + OFR12 New Feeder
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | 66.5813 | 92.3179 | 99.0036 | 33.2711 | 34.1557 | 35.6839 | 39.1649 | 41.4924 | 44.4438 | 45.9741 | 47.3185 | 44.8292 | 47.7394 | 52.3166 | 48.8374 | 48.8374 | 48.8374 | 48.8374 | 48.8374 | 48.8374 | 48.8374 | 48.8374 | 48.8374 | 48.8374 | 48.8374 | 48.8374 | 48.8374 | 48.8374 | 48.8374 | 48.8374 |  | 71.2634 | 96.6755 | 103.6223 | 37.825 | 38.503 | 39.998 | 43.5335 | 45.4607 | 49.138 | 60.3227 | 51.0944 | 49.287 | 51.719 | 57.0417 | 53.4333 | 53.4333 | 53.4333 | 53.4333 | 53.4333 | 53.4333 | 53.4333 | 53.4333 | 53.4333 | 53.4333 | 53.4333 | 53.4333 | 53.4333 | 53.4333 | 53.4333 | 53.4333
98% | 79.0946 | 109.6681 | 117.6103 | 38.7176 | 39.7684 | 41.5839 | 45.7191 | 48.484 | 51.9901 | 53.808 | 55.405 | 52.4479 | 55.9051 | 61.3424 | 57.2094 | 57.2094 | 57.2094 | 57.2094 | 57.2094 | 57.2094 | 57.2094 | 57.2094 | 57.2094 | 57.2094 | 57.2094 | 57.2094 | 57.2094 | 57.2094 | 57.2094 | 57.2094 |  | 84.6567 | 114.8446 | 123.097 | 44.1273 | 44.9328 | 46.7088 | 50.9087 | 53.1981 | 57.5665 | 70.8532 | 59.8906 | 57.7435 | 60.6326 | 66.9556 | 62.6691 | 62.6691 | 62.6691 | 62.6691 | 62.6691 | 62.6691 | 62.6691 | 62.6691 | 62.6691 | 62.6691 | 62.6691 | 62.6691 | 62.6691 | 62.6691 | 62.6691 | 62.6691
97% | 156.5832 | 217.1095 | 232.8326 | 75.0198 | 77.1001 | 80.6941 | 88.8806 | 94.3542 | 101.2952 | 104.8942 | 108.0557 | 102.2015 | 109.0457 | 119.81 | 111.6278 | 111.6278 | 111.6278 | 111.6278 | 111.6278 | 111.6278 | 111.6278 | 111.6278 | 111.6278 | 111.6278 | 111.6278 | 111.6278 | 111.6278 | 111.6278 | 111.6278 | 111.6278 |  | 167.5944 | 227.3573 | 243.6946 | 85.7293 | 87.3239 | 90.8398 | 99.1544 | 103.6867 | 112.3348 | 138.6385 | 116.9358 | 112.6853 | 118.4048 | 130.9224 | 122.4364 | 122.4364 | 122.4364 | 122.4364 | 122.4364 | 122.4364 | 122.4364 | 122.4364 | 122.4364 | 122.4364 | 122.4364 | 122.4364 | 122.4364 | 122.4364 | 122.4364 | 122.4364
95% | 462.5227 | 641.3081 | 687.7517 | 214.1898 | 220.3346 | 230.9507 | 255.1325 | 271.3005 | 291.8032 | 302.4343 | 311.7729 | 294.4803 | 314.6971 | 346.4933 | 322.3243 | 322.3243 | 322.3243 | 322.3243 | 322.3243 | 322.3243 | 322.3243 | 322.3243 | 322.3243 | 322.3243 | 322.3243 | 322.3243 | 322.3243 | 322.3243 | 322.3243 | 322.3243 |  | 495.0481 | 671.5786 | 719.8364 | 245.8241 | 250.5343 | 260.9198 | 285.4799 | 298.8673 | 324.4126 | 402.1097 | 338.0033 | 325.4479 | 342.3424 | 379.3175 | 354.2513 | 354.2513 | 354.2513 | 354.2513 | 354.2513 | 354.2513 | 354.2513 | 354.2513 | 354.2513 | 354.2513 | 354.2513 | 354.2513 | 354.2513 | 354.2513 | 354.2513 | 354.2513
90% | 2550.165 | 3535.9158 | 3791.9875 | 1080.5129 | 1114.3929 | 1172.926 | 1306.2548 | 1395.3988 | 1508.4422 | 1567.0578 | 1618.5473 | 1523.2029 | 1634.6701 | 1809.9816 | 1676.7232 | 1676.7232 | 1676.7232 | 1676.7232 | 1676.7232 | 1676.7232 | 1676.7232 | 1676.7232 | 1676.7232 | 1676.7232 | 1676.7232 | 1676.7232 | 1676.7232 | 1676.7232 | 1676.7232 | 1676.7232 |  | 2729.4971 | 3702.8155 | 3968.8899 | 1254.9319 | 1280.9021 | 1338.1633 | 1473.5779 | 1547.3909 | 1688.2374 | 2116.6282 | 1763.1711 | 1693.9456 | 1787.0953 | 1990.9607 | 1852.756 | 1852.756 | 1852.756 | 1852.756 | 1852.756 | 1852.756 | 1852.756 | 1852.756 | 1852.756 | 1852.756 | 1852.756 | 1852.756 | 1852.756 | 1852.756 | 1852.756 | 1852.756
85% | 6229.8705 | 8637.9889 | 9263.5537 | 2255.0247 | 2337.7909 | 2480.7832 | 2806.4959 | 3024.2683 | 3300.4252 | 3443.6191 | 3569.4041 | 3336.4846 | 3608.791 | 4037.0643 | 3711.5236 | 3711.5236 | 3711.5236 | 3711.5236 | 3711.5236 | 3711.5236 | 3711.5236 | 3711.5236 | 3711.5236 | 3711.5236 | 3711.5236 | 3711.5236 | 3711.5236 | 3711.5236 | 3711.5236 | 3711.5236 |  | 6667.9659 | 9045.7131 | 9695.7136 | 2681.1178 | 2744.5611 | 2884.4462 | 3215.2542 | 3395.5742 | 3739.652 | 4786.1802 | 3922.7097 | 3753.5967 | 3981.1549 | 4479.1835 | 4141.5593 | 4141.5593 | 4141.5593 | 4141.5593 | 4141.5593 | 4141.5593 | 4141.5593 | 4141.5593 | 4141.5593 | 4141.5593 | 4141.5593 | 4141.5593 | 4141.5593 | 4141.5593 | 4141.5593 | 4141.5593
80% | 9683.0656 | 13425.9956 | 14398.3087 | 2834.7517 | 2963.395 | 3185.6473 | 3691.9015 | 4030.3843 | 4459.614 | 4682.1797 | 4877.6869 | 4515.661 | 4938.906 | 5604.5696 | 5098.5828 | 5098.5828 | 5098.5828 | 5098.5828 | 5098.5828 | 5098.5828 | 5098.5828 | 5098.5828 | 5098.5828 | 5098.5828 | 5098.5828 | 5098.5828 | 5098.5828 | 5098.5828 | 5098.5828 | 5098.5828 |  | 10363.9958 | 14059.7198 | 15070.0133 | 3497.0267 | 3595.6364 | 3813.0593 | 4327.233 | 4607.5037 | 5142.3027 | 6768.9177 | 5426.8286 | 5163.9769 | 5517.6697 | 6291.7539 | 5766.9858 | 5766.9858 | 5766.9858 | 5766.9858 | 5766.9858 | 5766.9858 | 5766.9858 | 5766.9858 | 5766.9858 | 5766.9858 | 5766.9858 | 5766.9858 | 5766.9858 | 5766.9858 | 5766.9858 | 5766.9858
75% | 10683.1238 | 14812.6201 | 15885.3529 | 2292.6645 | 2434.594 | 2679.8003 | 3238.34 | 3611.781 | 4085.3412 | 4330.8933 | 4546.5923 | 4147.1766 | 4614.1339 | 5348.5467 | 4790.3021 | 4790.3021 | 4790.3021 | 4790.3021 | 4790.3021 | 4790.3021 | 4790.3021 | 4790.3021 | 4790.3021 | 4790.3021 | 4790.3021 | 4790.3021 | 4790.3021 | 4790.3021 | 4790.3021 | 4790.3021 |  | 11434.3798 | 15511.7948 | 16626.4305 | 3023.3387 | 3132.1327 | 3372.0108 | 3939.288 | 4248.5048 | 4838.5373 | 6633.1476 | 5152.4488 | 4862.45 | 5252.6719 | 6106.7027 | 5527.7371 | 5527.7371 | 5527.7371 | 5527.7371 | 5527.7371 | 5527.7371 | 5527.7371 | 5527.7371 | 5527.7371 | 5527.7371 | 5527.7371 | 5527.7371 | 5527.7371 | 5527.7371 | 5527.7371 | 5527.7371
70% | 11478.4193 | 15915.3323 | 17067.9236 | 1442.6067 | 1595.102 | 1858.5625 | 2458.6821 | 2859.9236 | 3368.7375 | 3632.5695 | 3864.326 | 3435.1762 | 3936.8958 | 4725.9813 | 4126.1786 | 4126.1786 | 4126.1786 | 4126.1786 | 4126.1786 | 4126.1786 | 4126.1786 | 4126.1786 | 4126.1786 | 4126.1786 | 4126.1786 | 4126.1786 | 4126.1786 | 4126.1786 | 4126.1786 | 4126.1786 |  | 12285.6019 | 16666.5563 | 17864.1701 | 2227.6752 | 2344.5683 | 2602.304 | 3211.8116 | 3544.0477 | 4178.0046 | 6106.2131 | 4515.285 | 4203.6975 | 4622.9692 | 5540.5775 | 4918.5113 | 4918.5113 | 4918.5113 | 4918.5113 | 4918.5113 | 4918.5113 | 4918.5113 | 4918.5113 | 4918.5113 | 4918.5113 | 4918.5113 | 4918.5113 | 4918.5113 | 4918.5113 | 4918.5113 | 4918.5113
65% | 12096.053 | 16771.7086 | 17986.3189 | 341.2438 | 466.0293 | 723.5548 | 1355.9659 | 1778.7974 | 2314.9898 | 2593.0181 | 2837.2451 | 2385.0034 | 2913.7197 | 3745.2644 | 3113.1874 | 3113.1874 | 3113.1874 | 3113.1874 | 3113.1874 | 3113.1874 | 3113.1874 | 3113.1874 | 3113.1874 | 3113.1874 | 3113.1874 | 3113.1874 | 3113.1874 | 3113.1874 | 3113.1874 | 3113.1874 |  | 12946.6687 | 17563.3547 | 18825.4101 | 1112.5289 | 1235.7118 | 1507.3158 | 2149.6199 | 2499.7331 | 3167.8021 | 5199.7642 | 3523.231 | 3194.8775 | 3636.7094 | 4603.6927 | 3948.1542 | 3948.1542 | 3948.1542 | 3948.1542 | 3948.1542 | 3948.1542 | 3948.1542 | 3948.1542 | 3948.1542 | 3948.1542 | 3948.1542 | 3948.1542 | 3948.1542 | 3948.1542 | 3948.1542 | 3948.1542
60% | 13316.2645 | 18463.5854 | 19800.7217 |  |  | 0.48365 | 171.9766 | 449.1607 | 971.385 | 1277.46 | 1546.3238 | 1048.4614 | 1630.5129 | 2545.9413 | 1850.1024 | 1850.1024 | 1850.1024 | 1850.1024 | 1850.1024 | 1850.1024 | 1850.1024 | 1850.1024 | 1850.1024 | 1850.1024 | 1850.1024 | 1850.1024 | 1850.1024 | 1850.1024 | 1850.1024 | 1850.1024 |  | 14252.6876 | 19335.0902 | 20724.4577 | 70.264 | 116.2969 | 256.8306 | 791.8285 | 1174.7647 | 1910.2264 | 4147.1663 | 2301.5098 | 1940.033 | 2426.4356 | 3490.9651 | 2769.2979 | 2769.2979 | 2769.2979 | 2769.2979 | 2769.2979 | 2769.2979 | 2769.2979 | 2769.2979 | 2769.2979 | 2769.2979 | 2769.2979 | 2769.2979 | 2769.2979 | 2769.2979 | 2769.2979 | 2769.2979
55% | 14813.5078 | 20539.579 | 22027.0592 | [5 empty] | 2.2205 | 47.0164 | 132.5181 | 8.1139 | 167.9103 | 803.9778 | 279.088 | 279.088 | 279.088 | 279.088 | 279.088 | 279.088 | 279.088 | 279.088 | 279.088 | 279.088 | 279.088 | 279.088 | 279.088 | 279.088 | 279.088 | 279.088 |  | 15855.2197 | 21509.0734 | 23054.6574 |  |  |  |  | 25.6474 | 314.2101 | 2553.8762 | 590.5515 | 332.3582 | 695.7965 | 1823.8935 | 1025.4557 | 1025.4557 | 1025.4557 | 1025.4557 | 1025.4557 | 1025.4557 | 1025.4557 | 1025.4557 | 1025.4557 | 1025.4557 | 1025.4557 | 1025.4557 | 1025.4557 | 1025.4557 | 1025.4557 | 1025.4557
50% | FY25: 15014.9247; FY26: 20818.8523; FY27: 22326.5575 |  | 16070.8005 | 21801.5288 | 23368.1279 | [6 empty] | 395.1133 |  |  |  | 90.5185
45% | FY25: 11588.8305; FY26: 16068.4223; FY27: 17232.1005 |  | 12403.7774 | 16826.8724 | 18036.0061
40% | FY25: 5693.5395; FY26: 7894.3425; FY27: 8466.0523 |  | 6093.9192 | 8266.9656 | 8861.0075
35% | FY25: 2127.9257; FY26: 2950.4624; FY27: 3164.1354 |  | 2277.5652 | 3089.728 | 3311.7475
30% | FY25: 1061.2862; FY26: 1471.5199; FY27: 1578.0877 |  | 1135.9177 | 1540.9775 | 1651.708
25% | FY25: 625.6637; FY26: 867.5102; FY27: 930.3354 |  | 669.6615 | 908.4578 | 973.7371
20% | FY25: 316.1776; FY26: 438.3942; FY27: 470.1428 |  | 338.4118 | 459.0869 | 492.0757
15% | FY25: 128.8131; FY26: 178.605; FY27: 191.5396 |  | 137.8715 | 187.0354 | 200.4753
10% | FY25: 51.8598; FY26: 71.9059; FY27: 77.1134 |  | 55.5067 | 75.3 | 80.7108
5% | FY25: 44.1645; FY26: 61.236; FY27: 65.6707 |  | 47.2702 | 64.1264 | 68.7344
9.992e-14% | FY25: 0; FY26: 0; FY27: 0 |  | 0 | 0 | 0
E @ R (MWh) | 118268.4368 | 163984.3799 | 175860.1598 | 10608.0025 | 11282.6629 | 12490.6702 | 15458.514 | 17605.3449 | 20500.6875 | 22080.9247 | 23515.1957 | 20893.2388 | 23972.9271 | 29201.2892 | 25185.6869 | 25185.6869 | 25185.6869 | 25185.6869 | 25185.6869 | 25185.6869 | 25185.6869 | 25185.6869 | 25185.6869 | 25185.6869 | 25185.6869 | 25185.6869 | 25185.6869 | 25185.6869 | 25185.6869 | 25185.6869 | E @ R (MWh) | 126585.2808 | 171724.6525 | 184064.3234 | 14280.3887 | 14871.1032 | 16212.5964 | 19587.6896 | 21544.3792 | 25522.4245 | 39378.9311 | 27761.6594 | 25690.0991 | 28493.6014 | 35052.4853 | 30543.2476 | 30543.2476 | 30543.2476 | 30543.2476 | 30543.2476 | 30543.2476 | 30543.2476 | 30543.2476 | 30543.2476 | 30543.2476 | 30543.2476 | 30543.2476 | 30543.2476 | 30543.2476 | 30543.2476 | 30543.2476
Option 3 Winter POE50 W E @ R (MWh) N 2 | 82787.9057 | 114789.066 | 123102.1118 | 7425.6018 | 7897.864 | 8743.4692 | 10820.9598 | 12323.7415 | 14350.4812 | 15456.6473 | 16460.637 | 14625.2671 | 16781.0489 | 20440.9025 | 17629.9808 | 17629.9808 | 17629.9808 | 17629.9808 | 17629.9808 | 17629.9808 | 17629.9808 | 17629.9808 | 17629.9808 | 17629.9808 | 17629.9808 | 17629.9808 | 17629.9808 | 17629.9808 | 17629.9808 | 17629.9808 | Option 3 Winter POE10 W E @ R (MWh) N 2 | 37975.5842 | 51517.3957 | 55219.297 | 4284.1166 | 4461.331 | 4863.7789 | 5876.3069 | 6463.3138 | 7656.7273 | 11813.6793 | 8328.4978 | 7707.0297 | 8548.0804 | 10515.7456 | 9162.9743 | 9162.9743 | 9162.9743 | 9162.9743 | 9162.9743 | 9162.9743 | 9162.9743 | 9162.9743 | 9162.9743 | 9162.9743 | 9162.9743 | 9162.9743 | 9162.9743 | 9162.9743 | 9162.9743 | 9162.9743
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 85.8327 | 111.1071 | 117.7202 | 49.2537 | 49.2817 | 49.9598 | 51.7502 | 52.9479 | 54.1209 | 55.493 | 56.7638 | 57.998 | 58.138 | 59.5788 | 58.4848 | 58.4848 | 58.4848 | 58.4848 | 58.4848 | 58.4848 | 58.4848 | 58.4848 | 58.4848 | 58.4848 | 58.4848 | 58.4848 | 58.4848 | 58.4848 | 58.4848 | 58.4848
98% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 42.4851 | 54.9952 | 58.2686 | 24.0373 | 24.0512 | 24.3868 | 25.273 | 25.8658 | 26.4464 | 27.1256 | 27.7546 | 28.3655 | 28.4348 | 29.1479 | 28.6065 | 28.6065 | 28.6065 | 28.6065 | 28.6065 | 28.6065 | 28.6065 | 28.6065 | 28.6065 | 28.6065 | 28.6065 | 28.6065 | 28.6065 | 28.6065 | 28.6065 | 28.6065
97% | 18.864 | 25.0432 | 26.7251 | 9.6587 | 9.6569 | 9.8486 | 10.059 | 10.4908 | 10.8011 | 10.9695 | 11.1536 | 11.3221 | 11.6266 | 12.0045 | 11.9781 | 11.9781 | 11.9781 | 11.9781 | 11.9781 | 11.9781 | 11.9781 | 11.9781 | 11.9781 | 11.9781 | 11.9781 | 11.9781 | 11.9781 | 11.9781 | 11.9781 | 11.9781 |  | 84.1075 | 108.8738 | 115.354 | 46.8955 | 46.9229 | 47.5873 | 49.3417 | 50.5154 | 51.6648 | 53.0093 | 54.2545 | 55.464 | 55.6012 | 57.013 | 55.941 | 55.941 | 55.941 | 55.941 | 55.941 | 55.941 | 55.941 | 55.941 | 55.941 | 55.941 | 55.941 | 55.941 | 55.941 | 55.941 | 55.941 | 55.941
95% | 92.8689 | 123.2894 | 131.5698 | 46.2417 | 46.2328 | 47.1765 | 48.212 | 50.3381 | 51.8658 | 52.6946 | 53.6008 | 54.4305 | 55.9296 | 57.7903 | 57.6602 | 57.6602 | 57.6602 | 57.6602 | 57.6602 | 57.6602 | 57.6602 | 57.6602 | 57.6602 | 57.6602 | 57.6602 | 57.6602 | 57.6602 | 57.6602 | 57.6602 | 57.6602 |  | 124.2203 | 160.7982 | 170.369 | 67.6901 | 67.7307 | 68.712 | 71.3031 | 73.0364 | 74.7341 | 76.7198 | 78.559 | 80.3452 | 80.5479 | 82.6329 | 81.0498 | 81.0498 | 81.0498 | 81.0498 | 81.0498 | 81.0498 | 81.0498 | 81.0498 | 81.0498 | 81.0498 | 81.0498 | 81.0498 | 81.0498 | 81.0498 | 81.0498 | 81.0498
90% | 161.0694 | 213.8301 | 228.1913 | 74.6165 | 74.6011 | 76.2379 | 78.0339 | 81.7213 | 84.371 | 85.8084 | 87.3801 | 88.819 | 91.4191 | 94.6462 | 94.4206 | 94.4206 | 94.4206 | 94.4206 | 94.4206 | 94.4206 | 94.4206 | 94.4206 | 94.4206 | 94.4206 | 94.4206 | 94.4206 | 94.4206 | 94.4206 | 94.4206 | 94.4206 |  | 538.6113 | 697.2109 | 738.7092 | 276.7487 | 276.9246 | 281.1792 | 292.4144 | 299.93 | 307.291 | 315.901 | 323.8752 | 331.6203 | 332.499 | 341.5397 | 334.6752 | 334.6752 | 334.6752 | 334.6752 | 334.6752 | 334.6752 | 334.6752 | 334.6752 | 334.6752 | 334.6752 | 334.6752 | 334.6752 | 334.6752 | 334.6752 | 334.6752 | 334.6752
85% | 457.0889 | 606.8151 | 647.57 | 186.9134 | 186.8697 | 191.5145 | 196.6114 | 207.0756 | 214.595 | 218.674 | 223.1344 | 227.2178 | 234.5963 | 243.7543 | 243.1142 | 243.1142 | 243.1142 | 243.1142 | 243.1142 | 243.1142 | 243.1142 | 243.1142 | 243.1142 | 243.1142 | 243.1142 | 243.1142 | 243.1142 | 243.1142 | 243.1142 | 243.1142 |  | 509.4971 | 659.5238 | 698.779 | 236.9532 | 237.1195 | 241.1442 | 251.772 | 258.8814 | 265.8444 | 273.989 | 281.5323 | 288.8587 | 289.6899 | 298.2419 | 291.7484 | 291.7484 | 291.7484 | 291.7484 | 291.7484 | 291.7484 | 291.7484 | 291.7484 | 291.7484 | 291.7484 | 291.7484 | 291.7484 | 291.7484 | 291.7484 | 291.7484 | 291.7484
80% | 638.4734 | 847.6148 | 904.5422 | 222.1885 | 222.1274 | 228.6154 | 235.7349 | 250.3515 | 260.8548 | 266.5525 | 272.783 | 278.4866 | 288.7932 | 301.5853 | 300.6912 | 300.6912 | 300.6912 | 300.6912 | 300.6912 | 300.6912 | 300.6912 | 300.6912 | 300.6912 | 300.6912 | 300.6912 | 300.6912 | 300.6912 | 300.6912 | 300.6912 | 300.6912 |  | 355.8393 | 460.6198 | 488.0361 | 146.0426 | 146.1588 | 148.9697 | 156.3923 | 161.3576 | 166.2207 | 171.909 | 177.1773 | 182.2941 | 182.8747 | 188.8475 | 184.3124 | 184.3124 | 184.3124 | 184.3124 | 184.3124 | 184.3124 | 184.3124 | 184.3124 | 184.3124 | 184.3124 | 184.3124 | 184.3124 | 184.3124 | 184.3124 | 184.3124 | 184.3124
75% | 1664.3841 | 2209.5776 | 2357.9769 | 464.7244 | 464.5651 | 481.4781 | 500.0374 | 538.1403 | 565.5205 | 580.3733 | 596.615 | 611.4834 | 638.3507 | 671.6975 | 669.3666 | 669.3666 | 669.3666 | 669.3666 | 669.3666 | 669.3666 | 669.3666 | 669.3666 | 669.3666 | 669.3666 | 669.3666 | 669.3666 | 669.3666 | 669.3666 | 669.3666 | 669.3666 |  | 635.1192 | 822.1366 | 871.0705 | 221.4724 | 221.6798 | 226.6968 | 239.945 | 248.8073 | 257.4872 | 267.6399 | 277.043 | 286.1758 | 287.212 | 297.8726 | 289.7781 | 289.7781 | 289.7781 | 289.7781 | 289.7781 | 289.7781 | 289.7781 | 289.7781 | 289.7781 | 289.7781 | 289.7781 | 289.7781 | 289.7781 | 289.7781 | 289.7781 | 289.7781
70% | 2875.5487 | 3817.4772 | 4073.866 | 577.8335 | 577.5583 | 606.7787 | 638.8436 | 704.6738 | 751.9784 | 777.6395 | 805.7002 | 831.3883 | 877.8068 | 935.42 | 931.3929 | 931.3929 | 931.3929 | 931.3929 | 931.3929 | 931.3929 | 931.3929 | 931.3929 | 931.3929 | 931.3929 | 931.3929 | 931.3929 | 931.3929 | 931.3929 | 931.3929 | 931.3929 |  | 1157.0168 | 1497.7123 | 1586.8569 | 322.219 | 322.5968 | 331.7364 | 355.8711 | 372.0158 | 387.8282 | 406.3238 | 423.4537 | 440.0913 | 441.9789 | 461.3997 | 446.6536 | 446.6536 | 446.6536 | 446.6536 | 446.6536 | 446.6536 | 446.6536 | 446.6536 | 446.6536 | 446.6536 | 446.6536 | 446.6536 | 446.6536 | 446.6536 | 446.6536 | 446.6536
65% | 7222.0048 | 9587.679 | 10231.6052 | 802.2336 | 801.5424 | 874.9301 | 955.4618 | 1120.7959 | 1239.6024 | 1304.0507 | 1374.5258 | 1439.0422 | 1555.6231 | 1700.32 | 1690.2059 | 1690.2059 | 1690.2059 | 1690.2059 | 1690.2059 | 1690.2059 | 1690.2059 | 1690.2059 | 1690.2059 | 1690.2059 | 1690.2059 | 1690.2059 | 1690.2059 | 1690.2059 | 1690.2059 | 1690.2059 |  | 1455.7061 | 1884.3537 | 1996.5114 | 288.04 | 288.5153 | 300.0144 | 330.3796 | 350.692 | 370.5866 | 393.8569 | 415.4089 | 436.3416 | 438.7165 | 463.1508 | 444.598 | 444.598 | 444.598 | 444.598 | 444.598 | 444.598 | 444.598 | 444.598 | 444.598 | 444.598 | 444.598 | 444.598 | 444.598 | 444.598 | 444.598 | 444.598
60% | 10556.5772 | 14014.5398 | 14955.7822 | 187.5582 | 186.9825 | 252.8081 | 335.7847 | 540.3015 | 711.4984 | 805.7041 | 908.7192 | 1003.0243 | 1173.4335 | 1384.9404 | 1370.1564 | 1370.1564 | 1370.1564 | 1370.1564 | 1370.1564 | 1370.1564 | 1370.1564 | 1370.1564 | 1370.1564 | 1370.1564 | 1370.1564 | 1370.1564 | 1370.1564 | 1370.1564 | 1370.1564 | 1370.1564 |  | 2277.9105 | 2948.6646 | 3124.1707 | 237.6968 | 238.4405 | 256.4344 | 303.9503 | 335.7356 | 366.8668 | 403.2805 | 437.0055 | 469.7612 | 473.4775 | 511.7128 | 482.681 | 482.681 | 482.681 | 482.681 | 482.681 | 482.681 | 482.681 | 482.681 | 482.681 | 482.681 | 482.681 | 482.681 | 482.681 | 482.681 | 482.681 | 482.681
55% | 11937.0341 | 15847.1857 | 16911.512 | [5 empty] | 3.8903 | 15.7556 | 37.6919 | 65.8304 | 135.7599 | 255.725 | 246.1724 | 246.1724 | 246.1724 | 246.1724 | 246.1724 | 246.1724 | 246.1724 | 246.1724 | 246.1724 | 246.1724 | 246.1724 | 246.1724 | 246.1724 | 246.1724 | 246.1724 | 246.1724 |  | 4377.3623 | 5666.3214 | 6003.5838 | 53.6808 | 54.3475 | 71.6739 | 128.262 | 174.6238 | 226.4176 | 294.3956 | 359.2034 | 422.1487 | 429.2901 | 502.7651 | 446.976 | 446.976 | 446.976 | 446.976 | 446.976 | 446.976 | 446.976 | 446.976 | 446.976 | 446.976 | 446.976 | 446.976 | 446.976 | 446.976 | 446.976 | 446.976
50% | FY25: 15327.7148; FY26: 20348.5339; FY27: 21715.179 |  | 9714.4123 | 12574.9205 | 13323.3863 | [6 empty] | 0.92441 | 14.9076 | 44.2124 | 48.4954 | 103.6497 | 59.9312 | 59.9312 | 59.9312 | 59.9312 | 59.9312 | 59.9312 | 59.9312 | 59.9312 | 59.9312 | 59.9312 | 59.9312 | 59.9312 | 59.9312 | 59.9312 | 59.9312 | 59.9312
45% | FY25: 20411.3174; FY26: 27097.3455; FY27: 28917.2533 |  | 14720.4239 | 19055.0036 | 20189.1672
40% | FY25: 14315.8312; FY26: 19005.1929; FY27: 20281.6168 |  | 15242.3215 | 19730.5793 | 20904.9535
35% | FY25: 7422.2532; FY26: 9853.5218; FY27: 10515.3025 |  | 20759.9869 | 26872.9779 | 28472.4713
30% | FY25: 3452.1096; FY26: 4582.899; FY27: 4890.695 |  | 19183.5111 | 24832.2926 | 26310.3234
25% | FY25: 2357.031; FY26: 3129.1112; FY27: 3339.2681 |  | 5533.3008 | 7162.6379 | 7588.9618
20% | FY25: 1427.8587; FY26: 1895.5749; FY27: 2022.8852 |  | 1484.8203 | 1922.0408 | 2036.4417
15% | FY25: 914.1778; FY26: 1213.6303; FY27: 1295.1399 |  | 818.9695 | 1060.1234 | 1123.2225
10% | FY25: 611.8703; FY26: 812.2975; FY27: 866.8529 |  | 191.3984 | 247.7576 | 262.5043
5% | FY25: 435.3228; FY26: 577.9192; FY27: 616.7333 |  | 0 | 0 | 0
9.992e-14% | FY25: 38.2117; FY26: 50.7285; FY27: 54.1355 |  | 0 | 0 | 0
E @ R (MWh) | 102337.6118 | 135859.8063 | 144984.402 | 2571.9686 | 2570.1362 | 2769.3877 | 2998.7788 | 3503.8889 | 3894.9777 | 4118.2221 | 4371.3041 | 4611.0446 | 5063.3387 | 5657.8836 | 5615.1586 | 5615.1586 | 5615.1586 | 5615.1586 | 5615.1586 | 5615.1586 | 5615.1586 | 5615.1586 | 5615.1586 | 5615.1586 | 5615.1586 | 5615.1586 | 5615.1586 | 5615.1586 | 5615.1586 | 5615.1586 | E @ R (MWh) | 99292.8528 | 128530.651 | 136180.8614 | 1970.7302 | 1973.7695 | 2048.4946 | 2256.6548 | 2404.4088 | 2555.5088 | 2740.5678 | 2926.9386 | 3123.6769 | 3146.9559 | 3397.5525 | 3205.4359 | 3205.4359 | 3205.4359 | 3205.4359 | 3205.4359 | 3205.4359 | 3205.4359 | 3205.4359 | 3205.4359 | 3205.4359 | 3205.4359 | 3205.4359 | 3205.4359 | 3205.4359 | 3205.4359 | 3205.4359
Option 3 Summer POE50 W E @ R (MWh) N 2 | 71636.3283 | 95101.8644 | 101489.0814 | 1800.378 | 1799.0954 | 1938.5714 | 2099.1452 | 2452.7222 | 2726.4844 | 2882.7555 | 3059.9129 | 3227.7312 | 3544.3371 | 3960.5185 | 3930.611 | 3930.611 | 3930.611 | 3930.611 | 3930.611 | 3930.611 | 3930.611 | 3930.611 | 3930.611 | 3930.611 | 3930.611 | 3930.611 | 3930.611 | 3930.611 | 3930.611 | 3930.611 | Option 3 Summer POE10 W E @ R (MWh) N 2 | 29787.8558 | 38559.1953 | 40854.2584 | 591.2191 | 592.1308 | 614.5484 | 676.9964 | 721.3226 | 766.6526 | 822.1703 | 878.0816 | 937.1031 | 944.0868 | 1019.2657 | 961.6308 | 961.6308 | 961.6308 | 961.6308 | 961.6308 | 961.6308 | 961.6308 | 961.6308 | 961.6308 | 961.6308 | 961.6308 | 961.6308 | 961.6308 | 961.6308 | 961.6308 | 961.6308
Option 4 - 3A OFR 3rd Tx + Switchroom + Three new feeders + OFR12 New Feeder
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | 66.5813 | 92.3179 | 99.0036 | 78.7016 | 79.5862 | 81.1144 | 84.5954 | 86.9229 | 89.8743 | 91.4047 | 92.749 | 90.2597 | 93.1699 | 97.7471 | 94.2679 | 94.2679 | 94.2679 | 94.2679 | 94.2679 | 94.2679 | 94.2679 | 94.2679 | 94.2679 | 94.2679 | 94.2679 | 94.2679 | 94.2679 | 94.2679 | 94.2679 | 94.2679 |  | 71.2634 | 96.6755 | 103.6223 | 83.2555 | 83.9335 | 85.4285 | 88.964 | 90.8912 | 94.5685 | 105.7532 | 96.5249 | 94.7175 | 97.1495 | 102.4722 | 98.8638 | 98.8638 | 98.8638 | 98.8638 | 98.8638 | 98.8638 | 98.8638 | 98.8638 | 98.8638 | 98.8638 | 98.8638 | 98.8638 | 98.8638 | 98.8638 | 98.8638 | 98.8638
98% | 79.0946 | 109.6681 | 117.6103 | 93.4928 | 94.5436 | 96.359 | 100.4943 | 103.2591 | 106.7652 | 108.5832 | 110.1802 | 107.223 | 110.6802 | 116.1176 | 111.9845 | 111.9845 | 111.9845 | 111.9845 | 111.9845 | 111.9845 | 111.9845 | 111.9845 | 111.9845 | 111.9845 | 111.9845 | 111.9845 | 111.9845 | 111.9845 | 111.9845 | 111.9845 |  | 84.6567 | 114.8446 | 123.097 | 98.9025 | 99.708 | 101.4839 | 105.6839 | 107.9732 | 112.3417 | 125.6284 | 114.6658 | 112.5187 | 115.4078 | 121.7308 | 117.4443 | 117.4443 | 117.4443 | 117.4443 | 117.4443 | 117.4443 | 117.4443 | 117.4443 | 117.4443 | 117.4443 | 117.4443 | 117.4443 | 117.4443 | 117.4443 | 117.4443 | 117.4443
97% | 156.5832 | 217.1095 | 232.8326 | 185.0873 | 187.1675 | 190.7615 | 198.9481 | 204.4216 | 211.3626 | 214.9617 | 218.1232 | 212.269 | 219.1132 | 229.8775 | 221.6953 | 221.6953 | 221.6953 | 221.6953 | 221.6953 | 221.6953 | 221.6953 | 221.6953 | 221.6953 | 221.6953 | 221.6953 | 221.6953 | 221.6953 | 221.6953 | 221.6953 | 221.6953 |  | 167.5944 | 227.3573 | 243.6946 | 195.7968 | 197.3914 | 200.9073 | 209.2219 | 213.7541 | 222.4023 | 248.706 | 227.0033 | 222.7528 | 228.4723 | 240.9899 | 232.5039 | 232.5039 | 232.5039 | 232.5039 | 232.5039 | 232.5039 | 232.5039 | 232.5039 | 232.5039 | 232.5039 | 232.5039 | 232.5039 | 232.5039 | 232.5039 | 232.5039 | 232.5039
95% | 462.5227 | 641.3081 | 687.7517 | 546.7193 | 552.8641 | 563.4802 | 587.662 | 603.8301 | 624.3327 | 634.9638 | 644.3024 | 627.0098 | 647.2266 | 679.0228 | 654.8538 | 654.8538 | 654.8538 | 654.8538 | 654.8538 | 654.8538 | 654.8538 | 654.8538 | 654.8538 | 654.8538 | 654.8538 | 654.8538 | 654.8538 | 654.8538 | 654.8538 | 654.8538 |  | 495.0481 | 671.5786 | 719.8364 | 578.3536 | 583.0638 | 593.4493 | 618.0094 | 631.3968 | 656.9421 | 734.6392 | 670.5328 | 657.9774 | 674.8719 | 711.847 | 686.7808 | 686.7808 | 686.7808 | 686.7808 | 686.7808 | 686.7808 | 686.7808 | 686.7808 | 686.7808 | 686.7808 | 686.7808 | 686.7808 | 686.7808 | 686.7808 | 686.7808 | 686.7808
90% | 2550.165 | 3535.9158 | 3791.9875 | 3014.3912 | 3048.2712 | 3106.8043 | 3240.1331 | 3329.2771 | 3442.3205 | 3500.9362 | 3552.4256 | 3457.0812 | 3568.5484 | 3743.8599 | 3610.6015 | 3610.6015 | 3610.6015 | 3610.6015 | 3610.6015 | 3610.6015 | 3610.6015 | 3610.6015 | 3610.6015 | 3610.6015 | 3610.6015 | 3610.6015 | 3610.6015 | 3610.6015 | 3610.6015 | 3610.6015 |  | 2729.4971 | 3702.8155 | 3968.8899 | 3188.8102 | 3214.7804 | 3272.0416 | 3407.4562 | 3481.2692 | 3622.1157 | 4050.5066 | 3697.0494 | 3627.8239 | 3720.9736 | 3924.8391 | 3786.6344 | 3786.6344 | 3786.6344 | 3786.6344 | 3786.6344 | 3786.6344 | 3786.6344 | 3786.6344 | 3786.6344 | 3786.6344 | 3786.6344 | 3786.6344 | 3786.6344 | 3786.6344 | 3786.6344 | 3786.6344
85% | 6229.8705 | 8637.9889 | 9263.5537 | 7363.9418 | 7446.7081 | 7589.7003 | 7915.4131 | 8133.1854 | 8409.3424 | 8552.5362 | 8678.3212 | 8445.4017 | 8717.7082 | 9145.9815 | 8820.4408 | 8820.4408 | 8820.4408 | 8820.4408 | 8820.4408 | 8820.4408 | 8820.4408 | 8820.4408 | 8820.4408 | 8820.4408 | 8820.4408 | 8820.4408 | 8820.4408 | 8820.4408 | 8820.4408 | 8820.4408 |  | 6667.9659 | 9045.7131 | 9695.7136 | 7790.0349 | 7853.4782 | 7993.3633 | 8324.1714 | 8504.4913 | 8848.5692 | 9895.0973 | 9031.6269 | 8862.5139 | 9090.072 | 9588.1007 | 9250.4765 | 9250.4765 | 9250.4765 | 9250.4765 | 9250.4765 | 9250.4765 | 9250.4765 | 9250.4765 | 9250.4765 | 9250.4765 | 9250.4765 | 9250.4765 | 9250.4765 | 9250.4765 | 9250.4765 | 9250.4765
80% | 9683.0656 | 13425.9956 | 14398.3087 | 11445.7487 | 11574.392 | 11796.6443 | 12302.8985 | 12641.3813 | 13070.611 | 13293.1768 | 13488.6839 | 13126.658 | 13549.903 | 14215.5666 | 13709.5798 | 13709.5798 | 13709.5798 | 13709.5798 | 13709.5798 | 13709.5798 | 13709.5798 | 13709.5798 | 13709.5798 | 13709.5798 | 13709.5798 | 13709.5798 | 13709.5798 | 13709.5798 | 13709.5798 | 13709.5798 |  | 10363.9958 | 14059.7198 | 15070.0133 | 12108.0237 | 12206.6334 | 12424.0563 | 12938.2301 | 13218.5008 | 13753.2997 | 15379.9147 | 14037.8256 | 13774.9739 | 14128.6668 | 14902.7509 | 14377.9828 | 14377.9828 | 14377.9828 | 14377.9828 | 14377.9828 | 14377.9828 | 14377.9828 | 14377.9828 | 14377.9828 | 14377.9828 | 14377.9828 | 14377.9828 | 14377.9828 | 14377.9828 | 14377.9828 | 14377.9828
75% | 10683.1238 | 14812.6201 | 15885.3529 | 12627.8551 | 12769.7846 | 13014.991 | 13573.5306 | 13946.9716 | 14420.5318 | 14666.0839 | 14881.7829 | 14482.3672 | 14949.3246 | 15683.7373 | 15125.4927 | 15125.4927 | 15125.4927 | 15125.4927 | 15125.4927 | 15125.4927 | 15125.4927 | 15125.4927 | 15125.4927 | 15125.4927 | 15125.4927 | 15125.4927 | 15125.4927 | 15125.4927 | 15125.4927 | 15125.4927 |  | 11434.3798 | 15511.7948 | 16626.4305 | 13358.5293 | 13467.3233 | 13707.2015 | 14274.4786 | 14583.6954 | 15173.7279 | 16968.3383 | 15487.6394 | 15197.6406 | 15587.8625 | 16441.8934 | 15862.9277 | 15862.9277 | 15862.9277 | 15862.9277 | 15862.9277 | 15862.9277 | 15862.9277 | 15862.9277 | 15862.9277 | 15862.9277 | 15862.9277 | 15862.9277 | 15862.9277 | 15862.9277 | 15862.9277 | 15862.9277
70% | 11478.4193 | 15915.3323 | 17067.9236 | 13567.9244 | 13720.4197 | 13983.8802 | 14583.9998 | 14985.2413 | 15494.0552 | 15757.8873 | 15989.6438 | 15560.4939 | 16062.2135 | 16851.299 | 16251.4963 | 16251.4963 | 16251.4963 | 16251.4963 | 16251.4963 | 16251.4963 | 16251.4963 | 16251.4963 | 16251.4963 | 16251.4963 | 16251.4963 | 16251.4963 | 16251.4963 | 16251.4963 | 16251.4963 | 16251.4963 |  | 12285.6019 | 16666.5563 | 17864.1701 | 14352.9929 | 14469.886 | 14727.6217 | 15337.1293 | 15669.3654 | 16303.3224 | 18231.5309 | 16640.6027 | 16329.0152 | 16748.2869 | 17665.8953 | 17043.829 | 17043.829 | 17043.829 | 17043.829 | 17043.829 | 17043.829 | 17043.829 | 17043.829 | 17043.829 | 17043.829 | 17043.829 | 17043.829 | 17043.829 | 17043.829 | 17043.829 | 17043.829
65% | 12096.053 | 16771.7086 | 17986.3189 | 14297.9908 | 14458.6916 | 14736.3285 | 15368.7395 | 15791.571 | 16327.7634 | 16605.7918 | 16850.0187 | 16397.7771 | 16926.4933 | 17758.0381 | 17125.9611 | 17125.9611 | 17125.9611 | 17125.9611 | 17125.9611 | 17125.9611 | 17125.9611 | 17125.9611 | 17125.9611 | 17125.9611 | 17125.9611 | 17125.9611 | 17125.9611 | 17125.9611 | 17125.9611 | 17125.9611 |  | 12946.6687 | 17563.3547 | 18825.4101 | 15125.3025 | 15248.4854 | 15520.0894 | 16162.3935 | 16512.5067 | 17180.5758 | 19212.5378 | 17536.0046 | 17207.6511 | 17649.4831 | 18616.4664 | 17960.9278 | 17960.9278 | 17960.9278 | 17960.9278 | 17960.9278 | 17960.9278 | 17960.9278 | 17960.9278 | 17960.9278 | 17960.9278 | 17960.9278 | 17960.9278 | 17960.9278 | 17960.9278 | 17960.9278 | 17960.9278
60% | 13316.2645 | 18463.5854 | 19800.7217 | 15740.3268 | 15917.2386 | 16222.8826 | 16919.0892 | 17384.5747 | 17974.8564 | 18280.9314 | 18549.7951 | 18051.9328 | 18633.9843 | 19549.4126 | 18853.5737 | 18853.5737 | 18853.5737 | 18853.5737 | 18853.5737 | 18853.5737 | 18853.5737 | 18853.5737 | 18853.5737 | 18853.5737 | 18853.5737 | 18853.5737 | 18853.5737 | 18853.5737 | 18853.5737 | 18853.5737 |  | 14252.6876 | 19335.0902 | 20724.4577 | 16651.0951 | 16786.7043 | 17085.7068 | 17792.8045 | 18178.2361 | 18913.6978 | 21150.6377 | 19304.9811 | 18943.5044 | 19429.9069 | 20494.4365 | 19772.7693 | 19772.7693 | 19772.7693 | 19772.7693 | 19772.7693 | 19772.7693 | 19772.7693 | 19772.7693 | 19772.7693 | 19772.7693 | 19772.7693 | 19772.7693 | 19772.7693 | 19772.7693 | 19772.7693 | 19772.7693
55% | 14813.5078 | 20539.579 | 22027.0592 | 17510.1248 | 17706.9281 | 18046.9378 | 18821.424 | 19339.2473 | 19995.8987 | 20336.3879 | 20635.4819 | 20081.6413 | 20729.137 | 21747.4936 | 20973.4165 | 20973.4165 | 20973.4165 | 20973.4165 | 20973.4165 | 20973.4165 | 20973.4165 | 20973.4165 | 20973.4165 | 20973.4165 | 20973.4165 | 20973.4165 | 20973.4165 | 20973.4165 | 20973.4165 | 20973.4165 |  | 15855.2197 | 21509.0734 | 23054.6574 | 18523.2973 | 18674.1541 | 19006.7756 | 19793.3774 | 20222.1458 | 21040.3007 | 23528.7559 | 21475.5789 | 21073.4587 | 21614.551 | 22798.7732 | 21995.9638 | 21995.9638 | 21995.9638 | 21995.9638 | 21995.9638 | 21995.9638 | 21995.9638 | 21995.9638 | 21995.9638 | 21995.9638 | 21995.9638 | 21995.9638 | 21995.9638 | 21995.9638 | 21995.9638 | 21995.9638
50% | 15014.9247 | 20818.8523 | 22326.5575 | 17748.2072 | 17947.6864 | 18292.3191 | 19077.3358 | 19602.1999 | 20267.7797 | 20612.8984 | 20916.0592 | 20354.6882 | 21010.9877 | 22043.1907 | 21258.5886 | 21258.5886 | 21258.5886 | 21258.5886 | 21258.5886 | 21258.5886 | 21258.5886 | 21258.5886 | 21258.5886 | 21258.5886 | 21258.5886 | 21258.5886 | 21258.5886 | 21258.5886 | 21258.5886 | 21258.5886 |  | 16070.8005 | 21801.5288 | 23368.1279 | 18775.1556 | 18928.0635 | 19265.2076 | 20062.5048 | 20497.103 | 21326.3823 | 23848.6726 | 21767.5788 | 21359.9911 | 21908.4406 | 23108.7644 | 22295.0394 | 22295.0394 | 22295.0394 | 22295.0394 | 22295.0394 | 22295.0394 | 22295.0394 | 22295.0394 | 22295.0394 | 22295.0394 | 22295.0394 | 22295.0394 | 22295.0394 | 22295.0394 | 22295.0394 | 22295.0394
45% | 11588.8305 | 16068.4223 | 17232.1005 | 13698.4346 | 13852.3968 | 14118.3915 | 14724.2837 | 15129.3847 | 15643.093 | 15909.4628 | 16143.4486 | 15710.1708 | 16216.7164 | 17013.3921 | 16407.8199 | 16407.8199 | 16407.8199 | 16407.8199 | 16407.8199 | 16407.8199 | 16407.8199 | 16407.8199 | 16407.8199 | 16407.8199 | 16407.8199 | 16407.8199 | 16407.8199 | 16407.8199 | 16407.8199 | 16407.8199 |  | 12403.7774 | 16826.8724 | 18036.0061 | 14491.0548 | 14609.0723 | 14869.2871 | 15484.6576 | 15820.0895 | 16460.1445 | 18406.9005 | 16800.6691 | 16486.0845 | 16909.3891 | 17835.824 | 17207.7741 | 17207.7741 | 17207.7741 | 17207.7741 | 17207.7741 | 17207.7741 | 17207.7741 | 17207.7741 | 17207.7741 | 17207.7741 | 17207.7741 | 17207.7741 | 17207.7741 | 17207.7741 | 17207.7741 | 17207.7741
40% | 5693.5395 | 7894.3425 | 8466.0523 | 6729.9784 | 6805.6193 | 6936.3013 | 7233.9734 | 7432.9977 | 7685.3802 | 7816.2465 | 7931.2026 | 7718.3352 | 7967.1988 | 8358.6019 | 8061.087 | 8061.087 | 8061.087 | 8061.087 | 8061.087 | 8061.087 | 8061.087 | 8061.087 | 8061.087 | 8061.087 | 8061.087 | 8061.087 | 8061.087 | 8061.087 | 8061.087 | 8061.087 |  | 6093.9192 | 8266.9656 | 8861.0075 | 7119.3891 | 7177.3705 | 7305.2129 | 7607.5416 | 7772.3378 | 8086.7938 | 9043.2262 | 8254.0921 | 8099.5381 | 8307.5057 | 8762.6589 | 8454.1009 | 8454.1009 | 8454.1009 | 8454.1009 | 8454.1009 | 8454.1009 | 8454.1009 | 8454.1009 | 8454.1009 | 8454.1009 | 8454.1009 | 8454.1009 | 8454.1009 | 8454.1009 | 8454.1009 | 8454.1009
35% | 2127.9257 | 2950.4624 | 3164.1354 | 2515.2884 | 2543.5587 | 2592.4003 | 2703.6535 | 2778.0376 | 2872.364 | 2921.2745 | 2964.2386 | 2884.6807 | 2977.692 | 3123.9765 | 3012.7821 | 3012.7821 | 3012.7821 | 3012.7821 | 3012.7821 | 3012.7821 | 3012.7821 | 3012.7821 | 3012.7821 | 3012.7821 | 3012.7821 | 3012.7821 | 3012.7821 | 3012.7821 | 3012.7821 | 3012.7821 |  | 2277.5652 | 3089.728 | 3311.7475 | 2660.8283 | 2682.4985 | 2730.2788 | 2843.2723 | 2904.8639 | 3022.3899 | 3379.8507 | 3084.9166 | 3027.153 | 3104.8796 | 3274.9903 | 3159.6687 | 3159.6687 | 3159.6687 | 3159.6687 | 3159.6687 | 3159.6687 | 3159.6687 | 3159.6687 | 3159.6687 | 3159.6687 | 3159.6687 | 3159.6687 | 3159.6687 | 3159.6687 | 3159.6687 | 3159.6687
30% | 1061.2862 | 1471.5199 | 1578.0877 | 1254.4803 | 1268.5799 | 1292.9393 | 1348.4259 | 1385.5244 | 1432.569 | 1456.9627 | 1478.3907 | 1438.7118 | 1485.1005 | 1558.0587 | 1502.6014 | 1502.6014 | 1502.6014 | 1502.6014 | 1502.6014 | 1502.6014 | 1502.6014 | 1502.6014 | 1502.6014 | 1502.6014 | 1502.6014 | 1502.6014 | 1502.6014 | 1502.6014 | 1502.6014 | 1502.6014 |  | 1135.9177 | 1540.9775 | 1651.708 | 1327.0672 | 1337.875 | 1361.7051 | 1418.0597 | 1448.778 | 1507.3932 | 1685.6739 | 1538.5779 | 1509.7687 | 1548.5343 | 1633.3757 | 1575.8599 | 1575.8599 | 1575.8599 | 1575.8599 | 1575.8599 | 1575.8599 | 1575.8599 | 1575.8599 | 1575.8599 | 1575.8599 | 1575.8599 | 1575.8599 | 1575.8599 | 1575.8599 | 1575.8599 | 1575.8599
25% | 625.6637 | 867.5102 | 930.3354 | 739.5581 | 747.8703 | 762.2309 | 794.9421 | 816.8129 | 844.5473 | 858.9282 | 871.5607 | 848.1687 | 875.5163 | 918.5277 | 885.8337 | 885.8337 | 885.8337 | 885.8337 | 885.8337 | 885.8337 | 885.8337 | 885.8337 | 885.8337 | 885.8337 | 885.8337 | 885.8337 | 885.8337 | 885.8337 | 885.8337 | 885.8337 |  | 669.6615 | 908.4578 | 973.7371 | 782.3504 | 788.722 | 802.7706 | 835.9936 | 854.1031 | 888.6587 | 993.7611 | 907.0431 | 890.0591 | 912.9127 | 962.9296 | 929.0221 | 929.0221 | 929.0221 | 929.0221 | 929.0221 | 929.0221 | 929.0221 | 929.0221 | 929.0221 | 929.0221 | 929.0221 | 929.0221 | 929.0221 | 929.0221 | 929.0221 | 929.0221
20% | 316.1776 | 438.3942 | 470.1428 | 373.7339 | 377.9344 | 385.1916 | 401.7221 | 412.7744 | 426.7899 | 434.0573 | 440.4411 | 428.62 | 442.4401 | 464.1758 | 447.6539 | 447.6539 | 447.6539 | 447.6539 | 447.6539 | 447.6539 | 447.6539 | 447.6539 | 447.6539 | 447.6539 | 447.6539 | 447.6539 | 447.6539 | 447.6539 | 447.6539 | 447.6539 |  | 338.4118 | 459.0869 | 492.0757 | 395.3589 | 398.5788 | 405.6782 | 422.4673 | 431.6189 | 449.0815 | 502.1948 | 458.372 | 449.7892 | 461.3382 | 486.6141 | 469.4791 | 469.4791 | 469.4791 | 469.4791 | 469.4791 | 469.4791 | 469.4791 | 469.4791 | 469.4791 | 469.4791 | 469.4791 | 469.4791 | 469.4791 | 469.4791 | 469.4791 | 469.4791
15% | 128.8131 | 178.605 | 191.5396 | 152.262 | 153.9733 | 156.9299 | 163.6646 | 168.1674 | 173.8774 | 176.8382 | 179.439 | 174.623 | 180.2534 | 189.1086 | 182.3775 | 182.3775 | 182.3775 | 182.3775 | 182.3775 | 182.3775 | 182.3775 | 182.3775 | 182.3775 | 182.3775 | 182.3775 | 182.3775 | 182.3775 | 182.3775 | 182.3775 | 182.3775 |  | 137.8715 | 187.0354 | 200.4753 | 161.0722 | 162.3839 | 165.2763 | 172.1163 | 175.8447 | 182.9591 | 204.5979 | 186.7442 | 183.2475 | 187.9526 | 198.2502 | 191.2693 | 191.2693 | 191.2693 | 191.2693 | 191.2693 | 191.2693 | 191.2693 | 191.2693 | 191.2693 | 191.2693 | 191.2693 | 191.2693 | 191.2693 | 191.2693 | 191.2693 | 191.2693
10% | 51.8598 | 71.9059 | 77.1134 | 61.3003 | 61.9892 | 63.1796 | 65.8909 | 67.7037 | 70.0026 | 71.1946 | 72.2417 | 70.3028 | 72.5695 | 76.1346 | 73.4247 | 73.4247 | 73.4247 | 73.4247 | 73.4247 | 73.4247 | 73.4247 | 73.4247 | 73.4247 | 73.4247 | 73.4247 | 73.4247 | 73.4247 | 73.4247 | 73.4247 | 73.4247 |  | 55.5067 | 75.3 | 80.7108 | 64.8472 | 65.3754 | 66.5398 | 69.2936 | 70.7946 | 73.6589 | 82.3706 | 75.1827 | 73.775 | 75.6692 | 79.815 | 77.0045 | 77.0045 | 77.0045 | 77.0045 | 77.0045 | 77.0045 | 77.0045 | 77.0045 | 77.0045 | 77.0045 | 77.0045 | 77.0045 | 77.0045 | 77.0045 | 77.0045 | 77.0045
5% | 44.1645 | 61.236 | 65.6707 | 52.2041 | 52.7908 | 53.8045 | 56.1136 | 57.6574 | 59.6151 | 60.6302 | 61.5219 | 59.8707 | 61.8012 | 64.8372 | 62.5294 | 62.5294 | 62.5294 | 62.5294 | 62.5294 | 62.5294 | 62.5294 | 62.5294 | 62.5294 | 62.5294 | 62.5294 | 62.5294 | 62.5294 | 62.5294 | 62.5294 | 62.5294 |  | 47.2702 | 64.1264 | 68.7344 | 55.2247 | 55.6745 | 56.6662 | 59.0113 | 60.2896 | 62.7288 | 70.1478 | 64.0266 | 62.8277 | 64.4409 | 67.9715 | 65.578 | 65.578 | 65.578 | 65.578 | 65.578 | 65.578 | 65.578 | 65.578 | 65.578 | 65.578 | 65.578 | 65.578 | 65.578 | 65.578 | 65.578 | 65.578
9.992e-14% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E @ R (MWh) | 118268.4368 | 163984.3799 | 175860.1598 | 139797.7518 | 141368.9947 | 144083.5721 | 150266.9334 | 154401.1435 | 159643.7322 | 162362.138 | 164750.0521 | 160328.2866 | 165497.7781 | 173628.1574 | 167448.0624 | 167448.0624 | 167448.0624 | 167448.0624 | 167448.0624 | 167448.0624 | 167448.0624 | 167448.0624 | 167448.0624 | 167448.0624 | 167448.0624 | 167448.0624 | 167448.0624 | 167448.0624 | 167448.0624 | 167448.0624 | E @ R (MWh) | 126585.2808 | 171724.6525 | 184064.3234 | 147886.7426 | 149091.1562 | 151746.7479 | 158026.8382 | 161450.0493 | 167982.0544 | 187849.4421 | 171457.2384 | 168246.7821 | 172566.7674 | 182021.3889 | 175611.9001 | 175611.9001 | 175611.9001 | 175611.9001 | 175611.9001 | 175611.9001 | 175611.9001 | 175611.9001 | 175611.9001 | 175611.9001 | 175611.9001 | 175611.9001 | 175611.9001 | 175611.9001 | 175611.9001 | 175611.9001
Option 4 Winter POE50 W E @ R (MWh) N 2 | 82787.9057 | 114789.066 | 123102.1118 | 97858.4263 | 98958.2963 | 100858.5005 | 105186.8534 | 108080.8005 | 111750.6126 | 113653.4966 | 115325.0365 | 112229.8006 | 115848.4447 | 121539.7102 | 117213.6437 | 117213.6437 | 117213.6437 | 117213.6437 | 117213.6437 | 117213.6437 | 117213.6437 | 117213.6437 | 117213.6437 | 117213.6437 | 117213.6437 | 117213.6437 | 117213.6437 | 117213.6437 | 117213.6437 | 117213.6437 | Option 4 Winter POE10 W E @ R (MWh) N 2 | 37975.5842 | 51517.3957 | 55219.297 | 44366.0228 | 44727.3469 | 45524.0244 | 47408.0515 | 48435.0148 | 50394.6163 | 56354.8326 | 51437.1715 | 50474.0346 | 51770.0302 | 54606.4167 | 52683.57 | 52683.57 | 52683.57 | 52683.57 | 52683.57 | 52683.57 | 52683.57 | 52683.57 | 52683.57 | 52683.57 | 52683.57 | 52683.57 | 52683.57 | 52683.57 | 52683.57 | 52683.57
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 85.8327 | 111.1071 | 117.7202 | 95.4994 | 95.5274 | 96.2055 | 97.9959 | 99.1936 | 100.3666 | 101.7387 | 103.0095 | 104.2437 | 104.3838 | 105.8245 | 104.7305 | 104.7305 | 104.7305 | 104.7305 | 104.7305 | 104.7305 | 104.7305 | 104.7305 | 104.7305 | 104.7305 | 104.7305 | 104.7305 | 104.7305 | 104.7305 | 104.7305 | 104.7305
98% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 42.4851 | 54.9952 | 58.2686 | 47.2698 | 47.2837 | 47.6193 | 48.5055 | 49.0983 | 49.679 | 50.3581 | 50.9871 | 51.598 | 51.6673 | 52.3805 | 51.839 | 51.839 | 51.839 | 51.839 | 51.839 | 51.839 | 51.839 | 51.839 | 51.839 | 51.839 | 51.839 | 51.839 | 51.839 | 51.839 | 51.839 | 51.839
97% | 18.864 | 25.0432 | 26.7251 | 21.3298 | 21.328 | 21.5197 | 21.7301 | 22.1619 | 22.4722 | 22.6406 | 22.8247 | 22.9932 | 23.2977 | 23.6756 | 23.6492 | 23.6492 | 23.6492 | 23.6492 | 23.6492 | 23.6492 | 23.6492 | 23.6492 | 23.6492 | 23.6492 | 23.6492 | 23.6492 | 23.6492 | 23.6492 | 23.6492 | 23.6492 |  | 84.1075 | 108.8738 | 115.354 | 93.5798 | 93.6073 | 94.2717 | 96.0261 | 97.1997 | 98.3492 | 99.6937 | 100.9389 | 102.1484 | 102.2856 | 103.6974 | 102.6254 | 102.6254 | 102.6254 | 102.6254 | 102.6254 | 102.6254 | 102.6254 | 102.6254 | 102.6254 | 102.6254 | 102.6254 | 102.6254 | 102.6254 | 102.6254 | 102.6254 | 102.6254
95% | 92.8689 | 123.2894 | 131.5698 | 105.0084 | 104.9995 | 105.9432 | 106.9788 | 109.1048 | 110.6326 | 111.4613 | 112.3676 | 113.1972 | 114.6963 | 116.557 | 116.427 | 116.427 | 116.427 | 116.427 | 116.427 | 116.427 | 116.427 | 116.427 | 116.427 | 116.427 | 116.427 | 116.427 | 116.427 | 116.427 | 116.427 | 116.427 |  | 124.2203 | 160.7982 | 170.369 | 138.2102 | 138.2508 | 139.232 | 141.8232 | 143.5565 | 145.2542 | 147.2399 | 149.079 | 150.8653 | 151.0679 | 153.153 | 151.5698 | 151.5698 | 151.5698 | 151.5698 | 151.5698 | 151.5698 | 151.5698 | 151.5698 | 151.5698 | 151.5698 | 151.5698 | 151.5698 | 151.5698 | 151.5698 | 151.5698 | 151.5698
90% | 161.0694 | 213.8301 | 228.1913 | 182.1239 | 182.1085 | 183.7452 | 185.5413 | 189.2287 | 191.8784 | 193.3157 | 194.8875 | 196.3264 | 198.9264 | 202.1536 | 201.928 | 201.928 | 201.928 | 201.928 | 201.928 | 201.928 | 201.928 | 201.928 | 201.928 | 201.928 | 201.928 | 201.928 | 201.928 | 201.928 | 201.928 | 201.928 |  | 538.6113 | 697.2109 | 738.7092 | 599.2709 | 599.4467 | 603.7014 | 614.9365 | 622.4521 | 629.8131 | 638.4231 | 646.3974 | 654.1425 | 655.0212 | 664.0619 | 657.1973 | 657.1973 | 657.1973 | 657.1973 | 657.1973 | 657.1973 | 657.1973 | 657.1973 | 657.1973 | 657.1973 | 657.1973 | 657.1973 | 657.1973 | 657.1973 | 657.1973 | 657.1973
85% | 457.0889 | 606.8151 | 647.57 | 516.8381 | 516.7944 | 521.4392 | 526.5361 | 537.0003 | 544.5197 | 548.5987 | 553.0592 | 557.1425 | 564.521 | 573.679 | 573.0389 | 573.0389 | 573.0389 | 573.0389 | 573.0389 | 573.0389 | 573.0389 | 573.0389 | 573.0389 | 573.0389 | 573.0389 | 573.0389 | 573.0389 | 573.0389 | 573.0389 | 573.0389 |  | 509.4971 | 659.5238 | 698.779 | 566.8779 | 567.0442 | 571.0689 | 581.6967 | 588.8061 | 595.7692 | 603.9137 | 611.457 | 618.7834 | 619.6146 | 628.1666 | 621.6731 | 621.6731 | 621.6731 | 621.6731 | 621.6731 | 621.6731 | 621.6731 | 621.6731 | 621.6731 | 621.6731 | 621.6731 | 621.6731 | 621.6731 | 621.6731 | 621.6731 | 621.6731
80% | 638.4734 | 847.6148 | 904.5422 | 721.9326 | 721.8715 | 728.3595 | 735.479 | 750.0957 | 760.5989 | 766.2966 | 772.5271 | 778.2307 | 788.5373 | 801.3294 | 800.4353 | 800.4353 | 800.4353 | 800.4353 | 800.4353 | 800.4353 | 800.4353 | 800.4353 | 800.4353 | 800.4353 | 800.4353 | 800.4353 | 800.4353 | 800.4353 | 800.4353 | 800.4353 |  | 355.8393 | 460.6198 | 488.0361 | 395.9147 | 396.0309 | 398.8418 | 406.2644 | 411.2296 | 416.0927 | 421.781 | 427.0493 | 432.1662 | 432.7467 | 438.7196 | 434.1844 | 434.1844 | 434.1844 | 434.1844 | 434.1844 | 434.1844 | 434.1844 | 434.1844 | 434.1844 | 434.1844 | 434.1844 | 434.1844 | 434.1844 | 434.1844 | 434.1844 | 434.1844
75% | 1664.3841 | 2209.5776 | 2357.9769 | 1881.9471 | 1881.7878 | 1898.7007 | 1917.2601 | 1955.363 | 1982.7431 | 1997.5959 | 2013.8376 | 2028.706 | 2055.5733 | 2088.9202 | 2086.5893 | 2086.5893 | 2086.5893 | 2086.5893 | 2086.5893 | 2086.5893 | 2086.5893 | 2086.5893 | 2086.5893 | 2086.5893 | 2086.5893 | 2086.5893 | 2086.5893 | 2086.5893 | 2086.5893 | 2086.5893 |  | 635.1192 | 822.1366 | 871.0705 | 706.6477 | 706.8551 | 711.8721 | 725.1203 | 733.9826 | 742.6625 | 752.8152 | 762.2183 | 771.3512 | 772.3873 | 783.0479 | 774.9534 | 774.9534 | 774.9534 | 774.9534 | 774.9534 | 774.9534 | 774.9534 | 774.9534 | 774.9534 | 774.9534 | 774.9534 | 774.9534 | 774.9534 | 774.9534 | 774.9534 | 774.9534
70% | 2875.5487 | 3817.4772 | 4073.866 | 3251.4314 | 3251.1562 | 3280.3766 | 3312.4415 | 3378.2717 | 3425.5763 | 3451.2373 | 3479.298 | 3504.9862 | 3551.4046 | 3609.0179 | 3604.9908 | 3604.9908 | 3604.9908 | 3604.9908 | 3604.9908 | 3604.9908 | 3604.9908 | 3604.9908 | 3604.9908 | 3604.9908 | 3604.9908 | 3604.9908 | 3604.9908 | 3604.9908 | 3604.9908 | 3604.9908 |  | 1157.0168 | 1497.7123 | 1586.8569 | 1287.3226 | 1287.7004 | 1296.84 | 1320.9747 | 1337.1194 | 1352.9319 | 1371.4274 | 1388.5573 | 1405.1949 | 1407.0825 | 1426.5033 | 1411.7572 | 1411.7572 | 1411.7572 | 1411.7572 | 1411.7572 | 1411.7572 | 1411.7572 | 1411.7572 | 1411.7572 | 1411.7572 | 1411.7572 | 1411.7572 | 1411.7572 | 1411.7572 | 1411.7572 | 1411.7572
65% | 7222.0048 | 9587.679 | 10231.6052 | 8166.0423 | 8165.3512 | 8238.7388 | 8319.2706 | 8484.6047 | 8603.4111 | 8667.8595 | 8738.3346 | 8802.8509 | 8919.4319 | 9064.1288 | 9054.0147 | 9054.0147 | 9054.0147 | 9054.0147 | 9054.0147 | 9054.0147 | 9054.0147 | 9054.0147 | 9054.0147 | 9054.0147 | 9054.0147 | 9054.0147 | 9054.0147 | 9054.0147 | 9054.0147 | 9054.0147 |  | 1455.7061 | 1884.3537 | 1996.5114 | 1619.651 | 1620.1263 | 1631.6253 | 1661.9906 | 1682.303 | 1702.1976 | 1725.4679 | 1747.0199 | 1767.9526 | 1770.3275 | 1794.7618 | 1776.209 | 1776.209 | 1776.209 | 1776.209 | 1776.209 | 1776.209 | 1776.209 | 1776.209 | 1776.209 | 1776.209 | 1776.209 | 1776.209 | 1776.209 | 1776.209 | 1776.209 | 1776.209
60% | 10556.5772 | 14014.5398 | 14955.7822 | 11936.4995 | 11935.4892 | 12042.7617 | 12160.4769 | 12402.1497 | 12575.8119 | 12670.0176 | 12773.0328 | 12867.3378 | 13037.747 | 13249.2539 | 13234.47 | 13234.47 | 13234.47 | 13234.47 | 13234.47 | 13234.47 | 13234.47 | 13234.47 | 13234.47 | 13234.47 | 13234.47 | 13234.47 | 13234.47 | 13234.47 | 13234.47 | 13234.47 |  | 2277.9105 | 2948.6646 | 3124.1707 | 2534.4539 | 2535.1977 | 2553.1915 | 2600.7075 | 2632.4927 | 2663.624 | 2700.0377 | 2733.7626 | 2766.5184 | 2770.2347 | 2808.4699 | 2779.4381 | 2779.4381 | 2779.4381 | 2779.4381 | 2779.4381 | 2779.4381 | 2779.4381 | 2779.4381 | 2779.4381 | 2779.4381 | 2779.4381 | 2779.4381 | 2779.4381 | 2779.4381 | 2779.4381 | 2779.4381
55% | 11937.0341 | 15847.1857 | 16911.512 | 13497.4053 | 13496.2629 | 13617.5632 | 13750.6717 | 14023.9474 | 14220.319 | 14326.8437 | 14443.3299 | 14549.967 | 14742.6602 | 14981.8253 | 14965.1081 | 14965.1081 | 14965.1081 | 14965.1081 | 14965.1081 | 14965.1081 | 14965.1081 | 14965.1081 | 14965.1081 | 14965.1081 | 14965.1081 | 14965.1081 | 14965.1081 | 14965.1081 | 14965.1081 | 14965.1081 |  | 4377.3623 | 5666.3214 | 6003.5838 | 4870.3506 | 4871.7799 | 4906.3578 | 4997.6672 | 5058.7475 | 5118.5712 | 5188.5457 | 5253.3535 | 5316.2989 | 5323.4403 | 5396.9153 | 5341.1261 | 5341.1261 | 5341.1261 | 5341.1261 | 5341.1261 | 5341.1261 | 5341.1261 | 5341.1261 | 5341.1261 | 5341.1261 | 5341.1261 | 5341.1261 | 5341.1261 | 5341.1261 | 5341.1261 | 5341.1261
50% | 15327.7148 | 20348.5339 | 21715.179 | 17331.305 | 17329.8381 | 17485.5934 | 17656.511 | 18007.4099 | 18259.5603 | 18396.3431 | 18545.9169 | 18682.8439 | 18930.271 | 19237.3703 | 19215.9046 | 19215.9046 | 19215.9046 | 19215.9046 | 19215.9046 | 19215.9046 | 19215.9046 | 19215.9046 | 19215.9046 | 19215.9046 | 19215.9046 | 19215.9046 | 19215.9046 | 19215.9046 | 19215.9046 | 19215.9046 |  | 9714.4123 | 12574.9205 | 13323.3863 | 10808.4711 | 10811.6431 | 10888.3798 | 11091.0172 | 11226.5689 | 11359.3318 | 11514.6221 | 11658.4461 | 11798.1368 | 11813.9854 | 11977.044 | 11853.2345 | 11853.2345 | 11853.2345 | 11853.2345 | 11853.2345 | 11853.2345 | 11853.2345 | 11853.2345 | 11853.2345 | 11853.2345 | 11853.2345 | 11853.2345 | 11853.2345 | 11853.2345 | 11853.2345 | 11853.2345
45% | 20411.3174 | 27097.3455 | 28917.2533 | 23079.42 | 23077.4666 | 23284.8798 | 23512.4841 | 23979.7624 | 24315.5412 | 24497.6895 | 24696.871 | 24879.2114 | 25208.7004 | 25617.6525 | 25589.0675 | 25589.0675 | 25589.0675 | 25589.0675 | 25589.0675 | 25589.0675 | 25589.0675 | 25589.0675 | 25589.0675 | 25589.0675 | 25589.0675 | 25589.0675 | 25589.0675 | 25589.0675 | 25589.0675 | 25589.0675 |  | 14720.4239 | 19055.0036 | 20189.1672 | 16378.271 | 16383.0775 | 16499.3581 | 16806.4181 | 17011.8221 | 17213.0002 | 17448.3144 | 17666.2534 | 17877.9293 | 17901.9448 | 18149.0305 | 17961.4198 | 17961.4198 | 17961.4198 | 17961.4198 | 17961.4198 | 17961.4198 | 17961.4198 | 17961.4198 | 17961.4198 | 17961.4198 | 17961.4198 | 17961.4198 | 17961.4198 | 17961.4198 | 17961.4198 | 17961.4198
40% | 14315.8312 | 19005.1929 | 20281.6168 | 16187.1512 | 16185.7811 | 16331.254 | 16490.8882 | 16818.622 | 17054.1262 | 17181.8791 | 17321.5785 | 17449.4661 | 17680.5589 | 17967.3846 | 17947.336 | 17947.336 | 17947.336 | 17947.336 | 17947.336 | 17947.336 | 17947.336 | 17947.336 | 17947.336 | 17947.336 | 17947.336 | 17947.336 | 17947.336 | 17947.336 | 17947.336 | 17947.336 |  | 15242.3215 | 19730.5793 | 20904.9535 | 16958.9458 | 16963.9228 | 17084.326 | 17402.2725 | 17614.9589 | 17823.2695 | 18066.9266 | 18292.5924 | 18511.773 | 18536.64 | 18792.4858 | 18598.2236 | 18598.2236 | 18598.2236 | 18598.2236 | 18598.2236 | 18598.2236 | 18598.2236 | 18598.2236 | 18598.2236 | 18598.2236 | 18598.2236 | 18598.2236 | 18598.2236 | 18598.2236 | 18598.2236 | 18598.2236
35% | 7422.2532 | 9853.5218 | 10515.3025 | 8392.4666 | 8391.7563 | 8467.1789 | 8549.9436 | 8719.8619 | 8841.9626 | 8908.198 | 8980.6272 | 9046.9324 | 9166.7458 | 9315.4548 | 9305.0603 | 9305.0603 | 9305.0603 | 9305.0603 | 9305.0603 | 9305.0603 | 9305.0603 | 9305.0603 | 9305.0603 | 9305.0603 | 9305.0603 | 9305.0603 | 9305.0603 | 9305.0603 | 9305.0603 | 9305.0603 |  | 20759.9869 | 26872.9779 | 28472.4713 | 23098.0231 | 23104.8017 | 23268.7903 | 23701.8324 | 23991.5105 | 24275.2288 | 24607.0888 | 24914.4449 | 25212.9681 | 25246.8368 | 25595.2979 | 25330.7134 | 25330.7134 | 25330.7134 | 25330.7134 | 25330.7134 | 25330.7134 | 25330.7134 | 25330.7134 | 25330.7134 | 25330.7134 | 25330.7134 | 25330.7134 | 25330.7134 | 25330.7134 | 25330.7134 | 25330.7134
30% | 3452.1096 | 4582.899 | 4890.695 | 3903.3584 | 3903.028 | 3938.1072 | 3976.6013 | 4055.6308 | 4112.4201 | 4143.2264 | 4176.9134 | 4207.7521 | 4263.4777 | 4332.6426 | 4327.8081 | 4327.8081 | 4327.8081 | 4327.8081 | 4327.8081 | 4327.8081 | 4327.8081 | 4327.8081 | 4327.8081 | 4327.8081 | 4327.8081 | 4327.8081 | 4327.8081 | 4327.8081 | 4327.8081 | 4327.8081 |  | 19183.5111 | 24832.2926 | 26310.3234 | 21344.001 | 21350.2648 | 21501.8005 | 21901.9581 | 22169.6386 | 22431.8118 | 22738.471 | 23022.487 | 23298.3409 | 23329.6377 | 23651.6373 | 23407.1449 | 23407.1449 | 23407.1449 | 23407.1449 | 23407.1449 | 23407.1449 | 23407.1449 | 23407.1449 | 23407.1449 | 23407.1449 | 23407.1449 | 23407.1449 | 23407.1449 | 23407.1449 | 23407.1449 | 23407.1449
25% | 2357.031 | 3129.1112 | 3339.2681 | 2665.1346 | 2664.909 | 2688.8604 | 2715.1434 | 2769.1031 | 2807.8777 | 2828.9116 | 2851.9124 | 2872.9685 | 2911.0168 | 2958.2412 | 2954.9403 | 2954.9403 | 2954.9403 | 2954.9403 | 2954.9403 | 2954.9403 | 2954.9403 | 2954.9403 | 2954.9403 | 2954.9403 | 2954.9403 | 2954.9403 | 2954.9403 | 2954.9403 | 2954.9403 | 2954.9403 |  | 5533.3008 | 7162.6379 | 7588.9618 | 6156.4735 | 6158.2802 | 6201.9892 | 6317.4109 | 6394.6208 | 6470.2421 | 6558.695 | 6640.6167 | 6720.1842 | 6729.2114 | 6822.0891 | 6751.5676 | 6751.5676 | 6751.5676 | 6751.5676 | 6751.5676 | 6751.5676 | 6751.5676 | 6751.5676 | 6751.5676 | 6751.5676 | 6751.5676 | 6751.5676 | 6751.5676 | 6751.5676 | 6751.5676 | 6751.5676
20% | 1427.8587 | 1895.5749 | 2022.8852 | 1614.5038 | 1614.3672 | 1628.8766 | 1644.7985 | 1677.4866 | 1700.9758 | 1713.7178 | 1727.6514 | 1740.4069 | 1763.4561 | 1792.064 | 1790.0644 | 1790.0644 | 1790.0644 | 1790.0644 | 1790.0644 | 1790.0644 | 1790.0644 | 1790.0644 | 1790.0644 | 1790.0644 | 1790.0644 | 1790.0644 | 1790.0644 | 1790.0644 | 1790.0644 | 1790.0644 |  | 1484.8203 | 1922.0408 | 2036.4417 | 1652.044 | 1652.5289 | 1664.2579 | 1695.2304 | 1715.9491 | 1736.2415 | 1759.9772 | 1781.9603 | 1803.3116 | 1805.734 | 1830.6571 | 1811.7331 | 1811.7331 | 1811.7331 | 1811.7331 | 1811.7331 | 1811.7331 | 1811.7331 | 1811.7331 | 1811.7331 | 1811.7331 | 1811.7331 | 1811.7331 | 1811.7331 | 1811.7331 | 1811.7331 | 1811.7331
15% | 914.1778 | 1213.6303 | 1295.1399 | 1033.6762 | 1033.5888 | 1042.8783 | 1053.0722 | 1074.0006 | 1089.0394 | 1097.1974 | 1106.1183 | 1114.2849 | 1129.042 | 1147.3581 | 1146.0778 | 1146.0778 | 1146.0778 | 1146.0778 | 1146.0778 | 1146.0778 | 1146.0778 | 1146.0778 | 1146.0778 | 1146.0778 | 1146.0778 | 1146.0778 | 1146.0778 | 1146.0778 | 1146.0778 | 1146.0778 |  | 818.9695 | 1060.1234 | 1123.2225 | 911.2037 | 911.4711 | 917.9403 | 935.0236 | 946.4512 | 957.6437 | 970.7354 | 982.8605 | 994.637 | 995.9731 | 1009.7197 | 999.282 | 999.282 | 999.282 | 999.282 | 999.282 | 999.282 | 999.282 | 999.282 | 999.282 | 999.282 | 999.282 | 999.282 | 999.282 | 999.282 | 999.282 | 999.282
10% | 611.8703 | 812.2975 | 866.8529 | 691.8521 | 691.7935 | 698.0112 | 704.8341 | 718.8417 | 728.9073 | 734.3676 | 740.3384 | 745.8045 | 755.6816 | 767.9407 | 767.0838 | 767.0838 | 767.0838 | 767.0838 | 767.0838 | 767.0838 | 767.0838 | 767.0838 | 767.0838 | 767.0838 | 767.0838 | 767.0838 | 767.0838 | 767.0838 | 767.0838 | 767.0838 |  | 191.3984 | 247.7576 | 262.5043 | 212.9541 | 213.0166 | 214.5285 | 218.521 | 221.1917 | 223.8075 | 226.8671 | 229.7008 | 232.453 | 232.7653 | 235.9779 | 233.5386 | 233.5386 | 233.5386 | 233.5386 | 233.5386 | 233.5386 | 233.5386 | 233.5386 | 233.5386 | 233.5386 | 233.5386 | 233.5386 | 233.5386 | 233.5386 | 233.5386 | 233.5386
5% | 435.3228 | 577.9192 | 616.7333 | 492.2268 | 492.1851 | 496.6087 | 501.463 | 511.4289 | 518.5902 | 522.475 | 526.723 | 530.6119 | 537.6391 | 546.361 | 545.7513 | 545.7513 | 545.7513 | 545.7513 | 545.7513 | 545.7513 | 545.7513 | 545.7513 | 545.7513 | 545.7513 | 545.7513 | 545.7513 | 545.7513 | 545.7513 | 545.7513 | 545.7513 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9.992e-14% | 38.2117 | 50.7285 | 54.1355 | 43.2066 | 43.2029 | 43.5912 | 44.0173 | 44.8921 | 45.5207 | 45.8617 | 46.2346 | 46.5759 | 47.1928 | 47.9584 | 47.9048 | 47.9048 | 47.9048 | 47.9048 | 47.9048 | 47.9048 | 47.9048 | 47.9048 | 47.9048 | 47.9048 | 47.9048 | 47.9048 | 47.9048 | 47.9048 | 47.9048 | 47.9048 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E @ R (MWh) | 102337.6118 | 135859.8063 | 144984.402 | 115714.8596 | 115705.0658 | 116744.9876 | 117886.1427 | 120228.9678 | 121912.4849 | 122825.7341 | 123824.3842 | 124738.5967 | 126390.5777 | 128440.969 | 128297.6502 | 128297.6502 | 128297.6502 | 128297.6502 | 128297.6502 | 128297.6502 | 128297.6502 | 128297.6502 | 128297.6502 | 128297.6502 | 128297.6502 | 128297.6502 | 128297.6502 | 128297.6502 | 128297.6502 | 128297.6502 | E @ R (MWh) | 99292.8528 | 128530.651 | 136180.8614 | 110475.4358 | 110507.8571 | 111292.1979 | 113363.3928 | 114748.8932 | 116105.888 | 117693.1398 | 119163.192 | 120590.9974 | 120752.988 | 122419.641 | 121154.161 | 121154.161 | 121154.161 | 121154.161 | 121154.161 | 121154.161 | 121154.161 | 121154.161 | 121154.161 | 121154.161 | 121154.161 | 121154.161 | 121154.161 | 121154.161 | 121154.161 | 121154.161
Option 4 Summer POE50 W E @ R (MWh) N 2 | 71636.3283 | 95101.8644 | 101489.0814 | 81000.4017 | 80993.546 | 81721.4913 | 82520.2999 | 84160.2774 | 85338.7394 | 85978.0139 | 86677.0689 | 87317.0177 | 88473.4044 | 89908.6783 | 89808.3551 | 89808.3551 | 89808.3551 | 89808.3551 | 89808.3551 | 89808.3551 | 89808.3551 | 89808.3551 | 89808.3551 | 89808.3551 | 89808.3551 | 89808.3551 | 89808.3551 | 89808.3551 | 89808.3551 | 89808.3551 | Option 4 Summer POE10 W E @ R (MWh) N 2 | 29787.8558 | 38559.1953 | 40854.2584 | 33142.6307 | 33152.3571 | 33387.6594 | 34009.0178 | 34424.6679 | 34831.7664 | 35307.942 | 35748.9576 | 36177.2992 | 36225.8964 | 36725.8923 | 36346.2483 | 36346.2483 | 36346.2483 | 36346.2483 | 36346.2483 | 36346.2483 | 36346.2483 | 36346.2483 | 36346.2483 | 36346.2483 | 36346.2483 | 36346.2483 | 36346.2483 | 36346.2483 | 36346.2483 | 36346.2483
Option 5 - 4A LLG 2nd Tx + Switchroom + Three new feeders + OFR12 New Feeder
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | 66.5813 | 92.3179 | 99.0036 | 57.2625 | 58.147 | 59.6753 | 63.1563 | 65.4837 | 68.4351 | 69.9655 | 71.3098 | 68.8205 | 71.7308 | 76.3079 | 72.8287 | 72.8287 | 72.8287 | 72.8287 | 72.8287 | 72.8287 | 72.8287 | 72.8287 | 72.8287 | 72.8287 | 72.8287 | 72.8287 | 72.8287 | 72.8287 | 72.8287 | 72.8287 |  | 71.2634 | 96.6755 | 103.6223 | 61.8163 | 62.4944 | 63.9894 | 67.5249 | 69.452 | 73.1293 | 84.314 | 75.0857 | 73.2784 | 75.7104 | 81.033 | 77.4247 | 77.4247 | 77.4247 | 77.4247 | 77.4247 | 77.4247 | 77.4247 | 77.4247 | 77.4247 | 77.4247 | 77.4247 | 77.4247 | 77.4247 | 77.4247 | 77.4247 | 77.4247
98% | 79.0946 | 109.6681 | 117.6103 | 68.0244 | 69.0752 | 70.8906 | 75.0259 | 77.7907 | 81.2968 | 83.1148 | 84.7118 | 81.7546 | 85.2118 | 90.6492 | 86.5161 | 86.5161 | 86.5161 | 86.5161 | 86.5161 | 86.5161 | 86.5161 | 86.5161 | 86.5161 | 86.5161 | 86.5161 | 86.5161 | 86.5161 | 86.5161 | 86.5161 | 86.5161 |  | 84.6567 | 114.8446 | 123.097 | 73.4341 | 74.2395 | 76.0155 | 80.2155 | 82.5048 | 86.8732 | 100.16 | 89.1973 | 87.0503 | 89.9394 | 96.2623 | 91.9759 | 91.9759 | 91.9759 | 91.9759 | 91.9759 | 91.9759 | 91.9759 | 91.9759 | 91.9759 | 91.9759 | 91.9759 | 91.9759 | 91.9759 | 91.9759 | 91.9759 | 91.9759
97% | 156.5832 | 217.1095 | 232.8326 | 134.6675 | 136.7478 | 140.3418 | 148.5284 | 154.0019 | 160.9429 | 164.542 | 167.7035 | 161.8492 | 168.6934 | 179.4578 | 171.2756 | 171.2756 | 171.2756 | 171.2756 | 171.2756 | 171.2756 | 171.2756 | 171.2756 | 171.2756 | 171.2756 | 171.2756 | 171.2756 | 171.2756 | 171.2756 | 171.2756 | 171.2756 |  | 167.5944 | 227.3573 | 243.6946 | 145.3771 | 146.9717 | 150.4876 | 158.8022 | 163.3344 | 171.9825 | 198.2863 | 176.5836 | 172.333 | 178.0525 | 190.5701 | 182.0842 | 182.0842 | 182.0842 | 182.0842 | 182.0842 | 182.0842 | 182.0842 | 182.0842 | 182.0842 | 182.0842 | 182.0842 | 182.0842 | 182.0842 | 182.0842 | 182.0842 | 182.0842
95% | 462.5227 | 641.3081 | 687.7517 | 397.7872 | 403.932 | 414.5481 | 438.7299 | 454.8979 | 475.4006 | 486.0317 | 495.3703 | 478.0777 | 498.2945 | 530.0907 | 505.9216 | 505.9216 | 505.9216 | 505.9216 | 505.9216 | 505.9216 | 505.9216 | 505.9216 | 505.9216 | 505.9216 | 505.9216 | 505.9216 | 505.9216 | 505.9216 | 505.9216 | 505.9216 |  | 495.0481 | 671.5786 | 719.8364 | 429.4215 | 434.1317 | 444.5171 | 469.0772 | 482.4647 | 508.01 | 585.7071 | 521.6007 | 509.0453 | 525.9398 | 562.9148 | 537.8487 | 537.8487 | 537.8487 | 537.8487 | 537.8487 | 537.8487 | 537.8487 | 537.8487 | 537.8487 | 537.8487 | 537.8487 | 537.8487 | 537.8487 | 537.8487 | 537.8487 | 537.8487
90% | 2550.165 | 3535.9158 | 3791.9875 | 2193.2391 | 2227.119 | 2285.6522 | 2418.981 | 2508.125 | 2621.1684 | 2679.784 | 2731.2735 | 2635.9291 | 2747.3963 | 2922.7077 | 2789.4493 | 2789.4493 | 2789.4493 | 2789.4493 | 2789.4493 | 2789.4493 | 2789.4493 | 2789.4493 | 2789.4493 | 2789.4493 | 2789.4493 | 2789.4493 | 2789.4493 | 2789.4493 | 2789.4493 | 2789.4493 |  | 2729.4971 | 3702.8155 | 3968.8899 | 2367.6581 | 2393.6283 | 2450.8895 | 2586.3041 | 2660.1171 | 2800.9636 | 3229.3544 | 2875.8973 | 2806.6718 | 2899.8215 | 3103.6869 | 2965.4822 | 2965.4822 | 2965.4822 | 2965.4822 | 2965.4822 | 2965.4822 | 2965.4822 | 2965.4822 | 2965.4822 | 2965.4822 | 2965.4822 | 2965.4822 | 2965.4822 | 2965.4822 | 2965.4822 | 2965.4822
85% | 6229.8705 | 8637.9889 | 9263.5537 | 5357.926 | 5440.6923 | 5583.6845 | 5909.3973 | 6127.1696 | 6403.3265 | 6546.5204 | 6672.3054 | 6439.3859 | 6711.6924 | 7139.9657 | 6814.4249 | 6814.4249 | 6814.4249 | 6814.4249 | 6814.4249 | 6814.4249 | 6814.4249 | 6814.4249 | 6814.4249 | 6814.4249 | 6814.4249 | 6814.4249 | 6814.4249 | 6814.4249 | 6814.4249 | 6814.4249 |  | 6667.9659 | 9045.7131 | 9695.7136 | 5784.0191 | 5847.4624 | 5987.3475 | 6318.1555 | 6498.4755 | 6842.5533 | 7889.0815 | 7025.611 | 6856.498 | 7084.0562 | 7582.0848 | 7244.4607 | 7244.4607 | 7244.4607 | 7244.4607 | 7244.4607 | 7244.4607 | 7244.4607 | 7244.4607 | 7244.4607 | 7244.4607 | 7244.4607 | 7244.4607 | 7244.4607 | 7244.4607 | 7244.4607 | 7244.4607
80% | 9683.0656 | 13425.9956 | 14398.3087 | 8327.8054 | 8456.4487 | 8678.701 | 9184.9552 | 9523.438 | 9952.6677 | 10175.2335 | 10370.7406 | 10008.7147 | 10431.9597 | 11097.6233 | 10591.6365 | 10591.6365 | 10591.6365 | 10591.6365 | 10591.6365 | 10591.6365 | 10591.6365 | 10591.6365 | 10591.6365 | 10591.6365 | 10591.6365 | 10591.6365 | 10591.6365 | 10591.6365 | 10591.6365 | 10591.6365 |  | 10363.9958 | 14059.7198 | 15070.0133 | 8990.0804 | 9088.6901 | 9306.113 | 9820.2868 | 10100.5575 | 10635.3564 | 12261.9714 | 10919.8823 | 10657.0306 | 11010.7235 | 11784.8076 | 11260.0395 | 11260.0395 | 11260.0395 | 11260.0395 | 11260.0395 | 11260.0395 | 11260.0395 | 11260.0395 | 11260.0395 | 11260.0395 | 11260.0395 | 11260.0395 | 11260.0395 | 11260.0395 | 11260.0395 | 11260.0395
75% | 10683.1238 | 14812.6201 | 15885.3529 | 9187.8935 | 9329.823 | 9575.0293 | 10133.569 | 10507.0099 | 10980.5701 | 11226.1223 | 11441.8212 | 11042.4056 | 11509.3629 | 12243.7757 | 11685.5311 | 11685.5311 | 11685.5311 | 11685.5311 | 11685.5311 | 11685.5311 | 11685.5311 | 11685.5311 | 11685.5311 | 11685.5311 | 11685.5311 | 11685.5311 | 11685.5311 | 11685.5311 | 11685.5311 | 11685.5311 |  | 11434.3798 | 15511.7948 | 16626.4305 | 9918.5676 | 10027.3617 | 10267.2398 | 10834.517 | 11143.7338 | 11733.7663 | 13528.3766 | 12047.6778 | 11757.679 | 12147.9009 | 13001.9317 | 12422.9661 | 12422.9661 | 12422.9661 | 12422.9661 | 12422.9661 | 12422.9661 | 12422.9661 | 12422.9661 | 12422.9661 | 12422.9661 | 12422.9661 | 12422.9661 | 12422.9661 | 12422.9661 | 12422.9661 | 12422.9661
70% | 11478.4193 | 15915.3323 | 17067.9236 | 9871.8779 | 10024.3733 | 10287.8337 | 10887.9534 | 11289.1948 | 11798.0088 | 12061.8408 | 12293.5973 | 11864.4475 | 12366.1671 | 13155.2525 | 12555.4499 | 12555.4499 | 12555.4499 | 12555.4499 | 12555.4499 | 12555.4499 | 12555.4499 | 12555.4499 | 12555.4499 | 12555.4499 | 12555.4499 | 12555.4499 | 12555.4499 | 12555.4499 | 12555.4499 | 12555.4499 |  | 12285.6019 | 16666.5563 | 17864.1701 | 10656.9465 | 10773.8396 | 11031.5752 | 11641.0828 | 11973.319 | 12607.2759 | 14535.4844 | 12944.5562 | 12632.9688 | 13052.2404 | 13969.8488 | 13347.7826 | 13347.7826 | 13347.7826 | 13347.7826 | 13347.7826 | 13347.7826 | 13347.7826 | 13347.7826 | 13347.7826 | 13347.7826 | 13347.7826 | 13347.7826 | 13347.7826 | 13347.7826 | 13347.7826 | 13347.7826
65% | 12096.053 | 16771.7086 | 17986.3189 | 10403.0665 | 10563.7673 | 10841.4042 | 11473.8152 | 11896.6467 | 12432.8391 | 12710.8675 | 12955.0944 | 12502.8528 | 13031.569 | 13863.1138 | 13231.0368 | 13231.0368 | 13231.0368 | 13231.0368 | 13231.0368 | 13231.0368 | 13231.0368 | 13231.0368 | 13231.0368 | 13231.0368 | 13231.0368 | 13231.0368 | 13231.0368 | 13231.0368 | 13231.0368 | 13231.0368 |  | 12946.6687 | 17563.3547 | 18825.4101 | 11230.3782 | 11353.5611 | 11625.1651 | 12267.4692 | 12617.5824 | 13285.6515 | 15317.6135 | 13641.0803 | 13312.7268 | 13754.5588 | 14721.5421 | 14066.0035 | 14066.0035 | 14066.0035 | 14066.0035 | 14066.0035 | 14066.0035 | 14066.0035 | 14066.0035 | 14066.0035 | 14066.0035 | 14066.0035 | 14066.0035 | 14066.0035 | 14066.0035 | 14066.0035 | 14066.0035
60% | 13316.2645 | 18463.5854 | 19800.7217 | 11452.4949 | 11629.4067 | 11935.0506 | 12631.2573 | 13096.7427 | 13687.0245 | 13993.0995 | 14261.9632 | 13764.1009 | 14346.1524 | 15261.5807 | 14565.7418 | 14565.7418 | 14565.7418 | 14565.7418 | 14565.7418 | 14565.7418 | 14565.7418 | 14565.7418 | 14565.7418 | 14565.7418 | 14565.7418 | 14565.7418 | 14565.7418 | 14565.7418 | 14565.7418 | 14565.7418 |  | 14252.6876 | 19335.0902 | 20724.4577 | 12363.2631 | 12498.8724 | 12797.8749 | 13504.9726 | 13890.4042 | 14625.8659 | 16862.8058 | 15017.1492 | 14655.6725 | 15142.075 | 16206.6045 | 15484.9374 | 15484.9374 | 15484.9374 | 15484.9374 | 15484.9374 | 15484.9374 | 15484.9374 | 15484.9374 | 15484.9374 | 15484.9374 | 15484.9374 | 15484.9374 | 15484.9374 | 15484.9374 | 15484.9374 | 15484.9374
55% | 14813.5078 | 20539.579 | 22027.0592 | 12740.1812 | 12936.9845 | 13276.9941 | 14051.4803 | 14569.3036 | 15225.955 | 15566.4442 | 15865.5382 | 15311.6977 | 15959.1934 | 16977.5499 | 16203.4728 | 16203.4728 | 16203.4728 | 16203.4728 | 16203.4728 | 16203.4728 | 16203.4728 | 16203.4728 | 16203.4728 | 16203.4728 | 16203.4728 | 16203.4728 | 16203.4728 | 16203.4728 | 16203.4728 | 16203.4728 |  | 15855.2197 | 21509.0734 | 23054.6574 | 13753.3537 | 13904.2104 | 14236.8319 | 15023.4337 | 15452.2021 | 16270.3571 | 18758.8122 | 16705.6352 | 16303.5151 | 16844.6073 | 18028.8295 | 17226.0202 | 17226.0202 | 17226.0202 | 17226.0202 | 17226.0202 | 17226.0202 | 17226.0202 | 17226.0202 | 17226.0202 | 17226.0202 | 17226.0202 | 17226.0202 | 17226.0202 | 17226.0202 | 17226.0202 | 17226.0202
50% | 15014.9247 | 20818.8523 | 22326.5575 | 12913.4073 | 13112.8865 | 13457.5193 | 14242.536 | 14767.4001 | 15432.9798 | 15778.0986 | 16081.2594 | 15519.8883 | 16176.1879 | 17208.3909 | 16423.7888 | 16423.7888 | 16423.7888 | 16423.7888 | 16423.7888 | 16423.7888 | 16423.7888 | 16423.7888 | 16423.7888 | 16423.7888 | 16423.7888 | 16423.7888 | 16423.7888 | 16423.7888 | 16423.7888 | 16423.7888 |  | 16070.8005 | 21801.5288 | 23368.1279 | 13940.3558 | 14093.2637 | 14430.4078 | 15227.7049 | 15662.3032 | 16491.5825 | 19013.8728 | 16932.779 | 16525.1913 | 17073.6407 | 18273.9646 | 17460.2396 | 17460.2396 | 17460.2396 | 17460.2396 | 17460.2396 | 17460.2396 | 17460.2396 | 17460.2396 | 17460.2396 | 17460.2396 | 17460.2396 | 17460.2396 | 17460.2396 | 17460.2396 | 17460.2396 | 17460.2396
45% | 11588.8305 | 16068.4223 | 17232.1005 | 9966.8358 | 10120.798 | 10386.7927 | 10992.6849 | 11397.7859 | 11911.4941 | 12177.864 | 12411.8498 | 11978.5719 | 12485.1176 | 13281.7933 | 12676.2211 | 12676.2211 | 12676.2211 | 12676.2211 | 12676.2211 | 12676.2211 | 12676.2211 | 12676.2211 | 12676.2211 | 12676.2211 | 12676.2211 | 12676.2211 | 12676.2211 | 12676.2211 | 12676.2211 | 12676.2211 |  | 12403.7774 | 16826.8724 | 18036.0061 | 10759.4559 | 10877.4734 | 11137.6883 | 11753.0587 | 12088.4907 | 12728.5456 | 14675.3016 | 13069.0703 | 12754.4856 | 13177.7903 | 14104.2252 | 13476.1753 | 13476.1753 | 13476.1753 | 13476.1753 | 13476.1753 | 13476.1753 | 13476.1753 | 13476.1753 | 13476.1753 | 13476.1753 | 13476.1753 | 13476.1753 | 13476.1753 | 13476.1753 | 13476.1753 | 13476.1753
40% | 5693.5395 | 7894.3425 | 8466.0523 | 4896.6609 | 4972.3019 | 5102.9838 | 5400.6559 | 5599.6802 | 5852.0627 | 5982.929 | 6097.8851 | 5885.0177 | 6133.8813 | 6525.2844 | 6227.7696 | 6227.7696 | 6227.7696 | 6227.7696 | 6227.7696 | 6227.7696 | 6227.7696 | 6227.7696 | 6227.7696 | 6227.7696 | 6227.7696 | 6227.7696 | 6227.7696 | 6227.7696 | 6227.7696 | 6227.7696 |  | 6093.9192 | 8266.9656 | 8861.0075 | 5286.0716 | 5344.053 | 5471.8954 | 5774.2241 | 5939.0203 | 6253.4764 | 7209.9087 | 6420.7746 | 6266.2206 | 6474.1882 | 6929.3414 | 6620.7834 | 6620.7834 | 6620.7834 | 6620.7834 | 6620.7834 | 6620.7834 | 6620.7834 | 6620.7834 | 6620.7834 | 6620.7834 | 6620.7834 | 6620.7834 | 6620.7834 | 6620.7834 | 6620.7834 | 6620.7834
35% | 2127.9257 | 2950.4624 | 3164.1354 | 1830.0972 | 1858.3675 | 1907.2091 | 2018.4622 | 2092.8463 | 2187.1728 | 2236.0832 | 2279.0474 | 2199.4895 | 2292.5007 | 2438.7853 | 2327.5909 | 2327.5909 | 2327.5909 | 2327.5909 | 2327.5909 | 2327.5909 | 2327.5909 | 2327.5909 | 2327.5909 | 2327.5909 | 2327.5909 | 2327.5909 | 2327.5909 | 2327.5909 | 2327.5909 | 2327.5909 |  | 2277.5652 | 3089.728 | 3311.7475 | 1975.637 | 1997.3072 | 2045.0875 | 2158.0811 | 2219.6726 | 2337.1987 | 2694.6594 | 2399.7254 | 2341.9617 | 2419.6884 | 2589.7991 | 2474.4774 | 2474.4774 | 2474.4774 | 2474.4774 | 2474.4774 | 2474.4774 | 2474.4774 | 2474.4774 | 2474.4774 | 2474.4774 | 2474.4774 | 2474.4774 | 2474.4774 | 2474.4774 | 2474.4774 | 2474.4774
30% | 1061.2862 | 1471.5199 | 1578.0877 | 912.7466 | 926.8462 | 951.2055 | 1006.6922 | 1043.7907 | 1090.8352 | 1115.2289 | 1136.657 | 1096.9781 | 1143.3667 | 1216.325 | 1160.8677 | 1160.8677 | 1160.8677 | 1160.8677 | 1160.8677 | 1160.8677 | 1160.8677 | 1160.8677 | 1160.8677 | 1160.8677 | 1160.8677 | 1160.8677 | 1160.8677 | 1160.8677 | 1160.8677 | 1160.8677 |  | 1135.9177 | 1540.9775 | 1651.708 | 985.3334 | 996.1413 | 1019.9713 | 1076.326 | 1107.0443 | 1165.6595 | 1343.9402 | 1196.8442 | 1168.035 | 1206.8006 | 1291.6419 | 1234.1262 | 1234.1262 | 1234.1262 | 1234.1262 | 1234.1262 | 1234.1262 | 1234.1262 | 1234.1262 | 1234.1262 | 1234.1262 | 1234.1262 | 1234.1262 | 1234.1262 | 1234.1262 | 1234.1262 | 1234.1262
25% | 625.6637 | 867.5102 | 930.3354 | 538.0946 | 546.4068 | 560.7675 | 593.4787 | 615.3495 | 643.0838 | 657.4647 | 670.0973 | 646.7052 | 674.0529 | 717.0642 | 684.3703 | 684.3703 | 684.3703 | 684.3703 | 684.3703 | 684.3703 | 684.3703 | 684.3703 | 684.3703 | 684.3703 | 684.3703 | 684.3703 | 684.3703 | 684.3703 | 684.3703 | 684.3703 |  | 669.6615 | 908.4578 | 973.7371 | 580.887 | 587.2586 | 601.3072 | 634.5301 | 652.6396 | 687.1952 | 792.2977 | 705.5796 | 688.5957 | 711.4493 | 761.4661 | 727.5586 | 727.5586 | 727.5586 | 727.5586 | 727.5586 | 727.5586 | 727.5586 | 727.5586 | 727.5586 | 727.5586 | 727.5586 | 727.5586 | 727.5586 | 727.5586 | 727.5586 | 727.5586
20% | 316.1776 | 438.3942 | 470.1428 | 271.9248 | 276.1254 | 283.3825 | 299.913 | 310.9654 | 324.9809 | 332.2482 | 338.632 | 326.8109 | 340.631 | 362.3667 | 345.8449 | 345.8449 | 345.8449 | 345.8449 | 345.8449 | 345.8449 | 345.8449 | 345.8449 | 345.8449 | 345.8449 | 345.8449 | 345.8449 | 345.8449 | 345.8449 | 345.8449 | 345.8449 |  | 338.4118 | 459.0869 | 492.0757 | 293.5498 | 296.7697 | 303.8691 | 320.6583 | 329.8098 | 347.2724 | 400.3857 | 356.563 | 347.9802 | 359.5292 | 384.8051 | 367.67 | 367.67 | 367.67 | 367.67 | 367.67 | 367.67 | 367.67 | 367.67 | 367.67 | 367.67 | 367.67 | 367.67 | 367.67 | 367.67 | 367.67 | 367.67
15% | 128.8131 | 178.605 | 191.5396 | 110.7842 | 112.4955 | 115.4521 | 122.1868 | 126.6896 | 132.3996 | 135.3604 | 137.9612 | 133.1452 | 138.7756 | 147.6309 | 140.8998 | 140.8998 | 140.8998 | 140.8998 | 140.8998 | 140.8998 | 140.8998 | 140.8998 | 140.8998 | 140.8998 | 140.8998 | 140.8998 | 140.8998 | 140.8998 | 140.8998 | 140.8998 |  | 137.8715 | 187.0354 | 200.4753 | 119.5944 | 120.9062 | 123.7985 | 130.6386 | 134.367 | 141.4814 | 163.1201 | 145.2664 | 141.7697 | 146.4748 | 156.7724 | 149.7915 | 149.7915 | 149.7915 | 149.7915 | 149.7915 | 149.7915 | 149.7915 | 149.7915 | 149.7915 | 149.7915 | 149.7915 | 149.7915 | 149.7915 | 149.7915 | 149.7915 | 149.7915
10% | 51.8598 | 71.9059 | 77.1134 | 44.6014 | 45.2904 | 46.4807 | 49.1921 | 51.0049 | 53.3037 | 54.4957 | 55.5428 | 53.6039 | 55.8707 | 59.4358 | 56.7259 | 56.7259 | 56.7259 | 56.7259 | 56.7259 | 56.7259 | 56.7259 | 56.7259 | 56.7259 | 56.7259 | 56.7259 | 56.7259 | 56.7259 | 56.7259 | 56.7259 | 56.7259 |  | 55.5067 | 75.3 | 80.7108 | 48.1484 | 48.6765 | 49.841 | 52.5947 | 54.0958 | 56.96 | 65.6717 | 58.4839 | 57.0761 | 58.9704 | 63.1162 | 60.3057 | 60.3057 | 60.3057 | 60.3057 | 60.3057 | 60.3057 | 60.3057 | 60.3057 | 60.3057 | 60.3057 | 60.3057 | 60.3057 | 60.3057 | 60.3057 | 60.3057 | 60.3057
5% | 44.1645 | 61.236 | 65.6707 | 37.9831 | 38.5699 | 39.5836 | 41.8926 | 43.4364 | 45.3942 | 46.4093 | 47.301 | 45.6498 | 47.5802 | 50.6163 | 48.3085 | 48.3085 | 48.3085 | 48.3085 | 48.3085 | 48.3085 | 48.3085 | 48.3085 | 48.3085 | 48.3085 | 48.3085 | 48.3085 | 48.3085 | 48.3085 | 48.3085 | 48.3085 |  | 47.2702 | 64.1264 | 68.7344 | 41.0038 | 41.4535 | 42.4452 | 44.7904 | 46.0687 | 48.5079 | 55.9269 | 49.8056 | 48.6068 | 50.2199 | 53.7505 | 51.3571 | 51.3571 | 51.3571 | 51.3571 | 51.3571 | 51.3571 | 51.3571 | 51.3571 | 51.3571 | 51.3571 | 51.3571 | 51.3571 | 51.3571 | 51.3571 | 51.3571 | 51.3571
9.992e-14% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E @ R (MWh) | 118268.4368 | 163984.3799 | 175860.1598 | 101715.3619 | 103286.6048 | 106001.1822 | 112184.5435 | 116318.7536 | 121561.3423 | 124279.7481 | 126667.6622 | 122245.8967 | 127415.3882 | 135545.7675 | 129365.6725 | 129365.6725 | 129365.6725 | 129365.6725 | 129365.6725 | 129365.6725 | 129365.6725 | 129365.6725 | 129365.6725 | 129365.6725 | 129365.6725 | 129365.6725 | 129365.6725 | 129365.6725 | 129365.6725 | 129365.6725 | E @ R (MWh) | 126585.2808 | 171724.6525 | 184064.3234 | 109804.3527 | 111008.7663 | 113664.358 | 119944.4483 | 123367.6594 | 129899.6645 | 149767.0522 | 133374.8485 | 130164.3922 | 134484.3775 | 143938.999 | 137529.5102 | 137529.5102 | 137529.5102 | 137529.5102 | 137529.5102 | 137529.5102 | 137529.5102 | 137529.5102 | 137529.5102 | 137529.5102 | 137529.5102 | 137529.5102 | 137529.5102 | 137529.5102 | 137529.5102 | 137529.5102
Option 5 Winter POE50 W E @ R (MWh) N 2 | 82787.9057 | 114789.066 | 123102.1118 | 71200.7533 | 72300.6234 | 74200.8276 | 78529.1804 | 81423.1275 | 85092.9396 | 86995.8236 | 88667.3635 | 85572.1277 | 89190.7717 | 94882.0373 | 90555.9708 | 90555.9708 | 90555.9708 | 90555.9708 | 90555.9708 | 90555.9708 | 90555.9708 | 90555.9708 | 90555.9708 | 90555.9708 | 90555.9708 | 90555.9708 | 90555.9708 | 90555.9708 | 90555.9708 | 90555.9708 | Option 5 Winter POE10 W E @ R (MWh) N 2 | 37975.5842 | 51517.3957 | 55219.297 | 32941.3058 | 33302.6299 | 34099.3074 | 35983.3345 | 37010.2978 | 38969.8993 | 44930.1157 | 40012.4546 | 39049.3177 | 40345.3132 | 43181.6997 | 41258.8531 | 41258.8531 | 41258.8531 | 41258.8531 | 41258.8531 | 41258.8531 | 41258.8531 | 41258.8531 | 41258.8531 | 41258.8531 | 41258.8531 | 41258.8531 | 41258.8531 | 41258.8531 | 41258.8531 | 41258.8531
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 85.8327 | 111.1071 | 117.7202 | 73.6756 | 73.7036 | 74.3816 | 76.172 | 77.3697 | 78.5428 | 79.9148 | 81.1856 | 82.4199 | 82.5599 | 84.0006 | 82.9067 | 82.9067 | 82.9067 | 82.9067 | 82.9067 | 82.9067 | 82.9067 | 82.9067 | 82.9067 | 82.9067 | 82.9067 | 82.9067 | 82.9067 | 82.9067 | 82.9067 | 82.9067
98% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 42.4851 | 54.9952 | 58.2686 | 36.4676 | 36.4814 | 36.817 | 37.7032 | 38.2961 | 38.8767 | 39.5558 | 40.1848 | 40.7958 | 40.8651 | 41.5782 | 41.0367 | 41.0367 | 41.0367 | 41.0367 | 41.0367 | 41.0367 | 41.0367 | 41.0367 | 41.0367 | 41.0367 | 41.0367 | 41.0367 | 41.0367 | 41.0367 | 41.0367 | 41.0367
97% | 18.864 | 25.0432 | 26.7251 | 15.9835 | 15.9817 | 16.1734 | 16.3838 | 16.8156 | 17.1259 | 17.2943 | 17.4784 | 17.6469 | 17.9514 | 18.3293 | 18.3029 | 18.3029 | 18.3029 | 18.3029 | 18.3029 | 18.3029 | 18.3029 | 18.3029 | 18.3029 | 18.3029 | 18.3029 | 18.3029 | 18.3029 | 18.3029 | 18.3029 | 18.3029 |  | 84.1075 | 108.8738 | 115.354 | 72.1946 | 72.2221 | 72.8865 | 74.6409 | 75.8145 | 76.964 | 78.3085 | 79.5537 | 80.7632 | 80.9004 | 82.3122 | 81.2402 | 81.2402 | 81.2402 | 81.2402 | 81.2402 | 81.2402 | 81.2402 | 81.2402 | 81.2402 | 81.2402 | 81.2402 | 81.2402 | 81.2402 | 81.2402 | 81.2402 | 81.2402
95% | 92.8689 | 123.2894 | 131.5698 | 78.6881 | 78.6793 | 79.623 | 80.6585 | 82.7846 | 84.3123 | 85.1411 | 86.0473 | 86.877 | 88.3761 | 90.2368 | 90.1067 | 90.1067 | 90.1067 | 90.1067 | 90.1067 | 90.1067 | 90.1067 | 90.1067 | 90.1067 | 90.1067 | 90.1067 | 90.1067 | 90.1067 | 90.1067 | 90.1067 | 90.1067 |  | 124.2203 | 160.7982 | 170.369 | 106.6259 | 106.6665 | 107.6477 | 110.2389 | 111.9722 | 113.6699 | 115.6556 | 117.4948 | 119.281 | 119.4837 | 121.5687 | 119.9856 | 119.9856 | 119.9856 | 119.9856 | 119.9856 | 119.9856 | 119.9856 | 119.9856 | 119.9856 | 119.9856 | 119.9856 | 119.9856 | 119.9856 | 119.9856 | 119.9856 | 119.9856
90% | 161.0694 | 213.8301 | 228.1913 | 136.4748 | 136.4593 | 138.0961 | 139.8921 | 143.5795 | 146.2292 | 147.6666 | 149.2384 | 150.6772 | 153.2773 | 156.5044 | 156.2788 | 156.2788 | 156.2788 | 156.2788 | 156.2788 | 156.2788 | 156.2788 | 156.2788 | 156.2788 | 156.2788 | 156.2788 | 156.2788 | 156.2788 | 156.2788 | 156.2788 | 156.2788 |  | 538.6113 | 697.2109 | 738.7092 | 462.3234 | 462.4993 | 466.7539 | 477.989 | 485.5047 | 492.8656 | 501.4756 | 509.4499 | 517.195 | 518.0737 | 527.1144 | 520.2498 | 520.2498 | 520.2498 | 520.2498 | 520.2498 | 520.2498 | 520.2498 | 520.2498 | 520.2498 | 520.2498 | 520.2498 | 520.2498 | 520.2498 | 520.2498 | 520.2498 | 520.2498
85% | 457.0889 | 606.8151 | 647.57 | 387.2932 | 387.2495 | 391.8943 | 396.9912 | 407.4554 | 414.9748 | 419.0538 | 423.5142 | 427.5976 | 434.9761 | 444.1341 | 443.494 | 443.494 | 443.494 | 443.494 | 443.494 | 443.494 | 443.494 | 443.494 | 443.494 | 443.494 | 443.494 | 443.494 | 443.494 | 443.494 | 443.494 | 443.494 |  | 509.4971 | 659.5238 | 698.779 | 437.333 | 437.4993 | 441.524 | 452.1518 | 459.2612 | 466.2242 | 474.3688 | 481.9121 | 489.2385 | 490.0697 | 498.6217 | 492.1282 | 492.1282 | 492.1282 | 492.1282 | 492.1282 | 492.1282 | 492.1282 | 492.1282 | 492.1282 | 492.1282 | 492.1282 | 492.1282 | 492.1282 | 492.1282 | 492.1282 | 492.1282
80% | 638.4734 | 847.6148 | 904.5422 | 540.981 | 540.9199 | 547.4079 | 554.5274 | 569.144 | 579.6473 | 585.345 | 591.5755 | 597.2791 | 607.5857 | 620.3778 | 619.4837 | 619.4837 | 619.4837 | 619.4837 | 619.4837 | 619.4837 | 619.4837 | 619.4837 | 619.4837 | 619.4837 | 619.4837 | 619.4837 | 619.4837 | 619.4837 | 619.4837 | 619.4837 |  | 355.8393 | 460.6198 | 488.0361 | 305.4389 | 305.5551 | 308.3659 | 315.7886 | 320.7538 | 325.6169 | 331.3052 | 336.5735 | 341.6904 | 342.2709 | 348.2438 | 343.7086 | 343.7086 | 343.7086 | 343.7086 | 343.7086 | 343.7086 | 343.7086 | 343.7086 | 343.7086 | 343.7086 | 343.7086 | 343.7086 | 343.7086 | 343.7086 | 343.7086 | 343.7086
75% | 1664.3841 | 2209.5776 | 2357.9769 | 1410.2391 | 1410.0798 | 1426.9928 | 1445.5521 | 1483.655 | 1511.0352 | 1525.888 | 1542.1297 | 1556.9981 | 1583.8654 | 1617.2122 | 1614.8813 | 1614.8813 | 1614.8813 | 1614.8813 | 1614.8813 | 1614.8813 | 1614.8813 | 1614.8813 | 1614.8813 | 1614.8813 | 1614.8813 | 1614.8813 | 1614.8813 | 1614.8813 | 1614.8813 | 1614.8813 |  | 635.1192 | 822.1366 | 871.0705 | 545.1621 | 545.3695 | 550.3865 | 563.6347 | 572.497 | 581.1769 | 591.3296 | 600.7327 | 609.8656 | 610.9017 | 621.5623 | 613.4678 | 613.4678 | 613.4678 | 613.4678 | 613.4678 | 613.4678 | 613.4678 | 613.4678 | 613.4678 | 613.4678 | 613.4678 | 613.4678 | 613.4678 | 613.4678 | 613.4678 | 613.4678
70% | 2875.5487 | 3817.4772 | 4073.866 | 2436.4637 | 2436.1885 | 2465.4089 | 2497.4738 | 2563.304 | 2610.6086 | 2636.2697 | 2664.3304 | 2690.0185 | 2736.437 | 2794.0502 | 2790.0231 | 2790.0231 | 2790.0231 | 2790.0231 | 2790.0231 | 2790.0231 | 2790.0231 | 2790.0231 | 2790.0231 | 2790.0231 | 2790.0231 | 2790.0231 | 2790.0231 | 2790.0231 | 2790.0231 | 2790.0231 |  | 1157.0168 | 1497.7123 | 1586.8569 | 993.1392 | 993.517 | 1002.6565 | 1026.7913 | 1042.9359 | 1058.7484 | 1077.244 | 1094.3738 | 1111.0114 | 1112.8991 | 1132.3198 | 1117.5737 | 1117.5737 | 1117.5737 | 1117.5737 | 1117.5737 | 1117.5737 | 1117.5737 | 1117.5737 | 1117.5737 | 1117.5737 | 1117.5737 | 1117.5737 | 1117.5737 | 1117.5737 | 1117.5737 | 1117.5737
65% | 7222.0048 | 9587.679 | 10231.6052 | 6119.2329 | 6118.5417 | 6191.9294 | 6272.4611 | 6437.7952 | 6556.6017 | 6621.05 | 6691.5251 | 6756.0415 | 6872.6224 | 7017.3193 | 7007.2052 | 7007.2052 | 7007.2052 | 7007.2052 | 7007.2052 | 7007.2052 | 7007.2052 | 7007.2052 | 7007.2052 | 7007.2052 | 7007.2052 | 7007.2052 | 7007.2052 | 7007.2052 | 7007.2052 | 7007.2052 |  | 1455.7061 | 1884.3537 | 1996.5114 | 1249.5227 | 1249.998 | 1261.4971 | 1291.8623 | 1312.1747 | 1332.0693 | 1355.3396 | 1376.8916 | 1397.8243 | 1400.1992 | 1424.6335 | 1406.0807 | 1406.0807 | 1406.0807 | 1406.0807 | 1406.0807 | 1406.0807 | 1406.0807 | 1406.0807 | 1406.0807 | 1406.0807 | 1406.0807 | 1406.0807 | 1406.0807 | 1406.0807 | 1406.0807 | 1406.0807
60% | 10556.5772 | 14014.5398 | 14955.7822 | 8944.6291 | 8943.6188 | 9050.8914 | 9168.6065 | 9410.2793 | 9583.9415 | 9678.1472 | 9781.1624 | 9875.4675 | 10045.8766 | 10257.3836 | 10242.5996 | 10242.5996 | 10242.5996 | 10242.5996 | 10242.5996 | 10242.5996 | 10242.5996 | 10242.5996 | 10242.5996 | 10242.5996 | 10242.5996 | 10242.5996 | 10242.5996 | 10242.5996 | 10242.5996 | 10242.5996 |  | 2277.9105 | 2948.6646 | 3124.1707 | 1955.2717 | 1956.0155 | 1974.0093 | 2021.5252 | 2053.3105 | 2084.4417 | 2120.8554 | 2154.5804 | 2187.3361 | 2191.0524 | 2229.2877 | 2200.2559 | 2200.2559 | 2200.2559 | 2200.2559 | 2200.2559 | 2200.2559 | 2200.2559 | 2200.2559 | 2200.2559 | 2200.2559 | 2200.2559 | 2200.2559 | 2200.2559 | 2200.2559 | 2200.2559 | 2200.2559
55% | 11937.0341 | 15847.1857 | 16911.512 | 10114.2956 | 10113.1532 | 10234.4535 | 10367.562 | 10640.8377 | 10837.2093 | 10943.7341 | 11060.2203 | 11166.8574 | 11359.5505 | 11598.7156 | 11581.9984 | 11581.9984 | 11581.9984 | 11581.9984 | 11581.9984 | 11581.9984 | 11581.9984 | 11581.9984 | 11581.9984 | 11581.9984 | 11581.9984 | 11581.9984 | 11581.9984 | 11581.9984 | 11581.9984 | 11581.9984 |  | 4377.3623 | 5666.3214 | 6003.5838 | 3757.3611 | 3758.7904 | 3793.3684 | 3884.6778 | 3945.758 | 4005.5817 | 4075.5563 | 4140.3641 | 4203.3094 | 4210.4508 | 4283.9258 | 4228.1367 | 4228.1367 | 4228.1367 | 4228.1367 | 4228.1367 | 4228.1367 | 4228.1367 | 4228.1367 | 4228.1367 | 4228.1367 | 4228.1367 | 4228.1367 | 4228.1367 | 4228.1367 | 4228.1367 | 4228.1367
50% | 15327.7148 | 20348.5339 | 21715.179 | 12987.2326 | 12985.7657 | 13141.521 | 13312.4386 | 13663.3375 | 13915.4879 | 14052.2707 | 14201.8445 | 14338.7715 | 14586.1986 | 14893.2979 | 14871.8322 | 14871.8322 | 14871.8322 | 14871.8322 | 14871.8322 | 14871.8322 | 14871.8322 | 14871.8322 | 14871.8322 | 14871.8322 | 14871.8322 | 14871.8322 | 14871.8322 | 14871.8322 | 14871.8322 | 14871.8322 |  | 9714.4123 | 12574.9205 | 13323.3863 | 8338.4816 | 8341.6536 | 8418.3903 | 8621.0277 | 8756.5794 | 8889.3424 | 9044.6327 | 9188.4566 | 9328.1474 | 9343.9959 | 9507.0545 | 9383.245 | 9383.245 | 9383.245 | 9383.245 | 9383.245 | 9383.245 | 9383.245 | 9383.245 | 9383.245 | 9383.245 | 9383.245 | 9383.245 | 9383.245 | 9383.245 | 9383.245 | 9383.245
45% | 20411.3174 | 27097.3455 | 28917.2533 | 17294.5889 | 17292.6355 | 17500.0488 | 17727.653 | 18194.9314 | 18530.7102 | 18712.8584 | 18912.04 | 19094.3804 | 19423.8693 | 19832.8215 | 19804.2364 | 19804.2364 | 19804.2364 | 19804.2364 | 19804.2364 | 19804.2364 | 19804.2364 | 19804.2364 | 19804.2364 | 19804.2364 | 19804.2364 | 19804.2364 | 19804.2364 | 19804.2364 | 19804.2364 | 19804.2364 |  | 14720.4239 | 19055.0036 | 20189.1672 | 12635.4514 | 12640.258 | 12756.5385 | 13063.5986 | 13269.0026 | 13470.1806 | 13705.4948 | 13923.4339 | 14135.1097 | 14159.1253 | 14406.2109 | 14218.6002 | 14218.6002 | 14218.6002 | 14218.6002 | 14218.6002 | 14218.6002 | 14218.6002 | 14218.6002 | 14218.6002 | 14218.6002 | 14218.6002 | 14218.6002 | 14218.6002 | 14218.6002 | 14218.6002 | 14218.6002
40% | 14315.8312 | 19005.1929 | 20281.6168 | 12129.8597 | 12128.4896 | 12273.9625 | 12433.5967 | 12761.3304 | 12996.8347 | 13124.5876 | 13264.287 | 13392.1746 | 13623.2674 | 13910.0931 | 13890.0444 | 13890.0444 | 13890.0444 | 13890.0444 | 13890.0444 | 13890.0444 | 13890.0444 | 13890.0444 | 13890.0444 | 13890.0444 | 13890.0444 | 13890.0444 | 13890.0444 | 13890.0444 | 13890.0444 | 13890.0444 |  | 15242.3215 | 19730.5793 | 20904.9535 | 13083.4284 | 13088.4054 | 13208.8086 | 13526.7551 | 13739.4415 | 13947.7521 | 14191.4092 | 14417.075 | 14636.2556 | 14661.1226 | 14916.9684 | 14722.7062 | 14722.7062 | 14722.7062 | 14722.7062 | 14722.7062 | 14722.7062 | 14722.7062 | 14722.7062 | 14722.7062 | 14722.7062 | 14722.7062 | 14722.7062 | 14722.7062 | 14722.7062 | 14722.7062 | 14722.7062
35% | 7422.2532 | 9853.5218 | 10515.3025 | 6288.9042 | 6288.1938 | 6363.6164 | 6446.3811 | 6616.2995 | 6738.4001 | 6804.6355 | 6877.0647 | 6943.3699 | 7063.1834 | 7211.8924 | 7201.4978 | 7201.4978 | 7201.4978 | 7201.4978 | 7201.4978 | 7201.4978 | 7201.4978 | 7201.4978 | 7201.4978 | 7201.4978 | 7201.4978 | 7201.4978 | 7201.4978 | 7201.4978 | 7201.4978 | 7201.4978 |  | 20759.9869 | 26872.9779 | 28472.4713 | 17819.5823 | 17826.3609 | 17990.3496 | 18423.3917 | 18713.0698 | 18996.7881 | 19328.6481 | 19636.0042 | 19934.5274 | 19968.3961 | 20316.8572 | 20052.2727 | 20052.2727 | 20052.2727 | 20052.2727 | 20052.2727 | 20052.2727 | 20052.2727 | 20052.2727 | 20052.2727 | 20052.2727 | 20052.2727 | 20052.2727 | 20052.2727 | 20052.2727 | 20052.2727 | 20052.2727
30% | 3452.1096 | 4582.899 | 4890.695 | 2924.9859 | 2924.6556 | 2959.7348 | 2998.2289 | 3077.2583 | 3134.0477 | 3164.8539 | 3198.5409 | 3229.3797 | 3285.1052 | 3354.2702 | 3349.4357 | 3349.4357 | 3349.4357 | 3349.4357 | 3349.4357 | 3349.4357 | 3349.4357 | 3349.4357 | 3349.4357 | 3349.4357 | 3349.4357 | 3349.4357 | 3349.4357 | 3349.4357 | 3349.4357 | 3349.4357 |  | 19183.5111 | 24832.2926 | 26310.3234 | 16466.3955 | 16472.6594 | 16624.195 | 17024.3526 | 17292.0332 | 17554.2064 | 17860.8655 | 18144.8816 | 18420.7354 | 18452.0323 | 18774.0318 | 18529.5394 | 18529.5394 | 18529.5394 | 18529.5394 | 18529.5394 | 18529.5394 | 18529.5394 | 18529.5394 | 18529.5394 | 18529.5394 | 18529.5394 | 18529.5394 | 18529.5394 | 18529.5394 | 18529.5394 | 18529.5394
25% | 2357.031 | 3129.1112 | 3339.2681 | 1997.1215 | 1996.896 | 2020.8474 | 2047.1303 | 2101.0901 | 2139.8647 | 2160.8986 | 2183.8994 | 2204.9555 | 2243.0037 | 2290.2282 | 2286.9273 | 2286.9273 | 2286.9273 | 2286.9273 | 2286.9273 | 2286.9273 | 2286.9273 | 2286.9273 | 2286.9273 | 2286.9273 | 2286.9273 | 2286.9273 | 2286.9273 | 2286.9273 | 2286.9273 | 2286.9273 |  | 5533.3008 | 7162.6379 | 7588.9618 | 4749.5747 | 4751.3814 | 4795.0905 | 4910.5121 | 4987.722 | 5063.3434 | 5151.7963 | 5233.718 | 5313.2854 | 5322.3127 | 5415.1904 | 5344.6689 | 5344.6689 | 5344.6689 | 5344.6689 | 5344.6689 | 5344.6689 | 5344.6689 | 5344.6689 | 5344.6689 | 5344.6689 | 5344.6689 | 5344.6689 | 5344.6689 | 5344.6689 | 5344.6689 | 5344.6689
20% | 1427.8587 | 1895.5749 | 2022.8852 | 1209.8302 | 1209.6936 | 1224.203 | 1240.1249 | 1272.813 | 1296.3022 | 1309.0442 | 1322.9778 | 1335.7333 | 1358.7825 | 1387.3904 | 1385.3908 | 1385.3908 | 1385.3908 | 1385.3908 | 1385.3908 | 1385.3908 | 1385.3908 | 1385.3908 | 1385.3908 | 1385.3908 | 1385.3908 | 1385.3908 | 1385.3908 | 1385.3908 | 1385.3908 | 1385.3908 |  | 1484.8203 | 1922.0408 | 2036.4417 | 1274.5132 | 1274.998 | 1286.727 | 1317.6995 | 1338.4182 | 1358.7107 | 1382.4464 | 1404.4294 | 1425.7808 | 1428.2032 | 1453.1262 | 1434.2023 | 1434.2023 | 1434.2023 | 1434.2023 | 1434.2023 | 1434.2023 | 1434.2023 | 1434.2023 | 1434.2023 | 1434.2023 | 1434.2023 | 1434.2023 | 1434.2023 | 1434.2023 | 1434.2023 | 1434.2023
15% | 914.1778 | 1213.6303 | 1295.1399 | 774.5864 | 774.4989 | 783.7885 | 793.9824 | 814.9108 | 829.9496 | 838.1076 | 847.0285 | 855.1951 | 869.9522 | 888.2683 | 886.988 | 886.988 | 886.988 | 886.988 | 886.988 | 886.988 | 886.988 | 886.988 | 886.988 | 886.988 | 886.988 | 886.988 | 886.988 | 886.988 | 886.988 | 886.988 |  | 818.9695 | 1060.1234 | 1123.2225 | 702.9722 | 703.2396 | 709.7089 | 726.7922 | 738.2198 | 749.4123 | 762.504 | 774.629 | 786.4056 | 787.7417 | 801.4883 | 791.0506 | 791.0506 | 791.0506 | 791.0506 | 791.0506 | 791.0506 | 791.0506 | 791.0506 | 791.0506 | 791.0506 | 791.0506 | 791.0506 | 791.0506 | 791.0506 | 791.0506 | 791.0506
10% | 611.8703 | 812.2975 | 866.8529 | 518.4401 | 518.3816 | 524.5992 | 531.4221 | 545.4297 | 555.4954 | 560.9556 | 566.9265 | 572.3925 | 582.2696 | 594.5288 | 593.6719 | 593.6719 | 593.6719 | 593.6719 | 593.6719 | 593.6719 | 593.6719 | 593.6719 | 593.6719 | 593.6719 | 593.6719 | 593.6719 | 593.6719 | 593.6719 | 593.6719 | 593.6719 |  | 191.3984 | 247.7576 | 262.5043 | 164.2891 | 164.3516 | 165.8635 | 169.856 | 172.5267 | 175.1424 | 178.2021 | 181.0357 | 183.788 | 184.1003 | 187.3129 | 184.8736 | 184.8736 | 184.8736 | 184.8736 | 184.8736 | 184.8736 | 184.8736 | 184.8736 | 184.8736 | 184.8736 | 184.8736 | 184.8736 | 184.8736 | 184.8736 | 184.8736 | 184.8736
5% | 435.3228 | 577.9192 | 616.7333 | 368.8507 | 368.809 | 373.2326 | 378.0869 | 388.0528 | 395.2141 | 399.0989 | 403.3469 | 407.2358 | 414.263 | 422.9849 | 422.3752 | 422.3752 | 422.3752 | 422.3752 | 422.3752 | 422.3752 | 422.3752 | 422.3752 | 422.3752 | 422.3752 | 422.3752 | 422.3752 | 422.3752 | 422.3752 | 422.3752 | 422.3752 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9.992e-14% | 38.2117 | 50.7285 | 54.1355 | 32.3769 | 32.3732 | 32.7615 | 33.1876 | 34.0624 | 34.691 | 35.032 | 35.4049 | 35.7463 | 36.3631 | 37.1287 | 37.0752 | 37.0752 | 37.0752 | 37.0752 | 37.0752 | 37.0752 | 37.0752 | 37.0752 | 37.0752 | 37.0752 | 37.0752 | 37.0752 | 37.0752 | 37.0752 | 37.0752 | 37.0752 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E @ R (MWh) | 102337.6118 | 135859.8063 | 144984.402 | 86711.0582 | 86701.2643 | 87741.1862 | 88882.3413 | 91225.1664 | 92908.6835 | 93821.9327 | 94820.5828 | 95734.7953 | 97386.7763 | 99437.1676 | 99293.8487 | 99293.8487 | 99293.8487 | 99293.8487 | 99293.8487 | 99293.8487 | 99293.8487 | 99293.8487 | 99293.8487 | 99293.8487 | 99293.8487 | 99293.8487 | 99293.8487 | 99293.8487 | 99293.8487 | 99293.8487 | E @ R (MWh) | 99292.8528 | 128530.651 | 136180.8614 | 85229.2042 | 85261.6256 | 86045.9663 | 88117.1612 | 89502.6616 | 90859.6565 | 92446.9083 | 93916.9604 | 95344.7658 | 95506.7565 | 97173.4094 | 95907.9294 | 95907.9294 | 95907.9294 | 95907.9294 | 95907.9294 | 95907.9294 | 95907.9294 | 95907.9294 | 95907.9294 | 95907.9294 | 95907.9294 | 95907.9294 | 95907.9294 | 95907.9294 | 95907.9294 | 95907.9294
Option 5 Summer POE50 W E @ R (MWh) N 2 | 71636.3283 | 95101.8644 | 101489.0814 | 60697.7407 | 60690.885 | 61418.8303 | 62217.6389 | 63857.6165 | 65036.0784 | 65675.3529 | 66374.4079 | 67014.3567 | 68170.7434 | 69606.0173 | 69505.6941 | 69505.6941 | 69505.6941 | 69505.6941 | 69505.6941 | 69505.6941 | 69505.6941 | 69505.6941 | 69505.6941 | 69505.6941 | 69505.6941 | 69505.6941 | 69505.6941 | 69505.6941 | 69505.6941 | 69505.6941 | Option 5 Summer POE10 W E @ R (MWh) N 2 | 29787.8558 | 38559.1953 | 40854.2584 | 25568.7613 | 25578.4877 | 25813.7899 | 26435.1484 | 26850.7985 | 27257.8969 | 27734.0725 | 28175.0881 | 28603.4297 | 28652.0269 | 29152.0228 | 28772.3788 | 28772.3788 | 28772.3788 | 28772.3788 | 28772.3788 | 28772.3788 | 28772.3788 | 28772.3788 | 28772.3788 | 28772.3788 | 28772.3788 | 28772.3788 | 28772.3788 | 28772.3788 | 28772.3788 | 28772.3788
Option 6 - Non Network
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | 55.129 | 77.591 | 83.4257 | 84.6182 | 85.505 | 86.9493 | 90.2022 | 92.3803 | 95.1837 | 96.5402 | 97.7257 | 95.0804 | 97.9764 | 102.3708 | 99.0372 | 99.0372 | 99.0372 | 99.0372 | 99.0372 | 99.0372 | 99.0372 | 99.0372 | 99.0372 | 99.0372 | 99.0372 | 99.0372 | 99.0372 | 99.0372 | 99.0372 | 99.0372 |  | 59.8111 | 81.9485 | 88.0444 | 89.1721 | 89.8523 | 91.2634 | 94.5708 | 96.3486 | 99.8779 | 110.8887 | 101.5016 | 99.5382 | 101.956 | 107.0959 | 103.6332 | 103.6332 | 103.6332 | 103.6332 | 103.6332 | 103.6332 | 103.6332 | 103.6332 | 103.6332 | 103.6332 | 103.6332 | 103.6332 | 103.6332 | 103.6332 | 103.6332 | 103.6332
98% | 65.49 | 92.1734 | 99.1047 | 100.5213 | 101.5748 | 103.2905 | 107.1548 | 109.7423 | 113.0725 | 114.6839 | 116.0922 | 112.9497 | 116.39 | 121.6103 | 117.6502 | 117.6502 | 117.6502 | 117.6502 | 117.6502 | 117.6502 | 117.6502 | 117.6502 | 117.6502 | 117.6502 | 117.6502 | 117.6502 | 117.6502 | 117.6502 | 117.6502 | 117.6502 |  | 71.052 | 97.3499 | 104.5914 | 105.931 | 106.7392 | 108.4154 | 112.3444 | 114.4564 | 118.6489 | 131.7291 | 120.5778 | 118.2454 | 121.1176 | 127.2234 | 123.11 | 123.11 | 123.11 | 123.11 | 123.11 | 123.11 | 123.11 | 123.11 | 123.11 | 123.11 | 123.11 | 123.11 | 123.11 | 123.11 | 123.11 | 123.11
97% | 129.6502 | 182.4753 | 196.1971 | 199.0017 | 201.0871 | 204.4837 | 212.1339 | 217.2563 | 223.849 | 227.0392 | 229.8273 | 223.6061 | 230.4168 | 240.7513 | 232.9116 | 232.9116 | 232.9116 | 232.9116 | 232.9116 | 232.9116 | 232.9116 | 232.9116 | 232.9116 | 232.9116 | 232.9116 | 232.9116 | 232.9116 | 232.9116 | 232.9116 | 232.9116 |  | 140.6614 | 192.7232 | 207.0592 | 209.7112 | 211.311 | 214.6295 | 222.4077 | 226.5888 | 234.8887 | 260.7835 | 238.7073 | 234.0899 | 239.7759 | 251.8637 | 243.7202 | 243.7202 | 243.7202 | 243.7202 | 243.7202 | 243.7202 | 243.7202 | 243.7202 | 243.7202 | 243.7202 | 243.7202 | 243.7202 | 243.7202 | 243.7202 | 243.7202 | 243.7202
95% | 382.9667 | 539.004 | 579.5362 | 587.8203 | 593.9805 | 604.0135 | 626.6109 | 641.7416 | 661.2156 | 670.6388 | 678.8743 | 660.498 | 680.6158 | 711.1424 | 687.985 | 687.985 | 687.985 | 687.985 | 687.985 | 687.985 | 687.985 | 687.985 | 687.985 | 687.985 | 687.985 | 687.985 | 687.985 | 687.985 | 687.985 | 687.985 |  | 415.4921 | 569.2746 | 611.6209 | 619.4546 | 624.1802 | 633.9825 | 656.9583 | 669.3084 | 693.825 | 770.3143 | 705.1047 | 691.4655 | 708.2611 | 743.9665 | 719.9121 | 719.9121 | 719.9121 | 719.9121 | 719.9121 | 719.9121 | 719.9121 | 719.9121 | 719.9121 | 719.9121 | 719.9121 | 719.9121 | 719.9121 | 719.9121 | 719.9121 | 719.9121
90% | 2111.5248 | 2971.8523 | 3195.3305 | 3241.0056 | 3274.9705 | 3330.2884 | 3454.8816 | 3538.3062 | 3645.6778 | 3697.6339 | 3743.0413 | 3641.7213 | 3752.643 | 3920.9543 | 3793.2739 | 3793.2739 | 3793.2739 | 3793.2739 | 3793.2739 | 3793.2739 | 3793.2739 | 3793.2739 | 3793.2739 | 3793.2739 | 3793.2739 | 3793.2739 | 3793.2739 | 3793.2739 | 3793.2739 | 3793.2739 |  | 2290.8569 | 3138.7521 | 3372.2329 | 3415.4246 | 3441.4797 | 3495.5257 | 3622.2047 | 3690.2984 | 3825.473 | 4247.2043 | 3887.6651 | 3812.464 | 3905.0682 | 4101.9335 | 3969.3068 | 3969.3068 | 3969.3068 | 3969.3068 | 3969.3068 | 3969.3068 | 3969.3068 | 3969.3068 | 3969.3068 | 3969.3068 | 3969.3068 | 3969.3068 | 3969.3068 | 3969.3068 | 3969.3068 | 3969.3068
85% | 5158.3039 | 7260.0223 | 7805.9635 | 7917.5445 | 8000.5184 | 8135.656 | 8440.0284 | 8643.8286 | 8906.1297 | 9033.0548 | 9143.9816 | 8896.4643 | 9167.4381 | 9578.6104 | 9266.6963 | 9266.6963 | 9266.6963 | 9266.6963 | 9266.6963 | 9266.6963 | 9266.6963 | 9266.6963 | 9266.6963 | 9266.6963 | 9266.6963 | 9266.6963 | 9266.6963 | 9266.6963 | 9266.6963 | 9266.6963 |  | 5596.3993 | 7667.7464 | 8238.1234 | 8343.6376 | 8407.2885 | 8539.319 | 8848.7867 | 9015.1345 | 9345.3565 | 10375.6159 | 9497.2873 | 9313.5764 | 9539.8019 | 10020.7296 | 9696.7321 | 9696.7321 | 9696.7321 | 9696.7321 | 9696.7321 | 9696.7321 | 9696.7321 | 9696.7321 | 9696.7321 | 9696.7321 | 9696.7321 | 9696.7321 | 9696.7321 | 9696.7321 | 9696.7321 | 9696.7321
80% | 8017.5335 | 11284.2269 | 12132.7813 | 12306.2113 | 12435.1774 | 12645.2212 | 13118.3062 | 13435.0722 | 13842.7659 | 14040.045 | 14212.4583 | 13827.7429 | 14248.9165 | 14888.0002 | 14403.1933 | 14403.1933 | 14403.1933 | 14403.1933 | 14403.1933 | 14403.1933 | 14403.1933 | 14403.1933 | 14403.1933 | 14403.1933 | 14403.1933 | 14403.1933 | 14403.1933 | 14403.1933 | 14403.1933 | 14403.1933 |  | 8698.4636 | 11917.9511 | 12804.4859 | 12968.4863 | 13067.4187 | 13272.6332 | 13753.6377 | 14012.1917 | 14525.4545 | 16126.783 | 14761.5999 | 14476.0588 | 14827.6803 | 15575.1845 | 15071.5963 | 15071.5963 | 15071.5963 | 15071.5963 | 15071.5963 | 15071.5963 | 15071.5963 | 15071.5963 | 15071.5963 | 15071.5963 | 15071.5963 | 15071.5963 | 15071.5963 | 15071.5963 | 15071.5963 | 15071.5963
75% | 8845.577 | 12449.6516 | 13385.8439 | 13577.1855 | 13719.4711 | 13951.2081 | 14473.1528 | 14822.6342 | 15272.4341 | 15490.0881 | 15680.3079 | 15255.8595 | 15720.5316 | 16425.6193 | 15890.7419 | 15890.7419 | 15890.7419 | 15890.7419 | 15890.7419 | 15890.7419 | 15890.7419 | 15890.7419 | 15890.7419 | 15890.7419 | 15890.7419 | 15890.7419 | 15890.7419 | 15890.7419 | 15890.7419 | 15890.7419 |  | 9596.833 | 13148.8262 | 14126.9215 | 14307.8597 | 14417.0098 | 14643.4186 | 15174.1008 | 15459.358 | 16025.6302 | 17792.3424 | 16286.1645 | 15971.1329 | 16359.0695 | 17183.7753 | 16628.1769 | 16628.1769 | 16628.1769 | 16628.1769 | 16628.1769 | 16628.1769 | 16628.1769 | 16628.1769 | 16628.1769 | 16628.1769 | 16628.1769 | 16628.1769 | 16628.1769 | 16628.1769 | 16628.1769 | 16628.1769
70% | 9504.078 | 13376.4546 | 14382.3409 | 14587.9269 | 14740.8047 | 14989.7932 | 15550.5936 | 15926.0918 | 16409.3766 | 16643.2337 | 16847.6143 | 16391.5682 | 16890.8323 | 17648.4097 | 17073.7138 | 17073.7138 | 17073.7138 | 17073.7138 | 17073.7138 | 17073.7138 | 17073.7138 | 17073.7138 | 17073.7138 | 17073.7138 | 17073.7138 | 17073.7138 | 17073.7138 | 17073.7138 | 17073.7138 | 17073.7138 |  | 10311.2605 | 14127.6787 | 15178.5874 | 15372.9954 | 15490.271 | 15733.5347 | 16303.7231 | 16610.2159 | 17218.6438 | 19116.8773 | 17498.5732 | 17160.0894 | 17576.9057 | 18463.006 | 17866.0465 | 17866.0465 | 17866.0465 | 17866.0465 | 17866.0465 | 17866.0465 | 17866.0465 | 17866.0465 | 17866.0465 | 17866.0465 | 17866.0465 | 17866.0465 | 17866.0465 | 17866.0465 | 17866.0465 | 17866.0465
65% | 10015.4759 | 14096.2184 | 15156.2297 | 15372.8778 | 15533.9818 | 15796.3679 | 16387.344 | 16783.0471 | 17292.3367 | 17538.7771 | 17754.1551 | 17273.5699 | 17799.6986 | 18598.0399 | 17992.4207 | 17992.4207 | 17992.4207 | 17992.4207 | 17992.4207 | 17992.4207 | 17992.4207 | 17992.4207 | 17992.4207 | 17992.4207 | 17992.4207 | 17992.4207 | 17992.4207 | 17992.4207 | 17992.4207 | 17992.4207 |  | 10866.0915 | 14887.8645 | 15995.3208 | 16200.1895 | 16323.7756 | 16580.1288 | 17180.9981 | 17503.9828 | 18145.149 | 20145.5232 | 18440.141 | 18083.444 | 18522.6884 | 19456.4682 | 18827.3874 | 18827.3874 | 18827.3874 | 18827.3874 | 18827.3874 | 18827.3874 | 18827.3874 | 18827.3874 | 18827.3874 | 18827.3874 | 18827.3874 | 18827.3874 | 18827.3874 | 18827.3874 | 18827.3874 | 18827.3874
60% | 11025.8053 | 15518.2002 | 16685.1421 | 16923.645 | 17101.0006 | 17389.8554 | 18040.4473 | 18476.0676 | 19036.7327 | 19308.0333 | 19545.138 | 19016.0729 | 19595.2758 | 20474.1512 | 19807.439 | 19807.439 | 19807.439 | 19807.439 | 19807.439 | 19807.439 | 19807.439 | 19807.439 | 19807.439 | 19807.439 | 19807.439 | 19807.439 | 19807.439 | 19807.439 | 19807.439 | 19807.439 |  | 11962.2284 | 16389.7051 | 17608.8781 | 17834.4133 | 17970.4663 | 18252.6796 | 18914.1627 | 19269.729 | 19975.5741 | 22177.7397 | 20300.324 | 19907.6445 | 20391.1985 | 21419.175 | 20726.6346 | 20726.6346 | 20726.6346 | 20726.6346 | 20726.6346 | 20726.6346 | 20726.6346 | 20726.6346 | 20726.6346 | 20726.6346 | 20726.6346 | 20726.6346 | 20726.6346 | 20726.6346 | 20726.6346 | 20726.6346
55% | 12265.5158 | 17263.023 | 18561.1725 | 18826.492 | 19023.789 | 19345.1218 | 20068.8645 | 20553.4647 | 21177.1694 | 21478.9743 | 21742.7383 | 21154.1866 | 21798.5135 | 22776.2071 | 22034.5317 | 22034.5317 | 22034.5317 | 22034.5317 | 22034.5317 | 22034.5317 | 22034.5317 | 22034.5317 | 22034.5317 | 22034.5317 | 22034.5317 | 22034.5317 | 22034.5317 | 22034.5317 | 22034.5317 | 22034.5317 |  | 13307.2277 | 18232.5174 | 19588.7708 | 19839.6645 | 19991.0149 | 20304.9595 | 21040.8179 | 21436.3632 | 22221.5715 | 24671.3423 | 22582.8353 | 22146.004 | 22683.9274 | 23827.4868 | 23057.079 | 23057.079 | 23057.079 | 23057.079 | 23057.079 | 23057.079 | 23057.079 | 23057.079 | 23057.079 | 23057.079 | 23057.079 | 23057.079 | 23057.079 | 23057.079 | 23057.079 | 23057.079
50% | 12432.2881 | 17497.7455 | 18813.5457 | 19082.4728 | 19282.4524 | 19608.1543 | 20341.7376 | 20832.9268 | 21465.1119 | 21771.0204 | 22038.3708 | 21441.8167 | 22094.9043 | 23085.8915 | 22334.1317 | 22334.1317 | 22334.1317 | 22334.1317 | 22334.1317 | 22334.1317 | 22334.1317 | 22334.1317 | 22334.1317 | 22334.1317 | 22334.1317 | 22334.1317 | 22334.1317 | 22334.1317 | 22334.1317 | 22334.1317 |  | 13488.1639 | 18480.422 | 19855.1161 | 20109.4212 | 20262.8295 | 20581.0428 | 21326.9065 | 21727.8299 | 22523.7146 | 25006.7946 | 22889.8904 | 22447.1197 | 22992.3571 | 24151.4652 | 23370.5824 | 23370.5824 | 23370.5824 | 23370.5824 | 23370.5824 | 23370.5824 | 23370.5824 | 23370.5824 | 23370.5824 | 23370.5824 | 23370.5824 | 23370.5824 | 23370.5824 | 23370.5824 | 23370.5824 | 23370.5824
45% | 9595.498 | 13505.1231 | 14520.6851 | 14728.2485 | 14882.5969 | 15133.9804 | 15700.1752 | 16079.2853 | 16567.2189 | 16803.3254 | 17009.672 | 16549.2391 | 17053.3057 | 17818.1702 | 17237.9464 | 17237.9464 | 17237.9464 | 17237.9464 | 17237.9464 | 17237.9464 | 17237.9464 | 17237.9464 | 17237.9464 | 17237.9464 | 17237.9464 | 17237.9464 | 17237.9464 | 17237.9464 | 17237.9464 | 17237.9464 |  | 10410.4449 | 14263.5732 | 15324.5907 | 15520.8687 | 15639.2724 | 15884.876 | 16460.549 | 16769.9901 | 17384.2704 | 19300.7631 | 17666.8925 | 17325.1528 | 17745.9784 | 18640.6021 | 18037.9006 | 18037.9006 | 18037.9006 | 18037.9006 | 18037.9006 | 18037.9006 | 18037.9006 | 18037.9006 | 18037.9006 | 18037.9006 | 18037.9006 | 18037.9006 | 18037.9006 | 18037.9006 | 18037.9006 | 18037.9006
40% | 4714.2243 | 6635.0054 | 7133.9463 | 7235.9213 | 7311.7519 | 7435.2555 | 7713.4244 | 7899.6795 | 8139.399 | 8255.3971 | 8356.7742 | 8130.5656 | 8378.2113 | 8753.9857 | 8468.9244 | 8468.9244 | 8468.9244 | 8468.9244 | 8468.9244 | 8468.9244 | 8468.9244 | 8468.9244 | 8468.9244 | 8468.9244 | 8468.9244 | 8468.9244 | 8468.9244 | 8468.9244 | 8468.9244 | 8468.9244 |  | 5114.604 | 7007.6284 | 7528.9015 | 7625.3319 | 7683.5031 | 7804.1671 | 8086.9926 | 8239.0196 | 8540.8127 | 9482.3768 | 8679.6637 | 8511.7685 | 8718.5182 | 9158.0427 | 8861.9382 | 8861.9382 | 8861.9382 | 8861.9382 | 8861.9382 | 8861.9382 | 8861.9382 | 8861.9382 | 8861.9382 | 8861.9382 | 8861.9382 | 8861.9382 | 8861.9382 | 8861.9382 | 8861.9382 | 8861.9382
35% | 1761.9126 | 2479.7928 | 2666.2689 | 2704.3815 | 2732.7227 | 2778.8814 | 2882.8454 | 2952.457 | 3042.0508 | 3085.4043 | 3123.2934 | 3038.7493 | 3131.3054 | 3271.7488 | 3165.2088 | 3165.2088 | 3165.2088 | 3165.2088 | 3165.2088 | 3165.2088 | 3165.2088 | 3165.2088 | 3165.2088 | 3165.2088 | 3165.2088 | 3165.2088 | 3165.2088 | 3165.2088 | 3165.2088 | 3165.2088 |  | 1911.5521 | 2619.0584 | 2813.881 | 2849.9213 | 2871.6625 | 2916.7599 | 3022.4642 | 3079.2833 | 3192.0767 | 3543.9805 | 3243.9714 | 3181.2216 | 3258.493 | 3422.7626 | 3312.0954 | 3312.0954 | 3312.0954 | 3312.0954 | 3312.0954 | 3312.0954 | 3312.0954 | 3312.0954 | 3312.0954 | 3312.0954 | 3312.0954 | 3312.0954 | 3312.0954 | 3312.0954 | 3312.0954 | 3312.0954
30% | 878.7401 | 1236.7772 | 1329.7807 | 1348.789 | 1362.924 | 1385.9453 | 1437.7965 | 1472.5147 | 1517.1989 | 1538.8211 | 1557.718 | 1515.5523 | 1561.7139 | 1631.759 | 1578.623 | 1578.623 | 1578.623 | 1578.623 | 1578.623 | 1578.623 | 1578.623 | 1578.623 | 1578.623 | 1578.623 | 1578.623 | 1578.623 | 1578.623 | 1578.623 | 1578.623 | 1578.623 |  | 953.3716 | 1306.2348 | 1403.401 | 1421.3759 | 1432.2191 | 1454.711 | 1507.4303 | 1535.7684 | 1592.0231 | 1767.5324 | 1617.9052 | 1586.6093 | 1625.1478 | 1707.076 | 1651.8815 | 1651.8815 | 1651.8815 | 1651.8815 | 1651.8815 | 1651.8815 | 1651.8815 | 1651.8815 | 1651.8815 | 1651.8815 | 1651.8815 | 1651.8815 | 1651.8815 | 1651.8815 | 1651.8815 | 1651.8815
25% | 518.0466 | 729.1215 | 783.9501 | 795.1562 | 803.4892 | 817.061 | 847.6291 | 868.0966 | 894.4395 | 907.1865 | 918.3268 | 893.4688 | 920.6826 | 961.9765 | 930.651 | 930.651 | 930.651 | 930.651 | 930.651 | 930.651 | 930.651 | 930.651 | 930.651 | 930.651 | 930.651 | 930.651 | 930.651 | 930.651 | 930.651 | 930.651 |  | 562.0444 | 770.0691 | 827.3518 | 837.9486 | 844.341 | 857.6008 | 888.6805 | 905.3868 | 938.5508 | 1042.0194 | 953.8092 | 935.3592 | 958.0789 | 1006.3783 | 973.8394 | 973.8394 | 973.8394 | 973.8394 | 973.8394 | 973.8394 | 973.8394 | 973.8394 | 973.8394 | 973.8394 | 973.8394 | 973.8394 | 973.8394 | 973.8394 | 973.8394 | 973.8394
20% | 261.7936 | 368.4598 | 396.1673 | 401.8303 | 406.0413 | 412.8998 | 428.3473 | 438.6906 | 452.0028 | 458.4445 | 464.0743 | 451.5123 | 465.2647 | 486.1325 | 470.3023 | 470.3023 | 470.3023 | 470.3023 | 470.3023 | 470.3023 | 470.3023 | 470.3023 | 470.3023 | 470.3023 | 470.3023 | 470.3023 | 470.3023 | 470.3023 | 470.3023 | 470.3023 |  | 284.0278 | 389.1525 | 418.1002 | 423.4553 | 426.6857 | 433.3865 | 449.0926 | 457.535 | 474.2944 | 526.582 | 482.0052 | 472.6815 | 484.1629 | 508.5709 | 492.1274 | 492.1274 | 492.1274 | 492.1274 | 492.1274 | 492.1274 | 492.1274 | 492.1274 | 492.1274 | 492.1274 | 492.1274 | 492.1274 | 492.1274 | 492.1274 | 492.1274 | 492.1274
15% | 106.6567 | 150.1132 | 161.4015 | 163.7086 | 165.4243 | 168.2185 | 174.5119 | 178.7258 | 184.1493 | 186.7737 | 189.0673 | 183.9494 | 189.5523 | 198.054 | 191.6046 | 191.6046 | 191.6046 | 191.6046 | 191.6046 | 191.6046 | 191.6046 | 191.6046 | 191.6046 | 191.6046 | 191.6046 | 191.6046 | 191.6046 | 191.6046 | 191.6046 | 191.6046 |  | 115.715 | 158.5436 | 170.3371 | 172.5188 | 173.8349 | 176.5649 | 182.9636 | 186.4032 | 193.2311 | 214.5334 | 196.3725 | 192.5739 | 197.2515 | 207.1955 | 200.4963 | 200.4963 | 200.4963 | 200.4963 | 200.4963 | 200.4963 | 200.4963 | 200.4963 | 200.4963 | 200.4963 | 200.4963 | 200.4963 | 200.4963 | 200.4963 | 200.4963 | 200.4963
10% | 42.9397 | 60.4352 | 64.9798 | 65.9087 | 66.5994 | 67.7243 | 70.258 | 71.9545 | 74.138 | 75.1946 | 76.118 | 74.0576 | 76.3133 | 79.736 | 77.1395 | 77.1395 | 77.1395 | 77.1395 | 77.1395 | 77.1395 | 77.1395 | 77.1395 | 77.1395 | 77.1395 | 77.1395 | 77.1395 | 77.1395 | 77.1395 | 77.1395 | 77.1395 |  | 46.5866 | 63.8293 | 68.5773 | 69.4556 | 69.9855 | 71.0846 | 73.6607 | 75.0454 | 77.7943 | 86.3706 | 79.0591 | 77.5298 | 79.413 | 83.4164 | 80.7193 | 80.7193 | 80.7193 | 80.7193 | 80.7193 | 80.7193 | 80.7193 | 80.7193 | 80.7193 | 80.7193 | 80.7193 | 80.7193 | 80.7193 | 80.7193 | 80.7193 | 80.7193
5% | 36.568 | 51.4674 | 55.3377 | 56.1287 | 56.7169 | 57.6749 | 59.8326 | 61.2774 | 63.1369 | 64.0367 | 64.8231 | 63.0684 | 64.9894 | 67.9042 | 65.693 | 65.693 | 65.693 | 65.693 | 65.693 | 65.693 | 65.693 | 65.693 | 65.693 | 65.693 | 65.693 | 65.693 | 65.693 | 65.693 | 65.693 | 65.693 |  | 39.6737 | 54.3578 | 58.4013 | 59.1493 | 59.6005 | 60.5365 | 62.7304 | 63.9097 | 66.2506 | 73.5543 | 67.3277 | 66.0254 | 67.6291 | 71.0385 | 68.7416 | 68.7416 | 68.7416 | 68.7416 | 68.7416 | 68.7416 | 68.7416 | 68.7416 | 68.7416 | 68.7416 | 68.7416 | 68.7416 | 68.7416 | 68.7416 | 68.7416 | 68.7416
9.992e-14% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E @ R (MWh) | 97925.7176 | 137824.9342 | 148189.1312 | 150307.3955 | 151882.58 | 154448.0441 | 160226.2783 | 164095.2411 | 169074.7897 | 171484.3466 | 173590.1923 | 168891.2991 | 174035.4911 | 181841.2252 | 175919.8194 | 175919.8194 | 175919.8194 | 175919.8194 | 175919.8194 | 175919.8194 | 175919.8194 | 175919.8194 | 175919.8194 | 175919.8194 | 175919.8194 | 175919.8194 | 175919.8194 | 175919.8194 | 175919.8194 | 175919.8194 | E @ R (MWh) | 106242.5616 | 145565.2067 | 156393.2949 | 158396.3863 | 159604.7415 | 162111.2199 | 167986.1832 | 171144.1469 | 177413.1118 | 196971.6508 | 180297.3786 | 176809.7946 | 181104.4804 | 190234.4566 | 184083.6571 | 184083.6571 | 184083.6571 | 184083.6571 | 184083.6571 | 184083.6571 | 184083.6571 | 184083.6571 | 184083.6571 | 184083.6571 | 184083.6571 | 184083.6571 | 184083.6571 | 184083.6571 | 184083.6571 | 184083.6571
Option 6 Winter POE50 W E @ R (MWh) N 2 | 68548.0023 | 96477.454 | 103732.3919 | 105215.1769 | 106317.806 | 108113.6309 | 112158.3948 | 114866.6688 | 118352.3528 | 120039.0426 | 121513.1346 | 118223.9094 | 121824.8438 | 127288.8576 | 123143.8736 | 123143.8736 | 123143.8736 | 123143.8736 | 123143.8736 | 123143.8736 | 123143.8736 | 123143.8736 | 123143.8736 | 123143.8736 | 123143.8736 | 123143.8736 | 123143.8736 | 123143.8736 | 123143.8736 | 123143.8736 | Option 6 Winter POE10 W E @ R (MWh) N 2 | 31872.7685 | 43669.562 | 46917.9885 | 47518.9159 | 47881.4224 | 48633.366 | 50395.855 | 51343.2441 | 53223.9335 | 59091.4952 | 54089.2136 | 53042.9384 | 54331.3441 | 57070.337 | 55225.0971 | 55225.0971 | 55225.0971 | 55225.0971 | 55225.0971 | 55225.0971 | 55225.0971 | 55225.0971 | 55225.0971 | 55225.0971 | 55225.0971 | 55225.0971 | 55225.0971 | 55225.0971 | 55225.0971 | 55225.0971
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 74.175 | 96.1159 | 101.8628 | 101.5222 | 101.5525 | 102.145 | 103.7033 | 104.749 | 105.7713 | 106.9664 | 108.0755 | 109.1509 | 109.2765 | 110.5311 | 109.5855 | 109.5855 | 109.5855 | 109.5855 | 109.5855 | 109.5855 | 109.5855 | 109.5855 | 109.5855 | 109.5855 | 109.5855 | 109.5855 | 109.5855 | 109.5855 | 109.5855 | 109.5855
98% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 36.7147 | 47.575 | 50.4195 | 50.2509 | 50.2659 | 50.5592 | 51.3305 | 51.8481 | 52.3541 | 52.9457 | 53.4946 | 54.027 | 54.0891 | 54.7101 | 54.242 | 54.242 | 54.242 | 54.242 | 54.242 | 54.242 | 54.242 | 54.242 | 54.242 | 54.242 | 54.242 | 54.242 | 54.242 | 54.242 | 54.242 | 54.242
97% | 16.0081 | 21.3707 | 22.8404 | 22.8053 | 22.804 | 22.9748 | 23.1282 | 23.5228 | 23.7962 | 23.9212 | 24.0657 | 24.1953 | 24.4963 | 24.8287 | 24.8386 | 24.8386 | 24.8386 | 24.8386 | 24.8386 | 24.8386 | 24.8386 | 24.8386 | 24.8386 | 24.8386 | 24.8386 | 24.8386 | 24.8386 | 24.8386 | 24.8386 | 24.8386 |  | 72.684 | 94.1839 | 99.8153 | 99.4815 | 99.5112 | 100.0919 | 101.6188 | 102.6435 | 103.6452 | 104.8163 | 105.9031 | 106.9569 | 107.0799 | 108.3094 | 107.3827 | 107.3827 | 107.3827 | 107.3827 | 107.3827 | 107.3827 | 107.3827 | 107.3827 | 107.3827 | 107.3827 | 107.3827 | 107.3827 | 107.3827 | 107.3827 | 107.3827 | 107.3827
95% | 78.8092 | 105.2096 | 112.4452 | 112.272 | 112.2658 | 113.1065 | 113.8621 | 115.8048 | 117.1507 | 117.766 | 118.4773 | 119.1154 | 120.5971 | 122.2334 | 122.2821 | 122.2821 | 122.2821 | 122.2821 | 122.2821 | 122.2821 | 122.2821 | 122.2821 | 122.2821 | 122.2821 | 122.2821 | 122.2821 | 122.2821 | 122.2821 | 122.2821 | 122.2821 |  | 107.3487 | 139.1024 | 147.4195 | 146.9266 | 146.9704 | 147.828 | 150.0831 | 151.5965 | 153.076 | 154.8056 | 156.4108 | 157.9672 | 158.1488 | 159.9647 | 158.596 | 158.596 | 158.596 | 158.596 | 158.596 | 158.596 | 158.596 | 158.596 | 158.596 | 158.596 | 158.596 | 158.596 | 158.596 | 158.596 | 158.596 | 158.596
90% | 136.6847 | 182.4729 | 195.0222 | 194.7218 | 194.7111 | 196.1691 | 197.4795 | 200.8489 | 203.1833 | 204.2505 | 205.4841 | 206.5908 | 209.1606 | 211.9985 | 212.083 | 212.083 | 212.083 | 212.083 | 212.083 | 212.083 | 212.083 | 212.083 | 212.083 | 212.083 | 212.083 | 212.083 | 212.083 | 212.083 | 212.083 | 212.083 |  | 465.4571 | 603.1393 | 639.2019 | 637.0644 | 637.2545 | 640.9729 | 650.7512 | 657.3129 | 663.728 | 671.2273 | 678.1872 | 684.9358 | 685.7235 | 693.5968 | 687.6625 | 687.6625 | 687.6625 | 687.6625 | 687.6625 | 687.6625 | 687.6625 | 687.6625 | 687.6625 | 687.6625 | 687.6625 | 687.6625 | 687.6625 | 687.6625 | 687.6625 | 687.6625
85% | 387.8891 | 517.8285 | 553.4414 | 552.5888 | 552.5585 | 556.696 | 560.4148 | 569.9767 | 576.6013 | 579.6297 | 583.1307 | 586.2713 | 593.5638 | 601.6174 | 601.8573 | 601.8573 | 601.8573 | 601.8573 | 601.8573 | 601.8573 | 601.8573 | 601.8573 | 601.8573 | 601.8573 | 601.8573 | 601.8573 | 601.8573 | 601.8573 | 601.8573 | 601.8573 |  | 440.2973 | 570.5372 | 604.6504 | 602.6285 | 602.8083 | 606.3257 | 615.5754 | 621.7825 | 627.8508 | 634.9448 | 641.5285 | 647.9122 | 648.6574 | 656.105 | 650.4915 | 650.4915 | 650.4915 | 650.4915 | 650.4915 | 650.4915 | 650.4915 | 650.4915 | 650.4915 | 650.4915 | 650.4915 | 650.4915 | 650.4915 | 650.4915 | 650.4915 | 650.4915
80% | 541.8133 | 723.316 | 773.061 | 771.8701 | 771.8277 | 777.6071 | 782.8017 | 796.158 | 805.4114 | 809.6415 | 814.5317 | 818.9186 | 829.1049 | 840.3545 | 840.6895 | 840.6895 | 840.6895 | 840.6895 | 840.6895 | 840.6895 | 840.6895 | 840.6895 | 840.6895 | 840.6895 | 840.6895 | 840.6895 | 840.6895 | 840.6895 | 840.6895 | 840.6895 |  | 307.5092 | 398.4704 | 422.2955 | 420.8834 | 421.009 | 423.4656 | 429.9257 | 434.2608 | 438.499 | 443.4535 | 448.0516 | 452.5101 | 453.0305 | 458.2321 | 454.3115 | 454.3115 | 454.3115 | 454.3115 | 454.3115 | 454.3115 | 454.3115 | 454.3115 | 454.3115 | 454.3115 | 454.3115 | 454.3115 | 454.3115 | 454.3115 | 454.3115 | 454.3115
75% | 1412.4087 | 1885.5533 | 2015.2294 | 2012.1249 | 2012.0144 | 2027.0804 | 2040.6216 | 2075.439 | 2099.561 | 2110.5882 | 2123.3361 | 2134.7719 | 2161.3258 | 2190.6514 | 2191.5248 | 2191.5248 | 2191.5248 | 2191.5248 | 2191.5248 | 2191.5248 | 2191.5248 | 2191.5248 | 2191.5248 | 2191.5248 | 2191.5248 | 2191.5248 | 2191.5248 | 2191.5248 | 2191.5248 | 2191.5248 |  | 548.8574 | 711.2093 | 753.7336 | 751.2131 | 751.4372 | 755.8219 | 767.3522 | 775.0897 | 782.6542 | 791.4973 | 799.7043 | 807.662 | 808.5909 | 817.8749 | 810.8773 | 810.8773 | 810.8773 | 810.8773 | 810.8773 | 810.8773 | 810.8773 | 810.8773 | 810.8773 | 810.8773 | 810.8773 | 810.8773 | 810.8773 | 810.8773 | 810.8773 | 810.8773
70% | 2440.2121 | 3257.6619 | 3481.7027 | 3476.339 | 3476.1481 | 3502.1775 | 3525.5726 | 3585.7265 | 3627.402 | 3646.4537 | 3668.4781 | 3688.2357 | 3734.1127 | 3784.7785 | 3786.2874 | 3786.2874 | 3786.2874 | 3786.2874 | 3786.2874 | 3786.2874 | 3786.2874 | 3786.2874 | 3786.2874 | 3786.2874 | 3786.2874 | 3786.2874 | 3786.2874 | 3786.2874 | 3786.2874 | 3786.2874 |  | 999.8709 | 1295.6326 | 1373.1004 | 1368.5088 | 1368.917 | 1376.9047 | 1397.9099 | 1412.0055 | 1425.786 | 1441.8958 | 1456.8467 | 1471.3435 | 1473.0357 | 1489.9486 | 1477.2009 | 1477.2009 | 1477.2009 | 1477.2009 | 1477.2009 | 1477.2009 | 1477.2009 | 1477.2009 | 1477.2009 | 1477.2009 | 1477.2009 | 1477.2009 | 1477.2009 | 1477.2009 | 1477.2009 | 1477.2009
65% | 6128.6472 | 8181.6905 | 8744.3739 | 8730.9028 | 8730.4235 | 8795.7968 | 8854.5543 | 9005.6321 | 9110.301 | 9158.1497 | 9213.4645 | 9263.0861 | 9378.3073 | 9505.5555 | 9509.3452 | 9509.3452 | 9509.3452 | 9509.3452 | 9509.3452 | 9509.3452 | 9509.3452 | 9509.3452 | 9509.3452 | 9509.3452 | 9509.3452 | 9509.3452 | 9509.3452 | 9509.3452 | 9509.3452 | 9509.3452 |  | 1257.9923 | 1630.1063 | 1727.5727 | 1721.7958 | 1722.3094 | 1732.3592 | 1758.7869 | 1776.5214 | 1793.8594 | 1814.1279 | 1832.9385 | 1851.1777 | 1853.3068 | 1874.5858 | 1858.5472 | 1858.5472 | 1858.5472 | 1858.5472 | 1858.5472 | 1858.5472 | 1858.5472 | 1858.5472 | 1858.5472 | 1858.5472 | 1858.5472 | 1858.5472 | 1858.5472 | 1858.5472 | 1858.5472 | 1858.5472
60% | 8958.3902 | 11959.3728 | 12781.8606 | 12762.1696 | 12761.469 | 12857.0267 | 12942.9139 | 13163.748 | 13316.745 | 13386.6866 | 13467.5415 | 13540.0746 | 13708.4961 | 13894.4979 | 13900.0374 | 13900.0374 | 13900.0374 | 13900.0374 | 13900.0374 | 13900.0374 | 13900.0374 | 13900.0374 | 13900.0374 | 13900.0374 | 13900.0374 | 13900.0374 | 13900.0374 | 13900.0374 | 13900.0374 | 13900.0374 |  | 1968.525 | 2550.8144 | 2703.3313 | 2694.2915 | 2695.0953 | 2710.8213 | 2752.1758 | 2779.927 | 2807.0578 | 2838.7743 | 2868.2093 | 2896.7504 | 2900.0819 | 2933.3797 | 2908.2822 | 2908.2822 | 2908.2822 | 2908.2822 | 2908.2822 | 2908.2822 | 2908.2822 | 2908.2822 | 2908.2822 | 2908.2822 | 2908.2822 | 2908.2822 | 2908.2822 | 2908.2822 | 2908.2822 | 2908.2822
55% | 10129.8563 | 13523.2697 | 14453.3121 | 14431.0462 | 14430.254 | 14538.3075 | 14635.426 | 14885.138 | 15058.142 | 15137.2297 | 15228.6579 | 15310.6759 | 15501.1215 | 15711.4463 | 15717.7101 | 15717.7101 | 15717.7101 | 15717.7101 | 15717.7101 | 15717.7101 | 15717.7101 | 15717.7101 | 15717.7101 | 15717.7101 | 15717.7101 | 15717.7101 | 15717.7101 | 15717.7101 | 15717.7101 | 15717.7101 |  | 3782.8294 | 4901.7899 | 5194.875 | 5177.5037 | 5179.0482 | 5209.2681 | 5288.7374 | 5342.0656 | 5394.2016 | 5455.1499 | 5511.714 | 5566.56 | 5572.962 | 5636.949 | 5588.7203 | 5588.7203 | 5588.7203 | 5588.7203 | 5588.7203 | 5588.7203 | 5588.7203 | 5588.7203 | 5588.7203 | 5588.7203 | 5588.7203 | 5588.7203 | 5588.7203 | 5588.7203 | 5588.7203 | 5588.7203
50% | 13007.2132 | 17364.5161 | 18558.7345 | 18530.144 | 18529.1267 | 18667.8726 | 18792.5772 | 19113.2192 | 19335.3646 | 19436.9168 | 19554.315 | 19659.63 | 19904.1711 | 20174.238 | 20182.2811 | 20182.2811 | 20182.2811 | 20182.2811 | 20182.2811 | 20182.2811 | 20182.2811 | 20182.2811 | 20182.2811 | 20182.2811 | 20182.2811 | 20182.2811 | 20182.2811 | 20182.2811 | 20182.2811 | 20182.2811 |  | 8395.0018 | 10878.2425 | 11528.6683 | 11490.1171 | 11493.5447 | 11560.6101 | 11736.9713 | 11855.3194 | 11971.0217 | 12106.2804 | 12231.8096 | 12353.5261 | 12367.7337 | 12509.7361 | 12402.705 | 12402.705 | 12402.705 | 12402.705 | 12402.705 | 12402.705 | 12402.705 | 12402.705 | 12402.705 | 12402.705 | 12402.705 | 12402.705 | 12402.705 | 12402.705 | 12402.705 | 12402.705
45% | 17321.1963 | 23123.646 | 24713.9397 | 24675.8669 | 24674.5122 | 24859.2747 | 25025.3389 | 25452.3254 | 25748.1476 | 25883.3808 | 26039.7153 | 26179.9591 | 26505.605 | 26865.2425 | 26875.9532 | 26875.9532 | 26875.9532 | 26875.9532 | 26875.9532 | 26875.9532 | 26875.9532 | 26875.9532 | 26875.9532 | 26875.9532 | 26875.9532 | 26875.9532 | 26875.9532 | 26875.9532 | 26875.9532 | 26875.9532 |  | 12721.0975 | 16483.9968 | 17469.5988 | 17411.1815 | 17416.3754 | 17518.0008 | 17785.244 | 17964.579 | 18139.9049 | 18344.8648 | 18535.0815 | 18719.5207 | 18741.0497 | 18956.2285 | 18794.0424 | 18794.0424 | 18794.0424 | 18794.0424 | 18794.0424 | 18794.0424 | 18794.0424 | 18794.0424 | 18794.0424 | 18794.0424 | 18794.0424 | 18794.0424 | 18794.0424 | 18794.0424 | 18794.0424 | 18794.0424
40% | 12148.5212 | 16218.1699 | 17333.5499 | 17306.8469 | 17305.8968 | 17435.4831 | 17551.9552 | 17851.4295 | 18058.9095 | 18153.7577 | 18263.4056 | 18361.7681 | 18590.1654 | 18842.4035 | 18849.9155 | 18849.9155 | 18849.9155 | 18849.9155 | 18849.9155 | 18849.9155 | 18849.9155 | 18849.9155 | 18849.9155 | 18849.9155 | 18849.9155 | 18849.9155 | 18849.9155 | 18849.9155 | 18849.9155 | 18849.9155 |  | 13172.1111 | 17068.4201 | 18088.9656 | 18028.4771 | 18033.8552 | 18139.0836 | 18415.8017 | 18601.4948 | 18783.0367 | 18995.2632 | 19192.2239 | 19383.2022 | 19405.4945 | 19628.3023 | 19460.3659 | 19460.3659 | 19460.3659 | 19460.3659 | 19460.3659 | 19460.3659 | 19460.3659 | 19460.3659 | 19460.3659 | 19460.3659 | 19460.3659 | 19460.3659 | 19460.3659 | 19460.3659 | 19460.3659 | 19460.3659
35% | 6298.5795 | 8408.5487 | 8986.8339 | 8972.9893 | 8972.4967 | 9039.6827 | 9100.0693 | 9255.3362 | 9362.9073 | 9412.0827 | 9468.9313 | 9519.9287 | 9638.3447 | 9769.1212 | 9773.016 | 9773.016 | 9773.016 | 9773.016 | 9773.016 | 9773.016 | 9773.016 | 9773.016 | 9773.016 | 9773.016 | 9773.016 | 9773.016 | 9773.016 | 9773.016 | 9773.016 | 9773.016 |  | 17940.3677 | 23247.1265 | 24637.1058 | 24554.7208 | 24562.0457 | 24705.3664 | 25082.2555 | 25335.1688 | 25582.4282 | 25871.48 | 26139.7397 | 26399.8514 | 26430.2135 | 26733.6769 | 26504.9482 | 26504.9482 | 26504.9482 | 26504.9482 | 26504.9482 | 26504.9482 | 26504.9482 | 26504.9482 | 26504.9482 | 26504.9482 | 26504.9482 | 26504.9482 | 26504.9482 | 26504.9482 | 26504.9482 | 26504.9482
30% | 2929.486 | 3910.8382 | 4179.8002 | 4173.361 | 4173.1319 | 4204.3803 | 4232.4663 | 4304.6813 | 4354.7129 | 4377.5845 | 4404.0249 | 4427.744 | 4482.8196 | 4543.6441 | 4545.4555 | 4545.4555 | 4545.4555 | 4545.4555 | 4545.4555 | 4545.4555 | 4545.4555 | 4545.4555 | 4545.4555 | 4545.4555 | 4545.4555 | 4545.4555 | 4545.4555 | 4545.4555 | 4545.4555 | 4545.4555 |  | 16578.0087 | 21481.7818 | 22766.2086 | 22690.0797 | 22696.8484 | 22829.2856 | 23177.5544 | 23411.262 | 23639.7449 | 23906.8466 | 24154.7352 | 24395.0945 | 24423.1509 | 24703.5698 | 24492.2104 | 24492.2104 | 24492.2104 | 24492.2104 | 24492.2104 | 24492.2104 | 24492.2104 | 24492.2104 | 24492.2104 | 24492.2104 | 24492.2104 | 24492.2104 | 24492.2104 | 24492.2104 | 24492.2104 | 24492.2104
25% | 2000.1941 | 2670.2416 | 2853.8835 | 2849.4869 | 2849.3305 | 2870.6663 | 2889.8428 | 2939.1498 | 2973.3103 | 2988.9266 | 3006.9796 | 3023.1745 | 3060.779 | 3102.3087 | 3103.5456 | 3103.5456 | 3103.5456 | 3103.5456 | 3103.5456 | 3103.5456 | 3103.5456 | 3103.5456 | 3103.5456 | 3103.5456 | 3103.5456 | 3103.5456 | 3103.5456 | 3103.5456 | 3103.5456 | 3103.5456 |  | 4781.7684 | 6196.215 | 6566.6957 | 6544.737 | 6546.6894 | 6584.8896 | 6685.3445 | 6752.7552 | 6818.6589 | 6895.7018 | 6967.2029 | 7036.5323 | 7044.6249 | 7125.509 | 7064.5444 | 7064.5444 | 7064.5444 | 7064.5444 | 7064.5444 | 7064.5444 | 7064.5444 | 7064.5444 | 7064.5444 | 7064.5444 | 7064.5444 | 7064.5444 | 7064.5444 | 7064.5444 | 7064.5444 | 7064.5444
20% | 1211.6915 | 1617.5976 | 1728.8455 | 1726.1821 | 1726.0873 | 1739.0123 | 1750.6292 | 1780.4987 | 1801.1927 | 1810.6529 | 1821.5891 | 1831.3998 | 1854.1801 | 1879.3383 | 1880.0875 | 1880.0875 | 1880.0875 | 1880.0875 | 1880.0875 | 1880.0875 | 1880.0875 | 1880.0875 | 1880.0875 | 1880.0875 | 1880.0875 | 1880.0875 | 1880.0875 | 1880.0875 | 1880.0875 | 1880.0875 |  | 1283.1521 | 1662.7084 | 1762.1241 | 1756.2317 | 1756.7556 | 1767.0063 | 1793.9626 | 1812.0518 | 1829.7366 | 1850.4105 | 1869.5973 | 1888.2013 | 1890.3729 | 1912.0775 | 1895.7181 | 1895.7181 | 1895.7181 | 1895.7181 | 1895.7181 | 1895.7181 | 1895.7181 | 1895.7181 | 1895.7181 | 1895.7181 | 1895.7181 | 1895.7181 | 1895.7181 | 1895.7181 | 1895.7181 | 1895.7181
15% | 775.7781 | 1035.657 | 1106.8828 | 1105.1776 | 1105.1169 | 1113.392 | 1120.8297 | 1139.9534 | 1153.2027 | 1159.2595 | 1166.2613 | 1172.5425 | 1187.1275 | 1203.2349 | 1203.7146 | 1203.7146 | 1203.7146 | 1203.7146 | 1203.7146 | 1203.7146 | 1203.7146 | 1203.7146 | 1203.7146 | 1203.7146 | 1203.7146 | 1203.7146 | 1203.7146 | 1203.7146 | 1203.7146 | 1203.7146 |  | 707.7371 | 917.0857 | 971.9196 | 968.6695 | 968.9585 | 974.6124 | 989.4805 | 999.4578 | 1009.212 | 1020.6149 | 1031.1976 | 1041.4589 | 1042.6567 | 1054.6281 | 1045.6049 | 1045.6049 | 1045.6049 | 1045.6049 | 1045.6049 | 1045.6049 | 1045.6049 | 1045.6049 | 1045.6049 | 1045.6049 | 1045.6049 | 1045.6049 | 1045.6049 | 1045.6049 | 1045.6049 | 1045.6049
10% | 519.2377 | 693.1779 | 740.8501 | 739.7088 | 739.6682 | 745.2068 | 750.1849 | 762.9847 | 771.8526 | 775.9065 | 780.5929 | 784.797 | 794.5589 | 805.3397 | 805.6608 | 805.6608 | 805.6608 | 805.6608 | 805.6608 | 805.6608 | 805.6608 | 805.6608 | 805.6608 | 805.6608 | 805.6608 | 805.6608 | 805.6608 | 805.6608 | 805.6608 | 805.6608 |  | 165.4027 | 214.3288 | 227.1438 | 226.3843 | 226.4518 | 227.7731 | 231.2479 | 233.5797 | 235.8593 | 238.5242 | 240.9975 | 243.3956 | 243.6755 | 246.4733 | 244.3645 | 244.3645 | 244.3645 | 244.3645 | 244.3645 | 244.3645 | 244.3645 | 244.3645 | 244.3645 | 244.3645 | 244.3645 | 244.3645 | 244.3645 | 244.3645 | 244.3645 | 244.3645
5% | 369.4182 | 493.17 | 527.087 | 526.275 | 526.2461 | 530.1867 | 533.7284 | 542.835 | 549.1441 | 552.0283 | 555.3625 | 558.3536 | 565.2988 | 572.969 | 573.1974 | 573.1974 | 573.1974 | 573.1974 | 573.1974 | 573.1974 | 573.1974 | 573.1974 | 573.1974 | 573.1974 | 573.1974 | 573.1974 | 573.1974 | 573.1974 | 573.1974 | 573.1974 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9.992e-14% | 32.4267 | 43.2894 | 46.2665 | 46.1953 | 46.1927 | 46.5386 | 46.8495 | 47.6488 | 48.2027 | 48.4558 | 48.7485 | 49.011 | 49.6207 | 50.2939 | 50.314 | 50.314 | 50.314 | 50.314 | 50.314 | 50.314 | 50.314 | 50.314 | 50.314 | 50.314 | 50.314 | 50.314 | 50.314 | 50.314 | 50.314 | 50.314 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E @ R (MWh) | 86844.4616 | 115936.5985 | 123909.9626 | 123719.0741 | 123712.2822 | 124638.6384 | 125471.2461 | 127612.057 | 129095.2409 | 129773.2689 | 130557.0937 | 131260.244 | 132892.9567 | 134696.096 | 134749.7966 | 134749.7966 | 134749.7966 | 134749.7966 | 134749.7966 | 134749.7966 | 134749.7966 | 134749.7966 | 134749.7966 | 134749.7966 | 134749.7966 | 134749.7966 | 134749.7966 | 134749.7966 | 134749.7966 | 134749.7966 | E @ R (MWh) | 85806.9082 | 111188.5822 | 117836.7082 | 117442.6692 | 117477.7035 | 118163.1915 | 119965.8127 | 121175.4707 | 122358.0865 | 123740.591 | 125023.6494 | 126267.7366 | 126412.9553 | 127864.3888 | 126770.4035 | 126770.4035 | 126770.4035 | 126770.4035 | 126770.4035 | 126770.4035 | 126770.4035 | 126770.4035 | 126770.4035 | 126770.4035 | 126770.4035 | 126770.4035 | 126770.4035 | 126770.4035 | 126770.4035 | 126770.4035
Option 6 Summer POE50 W E @ R (MWh) N 2 | 60791.1231 | 81155.6189 | 86736.9738 | 86603.3519 | 86598.5975 | 87247.0469 | 87829.8723 | 89328.4399 | 90366.6687 | 90841.2883 | 91389.9656 | 91882.1708 | 93025.0697 | 94287.2672 | 94324.8576 | 94324.8576 | 94324.8576 | 94324.8576 | 94324.8576 | 94324.8576 | 94324.8576 | 94324.8576 | 94324.8576 | 94324.8576 | 94324.8576 | 94324.8576 | 94324.8576 | 94324.8576 | 94324.8576 | 94324.8576 | Option 6 Summer POE10 W E @ R (MWh) N 2 | 25742.0725 | 33356.5747 | 35351.0125 | 35232.8008 | 35243.3111 | 35448.9575 | 35989.7438 | 36352.6412 | 36707.4259 | 37122.1773 | 37507.0948 | 37880.321 | 37923.8866 | 38359.3166 | 38031.1211 | 38031.1211 | 38031.1211 | 38031.1211 | 38031.1211 | 38031.1211 | 38031.1211 | 38031.1211 | 38031.1211 | 38031.1211 | 38031.1211 | 38031.1211 | 38031.1211 | 38031.1211 | 38031.1211 | 38031.1211
Option 7 -
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | 66.5813 | 92.3179 | 99.0036 | 100.1408 | 101.0254 | 102.5536 | 106.0346 | 108.362 | 111.3134 | 112.8438 | 114.1881 | 111.6988 | 114.6091 | 119.1862 | 115.707 | 115.707 | 115.707 | 115.707 | 115.707 | 115.707 | 115.707 | 115.707 | 115.707 | 115.707 | 115.707 | 115.707 | 115.707 | 115.707 | 115.707 | 115.707 |  | 71.2634 | 96.6755 | 103.6223 | 104.6946 | 105.3727 | 106.8677 | 110.4032 | 112.3303 | 116.0076 | 127.1923 | 117.9641 | 116.1567 | 118.5887 | 123.9113 | 120.303 | 120.303 | 120.303 | 120.303 | 120.303 | 120.303 | 120.303 | 120.303 | 120.303 | 120.303 | 120.303 | 120.303 | 120.303 | 120.303 | 120.303 | 120.303
98% | 79.0946 | 109.6681 | 117.6103 | 118.9612 | 120.012 | 121.8275 | 125.9627 | 128.7276 | 132.2337 | 134.0516 | 135.6486 | 132.6915 | 136.1487 | 141.586 | 137.453 | 137.453 | 137.453 | 137.453 | 137.453 | 137.453 | 137.453 | 137.453 | 137.453 | 137.453 | 137.453 | 137.453 | 137.453 | 137.453 | 137.453 | 137.453 |  | 84.6567 | 114.8446 | 123.097 | 124.3709 | 125.1764 | 126.9524 | 131.1523 | 133.4417 | 137.8101 | 151.0968 | 140.1342 | 137.9871 | 140.8762 | 147.1992 | 142.9127 | 142.9127 | 142.9127 | 142.9127 | 142.9127 | 142.9127 | 142.9127 | 142.9127 | 142.9127 | 142.9127 | 142.9127 | 142.9127 | 142.9127 | 142.9127 | 142.9127 | 142.9127
97% | 156.5832 | 217.1095 | 232.8326 | 235.507 | 237.5873 | 241.1813 | 249.3678 | 254.8414 | 261.7824 | 265.3814 | 268.543 | 262.6887 | 269.5329 | 280.2972 | 272.115 | 272.115 | 272.115 | 272.115 | 272.115 | 272.115 | 272.115 | 272.115 | 272.115 | 272.115 | 272.115 | 272.115 | 272.115 | 272.115 | 272.115 | 272.115 |  | 167.5944 | 227.3573 | 243.6946 | 246.2165 | 247.8111 | 251.327 | 259.6417 | 264.1739 | 272.822 | 299.1257 | 277.423 | 273.1725 | 278.892 | 291.4096 | 282.9237 | 282.9237 | 282.9237 | 282.9237 | 282.9237 | 282.9237 | 282.9237 | 282.9237 | 282.9237 | 282.9237 | 282.9237 | 282.9237 | 282.9237 | 282.9237 | 282.9237 | 282.9237
95% | 462.5227 | 641.3081 | 687.7517 | 695.6514 | 701.7962 | 712.4124 | 736.5942 | 752.7622 | 773.2648 | 783.8959 | 793.2346 | 775.942 | 796.1588 | 827.9549 | 803.7859 | 803.7859 | 803.7859 | 803.7859 | 803.7859 | 803.7859 | 803.7859 | 803.7859 | 803.7859 | 803.7859 | 803.7859 | 803.7859 | 803.7859 | 803.7859 | 803.7859 | 803.7859 |  | 495.0481 | 671.5786 | 719.8364 | 727.2857 | 731.996 | 742.3814 | 766.9415 | 780.329 | 805.8742 | 883.5714 | 819.4649 | 806.9095 | 823.8041 | 860.7791 | 835.7129 | 835.7129 | 835.7129 | 835.7129 | 835.7129 | 835.7129 | 835.7129 | 835.7129 | 835.7129 | 835.7129 | 835.7129 | 835.7129 | 835.7129 | 835.7129 | 835.7129 | 835.7129
90% | 2550.165 | 3535.9158 | 3791.9875 | 3835.5434 | 3869.4233 | 3927.9564 | 4061.2852 | 4150.4292 | 4263.4726 | 4322.0883 | 4373.5777 | 4278.2333 | 4389.7006 | 4565.012 | 4431.7536 | 4431.7536 | 4431.7536 | 4431.7536 | 4431.7536 | 4431.7536 | 4431.7536 | 4431.7536 | 4431.7536 | 4431.7536 | 4431.7536 | 4431.7536 | 4431.7536 | 4431.7536 | 4431.7536 | 4431.7536 |  | 2729.4971 | 3702.8155 | 3968.8899 | 4009.9623 | 4035.9325 | 4093.1938 | 4228.6083 | 4302.4214 | 4443.2678 | 4871.6587 | 4518.2015 | 4448.976 | 4542.1258 | 4745.9912 | 4607.7865 | 4607.7865 | 4607.7865 | 4607.7865 | 4607.7865 | 4607.7865 | 4607.7865 | 4607.7865 | 4607.7865 | 4607.7865 | 4607.7865 | 4607.7865 | 4607.7865 | 4607.7865 | 4607.7865 | 4607.7865
85% | 6229.8705 | 8637.9889 | 9263.5537 | 9369.9577 | 9452.724 | 9595.7162 | 9921.4289 | 10139.2013 | 10415.3582 | 10558.5521 | 10684.3371 | 10451.4176 | 10723.7241 | 11151.9973 | 10826.4566 | 10826.4566 | 10826.4566 | 10826.4566 | 10826.4566 | 10826.4566 | 10826.4566 | 10826.4566 | 10826.4566 | 10826.4566 | 10826.4566 | 10826.4566 | 10826.4566 | 10826.4566 | 10826.4566 | 10826.4566 |  | 6667.9659 | 9045.7131 | 9695.7136 | 9796.0508 | 9859.4941 | 9999.3792 | 10330.1872 | 10510.5072 | 10854.585 | 11901.1132 | 11037.6427 | 10868.5297 | 11096.0879 | 11594.1165 | 11256.4923 | 11256.4923 | 11256.4923 | 11256.4923 | 11256.4923 | 11256.4923 | 11256.4923 | 11256.4923 | 11256.4923 | 11256.4923 | 11256.4923 | 11256.4923 | 11256.4923 | 11256.4923 | 11256.4923 | 11256.4923
80% | 9683.0656 | 13425.9956 | 14398.3087 | 14563.692 | 14692.3353 | 14914.5876 | 15420.8418 | 15759.3246 | 16188.5543 | 16411.1201 | 16606.6272 | 16244.6013 | 16667.8463 | 17333.5099 | 16827.5231 | 16827.5231 | 16827.5231 | 16827.5231 | 16827.5231 | 16827.5231 | 16827.5231 | 16827.5231 | 16827.5231 | 16827.5231 | 16827.5231 | 16827.5231 | 16827.5231 | 16827.5231 | 16827.5231 | 16827.5231 |  | 10363.9958 | 14059.7198 | 15070.0133 | 15225.967 | 15324.5767 | 15541.9996 | 16056.1734 | 16336.4441 | 16871.243 | 18497.858 | 17155.7689 | 16892.9172 | 17246.6101 | 18020.6942 | 17495.9261 | 17495.9261 | 17495.9261 | 17495.9261 | 17495.9261 | 17495.9261 | 17495.9261 | 17495.9261 | 17495.9261 | 17495.9261 | 17495.9261 | 17495.9261 | 17495.9261 | 17495.9261 | 17495.9261 | 17495.9261
75% | 10683.1238 | 14812.6201 | 15885.3529 | 16067.8168 | 16209.7463 | 16454.9526 | 17013.4923 | 17386.9332 | 17860.4934 | 18106.0455 | 18321.7445 | 17922.3288 | 18389.2862 | 19123.699 | 18565.4543 | 18565.4543 | 18565.4543 | 18565.4543 | 18565.4543 | 18565.4543 | 18565.4543 | 18565.4543 | 18565.4543 | 18565.4543 | 18565.4543 | 18565.4543 | 18565.4543 | 18565.4543 | 18565.4543 | 18565.4543 |  | 11434.3798 | 15511.7948 | 16626.4305 | 16798.4909 | 16907.2849 | 17147.1631 | 17714.4402 | 18023.6571 | 18613.6895 | 20408.2999 | 18927.601 | 18637.6022 | 19027.8242 | 19881.855 | 19302.8894 | 19302.8894 | 19302.8894 | 19302.8894 | 19302.8894 | 19302.8894 | 19302.8894 | 19302.8894 | 19302.8894 | 19302.8894 | 19302.8894 | 19302.8894 | 19302.8894 | 19302.8894 | 19302.8894 | 19302.8894
70% | 11478.4193 | 15915.3323 | 17067.9236 | 17263.9709 | 17416.4662 | 17679.9267 | 18280.0463 | 18681.2877 | 19190.1017 | 19453.9337 | 19685.6902 | 19256.5404 | 19758.26 | 20547.3454 | 19947.5428 | 19947.5428 | 19947.5428 | 19947.5428 | 19947.5428 | 19947.5428 | 19947.5428 | 19947.5428 | 19947.5428 | 19947.5428 | 19947.5428 | 19947.5428 | 19947.5428 | 19947.5428 | 19947.5428 | 19947.5428 |  | 12285.6019 | 16666.5563 | 17864.1701 | 18049.0394 | 18165.9325 | 18423.6682 | 19033.1757 | 19365.4119 | 19999.3688 | 21927.5773 | 20336.6492 | 20025.0617 | 20444.3333 | 21361.9417 | 20739.8755 | 20739.8755 | 20739.8755 | 20739.8755 | 20739.8755 | 20739.8755 | 20739.8755 | 20739.8755 | 20739.8755 | 20739.8755 | 20739.8755 | 20739.8755 | 20739.8755 | 20739.8755 | 20739.8755 | 20739.8755
65% | 12096.053 | 16771.7086 | 17986.3189 | 18192.9151 | 18353.6159 | 18631.2528 | 19263.6638 | 19686.4953 | 20222.6877 | 20500.7161 | 20744.943 | 20292.7014 | 20821.4176 | 21652.9624 | 21020.8854 | 21020.8854 | 21020.8854 | 21020.8854 | 21020.8854 | 21020.8854 | 21020.8854 | 21020.8854 | 21020.8854 | 21020.8854 | 21020.8854 | 21020.8854 | 21020.8854 | 21020.8854 | 21020.8854 | 21020.8854 |  | 12946.6687 | 17563.3547 | 18825.4101 | 19020.2268 | 19143.4097 | 19415.0137 | 20057.3178 | 20407.431 | 21075.5001 | 23107.4621 | 21430.9289 | 21102.5754 | 21544.4074 | 22511.3907 | 21855.8521 | 21855.8521 | 21855.8521 | 21855.8521 | 21855.8521 | 21855.8521 | 21855.8521 | 21855.8521 | 21855.8521 | 21855.8521 | 21855.8521 | 21855.8521 | 21855.8521 | 21855.8521 | 21855.8521 | 21855.8521
60% | 13316.2645 | 18463.5854 | 19800.7217 | 20028.1587 | 20205.0705 | 20510.7145 | 21206.9211 | 21672.4066 | 22262.6883 | 22568.7633 | 22837.627 | 22339.7647 | 22921.8162 | 23837.2445 | 23141.4056 | 23141.4056 | 23141.4056 | 23141.4056 | 23141.4056 | 23141.4056 | 23141.4056 | 23141.4056 | 23141.4056 | 23141.4056 | 23141.4056 | 23141.4056 | 23141.4056 | 23141.4056 | 23141.4056 | 23141.4056 |  | 14252.6876 | 19335.0902 | 20724.4577 | 20938.927 | 21074.5362 | 21373.5387 | 22080.6365 | 22466.068 | 23201.5297 | 25438.4696 | 23592.813 | 23231.3363 | 23717.7389 | 24782.2684 | 24060.6012 | 24060.6012 | 24060.6012 | 24060.6012 | 24060.6012 | 24060.6012 | 24060.6012 | 24060.6012 | 24060.6012 | 24060.6012 | 24060.6012 | 24060.6012 | 24060.6012 | 24060.6012 | 24060.6012 | 24060.6012
55% | 14813.5078 | 20539.579 | 22027.0592 | 22280.0685 | 22476.8718 | 22816.8815 | 23591.3677 | 24109.191 | 24765.8423 | 25106.3315 | 25405.4256 | 24851.585 | 25499.0807 | 26517.4372 | 25743.3602 | 25743.3602 | 25743.3602 | 25743.3602 | 25743.3602 | 25743.3602 | 25743.3602 | 25743.3602 | 25743.3602 | 25743.3602 | 25743.3602 | 25743.3602 | 25743.3602 | 25743.3602 | 25743.3602 | 25743.3602 |  | 15855.2197 | 21509.0734 | 23054.6574 | 23293.241 | 23444.0977 | 23776.7193 | 24563.3211 | 24992.0894 | 25810.2444 | 28298.6996 | 26245.5225 | 25843.4024 | 26384.4947 | 27568.7169 | 26765.9075 | 26765.9075 | 26765.9075 | 26765.9075 | 26765.9075 | 26765.9075 | 26765.9075 | 26765.9075 | 26765.9075 | 26765.9075 | 26765.9075 | 26765.9075 | 26765.9075 | 26765.9075 | 26765.9075 | 26765.9075
50% | 15014.9247 | 20818.8523 | 22326.5575 | 22583.007 | 22782.4862 | 23127.1189 | 23912.1357 | 24436.9997 | 25102.5795 | 25447.6982 | 25750.859 | 25189.488 | 25845.7876 | 26877.9905 | 26093.3885 | 26093.3885 | 26093.3885 | 26093.3885 | 26093.3885 | 26093.3885 | 26093.3885 | 26093.3885 | 26093.3885 | 26093.3885 | 26093.3885 | 26093.3885 | 26093.3885 | 26093.3885 | 26093.3885 | 26093.3885 |  | 16070.8005 | 21801.5288 | 23368.1279 | 23609.9554 | 23762.8633 | 24100.0075 | 24897.3046 | 25331.9028 | 26161.1821 | 28683.4724 | 26602.3787 | 26194.791 | 26743.2404 | 27943.5643 | 27129.8392 | 27129.8392 | 27129.8392 | 27129.8392 | 27129.8392 | 27129.8392 | 27129.8392 | 27129.8392 | 27129.8392 | 27129.8392 | 27129.8392 | 27129.8392 | 27129.8392 | 27129.8392 | 27129.8392 | 27129.8392
45% | 11588.8305 | 16068.4223 | 17232.1005 | 17430.0335 | 17583.9957 | 17849.9904 | 18455.8826 | 18860.9836 | 19374.6918 | 19641.0617 | 19875.0474 | 19441.7696 | 19948.3153 | 20744.9909 | 20139.4188 | 20139.4188 | 20139.4188 | 20139.4188 | 20139.4188 | 20139.4188 | 20139.4188 | 20139.4188 | 20139.4188 | 20139.4188 | 20139.4188 | 20139.4188 | 20139.4188 | 20139.4188 | 20139.4188 | 20139.4188 |  | 12403.7774 | 16826.8724 | 18036.0061 | 18222.6536 | 18340.6711 | 18600.8859 | 19216.2564 | 19551.6884 | 20191.7433 | 22138.4993 | 20532.268 | 20217.6833 | 20640.988 | 21567.4228 | 20939.373 | 20939.373 | 20939.373 | 20939.373 | 20939.373 | 20939.373 | 20939.373 | 20939.373 | 20939.373 | 20939.373 | 20939.373 | 20939.373 | 20939.373 | 20939.373 | 20939.373 | 20939.373
40% | 5693.5395 | 7894.3425 | 8466.0523 | 8563.2959 | 8638.9368 | 8769.6188 | 9067.2909 | 9266.3151 | 9518.6977 | 9649.5639 | 9764.5201 | 9551.6527 | 9800.5162 | 10191.9194 | 9894.4045 | 9894.4045 | 9894.4045 | 9894.4045 | 9894.4045 | 9894.4045 | 9894.4045 | 9894.4045 | 9894.4045 | 9894.4045 | 9894.4045 | 9894.4045 | 9894.4045 | 9894.4045 | 9894.4045 | 9894.4045 |  | 6093.9192 | 8266.9656 | 8861.0075 | 8952.7065 | 9010.688 | 9138.5304 | 9440.8591 | 9605.6552 | 9920.1113 | 10876.5437 | 10087.4095 | 9932.8555 | 10140.8232 | 10595.9764 | 10287.4184 | 10287.4184 | 10287.4184 | 10287.4184 | 10287.4184 | 10287.4184 | 10287.4184 | 10287.4184 | 10287.4184 | 10287.4184 | 10287.4184 | 10287.4184 | 10287.4184 | 10287.4184 | 10287.4184 | 10287.4184
35% | 2127.9257 | 2950.4624 | 3164.1354 | 3200.4796 | 3228.75 | 3277.5916 | 3388.8447 | 3463.2288 | 3557.5552 | 3606.4657 | 3649.4298 | 3569.872 | 3662.8832 | 3809.1677 | 3697.9734 | 3697.9734 | 3697.9734 | 3697.9734 | 3697.9734 | 3697.9734 | 3697.9734 | 3697.9734 | 3697.9734 | 3697.9734 | 3697.9734 | 3697.9734 | 3697.9734 | 3697.9734 | 3697.9734 | 3697.9734 |  | 2277.5652 | 3089.728 | 3311.7475 | 3346.0195 | 3367.6897 | 3415.47 | 3528.4635 | 3590.0551 | 3707.5811 | 4065.0419 | 3770.1078 | 3712.3442 | 3790.0708 | 3960.1816 | 3844.8599 | 3844.8599 | 3844.8599 | 3844.8599 | 3844.8599 | 3844.8599 | 3844.8599 | 3844.8599 | 3844.8599 | 3844.8599 | 3844.8599 | 3844.8599 | 3844.8599 | 3844.8599 | 3844.8599 | 3844.8599
30% | 1061.2862 | 1471.5199 | 1578.0877 | 1596.2141 | 1610.3137 | 1634.673 | 1690.1596 | 1727.2581 | 1774.3027 | 1798.6964 | 1820.1244 | 1780.4456 | 1826.8342 | 1899.7925 | 1844.3351 | 1844.3351 | 1844.3351 | 1844.3351 | 1844.3351 | 1844.3351 | 1844.3351 | 1844.3351 | 1844.3351 | 1844.3351 | 1844.3351 | 1844.3351 | 1844.3351 | 1844.3351 | 1844.3351 | 1844.3351 |  | 1135.9177 | 1540.9775 | 1651.708 | 1668.8009 | 1679.6088 | 1703.4388 | 1759.7934 | 1790.5117 | 1849.1269 | 2027.4077 | 1880.3116 | 1851.5025 | 1890.268 | 1975.1094 | 1917.5936 | 1917.5936 | 1917.5936 | 1917.5936 | 1917.5936 | 1917.5936 | 1917.5936 | 1917.5936 | 1917.5936 | 1917.5936 | 1917.5936 | 1917.5936 | 1917.5936 | 1917.5936 | 1917.5936 | 1917.5936
25% | 625.6637 | 867.5102 | 930.3354 | 941.0215 | 949.3337 | 963.6944 | 996.4056 | 1018.2764 | 1046.0107 | 1060.3916 | 1073.0242 | 1049.6322 | 1076.9798 | 1119.9911 | 1087.2972 | 1087.2972 | 1087.2972 | 1087.2972 | 1087.2972 | 1087.2972 | 1087.2972 | 1087.2972 | 1087.2972 | 1087.2972 | 1087.2972 | 1087.2972 | 1087.2972 | 1087.2972 | 1087.2972 | 1087.2972 |  | 669.6615 | 908.4578 | 973.7371 | 983.8139 | 990.1855 | 1004.2341 | 1037.457 | 1055.5665 | 1090.1221 | 1195.2246 | 1108.5065 | 1091.5226 | 1114.3762 | 1164.393 | 1130.4855 | 1130.4855 | 1130.4855 | 1130.4855 | 1130.4855 | 1130.4855 | 1130.4855 | 1130.4855 | 1130.4855 | 1130.4855 | 1130.4855 | 1130.4855 | 1130.4855 | 1130.4855 | 1130.4855 | 1130.4855
20% | 316.1776 | 438.3942 | 470.1428 | 475.543 | 479.7435 | 487.0006 | 503.5312 | 514.5835 | 528.599 | 535.8664 | 542.2502 | 530.4291 | 544.2492 | 565.9848 | 549.463 | 549.463 | 549.463 | 549.463 | 549.463 | 549.463 | 549.463 | 549.463 | 549.463 | 549.463 | 549.463 | 549.463 | 549.463 | 549.463 | 549.463 | 549.463 |  | 338.4118 | 459.0869 | 492.0757 | 497.168 | 500.3879 | 507.4873 | 524.2764 | 533.428 | 550.8906 | 604.0039 | 560.1811 | 551.5983 | 563.1473 | 588.4232 | 571.2881 | 571.2881 | 571.2881 | 571.2881 | 571.2881 | 571.2881 | 571.2881 | 571.2881 | 571.2881 | 571.2881 | 571.2881 | 571.2881 | 571.2881 | 571.2881 | 571.2881 | 571.2881
15% | 128.8131 | 178.605 | 191.5396 | 193.7397 | 195.4511 | 198.4077 | 205.1423 | 209.6451 | 215.3552 | 218.3159 | 220.9167 | 216.1007 | 221.7311 | 230.5864 | 223.8553 | 223.8553 | 223.8553 | 223.8553 | 223.8553 | 223.8553 | 223.8553 | 223.8553 | 223.8553 | 223.8553 | 223.8553 | 223.8553 | 223.8553 | 223.8553 | 223.8553 | 223.8553 |  | 137.8715 | 187.0354 | 200.4753 | 202.5499 | 203.8617 | 206.7541 | 213.5941 | 217.3225 | 224.4369 | 246.0756 | 228.2219 | 224.7252 | 229.4304 | 239.728 | 232.747 | 232.747 | 232.747 | 232.747 | 232.747 | 232.747 | 232.747 | 232.747 | 232.747 | 232.747 | 232.747 | 232.747 | 232.747 | 232.747 | 232.747 | 232.747
10% | 51.8598 | 71.9059 | 77.1134 | 77.9991 | 78.6881 | 79.8784 | 82.5898 | 84.4026 | 86.7014 | 87.8934 | 88.9405 | 87.0016 | 89.2684 | 92.8335 | 90.1236 | 90.1236 | 90.1236 | 90.1236 | 90.1236 | 90.1236 | 90.1236 | 90.1236 | 90.1236 | 90.1236 | 90.1236 | 90.1236 | 90.1236 | 90.1236 | 90.1236 | 90.1236 |  | 55.5067 | 75.3 | 80.7108 | 81.5461 | 82.0742 | 83.2387 | 85.9924 | 87.4935 | 90.3577 | 99.0694 | 91.8816 | 90.4738 | 92.3681 | 96.5139 | 93.7033 | 93.7033 | 93.7033 | 93.7033 | 93.7033 | 93.7033 | 93.7033 | 93.7033 | 93.7033 | 93.7033 | 93.7033 | 93.7033 | 93.7033 | 93.7033 | 93.7033 | 93.7033
5% | 44.1645 | 61.236 | 65.6707 | 66.425 | 67.0118 | 68.0255 | 70.3345 | 71.8783 | 73.8361 | 74.8512 | 75.7429 | 74.0917 | 76.0221 | 79.0582 | 76.7504 | 76.7504 | 76.7504 | 76.7504 | 76.7504 | 76.7504 | 76.7504 | 76.7504 | 76.7504 | 76.7504 | 76.7504 | 76.7504 | 76.7504 | 76.7504 | 76.7504 | 76.7504 |  | 47.2702 | 64.1264 | 68.7344 | 69.4457 | 69.8954 | 70.8871 | 73.2323 | 74.5106 | 76.9498 | 84.3688 | 78.2475 | 77.0487 | 78.6618 | 82.1924 | 79.799 | 79.799 | 79.799 | 79.799 | 79.799 | 79.799 | 79.799 | 79.799 | 79.799 | 79.799 | 79.799 | 79.799 | 79.799 | 79.799 | 79.799 | 79.799
9.992e-14% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E @ R (MWh) | 118268.4368 | 163984.3799 | 175860.1598 | 177880.1417 | 179451.3847 | 182165.962 | 188349.3233 | 192483.5334 | 197726.1221 | 200444.5279 | 202832.442 | 198410.6765 | 203580.168 | 211710.5473 | 205530.4523 | 205530.4523 | 205530.4523 | 205530.4523 | 205530.4523 | 205530.4523 | 205530.4523 | 205530.4523 | 205530.4523 | 205530.4523 | 205530.4523 | 205530.4523 | 205530.4523 | 205530.4523 | 205530.4523 | 205530.4523 | E @ R (MWh) | 126585.2808 | 171724.6525 | 184064.3234 | 185969.1325 | 187173.5461 | 189829.1378 | 196109.2281 | 199532.4392 | 206064.4443 | 225931.832 | 209539.6283 | 206329.172 | 210649.1573 | 220103.7788 | 213694.29 | 213694.29 | 213694.29 | 213694.29 | 213694.29 | 213694.29 | 213694.29 | 213694.29 | 213694.29 | 213694.29 | 213694.29 | 213694.29 | 213694.29 | 213694.29 | 213694.29 | 213694.29
Option 7 Winter POE50 W E @ R (MWh) N 2 | 82787.9057 | 114789.066 | 123102.1118 | 124516.0992 | 125615.9693 | 127516.1734 | 131844.5263 | 134738.4734 | 138408.2855 | 140311.1695 | 141982.7094 | 138887.4736 | 142506.1176 | 148197.3831 | 143871.3166 | 143871.3166 | 143871.3166 | 143871.3166 | 143871.3166 | 143871.3166 | 143871.3166 | 143871.3166 | 143871.3166 | 143871.3166 | 143871.3166 | 143871.3166 | 143871.3166 | 143871.3166 | 143871.3166 | 143871.3166 | Option 7 Winter POE10 W E @ R (MWh) N 2 | 37975.5842 | 51517.3957 | 55219.297 | 55790.7397 | 56152.0638 | 56948.7413 | 58832.7684 | 59859.7318 | 61819.3333 | 67779.5496 | 62861.8885 | 61898.7516 | 63194.7472 | 66031.1336 | 64108.287 | 64108.287 | 64108.287 | 64108.287 | 64108.287 | 64108.287 | 64108.287 | 64108.287 | 64108.287 | 64108.287 | 64108.287 | 64108.287 | 64108.287 | 64108.287 | 64108.287 | 64108.287
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 85.8327 | 111.1071 | 117.7202 | 117.3233 | 117.3513 | 118.0293 | 119.8198 | 121.0174 | 122.1905 | 123.5626 | 124.8333 | 126.0676 | 126.2076 | 127.6483 | 126.5544 | 126.5544 | 126.5544 | 126.5544 | 126.5544 | 126.5544 | 126.5544 | 126.5544 | 126.5544 | 126.5544 | 126.5544 | 126.5544 | 126.5544 | 126.5544 | 126.5544 | 126.5544
98% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 42.4851 | 54.9952 | 58.2686 | 58.0721 | 58.0859 | 58.4216 | 59.3078 | 59.9006 | 60.4812 | 61.1604 | 61.7894 | 62.4003 | 62.4696 | 63.1827 | 62.6413 | 62.6413 | 62.6413 | 62.6413 | 62.6413 | 62.6413 | 62.6413 | 62.6413 | 62.6413 | 62.6413 | 62.6413 | 62.6413 | 62.6413 | 62.6413 | 62.6413 | 62.6413
97% | 18.864 | 25.0432 | 26.7251 | 26.6761 | 26.6743 | 26.866 | 27.0764 | 27.5082 | 27.8185 | 27.9869 | 28.171 | 28.3395 | 28.644 | 29.0219 | 28.9955 | 28.9955 | 28.9955 | 28.9955 | 28.9955 | 28.9955 | 28.9955 | 28.9955 | 28.9955 | 28.9955 | 28.9955 | 28.9955 | 28.9955 | 28.9955 | 28.9955 | 28.9955 |  | 84.1075 | 108.8738 | 115.354 | 114.965 | 114.9925 | 115.6569 | 117.4113 | 118.5849 | 119.7344 | 121.0789 | 122.3241 | 123.5336 | 123.6708 | 125.0825 | 124.0106 | 124.0106 | 124.0106 | 124.0106 | 124.0106 | 124.0106 | 124.0106 | 124.0106 | 124.0106 | 124.0106 | 124.0106 | 124.0106 | 124.0106 | 124.0106 | 124.0106 | 124.0106
95% | 92.8689 | 123.2894 | 131.5698 | 131.3286 | 131.3197 | 132.2634 | 133.299 | 135.4251 | 136.9528 | 137.7816 | 138.6878 | 139.5174 | 141.0166 | 142.8772 | 142.7472 | 142.7472 | 142.7472 | 142.7472 | 142.7472 | 142.7472 | 142.7472 | 142.7472 | 142.7472 | 142.7472 | 142.7472 | 142.7472 | 142.7472 | 142.7472 | 142.7472 | 142.7472 |  | 124.2203 | 160.7982 | 170.369 | 169.7945 | 169.8351 | 170.8163 | 173.4075 | 175.1408 | 176.8385 | 178.8242 | 180.6633 | 182.4496 | 182.6522 | 184.7373 | 183.1541 | 183.1541 | 183.1541 | 183.1541 | 183.1541 | 183.1541 | 183.1541 | 183.1541 | 183.1541 | 183.1541 | 183.1541 | 183.1541 | 183.1541 | 183.1541 | 183.1541 | 183.1541
90% | 161.0694 | 213.8301 | 228.1913 | 227.7731 | 227.7577 | 229.3944 | 231.1905 | 234.8778 | 237.5275 | 238.9649 | 240.5367 | 241.9755 | 244.5756 | 247.8027 | 247.5772 | 247.5772 | 247.5772 | 247.5772 | 247.5772 | 247.5772 | 247.5772 | 247.5772 | 247.5772 | 247.5772 | 247.5772 | 247.5772 | 247.5772 | 247.5772 | 247.5772 | 247.5772 |  | 538.6113 | 697.2109 | 738.7092 | 736.2183 | 736.3942 | 740.6488 | 751.884 | 759.3996 | 766.7606 | 775.3706 | 783.3448 | 791.0899 | 791.9686 | 801.0093 | 794.1448 | 794.1448 | 794.1448 | 794.1448 | 794.1448 | 794.1448 | 794.1448 | 794.1448 | 794.1448 | 794.1448 | 794.1448 | 794.1448 | 794.1448 | 794.1448 | 794.1448 | 794.1448
85% | 457.0889 | 606.8151 | 647.57 | 646.383 | 646.3393 | 650.9841 | 656.081 | 666.5452 | 674.0646 | 678.1436 | 682.6041 | 686.6874 | 694.0659 | 703.2239 | 702.5838 | 702.5838 | 702.5838 | 702.5838 | 702.5838 | 702.5838 | 702.5838 | 702.5838 | 702.5838 | 702.5838 | 702.5838 | 702.5838 | 702.5838 | 702.5838 | 702.5838 | 702.5838 |  | 509.4971 | 659.5238 | 698.779 | 696.4228 | 696.5891 | 700.6138 | 711.2416 | 718.351 | 725.3141 | 733.4587 | 741.0019 | 748.3283 | 749.1595 | 757.7115 | 751.218 | 751.218 | 751.218 | 751.218 | 751.218 | 751.218 | 751.218 | 751.218 | 751.218 | 751.218 | 751.218 | 751.218 | 751.218 | 751.218 | 751.218 | 751.218
80% | 638.4734 | 847.6148 | 904.5422 | 902.8842 | 902.8231 | 909.3111 | 916.4306 | 931.0473 | 941.5505 | 947.2482 | 953.4787 | 959.1824 | 969.4889 | 982.2811 | 981.3869 | 981.3869 | 981.3869 | 981.3869 | 981.3869 | 981.3869 | 981.3869 | 981.3869 | 981.3869 | 981.3869 | 981.3869 | 981.3869 | 981.3869 | 981.3869 | 981.3869 | 981.3869 |  | 355.8393 | 460.6198 | 488.0361 | 486.3905 | 486.5067 | 489.3176 | 496.7402 | 501.7054 | 506.5685 | 512.2568 | 517.5251 | 522.642 | 523.2225 | 529.1954 | 524.6602 | 524.6602 | 524.6602 | 524.6602 | 524.6602 | 524.6602 | 524.6602 | 524.6602 | 524.6602 | 524.6602 | 524.6602 | 524.6602 | 524.6602 | 524.6602 | 524.6602 | 524.6602
75% | 1664.3841 | 2209.5776 | 2357.9769 | 2353.655 | 2353.4957 | 2370.4087 | 2388.968 | 2427.0709 | 2454.4511 | 2469.3039 | 2485.5456 | 2500.414 | 2527.2813 | 2560.6281 | 2558.2972 | 2558.2972 | 2558.2972 | 2558.2972 | 2558.2972 | 2558.2972 | 2558.2972 | 2558.2972 | 2558.2972 | 2558.2972 | 2558.2972 | 2558.2972 | 2558.2972 | 2558.2972 | 2558.2972 | 2558.2972 |  | 635.1192 | 822.1366 | 871.0705 | 868.1333 | 868.3407 | 873.3577 | 886.6059 | 895.4682 | 904.1481 | 914.3008 | 923.7039 | 932.8368 | 933.8729 | 944.5335 | 936.439 | 936.439 | 936.439 | 936.439 | 936.439 | 936.439 | 936.439 | 936.439 | 936.439 | 936.439 | 936.439 | 936.439 | 936.439 | 936.439 | 936.439 | 936.439
70% | 2875.5487 | 3817.4772 | 4073.866 | 4066.399 | 4066.1238 | 4095.3442 | 4127.4091 | 4193.2394 | 4240.5439 | 4266.205 | 4294.2657 | 4319.9539 | 4366.3723 | 4423.9855 | 4419.9585 | 4419.9585 | 4419.9585 | 4419.9585 | 4419.9585 | 4419.9585 | 4419.9585 | 4419.9585 | 4419.9585 | 4419.9585 | 4419.9585 | 4419.9585 | 4419.9585 | 4419.9585 | 4419.9585 | 4419.9585 |  | 1157.0168 | 1497.7123 | 1586.8569 | 1581.5061 | 1581.8839 | 1591.0234 | 1615.1582 | 1631.3028 | 1647.1153 | 1665.6109 | 1682.7407 | 1699.3783 | 1701.266 | 1720.6867 | 1705.9407 | 1705.9407 | 1705.9407 | 1705.9407 | 1705.9407 | 1705.9407 | 1705.9407 | 1705.9407 | 1705.9407 | 1705.9407 | 1705.9407 | 1705.9407 | 1705.9407 | 1705.9407 | 1705.9407 | 1705.9407
65% | 7222.0048 | 9587.679 | 10231.6052 | 10212.8518 | 10212.1606 | 10285.5483 | 10366.0801 | 10531.4141 | 10650.2206 | 10714.6689 | 10785.1441 | 10849.6604 | 10966.2413 | 11110.9382 | 11100.8242 | 11100.8242 | 11100.8242 | 11100.8242 | 11100.8242 | 11100.8242 | 11100.8242 | 11100.8242 | 11100.8242 | 11100.8242 | 11100.8242 | 11100.8242 | 11100.8242 | 11100.8242 | 11100.8242 | 11100.8242 |  | 1455.7061 | 1884.3537 | 1996.5114 | 1989.7793 | 1990.2546 | 2001.7536 | 2032.1189 | 2052.4313 | 2072.3259 | 2095.5961 | 2117.1482 | 2138.0809 | 2140.4558 | 2164.8901 | 2146.3373 | 2146.3373 | 2146.3373 | 2146.3373 | 2146.3373 | 2146.3373 | 2146.3373 | 2146.3373 | 2146.3373 | 2146.3373 | 2146.3373 | 2146.3373 | 2146.3373 | 2146.3373 | 2146.3373 | 2146.3373
60% | 10556.5772 | 14014.5398 | 14955.7822 | 14928.3698 | 14927.3596 | 15034.6321 | 15152.3473 | 15394.0201 | 15567.6823 | 15661.888 | 15764.9032 | 15859.2082 | 16029.6174 | 16241.1243 | 16226.3403 | 16226.3403 | 16226.3403 | 16226.3403 | 16226.3403 | 16226.3403 | 16226.3403 | 16226.3403 | 16226.3403 | 16226.3403 | 16226.3403 | 16226.3403 | 16226.3403 | 16226.3403 | 16226.3403 | 16226.3403 |  | 2277.9105 | 2948.6646 | 3124.1707 | 3113.6361 | 3114.3799 | 3132.3737 | 3179.8897 | 3211.675 | 3242.8062 | 3279.2199 | 3312.9449 | 3345.7006 | 3349.4169 | 3387.6521 | 3358.6203 | 3358.6203 | 3358.6203 | 3358.6203 | 3358.6203 | 3358.6203 | 3358.6203 | 3358.6203 | 3358.6203 | 3358.6203 | 3358.6203 | 3358.6203 | 3358.6203 | 3358.6203 | 3358.6203 | 3358.6203
55% | 11937.0341 | 15847.1857 | 16911.512 | 16880.515 | 16879.3726 | 17000.6729 | 17133.7814 | 17407.0571 | 17603.4287 | 17709.9534 | 17826.4396 | 17933.0767 | 18125.7699 | 18364.935 | 18348.2178 | 18348.2178 | 18348.2178 | 18348.2178 | 18348.2178 | 18348.2178 | 18348.2178 | 18348.2178 | 18348.2178 | 18348.2178 | 18348.2178 | 18348.2178 | 18348.2178 | 18348.2178 | 18348.2178 | 18348.2178 |  | 4377.3623 | 5666.3214 | 6003.5838 | 5983.3401 | 5984.7694 | 6019.3473 | 6110.6567 | 6171.737 | 6231.5606 | 6301.5352 | 6366.343 | 6429.2884 | 6436.4298 | 6509.9048 | 6454.1156 | 6454.1156 | 6454.1156 | 6454.1156 | 6454.1156 | 6454.1156 | 6454.1156 | 6454.1156 | 6454.1156 | 6454.1156 | 6454.1156 | 6454.1156 | 6454.1156 | 6454.1156 | 6454.1156 | 6454.1156
50% | 15327.7148 | 20348.5339 | 21715.179 | 21675.3774 | 21673.9105 | 21829.6658 | 22000.5834 | 22351.4823 | 22603.6327 | 22740.4155 | 22889.9893 | 23026.9163 | 23274.3434 | 23581.4427 | 23559.977 | 23559.977 | 23559.977 | 23559.977 | 23559.977 | 23559.977 | 23559.977 | 23559.977 | 23559.977 | 23559.977 | 23559.977 | 23559.977 | 23559.977 | 23559.977 | 23559.977 | 23559.977 |  | 9714.4123 | 12574.9205 | 13323.3863 | 13278.4606 | 13281.6325 | 13358.3693 | 13561.0066 | 13696.5584 | 13829.3213 | 13984.6116 | 14128.4356 | 14268.1263 | 14283.9748 | 14447.0334 | 14323.224 | 14323.224 | 14323.224 | 14323.224 | 14323.224 | 14323.224 | 14323.224 | 14323.224 | 14323.224 | 14323.224 | 14323.224 | 14323.224 | 14323.224 | 14323.224 | 14323.224 | 14323.224
45% | 20411.3174 | 27097.3455 | 28917.2533 | 28864.251 | 28862.2976 | 29069.7109 | 29297.3152 | 29764.5935 | 30100.3723 | 30282.5206 | 30481.7021 | 30664.0425 | 30993.5314 | 31402.4836 | 31373.8985 | 31373.8985 | 31373.8985 | 31373.8985 | 31373.8985 | 31373.8985 | 31373.8985 | 31373.8985 | 31373.8985 | 31373.8985 | 31373.8985 | 31373.8985 | 31373.8985 | 31373.8985 | 31373.8985 | 31373.8985 |  | 14720.4239 | 19055.0036 | 20189.1672 | 20121.0905 | 20125.8971 | 20242.1776 | 20549.2377 | 20754.6417 | 20955.8197 | 21191.1339 | 21409.073 | 21620.7489 | 21644.7644 | 21891.85 | 21704.2393 | 21704.2393 | 21704.2393 | 21704.2393 | 21704.2393 | 21704.2393 | 21704.2393 | 21704.2393 | 21704.2393 | 21704.2393 | 21704.2393 | 21704.2393 | 21704.2393 | 21704.2393 | 21704.2393 | 21704.2393
40% | 14315.8312 | 19005.1929 | 20281.6168 | 20244.4427 | 20243.0727 | 20388.5455 | 20548.1797 | 20875.9135 | 21111.4178 | 21239.1706 | 21378.87 | 21506.7576 | 21737.8504 | 22024.6761 | 22004.6275 | 22004.6275 | 22004.6275 | 22004.6275 | 22004.6275 | 22004.6275 | 22004.6275 | 22004.6275 | 22004.6275 | 22004.6275 | 22004.6275 | 22004.6275 | 22004.6275 | 22004.6275 | 22004.6275 | 22004.6275 |  | 15242.3215 | 19730.5793 | 20904.9535 | 20834.4632 | 20839.4402 | 20959.8434 | 21277.7899 | 21490.4763 | 21698.7869 | 21942.444 | 22168.1098 | 22387.2904 | 22412.1574 | 22668.0032 | 22473.741 | 22473.741 | 22473.741 | 22473.741 | 22473.741 | 22473.741 | 22473.741 | 22473.741 | 22473.741 | 22473.741 | 22473.741 | 22473.741 | 22473.741 | 22473.741 | 22473.741 | 22473.741
35% | 7422.2532 | 9853.5218 | 10515.3025 | 10496.0291 | 10495.3188 | 10570.7413 | 10653.506 | 10823.4244 | 10945.5251 | 11011.7604 | 11084.1896 | 11150.4949 | 11270.3083 | 11419.0173 | 11408.6228 | 11408.6228 | 11408.6228 | 11408.6228 | 11408.6228 | 11408.6228 | 11408.6228 | 11408.6228 | 11408.6228 | 11408.6228 | 11408.6228 | 11408.6228 | 11408.6228 | 11408.6228 | 11408.6228 | 11408.6228 |  | 20759.9869 | 26872.9779 | 28472.4713 | 28376.4638 | 28383.2424 | 28547.2311 | 28980.2731 | 29269.9512 | 29553.6695 | 29885.5295 | 30192.8856 | 30491.4088 | 30525.2776 | 30873.7386 | 30609.1541 | 30609.1541 | 30609.1541 | 30609.1541 | 30609.1541 | 30609.1541 | 30609.1541 | 30609.1541 | 30609.1541 | 30609.1541 | 30609.1541 | 30609.1541 | 30609.1541 | 30609.1541 | 30609.1541 | 30609.1541
30% | 3452.1096 | 4582.899 | 4890.695 | 4881.7308 | 4881.4005 | 4916.4797 | 4954.9738 | 5034.0033 | 5090.7926 | 5121.5988 | 5155.2859 | 5186.1246 | 5241.8501 | 5311.0151 | 5306.1806 | 5306.1806 | 5306.1806 | 5306.1806 | 5306.1806 | 5306.1806 | 5306.1806 | 5306.1806 | 5306.1806 | 5306.1806 | 5306.1806 | 5306.1806 | 5306.1806 | 5306.1806 | 5306.1806 | 5306.1806 |  | 19183.5111 | 24832.2926 | 26310.3234 | 26221.6065 | 26227.8703 | 26379.406 | 26779.5636 | 27047.2441 | 27309.4173 | 27616.0765 | 27900.0925 | 28175.9464 | 28207.2432 | 28529.2428 | 28284.7504 | 28284.7504 | 28284.7504 | 28284.7504 | 28284.7504 | 28284.7504 | 28284.7504 | 28284.7504 | 28284.7504 | 28284.7504 | 28284.7504 | 28284.7504 | 28284.7504 | 28284.7504 | 28284.7504 | 28284.7504
25% | 2357.031 | 3129.1112 | 3339.2681 | 3333.1476 | 3332.922 | 3356.8734 | 3383.1564 | 3437.1161 | 3475.8908 | 3496.9246 | 3519.9255 | 3540.9815 | 3579.0298 | 3626.2542 | 3622.9533 | 3622.9533 | 3622.9533 | 3622.9533 | 3622.9533 | 3622.9533 | 3622.9533 | 3622.9533 | 3622.9533 | 3622.9533 | 3622.9533 | 3622.9533 | 3622.9533 | 3622.9533 | 3622.9533 | 3622.9533 |  | 5533.3008 | 7162.6379 | 7588.9618 | 7563.3722 | 7565.179 | 7608.888 | 7724.3096 | 7801.5195 | 7877.1409 | 7965.5938 | 8047.5155 | 8127.0829 | 8136.1102 | 8228.9879 | 8158.4664 | 8158.4664 | 8158.4664 | 8158.4664 | 8158.4664 | 8158.4664 | 8158.4664 | 8158.4664 | 8158.4664 | 8158.4664 | 8158.4664 | 8158.4664 | 8158.4664 | 8158.4664 | 8158.4664 | 8158.4664
20% | 1427.8587 | 1895.5749 | 2022.8852 | 2019.1774 | 2019.0408 | 2033.5502 | 2049.4721 | 2082.1602 | 2105.6494 | 2118.3914 | 2132.325 | 2145.0805 | 2168.1297 | 2196.7376 | 2194.738 | 2194.738 | 2194.738 | 2194.738 | 2194.738 | 2194.738 | 2194.738 | 2194.738 | 2194.738 | 2194.738 | 2194.738 | 2194.738 | 2194.738 | 2194.738 | 2194.738 | 2194.738 |  | 1484.8203 | 1922.0408 | 2036.4417 | 2029.5749 | 2030.0597 | 2041.7887 | 2072.7613 | 2093.48 | 2113.7724 | 2137.5081 | 2159.4912 | 2180.8425 | 2183.2649 | 2208.1879 | 2189.264 | 2189.264 | 2189.264 | 2189.264 | 2189.264 | 2189.264 | 2189.264 | 2189.264 | 2189.264 | 2189.264 | 2189.264 | 2189.264 | 2189.264 | 2189.264 | 2189.264 | 2189.264
15% | 914.1778 | 1213.6303 | 1295.1399 | 1292.766 | 1292.6786 | 1301.9681 | 1312.162 | 1333.0904 | 1348.1292 | 1356.2872 | 1365.2081 | 1373.3747 | 1388.1318 | 1406.4479 | 1405.1676 | 1405.1676 | 1405.1676 | 1405.1676 | 1405.1676 | 1405.1676 | 1405.1676 | 1405.1676 | 1405.1676 | 1405.1676 | 1405.1676 | 1405.1676 | 1405.1676 | 1405.1676 | 1405.1676 | 1405.1676 |  | 818.9695 | 1060.1234 | 1123.2225 | 1119.4351 | 1119.7025 | 1126.1718 | 1143.255 | 1154.6827 | 1165.8752 | 1178.9669 | 1191.0919 | 1202.8685 | 1204.2046 | 1217.9511 | 1207.5134 | 1207.5134 | 1207.5134 | 1207.5134 | 1207.5134 | 1207.5134 | 1207.5134 | 1207.5134 | 1207.5134 | 1207.5134 | 1207.5134 | 1207.5134 | 1207.5134 | 1207.5134 | 1207.5134 | 1207.5134
10% | 611.8703 | 812.2975 | 866.8529 | 865.264 | 865.2055 | 871.4231 | 878.246 | 892.2536 | 902.3193 | 907.7795 | 913.7504 | 919.2164 | 929.0935 | 941.3527 | 940.4958 | 940.4958 | 940.4958 | 940.4958 | 940.4958 | 940.4958 | 940.4958 | 940.4958 | 940.4958 | 940.4958 | 940.4958 | 940.4958 | 940.4958 | 940.4958 | 940.4958 | 940.4958 |  | 191.3984 | 247.7576 | 262.5043 | 261.6191 | 261.6816 | 263.1935 | 267.186 | 269.8567 | 272.4725 | 275.5321 | 278.3658 | 281.118 | 281.4303 | 284.643 | 282.2036 | 282.2036 | 282.2036 | 282.2036 | 282.2036 | 282.2036 | 282.2036 | 282.2036 | 282.2036 | 282.2036 | 282.2036 | 282.2036 | 282.2036 | 282.2036 | 282.2036 | 282.2036
5% | 435.3228 | 577.9192 | 616.7333 | 615.6029 | 615.5612 | 619.9848 | 624.8391 | 634.805 | 641.9663 | 645.8511 | 650.0991 | 653.988 | 661.0151 | 669.7371 | 669.1274 | 669.1274 | 669.1274 | 669.1274 | 669.1274 | 669.1274 | 669.1274 | 669.1274 | 669.1274 | 669.1274 | 669.1274 | 669.1274 | 669.1274 | 669.1274 | 669.1274 | 669.1274 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9.992e-14% | 38.2117 | 50.7285 | 54.1355 | 54.0363 | 54.0326 | 54.4209 | 54.847 | 55.7218 | 56.3504 | 56.6914 | 57.0643 | 57.4056 | 58.0224 | 58.788 | 58.7345 | 58.7345 | 58.7345 | 58.7345 | 58.7345 | 58.7345 | 58.7345 | 58.7345 | 58.7345 | 58.7345 | 58.7345 | 58.7345 | 58.7345 | 58.7345 | 58.7345 | 58.7345 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E @ R (MWh) | 102337.6118 | 135859.8063 | 144984.402 | 144718.661 | 144708.8672 | 145748.789 | 146889.9441 | 149232.7692 | 150916.2863 | 151829.5355 | 152828.1856 | 153742.3981 | 155394.3791 | 157444.7704 | 157301.4516 | 157301.4516 | 157301.4516 | 157301.4516 | 157301.4516 | 157301.4516 | 157301.4516 | 157301.4516 | 157301.4516 | 157301.4516 | 157301.4516 | 157301.4516 | 157301.4516 | 157301.4516 | 157301.4516 | 157301.4516 | E @ R (MWh) | 99292.8528 | 128530.651 | 136180.8614 | 135721.6674 | 135754.0887 | 136538.4294 | 138609.6244 | 139995.1247 | 141352.1196 | 142939.3714 | 144409.4236 | 145837.2289 | 145999.2196 | 147665.8725 | 146400.3925 | 146400.3925 | 146400.3925 | 146400.3925 | 146400.3925 | 146400.3925 | 146400.3925 | 146400.3925 | 146400.3925 | 146400.3925 | 146400.3925 | 146400.3925 | 146400.3925 | 146400.3925 | 146400.3925 | 146400.3925
Option 7 Summer POE50 W E @ R (MWh) N 2 | 71636.3283 | 95101.8644 | 101489.0814 | 101303.0627 | 101296.207 | 102024.1523 | 102822.9609 | 104462.9384 | 105641.4004 | 106280.6749 | 106979.7299 | 107619.6787 | 108776.0654 | 110211.3393 | 110111.0161 | 110111.0161 | 110111.0161 | 110111.0161 | 110111.0161 | 110111.0161 | 110111.0161 | 110111.0161 | 110111.0161 | 110111.0161 | 110111.0161 | 110111.0161 | 110111.0161 | 110111.0161 | 110111.0161 | 110111.0161 | Option 7 Summer POE10 W E @ R (MWh) N 2 | 29787.8558 | 38559.1953 | 40854.2584 | 40716.5002 | 40726.2266 | 40961.5288 | 41582.8873 | 41998.5374 | 42405.6359 | 42881.8114 | 43322.8271 | 43751.1687 | 43799.7659 | 44299.7618 | 43920.1178 | 43920.1178 | 43920.1178 | 43920.1178 | 43920.1178 | 43920.1178 | 43920.1178 | 43920.1178 | 43920.1178 | 43920.1178 | 43920.1178 | 43920.1178 | 43920.1178 | 43920.1178 | 43920.1178 | 43920.1178
Option 8 -
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | 66.5813 | 92.3179 | 99.0036 | 100.1408 | 101.0254 | 102.5536 | 106.0346 | 108.362 | 111.3134 | 112.8438 | 114.1881 | 111.6988 | 114.6091 | 119.1862 | 115.707 | 115.707 | 115.707 | 115.707 | 115.707 | 115.707 | 115.707 | 115.707 | 115.707 | 115.707 | 115.707 | 115.707 | 115.707 | 115.707 | 115.707 | 115.707 |  | 71.2634 | 96.6755 | 103.6223 | 104.6946 | 105.3727 | 106.8677 | 110.4032 | 112.3303 | 116.0076 | 127.1923 | 117.9641 | 116.1567 | 118.5887 | 123.9113 | 120.303 | 120.303 | 120.303 | 120.303 | 120.303 | 120.303 | 120.303 | 120.303 | 120.303 | 120.303 | 120.303 | 120.303 | 120.303 | 120.303 | 120.303 | 120.303
98% | 79.0946 | 109.6681 | 117.6103 | 118.9612 | 120.012 | 121.8275 | 125.9627 | 128.7276 | 132.2337 | 134.0516 | 135.6486 | 132.6915 | 136.1487 | 141.586 | 137.453 | 137.453 | 137.453 | 137.453 | 137.453 | 137.453 | 137.453 | 137.453 | 137.453 | 137.453 | 137.453 | 137.453 | 137.453 | 137.453 | 137.453 | 137.453 |  | 84.6567 | 114.8446 | 123.097 | 124.3709 | 125.1764 | 126.9524 | 131.1523 | 133.4417 | 137.8101 | 151.0968 | 140.1342 | 137.9871 | 140.8762 | 147.1992 | 142.9127 | 142.9127 | 142.9127 | 142.9127 | 142.9127 | 142.9127 | 142.9127 | 142.9127 | 142.9127 | 142.9127 | 142.9127 | 142.9127 | 142.9127 | 142.9127 | 142.9127 | 142.9127
97% | 156.5832 | 217.1095 | 232.8326 | 235.507 | 237.5873 | 241.1813 | 249.3678 | 254.8414 | 261.7824 | 265.3814 | 268.543 | 262.6887 | 269.5329 | 280.2972 | 272.115 | 272.115 | 272.115 | 272.115 | 272.115 | 272.115 | 272.115 | 272.115 | 272.115 | 272.115 | 272.115 | 272.115 | 272.115 | 272.115 | 272.115 | 272.115 |  | 167.5944 | 227.3573 | 243.6946 | 246.2165 | 247.8111 | 251.327 | 259.6417 | 264.1739 | 272.822 | 299.1257 | 277.423 | 273.1725 | 278.892 | 291.4096 | 282.9237 | 282.9237 | 282.9237 | 282.9237 | 282.9237 | 282.9237 | 282.9237 | 282.9237 | 282.9237 | 282.9237 | 282.9237 | 282.9237 | 282.9237 | 282.9237 | 282.9237 | 282.9237
95% | 462.5227 | 641.3081 | 687.7517 | 695.6514 | 701.7962 | 712.4124 | 736.5942 | 752.7622 | 773.2648 | 783.8959 | 793.2346 | 775.942 | 796.1588 | 827.9549 | 803.7859 | 803.7859 | 803.7859 | 803.7859 | 803.7859 | 803.7859 | 803.7859 | 803.7859 | 803.7859 | 803.7859 | 803.7859 | 803.7859 | 803.7859 | 803.7859 | 803.7859 | 803.7859 |  | 495.0481 | 671.5786 | 719.8364 | 727.2857 | 731.996 | 742.3814 | 766.9415 | 780.329 | 805.8742 | 883.5714 | 819.4649 | 806.9095 | 823.8041 | 860.7791 | 835.7129 | 835.7129 | 835.7129 | 835.7129 | 835.7129 | 835.7129 | 835.7129 | 835.7129 | 835.7129 | 835.7129 | 835.7129 | 835.7129 | 835.7129 | 835.7129 | 835.7129 | 835.7129
90% | 2550.165 | 3535.9158 | 3791.9875 | 3835.5434 | 3869.4233 | 3927.9564 | 4061.2852 | 4150.4292 | 4263.4726 | 4322.0883 | 4373.5777 | 4278.2333 | 4389.7006 | 4565.012 | 4431.7536 | 4431.7536 | 4431.7536 | 4431.7536 | 4431.7536 | 4431.7536 | 4431.7536 | 4431.7536 | 4431.7536 | 4431.7536 | 4431.7536 | 4431.7536 | 4431.7536 | 4431.7536 | 4431.7536 | 4431.7536 |  | 2729.4971 | 3702.8155 | 3968.8899 | 4009.9623 | 4035.9325 | 4093.1938 | 4228.6083 | 4302.4214 | 4443.2678 | 4871.6587 | 4518.2015 | 4448.976 | 4542.1258 | 4745.9912 | 4607.7865 | 4607.7865 | 4607.7865 | 4607.7865 | 4607.7865 | 4607.7865 | 4607.7865 | 4607.7865 | 4607.7865 | 4607.7865 | 4607.7865 | 4607.7865 | 4607.7865 | 4607.7865 | 4607.7865 | 4607.7865
85% | 6229.8705 | 8637.9889 | 9263.5537 | 9369.9577 | 9452.724 | 9595.7162 | 9921.4289 | 10139.2013 | 10415.3582 | 10558.5521 | 10684.3371 | 10451.4176 | 10723.7241 | 11151.9973 | 10826.4566 | 10826.4566 | 10826.4566 | 10826.4566 | 10826.4566 | 10826.4566 | 10826.4566 | 10826.4566 | 10826.4566 | 10826.4566 | 10826.4566 | 10826.4566 | 10826.4566 | 10826.4566 | 10826.4566 | 10826.4566 |  | 6667.9659 | 9045.7131 | 9695.7136 | 9796.0508 | 9859.4941 | 9999.3792 | 10330.1872 | 10510.5072 | 10854.585 | 11901.1132 | 11037.6427 | 10868.5297 | 11096.0879 | 11594.1165 | 11256.4923 | 11256.4923 | 11256.4923 | 11256.4923 | 11256.4923 | 11256.4923 | 11256.4923 | 11256.4923 | 11256.4923 | 11256.4923 | 11256.4923 | 11256.4923 | 11256.4923 | 11256.4923 | 11256.4923 | 11256.4923
80% | 9683.0656 | 13425.9956 | 14398.3087 | 14563.692 | 14692.3353 | 14914.5876 | 15420.8418 | 15759.3246 | 16188.5543 | 16411.1201 | 16606.6272 | 16244.6013 | 16667.8463 | 17333.5099 | 16827.5231 | 16827.5231 | 16827.5231 | 16827.5231 | 16827.5231 | 16827.5231 | 16827.5231 | 16827.5231 | 16827.5231 | 16827.5231 | 16827.5231 | 16827.5231 | 16827.5231 | 16827.5231 | 16827.5231 | 16827.5231 |  | 10363.9958 | 14059.7198 | 15070.0133 | 15225.967 | 15324.5767 | 15541.9996 | 16056.1734 | 16336.4441 | 16871.243 | 18497.858 | 17155.7689 | 16892.9172 | 17246.6101 | 18020.6942 | 17495.9261 | 17495.9261 | 17495.9261 | 17495.9261 | 17495.9261 | 17495.9261 | 17495.9261 | 17495.9261 | 17495.9261 | 17495.9261 | 17495.9261 | 17495.9261 | 17495.9261 | 17495.9261 | 17495.9261 | 17495.9261
75% | 10683.1238 | 14812.6201 | 15885.3529 | 16067.8168 | 16209.7463 | 16454.9526 | 17013.4923 | 17386.9332 | 17860.4934 | 18106.0455 | 18321.7445 | 17922.3288 | 18389.2862 | 19123.699 | 18565.4543 | 18565.4543 | 18565.4543 | 18565.4543 | 18565.4543 | 18565.4543 | 18565.4543 | 18565.4543 | 18565.4543 | 18565.4543 | 18565.4543 | 18565.4543 | 18565.4543 | 18565.4543 | 18565.4543 | 18565.4543 |  | 11434.3798 | 15511.7948 | 16626.4305 | 16798.4909 | 16907.2849 | 17147.1631 | 17714.4402 | 18023.6571 | 18613.6895 | 20408.2999 | 18927.601 | 18637.6022 | 19027.8242 | 19881.855 | 19302.8894 | 19302.8894 | 19302.8894 | 19302.8894 | 19302.8894 | 19302.8894 | 19302.8894 | 19302.8894 | 19302.8894 | 19302.8894 | 19302.8894 | 19302.8894 | 19302.8894 | 19302.8894 | 19302.8894 | 19302.8894
70% | 11478.4193 | 15915.3323 | 17067.9236 | 17263.9709 | 17416.4662 | 17679.9267 | 18280.0463 | 18681.2877 | 19190.1017 | 19453.9337 | 19685.6902 | 19256.5404 | 19758.26 | 20547.3454 | 19947.5428 | 19947.5428 | 19947.5428 | 19947.5428 | 19947.5428 | 19947.5428 | 19947.5428 | 19947.5428 | 19947.5428 | 19947.5428 | 19947.5428 | 19947.5428 | 19947.5428 | 19947.5428 | 19947.5428 | 19947.5428 |  | 12285.6019 | 16666.5563 | 17864.1701 | 18049.0394 | 18165.9325 | 18423.6682 | 19033.1757 | 19365.4119 | 19999.3688 | 21927.5773 | 20336.6492 | 20025.0617 | 20444.3333 | 21361.9417 | 20739.8755 | 20739.8755 | 20739.8755 | 20739.8755 | 20739.8755 | 20739.8755 | 20739.8755 | 20739.8755 | 20739.8755 | 20739.8755 | 20739.8755 | 20739.8755 | 20739.8755 | 20739.8755 | 20739.8755 | 20739.8755
65% | 12096.053 | 16771.7086 | 17986.3189 | 18192.9151 | 18353.6159 | 18631.2528 | 19263.6638 | 19686.4953 | 20222.6877 | 20500.7161 | 20744.943 | 20292.7014 | 20821.4176 | 21652.9624 | 21020.8854 | 21020.8854 | 21020.8854 | 21020.8854 | 21020.8854 | 21020.8854 | 21020.8854 | 21020.8854 | 21020.8854 | 21020.8854 | 21020.8854 | 21020.8854 | 21020.8854 | 21020.8854 | 21020.8854 | 21020.8854 |  | 12946.6687 | 17563.3547 | 18825.4101 | 19020.2268 | 19143.4097 | 19415.0137 | 20057.3178 | 20407.431 | 21075.5001 | 23107.4621 | 21430.9289 | 21102.5754 | 21544.4074 | 22511.3907 | 21855.8521 | 21855.8521 | 21855.8521 | 21855.8521 | 21855.8521 | 21855.8521 | 21855.8521 | 21855.8521 | 21855.8521 | 21855.8521 | 21855.8521 | 21855.8521 | 21855.8521 | 21855.8521 | 21855.8521 | 21855.8521
60% | 13316.2645 | 18463.5854 | 19800.7217 | 20028.1587 | 20205.0705 | 20510.7145 | 21206.9211 | 21672.4066 | 22262.6883 | 22568.7633 | 22837.627 | 22339.7647 | 22921.8162 | 23837.2445 | 23141.4056 | 23141.4056 | 23141.4056 | 23141.4056 | 23141.4056 | 23141.4056 | 23141.4056 | 23141.4056 | 23141.4056 | 23141.4056 | 23141.4056 | 23141.4056 | 23141.4056 | 23141.4056 | 23141.4056 | 23141.4056 |  | 14252.6876 | 19335.0902 | 20724.4577 | 20938.927 | 21074.5362 | 21373.5387 | 22080.6365 | 22466.068 | 23201.5297 | 25438.4696 | 23592.813 | 23231.3363 | 23717.7389 | 24782.2684 | 24060.6012 | 24060.6012 | 24060.6012 | 24060.6012 | 24060.6012 | 24060.6012 | 24060.6012 | 24060.6012 | 24060.6012 | 24060.6012 | 24060.6012 | 24060.6012 | 24060.6012 | 24060.6012 | 24060.6012 | 24060.6012
55% | 14813.5078 | 20539.579 | 22027.0592 | 22280.0685 | 22476.8718 | 22816.8815 | 23591.3677 | 24109.191 | 24765.8423 | 25106.3315 | 25405.4256 | 24851.585 | 25499.0807 | 26517.4372 | 25743.3602 | 25743.3602 | 25743.3602 | 25743.3602 | 25743.3602 | 25743.3602 | 25743.3602 | 25743.3602 | 25743.3602 | 25743.3602 | 25743.3602 | 25743.3602 | 25743.3602 | 25743.3602 | 25743.3602 | 25743.3602 |  | 15855.2197 | 21509.0734 | 23054.6574 | 23293.241 | 23444.0977 | 23776.7193 | 24563.3211 | 24992.0894 | 25810.2444 | 28298.6996 | 26245.5225 | 25843.4024 | 26384.4947 | 27568.7169 | 26765.9075 | 26765.9075 | 26765.9075 | 26765.9075 | 26765.9075 | 26765.9075 | 26765.9075 | 26765.9075 | 26765.9075 | 26765.9075 | 26765.9075 | 26765.9075 | 26765.9075 | 26765.9075 | 26765.9075 | 26765.9075
50% | 15014.9247 | 20818.8523 | 22326.5575 | 22583.007 | 22782.4862 | 23127.1189 | 23912.1357 | 24436.9997 | 25102.5795 | 25447.6982 | 25750.859 | 25189.488 | 25845.7876 | 26877.9905 | 26093.3885 | 26093.3885 | 26093.3885 | 26093.3885 | 26093.3885 | 26093.3885 | 26093.3885 | 26093.3885 | 26093.3885 | 26093.3885 | 26093.3885 | 26093.3885 | 26093.3885 | 26093.3885 | 26093.3885 | 26093.3885 |  | 16070.8005 | 21801.5288 | 23368.1279 | 23609.9554 | 23762.8633 | 24100.0075 | 24897.3046 | 25331.9028 | 26161.1821 | 28683.4724 | 26602.3787 | 26194.791 | 26743.2404 | 27943.5643 | 27129.8392 | 27129.8392 | 27129.8392 | 27129.8392 | 27129.8392 | 27129.8392 | 27129.8392 | 27129.8392 | 27129.8392 | 27129.8392 | 27129.8392 | 27129.8392 | 27129.8392 | 27129.8392 | 27129.8392 | 27129.8392
45% | 11588.8305 | 16068.4223 | 17232.1005 | 17430.0335 | 17583.9957 | 17849.9904 | 18455.8826 | 18860.9836 | 19374.6918 | 19641.0617 | 19875.0474 | 19441.7696 | 19948.3153 | 20744.9909 | 20139.4188 | 20139.4188 | 20139.4188 | 20139.4188 | 20139.4188 | 20139.4188 | 20139.4188 | 20139.4188 | 20139.4188 | 20139.4188 | 20139.4188 | 20139.4188 | 20139.4188 | 20139.4188 | 20139.4188 | 20139.4188 |  | 12403.7774 | 16826.8724 | 18036.0061 | 18222.6536 | 18340.6711 | 18600.8859 | 19216.2564 | 19551.6884 | 20191.7433 | 22138.4993 | 20532.268 | 20217.6833 | 20640.988 | 21567.4228 | 20939.373 | 20939.373 | 20939.373 | 20939.373 | 20939.373 | 20939.373 | 20939.373 | 20939.373 | 20939.373 | 20939.373 | 20939.373 | 20939.373 | 20939.373 | 20939.373 | 20939.373 | 20939.373
40% | 5693.5395 | 7894.3425 | 8466.0523 | 8563.2959 | 8638.9368 | 8769.6188 | 9067.2909 | 9266.3151 | 9518.6977 | 9649.5639 | 9764.5201 | 9551.6527 | 9800.5162 | 10191.9194 | 9894.4045 | 9894.4045 | 9894.4045 | 9894.4045 | 9894.4045 | 9894.4045 | 9894.4045 | 9894.4045 | 9894.4045 | 9894.4045 | 9894.4045 | 9894.4045 | 9894.4045 | 9894.4045 | 9894.4045 | 9894.4045 |  | 6093.9192 | 8266.9656 | 8861.0075 | 8952.7065 | 9010.688 | 9138.5304 | 9440.8591 | 9605.6552 | 9920.1113 | 10876.5437 | 10087.4095 | 9932.8555 | 10140.8232 | 10595.9764 | 10287.4184 | 10287.4184 | 10287.4184 | 10287.4184 | 10287.4184 | 10287.4184 | 10287.4184 | 10287.4184 | 10287.4184 | 10287.4184 | 10287.4184 | 10287.4184 | 10287.4184 | 10287.4184 | 10287.4184 | 10287.4184
35% | 2127.9257 | 2950.4624 | 3164.1354 | 3200.4796 | 3228.75 | 3277.5916 | 3388.8447 | 3463.2288 | 3557.5552 | 3606.4657 | 3649.4298 | 3569.872 | 3662.8832 | 3809.1677 | 3697.9734 | 3697.9734 | 3697.9734 | 3697.9734 | 3697.9734 | 3697.9734 | 3697.9734 | 3697.9734 | 3697.9734 | 3697.9734 | 3697.9734 | 3697.9734 | 3697.9734 | 3697.9734 | 3697.9734 | 3697.9734 |  | 2277.5652 | 3089.728 | 3311.7475 | 3346.0195 | 3367.6897 | 3415.47 | 3528.4635 | 3590.0551 | 3707.5811 | 4065.0419 | 3770.1078 | 3712.3442 | 3790.0708 | 3960.1816 | 3844.8599 | 3844.8599 | 3844.8599 | 3844.8599 | 3844.8599 | 3844.8599 | 3844.8599 | 3844.8599 | 3844.8599 | 3844.8599 | 3844.8599 | 3844.8599 | 3844.8599 | 3844.8599 | 3844.8599 | 3844.8599
30% | 1061.2862 | 1471.5199 | 1578.0877 | 1596.2141 | 1610.3137 | 1634.673 | 1690.1596 | 1727.2581 | 1774.3027 | 1798.6964 | 1820.1244 | 1780.4456 | 1826.8342 | 1899.7925 | 1844.3351 | 1844.3351 | 1844.3351 | 1844.3351 | 1844.3351 | 1844.3351 | 1844.3351 | 1844.3351 | 1844.3351 | 1844.3351 | 1844.3351 | 1844.3351 | 1844.3351 | 1844.3351 | 1844.3351 | 1844.3351 |  | 1135.9177 | 1540.9775 | 1651.708 | 1668.8009 | 1679.6088 | 1703.4388 | 1759.7934 | 1790.5117 | 1849.1269 | 2027.4077 | 1880.3116 | 1851.5025 | 1890.268 | 1975.1094 | 1917.5936 | 1917.5936 | 1917.5936 | 1917.5936 | 1917.5936 | 1917.5936 | 1917.5936 | 1917.5936 | 1917.5936 | 1917.5936 | 1917.5936 | 1917.5936 | 1917.5936 | 1917.5936 | 1917.5936 | 1917.5936
25% | 625.6637 | 867.5102 | 930.3354 | 941.0215 | 949.3337 | 963.6944 | 996.4056 | 1018.2764 | 1046.0107 | 1060.3916 | 1073.0242 | 1049.6322 | 1076.9798 | 1119.9911 | 1087.2972 | 1087.2972 | 1087.2972 | 1087.2972 | 1087.2972 | 1087.2972 | 1087.2972 | 1087.2972 | 1087.2972 | 1087.2972 | 1087.2972 | 1087.2972 | 1087.2972 | 1087.2972 | 1087.2972 | 1087.2972 |  | 669.6615 | 908.4578 | 973.7371 | 983.8139 | 990.1855 | 1004.2341 | 1037.457 | 1055.5665 | 1090.1221 | 1195.2246 | 1108.5065 | 1091.5226 | 1114.3762 | 1164.393 | 1130.4855 | 1130.4855 | 1130.4855 | 1130.4855 | 1130.4855 | 1130.4855 | 1130.4855 | 1130.4855 | 1130.4855 | 1130.4855 | 1130.4855 | 1130.4855 | 1130.4855 | 1130.4855 | 1130.4855 | 1130.4855
20% | 316.1776 | 438.3942 | 470.1428 | 475.543 | 479.7435 | 487.0006 | 503.5312 | 514.5835 | 528.599 | 535.8664 | 542.2502 | 530.4291 | 544.2492 | 565.9848 | 549.463 | 549.463 | 549.463 | 549.463 | 549.463 | 549.463 | 549.463 | 549.463 | 549.463 | 549.463 | 549.463 | 549.463 | 549.463 | 549.463 | 549.463 | 549.463 |  | 338.4118 | 459.0869 | 492.0757 | 497.168 | 500.3879 | 507.4873 | 524.2764 | 533.428 | 550.8906 | 604.0039 | 560.1811 | 551.5983 | 563.1473 | 588.4232 | 571.2881 | 571.2881 | 571.2881 | 571.2881 | 571.2881 | 571.2881 | 571.2881 | 571.2881 | 571.2881 | 571.2881 | 571.2881 | 571.2881 | 571.2881 | 571.2881 | 571.2881 | 571.2881
15% | 128.8131 | 178.605 | 191.5396 | 193.7397 | 195.4511 | 198.4077 | 205.1423 | 209.6451 | 215.3552 | 218.3159 | 220.9167 | 216.1007 | 221.7311 | 230.5864 | 223.8553 | 223.8553 | 223.8553 | 223.8553 | 223.8553 | 223.8553 | 223.8553 | 223.8553 | 223.8553 | 223.8553 | 223.8553 | 223.8553 | 223.8553 | 223.8553 | 223.8553 | 223.8553 |  | 137.8715 | 187.0354 | 200.4753 | 202.5499 | 203.8617 | 206.7541 | 213.5941 | 217.3225 | 224.4369 | 246.0756 | 228.2219 | 224.7252 | 229.4304 | 239.728 | 232.747 | 232.747 | 232.747 | 232.747 | 232.747 | 232.747 | 232.747 | 232.747 | 232.747 | 232.747 | 232.747 | 232.747 | 232.747 | 232.747 | 232.747 | 232.747
10% | 51.8598 | 71.9059 | 77.1134 | 77.9991 | 78.6881 | 79.8784 | 82.5898 | 84.4026 | 86.7014 | 87.8934 | 88.9405 | 87.0016 | 89.2684 | 92.8335 | 90.1236 | 90.1236 | 90.1236 | 90.1236 | 90.1236 | 90.1236 | 90.1236 | 90.1236 | 90.1236 | 90.1236 | 90.1236 | 90.1236 | 90.1236 | 90.1236 | 90.1236 | 90.1236 |  | 55.5067 | 75.3 | 80.7108 | 81.5461 | 82.0742 | 83.2387 | 85.9924 | 87.4935 | 90.3577 | 99.0694 | 91.8816 | 90.4738 | 92.3681 | 96.5139 | 93.7033 | 93.7033 | 93.7033 | 93.7033 | 93.7033 | 93.7033 | 93.7033 | 93.7033 | 93.7033 | 93.7033 | 93.7033 | 93.7033 | 93.7033 | 93.7033 | 93.7033 | 93.7033
5% | 44.1645 | 61.236 | 65.6707 | 66.425 | 67.0118 | 68.0255 | 70.3345 | 71.8783 | 73.8361 | 74.8512 | 75.7429 | 74.0917 | 76.0221 | 79.0582 | 76.7504 | 76.7504 | 76.7504 | 76.7504 | 76.7504 | 76.7504 | 76.7504 | 76.7504 | 76.7504 | 76.7504 | 76.7504 | 76.7504 | 76.7504 | 76.7504 | 76.7504 | 76.7504 |  | 47.2702 | 64.1264 | 68.7344 | 69.4457 | 69.8954 | 70.8871 | 73.2323 | 74.5106 | 76.9498 | 84.3688 | 78.2475 | 77.0487 | 78.6618 | 82.1924 | 79.799 | 79.799 | 79.799 | 79.799 | 79.799 | 79.799 | 79.799 | 79.799 | 79.799 | 79.799 | 79.799 | 79.799 | 79.799 | 79.799 | 79.799 | 79.799
9.992e-14% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E @ R (MWh) | 118268.4368 | 163984.3799 | 175860.1598 | 177880.1417 | 179451.3847 | 182165.962 | 188349.3233 | 192483.5334 | 197726.1221 | 200444.5279 | 202832.442 | 198410.6765 | 203580.168 | 211710.5473 | 205530.4523 | 205530.4523 | 205530.4523 | 205530.4523 | 205530.4523 | 205530.4523 | 205530.4523 | 205530.4523 | 205530.4523 | 205530.4523 | 205530.4523 | 205530.4523 | 205530.4523 | 205530.4523 | 205530.4523 | 205530.4523 | E @ R (MWh) | 126585.2808 | 171724.6525 | 184064.3234 | 185969.1325 | 187173.5461 | 189829.1378 | 196109.2281 | 199532.4392 | 206064.4443 | 225931.832 | 209539.6283 | 206329.172 | 210649.1573 | 220103.7788 | 213694.29 | 213694.29 | 213694.29 | 213694.29 | 213694.29 | 213694.29 | 213694.29 | 213694.29 | 213694.29 | 213694.29 | 213694.29 | 213694.29 | 213694.29 | 213694.29 | 213694.29 | 213694.29
Option 8 Winter POE50 W E @ R (MWh) N 2 | 82787.9057 | 114789.066 | 123102.1118 | 124516.0992 | 125615.9693 | 127516.1734 | 131844.5263 | 134738.4734 | 138408.2855 | 140311.1695 | 141982.7094 | 138887.4736 | 142506.1176 | 148197.3831 | 143871.3166 | 143871.3166 | 143871.3166 | 143871.3166 | 143871.3166 | 143871.3166 | 143871.3166 | 143871.3166 | 143871.3166 | 143871.3166 | 143871.3166 | 143871.3166 | 143871.3166 | 143871.3166 | 143871.3166 | 143871.3166 | Option 8 Winter POE10 W E @ R (MWh) N 2 | 37975.5842 | 51517.3957 | 55219.297 | 55790.7397 | 56152.0638 | 56948.7413 | 58832.7684 | 59859.7318 | 61819.3333 | 67779.5496 | 62861.8885 | 61898.7516 | 63194.7472 | 66031.1336 | 64108.287 | 64108.287 | 64108.287 | 64108.287 | 64108.287 | 64108.287 | 64108.287 | 64108.287 | 64108.287 | 64108.287 | 64108.287 | 64108.287 | 64108.287 | 64108.287 | 64108.287 | 64108.287
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 85.8327 | 111.1071 | 117.7202 | 117.3233 | 117.3513 | 118.0293 | 119.8198 | 121.0174 | 122.1905 | 123.5626 | 124.8333 | 126.0676 | 126.2076 | 127.6483 | 126.5544 | 126.5544 | 126.5544 | 126.5544 | 126.5544 | 126.5544 | 126.5544 | 126.5544 | 126.5544 | 126.5544 | 126.5544 | 126.5544 | 126.5544 | 126.5544 | 126.5544 | 126.5544
98% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 42.4851 | 54.9952 | 58.2686 | 58.0721 | 58.0859 | 58.4216 | 59.3078 | 59.9006 | 60.4812 | 61.1604 | 61.7894 | 62.4003 | 62.4696 | 63.1827 | 62.6413 | 62.6413 | 62.6413 | 62.6413 | 62.6413 | 62.6413 | 62.6413 | 62.6413 | 62.6413 | 62.6413 | 62.6413 | 62.6413 | 62.6413 | 62.6413 | 62.6413 | 62.6413
97% | 18.864 | 25.0432 | 26.7251 | 26.6761 | 26.6743 | 26.866 | 27.0764 | 27.5082 | 27.8185 | 27.9869 | 28.171 | 28.3395 | 28.644 | 29.0219 | 28.9955 | 28.9955 | 28.9955 | 28.9955 | 28.9955 | 28.9955 | 28.9955 | 28.9955 | 28.9955 | 28.9955 | 28.9955 | 28.9955 | 28.9955 | 28.9955 | 28.9955 | 28.9955 |  | 84.1075 | 108.8738 | 115.354 | 114.965 | 114.9925 | 115.6569 | 117.4113 | 118.5849 | 119.7344 | 121.0789 | 122.3241 | 123.5336 | 123.6708 | 125.0825 | 124.0106 | 124.0106 | 124.0106 | 124.0106 | 124.0106 | 124.0106 | 124.0106 | 124.0106 | 124.0106 | 124.0106 | 124.0106 | 124.0106 | 124.0106 | 124.0106 | 124.0106 | 124.0106
95% | 92.8689 | 123.2894 | 131.5698 | 131.3286 | 131.3197 | 132.2634 | 133.299 | 135.4251 | 136.9528 | 137.7816 | 138.6878 | 139.5174 | 141.0166 | 142.8772 | 142.7472 | 142.7472 | 142.7472 | 142.7472 | 142.7472 | 142.7472 | 142.7472 | 142.7472 | 142.7472 | 142.7472 | 142.7472 | 142.7472 | 142.7472 | 142.7472 | 142.7472 | 142.7472 |  | 124.2203 | 160.7982 | 170.369 | 169.7945 | 169.8351 | 170.8163 | 173.4075 | 175.1408 | 176.8385 | 178.8242 | 180.6633 | 182.4496 | 182.6522 | 184.7373 | 183.1541 | 183.1541 | 183.1541 | 183.1541 | 183.1541 | 183.1541 | 183.1541 | 183.1541 | 183.1541 | 183.1541 | 183.1541 | 183.1541 | 183.1541 | 183.1541 | 183.1541 | 183.1541
90% | 161.0694 | 213.8301 | 228.1913 | 227.7731 | 227.7577 | 229.3944 | 231.1905 | 234.8778 | 237.5275 | 238.9649 | 240.5367 | 241.9755 | 244.5756 | 247.8027 | 247.5772 | 247.5772 | 247.5772 | 247.5772 | 247.5772 | 247.5772 | 247.5772 | 247.5772 | 247.5772 | 247.5772 | 247.5772 | 247.5772 | 247.5772 | 247.5772 | 247.5772 | 247.5772 |  | 538.6113 | 697.2109 | 738.7092 | 736.2183 | 736.3942 | 740.6488 | 751.884 | 759.3996 | 766.7606 | 775.3706 | 783.3448 | 791.0899 | 791.9686 | 801.0093 | 794.1448 | 794.1448 | 794.1448 | 794.1448 | 794.1448 | 794.1448 | 794.1448 | 794.1448 | 794.1448 | 794.1448 | 794.1448 | 794.1448 | 794.1448 | 794.1448 | 794.1448 | 794.1448
85% | 457.0889 | 606.8151 | 647.57 | 646.383 | 646.3393 | 650.9841 | 656.081 | 666.5452 | 674.0646 | 678.1436 | 682.6041 | 686.6874 | 694.0659 | 703.2239 | 702.5838 | 702.5838 | 702.5838 | 702.5838 | 702.5838 | 702.5838 | 702.5838 | 702.5838 | 702.5838 | 702.5838 | 702.5838 | 702.5838 | 702.5838 | 702.5838 | 702.5838 | 702.5838 |  | 509.4971 | 659.5238 | 698.779 | 696.4228 | 696.5891 | 700.6138 | 711.2416 | 718.351 | 725.3141 | 733.4587 | 741.0019 | 748.3283 | 749.1595 | 757.7115 | 751.218 | 751.218 | 751.218 | 751.218 | 751.218 | 751.218 | 751.218 | 751.218 | 751.218 | 751.218 | 751.218 | 751.218 | 751.218 | 751.218 | 751.218 | 751.218
80% | 638.4734 | 847.6148 | 904.5422 | 902.8842 | 902.8231 | 909.3111 | 916.4306 | 931.0473 | 941.5505 | 947.2482 | 953.4787 | 959.1824 | 969.4889 | 982.2811 | 981.3869 | 981.3869 | 981.3869 | 981.3869 | 981.3869 | 981.3869 | 981.3869 | 981.3869 | 981.3869 | 981.3869 | 981.3869 | 981.3869 | 981.3869 | 981.3869 | 981.3869 | 981.3869 |  | 355.8393 | 460.6198 | 488.0361 | 486.3905 | 486.5067 | 489.3176 | 496.7402 | 501.7054 | 506.5685 | 512.2568 | 517.5251 | 522.642 | 523.2225 | 529.1954 | 524.6602 | 524.6602 | 524.6602 | 524.6602 | 524.6602 | 524.6602 | 524.6602 | 524.6602 | 524.6602 | 524.6602 | 524.6602 | 524.6602 | 524.6602 | 524.6602 | 524.6602 | 524.6602
75% | 1664.3841 | 2209.5776 | 2357.9769 | 2353.655 | 2353.4957 | 2370.4087 | 2388.968 | 2427.0709 | 2454.4511 | 2469.3039 | 2485.5456 | 2500.414 | 2527.2813 | 2560.6281 | 2558.2972 | 2558.2972 | 2558.2972 | 2558.2972 | 2558.2972 | 2558.2972 | 2558.2972 | 2558.2972 | 2558.2972 | 2558.2972 | 2558.2972 | 2558.2972 | 2558.2972 | 2558.2972 | 2558.2972 | 2558.2972 |  | 635.1192 | 822.1366 | 871.0705 | 868.1333 | 868.3407 | 873.3577 | 886.6059 | 895.4682 | 904.1481 | 914.3008 | 923.7039 | 932.8368 | 933.8729 | 944.5335 | 936.439 | 936.439 | 936.439 | 936.439 | 936.439 | 936.439 | 936.439 | 936.439 | 936.439 | 936.439 | 936.439 | 936.439 | 936.439 | 936.439 | 936.439 | 936.439
70% | 2875.5487 | 3817.4772 | 4073.866 | 4066.399 | 4066.1238 | 4095.3442 | 4127.4091 | 4193.2394 | 4240.5439 | 4266.205 | 4294.2657 | 4319.9539 | 4366.3723 | 4423.9855 | 4419.9585 | 4419.9585 | 4419.9585 | 4419.9585 | 4419.9585 | 4419.9585 | 4419.9585 | 4419.9585 | 4419.9585 | 4419.9585 | 4419.9585 | 4419.9585 | 4419.9585 | 4419.9585 | 4419.9585 | 4419.9585 |  | 1157.0168 | 1497.7123 | 1586.8569 | 1581.5061 | 1581.8839 | 1591.0234 | 1615.1582 | 1631.3028 | 1647.1153 | 1665.6109 | 1682.7407 | 1699.3783 | 1701.266 | 1720.6867 | 1705.9407 | 1705.9407 | 1705.9407 | 1705.9407 | 1705.9407 | 1705.9407 | 1705.9407 | 1705.9407 | 1705.9407 | 1705.9407 | 1705.9407 | 1705.9407 | 1705.9407 | 1705.9407 | 1705.9407 | 1705.9407
65% | 7222.0048 | 9587.679 | 10231.6052 | 10212.8518 | 10212.1606 | 10285.5483 | 10366.0801 | 10531.4141 | 10650.2206 | 10714.6689 | 10785.1441 | 10849.6604 | 10966.2413 | 11110.9382 | 11100.8242 | 11100.8242 | 11100.8242 | 11100.8242 | 11100.8242 | 11100.8242 | 11100.8242 | 11100.8242 | 11100.8242 | 11100.8242 | 11100.8242 | 11100.8242 | 11100.8242 | 11100.8242 | 11100.8242 | 11100.8242 |  | 1455.7061 | 1884.3537 | 1996.5114 | 1989.7793 | 1990.2546 | 2001.7536 | 2032.1189 | 2052.4313 | 2072.3259 | 2095.5961 | 2117.1482 | 2138.0809 | 2140.4558 | 2164.8901 | 2146.3373 | 2146.3373 | 2146.3373 | 2146.3373 | 2146.3373 | 2146.3373 | 2146.3373 | 2146.3373 | 2146.3373 | 2146.3373 | 2146.3373 | 2146.3373 | 2146.3373 | 2146.3373 | 2146.3373 | 2146.3373
60% | 10556.5772 | 14014.5398 | 14955.7822 | 14928.3698 | 14927.3596 | 15034.6321 | 15152.3473 | 15394.0201 | 15567.6823 | 15661.888 | 15764.9032 | 15859.2082 | 16029.6174 | 16241.1243 | 16226.3403 | 16226.3403 | 16226.3403 | 16226.3403 | 16226.3403 | 16226.3403 | 16226.3403 | 16226.3403 | 16226.3403 | 16226.3403 | 16226.3403 | 16226.3403 | 16226.3403 | 16226.3403 | 16226.3403 | 16226.3403 |  | 2277.9105 | 2948.6646 | 3124.1707 | 3113.6361 | 3114.3799 | 3132.3737 | 3179.8897 | 3211.675 | 3242.8062 | 3279.2199 | 3312.9449 | 3345.7006 | 3349.4169 | 3387.6521 | 3358.6203 | 3358.6203 | 3358.6203 | 3358.6203 | 3358.6203 | 3358.6203 | 3358.6203 | 3358.6203 | 3358.6203 | 3358.6203 | 3358.6203 | 3358.6203 | 3358.6203 | 3358.6203 | 3358.6203 | 3358.6203
55% | 11937.0341 | 15847.1857 | 16911.512 | 16880.515 | 16879.3726 | 17000.6729 | 17133.7814 | 17407.0571 | 17603.4287 | 17709.9534 | 17826.4396 | 17933.0767 | 18125.7699 | 18364.935 | 18348.2178 | 18348.2178 | 18348.2178 | 18348.2178 | 18348.2178 | 18348.2178 | 18348.2178 | 18348.2178 | 18348.2178 | 18348.2178 | 18348.2178 | 18348.2178 | 18348.2178 | 18348.2178 | 18348.2178 | 18348.2178 |  | 4377.3623 | 5666.3214 | 6003.5838 | 5983.3401 | 5984.7694 | 6019.3473 | 6110.6567 | 6171.737 | 6231.5606 | 6301.5352 | 6366.343 | 6429.2884 | 6436.4298 | 6509.9048 | 6454.1156 | 6454.1156 | 6454.1156 | 6454.1156 | 6454.1156 | 6454.1156 | 6454.1156 | 6454.1156 | 6454.1156 | 6454.1156 | 6454.1156 | 6454.1156 | 6454.1156 | 6454.1156 | 6454.1156 | 6454.1156
50% | 15327.7148 | 20348.5339 | 21715.179 | 21675.3774 | 21673.9105 | 21829.6658 | 22000.5834 | 22351.4823 | 22603.6327 | 22740.4155 | 22889.9893 | 23026.9163 | 23274.3434 | 23581.4427 | 23559.977 | 23559.977 | 23559.977 | 23559.977 | 23559.977 | 23559.977 | 23559.977 | 23559.977 | 23559.977 | 23559.977 | 23559.977 | 23559.977 | 23559.977 | 23559.977 | 23559.977 | 23559.977 |  | 9714.4123 | 12574.9205 | 13323.3863 | 13278.4606 | 13281.6325 | 13358.3693 | 13561.0066 | 13696.5584 | 13829.3213 | 13984.6116 | 14128.4356 | 14268.1263 | 14283.9748 | 14447.0334 | 14323.224 | 14323.224 | 14323.224 | 14323.224 | 14323.224 | 14323.224 | 14323.224 | 14323.224 | 14323.224 | 14323.224 | 14323.224 | 14323.224 | 14323.224 | 14323.224 | 14323.224 | 14323.224
45% | 20411.3174 | 27097.3455 | 28917.2533 | 28864.251 | 28862.2976 | 29069.7109 | 29297.3152 | 29764.5935 | 30100.3723 | 30282.5206 | 30481.7021 | 30664.0425 | 30993.5314 | 31402.4836 | 31373.8985 | 31373.8985 | 31373.8985 | 31373.8985 | 31373.8985 | 31373.8985 | 31373.8985 | 31373.8985 | 31373.8985 | 31373.8985 | 31373.8985 | 31373.8985 | 31373.8985 | 31373.8985 | 31373.8985 | 31373.8985 |  | 14720.4239 | 19055.0036 | 20189.1672 | 20121.0905 | 20125.8971 | 20242.1776 | 20549.2377 | 20754.6417 | 20955.8197 | 21191.1339 | 21409.073 | 21620.7489 | 21644.7644 | 21891.85 | 21704.2393 | 21704.2393 | 21704.2393 | 21704.2393 | 21704.2393 | 21704.2393 | 21704.2393 | 21704.2393 | 21704.2393 | 21704.2393 | 21704.2393 | 21704.2393 | 21704.2393 | 21704.2393 | 21704.2393 | 21704.2393
40% | 14315.8312 | 19005.1929 | 20281.6168 | 20244.4427 | 20243.0727 | 20388.5455 | 20548.1797 | 20875.9135 | 21111.4178 | 21239.1706 | 21378.87 | 21506.7576 | 21737.8504 | 22024.6761 | 22004.6275 | 22004.6275 | 22004.6275 | 22004.6275 | 22004.6275 | 22004.6275 | 22004.6275 | 22004.6275 | 22004.6275 | 22004.6275 | 22004.6275 | 22004.6275 | 22004.6275 | 22004.6275 | 22004.6275 | 22004.6275 |  | 15242.3215 | 19730.5793 | 20904.9535 | 20834.4632 | 20839.4402 | 20959.8434 | 21277.7899 | 21490.4763 | 21698.7869 | 21942.444 | 22168.1098 | 22387.2904 | 22412.1574 | 22668.0032 | 22473.741 | 22473.741 | 22473.741 | 22473.741 | 22473.741 | 22473.741 | 22473.741 | 22473.741 | 22473.741 | 22473.741 | 22473.741 | 22473.741 | 22473.741 | 22473.741 | 22473.741 | 22473.741
35% | 7422.2532 | 9853.5218 | 10515.3025 | 10496.0291 | 10495.3188 | 10570.7413 | 10653.506 | 10823.4244 | 10945.5251 | 11011.7604 | 11084.1896 | 11150.4949 | 11270.3083 | 11419.0173 | 11408.6228 | 11408.6228 | 11408.6228 | 11408.6228 | 11408.6228 | 11408.6228 | 11408.6228 | 11408.6228 | 11408.6228 | 11408.6228 | 11408.6228 | 11408.6228 | 11408.6228 | 11408.6228 | 11408.6228 | 11408.6228 |  | 20759.9869 | 26872.9779 | 28472.4713 | 28376.4638 | 28383.2424 | 28547.2311 | 28980.2731 | 29269.9512 | 29553.6695 | 29885.5295 | 30192.8856 | 30491.4088 | 30525.2776 | 30873.7386 | 30609.1541 | 30609.1541 | 30609.1541 | 30609.1541 | 30609.1541 | 30609.1541 | 30609.1541 | 30609.1541 | 30609.1541 | 30609.1541 | 30609.1541 | 30609.1541 | 30609.1541 | 30609.1541 | 30609.1541 | 30609.1541
30% | 3452.1096 | 4582.899 | 4890.695 | 4881.7308 | 4881.4005 | 4916.4797 | 4954.9738 | 5034.0033 | 5090.7926 | 5121.5988 | 5155.2859 | 5186.1246 | 5241.8501 | 5311.0151 | 5306.1806 | 5306.1806 | 5306.1806 | 5306.1806 | 5306.1806 | 5306.1806 | 5306.1806 | 5306.1806 | 5306.1806 | 5306.1806 | 5306.1806 | 5306.1806 | 5306.1806 | 5306.1806 | 5306.1806 | 5306.1806 |  | 19183.5111 | 24832.2926 | 26310.3234 | 26221.6065 | 26227.8703 | 26379.406 | 26779.5636 | 27047.2441 | 27309.4173 | 27616.0765 | 27900.0925 | 28175.9464 | 28207.2432 | 28529.2428 | 28284.7504 | 28284.7504 | 28284.7504 | 28284.7504 | 28284.7504 | 28284.7504 | 28284.7504 | 28284.7504 | 28284.7504 | 28284.7504 | 28284.7504 | 28284.7504 | 28284.7504 | 28284.7504 | 28284.7504 | 28284.7504
25% | 2357.031 | 3129.1112 | 3339.2681 | 3333.1476 | 3332.922 | 3356.8734 | 3383.1564 | 3437.1161 | 3475.8908 | 3496.9246 | 3519.9255 | 3540.9815 | 3579.0298 | 3626.2542 | 3622.9533 | 3622.9533 | 3622.9533 | 3622.9533 | 3622.9533 | 3622.9533 | 3622.9533 | 3622.9533 | 3622.9533 | 3622.9533 | 3622.9533 | 3622.9533 | 3622.9533 | 3622.9533 | 3622.9533 | 3622.9533 |  | 5533.3008 | 7162.6379 | 7588.9618 | 7563.3722 | 7565.179 | 7608.888 | 7724.3096 | 7801.5195 | 7877.1409 | 7965.5938 | 8047.5155 | 8127.0829 | 8136.1102 | 8228.9879 | 8158.4664 | 8158.4664 | 8158.4664 | 8158.4664 | 8158.4664 | 8158.4664 | 8158.4664 | 8158.4664 | 8158.4664 | 8158.4664 | 8158.4664 | 8158.4664 | 8158.4664 | 8158.4664 | 8158.4664 | 8158.4664
20% | 1427.8587 | 1895.5749 | 2022.8852 | 2019.1774 | 2019.0408 | 2033.5502 | 2049.4721 | 2082.1602 | 2105.6494 | 2118.3914 | 2132.325 | 2145.0805 | 2168.1297 | 2196.7376 | 2194.738 | 2194.738 | 2194.738 | 2194.738 | 2194.738 | 2194.738 | 2194.738 | 2194.738 | 2194.738 | 2194.738 | 2194.738 | 2194.738 | 2194.738 | 2194.738 | 2194.738 | 2194.738 |  | 1484.8203 | 1922.0408 | 2036.4417 | 2029.5749 | 2030.0597 | 2041.7887 | 2072.7613 | 2093.48 | 2113.7724 | 2137.5081 | 2159.4912 | 2180.8425 | 2183.2649 | 2208.1879 | 2189.264 | 2189.264 | 2189.264 | 2189.264 | 2189.264 | 2189.264 | 2189.264 | 2189.264 | 2189.264 | 2189.264 | 2189.264 | 2189.264 | 2189.264 | 2189.264 | 2189.264 | 2189.264
15% | 914.1778 | 1213.6303 | 1295.1399 | 1292.766 | 1292.6786 | 1301.9681 | 1312.162 | 1333.0904 | 1348.1292 | 1356.2872 | 1365.2081 | 1373.3747 | 1388.1318 | 1406.4479 | 1405.1676 | 1405.1676 | 1405.1676 | 1405.1676 | 1405.1676 | 1405.1676 | 1405.1676 | 1405.1676 | 1405.1676 | 1405.1676 | 1405.1676 | 1405.1676 | 1405.1676 | 1405.1676 | 1405.1676 | 1405.1676 |  | 818.9695 | 1060.1234 | 1123.2225 | 1119.4351 | 1119.7025 | 1126.1718 | 1143.255 | 1154.6827 | 1165.8752 | 1178.9669 | 1191.0919 | 1202.8685 | 1204.2046 | 1217.9511 | 1207.5134 | 1207.5134 | 1207.5134 | 1207.5134 | 1207.5134 | 1207.5134 | 1207.5134 | 1207.5134 | 1207.5134 | 1207.5134 | 1207.5134 | 1207.5134 | 1207.5134 | 1207.5134 | 1207.5134 | 1207.5134
10% | 611.8703 | 812.2975 | 866.8529 | 865.264 | 865.2055 | 871.4231 | 878.246 | 892.2536 | 902.3193 | 907.7795 | 913.7504 | 919.2164 | 929.0935 | 941.3527 | 940.4958 | 940.4958 | 940.4958 | 940.4958 | 940.4958 | 940.4958 | 940.4958 | 940.4958 | 940.4958 | 940.4958 | 940.4958 | 940.4958 | 940.4958 | 940.4958 | 940.4958 | 940.4958 |  | 191.3984 | 247.7576 | 262.5043 | 261.6191 | 261.6816 | 263.1935 | 267.186 | 269.8567 | 272.4725 | 275.5321 | 278.3658 | 281.118 | 281.4303 | 284.643 | 282.2036 | 282.2036 | 282.2036 | 282.2036 | 282.2036 | 282.2036 | 282.2036 | 282.2036 | 282.2036 | 282.2036 | 282.2036 | 282.2036 | 282.2036 | 282.2036 | 282.2036 | 282.2036
5% | 435.3228 | 577.9192 | 616.7333 | 615.6029 | 615.5612 | 619.9848 | 624.8391 | 634.805 | 641.9663 | 645.8511 | 650.0991 | 653.988 | 661.0151 | 669.7371 | 669.1274 | 669.1274 | 669.1274 | 669.1274 | 669.1274 | 669.1274 | 669.1274 | 669.1274 | 669.1274 | 669.1274 | 669.1274 | 669.1274 | 669.1274 | 669.1274 | 669.1274 | 669.1274 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9.992e-14% | 38.2117 | 50.7285 | 54.1355 | 54.0363 | 54.0326 | 54.4209 | 54.847 | 55.7218 | 56.3504 | 56.6914 | 57.0643 | 57.4056 | 58.0224 | 58.788 | 58.7345 | 58.7345 | 58.7345 | 58.7345 | 58.7345 | 58.7345 | 58.7345 | 58.7345 | 58.7345 | 58.7345 | 58.7345 | 58.7345 | 58.7345 | 58.7345 | 58.7345 | 58.7345 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E @ R (MWh) | 102337.6118 | 135859.8063 | 144984.402 | 144718.661 | 144708.8672 | 145748.789 | 146889.9441 | 149232.7692 | 150916.2863 | 151829.5355 | 152828.1856 | 153742.3981 | 155394.3791 | 157444.7704 | 157301.4516 | 157301.4516 | 157301.4516 | 157301.4516 | 157301.4516 | 157301.4516 | 157301.4516 | 157301.4516 | 157301.4516 | 157301.4516 | 157301.4516 | 157301.4516 | 157301.4516 | 157301.4516 | 157301.4516 | 157301.4516 | E @ R (MWh) | 99292.8528 | 128530.651 | 136180.8614 | 135721.6674 | 135754.0887 | 136538.4294 | 138609.6244 | 139995.1247 | 141352.1196 | 142939.3714 | 144409.4236 | 145837.2289 | 145999.2196 | 147665.8725 | 146400.3925 | 146400.3925 | 146400.3925 | 146400.3925 | 146400.3925 | 146400.3925 | 146400.3925 | 146400.3925 | 146400.3925 | 146400.3925 | 146400.3925 | 146400.3925 | 146400.3925 | 146400.3925 | 146400.3925 | 146400.3925
Option 8 Summer POE50 W E @ R (MWh) N 2 | 71636.3283 | 95101.8644 | 101489.0814 | 101303.0627 | 101296.207 | 102024.1523 | 102822.9609 | 104462.9384 | 105641.4004 | 106280.6749 | 106979.7299 | 107619.6787 | 108776.0654 | 110211.3393 | 110111.0161 | 110111.0161 | 110111.0161 | 110111.0161 | 110111.0161 | 110111.0161 | 110111.0161 | 110111.0161 | 110111.0161 | 110111.0161 | 110111.0161 | 110111.0161 | 110111.0161 | 110111.0161 | 110111.0161 | 110111.0161 | Option 8 Summer POE10 W E @ R (MWh) N 2 | 29787.8558 | 38559.1953 | 40854.2584 | 40716.5002 | 40726.2266 | 40961.5288 | 41582.8873 | 41998.5374 | 42405.6359 | 42881.8114 | 43322.8271 | 43751.1687 | 43799.7659 | 44299.7618 | 43920.1178 | 43920.1178 | 43920.1178 | 43920.1178 | 43920.1178 | 43920.1178 | 43920.1178 | 43920.1178 | 43920.1178 | 43920.1178 | 43920.1178 | 43920.1178 | 43920.1178 | 43920.1178 | 43920.1178 | 43920.1178

## POF N,N-1 & N-2 Risk
N-2 Method 1
| Asset name | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Tx 1 Pof | DS-PHM-TRNFMR-9000004393 | 0.006786% | 0.006786% | 0.008957% | 0.0115% | 0.01443% | 0.01777% | 0.02154% | 0.02575% | 0.03042% | 0.03556% | 0.04119% | 0.04732% | 0.05397% | 0.06116% | 0.06888% | 0.06888% | 0.06888% | 0.06888% | 0.06888% | 0.06888% | 0.06888% | 0.06888% | 0.06888% | 0.06888% | 0.06888% | 0.06888% | 0.06888% | 0.06888% | 0.06888% | 0.06888%
Tx 2 Pof | DS-PHM-TRNFMR-9000007050 | 0.006786% | 0.006786% | 0.008957% | 0.0115% | 0.01443% | 0.01777% | 0.02154% | 0.02575% | 0.03042% | 0.03556% | 0.04119% | 0.04732% | 0.05397% | 0.06116% | 0.06888% | 0.06888% | 0.06888% | 0.06888% | 0.06888% | 0.06888% | 0.06888% | 0.06888% | 0.06888% | 0.06888% | 0.06888% | 0.06888% | 0.06888% | 0.06888% | 0.06888% | 0.06888%
Tx 3 Pof | bar: FY25 to FY54
Tx 4 Pof
Tx 5 Pof
Total Tx Pof |  | 0.01357% | 0.01357% | 0.01791% | 0.023% | 0.02887% | 0.03555% | 0.04308% | 0.0515% | 0.06084% | 0.07112% | 0.08238% | 0.09465% | 0.1079% | 0.1223% | 0.1378% | 0.1378% | 0.1378% | 0.1378% | 0.1378% | 0.1378% | 0.1378% | 0.1378% | 0.1378% | 0.1378% | 0.1378% | 0.1378% | 0.1378% | 0.1378% | 0.1378% | 0.1378%
N-1 Risk |  | 0.005236% | 0.005236% | 0.006911% | 0.008873% | 0.01114% | 0.01371% | 0.01662% | 0.01987% | 0.02347% | 0.02744% | 0.03178% | 0.03651% | 0.04165% | 0.04719% | 0.05315% | 0.05315% | 0.05315% | 0.05315% | 0.05315% | 0.05315% | 0.05315% | 0.05315% | 0.05315% | 0.05315% | 0.05315% | 0.05315% | 0.05315% | 0.05315% | 0.05315% | 0.05315%
N-2 Risk |  | 1.079e-07% | 1.079e-07% | 1.881e-07% | 3.1e-07% | 4.883e-07% | 7.405e-07% | 1.088e-06% | 1.554e-06% | 2.169e-06% | 2.964e-06% | 3.977e-06% | 5.249e-06% | 6.829e-06% | 8.767e-06% | 1.112e-05% | 1.112e-05% | 1.112e-05% | 1.112e-05% | 1.112e-05% | 1.112e-05% | 1.112e-05% | 1.112e-05% | 1.112e-05% | 1.112e-05% | 1.112e-05% | 1.112e-05% | 1.112e-05% | 1.112e-05% | 1.112e-05% | 1.112e-05%
N Risk |  | 99.99% | 99.99% | 99.99% | 99.99% | 99.99% | 99.99% | 99.98% | 99.98% | 99.98% | 99.97% | 99.97% | 99.96% | 99.96% | 99.95% | 99.95% | 99.95% | 99.95% | 99.95% | 99.95% | 99.95% | 99.95% | 99.95% | 99.95% | 99.95% | 99.95% | 99.95% | 99.95% | 99.95% | 99.95% | 99.95%

## Summary
Involuntary load shedding (NER 5.17.1(c)(4)(ii))
Option 1 - Do Nothing / Base Case | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Weighted Energy @ Risk (MWh) under N Conditions | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Weighted Energy @ Risk (MWh) under N-1 Conditions | 0.0053489 | 0.25551 | 0.6825 | 0.9327 | 1.23 | 1.6873 | 2.5325 | 3.4943 | 4.8981 | 7.1332 | 7.614 | 8.0521 | 10.4859 | 14.6229 | 14.3758 | 14.3758 | 14.3758 | 14.3758 | 14.3758 | 14.3758 | 14.3758 | 14.3758 | 14.3758 | 14.3758 | 14.3758 | 14.3758 | 14.3758 | 14.3758 | 14.3758 | 14.3758
Weighted Energy @ Risk (MWh) under N-2 Conditions | 0.0002929 | 0.00039473 | 0.000735 | 0.0012171 | 0.0019252 | 0.0029518 | 0.0044325 | 0.0064455 | 0.0091777 | 0.01285 | 0.017155 | 0.022479 | 0.029729 | 0.039237 | 0.04892 | 0.04892 | 0.04892 | 0.04892 | 0.04892 | 0.04892 | 0.04892 | 0.04892 | 0.04892 | 0.04892 | 0.04892 | 0.04892 | 0.04892 | 0.04892 | 0.04892 | 0.04892
Total EUE (MWh) - Option 1 | 0.0056418 | 0.25591 | 0.68323 | 0.93391 | 1.2319 | 1.6902 | 2.537 | 3.5007 | 4.9073 | 7.146 | 7.6311 | 8.0746 | 10.5156 | 14.6621 | 14.4247 | 14.4247 | 14.4247 | 14.4247 | 14.4247 | 14.4247 | 14.4247 | 14.4247 | 14.4247 | 14.4247 | 14.4247 | 14.4247 | 14.4247 | 14.4247 | 14.4247 | 14.4247
Cost of EUE ($) - Option 1 | 217.8084 | 9879.5356 | 26376.9589 | 36054.8438 | 47558.8721 | 65252.4487 | 97942.7747 | 135148.7082 | 189450.6492 | 275881.0213 | 294608.8512 | 311729.6113 | 405968.4775 | 566048.0864 | 556883.0921 | 556883.0921 | 556883.0921 | 556883.0921 | 556883.0921 | 556883.0921 | 556883.0921 | 556883.0921 | 556883.0921 | 556883.0921 | 556883.0921 | 556883.0921 | 556883.0921 | 556883.0921 | 556883.0921 | 556883.0921
Hours at Risk pA. (Hrs) (N) | 1.486 | 1.486 | 1.486 | 1.486 | 1.486 | 1.486 | 1.486 | 1.486 | 1.486 | 1.486 | 1.486 | 1.486 | 1.486 | 1.486 | 1.486 | 1.486 | 1.486 | 1.486 | 1.486 | 1.486 | 1.486 | 1.486 | 1.486 | 1.486 | 1.486 | 1.486 | 1.486 | 1.486 | 1.486 | 1.486
Option 2 - 1A New PHS ZSS + Four new feeders | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Weighted Energy @ Risk (MWh) under N Conditions | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Weighted Energy @ Risk (MWh) under N-1 Conditions | 0.0053489 | 0.25551 | 0.6825 | 0.00075763 | 0.00096061 | 0.001494 | 0.0030243 | 0.0047873 | 0.007226 | 0.054376 | 0.016163 | 0.021571 | 0.027433 | 0.069558 | 0.042707 | 0.042707 | 0.042707 | 0.042707 | 0.042707 | 0.042707 | 0.042707 | 0.042707 | 0.042707 | 0.042707 | 0.042707 | 0.042707 | 0.042707 | 0.042707 | 0.042707 | 0.042707
Weighted Energy @ Risk (MWh) under N-2 Conditions | 0.0002929 | 0.00039473 | 0.000735 | 0.00072046 | 0.0011429 | 0.0017654 | 0.0026899 | 0.0039552 | 0.0057028 | 0.0081009 | 0.010784 | 0.014068 | 0.018789 | 0.025192 | 0.031102 | 0.031102 | 0.031102 | 0.031102 | 0.031102 | 0.031102 | 0.031102 | 0.031102 | 0.031102 | 0.031102 | 0.031102 | 0.031102 | 0.031102 | 0.031102 | 0.031102 | 0.031102
Total EUE (MWh) - Option 2 | 0.0056418 | 0.25591 | 0.68323 | 0.0014781 | 0.0021035 | 0.0032594 | 0.0057142 | 0.0087425 | 0.012929 | 0.062477 | 0.026947 | 0.035639 | 0.046222 | 0.09475 | 0.073809 | 0.073809 | 0.073809 | 0.073809 | 0.073809 | 0.073809 | 0.073809 | 0.073809 | 0.073809 | 0.073809 | 0.073809 | 0.073809 | 0.073809 | 0.073809 | 0.073809 | 0.073809
Cost of EUE ($) - Option 2 | 217.8084 | 9879.5356 | 26376.9589 | 57.0632 | 81.208 | 125.8316 | 220.604 | 337.5153 | 499.1298 | 2412.001 | 1040.3236 | 1375.9029 | 1784.4555 | 3657.9267 | 2849.4778 | 2849.4778 | 2849.4778 | 2849.4778 | 2849.4778 | 2849.4778 | 2849.4778 | 2849.4778 | 2849.4778 | 2849.4778 | 2849.4778 | 2849.4778 | 2849.4778 | 2849.4778 | 2849.4778 | 2849.4778
Option 3 - 2A PHM 3rd Tx + Switchroom + Three new feeders + OFR12 New Feeder | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Weighted Energy @ Risk (MWh) under N Conditions | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Weighted Energy @ Risk (MWh) under N-1 Conditions | 0.0053489 | 0.25551 | 0.6825 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Weighted Energy @ Risk (MWh) under N-2 Conditions | 0.0002929 | 0.00039473 | 0.000735 | 5.0878e-05 | 8.372e-05 | 0.00013901 | 0.00024538 | 0.00039558 | 0.00064011 | 0.0010594 | 0.0013223 | 0.0016155 | 0.0023621 | 0.0036473 | 0.0040907 | 0.0040907 | 0.0040907 | 0.0040907 | 0.0040907 | 0.0040907 | 0.0040907 | 0.0040907 | 0.0040907 | 0.0040907 | 0.0040907 | 0.0040907 | 0.0040907 | 0.0040907 | 0.0040907 | 0.0040907
Total EUE (MWh) - Option 3 | 0.0056418 | 0.25591 | 0.68323 | 5.0878e-05 | 8.372e-05 | 0.00013901 | 0.00024538 | 0.00039558 | 0.00064011 | 0.0010594 | 0.0013223 | 0.0016155 | 0.0023621 | 0.0036473 | 0.0040907 | 0.0040907 | 0.0040907 | 0.0040907 | 0.0040907 | 0.0040907 | 0.0040907 | 0.0040907 | 0.0040907 | 0.0040907 | 0.0040907 | 0.0040907 | 0.0040907 | 0.0040907 | 0.0040907 | 0.0040907
Cost of EUE ($) - Option 3 | 217.8084 | 9879.5356 | 26376.9589 | 1.9642 | 3.2321 | 5.3666 | 9.4732 | 15.2718 | 24.7123 | 40.9003 | 51.0486 | 62.3683 | 91.192 | 140.8067 | 157.9273 | 157.9273 | 157.9273 | 157.9273 | 157.9273 | 157.9273 | 157.9273 | 157.9273 | 157.9273 | 157.9273 | 157.9273 | 157.9273 | 157.9273 | 157.9273 | 157.9273 | 157.9273
Option 4 - 3A OFR 3rd Tx + Switchroom + Three new feeders + OFR12 New Feeder | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Weighted Energy @ Risk (MWh) under N Conditions | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Weighted Energy @ Risk (MWh) under N-1 Conditions | 0.0053489 | 0.25551 | 0.6825 | 0.04626 | 0.063752 | 0.099862 | 0.21235 | 0.36176 | 0.67049 | 1.4522 | 1.2569 | 1.1508 | 1.7953 | 3.2598 | 2.6667 | 2.6667 | 2.6667 | 2.6667 | 2.6667 | 2.6667 | 2.6667 | 2.6667 | 2.6667 | 2.6667 | 2.6667 | 2.6667 | 2.6667 | 2.6667 | 2.6667 | 2.6667
Weighted Energy @ Risk (MWh) under N-2 Conditions | 0.0002929 | 0.00039473 | 0.000735 | 0.00096879 | 0.001534 | 0.0023586 | 0.0035612 | 0.0052003 | 0.0074402 | 0.010475 | 0.01397 | 0.018273 | 0.024259 | 0.032214 | 0.040011 | 0.040011 | 0.040011 | 0.040011 | 0.040011 | 0.040011 | 0.040011 | 0.040011 | 0.040011 | 0.040011 | 0.040011 | 0.040011 | 0.040011 | 0.040011 | 0.040011 | 0.040011
Total EUE (MWh) - Option 4 | 0.0056418 | 0.25591 | 0.68323 | 0.047229 | 0.065286 | 0.10222 | 0.21591 | 0.36696 | 0.67793 | 1.4627 | 1.2709 | 1.169 | 1.8195 | 3.292 | 2.7067 | 2.7067 | 2.7067 | 2.7067 | 2.7067 | 2.7067 | 2.7067 | 2.7067 | 2.7067 | 2.7067 | 2.7067 | 2.7067 | 2.7067 | 2.7067 | 2.7067 | 2.7067
Cost of EUE ($) - Option 4 | 217.8084 | 9879.5356 | 26376.9589 | 1823.331 | 2520.453 | 3946.3546 | 8335.4413 | 14167.0095 | 26172.2139 | 56468.8661 | 49064.9017 | 45132.0021 | 70245.1814 | 127092.2891 | 104497.1881 | 104497.1881 | 104497.1881 | 104497.1881 | 104497.1881 | 104497.1881 | 104497.1881 | 104497.1881 | 104497.1881 | 104497.1881 | 104497.1881 | 104497.1881 | 104497.1881 | 104497.1881 | 104497.1881 | 104497.1881
Option 5 - 4A LLG 2nd Tx + Switchroom + Three new feeders + OFR12 New Feeder | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Weighted Energy @ Risk (MWh) under N Conditions | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Weighted Energy @ Risk (MWh) under N-1 Conditions | 0.0053489 | 0.25551 | 0.6825 | 0.00075763 | 0.00096061 | 0.001494 | 0.0030243 | 0.0047873 | 0.007226 | 0.054376 | 0.016163 | 0.021571 | 0.027433 | 0.069558 | 0.042707 | 0.042707 | 0.042707 | 0.042707 | 0.042707 | 0.042707 | 0.042707 | 0.042707 | 0.042707 | 0.042707 | 0.042707 | 0.042707 | 0.042707 | 0.042707 | 0.042707 | 0.042707
Weighted Energy @ Risk (MWh) under N-2 Conditions | 0.0002929 | 0.00039473 | 0.000735 | 0.00072046 | 0.0011429 | 0.0017654 | 0.0026899 | 0.0039552 | 0.0057028 | 0.0081009 | 0.010784 | 0.014068 | 0.018789 | 0.025192 | 0.031102 | 0.031102 | 0.031102 | 0.031102 | 0.031102 | 0.031102 | 0.031102 | 0.031102 | 0.031102 | 0.031102 | 0.031102 | 0.031102 | 0.031102 | 0.031102 | 0.031102 | 0.031102
Total EUE (MWh) - Option 5 | 0.0056418 | 0.25591 | 0.68323 | 0.0014781 | 0.0021035 | 0.0032594 | 0.0057142 | 0.0087425 | 0.012929 | 0.062477 | 0.026947 | 0.035639 | 0.046222 | 0.09475 | 0.073809 | 0.073809 | 0.073809 | 0.073809 | 0.073809 | 0.073809 | 0.073809 | 0.073809 | 0.073809 | 0.073809 | 0.073809 | 0.073809 | 0.073809 | 0.073809 | 0.073809 | 0.073809
Cost of EUE ($) - Option 5 | 217.8084 | 9879.5356 | 26376.9589 | 57.0632 | 81.208 | 125.8316 | 220.604 | 337.5153 | 499.1298 | 2412.001 | 1040.3236 | 1375.9029 | 1784.4555 | 3657.9267 | 2849.4778 | 2849.4778 | 2849.4778 | 2849.4778 | 2849.4778 | 2849.4778 | 2849.4778 | 2849.4778 | 2849.4778 | 2849.4778 | 2849.4778 | 2849.4778 | 2849.4778 | 2849.4778 | 2849.4778 | 2849.4778
Option 6 - Non Network | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Weighted Energy @ Risk (MWh) under N Conditions | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Weighted Energy @ Risk (MWh) under N-1 Conditions | 0.00053264 | 0.024666 | 0.093935 | 0.13705 | 0.18937 | 0.28501 | 0.52172 | 0.80306 | 1.3033 | 2.3466 | 2.192 | 2.0788 | 3.0373 | 4.9455 | 4.3726 | 4.3726 | 4.3726 | 4.3726 | 4.3726 | 4.3726 | 4.3726 | 4.3726 | 4.3726 | 4.3726 | 4.3726 | 4.3726 | 4.3726 | 4.3726 | 4.3726 | 4.3726
Weighted Energy @ Risk (MWh) under N-2 Conditions | 0.00024671 | 0.00033533 | 0.00062553 | 0.0010373 | 0.001642 | 0.00252 | 0.0037891 | 0.0055173 | 0.0078705 | 0.011044 | 0.014709 | 0.019219 | 0.025486 | 0.033729 | 0.041993 | 0.041993 | 0.041993 | 0.041993 | 0.041993 | 0.041993 | 0.041993 | 0.041993 | 0.041993 | 0.041993 | 0.041993 | 0.041993 | 0.041993 | 0.041993 | 0.041993 | 0.041993
Total EUE (MWh) - Option 6 | 0.00077936 | 0.025001 | 0.09456 | 0.13809 | 0.19101 | 0.28753 | 0.52551 | 0.80858 | 1.3112 | 2.3576 | 2.2067 | 2.098 | 3.0628 | 4.9792 | 4.4146 | 4.4146 | 4.4146 | 4.4146 | 4.4146 | 4.4146 | 4.4146 | 4.4146 | 4.4146 | 4.4146 | 4.4146 | 4.4146 | 4.4146 | 4.4146 | 4.4146 | 4.4146
Cost of EUE ($) - Option 6 | 30.0879 | 965.1927 | 3650.6002 | 5331.2005 | 7374.1791 | 11100.4844 | 20288.0126 | 31216.0396 | 50619.4372 | 91017.7275 | 85192.7774 | 80997.3924 | 118242.682 | 192228.1314 | 170429.3683 | 170429.3683 | 170429.3683 | 170429.3683 | 170429.3683 | 170429.3683 | 170429.3683 | 170429.3683 | 170429.3683 | 170429.3683 | 170429.3683 | 170429.3683 | 170429.3683 | 170429.3683 | 170429.3683 | 170429.3683
Option 7 - | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Weighted Energy @ Risk (MWh) under N Conditions | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Weighted Energy @ Risk (MWh) under N-1 Conditions | 0.0053489 | 0.25551 | 0.6825 | 0.9327 | 1.23 | 1.6873 | 2.5325 | 3.4943 | 4.8981 | 7.1332 | 7.614 | 8.0521 | 10.4859 | 14.6229 | 14.3758 | 14.3758 | 14.3758 | 14.3758 | 14.3758 | 14.3758 | 14.3758 | 14.3758 | 14.3758 | 14.3758 | 14.3758 | 14.3758 | 14.3758 | 14.3758 | 14.3758 | 14.3758
Weighted Energy @ Risk (MWh) under N-2 Conditions | 0.0002929 | 0.00039473 | 0.000735 | 0.0012171 | 0.0019252 | 0.0029518 | 0.0044325 | 0.0064455 | 0.0091777 | 0.01285 | 0.017155 | 0.022479 | 0.029729 | 0.039237 | 0.04892 | 0.04892 | 0.04892 | 0.04892 | 0.04892 | 0.04892 | 0.04892 | 0.04892 | 0.04892 | 0.04892 | 0.04892 | 0.04892 | 0.04892 | 0.04892 | 0.04892 | 0.04892
Total EUE (MWh) - Option 7 | 0.0056418 | 0.25591 | 0.68323 | 0.93391 | 1.2319 | 1.6902 | 2.537 | 3.5007 | 4.9073 | 7.146 | 7.6311 | 8.0746 | 10.5156 | 14.6621 | 14.4247 | 14.4247 | 14.4247 | 14.4247 | 14.4247 | 14.4247 | 14.4247 | 14.4247 | 14.4247 | 14.4247 | 14.4247 | 14.4247 | 14.4247 | 14.4247 | 14.4247 | 14.4247
Cost of EUE ($) - Option 7 | 217.8084 | 9879.5356 | 26376.9589 | 36054.8438 | 47558.8721 | 65252.4487 | 97942.7747 | 135148.7082 | 189450.6492 | 275881.0213 | 294608.8512 | 311729.6113 | 405968.4775 | 566048.0864 | 556883.0921 | 556883.0921 | 556883.0921 | 556883.0921 | 556883.0921 | 556883.0921 | 556883.0921 | 556883.0921 | 556883.0921 | 556883.0921 | 556883.0921 | 556883.0921 | 556883.0921 | 556883.0921 | 556883.0921 | 556883.0921
Option 8 - | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Weighted Energy @ Risk (MWh) under N Conditions | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Weighted Energy @ Risk (MWh) under N-1 Conditions | 0.0053489 | 0.25551 | 0.6825 | 0.9327 | 1.23 | 1.6873 | 2.5325 | 3.4943 | 4.8981 | 7.1332 | 7.614 | 8.0521 | 10.4859 | 14.6229 | 14.3758 | 14.3758 | 14.3758 | 14.3758 | 14.3758 | 14.3758 | 14.3758 | 14.3758 | 14.3758 | 14.3758 | 14.3758 | 14.3758 | 14.3758 | 14.3758 | 14.3758 | 14.3758
Weighted Energy @ Risk (MWh) under N-2 Conditions | 0.0002929 | 0.00039473 | 0.000735 | 0.0012171 | 0.0019252 | 0.0029518 | 0.0044325 | 0.0064455 | 0.0091777 | 0.01285 | 0.017155 | 0.022479 | 0.029729 | 0.039237 | 0.04892 | 0.04892 | 0.04892 | 0.04892 | 0.04892 | 0.04892 | 0.04892 | 0.04892 | 0.04892 | 0.04892 | 0.04892 | 0.04892 | 0.04892 | 0.04892 | 0.04892 | 0.04892
Total EUE (MWh) - Option 8 | 0.0056418 | 0.25591 | 0.68323 | 0.93391 | 1.2319 | 1.6902 | 2.537 | 3.5007 | 4.9073 | 7.146 | 7.6311 | 8.0746 | 10.5156 | 14.6621 | 14.4247 | 14.4247 | 14.4247 | 14.4247 | 14.4247 | 14.4247 | 14.4247 | 14.4247 | 14.4247 | 14.4247 | 14.4247 | 14.4247 | 14.4247 | 14.4247 | 14.4247 | 14.4247
Cost of EUE ($) - Option 8 | 217.8084 | 9879.5356 | 26376.9589 | 36054.8438 | 47558.8721 | 65252.4487 | 97942.7747 | 135148.7082 | 189450.6492 | 275881.0213 | 294608.8512 | 311729.6113 | 405968.4775 | 566048.0864 | 556883.0921 | 556883.0921 | 556883.0921 | 556883.0921 | 556883.0921 | 556883.0921 | 556883.0921 | 556883.0921 | 556883.0921 | 556883.0921 | 556883.0921 | 556883.0921 | 556883.0921 | 556883.0921 | 556883.0921 | 556883.0921