## Info
Document description
This model Energy at Risk model has been developed to calculated Energy at Risk (EaR) in terms of Expected Unsureved Energy (EUE) and the cost of EUE. The modelling inputs, calculation steps and outputs are described in the 'Modelling Steps' tab. Further detail on EaR/EUE calculations can be found in AusNet's Network Planning Policy and Guidelines.
Tab # | Tab Name | Description | Source/ Inputs
0.1 | Modelling Steps | E@R model process flowchart and underlying equations | N/A
0.2 | Modelling Example & QA | Example E@R model calculations and data flow; also used to validate base case | N/A
0.3 | QA | Quality assurance and data validation | Entire workbook
1.1 | Output for AusNet's NPV Model | Aggregates Supply Risk ($M) and EUE (MWh) for input into AusNet’s NPV model | Summary tab
2.1 | Key Model Assumptions & Inputs | E@R model inputs and asset selection | Augmentation plans from RPs/EPCs, Embedded Generation DB, Demand Management DB
2.2 | Tx PoF | Transformer Probabilities of Failure | Provided by Asset Management Team
2.3 | Customer No. and Volume per Feeder | Customer consumption data | Provided by Finance Team
2.4 | AER VCR Rates (2024) | AER 2024 VCR rates | AER VCR Factsheet
2.5 | Forecast - Summer | Summer Forecast Data | Extract from Forecasting Toolbox
2.6 | Forecast- Winter | Winter Forecast Data | Extract from Forecasting Toolbox
2.7 | Ratings | Station Rating Data | AMS 20-101 / Provided by Asset mangement Team
2.8 | FT (Forecast & Transfers) | Forecast, transfer & PF inputs | Forecast Summer , Forecast Winter , NP Transfer Sheet, PF = avg. max demand PF across stations
2.9 | Load Duration Curves | Load duration curve data | LDC Tool; data sourced from PI SCADA Historian and AEMO
3.1 | Capacity N | Option N capacity calculated | FT Sheet, Ratings & Key Model Assumptions
3.2 | Capacity N-1 | Option N-1 capacity calculated | FT Sheet, Ratings & Key Model Assumptions
3.3 | Capacity N-1 | Option N-2 capacity calculated | FT Sheet, Ratings & Key Model Assumptions
3.4 | Demand | Calculates maximum demand | FT Sheet & Key Model Assumptions
3.5 | MD Weighted LDC | Maps maximum demand forecast to load duration curve | Demand Sheet & Load Duration Curve Sheet
3.6 | Locational VCR | Calculates tailored VCR by location using feeder energy mix and AER rates | AER VCR Rates (2024) & Customer No./Volume per Feeder
3.7 | E@R N | Calculates N EUE using capacity and demand inputs | MD Weighted LDC & Capacity N
3.8 | E@R N-1 | Calculates N-1 EUE using capacity and demand inputs | MD Weighted LDC & Capacity N-1
3.9 | E@R N-2 | Calculates N-2 EUE using capacity and demand inputs | MD Weighted LDC & Capacity N-2
4 | POF N,N-1 & N-2 Risk | Calculates Station N , N-1 & N-2 PoF's from Tx PoF Data & MTTR | TX PoF & Key Model Assumptions
4.1 | Summary | Collates weighted EUE and calculates supply risk | E@R & Locational VCR
Revision table
Date | Editted by | Change
2025-10-14 | HT | Draft Version 2.1
2025-10-20 | HT | Version 2.2
2025-11-10 | HT | Version 2.3 Example Page Update and General Refinements

## Modelling Steps
Eq1. Locational VCR |  | Data Inputs |  |  | Calculations |  |  |  |  | Outputs
|  |  | Customer No. and Vol per Feeder |  | Eq1.
Locational VCR
Eq2. Maximum Demand
AER Latetst VCR Rates
Eq3. Options & Do nothing Capacity
Eq6. & Eq7.
Load Forecast
[9 empty] | Summary Sheet | Output for AusNet's NPV Model
Eq4. Help Sheet | Re Name Forecasted LDC add Forecast MD to eq
Transfer Capacity
Eq2.
Eq5. Energy at Risk ( Option/ Do Nothing Capacity) |  |  |  |  | Options & Do Nothing Max Demand
Embeded Generation
Eq6. Weighted Expected Unserved Energy
[6 empty] | Eq.4 | Eq.5
Demand Mangement Capacity
[6 empty] | Forecasted LDC |  | Energy @ Risk Sheet
Eq7. Supply Risk
Load Duration Curves
|  |  | Asset Ratings |  | Eq3.
Options & Do Nothing Capacity
Planned & Proposed Works

## Modelling Steps Example & QA
End of Sheet
Data Inputs |  |  | Calculations | [12 empty] | Outputs
AER VCR Rates(2024 |  |  | Locational (Tailored VCR)
Category | Rate |  | Base case |  | Energy Usage (CY 2024 kWh) | Energy Usage (CY 2024 %) | Tailored VCR
Dec 24 AER VCR ($/kWh) - Res | 49.23 |  | Dec 24 AER VCR ($/kWh) - Res | 49.23 | 67934749.1441 | 34.06% | 16.7657
Dec 24 AER VCR ($/kWh) - Com | 34.39 |  | Dec 24 AER VCR ($/kWh) - Com | 34.39 | 101368150.4504 | 50.82% | 17.4756
Dec 24 AER VCR ($/kWh) - Ind | 33.49 |  | Dec 24 AER VCR ($/kWh) - Ind | 33.49 | 17726336.2671 | 8.886% | 2.976
Dec 24 AER VCR ($/kWh) - Agr | 22.25 |  | Dec 24 AER VCR ($/kWh) - Agr | 22.25 | 12451243.5083 | 6.242% | 1.3888
[5 empty] | 199480479.3698 |  | 38.6062
Customer No. and Vol per Feeder | [6 empty] | 38606.1513 | [8 empty] | Summary |  | Outputs for NPV model
COMMERCIAL | 101368150.4504 | [14 empty] | Year | 2031 | Year | 2031
[16 empty] | E@R MWh | 10.0369 | E@R MWh | 10.0369
RESIDENTL | 67934749.1441 | [14 empty] | cost of EUE ($) | 387486.1996 | cost of EUE ($M) | 0.38749
FARM | 12451243.5083
INDUSTRIAL | 17726336.2671
Forecast (FCT)
Forecast | 2031
Summer POE50 | 82.5169
Summer POE10 | 89.3084
Winter POE50 | 80.6241
Winter POE10 | 83.8742
Transfer Capacity |  |  | Option Max Demand |  |  |  | MD Weighted LDC |  |  | E@R (N) |  | E@R (N-1) |  | E@R (N-2)
Year | 2031 |  | Forecast | 2031 |  |  | % of MD | Summer - AD - Hours | FY31 | % of MD | FY31 | % of MD | FY31 | % of MD | FY31
Capacity | 1.58 |  | Summer POE50 | 80.9369 |  |  | 100% | 0 | 80.9369 | 100% |  | 100% |  | 100%
|  |  | Summer POE10 | 87.7284 |  |  | 99% | 0 | 80.1275 | 99% |  | 99% | 0 | 99% | 0
Embedded Generation |  |  | Winter POE50 | 79.0441 |  |  | 98% | 0 | 79.3181 | 98% |  | 98% | 0 | 98% | 0
|  |  | Winter POE10 | 82.2942 |  |  | 97% | 0.37816 | 78.5088 | 97% |  | 97% | 12.8249 | 97% | 29.8423
Year | 2031 | [5 empty] | 95% | 2.269 | 76.89 | 95% |  | 95% | 61.8287 | 95% | 146.9157
Capacity | 0 | [5 empty] | 90% | 5.6725 | 72.8432 | 90% |  | 90% | 101.6504 | 90% | 254.8069
[7 empty] | 85% | 15.8829 | 68.7963 | 85% |  | 85% | 263.6311 | 85% | 723.1007
Demand Mangement | [6 empty] | 80% | 31.0095 | 64.7495 | 80% |  | 80% | 329.3497 | 80% | 1010.0454
[7 empty] | 75% | 72.9857 | 60.7027 | 75% |  | 75% | 744.0742 | 75% | 2633.0048
Year | 2031 | [5 empty] | 70% | 150.5094 | 56.6558 | 70% |  | 70% | 1060.4649 | 70% | 4549.0304
Capacity | 0 | [5 empty] | 65% | 359.6342 | 52.609 | 65% |  | 65% | 2014.373 | 65% | 11424.9912
[7 empty] | 60% | 689.7717 | 48.5621 | 60% |  | 60% | 1843.9992 | 60% | 16700.1831
LDC | [6 empty] | 55% | 1095.5419 | 44.5153 | 55% |  | 55% | 636.1403 | 55% | 18884.0238
[7 empty] | 50% | 1666.1918 | 40.4684 | 50% |  | 50% |  | 50% | 24247.9772
% of MD | Summer - AD - Duration % | Summer - AD - Hours |  |  |  |  | 45% | 2506.0947 | 36.4216 | 45% |  | 45% |  | 45% | 32290.0814
100% | 0% | 0 |  |  |  |  | 40% | 3164.4787 | 32.3748 | 40% |  | 40% |  | 40% | 22647.2082
99% | 0% | 0 |  |  |  |  | 35% | 3551.3408 | 28.3279 | 35% |  | 35% |  | 35% | 11741.7782
98% | 0% | 0 |  |  |  |  | 30% | 3758.953 | 24.2811 | 30% |  | 30% |  | 30% | 5461.132
97% | 0.00861% | 0.37816 |  |  |  |  | 25% | 3926.4798 | 20.2342 | 25% |  | 25% |  | 25% | 3728.7511
95% | 0.05166% | 2.269 |  |  |  |  | 20% | 4050.5177 | 16.1874 | 20% |  | 20% |  | 20% | 2258.8289
90% | 0.1292% | 5.6725 |  |  |  |  | 15% | 4152.622 | 12.1405 | 15% |  | 15% |  | 15% | 1446.2014
85% | 0.3616% | 15.8829 |  |  |  |  | 10% | 4248.2976 | 8.0937 | 10% |  | 10% |  | 10% | 967.9602
80% | 0.706% | 31.0095 |  |  |  |  | 5% | 4361.7469 | 4.0468 | 5% |  | 5% |  | 5% | 688.6673
75% | 1.662% | 72.9857 |  |  |  |  | 9.992e-14% | 4391.6218 | 8.0872e-14 | 9.992e-14% |  | 9.992e-14% |  | 9.992e-14% | 60.4497
70% | 3.427% | 150.5094 | [7 empty] | Total E@R | 0 | Total E@R | 7068.3364 | Total E@R | 161894.98
65% | 8.188% | 359.6342 | [7 empty] | Total WE@R | 0 | Total WE@R | 2.1876 | Total WE@R | 0.0065575
60% | 15.71% | 689.7717 |  |  |  |  | MD Weighted LDC
55% | 24.94% | 1095.5419
50% | 37.94% | 1666.1918 |  |  |  |  | % of MD | Summer - MD - Hours | FY31
45% | 57.06% | 2506.0947 |  |  |  |  | 100% | 0 | 87.7284 | E@R (N) |  | E@R (N-1) |  | E@R (N-2)
40% | 72.05% | 3164.4787 |  |  |  |  | 99% | 1.5127 | 86.8512
35% | 80.86% | 3551.3408 |  |  |  |  | 98% | 2.269 | 85.9739 | % of MD | FY31 | % of MD | FY31 | % of MD | FY31
30% | 85.59% | 3758.953 |  |  |  |  | 97% | 3.7816 | 85.0966 | 100% |  | 100% |  | 100%
25% | 89.4% | 3926.4798 |  |  |  |  | 95% | 6.0506 | 83.342 | 99% |  | 99% | 63.97 | 99% | 132.0395
20% | 92.22% | 4050.5177 |  |  |  |  | 90% | 16.2611 | 78.9556 | 98% |  | 98% | 31.3215 | 98% | 65.3562
15% | 94.55% | 4152.622 |  |  |  |  | 85% | 26.4715 | 74.5692 | 97% |  | 97% | 61.3159 | 97% | 129.3855
10% | 96.73% | 4248.2976 |  |  |  |  | 80% | 34.0348 | 70.1827 | 95% |  | 95% | 88.988 | 95% | 191.0924
5% | 99.31% | 4361.7469 |  |  |  |  | 75% | 48.405 | 65.7963 | 90% |  | 90% | 369.095 | 90% | 828.5646
9.992e-14% | 99.99% | 4391.6218 |  |  |  |  | 70% | 76.3892 | 61.4099 | 85% |  | 85% | 324.3078 | 85% | 783.7774
[7 empty] | 65% | 114.2056 | 57.0235 | 80% |  | 80% | 207.0522 | 80% | 547.4001
[7 empty] | 60% | 178.1154 | 52.6371 | 75% |  | 75% | 330.3652 | 75% | 977.0262
[7 empty] | 55% | 311.6074 | 48.2506 | 70% |  | 70% | 520.5925 | 70% | 1779.8796
LDC | [6 empty] | 50% | 636.0723 | 43.8642 | 65% |  | 65% | 537.6246 | 65% | 2239.3639
[7 empty] | 45% | 1179.4944 | 39.4778 | 60% |  | 60% | 628.2504 | 60% | 3504.1898
% of MD | Summer - MD - Duration % | Summer - MD - Hours |  |  |  |  | 40% | 1808.3816 | 35.0914 | 55% |  | 55% | 726.7105 | 55% | 6733.8501
100% | 0% | 0 |  |  |  |  | 35% | 2779.1293 | 30.705 | 50% |  | 50% | 390.8095 | 50% | 14944.0217
99% | 0.03444% | 1.5127 |  |  |  |  | 30% | 3814.165 | 26.3185 | 45% |  | 45% |  | 45% | 22644.9453
98% | 0.05166% | 2.269 |  |  |  |  | 25% | 4166.9923 | 21.9321 | 40% |  | 40% |  | 40% | 23447.7987
97% | 0.0861% | 3.7816 |  |  |  |  | 20% | 4282.7105 | 17.5457 | 35% |  | 35% |  | 35% | 31935.8172
95% | 0.1378% | 6.0506 |  |  |  |  | 15% | 4364.7722 | 13.1593 | 30% |  | 30% |  | 30% | 29510.6691
90% | 0.3702% | 16.2611 |  |  |  |  | 10% | 4391.6218 | 8.7728 | 25% |  | 25% |  | 25% | 8512.071
85% | 0.6027% | 26.4715 |  |  |  |  | 5% | 4391.6218 | 4.3864 | 20% |  | 20% |  | 20% | 2284.1512
80% | 0.7749% | 34.0348 |  |  |  |  | 9.992e-14% | 4391.6218 | 8.7658e-14 | 15% |  | 15% |  | 15% | 1259.8495
75% | 1.102% | 48.405 | [7 empty] | 10% |  | 10% |  | 10% | 294.4349
70% | 1.739% | 76.3892 | [7 empty] | 5% |  | 5% |  | 5% | 0
65% | 2.6% | 114.2056 | [7 empty] | 9.992e-14% |  | 9.992e-14% |  | 9.992e-14% | 0
60% | 4.055% | 178.1154 | [7 empty] | Total E@R | 0 | Total E@R | 4280.4031 | Total E@R | 152745.6837
55% | 7.095% | 311.6074 |  |  |  |  | MD Weighted LDC |  |  | Total WE@R | 0 | Total WE@R | 0.56774 | Total WE@R | 0.0026515
50% | 14.48% | 636.0723
45% | 26.86% | 1179.4944 |  |  |  |  | % of MD | Winter - AD - Hours | FY31
40% | 41.17% | 1808.3816 |  |  |  |  | 100% | 0 | 79.0441
35% | 63.28% | 2779.1293 |  |  |  |  | 99% | 1.486 | 78.2537 | E@R (N) |  | E@R (N-1) |  | E@R (N-2)
30% | 86.84% | 3814.165 |  |  |  |  | 98% | 3.2692 | 77.4632
25% | 94.88% | 4166.9923 |  |  |  |  | 97% | 6.8356 | 76.6728 | % of MD | FY31 | % of MD | FY31 | % of MD | FY31
20% | 97.51% | 4282.7105 |  |  |  |  | 95% | 17.5347 | 75.0919 | 100% |  | 100% |  | 100%
15% | 99.38% | 4364.7722 |  |  |  |  | 90% | 78.7576 | 71.1397 | 99% |  | 99% | 43.9094 | 99% | 116.8717
10% | 99.99% | 4391.6218 |  |  |  |  | 85% | 236.8672 | 67.1875 | 98% |  | 98% | 51.2818 | 98% | 138.8365
5% | 99.99% | 4391.6218 |  |  |  |  | 80% | 497.5104 | 63.2353 | 97% |  | 97% | 99.7446 | 97% | 274.854
9.992e-14% | 99.99% | 4391.6218 |  |  |  |  | 75% | 803.6248 | 59.2831 | 95% |  | 95% | 286.5483 | 95% | 811.8764
[7 empty] | 70% | 1155.2107 | 55.3309 | 90% |  | 90% | 1470.3172 | 90% | 4476.3615
[7 empty] | 65% | 1553.1596 | 51.3787 | 85% |  | 85% | 3172.248 | 85% | 10935.4305
[7 empty] | 60% | 2026.2996 | 47.4265 | 80% |  | 80% | 4199.3237 | 80% | 16996.9008
LDC | [6 empty] | 55% | 2598.4068 | 43.4743 | 75% |  | 75% | 3722.1035 | 75% | 18752.3252
[7 empty] | 50% | 3233.5201 | 39.5221 | 70% |  | 70% | 2885.4588 | 70% | 20148.3251
% of MD | Winter - AD (P50) - Duration % | Winter - AD - Hours |  |  |  |  | 45% | 3775.313 | 35.5699 | 65% |  | 65% | 1693.1832 | 65% | 21232.4714
100% | 0% | 0 |  |  |  |  | 40% | 4072.8088 | 31.6176 | 60% |  | 60% | 310.8024 | 60% | 23374.3358
99% | 0.03383% | 1.486 |  |  |  |  | 35% | 4198.821 | 27.6654 | 55% |  | 55% |  | 55% | 26002.4804
98% | 0.07443% | 3.2692 |  |  |  |  | 30% | 4271.3374 | 23.7132 | 50% |  | 50% |  | 50% | 26356.0319
97% | 0.1556% | 6.8356 |  |  |  |  | 25% | 4321.8611 | 19.761 | 45% |  | 45% |  | 45% | 20342.1324
95% | 0.3992% | 17.5347 |  |  |  |  | 20% | 4353.067 | 15.8088 | 40% |  | 40% |  | 40% | 9993.9968
90% | 1.793% | 78.7576 |  |  |  |  | 15% | 4369.4129 | 11.8566 | 35% |  | 35% |  | 35% | 3735.1954
85% | 5.393% | 236.8672 |  |  |  |  | 10% | 4378.6261 | 7.9044 | 30% |  | 30% |  | 30% | 1862.8993
80% | 11.33% | 497.5104 |  |  |  |  | 5% | 4391.7028 | 3.9522 | 25% |  | 25% |  | 25% | 1098.2414
75% | 18.3% | 803.6248 |  |  |  |  | 9.992e-14% | 4391.7028 | 7.8981e-14 | 20% |  | 20% |  | 20% | 554.9937
70% | 26.3% | 1155.2107 | [7 empty] | 15% |  | 15% |  | 15% | 226.1085
65% | 35.36% | 1553.1596 | [7 empty] | 10% |  | 10% |  | 10% | 91.0307
60% | 46.14% | 2026.2996 | [7 empty] | 5% |  | 5% |  | 5% | 77.5229
55% | 59.16% | 2598.4068 | [7 empty] | 9.992e-14% |  | 9.992e-14% |  | 9.992e-14% | 0
50% | 73.62% | 3233.5201 |  |  |  |  | MD Weighted LDC |  |  | Total E@R | 0 | Total E@R | 17934.9211 | Total E@R | 207599.2223
45% | 85.96% | 3775.313 | [7 empty] | Total WE@R | 0 | Total WE@R | 4.7159 | Total WE@R | 0.0071443
40% | 92.73% | 4072.8088 |  |  |  |  | % of MD | Winter - MD - Hours | FY31
35% | 95.6% | 4198.821 |  |  |  |  | 100% | 0 | 82.2942 | E@R (N) |  | E@R (N) |  | E@R (N)
30% | 97.25% | 4271.3374 |  |  |  |  | 99% | 1.486 | 81.4712
25% | 98.4% | 4321.8611 |  |  |  |  | 98% | 3.2692 | 80.6483 | % of MD | FY31 | % of MD | FY31 | % of MD | FY31
20% | 99.11% | 4353.067 |  |  |  |  | 97% | 6.8356 | 79.8254 | 100% |  | 100% |  | 100%
15% | 99.49% | 4369.4129 |  |  |  |  | 95% | 17.5347 | 78.1795 | 99% |  | 99% | 48.7149 | 99% | 121.6771
10% | 99.7% | 4378.6261 |  |  |  |  | 90% | 78.7576 | 74.0648 | 98% |  | 98% | 56.9904 | 98% | 144.5451
5% | 99.99% | 4391.7028 |  |  |  |  | 85% | 236.8672 | 69.9501 | 97% |  | 97% | 111.0458 | 97% | 286.1552
9.992e-14% | 99.99% | 4391.7028 |  |  |  |  | 80% | 497.5104 | 65.8353 | 95% |  | 95% | 319.9304 | 95% | 845.2585
[7 empty] | 75% | 803.6248 | 61.7206 | 90% |  | 90% | 1654.3725 | 90% | 4660.4169
[7 empty] | 70% | 1155.2107 | 57.6059 | 85% |  | 85% | 3621.8821 | 85% | 11385.0646
[7 empty] | 65% | 1553.1596 | 53.4912 | 80% |  | 80% | 4898.1884 | 80% | 17695.7655
LDC | [6 empty] | 60% | 2026.2996 | 49.3765 | 75% |  | 75% | 4493.1463 | 75% | 19523.368
[7 empty] | 55% | 2598.4068 | 45.2618 | 70% |  | 70% | 3713.9012 | 70% | 20976.7675
% of MD | Winter - MD (P10) - Duration % | Winter - MD - Hours |  |  |  |  | 50% | 3233.5201 | 41.1471 | 65% |  | 65% | 2566.2027 | 65% | 22105.4909
100% | 0% | 0 |  |  |  |  | 45% | 3775.313 | 37.0324 | 60% |  | 60% | 1104.2451 | 60% | 24335.4227
99% | 0.03383% | 1.486 |  |  |  |  | 40% | 4072.8088 | 32.9177 | 55% |  | 55% | 5.3153 | 55% | 27071.6291
98% | 0.07443% | 3.2692 |  |  |  |  | 35% | 4198.821 | 28.803 | 50% |  | 50% |  | 50% | 27439.7177
97% | 0.1556% | 6.8356 |  |  |  |  | 30% | 4271.3374 | 24.6883 | 45% |  | 45% |  | 45% | 21178.5436
95% | 0.3992% | 17.5347 |  |  |  |  | 25% | 4321.8611 | 20.5735 | 40% |  | 40% |  | 40% | 10404.9218
90% | 1.793% | 78.7576 |  |  |  |  | 20% | 4353.067 | 16.4588 | 35% |  | 35% |  | 35% | 3888.7761
85% | 5.393% | 236.8672 |  |  |  |  | 15% | 4369.4129 | 12.3441 | 30% |  | 30% |  | 30% | 1939.4965
80% | 11.33% | 497.5104 |  |  |  |  | 10% | 4378.6261 | 8.2294 | 25% |  | 25% |  | 25% | 1143.398
75% | 18.3% | 803.6248 |  |  |  |  | 5% | 4391.7028 | 4.1147 | 20% |  | 20% |  | 20% | 577.8134
70% | 26.3% | 1155.2107 |  |  |  |  | 9.992e-14% | 4391.7028 | 8.2228e-14 | 15% |  | 15% |  | 15% | 235.4055
65% | 35.36% | 1553.1596 | [7 empty] | 10% |  | 10% |  | 10% | 94.7736
60% | 46.14% | 2026.2996 | [7 empty] | 5% |  | 5% |  | 5% | 80.7104
55% | 59.16% | 2598.4068 | [7 empty] | 9.992e-14% |  | 9.992e-14% | 0 | 9.992e-14% | 0
50% | 73.62% | 3233.5201 | [7 empty] | Total E@R | 0 | Total E@R | 22593.9352 | Total E@R | 216135.1177
45% | 85.96% | 3775.313 | [7 empty] | Total WE@R | 0 | Total WE@R | 2.5461 | Total WE@R | 0.0031877
40% | 92.73% | 4072.8088
35% | 95.6% | 4198.821
30% | 97.25% | 4271.3374
25% | 98.4% | 4321.8611
20% | 99.11% | 4353.067
15% | 99.49% | 4369.4129
10% | 99.7% | 4378.6261
5% | 99.99% | 4391.7028
9.992e-14% | 99.99% | 4391.7028
Ratings (MVA) |  |  |  | Option Capacity
SCR (N) | 91.9 |  |  | Year | 2031
SCR (N-1) | 45 |  |  | SCR (N) | 91.9
SCR (N-2) | 0 |  |  | SCR (N-1) | 45
WCR (N) | 95.7 |  |  | SCR (N-2) | 0
WCR (N-1) | 49.1 |  |  | WCR (N) | 95.7
WCR (N-2) | 0 |  |  | WCR (N-1) | 49.1
|  |  |  | WCR (N-2) | 0
Planned Works
Year | 2031
Capacity (N) | 0
Capacity (N-1) | 0
Capacity (N-2) | 0
Power Factor
Value | 1
End of Sheet

## QA
Overall Status
Good
Number | Check Name | Status | Info
1 | Forecast | Good | Confirms POE10 forecast is higher than POE50
2 | Option Maximum Demand | Good | Confirms whether transfers, embedded generation, and demand management contribute to demand reduction when present
3 | EUE Base Case | Good | Confirms Do Nothing/Base Case EUE for FY31 is the same as the example / checks model in Modelling Steps Example Sheet
4 | Feeder Consumption | Good | Confirms if aggregated feeder energy consumption by customer category matches with total feeder energy consumption (excluding uncategorised consumption)

## Output for AusNet's NPV model
Involuntary load shedding (NER 5.17.1(c)(4)(ii))
Base Case
Cost
Option 1 - Do Nothing / Base Case | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Cost of EUE ($M) | 0.0013201 | 0.05225 | 0.11664 | 0.15651 | 0.20359 | 0.27196 | 0.38749 | 0.51872 | 0.70091 | 0.97181 | 1.0624 | 1.1495 | 1.4581 | 1.9768 | 1.9779 | 1.9779 | 1.9779 | 1.9779 | 1.9779 | 1.9779 | 1.9779 | 1.9779 | 1.9779 | 1.9779 | 1.9779 | 1.9779 | 1.9779 | 1.9779 | 1.9779 | 1.9779
Total EUE (MWh) | 0.034194 | 1.3534 | 3.0212 | 4.0541 | 5.2736 | 7.0444 | 10.0369 | 13.4362 | 18.1553 | 25.1725 | 27.5183 | 29.7749 | 37.7689 | 51.2051 | 51.234 | 51.234 | 51.234 | 51.234 | 51.234 | 51.234 | 51.234 | 51.234 | 51.234 | 51.234 | 51.234 | 51.234 | 51.234 | 51.234 | 51.234 | 51.234
Residual Values
Option 2 - 1B New PHS ZSS + Three new feeders | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Cost of Avoided EUE ($M) | 0.0013201 | 0.05225 | 0.11664 | 0.0071337 | 0.0099778 | 0.015796 | 0.032163 | 0.052943 | 0.092078 | 0.17967 | 0.16553 | 0.15711 | 0.23555 | 0.40207 | 0.34511 | 0.34511 | 0.34511 | 0.34511 | 0.34511 | 0.34511 | 0.34511 | 0.34511 | 0.34511 | 0.34511 | 0.34511 | 0.34511 | 0.34511 | 0.34511 | 0.34511 | 0.34511
Total EUE (MWh) | 0.034194 | 1.3534 | 3.0212 | 0.18478 | 0.25845 | 0.40916 | 0.83312 | 1.3714 | 2.385 | 4.6539 | 4.2878 | 4.0696 | 6.1013 | 10.4148 | 8.9393 | 8.9393 | 8.9393 | 8.9393 | 8.9393 | 8.9393 | 8.9393 | 8.9393 | 8.9393 | 8.9393 | 8.9393 | 8.9393 | 8.9393 | 8.9393 | 8.9393 | 8.9393
Option 3 - 2B PHM 3rd Tx + Switchroom + Two new feeders + OFR12 New Feeder | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Cost of Avoided EUE ($M) | 0.0013201 | 0.05225 | 0.11664 | 1.4963e-05 | 2.4358e-05 | 3.9698e-05 | 6.7481e-05 | 0.00010654 | 0.00016781 | 0.00027133 | 0.00035474 | 0.00046329 | 0.00065563 | 0.0010211 | 0.0011164 | 0.0011164 | 0.0011164 | 0.0011164 | 0.0011164 | 0.0011164 | 0.0011164 | 0.0011164 | 0.0011164 | 0.0011164 | 0.0011164 | 0.0011164 | 0.0011164 | 0.0011164 | 0.0011164 | 0.0011164
Total EUE (MWh) | 0.034194 | 1.3534 | 3.0212 | 0.00038758 | 0.00063093 | 0.0010283 | 0.0017479 | 0.0027597 | 0.0043468 | 0.0070283 | 0.0091888 | 0.012 | 0.016983 | 0.026449 | 0.028918 | 0.028918 | 0.028918 | 0.028918 | 0.028918 | 0.028918 | 0.028918 | 0.028918 | 0.028918 | 0.028918 | 0.028918 | 0.028918 | 0.028918 | 0.028918 | 0.028918 | 0.028918
Option 4 - 3B OFR 3rd Tx + Switchroom + Two new feeders + OFR12 New Feeder | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Cost of Avoided EUE ($M) | 0.0013201 | 0.05225 | 0.11664 | 0.10529 | 0.13815 | 0.18777 | 0.27663 | 0.37794 | 0.52316 | 0.74854 | 0.80691 | 0.86113 | 1.1105 | 1.526 | 1.5167 | 1.5167 | 1.5167 | 1.5167 | 1.5167 | 1.5167 | 1.5167 | 1.5167 | 1.5167 | 1.5167 | 1.5167 | 1.5167 | 1.5167 | 1.5167 | 1.5167 | 1.5167
Total EUE (MWh) | 0.034194 | 1.3534 | 3.0212 | 2.7274 | 3.5783 | 4.8637 | 7.1654 | 9.7897 | 13.5511 | 19.3891 | 20.9011 | 22.3056 | 28.7637 | 39.5273 | 39.2866 | 39.2866 | 39.2866 | 39.2866 | 39.2866 | 39.2866 | 39.2866 | 39.2866 | 39.2866 | 39.2866 | 39.2866 | 39.2866 | 39.2866 | 39.2866 | 39.2866 | 39.2866
Option 5 - 4B LLG 2nd Tx + Switchroom + Two new feeders + OFR12 New Feeder | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Cost of Avoided EUE ($M) | 0.0013201 | 0.05225 | 0.11664 | 0.0037995 | 0.0052739 | 0.0083624 | 0.018169 | 0.031477 | 0.059364 | 0.1307 | 0.11267 | 0.1031 | 0.16205 | 0.29635 | 0.24252 | 0.24252 | 0.24252 | 0.24252 | 0.24252 | 0.24252 | 0.24252 | 0.24252 | 0.24252 | 0.24252 | 0.24252 | 0.24252 | 0.24252 | 0.24252 | 0.24252 | 0.24252
Total EUE (MWh) | 0.034194 | 1.3534 | 3.0212 | 0.098418 | 0.13661 | 0.21661 | 0.47063 | 0.81534 | 1.5377 | 3.3854 | 2.9185 | 2.6705 | 4.1975 | 7.6761 | 6.2819 | 6.2819 | 6.2819 | 6.2819 | 6.2819 | 6.2819 | 6.2819 | 6.2819 | 6.2819 | 6.2819 | 6.2819 | 6.2819 | 6.2819 | 6.2819 | 6.2819 | 6.2819
Option 6 - | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Cost of Avoided EUE ($M) | 0.0013201 | 0.05225 | 0.11664 | 0.15651 | 0.20359 | 0.27196 | 0.38749 | 0.51872 | 0.70091 | 0.97181 | 1.0624 | 1.1495 | 1.4581 | 1.9768 | 1.9779 | 1.9779 | 1.9779 | 1.9779 | 1.9779 | 1.9779 | 1.9779 | 1.9779 | 1.9779 | 1.9779 | 1.9779 | 1.9779 | 1.9779 | 1.9779 | 1.9779 | 1.9779
Total EUE (MWh) | 0.034194 | 1.3534 | 3.0212 | 4.0541 | 5.2736 | 7.0444 | 10.0369 | 13.4362 | 18.1553 | 25.1725 | 27.5183 | 29.7749 | 37.7689 | 51.2051 | 51.234 | 51.234 | 51.234 | 51.234 | 51.234 | 51.234 | 51.234 | 51.234 | 51.234 | 51.234 | 51.234 | 51.234 | 51.234 | 51.234 | 51.234 | 51.234
Option 7 - | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Cost of Avoided EUE ($M) | 0.0013201 | 0.05225 | 0.11664 | 0.15651 | 0.20359 | 0.27196 | 0.38749 | 0.51872 | 0.70091 | 0.97181 | 1.0624 | 1.1495 | 1.4581 | 1.9768 | 1.9779 | 1.9779 | 1.9779 | 1.9779 | 1.9779 | 1.9779 | 1.9779 | 1.9779 | 1.9779 | 1.9779 | 1.9779 | 1.9779 | 1.9779 | 1.9779 | 1.9779 | 1.9779
Total EUE (MWh) | 0.034194 | 1.3534 | 3.0212 | 4.0541 | 5.2736 | 7.0444 | 10.0369 | 13.4362 | 18.1553 | 25.1725 | 27.5183 | 29.7749 | 37.7689 | 51.2051 | 51.234 | 51.234 | 51.234 | 51.234 | 51.234 | 51.234 | 51.234 | 51.234 | 51.234 | 51.234 | 51.234 | 51.234 | 51.234 | 51.234 | 51.234 | 51.234
Option 8 - | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Cost of Avoided EUE ($M) | 0.0013201 | 0.05225 | 0.11664 | 0.15651 | 0.20359 | 0.27196 | 0.38749 | 0.51872 | 0.70091 | 0.97181 | 1.0624 | 1.1495 | 1.4581 | 1.9768 | 1.9779 | 1.9779 | 1.9779 | 1.9779 | 1.9779 | 1.9779 | 1.9779 | 1.9779 | 1.9779 | 1.9779 | 1.9779 | 1.9779 | 1.9779 | 1.9779 | 1.9779 | 1.9779
Total EUE (MWh) | 0.034194 | 1.3534 | 3.0212 | 4.0541 | 5.2736 | 7.0444 | 10.0369 | 13.4362 | 18.1553 | 25.1725 | 27.5183 | 29.7749 | 37.7689 | 51.2051 | 51.234 | 51.234 | 51.234 | 51.234 | 51.234 | 51.234 | 51.234 | 51.234 | 51.234 | 51.234 | 51.234 | 51.234 | 51.234 | 51.234 | 51.234 | 51.234

## Key Model Assumption & Inputs
Select ZSS & Region | PHM | Central | MTTR
Probability Weighting for 10% POE MDs | 30% |  |  | Central | North | East | For Analysis
Probability Weighting for 50% POE MDs | 70% |  | N-1 MTTR (years) | 0.3858 | 0.1418 | 0.3858 | 0.3858
First year of analysis | FY25 |  | N-2 MTTR (years) | 0.2344 | 0.049 | 0.2344 | 0.2344
Select Sensitivity Variant | Forecast Sensitivity
High | 110% |  | PV Factor's |  |  | PoF Sensitvity
Options | Name |  | Summer | 1.33 |  | Varaint
Option 1 - Do Nothing / Base Case | Do Nothing / Base Case |  | Winter | 1.13 |  | Base | 100%
Option 2 - 1B New PHS ZSS + Three new feeders | 1B New PHS ZSS + Three new feeders
Option 3 - 2B PHM 3rd Tx + Switchroom + Two new feeders + OFR12 New Feeder | 2B PHM 3rd Tx + Switchroom + Two new feeders + OFR12 New Feeder |  | Demand Response
Option 4 - 3B OFR 3rd Tx + Switchroom + Two new feeders + OFR12 New Feeder | 3B OFR 3rd Tx + Switchroom + Two new feeders + OFR12 New Feeder |  | Average Rate % | 20%
Option 5 - 4B LLG 2nd Tx + Switchroom + Two new feeders + OFR12 New Feeder | 4B LLG 2nd Tx + Switchroom + Two new feeders + OFR12 New Feeder
Option 6 -
Option 7 -
Option 8 -
Added Capacity (MVA) | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39
Added Capacity (MVA) Option 1 N | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 1 N-1 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 1 N-2 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 2 N | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 2 N-1 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 2 N-2 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 3 N |  |  |  | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45
Added Capacity (MVA) Option 3 N-1 |  |  |  | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45
Added Capacity (MVA) Option 3 N-2 |  |  |  | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45
Added Capacity (MVA) Option 4 N | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 4 N-1 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 4 N-2 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 5 N | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 5 N-1 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 5 N-2 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 6 N | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 6 N-1 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 6 N-2 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 7 N | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 7 N-1 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 7 N-2 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 8 N | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 8 N-1 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 8 N-2 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Embedded Generation (MVA) | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39
Avaliable Embedded Generation (MVA) Option 1 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Embedded Generation (MVA) Option 2 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Embedded Generation (MVA) Option 3 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Embedded Generation (MVA) Option 4 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Embedded Generation (MVA) Option 5 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Embedded Generation (MVA) Option 6 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Embedded Generation (MVA) Option 7 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Embedded Generation (MVA) Option 8 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Demand Management (MVA) | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39
Avaliable Demand Management (MVA) Option 1 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Demand Management (MVA) Option 2 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Demand Management (MVA) Option 3 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Demand Management (MVA) Option 4 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Demand Management (MVA) Option 5 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Demand Management (MVA) Option 6 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Demand Management (MVA) Option 7 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Demand Management (MVA) Option 8 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Transfers (MVA) | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39
Planned Transfers (MVA) Option 1 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Transfers (MVA) Option 2 |  |  |  | 19.3333 | 19.3333 | 19.3333 | 19.3333 | 19.3333 | 19.3333 | 19.3333 | 19.3333 | 19.3333 | 19.3333 | 19.3333 | 19.3333
Added Transfers (MVA) Option 3 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Transfers (MVA) Option 4 |  |  |  | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
Added Transfers (MVA) Option 5 |  |  |  | 21.75 | 21.75 | 21.75 | 21.75 | 21.75 | 21.75 | 21.75 | 21.75 | 21.75 | 21.75 | 21.75 | 21.75
Added Transfers (MVA) Option 6 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Transfers (MVA) Option 7 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Transfers (MVA) Option 8 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Block Loads Not in Forecast (MVA) | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39
Block Loads (MVA) | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Base | FY25: 100%
High | FY25: 110%
Low | FY25: 90%

## Tx PoF
Transformer Failure Rates for individual Transformers
[5 empty] | 10 | 8 | 10 | 6 | 8 | 6 | 6 | 10 | 6
Zone | arm_asset_id | floc | user_status | Age | Major Winding insulation | Accelerated cellulose Aging | Winding insulating liquid | Hot metal fault covered by paper | Chemical contamination, degradation | Physical & chemical contamination, degradation | Physical contamination | Short Circuit Concern | OLTC | WMA Health Score | WMA CS | WMA effective age | WMA Beta | WMA Eta | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WGI | 30192717 | DS-WGI-TRNFMR-9000004493 |  | 59 | 5 | 3 | 1 | 5 | 2 | 1 | 5 | 5 | 5 | 351.4286 | 4 | 60 | 3.5 | 82 | 1.976% | 1.976% | 2.058% | 2.142% | 2.227% | 2.315% | 2.405% | 2.496% | 2.59% | 2.686% | 2.783% | 2.883% | 2.985% | 3.089% | 3.195% | 3.303% | 3.413% | 3.525% | 3.639% | 3.755% | 3.873% | 3.994% | 4.116% | 4.241% | 4.368% | 4.497% | 4.628% | 4.761% | 4.897% | 5.034%
WGI | 30111322 | DS-WGI-TRNFMR-9000003147 |  | 59 | 5 | 5 | 1 | 3 | 2 | 1 | 4 | 5 | 5 | 348.5714 | 3 | 44 | 3.5 | 82 | 0.9218% | 0.9218% | 0.9742% | 1.028% | 1.084% | 1.142% | 1.201% | 1.262% | 1.325% | 1.39% | 1.457% | 1.525% | 1.596% | 1.668% | 1.742% | 1.818% | 1.896% | 1.976% | 2.058% | 2.142% | 2.227% | 2.315% | 2.405% | 2.496% | 2.59% | 2.686% | 2.783% | 2.883% | 2.985% | 3.089%
EPG | 30026486 | DS-EPG-TRNFMR-9000010175 |  | 45 | 5 | 3 | 2 | 1 | 2 | 1 | 4 | 5 | 5 | 322.8571 | 3 | 44 | 3.5 | 84.05 | 0.8458% | 0.8458% | 0.8939% | 0.9436% | 0.9949% | 1.048% | 1.102% | 1.159% | 1.216% | 1.276% | 1.337% | 1.4% | 1.465% | 1.531% | 1.599% | 1.669% | 1.741% | 1.814% | 1.889% | 1.966% | 2.045% | 2.125% | 2.208% | 2.292% | 2.378% | 2.466% | 2.556% | 2.648% | 2.741% | 2.837%
EPG | 30058367 | DS-EPG-TRNFMR-9000010174 |  | 45 | 5 | 3 | 2 | 1 | 2 | 1 | 4 | 5 | 5 | 322.8571 | 3 | 44 | 3.5 | 84.05 | 0.8458% | 0.8458% | 0.8939% | 0.9436% | 0.9949% | 1.048% | 1.102% | 1.159% | 1.216% | 1.276% | 1.337% | 1.4% | 1.465% | 1.531% | 1.599% | 1.669% | 1.741% | 1.814% | 1.889% | 1.966% | 2.045% | 2.125% | 2.208% | 2.292% | 2.378% | 2.466% | 2.556% | 2.648% | 2.741% | 2.837%
WGI | 30475971 | DS-WGI-TRNFMR-9000007146 |  | 49 | 5 | 5 | 1 | 1 | 1 | 1 | 2 | 5 | 1 | 268.5714 | 3 | 44 | 3.5 | 82 | 0.9218% | 0.9218% | 0.9742% | 1.028% | 1.084% | 1.142% | 1.201% | 1.262% | 1.325% | 1.39% | 1.457% | 1.525% | 1.596% | 1.668% | 1.742% | 1.818% | 1.896% | 1.976% | 2.058% | 2.142% | 2.227% | 2.315% | 2.405% | 2.496% | 2.59% | 2.686% | 2.783% | 2.883% | 2.985% | 3.089%
EPG | 30209984 | DS-EPG-TRNFMR-9000007095 |  | 24 | 3 | 3 | 1 | 3 | 2 | 1 | 4 | 3 | 3 | 251.4286 | 3 | 44 | 3.5 | 84.05 | 0.8458% | 0.8458% | 0.8939% | 0.9436% | 0.9949% | 1.048% | 1.102% | 1.159% | 1.216% | 1.276% | 1.337% | 1.4% | 1.465% | 1.531% | 1.599% | 1.669% | 1.741% | 1.814% | 1.889% | 1.966% | 2.045% | 2.125% | 2.208% | 2.292% | 2.378% | 2.466% | 2.556% | 2.648% | 2.741% | 2.837%
CLN | 30338702 | DS-CLN-TRNFMR-9000006730 |  | 21 | 3 | 2 | 2 | 3 | 1 | 1 | 3 | 3 | 2 | 225.7143 | 2 | 24 | 3.5 | 84.05 | 0.1909% | 0.1909% | 0.211% | 0.2322% | 0.2547% | 0.2785% | 0.3035% | 0.3298% | 0.3575% | 0.3865% | 0.4168% | 0.4486% | 0.4817% | 0.5162% | 0.5522% | 0.5897% | 0.6286% | 0.669% | 0.7109% | 0.7543% | 0.7993% | 0.8458% | 0.8939% | 0.9436% | 0.9949% | 1.048% | 1.102% | 1.159% | 1.216% | 1.276%
CRE | 30165029 | DS-CRE-TRNFMR-9000525811 |  | 13 | 3 | 2 | 1 | 3 | 2 | 1 | 4 | 2 | 2 | 217.1429 | 2 | 24 | 3.5 | 84.05 | 0.1909% | 0.1909% | 0.211% | 0.2322% | 0.2547% | 0.2785% | 0.3035% | 0.3298% | 0.3575% | 0.3865% | 0.4168% | 0.4486% | 0.4817% | 0.5162% | 0.5522% | 0.5897% | 0.6286% | 0.669% | 0.7109% | 0.7543% | 0.7993% | 0.8458% | 0.8939% | 0.9436% | 0.9949% | 1.048% | 1.102% | 1.159% | 1.216% | 1.276%
LLG | 30359074 | DS-LLG-TRNFMR-9000007796 |  | 20 | 1 | 2 | 1 | 2 | 1 | 1 | 5 | 3 | 2 | 191.4286 | 2 | 24 | 3.5 | 84.05 | 0.1909% | 0.1909% | 0.211% | 0.2322% | 0.2547% | 0.2785% | 0.3035% | 0.3298% | 0.3575% | 0.3865% | 0.4168% | 0.4486% | 0.4817% | 0.5162% | 0.5522% | 0.5897% | 0.6286% | 0.669% | 0.7109% | 0.7543% | 0.7993% | 0.8458% | 0.8939% | 0.9436% | 0.9949% | 1.048% | 1.102% | 1.159% | 1.216% | 1.276%
CRE | 30380287 | DS-CRE-TRNFMR-9000525810 |  | 13 | 2 | 2 | 1 | 1 | 2 | 1 | 3 | 2 | 2 | 177.1429 | 2 | 24 | 3.5 | 84.05 | 0.1909% | 0.1909% | 0.211% | 0.2322% | 0.2547% | 0.2785% | 0.3035% | 0.3298% | 0.3575% | 0.3865% | 0.4168% | 0.4486% | 0.4817% | 0.5162% | 0.5522% | 0.5897% | 0.6286% | 0.669% | 0.7109% | 0.7543% | 0.7993% | 0.8458% | 0.8939% | 0.9436% | 0.9949% | 1.048% | 1.102% | 1.159% | 1.216% | 1.276%
CLN | 30000439 | DS-CLN-TRNFMR-9000001306 |  | 19 | 2 | 2 | 1 | 1 | 1 | 1 | 3 | 2 | 2 | 165.7143 | 2 | 24 | 3.5 | 84.05 | 0.1909% | 0.1909% | 0.211% | 0.2322% | 0.2547% | 0.2785% | 0.3035% | 0.3298% | 0.3575% | 0.3865% | 0.4168% | 0.4486% | 0.4817% | 0.5162% | 0.5522% | 0.5897% | 0.6286% | 0.669% | 0.7109% | 0.7543% | 0.7993% | 0.8458% | 0.8939% | 0.9436% | 0.9949% | 1.048% | 1.102% | 1.159% | 1.216% | 1.276%
OFR | 30035965 | DS-OFR-TRNFMR-9000014181 |  | 16 | 2 | 2 | 1 | 1 | 1 | 1 | 3 | 2 | 2 | 165.7143 | 2 | 24 | 3.5 | 84.05 | 0.1909% | 0.1909% | 0.211% | 0.2322% | 0.2547% | 0.2785% | 0.3035% | 0.3298% | 0.3575% | 0.3865% | 0.4168% | 0.4486% | 0.4817% | 0.5162% | 0.5522% | 0.5897% | 0.6286% | 0.669% | 0.7109% | 0.7543% | 0.7993% | 0.8458% | 0.8939% | 0.9436% | 0.9949% | 1.048% | 1.102% | 1.159% | 1.216% | 1.276%
KLO | 30002764 | DS-KLO-TRNFMR-9000412348 |  | 15 | 1 | 2 | 1 | 1 | 1 | 1 | 4 | 2 | 2 | 160 | 2 | 24 | 3.5 | 84.05 | 0.1909% | 0.1909% | 0.211% | 0.2322% | 0.2547% | 0.2785% | 0.3035% | 0.3298% | 0.3575% | 0.3865% | 0.4168% | 0.4486% | 0.4817% | 0.5162% | 0.5522% | 0.5897% | 0.6286% | 0.669% | 0.7109% | 0.7543% | 0.7993% | 0.8458% | 0.8939% | 0.9436% | 0.9949% | 1.048% | 1.102% | 1.159% | 1.216% | 1.276%
OFR | 30221642 | DS-OFR-TRNFMR-9000016122 |  | 16 | 1 | 2 | 1 | 1 | 1 | 1 | 3 | 2 | 2 | 151.4286 | 2 | 24 | 3.5 | 84.05 | 0.1909% | 0.1909% | 0.211% | 0.2322% | 0.2547% | 0.2785% | 0.3035% | 0.3298% | 0.3575% | 0.3865% | 0.4168% | 0.4486% | 0.4817% | 0.5162% | 0.5522% | 0.5897% | 0.6286% | 0.669% | 0.7109% | 0.7543% | 0.7993% | 0.8458% | 0.8939% | 0.9436% | 0.9949% | 1.048% | 1.102% | 1.159% | 1.216% | 1.276%
KLO | 30208816 | DS-KLO-TRNFMR-9000412347 |  | 15 | 1 | 2 | 1 | 1 | 1 | 1 | 3 | 2 | 2 | 151.4286 | 2 | 24 | 3.5 | 84.05 | 0.1909% | 0.1909% | 0.211% | 0.2322% | 0.2547% | 0.2785% | 0.3035% | 0.3298% | 0.3575% | 0.3865% | 0.4168% | 0.4486% | 0.4817% | 0.5162% | 0.5522% | 0.5897% | 0.6286% | 0.669% | 0.7109% | 0.7543% | 0.7993% | 0.8458% | 0.8939% | 0.9436% | 0.9949% | 1.048% | 1.102% | 1.159% | 1.216% | 1.276%
PHM | 32944656 | DS-PHM-TRNFMR-9000004393 |  | 8 | 2 | 2 | 1 | 1 | 1 | 1 | 3 | 1 | 1 | 142.8571 | 1 | 8 | 3.5 | 84.05 | 0.01357% | 0.01357% | 0.01791% | 0.023% | 0.02887% | 0.03555% | 0.04308% | 0.0515% | 0.06084% | 0.07112% | 0.08238% | 0.09465% | 0.1079% | 0.1223% | 0.1378% | 0.1543% | 0.172% | 0.1909% | 0.211% | 0.2322% | 0.2547% | 0.2785% | 0.3035% | 0.3298% | 0.3575% | 0.3865% | 0.4168% | 0.4486% | 0.4817% | 0.5162%
PHM | 32944654 | DS-PHM-TRNFMR-9000007050 |  | 8 | 2 | 2 | 1 | 1 | 1 | 1 | 3 | 1 | 1 | 142.8571 | 1 | 8 | 3.5 | 84.05 | 0.01357% | 0.01357% | 0.01791% | 0.023% | 0.02887% | 0.03555% | 0.04308% | 0.0515% | 0.06084% | 0.07112% | 0.08238% | 0.09465% | 0.1079% | 0.1223% | 0.1378% | 0.1543% | 0.172% | 0.1909% | 0.211% | 0.2322% | 0.2547% | 0.2785% | 0.3035% | 0.3298% | 0.3575% | 0.3865% | 0.4168% | 0.4486% | 0.4817% | 0.5162%

## AER VCR Rates(2024)
Category | Rate | Notes
Dec 24 AER VCR ($/kWh) - Res | 49.23 | Vic Av Res
Dec 24 AER VCR ($/kWh) - Com | 34.39 | Vic Av Com
Dec 24 AER VCR ($/kWh) - Ind | 33.49 | Vic Av Ind
Dec 24 AER VCR ($/kWh) - Agr | 22.25 | Vic Av Agr

## Customer No. and Vol per Feeder
CUSTOMER_CLASS | Feeder | VOL | CUST_NO | ZSS | Customer mix received from AusNet Financial Planning & Strategy on 25/7/2025
COMMERCIAL | bra11 | 9860526.7854 | 168 | bra
COMMERCIAL | bge13 | 654988.62 | 45 | bge
COMMERCIAL | phi11 | 1878610.03 | 37 | phi
NCONUML | moe11 | 47447.48 | 18 | moe
NCONUML | drn13 | 27414.73 | 17 | drn
COMMERCIAL | smg34 | 5224461.8 | 1 | smg
FARM | wgl13 | 901266.5312 | 97 | wgl
FARM | msd2 | 2808295.5668 | 471 | msd
NCONUML | elm34 | 86758.8 | 34 | elm
| rwt36 | 703.54 | 2 | rwt
COMMERCIAL | lga41 | 1099100.22 | 2 | lga
| bdl33 | 4298.82 | 8 | bdl
NCONUML | smr14 | 27225.34 | 18 | smr
COMMERCIAL | cln24 | 4484028.8333 | 290 | cln
RESIDENTL | ofr14 | 13024383.6958 | 3554 | ofr
NCONUML | bdl43 | 100361.9983 | 38 | bdl
| ofr22 | 16469.09 | 22 | ofr
NCONUML | rwn33 | 8721.79 | 7 | rwn
LIGHTING | hpk12 | 342838 | 1 | hpk
COMMERCIAL | bra23 | 6262297.01 | 84 | bra
FARM | tt1 | 1865.76 | 1 | tt
LIGHTING | mfa14 | 787800.53 | 1 | mfa
RESIDENTL | brt22 | 9968534.1043 | 1376 | brt
RESIDENTL | mwl25 | 4092575.372 | 493 | mwl
NCONUML | wgi22 | 83961.44 | 23 | wgi
INDUSTRIAL | ldl22 | 4379901.5885 | 45 | ldl
RESIDENTL | phm22 | 3628742.5283 | 796 | phm
FARM | mfa23 | 2691321.6324 | 201 | mfa
NCONUML | rwn32 | 60415.37 | 23 | rwn
FARM | cre22 | 55644.16 | 17 | cre
RESIDENTL | elm24 | 17367685.5307 | 2999 | elm
COMMERCIAL | tt9 | 7181168.3052 | 213 | tt
COMMERCIAL | kms12 | 15257134.8455 | 395 | kms
NCONUML | cyn31 | 24759.23 | 14 | cyn
| llg12 | 26420.7189 | 15 | llg
LIGHTING | ruba22 | 247422.69 | 1 | ruba
RESIDENTL | wt12 | 10803758.701 | 2579 | wt
COMMERCIAL | bwn14 | 6975240.1 | 156 | bwn
NCONUML | bge12 | 37366.03 | 11 | bge
NCONUML | rwn24 | 30489.76 | 21 | rwn
FARM | sfs1 | 113380.09 | 9 | sfs
| bwr13 | 80076.52 | 46 | bwr
FARM | wt13 | 37228.86 | 3 | wt
FARM | cre23 | 226478.55 | 9 | cre
COMMERCIAL | rwn22 | 1886562.0146 | 72 | rwn
| tgn23 | 13898.1302 | 15 | tgn
FARM | ldl22 | 7887.95 | 1 | ldl
RESIDENTL | fgy21 | 7153989.4877 | 1047 | fgy
FARM | mjg11 | 735019.886 | 74 | mjg
| ldl14 | 17432.2687 | 11 | ldl
INDUSTRIAL | ldl24 | 64751.4 | 12 | ldl
| sle13 | 253.3245 | 2 | sle
FARM | moe21 | 6301170.9744 | 504 | moe
FARM | bge23 | 671977.1074 | 66 | bge
RESIDENTL | elm32 | 19949095.4752 | 2463 | elm
COMMERCIAL | ftr12 | 1975462.7263 | 113 | ftr
RESIDENTL | lyd12 | 6657897.88 | 1592 | lyd
RESIDENTL | epg31 | 11862355.3417 | 3027 | epg
NCONUML | ofr11 | 57102.89 | 18 | ofr
FARM | moe11 | 65350.2807 | 7 | moe
FARM | nla32 | 1181128.1259 | 84 | nla
FARM | smr24 | 4141783.4574 | 392 | smr
RESIDENTL | fgy13 | 7970231.1446 | 1518 | fgy
FARM | bdl41 | 1305847.5951 | 258 | bdl
NCONUML | elm23 | 62172.37 | 40 | elm
| elm22 | 20617.5429 | 26 | elm
NCONUML | cre21 | 58240.1 | 18 | cre
FARM | phm32 | 50851.13 | 8 | phm
INDUSTRIAL | lga21 | 208132.02 | 16 | lga
INDUSTRIAL | nrn13 | 39703.59 | 6 | nrn
RESIDENTL | hpk22 | 18949862.0449 | 4569 | hpk
NCONUML | cyn13 | 17637.49 | 6 | cyn
COMMERCIAL | cre31 | 14851829.6913 | 363 | cre
COMMERCIAL | epg32 | 5001490.9226 | 156 | epg
| phm32 | 41386.12 | 47 | phm
NCONUML | wo33 | 6875.31 | 2 | wo
FARM | wgl21 | 5056187.7677 | 366 | wgl
INDUSTRIAL | cre22 | 240829.25 | 4 | cre
RESIDENTL | wgi34 | 3671110.7601 | 570 | wgi
INDUSTRIAL | ldl12 | 10352583.7 | 7 | ldl
INDUSTRIAL | wyk12 | 149433.7 | 6 | wyk
INDUSTRIAL | cyn14 | 23200.151 | 3 | cyn
| wo11 | 4136.2425 | 3 | wo
| msd4 | 20521.76 | 37 | msd
FARM | mby12 | 52034.88 | 19 | mby
COMMERCIAL | rwt22 | 7145877.6761 | 143 | rwt
COMMERCIAL | wo12 | 23719023.8 | 1 | wo
RESIDENTL | wn2 | 17414453.5902 | 3500 | wn
COMMERCIAL | wots25 | 3483725.2811 | 72 | wots
RESIDENTL | bwr33 | 46024.67 | 2 | bwr
RESIDENTL | wn3 | 12349888.6736 | 2099 | wn
RESIDENTL | bn24 | 2992797.8263 | 559 | bn
| bra21 | 41455.7142 | 65 | bra
INDUSTRIAL | hpk14 | 16381.88 | 4 | hpk
RESIDENTL | epg32 | 14811809.1158 | 3829 | epg
COMMERCIAL | cln14 | 10141314.5039 | 129 | cln
FARM | smg31 | 14995.46 | 5 | smg
INDUSTRIAL | drn22 | 2117102.6666 | 12 | drn
NCONUML | drn12 | 43785.8374 | 16 | drn
INDUSTRIAL | fgy34 | 128392.6893 | 5 | fgy
NCONUML | fgy31 | 6707.46 | 4 | fgy
| wt8 | 7059.0655 | 13 | wt
| bwn12 | 6521.57 | 6 | bwn
COMMERCIAL | myt12 | 10774273.2986 | 307 | myt
COMMERCIAL | ldl21 | 5339830.9491 | 117 | ldl
| cln21 | 32425.72 | 66 | cln
INDUSTRIAL | fgy14 | 162921.94 | 7 | fgy
| tgn12 | 22490.11 | 3 | tgn
COMMERCIAL | epg12 | 8214339.5389 | 163 | epg
NCONUML | moe23 | 69334.91 | 17 | moe
FARM | cyn14 | 7715.15 | 1 | cyn
RESIDENTL | lyd14 | 10580841.4317 | 1203 | lyd
COMMERCIAL | smg23 | 21963007.1063 | 434 | smg
INDUSTRIAL | bra33 | 2076536.62 | 34 | bra
INDUSTRIAL | rwt14 | 2271244.55 | 44 | rwt
COMMERCIAL | lga14 | 2174194.9787 | 115 | lga
INDUSTRIAL | myt22 | 3176.32 | 3 | myt
FARM | cyn21 | 10230.57 | 2 | cyn
| klo24 | 65411.35 | 119 | klo
COMMERCIAL | brt21 | 6571769.7252 | 216 | brt
FARM | kms11 | 665243.0597 | 75 | kms
| elm34 | 25999.6869 | 33 | elm
INDUSTRIAL | mwl11 | 366139.79 | 15 | mwl
INDUSTRIAL | lyd14 | 80895.88 | 12 | lyd
LIGHTING | cpk11 | 1086.88 | 1 | cpk
NCONUML | fgy23 | 34402.31 | 12 | fgy
| bra32 | 15753.982 | 22 | bra
RESIDENTL | epg12 | 26391788.5687 | 6905 | epg
COMMERCIAL | cyn24 | 15647575.1097 | 304 | cyn
INDUSTRIAL | phm21 | 511727.73 | 19 | phm
NCONUML | ftr12 | 5424.58 | 5 | ftr
| bwa23 | 5447.575 | 8 | bwa
NCONUML | llg12 | 4182.92 | 3 | llg
COMMERCIAL | drn13 | 5299129.684 | 96 | drn
INDUSTRIAL | hpk21 | 31624.71 | 8 | hpk
INDUSTRIAL | wyk23 | 1500537.4334 | 28 | wyk
RESIDENTL | lga12 | 4152631.2896 | 644 | lga
RESIDENTL | cyn11 | 6009338.551 | 1440 | cyn
NCONUML | fgy24 | 70027.41 | 43 | fgy
| moe23 | 74726.3012 | 22 | moe
COMMERCIAL | elm24 | 3531802.26 | 46 | elm
LIGHTING | elm33 | 1000.47 | 1 | elm
RESIDENTL | smg23 | 6500499.5996 | 1411 | smg
FARM | msd4 | 1851245.0012 | 252 | msd
COMMERCIAL | lga24 | 21693950.3379 | 92 | lga
COMMERCIAL | ldl11 | 7360578.73 | 74 | ldl
NCONUML | rve13 | 29515.6981 | 24 | rve
COMMERCIAL | trc01 | 365242.5067 | 42 | trc
COMMERCIAL | wt15 | 1164715.6471 | 30 | wt
COMMERCIAL | bra14 | 811059.401 | 59 | bra
| ftr21 | 17034.7542 | 20 | ftr
RESIDENTL | bra23 | 7643359.408 | 1736 | bra
INDUSTRIAL | cpk11 | 59065.36 | 14 | cpk
INDUSTRIAL | hpk12 | 531460.54 | 46 | hpk
FARM | fgy23 | 137430.23 | 3 | fgy
INDUSTRIAL | tt4 | 77015.1997 | 16 | tt
FARM | cpk22 | 45399.86 | 6 | cpk
INDUSTRIAL | yn31 | 1004932.7745 | 6 | yn
FARM | myt22 | 1873055.6433 | 191 | myt
| cpk12 | 20188.43 | 32 | cpk
RESIDENTL | bwa22 | 6606654.3694 | 1106 | bwa
| mfa34 | 1434.55 | 6 | mfa
| nla31 | 4780.58 | 5 | nla
FARM | mdg1 | 36782.2 | 6 | mdg
RESIDENTL | mwl21 | 3605605.4081 | 859 | mwl
COMMERCIAL | phm33 | 14452041.4603 | 180 | phm
INDUSTRIAL | ofr23 | 154535.41 | 17 | ofr
INDUSTRIAL | elm21 | 177435.466 | 7 | elm
INDUSTRIAL | wt5 | 89.11 | 1 | wt
FARM | llg13 | 1917532.2118 | 152 | llg
INDUSTRIAL | klk21 | 41156.68 | 10 | klk
NCONUML | wt9 | 48247.64 | 17 | wt
FARM | mdi1 | 153288.2952 | 21 | mdi
INDUSTRIAL | nrn14 | 19245.31 | 5 | nrn
INDUSTRIAL | wgl12 | 500659.11 | 16 | wgl
FARM | fgy13 | 80534.51 | 6 | fgy
INDUSTRIAL | bwr14 | 1597974.48 | 1 | bwr
LIGHTING | bn11 | 103048.5 | 1 | bn
RESIDENTL | klo14 | 40411755.0117 | 10946 | klo
RESIDENTL | fgy33 | 9101921.8028 | 1763 | fgy
LIGHTING | cre31 | 2308168.51 | 1 | cre
RESIDENTL | wn5 | 8555201.9981 | 1156 | wn
COMMERCIAL | mfa22 | 5299491.9938 | 179 | mfa
COMMERCIAL | lyd11 | 3798691.89 | 62 | lyd
LIGHTING | bn24 | 2014.81 | 1 | bn
COMMERCIAL | cf1 | 9360587.4941 | 189 | cf
FARM | lga11 | 4665290.6529 | 555 | lga
RESIDENTL | lyd13 | 10895753.2364 | 2051 | lyd
NCONUML | cre33 | 35388.67 | 19 | cre
| smg32 | 685.05 | 3 | smg
INDUSTRIAL | cyn11 | 1966971.1028 | 55 | cyn
COMMERCIAL | wn2 | 10157994.9798 | 156 | wn
| phm21 | 32464.7212 | 22 | phm
| sfs1 | 13890.635 | 10 | sfs
NCONUML | tt12 | 15011.94 | 8 | tt
FARM | lga21 | 1065599.6961 | 147 | lga
| ldl12 | 52350.63 | 6 | ldl
INDUSTRIAL | smg31 | 231921 | 9 | smg
LIGHTING | myt12 | 813470.88 | 6 | myt
| smr24 | 66801.9 | 34 | smr
NCONUML | cre32 | 49453.4427 | 23 | cre
INDUSTRIAL | bdl44 | 2337630.2078 | 41 | bdl
| rve11 | 302066.1 | 12 | rve
FARM | wo31 | 3245.01 | 1 | wo
LIGHTING | ofr13 | 171706.2 | 2 | ofr
RESIDENTL | tt9 | 13181645.445 | 3553 | tt
COMMERCIAL | wgl11 | 13522117.9742 | 216 | wgl
COMMERCIAL | hpk24 | 15242696.9791 | 271 | hpk
COMMERCIAL | bwr34 | 12222544.1423 | 437 | bwr
NCONUML | nla34 | 19980.17 | 11 | nla
FARM | bwr24 | 9303.26 | 1 | bwr
| wgi23 | 15962.8799 | 36 | wgi
RESIDENTL | cln13 | 18593732.5659 | 6830 | cln
RESIDENTL | lga13 | 1879247.7046 | 295 | lga
RESIDENTL | cnr3 | 108696.4186 | 22 | cnr
| wgl12 | 112644.3661 | 43 | wgl
COMMERCIAL | cln12 | 8203266.5202 | 86 | cln
NCONUML | ofr21 | 100427.35 | 34 | ofr
RESIDENTL | drn24 | 10021102.8231 | 2473 | drn
COMMERCIAL | cyn31 | 1940881.6507 | 53 | cyn
NCONUML | ldl24 | 34534.3 | 19 | ldl
COMMERCIAL | ofr13 | 9302944.2987 | 197 | ofr
| wots13 | 58538.6484 | 32 | wots
| cpk23 | 23360.0808 | 24 | cpk
NCONUML | cln11 | 4587.8606 | 9 | cln
| wt15 | 51811.4 | 11 | wt
COMMERCIAL | epg24 | 26841528 | 1 | epg
FARM | drn22 | 329138.5031 | 52 | drn
| mfa31 | 16838.31 | 22 | mfa
COMMERCIAL | bra32 | 4055727.3404 | 158 | bra
COMMERCIAL | cpk21 | 14974774.5549 | 258 | cpk
INDUSTRIAL | myt21 | 335981.9667 | 19 | myt
FARM | nrn14 | 139044.47 | 14 | nrn
| wt5 | 22324.85 | 13 | wt
INDUSTRIAL | mfa23 | 139940.33 | 14 | mfa
FARM | wyk12 | 2634438.6357 | 233 | wyk
RESIDENTL | epg23 | 3653084.6682 | 932 | epg
COMMERCIAL | tgn11 | 2525258.71 | 85 | tgn
| wt13 | 22551.0062 | 37 | wt
| cyn13 | 10533.28 | 7 | cyn
INDUSTRIAL | fgy13 | 259435.94 | 2 | fgy
RESIDENTL | cln12 | 23908773.0216 | 6775 | cln
COMMERCIAL | brt22 | 9042592.2197 | 210 | brt
COMMERCIAL | rwt25 | 7526054.6961 | 146 | rwt
FARM | mfa31 | 218040.8355 | 21 | mfa
COMMERCIAL | cln22 | 3248277.4443 | 37 | cln
NCONUML | bdl33 | 22970.8 | 8 | bdl
COMMERCIAL | fgy12 | 74427.591 | 4 | fgy
RESIDENTL | mwl16 | 8188909.2298 | 1700 | mwl
INDUSTRIAL | moe25 | 612177.9824 | 16 | moe
COMMERCIAL | tt7 | 24970154.3491 | 341 | tt
INDUSTRIAL | bwr24 | 4118148.7987 | 125 | bwr
RESIDENTL | moe13 | 2791200.4315 | 357 | moe
FARM | wyk24 | 694188.3378 | 94 | wyk
NCONUML | wo14 | 36996.26 | 12 | wo
RESIDENTL | bra13 | 6470560.8911 | 1572 | bra
RESIDENTL | tt7 | 39398.92 | 9 | tt
FARM | epg34 | 15821.91 | 5 | epg
INDUSTRIAL | yn35 | 6582.38 | 2 | yn
NCONUML | bwa23 | 749.23 | 1 | bwa
FARM | sle13 | 1461316.56 | 213 | sle
COMMERCIAL | cpk13 | 4127340.5971 | 198 | cpk
INDUSTRIAL | ldl14 | 1064067.7426 | 16 | ldl
| rwt14 | 62105.3312 | 18 | rwt
LIGHTING | hpk13 | 14513.85 | 1 | hpk
RESIDENTL | klk22 | 940238.19 | 128 | klk
COMMERCIAL | mwl25 | 259300.06 | 16 | mwl
| mjg11 | 96977.3135 | 7 | mjg
RESIDENTL | hpk24 | 4867180.3451 | 1284 | hpk
FARM | ftr21 | 6703423.0704 | 705 | ftr
FARM | smr12 | 441800.25 | 44 | smr
FARM | bwr13 | 73574.54 | 13 | bwr
| ldl22 | 9241.11 | 9 | ldl
FARM | wo22 | 35676.335 | 7 | wo
NCONUML | moe12 | 9318.9 | 3 | moe
INDUSTRIAL | bdl31 | 1561951.6978 | 44 | bdl
COMMERCIAL | ofr14 | 8393968.2568 | 77 | ofr
NCONUML | tgn23 | 48562.71 | 16 | tgn
NCONUML | cyn21 | 25127.29 | 5 | cyn
FARM | phm34 | 22945.58 | 3 | phm
INDUSTRIAL | cyn33 | 36519.92 | 4 | cyn
LIGHTING | bm8b32 | 1070.04 | 1 | bmb
FARM | llg12 | 5311057.9488 | 488 | llg
NCONUML | rwt32 | 94072.85 | 46 | rwt
COMMERCIAL | myt11 | 912988.53 | 42 | myt
INDUSTRIAL | cpk22 | 129954.91 | 11 | cpk
| cre22 | 20388.051 | 33 | cre
RESIDENTL | ldl21 | 5451727.7741 | 1502 | ldl
FARM | bdl44 | 8189534.7866 | 736 | bdl
INDUSTRIAL | bn11 | 1899511.3657 | 45 | bn
INDUSTRIAL | wgi31 | 152399.6 | 19 | wgi
INDUSTRIAL | mdi1 | 16.0426 | 1 | mdi
| ofr11 | 90492.4817 | 79 | ofr
LIGHTING | kms11 | 547479.19 | 1 | kms
RESIDENTL | phi12 | 18738852.0082 | 4967 | phi
COMMERCIAL | bwr12 | 7897915.6022 | 287 | bwr
FARM | msd1 | 2520603.4144 | 354 | msd
COMMERCIAL | tgn44 | 4662112.18 | 89 | tgn
NCONUML | uwy1 | 29815.85 | 15 | uwy
NCONUML | lga22 | 54192.29 | 17 | lga
NCONUML | lga23 | 17186.13 | 6 | lga
INDUSTRIAL | hpk13 | 1952010.47 | 3 | hpk
FARM | drn23 | 391232.6382 | 58 | drn
FARM | ldl23 | 5910515.5529 | 453 | ldl
FARM | bdl31 | 55336.85 | 12 | bdl
RESIDENTL | bwr34 | 11176240.016 | 2984 | bwr
RESIDENTL | ofr13 | 5689359.8131 | 1445 | ofr
NCONUML | bra21 | 145563.002 | 72 | bra
COMMERCIAL | cf2 | 1114027.3697 | 138 | cf
RESIDENTL | bdl32 | 16368580.902 | 3124 | bdl
COMMERCIAL | smr22 | 10240657.5236 | 95 | smr
NCONUML | rve12 | 34563.18 | 21 | rve
COMMERCIAL | cnr3 | 208527.63 | 11 | cnr
| elm25 | 9741.0155 | 15 | elm
INDUSTRIAL | lyd13 | 30651.21 | 5 | lyd
INDUSTRIAL | mby12 | 279353.09 | 7 | mby
INDUSTRIAL | epg21 | 31298.6803 | 2 | epg
FARM | wgl12 | 7817936.5802 | 624 | wgl
COMMERCIAL | moe13 | 1401894.0174 | 82 | moe
RESIDENTL | lga14 | 7239522.4699 | 1158 | lga
RESIDENTL | epg35 | 308209.78 | 22 | epg
FARM | hpk14 | 29274.39 | 5 | hpk
LIGHTING | bn22 | 341591.58 | 1 | bn
NCONUML | bge11 | 85890.46 | 45 | bge
NCONUML | wt7 | 26985.19 | 18 | wt
| wo31 | 27869.149 | 41 | wo
INDUSTRIAL | elm32 | 759094.4258 | 68 | elm
NCONUML | cre23 | 95638.5 | 25 | cre
RESIDENTL | cln23 | 19292170.1488 | 4992 | cln
| lga21 | 17263.28 | 18 | lga
NCONUML | bwn12 | 35975.24 | 12 | bwn
| fgy31 | 1671.76 | 6 | fgy
NCONUML | ftr23 | 39743.6852 | 30 | ftr
NCONUML | smg21 | 9405.11 | 5 | smg
RESIDENTL | epg13 | 24819451.0174 | 7299 | epg
RESIDENTL | ruba22 | 5955886.59 | 1080 | ruba
INDUSTRIAL | bwr23 | 1917390.4058 | 110 | bwr
COMMERCIAL | bn23 | 4585306.9 | 117 | bn
| fgy24 | 60212.15 | 95 | fgy
LIGHTING | brt21 | 27441.26 | 1 | brt
COMMERCIAL | mby14 | 13812.56 | 3 | mby
RESIDENTL | drn21 | 15235611.8074 | 3585 | drn
RESIDENTL | nrn11 | 3368324.1063 | 703 | nrn
NCONUML | cln21 | 97183.1897 | 28 | cln
NCONUML | tgn12 | 26909.78 | 9 | tgn
FARM | moe22 | 48531.59 | 7 | moe
RESIDENTL | bra14 | 17287022.2386 | 4193 | bra
RESIDENTL | brt21 | 8587133.8204 | 1368 | brt
INDUSTRIAL | ldl23 | 2181365.61 | 45 | ldl
NCONUML | klo24 | 121410.57 | 41 | klo
INDUSTRIAL | wt8 | 22231.36 | 5 | wt
| bdl41 | 27628.4721 | 32 | bdl
COMMERCIAL | sle14 | 13227565.7623 | 343 | sle
| smr14 | 17300.3116 | 19 | smr
INDUSTRIAL | llg11 | 439641.21 | 9 | llg
| wgi22 | 13903.1 | 35 | wgi
NCONUML | moe22 | 34069.45 | 10 | moe
| ftr12 | 15921.46 | 17 | ftr
COMMERCIAL | epg11 | 902129.45 | 16 | epg
RESIDENTL | cpk13 | 21255549.7429 | 4974 | cpk
| fgy23 | 9273.25 | 10 | fgy
FARM | cyn12 | 9105.46 | 2 | cyn
INDUSTRIAL | rwn31 | 527467.66 | 22 | rwn
RESIDENTL | bm8b32 | 357081.227 | 62 | bmb
FARM | ruba22 | 1060033.1321 | 158 | ruba
INDUSTRIAL | cnr1 | 88077.93 | 3 | cnr
FARM | cpk12 | 972803.9358 | 91 | cpk
COMMERCIAL | wo14 | 14658340.7796 | 304 | wo
COMMERCIAL | tt5 | 6134357.4395 | 224 | tt
INDUSTRIAL | wo11 | 18559582.74 | 7 | wo
| wgl23 | 17798.7289 | 12 | wgl
NCONUML | cyn12 | 64730.9 | 21 | cyn
COMMERCIAL | bwr33 | 3515549.759 | 83 | bwr
COMMERCIAL | cyn22 | 10287381.4837 | 183 | cyn
COMMERCIAL | rwt32 | 5482054.6843 | 198 | rwt
INDUSTRIAL | nrn12 | 7260.73 | 2 | nrn
RESIDENTL | cln22 | 8137131.1146 | 3340 | cln
| kms12 | 36774.1343 | 44 | kms
| cyn24 | 12784.0842 | 11 | cyn
| smg33 | 11524.64 | 21 | smg
COMMERCIAL | rve11 | 18192998.0721 | 274 | rve
FARM | wt5 | 8146.48 | 2 | wt
INDUSTRIAL | bge23 | 983662.8538 | 7 | bge
| msd2 | 9983.6 | 13 | msd
| bra12 | 98134.87 | 2 | bra
RESIDENTL | hpk23 | 13762355.5073 | 3377 | hpk
COMMERCIAL | smr13 | 15057236.7589 | 394 | smr
INDUSTRIAL | rwt21 | 372221.49 | 45 | rwt
FARM | rve12 | 22362.86 | 5 | rve
NCONUML | fgy32 | 32042.28 | 18 | fgy
INDUSTRIAL | smr12 | 37387308.69 | 3 | smr
NCONUML | mfa34 | 19451.19 | 8 | mfa
FARM | wots13 | 4844280.0942 | 510 | wots
COMMERCIAL | drn21 | 3220798.94 | 52 | drn
INDUSTRIAL | wo31 | 765.77 | 1 | wo
| fgy32 | 8528.5063 | 10 | fgy
INDUSTRIAL | bwr32 | 3058614 | 72 | bwr
| elm23 | 20831.6 | 30 | elm
INDUSTRIAL | mwl12 | 574569.29 | 12 | mwl
RESIDENTL | cpk21 | 7771248.352 | 1679 | cpk
COMMERCIAL | wots11 | 6621581.9604 | 243 | wots
INDUSTRIAL | ftr21 | 313604.8 | 24 | ftr
NCONUML | lyd11 | 43059.75 | 9 | lyd
FARM | phm21 | 25361.56 | 3 | phm
INDUSTRIAL | wyk13 | 453974.55 | 15 | wyk
INDUSTRIAL | mdg1 | 21781.42 | 1 | mdg
INDUSTRIAL | tt1 | 7434378.9861 | 77 | tt
INDUSTRIAL | wgi34 | 1206209.57 | 8 | wgi
LIGHTING | wgi33 | 1050486.0487 | 2 | wgi
COMMERCIAL | wgl15 | 27996457.3831 | 596 | wgl
RESIDENTL | bge23 | 16900476.9279 | 2094 | bge
INDUSTRIAL | bwr13 | 2417661.2776 | 147 | bwr
NCONUML | epg23 | 28250.73 | 7 | epg
INDUSTRIAL | drn14 | 25996.95 | 2 | drn
RESIDENTL | drn14 | 23831050.9741 | 4399 | drn
RESIDENTL | rwt31 | 5842296.4371 | 1436 | rwt
COMMERCIAL | drn24 | 1717660.9 | 35 | drn
FARM | epg14 | 3614.72 | 1 | epg
RESIDENTL | smr13 | 11225814.5464 | 2447 | smr
COMMERCIAL | wots12 | 14359758.4732 | 371 | wots
COMMERCIAL | klk11 | 3080934.4269 | 114 | klk
NCONUML | mwl14 | 31252.61 | 13 | mwl
INDUSTRIAL | sle11 | 266690.1 | 32 | sle
NCONUML | epg31 | 41319.36 | 24 | epg
RESIDENTL | cf1 | 4176161.3871 | 493 | cf
INDUSTRIAL | phm34 | 816155.12 | 6 | phm
FARM | rwn34 | 20402.21 | 4 | rwn
| mby12 | 1524.95 | 3 | mby
RESIDENTL | wgi31 | 14866992.8529 | 3617 | wgi
RESIDENTL | wots25 | 16858284.9544 | 3532 | wots
RESIDENTL | cre33 | 21876811.5892 | 4235 | cre
RESIDENTL | fgy34 | 4606270.9018 | 975 | fgy
RESIDENTL | cyn32 | 15011504.2579 | 3573 | cyn
RESIDENTL | klk11 | 9194980.7775 | 1227 | klk
INDUSTRIAL | fgy33 | 1452360.19 | 13 | fgy
INDUSTRIAL | wgl13 | 6688610.4344 | 14 | wgl
| tgn41 | 12751.16 | 13 | tgn
COMMERCIAL | klk22 | 85830.78 | 8 | klk
| mby11 | 4292.69 | 12 | mby
FARM | drn12 | 9939.61 | 1 | drn
RESIDENTL | rwn24 | 15617115.6722 | 2794 | rwn
RESIDENTL | cre32 | 8053371.5554 | 2218 | cre
COMMERCIAL | bwn11 | 5920812.2037 | 76 | bwn
NCONUML | smg33 | 19709.42 | 12 | smg
INDUSTRIAL | mby11 | 90387.22 | 16 | mby
COMMERCIAL | tgn41 | 8173213.7745 | 338 | tgn
INDUSTRIAL | wn7 | 3582803.57 | 9 | wn
FARM | bwr23 | 29264.76 | 8 | bwr
RESIDENTL | bwn13 | 8026926.4045 | 1629 | bwn
FARM | wgi24 | 1757204.2906 | 142 | wgi
| rve13 | 21148.03 | 29 | rve
RESIDENTL | wgl21 | 23764201.6622 | 4642 | wgl
COMMERCIAL | wn1 | 22168293.2818 | 620 | wn
INDUSTRIAL | cyn32 | 738566.1077 | 85 | cyn
| hpk21 | 27858.58 | 57 | hpk
COMMERCIAL | klo11 | 2030116.61 | 11 | klo
INDUSTRIAL | bn22 | 260832.7234 | 23 | bn
| ofr24 | 25053.77 | 43 | ofr
| drn12 | 30292.1138 | 29 | drn
COMMERCIAL | smg22 | 18806077.0677 | 136 | smg
COMMERCIAL | bwa22 | 4509592.2057 | 144 | bwa
COMMERCIAL | drn12 | 15118769.4919 | 112 | drn
| ldl23 | 80304.9161 | 48 | ldl
| rwn32 | 14306.27 | 22 | rwn
| drn23 | 12868.4314 | 15 | drn
RESIDENTL | mwl22 | 12904194.2639 | 2809 | mwl
COMMERCIAL | tt6 | 3682930.1298 | 115 | tt
COMMERCIAL | bra24 | 3429037.1414 | 127 | bra
NCONUML | hpk11 | 112614.82 | 31 | hpk
RESIDENTL | mfa21 | 12551518.2306 | 1921 | mfa
RESIDENTL | bge22 | 19945240.9452 | 3164 | bge
| tt4 | 9710.0483 | 41 | tt
NCONUML | phm22 | 22255.8232 | 9 | phm
COMMERCIAL | fgy21 | 1241019.6707 | 34 | fgy
INDUSTRIAL | nla31 | 516137.35 | 16 | nla
FARM | wyk13 | 707273.0378 | 84 | wyk
NCONUML | elm25 | 44655.33 | 20 | elm
| ofr23 | 28214.1089 | 26 | ofr
INDUSTRIAL | ruba22 | 167892.49 | 8 | ruba
FARM | hpk21 | 3124.97 | 1 | hpk
FARM | wn4 | 999664.927 | 129 | wn
COMMERCIAL | wn6 | 8795190.5545 | 246 | wn
| cre23 | 50195.43 | 25 | cre
COMMERCIAL | bwr22 | 15914202.1636 | 269 | bwr
INDUSTRIAL | elm22 | 545216.4127 | 27 | elm
NCONUML | bwr32 | 46210.27 | 31 | bwr
COMMERCIAL | moe12 | 4799517.76 | 51 | moe
| drn22 | 43438.5 | 28 | drn
FARM | bn22 | 13032.09 | 3 | bn
FARM | ldl24 | 222231.4641 | 11 | ldl
| bdl31 | 24144.6762 | 16 | bdl
FARM | cpk11 | 227979.0877 | 18 | cpk
FARM | elm33 | 50441.5205 | 4 | elm
INDUSTRIAL | rve13 | 147824.4003 | 10 | rve
COMMERCIAL | uwy1 | 603856.89 | 33 | uwy
FARM | mfa21 | 13347321.3386 | 701 | mfa
RESIDENTL | wo14 | 1446838.665 | 266 | wo
NCONUML | rwt14 | 102266.96 | 37 | rwt
| kms11 | 9612.23 | 20 | kms
RESIDENTL | phi11 | 5828644.3864 | 1391 | phi
COMMERCIAL | tgn12 | 10174331.2835 | 242 | tgn
LIGHTING | drn21 | 522455.53 | 1 | drn
INDUSTRIAL | smr22 | 2060432.23 | 13 | smr
| moe21 | 19173.8011 | 29 | moe
NCONUML | fgy12 | 1668.8419 | 4 | fgy
COMMERCIAL | elm25 | 2590499.6378 | 73 | elm
| epg34 | 11737.1961 | 27 | epg
COMMERCIAL | cpk23 | 2022573.8223 | 44 | cpk
COMMERCIAL | sle31 | 4198591.4215 | 178 | sle
FARM | nrn13 | 23844.37 | 5 | nrn
FARM | elm26 | 83060.0495 | 12 | elm
INDUSTRIAL | rve12 | 67014.5 | 12 | rve
INDUSTRIAL | moe21 | 304282.5341 | 37 | moe
COMMERCIAL | ofr21 | 9424773.56 | 126 | ofr
FARM | wn3 | 4385381.9629 | 585 | wn
FARM | klk21 | 574949.1868 | 82 | klk
NCONUML | wyk13 | 97422.66 | 49 | wyk
FARM | bwn12 | 14573.05 | 3 | bwn
NCONUML | msd2 | 8161.26 | 6 | msd
COMMERCIAL | elm31 | 474386.1613 | 1 | elm
RESIDENTL | rwt35 | 12065.95 | 2 | rwt
RESIDENTL | wt6 | 15702930.1084 | 3397 | wt
RESIDENTL | cln24 | 3991370.9732 | 1090 | cln
COMMERCIAL | smg21 | 2744632.8687 | 43 | smg
| myt21 | 64545.94 | 22 | myt
RESIDENTL | lga22 | 9862202.3617 | 1608 | lga
INDUSTRIAL | cyn13 | 4447831.06 | 67 | cyn
COMMERCIAL | ruba12 | 6703349.3664 | 290 | ruba
| smr23 | 7378.7014 | 9 | smr
FARM | phi13 | 230339.12 | 15 | phi
RESIDENTL | wt11 | 8665012.8839 | 2213 | wt
RESIDENTL | bge13 | 9255563.8982 | 1458 | bge
COMMERCIAL | bge11 | 11367890.3817 | 330 | bge
COMMERCIAL | wgi23 | 2290528.82 | 95 | wgi
COMMERCIAL | epg35 | 29855241.8371 | 304 | epg
NCONUML | mwl23 | 55631.52 | 20 | mwl
RESIDENTL | tgn11 | 18615536.7391 | 4196 | tgn
RESIDENTL | klo24 | 35150523.3753 | 8219 | klo
| wgi32 | 32777.55 | 36 | wgi
| uwy1 | 1895.86 | 6 | uwy
COMMERCIAL | wots24 | 5008654.6646 | 265 | wots
INDUSTRIAL | phi13 | 601326.64 | 38 | phi
LIGHTING | cf1 | 76883.018 | 3 | cf
RESIDENTL | cre21 | 18876617.5647 | 4715 | cre
INDUSTRIAL | wo32 | 73086.25 | 1 | wo
COMMERCIAL | lga13 | 621321.4861 | 47 | lga
FARM | cnr2 | 245915.51 | 48 | cnr
COMMERCIAL | bge22 | 4521687.9575 | 100 | bge
INDUSTRIAL | cyn12 | 101425.5 | 5 | cyn
FARM | drn11 | 51881.33 | 8 | drn
INDUSTRIAL | wo23 | 212041.78 | 1 | wo
RESIDENTL | lga23 | 5064870.5947 | 821 | lga
RESIDENTL | bn12 | 3438265.7182 | 625 | bn
RESIDENTL | bra21 | 23268334.8963 | 5707 | bra
| bdl42 | 11198.42 | 14 | bdl
FARM | cnr1 | 2440.03 | 2 | cnr
| phm34 | 68320.3174 | 32 | phm
FARM | rwt31 | 12148.87 | 1 | rwt
| smg31 | 8879.89 | 17 | smg
LIGHTING | tgn11 | 1064655.8 | 1 | tgn
FARM | llg14 | 4195351.6172 | 347 | llg
FARM | mwl11 | 2401732.236 | 295 | mwl
INDUSTRIAL | brt22 | 103539.39 | 15 | brt
COMMERCIAL | mwl14 | 15268408.4249 | 139 | mwl
RESIDENTL | wn1 | 4757807.4084 | 1039 | wn
COMMERCIAL | wo33 | 4706642.85 | 27 | wo
| nrn14 | 10562.91 | 10 | nrn
RESIDENTL | wgl15 | 10836827.2608 | 2158 | wgl
RESIDENTL | mfa22 | 4069843.249 | 701 | mfa
NCONUML | wyk24 | 96009.71 | 32 | wyk
NCONUML | rwn34 | 17137.95 | 21 | rwn
NCONUML | rve11 | 32578.28 | 16 | rve
INDUSTRIAL | klk11 | 54511.69 | 7 | klk
RESIDENTL | tt2 | 73044.37 | 7 | tt
COMMERCIAL | rwn32 | 3002784.6794 | 97 | rwn
NCONUML | tt1 | 9612.49 | 4 | tt
NCONUML | bwr23 | 79898.93 | 30 | bwr
NCONUML | epg14 | 19866.64 | 14 | epg
| elm26 | 27328.755 | 32 | elm
INDUSTRIAL | bdl32 | 418697.92 | 34 | bdl
FARM | wt11 | 3746.97 | 1 | wt
NCONUML | ofr23 | 50364.93 | 30 | ofr
INDUSTRIAL | smg23 | 412547.84 | 9 | smg
LIGHTING | klo14 | 3058096.87 | 1 | klo
| nrn13 | 13473.67 | 22 | nrn
FARM | bra12 | 12444.91 | 1 | bra
COMMERCIAL | cre21 | 15222170.3645 | 489 | cre
INDUSTRIAL | wgi32 | 984365.53 | 33 | wgi
NCONUML | rwt25 | 118451.05 | 54 | rwt
INDUSTRIAL | mwe236 | 280541.09 | 16 | mwe
RESIDENTL | epg33 | 183201.2006 | 6 | epg
INDUSTRIAL | elm33 | 243571.284 | 12 | elm
RESIDENTL | ldl11 | 13512975.3636 | 2241 | ldl
| mwl12 | 15850.97 | 9 | mwl
INDUSTRIAL | fgy21 | 6595081.67 | 18 | fgy
LIGHTING | smr24 | 109914.08 | 1 | smr
RESIDENTL | rwt25 | 10768082.8154 | 2324 | rwt
INDUSTRIAL | rwt15 | 3409961.2906 | 83 | rwt
INDUSTRIAL | phi12 | 3418741.3516 | 25 | phi
INDUSTRIAL | bwa22 | 1592049.74 | 9 | bwa
NCONUML | wo22 | 90587.46 | 26 | wo
INDUSTRIAL | ldl21 | 599666.7 | 44 | ldl
INDUSTRIAL | wt6 | 1814.16 | 1 | wt
NCONUML | ofr22 | 9198.59 | 2 | ofr
INDUSTRIAL | bra13 | 1860337.5903 | 47 | bra
COMMERCIAL | fgy24 | 2616699.5517 | 109 | fgy
RESIDENTL | epg11 | 6094828.0666 | 1503 | epg
NCONUML | rwt36 | 1279.88 | 1 | rwt
RESIDENTL | bwn14 | 23184606.5946 | 3016 | bwn
COMMERCIAL | bra31 | 7996775.7312 | 141 | bra
| nla32 | 13550.62 | 15 | nla
FARM | brt11 | 223967.42 | 33 | brt
| hpk12 | 10433.13 | 13 | hpk
INDUSTRIAL | llg13 | 899195.7591 | 21 | llg
INDUSTRIAL | wgl21 | 1687828.17 | 29 | wgl
INDUSTRIAL | cnr2 | 615523.18 | 19 | cnr
INDUSTRIAL | mfa14 | 499885.98 | 5 | mfa
RESIDENTL | drn13 | 15714620.5428 | 2698 | drn
FARM | kms12 | 1180373.8068 | 156 | kms
COMMERCIAL | rwn24 | 15303994.2605 | 63 | rwn
NCONUML | wn4 | 65357.11 | 21 | wn
COMMERCIAL | rwn33 | 562037.42 | 22 | rwn
| moe22 | 3614.75 | 12 | moe
| wgl13 | 39374.2 | 44 | wgl
| moe11 | 8193.3901 | 21 | moe
COMMERCIAL | wt7 | 4475658.5866 | 198 | wt
NCONUML | bwr13 | 106489.72 | 46 | bwr
NCONUML | kms12 | 115620.45 | 45 | kms
NCONUML | cyn24 | 41312.6858 | 21 | cyn
COMMERCIAL | mwl13 | 8520395.3383 | 232 | mwl
COMMERCIAL | cyn32 | 10902527.7138 | 351 | cyn
INDUSTRIAL | tgn31 | 3050316.88 | 29 | tgn
| wo13 | 12961.22 | 9 | wo
NCONUML | bra12 | 30121.15 | 6 | bra
| mwl24 | 4141.68 | 3 | mwl
RESIDENTL | ftr22 | 5196242.6186 | 1010 | ftr
| cyn12 | 33132.831 | 28 | cyn
| mwl11 | 4217.9 | 11 | mwl
NCONUML | sle13 | 9744.3474 | 7 | sle
RESIDENTL | sle14 | 16027394.2978 | 4223 | sle
RESIDENTL | wgl23 | 5362246.1099 | 739 | wgl
COMMERCIAL | cre23 | 25513720.5265 | 132 | cre
RESIDENTL | bdl43 | 5886157.096 | 1122 | bdl
RESIDENTL | bge21 | 100743.92 | 11 | bge
RESIDENTL | smg22 | 10427736.14 | 2476 | smg
FARM | rwn31 | 347566.14 | 21 | rwn
INDUSTRIAL | bn12 | 8173831.79 | 6 | bn
| wgi24 | 27543.5394 | 32 | wgi
| mfa23 | 2828.28 | 3 | mfa
NCONUML | elm22 | 93887.89 | 42 | elm
INDUSTRIAL | wots13 | 2426481.9937 | 28 | wots
RESIDENTL | mwl13 | 9372820.2657 | 1896 | mwl
COMMERCIAL | epg31 | 8736205.1691 | 170 | epg
| bdl44 | 43009.9658 | 33 | bdl
COMMERCIAL | wgl24 | 14484234.4559 | 200 | wgl
INDUSTRIAL | wn3 | 1104797.78 | 30 | wn
| wgi33 | 38017.7186 | 28 | wgi
NCONUML | wo31 | 91536.41 | 24 | wo
FARM | ldl14 | 3990495.203 | 142 | ldl
NCONUML | wyk12 | 43139.17 | 24 | wyk
INDUSTRIAL | mwl15 | 15961047.4 | 1 | mwl
LIGHTING | bdl32 | 23514.52 | 1 | bdl
| rve12 | 15159.19 | 33 | rve
NCONUML | phm34 | 55440.25 | 17 | phm
COMMERCIAL | phm22 | 18761180.3018 | 732 | phm
RESIDENTL | cyn22 | 8715945.6121 | 2142 | cyn
FARM | fgy31 | 3345.68 | 2 | fgy
RESIDENTL | smr22 | 8159798.5324 | 1327 | smr
RESIDENTL | cyn23 | 7298806.6664 | 1621 | cyn
FARM | bdl42 | 2407309.4815 | 483 | bdl
| wyk23 | 31976.68 | 33 | wyk
INDUSTRIAL | rwn26 | 257525.5397 | 10 | rwn
NCONUML | bwn11 | 91006.47 | 23 | bwn
COMMERCIAL | cyn23 | 7883296.3431 | 299 | cyn
| moe15 | 19145.0797 | 16 | moe
| drn11 | 44271.4909 | 65 | drn
INDUSTRIAL | moe22 | 88009.47 | 4 | moe
NCONUML | mdg1 | 4146.1 | 9 | mdg
FARM | bra33 | 5568.67 | 1 | bra
LIGHTING | bwa22 | 75542.46 | 1 | bwa
NCONUML | hpk14 | 64164.68 | 20 | hpk
NCONUML |  | 262.3928 | 5 | #REF!
INDUSTRIAL | cln13 | 2016187.9013 | 2 | cln
FARM | ofr11 | 1184021.9516 | 51 | ofr
FARM | phm31 | 2011038.4476 | 90 | phm
NCONUML | elm21 | 62554.36 | 23 | elm
NCONUML | wt8 | 36862.33 | 14 | wt
NCONUML | cnr1 | 1922.85 | 2 | cnr
INDUSTRIAL | cre31 | 212230.18 | 2 | cre
COMMERCIAL | mfa34 | 8313764.4144 | 170 | mfa
INDUSTRIAL | tt5 | 637183.9506 | 23 | tt
INDUSTRIAL | llg14 | 1201432.9268 | 29 | llg
RESIDENTL | wo23 | 1549813.7708 | 361 | wo
| bwr23 | 25383.1703 | 47 | bwr
| sle11 | 3997.21 | 10 | sle
NCONUML | epg22 | 8538.04 | 7 | epg
NCONUML | bwr24 | 20744.02 | 14 | bwr
INDUSTRIAL | myt12 | 952524.23 | 20 | myt
| ftr23 | 53453.1274 | 33 | ftr
RESIDENTL | bra11 | 9331476.9371 | 2277 | bra
FARM | ldl13 | 3504918.0126 | 302 | ldl
| brt11 | 8693.81 | 14 | brt
INDUSTRIAL | phm31 | 91642.7039 | 2 | phm
COMMERCIAL | bdl43 | 22280533.2345 | 523 | bdl
FARM | moe23 | 4928404.5033 | 365 | moe
| klk21 | 7164.56 | 8 | klk
| wt7 | 8483.27 | 17 | wt
FARM | llg11 | 4501914.1562 | 365 | llg
LIGHTING | cf2 | 13221.322 | 1 | cf
| tgn31 | 23134.1673 | 13 | tgn
RESIDENTL | nla31 | 3471883.5329 | 742 | nla
COMMERCIAL | bdl31 | 6479518.62 | 206 | bdl
COMMERCIAL | smr23 | 799486.21 | 26 | smr
INDUSTRIAL | rve11 | 154936.16 | 21 | rve
RESIDENTL | bm8b33 | 130717.0048 | 17 | bmb
FARM | phi12 | 364625.9 | 40 | phi
INDUSTRIAL | klk22 | 5518.6 | 1 | klk
RESIDENTL | llg12 | 7619865.2998 | 1210 | llg
RESIDENTL | cln21 | 24090170.4832 | 5877 | cln
NCONUML | cpk11 | 17830.25 | 17 | cpk
COMMERCIAL | ruba22 | 3463594.5603 | 120 | ruba
NCONUML | brt22 | 9306.55 | 7 | brt
INDUSTRIAL | epg32 | 7635590.16 | 5 | epg
INDUSTRIAL | cln12 | 360384.55 | 1 | cln
COMMERCIAL | bwr13 | 10101102.0366 | 288 | bwr
COMMERCIAL | wo22 | 9017310.64 | 153 | wo
INDUSTRIAL | hpk24 | 9439809.63 | 31 | hpk
COMMERCIAL | cpk12 | 5057421.24 | 115 | cpk
| lyd14 | 55928.8081 | 17 | lyd
INDUSTRIAL | klo11 | 67703.26 | 1 | klo
RESIDENTL | ldl14 | 11349760.1474 | 1905 | ldl
LIGHTING | myt21 | 2294.9 | 1 | myt
RESIDENTL | rwn22 | 13452598.5118 | 2640 | rwn
COMMERCIAL | bm8b32 | 168652.4116 | 16 | bmb
INDUSTRIAL | bdl34 | 328519.77 | 31 | bdl
| tt12 | 16952.1045 | 5 | tt
RESIDENTL | wots24 | 6979604.5034 | 1172 | wots
INDUSTRIAL | wyk24 | 160679.33 | 16 | wyk
COMMERCIAL | klo12 | 12237846.22 | 9 | klo
RESIDENTL | wo33 | 232024.16 | 58 | wo
COMMERCIAL | bn24 | 3468313.5774 | 163 | bn
COMMERCIAL | lga12 | 9341312.33 | 61 | lga
| msd1 | 16071.3636 | 20 | msd
INDUSTRIAL | ofr24 | 300622.14 | 4 | ofr
INDUSTRIAL | bwn13 | 24333.45 | 4 | bwn
| tt1 | 26786.62 | 3 | tt
INDUSTRIAL | rwt31 | 22449174.23 | 3 | rwt
FARM | mfa14 | 28798.91 | 1 | mfa
| bwr32 | 10607.4826 | 52 | bwr
INDUSTRIAL | wn4 | 1120535.2101 | 54 | wn
RESIDENTL | bwr12 | 975012.274 | 199 | bwr
INDUSTRIAL | wgi24 | 1432383.73 | 33 | wgi
| llg13 | 135285.4952 | 24 | llg
| rwn34 | 10950.9 | 10 | rwn
FARM | elm34 | 16399.68 | 6 | elm
RESIDENTL | ruba12 | 12797333.4035 | 1890 | ruba
COMMERCIAL | hpk22 | 5875279.82 | 181 | hpk
| cln11 | 262675.9461 | 229 | cln
RESIDENTL | cf2 | 494427.3912 | 409 | cf
FARM | elm22 | 15544.2323 | 4 | elm
INDUSTRIAL | smg32 | 67645.78 | 1 | smg
FARM | bwa23 | 3495492.525 | 169 | bwa
NCONUML | phm24 | 66511.6 | 15 | phm
NCONUML | wgi23 | 35701.3 | 15 | wgi
NCONUML | epg35 | 18576.68 | 9 | epg
NCONUML | llg13 | 26801.83 | 12 | llg
LIGHTING | phi13 | 74566.47 | 1 | phi
| ldl24 | 28689.7774 | 48 | ldl
| bge11 | 41147.6131 | 30 | bge
RESIDENTL | ofr21 | 18456788.2346 | 4412 | ofr
INDUSTRIAL | ofr11 | 52339.71 | 6 | ofr
COMMERCIAL | nrn11 | 8254682.48 | 13 | nrn
FARM | moe15 | 1053275.4428 | 126 | moe
INDUSTRIAL | lyd12 | 15947.41 | 3 | lyd
INDUSTRIAL | wt10 | 5540.7 | 1 | wt
RESIDENTL | rwt21 | 965731.93 | 282 | rwt
FARM | wo13 | 51683.13 | 6 | wo
INDUSTRIAL | epg34 | 25722.81 | 2 | epg
COMMERCIAL | lys36 | 31611.41 | 1 | lys
RESIDENTL | wn6 | 17451542.0984 | 3750 | wn
NCONUML | hpk12 | 23613.79 | 7 | hpk
INDUSTRIAL | ruba24 | 189283.4035 | 13 | ruba
| nrn12 | 36108.6 | 9 | nrn
NCONUML | nla32 | 30069.03 | 18 | nla
COMMERCIAL | bm8b31 | 174913.9253 | 14 | bmb
| wo22 | 26321.2427 | 38 | wo
INDUSTRIAL | fgy31 | 4952.61 | 1 | fgy
RESIDENTL | cln14 | 25051991.2109 | 8311 | cln
RESIDENTL | lga24 | 3807672.9803 | 653 | lga
RESIDENTL | bra31 | 2624204.8049 | 649 | bra
COMMERCIAL | cln21 | 7282112.3749 | 104 | cln
COMMERCIAL | ftr23 | 8984637.4811 | 336 | ftr
RESIDENTL | klo13 | 97850.5847 | 89 | klo
INDUSTRIAL | ofr14 | 250.62 | 1 | ofr
FARM | mwl24 | 966080.4815 | 75 | mwl
NCONUML | bdl41 | 86032.0652 | 28 | bdl
INDUSTRIAL | epg13 | 201122.3196 | 20 | epg
COMMERCIAL | tgn23 | 6173474.1124 | 95 | tgn
| moe12 | 11374.0239 | 16 | moe
INDUSTRIAL | drn11 | 8297.91 | 2 | drn
| wn4 | 46461.2191 | 29 | wn
NCONUML | wgl13 | 85005.64 | 23 | wgl
INDUSTRIAL | ftr22 | 264831.3749 | 23 | ftr
NCONUML | mjg11 | 5653.43 | 3 | mjg
RESIDENTL | klo12 | 526.2 | 1 | klo
COMMERCIAL | cln11 | 18408618.7138 | 182 | cln
NCONUML | wo13 | 11132.69 | 4 | wo
COMMERCIAL | yn38 | 28127.08 | 5 | yn
NCONUML | mwl24 | 19701.6 | 5 | mwl
RESIDENTL | wots12 | 7880580.6899 | 1786 | wots
COMMERCIAL | tgn43 | 5598797.62 | 126 | tgn
NCONUML | mfa23 | 6277.17 | 3 | mfa
NCONUML | bra32 | 63005.82 | 38 | bra
FARM | bdl34 | 247623.03 | 51 | bdl
INDUSTRIAL | wn5 | 6299826.69 | 33 | wn
| mby13 | 155.9226 | 1 | mby
FARM | ofr23 | 2419763.5413 | 305 | ofr
NCONUML | cre22 | 86458.6773 | 42 | cre
NCONUML | hpk23 | 84001.53 | 23 | hpk
RESIDENTL | bra24 | 8260262.5707 | 1824 | bra
| cyn14 | 12637.7523 | 26 | cyn
LIGHTING | wgl11 | 2443513.25 | 2 | wgl
NCONUML | wgi24 | 69610.83 | 24 | wgi
COMMERCIAL | klo14 | 11961206.944 | 269 | klo
FARM | drn14 | 379625.3327 | 36 | drn
RESIDENTL | bwr22 | 1941843.629 | 510 | bwr
| llg14 | 42684.6726 | 22 | llg
INDUSTRIAL | drn21 | 709809.96 | 3 | drn
INDUSTRIAL | tgn42 | 199383.97 | 5 | tgn
RESIDENTL | sle32 | 6677118.757 | 1350 | sle
RESIDENTL | myt12 | 14552002.0991 | 2380 | myt
FARM | myt21 | 821475.54 | 124 | myt
| bn11 | 39921.12 | 40 | bn
NCONUML | mby12 | 15769.2 | 4 | mby
NCONUML | bdl44 | 1602.59 | 5 | bdl
COMMERCIAL | tt12 | 10810239.5174 | 467 | tt
NCONUML | wn7 | 7884.6 | 2 | wn
| bdl34 | 14430.17 | 36 | bdl
RESIDENTL | lyd11 | 11014119.7855 | 2574 | lyd
FARM | wyk23 | 2329152.6841 | 202 | wyk
| epg23 | 66262.7623 | 20 | epg
RESIDENTL | rwt32 | 15157646.1346 | 3808 | rwt
RESIDENTL | cre31 | 23125994.5084 | 5990 | cre
FARM | bn11 | 9012293.1298 | 1372 | bn
COMMERCIAL |  | 2470964.7554 | 79 | #REF!
INDUSTRIAL | kms11 | 3849512.37 | 9 | kms
RESIDENTL | sle31 | 15232222.0022 | 4728 | sle
RESIDENTL | myt11 | 3230941.4261 | 365 | myt
| wyk12 | 33744.4845 | 17 | wyk
| lga11 | 13750.1489 | 25 | lga
COMMERCIAL | cre33 | 14716025.8299 | 132 | cre
RESIDENTL | trc01 | 404888.8876 | 85 | trc
| moe25 | 10579.3743 | 23 | moe
NCONUML | msd1 | 8725.66 | 9 | msd
RESIDENTL | mwl14 | 1637810.9082 | 178 | mwl
FARM | wn5 | 10157746.9699 | 1090 | wn
INDUSTRIAL | bwr33 | 13101695.07 | 41 | bwr
NCONUML | ofr24 | 72292.73 | 18 | ofr
| mdg1 | 5594.13 | 4 | mdg
FARM | wgi33 | 86057.74 | 7 | wgi
RESIDENTL | rwt22 | 12512450.4989 | 3066 | rwt
RESIDENTL | cnr2 | 3844076.3719 | 1054 | cnr
| hpk14 | 17565.23 | 35 | hpk
NCONUML | drn23 | 37389.78 | 20 | drn
RESIDENTL | tgn44 | 11943542.7304 | 2804 | tgn
| tgn42 | 0 | 1 | tgn
NCONUML | rwt22 | 27503.296 | 22 | rwt
FARM | mwl16 | 172184.54 | 14 | mwl
COMMERCIAL | nla34 | 1413700.5844 | 93 | nla
| epg22 | 2049.9261 | 2 | epg
FARM | tgn41 | 3728231.4432 | 423 | tgn
COMMERCIAL | lga23 | 3382991.9134 | 119 | lga
NCONUML | sle31 | 61055.23 | 20 | sle
NCONUML | tgn44 | 66469.79 | 20 | tgn
| phm24 | 18272.6834 | 34 | phm
RESIDENTL | hpk11 | 16523367.4098 | 4141 | hpk
| hpk13 | 40054.7485 | 22 | hpk
| bwr24 | 10180.34 | 28 | bwr
COMMERCIAL | bdl33 | 34051046.7333 | 257 | bdl
COMMERCIAL | wt9 | 7035668.1433 | 128 | wt
NCONUML | wt15 | 16005.53 | 14 | wt
FARM | ruba24 | 730484.142 | 55 | ruba
NCONUML | cpk23 | 20021.69 | 18 | cpk
INDUSTRIAL | mwl21 | 320021.87 | 5 | mwl
COMMERCIAL | hpk23 | 12064171.7331 | 206 | hpk
INDUSTRIAL | wt11 | 2563605.84 | 2 | wt
RESIDENTL | wt15 | 8580853.2399 | 1947 | wt
| elm21 | 24345.52 | 16 | elm
INDUSTRIAL | mwl16 | 183545.9668 | 9 | mwl
FARM | rve13 | 9637.99 | 1 | rve
NCONUML | drn22 | 69938.3 | 27 | drn
NCONUML | bdl31 | 70697.58 | 29 | bdl
NCONUML | bwa24 | 1320.25 | 1 | bwa
COMMERCIAL | mwl23 | 10773058.8537 | 154 | mwl
COMMERCIAL | elm23 | 5093994.3825 | 95 | elm
FARM | smr23 | 1078615.6398 | 156 | smr
| cpk11 | 37835.6667 | 47 | cpk
INDUSTRIAL | bra14 | 14750.52 | 4 | bra
RESIDENTL | rwn33 | 5693275.4596 | 1153 | rwn
| bn22 | 41634.09 | 21 | bn
INDUSTRIAL | tt2 | 11531135.8238 | 100 | tt
INDUSTRIAL | wt12 | 3871876.0911 | 67 | wt
INDUSTRIAL | mwl22 | 292678.42 | 8 | mwl
RESIDENTL | bn23 | 8695284.412 | 1665 | bn
COMMERCIAL | cyn11 | 9621618.8569 | 233 | cyn
| cyn21 | 22400.14 | 28 | cyn
INDUSTRIAL | mjg11 | 1321804.29 | 13 | mjg
INDUSTRIAL | cf2 | 1970.494 | 2 | cf
RESIDENTL | tt5 | 6560032.4165 | 1633 | tt
COMMERCIAL | smr14 | 6818307.6657 | 239 | smr
COMMERCIAL | smg33 | 1348313.99 | 14 | smg
RESIDENTL | rwt15 | 11066767.0768 | 2454 | rwt
COMMERCIAL | cre32 | 14440881.1645 | 427 | cre
INDUSTRIAL | smr24 | 4639865.5557 | 45 | smr
COMMERCIAL | fgy23 | 10185283.97 | 98 | fgy
COMMERCIAL | hpk11 | 3476478.711 | 53 | hpk
| cre32 | 19011.64 | 13 | cre
NCONUML | wgl23 | 12760.41 | 6 | wgl
COMMERCIAL | nrn15 | 84419.81 | 3 | nrn
NCONUML | moe15 | 22748.39 | 11 | moe
RESIDENTL | tt12 | 86039.86 | 6 | tt
RESIDENTL | cyn31 | 8632445.7043 | 2077 | cyn
RESIDENTL | wgl24 | 16633542.8094 | 2715 | wgl
COMMERCIAL | wgi22 | 6881286.006 | 159 | wgi
INDUSTRIAL | smr13 | 992080.85 | 26 | smr
NCONUML | cpk12 | 17033.61 | 10 | cpk
NCONUML | ftr21 | 16597.26 | 11 | ftr
FARM | mwl12 | 18529.37 | 2 | mwl
INDUSTRIAL | epg33 | 1129768.4897 | 4 | epg
| wyk13 | 9658.4809 | 15 | wyk
LIGHTING | trc01 | 669938.2281 | 2 | trc
FARM | hpk13 | 2305.94 | 1 | hpk
RESIDENTL | tt6 | 19150788.3328 | 4695 | tt
FARM | tgn31 | 5369095.0164 | 562 | tgn
NCONUML | wgl24 | 11028.97 | 10 | wgl
INDUSTRIAL | brt11 | 82545.9018 | 12 | brt
LIGHTING | mby11 | 10728.24 | 1 | mby
NCONUML | myt21 | 24178.1 | 12 | myt
| wt10 | 6115.9374 | 5 | wt
RESIDENTL | bge12 | 9796026.1467 | 1789 | bge
FARM | myt11 | 2640136.7565 | 257 | myt
NCONUML | cyn11 | 21168.08 | 13 | cyn
INDUSTRIAL |  | 942329979.1078 | 12 | #REF!
INDUSTRIAL | elm34 | 168803.0667 | 15 | elm
| brt22 | 30486.3216 | 18 | brt
INDUSTRIAL | epg11 | 6777.42 | 2 | epg
RESIDENTL | elm34 | 19825611.7814 | 4189 | elm
COMMERCIAL | sle13 | 974523.8832 | 109 | sle
INDUSTRIAL | lga13 | 207007.5439 | 9 | lga
RESIDENTL | mwl23 | 3618535.6291 | 812 | mwl
| fgy14 | 28887.99 | 26 | fgy
COMMERCIAL | mby13 | 2521770.2974 | 71 | mby
| lga12 | 14720.56 | 12 | lga
RESIDENTL | cpk12 | 17343162.547 | 2927 | cpk
COMMERCIAL | wt5 | 19785711.5258 | 118 | wt
INDUSTRIAL | drn24 | 4643890.64 | 3 | drn
FARM | drn21 | 13254.24 | 1 | drn
NCONUML | mwl11 | 360.93 | 3 | mwl
RESIDENTL | epg34 | 15669683.4078 | 3862 | epg
NCONUML | wt10 | 27658.61 | 16 | wt
LIGHTING | rwt14 | 962126.36 | 3 | rwt
COMMERCIAL | drn23 | 5472888.3558 | 161 | drn
LIGHTING | bwn11 | 6340546.01 | 1 | bwn
INDUSTRIAL | sfs1 | 80102.39 | 5 | sfs
COMMERCIAL | phm34 | 4610839.9937 | 66 | phm
COMMERCIAL | mfa31 | 3803351.87 | 100 | mfa
INDUSTRIAL | rwt25 | 2203508.65 | 42 | rwt
| bwa22 | 41045.3074 | 24 | bwa
FARM | smr13 | 139441.5096 | 27 | smr
NCONUML | phi12 | 84007.84 | 24 | phi
| fgy21 | 10377.87 | 9 | fgy
NCONUML | rwt15 | 44056.974 | 28 | rwt
LIGHTING | nla34 | 5187.52 | 1 | nla
RESIDENTL | sfs1 | 6449039.4989 | 958 | sfs
RESIDENTL | msd4 | 16354350.3097 | 2395 | msd
INDUSTRIAL | phm33 | 724516.58 | 21 | phm
COMMERCIAL | wgl14 | 59932538.6 | 1 | wgl
COMMERCIAL | rwt31 | 3904134.109 | 54 | rwt
RESIDENTL | wt5 | 5466545.168 | 1335 | wt
FARM | ftr22 | 3872176.8459 | 271 | ftr
| wn5 | 51237.831 | 23 | wn
INDUSTRIAL | kms12 | 880994.04 | 26 | kms
NCONUML | rwt31 | 27889.28 | 18 | rwt
RESIDENTL | elm22 | 20622579.4478 | 3120 | elm
| bn24 | 7126.586 | 9 | bn
FARM | wots11 | 7572710.4051 | 689 | wots
INDUSTRIAL | myt11 | 122662.09 | 11 | myt
NCONUML | bdl32 | 81716.25 | 38 | bdl
NCONUML | cyn33 | 39860.39 | 20 | cyn
| lga13 | 7900.07 | 12 | lga
COMMERCIAL | wn7 | 705796.26 | 31 | wn
RESIDENTL | tgn23 | 12995258.1614 | 2157 | tgn
RESIDENTL | wgl12 | 18309192.1093 | 3011 | wgl
NCONUML | drn14 | 58816.42 | 20 | drn
INDUSTRIAL | tt9 | 1853761.73 | 4 | tt
RESIDENTL | kms12 | 23913269.0041 | 4277 | kms
COMMERCIAL | wgi33 | 13737748.8552 | 364 | wgi
COMMERCIAL | phm21 | 28428865.0993 | 838 | phm
FARM | sle32 | 5441049.7096 | 310 | sle
NCONUML | cyn32 | 58907.16 | 38 | cyn
INDUSTRIAL | msd2 | 165834.72 | 18 | msd
COMMERCIAL | bwr23 | 26845428.111 | 233 | bwr
RESIDENTL | msd2 | 5810770.2828 | 1153 | msd
FARM | klk11 | 2014936.8264 | 177 | klk
| wots12 | 13459.1171 | 22 | wots
INDUSTRIAL | rwn24 | 4339629.96 | 13 | rwn
INDUSTRIAL | tgn41 | 1853911.3546 | 62 | tgn
COMMERCIAL | smg32 | 6595824.87 | 22 | smg
| wgi34 | 86239.94 | 15 | wgi
RESIDENTL | bn22 | 13286130.4589 | 3118 | bn
RESIDENTL | mfa31 | 9237847.4317 | 2206 | mfa
COMMERCIAL | wgi34 | 9571334.08 | 60 | wgi
RESIDENTL | mdi1 | 176577.17 | 31 | mdi
NCONUML | rwn31 | 16738.19 | 15 | rwn
INDUSTRIAL | drn13 | 239296.9 | 11 | drn
INDUSTRIAL | bdl43 | 306419.52 | 21 | bdl
NCONUML | wo23 | 56204.51 | 16 | wo
COMMERCIAL | ftr21 | 2804675.8206 | 100 | ftr
COMMERCIAL | bwa23 | 206762.2501 | 23 | bwa
NCONUML | mfa21 | 28416.84 | 12 | mfa
| cln23 | 52144.7804 | 85 | cln
RESIDENTL | rve11 | 2276471.0008 | 508 | rve
COMMERCIAL | ofr24 | 6649904.8426 | 113 | ofr
NCONUML | phi13 | 105028.33 | 33 | phi
FARM | smg22 | 25054.15 | 4 | smg
FARM | bwn11 | 18419.1 | 1 | bwn
INDUSTRIAL | epg31 | 360181.3871 | 31 | epg
COMMERCIAL | fgy14 | 7872993.2117 | 231 | fgy
| ldl11 | 24480.7 | 22 | ldl
INDUSTRIAL | wgl24 | 939120.3004 | 39 | wgl
| phm22 | 31542.7748 | 10 | phm
COMMERCIAL | moe15 | 2469270.3666 | 172 | moe
| cnr3 | 100.0469 | 1 | cnr
RESIDENTL | bwn12 | 4456239.3509 | 1013 | bwn
COMMERCIAL | mwl24 | 5791496.4979 | 78 | mwl
COMMERCIAL | wo13 | 2493976.37 | 46 | wo
RESIDENTL | elm25 | 10534980.5572 | 2009 | elm
RESIDENTL | phm32 | 14466986.7977 | 3288 | phm
COMMERCIAL | ofr11 | 14130002.2904 | 224 | ofr
INDUSTRIAL | bge13 | 1057475.88 | 11 | bge
RESIDENTL | ofr22 | 7907197.5875 | 2174 | ofr
INDUSTRIAL | lga22 | 745287.81 | 44 | lga
FARM | hpk22 | 33600.65 | 5 | hpk
COMMERCIAL | epg23 | 63543126.9632 | 711 | epg
NCONUML | epg34 | 29379.47 | 21 | epg
| mwl23 | 14018.9088 | 10 | mwl
FARM | lyd14 | 350081.37 | 31 | lyd
| elm33 | 18371.0537 | 30 | elm
RESIDENTL | bwn11 | 14758921.2622 | 2984 | bwn
| cyn33 | 33636.86 | 37 | cyn
INDUSTRIAL | ldl13 | 1566146.5513 | 31 | ldl
NCONUML | smg32 | 19512.15 | 10 | smg
NCONUML | lga21 | 24931.49 | 9 | lga
RESIDENTL | mfa34 | 6438005.323 | 995 | mfa
COMMERCIAL | lga22 | 10229963.6597 | 340 | lga
COMMERCIAL | wgi31 | 4363035.5887 | 128 | wgi
| wt9 | 17175.83 | 21 | wt
INDUSTRIAL | mfa21 | 1292894.4886 | 57 | mfa
FARM | wgi32 | 343056.5273 | 19 | wgi
COMMERCIAL | bge21 | 44944.8 | 1 | bge
INDUSTRIAL | elm26 | 46289.86 | 5 | elm
NCONUML | msd4 | 12187.83 | 6 | msd
COMMERCIAL | bra21 | 14789918.5926 | 289 | bra
| cpk22 | 7305.07 | 12 | cpk
NCONUML | phm32 | 76324.09 | 20 | phm
NCONUML | sfs1 | 44865.78 | 10 | sfs
COMMERCIAL | lyd13 | 6072257.17 | 42 | lyd
FARM | cyn33 | 36456.98 | 4 | cyn
NCONUML | phm21 | 71428.0533 | 24 | phm
COMMERCIAL | sle32 | 5434267.6149 | 190 | sle
NCONUML | smg31 | 21751.86 | 17 | smg
NCONUML | wots11 | 25057.91 | 11 | wots
RESIDENTL | tgn43 | 15724147.9465 | 3608 | tgn
INDUSTRIAL | cyn21 | 9259443.95 | 23 | cyn
INDUSTRIAL | bn23 | 1923467.13 | 19 | bn
NCONUML | nrn14 | 79150.17 | 17 | nrn
NCONUML | cyn22 | 32483.16 | 10 | cyn
NCONUML | wgl12 | 47271.49 | 20 | wgl
COMMERCIAL | phm24 | 600129.57 | 25 | phm
NCONUML | lga11 | 25837.14 | 8 | lga
NCONUML | tgn41 | 7415.11 | 5 | tgn
RESIDENTL | wgl11 | 17118670.1537 | 3818 | wgl
RESIDENTL | wots11 | 15871220.8415 | 2910 | wots
| rwn31 | 40233.5106 | 27 | rwn
COMMERCIAL | elm32 | 8171019.0636 | 263 | elm
FARM | mby11 | 1335559.7721 | 187 | mby
INDUSTRIAL | mwl25 | 33119.15 | 8 | mwl
FARM | rwn26 | 5055.63 | 2 | rwn
| nla34 | 8234.98 | 10 | nla
RESIDENTL |  | 349105.8277 | 492 | #REF!
FARM | epg13 | 82815.8863 | 12 | epg
| wyk24 | 32167.14 | 30 | wyk
FARM | sle11 | 16862.17 | 6 | sle
COMMERCIAL | bm8b33 | 3349.12 | 2 | bmb
RESIDENTL | smg21 | 17914575.4009 | 3718 | smg
INDUSTRIAL | bdl42 | 622534.62 | 24 | bdl
| yn38 | 7519.7419 | 1 | yn
| phi13 | 28221.5917 | 27 | phi
| epg14 | 9258.9052 | 38 | epg
FARM | nla31 | 1791184.5035 | 140 | nla
INDUSTRIAL | wgi33 | 1188063.8119 | 37 | wgi
LIGHTING | phm33 | 4303153.65 | 2 | phm
RESIDENTL | phm33 | 12878778.4238 | 2134 | phm
COMMERCIAL | wgl23 | 3870974.8784 | 252 | wgl
NCONUML | wt5 | 58508.56 | 14 | wt
NCONUML | bwn14 | 81385.02 | 37 | bwn
NCONUML | mfa31 | 49958.93 | 14 | mfa
COMMERCIAL | bra12 | 23355928.37 | 122 | bra
NCONUML | wt13 | 98966.19 | 41 | wt
COMMERCIAL | klo24 | 13267963.2484 | 244 | klo
COMMERCIAL | bge12 | 6262328.83 | 64 | bge
COMMERCIAL | wn4 | 10511680.2174 | 332 | wn
INDUSTRIAL | tt6 | 2940006.87 | 14 | tt
FARM | cln13 | 4519.0334 | 1 | cln
RESIDENTL | bwa23 | 1839261.5711 | 259 | bwa
RESIDENTL | smr12 | 601661.7559 | 102 | smr
NCONUML | bra31 | 17155.48 | 11 | bra
FARM | cln22 | 84599.56 | 6 | cln
RESIDENTL | moe23 | 10757204.18 | 1872 | moe
FARM | bn23 | 4995698.9571 | 709 | bn
INDUSTRIAL | bwr12 | 7576207.2428 | 317 | bwr
COMMERCIAL | elm33 | 8652520.7547 | 229 | elm
RESIDENTL | tgn12 | 769554.192 | 239 | tgn
NCONUML | bn23 | 5729.17 | 9 | bn
| cyn11 | 35169.6447 | 13 | cyn
INDUSTRIAL | wots12 | 5742170.47 | 22 | wots
INDUSTRIAL | llg12 | 8080777.31 | 18 | llg
NCONUML | ofr14 | 11958.45 | 3 | ofr
RESIDENTL | rwn34 | 11161403.5989 | 1490 | rwn
RESIDENTL | fgy12 | 975691.3435 | 398 | fgy
COMMERCIAL | wyk24 | 11852940.7836 | 290 | wyk
COMMERCIAL | smr12 | 1199230.8 | 20 | smr
INDUSTRIAL | wgl11 | 590499.13 | 17 | wgl
INDUSTRIAL | moe13 | 8896507.14 | 13 | moe
INDUSTRIAL | wots11 | 14616083.73 | 22 | wots
NCONUML | epg13 | 4325.18 | 2 | epg
NCONUML | bn22 | 72789.04 | 38 | bn
RESIDENTL | bwr23 | 15381612.1105 | 3589 | bwr
NCONUML | cln13 | 19538.3161 | 10 | cln
COMMERCIAL | bwa24 | 4350900.07 | 4 | bwa
COMMERCIAL | bwr32 | 11258727.4704 | 251 | bwr
RESIDENTL | bra32 | 8710928.5985 | 2041 | bra
FARM | klo14 | 681766.459 | 92 | klo
INDUSTRIAL | tt7 | 9353368.9205 | 125 | tt
RESIDENTL | wo11 | 815896.564 | 156 | wo
LIGHTING | mwl24 | 803944.3 | 2 | mwl
COMMERCIAL | bwr24 | 7860784.794 | 262 | bwr
COMMERCIAL | drn14 | 5284276.4061 | 147 | drn
NCONUML | hpk24 | 27055.52 | 10 | hpk
| cyn32 | 34865.18 | 48 | cyn
| bra23 | 7974.72 | 25 | bra
RESIDENTL | rve13 | 16767421.4281 | 3587 | rve
COMMERCIAL | bwn13 | 11531398.8601 | 263 | bwn
FARM | cln23 | 76487.94 | 5 | cln
NCONUML | ruba24 | 1482.28 | 4 | ruba
COMMERCIAL | msd1 | 4448954.738 | 126 | msd
| phm31 | 2299.25 | 4 | phm
LIGHTING | wn1 | 677520.74 | 1 | wn
COMMERCIAL | wt8 | 2125517.5597 | 71 | wt
RESIDENTL | bdl33 | 5101200.3632 | 906 | bdl
COMMERCIAL | rwt21 | 33203170.5825 | 281 | rwt
FARM |  | 15223.9488 | 53 | #REF!
| fgy13 | 16173.63 | 19 | fgy
| wt11 | 14907.843 | 20 | wt
RESIDENTL | mwl24 | 4259131.5949 | 729 | mwl
INDUSTRIAL | bwn12 | 375603.57 | 33 | bwn
| lyd12 | 10355.6 | 16 | lyd
| lyd13 | 31235.27 | 24 | lyd
| elm32 | 28931.8643 | 22 | elm
RESIDENTL | ldl13 | 20183081.1078 | 3515 | ldl
COMMERCIAL | epg14 | 4722560.1631 | 66 | epg
FARM | epg32 | 616929.8369 | 16 | epg
| smg23 | 6841.4304 | 12 | smg
NCONUML | mwl16 | 31954.29 | 10 | mwl
COMMERCIAL | ofr22 | 3955299.41 | 63 | ofr
FARM | wgl24 | 9990463.449 | 886 | wgl
COMMERCIAL | llg14 | 8402501.0583 | 280 | llg
COMMERCIAL | wgi24 | 3234685.3433 | 136 | wgi
FARM | cnr3 | 47812.597 | 17 | cnr
| epg33 | 55263.0616 | 6 | epg
INDUSTRIAL | bra24 | 1115020.317 | 14 | bra
NCONUML | wgi33 | 84992.31 | 23 | wgi
FARM | rwt15 | 1849.17 | 1 | rwt
RESIDENTL | ldl12 | 620798.3677 | 119 | ldl
INDUSTRIAL | bwr22 | 8606432.4227 | 334 | bwr
FARM | cf2 | 2033.193 | 1 | cf
NCONUML | klo14 | 36515.49 | 28 | klo
INDUSTRIAL | trc01 | 31629.57 | 2 | trc
RESIDENTL | lga21 | 9412760.8279 | 1623 | lga
RESIDENTL | wt13 | 15834142.0313 | 3223 | wt
RESIDENTL | cyn13 | 3260017.5153 | 858 | cyn
INDUSTRIAL | ofr21 | 138382.59 | 9 | ofr
NCONUML | sle32 | 22407.43 | 13 | sle
COMMERCIAL | lyd12 | 210380 | 9 | lyd
NCONUML | wyk23 | 87622.06 | 45 | wyk
| fgy33 | 11652.67 | 18 | fgy
INDUSTRIAL | hpk22 | 98414.21 | 14 | hpk
NCONUML | sle11 | 59204.61 | 19 | sle
RESIDENTL | bwr13 | 20902397.8318 | 4170 | bwr
COMMERCIAL | rwn34 | 3999387.7688 | 144 | rwn
| hpk22 | 19671.58 | 41 | hpk
FARM | klk22 | 332413.14 | 10 | klk
INDUSTRIAL | wn1 | 2988984.92 | 20 | wn
NCONUML | rwn26 | 27156.61 | 25 | rwn
| bwr33 | 13120.641 | 3 | bwr
NCONUML | mby11 | 20114.34 | 7 | mby
RESIDENTL | smg33 | 11198068.0634 | 2626 | smg
FARM | bn12 | 813334.585 | 146 | bn
FARM | bdl32 | 1026406.0127 | 170 | bdl
FARM | drn24 | 15422429 | 2 | drn
LIGHTING | cre21 | 378603.77 | 3 | cre
RESIDENTL | smg32 | 834640.09 | 219 | smg
| wt12 | 39199.7023 | 19 | wt
FARM | bwn14 | 804408.7 | 76 | bwn
NCONUML | bwr33 | 16865.43 | 3 | bwr
INDUSTRIAL | rwn22 | 12871.85 | 4 | rwn
NCONUML | drn11 | 63307.01 | 20 | drn
INDUSTRIAL | mwl13 | 228128.43 | 11 | mwl
COMMERCIAL | elm22 | 6567142.5918 | 154 | elm
FARM | trc01 | 521142.3328 | 100 | trc
COMMERCIAL | rwt14 | 11855990.576 | 301 | rwt
INDUSTRIAL | sle14 | 1780526.4437 | 64 | sle
RESIDENTL | smr24 | 17064871.7804 | 2952 | smr
FARM | bwa22 | 1586063.9755 | 254 | bwa
NCONUML | tt4 | 37478.54 | 17 | tt
| tt9 | 28146.8116 | 74 | tt
COMMERCIAL | epg34 | 4040655.8363 | 65 | epg
FARM | nrn11 | 7816.07 | 2 | nrn
LIGHTING | cpk23 | 1632459.3 | 1 | cpk
RESIDENTL | fgy31 | 4476808.4262 | 913 | fgy
COMMERCIAL | fgy33 | 6399813.6929 | 132 | fgy
| cnr2 | 20535.9245 | 15 | cnr
INDUSTRIAL | sle32 | 10933678.58 | 25 | sle
| bra13 | 120577.89 | 18 | bra
RESIDENTL | wgi23 | 12118480.0079 | 2685 | wgi
INDUSTRIAL | wn6 | 922850.6842 | 19 | wn
LIGHTING | tgn44 | 752.53 | 1 | tgn
RESIDENTL | wt8 | 8250779.9392 | 1851 | wt
COMMERCIAL | moe25 | 5695010.3572 | 176 | moe
FARM | wgi34 | 4315044.5216 | 374 | wgi
INDUSTRIAL | fgy32 | 667572.7217 | 61 | fgy
NCONUML | wo32 | 55386.46 | 14 | wo
INDUSTRIAL | lys36 | 1267258.48 | 1 | lys
| bn12 | 10728.35 | 13 | bn
NCONUML | brt11 | 10828.27 | 7 | brt
| drn21 | 27694.76 | 39 | drn
| drn24 | 16030.7 | 26 | drn
RESIDENTL | cpk23 | 11646034.7633 | 2466 | cpk
RESIDENTL | wots13 | 7948103.7952 | 1344 | wots
FARM | wgl23 | 3908847.1376 | 390 | wgl
COMMERCIAL | wyk13 | 4417313.7071 | 191 | wyk
NCONUML | klk21 | 10664.54 | 6 | klk
INDUSTRIAL | smg22 | 31514.93 | 2 | smg
RESIDENTL | wgi22 | 12719214.8315 | 3088 | wgi
| cpk13 | 49314.0333 | 41 | cpk
COMMERCIAL | bdl41 | 11311068.2286 | 367 | bdl
NCONUML | nrn12 | 43208.48 | 18 | nrn
RESIDENTL | fgy23 | 5177398.3937 | 1023 | fgy
NCONUML | brt21 | 3240.29 | 5 | brt
NCONUML | tgn31 | 2100.01 | 7 | tgn
RESIDENTL | mjg11 | 6256821.3625 | 1064 | mjg
INDUSTRIAL | lga24 | 175905.212 | 21 | lga
COMMERCIAL | moe21 | 6644337.36 | 291 | moe
INDUSTRIAL | bwn14 | 326743.47 | 17 | bwn
INDUSTRIAL | phm22 | 15545673.5732 | 29 | phm
LIGHTING | klo24 | 2201282.63 | 3 | klo
FARM | epg12 | 13782.33 | 2 | epg
INDUSTRIAL | cln14 | 247.5387 | 1 | cln
FARM | bge13 | 383352.554 | 75 | bge
NCONUML | bra14 | 25509.54 | 26 | bra
RESIDENTL | fgy24 | 17189073.2659 | 3574 | fgy
NCONUML | lyd14 | 37348.84 | 18 | lyd
FARM | fgy21 | 91303 | 9 | fgy
INDUSTRIAL | elm24 | 6476.78 | 2 | elm
FARM | bra24 | 985.88 | 1 | bra
COMMERCIAL | ldl24 | 1420329.0926 | 55 | ldl
INDUSTRIAL | wots24 | 329358.8434 | 32 | wots
| moe13 | 6325.43 | 5 | moe
COMMERCIAL | cyn14 | 5422735.5047 | 221 | cyn
LIGHTING | smg21 | 4640189.26 | 4 | smg
COMMERCIAL | tgn42 | 24454733.755 | 420 | tgn
INDUSTRIAL | lga14 | 502652.15 | 16 | lga
INDUSTRIAL | cre33 | 377497.19 | 17 | cre
FARM | ldl11 | 223383.36 | 16 | ldl
INDUSTRIAL | bn24 | 28582582.13 | 34 | bn
COMMERCIAL | tt1 | 14308038.8686 | 155 | tt
| wn3 | 30735.58 | 33 | wn
NCONUML | ldl21 | 10778.31 | 7 | ldl
NCONUML | wt6 | 188781.23 | 35 | wt
RESIDENTL | elm23 | 20356024.4153 | 3325 | elm
COMMERCIAL | drn11 | 4003224.2127 | 79 | drn
COMMERCIAL | bra34 | 7850026.49 | 9 | bra
FARM | cyn32 | 3133.97 | 2 | cyn
FARM | cpk23 | 18946.87 | 2 | cpk
FARM | wt15 | 5251.96 | 1 | wt
NCONUML | wgi32 | 95036.63 | 31 | wgi
COMMERCIAL | phm32 | 13343791.1884 | 221 | phm
COMMERCIAL | epg22 | 38007492.3668 | 89 | epg
INDUSTRIAL | wgl15 | 1553419.6108 | 26 | wgl
FARM | phm33 | 7138587.5126 | 545 | phm
LIGHTING | bra32 | 1301740.84 | 1 | bra
COMMERCIAL | bra22 | 30448240 | 1 | bra
COMMERCIAL | msd4 | 11090376.2999 | 395 | msd
COMMERCIAL | lyd14 | 7038791.6959 | 51 | lyd
| phi12 | 701365.4285 | 34 | phi
| nrn11 | 5120.38 | 9 | nrn
INDUSTRIAL | smg21 | 777155.28 | 5 | smg
NCONUML | nla31 | 5002.08 | 5 | nla
RESIDENTL | wyk13 | 19583843.7522 | 3346 | wyk
RESIDENTL | tgn41 | 6800482.2089 | 1104 | tgn
COMMERCIAL | fgy34 | 7285642.6158 | 201 | fgy
FARM | wgl11 | 5210774.8775 | 355 | wgl
FARM | tgn11 | 616949.6887 | 82 | tgn
NCONUML | wn5 | 5268.61 | 9 | wn
NCONUML | bdl42 | 6088.6 | 9 | bdl
INDUSTRIAL | hpk23 | 515987.93 | 6 | hpk
FARM | tgn44 | 47621.17 | 6 | tgn
| smr13 | 35140.976 | 19 | smr
| wgi31 | 18377.08 | 37 | wgi
NCONUML | bwr34 | 85519.21 | 30 | bwr
| bdl32 | 24365.9844 | 40 | bdl
COMMERCIAL | fgy13 | 5672167.28 | 57 | fgy
INDUSTRIAL | sle31 | 621920.2305 | 85 | sle
NCONUML | cyn23 | 72679.67 | 24 | cyn
NCONUML | hpk22 | 92149.17 | 38 | hpk
RESIDENTL | cre23 | 13902510.3441 | 3180 | cre
COMMERCIAL | lga21 | 4415159.211 | 179 | lga
| cre33 | 51988.0123 | 70 | cre
INDUSTRIAL | bra32 | 800790.5812 | 33 | bra
| rwn26 | 43959.1499 | 36 | rwn
NCONUML | ftr22 | 27457.1971 | 11 | ftr
FARM | cyn23 | 28738.28 | 3 | cyn
FARM | wn2 | 2722540.844 | 262 | wn
FARM | wots25 | 1192605.1156 | 155 | wots
COMMERCIAL | lga11 | 2601951.4442 | 115 | lga
COMMERCIAL | cnr1 | 836269.15 | 40 | cnr
RESIDENTL | cre22 | 15737441.9951 | 3931 | cre
RESIDENTL | cyn24 | 3227627.7482 | 729 | cyn
| drn14 | 42739.5968 | 43 | drn
NCONUML | wgi34 | 240.62 | 2 | wgi
COMMERCIAL | mdi1 | 200221.43 | 4 | mdi
LIGHTING | lga22 | 290997.27 | 1 | lga
RESIDENTL | sle13 | 2426821.6594 | 1643 | sle
RESIDENTL | mby12 | 3267894.3821 | 609 | mby
FARM | wgi31 | 368672.79 | 43 | wgi
INDUSTRIAL | cyn24 | 15644182.2427 | 207 | cyn
| fgy34 | 3433.61 | 11 | fgy
RESIDENTL | bge11 | 15368827.4604 | 2654 | bge
RESIDENTL | ftr12 | 3825364.7454 | 636 | ftr
| mfa21 | 17049.39 | 26 | mfa
COMMERCIAL | wgi21 | 45541.7604 | 2 | wgi
INDUSTRIAL | wo14 | 2975508 | 24 | wo
COMMERCIAL | wgl12 | 5759083.9004 | 210 | wgl
INDUSTRIAL | moe23 | 765740.5661 | 26 | moe
COMMERCIAL | hpk14 | 5487941.7 | 85 | hpk
NCONUML | tt2 | 10017.24 | 3 | tt
INDUSTRIAL | cpk13 | 1507420.269 | 6 | cpk
INDUSTRIAL | lga41 | 52440142.6 | 1 | lga
NCONUML | elm26 | 60173.53 | 25 | elm
FARM | cf1 | 12492.747 | 1 | cf
RESIDENTL | bwr32 | 11435795.4629 | 2903 | bwr
NCONUML | cln23 | 19017.15 | 5 | cln
RESIDENTL | bdl41 | 18711766.0554 | 3582 | bdl
RESIDENTL | tt4 | 9918702.5206 | 2673 | tt
NCONUML | nrn13 | 44749.68 | 14 | nrn
NCONUML | mwl12 | 43601.75 | 11 | mwl
FARM | cln12 | 30466.72 | 1 | cln
INDUSTRIAL | cpk21 | 122110.94 | 5 | cpk
NCONUML | epg11 | 2275 | 2 | epg
FARM | brt22 | 1064314.9433 | 146 | brt
NCONUML | moe21 | 60919.67 | 15 | moe
RESIDENTL | ldl22 | 4948357.507 | 1104 | ldl
INDUSTRIAL | epg22 | 206880.17 | 13 | epg
NCONUML | cln12 | 55224.6632 | 17 | cln
| wo14 | 16653.0726 | 14 | wo
INDUSTRIAL | wo13 | 14774006.15 | 3 | wo
INDUSTRIAL | wgi22 | 729700.7 | 28 | wgi
COMMERCIAL | msd2 | 2629949.014 | 87 | msd
NCONUML | ldl22 | 11421.24 | 5 | ldl
RESIDENTL | wo22 | 17812297.6729 | 4125 | wo
FARM | mwl25 | 2028215.2676 | 224 | mwl
| cln14 | 46492.03 | 68 | cln
INDUSTRIAL | smr14 | 413387.45 | 34 | smr
FARM | rwn33 | 39914.72 | 5 | rwn
NCONUML | tt7 | 28203.83 | 11 | tt
INDUSTRIAL | lga11 | 317451.8284 | 16 | lga
INDUSTRIAL | tt12 | 6074893.6495 | 86 | tt
INDUSTRIAL | rwn32 | 87972.96 | 1 | rwn
RESIDENTL | myt21 | 10899844.0445 | 1487 | myt
RESIDENTL | cyn14 | 9596207.6734 | 2758 | cyn
RESIDENTL | kms11 | 9874885.3712 | 1972 | kms
COMMERCIAL | wo32 | 9961950.2687 | 147 | wo
NCONUML | hpk21 | 96497.83 | 40 | hpk
FARM | mwl13 | 248036.6173 | 7 | mwl
RESIDENTL | smr23 | 3447913.5369 | 523 | smr
INDUSTRIAL | nla32 | 1443086.18 | 25 | nla
| rwt32 | 35174.87 | 36 | rwt
INDUSTRIAL | moe11 | 65970.59 | 6 | moe
INDUSTRIAL | wo33 | 33298223.9508 | 7 | wo
INDUSTRIAL | bra31 | 2919.84 | 1 | bra
RESIDENTL | moe15 | 9740983.6859 | 1552 | moe
RESIDENTL | moe12 | 4538532.291 | 887 | moe
INDUSTRIAL | bdl41 | 1328921.5447 | 34 | bdl
NCONUML | tt6 | 36560.52 | 20 | tt
RESIDENTL | uwy1 | 6496143.3356 | 1032 | uwy
RESIDENTL | wgi32 | 16438958.2366 | 3917 | wgi
COMMERCIAL | rwn31 | 2125446.8547 | 72 | rwn
| ldl13 | 45979.2126 | 34 | ldl
LIGHTING | hpk23 | 2010173.36 | 1 | hpk
RESIDENTL | fgy14 | 9703108.5669 | 2483 | fgy
FARM | rwn24 | 30208.83 | 4 | rwn
COMMERCIAL | wo23 | 11409957.4027 | 304 | wo
| myt12 | 115131.3847 | 34 | myt
| bge13 | 13458.3255 | 19 | bge
| sle32 | 15918.6359 | 20 | sle
FARM | epg11 | 14625.27 | 2 | epg
NCONUML | mwl21 | 34561.25 | 17 | mwl
COMMERCIAL | nrn12 | 21654160.6835 | 271 | nrn
COMMERCIAL | llg13 | 15983000.2277 | 99 | llg
| lga22 | 14116.8478 | 12 | lga
FARM | hpk11 | 14620.89 | 5 | hpk
RESIDENTL | ofr11 | 25072251.243 | 5672 | ofr
FARM | ftr12 | 9732520.1395 | 879 | ftr
RESIDENTL | epg21 | 580054.4394 | 151 | epg
FARM | bge22 | 343097.1961 | 60 | bge
COMMERCIAL | sfs1 | 1879673.1771 | 124 | sfs
| cln24 | 61460.6675 | 37 | cln
NCONUML | smg22 | 48204.28 | 25 | smg
RESIDENTL | phm34 | 11301839.7716 | 2904 | phm
RESIDENTL | phm31 | 2762476.4376 | 550 | phm
NCONUML | smr13 | 69764.68 | 26 | smr
RESIDENTL | wyk12 | 12357178.5976 | 1789 | wyk
INDUSTRIAL | sle13 | 125251.914 | 47 | sle
FARM | phm24 | 689286.43 | 52 | phm
| cre31 | 63798.4484 | 85 | cre
INDUSTRIAL | bge12 | 121322.77 | 7 | bge
FARM | wots12 | 5076.62 | 1 | wots
NCONUML | cf1 | 1922.85 | 2 | cf
RESIDENTL | wo31 | 20016820.444 | 4554 | wo
FARM | smr22 | 1275801.32 | 154 | smr
FARM | lga22 | 1443457.6222 | 105 | lga
COMMERCIAL | mwl22 | 10003347.9587 | 192 | mwl
FARM | bn24 | 2239563.0749 | 370 | bn
NCONUML | wots25 | 45798.68 | 13 | wots
NCONUML | wgi31 | 79233.36 | 21 | wgi
FARM | epg23 | 30049.96 | 2 | epg
NCONUML | klk11 | 24723.1 | 13 | klk
| mwl14 | 3593.32 | 2 | mwl
RESIDENTL | mdg1 | 4384126.608 | 684 | mdg
RESIDENTL | nrn14 | 9562152.1887 | 1877 | nrn
LIGHTING | msd4 | 139319.89 | 1 | msd
LIGHTING | sfs1 | 1558457.9 | 1 | sfs
| klo14 | 120043.1087 | 185 | klo
RESIDENTL | hpk14 | 17025183.7337 | 3944 | hpk
FARM | lga12 | 4046898.7707 | 351 | lga
COMMERCIAL | ldl14 | 12475957.7156 | 266 | ldl
RESIDENTL | bn11 | 14382992.5485 | 2912 | bn
COMMERCIAL | bdl34 | 6213094.4744 | 204 | bdl
FARM | lyd11 | 23799.7 | 3 | lyd
| mwl22 | 10189.434 | 23 | mwl
NCONUML | cf2 | 120.31 | 1 | cf
| epg32 | 18473.04 | 31 | epg
RESIDENTL | bdl34 | 21922135.2151 | 5106 | bdl
COMMERCIAL | rwn26 | 3719056.4225 | 81 | rwn
INDUSTRIAL | mby13 | 219583.33 | 2 | mby
NCONUML | fgy33 | 40029.49 | 14 | fgy
| ftr22 | 13372.1897 | 14 | ftr
NCONUML | mwl13 | 53127.87 | 17 | mwl
INDUSTRIAL | rwt32 | 132361.99 | 4 | rwt
COMMERCIAL | phm23 | 17053480.4 | 2 | phm
COMMERCIAL | bra13 | 19208526.3529 | 181 | bra
FARM | wn1 | 37241.96 | 7 | wn
FARM | bm8b33 | 1540.9 | 2 | bmb
COMMERCIAL | wt10 | 13883699.3972 | 155 | wt
INDUSTRIAL | uwy1 | 90405.23 | 3 | uwy
RESIDENTL | ldl23 | 26005181.5029 | 4084 | ldl
FARM | klo24 | 194259.84 | 22 | klo
| hpk11 | 33718.6052 | 42 | hpk
NCONUML | phm33 | 47915.862 | 19 | phm
FARM | wn6 | 4543418.3442 | 605 | wn
COMMERCIAL | cyn21 | 3633643.5973 | 195 | cyn
INDUSTRIAL | wo22 | 393144.5 | 11 | wo
RESIDENTL | tgn42 | 795534.2193 | 223 | tgn
INDUSTRIAL | mwl23 | 715134.0252 | 54 | mwl
| rwt22 | 26934.55 | 52 | rwt
COMMERCIAL | phm31 | 4117822.4369 | 32 | phm
RESIDENTL | epg22 | 39578.43 | 14 | epg
RESIDENTL | nla32 | 6559402.1513 | 1220 | nla
RESIDENTL | myt22 | 1017937.6841 | 120 | myt
| wgl15 | 30619.4 | 19 | wgl
LIGHTING | mjg11 | 68938.73 | 1 | mjg
COMMERCIAL | phi12 | 2400712.314 | 73 | phi
COMMERCIAL | rwt36 | 2264519.95 | 43 | rwt
INDUSTRIAL | wgi23 | 157973.74 | 15 | wgi
NCONUML | elm24 | 74942.52 | 25 | elm
RESIDENTL | wt10 | 3332972.5881 | 860 | wt
NCONUML | ruba22 | 360.93 | 3 | ruba
FARM | phi11 | 82538.05 | 19 | phi
| bra11 | 11169.2884 | 32 | bra
INDUSTRIAL | moe15 | 1465208.8927 | 46 | moe
| tt5 | 13084.5535 | 33 | tt
LIGHTING | elm34 | 2971413.79 | 6 | elm
FARM | rwt25 | 33966.32 | 4 | rwt
RESIDENTL | moe11 | 9711471.9521 | 1967 | moe
INDUSTRIAL | rwt22 | 12240.297 | 2 | rwt
FARM | tgn23 | 1979366.6929 | 215 | tgn
COMMERCIAL | elm34 | 4840398.0166 | 153 | elm
NCONUML | phi11 | 19831.48 | 5 | phi
NCONUML | bra13 | 31922.03 | 14 | bra
RESIDENTL | mwl11 | 7113484.1589 | 1047 | mwl
| sle14 | 9929.5555 | 28 | sle
COMMERCIAL | cpk11 | 7316179.79 | 51 | cpk
| cyn31 | 5192.9 | 11 | cyn
NCONUML | epg12 | 1563.57 | 9 | epg
| epg11 | 4794.77 | 9 | epg
INDUSTRIAL | bwa23 | 17470876.21 | 8 | bwa
FARM | cln21 | 792.83 | 1 | cln
COMMERCIAL | wn3 | 8489705.5245 | 275 | wn
COMMERCIAL | bwn12 | 29123057.9665 | 274 | bwn
NCONUML | bra23 | 28962.5293 | 21 | bra
| bge12 | 5967.8256 | 14 | bge
INDUSTRIAL | tgn12 | 464065.58 | 15 | tgn
LIGHTING | fgy31 | 1047083.29 | 1 | fgy
NCONUML | moe25 | 63582.44 | 18 | moe
NCONUML | fgy21 | 30728.13 | 12 | fgy
INDUSTRIAL | lyd11 | 151654.68 | 9 | lyd
FARM | bwn13 | 5960.02 | 1 | bwn
RESIDENTL | lga11 | 6965787.8425 | 1044 | lga
NCONUML | bwr22 | 31744.79 | 14 | bwr
COMMERCIAL | llg12 | 3977405.3306 | 115 | llg
COMMERCIAL | mfa21 | 3716072.0048 | 197 | mfa
INDUSTRIAL | phm32 | 1008.48 | 1 | phm
COMMERCIAL | nrn13 | 3605622.38 | 41 | nrn
FARM | cyn22 | 1131.4275 | 1 | cyn
INDUSTRIAL | ftr23 | 1828762.8842 | 76 | ftr
INDUSTRIAL | mfa31 | 463955.39 | 14 | mfa
INDUSTRIAL | bge11 | 395339.98 | 10 | bge
RESIDENTL | wo13 | 2691801.805 | 586 | wo
RESIDENTL | llg11 | 4969161.4408 | 709 | llg
| cpk21 | 8908.612 | 12 | cpk
INDUSTRIAL | cre23 | 238715.04 | 8 | cre
COMMERCIAL | epg33 | 43303826.6612 | 357 | epg
FARM | ofr21 | 60907.55 | 6 | ofr
COMMERCIAL | cpk22 | 8802072.7366 | 32 | cpk
NCONUML | bra24 | 34184.91 | 27 | bra
NCONUML | wn6 | 84222.69 | 35 | wn
FARM | mfa22 | 15017348.1505 | 702 | mfa
FARM | lga24 | 2675198.7919 | 323 | lga
COMMERCIAL | phi13 | 13565764.588 | 480 | phi
FARM | lga13 | 6142984.8245 | 572 | lga
NCONUML | wn2 | 74469.51 | 25 | wn
COMMERCIAL | wyk23 | 9043742.9219 | 306 | wyk
INDUSTRIAL | cyn31 | 110897.03 | 2 | cyn
RESIDENTL | wt7 | 9398293.9689 | 2293 | wt
COMMERCIAL | rwt15 | 2407529.701 | 118 | rwt
| wots11 | 29868.01 | 43 | wots
COMMERCIAL | wt12 | 9788397.4198 | 246 | wt
FARM | wots24 | 5049980.8194 | 706 | wots
COMMERCIAL | ftr22 | 3919173.7529 | 139 | ftr
INDUSTRIAL | ruba12 | 859698.6565 | 35 | ruba
| wots25 | 37134.4365 | 43 | wots
RESIDENTL | ofr24 | 14317680.0438 | 3420 | ofr
COMMERCIAL | bdl32 | 9327480.3168 | 349 | bdl
NCONUML | trc01 | 2600.11 | 1 | trc
RESIDENTL | wgi33 | 15074294.4922 | 2906 | wgi
RESIDENTL | wyk24 | 16651462.561 | 3130 | wyk
NCONUML | wn1 | 109135.95 | 32 | wn
NCONUML | fgy34 | 69468.4 | 26 | fgy
| tgn43 | 23585.3 | 37 | tgn
| bwn11 | 22540.96 | 33 | bwn
COMMERCIAL | bn11 | 11469939.8143 | 448 | bn
RESIDENTL | wn7 | 334597.06 | 81 | wn
FARM | lga23 | 6580772.0568 | 604 | lga
RESIDENTL | mby13 | 1114988.13 | 129 | mby
INDUSTRIAL | moe12 | 309363.05 | 10 | moe
NCONUML | wgl21 | 72341.71 | 26 | wgl
| rwn22 | 13422.17 | 20 | rwn
FARM | ofr13 | 1726.88 | 2 | ofr
INDUSTRIAL | smg33 | 3791.86 | 1 | smg
COMMERCIAL | cnr2 | 2241662.7301 | 123 | cnr
NCONUML | bwn13 | 114734.08 | 27 | bwn
INDUSTRIAL | tgn43 | 8336.37 | 2 | tgn
NCONUML | bra33 | 54640.5039 | 38 | bra
LIGHTING | drn23 | 137376.82 | 1 | drn
COMMERCIAL | wt11 | 6045415.4763 | 137 | wt
| wo23 | 3425.76 | 13 | wo
RESIDENTL | drn11 | 23689909.4015 | 5897 | drn
RESIDENTL | bra33 | 17227071.6094 | 3920 | bra
FARM | cre21 | 1165190.53 | 9 | cre
| wo32 | 20472.5797 | 26 | wo
NCONUML | mfa22 | 12133.93 | 8 | mfa
COMMERCIAL | fgy32 | 10874129.2215 | 316 | fgy
INDUSTRIAL | bdl33 | 6444229.03 | 34 | bdl
NCONUML | cnr3 | 880.96 | 3 | cnr
COMMERCIAL | bwr14 | 64319.73 | 1 | bwr
NCONUML | ldl11 | 15379.88 | 9 | ldl
FARM | bdl33 | 333127.23 | 48 | bdl
INDUSTRIAL | elm23 | 351538.3612 | 12 | elm
NCONUML | lga14 | 16509.29 | 6 | lga
NCONUML | rwt21 | 45520.76 | 13 | rwt
INDUSTRIAL | mwl24 | 3823292.43 | 15 | mwl
RESIDENTL | epg14 | 8906284.5994 | 2218 | epg
NCONUML | drn21 | 11559.57 | 6 | drn
FARM | ldl21 | 4274.77 | 1 | ldl
| lga14 | 13272.15 | 11 | lga
LIGHTING | wo22 | 1145144.2306 | 3 | wo
LIGHTING | bdl33 | 755365.47 | 1 | bdl
INDUSTRIAL | lga12 | 340570.559 | 7 | lga
RESIDENTL | ofr23 | 20573594.8025 | 3065 | ofr
LIGHTING | tgn12 | 393.8997 | 1 | tgn
RESIDENTL | fgy32 | 4718000.0914 | 1180 | fgy
COMMERCIAL | moe11 | 6876107.6583 | 169 | moe
COMMERCIAL | wgl13 | 16726185.3211 | 289 | wgl
COMMERCIAL | cre22 | 19152716.1468 | 212 | cre
RESIDENTL | drn12 | 16081122.8597 | 3986 | drn
COMMERCIAL | mfa23 | 8005013.26 | 78 | mfa
| cln13 | 39224.5517 | 61 | cln
INDUSTRIAL | mfa22 | 1793714.26 | 36 | mfa
LIGHTING | smr23 | 37560.88 | 1 | smr
RESIDENTL | rwn32 | 6727398.7344 | 1603 | rwn
FARM | lga14 | 4550189.1065 | 436 | lga
| cln12 | 24735.6225 | 51 | cln
COMMERCIAL | kms11 | 4936701.5866 | 120 | kms
RESIDENTL | smr14 | 10997106.9114 | 1697 | smr
| epg13 | 194183.3358 | 102 | epg
| brt21 | 9723.1397 | 7 | brt
INDUSTRIAL | drn12 | 10032.09 | 2 | drn
| tt7 | 34871.95 | 3 | tt
INDUSTRIAL | wots25 | 7153785.931 | 7 | wots
FARM | tgn43 | 14451.81 | 2 | tgn
NCONUML | ldl14 | 38917.21 | 26 | ldl
INDUSTRIAL | brt21 | 238786.6 | 10 | brt
| llg11 | 8477.8 | 10 | llg
RESIDENTL | wgi24 | 12721878.952 | 3596 | wgi
RESIDENTL | cyn21 | 10508542.767 | 2257 | cyn
INDUSTRIAL | bra11 | 3982632.29 | 3 | bra
INDUSTRIAL | phi11 | 184139.3994 | 13 | phi
| hpk24 | 8609.4373 | 14 | hpk
NCONUML | ldl13 | 24965.12 | 22 | ldl
RESIDENTL | hpk21 | 20637351.8958 | 5254 | hpk
RESIDENTL | wgl13 | 19626090.0794 | 4751 | wgl
COMMERCIAL | elm21 | 12124007.57 | 258 | elm
COMMERCIAL | wt13 | 23168272.4303 | 498 | wt
| hpk23 | 55023.71 | 41 | hpk
COMMERCIAL | mdg1 | 1157212.0402 | 52 | mdg
NCONUML | wt11 | 64055.27 | 25 | wt
NCONUML | phm31 | 9383.328 | 4 | phm
COMMERCIAL | bge23 | 4904566.2339 | 176 | bge
NCONUML | smg23 | 17942.69 | 11 | smg
| mwl16 | 4764.4783 | 12 | mwl
COMMERCIAL | hpk12 | 20352329.5415 | 361 | hpk
RESIDENTL | ruba24 | 4395729.6843 | 894 | ruba
COMMERCIAL | nla32 | 3390681.6399 | 175 | nla
NCONUML | lyd12 | 44439.84 | 9 | lyd
| cln22 | 289385.5413 | 85 | cln
NCONUML | cpk21 | 53769.1 | 26 | cpk
| ruba22 | 8482.6526 | 15 | ruba
COMMERCIAL | myt22 | 191990.12 | 18 | myt
RESIDENTL | mby11 | 5261006.6685 | 922 | mby
RESIDENTL | rwn26 | 21195116.3973 | 2454 | rwn
| rwt31 | 14608.62 | 19 | rwt
INDUSTRIAL | epg35 | 1615230.05 | 4 | epg
| bge23 | 30837.693 | 28 | bge
NCONUML | bdl34 | 70291.97 | 25 | bdl
NCONUML | ofr13 | 30258.73 | 11 | ofr
| klk11 | 25230.2094 | 21 | klk
NCONUML | bn12 | 1241.66 | 2 | bn
COMMERCIAL | wgi32 | 5461052.6827 | 195 | wgi
NCONUML | ldl12 | 45990.38 | 14 | ldl
INDUSTRIAL | bra23 | 3394433.4433 | 42 | bra
| wo33 | 4138.8 | 1 | wo
NCONUML | myt12 | 33269.22 | 16 | myt
INDUSTRIAL | ldl11 | 1468879.69 | 10 | ldl
RESIDENTL | msd1 | 8481569.4252 | 1750 | msd
NCONUML | bn11 | 57126.91 | 28 | bn
INDUSTRIAL | ftr12 | 2824402.5 | 31 | ftr
INDUSTRIAL | hpk11 | 29483.41 | 8 | hpk
NCONUML | epg33 | 5589.26 | 2 | epg
COMMERCIAL | wo31 | 10532525.1457 | 139 | wo
| wgl21 | 38182.04 | 53 | wgl
| bge22 | 25062.3495 | 31 | bge
RESIDENTL | tt1 | 171030.69 | 8 | tt
INDUSTRIAL | bwr34 | 134229.36 | 26 | bwr
COMMERCIAL | bra33 | 14409139.6368 | 303 | bra
COMMERCIAL | bdl44 | 4495186.894 | 197 | bdl
| bwn13 | 12482.8878 | 14 | bwn
NCONUML | wn3 | 40552.61 | 16 | wn
NCONUML | smr24 | 41055.27 | 16 | smr
INDUSTRIAL | mwl14 | 4499194.0326 | 50 | mwl
| wots24 | 36833.8626 | 36 | wots
NCONUML | wt12 | 74491.29 | 36 | wt
COMMERCIAL | smg31 | 17181337.4 | 81 | smg
FARM | lyd13 | 146611.14 | 18 | lyd
NCONUML | wots12 | 53576.05 | 15 | wots
INDUSTRIAL | fgy12 | 30820.7097 | 2 | fgy
FARM | myt12 | 4025860.4278 | 600 | myt
INDUSTRIAL | cyn22 | 204983.76 | 12 | cyn
COMMERCIAL | cyn33 | 3196035.4476 | 122 | cyn
COMMERCIAL | mby12 | 1853426.4391 | 89 | mby
NCONUML | tgn43 | 111938.06 | 34 | tgn
NCONUML | wo11 | 17571.55 | 5 | wo
INDUSTRIAL | epg12 | 1405424.52 | 3 | epg
| cf2 | 30699.57 | 2 | cf
COMMERCIAL | llg11 | 3213282.749 | 85 | llg
LIGHTING | rwn24 | 1936572.72 | 3 | rwn
INDUSTRIAL | cln24 | 15633.29 | 3 | cln
FARM | sle31 | 4999785.6618 | 315 | sle
INDUSTRIAL | cf1 | 129164.746 | 4 | cf
| ruba12 | 126134.0367 | 24 | ruba
| bwr12 | 18318.3952 | 15 | bwr
FARM | elm32 | 382389.8968 | 32 | elm
| ofr21 | 113717.1 | 52 | ofr
INDUSTRIAL | wn2 | 282430.54 | 13 | wn
NCONUML | bge22 | 82280.88 | 49 | bge
NCONUML | cnr2 | 33661.17 | 17 | cnr
NCONUML | wots13 | 10386.18 | 6 | wots
FARM | elm24 | 39172.3194 | 4 | elm
COMMERCIAL | nrn14 | 6896476.1265 | 116 | nrn
NCONUML | ruba12 | 27603.68 | 16 | ruba
NCONUML | hpk13 | 50290.3 | 16 | hpk
NCONUML | bra11 | 44798.92 | 35 | bra
| rwt21 | 23376.2409 | 6 | rwt
RESIDENTL | drn23 | 20613814.4846 | 2434 | drn
RESIDENTL | rwt36 | 2676215.9999 | 821 | rwt
RESIDENTL | llg13 | 6857833.0372 | 1230 | llg
COMMERCIAL | wyk12 | 4295149.2844 | 131 | wyk
INDUSTRIAL | ofr13 | 1622296.11 | 21 | ofr
| bra14 | 30334.7783 | 42 | bra
INDUSTRIAL | tgn11 | 3321263.75 | 18 | tgn
LIGHTING | mby13 | 9944.78 | 1 | mby
RESIDENTL | cln11 | 39284605.9906 | 12154 | cln
COMMERCIAL | drn22 | 10741065.2473 | 246 | drn
RESIDENTL | wo32 | 11244170.0715 | 2343 | wo
| bra33 | 27895.4569 | 47 | bra
COMMERCIAL | epg21 | 21867278.1603 | 75 | epg
INDUSTRIAL | cre21 | 293542.6 | 2 | cre
RESIDENTL | bwr24 | 1834966.95 | 415 | bwr
RESIDENTL | hpk13 | 8888406.848 | 2283 | hpk
NCONUML | moe13 | 240.62 | 2 | moe
RESIDENTL | mwl12 | 3605926.3697 | 887 | mwl
| elm24 | 29520.3106 | 27 | elm
COMMERCIAL | tgn31 | 5251765.7474 | 163 | tgn
| rwt25 | 17882.0217 | 23 | rwt
RESIDENTL | moe21 | 9438147.1697 | 1978 | moe
COMMERCIAL | mjg11 | 16973320.0649 | 258 | mjg
COMMERCIAL | moe22 | 1619971.835 | 34 | moe
NCONUML | cpk13 | 44472.2623 | 32 | cpk
| phi11 | 13149.9006 | 9 | phi
FARM | cyn11 | 2814.65 | 1 | cyn
FARM | cyn24 | 25049.8 | 2 | cyn
FARM | drn13 | 379220.8035 | 25 | drn
COMMERCIAL | mwe236 | 663523.2 | 21 | mwe
INDUSTRIAL | phm24 | 35612.08 | 4 | phm
INDUSTRIAL | bge22 | 36211.2493 | 9 | bge
RESIDENTL | cnr1 | 478523.9112 | 104 | cnr
| lga24 | 10918.35 | 11 | lga
NCONUML | sle14 | 98131.7526 | 34 | sle
NCONUML | tt5 | 14462.54 | 12 | tt
| epg12 | 53720.6497 | 70 | epg
NCONUML | kms11 | 42647.24 | 13 | kms
FARM | elm23 | 38507.8 | 8 | elm
COMMERCIAL | cyn12 | 12045879.7132 | 241 | cyn
INDUSTRIAL | fgy23 | 1420677.79 | 11 | fgy
COMMERCIAL | mfa14 | 259168.13 | 17 | mfa
| bra31 | 49797.7422 | 13 | bra
COMMERCIAL | mwl12 | 1780079.4127 | 78 | mwl
| bwr22 | 2405.71 | 25 | bwr
INDUSTRIAL | fgy24 | 415478.9 | 15 | fgy
COMMERCIAL | hpk13 | 9763023.5697 | 134 | hpk
| cyn22 | 22272.33 | 22 | cyn
| ldl21 | 13369.5383 | 42 | ldl
| wt6 | 17591.4373 | 23 | wt
RESIDENTL | wn4 | 11276854.4814 | 2349 | wn
FARM | mwl14 | 451834.7532 | 54 | mwl
RESIDENTL | bm8b31 | 357131.6719 | 111 | bmb
NCONUML | cyn14 | 48577.9677 | 22 | cyn
FARM | cre32 | 5136.47 | 1 | cre
FARM | bwr34 | 4550.33 | 1 | bwr
RESIDENTL | llg14 | 14855712.1657 | 2170 | llg
FARM | smg33 | 29400.19 | 7 | smg
RESIDENTL | drn22 | 21996972.8148 | 3999 | drn
NCONUML | elm32 | 42948.38 | 25 | elm
INDUSTRIAL | klo14 | 587332.99 | 17 | klo
| tgn11 | 22256.53 | 32 | tgn
INDUSTRIAL | tgn44 | 4536032.57 | 9 | tgn
COMMERCIAL | ldl23 | 15994398.5627 | 272 | ldl
| wn6 | 146062.0009 | 59 | wn
COMMERCIAL | tt2 | 18806104.6367 | 399 | tt
COMMERCIAL | brt11 | 4047117.81 | 129 | brt
NCONUML | llg14 | 65195.01 | 40 | llg
FARM | fgy24 | 95940.3 | 9 | fgy
NCONUML | fgy14 | 61562.37 | 33 | fgy
COMMERCIAL | rve12 | 3272242.91 | 54 | rve
INDUSTRIAL | cpk23 | 208291.634 | 5 | cpk
| lga23 | 41697.3391 | 21 | lga
INDUSTRIAL | yn38 | 642769.3081 | 6 | yn
COMMERCIAL | bwa21 | 7920817.52 | 6 | bwa
INDUSTRIAL | elm25 | 2097.04 | 1 | elm
COMMERCIAL | wots13 | 3416108.1488 | 213 | wots
FARM | wgi22 | 191494.2501 | 24 | wgi
NCONUML | fgy13 | 27847.71 | 7 | fgy
| bra24 | 9840.15 | 27 | bra
FARM | ofr14 | 100163.6258 | 21 | ofr
NCONUML | nrn11 | 16820.36 | 5 | nrn
RESIDENTL | smg31 | 12434679.8443 | 2879 | smg
COMMERCIAL | smr24 | 15083854.4686 | 348 | smr
| lyd11 | 12152.66 | 25 | lyd
INDUSTRIAL | bra12 | 1282907.1727 | 55 | bra
FARM | wgl15 | 3297105.6723 | 233 | wgl
INDUSTRIAL | msd1 | 544058.7154 | 15 | msd
| epg31 | 13971.3347 | 31 | epg
INDUSTRIAL | wgl23 | 572354.5027 | 44 | wgl
INDUSTRIAL | cpk12 | 343353.79 | 14 | cpk
INDUSTRIAL | mfa34 | 4790944.63 | 37 | mfa
| wn2 | 65478.1843 | 60 | wn
INDUSTRIAL | drn23 | 222019.33 | 21 | drn
| klo11 | 24997.4 | 1 | klo
COMMERCIAL | cyn13 | 11562540.4133 | 213 | cyn
| tgn44 | 15598.29 | 27 | tgn
| wn1 | 5093 | 9 | wn
NCONUML | wots24 | 22958.48 | 11 | wots
RESIDENTL | ftr21 | 5974099.1685 | 1654 | ftr
NCONUML | wgl11 | 116770.29 | 32 | wgl
FARM | phm22 | 2513172.8482 | 159 | phm
| mfa22 | 25912.0235 | 15 | mfa
| tt2 | 5693.01 | 1 | tt
RESIDENTL | cyn12 | 11384819.6049 | 2642 | cyn
COMMERCIAL | mby11 | 1920906.95 | 83 | mby
RESIDENTL | bdl42 | 7579399.6648 | 1528 | bdl
COMMERCIAL | sle11 | 16789466.3124 | 430 | sle
COMMERCIAL | bdl42 | 3935066.2305 | 228 | bdl
NCONUML | rwn22 | 25304.89 | 19 | rwn
INDUSTRIAL | cre32 | 1414910.91 | 33 | cre
INDUSTRIAL | bwn11 | 121807.37 | 8 | bwn
NCONUML | smr22 | 29006.3 | 13 | smr
RESIDENTL | phm24 | 12991887.5254 | 2975 | phm
RESIDENTL | phm21 | 5600884.0097 | 1319 | phm
NCONUML | ldl23 | 93357.12 | 44 | ldl
RESIDENTL | ldl24 | 19255310.9766 | 3964 | ldl
INDUSTRIAL | bra21 | 9682528.358 | 10 | bra
| sle31 | 21276.5675 | 34 | sle
| myt11 | 11671.01 | 10 | myt
RESIDENTL | elm21 | 10927220.6891 | 2208 | elm
COMMERCIAL | epg13 | 13081700.0195 | 121 | epg
COMMERCIAL | hpk21 | 6771211.022 | 80 | hpk
NCONUML | bwr12 | 55323.1848 | 22 | bwr
| trc01 | 7370.1419 | 1 | trc
| epg35 | 12733.43 | 3 | epg
INDUSTRIAL | bge21 | 30163.23 | 3 | bge
RESIDENTL | tgn31 | 10330935.5842 | 1504 | tgn
COMMERCIAL | moe23 | 8180066.6029 | 204 | moe
FARM | bra21 | 5211.11 | 2 | bra
LIGHTING | llg12 | 9573.66 | 1 | llg
RESIDENTL | bdl31 | 18828777.9984 | 3534 | bdl
COMMERCIAL | nla31 | 1365542.8767 | 73 | nla
INDUSTRIAL | klo24 | 421040.3606 | 14 | klo
FARM | bdl43 | 35833.9 | 4 | bdl
FARM | cyn31 | 3324.08 | 1 | cyn
FARM | sle14 | 508528.62 | 59 | sle
FARM | fgy34 | 3609.3 | 1 | fgy
RESIDENTL | elm26 | 19204314.084 | 3128 | elm
COMMERCIAL | ldl13 | 4974121.0157 | 271 | ldl
NCONUML | tgn42 | 32526.3 | 9 | tgn
RESIDENTL | nrn13 | 11128338.9236 | 2708 | nrn
| drn13 | 33230.29 | 35 | drn
RESIDENTL | mfa14 | 15628.16 | 8 | mfa
RESIDENTL | rwt14 | 5266292.5405 | 1232 | rwt
FARM | ftr23 | 7584335.745 | 587 | ftr
FARM | moe12 | 2890738.1544 | 266 | moe
RESIDENTL | klk21 | 6022162.144 | 692 | klk
COMMERCIAL | bn22 | 11917129.8815 | 407 | bn
COMMERCIAL | cln13 | 10498926.3291 | 102 | cln
INDUSTRIAL | cln11 | 955300.36 | 11 | cln
FARM | bge11 | 1450445.3683 | 132 | bge
| mwl25 | 368.2898 | 2 | mwl
| rwn33 | 13688.96 | 19 | rwn
| bdl43 | 33766.9817 | 15 | bdl
NCONUML | cln14 | 95979.5703 | 31 | cln
NCONUML | lga24 | 7306.35 | 4 | lga
| bn23 | 36133.4118 | 23 | bn
| ofr14 | 18460.3638 | 32 | ofr
FARM | wo14 | 29381.84 | 3 | wo
FARM | cln24 | 15169.45 | 1 | cln
FARM | smg21 | 2813.13 | 1 | smg
FARM | uwy1 | 50419.26 | 6 | uwy
RESIDENTL | cpk11 | 18255270.9798 | 3705 | cpk
INDUSTRIAL | rwn34 | 151721.8975 | 12 | rwn
FARM | mfa34 | 8352796.4311 | 398 | mfa
INDUSTRIAL | cyn23 | 283668.3977 | 39 | cyn
COMMERCIAL | cln23 | 7919442.4187 | 94 | cln
| rwn24 | 145239.1574 | 36 | rwn
INDUSTRIAL | cln21 | 91173.7471 | 8 | cln
INDUSTRIAL | wots23 | 9771996.01 | 2 | wots
COMMERCIAL | ofr23 | 7962081.4442 | 137 | ofr
FARM | cln11 | 5358747.3528 | 175 | cln
INDUSTRIAL | epg23 | 1603069.098 | 49 | epg
NCONUML | elm33 | 106570.09 | 33 | elm
| tt6 | 16214.4725 | 50 | tt
NCONUML | lga12 | 120.31 | 1 | lga
RESIDENTL | moe25 | 15202048.016 | 3044 | moe
RESIDENTL | moe22 | 6183768.6959 | 1343 | moe
RESIDENTL | mfa23 | 1535883.9368 | 206 | mfa
FARM | rwn22 | 76017.25 | 13 | rwn
COMMERCIAL | fgy31 | 26687.08 | 5 | fgy
RESIDENTL | elm33 | 17751529.9107 | 3238 | elm
COMMERCIAL | ldl22 | 7642772.3181 | 272 | ldl
NCONUML | llg11 | 13058.17 | 7 | llg
| ruba24 | 72607.09 | 10 | ruba
FARM | rwt32 | 21924.18 | 3 | rwt
FARM | ruba12 | 5735958.293 | 534 | ruba
FARM | brt21 | 526055.8565 | 65 | brt
| rwt15 | 24735.76 | 50 | rwt
NCONUML | bge13 | 40077 | 45 | bge
COMMERCIAL | klk21 | 1344972.0506 | 75 | klk
INDUSTRIAL | msd4 | 532825.24 | 27 | msd
| mwl21 | 2371.576 | 7 | mwl
RESIDENTL | wt9 | 13126762.7947 | 2901 | wt
FARM | wgi23 | 957555.9102 | 143 | wgi
| wgl24 | 12928.4076 | 27 | wgl
NCONUML | tgn11 | 50804.93 | 14 | tgn
LIGHTING | hpk22 | 402155.12 | 2 | hpk
INDUSTRIAL | wt13 | 198794.34 | 24 | wt
LIGHTING | wots24 | 69082.45 | 1 | wots
| ofr13 | 25120.5182 | 29 | ofr
| cre21 | 98632.2224 | 69 | cre
| smg22 | 13378.71 | 23 | smg
COMMERCIAL | tt4 | 4770691.1401 | 169 | tt
COMMERCIAL | elm26 | 2765254.86 | 47 | elm
NCONUML | bwa22 | 120.31 | 1 | bwa
| cyn23 | 386495.78 | 52 | cyn
INDUSTRIAL | nla34 | 227255.6563 | 13 | nla
FARM | mwl22 | 63.01 | 1 | mwl
| cf1 | 5771.13 | 3 | cf
NCONUML | cpk22 | 15413.02 | 10 | cpk
NCONUML | lyd13 | 28195.47 | 10 | lyd
NCONUML | cre31 | 35482.06 | 18 | cre
COMMERCIAL | wo11 | 6006584.4175 | 54 | wo
INDUSTRIAL | wt7 | 2382042.5333 | 25 | wt
| bwr34 | 19530.96 | 64 | bwr
NCONUML | bge23 | 57838.96 | 34 | bge
INDUSTRIAL | tgn23 | 187420.5 | 24 | tgn
RESIDENTL | cyn33 | 17836008.3498 | 3662 | cyn
RESIDENTL | nla34 | 7124747.0562 | 1408 | nla
| wgl11 | 21820.8596 | 38 | wgl
COMMERCIAL | bn12 | 3658135.6563 | 31 | bn
| mwl13 | 7054.2121 | 17 | mwl
COMMERCIAL | rwt26 | 65754589.65 | 1 | rwt
FARM | wt9 | 2789.4 | 1 | wt
RESIDENTL | bdl44 | 10906570.4152 | 1766 | bdl
FARM | cre33 | 2156267.3416 | 81 | cre
COMMERCIAL | wgl21 | 7364849.9167 | 150 | wgl
COMMERCIAL | wn5 | 3727109.367 | 208 | wn
NCONUML | mwl22 | 81020 | 27 | mwl
NCONUML | bn24 | 14677.57 | 9 | bn
| smr22 | 9887.67 | 15 | smr
|  | 8782.36 | 2 | #REF!
RESIDENTL | sle11 | 5311421.2716 | 1344 | sle
RESIDENTL | nw13 | 126364.0108 | 18 | nw
RESIDENTL | ftr23 | 12909653.9148 | 2620 | ftr
COMMERCIAL | mwl11 | 1278518.3133 | 72 | mwl
LIGHTING | llg13 | 66328.6913 | 1 | llg
NCONUML | klk22 | 2600.11 | 1 | klk
RESIDENTL | wyk23 | 22445865.182 | 3391 | wyk
COMMERCIAL | wt6 | 6354339.6482 | 191 | wt
RESIDENTL | brt11 | 6592458.6386 | 1001 | brt
NCONUML | tt9 | 66916.75 | 41 | tt
FARM | smr14 | 4406259.38 | 487 | smr
NCONUML | epg32 | 55568.91 | 13 | epg
RESIDENTL | rwn31 | 17135173.2235 | 2210 | rwn
| phm33 | 20993.1171 | 27 | phm
NCONUML | myt11 | 6079.5 | 6 | myt
RESIDENTL | nrn12 | 2807836.1314 | 591 | nrn
COMMERCIAL | mwl16 | 411566.3345 | 42 | mwl
INDUSTRIAL | lga23 | 1068068.6578 | 23 | lga
COMMERCIAL | ldl12 | 15390056.6509 | 380 | ldl
FARM | nla34 | 624678.3932 | 78 | nla
COMMERCIAL | rve13 | 1685040.429 | 44 | rve
NCONUML | drn24 | 11009.3526 | 4 | drn
COMMERCIAL | myt21 | 6919383.7104 | 251 | myt
FARM | moe13 | 3478506.4958 | 306 | moe
COMMERCIAL | mwl21 | 9182796.6603 | 240 | mwl
NCONUML | wgl15 | 97647.0301 | 36 | wgl
| bwn14 | 31300.22 | 31 | bwn
RESIDENTL | cpk22 | 8203984.593 | 1482 | cpk
RESIDENTL | rve12 | 17634581.2748 | 3656 | rve
RESIDENTL | phi13 | 17016004.0328 | 4317 | phi
RESIDENTL | hpk12 | 5058413.1519 | 1238 | hpk
COMMERCIAL | ruba24 | 4555190.3466 | 105 | ruba
FARM | cln14 | 51639.06 | 13 | cln
INDUSTRIAL | wt9 | 148098.11 | 5 | wt
| smg21 | 44014.37 | 27 | smg
INDUSTRIAL | smr23 | 883845.12 | 6 | smr

## Forecast - Summer
Forecasting Application - 13/10/2025
asset_type | asset | extremum | scenario | demand_year | season | poe | customer_count | pv_capacity | value | forecast_round | unit | region
zone_sub | cln | maximum |  | 2022 | Summer | 50 | 38619 | 72.2578 | 77.9086 | 202503 | MVA | central
zone_sub | cln | maximum |  | 2022 | Summer | 10 | 38619 | 72.2578 | 91.3183 | 202503 | MVA | central
zone_sub | cln | maximum |  | 2023 | Summer | 10 | 41429 | 81.3604 | 97.5884 | 202503 | MVA | central
zone_sub | cln | maximum |  | 2023 | Summer | 50 | 41429 | 81.3604 | 83.3369 | 202503 | MVA | central
zone_sub | cln | maximum |  | 2024 | Summer | 10 | 44846 | 94.6588 | 104.9463 | 202503 | MVA | central
zone_sub | cln | maximum |  | 2024 | Summer | 50 | 44846 | 94.6588 | 89.7351 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2025 | Summer | 10 |  |  | 119.6766 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2025 | Summer | 50 |  |  | 104.3341 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2026 | Summer | 10 |  |  | 124.2514 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2026 | Summer | 50 |  |  | 108.3435 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2027 | Summer | 10 |  |  | 128.0364 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2027 | Summer | 50 |  |  | 111.4611 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2028 | Summer | 10 |  |  | 131.3686 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2028 | Summer | 50 |  |  | 115.2173 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2029 | Summer | 10 |  |  | 136.7682 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2029 | Summer | 50 |  |  | 119.0984 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2030 | Summer | 10 |  |  | 141.634 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2030 | Summer | 50 |  |  | 123.2461 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2031 | Summer | 10 |  |  | 148.4809 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2031 | Summer | 50 |  |  | 128.0275 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2032 | Summer | 10 |  |  | 155.6302 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2032 | Summer | 50 |  |  | 133.6994 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2033 | Summer | 10 |  |  | 161.4365 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2033 | Summer | 50 |  |  | 139.0092 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2034 | Summer | 10 |  |  | 166.8996 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2034 | Summer | 50 |  |  | 144.6013 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2035 | Summer | 10 |  |  | 175.1342 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2035 | Summer | 50 |  |  | 154.2938 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2036 | Summer | 10 |  |  | 181.0486 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2036 | Summer | 50 |  |  | 157.43 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2037 | Summer | 10 |  |  | 187.0195 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2037 | Summer | 50 |  |  | 163.5566 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2038 | Summer | 10 |  |  | 193.3671 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2038 | Summer | 50 |  |  | 168.1999 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2039 | Summer | 10 |  |  | 192.0421 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2039 | Summer | 50 |  |  | 167.0472 | 202503 | MVA | central
zone_sub | cre | maximum |  | 2022 | Summer | 10 | 24937 | 39.5122 | 71.3044 | 202503 | MVA | central
zone_sub | cre | maximum |  | 2022 | Summer | 50 | 24937 | 39.5122 | 64.1683 | 202503 | MVA | central
zone_sub | cre | maximum |  | 2023 | Summer | 10 | 25835 | 43.8704 | 73.6781 | 202503 | MVA | central
zone_sub | cre | maximum |  | 2023 | Summer | 50 | 25835 | 43.8704 | 65.8328 | 202503 | MVA | central
zone_sub | cre | maximum |  | 2024 | Summer | 10 | 26314 | 48.9572 | 74.7994 | 202503 | MVA | central
zone_sub | cre | maximum |  | 2024 | Summer | 50 | 26314 | 48.9572 | 66.0879 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2025 | Summer | 10 |  |  | 89.8342 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2025 | Summer | 50 |  |  | 80.6612 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2026 | Summer | 10 |  |  | 90.653 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2026 | Summer | 50 |  |  | 81.4056 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2027 | Summer | 10 |  |  | 89.7773 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2027 | Summer | 50 |  |  | 80.6131 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2028 | Summer | 10 |  |  | 94.9573 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2028 | Summer | 50 |  |  | 85.9509 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2029 | Summer | 10 |  |  | 94.8385 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2029 | Summer | 50 |  |  | 85.6114 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2030 | Summer | 10 |  |  | 96.1186 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2030 | Summer | 50 |  |  | 85.7941 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2031 | Summer | 10 |  |  | 97.2062 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2031 | Summer | 50 |  |  | 86.4866 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2032 | Summer | 10 |  |  | 98.0786 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2032 | Summer | 50 |  |  | 87.2925 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2033 | Summer | 10 |  |  | 98.8781 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2033 | Summer | 50 |  |  | 88.2343 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2034 | Summer | 10 |  |  | 99.6475 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2034 | Summer | 50 |  |  | 88.9575 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2035 | Summer | 10 |  |  | 99.2707 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2035 | Summer | 50 |  |  | 89.8044 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2036 | Summer | 10 |  |  | 99.9981 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2036 | Summer | 50 |  |  | 89.5675 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2037 | Summer | 10 |  |  | 101.1509 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2037 | Summer | 50 |  |  | 90.5821 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2038 | Summer | 10 |  |  | 101.3208 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2038 | Summer | 50 |  |  | 90.3196 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2039 | Summer | 10 |  |  | 99.6095 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2039 | Summer | 50 |  |  | 88.5146 | 202503 | MVA | central
zone_sub | epg | maximum |  | 2022 | Summer | 10 | 29371 | 40.0067 | 87.2498 | 202503 | MVA | central
zone_sub | epg | maximum |  | 2022 | Summer | 50 | 29371 | 40.0067 | 72.9666 | 202503 | MVA | central
zone_sub | epg | maximum |  | 2023 | Summer | 10 | 30422 | 45.1511 | 90.3071 | 202503 | MVA | central
zone_sub | epg | maximum |  | 2023 | Summer | 50 | 30422 | 45.1511 | 75.7012 | 202503 | MVA | central
zone_sub | epg | maximum |  | 2024 | Summer | 10 | 32118 | 51.557 | 95.8895 | 202503 | MVA | central
zone_sub | epg | maximum |  | 2024 | Summer | 50 | 32118 | 51.557 | 79.9844 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2025 | Summer | 10 |  |  | 109.0669 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2025 | Summer | 50 |  |  | 92.5622 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2026 | Summer | 10 |  |  | 118.5447 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2026 | Summer | 50 |  |  | 101.6723 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2027 | Summer | 10 |  |  | 121.4869 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2027 | Summer | 50 |  |  | 104.4042 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2028 | Summer | 10 |  |  | 119.8786 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2028 | Summer | 50 |  |  | 102.6031 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2029 | Summer | 10 |  |  | 121.9204 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2029 | Summer | 50 |  |  | 105.5757 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2030 | Summer | 10 |  |  | 124.6444 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2030 | Summer | 50 |  |  | 106.371 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2031 | Summer | 10 |  |  | 127.5507 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2031 | Summer | 50 |  |  | 110.1341 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2032 | Summer | 10 |  |  | 131.8742 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2032 | Summer | 50 |  |  | 112.2581 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2033 | Summer | 10 |  |  | 136.3355 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2033 | Summer | 50 |  |  | 113.9316 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2034 | Summer | 10 |  |  | 140.9437 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2034 | Summer | 50 |  |  | 117.5793 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2035 | Summer | 10 |  |  | 144.5914 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2035 | Summer | 50 |  |  | 120.4726 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2036 | Summer | 50 |  |  | 128.0797 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2036 | Summer | 10 |  |  | 149.6115 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2037 | Summer | 10 |  |  | 152.9797 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2037 | Summer | 50 |  |  | 129.922 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2038 | Summer | 10 |  |  | 155.1715 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2038 | Summer | 50 |  |  | 132.5568 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2039 | Summer | 10 |  |  | 152.1644 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2039 | Summer | 50 |  |  | 125.7761 | 202503 | MVA | central
zone_sub | klo | maximum |  | 2022 | Summer | 10 | 14879 | 23.0226 | 53.5677 | 202503 | MVA | central
zone_sub | klo | maximum |  | 2022 | Summer | 50 | 14879 | 23.0226 | 41.9423 | 202503 | MVA | central
zone_sub | klo | maximum |  | 2023 | Summer | 10 | 17175 | 27.7177 | 61.121 | 202503 | MVA | central
zone_sub | klo | maximum |  | 2023 | Summer | 50 | 17175 | 27.7177 | 48.3019 | 202503 | MVA | central
zone_sub | klo | maximum |  | 2024 | Summer | 10 | 19951 | 34.2052 | 70.1897 | 202503 | MVA | central
zone_sub | klo | maximum |  | 2024 | Summer | 50 | 19951 | 34.2052 | 55.7613 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2025 | Summer | 10 |  |  | 83.6879 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2025 | Summer | 50 |  |  | 68.2523 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2026 | Summer | 10 |  |  | 94.1984 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2026 | Summer | 50 |  |  | 77.9353 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2027 | Summer | 10 |  |  | 102.4436 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2027 | Summer | 50 |  |  | 84.7194 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2028 | Summer | 10 |  |  | 118.3247 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2028 | Summer | 50 |  |  | 99.6669 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2029 | Summer | 10 |  |  | 126.3487 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2029 | Summer | 50 |  |  | 106.8624 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2030 | Summer | 10 |  |  | 135.5692 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2030 | Summer | 50 |  |  | 115.5707 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2031 | Summer | 10 |  |  | 148.561 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2031 | Summer | 50 |  |  | 127.0156 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2032 | Summer | 10 |  |  | 164.8827 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2032 | Summer | 50 |  |  | 137.8179 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2033 | Summer | 10 |  |  | 180.5841 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2033 | Summer | 50 |  |  | 151.2391 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2034 | Summer | 10 |  |  | 196.9964 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2034 | Summer | 50 |  |  | 164.8814 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2035 | Summer | 10 |  |  | 212.9758 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2035 | Summer | 50 |  |  | 181.5355 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2036 | Summer | 10 |  |  | 230.0573 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2036 | Summer | 50 |  |  | 195.8954 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2037 | Summer | 10 |  |  | 248.4456 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2037 | Summer | 50 |  |  | 212.2991 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2038 | Summer | 10 |  |  | 266.5409 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2038 | Summer | 50 |  |  | 225.6959 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2039 | Summer | 10 |  |  | 272.6357 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2039 | Summer | 50 |  |  | 228.9049 | 202503 | MVA | central
zone_sub | ofr | maximum |  | 2022 | Summer | 10 | 23246 | 35.5119 | 59.9776 | 202503 | MVA | central
zone_sub | ofr | maximum |  | 2022 | Summer | 50 | 23246 | 35.5119 | 53.856 | 202503 | MVA | central
zone_sub | ofr | maximum |  | 2023 | Summer | 10 | 24109 | 39.5748 | 62.0639 | 202503 | MVA | central
zone_sub | ofr | maximum |  | 2023 | Summer | 50 | 24109 | 39.5748 | 55.451 | 202503 | MVA | central
zone_sub | ofr | maximum |  | 2024 | Summer | 10 | 24997 | 44.4669 | 64.073 | 202503 | MVA | central
zone_sub | ofr | maximum |  | 2024 | Summer | 50 | 24997 | 44.4669 | 56.9594 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2025 | Summer | 10 |  |  | 69.589 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2025 | Summer | 50 |  |  | 61.9907 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2026 | Summer | 10 |  |  | 76.597 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2026 | Summer | 50 |  |  | 68.9791 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2027 | Summer | 10 |  |  | 81.5678 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2027 | Summer | 50 |  |  | 74.0072 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2028 | Summer | 10 |  |  | 84.5283 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2028 | Summer | 50 |  |  | 76.6284 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2029 | Summer | 10 |  |  | 86.8984 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2029 | Summer | 50 |  |  | 78.9811 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2030 | Summer | 10 |  |  | 88.8048 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2030 | Summer | 50 |  |  | 80.4506 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2031 | Summer | 10 |  |  | 90.6365 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2031 | Summer | 50 |  |  | 82.1352 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2032 | Summer | 10 |  |  | 92.2256 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2032 | Summer | 50 |  |  | 83.4813 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2033 | Summer | 10 |  |  | 92.9929 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2033 | Summer | 50 |  |  | 84.3346 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2034 | Summer | 10 |  |  | 94.1573 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2034 | Summer | 50 |  |  | 86.446 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2035 | Summer | 10 |  |  | 95.4952 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2035 | Summer | 50 |  |  | 87.894 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2036 | Summer | 10 |  |  | 96.8516 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2036 | Summer | 50 |  |  | 88.627 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2037 | Summer | 10 |  |  | 98.5806 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2037 | Summer | 50 |  |  | 90.0391 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2038 | Summer | 10 |  |  | 98.8168 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2038 | Summer | 50 |  |  | 89.5765 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2039 | Summer | 10 |  |  | 97.8239 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2039 | Summer | 50 |  |  | 88.3981 | 202503 | MVA | central
zone_sub | phm | maximum |  | 2022 | Summer | 50 | 16270 | 23.521 | 51.4174 | 202503 | MVA | central
zone_sub | phm | maximum |  | 2022 | Summer | 10 | 16270 | 23.521 | 56.9097 | 202503 | MVA | central
zone_sub | phm | maximum |  | 2023 | Summer | 10 | 16562 | 25.5412 | 57.758 | 202503 | MVA | central
zone_sub | phm | maximum |  | 2023 | Summer | 50 | 16562 | 25.5412 | 52.1386 | 202503 | MVA | central
zone_sub | phm | maximum |  | 2024 | Summer | 10 | 16854 | 27.7496 | 58.7282 | 202503 | MVA | central
zone_sub | phm | maximum |  | 2024 | Summer | 50 | 16854 | 27.7496 | 52.8621 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2025 | Summer | 10 |  |  | 75.5207 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2025 | Summer | 50 |  |  | 69.621 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2026 | Summer | 10 |  |  | 79.8845 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2026 | Summer | 50 |  |  | 74.1527 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2027 | Summer | 10 |  |  | 79.6008 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2027 | Summer | 50 |  |  | 73.9998 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2028 | Summer | 10 |  |  | 79.5894 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2028 | Summer | 50 |  |  | 73.965 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2029 | Summer | 10 |  |  | 80.0199 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2029 | Summer | 50 |  |  | 74.4648 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2030 | Summer | 10 |  |  | 81.1895 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2030 | Summer | 50 |  |  | 75.0153 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2031 | Summer | 10 |  |  | 81.9552 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2031 | Summer | 50 |  |  | 76.1566 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2032 | Summer | 10 |  |  | 82.7146 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2032 | Summer | 50 |  |  | 76.9783 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2033 | Summer | 10 |  |  | 83.6062 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2033 | Summer | 50 |  |  | 77.4148 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2034 | Summer | 10 |  |  | 84.4206 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2034 | Summer | 50 |  |  | 77.8841 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2035 | Summer | 10 |  |  | 85.2206 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2035 | Summer | 50 |  |  | 78.3211 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2036 | Summer | 10 |  |  | 85.2937 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2036 | Summer | 50 |  |  | 79.127 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2037 | Summer | 10 |  |  | 86.2309 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2037 | Summer | 50 |  |  | 80.1321 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2038 | Summer | 10 |  |  | 85.4841 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2038 | Summer | 50 |  |  | 80.0404 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2039 | Summer | 10 |  |  | 79.3417 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2039 | Summer | 50 |  |  | 73.3195 | 202503 | MVA | central
zone_sub | llg | maximum |  | 2022 | Summer | 10 | 7174 | 11.5134 | 25.3928 | 202503 | MVA | central
zone_sub | llg | maximum |  | 2022 | Summer | 50 | 7174 | 11.5134 | 23.4346 | 202503 | MVA | central
zone_sub | llg | maximum |  | 2023 | Summer | 10 | 7235 | 12.7349 | 25.4543 | 202503 | MVA | central
zone_sub | llg | maximum |  | 2023 | Summer | 50 | 7235 | 12.7349 | 23.4406 | 202503 | MVA | central
zone_sub | llg | maximum |  | 2024 | Summer | 10 | 7295 | 13.7538 | 25.544 | 202503 | MVA | central
zone_sub | llg | maximum |  | 2024 | Summer | 50 | 7295 | 13.7538 | 23.5081 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2025 | Summer | 10 |  |  | 28.7312 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2025 | Summer | 50 |  |  | 26.0976 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2026 | Summer | 10 |  |  | 33.0834 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2026 | Summer | 50 |  |  | 30.4575 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2027 | Summer | 10 |  |  | 33.0249 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2027 | Summer | 50 |  |  | 30.4247 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2028 | Summer | 10 |  |  | 33.0633 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2028 | Summer | 50 |  |  | 30.3952 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2029 | Summer | 10 |  |  | 33.1822 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2029 | Summer | 50 |  |  | 30.8677 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2030 | Summer | 10 |  |  | 33.5865 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2030 | Summer | 50 |  |  | 31.5616 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2031 | Summer | 10 |  |  | 33.8573 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2031 | Summer | 50 |  |  | 32.037 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2032 | Summer | 10 |  |  | 34.0794 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2032 | Summer | 50 |  |  | 31.4591 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2033 | Summer | 10 |  |  | 34.1121 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2033 | Summer | 50 |  |  | 31.5166 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2034 | Summer | 10 |  |  | 34.3124 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2034 | Summer | 50 |  |  | 31.792 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2035 | Summer | 10 |  |  | 34.3834 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2035 | Summer | 50 |  |  | 32.8827 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2036 | Summer | 10 |  |  | 34.3832 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2036 | Summer | 50 |  |  | 31.8492 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2037 | Summer | 10 |  |  | 34.3374 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2037 | Summer | 50 |  |  | 31.7885 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2038 | Summer | 10 |  |  | 34.3276 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2038 | Summer | 50 |  |  | 31.7234 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2039 | Summer | 10 |  |  | 32.6827 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2039 | Summer | 50 |  |  | 30.3101 | 202503 | MVA | central
zone_sub | wgi | maximum |  | 2022 | Summer | 10 | 21696 | 27.3902 | 50.299 | 202503 | MVA | east
zone_sub | wgi | maximum |  | 2022 | Summer | 50 | 21696 | 27.3902 | 41.2414 | 202503 | MVA | east
zone_sub | wgi | maximum |  | 2023 | Summer | 10 | 22045 | 30.4273 | 50.6919 | 202503 | MVA | east
zone_sub | wgi | maximum |  | 2023 | Summer | 50 | 22045 | 30.4273 | 41.4384 | 202503 | MVA | east
zone_sub | wgi | maximum |  | 2024 | Summer | 10 | 22388 | 33.5461 | 51.0465 | 202503 | MVA | east
zone_sub | wgi | maximum |  | 2024 | Summer | 50 | 22388 | 33.5461 | 41.5121 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2025 | Summer | 10 |  |  | 54.5057 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2025 | Summer | 50 |  |  | 44.6075 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2026 | Summer | 10 |  |  | 54.6012 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2026 | Summer | 50 |  |  | 44.9185 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2027 | Summer | 10 |  |  | 54.4983 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2027 | Summer | 50 |  |  | 44.7661 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2028 | Summer | 10 |  |  | 54.5247 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2028 | Summer | 50 |  |  | 44.911 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2029 | Summer | 10 |  |  | 54.7136 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2029 | Summer | 50 |  |  | 44.9706 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2030 | Summer | 10 |  |  | 55.0965 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2030 | Summer | 50 |  |  | 45.1615 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2031 | Summer | 10 |  |  | 55.7707 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2031 | Summer | 50 |  |  | 45.5541 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2032 | Summer | 50 |  |  | 45.8843 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2032 | Summer | 10 |  |  | 56.122 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2033 | Summer | 10 |  |  | 56.3761 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2033 | Summer | 50 |  |  | 46.0363 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2034 | Summer | 10 |  |  | 56.7608 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2034 | Summer | 50 |  |  | 45.9008 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2035 | Summer | 10 |  |  | 57.2519 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2035 | Summer | 50 |  |  | 46.4689 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2036 | Summer | 10 |  |  | 57.8457 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2036 | Summer | 50 |  |  | 46.559 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2037 | Summer | 10 |  |  | 58.1569 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2037 | Summer | 50 |  |  | 46.4523 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2038 | Summer | 10 |  |  | 58.056 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2038 | Summer | 50 |  |  | 46.6661 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2039 | Summer | 10 |  |  | 56.811 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2039 | Summer | 50 |  |  | 45.5652 | 202503 | MVA | east

## Forecast- Winter
Forecasting Application - 13/10/2025
asset_type | asset | extremum | scenario | demand_year | season | poe | customer_count | pv_capacity | value | forecast_round | unit | region
zone_sub | cln | maximum |  | 2022 | Winter | 10 | 38619 | 72.2578 | 63.0362 | 202503 | MVA | central
zone_sub | cln | maximum |  | 2022 | Winter | 50 | 38619 | 72.2578 | 58.8161 | 202503 | MVA | central
zone_sub | cln | maximum |  | 2023 | Winter | 10 | 41429 | 81.3604 | 67.9918 | 202503 | MVA | central
zone_sub | cln | maximum |  | 2023 | Winter | 50 | 41429 | 81.3604 | 63.4647 | 202503 | MVA | central
zone_sub | cln | maximum |  | 2024 | Winter | 10 | 44846 | 94.6588 | 74.018 | 202503 | MVA | central
zone_sub | cln | maximum |  | 2024 | Winter | 50 | 44846 | 94.6588 | 69.1182 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2025 | Winter | 10 |  |  | 89.4372 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2025 | Winter | 50 |  |  | 84.5179 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2026 | Winter | 10 |  |  | 93.2911 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2026 | Winter | 50 |  |  | 88.1502 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2027 | Winter | 10 |  |  | 98.0701 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2027 | Winter | 50 |  |  | 92.8679 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2028 | Winter | 10 |  |  | 102.5171 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2028 | Winter | 50 |  |  | 97.437 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2029 | Winter | 10 |  |  | 107.2692 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2029 | Winter | 50 |  |  | 101.4753 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2030 | Winter | 10 |  |  | 112.2902 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2030 | Winter | 50 |  |  | 107.1286 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2031 | Winter | 10 |  |  | 119.5588 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2031 | Winter | 50 |  |  | 113.3315 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2032 | Winter | 10 |  |  | 125.8642 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2032 | Winter | 50 |  |  | 119.6901 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2033 | Winter | 10 |  |  | 131.807 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2033 | Winter | 50 |  |  | 125.9989 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2034 | Winter | 10 |  |  | 137.993 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2034 | Winter | 50 |  |  | 131.579 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2035 | Winter | 10 |  |  | 145.465 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2035 | Winter | 50 |  |  | 137.6925 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2036 | Winter | 10 |  |  | 147.8036 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2036 | Winter | 50 |  |  | 139.8743 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2037 | Winter | 10 |  |  | 155.8793 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2037 | Winter | 50 |  |  | 147.8441 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2038 | Winter | 10 |  |  | 163.4009 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2038 | Winter | 50 |  |  | 156.1056 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2039 | Winter | 10 |  |  | 133.5693 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2039 | Winter | 50 |  |  | 127.2077 | 202503 | MVA | central
zone_sub | cre | maximum |  | 2022 | Winter | 10 | 24937 | 39.5122 | 50.635 | 202503 | MVA | central
zone_sub | cre | maximum |  | 2022 | Winter | 50 | 24937 | 39.5122 | 48.3881 | 202503 | MVA | central
zone_sub | cre | maximum |  | 2023 | Winter | 10 | 25835 | 43.8704 | 52.4586 | 202503 | MVA | central
zone_sub | cre | maximum |  | 2023 | Winter | 50 | 25835 | 43.8704 | 50.1308 | 202503 | MVA | central
zone_sub | cre | maximum |  | 2024 | Winter | 10 | 26314 | 48.9572 | 53.4328 | 202503 | MVA | central
zone_sub | cre | maximum |  | 2024 | Winter | 50 | 26314 | 48.9572 | 51.0617 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2025 | Winter | 10 |  |  | 68.4471 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2025 | Winter | 50 |  |  | 65.7336 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2026 | Winter | 10 |  |  | 69.4459 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2026 | Winter | 50 |  |  | 66.605 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2027 | Winter | 10 |  |  | 69.249 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2027 | Winter | 50 |  |  | 66.728 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2028 | Winter | 10 |  |  | 74.3386 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2028 | Winter | 50 |  |  | 72.0847 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2029 | Winter | 10 |  |  | 74.5773 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2029 | Winter | 50 |  |  | 72.2361 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2030 | Winter | 10 |  |  | 76.3193 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2030 | Winter | 50 |  |  | 74.0669 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2031 | Winter | 10 |  |  | 77.7248 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2031 | Winter | 50 |  |  | 75.6012 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2032 | Winter | 10 |  |  | 79.2116 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2032 | Winter | 50 |  |  | 76.7507 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2033 | Winter | 10 |  |  | 79.7367 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2033 | Winter | 50 |  |  | 77.8762 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2034 | Winter | 10 |  |  | 80.3545 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2034 | Winter | 50 |  |  | 78.6625 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2035 | Winter | 10 |  |  | 81.081 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2035 | Winter | 50 |  |  | 79.0014 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2036 | Winter | 10 |  |  | 80.0375 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2036 | Winter | 50 |  |  | 78.1499 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2037 | Winter | 10 |  |  | 83.4116 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2037 | Winter | 50 |  |  | 80.9567 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2038 | Winter | 10 |  |  | 84.3767 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2038 | Winter | 50 |  |  | 81.4995 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2039 | Winter | 10 |  |  | 72.4681 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2039 | Winter | 50 |  |  | 69.0004 | 202503 | MVA | central
zone_sub | epg | maximum |  | 2022 | Winter | 10 | 29371 | 40.0067 | 65.9271 | 202503 | MVA | central
zone_sub | epg | maximum |  | 2022 | Winter | 50 | 29371 | 40.0067 | 59.4269 | 202503 | MVA | central
zone_sub | epg | maximum |  | 2023 | Winter | 10 | 30422 | 45.1511 | 68.3101 | 202503 | MVA | central
zone_sub | epg | maximum |  | 2023 | Winter | 50 | 30422 | 45.1511 | 61.7598 | 202503 | MVA | central
zone_sub | epg | maximum |  | 2024 | Winter | 50 | 32118 | 51.557 | 65.5719 | 202503 | MVA | central
zone_sub | epg | maximum |  | 2024 | Winter | 10 | 32118 | 51.557 | 72.1952 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2025 | Winter | 10 |  |  | 85.9871 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2025 | Winter | 50 |  |  | 79.3939 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2026 | Winter | 10 |  |  | 95.0802 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2026 | Winter | 50 |  |  | 89.3565 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2027 | Winter | 10 |  |  | 100.5082 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2027 | Winter | 50 |  |  | 92.7492 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2028 | Winter | 10 |  |  | 99.8778 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2028 | Winter | 50 |  |  | 93.3308 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2029 | Winter | 10 |  |  | 103.1049 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2029 | Winter | 50 |  |  | 96.5577 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2030 | Winter | 10 |  |  | 109.1359 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2030 | Winter | 50 |  |  | 102.3455 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2031 | Winter | 10 |  |  | 112.51 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2031 | Winter | 50 |  |  | 104.2867 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2032 | Winter | 10 |  |  | 121.7799 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2032 | Winter | 50 |  |  | 114.0182 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2033 | Winter | 10 |  |  | 127.6696 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2033 | Winter | 50 |  |  | 119.7255 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2034 | Winter | 10 |  |  | 133.3287 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2034 | Winter | 50 |  |  | 125.5482 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2035 | Winter | 10 |  |  | 135.1129 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2035 | Winter | 50 |  |  | 126.6853 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2036 | Winter | 10 |  |  | 142.2751 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2036 | Winter | 50 |  |  | 134.3407 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2037 | Winter | 10 |  |  | 149.629 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2037 | Winter | 50 |  |  | 142.1357 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2038 | Winter | 10 |  |  | 150.109 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2038 | Winter | 50 |  |  | 141.9626 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2039 | Winter | 10 |  |  | 116.0207 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2039 | Winter | 50 |  |  | 101.3122 | 202503 | MVA | central
zone_sub | klo | maximum |  | 2022 | Winter | 10 | 14879 | 23.0226 | 48.7862 | 202503 | MVA | central
zone_sub | klo | maximum |  | 2022 | Winter | 50 | 14879 | 23.0226 | 43.3886 | 202503 | MVA | central
zone_sub | klo | maximum |  | 2023 | Winter | 10 | 17175 | 27.7177 | 56.3067 | 202503 | MVA | central
zone_sub | klo | maximum |  | 2023 | Winter | 50 | 17175 | 27.7177 | 50.077 | 202503 | MVA | central
zone_sub | klo | maximum |  | 2024 | Winter | 10 | 19951 | 34.2052 | 65.4015 | 202503 | MVA | central
zone_sub | klo | maximum |  | 2024 | Winter | 50 | 19951 | 34.2052 | 58.1655 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2025 | Winter | 10 |  |  | 79.8942 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2025 | Winter | 50 |  |  | 72.3119 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2026 | Winter | 10 |  |  | 92.3723 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2026 | Winter | 50 |  |  | 83.7626 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2027 | Winter | 10 |  |  | 102.9502 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2027 | Winter | 50 |  |  | 93.3778 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2028 | Winter | 10 |  |  | 120.3965 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2028 | Winter | 50 |  |  | 109.8362 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2029 | Winter | 10 |  |  | 129.7211 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2029 | Winter | 50 |  |  | 118.6301 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2030 | Winter | 10 |  |  | 142.5707 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2030 | Winter | 50 |  |  | 129.8167 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2031 | Winter | 10 |  |  | 159.4027 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2031 | Winter | 50 |  |  | 143.8497 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2032 | Winter | 10 |  |  | 178.8568 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2032 | Winter | 50 |  |  | 161.743 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2033 | Winter | 10 |  |  | 196.8658 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2033 | Winter | 50 |  |  | 178.8635 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2034 | Winter | 10 |  |  | 214.3536 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2034 | Winter | 50 |  |  | 194.8729 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2035 | Winter | 10 |  |  | 235.0946 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2035 | Winter | 50 |  |  | 213.0243 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2036 | Winter | 10 |  |  | 246.5584 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2036 | Winter | 50 |  |  | 225.0657 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2037 | Winter | 10 |  |  | 273.2503 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2037 | Winter | 50 |  |  | 249.8153 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2038 | Winter | 10 |  |  | 298.8878 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2038 | Winter | 50 |  |  | 271.7276 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2039 | Winter | 10 |  |  | 252.4111 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2039 | Winter | 50 |  |  | 227.0702 | 202503 | MVA | central
zone_sub | llg | maximum |  | 2022 | Winter | 10 | 7174 | 11.5134 | 22.426 | 202503 | MVA | central
zone_sub | llg | maximum |  | 2022 | Winter | 50 | 7174 | 11.5134 | 20.2322 | 202503 | MVA | central
zone_sub | llg | maximum |  | 2023 | Winter | 10 | 7235 | 12.7349 | 22.5982 | 202503 | MVA | central
zone_sub | llg | maximum |  | 2023 | Winter | 50 | 7235 | 12.7349 | 20.4035 | 202503 | MVA | central
zone_sub | llg | maximum |  | 2024 | Winter | 10 | 7295 | 13.7538 | 22.7705 | 202503 | MVA | central
zone_sub | llg | maximum |  | 2024 | Winter | 50 | 7295 | 13.7538 | 20.5738 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2025 | Winter | 10 |  |  | 26.1225 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2025 | Winter | 50 |  |  | 23.9159 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2026 | Winter | 10 |  |  | 30.6829 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2026 | Winter | 50 |  |  | 28.4398 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2027 | Winter | 10 |  |  | 31.049 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2027 | Winter | 50 |  |  | 28.8402 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2028 | Winter | 10 |  |  | 31.3064 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2028 | Winter | 50 |  |  | 29.108 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2029 | Winter | 10 |  |  | 31.5714 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2029 | Winter | 50 |  |  | 29.4846 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2030 | Winter | 10 |  |  | 32.5932 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2030 | Winter | 50 |  |  | 30.3426 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2031 | Winter | 10 |  |  | 33.1905 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2031 | Winter | 50 |  |  | 31.0163 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2032 | Winter | 10 |  |  | 33.8014 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2032 | Winter | 50 |  |  | 31.6154 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2033 | Winter | 10 |  |  | 34.0793 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2033 | Winter | 50 |  |  | 31.8255 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2034 | Winter | 10 |  |  | 34.2253 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2034 | Winter | 50 |  |  | 32.0656 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2035 | Winter | 10 |  |  | 33.7185 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2035 | Winter | 50 |  |  | 31.7299 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2036 | Winter | 10 |  |  | 33.9832 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2036 | Winter | 50 |  |  | 31.9069 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2037 | Winter | 10 |  |  | 34.9987 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2037 | Winter | 50 |  |  | 32.7389 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2038 | Winter | 10 |  |  | 34.5209 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2038 | Winter | 50 |  |  | 32.3709 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2039 | Winter | 10 |  |  | 28.3277 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2039 | Winter | 50 |  |  | 26.2847 | 202503 | MVA | central
zone_sub | ofr | maximum |  | 2022 | Winter | 10 | 23246 | 35.5119 | 49.8939 | 202503 | MVA | central
zone_sub | ofr | maximum |  | 2022 | Winter | 50 | 23246 | 35.5119 | 46.8764 | 202503 | MVA | central
zone_sub | ofr | maximum |  | 2023 | Winter | 10 | 24109 | 39.5748 | 51.7437 | 202503 | MVA | central
zone_sub | ofr | maximum |  | 2023 | Winter | 50 | 24109 | 39.5748 | 48.6149 | 202503 | MVA | central
zone_sub | ofr | maximum |  | 2024 | Winter | 10 | 24997 | 44.4669 | 53.6497 | 202503 | MVA | central
zone_sub | ofr | maximum |  | 2024 | Winter | 50 | 24997 | 44.4669 | 50.4065 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2025 | Winter | 10 |  |  | 59.4536 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2025 | Winter | 50 |  |  | 56.1183 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2026 | Winter | 10 |  |  | 66.5595 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2026 | Winter | 50 |  |  | 63.2802 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2027 | Winter | 10 |  |  | 72.8129 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2027 | Winter | 50 |  |  | 69.3039 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2028 | Winter | 10 |  |  | 76.0509 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2028 | Winter | 50 |  |  | 72.5305 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2029 | Winter | 10 |  |  | 78.6773 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2029 | Winter | 50 |  |  | 74.8582 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2030 | Winter | 10 |  |  | 81.1629 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2030 | Winter | 50 |  |  | 77.5373 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2031 | Winter | 10 |  |  | 83.2732 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2031 | Winter | 50 |  |  | 79.5294 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2032 | Winter | 10 |  |  | 85.4834 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2032 | Winter | 50 |  |  | 81.7407 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2033 | Winter | 10 |  |  | 86.4197 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2033 | Winter | 50 |  |  | 82.8706 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2034 | Winter | 10 |  |  | 87.7259 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2034 | Winter | 50 |  |  | 83.8526 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2035 | Winter | 10 |  |  | 90.1815 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2035 | Winter | 50 |  |  | 86.3425 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2036 | Winter | 10 |  |  | 89.3155 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2036 | Winter | 50 |  |  | 84.7668 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2037 | Winter | 10 |  |  | 92.5351 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2037 | Winter | 50 |  |  | 88.8524 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2038 | Winter | 10 |  |  | 94.3753 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2038 | Winter | 50 |  |  | 94.1939 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2039 | Winter | 10 |  |  | 80.6717 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2039 | Winter | 50 |  |  | 77.1549 | 202503 | MVA | central
zone_sub | phm | maximum |  | 2022 | Winter | 10 | 16270 | 23.521 | 48.1658 | 202503 | MVA | central
zone_sub | phm | maximum |  | 2022 | Winter | 50 | 16270 | 23.521 | 45.1092 | 202503 | MVA | central
zone_sub | phm | maximum |  | 2023 | Winter | 10 | 16562 | 25.5412 | 49.0318 | 202503 | MVA | central
zone_sub | phm | maximum |  | 2023 | Winter | 50 | 16562 | 25.5412 | 45.9202 | 202503 | MVA | central
zone_sub | phm | maximum |  | 2024 | Winter | 10 | 16854 | 27.7496 | 49.8978 | 202503 | MVA | central
zone_sub | phm | maximum |  | 2024 | Winter | 50 | 16854 | 27.7496 | 46.7311 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2025 | Winter | 10 |  |  | 67.0847 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2025 | Winter | 50 |  |  | 64.1376 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2026 | Winter | 10 |  |  | 71.7531 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2026 | Winter | 50 |  |  | 68.6294 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2027 | Winter | 10 |  |  | 72.4584 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2027 | Winter | 50 |  |  | 69.3785 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2028 | Winter | 10 |  |  | 72.887 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2028 | Winter | 50 |  |  | 69.9467 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2029 | Winter | 10 |  |  | 73.8781 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2029 | Winter | 50 |  |  | 70.9603 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2030 | Winter | 10 |  |  | 76.2493 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2030 | Winter | 50 |  |  | 73.2946 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2031 | Winter | 10 |  |  | 77.5227 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2031 | Winter | 50 |  |  | 74.8388 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2032 | Winter | 10 |  |  | 79.9897 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2032 | Winter | 50 |  |  | 76.8149 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2033 | Winter | 10 |  |  | 87.5343 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2033 | Winter | 50 |  |  | 77.8299 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2034 | Winter | 10 |  |  | 81.2629 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2034 | Winter | 50 |  |  | 78.7091 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2035 | Winter | 10 |  |  | 80.0205 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2035 | Winter | 50 |  |  | 77.0055 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2036 | Winter | 10 |  |  | 81.6454 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2036 | Winter | 50 |  |  | 78.9538 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2037 | Winter | 10 |  |  | 85.2253 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2037 | Winter | 50 |  |  | 82.0295 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2038 | Winter | 10 |  |  | 82.7648 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2038 | Winter | 50 |  |  | 79.6564 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2039 | Winter | 10 |  |  | 67.0558 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2039 | Winter | 50 |  |  | 63.9852 | 202503 | MVA | central
zone_sub | wgi | maximum |  | 2022 | Winter | 10 | 21696 | 27.3902 | 41.941 | 202503 | MVA | east
zone_sub | wgi | maximum |  | 2022 | Winter | 50 | 21696 | 27.3902 | 38.234 | 202503 | MVA | east
zone_sub | wgi | maximum |  | 2023 | Winter | 10 | 22045 | 30.4273 | 42.6315 | 202503 | MVA | east
zone_sub | wgi | maximum |  | 2023 | Winter | 50 | 22045 | 30.4273 | 38.883 | 202503 | MVA | east
zone_sub | wgi | maximum |  | 2024 | Winter | 10 | 22388 | 33.5461 | 43.3126 | 202503 | MVA | east
zone_sub | wgi | maximum |  | 2024 | Winter | 50 | 22388 | 33.5461 | 39.5207 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2025 | Winter | 10 |  |  | 47.2482 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2025 | Winter | 50 |  |  | 43.6466 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2026 | Winter | 10 |  |  | 47.6557 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2026 | Winter | 50 |  |  | 44.0841 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2027 | Winter | 10 |  |  | 49.0622 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2027 | Winter | 50 |  |  | 44.625 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2028 | Winter | 10 |  |  | 49.028 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2028 | Winter | 50 |  |  | 45.3431 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2029 | Winter | 10 |  |  | 49.3373 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2029 | Winter | 50 |  |  | 46.0239 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2030 | Winter | 10 |  |  | 50.5469 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2030 | Winter | 50 |  |  | 47.2137 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2031 | Winter | 10 |  |  | 54.0224 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2031 | Winter | 50 |  |  | 50.206 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2032 | Winter | 10 |  |  | 55.4565 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2032 | Winter | 50 |  |  | 51.8155 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2033 | Winter | 10 |  |  | 54.099 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2033 | Winter | 50 |  |  | 50.6413 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2034 | Winter | 10 |  |  | 57.8491 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2034 | Winter | 50 |  |  | 54.2764 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2035 | Winter | 10 |  |  | 56.2746 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2035 | Winter | 50 |  |  | 54.9313 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2036 | Winter | 10 |  |  | 57.6913 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2036 | Winter | 50 |  |  | 55.4021 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2037 | Winter | 10 |  |  | 58.7122 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2037 | Winter | 50 |  |  | 57.6212 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2038 | Winter | 10 |  |  | 58.2928 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2038 | Winter | 50 |  |  | 57.9824 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2039 | Winter | 10 |  |  | 49.2493 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2039 | Winter | 50 |  |  | 45.4578 | 202503 | MVA | east

## Ratings
STATION OUTPUT RATING (TRANSFORMER SUMMATION) SUMMARY
|  |  | Station N Rating |  | Station N-1 Rating |  | Station N-2 Rating
|  |  | SCR | WCR | SCR | WCR | SCR | WCR | Remarks | Remarks | Bus Target | Station Cap Bank
S/S Name | No. TX | Name Plate MVA | MVA | MVA | MVA | MVA | MVA | MVA | For N-1 Ratings | N-2 | Voltage kV | MVAr
CLN | 3 | 99 | 130.95 | 142.95 | 89.2 | 97.8 | 44.6 | 48.9
LLG | 1 | 33 | 47.4 | 48.3 | 0 | 0 | 0 | 0 | N rating only |  | 22 | 4
OFR | 2 | 66 | 93.2 | 93.2 | 45.2 | 48 | 0 | 0 | Loss of T1 or T2 |  | 22 | 6
PHM | 2 | 66 | 91.9 | 95.7 | 45 | 49.1 | 0 | 0 | Loss of T1 or T2 |  | 22 | 12

## Power Factor
asset_type | asset | PF
zone_sub | cln | 1
zone_sub | llg | 0.99
zone_sub | ofr | 1
zone_sub | phm | 1

## FT
Forecast tool (MVA) |  | Forecast Capacity & Transfers
ZSS |  | PHM
Summer
[5 empty] | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads
DY (Apr 1 to Mar 30) |  | 2022/23 | 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2028/29 | 2029/30 | 2030/31 | 2031/32 | 2032/33 | 2033/34 | 2034/35 | 2035/36 | 2036/37 | 2037/38 | 2038/39
DY (Apr 1 to Mar 30) |  | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038
FY (Jul 1 to Jun 30) |  | 2022/23 | 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2028/29 | 2029/30 | 2030/31 | 2031/32 | 2032/33 | 2033/34 | 2034/35 | 2035/36 | 2036/37 | 2037/38 | 2038/39
FY (Jul 1 to Jun 30) |  |  |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39
Summer POE50 | 50 |  |  | 52.8621 | 69.621 | 74.1527 | 73.9998 | 73.965 | 74.4648 | 75.0153 | 76.1566 | 76.9783 | 77.4148 | 77.8841 | 78.3211 | 79.127 | 80.1321 | 80.0404
Summer POE10 | 10 |  |  | 58.7282 | 75.5207 | 79.8845 | 79.6008 | 79.5894 | 80.0199 | 81.1895 | 81.9552 | 82.7146 | 83.6062 | 84.4206 | 85.2206 | 85.2937 | 86.2309 | 85.4841
Winter
[5 empty] | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads
DM (Apr 1 to Mar 30) |  |  |  | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2028/29 | 2029/30 | 2030/31 | 2031/32 | 2032/33 | 2033/34 | 2034/35 | 2035/36 | 2036/37 | 2037/38 | 2038/39
DY (Apr 1 to Mar 30) |  |  |  | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038
FY (Jul 1 to Jun 30) |  |  |  | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2028/29 | 2029/30 | 2030/31 | 2031/32 | 2032/33 | 2033/34 | 2034/35 | 2035/36 | 2036/37 | 2037/38 | 2038/39
FY (Jul 1 to Jun 30) |  |  |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39
Winter POE50 | 50 |  |  | 46.7311 | 64.1376 | 68.6294 | 69.3785 | 69.9467 | 70.9603 | 73.2946 | 74.8388 | 76.8149 | 77.8299 | 78.7091 | 77.0055 | 78.9538 | 82.0295 | 79.6564
Winter POE10 | 10 |  |  | 49.8978 | 67.0847 | 71.7531 | 72.4584 | 72.887 | 73.8781 | 76.2493 | 77.5227 | 79.9897 | 87.5343 | 81.2629 | 80.0205 | 81.6454 | 85.2253 | 82.7648
Transfers (MVA)
|  | Feeder | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39
|  | PHM | 1.7 | 1.7 | 1.67 | 1.65 | 1.62 | 1.6 | 1.58 | 1.55 | 1.53 | 1.51 | 1.48 | 1.46 | 1.44 | 1.42 | 1.4
|  | PowerFactor | 1

## Load Duration Curves
Station
PHM
POE10
[6 empty] | Stations | KLO |  | EPG |  | CRE |  | CLN |  | PHM |  | OFR |  | LLG |  | WGI
| % of MD | Winter - MD (P10) - Duration % | Winter - MD - Hours | Summer - MD - Duration % | Summer - MD - Hours | %MD | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration %
| 100% | 0% | 0 | 0% | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| 99% | 0.03383% | 1.486 | 0.03444% | 1.5127 | 99% | 0.01722% | 0.02707% | 0% | 0.04737% | 0% | 0% | 0.00861% | 0.01353% | 0.03444% | 0.03383% | 0.01722% | 0.0203% | 0.02583% | 0.006767% | 0% | 0.006767%
| 98% | 0.07443% | 3.2692 | 0.05166% | 2.269 | 98% | 0.01722% | 0.07443% | 0.00861% | 0.08797% | 0.02583% | 0.01353% | 0.02583% | 0.0203% | 0.05166% | 0.07443% | 0.02583% | 0.0812% | 0.04305% | 0.0203% | 0% | 0.006767%
| 97% | 0.1556% | 6.8356 | 0.0861% | 3.7816 | 97% | 0.02583% | 0.09474% | 0.02583% | 0.1421% | 0.04305% | 0.02707% | 0.05166% | 0.03383% | 0.0861% | 0.1556% | 0.04305% | 0.1083% | 0.05166% | 0.04737% | 0.00861% | 0.006767%
| 95% | 0.3992% | 17.5347 | 0.1378% | 6.0506 | 95% | 0.05166% | 0.1895% | 0.09471% | 0.3519% | 0.0861% | 0.08797% | 0.1033% | 0.05413% | 0.1378% | 0.3992% | 0.07749% | 0.1759% | 0.09471% | 0.09474% | 0.00861% | 0.03383%
| 90% | 1.793% | 78.7576 | 0.3702% | 16.2611 | 90% | 0.0861% | 0.9135% | 0.1894% | 1.786% | 0.1894% | 0.7579% | 0.1808% | 0.07443% | 0.3702% | 1.793% | 0.2066% | 0.8932% | 0.353% | 0.2639% | 0.01722% | 0.1962%
| 85% | 5.393% | 236.8672 | 0.6027% | 26.4715 | 85% | 0.1205% | 2.355% | 0.353% | 4.588% | 0.2669% | 2.761% | 0.3272% | 0.318% | 0.6027% | 5.393% | 0.3702% | 2.68% | 0.7147% | 0.7443% | 0.02583% | 0.9135%
| 80% | 11.33% | 497.5104 | 0.7749% | 34.0348 | 80% | 0.31% | 5.616% | 0.6458% | 8.885% | 0.4219% | 6.787% | 0.4477% | 0.9406% | 0.7749% | 11.33% | 0.5683% | 6.11% | 1.317% | 1.915% | 0.06027% | 2.118%
| 75% | 18.3% | 803.6248 | 1.102% | 48.405 | 75% | 0.4822% | 9.995% | 0.9988% | 14.05% | 0.5338% | 11.76% | 0.5855% | 2.876% | 1.102% | 18.3% | 0.7491% | 10.38% | 2.764% | 4.601% | 0.07749% | 4.486%
| 70% | 26.3% | 1155.2107 | 1.739% | 76.3892 | 70% | 0.7491% | 14.12% | 1.498% | 19.88% | 0.8438% | 17.56% | 0.7921% | 7.376% | 1.739% | 26.3% | 0.9557% | 15.73% | 6.225% | 8.837% | 0.1292% | 8.607%
| 65% | 35.36% | 1553.1596 | 2.6% | 114.2056 | 65% | 1.154% | 18.84% | 2.265% | 27.11% | 1.102% | 25.21% | 1.05% | 12.51% | 2.6% | 35.36% | 1.541% | 22.03% | 12.05% | 15.25% | 0.1464% | 14.03%
| 60% | 46.14% | 2026.2996 | 4.055% | 178.1154 | 60% | 1.602% | 25.14% | 3.203% | 35.21% | 1.627% | 33.62% | 1.748% | 18.2% | 4.055% | 46.14% | 2.247% | 29.44% | 20.92% | 25.15% | 0.2583% | 21.29%
| 55% | 59.16% | 2598.4068 | 7.095% | 311.6074 | 55% | 2.411% | 33.56% | 4.357% | 45.33% | 2.48% | 42.68% | 2.419% | 25.42% | 7.095% | 59.16% | 3.496% | 37.5% | 33.11% | 37.15% | 0.8094% | 29.85%
| 50% | 73.62% | 3233.5201 | 14.48% | 636.0723 | 50% | 4.598% | 44.25% | 6.303% | 58.26% | 3.84% | 54.87% | 4.064% | 34.04% | 14.48% | 73.62% | 5.881% | 47.91% | 47.93% | 51.32% | 2.17% | 39.4%
| 45% | 85.96% | 3775.313 | 26.86% | 1179.4944 | 45% | 9.592% | 58.98% | 10.8% | 69.36% | 6.535% | 71.48% | 8.378% | 45.63% | 26.86% | 85.96% | 11.13% | 62.3% | 62.8% | 65.85% | 4.753% | 49.36%
| 40% | 92.73% | 4072.8088 | 41.17% | 1808.3816 | 40% | 19.83% | 71.65% | 21.2% | 75.98% | 14.01% | 84.31% | 16.88% | 65.51% | 41.17% | 92.73% | 21.13% | 79.32% | 76.24% | 79.08% | 8.662% | 59.42%
| 35% | 95.6% | 4198.821 | 63.28% | 2779.1293 | 35% | 37.74% | 78.94% | 37.58% | 85.16% | 27.53% | 88.52% | 26.59% | 78.66% | 63.28% | 95.6% | 34.85% | 87.21% | 86.9% | 88.41% | 15.86% | 68.26%
| 30% | 97.25% | 4271.3374 | 86.84% | 3814.165 | 30% | 66.82% | 83.24% | 57.09% | 93.38% | 49.73% | 90.98% | 45.59% | 83.41% | 86.84% | 97.25% | 59.02% | 90.02% | 92.6% | 93.97% | 28.71% | 75.35%
| 25% | 98.4% | 4321.8611 | 94.88% | 4166.9923 | 25% | 77.33% | 87.43% | 77.75% | 96.1% | 81.07% | 93.44% | 72.26% | 87.95% | 94.88% | 98.4% | 83.32% | 92.46% | 96.47% | 96.66% | 44.75% | 80.55%
| 20% | 99.11% | 4353.067 | 97.51% | 4282.7105 | 20% | 85.59% | 92.06% | 96.84% | 97.65% | 89.22% | 95.65% | 79.18% | 93.87% | 97.51% | 99.11% | 91.2% | 94.84% | 98.65% | 98.41% | 56.7% | 84.95%
| 15% | 99.49% | 4369.4129 | 99.38% | 4364.7722 | 15% | 96.14% | 98.9% | 99.64% | 98.65% | 96.11% | 97.43% | 86.26% | 99.55% | 99.38% | 99.49% | 97.48% | 97.23% | 99.31% | 99.14% | 68.25% | 89.03%
| 10% | 99.7% | 4378.6261 | 99.99% | 4391.6218 | 10% | 99.99% | 99.99% | 99.99% | 99.16% | 99.9% | 98.78% | 98.3% | 99.6% | 99.99% | 99.7% | 99.99% | 99.59% | 99.63% | 99.41% | 79.5% | 92.79%
| 5% | 99.99% | 4391.7028 | 99.99% | 4391.6218 | 5% | 99.99% | 99.99% | 99.99% | 99.49% | 99.99% | 99.76% | 99.99% | 99.61% | 99.99% | 99.99% | 99.99% | 99.99% | 99.68% | 99.6% | 90.07% | 96.81%
| 9.992e-14% | 99.99% | 4391.7028 | 99.99% | 4391.6218 | 0% | 99.99% | 99.99% | 99.99% | 99.99% | 99.99% | 99.99% | 99.99% | 99.63% | 99.99% | 99.99% | 99.99% | 99.99% | 99.71% | 99.63% | 99.99% | 99.99%
POE 50
[6 empty] | Stations | KLO |  | EPG |  | CRE |  | CLN |  | PHM |  | OFR |  | LLG |  | WGI
| % of MD | Winter - AD (P50) - Duration % | Winter - AD - Hours | Summer - AD - Duration % | Summer - AD - Hours | %MD | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration %
| 100% | 0% | 0 | 0% | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| 99% | 0.03383% | 1.486 | 0% | 0 | 99% | 0.03444% | 0.02707% | 0.04305% | 0.04737% | 0% | 0% | 0% | 0.01353% | 0% | 0.03383% | 0% | 0.0203% | 0.00861% | 0.006767% | 0.00861% | 0.006767%
| 98% | 0.07443% | 3.2692 | 0% | 0 | 98% | 0.05166% | 0.07443% | 0.07749% | 0.08797% | 0% | 0.01353% | 0.00861% | 0.0203% | 0% | 0.07443% | 0.00861% | 0.0812% | 0.00861% | 0.0203% | 0.00861% | 0.006767%
| 97% | 0.1556% | 6.8356 | 0.00861% | 0.37816 | 97% | 0.06888% | 0.09474% | 0.07749% | 0.1421% | 0.02583% | 0.02707% | 0.01722% | 0.03383% | 0.00861% | 0.1556% | 0.01722% | 0.1083% | 0.01722% | 0.0406% | 0.00861% | 0.006767%
| 95% | 0.3992% | 17.5347 | 0.05166% | 2.269 | 95% | 0.0861% | 0.1895% | 0.1378% | 0.3519% | 0.04305% | 0.08797% | 0.02583% | 0.05413% | 0.05166% | 0.3992% | 0.04305% | 0.1759% | 0.01722% | 0.1015% | 0.01722% | 0.03383%
| 90% | 1.793% | 78.7576 | 0.1292% | 5.6725 | 90% | 0.1292% | 0.9135% | 0.2583% | 1.786% | 0.1119% | 0.7579% | 0.1033% | 0.07443% | 0.1292% | 1.793% | 0.1033% | 0.8932% | 0.0861% | 0.3451% | 0.2066% | 0.1962%
| 85% | 5.393% | 236.8672 | 0.3616% | 15.8829 | 85% | 0.2497% | 2.355% | 0.465% | 4.588% | 0.2755% | 2.761% | 0.1808% | 0.318% | 0.3616% | 5.393% | 0.2066% | 2.68% | 0.31% | 0.9% | 0.9213% | 0.9135%
| 80% | 11.33% | 497.5104 | 0.706% | 31.0095 | 80% | 0.4133% | 5.616% | 0.7835% | 8.885% | 0.6113% | 6.787% | 0.2669% | 0.9406% | 0.706% | 11.33% | 0.6286% | 6.11% | 0.8008% | 2.517% | 2.153% | 2.118%
| 75% | 18.3% | 803.6248 | 1.662% | 72.9857 | 75% | 0.8352% | 9.995% | 1.257% | 14.05% | 0.9902% | 11.76% | 0.4047% | 2.876% | 1.662% | 18.3% | 1.309% | 10.38% | 1.834% | 5.562% | 4.486% | 4.486%
| 70% | 26.3% | 1155.2107 | 3.427% | 150.5094 | 70% | 1.619% | 14.12% | 2.101% | 19.88% | 1.911% | 17.56% | 0.8008% | 7.376% | 3.427% | 26.3% | 2.419% | 15.73% | 4.374% | 10.11% | 7.672% | 8.607%
| 65% | 35.36% | 1553.1596 | 8.188% | 359.6342 | 65% | 3.057% | 18.84% | 4.288% | 27.11% | 3.504% | 25.21% | 1.352% | 12.51% | 8.188% | 35.36% | 4.598% | 22.03% | 9.179% | 17.54% | 11.87% | 14.03%
| 60% | 46.14% | 2026.2996 | 15.71% | 689.7717 | 60% | 5.528% | 25.14% | 9.342% | 35.21% | 7.758% | 33.62% | 3.573% | 18.2% | 15.71% | 46.14% | 9.17% | 29.44% | 16.83% | 27.53% | 18.5% | 21.29%
| 55% | 59.16% | 2598.4068 | 24.94% | 1095.5419 | 55% | 11.8% | 33.56% | 17.61% | 45.33% | 16.05% | 42.68% | 8.283% | 25.42% | 24.94% | 59.16% | 14.93% | 37.5% | 27.43% | 40.02% | 27.37% | 29.85%
| 50% | 73.62% | 3233.5201 | 37.94% | 1666.1918 | 50% | 21.47% | 44.25% | 28.46% | 58.26% | 24.85% | 54.87% | 17.57% | 34.04% | 37.94% | 73.62% | 22.35% | 47.91% | 40.6% | 54.15% | 38.39% | 39.4%
| 45% | 85.96% | 3775.313 | 57.06% | 2506.0947 | 45% | 35.07% | 58.98% | 42.44% | 69.36% | 37.15% | 71.48% | 28.59% | 45.63% | 57.06% | 85.96% | 36.95% | 62.3% | 53.97% | 68.39% | 48.48% | 49.36%
| 40% | 92.73% | 4072.8088 | 72.05% | 3164.4787 | 40% | 60.78% | 71.65% | 63.35% | 75.98% | 61.17% | 84.31% | 46.88% | 65.51% | 72.05% | 92.73% | 55.62% | 79.32% | 65.21% | 80.79% | 56.57% | 59.42%
| 35% | 95.6% | 4198.821 | 80.86% | 3551.3408 | 35% | 70.59% | 78.94% | 76.04% | 85.16% | 71.05% | 88.52% | 69.68% | 78.66% | 80.86% | 95.6% | 68.46% | 87.21% | 75.09% | 89.43% | 63.94% | 68.26%
| 30% | 97.25% | 4271.3374 | 85.59% | 3758.953 | 30% | 76.73% | 83.24% | 80.97% | 93.38% | 75.06% | 90.98% | 76.64% | 83.41% | 85.59% | 97.25% | 74.6% | 90.02% | 81.51% | 94.17% | 70.48% | 75.35%
| 25% | 98.4% | 4321.8611 | 89.4% | 3926.4798 | 25% | 83.08% | 87.43% | 85.41% | 96.1% | 78.56% | 93.44% | 83.93% | 87.95% | 89.4% | 98.4% | 78.93% | 92.46% | 86.44% | 96.81% | 76.48% | 80.55%
| 20% | 99.11% | 4353.067 | 92.22% | 4050.5177 | 20% | 91.12% | 92.06% | 89.28% | 97.65% | 81.79% | 95.65% | 91.73% | 93.87% | 92.22% | 99.11% | 84.56% | 94.84% | 90.52% | 98.48% | 81.71% | 84.95%
| 15% | 99.49% | 4369.4129 | 94.55% | 4152.622 | 15% | 99.18% | 98.9% | 92.61% | 98.65% | 86.18% | 97.43% | 98.93% | 99.55% | 94.55% | 99.49% | 92.06% | 97.23% | 93.75% | 99.28% | 86.58% | 89.03%
| 10% | 99.7% | 4378.6261 | 96.73% | 4248.2976 | 10% | 99.99% | 99.99% | 95.16% | 99.16% | 91.73% | 98.78% | 99.75% | 99.6% | 96.73% | 99.7% | 99.06% | 99.59% | 96.19% | 99.59% | 91.64% | 92.79%
| 5% | 99.99% | 4391.7028 | 99.31% | 4361.7469 | 5% | 99.99% | 99.99% | 97.15% | 99.49% | 97.84% | 99.76% | 99.99% | 99.61% | 99.31% | 99.99% | 99.99% | 99.99% | 98.14% | 99.77% | 96.54% | 96.81%
| 9.992e-14% | 99.99% | 4391.7028 | 99.99% | 4391.6218 | 0% | 99.99% | 99.99% | 99.99% | 99.99% | 99.99% | 99.99% | 99.99% | 99.63% | 99.99% | 99.99% | 99.99% | 99.99% | 99.78% | 99.99% | 99.99% | 99.99%
POE10
|  | Summer | Winter
| Year | 2019/2020 | 2023
| Start | 2024-10-01 | 2024-04-01
| End | 2025-04-01 | 2024-10-01
| Days | 183 | 183
| Hours | 4392 | 4392
POE50
|  | Summer | Winter
| Year | 2023/2024 | 2023
| Start | 2023-10-01 | 2024-04-01
| End | 2024-04-01 | 2024-10-01
| Days | 183 | 183
| Hours | 4392 | 4392

## Capacity N
Option 1 - Do Nothing / Base Case - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N Rating (MVA) - Option 1 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7
SCR N Rating (MVA) - Option 1 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9
Planned Additional Capacity (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2 - 1B New PHS ZSS + Three new feeders - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N Rating (MVA) - Option 2 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7
SCR N Rating (MVA) - Option 2 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 - 2B PHM 3rd Tx + Switchroom + Two new feeders + OFR12 New Feeder - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N Rating (MVA) - Option 3 | 95.7 | 95.7 | 95.7 | 140.7 | 140.7 | 140.7 | 140.7 | 140.7 | 140.7 | 140.7 | 140.7 | 140.7 | 140.7 | 140.7 | 140.7 | 140.7 | 140.7 | 140.7 | 140.7 | 140.7 | 140.7 | 140.7 | 140.7 | 140.7 | 140.7 | 140.7 | 140.7 | 140.7 | 140.7 | 140.7
SCR N Rating (MVA) - Option 3 | 91.9 | 91.9 | 91.9 | 136.9 | 136.9 | 136.9 | 136.9 | 136.9 | 136.9 | 136.9 | 136.9 | 136.9 | 136.9 | 136.9 | 136.9 | 136.9 | 136.9 | 136.9 | 136.9 | 136.9 | 136.9 | 136.9 | 136.9 | 136.9 | 136.9 | 136.9 | 136.9 | 136.9 | 136.9 | 136.9
Capacity Added (MVA) | 0 | 0 | 0 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45
Option 4 - 3B OFR 3rd Tx + Switchroom + Two new feeders + OFR12 New Feeder - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N Rating (MVA) - Option 4 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7
SCR N Rating (MVA) - Option 4 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 - 4B LLG 2nd Tx + Switchroom + Two new feeders + OFR12 New Feeder - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N Rating (MVA) - Option 5 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7
SCR N Rating (MVA) - Option 5 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 6 - - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N Rating (MVA) - Option 6 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7
SCR N Rating (MVA) - Option 6 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 7 - - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N Rating (MVA) - Option 7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7
SCR N Rating (MVA) - Option 7 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 8 - - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N Rating (MVA) - Option 8 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7
SCR N Rating (MVA) - Option 8 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Capacity N-1
Option 1 - Do Nothing / Base Case - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-1 Rating (MVA) - Option 1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1
SCR N-1 Rating (MVA) - Option 1 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45
Planned Additional Capacity (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2 - 1B New PHS ZSS + Three new feeders - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-1 Rating (MVA) - Option 2 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1
SCR N-1 Rating (MVA) - Option 2 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 - 2B PHM 3rd Tx + Switchroom + Two new feeders + OFR12 New Feeder - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-1 Rating (MVA) - Option 3 | 49.1 | 49.1 | 49.1 | 94.1 | 94.1 | 94.1 | 94.1 | 94.1 | 94.1 | 94.1 | 94.1 | 94.1 | 94.1 | 94.1 | 94.1 | 94.1 | 94.1 | 94.1 | 94.1 | 94.1 | 94.1 | 94.1 | 94.1 | 94.1 | 94.1 | 94.1 | 94.1 | 94.1 | 94.1 | 94.1
SCR N-1 Rating (MVA) - Option 3 | 45 | 45 | 45 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90
Capacity Added (MVA) | 0 | 0 | 0 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45
Option 4 - 3B OFR 3rd Tx + Switchroom + Two new feeders + OFR12 New Feeder - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-1 Rating (MVA) - Option 4 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1
SCR N-1 Rating (MVA) - Option 4 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 - 4B LLG 2nd Tx + Switchroom + Two new feeders + OFR12 New Feeder - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-1 Rating (MVA) - Option 5 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1
SCR N-1 Rating (MVA) - Option 5 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 6 - - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-1 Rating (MVA) - Option 6 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1
SCR N-1 Rating (MVA) - Option 6 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 7 - - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-1 Rating (MVA) - Option 7 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1
SCR N-1 Rating (MVA) - Option 7 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 8 - - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-1 Rating (MVA) - Option 8 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1
SCR N-1 Rating (MVA) - Option 8 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Capacity N-2
Option 1 - Do Nothing / Base Case - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-2 Rating (MVA) - Option 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCR N-2 Rating (MVA) - Option 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Planned Additional Capacity (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2 - 1B New PHS ZSS + Three new feeders - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-2 Rating (MVA) - Option 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCR N-2 Rating (MVA) - Option 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 - 2B PHM 3rd Tx + Switchroom + Two new feeders + OFR12 New Feeder - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-2 Rating (MVA) - Option 3 | 0 | 0 | 0 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45
SCR N-2 Rating (MVA) - Option 3 | 0 | 0 | 0 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45
Capacity Added (MVA) | 0 | 0 | 0 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45
Option 4 - 3B OFR 3rd Tx + Switchroom + Two new feeders + OFR12 New Feeder - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-2 Rating (MVA) - Option 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCR N-2 Rating (MVA) - Option 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 - 4B LLG 2nd Tx + Switchroom + Two new feeders + OFR12 New Feeder - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-2 Rating (MVA) - Option 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCR N-2 Rating (MVA) - Option 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 6 - - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-2 Rating (MVA) - Option 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCR N-2 Rating (MVA) - Option 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 7 - - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-2 Rating (MVA) - Option 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCR N-2 Rating (MVA) - Option 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 8 - - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-2 Rating (MVA) - Option 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCR N-2 Rating (MVA) - Option 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Demand
Option 1 - Do Nothing / Base Case
Winter Season | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Maximum Demand (MVA) - P50 | 51.4042 | 70.5514 | 75.4923 | 76.3163 | 76.9414 | 78.0563 | 80.6241 | 82.3226 | 84.4964 | 85.6129 | 86.5801 | 84.7061 | 86.8492 | 90.2325 | 87.6221 | 87.6221 | 87.6221 | 87.6221 | 87.6221 | 87.6221 | 87.6221 | 87.6221 | 87.6221 | 87.6221 | 87.6221 | 87.6221 | 87.6221 | 87.6221 | 87.6221 | 87.6221
Maximum Demand (MVA) - P10 | 54.8876 | 73.7932 | 78.9284 | 79.7042 | 80.1757 | 81.2659 | 83.8742 | 85.2749 | 87.9887 | 96.2877 | 89.3892 | 88.0226 | 89.8099 | 93.7478 | 91.0413 | 91.0413 | 91.0413 | 91.0413 | 91.0413 | 91.0413 | 91.0413 | 91.0413 | 91.0413 | 91.0413 | 91.0413 | 91.0413 | 91.0413 | 91.0413 | 91.0413 | 91.0413
Block loads (MVA) not in the forecast | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Available Transfers (MVA) | 1.7 | 1.7 | 1.67 | 1.65 | 1.62 | 1.6 | 1.58 | 1.55 | 1.53 | 1.51 | 1.48 | 1.46 | 1.44 | 1.42 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4
Demand management (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Embedded generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Maximum Demand (MVA) - Option 1 Winter POE50 | 49.7042 | 68.8514 | 73.8223 | 74.6663 | 75.3214 | 76.4563 | 79.0441 | 80.7726 | 82.9664 | 84.1029 | 85.1001 | 83.2461 | 85.4092 | 88.8125 | 86.2221 | 86.2221 | 86.2221 | 86.2221 | 86.2221 | 86.2221 | 86.2221 | 86.2221 | 86.2221 | 86.2221 | 86.2221 | 86.2221 | 86.2221 | 86.2221 | 86.2221 | 86.2221
Total Maximum Demand (MVA) - Option 1 Winter POE10 | 53.1876 | 72.0932 | 77.2584 | 78.0542 | 78.5557 | 79.6659 | 82.2942 | 83.7249 | 86.4587 | 94.7777 | 87.9092 | 86.5626 | 88.3699 | 92.3278 | 89.6413 | 89.6413 | 89.6413 | 89.6413 | 89.6413 | 89.6413 | 89.6413 | 89.6413 | 89.6413 | 89.6413 | 89.6413 | 89.6413 | 89.6413 | 89.6413 | 89.6413 | 89.6413
Summer Season | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Maximum Demand (MVA) - P50 | 58.1483 | 76.5831 | 81.568 | 81.3998 | 81.3614 | 81.9113 | 82.5169 | 83.7723 | 84.6761 | 85.1563 | 85.6725 | 86.1532 | 87.0397 | 88.1453 | 88.0445 | 88.0445 | 88.0445 | 88.0445 | 88.0445 | 88.0445 | 88.0445 | 88.0445 | 88.0445 | 88.0445 | 88.0445 | 88.0445 | 88.0445 | 88.0445 | 88.0445 | 88.0445
Maximum Demand (MVA) - P10 | 64.601 | 83.0728 | 87.873 | 87.5609 | 87.5484 | 88.0219 | 89.3084 | 90.1508 | 90.9861 | 91.9669 | 92.8626 | 93.7427 | 93.823 | 94.854 | 94.0325 | 94.0325 | 94.0325 | 94.0325 | 94.0325 | 94.0325 | 94.0325 | 94.0325 | 94.0325 | 94.0325 | 94.0325 | 94.0325 | 94.0325 | 94.0325 | 94.0325 | 94.0325
Block loads (MVA) not in the forecast | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Available Transfers (MVA) | 1.7 | 1.7 | 1.67 | 1.65 | 1.62 | 1.6 | 1.58 | 1.55 | 1.53 | 1.51 | 1.48 | 1.46 | 1.44 | 1.42 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4
Demand management (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Embedded generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Maximum Demand (MVA) - Option 1 Summer POE50 | 56.4483 | 74.8831 | 79.898 | 79.7498 | 79.7414 | 80.3113 | 80.9369 | 82.2223 | 83.1461 | 83.6463 | 84.1925 | 84.6932 | 85.5997 | 86.7253 | 86.6445 | 86.6445 | 86.6445 | 86.6445 | 86.6445 | 86.6445 | 86.6445 | 86.6445 | 86.6445 | 86.6445 | 86.6445 | 86.6445 | 86.6445 | 86.6445 | 86.6445 | 86.6445
Total Maximum Demand (MVA) - Option 1 Summer POE10 | 62.901 | 81.3728 | 86.203 | 85.9109 | 85.9284 | 86.4219 | 87.7284 | 88.6008 | 89.4561 | 90.4569 | 91.3826 | 92.2827 | 92.383 | 93.434 | 92.6325 | 92.6325 | 92.6325 | 92.6325 | 92.6325 | 92.6325 | 92.6325 | 92.6325 | 92.6325 | 92.6325 | 92.6325 | 92.6325 | 92.6325 | 92.6325 | 92.6325 | 92.6325
Option 2 - 1B New PHS ZSS + Three new feeders
Year | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Added Transfers (MVA) | 0 | 0 | 0 | 19.3333 | 19.3333 | 19.3333 | 19.3333 | 19.3333 | 19.3333 | 19.3333 | 19.3333 | 19.3333 | 19.3333 | 19.3333 | 19.3333 | 19.3333 | 19.3333 | 19.3333 | 19.3333 | 19.3333 | 19.3333 | 19.3333 | 19.3333 | 19.3333 | 19.3333 | 19.3333 | 19.3333 | 19.3333 | 19.3333 | 19.3333
Added Demand management (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Added Embedded generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Maximum Demand (MVA) - Option 2 Winter POE50 | 49.7042 | 68.8514 | 73.8223 | 55.333 | 55.9881 | 57.123 | 59.7108 | 61.4393 | 63.6331 | 64.7696 | 65.7667 | 63.9128 | 66.0759 | 69.4791 | 66.8887 | 66.8887 | 66.8887 | 66.8887 | 66.8887 | 66.8887 | 66.8887 | 66.8887 | 66.8887 | 66.8887 | 66.8887 | 66.8887 | 66.8887 | 66.8887 | 66.8887 | 66.8887
Total Maximum Demand (MVA) - Option 2 Winter POE10 | 53.1876 | 72.0932 | 77.2584 | 58.7209 | 59.2223 | 60.3326 | 62.9609 | 64.3916 | 67.1254 | 75.4444 | 68.5759 | 67.2293 | 69.0366 | 72.9945 | 70.308 | 70.308 | 70.308 | 70.308 | 70.308 | 70.308 | 70.308 | 70.308 | 70.308 | 70.308 | 70.308 | 70.308 | 70.308 | 70.308 | 70.308 | 70.308
Total Maximum Demand (MVA) - Option 2 Summer POE50 | 56.4483 | 74.8831 | 79.898 | 60.4165 | 60.4081 | 60.978 | 61.6035 | 62.8889 | 63.8127 | 64.313 | 64.8592 | 65.3599 | 66.2664 | 67.3919 | 67.3111 | 67.3111 | 67.3111 | 67.3111 | 67.3111 | 67.3111 | 67.3111 | 67.3111 | 67.3111 | 67.3111 | 67.3111 | 67.3111 | 67.3111 | 67.3111 | 67.3111 | 67.3111
Total Maximum Demand (MVA) - Option 2 Summer POE10 | 62.901 | 81.3728 | 86.203 | 66.5776 | 66.595 | 67.0886 | 68.3951 | 69.2674 | 70.1227 | 71.1235 | 72.0493 | 72.9493 | 73.0497 | 74.1006 | 73.2991 | 73.2991 | 73.2991 | 73.2991 | 73.2991 | 73.2991 | 73.2991 | 73.2991 | 73.2991 | 73.2991 | 73.2991 | 73.2991 | 73.2991 | 73.2991 | 73.2991 | 73.2991
Option 3 - 2B PHM 3rd Tx + Switchroom + Two new feeders + OFR12 New Feeder
Year | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Added Transfers (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Added Demand management (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Added Embedded generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Maximum Demand (MVA) - Option 3 Winter POE50 | 49.7042 | 68.8514 | 73.8223 | 74.6663 | 75.3214 | 76.4563 | 79.0441 | 80.7726 | 82.9664 | 84.1029 | 85.1001 | 83.2461 | 85.4092 | 88.8125 | 86.2221 | 86.2221 | 86.2221 | 86.2221 | 86.2221 | 86.2221 | 86.2221 | 86.2221 | 86.2221 | 86.2221 | 86.2221 | 86.2221 | 86.2221 | 86.2221 | 86.2221 | 86.2221
Total Maximum Demand (MVA) - Option 3 Winter POE10 | 53.1876 | 72.0932 | 77.2584 | 78.0542 | 78.5557 | 79.6659 | 82.2942 | 83.7249 | 86.4587 | 94.7777 | 87.9092 | 86.5626 | 88.3699 | 92.3278 | 89.6413 | 89.6413 | 89.6413 | 89.6413 | 89.6413 | 89.6413 | 89.6413 | 89.6413 | 89.6413 | 89.6413 | 89.6413 | 89.6413 | 89.6413 | 89.6413 | 89.6413 | 89.6413
Total Maximum Demand (MVA) - Option 3 Summer POE50 | 56.4483 | 74.8831 | 79.898 | 79.7498 | 79.7414 | 80.3113 | 80.9369 | 82.2223 | 83.1461 | 83.6463 | 84.1925 | 84.6932 | 85.5997 | 86.7253 | 86.6445 | 86.6445 | 86.6445 | 86.6445 | 86.6445 | 86.6445 | 86.6445 | 86.6445 | 86.6445 | 86.6445 | 86.6445 | 86.6445 | 86.6445 | 86.6445 | 86.6445 | 86.6445
Total Maximum Demand (MVA) - Option 3 Summer POE10 | 62.901 | 81.3728 | 86.203 | 85.9109 | 85.9284 | 86.4219 | 87.7284 | 88.6008 | 89.4561 | 90.4569 | 91.3826 | 92.2827 | 92.383 | 93.434 | 92.6325 | 92.6325 | 92.6325 | 92.6325 | 92.6325 | 92.6325 | 92.6325 | 92.6325 | 92.6325 | 92.6325 | 92.6325 | 92.6325 | 92.6325 | 92.6325 | 92.6325 | 92.6325
Option 4 - 3B OFR 3rd Tx + Switchroom + Two new feeders + OFR12 New Feeder
Year | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Added Transfers (MVA) | 0 | 0 | 0 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
Added Demand management (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Added Embedded generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Maximum Demand (MVA) - Option 4 Winter POE50 | 49.7042 | 68.8514 | 73.8223 | 70.6663 | 71.3214 | 72.4563 | 75.0441 | 76.7726 | 78.9664 | 80.1029 | 81.1001 | 79.2461 | 81.4092 | 84.8125 | 82.2221 | 82.2221 | 82.2221 | 82.2221 | 82.2221 | 82.2221 | 82.2221 | 82.2221 | 82.2221 | 82.2221 | 82.2221 | 82.2221 | 82.2221 | 82.2221 | 82.2221 | 82.2221
Total Maximum Demand (MVA) - Option 4 Winter POE10 | 53.1876 | 72.0932 | 77.2584 | 74.0542 | 74.5557 | 75.6659 | 78.2942 | 79.7249 | 82.4587 | 90.7777 | 83.9092 | 82.5626 | 84.3699 | 88.3278 | 85.6413 | 85.6413 | 85.6413 | 85.6413 | 85.6413 | 85.6413 | 85.6413 | 85.6413 | 85.6413 | 85.6413 | 85.6413 | 85.6413 | 85.6413 | 85.6413 | 85.6413 | 85.6413
Total Maximum Demand (MVA) - Option 4 Summer POE50 | 56.4483 | 74.8831 | 79.898 | 75.7498 | 75.7414 | 76.3113 | 76.9369 | 78.2223 | 79.1461 | 79.6463 | 80.1925 | 80.6932 | 81.5997 | 82.7253 | 82.6445 | 82.6445 | 82.6445 | 82.6445 | 82.6445 | 82.6445 | 82.6445 | 82.6445 | 82.6445 | 82.6445 | 82.6445 | 82.6445 | 82.6445 | 82.6445 | 82.6445 | 82.6445
Total Maximum Demand (MVA) - Option 4 Summer POE10 | 62.901 | 81.3728 | 86.203 | 81.9109 | 81.9284 | 82.4219 | 83.7284 | 84.6008 | 85.4561 | 86.4569 | 87.3826 | 88.2827 | 88.383 | 89.434 | 88.6325 | 88.6325 | 88.6325 | 88.6325 | 88.6325 | 88.6325 | 88.6325 | 88.6325 | 88.6325 | 88.6325 | 88.6325 | 88.6325 | 88.6325 | 88.6325 | 88.6325 | 88.6325
Option 5 - 4B LLG 2nd Tx + Switchroom + Two new feeders + OFR12 New Feeder
Year | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Added Transfers (MVA) | 0 | 0 | 0 | 21.75 | 21.75 | 21.75 | 21.75 | 21.75 | 21.75 | 21.75 | 21.75 | 21.75 | 21.75 | 21.75 | 21.75 | 21.75 | 21.75 | 21.75 | 21.75 | 21.75 | 21.75 | 21.75 | 21.75 | 21.75 | 21.75 | 21.75 | 21.75 | 21.75 | 21.75 | 21.75
Added Demand management (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Added Embedded generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Maximum Demand (MVA) - Option 5 Winter POE50 | 49.7042 | 68.8514 | 73.8223 | 52.9163 | 53.5714 | 54.7063 | 57.2941 | 59.0226 | 61.2164 | 62.3529 | 63.3501 | 61.4961 | 63.6592 | 67.0625 | 64.4721 | 64.4721 | 64.4721 | 64.4721 | 64.4721 | 64.4721 | 64.4721 | 64.4721 | 64.4721 | 64.4721 | 64.4721 | 64.4721 | 64.4721 | 64.4721 | 64.4721 | 64.4721
Total Maximum Demand (MVA) - Option 5 Winter POE10 | 53.1876 | 72.0932 | 77.2584 | 56.3042 | 56.8057 | 57.9159 | 60.5442 | 61.9749 | 64.7087 | 73.0277 | 66.1592 | 64.8126 | 66.6199 | 70.5778 | 67.8913 | 67.8913 | 67.8913 | 67.8913 | 67.8913 | 67.8913 | 67.8913 | 67.8913 | 67.8913 | 67.8913 | 67.8913 | 67.8913 | 67.8913 | 67.8913 | 67.8913 | 67.8913
Total Maximum Demand (MVA) - Option 5 Summer POE50 | 56.4483 | 74.8831 | 79.898 | 57.9998 | 57.9914 | 58.5613 | 59.1869 | 60.4723 | 61.3961 | 61.8963 | 62.4425 | 62.9432 | 63.8497 | 64.9753 | 64.8945 | 64.8945 | 64.8945 | 64.8945 | 64.8945 | 64.8945 | 64.8945 | 64.8945 | 64.8945 | 64.8945 | 64.8945 | 64.8945 | 64.8945 | 64.8945 | 64.8945 | 64.8945
Total Maximum Demand (MVA) - Option 5 Summer POE10 | 62.901 | 81.3728 | 86.203 | 64.1609 | 64.1784 | 64.6719 | 65.9784 | 66.8508 | 67.7061 | 68.7069 | 69.6326 | 70.5327 | 70.633 | 71.684 | 70.8825 | 70.8825 | 70.8825 | 70.8825 | 70.8825 | 70.8825 | 70.8825 | 70.8825 | 70.8825 | 70.8825 | 70.8825 | 70.8825 | 70.8825 | 70.8825 | 70.8825 | 70.8825
Option 6 -
Year | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Added Transfers (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Added Demand management (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Added Embedded generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Maximum Demand (MVA) - Option 6 Winter POE50 | 49.7042 | 68.8514 | 73.8223 | 74.6663 | 75.3214 | 76.4563 | 79.0441 | 80.7726 | 82.9664 | 84.1029 | 85.1001 | 83.2461 | 85.4092 | 88.8125 | 86.2221 | 86.2221 | 86.2221 | 86.2221 | 86.2221 | 86.2221 | 86.2221 | 86.2221 | 86.2221 | 86.2221 | 86.2221 | 86.2221 | 86.2221 | 86.2221 | 86.2221 | 86.2221
Total Maximum Demand (MVA) - Option 6 Winter POE10 | 53.1876 | 72.0932 | 77.2584 | 78.0542 | 78.5557 | 79.6659 | 82.2942 | 83.7249 | 86.4587 | 94.7777 | 87.9092 | 86.5626 | 88.3699 | 92.3278 | 89.6413 | 89.6413 | 89.6413 | 89.6413 | 89.6413 | 89.6413 | 89.6413 | 89.6413 | 89.6413 | 89.6413 | 89.6413 | 89.6413 | 89.6413 | 89.6413 | 89.6413 | 89.6413
Total Maximum Demand (MVA) - Option 6 Summer POE50 | 56.4483 | 74.8831 | 79.898 | 79.7498 | 79.7414 | 80.3113 | 80.9369 | 82.2223 | 83.1461 | 83.6463 | 84.1925 | 84.6932 | 85.5997 | 86.7253 | 86.6445 | 86.6445 | 86.6445 | 86.6445 | 86.6445 | 86.6445 | 86.6445 | 86.6445 | 86.6445 | 86.6445 | 86.6445 | 86.6445 | 86.6445 | 86.6445 | 86.6445 | 86.6445
Total Maximum Demand (MVA) - Option 6 Summer POE10 | 62.901 | 81.3728 | 86.203 | 85.9109 | 85.9284 | 86.4219 | 87.7284 | 88.6008 | 89.4561 | 90.4569 | 91.3826 | 92.2827 | 92.383 | 93.434 | 92.6325 | 92.6325 | 92.6325 | 92.6325 | 92.6325 | 92.6325 | 92.6325 | 92.6325 | 92.6325 | 92.6325 | 92.6325 | 92.6325 | 92.6325 | 92.6325 | 92.6325 | 92.6325
Option 7 -
Year | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Added Transfers (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Added Demand management (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Added Embedded generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Maximum Demand (MVA) - Option 7 Winter POE50 | 49.7042 | 68.8514 | 73.8223 | 74.6663 | 75.3214 | 76.4563 | 79.0441 | 80.7726 | 82.9664 | 84.1029 | 85.1001 | 83.2461 | 85.4092 | 88.8125 | 86.2221 | 86.2221 | 86.2221 | 86.2221 | 86.2221 | 86.2221 | 86.2221 | 86.2221 | 86.2221 | 86.2221 | 86.2221 | 86.2221 | 86.2221 | 86.2221 | 86.2221 | 86.2221
Total Maximum Demand (MVA) - Option 7 Winter POE10 | 53.1876 | 72.0932 | 77.2584 | 78.0542 | 78.5557 | 79.6659 | 82.2942 | 83.7249 | 86.4587 | 94.7777 | 87.9092 | 86.5626 | 88.3699 | 92.3278 | 89.6413 | 89.6413 | 89.6413 | 89.6413 | 89.6413 | 89.6413 | 89.6413 | 89.6413 | 89.6413 | 89.6413 | 89.6413 | 89.6413 | 89.6413 | 89.6413 | 89.6413 | 89.6413
Total Maximum Demand (MVA) - Option 7 Summer POE50 | 56.4483 | 74.8831 | 79.898 | 79.7498 | 79.7414 | 80.3113 | 80.9369 | 82.2223 | 83.1461 | 83.6463 | 84.1925 | 84.6932 | 85.5997 | 86.7253 | 86.6445 | 86.6445 | 86.6445 | 86.6445 | 86.6445 | 86.6445 | 86.6445 | 86.6445 | 86.6445 | 86.6445 | 86.6445 | 86.6445 | 86.6445 | 86.6445 | 86.6445 | 86.6445
Total Maximum Demand (MVA) - Option 7 Summer POE10 | 62.901 | 81.3728 | 86.203 | 85.9109 | 85.9284 | 86.4219 | 87.7284 | 88.6008 | 89.4561 | 90.4569 | 91.3826 | 92.2827 | 92.383 | 93.434 | 92.6325 | 92.6325 | 92.6325 | 92.6325 | 92.6325 | 92.6325 | 92.6325 | 92.6325 | 92.6325 | 92.6325 | 92.6325 | 92.6325 | 92.6325 | 92.6325 | 92.6325 | 92.6325
Option 8 -
Year | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Added Transfers (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Added Demand management (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Added Embedded generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Maximum Demand (MVA) - Option 8 Winter POE50 | 49.7042 | 68.8514 | 73.8223 | 74.6663 | 75.3214 | 76.4563 | 79.0441 | 80.7726 | 82.9664 | 84.1029 | 85.1001 | 83.2461 | 85.4092 | 88.8125 | 86.2221 | 86.2221 | 86.2221 | 86.2221 | 86.2221 | 86.2221 | 86.2221 | 86.2221 | 86.2221 | 86.2221 | 86.2221 | 86.2221 | 86.2221 | 86.2221 | 86.2221 | 86.2221
Total Maximum Demand (MVA) - Option 8 Winter POE10 | 53.1876 | 72.0932 | 77.2584 | 78.0542 | 78.5557 | 79.6659 | 82.2942 | 83.7249 | 86.4587 | 94.7777 | 87.9092 | 86.5626 | 88.3699 | 92.3278 | 89.6413 | 89.6413 | 89.6413 | 89.6413 | 89.6413 | 89.6413 | 89.6413 | 89.6413 | 89.6413 | 89.6413 | 89.6413 | 89.6413 | 89.6413 | 89.6413 | 89.6413 | 89.6413
Total Maximum Demand (MVA) - Option 8 Summer POE50 | 56.4483 | 74.8831 | 79.898 | 79.7498 | 79.7414 | 80.3113 | 80.9369 | 82.2223 | 83.1461 | 83.6463 | 84.1925 | 84.6932 | 85.5997 | 86.7253 | 86.6445 | 86.6445 | 86.6445 | 86.6445 | 86.6445 | 86.6445 | 86.6445 | 86.6445 | 86.6445 | 86.6445 | 86.6445 | 86.6445 | 86.6445 | 86.6445 | 86.6445 | 86.6445
Total Maximum Demand (MVA) - Option 8 Summer POE10 | 62.901 | 81.3728 | 86.203 | 85.9109 | 85.9284 | 86.4219 | 87.7284 | 88.6008 | 89.4561 | 90.4569 | 91.3826 | 92.2827 | 92.383 | 93.434 | 92.6325 | 92.6325 | 92.6325 | 92.6325 | 92.6325 | 92.6325 | 92.6325 | 92.6325 | 92.6325 | 92.6325 | 92.6325 | 92.6325 | 92.6325 | 92.6325 | 92.6325 | 92.6325

## Forecasted LDC
Option 1 - Do Nothing / Base Case
Winter Season | [31 empty] | Winter Season
P50 | [31 empty] | P10
% of MD | Winter - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Winter - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 49.7042 | 68.8514 | 73.8223 | 74.6663 | 75.3214 | 76.4563 | 79.0441 | 80.7726 | 82.9664 | 84.1029 | 85.1001 | 83.2461 | 85.4092 | 88.8125 | 86.2221 | 86.2221 | 86.2221 | 86.2221 | 86.2221 | 86.2221 | 86.2221 | 86.2221 | 86.2221 | 86.2221 | 86.2221 | 86.2221 | 86.2221 | 86.2221 | 86.2221 | 86.2221 | 100% | 0 | 53.1876 | 72.0932 | 77.2584 | 78.0542 | 78.5557 | 79.6659 | 82.2942 | 83.7249 | 86.4587 | 94.7777 | 87.9092 | 86.5626 | 88.3699 | 92.3278 | 89.6413 | 89.6413 | 89.6413 | 89.6413 | 89.6413 | 89.6413 | 89.6413 | 89.6413 | 89.6413 | 89.6413 | 89.6413 | 89.6413 | 89.6413 | 89.6413 | 89.6413 | 89.6413
99% | 1.486 | 49.2072 | 68.1629 | 73.0841 | 73.9197 | 74.5682 | 75.6918 | 78.2537 | 79.9649 | 82.1367 | 83.2619 | 84.2491 | 82.4136 | 84.5551 | 87.9243 | 85.3598 | 85.3598 | 85.3598 | 85.3598 | 85.3598 | 85.3598 | 85.3598 | 85.3598 | 85.3598 | 85.3598 | 85.3598 | 85.3598 | 85.3598 | 85.3598 | 85.3598 | 85.3598 | 99% | 1.486 | 52.6557 | 71.3723 | 76.4858 | 77.2737 | 77.7701 | 78.8692 | 81.4712 | 82.8877 | 85.5941 | 93.83 | 87.0301 | 85.697 | 87.4862 | 91.4045 | 88.7449 | 88.7449 | 88.7449 | 88.7449 | 88.7449 | 88.7449 | 88.7449 | 88.7449 | 88.7449 | 88.7449 | 88.7449 | 88.7449 | 88.7449 | 88.7449 | 88.7449 | 88.7449
98% | 3.2692 | 48.7101 | 67.4743 | 72.3458 | 73.173 | 73.815 | 74.9272 | 77.4632 | 79.1572 | 81.3071 | 82.4209 | 83.3981 | 81.5812 | 83.701 | 87.0362 | 84.4976 | 84.4976 | 84.4976 | 84.4976 | 84.4976 | 84.4976 | 84.4976 | 84.4976 | 84.4976 | 84.4976 | 84.4976 | 84.4976 | 84.4976 | 84.4976 | 84.4976 | 84.4976 | 98% | 3.2692 | 52.1238 | 70.6514 | 75.7133 | 76.4931 | 76.9846 | 78.0726 | 80.6483 | 82.0504 | 84.7295 | 92.8822 | 86.151 | 84.8313 | 86.6025 | 90.4812 | 87.8485 | 87.8485 | 87.8485 | 87.8485 | 87.8485 | 87.8485 | 87.8485 | 87.8485 | 87.8485 | 87.8485 | 87.8485 | 87.8485 | 87.8485 | 87.8485 | 87.8485 | 87.8485
97% | 6.8356 | 48.2131 | 66.7858 | 71.6076 | 72.4263 | 73.0618 | 74.1627 | 76.6728 | 78.3495 | 80.4774 | 81.5798 | 82.5471 | 80.7487 | 82.847 | 86.1481 | 83.6354 | 83.6354 | 83.6354 | 83.6354 | 83.6354 | 83.6354 | 83.6354 | 83.6354 | 83.6354 | 83.6354 | 83.6354 | 83.6354 | 83.6354 | 83.6354 | 83.6354 | 83.6354 | 97% | 6.8356 | 51.5919 | 69.9304 | 74.9407 | 75.7126 | 76.199 | 77.2759 | 79.8254 | 81.2132 | 83.865 | 91.9344 | 85.2719 | 83.9657 | 85.7188 | 89.558 | 86.9521 | 86.9521 | 86.9521 | 86.9521 | 86.9521 | 86.9521 | 86.9521 | 86.9521 | 86.9521 | 86.9521 | 86.9521 | 86.9521 | 86.9521 | 86.9521 | 86.9521 | 86.9521
95% | 17.5347 | 47.219 | 65.4088 | 70.1312 | 70.933 | 71.5553 | 72.6335 | 75.0919 | 76.734 | 78.8181 | 79.8978 | 80.8451 | 79.0838 | 81.1388 | 84.3718 | 81.911 | 81.911 | 81.911 | 81.911 | 81.911 | 81.911 | 81.911 | 81.911 | 81.911 | 81.911 | 81.911 | 81.911 | 81.911 | 81.911 | 81.911 | 81.911 | 95% | 17.5347 | 50.5282 | 68.4886 | 73.3955 | 74.1515 | 74.6279 | 75.6826 | 78.1795 | 79.5387 | 82.1358 | 90.0389 | 83.5138 | 82.2345 | 83.9514 | 87.7114 | 85.1592 | 85.1592 | 85.1592 | 85.1592 | 85.1592 | 85.1592 | 85.1592 | 85.1592 | 85.1592 | 85.1592 | 85.1592 | 85.1592 | 85.1592 | 85.1592 | 85.1592 | 85.1592
90% | 78.7576 | 44.7338 | 61.9662 | 66.4401 | 67.1997 | 67.7893 | 68.8107 | 71.1397 | 72.6954 | 74.6697 | 75.6926 | 76.5901 | 74.9215 | 76.8683 | 79.9312 | 77.5999 | 77.5999 | 77.5999 | 77.5999 | 77.5999 | 77.5999 | 77.5999 | 77.5999 | 77.5999 | 77.5999 | 77.5999 | 77.5999 | 77.5999 | 77.5999 | 77.5999 | 77.5999 | 90% | 78.7576 | 47.8688 | 64.8839 | 69.5326 | 70.2488 | 70.7001 | 71.6993 | 74.0648 | 75.3524 | 77.8128 | 85.3 | 79.1183 | 77.9063 | 79.5329 | 83.095 | 80.6772 | 80.6772 | 80.6772 | 80.6772 | 80.6772 | 80.6772 | 80.6772 | 80.6772 | 80.6772 | 80.6772 | 80.6772 | 80.6772 | 80.6772 | 80.6772 | 80.6772 | 80.6772
85% | 236.8672 | 42.2486 | 58.5237 | 62.7489 | 63.4664 | 64.0232 | 64.9879 | 67.1875 | 68.6567 | 70.5214 | 71.4875 | 72.3351 | 70.7592 | 72.5978 | 75.4906 | 73.2888 | 73.2888 | 73.2888 | 73.2888 | 73.2888 | 73.2888 | 73.2888 | 73.2888 | 73.2888 | 73.2888 | 73.2888 | 73.2888 | 73.2888 | 73.2888 | 73.2888 | 73.2888 | 85% | 236.8672 | 45.2094 | 61.2792 | 65.6697 | 66.3461 | 66.7723 | 67.716 | 69.9501 | 71.1662 | 73.4899 | 80.5611 | 74.7228 | 73.5782 | 75.1144 | 78.4786 | 76.1951 | 76.1951 | 76.1951 | 76.1951 | 76.1951 | 76.1951 | 76.1951 | 76.1951 | 76.1951 | 76.1951 | 76.1951 | 76.1951 | 76.1951 | 76.1951 | 76.1951 | 76.1951
80% | 497.5104 | 39.7634 | 55.0811 | 59.0578 | 59.7331 | 60.2571 | 61.1651 | 63.2353 | 64.6181 | 66.3731 | 67.2823 | 68.08 | 66.5969 | 68.3274 | 71.05 | 68.9777 | 68.9777 | 68.9777 | 68.9777 | 68.9777 | 68.9777 | 68.9777 | 68.9777 | 68.9777 | 68.9777 | 68.9777 | 68.9777 | 68.9777 | 68.9777 | 68.9777 | 68.9777 | 80% | 497.5104 | 42.55 | 57.6746 | 61.8067 | 62.4434 | 62.8445 | 63.7327 | 65.8353 | 66.9799 | 69.167 | 75.8222 | 70.3274 | 69.2501 | 70.6959 | 73.8622 | 71.7131 | 71.7131 | 71.7131 | 71.7131 | 71.7131 | 71.7131 | 71.7131 | 71.7131 | 71.7131 | 71.7131 | 71.7131 | 71.7131 | 71.7131 | 71.7131 | 71.7131 | 71.7131
75% | 803.6248 | 37.2782 | 51.6385 | 55.3667 | 55.9997 | 56.4911 | 57.3423 | 59.2831 | 60.5795 | 62.2248 | 63.0772 | 63.825 | 62.4346 | 64.0569 | 66.6093 | 64.6665 | 64.6665 | 64.6665 | 64.6665 | 64.6665 | 64.6665 | 64.6665 | 64.6665 | 64.6665 | 64.6665 | 64.6665 | 64.6665 | 64.6665 | 64.6665 | 64.6665 | 64.6665 | 75% | 803.6248 | 39.8907 | 54.0699 | 57.9438 | 58.5407 | 58.9167 | 59.7494 | 61.7206 | 62.7937 | 64.844 | 71.0833 | 65.9319 | 64.9219 | 66.2774 | 69.2458 | 67.231 | 67.231 | 67.231 | 67.231 | 67.231 | 67.231 | 67.231 | 67.231 | 67.231 | 67.231 | 67.231 | 67.231 | 67.231 | 67.231 | 67.231 | 67.231
70% | 1155.2107 | 34.793 | 48.196 | 51.6756 | 52.2664 | 52.725 | 53.5194 | 55.3309 | 56.5408 | 58.0765 | 58.8721 | 59.57 | 58.2723 | 59.7865 | 62.1687 | 60.3554 | 60.3554 | 60.3554 | 60.3554 | 60.3554 | 60.3554 | 60.3554 | 60.3554 | 60.3554 | 60.3554 | 60.3554 | 60.3554 | 60.3554 | 60.3554 | 60.3554 | 60.3554 | 70% | 1155.2107 | 37.2313 | 50.4653 | 54.0809 | 54.638 | 54.989 | 55.7661 | 57.6059 | 58.6074 | 60.5211 | 66.3444 | 61.5365 | 60.5938 | 61.8589 | 64.6295 | 62.7489 | 62.7489 | 62.7489 | 62.7489 | 62.7489 | 62.7489 | 62.7489 | 62.7489 | 62.7489 | 62.7489 | 62.7489 | 62.7489 | 62.7489 | 62.7489 | 62.7489 | 62.7489
65% | 1553.1596 | 32.3077 | 44.7534 | 47.9845 | 48.5331 | 48.9589 | 49.6966 | 51.3787 | 52.5022 | 53.9282 | 54.6669 | 55.315 | 54.11 | 55.516 | 57.7281 | 56.0443 | 56.0443 | 56.0443 | 56.0443 | 56.0443 | 56.0443 | 56.0443 | 56.0443 | 56.0443 | 56.0443 | 56.0443 | 56.0443 | 56.0443 | 56.0443 | 56.0443 | 56.0443 | 65% | 1553.1596 | 34.5719 | 46.8606 | 50.218 | 50.7352 | 51.0612 | 51.7828 | 53.4912 | 54.4212 | 56.1982 | 61.6055 | 57.141 | 56.2657 | 57.4405 | 60.0131 | 58.2669 | 58.2669 | 58.2669 | 58.2669 | 58.2669 | 58.2669 | 58.2669 | 58.2669 | 58.2669 | 58.2669 | 58.2669 | 58.2669 | 58.2669 | 58.2669 | 58.2669 | 58.2669
60% | 2026.2996 | 29.8225 | 41.3108 | 44.2934 | 44.7998 | 45.1928 | 45.8738 | 47.4265 | 48.4636 | 49.7798 | 50.4618 | 51.06 | 49.9477 | 51.2455 | 53.2875 | 51.7332 | 51.7332 | 51.7332 | 51.7332 | 51.7332 | 51.7332 | 51.7332 | 51.7332 | 51.7332 | 51.7332 | 51.7332 | 51.7332 | 51.7332 | 51.7332 | 51.7332 | 51.7332 | 60% | 2026.2996 | 31.9125 | 43.2559 | 46.3551 | 46.8325 | 47.1334 | 47.7995 | 49.3765 | 50.235 | 51.8752 | 56.8666 | 52.7455 | 51.9376 | 53.022 | 55.3967 | 53.7848 | 53.7848 | 53.7848 | 53.7848 | 53.7848 | 53.7848 | 53.7848 | 53.7848 | 53.7848 | 53.7848 | 53.7848 | 53.7848 | 53.7848 | 53.7848 | 53.7848 | 53.7848
55% | 2598.4068 | 27.3373 | 37.8683 | 40.6023 | 41.0665 | 41.4268 | 42.051 | 43.4743 | 44.425 | 45.6315 | 46.2566 | 46.805 | 45.7854 | 46.9751 | 48.8469 | 47.4221 | 47.4221 | 47.4221 | 47.4221 | 47.4221 | 47.4221 | 47.4221 | 47.4221 | 47.4221 | 47.4221 | 47.4221 | 47.4221 | 47.4221 | 47.4221 | 47.4221 | 47.4221 | 55% | 2598.4068 | 29.2532 | 39.6513 | 42.4921 | 42.9298 | 43.2056 | 43.8162 | 45.2618 | 46.0487 | 47.5523 | 52.1278 | 48.3501 | 47.6094 | 48.6035 | 50.7803 | 49.3027 | 49.3027 | 49.3027 | 49.3027 | 49.3027 | 49.3027 | 49.3027 | 49.3027 | 49.3027 | 49.3027 | 49.3027 | 49.3027 | 49.3027 | 49.3027 | 49.3027 | 49.3027
50% | 3233.5201 | 24.8521 | 34.4257 | 36.9111 | 37.3332 | 37.6607 | 38.2282 | 39.5221 | 40.3863 | 41.4832 | 42.0515 | 42.55 | 41.623 | 42.7046 | 44.4062 | 43.111 | 43.111 | 43.111 | 43.111 | 43.111 | 43.111 | 43.111 | 43.111 | 43.111 | 43.111 | 43.111 | 43.111 | 43.111 | 43.111 | 43.111 | 43.111 | 50% | 3233.5201 | 26.5938 | 36.0466 | 38.6292 | 39.0271 | 39.2778 | 39.833 | 41.1471 | 41.8625 | 43.2294 | 47.3889 | 43.9546 | 43.2813 | 44.185 | 46.1639 | 44.8207 | 44.8207 | 44.8207 | 44.8207 | 44.8207 | 44.8207 | 44.8207 | 44.8207 | 44.8207 | 44.8207 | 44.8207 | 44.8207 | 44.8207 | 44.8207 | 44.8207 | 44.8207
45% | 3775.313 | 22.3669 | 30.9831 | 33.22 | 33.5998 | 33.8946 | 34.4054 | 35.5699 | 36.3477 | 37.3349 | 37.8463 | 38.295 | 37.4607 | 38.4342 | 39.9656 | 38.7999 | 38.7999 | 38.7999 | 38.7999 | 38.7999 | 38.7999 | 38.7999 | 38.7999 | 38.7999 | 38.7999 | 38.7999 | 38.7999 | 38.7999 | 38.7999 | 38.7999 | 38.7999 | 45% | 3775.313 | 23.9344 | 32.442 | 34.7663 | 35.1244 | 35.35 | 35.8497 | 37.0324 | 37.6762 | 38.9064 | 42.65 | 39.5591 | 38.9532 | 39.7665 | 41.5475 | 40.3386 | 40.3386 | 40.3386 | 40.3386 | 40.3386 | 40.3386 | 40.3386 | 40.3386 | 40.3386 | 40.3386 | 40.3386 | 40.3386 | 40.3386 | 40.3386 | 40.3386 | 40.3386
40% | 4072.8088 | 19.8817 | 27.5405 | 29.5289 | 29.8665 | 30.1286 | 30.5825 | 31.6176 | 32.3091 | 33.1866 | 33.6412 | 34.04 | 33.2984 | 34.1637 | 35.525 | 34.4888 | 34.4888 | 34.4888 | 34.4888 | 34.4888 | 34.4888 | 34.4888 | 34.4888 | 34.4888 | 34.4888 | 34.4888 | 34.4888 | 34.4888 | 34.4888 | 34.4888 | 34.4888 | 40% | 4072.8088 | 21.275 | 28.8373 | 30.9034 | 31.2217 | 31.4223 | 31.8664 | 32.9177 | 33.49 | 34.5835 | 37.9111 | 35.1637 | 34.625 | 35.348 | 36.9311 | 35.8565 | 35.8565 | 35.8565 | 35.8565 | 35.8565 | 35.8565 | 35.8565 | 35.8565 | 35.8565 | 35.8565 | 35.8565 | 35.8565 | 35.8565 | 35.8565 | 35.8565 | 35.8565
35% | 4198.821 | 17.3965 | 24.098 | 25.8378 | 26.1332 | 26.3625 | 26.7597 | 27.6654 | 28.2704 | 29.0382 | 29.436 | 29.785 | 29.1361 | 29.8932 | 31.0844 | 30.1777 | 30.1777 | 30.1777 | 30.1777 | 30.1777 | 30.1777 | 30.1777 | 30.1777 | 30.1777 | 30.1777 | 30.1777 | 30.1777 | 30.1777 | 30.1777 | 30.1777 | 30.1777 | 35% | 4198.821 | 18.6156 | 25.2326 | 27.0405 | 27.319 | 27.4945 | 27.8831 | 28.803 | 29.3037 | 30.2606 | 33.1722 | 30.7682 | 30.2969 | 30.9295 | 32.3147 | 31.3745 | 31.3745 | 31.3745 | 31.3745 | 31.3745 | 31.3745 | 31.3745 | 31.3745 | 31.3745 | 31.3745 | 31.3745 | 31.3745 | 31.3745 | 31.3745 | 31.3745 | 31.3745
30% | 4271.3374 | 14.9113 | 20.6554 | 22.1467 | 22.3999 | 22.5964 | 22.9369 | 23.7132 | 24.2318 | 24.8899 | 25.2309 | 25.53 | 24.9738 | 25.6228 | 26.6437 | 25.8666 | 25.8666 | 25.8666 | 25.8666 | 25.8666 | 25.8666 | 25.8666 | 25.8666 | 25.8666 | 25.8666 | 25.8666 | 25.8666 | 25.8666 | 25.8666 | 25.8666 | 25.8666 | 30% | 4271.3374 | 15.9563 | 21.628 | 23.1775 | 23.4163 | 23.5667 | 23.8998 | 24.6883 | 25.1175 | 25.9376 | 28.4333 | 26.3728 | 25.9688 | 26.511 | 27.6983 | 26.8924 | 26.8924 | 26.8924 | 26.8924 | 26.8924 | 26.8924 | 26.8924 | 26.8924 | 26.8924 | 26.8924 | 26.8924 | 26.8924 | 26.8924 | 26.8924 | 26.8924 | 26.8924
25% | 4321.8611 | 12.4261 | 17.2128 | 18.4556 | 18.6666 | 18.8304 | 19.1141 | 19.761 | 20.1932 | 20.7416 | 21.0257 | 21.275 | 20.8115 | 21.3523 | 22.2031 | 21.5555 | 21.5555 | 21.5555 | 21.5555 | 21.5555 | 21.5555 | 21.5555 | 21.5555 | 21.5555 | 21.5555 | 21.5555 | 21.5555 | 21.5555 | 21.5555 | 21.5555 | 21.5555 | 25% | 4321.8611 | 13.2969 | 18.0233 | 19.3146 | 19.5136 | 19.6389 | 19.9165 | 20.5735 | 20.9312 | 21.6147 | 23.6944 | 21.9773 | 21.6406 | 22.0925 | 23.0819 | 22.4103 | 22.4103 | 22.4103 | 22.4103 | 22.4103 | 22.4103 | 22.4103 | 22.4103 | 22.4103 | 22.4103 | 22.4103 | 22.4103 | 22.4103 | 22.4103 | 22.4103 | 22.4103
20% | 4353.067 | 9.9408 | 13.7703 | 14.7645 | 14.9333 | 15.0643 | 15.2913 | 15.8088 | 16.1545 | 16.5933 | 16.8206 | 17.02 | 16.6492 | 17.0818 | 17.7625 | 17.2444 | 17.2444 | 17.2444 | 17.2444 | 17.2444 | 17.2444 | 17.2444 | 17.2444 | 17.2444 | 17.2444 | 17.2444 | 17.2444 | 17.2444 | 17.2444 | 17.2444 | 17.2444 | 20% | 4353.067 | 10.6375 | 14.4186 | 15.4517 | 15.6108 | 15.7111 | 15.9332 | 16.4588 | 16.745 | 17.2917 | 18.9555 | 17.5818 | 17.3125 | 17.674 | 18.4656 | 17.9283 | 17.9283 | 17.9283 | 17.9283 | 17.9283 | 17.9283 | 17.9283 | 17.9283 | 17.9283 | 17.9283 | 17.9283 | 17.9283 | 17.9283 | 17.9283 | 17.9283 | 17.9283
15% | 4369.4129 | 7.4556 | 10.3277 | 11.0733 | 11.1999 | 11.2982 | 11.4685 | 11.8566 | 12.1159 | 12.445 | 12.6154 | 12.765 | 12.4869 | 12.8114 | 13.3219 | 12.9333 | 12.9333 | 12.9333 | 12.9333 | 12.9333 | 12.9333 | 12.9333 | 12.9333 | 12.9333 | 12.9333 | 12.9333 | 12.9333 | 12.9333 | 12.9333 | 12.9333 | 12.9333 | 15% | 4369.4129 | 7.9781 | 10.814 | 11.5888 | 11.7081 | 11.7833 | 11.9499 | 12.3441 | 12.5587 | 12.9688 | 14.2167 | 13.1864 | 12.9844 | 13.2555 | 13.8492 | 13.4462 | 13.4462 | 13.4462 | 13.4462 | 13.4462 | 13.4462 | 13.4462 | 13.4462 | 13.4462 | 13.4462 | 13.4462 | 13.4462 | 13.4462 | 13.4462 | 13.4462 | 13.4462
10% | 4378.6261 | 4.9704 | 6.8851 | 7.3822 | 7.4666 | 7.5321 | 7.6456 | 7.9044 | 8.0773 | 8.2966 | 8.4103 | 8.51 | 8.3246 | 8.5409 | 8.8812 | 8.6222 | 8.6222 | 8.6222 | 8.6222 | 8.6222 | 8.6222 | 8.6222 | 8.6222 | 8.6222 | 8.6222 | 8.6222 | 8.6222 | 8.6222 | 8.6222 | 8.6222 | 8.6222 | 10% | 4378.6261 | 5.3188 | 7.2093 | 7.7258 | 7.8054 | 7.8556 | 7.9666 | 8.2294 | 8.3725 | 8.6459 | 9.4778 | 8.7909 | 8.6563 | 8.837 | 9.2328 | 8.9641 | 8.9641 | 8.9641 | 8.9641 | 8.9641 | 8.9641 | 8.9641 | 8.9641 | 8.9641 | 8.9641 | 8.9641 | 8.9641 | 8.9641 | 8.9641 | 8.9641 | 8.9641
5% | 4391.7028 | 2.4852 | 3.4426 | 3.6911 | 3.7333 | 3.7661 | 3.8228 | 3.9522 | 4.0386 | 4.1483 | 4.2051 | 4.255 | 4.1623 | 4.2705 | 4.4406 | 4.3111 | 4.3111 | 4.3111 | 4.3111 | 4.3111 | 4.3111 | 4.3111 | 4.3111 | 4.3111 | 4.3111 | 4.3111 | 4.3111 | 4.3111 | 4.3111 | 4.3111 | 4.3111 | 5% | 4391.7028 | 2.6594 | 3.6047 | 3.8629 | 3.9027 | 3.9278 | 3.9833 | 4.1147 | 4.1862 | 4.3229 | 4.7389 | 4.3955 | 4.3281 | 4.4185 | 4.6164 | 4.4821 | 4.4821 | 4.4821 | 4.4821 | 4.4821 | 4.4821 | 4.4821 | 4.4821 | 4.4821 | 4.4821 | 4.4821 | 4.4821 | 4.4821 | 4.4821 | 4.4821 | 4.4821
9.992e-14% | 4391.7028 | 4.9664e-14 | 6.8796e-14 | 7.3763e-14 | 7.4607e-14 | 7.5261e-14 | 7.6395e-14 | 7.8981e-14 | 8.0708e-14 | 8.29e-14 | 8.4036e-14 | 8.5032e-14 | 8.318e-14 | 8.5341e-14 | 8.8741e-14 | 8.6153e-14 | 8.6153e-14 | 8.6153e-14 | 8.6153e-14 | 8.6153e-14 | 8.6153e-14 | 8.6153e-14 | 8.6153e-14 | 8.6153e-14 | 8.6153e-14 | 8.6153e-14 | 8.6153e-14 | 8.6153e-14 | 8.6153e-14 | 8.6153e-14 | 8.6153e-14 | 9.992e-14% | 4391.7028 | 5.3145e-14 | 7.2036e-14 | 7.7197e-14 | 7.7992e-14 | 7.8493e-14 | 7.9602e-14 | 8.2228e-14 | 8.3658e-14 | 8.639e-14 | 9.4702e-14 | 8.7839e-14 | 8.6493e-14 | 8.8299e-14 | 9.2254e-14 | 8.957e-14 | 8.957e-14 | 8.957e-14 | 8.957e-14 | 8.957e-14 | 8.957e-14 | 8.957e-14 | 8.957e-14 | 8.957e-14 | 8.957e-14 | 8.957e-14 | 8.957e-14 | 8.957e-14 | 8.957e-14 | 8.957e-14 | 8.957e-14
Summer Season | [31 empty] | Summer Season
P50 | [31 empty] | P10
% of MD | Summer - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Summer - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 56.4483 | 74.8831 | 79.898 | 79.7498 | 79.7414 | 80.3113 | 80.9369 | 82.2223 | 83.1461 | 83.6463 | 84.1925 | 84.6932 | 85.5997 | 86.7253 | 86.6445 | 86.6445 | 86.6445 | 86.6445 | 86.6445 | 86.6445 | 86.6445 | 86.6445 | 86.6445 | 86.6445 | 86.6445 | 86.6445 | 86.6445 | 86.6445 | 86.6445 | 86.6445 | 100% | 0 | 62.901 | 81.3728 | 86.203 | 85.9109 | 85.9284 | 86.4219 | 87.7284 | 88.6008 | 89.4561 | 90.4569 | 91.3826 | 92.2827 | 92.383 | 93.434 | 92.6325 | 92.6325 | 92.6325 | 92.6325 | 92.6325 | 92.6325 | 92.6325 | 92.6325 | 92.6325 | 92.6325 | 92.6325 | 92.6325 | 92.6325 | 92.6325 | 92.6325 | 92.6325
99% | 0 | 55.8838 | 74.1343 | 79.099 | 78.9523 | 78.944 | 79.5082 | 80.1275 | 81.4 | 82.3146 | 82.8098 | 83.3506 | 83.8463 | 84.7437 | 85.858 | 85.778 | 85.778 | 85.778 | 85.778 | 85.778 | 85.778 | 85.778 | 85.778 | 85.778 | 85.778 | 85.778 | 85.778 | 85.778 | 85.778 | 85.778 | 85.778 | 99% | 1.5127 | 62.272 | 80.559 | 85.341 | 85.0518 | 85.0691 | 85.5577 | 86.8512 | 87.7148 | 88.5615 | 89.5523 | 90.4688 | 91.3598 | 91.4592 | 92.4996 | 91.7061 | 91.7061 | 91.7061 | 91.7061 | 91.7061 | 91.7061 | 91.7061 | 91.7061 | 91.7061 | 91.7061 | 91.7061 | 91.7061 | 91.7061 | 91.7061 | 91.7061 | 91.7061
98% | 0 | 55.3193 | 73.3854 | 78.3 | 78.1548 | 78.1466 | 78.7051 | 79.3181 | 80.5778 | 81.4832 | 81.9734 | 82.5086 | 82.9994 | 83.8877 | 84.9908 | 84.9116 | 84.9116 | 84.9116 | 84.9116 | 84.9116 | 84.9116 | 84.9116 | 84.9116 | 84.9116 | 84.9116 | 84.9116 | 84.9116 | 84.9116 | 84.9116 | 84.9116 | 84.9116 | 98% | 2.269 | 61.643 | 79.7453 | 84.4789 | 84.1927 | 84.2098 | 84.6935 | 85.9739 | 86.8287 | 87.667 | 88.6477 | 89.555 | 90.437 | 90.5354 | 91.5653 | 90.7798 | 90.7798 | 90.7798 | 90.7798 | 90.7798 | 90.7798 | 90.7798 | 90.7798 | 90.7798 | 90.7798 | 90.7798 | 90.7798 | 90.7798 | 90.7798 | 90.7798 | 90.7798
97% | 0.37816 | 54.7549 | 72.6366 | 77.501 | 77.3573 | 77.3492 | 77.902 | 78.5088 | 79.7556 | 80.6517 | 81.1369 | 81.6667 | 82.1524 | 83.0317 | 84.1235 | 84.0451 | 84.0451 | 84.0451 | 84.0451 | 84.0451 | 84.0451 | 84.0451 | 84.0451 | 84.0451 | 84.0451 | 84.0451 | 84.0451 | 84.0451 | 84.0451 | 84.0451 | 84.0451 | 97% | 3.7816 | 61.014 | 78.9316 | 83.6169 | 83.3336 | 83.3505 | 83.8292 | 85.0966 | 85.9427 | 86.7724 | 87.7432 | 88.6411 | 89.5142 | 89.6115 | 90.631 | 89.8535 | 89.8535 | 89.8535 | 89.8535 | 89.8535 | 89.8535 | 89.8535 | 89.8535 | 89.8535 | 89.8535 | 89.8535 | 89.8535 | 89.8535 | 89.8535 | 89.8535 | 89.8535
95% | 2.269 | 53.6259 | 71.1389 | 75.9031 | 75.7623 | 75.7544 | 76.2958 | 76.89 | 78.1112 | 78.9888 | 79.464 | 79.9829 | 80.4586 | 81.3197 | 82.389 | 82.3122 | 82.3122 | 82.3122 | 82.3122 | 82.3122 | 82.3122 | 82.3122 | 82.3122 | 82.3122 | 82.3122 | 82.3122 | 82.3122 | 82.3122 | 82.3122 | 82.3122 | 82.3122 | 95% | 6.0506 | 59.7559 | 77.3041 | 81.8928 | 81.6153 | 81.632 | 82.1008 | 83.342 | 84.1707 | 84.9833 | 85.934 | 86.8135 | 87.6685 | 87.7639 | 88.7623 | 88.0008 | 88.0008 | 88.0008 | 88.0008 | 88.0008 | 88.0008 | 88.0008 | 88.0008 | 88.0008 | 88.0008 | 88.0008 | 88.0008 | 88.0008 | 88.0008 | 88.0008 | 88.0008
90% | 5.6725 | 50.8035 | 67.3948 | 71.9082 | 71.7748 | 71.7673 | 72.2802 | 72.8432 | 74 | 74.8315 | 75.2817 | 75.7732 | 76.2239 | 77.0397 | 78.0527 | 77.98 | 77.98 | 77.98 | 77.98 | 77.98 | 77.98 | 77.98 | 77.98 | 77.98 | 77.98 | 77.98 | 77.98 | 77.98 | 77.98 | 77.98 | 77.98 | 90% | 16.2611 | 56.6109 | 73.2355 | 77.5827 | 77.3198 | 77.3355 | 77.7797 | 78.9556 | 79.7407 | 80.5105 | 81.4112 | 82.2444 | 83.0544 | 83.1447 | 84.0906 | 83.3692 | 83.3692 | 83.3692 | 83.3692 | 83.3692 | 83.3692 | 83.3692 | 83.3692 | 83.3692 | 83.3692 | 83.3692 | 83.3692 | 83.3692 | 83.3692 | 83.3692 | 83.3692
85% | 15.8829 | 47.9811 | 63.6506 | 67.9133 | 67.7874 | 67.7802 | 68.2646 | 68.7963 | 69.8889 | 70.6742 | 71.0994 | 71.5636 | 71.9893 | 72.7598 | 73.7165 | 73.6478 | 73.6478 | 73.6478 | 73.6478 | 73.6478 | 73.6478 | 73.6478 | 73.6478 | 73.6478 | 73.6478 | 73.6478 | 73.6478 | 73.6478 | 73.6478 | 73.6478 | 73.6478 | 85% | 26.4715 | 53.4658 | 69.1669 | 73.2725 | 73.0243 | 73.0391 | 73.4586 | 74.5692 | 75.3106 | 76.0377 | 76.8883 | 77.6752 | 78.4403 | 78.5256 | 79.4189 | 78.7376 | 78.7376 | 78.7376 | 78.7376 | 78.7376 | 78.7376 | 78.7376 | 78.7376 | 78.7376 | 78.7376 | 78.7376 | 78.7376 | 78.7376 | 78.7376 | 78.7376 | 78.7376
80% | 31.0095 | 45.1586 | 59.9065 | 63.9184 | 63.7999 | 63.7932 | 64.2491 | 64.7495 | 65.7778 | 66.5169 | 66.917 | 67.354 | 67.7546 | 68.4798 | 69.3802 | 69.3156 | 69.3156 | 69.3156 | 69.3156 | 69.3156 | 69.3156 | 69.3156 | 69.3156 | 69.3156 | 69.3156 | 69.3156 | 69.3156 | 69.3156 | 69.3156 | 69.3156 | 69.3156 | 80% | 34.0348 | 50.3208 | 65.0982 | 68.9624 | 68.7287 | 68.7427 | 69.1375 | 70.1827 | 70.8806 | 71.5649 | 72.3655 | 73.1061 | 73.8261 | 73.9064 | 74.7472 | 74.106 | 74.106 | 74.106 | 74.106 | 74.106 | 74.106 | 74.106 | 74.106 | 74.106 | 74.106 | 74.106 | 74.106 | 74.106 | 74.106 | 74.106 | 74.106
75% | 72.9857 | 42.3362 | 56.1623 | 59.9235 | 59.8124 | 59.8061 | 60.2335 | 60.7027 | 61.6667 | 62.3596 | 62.7347 | 63.1444 | 63.5199 | 64.1998 | 65.044 | 64.9833 | 64.9833 | 64.9833 | 64.9833 | 64.9833 | 64.9833 | 64.9833 | 64.9833 | 64.9833 | 64.9833 | 64.9833 | 64.9833 | 64.9833 | 64.9833 | 64.9833 | 64.9833 | 75% | 48.405 | 47.1757 | 61.0296 | 64.6522 | 64.4332 | 64.4463 | 64.8164 | 65.7963 | 66.4506 | 67.0921 | 67.8427 | 68.537 | 69.212 | 69.2873 | 70.0755 | 69.4744 | 69.4744 | 69.4744 | 69.4744 | 69.4744 | 69.4744 | 69.4744 | 69.4744 | 69.4744 | 69.4744 | 69.4744 | 69.4744 | 69.4744 | 69.4744 | 69.4744 | 69.4744
70% | 150.5094 | 39.5138 | 52.4182 | 55.9286 | 55.8249 | 55.819 | 56.2179 | 56.6558 | 57.5556 | 58.2023 | 58.5524 | 58.9347 | 59.2853 | 59.9198 | 60.7077 | 60.6511 | 60.6511 | 60.6511 | 60.6511 | 60.6511 | 60.6511 | 60.6511 | 60.6511 | 60.6511 | 60.6511 | 60.6511 | 60.6511 | 60.6511 | 60.6511 | 60.6511 | 60.6511 | 70% | 76.3892 | 44.0307 | 56.9609 | 60.3421 | 60.1376 | 60.1499 | 60.4953 | 61.4099 | 62.0205 | 62.6193 | 63.3198 | 63.9678 | 64.5979 | 64.6681 | 65.4038 | 64.8427 | 64.8427 | 64.8427 | 64.8427 | 64.8427 | 64.8427 | 64.8427 | 64.8427 | 64.8427 | 64.8427 | 64.8427 | 64.8427 | 64.8427 | 64.8427 | 64.8427 | 64.8427
65% | 359.6342 | 36.6914 | 48.674 | 51.9337 | 51.8374 | 51.8319 | 52.2024 | 52.609 | 53.4445 | 54.045 | 54.3701 | 54.7251 | 55.0506 | 55.6398 | 56.3714 | 56.3189 | 56.3189 | 56.3189 | 56.3189 | 56.3189 | 56.3189 | 56.3189 | 56.3189 | 56.3189 | 56.3189 | 56.3189 | 56.3189 | 56.3189 | 56.3189 | 56.3189 | 56.3189 | 65% | 114.2056 | 40.8856 | 52.8923 | 56.0319 | 55.8421 | 55.8534 | 56.1742 | 57.0235 | 57.5905 | 58.1465 | 58.797 | 59.3987 | 59.9837 | 60.049 | 60.7321 | 60.2111 | 60.2111 | 60.2111 | 60.2111 | 60.2111 | 60.2111 | 60.2111 | 60.2111 | 60.2111 | 60.2111 | 60.2111 | 60.2111 | 60.2111 | 60.2111 | 60.2111 | 60.2111
60% | 689.7717 | 33.869 | 44.9299 | 47.9388 | 47.8499 | 47.8449 | 48.1868 | 48.5621 | 49.3334 | 49.8876 | 50.1878 | 50.5155 | 50.8159 | 51.3598 | 52.0352 | 51.9867 | 51.9867 | 51.9867 | 51.9867 | 51.9867 | 51.9867 | 51.9867 | 51.9867 | 51.9867 | 51.9867 | 51.9867 | 51.9867 | 51.9867 | 51.9867 | 51.9867 | 51.9867 | 60% | 178.1154 | 37.7406 | 48.8237 | 51.7218 | 51.5465 | 51.557 | 51.8531 | 52.6371 | 53.1605 | 53.6736 | 54.2741 | 54.8296 | 55.3696 | 55.4298 | 56.0604 | 55.5795 | 55.5795 | 55.5795 | 55.5795 | 55.5795 | 55.5795 | 55.5795 | 55.5795 | 55.5795 | 55.5795 | 55.5795 | 55.5795 | 55.5795 | 55.5795 | 55.5795 | 55.5795
55% | 1095.5419 | 31.0466 | 41.1857 | 43.9439 | 43.8624 | 43.8578 | 44.1712 | 44.5153 | 45.2222 | 45.7303 | 46.0055 | 46.3059 | 46.5813 | 47.0798 | 47.6989 | 47.6545 | 47.6545 | 47.6545 | 47.6545 | 47.6545 | 47.6545 | 47.6545 | 47.6545 | 47.6545 | 47.6545 | 47.6545 | 47.6545 | 47.6545 | 47.6545 | 47.6545 | 47.6545 | 55% | 311.6074 | 34.5955 | 44.755 | 47.4116 | 47.251 | 47.2606 | 47.532 | 48.2506 | 48.7304 | 49.2008 | 49.7513 | 50.2604 | 50.7555 | 50.8107 | 51.3887 | 50.9479 | 50.9479 | 50.9479 | 50.9479 | 50.9479 | 50.9479 | 50.9479 | 50.9479 | 50.9479 | 50.9479 | 50.9479 | 50.9479 | 50.9479 | 50.9479 | 50.9479 | 50.9479
50% | 1666.1918 | 28.2242 | 37.4415 | 39.949 | 39.8749 | 39.8707 | 40.1557 | 40.4684 | 41.1111 | 41.573 | 41.8231 | 42.0962 | 42.3466 | 42.7999 | 43.3626 | 43.3222 | 43.3222 | 43.3222 | 43.3222 | 43.3222 | 43.3222 | 43.3222 | 43.3222 | 43.3222 | 43.3222 | 43.3222 | 43.3222 | 43.3222 | 43.3222 | 43.3222 | 43.3222 | 50% | 636.0723 | 31.4505 | 40.6864 | 43.1015 | 42.9554 | 42.9642 | 43.211 | 43.8642 | 44.3004 | 44.728 | 45.2284 | 45.6913 | 46.1413 | 46.1915 | 46.717 | 46.3162 | 46.3162 | 46.3162 | 46.3162 | 46.3162 | 46.3162 | 46.3162 | 46.3162 | 46.3162 | 46.3162 | 46.3162 | 46.3162 | 46.3162 | 46.3162 | 46.3162 | 46.3162
45% | 2506.0947 | 25.4017 | 33.6974 | 35.9541 | 35.8874 | 35.8837 | 36.1401 | 36.4216 | 37 | 37.4157 | 37.6408 | 37.8866 | 38.112 | 38.5199 | 39.0264 | 38.99 | 38.99 | 38.99 | 38.99 | 38.99 | 38.99 | 38.99 | 38.99 | 38.99 | 38.99 | 38.99 | 38.99 | 38.99 | 38.99 | 38.99 | 38.99 | 45% | 1179.4944 | 28.3054 | 36.6177 | 38.7913 | 38.6599 | 38.6678 | 38.8899 | 39.4778 | 39.8703 | 40.2552 | 40.7056 | 41.1222 | 41.5272 | 41.5724 | 42.0453 | 41.6846 | 41.6846 | 41.6846 | 41.6846 | 41.6846 | 41.6846 | 41.6846 | 41.6846 | 41.6846 | 41.6846 | 41.6846 | 41.6846 | 41.6846 | 41.6846 | 41.6846 | 41.6846
40% | 3164.4787 | 22.5793 | 29.9532 | 31.9592 | 31.8999 | 31.8966 | 32.1245 | 32.3748 | 32.8889 | 33.2584 | 33.4585 | 33.677 | 33.8773 | 34.2399 | 34.6901 | 34.6578 | 34.6578 | 34.6578 | 34.6578 | 34.6578 | 34.6578 | 34.6578 | 34.6578 | 34.6578 | 34.6578 | 34.6578 | 34.6578 | 34.6578 | 34.6578 | 34.6578 | 34.6578 | 40% | 1808.3816 | 25.1604 | 32.5491 | 34.4812 | 34.3644 | 34.3713 | 34.5688 | 35.0914 | 35.4403 | 35.7824 | 36.1827 | 36.553 | 36.9131 | 36.9532 | 37.3736 | 37.053 | 37.053 | 37.053 | 37.053 | 37.053 | 37.053 | 37.053 | 37.053 | 37.053 | 37.053 | 37.053 | 37.053 | 37.053 | 37.053 | 37.053 | 37.053
35% | 3551.3408 | 19.7569 | 26.2091 | 27.9643 | 27.9124 | 27.9095 | 28.109 | 28.3279 | 28.7778 | 29.1011 | 29.2762 | 29.4674 | 29.6426 | 29.9599 | 30.3538 | 30.3256 | 30.3256 | 30.3256 | 30.3256 | 30.3256 | 30.3256 | 30.3256 | 30.3256 | 30.3256 | 30.3256 | 30.3256 | 30.3256 | 30.3256 | 30.3256 | 30.3256 | 30.3256 | 35% | 2779.1293 | 22.0153 | 28.4805 | 30.171 | 30.0688 | 30.0749 | 30.2477 | 30.705 | 31.0103 | 31.3096 | 31.6599 | 31.9839 | 32.2989 | 32.3341 | 32.7019 | 32.4214 | 32.4214 | 32.4214 | 32.4214 | 32.4214 | 32.4214 | 32.4214 | 32.4214 | 32.4214 | 32.4214 | 32.4214 | 32.4214 | 32.4214 | 32.4214 | 32.4214 | 32.4214
30% | 3758.953 | 16.9345 | 22.4649 | 23.9694 | 23.9249 | 23.9224 | 24.0934 | 24.2811 | 24.6667 | 24.9438 | 25.0939 | 25.2577 | 25.408 | 25.6799 | 26.0176 | 25.9933 | 25.9933 | 25.9933 | 25.9933 | 25.9933 | 25.9933 | 25.9933 | 25.9933 | 25.9933 | 25.9933 | 25.9933 | 25.9933 | 25.9933 | 25.9933 | 25.9933 | 25.9933 | 30% | 3814.165 | 18.8703 | 24.4118 | 25.8609 | 25.7733 | 25.7785 | 25.9266 | 26.3185 | 26.5802 | 26.8368 | 27.1371 | 27.4148 | 27.6848 | 27.7149 | 28.0302 | 27.7897 | 27.7897 | 27.7897 | 27.7897 | 27.7897 | 27.7897 | 27.7897 | 27.7897 | 27.7897 | 27.7897 | 27.7897 | 27.7897 | 27.7897 | 27.7897 | 27.7897 | 27.7897
25% | 3926.4798 | 14.1121 | 18.7208 | 19.9745 | 19.9375 | 19.9354 | 20.0778 | 20.2342 | 20.5556 | 20.7865 | 20.9116 | 21.0481 | 21.1733 | 21.3999 | 21.6813 | 21.6611 | 21.6611 | 21.6611 | 21.6611 | 21.6611 | 21.6611 | 21.6611 | 21.6611 | 21.6611 | 21.6611 | 21.6611 | 21.6611 | 21.6611 | 21.6611 | 21.6611 | 21.6611 | 25% | 4166.9923 | 15.7252 | 20.3432 | 21.5507 | 21.4777 | 21.4821 | 21.6055 | 21.9321 | 22.1502 | 22.364 | 22.6142 | 22.8457 | 23.0707 | 23.0958 | 23.3585 | 23.1581 | 23.1581 | 23.1581 | 23.1581 | 23.1581 | 23.1581 | 23.1581 | 23.1581 | 23.1581 | 23.1581 | 23.1581 | 23.1581 | 23.1581 | 23.1581 | 23.1581 | 23.1581
20% | 4050.5177 | 11.2897 | 14.9766 | 15.9796 | 15.95 | 15.9483 | 16.0623 | 16.1874 | 16.4445 | 16.6292 | 16.7293 | 16.8385 | 16.9386 | 17.1199 | 17.3451 | 17.3289 | 17.3289 | 17.3289 | 17.3289 | 17.3289 | 17.3289 | 17.3289 | 17.3289 | 17.3289 | 17.3289 | 17.3289 | 17.3289 | 17.3289 | 17.3289 | 17.3289 | 17.3289 | 20% | 4282.7105 | 12.5802 | 16.2746 | 17.2406 | 17.1822 | 17.1857 | 17.2844 | 17.5457 | 17.7202 | 17.8912 | 18.0914 | 18.2765 | 18.4565 | 18.4766 | 18.6868 | 18.5265 | 18.5265 | 18.5265 | 18.5265 | 18.5265 | 18.5265 | 18.5265 | 18.5265 | 18.5265 | 18.5265 | 18.5265 | 18.5265 | 18.5265 | 18.5265 | 18.5265 | 18.5265
15% | 4152.622 | 8.4672 | 11.2325 | 11.9847 | 11.9625 | 11.9612 | 12.0467 | 12.1405 | 12.3333 | 12.4719 | 12.5469 | 12.6289 | 12.704 | 12.84 | 13.0088 | 12.9967 | 12.9967 | 12.9967 | 12.9967 | 12.9967 | 12.9967 | 12.9967 | 12.9967 | 12.9967 | 12.9967 | 12.9967 | 12.9967 | 12.9967 | 12.9967 | 12.9967 | 12.9967 | 15% | 4364.7722 | 9.4351 | 12.2059 | 12.9304 | 12.8866 | 12.8893 | 12.9633 | 13.1593 | 13.2901 | 13.4184 | 13.5685 | 13.7074 | 13.8424 | 13.8575 | 14.0151 | 13.8949 | 13.8949 | 13.8949 | 13.8949 | 13.8949 | 13.8949 | 13.8949 | 13.8949 | 13.8949 | 13.8949 | 13.8949 | 13.8949 | 13.8949 | 13.8949 | 13.8949 | 13.8949
10% | 4248.2976 | 5.6448 | 7.4883 | 7.9898 | 7.975 | 7.9741 | 8.0311 | 8.0937 | 8.2222 | 8.3146 | 8.3646 | 8.4192 | 8.4693 | 8.56 | 8.6725 | 8.6644 | 8.6644 | 8.6644 | 8.6644 | 8.6644 | 8.6644 | 8.6644 | 8.6644 | 8.6644 | 8.6644 | 8.6644 | 8.6644 | 8.6644 | 8.6644 | 8.6644 | 8.6644 | 10% | 4391.6218 | 6.2901 | 8.1373 | 8.6203 | 8.5911 | 8.5928 | 8.6422 | 8.7728 | 8.8601 | 8.9456 | 9.0457 | 9.1383 | 9.2283 | 9.2383 | 9.3434 | 9.2632 | 9.2632 | 9.2632 | 9.2632 | 9.2632 | 9.2632 | 9.2632 | 9.2632 | 9.2632 | 9.2632 | 9.2632 | 9.2632 | 9.2632 | 9.2632 | 9.2632 | 9.2632
5% | 4361.7469 | 2.8224 | 3.7442 | 3.9949 | 3.9875 | 3.9871 | 4.0156 | 4.0468 | 4.1111 | 4.1573 | 4.1823 | 4.2096 | 4.2347 | 4.28 | 4.3363 | 4.3322 | 4.3322 | 4.3322 | 4.3322 | 4.3322 | 4.3322 | 4.3322 | 4.3322 | 4.3322 | 4.3322 | 4.3322 | 4.3322 | 4.3322 | 4.3322 | 4.3322 | 4.3322 | 5% | 4391.6218 | 3.145 | 4.0686 | 4.3101 | 4.2955 | 4.2964 | 4.3211 | 4.3864 | 4.43 | 4.4728 | 4.5228 | 4.5691 | 4.6141 | 4.6192 | 4.6717 | 4.6316 | 4.6316 | 4.6316 | 4.6316 | 4.6316 | 4.6316 | 4.6316 | 4.6316 | 4.6316 | 4.6316 | 4.6316 | 4.6316 | 4.6316 | 4.6316 | 4.6316 | 4.6316
9.992e-14% | 4391.6218 | 5.6403e-14 | 7.4823e-14 | 7.9834e-14 | 7.9686e-14 | 7.9678e-14 | 8.0247e-14 | 8.0872e-14 | 8.2157e-14 | 8.308e-14 | 8.3579e-14 | 8.4125e-14 | 8.4626e-14 | 8.5531e-14 | 8.6656e-14 | 8.6575e-14 | 8.6575e-14 | 8.6575e-14 | 8.6575e-14 | 8.6575e-14 | 8.6575e-14 | 8.6575e-14 | 8.6575e-14 | 8.6575e-14 | 8.6575e-14 | 8.6575e-14 | 8.6575e-14 | 8.6575e-14 | 8.6575e-14 | 8.6575e-14 | 8.6575e-14 | 9.992e-14% | 4391.6218 | 6.2851e-14 | 8.1308e-14 | 8.6134e-14 | 8.5842e-14 | 8.586e-14 | 8.6353e-14 | 8.7658e-14 | 8.853e-14 | 8.9385e-14 | 9.0385e-14 | 9.131e-14 | 9.2209e-14 | 9.2309e-14 | 9.3359e-14 | 9.2558e-14 | 9.2558e-14 | 9.2558e-14 | 9.2558e-14 | 9.2558e-14 | 9.2558e-14 | 9.2558e-14 | 9.2558e-14 | 9.2558e-14 | 9.2558e-14 | 9.2558e-14 | 9.2558e-14 | 9.2558e-14 | 9.2558e-14 | 9.2558e-14 | 9.2558e-14
Option 2
Winter Season | [31 empty] | Winter Season
P50 | [31 empty] | P10
% of MD | Winter - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Winter - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 49.7042 | 68.8514 | 73.8223 | 55.333 | 55.9881 | 57.123 | 59.7108 | 61.4393 | 63.6331 | 64.7696 | 65.7667 | 63.9128 | 66.0759 | 69.4791 | 66.8887 | 66.8887 | 66.8887 | 66.8887 | 66.8887 | 66.8887 | 66.8887 | 66.8887 | 66.8887 | 66.8887 | 66.8887 | 66.8887 | 66.8887 | 66.8887 | 66.8887 | 66.8887 | 100% | 0 | 53.1876 | 72.0932 | 77.2584 | 58.7209 | 59.2223 | 60.3326 | 62.9609 | 64.3916 | 67.1254 | 75.4444 | 68.5759 | 67.2293 | 69.0366 | 72.9945 | 70.308 | 70.308 | 70.308 | 70.308 | 70.308 | 70.308 | 70.308 | 70.308 | 70.308 | 70.308 | 70.308 | 70.308 | 70.308 | 70.308 | 70.308 | 70.308
99% | 1.486 | 49.2072 | 68.1629 | 73.0841 | 54.7797 | 55.4282 | 56.5518 | 59.1137 | 60.8249 | 62.9967 | 64.1219 | 65.1091 | 63.2736 | 65.4151 | 68.7843 | 66.2198 | 66.2198 | 66.2198 | 66.2198 | 66.2198 | 66.2198 | 66.2198 | 66.2198 | 66.2198 | 66.2198 | 66.2198 | 66.2198 | 66.2198 | 66.2198 | 66.2198 | 66.2198 | 99% | 1.486 | 52.6557 | 71.3723 | 76.4858 | 58.1337 | 58.6301 | 59.7292 | 62.3312 | 63.7477 | 66.4541 | 74.69 | 67.8901 | 66.557 | 68.3462 | 72.2645 | 69.6049 | 69.6049 | 69.6049 | 69.6049 | 69.6049 | 69.6049 | 69.6049 | 69.6049 | 69.6049 | 69.6049 | 69.6049 | 69.6049 | 69.6049 | 69.6049 | 69.6049 | 69.6049
98% | 3.2692 | 48.7101 | 67.4743 | 72.3458 | 54.2263 | 54.8683 | 55.9805 | 58.5166 | 60.2105 | 62.3604 | 63.4742 | 64.4514 | 62.6345 | 64.7544 | 68.0895 | 65.551 | 65.551 | 65.551 | 65.551 | 65.551 | 65.551 | 65.551 | 65.551 | 65.551 | 65.551 | 65.551 | 65.551 | 65.551 | 65.551 | 65.551 | 65.551 | 98% | 3.2692 | 52.1238 | 70.6514 | 75.7133 | 57.5465 | 58.0379 | 59.1259 | 61.7016 | 63.1038 | 65.7829 | 73.9355 | 67.2044 | 65.8847 | 67.6559 | 71.5346 | 68.9018 | 68.9018 | 68.9018 | 68.9018 | 68.9018 | 68.9018 | 68.9018 | 68.9018 | 68.9018 | 68.9018 | 68.9018 | 68.9018 | 68.9018 | 68.9018 | 68.9018 | 68.9018
97% | 6.8356 | 48.2131 | 66.7858 | 71.6076 | 53.673 | 54.3084 | 55.4093 | 57.9195 | 59.5961 | 61.7241 | 62.8265 | 63.7937 | 61.9954 | 64.0936 | 67.3948 | 64.8821 | 64.8821 | 64.8821 | 64.8821 | 64.8821 | 64.8821 | 64.8821 | 64.8821 | 64.8821 | 64.8821 | 64.8821 | 64.8821 | 64.8821 | 64.8821 | 64.8821 | 64.8821 | 97% | 6.8356 | 51.5919 | 69.9304 | 74.9407 | 56.9593 | 57.4457 | 58.5226 | 61.072 | 62.4598 | 65.1116 | 73.1811 | 66.5186 | 65.2124 | 66.9655 | 70.8046 | 68.1987 | 68.1987 | 68.1987 | 68.1987 | 68.1987 | 68.1987 | 68.1987 | 68.1987 | 68.1987 | 68.1987 | 68.1987 | 68.1987 | 68.1987 | 68.1987 | 68.1987 | 68.1987
95% | 17.5347 | 47.219 | 65.4088 | 70.1312 | 52.5663 | 53.1887 | 54.2669 | 56.7252 | 58.3673 | 60.4514 | 61.5311 | 62.4784 | 60.7171 | 62.7721 | 66.0052 | 63.5443 | 63.5443 | 63.5443 | 63.5443 | 63.5443 | 63.5443 | 63.5443 | 63.5443 | 63.5443 | 63.5443 | 63.5443 | 63.5443 | 63.5443 | 63.5443 | 63.5443 | 63.5443 | 95% | 17.5347 | 50.5282 | 68.4886 | 73.3955 | 55.7848 | 56.2612 | 57.3159 | 59.8128 | 61.172 | 63.7691 | 71.6722 | 65.1471 | 63.8678 | 65.5848 | 69.3447 | 66.7926 | 66.7926 | 66.7926 | 66.7926 | 66.7926 | 66.7926 | 66.7926 | 66.7926 | 66.7926 | 66.7926 | 66.7926 | 66.7926 | 66.7926 | 66.7926 | 66.7926 | 66.7926
90% | 78.7576 | 44.7338 | 61.9662 | 66.4401 | 49.7997 | 50.3893 | 51.4107 | 53.7397 | 55.2954 | 57.2697 | 58.2926 | 59.1901 | 57.5215 | 59.4683 | 62.5312 | 60.1999 | 60.1999 | 60.1999 | 60.1999 | 60.1999 | 60.1999 | 60.1999 | 60.1999 | 60.1999 | 60.1999 | 60.1999 | 60.1999 | 60.1999 | 60.1999 | 60.1999 | 60.1999 | 90% | 78.7576 | 47.8688 | 64.8839 | 69.5326 | 52.8488 | 53.3001 | 54.2993 | 56.6648 | 57.9524 | 60.4128 | 67.9 | 61.7183 | 60.5063 | 62.1329 | 65.695 | 63.2772 | 63.2772 | 63.2772 | 63.2772 | 63.2772 | 63.2772 | 63.2772 | 63.2772 | 63.2772 | 63.2772 | 63.2772 | 63.2772 | 63.2772 | 63.2772 | 63.2772 | 63.2772
85% | 236.8672 | 42.2486 | 58.5237 | 62.7489 | 47.033 | 47.5899 | 48.5546 | 50.7542 | 52.2234 | 54.0881 | 55.0542 | 55.9017 | 54.3258 | 56.1645 | 59.0573 | 56.8554 | 56.8554 | 56.8554 | 56.8554 | 56.8554 | 56.8554 | 56.8554 | 56.8554 | 56.8554 | 56.8554 | 56.8554 | 56.8554 | 56.8554 | 56.8554 | 56.8554 | 56.8554 | 85% | 236.8672 | 45.2094 | 61.2792 | 65.6697 | 49.9128 | 50.339 | 51.2827 | 53.5167 | 54.7329 | 57.0566 | 64.1278 | 58.2895 | 57.1449 | 58.6811 | 62.0453 | 59.7618 | 59.7618 | 59.7618 | 59.7618 | 59.7618 | 59.7618 | 59.7618 | 59.7618 | 59.7618 | 59.7618 | 59.7618 | 59.7618 | 59.7618 | 59.7618 | 59.7618 | 59.7618
80% | 497.5104 | 39.7634 | 55.0811 | 59.0578 | 44.2664 | 44.7905 | 45.6984 | 47.7686 | 49.1514 | 50.9064 | 51.8157 | 52.6134 | 51.1302 | 52.8607 | 55.5833 | 53.511 | 53.511 | 53.511 | 53.511 | 53.511 | 53.511 | 53.511 | 53.511 | 53.511 | 53.511 | 53.511 | 53.511 | 53.511 | 53.511 | 53.511 | 53.511 | 80% | 497.5104 | 42.55 | 57.6746 | 61.8067 | 46.9767 | 47.3779 | 48.2661 | 50.3687 | 51.5133 | 53.7003 | 60.3555 | 54.8607 | 53.7834 | 55.2293 | 58.3956 | 56.2464 | 56.2464 | 56.2464 | 56.2464 | 56.2464 | 56.2464 | 56.2464 | 56.2464 | 56.2464 | 56.2464 | 56.2464 | 56.2464 | 56.2464 | 56.2464 | 56.2464 | 56.2464
75% | 803.6248 | 37.2782 | 51.6385 | 55.3667 | 41.4997 | 41.9911 | 42.8423 | 44.7831 | 46.0795 | 47.7248 | 48.5772 | 49.325 | 47.9346 | 49.5569 | 52.1093 | 50.1665 | 50.1665 | 50.1665 | 50.1665 | 50.1665 | 50.1665 | 50.1665 | 50.1665 | 50.1665 | 50.1665 | 50.1665 | 50.1665 | 50.1665 | 50.1665 | 50.1665 | 50.1665 | 75% | 803.6248 | 39.8907 | 54.0699 | 57.9438 | 44.0407 | 44.4167 | 45.2494 | 47.2206 | 48.2937 | 50.344 | 56.5833 | 51.4319 | 50.4219 | 51.7774 | 54.7458 | 52.731 | 52.731 | 52.731 | 52.731 | 52.731 | 52.731 | 52.731 | 52.731 | 52.731 | 52.731 | 52.731 | 52.731 | 52.731 | 52.731 | 52.731 | 52.731
70% | 1155.2107 | 34.793 | 48.196 | 51.6756 | 38.7331 | 39.1916 | 39.9861 | 41.7975 | 43.0075 | 44.5431 | 45.3387 | 46.0367 | 44.7389 | 46.2531 | 48.6354 | 46.8221 | 46.8221 | 46.8221 | 46.8221 | 46.8221 | 46.8221 | 46.8221 | 46.8221 | 46.8221 | 46.8221 | 46.8221 | 46.8221 | 46.8221 | 46.8221 | 46.8221 | 46.8221 | 70% | 1155.2107 | 37.2313 | 50.4653 | 54.0809 | 41.1046 | 41.4556 | 42.2328 | 44.0726 | 45.0741 | 46.9878 | 52.8111 | 48.0031 | 47.0605 | 48.3256 | 51.0961 | 49.2156 | 49.2156 | 49.2156 | 49.2156 | 49.2156 | 49.2156 | 49.2156 | 49.2156 | 49.2156 | 49.2156 | 49.2156 | 49.2156 | 49.2156 | 49.2156 | 49.2156 | 49.2156
65% | 1553.1596 | 32.3077 | 44.7534 | 47.9845 | 35.9664 | 36.3922 | 37.13 | 38.812 | 39.9355 | 41.3615 | 42.1002 | 42.7484 | 41.5433 | 42.9493 | 45.1614 | 43.4777 | 43.4777 | 43.4777 | 43.4777 | 43.4777 | 43.4777 | 43.4777 | 43.4777 | 43.4777 | 43.4777 | 43.4777 | 43.4777 | 43.4777 | 43.4777 | 43.4777 | 43.4777 | 65% | 1553.1596 | 34.5719 | 46.8606 | 50.218 | 38.1686 | 38.4945 | 39.2162 | 40.9246 | 41.8545 | 43.6315 | 49.0389 | 44.5743 | 43.699 | 44.8738 | 47.4464 | 45.7002 | 45.7002 | 45.7002 | 45.7002 | 45.7002 | 45.7002 | 45.7002 | 45.7002 | 45.7002 | 45.7002 | 45.7002 | 45.7002 | 45.7002 | 45.7002 | 45.7002 | 45.7002
60% | 2026.2996 | 29.8225 | 41.3108 | 44.2934 | 33.1998 | 33.5928 | 34.2738 | 35.8265 | 36.8636 | 38.1798 | 38.8618 | 39.46 | 38.3477 | 39.6455 | 41.6875 | 40.1332 | 40.1332 | 40.1332 | 40.1332 | 40.1332 | 40.1332 | 40.1332 | 40.1332 | 40.1332 | 40.1332 | 40.1332 | 40.1332 | 40.1332 | 40.1332 | 40.1332 | 40.1332 | 60% | 2026.2996 | 31.9125 | 43.2559 | 46.3551 | 35.2325 | 35.5334 | 36.1995 | 37.7765 | 38.635 | 40.2752 | 45.2666 | 41.1455 | 40.3376 | 41.422 | 43.7967 | 42.1848 | 42.1848 | 42.1848 | 42.1848 | 42.1848 | 42.1848 | 42.1848 | 42.1848 | 42.1848 | 42.1848 | 42.1848 | 42.1848 | 42.1848 | 42.1848 | 42.1848 | 42.1848
55% | 2598.4068 | 27.3373 | 37.8683 | 40.6023 | 30.4331 | 30.7934 | 31.4177 | 32.8409 | 33.7916 | 34.9982 | 35.6233 | 36.1717 | 35.152 | 36.3417 | 38.2135 | 36.7888 | 36.7888 | 36.7888 | 36.7888 | 36.7888 | 36.7888 | 36.7888 | 36.7888 | 36.7888 | 36.7888 | 36.7888 | 36.7888 | 36.7888 | 36.7888 | 36.7888 | 36.7888 | 55% | 2598.4068 | 29.2532 | 39.6513 | 42.4921 | 32.2965 | 32.5723 | 33.1829 | 34.6285 | 35.4154 | 36.919 | 41.4944 | 37.7167 | 36.9761 | 37.9701 | 40.147 | 38.6694 | 38.6694 | 38.6694 | 38.6694 | 38.6694 | 38.6694 | 38.6694 | 38.6694 | 38.6694 | 38.6694 | 38.6694 | 38.6694 | 38.6694 | 38.6694 | 38.6694 | 38.6694
50% | 3233.5201 | 24.8521 | 34.4257 | 36.9111 | 27.6665 | 27.994 | 28.5615 | 29.8554 | 30.7197 | 31.8165 | 32.3848 | 32.8834 | 31.9564 | 33.0379 | 34.7396 | 33.4444 | 33.4444 | 33.4444 | 33.4444 | 33.4444 | 33.4444 | 33.4444 | 33.4444 | 33.4444 | 33.4444 | 33.4444 | 33.4444 | 33.4444 | 33.4444 | 33.4444 | 33.4444 | 50% | 3233.5201 | 26.5938 | 36.0466 | 38.6292 | 29.3604 | 29.6112 | 30.1663 | 31.4804 | 32.1958 | 33.5627 | 37.7222 | 34.2879 | 33.6146 | 34.5183 | 36.4972 | 35.154 | 35.154 | 35.154 | 35.154 | 35.154 | 35.154 | 35.154 | 35.154 | 35.154 | 35.154 | 35.154 | 35.154 | 35.154 | 35.154 | 35.154 | 35.154
45% | 3775.313 | 22.3669 | 30.9831 | 33.22 | 24.8998 | 25.1946 | 25.7054 | 26.8699 | 27.6477 | 28.6349 | 29.1463 | 29.595 | 28.7607 | 29.7342 | 31.2656 | 30.0999 | 30.0999 | 30.0999 | 30.0999 | 30.0999 | 30.0999 | 30.0999 | 30.0999 | 30.0999 | 30.0999 | 30.0999 | 30.0999 | 30.0999 | 30.0999 | 30.0999 | 30.0999 | 45% | 3775.313 | 23.9344 | 32.442 | 34.7663 | 26.4244 | 26.65 | 27.1497 | 28.3324 | 28.9762 | 30.2064 | 33.95 | 30.8591 | 30.2532 | 31.0665 | 32.8475 | 31.6386 | 31.6386 | 31.6386 | 31.6386 | 31.6386 | 31.6386 | 31.6386 | 31.6386 | 31.6386 | 31.6386 | 31.6386 | 31.6386 | 31.6386 | 31.6386 | 31.6386 | 31.6386
40% | 4072.8088 | 19.8817 | 27.5405 | 29.5289 | 22.1332 | 22.3952 | 22.8492 | 23.8843 | 24.5757 | 25.4532 | 25.9078 | 26.3067 | 25.5651 | 26.4304 | 27.7917 | 26.7555 | 26.7555 | 26.7555 | 26.7555 | 26.7555 | 26.7555 | 26.7555 | 26.7555 | 26.7555 | 26.7555 | 26.7555 | 26.7555 | 26.7555 | 26.7555 | 26.7555 | 26.7555 | 40% | 4072.8088 | 21.275 | 28.8373 | 30.9034 | 23.4884 | 23.6889 | 24.133 | 25.1843 | 25.7566 | 26.8502 | 30.1778 | 27.4304 | 26.8917 | 27.6146 | 29.1978 | 28.1232 | 28.1232 | 28.1232 | 28.1232 | 28.1232 | 28.1232 | 28.1232 | 28.1232 | 28.1232 | 28.1232 | 28.1232 | 28.1232 | 28.1232 | 28.1232 | 28.1232 | 28.1232
35% | 4198.821 | 17.3965 | 24.098 | 25.8378 | 19.3665 | 19.5958 | 19.9931 | 20.8988 | 21.5038 | 22.2716 | 22.6694 | 23.0184 | 22.3695 | 23.1266 | 24.3177 | 23.4111 | 23.4111 | 23.4111 | 23.4111 | 23.4111 | 23.4111 | 23.4111 | 23.4111 | 23.4111 | 23.4111 | 23.4111 | 23.4111 | 23.4111 | 23.4111 | 23.4111 | 23.4111 | 35% | 4198.821 | 18.6156 | 25.2326 | 27.0405 | 20.5523 | 20.7278 | 21.1164 | 22.0363 | 22.5371 | 23.4939 | 26.4055 | 24.0016 | 23.5302 | 24.1628 | 25.5481 | 24.6078 | 24.6078 | 24.6078 | 24.6078 | 24.6078 | 24.6078 | 24.6078 | 24.6078 | 24.6078 | 24.6078 | 24.6078 | 24.6078 | 24.6078 | 24.6078 | 24.6078 | 24.6078
30% | 4271.3374 | 14.9113 | 20.6554 | 22.1467 | 16.5999 | 16.7964 | 17.1369 | 17.9132 | 18.4318 | 19.0899 | 19.4309 | 19.73 | 19.1738 | 19.8228 | 20.8437 | 20.0666 | 20.0666 | 20.0666 | 20.0666 | 20.0666 | 20.0666 | 20.0666 | 20.0666 | 20.0666 | 20.0666 | 20.0666 | 20.0666 | 20.0666 | 20.0666 | 20.0666 | 20.0666 | 30% | 4271.3374 | 15.9563 | 21.628 | 23.1775 | 17.6163 | 17.7667 | 18.0998 | 18.8883 | 19.3175 | 20.1376 | 22.6333 | 20.5728 | 20.1688 | 20.711 | 21.8983 | 21.0924 | 21.0924 | 21.0924 | 21.0924 | 21.0924 | 21.0924 | 21.0924 | 21.0924 | 21.0924 | 21.0924 | 21.0924 | 21.0924 | 21.0924 | 21.0924 | 21.0924 | 21.0924
25% | 4321.8611 | 12.4261 | 17.2128 | 18.4556 | 13.8332 | 13.997 | 14.2808 | 14.9277 | 15.3598 | 15.9083 | 16.1924 | 16.4417 | 15.9782 | 16.519 | 17.3698 | 16.7222 | 16.7222 | 16.7222 | 16.7222 | 16.7222 | 16.7222 | 16.7222 | 16.7222 | 16.7222 | 16.7222 | 16.7222 | 16.7222 | 16.7222 | 16.7222 | 16.7222 | 16.7222 | 25% | 4321.8611 | 13.2969 | 18.0233 | 19.3146 | 14.6802 | 14.8056 | 15.0831 | 15.7402 | 16.0979 | 16.7813 | 18.8611 | 17.144 | 16.8073 | 17.2591 | 18.2486 | 17.577 | 17.577 | 17.577 | 17.577 | 17.577 | 17.577 | 17.577 | 17.577 | 17.577 | 17.577 | 17.577 | 17.577 | 17.577 | 17.577 | 17.577 | 17.577
20% | 4353.067 | 9.9408 | 13.7703 | 14.7645 | 11.0666 | 11.1976 | 11.4246 | 11.9422 | 12.2879 | 12.7266 | 12.9539 | 13.1533 | 12.7826 | 13.2152 | 13.8958 | 13.3777 | 13.3777 | 13.3777 | 13.3777 | 13.3777 | 13.3777 | 13.3777 | 13.3777 | 13.3777 | 13.3777 | 13.3777 | 13.3777 | 13.3777 | 13.3777 | 13.3777 | 13.3777 | 20% | 4353.067 | 10.6375 | 14.4186 | 15.4517 | 11.7442 | 11.8445 | 12.0665 | 12.5922 | 12.8783 | 13.4251 | 15.0889 | 13.7152 | 13.4459 | 13.8073 | 14.5989 | 14.0616 | 14.0616 | 14.0616 | 14.0616 | 14.0616 | 14.0616 | 14.0616 | 14.0616 | 14.0616 | 14.0616 | 14.0616 | 14.0616 | 14.0616 | 14.0616 | 14.0616 | 14.0616
15% | 4369.4129 | 7.4556 | 10.3277 | 11.0733 | 8.2999 | 8.3982 | 8.5685 | 8.9566 | 9.2159 | 9.545 | 9.7154 | 9.865 | 9.5869 | 9.9114 | 10.4219 | 10.0333 | 10.0333 | 10.0333 | 10.0333 | 10.0333 | 10.0333 | 10.0333 | 10.0333 | 10.0333 | 10.0333 | 10.0333 | 10.0333 | 10.0333 | 10.0333 | 10.0333 | 10.0333 | 15% | 4369.4129 | 7.9781 | 10.814 | 11.5888 | 8.8081 | 8.8833 | 9.0499 | 9.4441 | 9.6587 | 10.0688 | 11.3167 | 10.2864 | 10.0844 | 10.3555 | 10.9492 | 10.5462 | 10.5462 | 10.5462 | 10.5462 | 10.5462 | 10.5462 | 10.5462 | 10.5462 | 10.5462 | 10.5462 | 10.5462 | 10.5462 | 10.5462 | 10.5462 | 10.5462 | 10.5462
10% | 4378.6261 | 4.9704 | 6.8851 | 7.3822 | 5.5333 | 5.5988 | 5.7123 | 5.9711 | 6.1439 | 6.3633 | 6.477 | 6.5767 | 6.3913 | 6.6076 | 6.9479 | 6.6889 | 6.6889 | 6.6889 | 6.6889 | 6.6889 | 6.6889 | 6.6889 | 6.6889 | 6.6889 | 6.6889 | 6.6889 | 6.6889 | 6.6889 | 6.6889 | 6.6889 | 6.6889 | 10% | 4378.6261 | 5.3188 | 7.2093 | 7.7258 | 5.8721 | 5.9222 | 6.0333 | 6.2961 | 6.4392 | 6.7125 | 7.5444 | 6.8576 | 6.7229 | 6.9037 | 7.2994 | 7.0308 | 7.0308 | 7.0308 | 7.0308 | 7.0308 | 7.0308 | 7.0308 | 7.0308 | 7.0308 | 7.0308 | 7.0308 | 7.0308 | 7.0308 | 7.0308 | 7.0308 | 7.0308
5% | 4391.7028 | 2.4852 | 3.4426 | 3.6911 | 2.7666 | 2.7994 | 2.8562 | 2.9855 | 3.072 | 3.1817 | 3.2385 | 3.2883 | 3.1956 | 3.3038 | 3.474 | 3.3444 | 3.3444 | 3.3444 | 3.3444 | 3.3444 | 3.3444 | 3.3444 | 3.3444 | 3.3444 | 3.3444 | 3.3444 | 3.3444 | 3.3444 | 3.3444 | 3.3444 | 3.3444 | 5% | 4391.7028 | 2.6594 | 3.6047 | 3.8629 | 2.936 | 2.9611 | 3.0166 | 3.148 | 3.2196 | 3.3563 | 3.7722 | 3.4288 | 3.3615 | 3.4518 | 3.6497 | 3.5154 | 3.5154 | 3.5154 | 3.5154 | 3.5154 | 3.5154 | 3.5154 | 3.5154 | 3.5154 | 3.5154 | 3.5154 | 3.5154 | 3.5154 | 3.5154 | 3.5154 | 3.5154
9.992e-14% | 4391.7028 | 4.9664e-14 | 6.8796e-14 | 7.3763e-14 | 5.5289e-14 | 5.5943e-14 | 5.7077e-14 | 5.9663e-14 | 6.139e-14 | 6.3582e-14 | 6.4718e-14 | 6.5714e-14 | 6.3862e-14 | 6.6023e-14 | 6.9424e-14 | 6.6835e-14 | 6.6835e-14 | 6.6835e-14 | 6.6835e-14 | 6.6835e-14 | 6.6835e-14 | 6.6835e-14 | 6.6835e-14 | 6.6835e-14 | 6.6835e-14 | 6.6835e-14 | 6.6835e-14 | 6.6835e-14 | 6.6835e-14 | 6.6835e-14 | 6.6835e-14 | 9.992e-14% | 4391.7028 | 5.3145e-14 | 7.2036e-14 | 7.7197e-14 | 5.8674e-14 | 5.9175e-14 | 6.0284e-14 | 6.2911e-14 | 6.434e-14 | 6.7072e-14 | 7.5384e-14 | 6.8521e-14 | 6.7176e-14 | 6.8981e-14 | 7.2936e-14 | 7.0252e-14 | 7.0252e-14 | 7.0252e-14 | 7.0252e-14 | 7.0252e-14 | 7.0252e-14 | 7.0252e-14 | 7.0252e-14 | 7.0252e-14 | 7.0252e-14 | 7.0252e-14 | 7.0252e-14 | 7.0252e-14 | 7.0252e-14 | 7.0252e-14 | 7.0252e-14
Summer Season | [31 empty] | Summer Season
P50 | [31 empty] | P10
% of MD | Summer - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Summer - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 56.4483 | 74.8831 | 79.898 | 60.4165 | 60.4081 | 60.978 | 61.6035 | 62.8889 | 63.8127 | 64.313 | 64.8592 | 65.3599 | 66.2664 | 67.3919 | 67.3111 | 67.3111 | 67.3111 | 67.3111 | 67.3111 | 67.3111 | 67.3111 | 67.3111 | 67.3111 | 67.3111 | 67.3111 | 67.3111 | 67.3111 | 67.3111 | 67.3111 | 67.3111 | 100% | 0 | 62.901 | 81.3728 | 86.203 | 66.5776 | 66.595 | 67.0886 | 68.3951 | 69.2674 | 70.1227 | 71.1235 | 72.0493 | 72.9493 | 73.0497 | 74.1006 | 73.2991 | 73.2991 | 73.2991 | 73.2991 | 73.2991 | 73.2991 | 73.2991 | 73.2991 | 73.2991 | 73.2991 | 73.2991 | 73.2991 | 73.2991 | 73.2991 | 73.2991 | 73.2991
99% | 0 | 55.8838 | 74.1343 | 79.099 | 59.8123 | 59.804 | 60.3682 | 60.9875 | 62.26 | 63.1746 | 63.6698 | 64.2106 | 64.7063 | 65.6037 | 66.718 | 66.638 | 66.638 | 66.638 | 66.638 | 66.638 | 66.638 | 66.638 | 66.638 | 66.638 | 66.638 | 66.638 | 66.638 | 66.638 | 66.638 | 66.638 | 66.638 | 99% | 1.5127 | 62.272 | 80.559 | 85.341 | 65.9118 | 65.9291 | 66.4177 | 67.7112 | 68.5748 | 69.4215 | 70.4123 | 71.3288 | 72.2198 | 72.3192 | 73.3596 | 72.5661 | 72.5661 | 72.5661 | 72.5661 | 72.5661 | 72.5661 | 72.5661 | 72.5661 | 72.5661 | 72.5661 | 72.5661 | 72.5661 | 72.5661 | 72.5661 | 72.5661 | 72.5661
98% | 0 | 55.3193 | 73.3854 | 78.3 | 59.2082 | 59.1999 | 59.7584 | 60.3715 | 61.6312 | 62.5365 | 63.0267 | 63.562 | 64.0527 | 64.941 | 66.0441 | 65.9649 | 65.9649 | 65.9649 | 65.9649 | 65.9649 | 65.9649 | 65.9649 | 65.9649 | 65.9649 | 65.9649 | 65.9649 | 65.9649 | 65.9649 | 65.9649 | 65.9649 | 65.9649 | 98% | 2.269 | 61.643 | 79.7453 | 84.4789 | 65.246 | 65.2631 | 65.7468 | 67.0272 | 67.8821 | 68.7203 | 69.7011 | 70.6083 | 71.4904 | 71.5887 | 72.6186 | 71.8332 | 71.8332 | 71.8332 | 71.8332 | 71.8332 | 71.8332 | 71.8332 | 71.8332 | 71.8332 | 71.8332 | 71.8332 | 71.8332 | 71.8332 | 71.8332 | 71.8332 | 71.8332
97% | 0.37816 | 54.7549 | 72.6366 | 77.501 | 58.604 | 58.5959 | 59.1487 | 59.7554 | 61.0023 | 61.8984 | 62.3836 | 62.9134 | 63.3991 | 64.2784 | 65.3702 | 65.2918 | 65.2918 | 65.2918 | 65.2918 | 65.2918 | 65.2918 | 65.2918 | 65.2918 | 65.2918 | 65.2918 | 65.2918 | 65.2918 | 65.2918 | 65.2918 | 65.2918 | 65.2918 | 97% | 3.7816 | 61.014 | 78.9316 | 83.6169 | 64.5802 | 64.5972 | 65.0759 | 66.3432 | 67.1894 | 68.0191 | 68.9898 | 69.8878 | 70.7609 | 70.8582 | 71.8776 | 71.1002 | 71.1002 | 71.1002 | 71.1002 | 71.1002 | 71.1002 | 71.1002 | 71.1002 | 71.1002 | 71.1002 | 71.1002 | 71.1002 | 71.1002 | 71.1002 | 71.1002 | 71.1002
95% | 2.269 | 53.6259 | 71.1389 | 75.9031 | 57.3957 | 57.3877 | 57.9291 | 58.5234 | 59.7445 | 60.6221 | 61.0973 | 61.6162 | 62.0919 | 62.9531 | 64.0223 | 63.9456 | 63.9456 | 63.9456 | 63.9456 | 63.9456 | 63.9456 | 63.9456 | 63.9456 | 63.9456 | 63.9456 | 63.9456 | 63.9456 | 63.9456 | 63.9456 | 63.9456 | 63.9456 | 95% | 6.0506 | 59.7559 | 77.3041 | 81.8928 | 63.2487 | 63.2653 | 63.7341 | 64.9753 | 65.8041 | 66.6166 | 67.5674 | 68.4468 | 69.3019 | 69.3972 | 70.3956 | 69.6342 | 69.6342 | 69.6342 | 69.6342 | 69.6342 | 69.6342 | 69.6342 | 69.6342 | 69.6342 | 69.6342 | 69.6342 | 69.6342 | 69.6342 | 69.6342 | 69.6342 | 69.6342
90% | 5.6725 | 50.8035 | 67.3948 | 71.9082 | 54.3748 | 54.3673 | 54.8802 | 55.4432 | 56.6 | 57.4315 | 57.8817 | 58.3732 | 58.8239 | 59.6397 | 60.6527 | 60.58 | 60.58 | 60.58 | 60.58 | 60.58 | 60.58 | 60.58 | 60.58 | 60.58 | 60.58 | 60.58 | 60.58 | 60.58 | 60.58 | 60.58 | 60.58 | 90% | 16.2611 | 56.6109 | 73.2355 | 77.5827 | 59.9198 | 59.9355 | 60.3797 | 61.5556 | 62.3407 | 63.1105 | 64.0112 | 64.8444 | 65.6544 | 65.7447 | 66.6906 | 65.9692 | 65.9692 | 65.9692 | 65.9692 | 65.9692 | 65.9692 | 65.9692 | 65.9692 | 65.9692 | 65.9692 | 65.9692 | 65.9692 | 65.9692 | 65.9692 | 65.9692 | 65.9692
85% | 15.8829 | 47.9811 | 63.6506 | 67.9133 | 51.354 | 51.3469 | 51.8313 | 52.363 | 53.4556 | 54.2408 | 54.666 | 55.1303 | 55.5559 | 56.3264 | 57.2831 | 57.2145 | 57.2145 | 57.2145 | 57.2145 | 57.2145 | 57.2145 | 57.2145 | 57.2145 | 57.2145 | 57.2145 | 57.2145 | 57.2145 | 57.2145 | 57.2145 | 57.2145 | 57.2145 | 85% | 26.4715 | 53.4658 | 69.1669 | 73.2725 | 56.5909 | 56.6058 | 57.0253 | 58.1358 | 58.8773 | 59.6043 | 60.455 | 61.2419 | 62.0069 | 62.0922 | 62.9855 | 62.3043 | 62.3043 | 62.3043 | 62.3043 | 62.3043 | 62.3043 | 62.3043 | 62.3043 | 62.3043 | 62.3043 | 62.3043 | 62.3043 | 62.3043 | 62.3043 | 62.3043 | 62.3043
80% | 31.0095 | 45.1586 | 59.9065 | 63.9184 | 48.3332 | 48.3265 | 48.7824 | 49.2828 | 50.3111 | 51.0502 | 51.4504 | 51.8873 | 52.2879 | 53.0131 | 53.9136 | 53.8489 | 53.8489 | 53.8489 | 53.8489 | 53.8489 | 53.8489 | 53.8489 | 53.8489 | 53.8489 | 53.8489 | 53.8489 | 53.8489 | 53.8489 | 53.8489 | 53.8489 | 53.8489 | 80% | 34.0348 | 50.3208 | 65.0982 | 68.9624 | 53.262 | 53.276 | 53.6709 | 54.7161 | 55.4139 | 56.0982 | 56.8988 | 57.6394 | 58.3595 | 58.4397 | 59.2805 | 58.6393 | 58.6393 | 58.6393 | 58.6393 | 58.6393 | 58.6393 | 58.6393 | 58.6393 | 58.6393 | 58.6393 | 58.6393 | 58.6393 | 58.6393 | 58.6393 | 58.6393 | 58.6393
75% | 72.9857 | 42.3362 | 56.1623 | 59.9235 | 45.3124 | 45.3061 | 45.7335 | 46.2027 | 47.1667 | 47.8596 | 48.2347 | 48.6444 | 49.0199 | 49.6998 | 50.544 | 50.4833 | 50.4833 | 50.4833 | 50.4833 | 50.4833 | 50.4833 | 50.4833 | 50.4833 | 50.4833 | 50.4833 | 50.4833 | 50.4833 | 50.4833 | 50.4833 | 50.4833 | 50.4833 | 75% | 48.405 | 47.1757 | 61.0296 | 64.6522 | 49.9332 | 49.9463 | 50.3164 | 51.2963 | 51.9506 | 52.5921 | 53.3427 | 54.037 | 54.712 | 54.7873 | 55.5755 | 54.9744 | 54.9744 | 54.9744 | 54.9744 | 54.9744 | 54.9744 | 54.9744 | 54.9744 | 54.9744 | 54.9744 | 54.9744 | 54.9744 | 54.9744 | 54.9744 | 54.9744 | 54.9744
70% | 150.5094 | 39.5138 | 52.4182 | 55.9286 | 42.2915 | 42.2857 | 42.6846 | 43.1225 | 44.0223 | 44.6689 | 45.0191 | 45.4014 | 45.7519 | 46.3865 | 47.1744 | 47.1178 | 47.1178 | 47.1178 | 47.1178 | 47.1178 | 47.1178 | 47.1178 | 47.1178 | 47.1178 | 47.1178 | 47.1178 | 47.1178 | 47.1178 | 47.1178 | 47.1178 | 47.1178 | 70% | 76.3892 | 44.0307 | 56.9609 | 60.3421 | 46.6043 | 46.6165 | 46.962 | 47.8766 | 48.4872 | 49.0859 | 49.7865 | 50.4345 | 51.0645 | 51.1348 | 51.8704 | 51.3094 | 51.3094 | 51.3094 | 51.3094 | 51.3094 | 51.3094 | 51.3094 | 51.3094 | 51.3094 | 51.3094 | 51.3094 | 51.3094 | 51.3094 | 51.3094 | 51.3094 | 51.3094
65% | 359.6342 | 36.6914 | 48.674 | 51.9337 | 39.2707 | 39.2653 | 39.6357 | 40.0423 | 40.8778 | 41.4783 | 41.8034 | 42.1584 | 42.4839 | 43.0731 | 43.8048 | 43.7522 | 43.7522 | 43.7522 | 43.7522 | 43.7522 | 43.7522 | 43.7522 | 43.7522 | 43.7522 | 43.7522 | 43.7522 | 43.7522 | 43.7522 | 43.7522 | 43.7522 | 43.7522 | 65% | 114.2056 | 40.8856 | 52.8923 | 56.0319 | 43.2754 | 43.2868 | 43.6076 | 44.4568 | 45.0238 | 45.5798 | 46.2303 | 46.832 | 47.4171 | 47.4823 | 48.1654 | 47.6444 | 47.6444 | 47.6444 | 47.6444 | 47.6444 | 47.6444 | 47.6444 | 47.6444 | 47.6444 | 47.6444 | 47.6444 | 47.6444 | 47.6444 | 47.6444 | 47.6444 | 47.6444
60% | 689.7717 | 33.869 | 44.9299 | 47.9388 | 36.2499 | 36.2449 | 36.5868 | 36.9621 | 37.7334 | 38.2876 | 38.5878 | 38.9155 | 39.2159 | 39.7598 | 40.4352 | 40.3867 | 40.3867 | 40.3867 | 40.3867 | 40.3867 | 40.3867 | 40.3867 | 40.3867 | 40.3867 | 40.3867 | 40.3867 | 40.3867 | 40.3867 | 40.3867 | 40.3867 | 40.3867 | 60% | 178.1154 | 37.7406 | 48.8237 | 51.7218 | 39.9465 | 39.957 | 40.2531 | 41.0371 | 41.5605 | 42.0736 | 42.6741 | 43.2296 | 43.7696 | 43.8298 | 44.4604 | 43.9795 | 43.9795 | 43.9795 | 43.9795 | 43.9795 | 43.9795 | 43.9795 | 43.9795 | 43.9795 | 43.9795 | 43.9795 | 43.9795 | 43.9795 | 43.9795 | 43.9795 | 43.9795
55% | 1095.5419 | 31.0466 | 41.1857 | 43.9439 | 33.2291 | 33.2245 | 33.5379 | 33.882 | 34.5889 | 35.097 | 35.3721 | 35.6725 | 35.9479 | 36.4465 | 37.0656 | 37.0211 | 37.0211 | 37.0211 | 37.0211 | 37.0211 | 37.0211 | 37.0211 | 37.0211 | 37.0211 | 37.0211 | 37.0211 | 37.0211 | 37.0211 | 37.0211 | 37.0211 | 37.0211 | 55% | 311.6074 | 34.5955 | 44.755 | 47.4116 | 36.6177 | 36.6273 | 36.8987 | 37.6173 | 38.0971 | 38.5675 | 39.1179 | 39.6271 | 40.1221 | 40.1773 | 40.7553 | 40.3145 | 40.3145 | 40.3145 | 40.3145 | 40.3145 | 40.3145 | 40.3145 | 40.3145 | 40.3145 | 40.3145 | 40.3145 | 40.3145 | 40.3145 | 40.3145 | 40.3145 | 40.3145
50% | 1666.1918 | 28.2242 | 37.4415 | 39.949 | 30.2082 | 30.2041 | 30.489 | 30.8018 | 31.4445 | 31.9064 | 32.1565 | 32.4296 | 32.68 | 33.1332 | 33.696 | 33.6556 | 33.6556 | 33.6556 | 33.6556 | 33.6556 | 33.6556 | 33.6556 | 33.6556 | 33.6556 | 33.6556 | 33.6556 | 33.6556 | 33.6556 | 33.6556 | 33.6556 | 33.6556 | 50% | 636.0723 | 31.4505 | 40.6864 | 43.1015 | 33.2888 | 33.2975 | 33.5443 | 34.1976 | 34.6337 | 35.0614 | 35.5618 | 36.0246 | 36.4747 | 36.5248 | 37.0503 | 36.6496 | 36.6496 | 36.6496 | 36.6496 | 36.6496 | 36.6496 | 36.6496 | 36.6496 | 36.6496 | 36.6496 | 36.6496 | 36.6496 | 36.6496 | 36.6496 | 36.6496 | 36.6496
45% | 2506.0947 | 25.4017 | 33.6974 | 35.9541 | 27.1874 | 27.1837 | 27.4401 | 27.7216 | 28.3 | 28.7157 | 28.9408 | 29.1866 | 29.412 | 29.8199 | 30.3264 | 30.29 | 30.29 | 30.29 | 30.29 | 30.29 | 30.29 | 30.29 | 30.29 | 30.29 | 30.29 | 30.29 | 30.29 | 30.29 | 30.29 | 30.29 | 30.29 | 45% | 1179.4944 | 28.3054 | 36.6177 | 38.7913 | 29.9599 | 29.9678 | 30.1899 | 30.7778 | 31.1703 | 31.5552 | 32.0056 | 32.4222 | 32.8272 | 32.8724 | 33.3453 | 32.9846 | 32.9846 | 32.9846 | 32.9846 | 32.9846 | 32.9846 | 32.9846 | 32.9846 | 32.9846 | 32.9846 | 32.9846 | 32.9846 | 32.9846 | 32.9846 | 32.9846 | 32.9846
40% | 3164.4787 | 22.5793 | 29.9532 | 31.9592 | 24.1666 | 24.1632 | 24.3912 | 24.6414 | 25.1556 | 25.5251 | 25.7252 | 25.9437 | 26.144 | 26.5065 | 26.9568 | 26.9245 | 26.9245 | 26.9245 | 26.9245 | 26.9245 | 26.9245 | 26.9245 | 26.9245 | 26.9245 | 26.9245 | 26.9245 | 26.9245 | 26.9245 | 26.9245 | 26.9245 | 26.9245 | 40% | 1808.3816 | 25.1604 | 32.5491 | 34.4812 | 26.631 | 26.638 | 26.8354 | 27.358 | 27.707 | 28.0491 | 28.4494 | 28.8197 | 29.1797 | 29.2199 | 29.6403 | 29.3197 | 29.3197 | 29.3197 | 29.3197 | 29.3197 | 29.3197 | 29.3197 | 29.3197 | 29.3197 | 29.3197 | 29.3197 | 29.3197 | 29.3197 | 29.3197 | 29.3197 | 29.3197
35% | 3551.3408 | 19.7569 | 26.2091 | 27.9643 | 21.1458 | 21.1428 | 21.3423 | 21.5612 | 22.0111 | 22.3345 | 22.5095 | 22.7007 | 22.876 | 23.1932 | 23.5872 | 23.5589 | 23.5589 | 23.5589 | 23.5589 | 23.5589 | 23.5589 | 23.5589 | 23.5589 | 23.5589 | 23.5589 | 23.5589 | 23.5589 | 23.5589 | 23.5589 | 23.5589 | 23.5589 | 35% | 2779.1293 | 22.0153 | 28.4805 | 30.171 | 23.3021 | 23.3083 | 23.481 | 23.9383 | 24.2436 | 24.543 | 24.8932 | 25.2172 | 25.5323 | 25.5674 | 25.9352 | 25.6547 | 25.6547 | 25.6547 | 25.6547 | 25.6547 | 25.6547 | 25.6547 | 25.6547 | 25.6547 | 25.6547 | 25.6547 | 25.6547 | 25.6547 | 25.6547 | 25.6547 | 25.6547
30% | 3758.953 | 16.9345 | 22.4649 | 23.9694 | 18.1249 | 18.1224 | 18.2934 | 18.4811 | 18.8667 | 19.1438 | 19.2939 | 19.4577 | 19.608 | 19.8799 | 20.2176 | 20.1933 | 20.1933 | 20.1933 | 20.1933 | 20.1933 | 20.1933 | 20.1933 | 20.1933 | 20.1933 | 20.1933 | 20.1933 | 20.1933 | 20.1933 | 20.1933 | 20.1933 | 20.1933 | 30% | 3814.165 | 18.8703 | 24.4118 | 25.8609 | 19.9733 | 19.9785 | 20.1266 | 20.5185 | 20.7802 | 21.0368 | 21.3371 | 21.6148 | 21.8848 | 21.9149 | 22.2302 | 21.9897 | 21.9897 | 21.9897 | 21.9897 | 21.9897 | 21.9897 | 21.9897 | 21.9897 | 21.9897 | 21.9897 | 21.9897 | 21.9897 | 21.9897 | 21.9897 | 21.9897 | 21.9897
25% | 3926.4798 | 14.1121 | 18.7208 | 19.9745 | 15.1041 | 15.102 | 15.2445 | 15.4009 | 15.7222 | 15.9532 | 16.0782 | 16.2148 | 16.34 | 16.5666 | 16.848 | 16.8278 | 16.8278 | 16.8278 | 16.8278 | 16.8278 | 16.8278 | 16.8278 | 16.8278 | 16.8278 | 16.8278 | 16.8278 | 16.8278 | 16.8278 | 16.8278 | 16.8278 | 16.8278 | 25% | 4166.9923 | 15.7252 | 20.3432 | 21.5507 | 16.6444 | 16.6488 | 16.7721 | 17.0988 | 17.3169 | 17.5307 | 17.7809 | 18.0123 | 18.2373 | 18.2624 | 18.5252 | 18.3248 | 18.3248 | 18.3248 | 18.3248 | 18.3248 | 18.3248 | 18.3248 | 18.3248 | 18.3248 | 18.3248 | 18.3248 | 18.3248 | 18.3248 | 18.3248 | 18.3248 | 18.3248
20% | 4050.5177 | 11.2897 | 14.9766 | 15.9796 | 12.0833 | 12.0816 | 12.1956 | 12.3207 | 12.5778 | 12.7625 | 12.8626 | 12.9718 | 13.072 | 13.2533 | 13.4784 | 13.4622 | 13.4622 | 13.4622 | 13.4622 | 13.4622 | 13.4622 | 13.4622 | 13.4622 | 13.4622 | 13.4622 | 13.4622 | 13.4622 | 13.4622 | 13.4622 | 13.4622 | 13.4622 | 20% | 4282.7105 | 12.5802 | 16.2746 | 17.2406 | 13.3155 | 13.319 | 13.4177 | 13.679 | 13.8535 | 14.0245 | 14.2247 | 14.4099 | 14.5899 | 14.6099 | 14.8201 | 14.6598 | 14.6598 | 14.6598 | 14.6598 | 14.6598 | 14.6598 | 14.6598 | 14.6598 | 14.6598 | 14.6598 | 14.6598 | 14.6598 | 14.6598 | 14.6598 | 14.6598 | 14.6598
15% | 4152.622 | 8.4672 | 11.2325 | 11.9847 | 9.0625 | 9.0612 | 9.1467 | 9.2405 | 9.4333 | 9.5719 | 9.6469 | 9.7289 | 9.804 | 9.94 | 10.1088 | 10.0967 | 10.0967 | 10.0967 | 10.0967 | 10.0967 | 10.0967 | 10.0967 | 10.0967 | 10.0967 | 10.0967 | 10.0967 | 10.0967 | 10.0967 | 10.0967 | 10.0967 | 10.0967 | 15% | 4364.7722 | 9.4351 | 12.2059 | 12.9304 | 9.9866 | 9.9893 | 10.0633 | 10.2593 | 10.3901 | 10.5184 | 10.6685 | 10.8074 | 10.9424 | 10.9575 | 11.1151 | 10.9949 | 10.9949 | 10.9949 | 10.9949 | 10.9949 | 10.9949 | 10.9949 | 10.9949 | 10.9949 | 10.9949 | 10.9949 | 10.9949 | 10.9949 | 10.9949 | 10.9949 | 10.9949
10% | 4248.2976 | 5.6448 | 7.4883 | 7.9898 | 6.0416 | 6.0408 | 6.0978 | 6.1604 | 6.2889 | 6.3813 | 6.4313 | 6.4859 | 6.536 | 6.6266 | 6.7392 | 6.7311 | 6.7311 | 6.7311 | 6.7311 | 6.7311 | 6.7311 | 6.7311 | 6.7311 | 6.7311 | 6.7311 | 6.7311 | 6.7311 | 6.7311 | 6.7311 | 6.7311 | 6.7311 | 10% | 4391.6218 | 6.2901 | 8.1373 | 8.6203 | 6.6578 | 6.6595 | 6.7089 | 6.8395 | 6.9267 | 7.0123 | 7.1124 | 7.2049 | 7.2949 | 7.305 | 7.4101 | 7.3299 | 7.3299 | 7.3299 | 7.3299 | 7.3299 | 7.3299 | 7.3299 | 7.3299 | 7.3299 | 7.3299 | 7.3299 | 7.3299 | 7.3299 | 7.3299 | 7.3299 | 7.3299
5% | 4361.7469 | 2.8224 | 3.7442 | 3.9949 | 3.0208 | 3.0204 | 3.0489 | 3.0802 | 3.1444 | 3.1906 | 3.2156 | 3.243 | 3.268 | 3.3133 | 3.3696 | 3.3656 | 3.3656 | 3.3656 | 3.3656 | 3.3656 | 3.3656 | 3.3656 | 3.3656 | 3.3656 | 3.3656 | 3.3656 | 3.3656 | 3.3656 | 3.3656 | 3.3656 | 3.3656 | 5% | 4391.6218 | 3.145 | 4.0686 | 4.3101 | 3.3289 | 3.3298 | 3.3544 | 3.4198 | 3.4634 | 3.5061 | 3.5562 | 3.6025 | 3.6475 | 3.6525 | 3.705 | 3.665 | 3.665 | 3.665 | 3.665 | 3.665 | 3.665 | 3.665 | 3.665 | 3.665 | 3.665 | 3.665 | 3.665 | 3.665 | 3.665 | 3.665 | 3.665
9.992e-14% | 4391.6218 | 5.6403e-14 | 7.4823e-14 | 7.9834e-14 | 6.0368e-14 | 6.036e-14 | 6.0929e-14 | 6.1554e-14 | 6.2839e-14 | 6.3762e-14 | 6.4262e-14 | 6.4807e-14 | 6.5308e-14 | 6.6213e-14 | 6.7338e-14 | 6.7257e-14 | 6.7257e-14 | 6.7257e-14 | 6.7257e-14 | 6.7257e-14 | 6.7257e-14 | 6.7257e-14 | 6.7257e-14 | 6.7257e-14 | 6.7257e-14 | 6.7257e-14 | 6.7257e-14 | 6.7257e-14 | 6.7257e-14 | 6.7257e-14 | 6.7257e-14 | 9.992e-14% | 4391.6218 | 6.2851e-14 | 8.1308e-14 | 8.6134e-14 | 6.6524e-14 | 6.6542e-14 | 6.7035e-14 | 6.834e-14 | 6.9212e-14 | 7.0067e-14 | 7.1067e-14 | 7.1992e-14 | 7.2891e-14 | 7.2991e-14 | 7.4041e-14 | 7.3241e-14 | 7.3241e-14 | 7.3241e-14 | 7.3241e-14 | 7.3241e-14 | 7.3241e-14 | 7.3241e-14 | 7.3241e-14 | 7.3241e-14 | 7.3241e-14 | 7.3241e-14 | 7.3241e-14 | 7.3241e-14 | 7.3241e-14 | 7.3241e-14 | 7.3241e-14
Option 3
Winter Season | [31 empty] | Winter Season
P50 | [31 empty] | P10
% of MD | Winter - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Winter - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 49.7042 | 68.8514 | 73.8223 | 74.6663 | 75.3214 | 76.4563 | 79.0441 | 80.7726 | 82.9664 | 84.1029 | 85.1001 | 83.2461 | 85.4092 | 88.8125 | 86.2221 | 86.2221 | 86.2221 | 86.2221 | 86.2221 | 86.2221 | 86.2221 | 86.2221 | 86.2221 | 86.2221 | 86.2221 | 86.2221 | 86.2221 | 86.2221 | 86.2221 | 86.2221 | 100% | 0 | 53.1876 | 72.0932 | 77.2584 | 78.0542 | 78.5557 | 79.6659 | 82.2942 | 83.7249 | 86.4587 | 94.7777 | 87.9092 | 86.5626 | 88.3699 | 92.3278 | 89.6413 | 89.6413 | 89.6413 | 89.6413 | 89.6413 | 89.6413 | 89.6413 | 89.6413 | 89.6413 | 89.6413 | 89.6413 | 89.6413 | 89.6413 | 89.6413 | 89.6413 | 89.6413
99% | 1.486 | 49.2072 | 68.1629 | 73.0841 | 73.9197 | 74.5682 | 75.6918 | 78.2537 | 79.9649 | 82.1367 | 83.2619 | 84.2491 | 82.4136 | 84.5551 | 87.9243 | 85.3598 | 85.3598 | 85.3598 | 85.3598 | 85.3598 | 85.3598 | 85.3598 | 85.3598 | 85.3598 | 85.3598 | 85.3598 | 85.3598 | 85.3598 | 85.3598 | 85.3598 | 85.3598 | 99% | 1.486 | 52.6557 | 71.3723 | 76.4858 | 77.2737 | 77.7701 | 78.8692 | 81.4712 | 82.8877 | 85.5941 | 93.83 | 87.0301 | 85.697 | 87.4862 | 91.4045 | 88.7449 | 88.7449 | 88.7449 | 88.7449 | 88.7449 | 88.7449 | 88.7449 | 88.7449 | 88.7449 | 88.7449 | 88.7449 | 88.7449 | 88.7449 | 88.7449 | 88.7449 | 88.7449
98% | 3.2692 | 48.7101 | 67.4743 | 72.3458 | 73.173 | 73.815 | 74.9272 | 77.4632 | 79.1572 | 81.3071 | 82.4209 | 83.3981 | 81.5812 | 83.701 | 87.0362 | 84.4976 | 84.4976 | 84.4976 | 84.4976 | 84.4976 | 84.4976 | 84.4976 | 84.4976 | 84.4976 | 84.4976 | 84.4976 | 84.4976 | 84.4976 | 84.4976 | 84.4976 | 84.4976 | 98% | 3.2692 | 52.1238 | 70.6514 | 75.7133 | 76.4931 | 76.9846 | 78.0726 | 80.6483 | 82.0504 | 84.7295 | 92.8822 | 86.151 | 84.8313 | 86.6025 | 90.4812 | 87.8485 | 87.8485 | 87.8485 | 87.8485 | 87.8485 | 87.8485 | 87.8485 | 87.8485 | 87.8485 | 87.8485 | 87.8485 | 87.8485 | 87.8485 | 87.8485 | 87.8485 | 87.8485
97% | 6.8356 | 48.2131 | 66.7858 | 71.6076 | 72.4263 | 73.0618 | 74.1627 | 76.6728 | 78.3495 | 80.4774 | 81.5798 | 82.5471 | 80.7487 | 82.847 | 86.1481 | 83.6354 | 83.6354 | 83.6354 | 83.6354 | 83.6354 | 83.6354 | 83.6354 | 83.6354 | 83.6354 | 83.6354 | 83.6354 | 83.6354 | 83.6354 | 83.6354 | 83.6354 | 83.6354 | 97% | 6.8356 | 51.5919 | 69.9304 | 74.9407 | 75.7126 | 76.199 | 77.2759 | 79.8254 | 81.2132 | 83.865 | 91.9344 | 85.2719 | 83.9657 | 85.7188 | 89.558 | 86.9521 | 86.9521 | 86.9521 | 86.9521 | 86.9521 | 86.9521 | 86.9521 | 86.9521 | 86.9521 | 86.9521 | 86.9521 | 86.9521 | 86.9521 | 86.9521 | 86.9521 | 86.9521
95% | 17.5347 | 47.219 | 65.4088 | 70.1312 | 70.933 | 71.5553 | 72.6335 | 75.0919 | 76.734 | 78.8181 | 79.8978 | 80.8451 | 79.0838 | 81.1388 | 84.3718 | 81.911 | 81.911 | 81.911 | 81.911 | 81.911 | 81.911 | 81.911 | 81.911 | 81.911 | 81.911 | 81.911 | 81.911 | 81.911 | 81.911 | 81.911 | 81.911 | 95% | 17.5347 | 50.5282 | 68.4886 | 73.3955 | 74.1515 | 74.6279 | 75.6826 | 78.1795 | 79.5387 | 82.1358 | 90.0389 | 83.5138 | 82.2345 | 83.9514 | 87.7114 | 85.1592 | 85.1592 | 85.1592 | 85.1592 | 85.1592 | 85.1592 | 85.1592 | 85.1592 | 85.1592 | 85.1592 | 85.1592 | 85.1592 | 85.1592 | 85.1592 | 85.1592 | 85.1592
90% | 78.7576 | 44.7338 | 61.9662 | 66.4401 | 67.1997 | 67.7893 | 68.8107 | 71.1397 | 72.6954 | 74.6697 | 75.6926 | 76.5901 | 74.9215 | 76.8683 | 79.9312 | 77.5999 | 77.5999 | 77.5999 | 77.5999 | 77.5999 | 77.5999 | 77.5999 | 77.5999 | 77.5999 | 77.5999 | 77.5999 | 77.5999 | 77.5999 | 77.5999 | 77.5999 | 77.5999 | 90% | 78.7576 | 47.8688 | 64.8839 | 69.5326 | 70.2488 | 70.7001 | 71.6993 | 74.0648 | 75.3524 | 77.8128 | 85.3 | 79.1183 | 77.9063 | 79.5329 | 83.095 | 80.6772 | 80.6772 | 80.6772 | 80.6772 | 80.6772 | 80.6772 | 80.6772 | 80.6772 | 80.6772 | 80.6772 | 80.6772 | 80.6772 | 80.6772 | 80.6772 | 80.6772 | 80.6772
85% | 236.8672 | 42.2486 | 58.5237 | 62.7489 | 63.4664 | 64.0232 | 64.9879 | 67.1875 | 68.6567 | 70.5214 | 71.4875 | 72.3351 | 70.7592 | 72.5978 | 75.4906 | 73.2888 | 73.2888 | 73.2888 | 73.2888 | 73.2888 | 73.2888 | 73.2888 | 73.2888 | 73.2888 | 73.2888 | 73.2888 | 73.2888 | 73.2888 | 73.2888 | 73.2888 | 73.2888 | 85% | 236.8672 | 45.2094 | 61.2792 | 65.6697 | 66.3461 | 66.7723 | 67.716 | 69.9501 | 71.1662 | 73.4899 | 80.5611 | 74.7228 | 73.5782 | 75.1144 | 78.4786 | 76.1951 | 76.1951 | 76.1951 | 76.1951 | 76.1951 | 76.1951 | 76.1951 | 76.1951 | 76.1951 | 76.1951 | 76.1951 | 76.1951 | 76.1951 | 76.1951 | 76.1951 | 76.1951
80% | 497.5104 | 39.7634 | 55.0811 | 59.0578 | 59.7331 | 60.2571 | 61.1651 | 63.2353 | 64.6181 | 66.3731 | 67.2823 | 68.08 | 66.5969 | 68.3274 | 71.05 | 68.9777 | 68.9777 | 68.9777 | 68.9777 | 68.9777 | 68.9777 | 68.9777 | 68.9777 | 68.9777 | 68.9777 | 68.9777 | 68.9777 | 68.9777 | 68.9777 | 68.9777 | 68.9777 | 80% | 497.5104 | 42.55 | 57.6746 | 61.8067 | 62.4434 | 62.8445 | 63.7327 | 65.8353 | 66.9799 | 69.167 | 75.8222 | 70.3274 | 69.2501 | 70.6959 | 73.8622 | 71.7131 | 71.7131 | 71.7131 | 71.7131 | 71.7131 | 71.7131 | 71.7131 | 71.7131 | 71.7131 | 71.7131 | 71.7131 | 71.7131 | 71.7131 | 71.7131 | 71.7131 | 71.7131
75% | 803.6248 | 37.2782 | 51.6385 | 55.3667 | 55.9997 | 56.4911 | 57.3423 | 59.2831 | 60.5795 | 62.2248 | 63.0772 | 63.825 | 62.4346 | 64.0569 | 66.6093 | 64.6665 | 64.6665 | 64.6665 | 64.6665 | 64.6665 | 64.6665 | 64.6665 | 64.6665 | 64.6665 | 64.6665 | 64.6665 | 64.6665 | 64.6665 | 64.6665 | 64.6665 | 64.6665 | 75% | 803.6248 | 39.8907 | 54.0699 | 57.9438 | 58.5407 | 58.9167 | 59.7494 | 61.7206 | 62.7937 | 64.844 | 71.0833 | 65.9319 | 64.9219 | 66.2774 | 69.2458 | 67.231 | 67.231 | 67.231 | 67.231 | 67.231 | 67.231 | 67.231 | 67.231 | 67.231 | 67.231 | 67.231 | 67.231 | 67.231 | 67.231 | 67.231 | 67.231
70% | 1155.2107 | 34.793 | 48.196 | 51.6756 | 52.2664 | 52.725 | 53.5194 | 55.3309 | 56.5408 | 58.0765 | 58.8721 | 59.57 | 58.2723 | 59.7865 | 62.1687 | 60.3554 | 60.3554 | 60.3554 | 60.3554 | 60.3554 | 60.3554 | 60.3554 | 60.3554 | 60.3554 | 60.3554 | 60.3554 | 60.3554 | 60.3554 | 60.3554 | 60.3554 | 60.3554 | 70% | 1155.2107 | 37.2313 | 50.4653 | 54.0809 | 54.638 | 54.989 | 55.7661 | 57.6059 | 58.6074 | 60.5211 | 66.3444 | 61.5365 | 60.5938 | 61.8589 | 64.6295 | 62.7489 | 62.7489 | 62.7489 | 62.7489 | 62.7489 | 62.7489 | 62.7489 | 62.7489 | 62.7489 | 62.7489 | 62.7489 | 62.7489 | 62.7489 | 62.7489 | 62.7489 | 62.7489
65% | 1553.1596 | 32.3077 | 44.7534 | 47.9845 | 48.5331 | 48.9589 | 49.6966 | 51.3787 | 52.5022 | 53.9282 | 54.6669 | 55.315 | 54.11 | 55.516 | 57.7281 | 56.0443 | 56.0443 | 56.0443 | 56.0443 | 56.0443 | 56.0443 | 56.0443 | 56.0443 | 56.0443 | 56.0443 | 56.0443 | 56.0443 | 56.0443 | 56.0443 | 56.0443 | 56.0443 | 65% | 1553.1596 | 34.5719 | 46.8606 | 50.218 | 50.7352 | 51.0612 | 51.7828 | 53.4912 | 54.4212 | 56.1982 | 61.6055 | 57.141 | 56.2657 | 57.4405 | 60.0131 | 58.2669 | 58.2669 | 58.2669 | 58.2669 | 58.2669 | 58.2669 | 58.2669 | 58.2669 | 58.2669 | 58.2669 | 58.2669 | 58.2669 | 58.2669 | 58.2669 | 58.2669 | 58.2669
60% | 2026.2996 | 29.8225 | 41.3108 | 44.2934 | 44.7998 | 45.1928 | 45.8738 | 47.4265 | 48.4636 | 49.7798 | 50.4618 | 51.06 | 49.9477 | 51.2455 | 53.2875 | 51.7332 | 51.7332 | 51.7332 | 51.7332 | 51.7332 | 51.7332 | 51.7332 | 51.7332 | 51.7332 | 51.7332 | 51.7332 | 51.7332 | 51.7332 | 51.7332 | 51.7332 | 51.7332 | 60% | 2026.2996 | 31.9125 | 43.2559 | 46.3551 | 46.8325 | 47.1334 | 47.7995 | 49.3765 | 50.235 | 51.8752 | 56.8666 | 52.7455 | 51.9376 | 53.022 | 55.3967 | 53.7848 | 53.7848 | 53.7848 | 53.7848 | 53.7848 | 53.7848 | 53.7848 | 53.7848 | 53.7848 | 53.7848 | 53.7848 | 53.7848 | 53.7848 | 53.7848 | 53.7848 | 53.7848
55% | 2598.4068 | 27.3373 | 37.8683 | 40.6023 | 41.0665 | 41.4268 | 42.051 | 43.4743 | 44.425 | 45.6315 | 46.2566 | 46.805 | 45.7854 | 46.9751 | 48.8469 | 47.4221 | 47.4221 | 47.4221 | 47.4221 | 47.4221 | 47.4221 | 47.4221 | 47.4221 | 47.4221 | 47.4221 | 47.4221 | 47.4221 | 47.4221 | 47.4221 | 47.4221 | 47.4221 | 55% | 2598.4068 | 29.2532 | 39.6513 | 42.4921 | 42.9298 | 43.2056 | 43.8162 | 45.2618 | 46.0487 | 47.5523 | 52.1278 | 48.3501 | 47.6094 | 48.6035 | 50.7803 | 49.3027 | 49.3027 | 49.3027 | 49.3027 | 49.3027 | 49.3027 | 49.3027 | 49.3027 | 49.3027 | 49.3027 | 49.3027 | 49.3027 | 49.3027 | 49.3027 | 49.3027 | 49.3027
50% | 3233.5201 | 24.8521 | 34.4257 | 36.9111 | 37.3332 | 37.6607 | 38.2282 | 39.5221 | 40.3863 | 41.4832 | 42.0515 | 42.55 | 41.623 | 42.7046 | 44.4062 | 43.111 | 43.111 | 43.111 | 43.111 | 43.111 | 43.111 | 43.111 | 43.111 | 43.111 | 43.111 | 43.111 | 43.111 | 43.111 | 43.111 | 43.111 | 43.111 | 50% | 3233.5201 | 26.5938 | 36.0466 | 38.6292 | 39.0271 | 39.2778 | 39.833 | 41.1471 | 41.8625 | 43.2294 | 47.3889 | 43.9546 | 43.2813 | 44.185 | 46.1639 | 44.8207 | 44.8207 | 44.8207 | 44.8207 | 44.8207 | 44.8207 | 44.8207 | 44.8207 | 44.8207 | 44.8207 | 44.8207 | 44.8207 | 44.8207 | 44.8207 | 44.8207 | 44.8207
45% | 3775.313 | 22.3669 | 30.9831 | 33.22 | 33.5998 | 33.8946 | 34.4054 | 35.5699 | 36.3477 | 37.3349 | 37.8463 | 38.295 | 37.4607 | 38.4342 | 39.9656 | 38.7999 | 38.7999 | 38.7999 | 38.7999 | 38.7999 | 38.7999 | 38.7999 | 38.7999 | 38.7999 | 38.7999 | 38.7999 | 38.7999 | 38.7999 | 38.7999 | 38.7999 | 38.7999 | 45% | 3775.313 | 23.9344 | 32.442 | 34.7663 | 35.1244 | 35.35 | 35.8497 | 37.0324 | 37.6762 | 38.9064 | 42.65 | 39.5591 | 38.9532 | 39.7665 | 41.5475 | 40.3386 | 40.3386 | 40.3386 | 40.3386 | 40.3386 | 40.3386 | 40.3386 | 40.3386 | 40.3386 | 40.3386 | 40.3386 | 40.3386 | 40.3386 | 40.3386 | 40.3386 | 40.3386
40% | 4072.8088 | 19.8817 | 27.5405 | 29.5289 | 29.8665 | 30.1286 | 30.5825 | 31.6176 | 32.3091 | 33.1866 | 33.6412 | 34.04 | 33.2984 | 34.1637 | 35.525 | 34.4888 | 34.4888 | 34.4888 | 34.4888 | 34.4888 | 34.4888 | 34.4888 | 34.4888 | 34.4888 | 34.4888 | 34.4888 | 34.4888 | 34.4888 | 34.4888 | 34.4888 | 34.4888 | 40% | 4072.8088 | 21.275 | 28.8373 | 30.9034 | 31.2217 | 31.4223 | 31.8664 | 32.9177 | 33.49 | 34.5835 | 37.9111 | 35.1637 | 34.625 | 35.348 | 36.9311 | 35.8565 | 35.8565 | 35.8565 | 35.8565 | 35.8565 | 35.8565 | 35.8565 | 35.8565 | 35.8565 | 35.8565 | 35.8565 | 35.8565 | 35.8565 | 35.8565 | 35.8565 | 35.8565
35% | 4198.821 | 17.3965 | 24.098 | 25.8378 | 26.1332 | 26.3625 | 26.7597 | 27.6654 | 28.2704 | 29.0382 | 29.436 | 29.785 | 29.1361 | 29.8932 | 31.0844 | 30.1777 | 30.1777 | 30.1777 | 30.1777 | 30.1777 | 30.1777 | 30.1777 | 30.1777 | 30.1777 | 30.1777 | 30.1777 | 30.1777 | 30.1777 | 30.1777 | 30.1777 | 30.1777 | 35% | 4198.821 | 18.6156 | 25.2326 | 27.0405 | 27.319 | 27.4945 | 27.8831 | 28.803 | 29.3037 | 30.2606 | 33.1722 | 30.7682 | 30.2969 | 30.9295 | 32.3147 | 31.3745 | 31.3745 | 31.3745 | 31.3745 | 31.3745 | 31.3745 | 31.3745 | 31.3745 | 31.3745 | 31.3745 | 31.3745 | 31.3745 | 31.3745 | 31.3745 | 31.3745 | 31.3745
30% | 4271.3374 | 14.9113 | 20.6554 | 22.1467 | 22.3999 | 22.5964 | 22.9369 | 23.7132 | 24.2318 | 24.8899 | 25.2309 | 25.53 | 24.9738 | 25.6228 | 26.6437 | 25.8666 | 25.8666 | 25.8666 | 25.8666 | 25.8666 | 25.8666 | 25.8666 | 25.8666 | 25.8666 | 25.8666 | 25.8666 | 25.8666 | 25.8666 | 25.8666 | 25.8666 | 25.8666 | 30% | 4271.3374 | 15.9563 | 21.628 | 23.1775 | 23.4163 | 23.5667 | 23.8998 | 24.6883 | 25.1175 | 25.9376 | 28.4333 | 26.3728 | 25.9688 | 26.511 | 27.6983 | 26.8924 | 26.8924 | 26.8924 | 26.8924 | 26.8924 | 26.8924 | 26.8924 | 26.8924 | 26.8924 | 26.8924 | 26.8924 | 26.8924 | 26.8924 | 26.8924 | 26.8924 | 26.8924
25% | 4321.8611 | 12.4261 | 17.2128 | 18.4556 | 18.6666 | 18.8304 | 19.1141 | 19.761 | 20.1932 | 20.7416 | 21.0257 | 21.275 | 20.8115 | 21.3523 | 22.2031 | 21.5555 | 21.5555 | 21.5555 | 21.5555 | 21.5555 | 21.5555 | 21.5555 | 21.5555 | 21.5555 | 21.5555 | 21.5555 | 21.5555 | 21.5555 | 21.5555 | 21.5555 | 21.5555 | 25% | 4321.8611 | 13.2969 | 18.0233 | 19.3146 | 19.5136 | 19.6389 | 19.9165 | 20.5735 | 20.9312 | 21.6147 | 23.6944 | 21.9773 | 21.6406 | 22.0925 | 23.0819 | 22.4103 | 22.4103 | 22.4103 | 22.4103 | 22.4103 | 22.4103 | 22.4103 | 22.4103 | 22.4103 | 22.4103 | 22.4103 | 22.4103 | 22.4103 | 22.4103 | 22.4103 | 22.4103
20% | 4353.067 | 9.9408 | 13.7703 | 14.7645 | 14.9333 | 15.0643 | 15.2913 | 15.8088 | 16.1545 | 16.5933 | 16.8206 | 17.02 | 16.6492 | 17.0818 | 17.7625 | 17.2444 | 17.2444 | 17.2444 | 17.2444 | 17.2444 | 17.2444 | 17.2444 | 17.2444 | 17.2444 | 17.2444 | 17.2444 | 17.2444 | 17.2444 | 17.2444 | 17.2444 | 17.2444 | 20% | 4353.067 | 10.6375 | 14.4186 | 15.4517 | 15.6108 | 15.7111 | 15.9332 | 16.4588 | 16.745 | 17.2917 | 18.9555 | 17.5818 | 17.3125 | 17.674 | 18.4656 | 17.9283 | 17.9283 | 17.9283 | 17.9283 | 17.9283 | 17.9283 | 17.9283 | 17.9283 | 17.9283 | 17.9283 | 17.9283 | 17.9283 | 17.9283 | 17.9283 | 17.9283 | 17.9283
15% | 4369.4129 | 7.4556 | 10.3277 | 11.0733 | 11.1999 | 11.2982 | 11.4685 | 11.8566 | 12.1159 | 12.445 | 12.6154 | 12.765 | 12.4869 | 12.8114 | 13.3219 | 12.9333 | 12.9333 | 12.9333 | 12.9333 | 12.9333 | 12.9333 | 12.9333 | 12.9333 | 12.9333 | 12.9333 | 12.9333 | 12.9333 | 12.9333 | 12.9333 | 12.9333 | 12.9333 | 15% | 4369.4129 | 7.9781 | 10.814 | 11.5888 | 11.7081 | 11.7833 | 11.9499 | 12.3441 | 12.5587 | 12.9688 | 14.2167 | 13.1864 | 12.9844 | 13.2555 | 13.8492 | 13.4462 | 13.4462 | 13.4462 | 13.4462 | 13.4462 | 13.4462 | 13.4462 | 13.4462 | 13.4462 | 13.4462 | 13.4462 | 13.4462 | 13.4462 | 13.4462 | 13.4462 | 13.4462
10% | 4378.6261 | 4.9704 | 6.8851 | 7.3822 | 7.4666 | 7.5321 | 7.6456 | 7.9044 | 8.0773 | 8.2966 | 8.4103 | 8.51 | 8.3246 | 8.5409 | 8.8812 | 8.6222 | 8.6222 | 8.6222 | 8.6222 | 8.6222 | 8.6222 | 8.6222 | 8.6222 | 8.6222 | 8.6222 | 8.6222 | 8.6222 | 8.6222 | 8.6222 | 8.6222 | 8.6222 | 10% | 4378.6261 | 5.3188 | 7.2093 | 7.7258 | 7.8054 | 7.8556 | 7.9666 | 8.2294 | 8.3725 | 8.6459 | 9.4778 | 8.7909 | 8.6563 | 8.837 | 9.2328 | 8.9641 | 8.9641 | 8.9641 | 8.9641 | 8.9641 | 8.9641 | 8.9641 | 8.9641 | 8.9641 | 8.9641 | 8.9641 | 8.9641 | 8.9641 | 8.9641 | 8.9641 | 8.9641
5% | 4391.7028 | 2.4852 | 3.4426 | 3.6911 | 3.7333 | 3.7661 | 3.8228 | 3.9522 | 4.0386 | 4.1483 | 4.2051 | 4.255 | 4.1623 | 4.2705 | 4.4406 | 4.3111 | 4.3111 | 4.3111 | 4.3111 | 4.3111 | 4.3111 | 4.3111 | 4.3111 | 4.3111 | 4.3111 | 4.3111 | 4.3111 | 4.3111 | 4.3111 | 4.3111 | 4.3111 | 5% | 4391.7028 | 2.6594 | 3.6047 | 3.8629 | 3.9027 | 3.9278 | 3.9833 | 4.1147 | 4.1862 | 4.3229 | 4.7389 | 4.3955 | 4.3281 | 4.4185 | 4.6164 | 4.4821 | 4.4821 | 4.4821 | 4.4821 | 4.4821 | 4.4821 | 4.4821 | 4.4821 | 4.4821 | 4.4821 | 4.4821 | 4.4821 | 4.4821 | 4.4821 | 4.4821 | 4.4821
9.992e-14% | 4391.7028 | 4.9664e-14 | 6.8796e-14 | 7.3763e-14 | 7.4607e-14 | 7.5261e-14 | 7.6395e-14 | 7.8981e-14 | 8.0708e-14 | 8.29e-14 | 8.4036e-14 | 8.5032e-14 | 8.318e-14 | 8.5341e-14 | 8.8741e-14 | 8.6153e-14 | 8.6153e-14 | 8.6153e-14 | 8.6153e-14 | 8.6153e-14 | 8.6153e-14 | 8.6153e-14 | 8.6153e-14 | 8.6153e-14 | 8.6153e-14 | 8.6153e-14 | 8.6153e-14 | 8.6153e-14 | 8.6153e-14 | 8.6153e-14 | 8.6153e-14 | 9.992e-14% | 4391.7028 | 5.3145e-14 | 7.2036e-14 | 7.7197e-14 | 7.7992e-14 | 7.8493e-14 | 7.9602e-14 | 8.2228e-14 | 8.3658e-14 | 8.639e-14 | 9.4702e-14 | 8.7839e-14 | 8.6493e-14 | 8.8299e-14 | 9.2254e-14 | 8.957e-14 | 8.957e-14 | 8.957e-14 | 8.957e-14 | 8.957e-14 | 8.957e-14 | 8.957e-14 | 8.957e-14 | 8.957e-14 | 8.957e-14 | 8.957e-14 | 8.957e-14 | 8.957e-14 | 8.957e-14 | 8.957e-14 | 8.957e-14
Summer Season | [31 empty] | Summer Season
P50 | [31 empty] | P10
% of MD | Summer - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Summer - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 56.4483 | 74.8831 | 79.898 | 79.7498 | 79.7414 | 80.3113 | 80.9369 | 82.2223 | 83.1461 | 83.6463 | 84.1925 | 84.6932 | 85.5997 | 86.7253 | 86.6445 | 86.6445 | 86.6445 | 86.6445 | 86.6445 | 86.6445 | 86.6445 | 86.6445 | 86.6445 | 86.6445 | 86.6445 | 86.6445 | 86.6445 | 86.6445 | 86.6445 | 86.6445 | 100% | 0 | 62.901 | 81.3728 | 86.203 | 85.9109 | 85.9284 | 86.4219 | 87.7284 | 88.6008 | 89.4561 | 90.4569 | 91.3826 | 92.2827 | 92.383 | 93.434 | 92.6325 | 92.6325 | 92.6325 | 92.6325 | 92.6325 | 92.6325 | 92.6325 | 92.6325 | 92.6325 | 92.6325 | 92.6325 | 92.6325 | 92.6325 | 92.6325 | 92.6325 | 92.6325
99% | 0 | 55.8838 | 74.1343 | 79.099 | 78.9523 | 78.944 | 79.5082 | 80.1275 | 81.4 | 82.3146 | 82.8098 | 83.3506 | 83.8463 | 84.7437 | 85.858 | 85.778 | 85.778 | 85.778 | 85.778 | 85.778 | 85.778 | 85.778 | 85.778 | 85.778 | 85.778 | 85.778 | 85.778 | 85.778 | 85.778 | 85.778 | 85.778 | 99% | 1.5127 | 62.272 | 80.559 | 85.341 | 85.0518 | 85.0691 | 85.5577 | 86.8512 | 87.7148 | 88.5615 | 89.5523 | 90.4688 | 91.3598 | 91.4592 | 92.4996 | 91.7061 | 91.7061 | 91.7061 | 91.7061 | 91.7061 | 91.7061 | 91.7061 | 91.7061 | 91.7061 | 91.7061 | 91.7061 | 91.7061 | 91.7061 | 91.7061 | 91.7061 | 91.7061
98% | 0 | 55.3193 | 73.3854 | 78.3 | 78.1548 | 78.1466 | 78.7051 | 79.3181 | 80.5778 | 81.4832 | 81.9734 | 82.5086 | 82.9994 | 83.8877 | 84.9908 | 84.9116 | 84.9116 | 84.9116 | 84.9116 | 84.9116 | 84.9116 | 84.9116 | 84.9116 | 84.9116 | 84.9116 | 84.9116 | 84.9116 | 84.9116 | 84.9116 | 84.9116 | 84.9116 | 98% | 2.269 | 61.643 | 79.7453 | 84.4789 | 84.1927 | 84.2098 | 84.6935 | 85.9739 | 86.8287 | 87.667 | 88.6477 | 89.555 | 90.437 | 90.5354 | 91.5653 | 90.7798 | 90.7798 | 90.7798 | 90.7798 | 90.7798 | 90.7798 | 90.7798 | 90.7798 | 90.7798 | 90.7798 | 90.7798 | 90.7798 | 90.7798 | 90.7798 | 90.7798 | 90.7798
97% | 0.37816 | 54.7549 | 72.6366 | 77.501 | 77.3573 | 77.3492 | 77.902 | 78.5088 | 79.7556 | 80.6517 | 81.1369 | 81.6667 | 82.1524 | 83.0317 | 84.1235 | 84.0451 | 84.0451 | 84.0451 | 84.0451 | 84.0451 | 84.0451 | 84.0451 | 84.0451 | 84.0451 | 84.0451 | 84.0451 | 84.0451 | 84.0451 | 84.0451 | 84.0451 | 84.0451 | 97% | 3.7816 | 61.014 | 78.9316 | 83.6169 | 83.3336 | 83.3505 | 83.8292 | 85.0966 | 85.9427 | 86.7724 | 87.7432 | 88.6411 | 89.5142 | 89.6115 | 90.631 | 89.8535 | 89.8535 | 89.8535 | 89.8535 | 89.8535 | 89.8535 | 89.8535 | 89.8535 | 89.8535 | 89.8535 | 89.8535 | 89.8535 | 89.8535 | 89.8535 | 89.8535 | 89.8535
95% | 2.269 | 53.6259 | 71.1389 | 75.9031 | 75.7623 | 75.7544 | 76.2958 | 76.89 | 78.1112 | 78.9888 | 79.464 | 79.9829 | 80.4586 | 81.3197 | 82.389 | 82.3122 | 82.3122 | 82.3122 | 82.3122 | 82.3122 | 82.3122 | 82.3122 | 82.3122 | 82.3122 | 82.3122 | 82.3122 | 82.3122 | 82.3122 | 82.3122 | 82.3122 | 82.3122 | 95% | 6.0506 | 59.7559 | 77.3041 | 81.8928 | 81.6153 | 81.632 | 82.1008 | 83.342 | 84.1707 | 84.9833 | 85.934 | 86.8135 | 87.6685 | 87.7639 | 88.7623 | 88.0008 | 88.0008 | 88.0008 | 88.0008 | 88.0008 | 88.0008 | 88.0008 | 88.0008 | 88.0008 | 88.0008 | 88.0008 | 88.0008 | 88.0008 | 88.0008 | 88.0008 | 88.0008
90% | 5.6725 | 50.8035 | 67.3948 | 71.9082 | 71.7748 | 71.7673 | 72.2802 | 72.8432 | 74 | 74.8315 | 75.2817 | 75.7732 | 76.2239 | 77.0397 | 78.0527 | 77.98 | 77.98 | 77.98 | 77.98 | 77.98 | 77.98 | 77.98 | 77.98 | 77.98 | 77.98 | 77.98 | 77.98 | 77.98 | 77.98 | 77.98 | 77.98 | 90% | 16.2611 | 56.6109 | 73.2355 | 77.5827 | 77.3198 | 77.3355 | 77.7797 | 78.9556 | 79.7407 | 80.5105 | 81.4112 | 82.2444 | 83.0544 | 83.1447 | 84.0906 | 83.3692 | 83.3692 | 83.3692 | 83.3692 | 83.3692 | 83.3692 | 83.3692 | 83.3692 | 83.3692 | 83.3692 | 83.3692 | 83.3692 | 83.3692 | 83.3692 | 83.3692 | 83.3692
85% | 15.8829 | 47.9811 | 63.6506 | 67.9133 | 67.7874 | 67.7802 | 68.2646 | 68.7963 | 69.8889 | 70.6742 | 71.0994 | 71.5636 | 71.9893 | 72.7598 | 73.7165 | 73.6478 | 73.6478 | 73.6478 | 73.6478 | 73.6478 | 73.6478 | 73.6478 | 73.6478 | 73.6478 | 73.6478 | 73.6478 | 73.6478 | 73.6478 | 73.6478 | 73.6478 | 73.6478 | 85% | 26.4715 | 53.4658 | 69.1669 | 73.2725 | 73.0243 | 73.0391 | 73.4586 | 74.5692 | 75.3106 | 76.0377 | 76.8883 | 77.6752 | 78.4403 | 78.5256 | 79.4189 | 78.7376 | 78.7376 | 78.7376 | 78.7376 | 78.7376 | 78.7376 | 78.7376 | 78.7376 | 78.7376 | 78.7376 | 78.7376 | 78.7376 | 78.7376 | 78.7376 | 78.7376 | 78.7376
80% | 31.0095 | 45.1586 | 59.9065 | 63.9184 | 63.7999 | 63.7932 | 64.2491 | 64.7495 | 65.7778 | 66.5169 | 66.917 | 67.354 | 67.7546 | 68.4798 | 69.3802 | 69.3156 | 69.3156 | 69.3156 | 69.3156 | 69.3156 | 69.3156 | 69.3156 | 69.3156 | 69.3156 | 69.3156 | 69.3156 | 69.3156 | 69.3156 | 69.3156 | 69.3156 | 69.3156 | 80% | 34.0348 | 50.3208 | 65.0982 | 68.9624 | 68.7287 | 68.7427 | 69.1375 | 70.1827 | 70.8806 | 71.5649 | 72.3655 | 73.1061 | 73.8261 | 73.9064 | 74.7472 | 74.106 | 74.106 | 74.106 | 74.106 | 74.106 | 74.106 | 74.106 | 74.106 | 74.106 | 74.106 | 74.106 | 74.106 | 74.106 | 74.106 | 74.106 | 74.106
75% | 72.9857 | 42.3362 | 56.1623 | 59.9235 | 59.8124 | 59.8061 | 60.2335 | 60.7027 | 61.6667 | 62.3596 | 62.7347 | 63.1444 | 63.5199 | 64.1998 | 65.044 | 64.9833 | 64.9833 | 64.9833 | 64.9833 | 64.9833 | 64.9833 | 64.9833 | 64.9833 | 64.9833 | 64.9833 | 64.9833 | 64.9833 | 64.9833 | 64.9833 | 64.9833 | 64.9833 | 75% | 48.405 | 47.1757 | 61.0296 | 64.6522 | 64.4332 | 64.4463 | 64.8164 | 65.7963 | 66.4506 | 67.0921 | 67.8427 | 68.537 | 69.212 | 69.2873 | 70.0755 | 69.4744 | 69.4744 | 69.4744 | 69.4744 | 69.4744 | 69.4744 | 69.4744 | 69.4744 | 69.4744 | 69.4744 | 69.4744 | 69.4744 | 69.4744 | 69.4744 | 69.4744 | 69.4744
70% | 150.5094 | 39.5138 | 52.4182 | 55.9286 | 55.8249 | 55.819 | 56.2179 | 56.6558 | 57.5556 | 58.2023 | 58.5524 | 58.9347 | 59.2853 | 59.9198 | 60.7077 | 60.6511 | 60.6511 | 60.6511 | 60.6511 | 60.6511 | 60.6511 | 60.6511 | 60.6511 | 60.6511 | 60.6511 | 60.6511 | 60.6511 | 60.6511 | 60.6511 | 60.6511 | 60.6511 | 70% | 76.3892 | 44.0307 | 56.9609 | 60.3421 | 60.1376 | 60.1499 | 60.4953 | 61.4099 | 62.0205 | 62.6193 | 63.3198 | 63.9678 | 64.5979 | 64.6681 | 65.4038 | 64.8427 | 64.8427 | 64.8427 | 64.8427 | 64.8427 | 64.8427 | 64.8427 | 64.8427 | 64.8427 | 64.8427 | 64.8427 | 64.8427 | 64.8427 | 64.8427 | 64.8427 | 64.8427
65% | 359.6342 | 36.6914 | 48.674 | 51.9337 | 51.8374 | 51.8319 | 52.2024 | 52.609 | 53.4445 | 54.045 | 54.3701 | 54.7251 | 55.0506 | 55.6398 | 56.3714 | 56.3189 | 56.3189 | 56.3189 | 56.3189 | 56.3189 | 56.3189 | 56.3189 | 56.3189 | 56.3189 | 56.3189 | 56.3189 | 56.3189 | 56.3189 | 56.3189 | 56.3189 | 56.3189 | 65% | 114.2056 | 40.8856 | 52.8923 | 56.0319 | 55.8421 | 55.8534 | 56.1742 | 57.0235 | 57.5905 | 58.1465 | 58.797 | 59.3987 | 59.9837 | 60.049 | 60.7321 | 60.2111 | 60.2111 | 60.2111 | 60.2111 | 60.2111 | 60.2111 | 60.2111 | 60.2111 | 60.2111 | 60.2111 | 60.2111 | 60.2111 | 60.2111 | 60.2111 | 60.2111 | 60.2111
60% | 689.7717 | 33.869 | 44.9299 | 47.9388 | 47.8499 | 47.8449 | 48.1868 | 48.5621 | 49.3334 | 49.8876 | 50.1878 | 50.5155 | 50.8159 | 51.3598 | 52.0352 | 51.9867 | 51.9867 | 51.9867 | 51.9867 | 51.9867 | 51.9867 | 51.9867 | 51.9867 | 51.9867 | 51.9867 | 51.9867 | 51.9867 | 51.9867 | 51.9867 | 51.9867 | 51.9867 | 60% | 178.1154 | 37.7406 | 48.8237 | 51.7218 | 51.5465 | 51.557 | 51.8531 | 52.6371 | 53.1605 | 53.6736 | 54.2741 | 54.8296 | 55.3696 | 55.4298 | 56.0604 | 55.5795 | 55.5795 | 55.5795 | 55.5795 | 55.5795 | 55.5795 | 55.5795 | 55.5795 | 55.5795 | 55.5795 | 55.5795 | 55.5795 | 55.5795 | 55.5795 | 55.5795 | 55.5795
55% | 1095.5419 | 31.0466 | 41.1857 | 43.9439 | 43.8624 | 43.8578 | 44.1712 | 44.5153 | 45.2222 | 45.7303 | 46.0055 | 46.3059 | 46.5813 | 47.0798 | 47.6989 | 47.6545 | 47.6545 | 47.6545 | 47.6545 | 47.6545 | 47.6545 | 47.6545 | 47.6545 | 47.6545 | 47.6545 | 47.6545 | 47.6545 | 47.6545 | 47.6545 | 47.6545 | 47.6545 | 55% | 311.6074 | 34.5955 | 44.755 | 47.4116 | 47.251 | 47.2606 | 47.532 | 48.2506 | 48.7304 | 49.2008 | 49.7513 | 50.2604 | 50.7555 | 50.8107 | 51.3887 | 50.9479 | 50.9479 | 50.9479 | 50.9479 | 50.9479 | 50.9479 | 50.9479 | 50.9479 | 50.9479 | 50.9479 | 50.9479 | 50.9479 | 50.9479 | 50.9479 | 50.9479 | 50.9479
50% | 1666.1918 | 28.2242 | 37.4415 | 39.949 | 39.8749 | 39.8707 | 40.1557 | 40.4684 | 41.1111 | 41.573 | 41.8231 | 42.0962 | 42.3466 | 42.7999 | 43.3626 | 43.3222 | 43.3222 | 43.3222 | 43.3222 | 43.3222 | 43.3222 | 43.3222 | 43.3222 | 43.3222 | 43.3222 | 43.3222 | 43.3222 | 43.3222 | 43.3222 | 43.3222 | 43.3222 | 50% | 636.0723 | 31.4505 | 40.6864 | 43.1015 | 42.9554 | 42.9642 | 43.211 | 43.8642 | 44.3004 | 44.728 | 45.2284 | 45.6913 | 46.1413 | 46.1915 | 46.717 | 46.3162 | 46.3162 | 46.3162 | 46.3162 | 46.3162 | 46.3162 | 46.3162 | 46.3162 | 46.3162 | 46.3162 | 46.3162 | 46.3162 | 46.3162 | 46.3162 | 46.3162 | 46.3162
45% | 2506.0947 | 25.4017 | 33.6974 | 35.9541 | 35.8874 | 35.8837 | 36.1401 | 36.4216 | 37 | 37.4157 | 37.6408 | 37.8866 | 38.112 | 38.5199 | 39.0264 | 38.99 | 38.99 | 38.99 | 38.99 | 38.99 | 38.99 | 38.99 | 38.99 | 38.99 | 38.99 | 38.99 | 38.99 | 38.99 | 38.99 | 38.99 | 38.99 | 45% | 1179.4944 | 28.3054 | 36.6177 | 38.7913 | 38.6599 | 38.6678 | 38.8899 | 39.4778 | 39.8703 | 40.2552 | 40.7056 | 41.1222 | 41.5272 | 41.5724 | 42.0453 | 41.6846 | 41.6846 | 41.6846 | 41.6846 | 41.6846 | 41.6846 | 41.6846 | 41.6846 | 41.6846 | 41.6846 | 41.6846 | 41.6846 | 41.6846 | 41.6846 | 41.6846 | 41.6846
40% | 3164.4787 | 22.5793 | 29.9532 | 31.9592 | 31.8999 | 31.8966 | 32.1245 | 32.3748 | 32.8889 | 33.2584 | 33.4585 | 33.677 | 33.8773 | 34.2399 | 34.6901 | 34.6578 | 34.6578 | 34.6578 | 34.6578 | 34.6578 | 34.6578 | 34.6578 | 34.6578 | 34.6578 | 34.6578 | 34.6578 | 34.6578 | 34.6578 | 34.6578 | 34.6578 | 34.6578 | 40% | 1808.3816 | 25.1604 | 32.5491 | 34.4812 | 34.3644 | 34.3713 | 34.5688 | 35.0914 | 35.4403 | 35.7824 | 36.1827 | 36.553 | 36.9131 | 36.9532 | 37.3736 | 37.053 | 37.053 | 37.053 | 37.053 | 37.053 | 37.053 | 37.053 | 37.053 | 37.053 | 37.053 | 37.053 | 37.053 | 37.053 | 37.053 | 37.053 | 37.053
35% | 3551.3408 | 19.7569 | 26.2091 | 27.9643 | 27.9124 | 27.9095 | 28.109 | 28.3279 | 28.7778 | 29.1011 | 29.2762 | 29.4674 | 29.6426 | 29.9599 | 30.3538 | 30.3256 | 30.3256 | 30.3256 | 30.3256 | 30.3256 | 30.3256 | 30.3256 | 30.3256 | 30.3256 | 30.3256 | 30.3256 | 30.3256 | 30.3256 | 30.3256 | 30.3256 | 30.3256 | 35% | 2779.1293 | 22.0153 | 28.4805 | 30.171 | 30.0688 | 30.0749 | 30.2477 | 30.705 | 31.0103 | 31.3096 | 31.6599 | 31.9839 | 32.2989 | 32.3341 | 32.7019 | 32.4214 | 32.4214 | 32.4214 | 32.4214 | 32.4214 | 32.4214 | 32.4214 | 32.4214 | 32.4214 | 32.4214 | 32.4214 | 32.4214 | 32.4214 | 32.4214 | 32.4214 | 32.4214
30% | 3758.953 | 16.9345 | 22.4649 | 23.9694 | 23.9249 | 23.9224 | 24.0934 | 24.2811 | 24.6667 | 24.9438 | 25.0939 | 25.2577 | 25.408 | 25.6799 | 26.0176 | 25.9933 | 25.9933 | 25.9933 | 25.9933 | 25.9933 | 25.9933 | 25.9933 | 25.9933 | 25.9933 | 25.9933 | 25.9933 | 25.9933 | 25.9933 | 25.9933 | 25.9933 | 25.9933 | 30% | 3814.165 | 18.8703 | 24.4118 | 25.8609 | 25.7733 | 25.7785 | 25.9266 | 26.3185 | 26.5802 | 26.8368 | 27.1371 | 27.4148 | 27.6848 | 27.7149 | 28.0302 | 27.7897 | 27.7897 | 27.7897 | 27.7897 | 27.7897 | 27.7897 | 27.7897 | 27.7897 | 27.7897 | 27.7897 | 27.7897 | 27.7897 | 27.7897 | 27.7897 | 27.7897 | 27.7897
25% | 3926.4798 | 14.1121 | 18.7208 | 19.9745 | 19.9375 | 19.9354 | 20.0778 | 20.2342 | 20.5556 | 20.7865 | 20.9116 | 21.0481 | 21.1733 | 21.3999 | 21.6813 | 21.6611 | 21.6611 | 21.6611 | 21.6611 | 21.6611 | 21.6611 | 21.6611 | 21.6611 | 21.6611 | 21.6611 | 21.6611 | 21.6611 | 21.6611 | 21.6611 | 21.6611 | 21.6611 | 25% | 4166.9923 | 15.7252 | 20.3432 | 21.5507 | 21.4777 | 21.4821 | 21.6055 | 21.9321 | 22.1502 | 22.364 | 22.6142 | 22.8457 | 23.0707 | 23.0958 | 23.3585 | 23.1581 | 23.1581 | 23.1581 | 23.1581 | 23.1581 | 23.1581 | 23.1581 | 23.1581 | 23.1581 | 23.1581 | 23.1581 | 23.1581 | 23.1581 | 23.1581 | 23.1581 | 23.1581
20% | 4050.5177 | 11.2897 | 14.9766 | 15.9796 | 15.95 | 15.9483 | 16.0623 | 16.1874 | 16.4445 | 16.6292 | 16.7293 | 16.8385 | 16.9386 | 17.1199 | 17.3451 | 17.3289 | 17.3289 | 17.3289 | 17.3289 | 17.3289 | 17.3289 | 17.3289 | 17.3289 | 17.3289 | 17.3289 | 17.3289 | 17.3289 | 17.3289 | 17.3289 | 17.3289 | 17.3289 | 20% | 4282.7105 | 12.5802 | 16.2746 | 17.2406 | 17.1822 | 17.1857 | 17.2844 | 17.5457 | 17.7202 | 17.8912 | 18.0914 | 18.2765 | 18.4565 | 18.4766 | 18.6868 | 18.5265 | 18.5265 | 18.5265 | 18.5265 | 18.5265 | 18.5265 | 18.5265 | 18.5265 | 18.5265 | 18.5265 | 18.5265 | 18.5265 | 18.5265 | 18.5265 | 18.5265 | 18.5265
15% | 4152.622 | 8.4672 | 11.2325 | 11.9847 | 11.9625 | 11.9612 | 12.0467 | 12.1405 | 12.3333 | 12.4719 | 12.5469 | 12.6289 | 12.704 | 12.84 | 13.0088 | 12.9967 | 12.9967 | 12.9967 | 12.9967 | 12.9967 | 12.9967 | 12.9967 | 12.9967 | 12.9967 | 12.9967 | 12.9967 | 12.9967 | 12.9967 | 12.9967 | 12.9967 | 12.9967 | 15% | 4364.7722 | 9.4351 | 12.2059 | 12.9304 | 12.8866 | 12.8893 | 12.9633 | 13.1593 | 13.2901 | 13.4184 | 13.5685 | 13.7074 | 13.8424 | 13.8575 | 14.0151 | 13.8949 | 13.8949 | 13.8949 | 13.8949 | 13.8949 | 13.8949 | 13.8949 | 13.8949 | 13.8949 | 13.8949 | 13.8949 | 13.8949 | 13.8949 | 13.8949 | 13.8949 | 13.8949
10% | 4248.2976 | 5.6448 | 7.4883 | 7.9898 | 7.975 | 7.9741 | 8.0311 | 8.0937 | 8.2222 | 8.3146 | 8.3646 | 8.4192 | 8.4693 | 8.56 | 8.6725 | 8.6644 | 8.6644 | 8.6644 | 8.6644 | 8.6644 | 8.6644 | 8.6644 | 8.6644 | 8.6644 | 8.6644 | 8.6644 | 8.6644 | 8.6644 | 8.6644 | 8.6644 | 8.6644 | 10% | 4391.6218 | 6.2901 | 8.1373 | 8.6203 | 8.5911 | 8.5928 | 8.6422 | 8.7728 | 8.8601 | 8.9456 | 9.0457 | 9.1383 | 9.2283 | 9.2383 | 9.3434 | 9.2632 | 9.2632 | 9.2632 | 9.2632 | 9.2632 | 9.2632 | 9.2632 | 9.2632 | 9.2632 | 9.2632 | 9.2632 | 9.2632 | 9.2632 | 9.2632 | 9.2632 | 9.2632
5% | 4361.7469 | 2.8224 | 3.7442 | 3.9949 | 3.9875 | 3.9871 | 4.0156 | 4.0468 | 4.1111 | 4.1573 | 4.1823 | 4.2096 | 4.2347 | 4.28 | 4.3363 | 4.3322 | 4.3322 | 4.3322 | 4.3322 | 4.3322 | 4.3322 | 4.3322 | 4.3322 | 4.3322 | 4.3322 | 4.3322 | 4.3322 | 4.3322 | 4.3322 | 4.3322 | 4.3322 | 5% | 4391.6218 | 3.145 | 4.0686 | 4.3101 | 4.2955 | 4.2964 | 4.3211 | 4.3864 | 4.43 | 4.4728 | 4.5228 | 4.5691 | 4.6141 | 4.6192 | 4.6717 | 4.6316 | 4.6316 | 4.6316 | 4.6316 | 4.6316 | 4.6316 | 4.6316 | 4.6316 | 4.6316 | 4.6316 | 4.6316 | 4.6316 | 4.6316 | 4.6316 | 4.6316 | 4.6316
9.992e-14% | 4391.6218 | 5.6403e-14 | 7.4823e-14 | 7.9834e-14 | 7.9686e-14 | 7.9678e-14 | 8.0247e-14 | 8.0872e-14 | 8.2157e-14 | 8.308e-14 | 8.3579e-14 | 8.4125e-14 | 8.4626e-14 | 8.5531e-14 | 8.6656e-14 | 8.6575e-14 | 8.6575e-14 | 8.6575e-14 | 8.6575e-14 | 8.6575e-14 | 8.6575e-14 | 8.6575e-14 | 8.6575e-14 | 8.6575e-14 | 8.6575e-14 | 8.6575e-14 | 8.6575e-14 | 8.6575e-14 | 8.6575e-14 | 8.6575e-14 | 8.6575e-14 | 9.992e-14% | 4391.6218 | 6.2851e-14 | 8.1308e-14 | 8.6134e-14 | 8.5842e-14 | 8.586e-14 | 8.6353e-14 | 8.7658e-14 | 8.853e-14 | 8.9385e-14 | 9.0385e-14 | 9.131e-14 | 9.2209e-14 | 9.2309e-14 | 9.3359e-14 | 9.2558e-14 | 9.2558e-14 | 9.2558e-14 | 9.2558e-14 | 9.2558e-14 | 9.2558e-14 | 9.2558e-14 | 9.2558e-14 | 9.2558e-14 | 9.2558e-14 | 9.2558e-14 | 9.2558e-14 | 9.2558e-14 | 9.2558e-14 | 9.2558e-14 | 9.2558e-14
Option 4
Winter Season | [31 empty] | Winter Season
P50 | [31 empty] | P10
% of MD | Winter - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Winter - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 49.7042 | 68.8514 | 73.8223 | 70.6663 | 71.3214 | 72.4563 | 75.0441 | 76.7726 | 78.9664 | 80.1029 | 81.1001 | 79.2461 | 81.4092 | 84.8125 | 82.2221 | 82.2221 | 82.2221 | 82.2221 | 82.2221 | 82.2221 | 82.2221 | 82.2221 | 82.2221 | 82.2221 | 82.2221 | 82.2221 | 82.2221 | 82.2221 | 82.2221 | 82.2221 | 100% | 0 | 53.1876 | 72.0932 | 77.2584 | 74.0542 | 74.5557 | 75.6659 | 78.2942 | 79.7249 | 82.4587 | 90.7777 | 83.9092 | 82.5626 | 84.3699 | 88.3278 | 85.6413 | 85.6413 | 85.6413 | 85.6413 | 85.6413 | 85.6413 | 85.6413 | 85.6413 | 85.6413 | 85.6413 | 85.6413 | 85.6413 | 85.6413 | 85.6413 | 85.6413 | 85.6413
99% | 1.486 | 49.2072 | 68.1629 | 73.0841 | 69.9597 | 70.6082 | 71.7318 | 74.2937 | 76.0049 | 78.1767 | 79.3019 | 80.2891 | 78.4536 | 80.5951 | 83.9643 | 81.3998 | 81.3998 | 81.3998 | 81.3998 | 81.3998 | 81.3998 | 81.3998 | 81.3998 | 81.3998 | 81.3998 | 81.3998 | 81.3998 | 81.3998 | 81.3998 | 81.3998 | 81.3998 | 99% | 1.486 | 52.6557 | 71.3723 | 76.4858 | 73.3137 | 73.8101 | 74.9092 | 77.5112 | 78.9277 | 81.6341 | 89.87 | 83.0701 | 81.737 | 83.5262 | 87.4445 | 84.7849 | 84.7849 | 84.7849 | 84.7849 | 84.7849 | 84.7849 | 84.7849 | 84.7849 | 84.7849 | 84.7849 | 84.7849 | 84.7849 | 84.7849 | 84.7849 | 84.7849 | 84.7849
98% | 3.2692 | 48.7101 | 67.4743 | 72.3458 | 69.253 | 69.895 | 71.0072 | 73.5432 | 75.2372 | 77.3871 | 78.5009 | 79.4781 | 77.6612 | 79.781 | 83.1162 | 80.5776 | 80.5776 | 80.5776 | 80.5776 | 80.5776 | 80.5776 | 80.5776 | 80.5776 | 80.5776 | 80.5776 | 80.5776 | 80.5776 | 80.5776 | 80.5776 | 80.5776 | 80.5776 | 98% | 3.2692 | 52.1238 | 70.6514 | 75.7133 | 72.5731 | 73.0646 | 74.1526 | 76.7283 | 78.1304 | 80.8095 | 88.9622 | 82.231 | 80.9113 | 82.6825 | 86.5612 | 83.9285 | 83.9285 | 83.9285 | 83.9285 | 83.9285 | 83.9285 | 83.9285 | 83.9285 | 83.9285 | 83.9285 | 83.9285 | 83.9285 | 83.9285 | 83.9285 | 83.9285 | 83.9285
97% | 6.8356 | 48.2131 | 66.7858 | 71.6076 | 68.5463 | 69.1818 | 70.2827 | 72.7928 | 74.4695 | 76.5974 | 77.6998 | 78.6671 | 76.8687 | 78.967 | 82.2681 | 79.7554 | 79.7554 | 79.7554 | 79.7554 | 79.7554 | 79.7554 | 79.7554 | 79.7554 | 79.7554 | 79.7554 | 79.7554 | 79.7554 | 79.7554 | 79.7554 | 79.7554 | 79.7554 | 97% | 6.8356 | 51.5919 | 69.9304 | 74.9407 | 71.8326 | 72.319 | 73.3959 | 75.9454 | 77.3332 | 79.985 | 88.0544 | 81.3919 | 80.0857 | 81.8388 | 85.678 | 83.0721 | 83.0721 | 83.0721 | 83.0721 | 83.0721 | 83.0721 | 83.0721 | 83.0721 | 83.0721 | 83.0721 | 83.0721 | 83.0721 | 83.0721 | 83.0721 | 83.0721 | 83.0721
95% | 17.5347 | 47.219 | 65.4088 | 70.1312 | 67.133 | 67.7553 | 68.8335 | 71.2919 | 72.934 | 75.0181 | 76.0978 | 77.0451 | 75.2838 | 77.3388 | 80.5718 | 78.111 | 78.111 | 78.111 | 78.111 | 78.111 | 78.111 | 78.111 | 78.111 | 78.111 | 78.111 | 78.111 | 78.111 | 78.111 | 78.111 | 78.111 | 78.111 | 95% | 17.5347 | 50.5282 | 68.4886 | 73.3955 | 70.3515 | 70.8279 | 71.8826 | 74.3795 | 75.7387 | 78.3358 | 86.2389 | 79.7138 | 78.4345 | 80.1514 | 83.9114 | 81.3592 | 81.3592 | 81.3592 | 81.3592 | 81.3592 | 81.3592 | 81.3592 | 81.3592 | 81.3592 | 81.3592 | 81.3592 | 81.3592 | 81.3592 | 81.3592 | 81.3592 | 81.3592
90% | 78.7576 | 44.7338 | 61.9662 | 66.4401 | 63.5997 | 64.1893 | 65.2107 | 67.5397 | 69.0954 | 71.0697 | 72.0926 | 72.9901 | 71.3215 | 73.2683 | 76.3312 | 73.9999 | 73.9999 | 73.9999 | 73.9999 | 73.9999 | 73.9999 | 73.9999 | 73.9999 | 73.9999 | 73.9999 | 73.9999 | 73.9999 | 73.9999 | 73.9999 | 73.9999 | 73.9999 | 90% | 78.7576 | 47.8688 | 64.8839 | 69.5326 | 66.6488 | 67.1001 | 68.0993 | 70.4648 | 71.7524 | 74.2128 | 81.7 | 75.5183 | 74.3063 | 75.9329 | 79.495 | 77.0772 | 77.0772 | 77.0772 | 77.0772 | 77.0772 | 77.0772 | 77.0772 | 77.0772 | 77.0772 | 77.0772 | 77.0772 | 77.0772 | 77.0772 | 77.0772 | 77.0772 | 77.0772
85% | 236.8672 | 42.2486 | 58.5237 | 62.7489 | 60.0664 | 60.6232 | 61.5879 | 63.7875 | 65.2567 | 67.1214 | 68.0875 | 68.9351 | 67.3592 | 69.1978 | 72.0906 | 69.8888 | 69.8888 | 69.8888 | 69.8888 | 69.8888 | 69.8888 | 69.8888 | 69.8888 | 69.8888 | 69.8888 | 69.8888 | 69.8888 | 69.8888 | 69.8888 | 69.8888 | 69.8888 | 85% | 236.8672 | 45.2094 | 61.2792 | 65.6697 | 62.9461 | 63.3723 | 64.316 | 66.5501 | 67.7662 | 70.0899 | 77.1611 | 71.3228 | 70.1782 | 71.7144 | 75.0786 | 72.7951 | 72.7951 | 72.7951 | 72.7951 | 72.7951 | 72.7951 | 72.7951 | 72.7951 | 72.7951 | 72.7951 | 72.7951 | 72.7951 | 72.7951 | 72.7951 | 72.7951 | 72.7951
80% | 497.5104 | 39.7634 | 55.0811 | 59.0578 | 56.5331 | 57.0571 | 57.9651 | 60.0353 | 61.4181 | 63.1731 | 64.0823 | 64.88 | 63.3969 | 65.1274 | 67.85 | 65.7777 | 65.7777 | 65.7777 | 65.7777 | 65.7777 | 65.7777 | 65.7777 | 65.7777 | 65.7777 | 65.7777 | 65.7777 | 65.7777 | 65.7777 | 65.7777 | 65.7777 | 65.7777 | 80% | 497.5104 | 42.55 | 57.6746 | 61.8067 | 59.2434 | 59.6445 | 60.5327 | 62.6353 | 63.7799 | 65.967 | 72.6222 | 67.1274 | 66.0501 | 67.4959 | 70.6622 | 68.5131 | 68.5131 | 68.5131 | 68.5131 | 68.5131 | 68.5131 | 68.5131 | 68.5131 | 68.5131 | 68.5131 | 68.5131 | 68.5131 | 68.5131 | 68.5131 | 68.5131 | 68.5131
75% | 803.6248 | 37.2782 | 51.6385 | 55.3667 | 52.9997 | 53.4911 | 54.3423 | 56.2831 | 57.5795 | 59.2248 | 60.0772 | 60.825 | 59.4346 | 61.0569 | 63.6093 | 61.6665 | 61.6665 | 61.6665 | 61.6665 | 61.6665 | 61.6665 | 61.6665 | 61.6665 | 61.6665 | 61.6665 | 61.6665 | 61.6665 | 61.6665 | 61.6665 | 61.6665 | 61.6665 | 75% | 803.6248 | 39.8907 | 54.0699 | 57.9438 | 55.5407 | 55.9167 | 56.7494 | 58.7206 | 59.7937 | 61.844 | 68.0833 | 62.9319 | 61.9219 | 63.2774 | 66.2458 | 64.231 | 64.231 | 64.231 | 64.231 | 64.231 | 64.231 | 64.231 | 64.231 | 64.231 | 64.231 | 64.231 | 64.231 | 64.231 | 64.231 | 64.231 | 64.231
70% | 1155.2107 | 34.793 | 48.196 | 51.6756 | 49.4664 | 49.925 | 50.7194 | 52.5309 | 53.7408 | 55.2765 | 56.0721 | 56.77 | 55.4723 | 56.9865 | 59.3687 | 57.5554 | 57.5554 | 57.5554 | 57.5554 | 57.5554 | 57.5554 | 57.5554 | 57.5554 | 57.5554 | 57.5554 | 57.5554 | 57.5554 | 57.5554 | 57.5554 | 57.5554 | 57.5554 | 70% | 1155.2107 | 37.2313 | 50.4653 | 54.0809 | 51.838 | 52.189 | 52.9661 | 54.8059 | 55.8074 | 57.7211 | 63.5444 | 58.7365 | 57.7938 | 59.0589 | 61.8295 | 59.9489 | 59.9489 | 59.9489 | 59.9489 | 59.9489 | 59.9489 | 59.9489 | 59.9489 | 59.9489 | 59.9489 | 59.9489 | 59.9489 | 59.9489 | 59.9489 | 59.9489 | 59.9489
65% | 1553.1596 | 32.3077 | 44.7534 | 47.9845 | 45.9331 | 46.3589 | 47.0966 | 48.7787 | 49.9022 | 51.3282 | 52.0669 | 52.715 | 51.51 | 52.916 | 55.1281 | 53.4443 | 53.4443 | 53.4443 | 53.4443 | 53.4443 | 53.4443 | 53.4443 | 53.4443 | 53.4443 | 53.4443 | 53.4443 | 53.4443 | 53.4443 | 53.4443 | 53.4443 | 53.4443 | 65% | 1553.1596 | 34.5719 | 46.8606 | 50.218 | 48.1352 | 48.4612 | 49.1828 | 50.8912 | 51.8212 | 53.5982 | 59.0055 | 54.541 | 53.6657 | 54.8405 | 57.4131 | 55.6669 | 55.6669 | 55.6669 | 55.6669 | 55.6669 | 55.6669 | 55.6669 | 55.6669 | 55.6669 | 55.6669 | 55.6669 | 55.6669 | 55.6669 | 55.6669 | 55.6669 | 55.6669
60% | 2026.2996 | 29.8225 | 41.3108 | 44.2934 | 42.3998 | 42.7928 | 43.4738 | 45.0265 | 46.0636 | 47.3798 | 48.0618 | 48.66 | 47.5477 | 48.8455 | 50.8875 | 49.3332 | 49.3332 | 49.3332 | 49.3332 | 49.3332 | 49.3332 | 49.3332 | 49.3332 | 49.3332 | 49.3332 | 49.3332 | 49.3332 | 49.3332 | 49.3332 | 49.3332 | 49.3332 | 60% | 2026.2996 | 31.9125 | 43.2559 | 46.3551 | 44.4325 | 44.7334 | 45.3995 | 46.9765 | 47.835 | 49.4752 | 54.4666 | 50.3455 | 49.5376 | 50.622 | 52.9967 | 51.3848 | 51.3848 | 51.3848 | 51.3848 | 51.3848 | 51.3848 | 51.3848 | 51.3848 | 51.3848 | 51.3848 | 51.3848 | 51.3848 | 51.3848 | 51.3848 | 51.3848 | 51.3848
55% | 2598.4068 | 27.3373 | 37.8683 | 40.6023 | 38.8665 | 39.2268 | 39.851 | 41.2743 | 42.225 | 43.4315 | 44.0566 | 44.605 | 43.5854 | 44.7751 | 46.6469 | 45.2221 | 45.2221 | 45.2221 | 45.2221 | 45.2221 | 45.2221 | 45.2221 | 45.2221 | 45.2221 | 45.2221 | 45.2221 | 45.2221 | 45.2221 | 45.2221 | 45.2221 | 45.2221 | 55% | 2598.4068 | 29.2532 | 39.6513 | 42.4921 | 40.7298 | 41.0056 | 41.6162 | 43.0618 | 43.8487 | 45.3523 | 49.9278 | 46.1501 | 45.4094 | 46.4035 | 48.5803 | 47.1027 | 47.1027 | 47.1027 | 47.1027 | 47.1027 | 47.1027 | 47.1027 | 47.1027 | 47.1027 | 47.1027 | 47.1027 | 47.1027 | 47.1027 | 47.1027 | 47.1027 | 47.1027
50% | 3233.5201 | 24.8521 | 34.4257 | 36.9111 | 35.3332 | 35.6607 | 36.2282 | 37.5221 | 38.3863 | 39.4832 | 40.0515 | 40.55 | 39.623 | 40.7046 | 42.4062 | 41.111 | 41.111 | 41.111 | 41.111 | 41.111 | 41.111 | 41.111 | 41.111 | 41.111 | 41.111 | 41.111 | 41.111 | 41.111 | 41.111 | 41.111 | 41.111 | 50% | 3233.5201 | 26.5938 | 36.0466 | 38.6292 | 37.0271 | 37.2778 | 37.833 | 39.1471 | 39.8625 | 41.2294 | 45.3889 | 41.9546 | 41.2813 | 42.185 | 44.1639 | 42.8207 | 42.8207 | 42.8207 | 42.8207 | 42.8207 | 42.8207 | 42.8207 | 42.8207 | 42.8207 | 42.8207 | 42.8207 | 42.8207 | 42.8207 | 42.8207 | 42.8207 | 42.8207
45% | 3775.313 | 22.3669 | 30.9831 | 33.22 | 31.7998 | 32.0946 | 32.6054 | 33.7699 | 34.5477 | 35.5349 | 36.0463 | 36.495 | 35.6607 | 36.6342 | 38.1656 | 36.9999 | 36.9999 | 36.9999 | 36.9999 | 36.9999 | 36.9999 | 36.9999 | 36.9999 | 36.9999 | 36.9999 | 36.9999 | 36.9999 | 36.9999 | 36.9999 | 36.9999 | 36.9999 | 45% | 3775.313 | 23.9344 | 32.442 | 34.7663 | 33.3244 | 33.55 | 34.0497 | 35.2324 | 35.8762 | 37.1064 | 40.85 | 37.7591 | 37.1532 | 37.9665 | 39.7475 | 38.5386 | 38.5386 | 38.5386 | 38.5386 | 38.5386 | 38.5386 | 38.5386 | 38.5386 | 38.5386 | 38.5386 | 38.5386 | 38.5386 | 38.5386 | 38.5386 | 38.5386 | 38.5386
40% | 4072.8088 | 19.8817 | 27.5405 | 29.5289 | 28.2665 | 28.5286 | 28.9825 | 30.0176 | 30.7091 | 31.5866 | 32.0412 | 32.44 | 31.6984 | 32.5637 | 33.925 | 32.8888 | 32.8888 | 32.8888 | 32.8888 | 32.8888 | 32.8888 | 32.8888 | 32.8888 | 32.8888 | 32.8888 | 32.8888 | 32.8888 | 32.8888 | 32.8888 | 32.8888 | 32.8888 | 40% | 4072.8088 | 21.275 | 28.8373 | 30.9034 | 29.6217 | 29.8223 | 30.2664 | 31.3177 | 31.89 | 32.9835 | 36.3111 | 33.5637 | 33.025 | 33.748 | 35.3311 | 34.2565 | 34.2565 | 34.2565 | 34.2565 | 34.2565 | 34.2565 | 34.2565 | 34.2565 | 34.2565 | 34.2565 | 34.2565 | 34.2565 | 34.2565 | 34.2565 | 34.2565 | 34.2565
35% | 4198.821 | 17.3965 | 24.098 | 25.8378 | 24.7332 | 24.9625 | 25.3597 | 26.2654 | 26.8704 | 27.6382 | 28.036 | 28.385 | 27.7361 | 28.4932 | 29.6844 | 28.7777 | 28.7777 | 28.7777 | 28.7777 | 28.7777 | 28.7777 | 28.7777 | 28.7777 | 28.7777 | 28.7777 | 28.7777 | 28.7777 | 28.7777 | 28.7777 | 28.7777 | 28.7777 | 35% | 4198.821 | 18.6156 | 25.2326 | 27.0405 | 25.919 | 26.0945 | 26.4831 | 27.403 | 27.9037 | 28.8606 | 31.7722 | 29.3682 | 28.8969 | 29.5295 | 30.9147 | 29.9745 | 29.9745 | 29.9745 | 29.9745 | 29.9745 | 29.9745 | 29.9745 | 29.9745 | 29.9745 | 29.9745 | 29.9745 | 29.9745 | 29.9745 | 29.9745 | 29.9745 | 29.9745
30% | 4271.3374 | 14.9113 | 20.6554 | 22.1467 | 21.1999 | 21.3964 | 21.7369 | 22.5132 | 23.0318 | 23.6899 | 24.0309 | 24.33 | 23.7738 | 24.4228 | 25.4437 | 24.6666 | 24.6666 | 24.6666 | 24.6666 | 24.6666 | 24.6666 | 24.6666 | 24.6666 | 24.6666 | 24.6666 | 24.6666 | 24.6666 | 24.6666 | 24.6666 | 24.6666 | 24.6666 | 30% | 4271.3374 | 15.9563 | 21.628 | 23.1775 | 22.2163 | 22.3667 | 22.6998 | 23.4883 | 23.9175 | 24.7376 | 27.2333 | 25.1728 | 24.7688 | 25.311 | 26.4983 | 25.6924 | 25.6924 | 25.6924 | 25.6924 | 25.6924 | 25.6924 | 25.6924 | 25.6924 | 25.6924 | 25.6924 | 25.6924 | 25.6924 | 25.6924 | 25.6924 | 25.6924 | 25.6924
25% | 4321.8611 | 12.4261 | 17.2128 | 18.4556 | 17.6666 | 17.8304 | 18.1141 | 18.761 | 19.1932 | 19.7416 | 20.0257 | 20.275 | 19.8115 | 20.3523 | 21.2031 | 20.5555 | 20.5555 | 20.5555 | 20.5555 | 20.5555 | 20.5555 | 20.5555 | 20.5555 | 20.5555 | 20.5555 | 20.5555 | 20.5555 | 20.5555 | 20.5555 | 20.5555 | 20.5555 | 25% | 4321.8611 | 13.2969 | 18.0233 | 19.3146 | 18.5136 | 18.6389 | 18.9165 | 19.5735 | 19.9312 | 20.6147 | 22.6944 | 20.9773 | 20.6406 | 21.0925 | 22.0819 | 21.4103 | 21.4103 | 21.4103 | 21.4103 | 21.4103 | 21.4103 | 21.4103 | 21.4103 | 21.4103 | 21.4103 | 21.4103 | 21.4103 | 21.4103 | 21.4103 | 21.4103 | 21.4103
20% | 4353.067 | 9.9408 | 13.7703 | 14.7645 | 14.1333 | 14.2643 | 14.4913 | 15.0088 | 15.3545 | 15.7933 | 16.0206 | 16.22 | 15.8492 | 16.2818 | 16.9625 | 16.4444 | 16.4444 | 16.4444 | 16.4444 | 16.4444 | 16.4444 | 16.4444 | 16.4444 | 16.4444 | 16.4444 | 16.4444 | 16.4444 | 16.4444 | 16.4444 | 16.4444 | 16.4444 | 20% | 4353.067 | 10.6375 | 14.4186 | 15.4517 | 14.8108 | 14.9111 | 15.1332 | 15.6588 | 15.945 | 16.4917 | 18.1555 | 16.7818 | 16.5125 | 16.874 | 17.6656 | 17.1283 | 17.1283 | 17.1283 | 17.1283 | 17.1283 | 17.1283 | 17.1283 | 17.1283 | 17.1283 | 17.1283 | 17.1283 | 17.1283 | 17.1283 | 17.1283 | 17.1283 | 17.1283
15% | 4369.4129 | 7.4556 | 10.3277 | 11.0733 | 10.5999 | 10.6982 | 10.8685 | 11.2566 | 11.5159 | 11.845 | 12.0154 | 12.165 | 11.8869 | 12.2114 | 12.7219 | 12.3333 | 12.3333 | 12.3333 | 12.3333 | 12.3333 | 12.3333 | 12.3333 | 12.3333 | 12.3333 | 12.3333 | 12.3333 | 12.3333 | 12.3333 | 12.3333 | 12.3333 | 12.3333 | 15% | 4369.4129 | 7.9781 | 10.814 | 11.5888 | 11.1081 | 11.1833 | 11.3499 | 11.7441 | 11.9587 | 12.3688 | 13.6167 | 12.5864 | 12.3844 | 12.6555 | 13.2492 | 12.8462 | 12.8462 | 12.8462 | 12.8462 | 12.8462 | 12.8462 | 12.8462 | 12.8462 | 12.8462 | 12.8462 | 12.8462 | 12.8462 | 12.8462 | 12.8462 | 12.8462 | 12.8462
10% | 4378.6261 | 4.9704 | 6.8851 | 7.3822 | 7.0666 | 7.1321 | 7.2456 | 7.5044 | 7.6773 | 7.8966 | 8.0103 | 8.11 | 7.9246 | 8.1409 | 8.4812 | 8.2222 | 8.2222 | 8.2222 | 8.2222 | 8.2222 | 8.2222 | 8.2222 | 8.2222 | 8.2222 | 8.2222 | 8.2222 | 8.2222 | 8.2222 | 8.2222 | 8.2222 | 8.2222 | 10% | 4378.6261 | 5.3188 | 7.2093 | 7.7258 | 7.4054 | 7.4556 | 7.5666 | 7.8294 | 7.9725 | 8.2459 | 9.0778 | 8.3909 | 8.2563 | 8.437 | 8.8328 | 8.5641 | 8.5641 | 8.5641 | 8.5641 | 8.5641 | 8.5641 | 8.5641 | 8.5641 | 8.5641 | 8.5641 | 8.5641 | 8.5641 | 8.5641 | 8.5641 | 8.5641 | 8.5641
5% | 4391.7028 | 2.4852 | 3.4426 | 3.6911 | 3.5333 | 3.5661 | 3.6228 | 3.7522 | 3.8386 | 3.9483 | 4.0051 | 4.055 | 3.9623 | 4.0705 | 4.2406 | 4.1111 | 4.1111 | 4.1111 | 4.1111 | 4.1111 | 4.1111 | 4.1111 | 4.1111 | 4.1111 | 4.1111 | 4.1111 | 4.1111 | 4.1111 | 4.1111 | 4.1111 | 4.1111 | 5% | 4391.7028 | 2.6594 | 3.6047 | 3.8629 | 3.7027 | 3.7278 | 3.7833 | 3.9147 | 3.9862 | 4.1229 | 4.5389 | 4.1955 | 4.1281 | 4.2185 | 4.4164 | 4.2821 | 4.2821 | 4.2821 | 4.2821 | 4.2821 | 4.2821 | 4.2821 | 4.2821 | 4.2821 | 4.2821 | 4.2821 | 4.2821 | 4.2821 | 4.2821 | 4.2821 | 4.2821
9.992e-14% | 4391.7028 | 4.9664e-14 | 6.8796e-14 | 7.3763e-14 | 7.061e-14 | 7.1264e-14 | 7.2398e-14 | 7.4984e-14 | 7.6711e-14 | 7.8903e-14 | 8.0039e-14 | 8.1035e-14 | 7.9183e-14 | 8.1344e-14 | 8.4745e-14 | 8.2156e-14 | 8.2156e-14 | 8.2156e-14 | 8.2156e-14 | 8.2156e-14 | 8.2156e-14 | 8.2156e-14 | 8.2156e-14 | 8.2156e-14 | 8.2156e-14 | 8.2156e-14 | 8.2156e-14 | 8.2156e-14 | 8.2156e-14 | 8.2156e-14 | 8.2156e-14 | 9.992e-14% | 4391.7028 | 5.3145e-14 | 7.2036e-14 | 7.7197e-14 | 7.3995e-14 | 7.4496e-14 | 7.5605e-14 | 7.8232e-14 | 7.9661e-14 | 8.2393e-14 | 9.0705e-14 | 8.3842e-14 | 8.2497e-14 | 8.4302e-14 | 8.8257e-14 | 8.5573e-14 | 8.5573e-14 | 8.5573e-14 | 8.5573e-14 | 8.5573e-14 | 8.5573e-14 | 8.5573e-14 | 8.5573e-14 | 8.5573e-14 | 8.5573e-14 | 8.5573e-14 | 8.5573e-14 | 8.5573e-14 | 8.5573e-14 | 8.5573e-14 | 8.5573e-14
Summer Season | [31 empty] | Summer Season
P50 | [31 empty] | P10
% of MD | Summer - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Summer - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 56.4483 | 74.8831 | 79.898 | 75.7498 | 75.7414 | 76.3113 | 76.9369 | 78.2223 | 79.1461 | 79.6463 | 80.1925 | 80.6932 | 81.5997 | 82.7253 | 82.6445 | 82.6445 | 82.6445 | 82.6445 | 82.6445 | 82.6445 | 82.6445 | 82.6445 | 82.6445 | 82.6445 | 82.6445 | 82.6445 | 82.6445 | 82.6445 | 82.6445 | 82.6445 | 100% | 0 | 62.901 | 81.3728 | 86.203 | 81.9109 | 81.9284 | 82.4219 | 83.7284 | 84.6008 | 85.4561 | 86.4569 | 87.3826 | 88.2827 | 88.383 | 89.434 | 88.6325 | 88.6325 | 88.6325 | 88.6325 | 88.6325 | 88.6325 | 88.6325 | 88.6325 | 88.6325 | 88.6325 | 88.6325 | 88.6325 | 88.6325 | 88.6325 | 88.6325 | 88.6325
99% | 0 | 55.8838 | 74.1343 | 79.099 | 74.9923 | 74.984 | 75.5482 | 76.1675 | 77.44 | 78.3546 | 78.8498 | 79.3906 | 79.8863 | 80.7837 | 81.898 | 81.818 | 81.818 | 81.818 | 81.818 | 81.818 | 81.818 | 81.818 | 81.818 | 81.818 | 81.818 | 81.818 | 81.818 | 81.818 | 81.818 | 81.818 | 81.818 | 99% | 1.5127 | 62.272 | 80.559 | 85.341 | 81.0918 | 81.1091 | 81.5977 | 82.8912 | 83.7548 | 84.6015 | 85.5923 | 86.5088 | 87.3998 | 87.4992 | 88.5396 | 87.7461 | 87.7461 | 87.7461 | 87.7461 | 87.7461 | 87.7461 | 87.7461 | 87.7461 | 87.7461 | 87.7461 | 87.7461 | 87.7461 | 87.7461 | 87.7461 | 87.7461 | 87.7461
98% | 0 | 55.3193 | 73.3854 | 78.3 | 74.2348 | 74.2266 | 74.7851 | 75.3981 | 76.6578 | 77.5632 | 78.0534 | 78.5886 | 79.0794 | 79.9677 | 81.0708 | 80.9916 | 80.9916 | 80.9916 | 80.9916 | 80.9916 | 80.9916 | 80.9916 | 80.9916 | 80.9916 | 80.9916 | 80.9916 | 80.9916 | 80.9916 | 80.9916 | 80.9916 | 80.9916 | 98% | 2.269 | 61.643 | 79.7453 | 84.4789 | 80.2727 | 80.2898 | 80.7735 | 82.0539 | 82.9087 | 83.747 | 84.7277 | 85.635 | 86.517 | 86.6154 | 87.6453 | 86.8598 | 86.8598 | 86.8598 | 86.8598 | 86.8598 | 86.8598 | 86.8598 | 86.8598 | 86.8598 | 86.8598 | 86.8598 | 86.8598 | 86.8598 | 86.8598 | 86.8598 | 86.8598
97% | 0.37816 | 54.7549 | 72.6366 | 77.501 | 73.4773 | 73.4692 | 74.022 | 74.6288 | 75.8756 | 76.7717 | 77.2569 | 77.7867 | 78.2724 | 79.1517 | 80.2435 | 80.1651 | 80.1651 | 80.1651 | 80.1651 | 80.1651 | 80.1651 | 80.1651 | 80.1651 | 80.1651 | 80.1651 | 80.1651 | 80.1651 | 80.1651 | 80.1651 | 80.1651 | 80.1651 | 97% | 3.7816 | 61.014 | 78.9316 | 83.6169 | 79.4536 | 79.4705 | 79.9492 | 81.2166 | 82.0627 | 82.8924 | 83.8632 | 84.7611 | 85.6342 | 85.7315 | 86.751 | 85.9735 | 85.9735 | 85.9735 | 85.9735 | 85.9735 | 85.9735 | 85.9735 | 85.9735 | 85.9735 | 85.9735 | 85.9735 | 85.9735 | 85.9735 | 85.9735 | 85.9735 | 85.9735
95% | 2.269 | 53.6259 | 71.1389 | 75.9031 | 71.9623 | 71.9544 | 72.4958 | 73.09 | 74.3112 | 75.1888 | 75.664 | 76.1829 | 76.6586 | 77.5197 | 78.589 | 78.5122 | 78.5122 | 78.5122 | 78.5122 | 78.5122 | 78.5122 | 78.5122 | 78.5122 | 78.5122 | 78.5122 | 78.5122 | 78.5122 | 78.5122 | 78.5122 | 78.5122 | 78.5122 | 95% | 6.0506 | 59.7559 | 77.3041 | 81.8928 | 77.8153 | 77.832 | 78.3008 | 79.542 | 80.3707 | 81.1833 | 82.134 | 83.0135 | 83.8685 | 83.9639 | 84.9623 | 84.2008 | 84.2008 | 84.2008 | 84.2008 | 84.2008 | 84.2008 | 84.2008 | 84.2008 | 84.2008 | 84.2008 | 84.2008 | 84.2008 | 84.2008 | 84.2008 | 84.2008 | 84.2008
90% | 5.6725 | 50.8035 | 67.3948 | 71.9082 | 68.1748 | 68.1673 | 68.6802 | 69.2432 | 70.4 | 71.2315 | 71.6817 | 72.1732 | 72.6239 | 73.4397 | 74.4527 | 74.38 | 74.38 | 74.38 | 74.38 | 74.38 | 74.38 | 74.38 | 74.38 | 74.38 | 74.38 | 74.38 | 74.38 | 74.38 | 74.38 | 74.38 | 74.38 | 90% | 16.2611 | 56.6109 | 73.2355 | 77.5827 | 73.7198 | 73.7355 | 74.1797 | 75.3556 | 76.1407 | 76.9105 | 77.8112 | 78.6444 | 79.4544 | 79.5447 | 80.4906 | 79.7692 | 79.7692 | 79.7692 | 79.7692 | 79.7692 | 79.7692 | 79.7692 | 79.7692 | 79.7692 | 79.7692 | 79.7692 | 79.7692 | 79.7692 | 79.7692 | 79.7692 | 79.7692
85% | 15.8829 | 47.9811 | 63.6506 | 67.9133 | 64.3874 | 64.3802 | 64.8646 | 65.3963 | 66.4889 | 67.2742 | 67.6994 | 68.1636 | 68.5893 | 69.3598 | 70.3165 | 70.2478 | 70.2478 | 70.2478 | 70.2478 | 70.2478 | 70.2478 | 70.2478 | 70.2478 | 70.2478 | 70.2478 | 70.2478 | 70.2478 | 70.2478 | 70.2478 | 70.2478 | 70.2478 | 85% | 26.4715 | 53.4658 | 69.1669 | 73.2725 | 69.6243 | 69.6391 | 70.0586 | 71.1692 | 71.9106 | 72.6377 | 73.4883 | 74.2752 | 75.0403 | 75.1256 | 76.0189 | 75.3376 | 75.3376 | 75.3376 | 75.3376 | 75.3376 | 75.3376 | 75.3376 | 75.3376 | 75.3376 | 75.3376 | 75.3376 | 75.3376 | 75.3376 | 75.3376 | 75.3376 | 75.3376
80% | 31.0095 | 45.1586 | 59.9065 | 63.9184 | 60.5999 | 60.5932 | 61.0491 | 61.5495 | 62.5778 | 63.3169 | 63.717 | 64.154 | 64.5546 | 65.2798 | 66.1802 | 66.1156 | 66.1156 | 66.1156 | 66.1156 | 66.1156 | 66.1156 | 66.1156 | 66.1156 | 66.1156 | 66.1156 | 66.1156 | 66.1156 | 66.1156 | 66.1156 | 66.1156 | 66.1156 | 80% | 34.0348 | 50.3208 | 65.0982 | 68.9624 | 65.5287 | 65.5427 | 65.9375 | 66.9827 | 67.6806 | 68.3649 | 69.1655 | 69.9061 | 70.6261 | 70.7064 | 71.5472 | 70.906 | 70.906 | 70.906 | 70.906 | 70.906 | 70.906 | 70.906 | 70.906 | 70.906 | 70.906 | 70.906 | 70.906 | 70.906 | 70.906 | 70.906 | 70.906
75% | 72.9857 | 42.3362 | 56.1623 | 59.9235 | 56.8124 | 56.8061 | 57.2335 | 57.7027 | 58.6667 | 59.3596 | 59.7347 | 60.1444 | 60.5199 | 61.1998 | 62.044 | 61.9833 | 61.9833 | 61.9833 | 61.9833 | 61.9833 | 61.9833 | 61.9833 | 61.9833 | 61.9833 | 61.9833 | 61.9833 | 61.9833 | 61.9833 | 61.9833 | 61.9833 | 61.9833 | 75% | 48.405 | 47.1757 | 61.0296 | 64.6522 | 61.4332 | 61.4463 | 61.8164 | 62.7963 | 63.4506 | 64.0921 | 64.8427 | 65.537 | 66.212 | 66.2873 | 67.0755 | 66.4744 | 66.4744 | 66.4744 | 66.4744 | 66.4744 | 66.4744 | 66.4744 | 66.4744 | 66.4744 | 66.4744 | 66.4744 | 66.4744 | 66.4744 | 66.4744 | 66.4744 | 66.4744
70% | 150.5094 | 39.5138 | 52.4182 | 55.9286 | 53.0249 | 53.019 | 53.4179 | 53.8558 | 54.7556 | 55.4023 | 55.7524 | 56.1347 | 56.4853 | 57.1198 | 57.9077 | 57.8511 | 57.8511 | 57.8511 | 57.8511 | 57.8511 | 57.8511 | 57.8511 | 57.8511 | 57.8511 | 57.8511 | 57.8511 | 57.8511 | 57.8511 | 57.8511 | 57.8511 | 57.8511 | 70% | 76.3892 | 44.0307 | 56.9609 | 60.3421 | 57.3376 | 57.3499 | 57.6953 | 58.6099 | 59.2205 | 59.8193 | 60.5198 | 61.1678 | 61.7979 | 61.8681 | 62.6038 | 62.0427 | 62.0427 | 62.0427 | 62.0427 | 62.0427 | 62.0427 | 62.0427 | 62.0427 | 62.0427 | 62.0427 | 62.0427 | 62.0427 | 62.0427 | 62.0427 | 62.0427 | 62.0427
65% | 359.6342 | 36.6914 | 48.674 | 51.9337 | 49.2374 | 49.2319 | 49.6024 | 50.009 | 50.8445 | 51.445 | 51.7701 | 52.1251 | 52.4506 | 53.0398 | 53.7714 | 53.7189 | 53.7189 | 53.7189 | 53.7189 | 53.7189 | 53.7189 | 53.7189 | 53.7189 | 53.7189 | 53.7189 | 53.7189 | 53.7189 | 53.7189 | 53.7189 | 53.7189 | 53.7189 | 65% | 114.2056 | 40.8856 | 52.8923 | 56.0319 | 53.2421 | 53.2534 | 53.5742 | 54.4235 | 54.9905 | 55.5465 | 56.197 | 56.7987 | 57.3837 | 57.449 | 58.1321 | 57.6111 | 57.6111 | 57.6111 | 57.6111 | 57.6111 | 57.6111 | 57.6111 | 57.6111 | 57.6111 | 57.6111 | 57.6111 | 57.6111 | 57.6111 | 57.6111 | 57.6111 | 57.6111
60% | 689.7717 | 33.869 | 44.9299 | 47.9388 | 45.4499 | 45.4449 | 45.7868 | 46.1621 | 46.9334 | 47.4876 | 47.7878 | 48.1155 | 48.4159 | 48.9598 | 49.6352 | 49.5867 | 49.5867 | 49.5867 | 49.5867 | 49.5867 | 49.5867 | 49.5867 | 49.5867 | 49.5867 | 49.5867 | 49.5867 | 49.5867 | 49.5867 | 49.5867 | 49.5867 | 49.5867 | 60% | 178.1154 | 37.7406 | 48.8237 | 51.7218 | 49.1465 | 49.157 | 49.4531 | 50.2371 | 50.7605 | 51.2736 | 51.8741 | 52.4296 | 52.9696 | 53.0298 | 53.6604 | 53.1795 | 53.1795 | 53.1795 | 53.1795 | 53.1795 | 53.1795 | 53.1795 | 53.1795 | 53.1795 | 53.1795 | 53.1795 | 53.1795 | 53.1795 | 53.1795 | 53.1795 | 53.1795
55% | 1095.5419 | 31.0466 | 41.1857 | 43.9439 | 41.6624 | 41.6578 | 41.9712 | 42.3153 | 43.0222 | 43.5303 | 43.8055 | 44.1059 | 44.3813 | 44.8798 | 45.4989 | 45.4545 | 45.4545 | 45.4545 | 45.4545 | 45.4545 | 45.4545 | 45.4545 | 45.4545 | 45.4545 | 45.4545 | 45.4545 | 45.4545 | 45.4545 | 45.4545 | 45.4545 | 45.4545 | 55% | 311.6074 | 34.5955 | 44.755 | 47.4116 | 45.051 | 45.0606 | 45.332 | 46.0506 | 46.5304 | 47.0008 | 47.5513 | 48.0604 | 48.5555 | 48.6107 | 49.1887 | 48.7479 | 48.7479 | 48.7479 | 48.7479 | 48.7479 | 48.7479 | 48.7479 | 48.7479 | 48.7479 | 48.7479 | 48.7479 | 48.7479 | 48.7479 | 48.7479 | 48.7479 | 48.7479
50% | 1666.1918 | 28.2242 | 37.4415 | 39.949 | 37.8749 | 37.8707 | 38.1557 | 38.4684 | 39.1111 | 39.573 | 39.8231 | 40.0962 | 40.3466 | 40.7999 | 41.3626 | 41.3222 | 41.3222 | 41.3222 | 41.3222 | 41.3222 | 41.3222 | 41.3222 | 41.3222 | 41.3222 | 41.3222 | 41.3222 | 41.3222 | 41.3222 | 41.3222 | 41.3222 | 41.3222 | 50% | 636.0723 | 31.4505 | 40.6864 | 43.1015 | 40.9554 | 40.9642 | 41.211 | 41.8642 | 42.3004 | 42.728 | 43.2284 | 43.6913 | 44.1413 | 44.1915 | 44.717 | 44.3162 | 44.3162 | 44.3162 | 44.3162 | 44.3162 | 44.3162 | 44.3162 | 44.3162 | 44.3162 | 44.3162 | 44.3162 | 44.3162 | 44.3162 | 44.3162 | 44.3162 | 44.3162
45% | 2506.0947 | 25.4017 | 33.6974 | 35.9541 | 34.0874 | 34.0837 | 34.3401 | 34.6216 | 35.2 | 35.6157 | 35.8408 | 36.0866 | 36.312 | 36.7199 | 37.2264 | 37.19 | 37.19 | 37.19 | 37.19 | 37.19 | 37.19 | 37.19 | 37.19 | 37.19 | 37.19 | 37.19 | 37.19 | 37.19 | 37.19 | 37.19 | 37.19 | 45% | 1179.4944 | 28.3054 | 36.6177 | 38.7913 | 36.8599 | 36.8678 | 37.0899 | 37.6778 | 38.0703 | 38.4552 | 38.9056 | 39.3222 | 39.7272 | 39.7724 | 40.2453 | 39.8846 | 39.8846 | 39.8846 | 39.8846 | 39.8846 | 39.8846 | 39.8846 | 39.8846 | 39.8846 | 39.8846 | 39.8846 | 39.8846 | 39.8846 | 39.8846 | 39.8846 | 39.8846
40% | 3164.4787 | 22.5793 | 29.9532 | 31.9592 | 30.2999 | 30.2966 | 30.5245 | 30.7748 | 31.2889 | 31.6584 | 31.8585 | 32.077 | 32.2773 | 32.6399 | 33.0901 | 33.0578 | 33.0578 | 33.0578 | 33.0578 | 33.0578 | 33.0578 | 33.0578 | 33.0578 | 33.0578 | 33.0578 | 33.0578 | 33.0578 | 33.0578 | 33.0578 | 33.0578 | 33.0578 | 40% | 1808.3816 | 25.1604 | 32.5491 | 34.4812 | 32.7644 | 32.7713 | 32.9688 | 33.4914 | 33.8403 | 34.1824 | 34.5827 | 34.953 | 35.3131 | 35.3532 | 35.7736 | 35.453 | 35.453 | 35.453 | 35.453 | 35.453 | 35.453 | 35.453 | 35.453 | 35.453 | 35.453 | 35.453 | 35.453 | 35.453 | 35.453 | 35.453 | 35.453
35% | 3551.3408 | 19.7569 | 26.2091 | 27.9643 | 26.5124 | 26.5095 | 26.709 | 26.9279 | 27.3778 | 27.7011 | 27.8762 | 28.0674 | 28.2426 | 28.5599 | 28.9538 | 28.9256 | 28.9256 | 28.9256 | 28.9256 | 28.9256 | 28.9256 | 28.9256 | 28.9256 | 28.9256 | 28.9256 | 28.9256 | 28.9256 | 28.9256 | 28.9256 | 28.9256 | 28.9256 | 35% | 2779.1293 | 22.0153 | 28.4805 | 30.171 | 28.6688 | 28.6749 | 28.8477 | 29.305 | 29.6103 | 29.9096 | 30.2599 | 30.5839 | 30.8989 | 30.9341 | 31.3019 | 31.0214 | 31.0214 | 31.0214 | 31.0214 | 31.0214 | 31.0214 | 31.0214 | 31.0214 | 31.0214 | 31.0214 | 31.0214 | 31.0214 | 31.0214 | 31.0214 | 31.0214 | 31.0214
30% | 3758.953 | 16.9345 | 22.4649 | 23.9694 | 22.7249 | 22.7224 | 22.8934 | 23.0811 | 23.4667 | 23.7438 | 23.8939 | 24.0577 | 24.208 | 24.4799 | 24.8176 | 24.7933 | 24.7933 | 24.7933 | 24.7933 | 24.7933 | 24.7933 | 24.7933 | 24.7933 | 24.7933 | 24.7933 | 24.7933 | 24.7933 | 24.7933 | 24.7933 | 24.7933 | 24.7933 | 30% | 3814.165 | 18.8703 | 24.4118 | 25.8609 | 24.5733 | 24.5785 | 24.7266 | 25.1185 | 25.3802 | 25.6368 | 25.9371 | 26.2148 | 26.4848 | 26.5149 | 26.8302 | 26.5897 | 26.5897 | 26.5897 | 26.5897 | 26.5897 | 26.5897 | 26.5897 | 26.5897 | 26.5897 | 26.5897 | 26.5897 | 26.5897 | 26.5897 | 26.5897 | 26.5897 | 26.5897
25% | 3926.4798 | 14.1121 | 18.7208 | 19.9745 | 18.9375 | 18.9354 | 19.0778 | 19.2342 | 19.5556 | 19.7865 | 19.9116 | 20.0481 | 20.1733 | 20.3999 | 20.6813 | 20.6611 | 20.6611 | 20.6611 | 20.6611 | 20.6611 | 20.6611 | 20.6611 | 20.6611 | 20.6611 | 20.6611 | 20.6611 | 20.6611 | 20.6611 | 20.6611 | 20.6611 | 20.6611 | 25% | 4166.9923 | 15.7252 | 20.3432 | 21.5507 | 20.4777 | 20.4821 | 20.6055 | 20.9321 | 21.1502 | 21.364 | 21.6142 | 21.8457 | 22.0707 | 22.0958 | 22.3585 | 22.1581 | 22.1581 | 22.1581 | 22.1581 | 22.1581 | 22.1581 | 22.1581 | 22.1581 | 22.1581 | 22.1581 | 22.1581 | 22.1581 | 22.1581 | 22.1581 | 22.1581 | 22.1581
20% | 4050.5177 | 11.2897 | 14.9766 | 15.9796 | 15.15 | 15.1483 | 15.2623 | 15.3874 | 15.6445 | 15.8292 | 15.9293 | 16.0385 | 16.1386 | 16.3199 | 16.5451 | 16.5289 | 16.5289 | 16.5289 | 16.5289 | 16.5289 | 16.5289 | 16.5289 | 16.5289 | 16.5289 | 16.5289 | 16.5289 | 16.5289 | 16.5289 | 16.5289 | 16.5289 | 16.5289 | 20% | 4282.7105 | 12.5802 | 16.2746 | 17.2406 | 16.3822 | 16.3857 | 16.4844 | 16.7457 | 16.9202 | 17.0912 | 17.2914 | 17.4765 | 17.6565 | 17.6766 | 17.8868 | 17.7265 | 17.7265 | 17.7265 | 17.7265 | 17.7265 | 17.7265 | 17.7265 | 17.7265 | 17.7265 | 17.7265 | 17.7265 | 17.7265 | 17.7265 | 17.7265 | 17.7265 | 17.7265
15% | 4152.622 | 8.4672 | 11.2325 | 11.9847 | 11.3625 | 11.3612 | 11.4467 | 11.5405 | 11.7333 | 11.8719 | 11.9469 | 12.0289 | 12.104 | 12.24 | 12.4088 | 12.3967 | 12.3967 | 12.3967 | 12.3967 | 12.3967 | 12.3967 | 12.3967 | 12.3967 | 12.3967 | 12.3967 | 12.3967 | 12.3967 | 12.3967 | 12.3967 | 12.3967 | 12.3967 | 15% | 4364.7722 | 9.4351 | 12.2059 | 12.9304 | 12.2866 | 12.2893 | 12.3633 | 12.5593 | 12.6901 | 12.8184 | 12.9685 | 13.1074 | 13.2424 | 13.2575 | 13.4151 | 13.2949 | 13.2949 | 13.2949 | 13.2949 | 13.2949 | 13.2949 | 13.2949 | 13.2949 | 13.2949 | 13.2949 | 13.2949 | 13.2949 | 13.2949 | 13.2949 | 13.2949 | 13.2949
10% | 4248.2976 | 5.6448 | 7.4883 | 7.9898 | 7.575 | 7.5741 | 7.6311 | 7.6937 | 7.8222 | 7.9146 | 7.9646 | 8.0192 | 8.0693 | 8.16 | 8.2725 | 8.2644 | 8.2644 | 8.2644 | 8.2644 | 8.2644 | 8.2644 | 8.2644 | 8.2644 | 8.2644 | 8.2644 | 8.2644 | 8.2644 | 8.2644 | 8.2644 | 8.2644 | 8.2644 | 10% | 4391.6218 | 6.2901 | 8.1373 | 8.6203 | 8.1911 | 8.1928 | 8.2422 | 8.3728 | 8.4601 | 8.5456 | 8.6457 | 8.7383 | 8.8283 | 8.8383 | 8.9434 | 8.8632 | 8.8632 | 8.8632 | 8.8632 | 8.8632 | 8.8632 | 8.8632 | 8.8632 | 8.8632 | 8.8632 | 8.8632 | 8.8632 | 8.8632 | 8.8632 | 8.8632 | 8.8632
5% | 4361.7469 | 2.8224 | 3.7442 | 3.9949 | 3.7875 | 3.7871 | 3.8156 | 3.8468 | 3.9111 | 3.9573 | 3.9823 | 4.0096 | 4.0347 | 4.08 | 4.1363 | 4.1322 | 4.1322 | 4.1322 | 4.1322 | 4.1322 | 4.1322 | 4.1322 | 4.1322 | 4.1322 | 4.1322 | 4.1322 | 4.1322 | 4.1322 | 4.1322 | 4.1322 | 4.1322 | 5% | 4391.6218 | 3.145 | 4.0686 | 4.3101 | 4.0955 | 4.0964 | 4.1211 | 4.1864 | 4.23 | 4.2728 | 4.3228 | 4.3691 | 4.4141 | 4.4192 | 4.4717 | 4.4316 | 4.4316 | 4.4316 | 4.4316 | 4.4316 | 4.4316 | 4.4316 | 4.4316 | 4.4316 | 4.4316 | 4.4316 | 4.4316 | 4.4316 | 4.4316 | 4.4316 | 4.4316
9.992e-14% | 4391.6218 | 5.6403e-14 | 7.4823e-14 | 7.9834e-14 | 7.5689e-14 | 7.5681e-14 | 7.625e-14 | 7.6875e-14 | 7.816e-14 | 7.9083e-14 | 7.9583e-14 | 8.0128e-14 | 8.0629e-14 | 8.1534e-14 | 8.2659e-14 | 8.2578e-14 | 8.2578e-14 | 8.2578e-14 | 8.2578e-14 | 8.2578e-14 | 8.2578e-14 | 8.2578e-14 | 8.2578e-14 | 8.2578e-14 | 8.2578e-14 | 8.2578e-14 | 8.2578e-14 | 8.2578e-14 | 8.2578e-14 | 8.2578e-14 | 8.2578e-14 | 9.992e-14% | 4391.6218 | 6.2851e-14 | 8.1308e-14 | 8.6134e-14 | 8.1845e-14 | 8.1863e-14 | 8.2356e-14 | 8.3662e-14 | 8.4533e-14 | 8.5388e-14 | 8.6388e-14 | 8.7313e-14 | 8.8212e-14 | 8.8312e-14 | 8.9362e-14 | 8.8562e-14 | 8.8562e-14 | 8.8562e-14 | 8.8562e-14 | 8.8562e-14 | 8.8562e-14 | 8.8562e-14 | 8.8562e-14 | 8.8562e-14 | 8.8562e-14 | 8.8562e-14 | 8.8562e-14 | 8.8562e-14 | 8.8562e-14 | 8.8562e-14 | 8.8562e-14
Option 5
Winter Season | [31 empty] | Winter Season
P50 | [31 empty] | P10
% of MD | Winter - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Winter - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 49.7042 | 68.8514 | 73.8223 | 52.9163 | 53.5714 | 54.7063 | 57.2941 | 59.0226 | 61.2164 | 62.3529 | 63.3501 | 61.4961 | 63.6592 | 67.0625 | 64.4721 | 64.4721 | 64.4721 | 64.4721 | 64.4721 | 64.4721 | 64.4721 | 64.4721 | 64.4721 | 64.4721 | 64.4721 | 64.4721 | 64.4721 | 64.4721 | 64.4721 | 64.4721 | 100% | 0 | 53.1876 | 72.0932 | 77.2584 | 56.3042 | 56.8057 | 57.9159 | 60.5442 | 61.9749 | 64.7087 | 73.0277 | 66.1592 | 64.8126 | 66.6199 | 70.5778 | 67.8913 | 67.8913 | 67.8913 | 67.8913 | 67.8913 | 67.8913 | 67.8913 | 67.8913 | 67.8913 | 67.8913 | 67.8913 | 67.8913 | 67.8913 | 67.8913 | 67.8913 | 67.8913
99% | 1.486 | 49.2072 | 68.1629 | 73.0841 | 52.3872 | 53.0357 | 54.1593 | 56.7212 | 58.4324 | 60.6042 | 61.7294 | 62.7166 | 60.8811 | 63.0226 | 66.3918 | 63.8273 | 63.8273 | 63.8273 | 63.8273 | 63.8273 | 63.8273 | 63.8273 | 63.8273 | 63.8273 | 63.8273 | 63.8273 | 63.8273 | 63.8273 | 63.8273 | 63.8273 | 63.8273 | 99% | 1.486 | 52.6557 | 71.3723 | 76.4858 | 55.7412 | 56.2376 | 57.3367 | 59.9387 | 61.3552 | 64.0616 | 72.2975 | 65.4976 | 64.1645 | 65.9537 | 69.872 | 67.2124 | 67.2124 | 67.2124 | 67.2124 | 67.2124 | 67.2124 | 67.2124 | 67.2124 | 67.2124 | 67.2124 | 67.2124 | 67.2124 | 67.2124 | 67.2124 | 67.2124 | 67.2124
98% | 3.2692 | 48.7101 | 67.4743 | 72.3458 | 51.858 | 52.5 | 53.6122 | 56.1482 | 57.8422 | 59.9921 | 61.1059 | 62.0831 | 60.2662 | 62.386 | 65.7212 | 63.1826 | 63.1826 | 63.1826 | 63.1826 | 63.1826 | 63.1826 | 63.1826 | 63.1826 | 63.1826 | 63.1826 | 63.1826 | 63.1826 | 63.1826 | 63.1826 | 63.1826 | 63.1826 | 98% | 3.2692 | 52.1238 | 70.6514 | 75.7133 | 55.1781 | 55.6696 | 56.7576 | 59.3333 | 60.7354 | 63.4145 | 71.5672 | 64.836 | 63.5163 | 65.2875 | 69.1662 | 66.5335 | 66.5335 | 66.5335 | 66.5335 | 66.5335 | 66.5335 | 66.5335 | 66.5335 | 66.5335 | 66.5335 | 66.5335 | 66.5335 | 66.5335 | 66.5335 | 66.5335 | 66.5335
97% | 6.8356 | 48.2131 | 66.7858 | 71.6076 | 51.3288 | 51.9643 | 53.0652 | 55.5753 | 57.252 | 59.3799 | 60.4823 | 61.4496 | 59.6512 | 61.7495 | 65.0506 | 62.5379 | 62.5379 | 62.5379 | 62.5379 | 62.5379 | 62.5379 | 62.5379 | 62.5379 | 62.5379 | 62.5379 | 62.5379 | 62.5379 | 62.5379 | 62.5379 | 62.5379 | 62.5379 | 97% | 6.8356 | 51.5919 | 69.9304 | 74.9407 | 54.6151 | 55.1015 | 56.1784 | 58.7279 | 60.1157 | 62.7675 | 70.8369 | 64.1744 | 62.8682 | 64.6213 | 68.4605 | 65.8546 | 65.8546 | 65.8546 | 65.8546 | 65.8546 | 65.8546 | 65.8546 | 65.8546 | 65.8546 | 65.8546 | 65.8546 | 65.8546 | 65.8546 | 65.8546 | 65.8546 | 65.8546
95% | 17.5347 | 47.219 | 65.4088 | 70.1312 | 50.2705 | 50.8928 | 51.971 | 54.4294 | 56.0715 | 58.1556 | 59.2353 | 60.1826 | 58.4213 | 60.4763 | 63.7093 | 61.2485 | 61.2485 | 61.2485 | 61.2485 | 61.2485 | 61.2485 | 61.2485 | 61.2485 | 61.2485 | 61.2485 | 61.2485 | 61.2485 | 61.2485 | 61.2485 | 61.2485 | 61.2485 | 95% | 17.5347 | 50.5282 | 68.4886 | 73.3955 | 53.489 | 53.9654 | 55.0201 | 57.517 | 58.8762 | 61.4733 | 69.3764 | 62.8513 | 61.572 | 63.2889 | 67.0489 | 64.4967 | 64.4967 | 64.4967 | 64.4967 | 64.4967 | 64.4967 | 64.4967 | 64.4967 | 64.4967 | 64.4967 | 64.4967 | 64.4967 | 64.4967 | 64.4967 | 64.4967 | 64.4967
90% | 78.7576 | 44.7338 | 61.9662 | 66.4401 | 47.6247 | 48.2143 | 49.2357 | 51.5647 | 53.1204 | 55.0947 | 56.1176 | 57.0151 | 55.3465 | 57.2933 | 60.3562 | 58.0249 | 58.0249 | 58.0249 | 58.0249 | 58.0249 | 58.0249 | 58.0249 | 58.0249 | 58.0249 | 58.0249 | 58.0249 | 58.0249 | 58.0249 | 58.0249 | 58.0249 | 58.0249 | 90% | 78.7576 | 47.8688 | 64.8839 | 69.5326 | 50.6738 | 51.1251 | 52.1243 | 54.4898 | 55.7774 | 58.2378 | 65.725 | 59.5433 | 58.3313 | 59.9579 | 63.52 | 61.1022 | 61.1022 | 61.1022 | 61.1022 | 61.1022 | 61.1022 | 61.1022 | 61.1022 | 61.1022 | 61.1022 | 61.1022 | 61.1022 | 61.1022 | 61.1022 | 61.1022 | 61.1022
85% | 236.8672 | 42.2486 | 58.5237 | 62.7489 | 44.9789 | 45.5357 | 46.5004 | 48.7 | 50.1692 | 52.0339 | 53 | 53.8476 | 52.2717 | 54.1103 | 57.0031 | 54.8013 | 54.8013 | 54.8013 | 54.8013 | 54.8013 | 54.8013 | 54.8013 | 54.8013 | 54.8013 | 54.8013 | 54.8013 | 54.8013 | 54.8013 | 54.8013 | 54.8013 | 54.8013 | 85% | 236.8672 | 45.2094 | 61.2792 | 65.6697 | 47.8586 | 48.2848 | 49.2285 | 51.4626 | 52.6787 | 55.0024 | 62.0736 | 56.2353 | 55.0907 | 56.6269 | 59.9911 | 57.7076 | 57.7076 | 57.7076 | 57.7076 | 57.7076 | 57.7076 | 57.7076 | 57.7076 | 57.7076 | 57.7076 | 57.7076 | 57.7076 | 57.7076 | 57.7076 | 57.7076 | 57.7076
80% | 497.5104 | 39.7634 | 55.0811 | 59.0578 | 42.3331 | 42.8571 | 43.7651 | 45.8353 | 47.2181 | 48.9731 | 49.8823 | 50.68 | 49.1969 | 50.9274 | 53.65 | 51.5777 | 51.5777 | 51.5777 | 51.5777 | 51.5777 | 51.5777 | 51.5777 | 51.5777 | 51.5777 | 51.5777 | 51.5777 | 51.5777 | 51.5777 | 51.5777 | 51.5777 | 51.5777 | 80% | 497.5104 | 42.55 | 57.6746 | 61.8067 | 45.0434 | 45.4445 | 46.3327 | 48.4353 | 49.5799 | 51.767 | 58.4222 | 52.9274 | 51.8501 | 53.2959 | 56.4622 | 54.3131 | 54.3131 | 54.3131 | 54.3131 | 54.3131 | 54.3131 | 54.3131 | 54.3131 | 54.3131 | 54.3131 | 54.3131 | 54.3131 | 54.3131 | 54.3131 | 54.3131 | 54.3131
75% | 803.6248 | 37.2782 | 51.6385 | 55.3667 | 39.6872 | 40.1786 | 41.0298 | 42.9706 | 44.267 | 45.9123 | 46.7647 | 47.5125 | 46.1221 | 47.7444 | 50.2968 | 48.354 | 48.354 | 48.354 | 48.354 | 48.354 | 48.354 | 48.354 | 48.354 | 48.354 | 48.354 | 48.354 | 48.354 | 48.354 | 48.354 | 48.354 | 48.354 | 75% | 803.6248 | 39.8907 | 54.0699 | 57.9438 | 42.2282 | 42.6042 | 43.4369 | 45.4081 | 46.4812 | 48.5315 | 54.7708 | 49.6194 | 48.6094 | 49.9649 | 52.9333 | 50.9185 | 50.9185 | 50.9185 | 50.9185 | 50.9185 | 50.9185 | 50.9185 | 50.9185 | 50.9185 | 50.9185 | 50.9185 | 50.9185 | 50.9185 | 50.9185 | 50.9185 | 50.9185
70% | 1155.2107 | 34.793 | 48.196 | 51.6756 | 37.0414 | 37.5 | 38.2944 | 40.1059 | 41.3158 | 42.8515 | 43.6471 | 44.345 | 43.0473 | 44.5615 | 46.9437 | 45.1304 | 45.1304 | 45.1304 | 45.1304 | 45.1304 | 45.1304 | 45.1304 | 45.1304 | 45.1304 | 45.1304 | 45.1304 | 45.1304 | 45.1304 | 45.1304 | 45.1304 | 45.1304 | 70% | 1155.2107 | 37.2313 | 50.4653 | 54.0809 | 39.413 | 39.764 | 40.5411 | 42.3809 | 43.3824 | 45.2961 | 51.1194 | 46.3115 | 45.3688 | 46.6339 | 49.4045 | 47.5239 | 47.5239 | 47.5239 | 47.5239 | 47.5239 | 47.5239 | 47.5239 | 47.5239 | 47.5239 | 47.5239 | 47.5239 | 47.5239 | 47.5239 | 47.5239 | 47.5239 | 47.5239
65% | 1553.1596 | 32.3077 | 44.7534 | 47.9845 | 34.3956 | 34.8214 | 35.5591 | 37.2412 | 38.3647 | 39.7907 | 40.5294 | 41.1775 | 39.9725 | 41.3785 | 43.5906 | 41.9068 | 41.9068 | 41.9068 | 41.9068 | 41.9068 | 41.9068 | 41.9068 | 41.9068 | 41.9068 | 41.9068 | 41.9068 | 41.9068 | 41.9068 | 41.9068 | 41.9068 | 41.9068 | 65% | 1553.1596 | 34.5719 | 46.8606 | 50.218 | 36.5977 | 36.9237 | 37.6453 | 39.3537 | 40.2837 | 42.0607 | 47.468 | 43.0035 | 42.1282 | 43.303 | 45.8756 | 44.1294 | 44.1294 | 44.1294 | 44.1294 | 44.1294 | 44.1294 | 44.1294 | 44.1294 | 44.1294 | 44.1294 | 44.1294 | 44.1294 | 44.1294 | 44.1294 | 44.1294 | 44.1294
60% | 2026.2996 | 29.8225 | 41.3108 | 44.2934 | 31.7498 | 32.1428 | 32.8238 | 34.3765 | 35.4136 | 36.7298 | 37.4118 | 38.01 | 36.8977 | 38.1955 | 40.2375 | 38.6832 | 38.6832 | 38.6832 | 38.6832 | 38.6832 | 38.6832 | 38.6832 | 38.6832 | 38.6832 | 38.6832 | 38.6832 | 38.6832 | 38.6832 | 38.6832 | 38.6832 | 38.6832 | 60% | 2026.2996 | 31.9125 | 43.2559 | 46.3551 | 33.7825 | 34.0834 | 34.7495 | 36.3265 | 37.185 | 38.8252 | 43.8166 | 39.6955 | 38.8876 | 39.972 | 42.3467 | 40.7348 | 40.7348 | 40.7348 | 40.7348 | 40.7348 | 40.7348 | 40.7348 | 40.7348 | 40.7348 | 40.7348 | 40.7348 | 40.7348 | 40.7348 | 40.7348 | 40.7348 | 40.7348
55% | 2598.4068 | 27.3373 | 37.8683 | 40.6023 | 29.104 | 29.4643 | 30.0885 | 31.5118 | 32.4625 | 33.669 | 34.2941 | 34.8425 | 33.8229 | 35.0126 | 36.8844 | 35.4596 | 35.4596 | 35.4596 | 35.4596 | 35.4596 | 35.4596 | 35.4596 | 35.4596 | 35.4596 | 35.4596 | 35.4596 | 35.4596 | 35.4596 | 35.4596 | 35.4596 | 35.4596 | 55% | 2598.4068 | 29.2532 | 39.6513 | 42.4921 | 30.9673 | 31.2431 | 31.8537 | 33.2993 | 34.0862 | 35.5898 | 40.1653 | 36.3876 | 35.6469 | 36.641 | 38.8178 | 37.3402 | 37.3402 | 37.3402 | 37.3402 | 37.3402 | 37.3402 | 37.3402 | 37.3402 | 37.3402 | 37.3402 | 37.3402 | 37.3402 | 37.3402 | 37.3402 | 37.3402 | 37.3402
50% | 3233.5201 | 24.8521 | 34.4257 | 36.9111 | 26.4582 | 26.7857 | 27.3532 | 28.6471 | 29.5113 | 30.6082 | 31.1765 | 31.675 | 30.748 | 31.8296 | 33.5312 | 32.236 | 32.236 | 32.236 | 32.236 | 32.236 | 32.236 | 32.236 | 32.236 | 32.236 | 32.236 | 32.236 | 32.236 | 32.236 | 32.236 | 32.236 | 32.236 | 50% | 3233.5201 | 26.5938 | 36.0466 | 38.6292 | 28.1521 | 28.4028 | 28.958 | 30.2721 | 30.9875 | 32.3544 | 36.5139 | 33.0796 | 32.4063 | 33.31 | 35.2889 | 33.9457 | 33.9457 | 33.9457 | 33.9457 | 33.9457 | 33.9457 | 33.9457 | 33.9457 | 33.9457 | 33.9457 | 33.9457 | 33.9457 | 33.9457 | 33.9457 | 33.9457 | 33.9457
45% | 3775.313 | 22.3669 | 30.9831 | 33.22 | 23.8123 | 24.1071 | 24.6179 | 25.7824 | 26.5602 | 27.5474 | 28.0588 | 28.5075 | 27.6732 | 28.6467 | 30.1781 | 29.0124 | 29.0124 | 29.0124 | 29.0124 | 29.0124 | 29.0124 | 29.0124 | 29.0124 | 29.0124 | 29.0124 | 29.0124 | 29.0124 | 29.0124 | 29.0124 | 29.0124 | 29.0124 | 45% | 3775.313 | 23.9344 | 32.442 | 34.7663 | 25.3369 | 25.5625 | 26.0622 | 27.2449 | 27.8887 | 29.1189 | 32.8625 | 29.7716 | 29.1657 | 29.979 | 31.76 | 30.5511 | 30.5511 | 30.5511 | 30.5511 | 30.5511 | 30.5511 | 30.5511 | 30.5511 | 30.5511 | 30.5511 | 30.5511 | 30.5511 | 30.5511 | 30.5511 | 30.5511 | 30.5511
40% | 4072.8088 | 19.8817 | 27.5405 | 29.5289 | 21.1665 | 21.4286 | 21.8825 | 22.9176 | 23.6091 | 24.4866 | 24.9412 | 25.34 | 24.5984 | 25.4637 | 26.825 | 25.7888 | 25.7888 | 25.7888 | 25.7888 | 25.7888 | 25.7888 | 25.7888 | 25.7888 | 25.7888 | 25.7888 | 25.7888 | 25.7888 | 25.7888 | 25.7888 | 25.7888 | 25.7888 | 40% | 4072.8088 | 21.275 | 28.8373 | 30.9034 | 22.5217 | 22.7223 | 23.1664 | 24.2177 | 24.79 | 25.8835 | 29.2111 | 26.4637 | 25.925 | 26.648 | 28.2311 | 27.1565 | 27.1565 | 27.1565 | 27.1565 | 27.1565 | 27.1565 | 27.1565 | 27.1565 | 27.1565 | 27.1565 | 27.1565 | 27.1565 | 27.1565 | 27.1565 | 27.1565 | 27.1565
35% | 4198.821 | 17.3965 | 24.098 | 25.8378 | 18.5207 | 18.75 | 19.1472 | 20.0529 | 20.6579 | 21.4257 | 21.8235 | 22.1725 | 21.5236 | 22.2807 | 23.4719 | 22.5652 | 22.5652 | 22.5652 | 22.5652 | 22.5652 | 22.5652 | 22.5652 | 22.5652 | 22.5652 | 22.5652 | 22.5652 | 22.5652 | 22.5652 | 22.5652 | 22.5652 | 22.5652 | 35% | 4198.821 | 18.6156 | 25.2326 | 27.0405 | 19.7065 | 19.882 | 20.2706 | 21.1905 | 21.6912 | 22.6481 | 25.5597 | 23.1557 | 22.6844 | 23.317 | 24.7022 | 23.762 | 23.762 | 23.762 | 23.762 | 23.762 | 23.762 | 23.762 | 23.762 | 23.762 | 23.762 | 23.762 | 23.762 | 23.762 | 23.762 | 23.762 | 23.762
30% | 4271.3374 | 14.9113 | 20.6554 | 22.1467 | 15.8749 | 16.0714 | 16.4119 | 17.1882 | 17.7068 | 18.3649 | 18.7059 | 19.005 | 18.4488 | 19.0978 | 20.1187 | 19.3416 | 19.3416 | 19.3416 | 19.3416 | 19.3416 | 19.3416 | 19.3416 | 19.3416 | 19.3416 | 19.3416 | 19.3416 | 19.3416 | 19.3416 | 19.3416 | 19.3416 | 19.3416 | 30% | 4271.3374 | 15.9563 | 21.628 | 23.1775 | 16.8913 | 17.0417 | 17.3748 | 18.1633 | 18.5925 | 19.4126 | 21.9083 | 19.8478 | 19.4438 | 19.986 | 21.1733 | 20.3674 | 20.3674 | 20.3674 | 20.3674 | 20.3674 | 20.3674 | 20.3674 | 20.3674 | 20.3674 | 20.3674 | 20.3674 | 20.3674 | 20.3674 | 20.3674 | 20.3674 | 20.3674
25% | 4321.8611 | 12.4261 | 17.2128 | 18.4556 | 13.2291 | 13.3929 | 13.6766 | 14.3235 | 14.7557 | 15.3041 | 15.5882 | 15.8375 | 15.374 | 15.9148 | 16.7656 | 16.118 | 16.118 | 16.118 | 16.118 | 16.118 | 16.118 | 16.118 | 16.118 | 16.118 | 16.118 | 16.118 | 16.118 | 16.118 | 16.118 | 16.118 | 16.118 | 25% | 4321.8611 | 13.2969 | 18.0233 | 19.3146 | 14.0761 | 14.2014 | 14.479 | 15.136 | 15.4937 | 16.1772 | 18.2569 | 16.5398 | 16.2031 | 16.655 | 17.6444 | 16.9728 | 16.9728 | 16.9728 | 16.9728 | 16.9728 | 16.9728 | 16.9728 | 16.9728 | 16.9728 | 16.9728 | 16.9728 | 16.9728 | 16.9728 | 16.9728 | 16.9728 | 16.9728
20% | 4353.067 | 9.9408 | 13.7703 | 14.7645 | 10.5833 | 10.7143 | 10.9413 | 11.4588 | 11.8045 | 12.2433 | 12.4706 | 12.67 | 12.2992 | 12.7318 | 13.4125 | 12.8944 | 12.8944 | 12.8944 | 12.8944 | 12.8944 | 12.8944 | 12.8944 | 12.8944 | 12.8944 | 12.8944 | 12.8944 | 12.8944 | 12.8944 | 12.8944 | 12.8944 | 12.8944 | 20% | 4353.067 | 10.6375 | 14.4186 | 15.4517 | 11.2608 | 11.3611 | 11.5832 | 12.1088 | 12.395 | 12.9417 | 14.6055 | 13.2318 | 12.9625 | 13.324 | 14.1156 | 13.5783 | 13.5783 | 13.5783 | 13.5783 | 13.5783 | 13.5783 | 13.5783 | 13.5783 | 13.5783 | 13.5783 | 13.5783 | 13.5783 | 13.5783 | 13.5783 | 13.5783 | 13.5783
15% | 4369.4129 | 7.4556 | 10.3277 | 11.0733 | 7.9374 | 8.0357 | 8.206 | 8.5941 | 8.8534 | 9.1825 | 9.3529 | 9.5025 | 9.2244 | 9.5489 | 10.0594 | 9.6708 | 9.6708 | 9.6708 | 9.6708 | 9.6708 | 9.6708 | 9.6708 | 9.6708 | 9.6708 | 9.6708 | 9.6708 | 9.6708 | 9.6708 | 9.6708 | 9.6708 | 9.6708 | 15% | 4369.4129 | 7.9781 | 10.814 | 11.5888 | 8.4456 | 8.5208 | 8.6874 | 9.0816 | 9.2962 | 9.7063 | 10.9542 | 9.9239 | 9.7219 | 9.993 | 10.5867 | 10.1837 | 10.1837 | 10.1837 | 10.1837 | 10.1837 | 10.1837 | 10.1837 | 10.1837 | 10.1837 | 10.1837 | 10.1837 | 10.1837 | 10.1837 | 10.1837 | 10.1837 | 10.1837
10% | 4378.6261 | 4.9704 | 6.8851 | 7.3822 | 5.2916 | 5.3571 | 5.4706 | 5.7294 | 5.9023 | 6.1216 | 6.2353 | 6.335 | 6.1496 | 6.3659 | 6.7062 | 6.4472 | 6.4472 | 6.4472 | 6.4472 | 6.4472 | 6.4472 | 6.4472 | 6.4472 | 6.4472 | 6.4472 | 6.4472 | 6.4472 | 6.4472 | 6.4472 | 6.4472 | 6.4472 | 10% | 4378.6261 | 5.3188 | 7.2093 | 7.7258 | 5.6304 | 5.6806 | 5.7916 | 6.0544 | 6.1975 | 6.4709 | 7.3028 | 6.6159 | 6.4813 | 6.662 | 7.0578 | 6.7891 | 6.7891 | 6.7891 | 6.7891 | 6.7891 | 6.7891 | 6.7891 | 6.7891 | 6.7891 | 6.7891 | 6.7891 | 6.7891 | 6.7891 | 6.7891 | 6.7891 | 6.7891
5% | 4391.7028 | 2.4852 | 3.4426 | 3.6911 | 2.6458 | 2.6786 | 2.7353 | 2.8647 | 2.9511 | 3.0608 | 3.1176 | 3.1675 | 3.0748 | 3.183 | 3.3531 | 3.2236 | 3.2236 | 3.2236 | 3.2236 | 3.2236 | 3.2236 | 3.2236 | 3.2236 | 3.2236 | 3.2236 | 3.2236 | 3.2236 | 3.2236 | 3.2236 | 3.2236 | 3.2236 | 5% | 4391.7028 | 2.6594 | 3.6047 | 3.8629 | 2.8152 | 2.8403 | 2.8958 | 3.0272 | 3.0987 | 3.2354 | 3.6514 | 3.308 | 3.2406 | 3.331 | 3.5289 | 3.3946 | 3.3946 | 3.3946 | 3.3946 | 3.3946 | 3.3946 | 3.3946 | 3.3946 | 3.3946 | 3.3946 | 3.3946 | 3.3946 | 3.3946 | 3.3946 | 3.3946 | 3.3946
9.992e-14% | 4391.7028 | 4.9664e-14 | 6.8796e-14 | 7.3763e-14 | 5.2874e-14 | 5.3529e-14 | 5.4663e-14 | 5.7248e-14 | 5.8975e-14 | 6.1167e-14 | 6.2303e-14 | 6.3299e-14 | 6.1447e-14 | 6.3608e-14 | 6.7009e-14 | 6.4421e-14 | 6.4421e-14 | 6.4421e-14 | 6.4421e-14 | 6.4421e-14 | 6.4421e-14 | 6.4421e-14 | 6.4421e-14 | 6.4421e-14 | 6.4421e-14 | 6.4421e-14 | 6.4421e-14 | 6.4421e-14 | 6.4421e-14 | 6.4421e-14 | 6.4421e-14 | 9.992e-14% | 4391.7028 | 5.3145e-14 | 7.2036e-14 | 7.7197e-14 | 5.6259e-14 | 5.676e-14 | 5.787e-14 | 6.0496e-14 | 6.1925e-14 | 6.4657e-14 | 7.2969e-14 | 6.6106e-14 | 6.4761e-14 | 6.6567e-14 | 7.0521e-14 | 6.7837e-14 | 6.7837e-14 | 6.7837e-14 | 6.7837e-14 | 6.7837e-14 | 6.7837e-14 | 6.7837e-14 | 6.7837e-14 | 6.7837e-14 | 6.7837e-14 | 6.7837e-14 | 6.7837e-14 | 6.7837e-14 | 6.7837e-14 | 6.7837e-14 | 6.7837e-14
Summer Season | [31 empty] | Summer Season
P50 | [31 empty] | P10
% of MD | Summer - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Summer - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 56.4483 | 74.8831 | 79.898 | 57.9998 | 57.9914 | 58.5613 | 59.1869 | 60.4723 | 61.3961 | 61.8963 | 62.4425 | 62.9432 | 63.8497 | 64.9753 | 64.8945 | 64.8945 | 64.8945 | 64.8945 | 64.8945 | 64.8945 | 64.8945 | 64.8945 | 64.8945 | 64.8945 | 64.8945 | 64.8945 | 64.8945 | 64.8945 | 64.8945 | 64.8945 | 100% | 0 | 62.901 | 81.3728 | 86.203 | 64.1609 | 64.1784 | 64.6719 | 65.9784 | 66.8508 | 67.7061 | 68.7069 | 69.6326 | 70.5327 | 70.633 | 71.684 | 70.8825 | 70.8825 | 70.8825 | 70.8825 | 70.8825 | 70.8825 | 70.8825 | 70.8825 | 70.8825 | 70.8825 | 70.8825 | 70.8825 | 70.8825 | 70.8825 | 70.8825 | 70.8825
99% | 0 | 55.8838 | 74.1343 | 79.099 | 57.4198 | 57.4115 | 57.9757 | 58.595 | 59.8675 | 60.7821 | 61.2773 | 61.8181 | 62.3138 | 63.2112 | 64.3255 | 64.2455 | 64.2455 | 64.2455 | 64.2455 | 64.2455 | 64.2455 | 64.2455 | 64.2455 | 64.2455 | 64.2455 | 64.2455 | 64.2455 | 64.2455 | 64.2455 | 64.2455 | 64.2455 | 99% | 1.5127 | 62.272 | 80.559 | 85.341 | 63.5193 | 63.5366 | 64.0252 | 65.3187 | 66.1823 | 67.029 | 68.0198 | 68.9363 | 69.8273 | 69.9267 | 70.9671 | 70.1736 | 70.1736 | 70.1736 | 70.1736 | 70.1736 | 70.1736 | 70.1736 | 70.1736 | 70.1736 | 70.1736 | 70.1736 | 70.1736 | 70.1736 | 70.1736 | 70.1736 | 70.1736
98% | 0 | 55.3193 | 73.3854 | 78.3 | 56.8398 | 56.8316 | 57.3901 | 58.0031 | 59.2628 | 60.1682 | 60.6584 | 61.1936 | 61.6844 | 62.5727 | 63.6758 | 63.5966 | 63.5966 | 63.5966 | 63.5966 | 63.5966 | 63.5966 | 63.5966 | 63.5966 | 63.5966 | 63.5966 | 63.5966 | 63.5966 | 63.5966 | 63.5966 | 63.5966 | 63.5966 | 98% | 2.269 | 61.643 | 79.7453 | 84.4789 | 62.8777 | 62.8948 | 63.3785 | 64.6589 | 65.5137 | 66.352 | 67.3327 | 68.24 | 69.122 | 69.2204 | 70.2503 | 69.4648 | 69.4648 | 69.4648 | 69.4648 | 69.4648 | 69.4648 | 69.4648 | 69.4648 | 69.4648 | 69.4648 | 69.4648 | 69.4648 | 69.4648 | 69.4648 | 69.4648 | 69.4648
97% | 0.37816 | 54.7549 | 72.6366 | 77.501 | 56.2598 | 56.2517 | 56.8045 | 57.4113 | 58.6581 | 59.5542 | 60.0394 | 60.5692 | 61.0549 | 61.9342 | 63.026 | 62.9476 | 62.9476 | 62.9476 | 62.9476 | 62.9476 | 62.9476 | 62.9476 | 62.9476 | 62.9476 | 62.9476 | 62.9476 | 62.9476 | 62.9476 | 62.9476 | 62.9476 | 62.9476 | 97% | 3.7816 | 61.014 | 78.9316 | 83.6169 | 62.2361 | 62.253 | 62.7317 | 63.9991 | 64.8452 | 65.6749 | 66.6457 | 67.5436 | 68.4167 | 68.514 | 69.5335 | 68.756 | 68.756 | 68.756 | 68.756 | 68.756 | 68.756 | 68.756 | 68.756 | 68.756 | 68.756 | 68.756 | 68.756 | 68.756 | 68.756 | 68.756 | 68.756
95% | 2.269 | 53.6259 | 71.1389 | 75.9031 | 55.0998 | 55.0919 | 55.6333 | 56.2275 | 57.4487 | 58.3263 | 58.8015 | 59.3204 | 59.7961 | 60.6572 | 61.7265 | 61.6497 | 61.6497 | 61.6497 | 61.6497 | 61.6497 | 61.6497 | 61.6497 | 61.6497 | 61.6497 | 61.6497 | 61.6497 | 61.6497 | 61.6497 | 61.6497 | 61.6497 | 61.6497 | 95% | 6.0506 | 59.7559 | 77.3041 | 81.8928 | 60.9528 | 60.9695 | 61.4383 | 62.6795 | 63.5082 | 64.3208 | 65.2715 | 66.151 | 67.006 | 67.1014 | 68.0998 | 67.3383 | 67.3383 | 67.3383 | 67.3383 | 67.3383 | 67.3383 | 67.3383 | 67.3383 | 67.3383 | 67.3383 | 67.3383 | 67.3383 | 67.3383 | 67.3383 | 67.3383 | 67.3383
90% | 5.6725 | 50.8035 | 67.3948 | 71.9082 | 52.1998 | 52.1923 | 52.7052 | 53.2682 | 54.425 | 55.2565 | 55.7067 | 56.1982 | 56.6489 | 57.4647 | 58.4777 | 58.405 | 58.405 | 58.405 | 58.405 | 58.405 | 58.405 | 58.405 | 58.405 | 58.405 | 58.405 | 58.405 | 58.405 | 58.405 | 58.405 | 58.405 | 58.405 | 90% | 16.2611 | 56.6109 | 73.2355 | 77.5827 | 57.7448 | 57.7605 | 58.2047 | 59.3806 | 60.1657 | 60.9355 | 61.8362 | 62.6694 | 63.4794 | 63.5697 | 64.5156 | 63.7942 | 63.7942 | 63.7942 | 63.7942 | 63.7942 | 63.7942 | 63.7942 | 63.7942 | 63.7942 | 63.7942 | 63.7942 | 63.7942 | 63.7942 | 63.7942 | 63.7942 | 63.7942
85% | 15.8829 | 47.9811 | 63.6506 | 67.9133 | 49.2999 | 49.2927 | 49.7771 | 50.3088 | 51.4014 | 52.1867 | 52.6119 | 53.0761 | 53.5018 | 54.2723 | 55.229 | 55.1603 | 55.1603 | 55.1603 | 55.1603 | 55.1603 | 55.1603 | 55.1603 | 55.1603 | 55.1603 | 55.1603 | 55.1603 | 55.1603 | 55.1603 | 55.1603 | 55.1603 | 55.1603 | 85% | 26.4715 | 53.4658 | 69.1669 | 73.2725 | 54.5368 | 54.5516 | 54.9711 | 56.0817 | 56.8231 | 57.5502 | 58.4008 | 59.1877 | 59.9528 | 60.0381 | 60.9314 | 60.2501 | 60.2501 | 60.2501 | 60.2501 | 60.2501 | 60.2501 | 60.2501 | 60.2501 | 60.2501 | 60.2501 | 60.2501 | 60.2501 | 60.2501 | 60.2501 | 60.2501 | 60.2501
80% | 31.0095 | 45.1586 | 59.9065 | 63.9184 | 46.3999 | 46.3932 | 46.8491 | 47.3495 | 48.3778 | 49.1169 | 49.517 | 49.954 | 50.3546 | 51.0798 | 51.9802 | 51.9156 | 51.9156 | 51.9156 | 51.9156 | 51.9156 | 51.9156 | 51.9156 | 51.9156 | 51.9156 | 51.9156 | 51.9156 | 51.9156 | 51.9156 | 51.9156 | 51.9156 | 51.9156 | 80% | 34.0348 | 50.3208 | 65.0982 | 68.9624 | 51.3287 | 51.3427 | 51.7375 | 52.7827 | 53.4806 | 54.1649 | 54.9655 | 55.7061 | 56.4261 | 56.5064 | 57.3472 | 56.706 | 56.706 | 56.706 | 56.706 | 56.706 | 56.706 | 56.706 | 56.706 | 56.706 | 56.706 | 56.706 | 56.706 | 56.706 | 56.706 | 56.706 | 56.706
75% | 72.9857 | 42.3362 | 56.1623 | 59.9235 | 43.4999 | 43.4936 | 43.921 | 44.3902 | 45.3542 | 46.0471 | 46.4222 | 46.8319 | 47.2074 | 47.8873 | 48.7315 | 48.6708 | 48.6708 | 48.6708 | 48.6708 | 48.6708 | 48.6708 | 48.6708 | 48.6708 | 48.6708 | 48.6708 | 48.6708 | 48.6708 | 48.6708 | 48.6708 | 48.6708 | 48.6708 | 75% | 48.405 | 47.1757 | 61.0296 | 64.6522 | 48.1207 | 48.1338 | 48.5039 | 49.4838 | 50.1381 | 50.7796 | 51.5302 | 52.2245 | 52.8995 | 52.9748 | 53.763 | 53.1619 | 53.1619 | 53.1619 | 53.1619 | 53.1619 | 53.1619 | 53.1619 | 53.1619 | 53.1619 | 53.1619 | 53.1619 | 53.1619 | 53.1619 | 53.1619 | 53.1619 | 53.1619
70% | 150.5094 | 39.5138 | 52.4182 | 55.9286 | 40.5999 | 40.594 | 40.9929 | 41.4308 | 42.3306 | 42.9773 | 43.3274 | 43.7097 | 44.0603 | 44.6948 | 45.4827 | 45.4261 | 45.4261 | 45.4261 | 45.4261 | 45.4261 | 45.4261 | 45.4261 | 45.4261 | 45.4261 | 45.4261 | 45.4261 | 45.4261 | 45.4261 | 45.4261 | 45.4261 | 45.4261 | 70% | 76.3892 | 44.0307 | 56.9609 | 60.3421 | 44.9126 | 44.9249 | 45.2703 | 46.1849 | 46.7955 | 47.3943 | 48.0948 | 48.7428 | 49.3729 | 49.4431 | 50.1788 | 49.6177 | 49.6177 | 49.6177 | 49.6177 | 49.6177 | 49.6177 | 49.6177 | 49.6177 | 49.6177 | 49.6177 | 49.6177 | 49.6177 | 49.6177 | 49.6177 | 49.6177 | 49.6177
65% | 359.6342 | 36.6914 | 48.674 | 51.9337 | 37.6999 | 37.6944 | 38.0649 | 38.4715 | 39.307 | 39.9075 | 40.2326 | 40.5876 | 40.9131 | 41.5023 | 42.2339 | 42.1814 | 42.1814 | 42.1814 | 42.1814 | 42.1814 | 42.1814 | 42.1814 | 42.1814 | 42.1814 | 42.1814 | 42.1814 | 42.1814 | 42.1814 | 42.1814 | 42.1814 | 42.1814 | 65% | 114.2056 | 40.8856 | 52.8923 | 56.0319 | 41.7046 | 41.7159 | 42.0367 | 42.886 | 43.453 | 44.009 | 44.6595 | 45.2612 | 45.8462 | 45.9115 | 46.5946 | 46.0736 | 46.0736 | 46.0736 | 46.0736 | 46.0736 | 46.0736 | 46.0736 | 46.0736 | 46.0736 | 46.0736 | 46.0736 | 46.0736 | 46.0736 | 46.0736 | 46.0736 | 46.0736
60% | 689.7717 | 33.869 | 44.9299 | 47.9388 | 34.7999 | 34.7949 | 35.1368 | 35.5121 | 36.2834 | 36.8376 | 37.1378 | 37.4655 | 37.7659 | 38.3098 | 38.9852 | 38.9367 | 38.9367 | 38.9367 | 38.9367 | 38.9367 | 38.9367 | 38.9367 | 38.9367 | 38.9367 | 38.9367 | 38.9367 | 38.9367 | 38.9367 | 38.9367 | 38.9367 | 38.9367 | 60% | 178.1154 | 37.7406 | 48.8237 | 51.7218 | 38.4965 | 38.507 | 38.8031 | 39.5871 | 40.1105 | 40.6236 | 41.2241 | 41.7796 | 42.3196 | 42.3798 | 43.0104 | 42.5295 | 42.5295 | 42.5295 | 42.5295 | 42.5295 | 42.5295 | 42.5295 | 42.5295 | 42.5295 | 42.5295 | 42.5295 | 42.5295 | 42.5295 | 42.5295 | 42.5295 | 42.5295
55% | 1095.5419 | 31.0466 | 41.1857 | 43.9439 | 31.8999 | 31.8953 | 32.2087 | 32.5528 | 33.2597 | 33.7678 | 34.043 | 34.3434 | 34.6188 | 35.1173 | 35.7364 | 35.692 | 35.692 | 35.692 | 35.692 | 35.692 | 35.692 | 35.692 | 35.692 | 35.692 | 35.692 | 35.692 | 35.692 | 35.692 | 35.692 | 35.692 | 35.692 | 55% | 311.6074 | 34.5955 | 44.755 | 47.4116 | 35.2885 | 35.2981 | 35.5695 | 36.2881 | 36.7679 | 37.2383 | 37.7888 | 38.2979 | 38.793 | 38.8482 | 39.4262 | 38.9854 | 38.9854 | 38.9854 | 38.9854 | 38.9854 | 38.9854 | 38.9854 | 38.9854 | 38.9854 | 38.9854 | 38.9854 | 38.9854 | 38.9854 | 38.9854 | 38.9854 | 38.9854
50% | 1666.1918 | 28.2242 | 37.4415 | 39.949 | 28.9999 | 28.9957 | 29.2807 | 29.5934 | 30.2361 | 30.698 | 30.9481 | 31.2212 | 31.4716 | 31.9249 | 32.4876 | 32.4472 | 32.4472 | 32.4472 | 32.4472 | 32.4472 | 32.4472 | 32.4472 | 32.4472 | 32.4472 | 32.4472 | 32.4472 | 32.4472 | 32.4472 | 32.4472 | 32.4472 | 32.4472 | 50% | 636.0723 | 31.4505 | 40.6864 | 43.1015 | 32.0804 | 32.0892 | 32.336 | 32.9892 | 33.4254 | 33.853 | 34.3534 | 34.8163 | 35.2663 | 35.3165 | 35.842 | 35.4412 | 35.4412 | 35.4412 | 35.4412 | 35.4412 | 35.4412 | 35.4412 | 35.4412 | 35.4412 | 35.4412 | 35.4412 | 35.4412 | 35.4412 | 35.4412 | 35.4412 | 35.4412
45% | 2506.0947 | 25.4017 | 33.6974 | 35.9541 | 26.0999 | 26.0962 | 26.3526 | 26.6341 | 27.2125 | 27.6282 | 27.8533 | 28.0991 | 28.3245 | 28.7324 | 29.2389 | 29.2025 | 29.2025 | 29.2025 | 29.2025 | 29.2025 | 29.2025 | 29.2025 | 29.2025 | 29.2025 | 29.2025 | 29.2025 | 29.2025 | 29.2025 | 29.2025 | 29.2025 | 29.2025 | 45% | 1179.4944 | 28.3054 | 36.6177 | 38.7913 | 28.8724 | 28.8803 | 29.1024 | 29.6903 | 30.0828 | 30.4677 | 30.9181 | 31.3347 | 31.7397 | 31.7849 | 32.2578 | 31.8971 | 31.8971 | 31.8971 | 31.8971 | 31.8971 | 31.8971 | 31.8971 | 31.8971 | 31.8971 | 31.8971 | 31.8971 | 31.8971 | 31.8971 | 31.8971 | 31.8971 | 31.8971
40% | 3164.4787 | 22.5793 | 29.9532 | 31.9592 | 23.1999 | 23.1966 | 23.4245 | 23.6748 | 24.1889 | 24.5584 | 24.7585 | 24.977 | 25.1773 | 25.5399 | 25.9901 | 25.9578 | 25.9578 | 25.9578 | 25.9578 | 25.9578 | 25.9578 | 25.9578 | 25.9578 | 25.9578 | 25.9578 | 25.9578 | 25.9578 | 25.9578 | 25.9578 | 25.9578 | 25.9578 | 40% | 1808.3816 | 25.1604 | 32.5491 | 34.4812 | 25.6644 | 25.6713 | 25.8688 | 26.3914 | 26.7403 | 27.0824 | 27.4827 | 27.853 | 28.2131 | 28.2532 | 28.6736 | 28.353 | 28.353 | 28.353 | 28.353 | 28.353 | 28.353 | 28.353 | 28.353 | 28.353 | 28.353 | 28.353 | 28.353 | 28.353 | 28.353 | 28.353 | 28.353
35% | 3551.3408 | 19.7569 | 26.2091 | 27.9643 | 20.2999 | 20.297 | 20.4965 | 20.7154 | 21.1653 | 21.4886 | 21.6637 | 21.8549 | 22.0301 | 22.3474 | 22.7413 | 22.7131 | 22.7131 | 22.7131 | 22.7131 | 22.7131 | 22.7131 | 22.7131 | 22.7131 | 22.7131 | 22.7131 | 22.7131 | 22.7131 | 22.7131 | 22.7131 | 22.7131 | 22.7131 | 35% | 2779.1293 | 22.0153 | 28.4805 | 30.171 | 22.4563 | 22.4624 | 22.6352 | 23.0925 | 23.3978 | 23.6971 | 24.0474 | 24.3714 | 24.6864 | 24.7216 | 25.0894 | 24.8089 | 24.8089 | 24.8089 | 24.8089 | 24.8089 | 24.8089 | 24.8089 | 24.8089 | 24.8089 | 24.8089 | 24.8089 | 24.8089 | 24.8089 | 24.8089 | 24.8089 | 24.8089
30% | 3758.953 | 16.9345 | 22.4649 | 23.9694 | 17.3999 | 17.3974 | 17.5684 | 17.7561 | 18.1417 | 18.4188 | 18.5689 | 18.7327 | 18.883 | 19.1549 | 19.4926 | 19.4683 | 19.4683 | 19.4683 | 19.4683 | 19.4683 | 19.4683 | 19.4683 | 19.4683 | 19.4683 | 19.4683 | 19.4683 | 19.4683 | 19.4683 | 19.4683 | 19.4683 | 19.4683 | 30% | 3814.165 | 18.8703 | 24.4118 | 25.8609 | 19.2483 | 19.2535 | 19.4016 | 19.7935 | 20.0552 | 20.3118 | 20.6121 | 20.8898 | 21.1598 | 21.1899 | 21.5052 | 21.2647 | 21.2647 | 21.2647 | 21.2647 | 21.2647 | 21.2647 | 21.2647 | 21.2647 | 21.2647 | 21.2647 | 21.2647 | 21.2647 | 21.2647 | 21.2647 | 21.2647 | 21.2647
25% | 3926.4798 | 14.1121 | 18.7208 | 19.9745 | 14.5 | 14.4979 | 14.6403 | 14.7967 | 15.1181 | 15.349 | 15.4741 | 15.6106 | 15.7358 | 15.9624 | 16.2438 | 16.2236 | 16.2236 | 16.2236 | 16.2236 | 16.2236 | 16.2236 | 16.2236 | 16.2236 | 16.2236 | 16.2236 | 16.2236 | 16.2236 | 16.2236 | 16.2236 | 16.2236 | 16.2236 | 25% | 4166.9923 | 15.7252 | 20.3432 | 21.5507 | 16.0402 | 16.0446 | 16.168 | 16.4946 | 16.7127 | 16.9265 | 17.1767 | 17.4082 | 17.6332 | 17.6583 | 17.921 | 17.7206 | 17.7206 | 17.7206 | 17.7206 | 17.7206 | 17.7206 | 17.7206 | 17.7206 | 17.7206 | 17.7206 | 17.7206 | 17.7206 | 17.7206 | 17.7206 | 17.7206 | 17.7206
20% | 4050.5177 | 11.2897 | 14.9766 | 15.9796 | 11.6 | 11.5983 | 11.7123 | 11.8374 | 12.0945 | 12.2792 | 12.3793 | 12.4885 | 12.5886 | 12.7699 | 12.9951 | 12.9789 | 12.9789 | 12.9789 | 12.9789 | 12.9789 | 12.9789 | 12.9789 | 12.9789 | 12.9789 | 12.9789 | 12.9789 | 12.9789 | 12.9789 | 12.9789 | 12.9789 | 12.9789 | 20% | 4282.7105 | 12.5802 | 16.2746 | 17.2406 | 12.8322 | 12.8357 | 12.9344 | 13.1957 | 13.3702 | 13.5412 | 13.7414 | 13.9265 | 14.1065 | 14.1266 | 14.3368 | 14.1765 | 14.1765 | 14.1765 | 14.1765 | 14.1765 | 14.1765 | 14.1765 | 14.1765 | 14.1765 | 14.1765 | 14.1765 | 14.1765 | 14.1765 | 14.1765 | 14.1765 | 14.1765
15% | 4152.622 | 8.4672 | 11.2325 | 11.9847 | 8.7 | 8.6987 | 8.7842 | 8.878 | 9.0708 | 9.2094 | 9.2844 | 9.3664 | 9.4415 | 9.5775 | 9.7463 | 9.7342 | 9.7342 | 9.7342 | 9.7342 | 9.7342 | 9.7342 | 9.7342 | 9.7342 | 9.7342 | 9.7342 | 9.7342 | 9.7342 | 9.7342 | 9.7342 | 9.7342 | 9.7342 | 15% | 4364.7722 | 9.4351 | 12.2059 | 12.9304 | 9.6241 | 9.6268 | 9.7008 | 9.8968 | 10.0276 | 10.1559 | 10.306 | 10.4449 | 10.5799 | 10.595 | 10.7526 | 10.6324 | 10.6324 | 10.6324 | 10.6324 | 10.6324 | 10.6324 | 10.6324 | 10.6324 | 10.6324 | 10.6324 | 10.6324 | 10.6324 | 10.6324 | 10.6324 | 10.6324 | 10.6324
10% | 4248.2976 | 5.6448 | 7.4883 | 7.9898 | 5.8 | 5.7991 | 5.8561 | 5.9187 | 6.0472 | 6.1396 | 6.1896 | 6.2442 | 6.2943 | 6.385 | 6.4975 | 6.4894 | 6.4894 | 6.4894 | 6.4894 | 6.4894 | 6.4894 | 6.4894 | 6.4894 | 6.4894 | 6.4894 | 6.4894 | 6.4894 | 6.4894 | 6.4894 | 6.4894 | 6.4894 | 10% | 4391.6218 | 6.2901 | 8.1373 | 8.6203 | 6.4161 | 6.4178 | 6.4672 | 6.5978 | 6.6851 | 6.7706 | 6.8707 | 6.9633 | 7.0533 | 7.0633 | 7.1684 | 7.0882 | 7.0882 | 7.0882 | 7.0882 | 7.0882 | 7.0882 | 7.0882 | 7.0882 | 7.0882 | 7.0882 | 7.0882 | 7.0882 | 7.0882 | 7.0882 | 7.0882 | 7.0882
5% | 4361.7469 | 2.8224 | 3.7442 | 3.9949 | 2.9 | 2.8996 | 2.9281 | 2.9593 | 3.0236 | 3.0698 | 3.0948 | 3.1221 | 3.1472 | 3.1925 | 3.2488 | 3.2447 | 3.2447 | 3.2447 | 3.2447 | 3.2447 | 3.2447 | 3.2447 | 3.2447 | 3.2447 | 3.2447 | 3.2447 | 3.2447 | 3.2447 | 3.2447 | 3.2447 | 3.2447 | 5% | 4391.6218 | 3.145 | 4.0686 | 4.3101 | 3.208 | 3.2089 | 3.2336 | 3.2989 | 3.3425 | 3.3853 | 3.4353 | 3.4816 | 3.5266 | 3.5317 | 3.5842 | 3.5441 | 3.5441 | 3.5441 | 3.5441 | 3.5441 | 3.5441 | 3.5441 | 3.5441 | 3.5441 | 3.5441 | 3.5441 | 3.5441 | 3.5441 | 3.5441 | 3.5441 | 3.5441
9.992e-14% | 4391.6218 | 5.6403e-14 | 7.4823e-14 | 7.9834e-14 | 5.7953e-14 | 5.7945e-14 | 5.8515e-14 | 5.914e-14 | 6.0424e-14 | 6.1347e-14 | 6.1847e-14 | 6.2393e-14 | 6.2893e-14 | 6.3799e-14 | 6.4923e-14 | 6.4843e-14 | 6.4843e-14 | 6.4843e-14 | 6.4843e-14 | 6.4843e-14 | 6.4843e-14 | 6.4843e-14 | 6.4843e-14 | 6.4843e-14 | 6.4843e-14 | 6.4843e-14 | 6.4843e-14 | 6.4843e-14 | 6.4843e-14 | 6.4843e-14 | 6.4843e-14 | 9.992e-14% | 4391.6218 | 6.2851e-14 | 8.1308e-14 | 8.6134e-14 | 6.411e-14 | 6.4127e-14 | 6.462e-14 | 6.5926e-14 | 6.6797e-14 | 6.7652e-14 | 6.8652e-14 | 6.9577e-14 | 7.0476e-14 | 7.0577e-14 | 7.1627e-14 | 7.0826e-14 | 7.0826e-14 | 7.0826e-14 | 7.0826e-14 | 7.0826e-14 | 7.0826e-14 | 7.0826e-14 | 7.0826e-14 | 7.0826e-14 | 7.0826e-14 | 7.0826e-14 | 7.0826e-14 | 7.0826e-14 | 7.0826e-14 | 7.0826e-14 | 7.0826e-14
Option 6
Winter Season | [31 empty] | Winter Season
P50 | [31 empty] | P10
% of MD | Winter - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Winter - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 49.7042 | 68.8514 | 73.8223 | 74.6663 | 75.3214 | 76.4563 | 79.0441 | 80.7726 | 82.9664 | 84.1029 | 85.1001 | 83.2461 | 85.4092 | 88.8125 | 86.2221 | 86.2221 | 86.2221 | 86.2221 | 86.2221 | 86.2221 | 86.2221 | 86.2221 | 86.2221 | 86.2221 | 86.2221 | 86.2221 | 86.2221 | 86.2221 | 86.2221 | 86.2221 | 100% | 0 | 53.1876 | 72.0932 | 77.2584 | 78.0542 | 78.5557 | 79.6659 | 82.2942 | 83.7249 | 86.4587 | 94.7777 | 87.9092 | 86.5626 | 88.3699 | 92.3278 | 89.6413 | 89.6413 | 89.6413 | 89.6413 | 89.6413 | 89.6413 | 89.6413 | 89.6413 | 89.6413 | 89.6413 | 89.6413 | 89.6413 | 89.6413 | 89.6413 | 89.6413 | 89.6413
99% | 1.486 | 49.2072 | 68.1629 | 73.0841 | 73.9197 | 74.5682 | 75.6918 | 78.2537 | 79.9649 | 82.1367 | 83.2619 | 84.2491 | 82.4136 | 84.5551 | 87.9243 | 85.3598 | 85.3598 | 85.3598 | 85.3598 | 85.3598 | 85.3598 | 85.3598 | 85.3598 | 85.3598 | 85.3598 | 85.3598 | 85.3598 | 85.3598 | 85.3598 | 85.3598 | 85.3598 | 99% | 1.486 | 52.6557 | 71.3723 | 76.4858 | 77.2737 | 77.7701 | 78.8692 | 81.4712 | 82.8877 | 85.5941 | 93.83 | 87.0301 | 85.697 | 87.4862 | 91.4045 | 88.7449 | 88.7449 | 88.7449 | 88.7449 | 88.7449 | 88.7449 | 88.7449 | 88.7449 | 88.7449 | 88.7449 | 88.7449 | 88.7449 | 88.7449 | 88.7449 | 88.7449 | 88.7449
98% | 3.2692 | 48.7101 | 67.4743 | 72.3458 | 73.173 | 73.815 | 74.9272 | 77.4632 | 79.1572 | 81.3071 | 82.4209 | 83.3981 | 81.5812 | 83.701 | 87.0362 | 84.4976 | 84.4976 | 84.4976 | 84.4976 | 84.4976 | 84.4976 | 84.4976 | 84.4976 | 84.4976 | 84.4976 | 84.4976 | 84.4976 | 84.4976 | 84.4976 | 84.4976 | 84.4976 | 98% | 3.2692 | 52.1238 | 70.6514 | 75.7133 | 76.4931 | 76.9846 | 78.0726 | 80.6483 | 82.0504 | 84.7295 | 92.8822 | 86.151 | 84.8313 | 86.6025 | 90.4812 | 87.8485 | 87.8485 | 87.8485 | 87.8485 | 87.8485 | 87.8485 | 87.8485 | 87.8485 | 87.8485 | 87.8485 | 87.8485 | 87.8485 | 87.8485 | 87.8485 | 87.8485 | 87.8485
97% | 6.8356 | 48.2131 | 66.7858 | 71.6076 | 72.4263 | 73.0618 | 74.1627 | 76.6728 | 78.3495 | 80.4774 | 81.5798 | 82.5471 | 80.7487 | 82.847 | 86.1481 | 83.6354 | 83.6354 | 83.6354 | 83.6354 | 83.6354 | 83.6354 | 83.6354 | 83.6354 | 83.6354 | 83.6354 | 83.6354 | 83.6354 | 83.6354 | 83.6354 | 83.6354 | 83.6354 | 97% | 6.8356 | 51.5919 | 69.9304 | 74.9407 | 75.7126 | 76.199 | 77.2759 | 79.8254 | 81.2132 | 83.865 | 91.9344 | 85.2719 | 83.9657 | 85.7188 | 89.558 | 86.9521 | 86.9521 | 86.9521 | 86.9521 | 86.9521 | 86.9521 | 86.9521 | 86.9521 | 86.9521 | 86.9521 | 86.9521 | 86.9521 | 86.9521 | 86.9521 | 86.9521 | 86.9521
95% | 17.5347 | 47.219 | 65.4088 | 70.1312 | 70.933 | 71.5553 | 72.6335 | 75.0919 | 76.734 | 78.8181 | 79.8978 | 80.8451 | 79.0838 | 81.1388 | 84.3718 | 81.911 | 81.911 | 81.911 | 81.911 | 81.911 | 81.911 | 81.911 | 81.911 | 81.911 | 81.911 | 81.911 | 81.911 | 81.911 | 81.911 | 81.911 | 81.911 | 95% | 17.5347 | 50.5282 | 68.4886 | 73.3955 | 74.1515 | 74.6279 | 75.6826 | 78.1795 | 79.5387 | 82.1358 | 90.0389 | 83.5138 | 82.2345 | 83.9514 | 87.7114 | 85.1592 | 85.1592 | 85.1592 | 85.1592 | 85.1592 | 85.1592 | 85.1592 | 85.1592 | 85.1592 | 85.1592 | 85.1592 | 85.1592 | 85.1592 | 85.1592 | 85.1592 | 85.1592
90% | 78.7576 | 44.7338 | 61.9662 | 66.4401 | 67.1997 | 67.7893 | 68.8107 | 71.1397 | 72.6954 | 74.6697 | 75.6926 | 76.5901 | 74.9215 | 76.8683 | 79.9312 | 77.5999 | 77.5999 | 77.5999 | 77.5999 | 77.5999 | 77.5999 | 77.5999 | 77.5999 | 77.5999 | 77.5999 | 77.5999 | 77.5999 | 77.5999 | 77.5999 | 77.5999 | 77.5999 | 90% | 78.7576 | 47.8688 | 64.8839 | 69.5326 | 70.2488 | 70.7001 | 71.6993 | 74.0648 | 75.3524 | 77.8128 | 85.3 | 79.1183 | 77.9063 | 79.5329 | 83.095 | 80.6772 | 80.6772 | 80.6772 | 80.6772 | 80.6772 | 80.6772 | 80.6772 | 80.6772 | 80.6772 | 80.6772 | 80.6772 | 80.6772 | 80.6772 | 80.6772 | 80.6772 | 80.6772
85% | 236.8672 | 42.2486 | 58.5237 | 62.7489 | 63.4664 | 64.0232 | 64.9879 | 67.1875 | 68.6567 | 70.5214 | 71.4875 | 72.3351 | 70.7592 | 72.5978 | 75.4906 | 73.2888 | 73.2888 | 73.2888 | 73.2888 | 73.2888 | 73.2888 | 73.2888 | 73.2888 | 73.2888 | 73.2888 | 73.2888 | 73.2888 | 73.2888 | 73.2888 | 73.2888 | 73.2888 | 85% | 236.8672 | 45.2094 | 61.2792 | 65.6697 | 66.3461 | 66.7723 | 67.716 | 69.9501 | 71.1662 | 73.4899 | 80.5611 | 74.7228 | 73.5782 | 75.1144 | 78.4786 | 76.1951 | 76.1951 | 76.1951 | 76.1951 | 76.1951 | 76.1951 | 76.1951 | 76.1951 | 76.1951 | 76.1951 | 76.1951 | 76.1951 | 76.1951 | 76.1951 | 76.1951 | 76.1951
80% | 497.5104 | 39.7634 | 55.0811 | 59.0578 | 59.7331 | 60.2571 | 61.1651 | 63.2353 | 64.6181 | 66.3731 | 67.2823 | 68.08 | 66.5969 | 68.3274 | 71.05 | 68.9777 | 68.9777 | 68.9777 | 68.9777 | 68.9777 | 68.9777 | 68.9777 | 68.9777 | 68.9777 | 68.9777 | 68.9777 | 68.9777 | 68.9777 | 68.9777 | 68.9777 | 68.9777 | 80% | 497.5104 | 42.55 | 57.6746 | 61.8067 | 62.4434 | 62.8445 | 63.7327 | 65.8353 | 66.9799 | 69.167 | 75.8222 | 70.3274 | 69.2501 | 70.6959 | 73.8622 | 71.7131 | 71.7131 | 71.7131 | 71.7131 | 71.7131 | 71.7131 | 71.7131 | 71.7131 | 71.7131 | 71.7131 | 71.7131 | 71.7131 | 71.7131 | 71.7131 | 71.7131 | 71.7131
75% | 803.6248 | 37.2782 | 51.6385 | 55.3667 | 55.9997 | 56.4911 | 57.3423 | 59.2831 | 60.5795 | 62.2248 | 63.0772 | 63.825 | 62.4346 | 64.0569 | 66.6093 | 64.6665 | 64.6665 | 64.6665 | 64.6665 | 64.6665 | 64.6665 | 64.6665 | 64.6665 | 64.6665 | 64.6665 | 64.6665 | 64.6665 | 64.6665 | 64.6665 | 64.6665 | 64.6665 | 75% | 803.6248 | 39.8907 | 54.0699 | 57.9438 | 58.5407 | 58.9167 | 59.7494 | 61.7206 | 62.7937 | 64.844 | 71.0833 | 65.9319 | 64.9219 | 66.2774 | 69.2458 | 67.231 | 67.231 | 67.231 | 67.231 | 67.231 | 67.231 | 67.231 | 67.231 | 67.231 | 67.231 | 67.231 | 67.231 | 67.231 | 67.231 | 67.231 | 67.231
70% | 1155.2107 | 34.793 | 48.196 | 51.6756 | 52.2664 | 52.725 | 53.5194 | 55.3309 | 56.5408 | 58.0765 | 58.8721 | 59.57 | 58.2723 | 59.7865 | 62.1687 | 60.3554 | 60.3554 | 60.3554 | 60.3554 | 60.3554 | 60.3554 | 60.3554 | 60.3554 | 60.3554 | 60.3554 | 60.3554 | 60.3554 | 60.3554 | 60.3554 | 60.3554 | 60.3554 | 70% | 1155.2107 | 37.2313 | 50.4653 | 54.0809 | 54.638 | 54.989 | 55.7661 | 57.6059 | 58.6074 | 60.5211 | 66.3444 | 61.5365 | 60.5938 | 61.8589 | 64.6295 | 62.7489 | 62.7489 | 62.7489 | 62.7489 | 62.7489 | 62.7489 | 62.7489 | 62.7489 | 62.7489 | 62.7489 | 62.7489 | 62.7489 | 62.7489 | 62.7489 | 62.7489 | 62.7489
65% | 1553.1596 | 32.3077 | 44.7534 | 47.9845 | 48.5331 | 48.9589 | 49.6966 | 51.3787 | 52.5022 | 53.9282 | 54.6669 | 55.315 | 54.11 | 55.516 | 57.7281 | 56.0443 | 56.0443 | 56.0443 | 56.0443 | 56.0443 | 56.0443 | 56.0443 | 56.0443 | 56.0443 | 56.0443 | 56.0443 | 56.0443 | 56.0443 | 56.0443 | 56.0443 | 56.0443 | 65% | 1553.1596 | 34.5719 | 46.8606 | 50.218 | 50.7352 | 51.0612 | 51.7828 | 53.4912 | 54.4212 | 56.1982 | 61.6055 | 57.141 | 56.2657 | 57.4405 | 60.0131 | 58.2669 | 58.2669 | 58.2669 | 58.2669 | 58.2669 | 58.2669 | 58.2669 | 58.2669 | 58.2669 | 58.2669 | 58.2669 | 58.2669 | 58.2669 | 58.2669 | 58.2669 | 58.2669
60% | 2026.2996 | 29.8225 | 41.3108 | 44.2934 | 44.7998 | 45.1928 | 45.8738 | 47.4265 | 48.4636 | 49.7798 | 50.4618 | 51.06 | 49.9477 | 51.2455 | 53.2875 | 51.7332 | 51.7332 | 51.7332 | 51.7332 | 51.7332 | 51.7332 | 51.7332 | 51.7332 | 51.7332 | 51.7332 | 51.7332 | 51.7332 | 51.7332 | 51.7332 | 51.7332 | 51.7332 | 60% | 2026.2996 | 31.9125 | 43.2559 | 46.3551 | 46.8325 | 47.1334 | 47.7995 | 49.3765 | 50.235 | 51.8752 | 56.8666 | 52.7455 | 51.9376 | 53.022 | 55.3967 | 53.7848 | 53.7848 | 53.7848 | 53.7848 | 53.7848 | 53.7848 | 53.7848 | 53.7848 | 53.7848 | 53.7848 | 53.7848 | 53.7848 | 53.7848 | 53.7848 | 53.7848 | 53.7848
55% | 2598.4068 | 27.3373 | 37.8683 | 40.6023 | 41.0665 | 41.4268 | 42.051 | 43.4743 | 44.425 | 45.6315 | 46.2566 | 46.805 | 45.7854 | 46.9751 | 48.8469 | 47.4221 | 47.4221 | 47.4221 | 47.4221 | 47.4221 | 47.4221 | 47.4221 | 47.4221 | 47.4221 | 47.4221 | 47.4221 | 47.4221 | 47.4221 | 47.4221 | 47.4221 | 47.4221 | 55% | 2598.4068 | 29.2532 | 39.6513 | 42.4921 | 42.9298 | 43.2056 | 43.8162 | 45.2618 | 46.0487 | 47.5523 | 52.1278 | 48.3501 | 47.6094 | 48.6035 | 50.7803 | 49.3027 | 49.3027 | 49.3027 | 49.3027 | 49.3027 | 49.3027 | 49.3027 | 49.3027 | 49.3027 | 49.3027 | 49.3027 | 49.3027 | 49.3027 | 49.3027 | 49.3027 | 49.3027
50% | 3233.5201 | 24.8521 | 34.4257 | 36.9111 | 37.3332 | 37.6607 | 38.2282 | 39.5221 | 40.3863 | 41.4832 | 42.0515 | 42.55 | 41.623 | 42.7046 | 44.4062 | 43.111 | 43.111 | 43.111 | 43.111 | 43.111 | 43.111 | 43.111 | 43.111 | 43.111 | 43.111 | 43.111 | 43.111 | 43.111 | 43.111 | 43.111 | 43.111 | 50% | 3233.5201 | 26.5938 | 36.0466 | 38.6292 | 39.0271 | 39.2778 | 39.833 | 41.1471 | 41.8625 | 43.2294 | 47.3889 | 43.9546 | 43.2813 | 44.185 | 46.1639 | 44.8207 | 44.8207 | 44.8207 | 44.8207 | 44.8207 | 44.8207 | 44.8207 | 44.8207 | 44.8207 | 44.8207 | 44.8207 | 44.8207 | 44.8207 | 44.8207 | 44.8207 | 44.8207
45% | 3775.313 | 22.3669 | 30.9831 | 33.22 | 33.5998 | 33.8946 | 34.4054 | 35.5699 | 36.3477 | 37.3349 | 37.8463 | 38.295 | 37.4607 | 38.4342 | 39.9656 | 38.7999 | 38.7999 | 38.7999 | 38.7999 | 38.7999 | 38.7999 | 38.7999 | 38.7999 | 38.7999 | 38.7999 | 38.7999 | 38.7999 | 38.7999 | 38.7999 | 38.7999 | 38.7999 | 45% | 3775.313 | 23.9344 | 32.442 | 34.7663 | 35.1244 | 35.35 | 35.8497 | 37.0324 | 37.6762 | 38.9064 | 42.65 | 39.5591 | 38.9532 | 39.7665 | 41.5475 | 40.3386 | 40.3386 | 40.3386 | 40.3386 | 40.3386 | 40.3386 | 40.3386 | 40.3386 | 40.3386 | 40.3386 | 40.3386 | 40.3386 | 40.3386 | 40.3386 | 40.3386 | 40.3386
40% | 4072.8088 | 19.8817 | 27.5405 | 29.5289 | 29.8665 | 30.1286 | 30.5825 | 31.6176 | 32.3091 | 33.1866 | 33.6412 | 34.04 | 33.2984 | 34.1637 | 35.525 | 34.4888 | 34.4888 | 34.4888 | 34.4888 | 34.4888 | 34.4888 | 34.4888 | 34.4888 | 34.4888 | 34.4888 | 34.4888 | 34.4888 | 34.4888 | 34.4888 | 34.4888 | 34.4888 | 40% | 4072.8088 | 21.275 | 28.8373 | 30.9034 | 31.2217 | 31.4223 | 31.8664 | 32.9177 | 33.49 | 34.5835 | 37.9111 | 35.1637 | 34.625 | 35.348 | 36.9311 | 35.8565 | 35.8565 | 35.8565 | 35.8565 | 35.8565 | 35.8565 | 35.8565 | 35.8565 | 35.8565 | 35.8565 | 35.8565 | 35.8565 | 35.8565 | 35.8565 | 35.8565 | 35.8565
35% | 4198.821 | 17.3965 | 24.098 | 25.8378 | 26.1332 | 26.3625 | 26.7597 | 27.6654 | 28.2704 | 29.0382 | 29.436 | 29.785 | 29.1361 | 29.8932 | 31.0844 | 30.1777 | 30.1777 | 30.1777 | 30.1777 | 30.1777 | 30.1777 | 30.1777 | 30.1777 | 30.1777 | 30.1777 | 30.1777 | 30.1777 | 30.1777 | 30.1777 | 30.1777 | 30.1777 | 35% | 4198.821 | 18.6156 | 25.2326 | 27.0405 | 27.319 | 27.4945 | 27.8831 | 28.803 | 29.3037 | 30.2606 | 33.1722 | 30.7682 | 30.2969 | 30.9295 | 32.3147 | 31.3745 | 31.3745 | 31.3745 | 31.3745 | 31.3745 | 31.3745 | 31.3745 | 31.3745 | 31.3745 | 31.3745 | 31.3745 | 31.3745 | 31.3745 | 31.3745 | 31.3745 | 31.3745
30% | 4271.3374 | 14.9113 | 20.6554 | 22.1467 | 22.3999 | 22.5964 | 22.9369 | 23.7132 | 24.2318 | 24.8899 | 25.2309 | 25.53 | 24.9738 | 25.6228 | 26.6437 | 25.8666 | 25.8666 | 25.8666 | 25.8666 | 25.8666 | 25.8666 | 25.8666 | 25.8666 | 25.8666 | 25.8666 | 25.8666 | 25.8666 | 25.8666 | 25.8666 | 25.8666 | 25.8666 | 30% | 4271.3374 | 15.9563 | 21.628 | 23.1775 | 23.4163 | 23.5667 | 23.8998 | 24.6883 | 25.1175 | 25.9376 | 28.4333 | 26.3728 | 25.9688 | 26.511 | 27.6983 | 26.8924 | 26.8924 | 26.8924 | 26.8924 | 26.8924 | 26.8924 | 26.8924 | 26.8924 | 26.8924 | 26.8924 | 26.8924 | 26.8924 | 26.8924 | 26.8924 | 26.8924 | 26.8924
25% | 4321.8611 | 12.4261 | 17.2128 | 18.4556 | 18.6666 | 18.8304 | 19.1141 | 19.761 | 20.1932 | 20.7416 | 21.0257 | 21.275 | 20.8115 | 21.3523 | 22.2031 | 21.5555 | 21.5555 | 21.5555 | 21.5555 | 21.5555 | 21.5555 | 21.5555 | 21.5555 | 21.5555 | 21.5555 | 21.5555 | 21.5555 | 21.5555 | 21.5555 | 21.5555 | 21.5555 | 25% | 4321.8611 | 13.2969 | 18.0233 | 19.3146 | 19.5136 | 19.6389 | 19.9165 | 20.5735 | 20.9312 | 21.6147 | 23.6944 | 21.9773 | 21.6406 | 22.0925 | 23.0819 | 22.4103 | 22.4103 | 22.4103 | 22.4103 | 22.4103 | 22.4103 | 22.4103 | 22.4103 | 22.4103 | 22.4103 | 22.4103 | 22.4103 | 22.4103 | 22.4103 | 22.4103 | 22.4103
20% | 4353.067 | 9.9408 | 13.7703 | 14.7645 | 14.9333 | 15.0643 | 15.2913 | 15.8088 | 16.1545 | 16.5933 | 16.8206 | 17.02 | 16.6492 | 17.0818 | 17.7625 | 17.2444 | 17.2444 | 17.2444 | 17.2444 | 17.2444 | 17.2444 | 17.2444 | 17.2444 | 17.2444 | 17.2444 | 17.2444 | 17.2444 | 17.2444 | 17.2444 | 17.2444 | 17.2444 | 20% | 4353.067 | 10.6375 | 14.4186 | 15.4517 | 15.6108 | 15.7111 | 15.9332 | 16.4588 | 16.745 | 17.2917 | 18.9555 | 17.5818 | 17.3125 | 17.674 | 18.4656 | 17.9283 | 17.9283 | 17.9283 | 17.9283 | 17.9283 | 17.9283 | 17.9283 | 17.9283 | 17.9283 | 17.9283 | 17.9283 | 17.9283 | 17.9283 | 17.9283 | 17.9283 | 17.9283
15% | 4369.4129 | 7.4556 | 10.3277 | 11.0733 | 11.1999 | 11.2982 | 11.4685 | 11.8566 | 12.1159 | 12.445 | 12.6154 | 12.765 | 12.4869 | 12.8114 | 13.3219 | 12.9333 | 12.9333 | 12.9333 | 12.9333 | 12.9333 | 12.9333 | 12.9333 | 12.9333 | 12.9333 | 12.9333 | 12.9333 | 12.9333 | 12.9333 | 12.9333 | 12.9333 | 12.9333 | 15% | 4369.4129 | 7.9781 | 10.814 | 11.5888 | 11.7081 | 11.7833 | 11.9499 | 12.3441 | 12.5587 | 12.9688 | 14.2167 | 13.1864 | 12.9844 | 13.2555 | 13.8492 | 13.4462 | 13.4462 | 13.4462 | 13.4462 | 13.4462 | 13.4462 | 13.4462 | 13.4462 | 13.4462 | 13.4462 | 13.4462 | 13.4462 | 13.4462 | 13.4462 | 13.4462 | 13.4462
10% | 4378.6261 | 4.9704 | 6.8851 | 7.3822 | 7.4666 | 7.5321 | 7.6456 | 7.9044 | 8.0773 | 8.2966 | 8.4103 | 8.51 | 8.3246 | 8.5409 | 8.8812 | 8.6222 | 8.6222 | 8.6222 | 8.6222 | 8.6222 | 8.6222 | 8.6222 | 8.6222 | 8.6222 | 8.6222 | 8.6222 | 8.6222 | 8.6222 | 8.6222 | 8.6222 | 8.6222 | 10% | 4378.6261 | 5.3188 | 7.2093 | 7.7258 | 7.8054 | 7.8556 | 7.9666 | 8.2294 | 8.3725 | 8.6459 | 9.4778 | 8.7909 | 8.6563 | 8.837 | 9.2328 | 8.9641 | 8.9641 | 8.9641 | 8.9641 | 8.9641 | 8.9641 | 8.9641 | 8.9641 | 8.9641 | 8.9641 | 8.9641 | 8.9641 | 8.9641 | 8.9641 | 8.9641 | 8.9641
5% | 4391.7028 | 2.4852 | 3.4426 | 3.6911 | 3.7333 | 3.7661 | 3.8228 | 3.9522 | 4.0386 | 4.1483 | 4.2051 | 4.255 | 4.1623 | 4.2705 | 4.4406 | 4.3111 | 4.3111 | 4.3111 | 4.3111 | 4.3111 | 4.3111 | 4.3111 | 4.3111 | 4.3111 | 4.3111 | 4.3111 | 4.3111 | 4.3111 | 4.3111 | 4.3111 | 4.3111 | 5% | 4391.7028 | 2.6594 | 3.6047 | 3.8629 | 3.9027 | 3.9278 | 3.9833 | 4.1147 | 4.1862 | 4.3229 | 4.7389 | 4.3955 | 4.3281 | 4.4185 | 4.6164 | 4.4821 | 4.4821 | 4.4821 | 4.4821 | 4.4821 | 4.4821 | 4.4821 | 4.4821 | 4.4821 | 4.4821 | 4.4821 | 4.4821 | 4.4821 | 4.4821 | 4.4821 | 4.4821
9.992e-14% | 4391.7028 | 4.9664e-14 | 6.8796e-14 | 7.3763e-14 | 7.4607e-14 | 7.5261e-14 | 7.6395e-14 | 7.8981e-14 | 8.0708e-14 | 8.29e-14 | 8.4036e-14 | 8.5032e-14 | 8.318e-14 | 8.5341e-14 | 8.8741e-14 | 8.6153e-14 | 8.6153e-14 | 8.6153e-14 | 8.6153e-14 | 8.6153e-14 | 8.6153e-14 | 8.6153e-14 | 8.6153e-14 | 8.6153e-14 | 8.6153e-14 | 8.6153e-14 | 8.6153e-14 | 8.6153e-14 | 8.6153e-14 | 8.6153e-14 | 8.6153e-14 | 9.992e-14% | 4391.7028 | 5.3145e-14 | 7.2036e-14 | 7.7197e-14 | 7.7992e-14 | 7.8493e-14 | 7.9602e-14 | 8.2228e-14 | 8.3658e-14 | 8.639e-14 | 9.4702e-14 | 8.7839e-14 | 8.6493e-14 | 8.8299e-14 | 9.2254e-14 | 8.957e-14 | 8.957e-14 | 8.957e-14 | 8.957e-14 | 8.957e-14 | 8.957e-14 | 8.957e-14 | 8.957e-14 | 8.957e-14 | 8.957e-14 | 8.957e-14 | 8.957e-14 | 8.957e-14 | 8.957e-14 | 8.957e-14 | 8.957e-14
Summer Season | [31 empty] | Summer Season
P50 | [31 empty] | P10
% of MD | Summer - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Summer - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 56.4483 | 74.8831 | 79.898 | 79.7498 | 79.7414 | 80.3113 | 80.9369 | 82.2223 | 83.1461 | 83.6463 | 84.1925 | 84.6932 | 85.5997 | 86.7253 | 86.6445 | 86.6445 | 86.6445 | 86.6445 | 86.6445 | 86.6445 | 86.6445 | 86.6445 | 86.6445 | 86.6445 | 86.6445 | 86.6445 | 86.6445 | 86.6445 | 86.6445 | 86.6445 | 100% | 0 | 62.901 | 81.3728 | 86.203 | 85.9109 | 85.9284 | 86.4219 | 87.7284 | 88.6008 | 89.4561 | 90.4569 | 91.3826 | 92.2827 | 92.383 | 93.434 | 92.6325 | 92.6325 | 92.6325 | 92.6325 | 92.6325 | 92.6325 | 92.6325 | 92.6325 | 92.6325 | 92.6325 | 92.6325 | 92.6325 | 92.6325 | 92.6325 | 92.6325 | 92.6325
99% | 0 | 55.8838 | 74.1343 | 79.099 | 78.9523 | 78.944 | 79.5082 | 80.1275 | 81.4 | 82.3146 | 82.8098 | 83.3506 | 83.8463 | 84.7437 | 85.858 | 85.778 | 85.778 | 85.778 | 85.778 | 85.778 | 85.778 | 85.778 | 85.778 | 85.778 | 85.778 | 85.778 | 85.778 | 85.778 | 85.778 | 85.778 | 85.778 | 99% | 1.5127 | 62.272 | 80.559 | 85.341 | 85.0518 | 85.0691 | 85.5577 | 86.8512 | 87.7148 | 88.5615 | 89.5523 | 90.4688 | 91.3598 | 91.4592 | 92.4996 | 91.7061 | 91.7061 | 91.7061 | 91.7061 | 91.7061 | 91.7061 | 91.7061 | 91.7061 | 91.7061 | 91.7061 | 91.7061 | 91.7061 | 91.7061 | 91.7061 | 91.7061 | 91.7061
98% | 0 | 55.3193 | 73.3854 | 78.3 | 78.1548 | 78.1466 | 78.7051 | 79.3181 | 80.5778 | 81.4832 | 81.9734 | 82.5086 | 82.9994 | 83.8877 | 84.9908 | 84.9116 | 84.9116 | 84.9116 | 84.9116 | 84.9116 | 84.9116 | 84.9116 | 84.9116 | 84.9116 | 84.9116 | 84.9116 | 84.9116 | 84.9116 | 84.9116 | 84.9116 | 84.9116 | 98% | 2.269 | 61.643 | 79.7453 | 84.4789 | 84.1927 | 84.2098 | 84.6935 | 85.9739 | 86.8287 | 87.667 | 88.6477 | 89.555 | 90.437 | 90.5354 | 91.5653 | 90.7798 | 90.7798 | 90.7798 | 90.7798 | 90.7798 | 90.7798 | 90.7798 | 90.7798 | 90.7798 | 90.7798 | 90.7798 | 90.7798 | 90.7798 | 90.7798 | 90.7798 | 90.7798
97% | 0.37816 | 54.7549 | 72.6366 | 77.501 | 77.3573 | 77.3492 | 77.902 | 78.5088 | 79.7556 | 80.6517 | 81.1369 | 81.6667 | 82.1524 | 83.0317 | 84.1235 | 84.0451 | 84.0451 | 84.0451 | 84.0451 | 84.0451 | 84.0451 | 84.0451 | 84.0451 | 84.0451 | 84.0451 | 84.0451 | 84.0451 | 84.0451 | 84.0451 | 84.0451 | 84.0451 | 97% | 3.7816 | 61.014 | 78.9316 | 83.6169 | 83.3336 | 83.3505 | 83.8292 | 85.0966 | 85.9427 | 86.7724 | 87.7432 | 88.6411 | 89.5142 | 89.6115 | 90.631 | 89.8535 | 89.8535 | 89.8535 | 89.8535 | 89.8535 | 89.8535 | 89.8535 | 89.8535 | 89.8535 | 89.8535 | 89.8535 | 89.8535 | 89.8535 | 89.8535 | 89.8535 | 89.8535
95% | 2.269 | 53.6259 | 71.1389 | 75.9031 | 75.7623 | 75.7544 | 76.2958 | 76.89 | 78.1112 | 78.9888 | 79.464 | 79.9829 | 80.4586 | 81.3197 | 82.389 | 82.3122 | 82.3122 | 82.3122 | 82.3122 | 82.3122 | 82.3122 | 82.3122 | 82.3122 | 82.3122 | 82.3122 | 82.3122 | 82.3122 | 82.3122 | 82.3122 | 82.3122 | 82.3122 | 95% | 6.0506 | 59.7559 | 77.3041 | 81.8928 | 81.6153 | 81.632 | 82.1008 | 83.342 | 84.1707 | 84.9833 | 85.934 | 86.8135 | 87.6685 | 87.7639 | 88.7623 | 88.0008 | 88.0008 | 88.0008 | 88.0008 | 88.0008 | 88.0008 | 88.0008 | 88.0008 | 88.0008 | 88.0008 | 88.0008 | 88.0008 | 88.0008 | 88.0008 | 88.0008 | 88.0008
90% | 5.6725 | 50.8035 | 67.3948 | 71.9082 | 71.7748 | 71.7673 | 72.2802 | 72.8432 | 74 | 74.8315 | 75.2817 | 75.7732 | 76.2239 | 77.0397 | 78.0527 | 77.98 | 77.98 | 77.98 | 77.98 | 77.98 | 77.98 | 77.98 | 77.98 | 77.98 | 77.98 | 77.98 | 77.98 | 77.98 | 77.98 | 77.98 | 77.98 | 90% | 16.2611 | 56.6109 | 73.2355 | 77.5827 | 77.3198 | 77.3355 | 77.7797 | 78.9556 | 79.7407 | 80.5105 | 81.4112 | 82.2444 | 83.0544 | 83.1447 | 84.0906 | 83.3692 | 83.3692 | 83.3692 | 83.3692 | 83.3692 | 83.3692 | 83.3692 | 83.3692 | 83.3692 | 83.3692 | 83.3692 | 83.3692 | 83.3692 | 83.3692 | 83.3692 | 83.3692
85% | 15.8829 | 47.9811 | 63.6506 | 67.9133 | 67.7874 | 67.7802 | 68.2646 | 68.7963 | 69.8889 | 70.6742 | 71.0994 | 71.5636 | 71.9893 | 72.7598 | 73.7165 | 73.6478 | 73.6478 | 73.6478 | 73.6478 | 73.6478 | 73.6478 | 73.6478 | 73.6478 | 73.6478 | 73.6478 | 73.6478 | 73.6478 | 73.6478 | 73.6478 | 73.6478 | 73.6478 | 85% | 26.4715 | 53.4658 | 69.1669 | 73.2725 | 73.0243 | 73.0391 | 73.4586 | 74.5692 | 75.3106 | 76.0377 | 76.8883 | 77.6752 | 78.4403 | 78.5256 | 79.4189 | 78.7376 | 78.7376 | 78.7376 | 78.7376 | 78.7376 | 78.7376 | 78.7376 | 78.7376 | 78.7376 | 78.7376 | 78.7376 | 78.7376 | 78.7376 | 78.7376 | 78.7376 | 78.7376
80% | 31.0095 | 45.1586 | 59.9065 | 63.9184 | 63.7999 | 63.7932 | 64.2491 | 64.7495 | 65.7778 | 66.5169 | 66.917 | 67.354 | 67.7546 | 68.4798 | 69.3802 | 69.3156 | 69.3156 | 69.3156 | 69.3156 | 69.3156 | 69.3156 | 69.3156 | 69.3156 | 69.3156 | 69.3156 | 69.3156 | 69.3156 | 69.3156 | 69.3156 | 69.3156 | 69.3156 | 80% | 34.0348 | 50.3208 | 65.0982 | 68.9624 | 68.7287 | 68.7427 | 69.1375 | 70.1827 | 70.8806 | 71.5649 | 72.3655 | 73.1061 | 73.8261 | 73.9064 | 74.7472 | 74.106 | 74.106 | 74.106 | 74.106 | 74.106 | 74.106 | 74.106 | 74.106 | 74.106 | 74.106 | 74.106 | 74.106 | 74.106 | 74.106 | 74.106 | 74.106
75% | 72.9857 | 42.3362 | 56.1623 | 59.9235 | 59.8124 | 59.8061 | 60.2335 | 60.7027 | 61.6667 | 62.3596 | 62.7347 | 63.1444 | 63.5199 | 64.1998 | 65.044 | 64.9833 | 64.9833 | 64.9833 | 64.9833 | 64.9833 | 64.9833 | 64.9833 | 64.9833 | 64.9833 | 64.9833 | 64.9833 | 64.9833 | 64.9833 | 64.9833 | 64.9833 | 64.9833 | 75% | 48.405 | 47.1757 | 61.0296 | 64.6522 | 64.4332 | 64.4463 | 64.8164 | 65.7963 | 66.4506 | 67.0921 | 67.8427 | 68.537 | 69.212 | 69.2873 | 70.0755 | 69.4744 | 69.4744 | 69.4744 | 69.4744 | 69.4744 | 69.4744 | 69.4744 | 69.4744 | 69.4744 | 69.4744 | 69.4744 | 69.4744 | 69.4744 | 69.4744 | 69.4744 | 69.4744
70% | 150.5094 | 39.5138 | 52.4182 | 55.9286 | 55.8249 | 55.819 | 56.2179 | 56.6558 | 57.5556 | 58.2023 | 58.5524 | 58.9347 | 59.2853 | 59.9198 | 60.7077 | 60.6511 | 60.6511 | 60.6511 | 60.6511 | 60.6511 | 60.6511 | 60.6511 | 60.6511 | 60.6511 | 60.6511 | 60.6511 | 60.6511 | 60.6511 | 60.6511 | 60.6511 | 60.6511 | 70% | 76.3892 | 44.0307 | 56.9609 | 60.3421 | 60.1376 | 60.1499 | 60.4953 | 61.4099 | 62.0205 | 62.6193 | 63.3198 | 63.9678 | 64.5979 | 64.6681 | 65.4038 | 64.8427 | 64.8427 | 64.8427 | 64.8427 | 64.8427 | 64.8427 | 64.8427 | 64.8427 | 64.8427 | 64.8427 | 64.8427 | 64.8427 | 64.8427 | 64.8427 | 64.8427 | 64.8427
65% | 359.6342 | 36.6914 | 48.674 | 51.9337 | 51.8374 | 51.8319 | 52.2024 | 52.609 | 53.4445 | 54.045 | 54.3701 | 54.7251 | 55.0506 | 55.6398 | 56.3714 | 56.3189 | 56.3189 | 56.3189 | 56.3189 | 56.3189 | 56.3189 | 56.3189 | 56.3189 | 56.3189 | 56.3189 | 56.3189 | 56.3189 | 56.3189 | 56.3189 | 56.3189 | 56.3189 | 65% | 114.2056 | 40.8856 | 52.8923 | 56.0319 | 55.8421 | 55.8534 | 56.1742 | 57.0235 | 57.5905 | 58.1465 | 58.797 | 59.3987 | 59.9837 | 60.049 | 60.7321 | 60.2111 | 60.2111 | 60.2111 | 60.2111 | 60.2111 | 60.2111 | 60.2111 | 60.2111 | 60.2111 | 60.2111 | 60.2111 | 60.2111 | 60.2111 | 60.2111 | 60.2111 | 60.2111
60% | 689.7717 | 33.869 | 44.9299 | 47.9388 | 47.8499 | 47.8449 | 48.1868 | 48.5621 | 49.3334 | 49.8876 | 50.1878 | 50.5155 | 50.8159 | 51.3598 | 52.0352 | 51.9867 | 51.9867 | 51.9867 | 51.9867 | 51.9867 | 51.9867 | 51.9867 | 51.9867 | 51.9867 | 51.9867 | 51.9867 | 51.9867 | 51.9867 | 51.9867 | 51.9867 | 51.9867 | 60% | 178.1154 | 37.7406 | 48.8237 | 51.7218 | 51.5465 | 51.557 | 51.8531 | 52.6371 | 53.1605 | 53.6736 | 54.2741 | 54.8296 | 55.3696 | 55.4298 | 56.0604 | 55.5795 | 55.5795 | 55.5795 | 55.5795 | 55.5795 | 55.5795 | 55.5795 | 55.5795 | 55.5795 | 55.5795 | 55.5795 | 55.5795 | 55.5795 | 55.5795 | 55.5795 | 55.5795
55% | 1095.5419 | 31.0466 | 41.1857 | 43.9439 | 43.8624 | 43.8578 | 44.1712 | 44.5153 | 45.2222 | 45.7303 | 46.0055 | 46.3059 | 46.5813 | 47.0798 | 47.6989 | 47.6545 | 47.6545 | 47.6545 | 47.6545 | 47.6545 | 47.6545 | 47.6545 | 47.6545 | 47.6545 | 47.6545 | 47.6545 | 47.6545 | 47.6545 | 47.6545 | 47.6545 | 47.6545 | 55% | 311.6074 | 34.5955 | 44.755 | 47.4116 | 47.251 | 47.2606 | 47.532 | 48.2506 | 48.7304 | 49.2008 | 49.7513 | 50.2604 | 50.7555 | 50.8107 | 51.3887 | 50.9479 | 50.9479 | 50.9479 | 50.9479 | 50.9479 | 50.9479 | 50.9479 | 50.9479 | 50.9479 | 50.9479 | 50.9479 | 50.9479 | 50.9479 | 50.9479 | 50.9479 | 50.9479
50% | 1666.1918 | 28.2242 | 37.4415 | 39.949 | 39.8749 | 39.8707 | 40.1557 | 40.4684 | 41.1111 | 41.573 | 41.8231 | 42.0962 | 42.3466 | 42.7999 | 43.3626 | 43.3222 | 43.3222 | 43.3222 | 43.3222 | 43.3222 | 43.3222 | 43.3222 | 43.3222 | 43.3222 | 43.3222 | 43.3222 | 43.3222 | 43.3222 | 43.3222 | 43.3222 | 43.3222 | 50% | 636.0723 | 31.4505 | 40.6864 | 43.1015 | 42.9554 | 42.9642 | 43.211 | 43.8642 | 44.3004 | 44.728 | 45.2284 | 45.6913 | 46.1413 | 46.1915 | 46.717 | 46.3162 | 46.3162 | 46.3162 | 46.3162 | 46.3162 | 46.3162 | 46.3162 | 46.3162 | 46.3162 | 46.3162 | 46.3162 | 46.3162 | 46.3162 | 46.3162 | 46.3162 | 46.3162
45% | 2506.0947 | 25.4017 | 33.6974 | 35.9541 | 35.8874 | 35.8837 | 36.1401 | 36.4216 | 37 | 37.4157 | 37.6408 | 37.8866 | 38.112 | 38.5199 | 39.0264 | 38.99 | 38.99 | 38.99 | 38.99 | 38.99 | 38.99 | 38.99 | 38.99 | 38.99 | 38.99 | 38.99 | 38.99 | 38.99 | 38.99 | 38.99 | 38.99 | 45% | 1179.4944 | 28.3054 | 36.6177 | 38.7913 | 38.6599 | 38.6678 | 38.8899 | 39.4778 | 39.8703 | 40.2552 | 40.7056 | 41.1222 | 41.5272 | 41.5724 | 42.0453 | 41.6846 | 41.6846 | 41.6846 | 41.6846 | 41.6846 | 41.6846 | 41.6846 | 41.6846 | 41.6846 | 41.6846 | 41.6846 | 41.6846 | 41.6846 | 41.6846 | 41.6846 | 41.6846
40% | 3164.4787 | 22.5793 | 29.9532 | 31.9592 | 31.8999 | 31.8966 | 32.1245 | 32.3748 | 32.8889 | 33.2584 | 33.4585 | 33.677 | 33.8773 | 34.2399 | 34.6901 | 34.6578 | 34.6578 | 34.6578 | 34.6578 | 34.6578 | 34.6578 | 34.6578 | 34.6578 | 34.6578 | 34.6578 | 34.6578 | 34.6578 | 34.6578 | 34.6578 | 34.6578 | 34.6578 | 40% | 1808.3816 | 25.1604 | 32.5491 | 34.4812 | 34.3644 | 34.3713 | 34.5688 | 35.0914 | 35.4403 | 35.7824 | 36.1827 | 36.553 | 36.9131 | 36.9532 | 37.3736 | 37.053 | 37.053 | 37.053 | 37.053 | 37.053 | 37.053 | 37.053 | 37.053 | 37.053 | 37.053 | 37.053 | 37.053 | 37.053 | 37.053 | 37.053 | 37.053
35% | 3551.3408 | 19.7569 | 26.2091 | 27.9643 | 27.9124 | 27.9095 | 28.109 | 28.3279 | 28.7778 | 29.1011 | 29.2762 | 29.4674 | 29.6426 | 29.9599 | 30.3538 | 30.3256 | 30.3256 | 30.3256 | 30.3256 | 30.3256 | 30.3256 | 30.3256 | 30.3256 | 30.3256 | 30.3256 | 30.3256 | 30.3256 | 30.3256 | 30.3256 | 30.3256 | 30.3256 | 35% | 2779.1293 | 22.0153 | 28.4805 | 30.171 | 30.0688 | 30.0749 | 30.2477 | 30.705 | 31.0103 | 31.3096 | 31.6599 | 31.9839 | 32.2989 | 32.3341 | 32.7019 | 32.4214 | 32.4214 | 32.4214 | 32.4214 | 32.4214 | 32.4214 | 32.4214 | 32.4214 | 32.4214 | 32.4214 | 32.4214 | 32.4214 | 32.4214 | 32.4214 | 32.4214 | 32.4214
30% | 3758.953 | 16.9345 | 22.4649 | 23.9694 | 23.9249 | 23.9224 | 24.0934 | 24.2811 | 24.6667 | 24.9438 | 25.0939 | 25.2577 | 25.408 | 25.6799 | 26.0176 | 25.9933 | 25.9933 | 25.9933 | 25.9933 | 25.9933 | 25.9933 | 25.9933 | 25.9933 | 25.9933 | 25.9933 | 25.9933 | 25.9933 | 25.9933 | 25.9933 | 25.9933 | 25.9933 | 30% | 3814.165 | 18.8703 | 24.4118 | 25.8609 | 25.7733 | 25.7785 | 25.9266 | 26.3185 | 26.5802 | 26.8368 | 27.1371 | 27.4148 | 27.6848 | 27.7149 | 28.0302 | 27.7897 | 27.7897 | 27.7897 | 27.7897 | 27.7897 | 27.7897 | 27.7897 | 27.7897 | 27.7897 | 27.7897 | 27.7897 | 27.7897 | 27.7897 | 27.7897 | 27.7897 | 27.7897
25% | 3926.4798 | 14.1121 | 18.7208 | 19.9745 | 19.9375 | 19.9354 | 20.0778 | 20.2342 | 20.5556 | 20.7865 | 20.9116 | 21.0481 | 21.1733 | 21.3999 | 21.6813 | 21.6611 | 21.6611 | 21.6611 | 21.6611 | 21.6611 | 21.6611 | 21.6611 | 21.6611 | 21.6611 | 21.6611 | 21.6611 | 21.6611 | 21.6611 | 21.6611 | 21.6611 | 21.6611 | 25% | 4166.9923 | 15.7252 | 20.3432 | 21.5507 | 21.4777 | 21.4821 | 21.6055 | 21.9321 | 22.1502 | 22.364 | 22.6142 | 22.8457 | 23.0707 | 23.0958 | 23.3585 | 23.1581 | 23.1581 | 23.1581 | 23.1581 | 23.1581 | 23.1581 | 23.1581 | 23.1581 | 23.1581 | 23.1581 | 23.1581 | 23.1581 | 23.1581 | 23.1581 | 23.1581 | 23.1581
20% | 4050.5177 | 11.2897 | 14.9766 | 15.9796 | 15.95 | 15.9483 | 16.0623 | 16.1874 | 16.4445 | 16.6292 | 16.7293 | 16.8385 | 16.9386 | 17.1199 | 17.3451 | 17.3289 | 17.3289 | 17.3289 | 17.3289 | 17.3289 | 17.3289 | 17.3289 | 17.3289 | 17.3289 | 17.3289 | 17.3289 | 17.3289 | 17.3289 | 17.3289 | 17.3289 | 17.3289 | 20% | 4282.7105 | 12.5802 | 16.2746 | 17.2406 | 17.1822 | 17.1857 | 17.2844 | 17.5457 | 17.7202 | 17.8912 | 18.0914 | 18.2765 | 18.4565 | 18.4766 | 18.6868 | 18.5265 | 18.5265 | 18.5265 | 18.5265 | 18.5265 | 18.5265 | 18.5265 | 18.5265 | 18.5265 | 18.5265 | 18.5265 | 18.5265 | 18.5265 | 18.5265 | 18.5265 | 18.5265
15% | 4152.622 | 8.4672 | 11.2325 | 11.9847 | 11.9625 | 11.9612 | 12.0467 | 12.1405 | 12.3333 | 12.4719 | 12.5469 | 12.6289 | 12.704 | 12.84 | 13.0088 | 12.9967 | 12.9967 | 12.9967 | 12.9967 | 12.9967 | 12.9967 | 12.9967 | 12.9967 | 12.9967 | 12.9967 | 12.9967 | 12.9967 | 12.9967 | 12.9967 | 12.9967 | 12.9967 | 15% | 4364.7722 | 9.4351 | 12.2059 | 12.9304 | 12.8866 | 12.8893 | 12.9633 | 13.1593 | 13.2901 | 13.4184 | 13.5685 | 13.7074 | 13.8424 | 13.8575 | 14.0151 | 13.8949 | 13.8949 | 13.8949 | 13.8949 | 13.8949 | 13.8949 | 13.8949 | 13.8949 | 13.8949 | 13.8949 | 13.8949 | 13.8949 | 13.8949 | 13.8949 | 13.8949 | 13.8949
10% | 4248.2976 | 5.6448 | 7.4883 | 7.9898 | 7.975 | 7.9741 | 8.0311 | 8.0937 | 8.2222 | 8.3146 | 8.3646 | 8.4192 | 8.4693 | 8.56 | 8.6725 | 8.6644 | 8.6644 | 8.6644 | 8.6644 | 8.6644 | 8.6644 | 8.6644 | 8.6644 | 8.6644 | 8.6644 | 8.6644 | 8.6644 | 8.6644 | 8.6644 | 8.6644 | 8.6644 | 10% | 4391.6218 | 6.2901 | 8.1373 | 8.6203 | 8.5911 | 8.5928 | 8.6422 | 8.7728 | 8.8601 | 8.9456 | 9.0457 | 9.1383 | 9.2283 | 9.2383 | 9.3434 | 9.2632 | 9.2632 | 9.2632 | 9.2632 | 9.2632 | 9.2632 | 9.2632 | 9.2632 | 9.2632 | 9.2632 | 9.2632 | 9.2632 | 9.2632 | 9.2632 | 9.2632 | 9.2632
5% | 4361.7469 | 2.8224 | 3.7442 | 3.9949 | 3.9875 | 3.9871 | 4.0156 | 4.0468 | 4.1111 | 4.1573 | 4.1823 | 4.2096 | 4.2347 | 4.28 | 4.3363 | 4.3322 | 4.3322 | 4.3322 | 4.3322 | 4.3322 | 4.3322 | 4.3322 | 4.3322 | 4.3322 | 4.3322 | 4.3322 | 4.3322 | 4.3322 | 4.3322 | 4.3322 | 4.3322 | 5% | 4391.6218 | 3.145 | 4.0686 | 4.3101 | 4.2955 | 4.2964 | 4.3211 | 4.3864 | 4.43 | 4.4728 | 4.5228 | 4.5691 | 4.6141 | 4.6192 | 4.6717 | 4.6316 | 4.6316 | 4.6316 | 4.6316 | 4.6316 | 4.6316 | 4.6316 | 4.6316 | 4.6316 | 4.6316 | 4.6316 | 4.6316 | 4.6316 | 4.6316 | 4.6316 | 4.6316
9.992e-14% | 4391.6218 | 5.6403e-14 | 7.4823e-14 | 7.9834e-14 | 7.9686e-14 | 7.9678e-14 | 8.0247e-14 | 8.0872e-14 | 8.2157e-14 | 8.308e-14 | 8.3579e-14 | 8.4125e-14 | 8.4626e-14 | 8.5531e-14 | 8.6656e-14 | 8.6575e-14 | 8.6575e-14 | 8.6575e-14 | 8.6575e-14 | 8.6575e-14 | 8.6575e-14 | 8.6575e-14 | 8.6575e-14 | 8.6575e-14 | 8.6575e-14 | 8.6575e-14 | 8.6575e-14 | 8.6575e-14 | 8.6575e-14 | 8.6575e-14 | 8.6575e-14 | 9.992e-14% | 4391.6218 | 6.2851e-14 | 8.1308e-14 | 8.6134e-14 | 8.5842e-14 | 8.586e-14 | 8.6353e-14 | 8.7658e-14 | 8.853e-14 | 8.9385e-14 | 9.0385e-14 | 9.131e-14 | 9.2209e-14 | 9.2309e-14 | 9.3359e-14 | 9.2558e-14 | 9.2558e-14 | 9.2558e-14 | 9.2558e-14 | 9.2558e-14 | 9.2558e-14 | 9.2558e-14 | 9.2558e-14 | 9.2558e-14 | 9.2558e-14 | 9.2558e-14 | 9.2558e-14 | 9.2558e-14 | 9.2558e-14 | 9.2558e-14 | 9.2558e-14
Option 7
Winter Season | [31 empty] | Winter Season
P50 | [31 empty] | P10
% of MD | Winter - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Winter - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 49.7042 | 68.8514 | 73.8223 | 74.6663 | 75.3214 | 76.4563 | 79.0441 | 80.7726 | 82.9664 | 84.1029 | 85.1001 | 83.2461 | 85.4092 | 88.8125 | 86.2221 | 86.2221 | 86.2221 | 86.2221 | 86.2221 | 86.2221 | 86.2221 | 86.2221 | 86.2221 | 86.2221 | 86.2221 | 86.2221 | 86.2221 | 86.2221 | 86.2221 | 86.2221 | 100% | 0 | 53.1876 | 72.0932 | 77.2584 | 78.0542 | 78.5557 | 79.6659 | 82.2942 | 83.7249 | 86.4587 | 94.7777 | 87.9092 | 86.5626 | 88.3699 | 92.3278 | 89.6413 | 89.6413 | 89.6413 | 89.6413 | 89.6413 | 89.6413 | 89.6413 | 89.6413 | 89.6413 | 89.6413 | 89.6413 | 89.6413 | 89.6413 | 89.6413 | 89.6413 | 89.6413
99% | 1.486 | 49.2072 | 68.1629 | 73.0841 | 73.9197 | 74.5682 | 75.6918 | 78.2537 | 79.9649 | 82.1367 | 83.2619 | 84.2491 | 82.4136 | 84.5551 | 87.9243 | 85.3598 | 85.3598 | 85.3598 | 85.3598 | 85.3598 | 85.3598 | 85.3598 | 85.3598 | 85.3598 | 85.3598 | 85.3598 | 85.3598 | 85.3598 | 85.3598 | 85.3598 | 85.3598 | 99% | 1.486 | 52.6557 | 71.3723 | 76.4858 | 77.2737 | 77.7701 | 78.8692 | 81.4712 | 82.8877 | 85.5941 | 93.83 | 87.0301 | 85.697 | 87.4862 | 91.4045 | 88.7449 | 88.7449 | 88.7449 | 88.7449 | 88.7449 | 88.7449 | 88.7449 | 88.7449 | 88.7449 | 88.7449 | 88.7449 | 88.7449 | 88.7449 | 88.7449 | 88.7449 | 88.7449
98% | 3.2692 | 48.7101 | 67.4743 | 72.3458 | 73.173 | 73.815 | 74.9272 | 77.4632 | 79.1572 | 81.3071 | 82.4209 | 83.3981 | 81.5812 | 83.701 | 87.0362 | 84.4976 | 84.4976 | 84.4976 | 84.4976 | 84.4976 | 84.4976 | 84.4976 | 84.4976 | 84.4976 | 84.4976 | 84.4976 | 84.4976 | 84.4976 | 84.4976 | 84.4976 | 84.4976 | 98% | 3.2692 | 52.1238 | 70.6514 | 75.7133 | 76.4931 | 76.9846 | 78.0726 | 80.6483 | 82.0504 | 84.7295 | 92.8822 | 86.151 | 84.8313 | 86.6025 | 90.4812 | 87.8485 | 87.8485 | 87.8485 | 87.8485 | 87.8485 | 87.8485 | 87.8485 | 87.8485 | 87.8485 | 87.8485 | 87.8485 | 87.8485 | 87.8485 | 87.8485 | 87.8485 | 87.8485
97% | 6.8356 | 48.2131 | 66.7858 | 71.6076 | 72.4263 | 73.0618 | 74.1627 | 76.6728 | 78.3495 | 80.4774 | 81.5798 | 82.5471 | 80.7487 | 82.847 | 86.1481 | 83.6354 | 83.6354 | 83.6354 | 83.6354 | 83.6354 | 83.6354 | 83.6354 | 83.6354 | 83.6354 | 83.6354 | 83.6354 | 83.6354 | 83.6354 | 83.6354 | 83.6354 | 83.6354 | 97% | 6.8356 | 51.5919 | 69.9304 | 74.9407 | 75.7126 | 76.199 | 77.2759 | 79.8254 | 81.2132 | 83.865 | 91.9344 | 85.2719 | 83.9657 | 85.7188 | 89.558 | 86.9521 | 86.9521 | 86.9521 | 86.9521 | 86.9521 | 86.9521 | 86.9521 | 86.9521 | 86.9521 | 86.9521 | 86.9521 | 86.9521 | 86.9521 | 86.9521 | 86.9521 | 86.9521
95% | 17.5347 | 47.219 | 65.4088 | 70.1312 | 70.933 | 71.5553 | 72.6335 | 75.0919 | 76.734 | 78.8181 | 79.8978 | 80.8451 | 79.0838 | 81.1388 | 84.3718 | 81.911 | 81.911 | 81.911 | 81.911 | 81.911 | 81.911 | 81.911 | 81.911 | 81.911 | 81.911 | 81.911 | 81.911 | 81.911 | 81.911 | 81.911 | 81.911 | 95% | 17.5347 | 50.5282 | 68.4886 | 73.3955 | 74.1515 | 74.6279 | 75.6826 | 78.1795 | 79.5387 | 82.1358 | 90.0389 | 83.5138 | 82.2345 | 83.9514 | 87.7114 | 85.1592 | 85.1592 | 85.1592 | 85.1592 | 85.1592 | 85.1592 | 85.1592 | 85.1592 | 85.1592 | 85.1592 | 85.1592 | 85.1592 | 85.1592 | 85.1592 | 85.1592 | 85.1592
90% | 78.7576 | 44.7338 | 61.9662 | 66.4401 | 67.1997 | 67.7893 | 68.8107 | 71.1397 | 72.6954 | 74.6697 | 75.6926 | 76.5901 | 74.9215 | 76.8683 | 79.9312 | 77.5999 | 77.5999 | 77.5999 | 77.5999 | 77.5999 | 77.5999 | 77.5999 | 77.5999 | 77.5999 | 77.5999 | 77.5999 | 77.5999 | 77.5999 | 77.5999 | 77.5999 | 77.5999 | 90% | 78.7576 | 47.8688 | 64.8839 | 69.5326 | 70.2488 | 70.7001 | 71.6993 | 74.0648 | 75.3524 | 77.8128 | 85.3 | 79.1183 | 77.9063 | 79.5329 | 83.095 | 80.6772 | 80.6772 | 80.6772 | 80.6772 | 80.6772 | 80.6772 | 80.6772 | 80.6772 | 80.6772 | 80.6772 | 80.6772 | 80.6772 | 80.6772 | 80.6772 | 80.6772 | 80.6772
85% | 236.8672 | 42.2486 | 58.5237 | 62.7489 | 63.4664 | 64.0232 | 64.9879 | 67.1875 | 68.6567 | 70.5214 | 71.4875 | 72.3351 | 70.7592 | 72.5978 | 75.4906 | 73.2888 | 73.2888 | 73.2888 | 73.2888 | 73.2888 | 73.2888 | 73.2888 | 73.2888 | 73.2888 | 73.2888 | 73.2888 | 73.2888 | 73.2888 | 73.2888 | 73.2888 | 73.2888 | 85% | 236.8672 | 45.2094 | 61.2792 | 65.6697 | 66.3461 | 66.7723 | 67.716 | 69.9501 | 71.1662 | 73.4899 | 80.5611 | 74.7228 | 73.5782 | 75.1144 | 78.4786 | 76.1951 | 76.1951 | 76.1951 | 76.1951 | 76.1951 | 76.1951 | 76.1951 | 76.1951 | 76.1951 | 76.1951 | 76.1951 | 76.1951 | 76.1951 | 76.1951 | 76.1951 | 76.1951
80% | 497.5104 | 39.7634 | 55.0811 | 59.0578 | 59.7331 | 60.2571 | 61.1651 | 63.2353 | 64.6181 | 66.3731 | 67.2823 | 68.08 | 66.5969 | 68.3274 | 71.05 | 68.9777 | 68.9777 | 68.9777 | 68.9777 | 68.9777 | 68.9777 | 68.9777 | 68.9777 | 68.9777 | 68.9777 | 68.9777 | 68.9777 | 68.9777 | 68.9777 | 68.9777 | 68.9777 | 80% | 497.5104 | 42.55 | 57.6746 | 61.8067 | 62.4434 | 62.8445 | 63.7327 | 65.8353 | 66.9799 | 69.167 | 75.8222 | 70.3274 | 69.2501 | 70.6959 | 73.8622 | 71.7131 | 71.7131 | 71.7131 | 71.7131 | 71.7131 | 71.7131 | 71.7131 | 71.7131 | 71.7131 | 71.7131 | 71.7131 | 71.7131 | 71.7131 | 71.7131 | 71.7131 | 71.7131
75% | 803.6248 | 37.2782 | 51.6385 | 55.3667 | 55.9997 | 56.4911 | 57.3423 | 59.2831 | 60.5795 | 62.2248 | 63.0772 | 63.825 | 62.4346 | 64.0569 | 66.6093 | 64.6665 | 64.6665 | 64.6665 | 64.6665 | 64.6665 | 64.6665 | 64.6665 | 64.6665 | 64.6665 | 64.6665 | 64.6665 | 64.6665 | 64.6665 | 64.6665 | 64.6665 | 64.6665 | 75% | 803.6248 | 39.8907 | 54.0699 | 57.9438 | 58.5407 | 58.9167 | 59.7494 | 61.7206 | 62.7937 | 64.844 | 71.0833 | 65.9319 | 64.9219 | 66.2774 | 69.2458 | 67.231 | 67.231 | 67.231 | 67.231 | 67.231 | 67.231 | 67.231 | 67.231 | 67.231 | 67.231 | 67.231 | 67.231 | 67.231 | 67.231 | 67.231 | 67.231
70% | 1155.2107 | 34.793 | 48.196 | 51.6756 | 52.2664 | 52.725 | 53.5194 | 55.3309 | 56.5408 | 58.0765 | 58.8721 | 59.57 | 58.2723 | 59.7865 | 62.1687 | 60.3554 | 60.3554 | 60.3554 | 60.3554 | 60.3554 | 60.3554 | 60.3554 | 60.3554 | 60.3554 | 60.3554 | 60.3554 | 60.3554 | 60.3554 | 60.3554 | 60.3554 | 60.3554 | 70% | 1155.2107 | 37.2313 | 50.4653 | 54.0809 | 54.638 | 54.989 | 55.7661 | 57.6059 | 58.6074 | 60.5211 | 66.3444 | 61.5365 | 60.5938 | 61.8589 | 64.6295 | 62.7489 | 62.7489 | 62.7489 | 62.7489 | 62.7489 | 62.7489 | 62.7489 | 62.7489 | 62.7489 | 62.7489 | 62.7489 | 62.7489 | 62.7489 | 62.7489 | 62.7489 | 62.7489
65% | 1553.1596 | 32.3077 | 44.7534 | 47.9845 | 48.5331 | 48.9589 | 49.6966 | 51.3787 | 52.5022 | 53.9282 | 54.6669 | 55.315 | 54.11 | 55.516 | 57.7281 | 56.0443 | 56.0443 | 56.0443 | 56.0443 | 56.0443 | 56.0443 | 56.0443 | 56.0443 | 56.0443 | 56.0443 | 56.0443 | 56.0443 | 56.0443 | 56.0443 | 56.0443 | 56.0443 | 65% | 1553.1596 | 34.5719 | 46.8606 | 50.218 | 50.7352 | 51.0612 | 51.7828 | 53.4912 | 54.4212 | 56.1982 | 61.6055 | 57.141 | 56.2657 | 57.4405 | 60.0131 | 58.2669 | 58.2669 | 58.2669 | 58.2669 | 58.2669 | 58.2669 | 58.2669 | 58.2669 | 58.2669 | 58.2669 | 58.2669 | 58.2669 | 58.2669 | 58.2669 | 58.2669 | 58.2669
60% | 2026.2996 | 29.8225 | 41.3108 | 44.2934 | 44.7998 | 45.1928 | 45.8738 | 47.4265 | 48.4636 | 49.7798 | 50.4618 | 51.06 | 49.9477 | 51.2455 | 53.2875 | 51.7332 | 51.7332 | 51.7332 | 51.7332 | 51.7332 | 51.7332 | 51.7332 | 51.7332 | 51.7332 | 51.7332 | 51.7332 | 51.7332 | 51.7332 | 51.7332 | 51.7332 | 51.7332 | 60% | 2026.2996 | 31.9125 | 43.2559 | 46.3551 | 46.8325 | 47.1334 | 47.7995 | 49.3765 | 50.235 | 51.8752 | 56.8666 | 52.7455 | 51.9376 | 53.022 | 55.3967 | 53.7848 | 53.7848 | 53.7848 | 53.7848 | 53.7848 | 53.7848 | 53.7848 | 53.7848 | 53.7848 | 53.7848 | 53.7848 | 53.7848 | 53.7848 | 53.7848 | 53.7848 | 53.7848
55% | 2598.4068 | 27.3373 | 37.8683 | 40.6023 | 41.0665 | 41.4268 | 42.051 | 43.4743 | 44.425 | 45.6315 | 46.2566 | 46.805 | 45.7854 | 46.9751 | 48.8469 | 47.4221 | 47.4221 | 47.4221 | 47.4221 | 47.4221 | 47.4221 | 47.4221 | 47.4221 | 47.4221 | 47.4221 | 47.4221 | 47.4221 | 47.4221 | 47.4221 | 47.4221 | 47.4221 | 55% | 2598.4068 | 29.2532 | 39.6513 | 42.4921 | 42.9298 | 43.2056 | 43.8162 | 45.2618 | 46.0487 | 47.5523 | 52.1278 | 48.3501 | 47.6094 | 48.6035 | 50.7803 | 49.3027 | 49.3027 | 49.3027 | 49.3027 | 49.3027 | 49.3027 | 49.3027 | 49.3027 | 49.3027 | 49.3027 | 49.3027 | 49.3027 | 49.3027 | 49.3027 | 49.3027 | 49.3027
50% | 3233.5201 | 24.8521 | 34.4257 | 36.9111 | 37.3332 | 37.6607 | 38.2282 | 39.5221 | 40.3863 | 41.4832 | 42.0515 | 42.55 | 41.623 | 42.7046 | 44.4062 | 43.111 | 43.111 | 43.111 | 43.111 | 43.111 | 43.111 | 43.111 | 43.111 | 43.111 | 43.111 | 43.111 | 43.111 | 43.111 | 43.111 | 43.111 | 43.111 | 50% | 3233.5201 | 26.5938 | 36.0466 | 38.6292 | 39.0271 | 39.2778 | 39.833 | 41.1471 | 41.8625 | 43.2294 | 47.3889 | 43.9546 | 43.2813 | 44.185 | 46.1639 | 44.8207 | 44.8207 | 44.8207 | 44.8207 | 44.8207 | 44.8207 | 44.8207 | 44.8207 | 44.8207 | 44.8207 | 44.8207 | 44.8207 | 44.8207 | 44.8207 | 44.8207 | 44.8207
45% | 3775.313 | 22.3669 | 30.9831 | 33.22 | 33.5998 | 33.8946 | 34.4054 | 35.5699 | 36.3477 | 37.3349 | 37.8463 | 38.295 | 37.4607 | 38.4342 | 39.9656 | 38.7999 | 38.7999 | 38.7999 | 38.7999 | 38.7999 | 38.7999 | 38.7999 | 38.7999 | 38.7999 | 38.7999 | 38.7999 | 38.7999 | 38.7999 | 38.7999 | 38.7999 | 38.7999 | 45% | 3775.313 | 23.9344 | 32.442 | 34.7663 | 35.1244 | 35.35 | 35.8497 | 37.0324 | 37.6762 | 38.9064 | 42.65 | 39.5591 | 38.9532 | 39.7665 | 41.5475 | 40.3386 | 40.3386 | 40.3386 | 40.3386 | 40.3386 | 40.3386 | 40.3386 | 40.3386 | 40.3386 | 40.3386 | 40.3386 | 40.3386 | 40.3386 | 40.3386 | 40.3386 | 40.3386
40% | 4072.8088 | 19.8817 | 27.5405 | 29.5289 | 29.8665 | 30.1286 | 30.5825 | 31.6176 | 32.3091 | 33.1866 | 33.6412 | 34.04 | 33.2984 | 34.1637 | 35.525 | 34.4888 | 34.4888 | 34.4888 | 34.4888 | 34.4888 | 34.4888 | 34.4888 | 34.4888 | 34.4888 | 34.4888 | 34.4888 | 34.4888 | 34.4888 | 34.4888 | 34.4888 | 34.4888 | 40% | 4072.8088 | 21.275 | 28.8373 | 30.9034 | 31.2217 | 31.4223 | 31.8664 | 32.9177 | 33.49 | 34.5835 | 37.9111 | 35.1637 | 34.625 | 35.348 | 36.9311 | 35.8565 | 35.8565 | 35.8565 | 35.8565 | 35.8565 | 35.8565 | 35.8565 | 35.8565 | 35.8565 | 35.8565 | 35.8565 | 35.8565 | 35.8565 | 35.8565 | 35.8565 | 35.8565
35% | 4198.821 | 17.3965 | 24.098 | 25.8378 | 26.1332 | 26.3625 | 26.7597 | 27.6654 | 28.2704 | 29.0382 | 29.436 | 29.785 | 29.1361 | 29.8932 | 31.0844 | 30.1777 | 30.1777 | 30.1777 | 30.1777 | 30.1777 | 30.1777 | 30.1777 | 30.1777 | 30.1777 | 30.1777 | 30.1777 | 30.1777 | 30.1777 | 30.1777 | 30.1777 | 30.1777 | 35% | 4198.821 | 18.6156 | 25.2326 | 27.0405 | 27.319 | 27.4945 | 27.8831 | 28.803 | 29.3037 | 30.2606 | 33.1722 | 30.7682 | 30.2969 | 30.9295 | 32.3147 | 31.3745 | 31.3745 | 31.3745 | 31.3745 | 31.3745 | 31.3745 | 31.3745 | 31.3745 | 31.3745 | 31.3745 | 31.3745 | 31.3745 | 31.3745 | 31.3745 | 31.3745 | 31.3745
30% | 4271.3374 | 14.9113 | 20.6554 | 22.1467 | 22.3999 | 22.5964 | 22.9369 | 23.7132 | 24.2318 | 24.8899 | 25.2309 | 25.53 | 24.9738 | 25.6228 | 26.6437 | 25.8666 | 25.8666 | 25.8666 | 25.8666 | 25.8666 | 25.8666 | 25.8666 | 25.8666 | 25.8666 | 25.8666 | 25.8666 | 25.8666 | 25.8666 | 25.8666 | 25.8666 | 25.8666 | 30% | 4271.3374 | 15.9563 | 21.628 | 23.1775 | 23.4163 | 23.5667 | 23.8998 | 24.6883 | 25.1175 | 25.9376 | 28.4333 | 26.3728 | 25.9688 | 26.511 | 27.6983 | 26.8924 | 26.8924 | 26.8924 | 26.8924 | 26.8924 | 26.8924 | 26.8924 | 26.8924 | 26.8924 | 26.8924 | 26.8924 | 26.8924 | 26.8924 | 26.8924 | 26.8924 | 26.8924
25% | 4321.8611 | 12.4261 | 17.2128 | 18.4556 | 18.6666 | 18.8304 | 19.1141 | 19.761 | 20.1932 | 20.7416 | 21.0257 | 21.275 | 20.8115 | 21.3523 | 22.2031 | 21.5555 | 21.5555 | 21.5555 | 21.5555 | 21.5555 | 21.5555 | 21.5555 | 21.5555 | 21.5555 | 21.5555 | 21.5555 | 21.5555 | 21.5555 | 21.5555 | 21.5555 | 21.5555 | 25% | 4321.8611 | 13.2969 | 18.0233 | 19.3146 | 19.5136 | 19.6389 | 19.9165 | 20.5735 | 20.9312 | 21.6147 | 23.6944 | 21.9773 | 21.6406 | 22.0925 | 23.0819 | 22.4103 | 22.4103 | 22.4103 | 22.4103 | 22.4103 | 22.4103 | 22.4103 | 22.4103 | 22.4103 | 22.4103 | 22.4103 | 22.4103 | 22.4103 | 22.4103 | 22.4103 | 22.4103
20% | 4353.067 | 9.9408 | 13.7703 | 14.7645 | 14.9333 | 15.0643 | 15.2913 | 15.8088 | 16.1545 | 16.5933 | 16.8206 | 17.02 | 16.6492 | 17.0818 | 17.7625 | 17.2444 | 17.2444 | 17.2444 | 17.2444 | 17.2444 | 17.2444 | 17.2444 | 17.2444 | 17.2444 | 17.2444 | 17.2444 | 17.2444 | 17.2444 | 17.2444 | 17.2444 | 17.2444 | 20% | 4353.067 | 10.6375 | 14.4186 | 15.4517 | 15.6108 | 15.7111 | 15.9332 | 16.4588 | 16.745 | 17.2917 | 18.9555 | 17.5818 | 17.3125 | 17.674 | 18.4656 | 17.9283 | 17.9283 | 17.9283 | 17.9283 | 17.9283 | 17.9283 | 17.9283 | 17.9283 | 17.9283 | 17.9283 | 17.9283 | 17.9283 | 17.9283 | 17.9283 | 17.9283 | 17.9283
15% | 4369.4129 | 7.4556 | 10.3277 | 11.0733 | 11.1999 | 11.2982 | 11.4685 | 11.8566 | 12.1159 | 12.445 | 12.6154 | 12.765 | 12.4869 | 12.8114 | 13.3219 | 12.9333 | 12.9333 | 12.9333 | 12.9333 | 12.9333 | 12.9333 | 12.9333 | 12.9333 | 12.9333 | 12.9333 | 12.9333 | 12.9333 | 12.9333 | 12.9333 | 12.9333 | 12.9333 | 15% | 4369.4129 | 7.9781 | 10.814 | 11.5888 | 11.7081 | 11.7833 | 11.9499 | 12.3441 | 12.5587 | 12.9688 | 14.2167 | 13.1864 | 12.9844 | 13.2555 | 13.8492 | 13.4462 | 13.4462 | 13.4462 | 13.4462 | 13.4462 | 13.4462 | 13.4462 | 13.4462 | 13.4462 | 13.4462 | 13.4462 | 13.4462 | 13.4462 | 13.4462 | 13.4462 | 13.4462
10% | 4378.6261 | 4.9704 | 6.8851 | 7.3822 | 7.4666 | 7.5321 | 7.6456 | 7.9044 | 8.0773 | 8.2966 | 8.4103 | 8.51 | 8.3246 | 8.5409 | 8.8812 | 8.6222 | 8.6222 | 8.6222 | 8.6222 | 8.6222 | 8.6222 | 8.6222 | 8.6222 | 8.6222 | 8.6222 | 8.6222 | 8.6222 | 8.6222 | 8.6222 | 8.6222 | 8.6222 | 10% | 4378.6261 | 5.3188 | 7.2093 | 7.7258 | 7.8054 | 7.8556 | 7.9666 | 8.2294 | 8.3725 | 8.6459 | 9.4778 | 8.7909 | 8.6563 | 8.837 | 9.2328 | 8.9641 | 8.9641 | 8.9641 | 8.9641 | 8.9641 | 8.9641 | 8.9641 | 8.9641 | 8.9641 | 8.9641 | 8.9641 | 8.9641 | 8.9641 | 8.9641 | 8.9641 | 8.9641
5% | 4391.7028 | 2.4852 | 3.4426 | 3.6911 | 3.7333 | 3.7661 | 3.8228 | 3.9522 | 4.0386 | 4.1483 | 4.2051 | 4.255 | 4.1623 | 4.2705 | 4.4406 | 4.3111 | 4.3111 | 4.3111 | 4.3111 | 4.3111 | 4.3111 | 4.3111 | 4.3111 | 4.3111 | 4.3111 | 4.3111 | 4.3111 | 4.3111 | 4.3111 | 4.3111 | 4.3111 | 5% | 4391.7028 | 2.6594 | 3.6047 | 3.8629 | 3.9027 | 3.9278 | 3.9833 | 4.1147 | 4.1862 | 4.3229 | 4.7389 | 4.3955 | 4.3281 | 4.4185 | 4.6164 | 4.4821 | 4.4821 | 4.4821 | 4.4821 | 4.4821 | 4.4821 | 4.4821 | 4.4821 | 4.4821 | 4.4821 | 4.4821 | 4.4821 | 4.4821 | 4.4821 | 4.4821 | 4.4821
9.992e-14% | 4391.7028 | 4.9664e-14 | 6.8796e-14 | 7.3763e-14 | 7.4607e-14 | 7.5261e-14 | 7.6395e-14 | 7.8981e-14 | 8.0708e-14 | 8.29e-14 | 8.4036e-14 | 8.5032e-14 | 8.318e-14 | 8.5341e-14 | 8.8741e-14 | 8.6153e-14 | 8.6153e-14 | 8.6153e-14 | 8.6153e-14 | 8.6153e-14 | 8.6153e-14 | 8.6153e-14 | 8.6153e-14 | 8.6153e-14 | 8.6153e-14 | 8.6153e-14 | 8.6153e-14 | 8.6153e-14 | 8.6153e-14 | 8.6153e-14 | 8.6153e-14 | 9.992e-14% | 4391.7028 | 5.3145e-14 | 7.2036e-14 | 7.7197e-14 | 7.7992e-14 | 7.8493e-14 | 7.9602e-14 | 8.2228e-14 | 8.3658e-14 | 8.639e-14 | 9.4702e-14 | 8.7839e-14 | 8.6493e-14 | 8.8299e-14 | 9.2254e-14 | 8.957e-14 | 8.957e-14 | 8.957e-14 | 8.957e-14 | 8.957e-14 | 8.957e-14 | 8.957e-14 | 8.957e-14 | 8.957e-14 | 8.957e-14 | 8.957e-14 | 8.957e-14 | 8.957e-14 | 8.957e-14 | 8.957e-14 | 8.957e-14
Summer Season | [31 empty] | Summer Season
P50 | [31 empty] | P10
% of MD | Summer - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Summer - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 56.4483 | 74.8831 | 79.898 | 79.7498 | 79.7414 | 80.3113 | 80.9369 | 82.2223 | 83.1461 | 83.6463 | 84.1925 | 84.6932 | 85.5997 | 86.7253 | 86.6445 | 86.6445 | 86.6445 | 86.6445 | 86.6445 | 86.6445 | 86.6445 | 86.6445 | 86.6445 | 86.6445 | 86.6445 | 86.6445 | 86.6445 | 86.6445 | 86.6445 | 86.6445 | 100% | 0 | 62.901 | 81.3728 | 86.203 | 85.9109 | 85.9284 | 86.4219 | 87.7284 | 88.6008 | 89.4561 | 90.4569 | 91.3826 | 92.2827 | 92.383 | 93.434 | 92.6325 | 92.6325 | 92.6325 | 92.6325 | 92.6325 | 92.6325 | 92.6325 | 92.6325 | 92.6325 | 92.6325 | 92.6325 | 92.6325 | 92.6325 | 92.6325 | 92.6325 | 92.6325
99% | 0 | 55.8838 | 74.1343 | 79.099 | 78.9523 | 78.944 | 79.5082 | 80.1275 | 81.4 | 82.3146 | 82.8098 | 83.3506 | 83.8463 | 84.7437 | 85.858 | 85.778 | 85.778 | 85.778 | 85.778 | 85.778 | 85.778 | 85.778 | 85.778 | 85.778 | 85.778 | 85.778 | 85.778 | 85.778 | 85.778 | 85.778 | 85.778 | 99% | 1.5127 | 62.272 | 80.559 | 85.341 | 85.0518 | 85.0691 | 85.5577 | 86.8512 | 87.7148 | 88.5615 | 89.5523 | 90.4688 | 91.3598 | 91.4592 | 92.4996 | 91.7061 | 91.7061 | 91.7061 | 91.7061 | 91.7061 | 91.7061 | 91.7061 | 91.7061 | 91.7061 | 91.7061 | 91.7061 | 91.7061 | 91.7061 | 91.7061 | 91.7061 | 91.7061
98% | 0 | 55.3193 | 73.3854 | 78.3 | 78.1548 | 78.1466 | 78.7051 | 79.3181 | 80.5778 | 81.4832 | 81.9734 | 82.5086 | 82.9994 | 83.8877 | 84.9908 | 84.9116 | 84.9116 | 84.9116 | 84.9116 | 84.9116 | 84.9116 | 84.9116 | 84.9116 | 84.9116 | 84.9116 | 84.9116 | 84.9116 | 84.9116 | 84.9116 | 84.9116 | 84.9116 | 98% | 2.269 | 61.643 | 79.7453 | 84.4789 | 84.1927 | 84.2098 | 84.6935 | 85.9739 | 86.8287 | 87.667 | 88.6477 | 89.555 | 90.437 | 90.5354 | 91.5653 | 90.7798 | 90.7798 | 90.7798 | 90.7798 | 90.7798 | 90.7798 | 90.7798 | 90.7798 | 90.7798 | 90.7798 | 90.7798 | 90.7798 | 90.7798 | 90.7798 | 90.7798 | 90.7798
97% | 0.37816 | 54.7549 | 72.6366 | 77.501 | 77.3573 | 77.3492 | 77.902 | 78.5088 | 79.7556 | 80.6517 | 81.1369 | 81.6667 | 82.1524 | 83.0317 | 84.1235 | 84.0451 | 84.0451 | 84.0451 | 84.0451 | 84.0451 | 84.0451 | 84.0451 | 84.0451 | 84.0451 | 84.0451 | 84.0451 | 84.0451 | 84.0451 | 84.0451 | 84.0451 | 84.0451 | 97% | 3.7816 | 61.014 | 78.9316 | 83.6169 | 83.3336 | 83.3505 | 83.8292 | 85.0966 | 85.9427 | 86.7724 | 87.7432 | 88.6411 | 89.5142 | 89.6115 | 90.631 | 89.8535 | 89.8535 | 89.8535 | 89.8535 | 89.8535 | 89.8535 | 89.8535 | 89.8535 | 89.8535 | 89.8535 | 89.8535 | 89.8535 | 89.8535 | 89.8535 | 89.8535 | 89.8535
95% | 2.269 | 53.6259 | 71.1389 | 75.9031 | 75.7623 | 75.7544 | 76.2958 | 76.89 | 78.1112 | 78.9888 | 79.464 | 79.9829 | 80.4586 | 81.3197 | 82.389 | 82.3122 | 82.3122 | 82.3122 | 82.3122 | 82.3122 | 82.3122 | 82.3122 | 82.3122 | 82.3122 | 82.3122 | 82.3122 | 82.3122 | 82.3122 | 82.3122 | 82.3122 | 82.3122 | 95% | 6.0506 | 59.7559 | 77.3041 | 81.8928 | 81.6153 | 81.632 | 82.1008 | 83.342 | 84.1707 | 84.9833 | 85.934 | 86.8135 | 87.6685 | 87.7639 | 88.7623 | 88.0008 | 88.0008 | 88.0008 | 88.0008 | 88.0008 | 88.0008 | 88.0008 | 88.0008 | 88.0008 | 88.0008 | 88.0008 | 88.0008 | 88.0008 | 88.0008 | 88.0008 | 88.0008
90% | 5.6725 | 50.8035 | 67.3948 | 71.9082 | 71.7748 | 71.7673 | 72.2802 | 72.8432 | 74 | 74.8315 | 75.2817 | 75.7732 | 76.2239 | 77.0397 | 78.0527 | 77.98 | 77.98 | 77.98 | 77.98 | 77.98 | 77.98 | 77.98 | 77.98 | 77.98 | 77.98 | 77.98 | 77.98 | 77.98 | 77.98 | 77.98 | 77.98 | 90% | 16.2611 | 56.6109 | 73.2355 | 77.5827 | 77.3198 | 77.3355 | 77.7797 | 78.9556 | 79.7407 | 80.5105 | 81.4112 | 82.2444 | 83.0544 | 83.1447 | 84.0906 | 83.3692 | 83.3692 | 83.3692 | 83.3692 | 83.3692 | 83.3692 | 83.3692 | 83.3692 | 83.3692 | 83.3692 | 83.3692 | 83.3692 | 83.3692 | 83.3692 | 83.3692 | 83.3692
85% | 15.8829 | 47.9811 | 63.6506 | 67.9133 | 67.7874 | 67.7802 | 68.2646 | 68.7963 | 69.8889 | 70.6742 | 71.0994 | 71.5636 | 71.9893 | 72.7598 | 73.7165 | 73.6478 | 73.6478 | 73.6478 | 73.6478 | 73.6478 | 73.6478 | 73.6478 | 73.6478 | 73.6478 | 73.6478 | 73.6478 | 73.6478 | 73.6478 | 73.6478 | 73.6478 | 73.6478 | 85% | 26.4715 | 53.4658 | 69.1669 | 73.2725 | 73.0243 | 73.0391 | 73.4586 | 74.5692 | 75.3106 | 76.0377 | 76.8883 | 77.6752 | 78.4403 | 78.5256 | 79.4189 | 78.7376 | 78.7376 | 78.7376 | 78.7376 | 78.7376 | 78.7376 | 78.7376 | 78.7376 | 78.7376 | 78.7376 | 78.7376 | 78.7376 | 78.7376 | 78.7376 | 78.7376 | 78.7376
80% | 31.0095 | 45.1586 | 59.9065 | 63.9184 | 63.7999 | 63.7932 | 64.2491 | 64.7495 | 65.7778 | 66.5169 | 66.917 | 67.354 | 67.7546 | 68.4798 | 69.3802 | 69.3156 | 69.3156 | 69.3156 | 69.3156 | 69.3156 | 69.3156 | 69.3156 | 69.3156 | 69.3156 | 69.3156 | 69.3156 | 69.3156 | 69.3156 | 69.3156 | 69.3156 | 69.3156 | 80% | 34.0348 | 50.3208 | 65.0982 | 68.9624 | 68.7287 | 68.7427 | 69.1375 | 70.1827 | 70.8806 | 71.5649 | 72.3655 | 73.1061 | 73.8261 | 73.9064 | 74.7472 | 74.106 | 74.106 | 74.106 | 74.106 | 74.106 | 74.106 | 74.106 | 74.106 | 74.106 | 74.106 | 74.106 | 74.106 | 74.106 | 74.106 | 74.106 | 74.106
75% | 72.9857 | 42.3362 | 56.1623 | 59.9235 | 59.8124 | 59.8061 | 60.2335 | 60.7027 | 61.6667 | 62.3596 | 62.7347 | 63.1444 | 63.5199 | 64.1998 | 65.044 | 64.9833 | 64.9833 | 64.9833 | 64.9833 | 64.9833 | 64.9833 | 64.9833 | 64.9833 | 64.9833 | 64.9833 | 64.9833 | 64.9833 | 64.9833 | 64.9833 | 64.9833 | 64.9833 | 75% | 48.405 | 47.1757 | 61.0296 | 64.6522 | 64.4332 | 64.4463 | 64.8164 | 65.7963 | 66.4506 | 67.0921 | 67.8427 | 68.537 | 69.212 | 69.2873 | 70.0755 | 69.4744 | 69.4744 | 69.4744 | 69.4744 | 69.4744 | 69.4744 | 69.4744 | 69.4744 | 69.4744 | 69.4744 | 69.4744 | 69.4744 | 69.4744 | 69.4744 | 69.4744 | 69.4744
70% | 150.5094 | 39.5138 | 52.4182 | 55.9286 | 55.8249 | 55.819 | 56.2179 | 56.6558 | 57.5556 | 58.2023 | 58.5524 | 58.9347 | 59.2853 | 59.9198 | 60.7077 | 60.6511 | 60.6511 | 60.6511 | 60.6511 | 60.6511 | 60.6511 | 60.6511 | 60.6511 | 60.6511 | 60.6511 | 60.6511 | 60.6511 | 60.6511 | 60.6511 | 60.6511 | 60.6511 | 70% | 76.3892 | 44.0307 | 56.9609 | 60.3421 | 60.1376 | 60.1499 | 60.4953 | 61.4099 | 62.0205 | 62.6193 | 63.3198 | 63.9678 | 64.5979 | 64.6681 | 65.4038 | 64.8427 | 64.8427 | 64.8427 | 64.8427 | 64.8427 | 64.8427 | 64.8427 | 64.8427 | 64.8427 | 64.8427 | 64.8427 | 64.8427 | 64.8427 | 64.8427 | 64.8427 | 64.8427
65% | 359.6342 | 36.6914 | 48.674 | 51.9337 | 51.8374 | 51.8319 | 52.2024 | 52.609 | 53.4445 | 54.045 | 54.3701 | 54.7251 | 55.0506 | 55.6398 | 56.3714 | 56.3189 | 56.3189 | 56.3189 | 56.3189 | 56.3189 | 56.3189 | 56.3189 | 56.3189 | 56.3189 | 56.3189 | 56.3189 | 56.3189 | 56.3189 | 56.3189 | 56.3189 | 56.3189 | 65% | 114.2056 | 40.8856 | 52.8923 | 56.0319 | 55.8421 | 55.8534 | 56.1742 | 57.0235 | 57.5905 | 58.1465 | 58.797 | 59.3987 | 59.9837 | 60.049 | 60.7321 | 60.2111 | 60.2111 | 60.2111 | 60.2111 | 60.2111 | 60.2111 | 60.2111 | 60.2111 | 60.2111 | 60.2111 | 60.2111 | 60.2111 | 60.2111 | 60.2111 | 60.2111 | 60.2111
60% | 689.7717 | 33.869 | 44.9299 | 47.9388 | 47.8499 | 47.8449 | 48.1868 | 48.5621 | 49.3334 | 49.8876 | 50.1878 | 50.5155 | 50.8159 | 51.3598 | 52.0352 | 51.9867 | 51.9867 | 51.9867 | 51.9867 | 51.9867 | 51.9867 | 51.9867 | 51.9867 | 51.9867 | 51.9867 | 51.9867 | 51.9867 | 51.9867 | 51.9867 | 51.9867 | 51.9867 | 60% | 178.1154 | 37.7406 | 48.8237 | 51.7218 | 51.5465 | 51.557 | 51.8531 | 52.6371 | 53.1605 | 53.6736 | 54.2741 | 54.8296 | 55.3696 | 55.4298 | 56.0604 | 55.5795 | 55.5795 | 55.5795 | 55.5795 | 55.5795 | 55.5795 | 55.5795 | 55.5795 | 55.5795 | 55.5795 | 55.5795 | 55.5795 | 55.5795 | 55.5795 | 55.5795 | 55.5795
55% | 1095.5419 | 31.0466 | 41.1857 | 43.9439 | 43.8624 | 43.8578 | 44.1712 | 44.5153 | 45.2222 | 45.7303 | 46.0055 | 46.3059 | 46.5813 | 47.0798 | 47.6989 | 47.6545 | 47.6545 | 47.6545 | 47.6545 | 47.6545 | 47.6545 | 47.6545 | 47.6545 | 47.6545 | 47.6545 | 47.6545 | 47.6545 | 47.6545 | 47.6545 | 47.6545 | 47.6545 | 55% | 311.6074 | 34.5955 | 44.755 | 47.4116 | 47.251 | 47.2606 | 47.532 | 48.2506 | 48.7304 | 49.2008 | 49.7513 | 50.2604 | 50.7555 | 50.8107 | 51.3887 | 50.9479 | 50.9479 | 50.9479 | 50.9479 | 50.9479 | 50.9479 | 50.9479 | 50.9479 | 50.9479 | 50.9479 | 50.9479 | 50.9479 | 50.9479 | 50.9479 | 50.9479 | 50.9479
50% | 1666.1918 | 28.2242 | 37.4415 | 39.949 | 39.8749 | 39.8707 | 40.1557 | 40.4684 | 41.1111 | 41.573 | 41.8231 | 42.0962 | 42.3466 | 42.7999 | 43.3626 | 43.3222 | 43.3222 | 43.3222 | 43.3222 | 43.3222 | 43.3222 | 43.3222 | 43.3222 | 43.3222 | 43.3222 | 43.3222 | 43.3222 | 43.3222 | 43.3222 | 43.3222 | 43.3222 | 50% | 636.0723 | 31.4505 | 40.6864 | 43.1015 | 42.9554 | 42.9642 | 43.211 | 43.8642 | 44.3004 | 44.728 | 45.2284 | 45.6913 | 46.1413 | 46.1915 | 46.717 | 46.3162 | 46.3162 | 46.3162 | 46.3162 | 46.3162 | 46.3162 | 46.3162 | 46.3162 | 46.3162 | 46.3162 | 46.3162 | 46.3162 | 46.3162 | 46.3162 | 46.3162 | 46.3162
45% | 2506.0947 | 25.4017 | 33.6974 | 35.9541 | 35.8874 | 35.8837 | 36.1401 | 36.4216 | 37 | 37.4157 | 37.6408 | 37.8866 | 38.112 | 38.5199 | 39.0264 | 38.99 | 38.99 | 38.99 | 38.99 | 38.99 | 38.99 | 38.99 | 38.99 | 38.99 | 38.99 | 38.99 | 38.99 | 38.99 | 38.99 | 38.99 | 38.99 | 45% | 1179.4944 | 28.3054 | 36.6177 | 38.7913 | 38.6599 | 38.6678 | 38.8899 | 39.4778 | 39.8703 | 40.2552 | 40.7056 | 41.1222 | 41.5272 | 41.5724 | 42.0453 | 41.6846 | 41.6846 | 41.6846 | 41.6846 | 41.6846 | 41.6846 | 41.6846 | 41.6846 | 41.6846 | 41.6846 | 41.6846 | 41.6846 | 41.6846 | 41.6846 | 41.6846 | 41.6846
40% | 3164.4787 | 22.5793 | 29.9532 | 31.9592 | 31.8999 | 31.8966 | 32.1245 | 32.3748 | 32.8889 | 33.2584 | 33.4585 | 33.677 | 33.8773 | 34.2399 | 34.6901 | 34.6578 | 34.6578 | 34.6578 | 34.6578 | 34.6578 | 34.6578 | 34.6578 | 34.6578 | 34.6578 | 34.6578 | 34.6578 | 34.6578 | 34.6578 | 34.6578 | 34.6578 | 34.6578 | 40% | 1808.3816 | 25.1604 | 32.5491 | 34.4812 | 34.3644 | 34.3713 | 34.5688 | 35.0914 | 35.4403 | 35.7824 | 36.1827 | 36.553 | 36.9131 | 36.9532 | 37.3736 | 37.053 | 37.053 | 37.053 | 37.053 | 37.053 | 37.053 | 37.053 | 37.053 | 37.053 | 37.053 | 37.053 | 37.053 | 37.053 | 37.053 | 37.053 | 37.053
35% | 3551.3408 | 19.7569 | 26.2091 | 27.9643 | 27.9124 | 27.9095 | 28.109 | 28.3279 | 28.7778 | 29.1011 | 29.2762 | 29.4674 | 29.6426 | 29.9599 | 30.3538 | 30.3256 | 30.3256 | 30.3256 | 30.3256 | 30.3256 | 30.3256 | 30.3256 | 30.3256 | 30.3256 | 30.3256 | 30.3256 | 30.3256 | 30.3256 | 30.3256 | 30.3256 | 30.3256 | 35% | 2779.1293 | 22.0153 | 28.4805 | 30.171 | 30.0688 | 30.0749 | 30.2477 | 30.705 | 31.0103 | 31.3096 | 31.6599 | 31.9839 | 32.2989 | 32.3341 | 32.7019 | 32.4214 | 32.4214 | 32.4214 | 32.4214 | 32.4214 | 32.4214 | 32.4214 | 32.4214 | 32.4214 | 32.4214 | 32.4214 | 32.4214 | 32.4214 | 32.4214 | 32.4214 | 32.4214
30% | 3758.953 | 16.9345 | 22.4649 | 23.9694 | 23.9249 | 23.9224 | 24.0934 | 24.2811 | 24.6667 | 24.9438 | 25.0939 | 25.2577 | 25.408 | 25.6799 | 26.0176 | 25.9933 | 25.9933 | 25.9933 | 25.9933 | 25.9933 | 25.9933 | 25.9933 | 25.9933 | 25.9933 | 25.9933 | 25.9933 | 25.9933 | 25.9933 | 25.9933 | 25.9933 | 25.9933 | 30% | 3814.165 | 18.8703 | 24.4118 | 25.8609 | 25.7733 | 25.7785 | 25.9266 | 26.3185 | 26.5802 | 26.8368 | 27.1371 | 27.4148 | 27.6848 | 27.7149 | 28.0302 | 27.7897 | 27.7897 | 27.7897 | 27.7897 | 27.7897 | 27.7897 | 27.7897 | 27.7897 | 27.7897 | 27.7897 | 27.7897 | 27.7897 | 27.7897 | 27.7897 | 27.7897 | 27.7897
25% | 3926.4798 | 14.1121 | 18.7208 | 19.9745 | 19.9375 | 19.9354 | 20.0778 | 20.2342 | 20.5556 | 20.7865 | 20.9116 | 21.0481 | 21.1733 | 21.3999 | 21.6813 | 21.6611 | 21.6611 | 21.6611 | 21.6611 | 21.6611 | 21.6611 | 21.6611 | 21.6611 | 21.6611 | 21.6611 | 21.6611 | 21.6611 | 21.6611 | 21.6611 | 21.6611 | 21.6611 | 25% | 4166.9923 | 15.7252 | 20.3432 | 21.5507 | 21.4777 | 21.4821 | 21.6055 | 21.9321 | 22.1502 | 22.364 | 22.6142 | 22.8457 | 23.0707 | 23.0958 | 23.3585 | 23.1581 | 23.1581 | 23.1581 | 23.1581 | 23.1581 | 23.1581 | 23.1581 | 23.1581 | 23.1581 | 23.1581 | 23.1581 | 23.1581 | 23.1581 | 23.1581 | 23.1581 | 23.1581
20% | 4050.5177 | 11.2897 | 14.9766 | 15.9796 | 15.95 | 15.9483 | 16.0623 | 16.1874 | 16.4445 | 16.6292 | 16.7293 | 16.8385 | 16.9386 | 17.1199 | 17.3451 | 17.3289 | 17.3289 | 17.3289 | 17.3289 | 17.3289 | 17.3289 | 17.3289 | 17.3289 | 17.3289 | 17.3289 | 17.3289 | 17.3289 | 17.3289 | 17.3289 | 17.3289 | 17.3289 | 20% | 4282.7105 | 12.5802 | 16.2746 | 17.2406 | 17.1822 | 17.1857 | 17.2844 | 17.5457 | 17.7202 | 17.8912 | 18.0914 | 18.2765 | 18.4565 | 18.4766 | 18.6868 | 18.5265 | 18.5265 | 18.5265 | 18.5265 | 18.5265 | 18.5265 | 18.5265 | 18.5265 | 18.5265 | 18.5265 | 18.5265 | 18.5265 | 18.5265 | 18.5265 | 18.5265 | 18.5265
15% | 4152.622 | 8.4672 | 11.2325 | 11.9847 | 11.9625 | 11.9612 | 12.0467 | 12.1405 | 12.3333 | 12.4719 | 12.5469 | 12.6289 | 12.704 | 12.84 | 13.0088 | 12.9967 | 12.9967 | 12.9967 | 12.9967 | 12.9967 | 12.9967 | 12.9967 | 12.9967 | 12.9967 | 12.9967 | 12.9967 | 12.9967 | 12.9967 | 12.9967 | 12.9967 | 12.9967 | 15% | 4364.7722 | 9.4351 | 12.2059 | 12.9304 | 12.8866 | 12.8893 | 12.9633 | 13.1593 | 13.2901 | 13.4184 | 13.5685 | 13.7074 | 13.8424 | 13.8575 | 14.0151 | 13.8949 | 13.8949 | 13.8949 | 13.8949 | 13.8949 | 13.8949 | 13.8949 | 13.8949 | 13.8949 | 13.8949 | 13.8949 | 13.8949 | 13.8949 | 13.8949 | 13.8949 | 13.8949
10% | 4248.2976 | 5.6448 | 7.4883 | 7.9898 | 7.975 | 7.9741 | 8.0311 | 8.0937 | 8.2222 | 8.3146 | 8.3646 | 8.4192 | 8.4693 | 8.56 | 8.6725 | 8.6644 | 8.6644 | 8.6644 | 8.6644 | 8.6644 | 8.6644 | 8.6644 | 8.6644 | 8.6644 | 8.6644 | 8.6644 | 8.6644 | 8.6644 | 8.6644 | 8.6644 | 8.6644 | 10% | 4391.6218 | 6.2901 | 8.1373 | 8.6203 | 8.5911 | 8.5928 | 8.6422 | 8.7728 | 8.8601 | 8.9456 | 9.0457 | 9.1383 | 9.2283 | 9.2383 | 9.3434 | 9.2632 | 9.2632 | 9.2632 | 9.2632 | 9.2632 | 9.2632 | 9.2632 | 9.2632 | 9.2632 | 9.2632 | 9.2632 | 9.2632 | 9.2632 | 9.2632 | 9.2632 | 9.2632
5% | 4361.7469 | 2.8224 | 3.7442 | 3.9949 | 3.9875 | 3.9871 | 4.0156 | 4.0468 | 4.1111 | 4.1573 | 4.1823 | 4.2096 | 4.2347 | 4.28 | 4.3363 | 4.3322 | 4.3322 | 4.3322 | 4.3322 | 4.3322 | 4.3322 | 4.3322 | 4.3322 | 4.3322 | 4.3322 | 4.3322 | 4.3322 | 4.3322 | 4.3322 | 4.3322 | 4.3322 | 5% | 4391.6218 | 3.145 | 4.0686 | 4.3101 | 4.2955 | 4.2964 | 4.3211 | 4.3864 | 4.43 | 4.4728 | 4.5228 | 4.5691 | 4.6141 | 4.6192 | 4.6717 | 4.6316 | 4.6316 | 4.6316 | 4.6316 | 4.6316 | 4.6316 | 4.6316 | 4.6316 | 4.6316 | 4.6316 | 4.6316 | 4.6316 | 4.6316 | 4.6316 | 4.6316 | 4.6316
9.992e-14% | 4391.6218 | 5.6403e-14 | 7.4823e-14 | 7.9834e-14 | 7.9686e-14 | 7.9678e-14 | 8.0247e-14 | 8.0872e-14 | 8.2157e-14 | 8.308e-14 | 8.3579e-14 | 8.4125e-14 | 8.4626e-14 | 8.5531e-14 | 8.6656e-14 | 8.6575e-14 | 8.6575e-14 | 8.6575e-14 | 8.6575e-14 | 8.6575e-14 | 8.6575e-14 | 8.6575e-14 | 8.6575e-14 | 8.6575e-14 | 8.6575e-14 | 8.6575e-14 | 8.6575e-14 | 8.6575e-14 | 8.6575e-14 | 8.6575e-14 | 8.6575e-14 | 9.992e-14% | 4391.6218 | 6.2851e-14 | 8.1308e-14 | 8.6134e-14 | 8.5842e-14 | 8.586e-14 | 8.6353e-14 | 8.7658e-14 | 8.853e-14 | 8.9385e-14 | 9.0385e-14 | 9.131e-14 | 9.2209e-14 | 9.2309e-14 | 9.3359e-14 | 9.2558e-14 | 9.2558e-14 | 9.2558e-14 | 9.2558e-14 | 9.2558e-14 | 9.2558e-14 | 9.2558e-14 | 9.2558e-14 | 9.2558e-14 | 9.2558e-14 | 9.2558e-14 | 9.2558e-14 | 9.2558e-14 | 9.2558e-14 | 9.2558e-14 | 9.2558e-14
Option 8
Winter Season | [31 empty] | Winter Season
P50 | [31 empty] | P10
% of MD | Winter - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Winter - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 49.7042 | 68.8514 | 73.8223 | 74.6663 | 75.3214 | 76.4563 | 79.0441 | 80.7726 | 82.9664 | 84.1029 | 85.1001 | 83.2461 | 85.4092 | 88.8125 | 86.2221 | 86.2221 | 86.2221 | 86.2221 | 86.2221 | 86.2221 | 86.2221 | 86.2221 | 86.2221 | 86.2221 | 86.2221 | 86.2221 | 86.2221 | 86.2221 | 86.2221 | 86.2221 | 100% | 0 | 53.1876 | 72.0932 | 77.2584 | 78.0542 | 78.5557 | 79.6659 | 82.2942 | 83.7249 | 86.4587 | 94.7777 | 87.9092 | 86.5626 | 88.3699 | 92.3278 | 89.6413 | 89.6413 | 89.6413 | 89.6413 | 89.6413 | 89.6413 | 89.6413 | 89.6413 | 89.6413 | 89.6413 | 89.6413 | 89.6413 | 89.6413 | 89.6413 | 89.6413 | 89.6413
99% | 1.486 | 49.2072 | 68.1629 | 73.0841 | 73.9197 | 74.5682 | 75.6918 | 78.2537 | 79.9649 | 82.1367 | 83.2619 | 84.2491 | 82.4136 | 84.5551 | 87.9243 | 85.3598 | 85.3598 | 85.3598 | 85.3598 | 85.3598 | 85.3598 | 85.3598 | 85.3598 | 85.3598 | 85.3598 | 85.3598 | 85.3598 | 85.3598 | 85.3598 | 85.3598 | 85.3598 | 99% | 1.486 | 52.6557 | 71.3723 | 76.4858 | 77.2737 | 77.7701 | 78.8692 | 81.4712 | 82.8877 | 85.5941 | 93.83 | 87.0301 | 85.697 | 87.4862 | 91.4045 | 88.7449 | 88.7449 | 88.7449 | 88.7449 | 88.7449 | 88.7449 | 88.7449 | 88.7449 | 88.7449 | 88.7449 | 88.7449 | 88.7449 | 88.7449 | 88.7449 | 88.7449 | 88.7449
98% | 3.2692 | 48.7101 | 67.4743 | 72.3458 | 73.173 | 73.815 | 74.9272 | 77.4632 | 79.1572 | 81.3071 | 82.4209 | 83.3981 | 81.5812 | 83.701 | 87.0362 | 84.4976 | 84.4976 | 84.4976 | 84.4976 | 84.4976 | 84.4976 | 84.4976 | 84.4976 | 84.4976 | 84.4976 | 84.4976 | 84.4976 | 84.4976 | 84.4976 | 84.4976 | 84.4976 | 98% | 3.2692 | 52.1238 | 70.6514 | 75.7133 | 76.4931 | 76.9846 | 78.0726 | 80.6483 | 82.0504 | 84.7295 | 92.8822 | 86.151 | 84.8313 | 86.6025 | 90.4812 | 87.8485 | 87.8485 | 87.8485 | 87.8485 | 87.8485 | 87.8485 | 87.8485 | 87.8485 | 87.8485 | 87.8485 | 87.8485 | 87.8485 | 87.8485 | 87.8485 | 87.8485 | 87.8485
97% | 6.8356 | 48.2131 | 66.7858 | 71.6076 | 72.4263 | 73.0618 | 74.1627 | 76.6728 | 78.3495 | 80.4774 | 81.5798 | 82.5471 | 80.7487 | 82.847 | 86.1481 | 83.6354 | 83.6354 | 83.6354 | 83.6354 | 83.6354 | 83.6354 | 83.6354 | 83.6354 | 83.6354 | 83.6354 | 83.6354 | 83.6354 | 83.6354 | 83.6354 | 83.6354 | 83.6354 | 97% | 6.8356 | 51.5919 | 69.9304 | 74.9407 | 75.7126 | 76.199 | 77.2759 | 79.8254 | 81.2132 | 83.865 | 91.9344 | 85.2719 | 83.9657 | 85.7188 | 89.558 | 86.9521 | 86.9521 | 86.9521 | 86.9521 | 86.9521 | 86.9521 | 86.9521 | 86.9521 | 86.9521 | 86.9521 | 86.9521 | 86.9521 | 86.9521 | 86.9521 | 86.9521 | 86.9521
95% | 17.5347 | 47.219 | 65.4088 | 70.1312 | 70.933 | 71.5553 | 72.6335 | 75.0919 | 76.734 | 78.8181 | 79.8978 | 80.8451 | 79.0838 | 81.1388 | 84.3718 | 81.911 | 81.911 | 81.911 | 81.911 | 81.911 | 81.911 | 81.911 | 81.911 | 81.911 | 81.911 | 81.911 | 81.911 | 81.911 | 81.911 | 81.911 | 81.911 | 95% | 17.5347 | 50.5282 | 68.4886 | 73.3955 | 74.1515 | 74.6279 | 75.6826 | 78.1795 | 79.5387 | 82.1358 | 90.0389 | 83.5138 | 82.2345 | 83.9514 | 87.7114 | 85.1592 | 85.1592 | 85.1592 | 85.1592 | 85.1592 | 85.1592 | 85.1592 | 85.1592 | 85.1592 | 85.1592 | 85.1592 | 85.1592 | 85.1592 | 85.1592 | 85.1592 | 85.1592
90% | 78.7576 | 44.7338 | 61.9662 | 66.4401 | 67.1997 | 67.7893 | 68.8107 | 71.1397 | 72.6954 | 74.6697 | 75.6926 | 76.5901 | 74.9215 | 76.8683 | 79.9312 | 77.5999 | 77.5999 | 77.5999 | 77.5999 | 77.5999 | 77.5999 | 77.5999 | 77.5999 | 77.5999 | 77.5999 | 77.5999 | 77.5999 | 77.5999 | 77.5999 | 77.5999 | 77.5999 | 90% | 78.7576 | 47.8688 | 64.8839 | 69.5326 | 70.2488 | 70.7001 | 71.6993 | 74.0648 | 75.3524 | 77.8128 | 85.3 | 79.1183 | 77.9063 | 79.5329 | 83.095 | 80.6772 | 80.6772 | 80.6772 | 80.6772 | 80.6772 | 80.6772 | 80.6772 | 80.6772 | 80.6772 | 80.6772 | 80.6772 | 80.6772 | 80.6772 | 80.6772 | 80.6772 | 80.6772
85% | 236.8672 | 42.2486 | 58.5237 | 62.7489 | 63.4664 | 64.0232 | 64.9879 | 67.1875 | 68.6567 | 70.5214 | 71.4875 | 72.3351 | 70.7592 | 72.5978 | 75.4906 | 73.2888 | 73.2888 | 73.2888 | 73.2888 | 73.2888 | 73.2888 | 73.2888 | 73.2888 | 73.2888 | 73.2888 | 73.2888 | 73.2888 | 73.2888 | 73.2888 | 73.2888 | 73.2888 | 85% | 236.8672 | 45.2094 | 61.2792 | 65.6697 | 66.3461 | 66.7723 | 67.716 | 69.9501 | 71.1662 | 73.4899 | 80.5611 | 74.7228 | 73.5782 | 75.1144 | 78.4786 | 76.1951 | 76.1951 | 76.1951 | 76.1951 | 76.1951 | 76.1951 | 76.1951 | 76.1951 | 76.1951 | 76.1951 | 76.1951 | 76.1951 | 76.1951 | 76.1951 | 76.1951 | 76.1951
80% | 497.5104 | 39.7634 | 55.0811 | 59.0578 | 59.7331 | 60.2571 | 61.1651 | 63.2353 | 64.6181 | 66.3731 | 67.2823 | 68.08 | 66.5969 | 68.3274 | 71.05 | 68.9777 | 68.9777 | 68.9777 | 68.9777 | 68.9777 | 68.9777 | 68.9777 | 68.9777 | 68.9777 | 68.9777 | 68.9777 | 68.9777 | 68.9777 | 68.9777 | 68.9777 | 68.9777 | 80% | 497.5104 | 42.55 | 57.6746 | 61.8067 | 62.4434 | 62.8445 | 63.7327 | 65.8353 | 66.9799 | 69.167 | 75.8222 | 70.3274 | 69.2501 | 70.6959 | 73.8622 | 71.7131 | 71.7131 | 71.7131 | 71.7131 | 71.7131 | 71.7131 | 71.7131 | 71.7131 | 71.7131 | 71.7131 | 71.7131 | 71.7131 | 71.7131 | 71.7131 | 71.7131 | 71.7131
75% | 803.6248 | 37.2782 | 51.6385 | 55.3667 | 55.9997 | 56.4911 | 57.3423 | 59.2831 | 60.5795 | 62.2248 | 63.0772 | 63.825 | 62.4346 | 64.0569 | 66.6093 | 64.6665 | 64.6665 | 64.6665 | 64.6665 | 64.6665 | 64.6665 | 64.6665 | 64.6665 | 64.6665 | 64.6665 | 64.6665 | 64.6665 | 64.6665 | 64.6665 | 64.6665 | 64.6665 | 75% | 803.6248 | 39.8907 | 54.0699 | 57.9438 | 58.5407 | 58.9167 | 59.7494 | 61.7206 | 62.7937 | 64.844 | 71.0833 | 65.9319 | 64.9219 | 66.2774 | 69.2458 | 67.231 | 67.231 | 67.231 | 67.231 | 67.231 | 67.231 | 67.231 | 67.231 | 67.231 | 67.231 | 67.231 | 67.231 | 67.231 | 67.231 | 67.231 | 67.231
70% | 1155.2107 | 34.793 | 48.196 | 51.6756 | 52.2664 | 52.725 | 53.5194 | 55.3309 | 56.5408 | 58.0765 | 58.8721 | 59.57 | 58.2723 | 59.7865 | 62.1687 | 60.3554 | 60.3554 | 60.3554 | 60.3554 | 60.3554 | 60.3554 | 60.3554 | 60.3554 | 60.3554 | 60.3554 | 60.3554 | 60.3554 | 60.3554 | 60.3554 | 60.3554 | 60.3554 | 70% | 1155.2107 | 37.2313 | 50.4653 | 54.0809 | 54.638 | 54.989 | 55.7661 | 57.6059 | 58.6074 | 60.5211 | 66.3444 | 61.5365 | 60.5938 | 61.8589 | 64.6295 | 62.7489 | 62.7489 | 62.7489 | 62.7489 | 62.7489 | 62.7489 | 62.7489 | 62.7489 | 62.7489 | 62.7489 | 62.7489 | 62.7489 | 62.7489 | 62.7489 | 62.7489 | 62.7489
65% | 1553.1596 | 32.3077 | 44.7534 | 47.9845 | 48.5331 | 48.9589 | 49.6966 | 51.3787 | 52.5022 | 53.9282 | 54.6669 | 55.315 | 54.11 | 55.516 | 57.7281 | 56.0443 | 56.0443 | 56.0443 | 56.0443 | 56.0443 | 56.0443 | 56.0443 | 56.0443 | 56.0443 | 56.0443 | 56.0443 | 56.0443 | 56.0443 | 56.0443 | 56.0443 | 56.0443 | 65% | 1553.1596 | 34.5719 | 46.8606 | 50.218 | 50.7352 | 51.0612 | 51.7828 | 53.4912 | 54.4212 | 56.1982 | 61.6055 | 57.141 | 56.2657 | 57.4405 | 60.0131 | 58.2669 | 58.2669 | 58.2669 | 58.2669 | 58.2669 | 58.2669 | 58.2669 | 58.2669 | 58.2669 | 58.2669 | 58.2669 | 58.2669 | 58.2669 | 58.2669 | 58.2669 | 58.2669
60% | 2026.2996 | 29.8225 | 41.3108 | 44.2934 | 44.7998 | 45.1928 | 45.8738 | 47.4265 | 48.4636 | 49.7798 | 50.4618 | 51.06 | 49.9477 | 51.2455 | 53.2875 | 51.7332 | 51.7332 | 51.7332 | 51.7332 | 51.7332 | 51.7332 | 51.7332 | 51.7332 | 51.7332 | 51.7332 | 51.7332 | 51.7332 | 51.7332 | 51.7332 | 51.7332 | 51.7332 | 60% | 2026.2996 | 31.9125 | 43.2559 | 46.3551 | 46.8325 | 47.1334 | 47.7995 | 49.3765 | 50.235 | 51.8752 | 56.8666 | 52.7455 | 51.9376 | 53.022 | 55.3967 | 53.7848 | 53.7848 | 53.7848 | 53.7848 | 53.7848 | 53.7848 | 53.7848 | 53.7848 | 53.7848 | 53.7848 | 53.7848 | 53.7848 | 53.7848 | 53.7848 | 53.7848 | 53.7848
55% | 2598.4068 | 27.3373 | 37.8683 | 40.6023 | 41.0665 | 41.4268 | 42.051 | 43.4743 | 44.425 | 45.6315 | 46.2566 | 46.805 | 45.7854 | 46.9751 | 48.8469 | 47.4221 | 47.4221 | 47.4221 | 47.4221 | 47.4221 | 47.4221 | 47.4221 | 47.4221 | 47.4221 | 47.4221 | 47.4221 | 47.4221 | 47.4221 | 47.4221 | 47.4221 | 47.4221 | 55% | 2598.4068 | 29.2532 | 39.6513 | 42.4921 | 42.9298 | 43.2056 | 43.8162 | 45.2618 | 46.0487 | 47.5523 | 52.1278 | 48.3501 | 47.6094 | 48.6035 | 50.7803 | 49.3027 | 49.3027 | 49.3027 | 49.3027 | 49.3027 | 49.3027 | 49.3027 | 49.3027 | 49.3027 | 49.3027 | 49.3027 | 49.3027 | 49.3027 | 49.3027 | 49.3027 | 49.3027
50% | 3233.5201 | 24.8521 | 34.4257 | 36.9111 | 37.3332 | 37.6607 | 38.2282 | 39.5221 | 40.3863 | 41.4832 | 42.0515 | 42.55 | 41.623 | 42.7046 | 44.4062 | 43.111 | 43.111 | 43.111 | 43.111 | 43.111 | 43.111 | 43.111 | 43.111 | 43.111 | 43.111 | 43.111 | 43.111 | 43.111 | 43.111 | 43.111 | 43.111 | 50% | 3233.5201 | 26.5938 | 36.0466 | 38.6292 | 39.0271 | 39.2778 | 39.833 | 41.1471 | 41.8625 | 43.2294 | 47.3889 | 43.9546 | 43.2813 | 44.185 | 46.1639 | 44.8207 | 44.8207 | 44.8207 | 44.8207 | 44.8207 | 44.8207 | 44.8207 | 44.8207 | 44.8207 | 44.8207 | 44.8207 | 44.8207 | 44.8207 | 44.8207 | 44.8207 | 44.8207
45% | 3775.313 | 22.3669 | 30.9831 | 33.22 | 33.5998 | 33.8946 | 34.4054 | 35.5699 | 36.3477 | 37.3349 | 37.8463 | 38.295 | 37.4607 | 38.4342 | 39.9656 | 38.7999 | 38.7999 | 38.7999 | 38.7999 | 38.7999 | 38.7999 | 38.7999 | 38.7999 | 38.7999 | 38.7999 | 38.7999 | 38.7999 | 38.7999 | 38.7999 | 38.7999 | 38.7999 | 45% | 3775.313 | 23.9344 | 32.442 | 34.7663 | 35.1244 | 35.35 | 35.8497 | 37.0324 | 37.6762 | 38.9064 | 42.65 | 39.5591 | 38.9532 | 39.7665 | 41.5475 | 40.3386 | 40.3386 | 40.3386 | 40.3386 | 40.3386 | 40.3386 | 40.3386 | 40.3386 | 40.3386 | 40.3386 | 40.3386 | 40.3386 | 40.3386 | 40.3386 | 40.3386 | 40.3386
40% | 4072.8088 | 19.8817 | 27.5405 | 29.5289 | 29.8665 | 30.1286 | 30.5825 | 31.6176 | 32.3091 | 33.1866 | 33.6412 | 34.04 | 33.2984 | 34.1637 | 35.525 | 34.4888 | 34.4888 | 34.4888 | 34.4888 | 34.4888 | 34.4888 | 34.4888 | 34.4888 | 34.4888 | 34.4888 | 34.4888 | 34.4888 | 34.4888 | 34.4888 | 34.4888 | 34.4888 | 40% | 4072.8088 | 21.275 | 28.8373 | 30.9034 | 31.2217 | 31.4223 | 31.8664 | 32.9177 | 33.49 | 34.5835 | 37.9111 | 35.1637 | 34.625 | 35.348 | 36.9311 | 35.8565 | 35.8565 | 35.8565 | 35.8565 | 35.8565 | 35.8565 | 35.8565 | 35.8565 | 35.8565 | 35.8565 | 35.8565 | 35.8565 | 35.8565 | 35.8565 | 35.8565 | 35.8565
35% | 4198.821 | 17.3965 | 24.098 | 25.8378 | 26.1332 | 26.3625 | 26.7597 | 27.6654 | 28.2704 | 29.0382 | 29.436 | 29.785 | 29.1361 | 29.8932 | 31.0844 | 30.1777 | 30.1777 | 30.1777 | 30.1777 | 30.1777 | 30.1777 | 30.1777 | 30.1777 | 30.1777 | 30.1777 | 30.1777 | 30.1777 | 30.1777 | 30.1777 | 30.1777 | 30.1777 | 35% | 4198.821 | 18.6156 | 25.2326 | 27.0405 | 27.319 | 27.4945 | 27.8831 | 28.803 | 29.3037 | 30.2606 | 33.1722 | 30.7682 | 30.2969 | 30.9295 | 32.3147 | 31.3745 | 31.3745 | 31.3745 | 31.3745 | 31.3745 | 31.3745 | 31.3745 | 31.3745 | 31.3745 | 31.3745 | 31.3745 | 31.3745 | 31.3745 | 31.3745 | 31.3745 | 31.3745
30% | 4271.3374 | 14.9113 | 20.6554 | 22.1467 | 22.3999 | 22.5964 | 22.9369 | 23.7132 | 24.2318 | 24.8899 | 25.2309 | 25.53 | 24.9738 | 25.6228 | 26.6437 | 25.8666 | 25.8666 | 25.8666 | 25.8666 | 25.8666 | 25.8666 | 25.8666 | 25.8666 | 25.8666 | 25.8666 | 25.8666 | 25.8666 | 25.8666 | 25.8666 | 25.8666 | 25.8666 | 30% | 4271.3374 | 15.9563 | 21.628 | 23.1775 | 23.4163 | 23.5667 | 23.8998 | 24.6883 | 25.1175 | 25.9376 | 28.4333 | 26.3728 | 25.9688 | 26.511 | 27.6983 | 26.8924 | 26.8924 | 26.8924 | 26.8924 | 26.8924 | 26.8924 | 26.8924 | 26.8924 | 26.8924 | 26.8924 | 26.8924 | 26.8924 | 26.8924 | 26.8924 | 26.8924 | 26.8924
25% | 4321.8611 | 12.4261 | 17.2128 | 18.4556 | 18.6666 | 18.8304 | 19.1141 | 19.761 | 20.1932 | 20.7416 | 21.0257 | 21.275 | 20.8115 | 21.3523 | 22.2031 | 21.5555 | 21.5555 | 21.5555 | 21.5555 | 21.5555 | 21.5555 | 21.5555 | 21.5555 | 21.5555 | 21.5555 | 21.5555 | 21.5555 | 21.5555 | 21.5555 | 21.5555 | 21.5555 | 25% | 4321.8611 | 13.2969 | 18.0233 | 19.3146 | 19.5136 | 19.6389 | 19.9165 | 20.5735 | 20.9312 | 21.6147 | 23.6944 | 21.9773 | 21.6406 | 22.0925 | 23.0819 | 22.4103 | 22.4103 | 22.4103 | 22.4103 | 22.4103 | 22.4103 | 22.4103 | 22.4103 | 22.4103 | 22.4103 | 22.4103 | 22.4103 | 22.4103 | 22.4103 | 22.4103 | 22.4103
20% | 4353.067 | 9.9408 | 13.7703 | 14.7645 | 14.9333 | 15.0643 | 15.2913 | 15.8088 | 16.1545 | 16.5933 | 16.8206 | 17.02 | 16.6492 | 17.0818 | 17.7625 | 17.2444 | 17.2444 | 17.2444 | 17.2444 | 17.2444 | 17.2444 | 17.2444 | 17.2444 | 17.2444 | 17.2444 | 17.2444 | 17.2444 | 17.2444 | 17.2444 | 17.2444 | 17.2444 | 20% | 4353.067 | 10.6375 | 14.4186 | 15.4517 | 15.6108 | 15.7111 | 15.9332 | 16.4588 | 16.745 | 17.2917 | 18.9555 | 17.5818 | 17.3125 | 17.674 | 18.4656 | 17.9283 | 17.9283 | 17.9283 | 17.9283 | 17.9283 | 17.9283 | 17.9283 | 17.9283 | 17.9283 | 17.9283 | 17.9283 | 17.9283 | 17.9283 | 17.9283 | 17.9283 | 17.9283
15% | 4369.4129 | 7.4556 | 10.3277 | 11.0733 | 11.1999 | 11.2982 | 11.4685 | 11.8566 | 12.1159 | 12.445 | 12.6154 | 12.765 | 12.4869 | 12.8114 | 13.3219 | 12.9333 | 12.9333 | 12.9333 | 12.9333 | 12.9333 | 12.9333 | 12.9333 | 12.9333 | 12.9333 | 12.9333 | 12.9333 | 12.9333 | 12.9333 | 12.9333 | 12.9333 | 12.9333 | 15% | 4369.4129 | 7.9781 | 10.814 | 11.5888 | 11.7081 | 11.7833 | 11.9499 | 12.3441 | 12.5587 | 12.9688 | 14.2167 | 13.1864 | 12.9844 | 13.2555 | 13.8492 | 13.4462 | 13.4462 | 13.4462 | 13.4462 | 13.4462 | 13.4462 | 13.4462 | 13.4462 | 13.4462 | 13.4462 | 13.4462 | 13.4462 | 13.4462 | 13.4462 | 13.4462 | 13.4462
10% | 4378.6261 | 4.9704 | 6.8851 | 7.3822 | 7.4666 | 7.5321 | 7.6456 | 7.9044 | 8.0773 | 8.2966 | 8.4103 | 8.51 | 8.3246 | 8.5409 | 8.8812 | 8.6222 | 8.6222 | 8.6222 | 8.6222 | 8.6222 | 8.6222 | 8.6222 | 8.6222 | 8.6222 | 8.6222 | 8.6222 | 8.6222 | 8.6222 | 8.6222 | 8.6222 | 8.6222 | 10% | 4378.6261 | 5.3188 | 7.2093 | 7.7258 | 7.8054 | 7.8556 | 7.9666 | 8.2294 | 8.3725 | 8.6459 | 9.4778 | 8.7909 | 8.6563 | 8.837 | 9.2328 | 8.9641 | 8.9641 | 8.9641 | 8.9641 | 8.9641 | 8.9641 | 8.9641 | 8.9641 | 8.9641 | 8.9641 | 8.9641 | 8.9641 | 8.9641 | 8.9641 | 8.9641 | 8.9641
5% | 4391.7028 | 2.4852 | 3.4426 | 3.6911 | 3.7333 | 3.7661 | 3.8228 | 3.9522 | 4.0386 | 4.1483 | 4.2051 | 4.255 | 4.1623 | 4.2705 | 4.4406 | 4.3111 | 4.3111 | 4.3111 | 4.3111 | 4.3111 | 4.3111 | 4.3111 | 4.3111 | 4.3111 | 4.3111 | 4.3111 | 4.3111 | 4.3111 | 4.3111 | 4.3111 | 4.3111 | 5% | 4391.7028 | 2.6594 | 3.6047 | 3.8629 | 3.9027 | 3.9278 | 3.9833 | 4.1147 | 4.1862 | 4.3229 | 4.7389 | 4.3955 | 4.3281 | 4.4185 | 4.6164 | 4.4821 | 4.4821 | 4.4821 | 4.4821 | 4.4821 | 4.4821 | 4.4821 | 4.4821 | 4.4821 | 4.4821 | 4.4821 | 4.4821 | 4.4821 | 4.4821 | 4.4821 | 4.4821
9.992e-14% | 4391.7028 | 4.9664e-14 | 6.8796e-14 | 7.3763e-14 | 7.4607e-14 | 7.5261e-14 | 7.6395e-14 | 7.8981e-14 | 8.0708e-14 | 8.29e-14 | 8.4036e-14 | 8.5032e-14 | 8.318e-14 | 8.5341e-14 | 8.8741e-14 | 8.6153e-14 | 8.6153e-14 | 8.6153e-14 | 8.6153e-14 | 8.6153e-14 | 8.6153e-14 | 8.6153e-14 | 8.6153e-14 | 8.6153e-14 | 8.6153e-14 | 8.6153e-14 | 8.6153e-14 | 8.6153e-14 | 8.6153e-14 | 8.6153e-14 | 8.6153e-14 | 9.992e-14% | 4391.7028 | 5.3145e-14 | 7.2036e-14 | 7.7197e-14 | 7.7992e-14 | 7.8493e-14 | 7.9602e-14 | 8.2228e-14 | 8.3658e-14 | 8.639e-14 | 9.4702e-14 | 8.7839e-14 | 8.6493e-14 | 8.8299e-14 | 9.2254e-14 | 8.957e-14 | 8.957e-14 | 8.957e-14 | 8.957e-14 | 8.957e-14 | 8.957e-14 | 8.957e-14 | 8.957e-14 | 8.957e-14 | 8.957e-14 | 8.957e-14 | 8.957e-14 | 8.957e-14 | 8.957e-14 | 8.957e-14 | 8.957e-14
Summer Season | [31 empty] | Summer Season
P50 | [31 empty] | P10
% of MD | Summer - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Summer - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 56.4483 | 74.8831 | 79.898 | 79.7498 | 79.7414 | 80.3113 | 80.9369 | 82.2223 | 83.1461 | 83.6463 | 84.1925 | 84.6932 | 85.5997 | 86.7253 | 86.6445 | 86.6445 | 86.6445 | 86.6445 | 86.6445 | 86.6445 | 86.6445 | 86.6445 | 86.6445 | 86.6445 | 86.6445 | 86.6445 | 86.6445 | 86.6445 | 86.6445 | 86.6445 | 100% | 0 | 62.901 | 81.3728 | 86.203 | 85.9109 | 85.9284 | 86.4219 | 87.7284 | 88.6008 | 89.4561 | 90.4569 | 91.3826 | 92.2827 | 92.383 | 93.434 | 92.6325 | 92.6325 | 92.6325 | 92.6325 | 92.6325 | 92.6325 | 92.6325 | 92.6325 | 92.6325 | 92.6325 | 92.6325 | 92.6325 | 92.6325 | 92.6325 | 92.6325 | 92.6325
99% | 0 | 55.8838 | 74.1343 | 79.099 | 78.9523 | 78.944 | 79.5082 | 80.1275 | 81.4 | 82.3146 | 82.8098 | 83.3506 | 83.8463 | 84.7437 | 85.858 | 85.778 | 85.778 | 85.778 | 85.778 | 85.778 | 85.778 | 85.778 | 85.778 | 85.778 | 85.778 | 85.778 | 85.778 | 85.778 | 85.778 | 85.778 | 85.778 | 99% | 1.5127 | 62.272 | 80.559 | 85.341 | 85.0518 | 85.0691 | 85.5577 | 86.8512 | 87.7148 | 88.5615 | 89.5523 | 90.4688 | 91.3598 | 91.4592 | 92.4996 | 91.7061 | 91.7061 | 91.7061 | 91.7061 | 91.7061 | 91.7061 | 91.7061 | 91.7061 | 91.7061 | 91.7061 | 91.7061 | 91.7061 | 91.7061 | 91.7061 | 91.7061 | 91.7061
98% | 0 | 55.3193 | 73.3854 | 78.3 | 78.1548 | 78.1466 | 78.7051 | 79.3181 | 80.5778 | 81.4832 | 81.9734 | 82.5086 | 82.9994 | 83.8877 | 84.9908 | 84.9116 | 84.9116 | 84.9116 | 84.9116 | 84.9116 | 84.9116 | 84.9116 | 84.9116 | 84.9116 | 84.9116 | 84.9116 | 84.9116 | 84.9116 | 84.9116 | 84.9116 | 84.9116 | 98% | 2.269 | 61.643 | 79.7453 | 84.4789 | 84.1927 | 84.2098 | 84.6935 | 85.9739 | 86.8287 | 87.667 | 88.6477 | 89.555 | 90.437 | 90.5354 | 91.5653 | 90.7798 | 90.7798 | 90.7798 | 90.7798 | 90.7798 | 90.7798 | 90.7798 | 90.7798 | 90.7798 | 90.7798 | 90.7798 | 90.7798 | 90.7798 | 90.7798 | 90.7798 | 90.7798
97% | 0.37816 | 54.7549 | 72.6366 | 77.501 | 77.3573 | 77.3492 | 77.902 | 78.5088 | 79.7556 | 80.6517 | 81.1369 | 81.6667 | 82.1524 | 83.0317 | 84.1235 | 84.0451 | 84.0451 | 84.0451 | 84.0451 | 84.0451 | 84.0451 | 84.0451 | 84.0451 | 84.0451 | 84.0451 | 84.0451 | 84.0451 | 84.0451 | 84.0451 | 84.0451 | 84.0451 | 97% | 3.7816 | 61.014 | 78.9316 | 83.6169 | 83.3336 | 83.3505 | 83.8292 | 85.0966 | 85.9427 | 86.7724 | 87.7432 | 88.6411 | 89.5142 | 89.6115 | 90.631 | 89.8535 | 89.8535 | 89.8535 | 89.8535 | 89.8535 | 89.8535 | 89.8535 | 89.8535 | 89.8535 | 89.8535 | 89.8535 | 89.8535 | 89.8535 | 89.8535 | 89.8535 | 89.8535
95% | 2.269 | 53.6259 | 71.1389 | 75.9031 | 75.7623 | 75.7544 | 76.2958 | 76.89 | 78.1112 | 78.9888 | 79.464 | 79.9829 | 80.4586 | 81.3197 | 82.389 | 82.3122 | 82.3122 | 82.3122 | 82.3122 | 82.3122 | 82.3122 | 82.3122 | 82.3122 | 82.3122 | 82.3122 | 82.3122 | 82.3122 | 82.3122 | 82.3122 | 82.3122 | 82.3122 | 95% | 6.0506 | 59.7559 | 77.3041 | 81.8928 | 81.6153 | 81.632 | 82.1008 | 83.342 | 84.1707 | 84.9833 | 85.934 | 86.8135 | 87.6685 | 87.7639 | 88.7623 | 88.0008 | 88.0008 | 88.0008 | 88.0008 | 88.0008 | 88.0008 | 88.0008 | 88.0008 | 88.0008 | 88.0008 | 88.0008 | 88.0008 | 88.0008 | 88.0008 | 88.0008 | 88.0008
90% | 5.6725 | 50.8035 | 67.3948 | 71.9082 | 71.7748 | 71.7673 | 72.2802 | 72.8432 | 74 | 74.8315 | 75.2817 | 75.7732 | 76.2239 | 77.0397 | 78.0527 | 77.98 | 77.98 | 77.98 | 77.98 | 77.98 | 77.98 | 77.98 | 77.98 | 77.98 | 77.98 | 77.98 | 77.98 | 77.98 | 77.98 | 77.98 | 77.98 | 90% | 16.2611 | 56.6109 | 73.2355 | 77.5827 | 77.3198 | 77.3355 | 77.7797 | 78.9556 | 79.7407 | 80.5105 | 81.4112 | 82.2444 | 83.0544 | 83.1447 | 84.0906 | 83.3692 | 83.3692 | 83.3692 | 83.3692 | 83.3692 | 83.3692 | 83.3692 | 83.3692 | 83.3692 | 83.3692 | 83.3692 | 83.3692 | 83.3692 | 83.3692 | 83.3692 | 83.3692
85% | 15.8829 | 47.9811 | 63.6506 | 67.9133 | 67.7874 | 67.7802 | 68.2646 | 68.7963 | 69.8889 | 70.6742 | 71.0994 | 71.5636 | 71.9893 | 72.7598 | 73.7165 | 73.6478 | 73.6478 | 73.6478 | 73.6478 | 73.6478 | 73.6478 | 73.6478 | 73.6478 | 73.6478 | 73.6478 | 73.6478 | 73.6478 | 73.6478 | 73.6478 | 73.6478 | 73.6478 | 85% | 26.4715 | 53.4658 | 69.1669 | 73.2725 | 73.0243 | 73.0391 | 73.4586 | 74.5692 | 75.3106 | 76.0377 | 76.8883 | 77.6752 | 78.4403 | 78.5256 | 79.4189 | 78.7376 | 78.7376 | 78.7376 | 78.7376 | 78.7376 | 78.7376 | 78.7376 | 78.7376 | 78.7376 | 78.7376 | 78.7376 | 78.7376 | 78.7376 | 78.7376 | 78.7376 | 78.7376
80% | 31.0095 | 45.1586 | 59.9065 | 63.9184 | 63.7999 | 63.7932 | 64.2491 | 64.7495 | 65.7778 | 66.5169 | 66.917 | 67.354 | 67.7546 | 68.4798 | 69.3802 | 69.3156 | 69.3156 | 69.3156 | 69.3156 | 69.3156 | 69.3156 | 69.3156 | 69.3156 | 69.3156 | 69.3156 | 69.3156 | 69.3156 | 69.3156 | 69.3156 | 69.3156 | 69.3156 | 80% | 34.0348 | 50.3208 | 65.0982 | 68.9624 | 68.7287 | 68.7427 | 69.1375 | 70.1827 | 70.8806 | 71.5649 | 72.3655 | 73.1061 | 73.8261 | 73.9064 | 74.7472 | 74.106 | 74.106 | 74.106 | 74.106 | 74.106 | 74.106 | 74.106 | 74.106 | 74.106 | 74.106 | 74.106 | 74.106 | 74.106 | 74.106 | 74.106 | 74.106
75% | 72.9857 | 42.3362 | 56.1623 | 59.9235 | 59.8124 | 59.8061 | 60.2335 | 60.7027 | 61.6667 | 62.3596 | 62.7347 | 63.1444 | 63.5199 | 64.1998 | 65.044 | 64.9833 | 64.9833 | 64.9833 | 64.9833 | 64.9833 | 64.9833 | 64.9833 | 64.9833 | 64.9833 | 64.9833 | 64.9833 | 64.9833 | 64.9833 | 64.9833 | 64.9833 | 64.9833 | 75% | 48.405 | 47.1757 | 61.0296 | 64.6522 | 64.4332 | 64.4463 | 64.8164 | 65.7963 | 66.4506 | 67.0921 | 67.8427 | 68.537 | 69.212 | 69.2873 | 70.0755 | 69.4744 | 69.4744 | 69.4744 | 69.4744 | 69.4744 | 69.4744 | 69.4744 | 69.4744 | 69.4744 | 69.4744 | 69.4744 | 69.4744 | 69.4744 | 69.4744 | 69.4744 | 69.4744
70% | 150.5094 | 39.5138 | 52.4182 | 55.9286 | 55.8249 | 55.819 | 56.2179 | 56.6558 | 57.5556 | 58.2023 | 58.5524 | 58.9347 | 59.2853 | 59.9198 | 60.7077 | 60.6511 | 60.6511 | 60.6511 | 60.6511 | 60.6511 | 60.6511 | 60.6511 | 60.6511 | 60.6511 | 60.6511 | 60.6511 | 60.6511 | 60.6511 | 60.6511 | 60.6511 | 60.6511 | 70% | 76.3892 | 44.0307 | 56.9609 | 60.3421 | 60.1376 | 60.1499 | 60.4953 | 61.4099 | 62.0205 | 62.6193 | 63.3198 | 63.9678 | 64.5979 | 64.6681 | 65.4038 | 64.8427 | 64.8427 | 64.8427 | 64.8427 | 64.8427 | 64.8427 | 64.8427 | 64.8427 | 64.8427 | 64.8427 | 64.8427 | 64.8427 | 64.8427 | 64.8427 | 64.8427 | 64.8427
65% | 359.6342 | 36.6914 | 48.674 | 51.9337 | 51.8374 | 51.8319 | 52.2024 | 52.609 | 53.4445 | 54.045 | 54.3701 | 54.7251 | 55.0506 | 55.6398 | 56.3714 | 56.3189 | 56.3189 | 56.3189 | 56.3189 | 56.3189 | 56.3189 | 56.3189 | 56.3189 | 56.3189 | 56.3189 | 56.3189 | 56.3189 | 56.3189 | 56.3189 | 56.3189 | 56.3189 | 65% | 114.2056 | 40.8856 | 52.8923 | 56.0319 | 55.8421 | 55.8534 | 56.1742 | 57.0235 | 57.5905 | 58.1465 | 58.797 | 59.3987 | 59.9837 | 60.049 | 60.7321 | 60.2111 | 60.2111 | 60.2111 | 60.2111 | 60.2111 | 60.2111 | 60.2111 | 60.2111 | 60.2111 | 60.2111 | 60.2111 | 60.2111 | 60.2111 | 60.2111 | 60.2111 | 60.2111
60% | 689.7717 | 33.869 | 44.9299 | 47.9388 | 47.8499 | 47.8449 | 48.1868 | 48.5621 | 49.3334 | 49.8876 | 50.1878 | 50.5155 | 50.8159 | 51.3598 | 52.0352 | 51.9867 | 51.9867 | 51.9867 | 51.9867 | 51.9867 | 51.9867 | 51.9867 | 51.9867 | 51.9867 | 51.9867 | 51.9867 | 51.9867 | 51.9867 | 51.9867 | 51.9867 | 51.9867 | 60% | 178.1154 | 37.7406 | 48.8237 | 51.7218 | 51.5465 | 51.557 | 51.8531 | 52.6371 | 53.1605 | 53.6736 | 54.2741 | 54.8296 | 55.3696 | 55.4298 | 56.0604 | 55.5795 | 55.5795 | 55.5795 | 55.5795 | 55.5795 | 55.5795 | 55.5795 | 55.5795 | 55.5795 | 55.5795 | 55.5795 | 55.5795 | 55.5795 | 55.5795 | 55.5795 | 55.5795
55% | 1095.5419 | 31.0466 | 41.1857 | 43.9439 | 43.8624 | 43.8578 | 44.1712 | 44.5153 | 45.2222 | 45.7303 | 46.0055 | 46.3059 | 46.5813 | 47.0798 | 47.6989 | 47.6545 | 47.6545 | 47.6545 | 47.6545 | 47.6545 | 47.6545 | 47.6545 | 47.6545 | 47.6545 | 47.6545 | 47.6545 | 47.6545 | 47.6545 | 47.6545 | 47.6545 | 47.6545 | 55% | 311.6074 | 34.5955 | 44.755 | 47.4116 | 47.251 | 47.2606 | 47.532 | 48.2506 | 48.7304 | 49.2008 | 49.7513 | 50.2604 | 50.7555 | 50.8107 | 51.3887 | 50.9479 | 50.9479 | 50.9479 | 50.9479 | 50.9479 | 50.9479 | 50.9479 | 50.9479 | 50.9479 | 50.9479 | 50.9479 | 50.9479 | 50.9479 | 50.9479 | 50.9479 | 50.9479
50% | 1666.1918 | 28.2242 | 37.4415 | 39.949 | 39.8749 | 39.8707 | 40.1557 | 40.4684 | 41.1111 | 41.573 | 41.8231 | 42.0962 | 42.3466 | 42.7999 | 43.3626 | 43.3222 | 43.3222 | 43.3222 | 43.3222 | 43.3222 | 43.3222 | 43.3222 | 43.3222 | 43.3222 | 43.3222 | 43.3222 | 43.3222 | 43.3222 | 43.3222 | 43.3222 | 43.3222 | 50% | 636.0723 | 31.4505 | 40.6864 | 43.1015 | 42.9554 | 42.9642 | 43.211 | 43.8642 | 44.3004 | 44.728 | 45.2284 | 45.6913 | 46.1413 | 46.1915 | 46.717 | 46.3162 | 46.3162 | 46.3162 | 46.3162 | 46.3162 | 46.3162 | 46.3162 | 46.3162 | 46.3162 | 46.3162 | 46.3162 | 46.3162 | 46.3162 | 46.3162 | 46.3162 | 46.3162
45% | 2506.0947 | 25.4017 | 33.6974 | 35.9541 | 35.8874 | 35.8837 | 36.1401 | 36.4216 | 37 | 37.4157 | 37.6408 | 37.8866 | 38.112 | 38.5199 | 39.0264 | 38.99 | 38.99 | 38.99 | 38.99 | 38.99 | 38.99 | 38.99 | 38.99 | 38.99 | 38.99 | 38.99 | 38.99 | 38.99 | 38.99 | 38.99 | 38.99 | 45% | 1179.4944 | 28.3054 | 36.6177 | 38.7913 | 38.6599 | 38.6678 | 38.8899 | 39.4778 | 39.8703 | 40.2552 | 40.7056 | 41.1222 | 41.5272 | 41.5724 | 42.0453 | 41.6846 | 41.6846 | 41.6846 | 41.6846 | 41.6846 | 41.6846 | 41.6846 | 41.6846 | 41.6846 | 41.6846 | 41.6846 | 41.6846 | 41.6846 | 41.6846 | 41.6846 | 41.6846
40% | 3164.4787 | 22.5793 | 29.9532 | 31.9592 | 31.8999 | 31.8966 | 32.1245 | 32.3748 | 32.8889 | 33.2584 | 33.4585 | 33.677 | 33.8773 | 34.2399 | 34.6901 | 34.6578 | 34.6578 | 34.6578 | 34.6578 | 34.6578 | 34.6578 | 34.6578 | 34.6578 | 34.6578 | 34.6578 | 34.6578 | 34.6578 | 34.6578 | 34.6578 | 34.6578 | 34.6578 | 40% | 1808.3816 | 25.1604 | 32.5491 | 34.4812 | 34.3644 | 34.3713 | 34.5688 | 35.0914 | 35.4403 | 35.7824 | 36.1827 | 36.553 | 36.9131 | 36.9532 | 37.3736 | 37.053 | 37.053 | 37.053 | 37.053 | 37.053 | 37.053 | 37.053 | 37.053 | 37.053 | 37.053 | 37.053 | 37.053 | 37.053 | 37.053 | 37.053 | 37.053
35% | 3551.3408 | 19.7569 | 26.2091 | 27.9643 | 27.9124 | 27.9095 | 28.109 | 28.3279 | 28.7778 | 29.1011 | 29.2762 | 29.4674 | 29.6426 | 29.9599 | 30.3538 | 30.3256 | 30.3256 | 30.3256 | 30.3256 | 30.3256 | 30.3256 | 30.3256 | 30.3256 | 30.3256 | 30.3256 | 30.3256 | 30.3256 | 30.3256 | 30.3256 | 30.3256 | 30.3256 | 35% | 2779.1293 | 22.0153 | 28.4805 | 30.171 | 30.0688 | 30.0749 | 30.2477 | 30.705 | 31.0103 | 31.3096 | 31.6599 | 31.9839 | 32.2989 | 32.3341 | 32.7019 | 32.4214 | 32.4214 | 32.4214 | 32.4214 | 32.4214 | 32.4214 | 32.4214 | 32.4214 | 32.4214 | 32.4214 | 32.4214 | 32.4214 | 32.4214 | 32.4214 | 32.4214 | 32.4214
30% | 3758.953 | 16.9345 | 22.4649 | 23.9694 | 23.9249 | 23.9224 | 24.0934 | 24.2811 | 24.6667 | 24.9438 | 25.0939 | 25.2577 | 25.408 | 25.6799 | 26.0176 | 25.9933 | 25.9933 | 25.9933 | 25.9933 | 25.9933 | 25.9933 | 25.9933 | 25.9933 | 25.9933 | 25.9933 | 25.9933 | 25.9933 | 25.9933 | 25.9933 | 25.9933 | 25.9933 | 30% | 3814.165 | 18.8703 | 24.4118 | 25.8609 | 25.7733 | 25.7785 | 25.9266 | 26.3185 | 26.5802 | 26.8368 | 27.1371 | 27.4148 | 27.6848 | 27.7149 | 28.0302 | 27.7897 | 27.7897 | 27.7897 | 27.7897 | 27.7897 | 27.7897 | 27.7897 | 27.7897 | 27.7897 | 27.7897 | 27.7897 | 27.7897 | 27.7897 | 27.7897 | 27.7897 | 27.7897
25% | 3926.4798 | 14.1121 | 18.7208 | 19.9745 | 19.9375 | 19.9354 | 20.0778 | 20.2342 | 20.5556 | 20.7865 | 20.9116 | 21.0481 | 21.1733 | 21.3999 | 21.6813 | 21.6611 | 21.6611 | 21.6611 | 21.6611 | 21.6611 | 21.6611 | 21.6611 | 21.6611 | 21.6611 | 21.6611 | 21.6611 | 21.6611 | 21.6611 | 21.6611 | 21.6611 | 21.6611 | 25% | 4166.9923 | 15.7252 | 20.3432 | 21.5507 | 21.4777 | 21.4821 | 21.6055 | 21.9321 | 22.1502 | 22.364 | 22.6142 | 22.8457 | 23.0707 | 23.0958 | 23.3585 | 23.1581 | 23.1581 | 23.1581 | 23.1581 | 23.1581 | 23.1581 | 23.1581 | 23.1581 | 23.1581 | 23.1581 | 23.1581 | 23.1581 | 23.1581 | 23.1581 | 23.1581 | 23.1581
20% | 4050.5177 | 11.2897 | 14.9766 | 15.9796 | 15.95 | 15.9483 | 16.0623 | 16.1874 | 16.4445 | 16.6292 | 16.7293 | 16.8385 | 16.9386 | 17.1199 | 17.3451 | 17.3289 | 17.3289 | 17.3289 | 17.3289 | 17.3289 | 17.3289 | 17.3289 | 17.3289 | 17.3289 | 17.3289 | 17.3289 | 17.3289 | 17.3289 | 17.3289 | 17.3289 | 17.3289 | 20% | 4282.7105 | 12.5802 | 16.2746 | 17.2406 | 17.1822 | 17.1857 | 17.2844 | 17.5457 | 17.7202 | 17.8912 | 18.0914 | 18.2765 | 18.4565 | 18.4766 | 18.6868 | 18.5265 | 18.5265 | 18.5265 | 18.5265 | 18.5265 | 18.5265 | 18.5265 | 18.5265 | 18.5265 | 18.5265 | 18.5265 | 18.5265 | 18.5265 | 18.5265 | 18.5265 | 18.5265
15% | 4152.622 | 8.4672 | 11.2325 | 11.9847 | 11.9625 | 11.9612 | 12.0467 | 12.1405 | 12.3333 | 12.4719 | 12.5469 | 12.6289 | 12.704 | 12.84 | 13.0088 | 12.9967 | 12.9967 | 12.9967 | 12.9967 | 12.9967 | 12.9967 | 12.9967 | 12.9967 | 12.9967 | 12.9967 | 12.9967 | 12.9967 | 12.9967 | 12.9967 | 12.9967 | 12.9967 | 15% | 4364.7722 | 9.4351 | 12.2059 | 12.9304 | 12.8866 | 12.8893 | 12.9633 | 13.1593 | 13.2901 | 13.4184 | 13.5685 | 13.7074 | 13.8424 | 13.8575 | 14.0151 | 13.8949 | 13.8949 | 13.8949 | 13.8949 | 13.8949 | 13.8949 | 13.8949 | 13.8949 | 13.8949 | 13.8949 | 13.8949 | 13.8949 | 13.8949 | 13.8949 | 13.8949 | 13.8949
10% | 4248.2976 | 5.6448 | 7.4883 | 7.9898 | 7.975 | 7.9741 | 8.0311 | 8.0937 | 8.2222 | 8.3146 | 8.3646 | 8.4192 | 8.4693 | 8.56 | 8.6725 | 8.6644 | 8.6644 | 8.6644 | 8.6644 | 8.6644 | 8.6644 | 8.6644 | 8.6644 | 8.6644 | 8.6644 | 8.6644 | 8.6644 | 8.6644 | 8.6644 | 8.6644 | 8.6644 | 10% | 4391.6218 | 6.2901 | 8.1373 | 8.6203 | 8.5911 | 8.5928 | 8.6422 | 8.7728 | 8.8601 | 8.9456 | 9.0457 | 9.1383 | 9.2283 | 9.2383 | 9.3434 | 9.2632 | 9.2632 | 9.2632 | 9.2632 | 9.2632 | 9.2632 | 9.2632 | 9.2632 | 9.2632 | 9.2632 | 9.2632 | 9.2632 | 9.2632 | 9.2632 | 9.2632 | 9.2632
5% | 4361.7469 | 2.8224 | 3.7442 | 3.9949 | 3.9875 | 3.9871 | 4.0156 | 4.0468 | 4.1111 | 4.1573 | 4.1823 | 4.2096 | 4.2347 | 4.28 | 4.3363 | 4.3322 | 4.3322 | 4.3322 | 4.3322 | 4.3322 | 4.3322 | 4.3322 | 4.3322 | 4.3322 | 4.3322 | 4.3322 | 4.3322 | 4.3322 | 4.3322 | 4.3322 | 4.3322 | 5% | 4391.6218 | 3.145 | 4.0686 | 4.3101 | 4.2955 | 4.2964 | 4.3211 | 4.3864 | 4.43 | 4.4728 | 4.5228 | 4.5691 | 4.6141 | 4.6192 | 4.6717 | 4.6316 | 4.6316 | 4.6316 | 4.6316 | 4.6316 | 4.6316 | 4.6316 | 4.6316 | 4.6316 | 4.6316 | 4.6316 | 4.6316 | 4.6316 | 4.6316 | 4.6316 | 4.6316
9.992e-14% | 4391.6218 | 5.6403e-14 | 7.4823e-14 | 7.9834e-14 | 7.9686e-14 | 7.9678e-14 | 8.0247e-14 | 8.0872e-14 | 8.2157e-14 | 8.308e-14 | 8.3579e-14 | 8.4125e-14 | 8.4626e-14 | 8.5531e-14 | 8.6656e-14 | 8.6575e-14 | 8.6575e-14 | 8.6575e-14 | 8.6575e-14 | 8.6575e-14 | 8.6575e-14 | 8.6575e-14 | 8.6575e-14 | 8.6575e-14 | 8.6575e-14 | 8.6575e-14 | 8.6575e-14 | 8.6575e-14 | 8.6575e-14 | 8.6575e-14 | 8.6575e-14 | 9.992e-14% | 4391.6218 | 6.2851e-14 | 8.1308e-14 | 8.6134e-14 | 8.5842e-14 | 8.586e-14 | 8.6353e-14 | 8.7658e-14 | 8.853e-14 | 8.9385e-14 | 9.0385e-14 | 9.131e-14 | 9.2209e-14 | 9.2309e-14 | 9.3359e-14 | 9.2558e-14 | 9.2558e-14 | 9.2558e-14 | 9.2558e-14 | 9.2558e-14 | 9.2558e-14 | 9.2558e-14 | 9.2558e-14 | 9.2558e-14 | 9.2558e-14 | 9.2558e-14 | 9.2558e-14 | 9.2558e-14 | 9.2558e-14 | 9.2558e-14 | 9.2558e-14

## Locational VCR
Base case |  | Energy Usage (CY 2024 kWh) | Energy Usage (CY 2024 %) | Tailored VCR
Dec 24 AER VCR ($/kWh) - Res | 49.23 | 67934749.1441 | 34.06% | 16.7657
Dec 24 AER VCR ($/kWh) - Com | 34.39 | 101368150.4504 | 50.82% | 17.4756
Dec 24 AER VCR ($/kWh) - Ind | 33.49 | 17726336.2671 | 8.886% | 2.976
Dec 24 AER VCR ($/kWh) - Agr | 22.25 | 12451243.5083 | 6.242% | 1.3888
|  | 199480479.3698 |  | 38.6062 | KW/h
|  |  |  | 38606.1513 | MW/h

## E@R N
Option 1 - Do Nothing / Base Case
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99%
98%
97%
95%
90%
85%
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1 Winter POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 1 Winter POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | [42 empty] | 0.12002 | 0.191 | 1.6137 | 0.43805 | 0.43805 | 0.43805 | 0.43805 | 0.43805 | 0.43805 | 0.43805 | 0.43805 | 0.43805 | 0.43805 | 0.43805 | 0.43805 | 0.43805 | 0.43805 | 0.43805 | 0.43805
98% | [44 empty] | 0.14553
97%
95%
90%
85%
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.12002 | 0.191 | 1.7592 | 0.43805 | 0.43805 | 0.43805 | 0.43805 | 0.43805 | 0.43805 | 0.43805 | 0.43805 | 0.43805 | 0.43805 | 0.43805 | 0.43805 | 0.43805 | 0.43805 | 0.43805 | 0.43805
Option 1 Summer POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 1 Summer POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.036006 | 0.057301 | 0.52777 | 0.13142 | 0.13142 | 0.13142 | 0.13142 | 0.13142 | 0.13142 | 0.13142 | 0.13142 | 0.13142 | 0.13142 | 0.13142 | 0.13142 | 0.13142 | 0.13142 | 0.13142 | 0.13142
Option 2 - 1B New PHS ZSS + Three new feeders
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99%
98%
97%
95%
90%
85%
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2 Winter POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 2 Winter POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99
98%
97%
95%
90%
85%
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2 Summer POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 2 Summer POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 - 2B PHM 3rd Tx + Switchroom + Two new feeders + OFR12 New Feeder
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99%
98%
97%
95%
90%
85%
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 Winter POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 3 Winter POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99
98%
97%
95%
90%
85%
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 Summer POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 3 Summer POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 - 3B OFR 3rd Tx + Switchroom + Two new feeders + OFR12 New Feeder
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99%
98%
97%
95%
90%
85%
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 Winter POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 4 Winter POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99
98%
97%
95%
90%
85%
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 Summer POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 4 Summer POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 - 4B LLG 2nd Tx + Switchroom + Two new feeders + OFR12 New Feeder
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99%
98%
97%
95%
90%
85%
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 Winter POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 5 Winter POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99
98%
97%
95%
90%
85%
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 Summer POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 5 Summer POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 6 -
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99%
98%
97%
95%
90%
85%
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 6 Winter POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 6 Winter POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | [42 empty] | 0.12002 | 0.191 | 1.6137 | 0.43805 | 0.43805 | 0.43805 | 0.43805 | 0.43805 | 0.43805 | 0.43805 | 0.43805 | 0.43805 | 0.43805 | 0.43805 | 0.43805 | 0.43805 | 0.43805 | 0.43805 | 0.43805
98% | [44 empty] | 0.14553
97%
95%
90%
85%
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.12002 | 0.191 | 1.7592 | 0.43805 | 0.43805 | 0.43805 | 0.43805 | 0.43805 | 0.43805 | 0.43805 | 0.43805 | 0.43805 | 0.43805 | 0.43805 | 0.43805 | 0.43805 | 0.43805 | 0.43805 | 0.43805
Option 6 Summer POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 6 Summer POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.036006 | 0.057301 | 0.52777 | 0.13142 | 0.13142 | 0.13142 | 0.13142 | 0.13142 | 0.13142 | 0.13142 | 0.13142 | 0.13142 | 0.13142 | 0.13142 | 0.13142 | 0.13142 | 0.13142 | 0.13142 | 0.13142
Option 7 -
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99%
98%
97%
95%
90%
85%
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 7 Winter POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 7 Winter POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | [42 empty] | 0.12002 | 0.191 | 1.6137 | 0.43805 | 0.43805 | 0.43805 | 0.43805 | 0.43805 | 0.43805 | 0.43805 | 0.43805 | 0.43805 | 0.43805 | 0.43805 | 0.43805 | 0.43805 | 0.43805 | 0.43805 | 0.43805
98% | [44 empty] | 0.14553
97%
95%
90%
85%
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.12002 | 0.191 | 1.7592 | 0.43805 | 0.43805 | 0.43805 | 0.43805 | 0.43805 | 0.43805 | 0.43805 | 0.43805 | 0.43805 | 0.43805 | 0.43805 | 0.43805 | 0.43805 | 0.43805 | 0.43805 | 0.43805
Option 7 Summer POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 7 Summer POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.036006 | 0.057301 | 0.52777 | 0.13142 | 0.13142 | 0.13142 | 0.13142 | 0.13142 | 0.13142 | 0.13142 | 0.13142 | 0.13142 | 0.13142 | 0.13142 | 0.13142 | 0.13142 | 0.13142 | 0.13142 | 0.13142
Option 8 -
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99%
98%
97%
95%
90%
85%
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 8 Winter POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 8 Winter POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | [42 empty] | 0.12002 | 0.191 | 1.6137 | 0.43805 | 0.43805 | 0.43805 | 0.43805 | 0.43805 | 0.43805 | 0.43805 | 0.43805 | 0.43805 | 0.43805 | 0.43805 | 0.43805 | 0.43805 | 0.43805 | 0.43805 | 0.43805
98% | [44 empty] | 0.14553
97%
95%
90%
85%
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.12002 | 0.191 | 1.7592 | 0.43805 | 0.43805 | 0.43805 | 0.43805 | 0.43805 | 0.43805 | 0.43805 | 0.43805 | 0.43805 | 0.43805 | 0.43805 | 0.43805 | 0.43805 | 0.43805 | 0.43805 | 0.43805
Option 8 Summer POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 8 Summer POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.036006 | 0.057301 | 0.52777 | 0.13142 | 0.13142 | 0.13142 | 0.13142 | 0.13142 | 0.13142 | 0.13142 | 0.13142 | 0.13142 | 0.13142 | 0.13142 | 0.13142 | 0.13142 | 0.13142 | 0.13142 | 0.13142

## E@R N-1
Option 1 - Do Nothing / Base Case
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | 0.52857 | 28.8388 | 36.1886 | 37.4366 | 38.4052 | 40.0833 | 43.9094 | 46.4652 | 49.7088 | 51.3892 | 52.8635 | 50.1223 | 53.3207 | 58.3526 | 54.5225 | 54.5225 | 54.5225 | 54.5225 | 54.5225 | 54.5225 | 54.5225 | 54.5225 | 54.5225 | 54.5225 | 54.5225 | 54.5225 | 54.5225 | 54.5225 | 54.5225 | 54.5225 |  | 5.6789 | 33.6321 | 41.2692 | 42.4458 | 43.1872 | 44.8288 | 48.7149 | 50.8303 | 54.8724 | 67.1726 | 57.0171 | 55.026 | 57.6982 | 63.5502 | 59.5781 | 59.5781 | 59.5781 | 59.5781 | 59.5781 | 59.5781 | 59.5781 | 59.5781 | 59.5781 | 59.5781 | 59.5781 | 59.5781 | 59.5781 | 59.5781 | 59.5781 | 59.5781
98% | 0.020606 | 33.3788 | 42.11 | 43.5925 | 44.7431 | 46.7365 | 51.2818 | 54.3179 | 58.1711 | 60.1673 | 61.9187 | 58.6624 | 62.4618 | 68.4394 | 63.8895 | 63.8895 | 63.8895 | 63.8895 | 63.8895 | 63.8895 | 63.8895 | 63.8895 | 63.8895 | 63.8895 | 63.8895 | 63.8895 | 63.8895 | 63.8895 | 63.8895 | 63.8895 |  | 5.8662 | 39.073 | 48.1454 | 49.5431 | 50.4239 | 52.374 | 56.9904 | 59.5034 | 64.3051 | 78.9171 | 66.8529 | 64.4876 | 67.6621 | 74.6138 | 69.8952 | 69.8952 | 69.8952 | 69.8952 | 69.8952 | 69.8952 | 69.8952 | 69.8952 | 69.8952 | 69.8952 | 69.8952 | 69.8952 | 69.8952 | 69.8952 | 69.8952 | 69.8952
97% |  | 64.3022 | 81.5872 | 84.5221 | 86.7999 | 90.7464 | 99.7446 | 105.7551 | 113.3832 | 117.3353 | 120.8025 | 114.3559 | 121.8775 | 133.7114 | 124.704 | 124.704 | 124.704 | 124.704 | 124.704 | 124.704 | 124.704 | 124.704 | 124.704 | 124.704 | 124.704 | 124.704 | 124.704 | 124.704 | 124.704 | 124.704 |  | 9.8356 | 75.5748 | 93.5354 | 96.3025 | 98.0462 | 101.9067 | 111.0458 | 116.0208 | 125.5268 | 154.454 | 130.5706 | 125.888 | 132.1725 | 145.9349 | 136.5934 | 136.5934 | 136.5934 | 136.5934 | 136.5934 | 136.5934 | 136.5934 | 136.5934 | 136.5934 | 136.5934 | 136.5934 | 136.5934 | 136.5934 | 136.5934 | 136.5934 | 136.5934
95% |  | 181.8568 | 232.914 | 241.5832 | 248.3116 | 259.9688 | 286.5483 | 304.3023 | 326.8347 | 338.5083 | 348.75 | 329.7076 | 351.9256 | 386.8808 | 360.2743 | 360.2743 | 360.2743 | 360.2743 | 360.2743 | 360.2743 | 360.2743 | 360.2743 | 360.2743 | 360.2743 | 360.2743 | 360.2743 | 360.2743 | 360.2743 | 360.2743 | 360.2743 |  | 20.9709 | 215.1544 | 268.2072 | 276.3809 | 281.5313 | 292.9348 | 319.9304 | 334.6257 | 362.705 | 448.1513 | 377.6034 | 363.7719 | 382.3354 | 422.9874 | 395.3941 | 395.3941 | 395.3941 | 395.3941 | 395.3941 | 395.3941 | 395.3941 | 395.3941 | 395.3941 | 395.3941 | 395.3941 | 395.3941 | 395.3941 | 395.3941 | 395.3941 | 395.3941
90% |  | 893.0903 | 1174.5993 | 1222.3975 | 1259.4956 | 1323.7687 | 1470.3172 | 1568.2056 | 1692.4401 | 1756.8041 | 1813.2726 | 1708.2805 | 1830.7812 | 2023.5105 | 1876.813 | 1876.813 | 1876.813 | 1876.813 | 1876.813 | 1876.813 | 1876.813 | 1876.813 | 1876.813 | 1876.813 | 1876.813 | 1876.813 | 1876.813 | 1876.813 | 1876.813 | 1876.813 |  | 23.4784 | 1076.68 | 1369.1919 | 1414.2584 | 1442.6557 | 1505.5298 | 1654.3725 | 1735.397 | 1890.2148 | 2361.3315 | 1972.3588 | 1896.0974 | 1998.4489 | 2222.5876 | 2070.4492 | 2070.4492 | 2070.4492 | 2070.4492 | 2070.4492 | 2070.4492 | 2070.4492 | 2070.4492 | 2070.4492 | 2070.4492 | 2070.4492 | 2070.4492 | 2070.4492 | 2070.4492 | 2070.4492 | 2070.4492
85% |  | 1762.1242 | 2449.8304 | 2566.598 | 2657.2259 | 2814.2407 | 3172.248 | 3411.3825 | 3714.8785 | 3872.1151 | 4010.0635 | 3753.5754 | 4052.8358 | 4523.6597 | 4165.2882 | 4165.2882 | 4165.2882 | 4165.2882 | 4165.2882 | 4165.2882 | 4165.2882 | 4165.2882 | 4165.2882 | 4165.2882 | 4165.2882 | 4165.2882 | 4165.2882 | 4165.2882 | 4165.2882 | 4165.2882 |  |  | 2210.6207 | 2925.2063 | 3035.3005 | 3104.6731 | 3258.27 | 3621.8821 | 3819.8191 | 4198.028 | 5348.9323 | 4398.6997 | 4212.3987 | 4462.436 | 5009.9908 | 4638.3275 | 4638.3275 | 4638.3275 | 4638.3275 | 4638.3275 | 4638.3275 | 4638.3275 | 4638.3275 | 4638.3275 | 4638.3275 | 4638.3275 | 4638.3275 | 4638.3275 | 4638.3275 | 4638.3275 | 4638.3275
80% |  | 2007.5732 | 3076.4726 | 3257.9641 | 3398.8267 | 3642.8742 | 4199.3237 | 4571.0097 | 5042.7323 | 5287.1246 | 5501.5374 | 5102.8788 | 5568.0182 | 6299.8181 | 5742.8026 | 5742.8026 | 5742.8026 | 5742.8026 | 5742.8026 | 5742.8026 | 5742.8026 | 5742.8026 | 5742.8026 | 5742.8026 | 5742.8026 | 5742.8026 | 5742.8026 | 5742.8026 | 5742.8026 | 5742.8026 |  |  | 2704.6698 | 3815.3477 | 3986.4666 | 4094.2922 | 4333.0273 | 4898.1884 | 5205.8411 | 5793.6899 | 7582.5364 | 6105.5932 | 5816.0263 | 6204.6584 | 7055.7208 | 6478.0459 | 6478.0459 | 6478.0459 | 6478.0459 | 6478.0459 | 6478.0459 | 6478.0459 | 6478.0459 | 6478.0459 | 6478.0459 | 6478.0459 | 6478.0459 | 6478.0459 | 6478.0459 | 6478.0459 | 6478.0459
75% |  | 1303.991 | 2483.2854 | 2683.5211 | 2838.9319 | 3108.1844 | 3722.1035 | 4132.1769 | 4652.6186 | 4922.2514 | 5158.8086 | 4718.9769 | 5232.1555 | 6039.5351 | 5424.9915 | 5424.9915 | 5424.9915 | 5424.9915 | 5424.9915 | 5424.9915 | 5424.9915 | 5424.9915 | 5424.9915 | 5424.9915 | 5424.9915 | 5424.9915 | 5424.9915 | 5424.9915 | 5424.9915 | 5424.9915 |  |  | 2073.0831 | 3298.4708 | 3487.2627 | 3606.2244 | 3869.6159 | 4493.1463 | 4832.5731 | 5481.1343 | 7454.7312 | 5825.2508 | 5505.7776 | 5934.5473 | 6873.5067 | 6236.17 | 6236.17 | 6236.17 | 6236.17 | 6236.17 | 6236.17 | 6236.17 | 6236.17 | 6236.17 | 6236.17 | 6236.17 | 6236.17 | 6236.17 | 6236.17 | 6236.17 | 6236.17
70% |  | 329.0664 | 1554.418 | 1769.5601 | 1936.5403 | 2225.837 | 2885.4588 | 3326.0597 | 3885.2453 | 4174.9507 | 4429.1182 | 3956.5436 | 4507.9253 | 5375.4095 | 4715.1168 | 4715.1168 | 4715.1168 | 4715.1168 | 4715.1168 | 4715.1168 | 4715.1168 | 4715.1168 | 4715.1168 | 4715.1168 | 4715.1168 | 4715.1168 | 4715.1168 | 4715.1168 | 4715.1168 | 4715.1168 |  |  | 1113.6786 | 2430.2892 | 2633.1355 | 2760.9532 | 3043.9527 | 3713.9012 | 4078.5963 | 4775.4391 | 6895.9587 | 5145.173 | 4801.917 | 5262.606 | 6271.4654 | 5586.6828 | 5586.6828 | 5586.6828 | 5586.6828 | 5586.6828 | 5586.6828 | 5586.6828 | 5586.6828 | 5586.6828 | 5586.6828 | 5586.6828 | 5586.6828 | 5586.6828 | 5586.6828 | 5586.6828 | 5586.6828
65% |  |  | 357.6004 | 534.3679 | 694.2568 | 998.0683 | 1693.1832 | 2157.4921 | 2746.7664 | 3052.0604 | 3319.9042 | 2821.9012 | 3402.9518 | 4317.1138 | 3621.2919 | 3621.2919 | 3621.2919 | 3621.2919 | 3621.2919 | 3621.2919 | 3621.2919 | 3621.2919 | 3621.2919 | 3621.2919 | 3621.2919 | 3621.2919 | 3621.2919 | 3621.2919 | 3621.2919 | 3621.2919 |  |  | 102.8871 | 1213.5217 | 1427.2829 | 1561.9782 | 1860.2054 | 2566.2027 | 2950.5214 | 3684.8601 | 5919.4811 | 4074.4887 | 3712.7627 | 4198.2405 | 5261.3849 | 4539.7553 | 4539.7553 | 4539.7553 | 4539.7553 | 4539.7553 | 4539.7553 | 4539.7553 | 4539.7553 | 4539.7553 | 4539.7553 | 4539.7553 | 4539.7553 | 4539.7553 | 4539.7553 | 4539.7553 | 4539.7553
60% | [5 empty] | 22.0281 | 310.8024 | 678.0302 | 1303.0236 | 1639.1146 | 1933.9776 | 1385.7376 | 2025.4028 | 3031.7826 | 2265.7684 | 2265.7684 | 2265.7684 | 2265.7684 | 2265.7684 | 2265.7684 | 2265.7684 | 2265.7684 | 2265.7684 | 2265.7684 | 2265.7684 | 2265.7684 | 2265.7684 | 2265.7684 | 2265.7684 | 2265.7684 |  |  |  | 76.5442 | 162.0907 | 231.6582 | 427.4699 | 1104.2451 | 1527.3326 | 2335.7491 | 4795.7916 | 2764.6822 | 2366.4664 | 2900.9178 | 4071.3088 | 3276.8835 | 3276.8835 | 3276.8835 | 3276.8835 | 3276.8835 | 3276.8835 | 3276.8835 | 3276.8835 | 3276.8835 | 3276.8835 | 3276.8835 | 3276.8835 | 3276.8835 | 3276.8835 | 3276.8835 | 3276.8835
55% | [8 empty] | 31.8697 | 126.1441 | 258.2709 | 49.3804 | 308.3505 | 1129.5587 | 460.0863 | 460.0863 | 460.0863 | 460.0863 | 460.0863 | 460.0863 | 460.0863 | 460.0863 | 460.0863 | 460.0863 | 460.0863 | 460.0863 | 460.0863 | 460.0863 | 460.0863 | 460.0863 | [7 empty] | 5.3153 | 88.0196 | 509.6432 | 3087.7799 | 864.8984 | 532.1518 | 995.8136 | 2281.8383 | 1398.09 | 1398.09 | 1398.09 | 1398.09 | 1398.09 | 1398.09 | 1398.09 | 1398.09 | 1398.09 | 1398.09 | 1398.09 | 1398.09 | 1398.09 | 1398.09 | 1398.09 | 1398.09
50% | [40 empty] | 614.3108 |  |  |  | 194.216 | 2.9117 | 2.9117 | 2.9117 | 2.9117 | 2.9117 | 2.9117 | 2.9117 | 2.9117 | 2.9117 | 2.9117 | 2.9117 | 2.9117 | 2.9117 | 2.9117 | 2.9117 | 2.9117
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0.54918 | 6604.2219 | 11489.0059 | 12441.5431 | 13203.537 | 14572.5364 | 17934.9211 | 20355.1972 | 23617.6722 | 25397.9652 | 27009.2878 | 24050.1225 | 27518.0067 | 33387.7721 | 28875.549 | 28875.549 | 28875.549 | 28875.549 | 28875.549 | 28875.549 | 28875.549 | 28875.549 | 28875.549 | 28875.549 | 28875.549 | 28875.549 | 28875.549 | 28875.549 | 28875.549 | 28875.549 | E @ R (MWh) | 65.83 | 9645.0538 | 15579.729 | 16610.4697 | 17275.6237 | 18790.1152 | 22593.9352 | 24799.0804 | 29276.1679 | 44809.5484 | 31783.1886 | 29452.7715 | 32597.5368 | 39949.1057 | 34888.7767 | 34888.7767 | 34888.7767 | 34888.7767 | 34888.7767 | 34888.7767 | 34888.7767 | 34888.7767 | 34888.7767 | 34888.7767 | 34888.7767 | 34888.7767 | 34888.7767 | 34888.7767 | 34888.7767 | 34888.7767
Option 1 Winter POE50 W E @ R (MWh) N 1 | 0.38442 | 4622.9553 | 8042.3041 | 8709.0802 | 9242.4759 | 10200.7755 | 12554.4447 | 14248.638 | 16532.3706 | 17778.5756 | 18906.5014 | 16835.0857 | 19262.6047 | 23371.4405 | 20212.8843 | 20212.8843 | 20212.8843 | 20212.8843 | 20212.8843 | 20212.8843 | 20212.8843 | 20212.8843 | 20212.8843 | 20212.8843 | 20212.8843 | 20212.8843 | 20212.8843 | 20212.8843 | 20212.8843 | 20212.8843 | Option 1 Winter POE10 W E @ R (MWh) N 1 | 19.749 | 2893.5161 | 4673.9187 | 4983.1409 | 5182.6871 | 5637.0346 | 6778.1806 | 7439.7241 | 8782.8504 | 13442.8645 | 9534.9566 | 8835.8314 | 9779.261 | 11984.7317 | 10466.633 | 10466.633 | 10466.633 | 10466.633 | 10466.633 | 10466.633 | 10466.633 | 10466.633 | 10466.633 | 10466.633 | 10466.633 | 10466.633 | 10466.633 | 10466.633 | 10466.633 | 10466.633
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 26.6023 | 54.4041 | 61.674 | 61.2344 | 61.2607 | 62.0035 | 63.97 | 65.2829 | 66.5702 | 68.0765 | 69.4698 | 70.8245 | 70.9755 | 72.5573 | 71.351 | 71.351 | 71.351 | 71.351 | 71.351 | 71.351 | 71.351 | 71.351 | 71.351 | 71.351 | 71.351 | 71.351 | 71.351 | 71.351 | 71.351 | 71.351
98% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 12.8254 | 26.5866 | 30.185 | 29.9674 | 29.9804 | 30.3481 | 31.3215 | 31.9713 | 32.6085 | 33.3541 | 34.0438 | 34.7143 | 34.789 | 35.572 | 34.9749 | 34.9749 | 34.9749 | 34.9749 | 34.9749 | 34.9749 | 34.9749 | 34.9749 | 34.9749 | 34.9749 | 34.9749 | 34.9749 | 34.9749 | 34.9749 | 34.9749 | 34.9749
97% | 3.7957 | 10.5928 | 12.4418 | 12.3872 | 12.3841 | 12.5942 | 12.8249 | 13.2988 | 13.6394 | 13.8238 | 14.0252 | 14.2099 | 14.5441 | 14.9591 | 14.9293 | 14.9293 | 14.9293 | 14.9293 | 14.9293 | 14.9293 | 14.9293 | 14.9293 | 14.9293 | 14.9293 | 14.9293 | 14.9293 | 14.9293 | 14.9293 | 14.9293 | 14.9293 |  | 24.6994 | 51.9423 | 59.0661 | 58.6353 | 58.6611 | 59.389 | 61.3159 | 62.6024 | 63.8639 | 65.3399 | 66.7052 | 68.0327 | 68.1807 | 69.7307 | 68.5486 | 68.5486 | 68.5486 | 68.5486 | 68.5486 | 68.5486 | 68.5486 | 68.5486 | 68.5486 | 68.5486 | 68.5486 | 68.5486 | 68.5486 | 68.5486 | 68.5486 | 68.5486
95% | 17.3774 | 50.84 | 59.9429 | 59.674 | 59.6588 | 60.6932 | 61.8287 | 64.162 | 65.8388 | 66.7468 | 67.7383 | 68.6472 | 70.2926 | 72.3358 | 72.1891 | 72.1891 | 72.1891 | 72.1891 | 72.1891 | 72.1891 | 72.1891 | 72.1891 | 72.1891 | 72.1891 | 72.1891 | 72.1891 | 72.1891 | 72.1891 | 72.1891 | 72.1891 |  | 34.9082 | 75.1439 | 85.6653 | 85.029 | 85.0671 | 86.1421 | 88.988 | 90.8882 | 92.7512 | 94.9312 | 96.9477 | 98.9082 | 99.1268 | 101.416 | 99.6701 | 99.6701 | 99.6701 | 99.6701 | 99.6701 | 99.6701 | 99.6701 | 99.6701 | 99.6701 | 99.6701 | 99.6701 | 99.6701 | 99.6701 | 99.6701 | 99.6701 | 99.6701
90% | 24.555 | 82.5918 | 98.3797 | 97.9133 | 97.8869 | 99.681 | 101.6504 | 105.6971 | 108.6054 | 110.1802 | 111.8997 | 113.4762 | 116.33 | 119.8735 | 119.6191 | 119.6191 | 119.6191 | 119.6191 | 119.6191 | 119.6191 | 119.6191 | 119.6191 | 119.6191 | 119.6191 | 119.6191 | 119.6191 | 119.6191 | 119.6191 | 119.6191 | 119.6191 |  | 134.6084 | 309.068 | 354.6878 | 351.9289 | 352.0941 | 356.7553 | 369.095 | 377.3339 | 385.4121 | 394.8642 | 403.6075 | 412.1082 | 413.0559 | 422.9818 | 415.4119 | 415.4119 | 415.4119 | 415.4119 | 415.4119 | 415.4119 | 415.4119 | 415.4119 | 415.4119 | 415.4119 | 415.4119 | 415.4119 | 415.4119 | 415.4119 | 415.4119 | 415.4119
85% | 44.847 | 209.5458 | 254.3493 | 253.0259 | 252.9509 | 258.0423 | 263.6311 | 275.1149 | 283.3684 | 287.8374 | 292.7171 | 297.1909 | 305.2894 | 315.3454 | 314.6234 | 314.6234 | 314.6234 | 314.6234 | 314.6234 | 314.6234 | 314.6234 | 314.6234 | 314.6234 | 314.6234 | 314.6234 | 314.6234 | 314.6234 | 314.6234 | 314.6234 | 314.6234 |  | 102.4961 | 267.5254 | 310.6793 | 308.0696 | 308.2258 | 312.635 | 324.3078 | 332.1012 | 339.7428 | 348.684 | 356.9547 | 364.9959 | 365.8924 | 375.2817 | 368.121 | 368.121 | 368.121 | 368.121 | 368.121 | 368.121 | 368.121 | 368.121 | 368.121 | 368.121 | 368.121 | 368.121 | 368.121 | 368.121 | 368.121 | 368.121
80% | 23.7465 | 253.802 | 316.3847 | 314.536 | 314.4314 | 321.5432 | 329.3497 | 345.3906 | 356.9192 | 363.1617 | 369.9778 | 376.2269 | 387.5391 | 401.5855 | 400.577 | 400.577 | 400.577 | 400.577 | 400.577 | 400.577 | 400.577 | 400.577 | 400.577 | 400.577 | 400.577 | 400.577 | 400.577 | 400.577 | 400.577 | 400.577 |  | 52.1361 | 167.3947 | 197.5339 | 195.7112 | 195.8203 | 198.8998 | 207.0522 | 212.4953 | 217.8322 | 224.0769 | 229.8532 | 235.4693 | 236.0954 | 242.6531 | 237.6519 | 237.6519 | 237.6519 | 237.6519 | 237.6519 | 237.6519 | 237.6519 | 237.6519 | 237.6519 | 237.6519 | 237.6519 | 237.6519 | 237.6519 | 237.6519 | 237.6519 | 237.6519
75% | 0.18716 | 547.1351 | 710.2768 | 705.4576 | 705.1848 | 723.724 | 744.0742 | 785.8898 | 815.9429 | 832.2159 | 849.9842 | 866.2744 | 895.7633 | 932.3798 | 929.7508 | 929.7508 | 929.7508 | 929.7508 | 929.7508 | 929.7508 | 929.7508 | 929.7508 | 929.7508 | 929.7508 | 929.7508 | 929.7508 | 929.7508 | 929.7508 | 929.7508 | 929.7508 |  | 53.8635 | 259.5826 | 313.3765 | 310.1233 | 310.3181 | 315.8145 | 330.3652 | 340.0803 | 349.6059 | 360.7517 | 371.0616 | 381.0855 | 382.203 | 393.9074 | 384.9811 | 384.9811 | 384.9811 | 384.9811 | 384.9811 | 384.9811 | 384.9811 | 384.9811 | 384.9811 | 384.9811 | 384.9811 | 384.9811 | 384.9811 | 384.9811 | 384.9811 | 384.9811
70% |  | 720.2141 | 1002.0732 | 993.7472 | 993.2758 | 1025.3059 | 1060.4649 | 1132.7095 | 1184.6321 | 1212.7469 | 1243.4451 | 1271.5896 | 1322.5375 | 1385.7996 | 1381.2574 | 1381.2574 | 1381.2574 | 1381.2574 | 1381.2574 | 1381.2574 | 1381.2574 | 1381.2574 | 1381.2574 | 1381.2574 | 1381.2574 | 1381.2574 | 1381.2574 | 1381.2574 | 1381.2574 | 1381.2574 |  | 21.0605 | 391.6455 | 489.6437 | 483.7172 | 484.0719 | 494.0849 | 520.5925 | 538.2908 | 555.6439 | 575.9484 | 594.7305 | 612.9912 | 615.027 | 636.3493 | 620.088 | 620.088 | 620.088 | 620.088 | 620.088 | 620.088 | 620.088 | 620.088 | 620.088 | 620.088 | 620.088 | 620.088 | 620.088 | 620.088 | 620.088 | 620.088
65% |  | 1159.8257 | 1867.7211 | 1846.81 | 1845.6263 | 1926.0704 | 2014.373 | 2195.817 | 2326.2218 | 2396.8327 | 2473.9318 | 2544.6175 | 2672.5742 | 2831.4585 | 2820.0507 | 2820.0507 | 2820.0507 | 2820.0507 | 2820.0507 | 2820.0507 | 2820.0507 | 2820.0507 | 2820.0507 | 2820.0507 | 2820.0507 | 2820.0507 | 2820.0507 | 2820.0507 | 2820.0507 | 2820.0507 |  |  | 375.3893 | 498.6861 | 491.2298 | 491.676 | 504.2739 | 537.6246 | 559.8917 | 581.7247 | 607.2709 | 630.9016 | 653.8765 | 656.4378 | 683.2646 | 662.8054 | 662.8054 | 662.8054 | 662.8054 | 662.8054 | 662.8054 | 662.8054 | 662.8054 | 662.8054 | 662.8054 | 662.8054 | 662.8054 | 662.8054 | 662.8054 | 662.8054 | 662.8054
60% |  | 595.1039 | 1629.6346 | 1599.0683 | 1597.338 | 1714.9251 | 1843.9992 | 2109.2202 | 2299.836 | 2403.0496 | 2515.7473 | 2619.0702 | 2806.1076 | 3038.3525 | 3021.6775 | 3021.6775 | 3021.6775 | 3021.6775 | 3021.6775 | 3021.6775 | 3021.6775 | 3021.6775 | 3021.6775 | 3021.6775 | 3021.6775 | 3021.6775 | 3021.6775 | 3021.6775 | 3021.6775 | 3021.6775 |  |  | 374.3821 | 567.3189 | 555.6511 | 556.3494 | 576.0627 | 628.2504 | 663.0943 | 697.2588 | 737.234 | 774.2116 | 810.1631 | 814.1711 | 856.15 | 824.1351 | 824.1351 | 824.1351 | 824.1351 | 824.1351 | 824.1351 | 824.1351 | 824.1351 | 824.1351 | 824.1351 | 824.1351 | 824.1351 | 824.1351 | 824.1351 | 824.1351 | 824.1351
55% |  |  | 438.6107 | 413.2466 | 411.832 | 513.1119 | 636.1403 | 924.2646 | 1139.8067 | 1256.5173 | 1383.9522 | 1500.7863 | 1712.2821 | 1974.8972 | 1956.0416 | 1956.0416 | 1956.0416 | 1956.0416 | 1956.0416 | 1956.0416 | 1956.0416 | 1956.0416 | 1956.0416 | 1956.0416 | 1956.0416 | 1956.0416 | 1956.0416 | 1956.0416 | 1956.0416 | 1956.0416 |  |  | 239.8473 | 609.6211 | 587.1995 | 588.5414 | 626.4237 | 726.7105 | 793.6685 | 859.321 | 936.1395 | 1007.1978 | 1076.2842 | 1083.9862 | 1164.6552 | 1103.1336 | 1103.1336 | 1103.1336 | 1103.1336 | 1103.1336 | 1103.1336 | 1103.1336 | 1103.1336 | 1103.1336 | 1103.1336 | 1103.1336 | 1103.1336 | 1103.1336 | 1103.1336 | 1103.1336 | 1103.1336
50% | [7 empty] | 3.4281 | 36.6085 | 68.9695 | 115.5831 | 168.4762 | 288.3744 | 479.2895 | 464.0651 | 464.0651 | 464.0651 | 464.0651 | 464.0651 | 464.0651 | 464.0651 | 464.0651 | 464.0651 | 464.0651 | 464.0651 | 464.0651 | 464.0651 | 464.0651 | 464.0651 | 464.0651 |  |  |  | 218.9141 | 191.3668 | 192.9659 | 240.7061 | 390.8095 | 509.6193 | 640.0757 | 807.8717 | 965.5671 | 1118.8862 | 1135.9788 | 1315.0026 | 1178.4715 | 1178.4715 | 1178.4715 | 1178.4715 | 1178.4715 | 1178.4715 | 1178.4715 | 1178.4715 | 1178.4715 | 1178.4715 | 1178.4715 | 1178.4715 | 1178.4715 | 1178.4715 | 1178.4715 | 1178.4715
45% | [40 empty] | 3.1349 | 28.4196 | 76.7087 | 83.5101 | 171.461 | 101.6343 | 101.6343 | 101.6343 | 101.6343 | 101.6343 | 101.6343 | 101.6343 | 101.6343 | 101.6343 | 101.6343 | 101.6343 | 101.6343 | 101.6343 | 101.6343 | 101.6343 | 101.6343
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 114.5088 | 3629.6513 | 6389.8148 | 6295.8662 | 6290.5691 | 6655.6913 | 7068.3364 | 7954.9925 | 8631.4193 | 9012.0818 | 9439.0017 | 9840.5652 | 10591.6343 | 11566.2763 | 11494.7808 | 11494.7808 | 11494.7808 | 11494.7808 | 11494.7808 | 11494.7808 | 11494.7808 | 11494.7808 | 11494.7808 | 11494.7808 | 11494.7808 | 11494.7808 | 11494.7808 | 11494.7808 | 11494.7808 | 11494.7808 | E @ R (MWh) | 463.1998 | 2592.9116 | 3797.0519 | 3709.8635 | 3715.0322 | 3863.5385 | 4280.4031 | 4577.3201 | 4882.411 | 5257.6779 | 5629.6718 | 6015.0485 | 6059.4299 | 6540.9827 | 6170.9785 | 6170.9785 | 6170.9785 | 6170.9785 | 6170.9785 | 6170.9785 | 6170.9785 | 6170.9785 | 6170.9785 | 6170.9785 | 6170.9785 | 6170.9785 | 6170.9785 | 6170.9785 | 6170.9785 | 6170.9785
Option 1 Summer POE50 W E @ R (MWh) N 1 | 80.1561 | 2540.7559 | 4472.8704 | 4407.1063 | 4403.3984 | 4658.9839 | 4947.8355 | 5568.4947 | 6041.9935 | 6308.4573 | 6607.3012 | 6888.3957 | 7414.144 | 8096.3934 | 8046.3465 | 8046.3465 | 8046.3465 | 8046.3465 | 8046.3465 | 8046.3465 | 8046.3465 | 8046.3465 | 8046.3465 | 8046.3465 | 8046.3465 | 8046.3465 | 8046.3465 | 8046.3465 | 8046.3465 | 8046.3465 | Option 1 Summer POE10 W E @ R (MWh) N 1 | 138.9599 | 777.8735 | 1139.1156 | 1112.959 | 1114.5097 | 1159.0616 | 1284.1209 | 1373.196 | 1464.7233 | 1577.3034 | 1688.9015 | 1804.5146 | 1817.829 | 1962.2948 | 1851.2936 | 1851.2936 | 1851.2936 | 1851.2936 | 1851.2936 | 1851.2936 | 1851.2936 | 1851.2936 | 1851.2936 | 1851.2936 | 1851.2936 | 1851.2936 | 1851.2936 | 1851.2936 | 1851.2936 | 1851.2936
Option 2 - 1B New PHS ZSS + Three new feeders
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | 0.52857 | 28.8388 | 36.1886 | 8.851 | 9.8196 | 11.4977 | 15.3239 | 17.8796 | 21.1232 | 22.8037 | 24.278 | 21.5368 | 24.7351 | 29.767 | 25.9369 | 25.9369 | 25.9369 | 25.9369 | 25.9369 | 25.9369 | 25.9369 | 25.9369 | 25.9369 | 25.9369 | 25.9369 | 25.9369 | 25.9369 | 25.9369 | 25.9369 | 25.9369 |  | 5.6789 | 33.6321 | 41.2692 | 13.8603 | 14.6017 | 16.2432 | 20.1293 | 22.2448 | 26.2868 | 38.5871 | 28.4315 | 26.4404 | 29.1127 | 34.9646 | 30.9925 | 30.9925 | 30.9925 | 30.9925 | 30.9925 | 30.9925 | 30.9925 | 30.9925 | 30.9925 | 30.9925 | 30.9925 | 30.9925 | 30.9925 | 30.9925 | 30.9925 | 30.9925
98% | 0.020606 | 33.3788 | 42.11 | 9.6346 | 10.7852 | 12.7786 | 17.3239 | 20.36 | 24.2132 | 26.2094 | 27.9608 | 24.7045 | 28.5039 | 34.4815 | 29.9316 | 29.9316 | 29.9316 | 29.9316 | 29.9316 | 29.9316 | 29.9316 | 29.9316 | 29.9316 | 29.9316 | 29.9316 | 29.9316 | 29.9316 | 29.9316 | 29.9316 | 29.9316 |  | 5.8662 | 39.073 | 48.1454 | 15.5852 | 16.466 | 18.416 | 23.0325 | 25.5455 | 30.3472 | 44.9592 | 32.895 | 30.5297 | 33.7042 | 40.6559 | 35.9373 | 35.9373 | 35.9373 | 35.9373 | 35.9373 | 35.9373 | 35.9373 | 35.9373 | 35.9373 | 35.9373 | 35.9373 | 35.9373 | 35.9373 | 35.9373 | 35.9373 | 35.9373
97% |  | 64.3022 | 81.5872 | 17.2957 | 19.5736 | 23.5201 | 32.5183 | 38.5288 | 46.1569 | 50.109 | 53.5762 | 47.1295 | 54.6512 | 66.485 | 57.4776 | 57.4776 | 57.4776 | 57.4776 | 57.4776 | 57.4776 | 57.4776 | 57.4776 | 57.4776 | 57.4776 | 57.4776 | 57.4776 | 57.4776 | 57.4776 | 57.4776 | 57.4776 |  | 9.8356 | 75.5748 | 93.5354 | 29.0762 | 30.8199 | 34.6804 | 43.8195 | 48.7945 | 58.3005 | 87.2277 | 63.3443 | 58.6617 | 64.9462 | 78.7086 | 69.3671 | 69.3671 | 69.3671 | 69.3671 | 69.3671 | 69.3671 | 69.3671 | 69.3671 | 69.3671 | 69.3671 | 69.3671 | 69.3671 | 69.3671 | 69.3671 | 69.3671 | 69.3671
95% |  | 181.8568 | 232.914 | 43.007 | 49.7355 | 61.3927 | 87.9721 | 105.7261 | 128.2585 | 139.9322 | 150.1738 | 131.1315 | 153.3494 | 188.3046 | 161.6982 | 161.6982 | 161.6982 | 161.6982 | 161.6982 | 161.6982 | 161.6982 | 161.6982 | 161.6982 | 161.6982 | 161.6982 | 161.6982 | 161.6982 | 161.6982 | 161.6982 | 161.6982 |  | 20.9709 | 215.1544 | 268.2072 | 77.8048 | 82.9552 | 94.3586 | 121.3542 | 136.0496 | 164.1288 | 249.5751 | 179.0273 | 165.1958 | 183.7592 | 224.4112 | 196.8179 | 196.8179 | 196.8179 | 196.8179 | 196.8179 | 196.8179 | 196.8179 | 196.8179 | 196.8179 | 196.8179 | 196.8179 | 196.8179 | 196.8179 | 196.8179 | 196.8179 | 196.8179
90% |  | 893.0903 | 1174.5993 | 127.528 | 164.626 | 228.8992 | 375.4477 | 473.3361 | 597.5706 | 661.9346 | 718.4031 | 613.411 | 735.9117 | 928.641 | 781.9435 | 781.9435 | 781.9435 | 781.9435 | 781.9435 | 781.9435 | 781.9435 | 781.9435 | 781.9435 | 781.9435 | 781.9435 | 781.9435 | 781.9435 | 781.9435 | 781.9435 | 781.9435 |  | 23.4784 | 1076.68 | 1369.1919 | 319.3889 | 347.7862 | 410.6603 | 559.503 | 640.5275 | 795.3453 | 1266.462 | 877.4893 | 801.2279 | 903.5794 | 1127.7181 | 975.5797 | 975.5797 | 975.5797 | 975.5797 | 975.5797 | 975.5797 | 975.5797 | 975.5797 | 975.5797 | 975.5797 | 975.5797 | 975.5797 | 975.5797 | 975.5797 | 975.5797 | 975.5797
85% |  | 1762.1242 | 2449.8304 | 13.9888 | 46.9401 | 147.7875 | 497.5602 | 736.6948 | 1040.1907 | 1197.4273 | 1335.3757 | 1078.8876 | 1378.148 | 1848.9719 | 1490.6005 | 1490.6005 | 1490.6005 | 1490.6005 | 1490.6005 | 1490.6005 | 1490.6005 | 1490.6005 | 1490.6005 | 1490.6005 | 1490.6005 | 1490.6005 | 1490.6005 | 1490.6005 | 1490.6005 | 1490.6005 |  |  | 2210.6207 | 2925.2063 | 360.6127 | 429.9853 | 583.5822 | 947.1943 | 1145.1313 | 1523.3402 | 2674.2445 | 1724.0119 | 1537.7109 | 1787.7482 | 2335.303 | 1963.6397 | 1963.6397 | 1963.6397 | 1963.6397 | 1963.6397 | 1963.6397 | 1963.6397 | 1963.6397 | 1963.6397 | 1963.6397 | 1963.6397 | 1963.6397 | 1963.6397 | 1963.6397 | 1963.6397 | 1963.6397
80% |  | 2007.5732 | 3076.4726 |  |  |  | 119.44 | 413.752 | 885.4746 | 1129.8668 | 1344.2797 | 945.621 | 1410.7605 | 2142.5604 | 1585.5449 | 1585.5449 | 1585.5449 | 1585.5449 | 1585.5449 | 1585.5449 | 1585.5449 | 1585.5449 | 1585.5449 | 1585.5449 | 1585.5449 | 1585.5449 | 1585.5449 | 1585.5449 | 1585.5449 | 1585.5449 |  |  | 2704.6698 | 3815.3477 | 29.3205 | 67.56 | 205.8144 | 740.9307 | 1048.5834 | 1636.4321 | 3425.2786 | 1948.3355 | 1658.7686 | 2047.4006 | 2898.4631 | 2320.7882 | 2320.7882 | 2320.7882 | 2320.7882 | 2320.7882 | 2320.7882 | 2320.7882 | 2320.7882 | 2320.7882 | 2320.7882 | 2320.7882 | 2320.7882 | 2320.7882 | 2320.7882 | 2320.7882 | 2320.7882
75% |  | 1303.991 | 2483.2854 |  |  |  |  | 0.13186 | 156.9818 | 348.5536 | 572.1931 | 197.4143 | 645.54 | 1452.9196 | 838.376 | 838.376 | 838.376 | 838.376 | 838.376 | 838.376 | 838.376 | 838.376 | 838.376 | 838.376 | 838.376 | 838.376 | 838.376 | 838.376 | 838.376 | 838.376 |  |  | 2073.0831 | 3298.4708 |  |  |  | 78.256 | 276.8645 | 894.5188 | 2868.1157 | 1238.6353 | 919.1621 | 1347.9318 | 2286.8912 | 1649.5545 | 1649.5545 | 1649.5545 | 1649.5545 | 1649.5545 | 1649.5545 | 1649.5545 | 1649.5545 | 1649.5545 | 1649.5545 | 1649.5545 | 1649.5545 | 1649.5545 | 1649.5545 | 1649.5545 | 1649.5545
70% |  | 329.0664 | 1554.418 | [7 empty] | 2.7075 |  | 11.1089 | 458.2707 | 59.7915 | 59.7915 | 59.7915 | 59.7915 | 59.7915 | 59.7915 | 59.7915 | 59.7915 | 59.7915 | 59.7915 | 59.7915 | 59.7915 | 59.7915 | 59.7915 | 59.7915 | 59.7915 |  |  | 1113.6786 | 2430.2892 | [5 empty] | 81.0608 | 1967.8967 | 278.7956 | 91.39 | 365.0839 | 1343.4035 | 658.6208 | 658.6208 | 658.6208 | 658.6208 | 658.6208 | 658.6208 | 658.6208 | 658.6208 | 658.6208 | 658.6208 | 658.6208 | 658.6208 | 658.6208 | 658.6208 | 658.6208 | 658.6208
65% | FY27: 357.6004 |  |  | 102.8871 | 1213.5217 | [6 empty] | 726.4458 |  |  |  | 217.2256 | 0.7562 | 0.7562 | 0.7562 | 0.7562 | 0.7562 | 0.7562 | 0.7562 | 0.7562 | 0.7562 | 0.7562 | 0.7562 | 0.7562 | 0.7562 | 0.7562 | 0.7562 | 0.7562
60% | [33 empty] | 76.5442
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0.54918 | 6604.2219 | 11489.0059 | 220.3052 | 301.48 | 485.8758 | 1145.5862 | 1806.4092 | 2899.9695 | 3576.8366 | 4228.9479 | 3059.8361 | 4442.7087 | 7150.4018 | 5031.3006 | 5031.3006 | 5031.3006 | 5031.3006 | 5031.3006 | 5031.3006 | 5031.3006 | 5031.3006 | 5031.3006 | 5031.3006 | 5031.3006 | 5031.3006 | 5031.3006 | 5031.3006 | 5031.3006 | 5031.3006 | E @ R (MWh) | 65.83 | 9645.0538 | 15579.729 | 845.6486 | 990.1742 | 1363.7552 | 2534.2196 | 3343.741 | 5209.7607 | 13348.7924 | 6370.9655 | 5289.0871 | 6763.2663 | 10587.745 | 7902.054 | 7902.054 | 7902.054 | 7902.054 | 7902.054 | 7902.054 | 7902.054 | 7902.054 | 7902.054 | 7902.054 | 7902.054 | 7902.054 | 7902.054 | 7902.054 | 7902.054 | 7902.054
Option 2 Winter POE50 W E @ R (MWh) N 1 | 0.38442 | 4622.9553 | 8042.3041 | 154.2136 | 211.036 | 340.1131 | 801.9103 | 1264.4864 | 2029.9786 | 2503.7856 | 2960.2635 | 2141.8853 | 3109.8961 | 5005.2813 | 3521.9104 | 3521.9104 | 3521.9104 | 3521.9104 | 3521.9104 | 3521.9104 | 3521.9104 | 3521.9104 | 3521.9104 | 3521.9104 | 3521.9104 | 3521.9104 | 3521.9104 | 3521.9104 | 3521.9104 | 3521.9104 | Option 2 Winter POE10 W E @ R (MWh) N 1 | 19.749 | 2893.5161 | 4673.9187 | 253.6946 | 297.0523 | 409.1266 | 760.2659 | 1003.1223 | 1562.9282 | 4004.6377 | 1911.2897 | 1586.7261 | 2028.9799 | 3176.3235 | 2370.6162 | 2370.6162 | 2370.6162 | 2370.6162 | 2370.6162 | 2370.6162 | 2370.6162 | 2370.6162 | 2370.6162 | 2370.6162 | 2370.6162 | 2370.6162 | 2370.6162 | 2370.6162 | 2370.6162 | 2370.6162
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 26.6023 | 54.4041 | 61.674 | 32.1359 | 32.1622 | 32.905 | 34.8715 | 36.1844 | 37.4717 | 38.978 | 40.3714 | 41.726 | 41.8771 | 43.4588 | 42.2525 | 42.2525 | 42.2525 | 42.2525 | 42.2525 | 42.2525 | 42.2525 | 42.2525 | 42.2525 | 42.2525 | 42.2525 | 42.2525 | 42.2525 | 42.2525 | 42.2525 | 42.2525
98% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 12.8254 | 26.5866 | 30.185 | 15.5644 | 15.5774 | 15.9451 | 16.9184 | 17.5683 | 18.2055 | 18.9511 | 19.6408 | 20.3113 | 20.386 | 21.169 | 20.5719 | 20.5719 | 20.5719 | 20.5719 | 20.5719 | 20.5719 | 20.5719 | 20.5719 | 20.5719 | 20.5719 | 20.5719 | 20.5719 | 20.5719 | 20.5719 | 20.5719 | 20.5719
97% | 3.7957 | 10.5928 | 12.4418 | 5.2588 | 5.2557 | 5.4658 | 5.6965 | 6.1704 | 6.511 | 6.6955 | 6.8968 | 7.0815 | 7.4157 | 7.8307 | 7.8009 | 7.8009 | 7.8009 | 7.8009 | 7.8009 | 7.8009 | 7.8009 | 7.8009 | 7.8009 | 7.8009 | 7.8009 | 7.8009 | 7.8009 | 7.8009 | 7.8009 | 7.8009 |  | 24.6994 | 51.9423 | 59.0661 | 30.1217 | 30.1475 | 30.8754 | 32.8023 | 34.0889 | 35.3503 | 36.8263 | 38.1916 | 39.5191 | 39.6671 | 41.2171 | 40.035 | 40.035 | 40.035 | 40.035 | 40.035 | 40.035 | 40.035 | 40.035 | 40.035 | 40.035 | 40.035 | 40.035 | 40.035 | 40.035 | 40.035 | 40.035
95% | 17.3774 | 50.84 | 59.9429 | 24.5804 | 24.5652 | 25.5996 | 26.7351 | 29.0683 | 30.7452 | 31.6532 | 32.6446 | 33.5536 | 35.199 | 37.2421 | 37.0954 | 37.0954 | 37.0954 | 37.0954 | 37.0954 | 37.0954 | 37.0954 | 37.0954 | 37.0954 | 37.0954 | 37.0954 | 37.0954 | 37.0954 | 37.0954 | 37.0954 | 37.0954 |  | 34.9082 | 75.1439 | 85.6653 | 42.9166 | 42.9547 | 44.0297 | 46.8757 | 48.7758 | 50.6389 | 52.8188 | 54.8353 | 56.7958 | 57.0144 | 59.3036 | 57.5577 | 57.5577 | 57.5577 | 57.5577 | 57.5577 | 57.5577 | 57.5577 | 57.5577 | 57.5577 | 57.5577 | 57.5577 | 57.5577 | 57.5577 | 57.5577 | 57.5577 | 57.5577
90% | 24.555 | 82.5918 | 98.3797 | 37.0478 | 37.0214 | 38.8155 | 40.7848 | 44.8315 | 47.7399 | 49.3147 | 51.0342 | 52.6107 | 55.4644 | 59.008 | 58.7535 | 58.7535 | 58.7535 | 58.7535 | 58.7535 | 58.7535 | 58.7535 | 58.7535 | 58.7535 | 58.7535 | 58.7535 | 58.7535 | 58.7535 | 58.7535 | 58.7535 | 58.7535 |  | 134.6084 | 309.068 | 354.6878 | 169.3323 | 169.4974 | 174.1586 | 186.4984 | 194.7372 | 202.8154 | 212.2675 | 221.0109 | 229.5116 | 230.4593 | 240.3852 | 232.8153 | 232.8153 | 232.8153 | 232.8153 | 232.8153 | 232.8153 | 232.8153 | 232.8153 | 232.8153 | 232.8153 | 232.8153 | 232.8153 | 232.8153 | 232.8153 | 232.8153 | 232.8153
85% | 44.847 | 209.5458 | 254.3493 | 80.2993 | 80.2244 | 85.3158 | 90.9046 | 102.3884 | 110.6418 | 115.1109 | 119.9906 | 124.4643 | 132.5629 | 142.6188 | 141.8968 | 141.8968 | 141.8968 | 141.8968 | 141.8968 | 141.8968 | 141.8968 | 141.8968 | 141.8968 | 141.8968 | 141.8968 | 141.8968 | 141.8968 | 141.8968 | 141.8968 | 141.8968 |  | 102.4961 | 267.5254 | 310.6793 | 135.343 | 135.4992 | 139.9085 | 151.5812 | 159.3747 | 167.0162 | 175.9574 | 184.2282 | 192.2694 | 193.1658 | 202.5552 | 195.3945 | 195.3945 | 195.3945 | 195.3945 | 195.3945 | 195.3945 | 195.3945 | 195.3945 | 195.3945 | 195.3945 | 195.3945 | 195.3945 | 195.3945 | 195.3945 | 195.3945 | 195.3945
80% | 23.7465 | 253.802 | 316.3847 | 73.2672 | 73.1626 | 80.2744 | 88.0809 | 104.1218 | 115.6504 | 121.8929 | 128.709 | 134.9581 | 146.2703 | 160.3167 | 159.3082 | 159.3082 | 159.3082 | 159.3082 | 159.3082 | 159.3082 | 159.3082 | 159.3082 | 159.3082 | 159.3082 | 159.3082 | 159.3082 | 159.3082 | 159.3082 | 159.3082 | 159.3082 |  | 52.1361 | 167.3947 | 197.5339 | 75.0768 | 75.1859 | 78.2654 | 86.4178 | 91.8609 | 97.1978 | 103.4425 | 109.2188 | 114.8349 | 115.461 | 122.0187 | 117.0175 | 117.0175 | 117.0175 | 117.0175 | 117.0175 | 117.0175 | 117.0175 | 117.0175 | 117.0175 | 117.0175 | 117.0175 | 117.0175 | 117.0175 | 117.0175 | 117.0175 | 117.0175
75% | 0.18716 | 547.1351 | 710.2768 | 76.5137 | 76.2409 | 94.7801 | 115.1303 | 156.9459 | 186.999 | 203.272 | 221.0403 | 237.3305 | 266.8194 | 303.4359 | 300.8068 | 300.8068 | 300.8068 | 300.8068 | 300.8068 | 300.8068 | 300.8068 | 300.8068 | 300.8068 | 300.8068 | 300.8068 | 300.8068 | 300.8068 | 300.8068 | 300.8068 | 300.8068 |  | 53.8635 | 259.5826 | 313.3765 | 94.8092 | 95.0039 | 100.5003 | 115.0511 | 124.7662 | 134.2918 | 145.4375 | 155.7475 | 165.7714 | 166.8889 | 178.5933 | 169.667 | 169.667 | 169.667 | 169.667 | 169.667 | 169.667 | 169.667 | 169.667 | 169.667 | 169.667 | 169.667 | 169.667 | 169.667 | 169.667 | 169.667 | 169.667
70% |  | 720.2141 | 1002.0732 | 1.2521 | 1.2023 | 6.84 | 18.2018 | 57.8705 | 99.3402 | 126.1233 | 156.8215 | 184.966 | 235.9139 | 299.1761 | 294.6339 | 294.6339 | 294.6339 | 294.6339 | 294.6339 | 294.6339 | 294.6339 | 294.6339 | 294.6339 | 294.6339 | 294.6339 | 294.6339 | 294.6339 | 294.6339 | 294.6339 | 294.6339 |  | 21.0605 | 391.6455 | 489.6437 | 91.4726 | 91.8273 | 101.8403 | 128.3479 | 146.0462 | 163.3993 | 183.7038 | 202.4859 | 220.7466 | 222.7824 | 244.1047 | 227.8434 | 227.8434 | 227.8434 | 227.8434 | 227.8434 | 227.8434 | 227.8434 | 227.8434 | 227.8434 | 227.8434 | 227.8434 | 227.8434 | 227.8434 | 227.8434 | 227.8434 | 227.8434
65% |  | 1159.8257 | 1867.7211 | [6 empty] | 0.011833 | 5.1952 | 18.0905 | 60.6636 | 146.7101 | 139.3426 | 139.3426 | 139.3426 | 139.3426 | 139.3426 | 139.3426 | 139.3426 | 139.3426 | 139.3426 | 139.3426 | 139.3426 | 139.3426 | 139.3426 | 139.3426 | 139.3426 | 139.3426 |  |  | 375.3893 | 498.6861 | 14.619 | 14.839 | 21.6985 | 45.7516 | 66.3873 | 88.2203 | 113.7665 | 137.3972 | 160.3721 | 162.9334 | 189.7602 | 169.301 | 169.301 | 169.301 | 169.301 | 169.301 | 169.301 | 169.301 | 169.301 | 169.301 | 169.301 | 169.301 | 169.301 | 169.301 | 169.301 | 169.301 | 169.301
60% | FY26: 595.1039; FY27: 1629.6346 |  |  | 374.3821 | 567.3189 |  |  |  |  | 0.0052394 | 3.0637 | 13.6012 | 29.7718 | 51.1829 | 53.9082 | 86.4184 | 60.9726 | 60.9726 | 60.9726 | 60.9726 | 60.9726 | 60.9726 | 60.9726 | 60.9726 | 60.9726 | 60.9726 | 60.9726 | 60.9726 | 60.9726 | 60.9726 | 60.9726 | 60.9726
55% | FY27: 438.6107 |  |  | 239.8473 | 609.6211
50% | [33 empty] | 218.9141
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 114.5088 | 3629.6513 | 6389.8148 | 298.2192 | 297.6724 | 337.0911 | 385.534 | 501.3968 | 597.6275 | 654.0742 | 722.3322 | 793.0552 | 940.3092 | 1156.3384 | 1139.6381 | 1139.6381 | 1139.6381 | 1139.6381 | 1139.6381 | 1139.6381 | 1139.6381 | 1139.6381 | 1139.6381 | 1139.6381 | 1139.6381 | 1139.6381 | 1139.6381 | 1139.6381 | 1139.6381 | 1139.6381 | E @ R (MWh) | 463.1998 | 2592.9116 | 3797.0519 | 701.3917 | 702.6947 | 740.1268 | 845.1159 | 919.7951 | 997.671 | 1095.7508 | 1192.8993 | 1293.0411 | 1304.5437 | 1428.9841 | 1333.4284 | 1333.4284 | 1333.4284 | 1333.4284 | 1333.4284 | 1333.4284 | 1333.4284 | 1333.4284 | 1333.4284 | 1333.4284 | 1333.4284 | 1333.4284 | 1333.4284 | 1333.4284 | 1333.4284 | 1333.4284
Option 2 Summer POE50 W E @ R (MWh) N 1 | 80.1561 | 2540.7559 | 4472.8704 | 208.7534 | 208.3707 | 235.9638 | 269.8738 | 350.9777 | 418.3393 | 457.852 | 505.6325 | 555.1386 | 658.2164 | 809.4369 | 797.7467 | 797.7467 | 797.7467 | 797.7467 | 797.7467 | 797.7467 | 797.7467 | 797.7467 | 797.7467 | 797.7467 | 797.7467 | 797.7467 | 797.7467 | 797.7467 | 797.7467 | 797.7467 | Option 2 Summer POE10 W E @ R (MWh) N 1 | 138.9599 | 777.8735 | 1139.1156 | 210.4175 | 210.8084 | 222.038 | 253.5348 | 275.9385 | 299.3013 | 328.7252 | 357.8698 | 387.9123 | 391.3631 | 428.6952 | 400.0285 | 400.0285 | 400.0285 | 400.0285 | 400.0285 | 400.0285 | 400.0285 | 400.0285 | 400.0285 | 400.0285 | 400.0285 | 400.0285 | 400.0285 | 400.0285 | 400.0285 | 400.0285
Option 3 - 2B PHM 3rd Tx + Switchroom + Two new feeders + OFR12 New Feeder
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | FY25: 0.52857; FY26: 28.8388; FY27: 36.1886 |  | 5.6789 | 33.6321 | 41.2692 | [6 empty] | 0.36009
98% | FY25: 0.020606; FY26: 33.3788; FY27: 42.11 |  | 5.8662 | 39.073 | 48.1454
97% | FY26: 64.3022; FY27: 81.5872 |  | 9.8356 | 75.5748 | 93.5354
95% | FY26: 181.8568; FY27: 232.914 |  | 20.9709 | 215.1544 | 268.2072
90% | FY26: 893.0903; FY27: 1174.5993 |  | 23.4784 | 1076.68 | 1369.1919
85% | FY26: 1762.1242; FY27: 2449.8304 |  |  | 2210.6207 | 2925.2063
80% | FY26: 2007.5732; FY27: 3076.4726 |  |  | 2704.6698 | 3815.3477
75% | FY26: 1303.991; FY27: 2483.2854 |  |  | 2073.0831 | 3298.4708
70% | FY26: 329.0664; FY27: 1554.418 |  |  | 1113.6786 | 2430.2892
65% | FY27: 357.6004 |  |  | 102.8871 | 1213.5217
60% | [33 empty] | 76.5442
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0.54918 | 6604.2219 | 11489.0059 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 65.83 | 9645.0538 | 15579.729 | 0 | 0 | 0 | 0 | 0 | 0 | 0.36009 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 Winter POE50 W E @ R (MWh) N 1 | 0.38442 | 4622.9553 | 8042.3041 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 3 Winter POE10 W E @ R (MWh) N 1 | 19.749 | 2893.5161 | 4673.9187 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10803 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | FY25: 0; FY26: 0; FY27: 0 |  | 26.6023 | 54.4041 | 61.674 | [6 empty] | 0.17453 | 1.4003 | 2.7549 | 2.906 | 4.4878 | 3.2814 | 3.2814 | 3.2814 | 3.2814 | 3.2814 | 3.2814 | 3.2814 | 3.2814 | 3.2814 | 3.2814 | 3.2814 | 3.2814 | 3.2814 | 3.2814 | 3.2814 | 3.2814
98% | FY25: 0; FY26: 0; FY27: 0 |  | 12.8254 | 26.5866 | 30.185 | [7 empty] | 0.090945 | 0.67951 | 0.75426 | 1.5372 | 0.9401 | 0.9401 | 0.9401 | 0.9401 | 0.9401 | 0.9401 | 0.9401 | 0.9401 | 0.9401 | 0.9401 | 0.9401 | 0.9401 | 0.9401 | 0.9401 | 0.9401 | 0.9401
97% | FY25: 3.7957; FY26: 10.5928; FY27: 12.4418 |  | 24.6994 | 51.9423 | 59.0661 | [8 empty] | 0.15653 | 0.23464 | 1.6611 | 0.49652 | 0.49652 | 0.49652 | 0.49652 | 0.49652 | 0.49652 | 0.49652 | 0.49652 | 0.49652 | 0.49652 | 0.49652 | 0.49652 | 0.49652 | 0.49652 | 0.49652 | 0.49652
95% | FY25: 17.3774; FY26: 50.84; FY27: 59.9429 |  | 34.9082 | 75.1439 | 85.6653 | [10 empty] | 0.24169
90% | FY25: 24.555; FY26: 82.5918; FY27: 98.3797 |  | 134.6084 | 309.068 | 354.6878
85% | FY25: 44.847; FY26: 209.5458; FY27: 254.3493 |  | 102.4961 | 267.5254 | 310.6793
80% | FY25: 23.7465; FY26: 253.802; FY27: 316.3847 |  | 52.1361 | 167.3947 | 197.5339
75% | FY25: 0.18716; FY26: 547.1351; FY27: 710.2768 |  | 53.8635 | 259.5826 | 313.3765
70% | FY26: 720.2141; FY27: 1002.0732 |  | 21.0605 | 391.6455 | 489.6437
65% | FY26: 1159.8257; FY27: 1867.7211 |  |  | 375.3893 | 498.6861
60% | FY26: 595.1039; FY27: 1629.6346 |  |  | 374.3821 | 567.3189
55% | FY27: 438.6107 |  |  | 239.8473 | 609.6211
50% | [33 empty] | 218.9141
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 114.5088 | 3629.6513 | 6389.8148 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 463.1998 | 2592.9116 | 3797.0519 | 0 | 0 | 0 | 0 | 0 | 0 | 0.17453 | 1.4912 | 3.591 | 3.8949 | 7.9277 | 4.718 | 4.718 | 4.718 | 4.718 | 4.718 | 4.718 | 4.718 | 4.718 | 4.718 | 4.718 | 4.718 | 4.718 | 4.718 | 4.718 | 4.718 | 4.718
Option 3 Summer POE50 W E @ R (MWh) N 1 | 80.1561 | 2540.7559 | 4472.8704 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 3 Summer POE10 W E @ R (MWh) N 1 | 138.9599 | 777.8735 | 1139.1156 | 0 | 0 | 0 | 0 | 0 | 0 | 0.052358 | 0.44737 | 1.0773 | 1.1685 | 2.3783 | 1.4154 | 1.4154 | 1.4154 | 1.4154 | 1.4154 | 1.4154 | 1.4154 | 1.4154 | 1.4154 | 1.4154 | 1.4154 | 1.4154 | 1.4154 | 1.4154 | 1.4154 | 1.4154
Option 4 - 3B OFR 3rd Tx + Switchroom + Two new feeders + OFR12 New Feeder
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | 0.52857 | 28.8388 | 36.1886 | 31.5223 | 32.4909 | 34.169 | 37.9952 | 40.5509 | 43.7945 | 45.475 | 46.9493 | 44.2081 | 47.4064 | 52.4383 | 48.6082 | 48.6082 | 48.6082 | 48.6082 | 48.6082 | 48.6082 | 48.6082 | 48.6082 | 48.6082 | 48.6082 | 48.6082 | 48.6082 | 48.6082 | 48.6082 | 48.6082 | 48.6082 |  | 5.6789 | 33.6321 | 41.2692 | 36.5316 | 37.273 | 38.9145 | 42.8006 | 44.9161 | 48.9581 | 61.2584 | 51.1028 | 49.1117 | 51.784 | 57.6359 | 53.6638 | 53.6638 | 53.6638 | 53.6638 | 53.6638 | 53.6638 | 53.6638 | 53.6638 | 53.6638 | 53.6638 | 53.6638 | 53.6638 | 53.6638 | 53.6638 | 53.6638 | 53.6638
98% | 0.020606 | 33.3788 | 42.11 | 36.5667 | 37.7173 | 39.7108 | 44.256 | 47.2921 | 51.1453 | 53.1416 | 54.893 | 51.6366 | 55.436 | 61.4136 | 56.8637 | 56.8637 | 56.8637 | 56.8637 | 56.8637 | 56.8637 | 56.8637 | 56.8637 | 56.8637 | 56.8637 | 56.8637 | 56.8637 | 56.8637 | 56.8637 | 56.8637 | 56.8637 |  | 5.8662 | 39.073 | 48.1454 | 42.5174 | 43.3981 | 45.3482 | 49.9646 | 52.4776 | 57.2794 | 71.8913 | 59.8271 | 57.4618 | 60.6363 | 67.5881 | 62.8694 | 62.8694 | 62.8694 | 62.8694 | 62.8694 | 62.8694 | 62.8694 | 62.8694 | 62.8694 | 62.8694 | 62.8694 | 62.8694 | 62.8694 | 62.8694 | 62.8694 | 62.8694
97% |  | 64.3022 | 81.5872 | 70.6132 | 72.891 | 76.8375 | 85.8357 | 91.8462 | 99.4743 | 103.4264 | 106.8936 | 100.447 | 107.9687 | 119.8025 | 110.7951 | 110.7951 | 110.7951 | 110.7951 | 110.7951 | 110.7951 | 110.7951 | 110.7951 | 110.7951 | 110.7951 | 110.7951 | 110.7951 | 110.7951 | 110.7951 | 110.7951 | 110.7951 |  | 9.8356 | 75.5748 | 93.5354 | 82.3937 | 84.1373 | 87.9978 | 97.137 | 102.112 | 111.618 | 140.5451 | 116.6617 | 111.9792 | 118.2637 | 132.026 | 122.6846 | 122.6846 | 122.6846 | 122.6846 | 122.6846 | 122.6846 | 122.6846 | 122.6846 | 122.6846 | 122.6846 | 122.6846 | 122.6846 | 122.6846 | 122.6846 | 122.6846 | 122.6846
95% |  | 181.8568 | 232.914 | 200.4984 | 207.2269 | 218.8841 | 245.4636 | 263.2176 | 285.7499 | 297.4236 | 307.6653 | 288.6229 | 310.8408 | 345.7961 | 319.1896 | 319.1896 | 319.1896 | 319.1896 | 319.1896 | 319.1896 | 319.1896 | 319.1896 | 319.1896 | 319.1896 | 319.1896 | 319.1896 | 319.1896 | 319.1896 | 319.1896 | 319.1896 |  | 20.9709 | 215.1544 | 268.2072 | 235.2962 | 240.4466 | 251.8501 | 278.8456 | 293.541 | 321.6203 | 407.0666 | 336.5187 | 322.6872 | 341.2507 | 381.9026 | 354.3093 | 354.3093 | 354.3093 | 354.3093 | 354.3093 | 354.3093 | 354.3093 | 354.3093 | 354.3093 | 354.3093 | 354.3093 | 354.3093 | 354.3093 | 354.3093 | 354.3093 | 354.3093
90% |  | 893.0903 | 1174.5993 | 995.8728 | 1032.9708 | 1097.244 | 1243.7924 | 1341.6809 | 1465.9154 | 1530.2794 | 1586.7478 | 1481.7558 | 1604.2565 | 1796.9858 | 1650.2883 | 1650.2883 | 1650.2883 | 1650.2883 | 1650.2883 | 1650.2883 | 1650.2883 | 1650.2883 | 1650.2883 | 1650.2883 | 1650.2883 | 1650.2883 | 1650.2883 | 1650.2883 | 1650.2883 | 1650.2883 |  | 23.4784 | 1076.68 | 1369.1919 | 1187.7337 | 1216.131 | 1279.0051 | 1427.8478 | 1508.8723 | 1663.6901 | 2134.8068 | 1745.834 | 1669.5727 | 1771.9242 | 1996.0629 | 1843.9244 | 1843.9244 | 1843.9244 | 1843.9244 | 1843.9244 | 1843.9244 | 1843.9244 | 1843.9244 | 1843.9244 | 1843.9244 | 1843.9244 | 1843.9244 | 1843.9244 | 1843.9244 | 1843.9244 | 1843.9244
85% |  | 1762.1242 | 2449.8304 | 2013.2144 | 2103.8422 | 2260.857 | 2618.8643 | 2857.9989 | 3161.4948 | 3318.7314 | 3456.6798 | 3200.1917 | 3499.4521 | 3970.276 | 3611.9046 | 3611.9046 | 3611.9046 | 3611.9046 | 3611.9046 | 3611.9046 | 3611.9046 | 3611.9046 | 3611.9046 | 3611.9046 | 3611.9046 | 3611.9046 | 3611.9046 | 3611.9046 | 3611.9046 | 3611.9046 |  |  | 2210.6207 | 2925.2063 | 2481.9168 | 2551.2894 | 2704.8863 | 3068.4984 | 3266.4354 | 3644.6443 | 4795.5486 | 3845.316 | 3659.015 | 3909.0523 | 4456.6071 | 4084.9438 | 4084.9438 | 4084.9438 | 4084.9438 | 4084.9438 | 4084.9438 | 4084.9438 | 4084.9438 | 4084.9438 | 4084.9438 | 4084.9438 | 4084.9438 | 4084.9438 | 4084.9438 | 4084.9438 | 4084.9438
80% |  | 2007.5732 | 3076.4726 | 2397.8418 | 2538.7044 | 2782.7519 | 3339.2014 | 3710.8874 | 4182.61 | 4427.0023 | 4641.4151 | 4242.7565 | 4707.8959 | 5439.6959 | 4882.6803 | 4882.6803 | 4882.6803 | 4882.6803 | 4882.6803 | 4882.6803 | 4882.6803 | 4882.6803 | 4882.6803 | 4882.6803 | 4882.6803 | 4882.6803 | 4882.6803 | 4882.6803 | 4882.6803 | 4882.6803 |  |  | 2704.6698 | 3815.3477 | 3126.3443 | 3234.1699 | 3472.9051 | 4038.0661 | 4345.7188 | 4933.5676 | 6722.4141 | 5245.4709 | 4955.904 | 5344.5361 | 6195.5986 | 5617.9236 | 5617.9236 | 5617.9236 | 5617.9236 | 5617.9236 | 5617.9236 | 5617.9236 | 5617.9236 | 5617.9236 | 5617.9236 | 5617.9236 | 5617.9236 | 5617.9236 | 5617.9236 | 5617.9236 | 5617.9236
75% |  | 1303.991 | 2483.2854 | 1734.5662 | 1889.977 | 2159.2294 | 2773.1486 | 3183.2219 | 3703.6637 | 3973.2965 | 4209.8537 | 3770.022 | 4283.2006 | 5090.5801 | 4476.0366 | 4476.0366 | 4476.0366 | 4476.0366 | 4476.0366 | 4476.0366 | 4476.0366 | 4476.0366 | 4476.0366 | 4476.0366 | 4476.0366 | 4476.0366 | 4476.0366 | 4476.0366 | 4476.0366 | 4476.0366 |  |  | 2073.0831 | 3298.4708 | 2538.3078 | 2657.2695 | 2920.661 | 3544.1914 | 3883.6181 | 4532.1794 | 6505.7763 | 4876.2958 | 4556.8227 | 4985.5923 | 5924.5518 | 5287.2151 | 5287.2151 | 5287.2151 | 5287.2151 | 5287.2151 | 5287.2151 | 5287.2151 | 5287.2151 | 5287.2151 | 5287.2151 | 5287.2151 | 5287.2151 | 5287.2151 | 5287.2151 | 5287.2151 | 5287.2151
70% |  | 329.0664 | 1554.418 | 749.9611 | 916.9413 | 1206.238 | 1865.8598 | 2306.4607 | 2865.6462 | 3155.3517 | 3409.5191 | 2936.9445 | 3488.3263 | 4355.8105 | 3695.5178 | 3695.5178 | 3695.5178 | 3695.5178 | 3695.5178 | 3695.5178 | 3695.5178 | 3695.5178 | 3695.5178 | 3695.5178 | 3695.5178 | 3695.5178 | 3695.5178 | 3695.5178 | 3695.5178 | 3695.5178 |  |  | 1113.6786 | 2430.2892 | 1613.5365 | 1741.3542 | 2024.3536 | 2694.3022 | 3058.9973 | 3755.8401 | 5876.3596 | 4125.574 | 3782.3179 | 4243.007 | 5251.8664 | 4567.0837 | 4567.0837 | 4567.0837 | 4567.0837 | 4567.0837 | 4567.0837 | 4567.0837 | 4567.0837 | 4567.0837 | 4567.0837 | 4567.0837 | 4567.0837 | 4567.0837 | 4567.0837 | 4567.0837 | 4567.0837
65% |  |  | 357.6004 | 7.561 | 37.9747 | 144.0392 | 624.1966 | 1083.0302 | 1672.3046 | 1977.5985 | 2245.4423 | 1747.4393 | 2328.4899 | 3242.6519 | 2546.83 | 2546.83 | 2546.83 | 2546.83 | 2546.83 | 2546.83 | 2546.83 | 2546.83 | 2546.83 | 2546.83 | 2546.83 | 2546.83 | 2546.83 | 2546.83 | 2546.83 | 2546.83 |  |  | 102.8871 | 1213.5217 | 402.8374 | 509.2985 | 785.7435 | 1491.7408 | 1876.0595 | 2610.3982 | 4845.0192 | 3000.0268 | 2638.3008 | 3123.7787 | 4186.9231 | 3465.2935 | 3465.2935 | 3465.2935 | 3465.2935 | 3465.2935 | 3465.2935 | 3465.2935 | 3465.2935 | 3465.2935 | 3465.2935 | 3465.2935 | 3465.2935 | 3465.2935 | 3465.2935 | 3465.2935 | 3465.2935
60% | [7 empty] | 39.6611 | 297.4655 | 519.9348 | 762.4203 | 346.7629 | 846.3159 | 1848.9324 | 1082.9182 | 1082.9182 | 1082.9182 | 1082.9182 | 1082.9182 | 1082.9182 | 1082.9182 | 1082.9182 | 1082.9182 | 1082.9182 | 1082.9182 | 1082.9182 | 1082.9182 | 1082.9182 | 1082.9182 | 1082.9182 |  |  |  | 76.5442 |  |  | 0.42907 | 193.8911 | 439.4572 | 1152.8989 | 3612.9414 | 1581.832 | 1183.6162 | 1718.0676 | 2888.4586 | 2094.0333 | 2094.0333 | 2094.0333 | 2094.0333 | 2094.0333 | 2094.0333 | 2094.0333 | 2094.0333 | 2094.0333 | 2094.0333 | 2094.0333 | 2094.0333 | 2094.0333 | 2094.0333 | 2094.0333 | 2094.0333
55% | FY38: 215.526; FY39: 3.7852; FY40: 3.7852; FY41: 3.7852; FY42: 3.7852; FY43: 3.7852; FY44: 3.7852; FY45: 3.7852; FY46: 3.7852; FY47: 3.7852; FY48: 3.7852; FY49: 3.7852; FY50: 3.7852; FY51: 3.7852; FY52: 3.7852; FY53: 3.7852; FY54: 3.7852 | [9 empty] | 9.7686 | 1771.9334 | 105.7738 | 13.2665 | 157.07 | 983.4866 | 348.7273 | 348.7273 | 348.7273 | 348.7273 | 348.7273 | 348.7273 | 348.7273 | 348.7273 | 348.7273 | 348.7273 | 348.7273 | 348.7273 | 348.7273 | 348.7273 | 348.7273 | 348.7273
50% | [40 empty] | 47.9383
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0.54918 | 6604.2219 | 11489.0059 | 8238.218 | 8870.7366 | 10019.9609 | 12878.6138 | 14965.8479 | 17829.2643 | 19401.6611 | 20828.4794 | 18210.7871 | 21279.5891 | 26539.9091 | 22485.4175 | 22485.4175 | 22485.4175 | 22485.4175 | 22485.4175 | 22485.4175 | 22485.4175 | 22485.4175 | 22485.4175 | 22485.4175 | 22485.4175 | 22485.4175 | 22485.4175 | 22485.4175 | 22485.4175 | 22485.4175 | E @ R (MWh) | 65.83 | 9645.0538 | 15579.729 | 11747.4153 | 12314.7675 | 13612.0942 | 16927.2857 | 18872.2052 | 22842.4629 | 36993.499 | 25090.2338 | 23000.0559 | 25824.9628 | 32522.7077 | 27902.672 | 27902.672 | 27902.672 | 27902.672 | 27902.672 | 27902.672 | 27902.672 | 27902.672 | 27902.672 | 27902.672 | 27902.672 | 27902.672 | 27902.672 | 27902.672 | 27902.672 | 27902.672
Option 4 Winter POE50 W E @ R (MWh) N 1 | 0.38442 | 4622.9553 | 8042.3041 | 5766.7526 | 6209.5156 | 7013.9726 | 9015.0296 | 10476.0936 | 12480.485 | 13581.1628 | 14579.9356 | 12747.551 | 14895.7124 | 18577.9364 | 15739.7923 | 15739.7923 | 15739.7923 | 15739.7923 | 15739.7923 | 15739.7923 | 15739.7923 | 15739.7923 | 15739.7923 | 15739.7923 | 15739.7923 | 15739.7923 | 15739.7923 | 15739.7923 | 15739.7923 | 15739.7923 | Option 4 Winter POE10 W E @ R (MWh) N 1 | 19.749 | 2893.5161 | 4673.9187 | 3524.2246 | 3694.4303 | 4083.6283 | 5078.1857 | 5661.6616 | 6852.7389 | 11098.0497 | 7527.0701 | 6900.0168 | 7747.4888 | 9756.8123 | 8370.8016 | 8370.8016 | 8370.8016 | 8370.8016 | 8370.8016 | 8370.8016 | 8370.8016 | 8370.8016 | 8370.8016 | 8370.8016 | 8370.8016 | 8370.8016 | 8370.8016 | 8370.8016 | 8370.8016 | 8370.8016
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 26.6023 | 54.4041 | 61.674 | 55.214 | 55.2403 | 55.9831 | 57.9496 | 59.2625 | 60.5499 | 62.0561 | 63.4495 | 64.8041 | 64.9552 | 66.5369 | 65.3306 | 65.3306 | 65.3306 | 65.3306 | 65.3306 | 65.3306 | 65.3306 | 65.3306 | 65.3306 | 65.3306 | 65.3306 | 65.3306 | 65.3306 | 65.3306 | 65.3306 | 65.3306
98% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 12.8254 | 26.5866 | 30.185 | 26.9875 | 27.0005 | 27.3682 | 28.3415 | 28.9914 | 29.6286 | 30.3742 | 31.0638 | 31.7344 | 31.8091 | 32.5921 | 31.995 | 31.995 | 31.995 | 31.995 | 31.995 | 31.995 | 31.995 | 31.995 | 31.995 | 31.995 | 31.995 | 31.995 | 31.995 | 31.995 | 31.995 | 31.995
97% | 3.7957 | 10.5928 | 12.4418 | 10.9123 | 10.9092 | 11.1194 | 11.35 | 11.824 | 12.1646 | 12.349 | 12.5504 | 12.735 | 13.0692 | 13.4843 | 13.4545 | 13.4545 | 13.4545 | 13.4545 | 13.4545 | 13.4545 | 13.4545 | 13.4545 | 13.4545 | 13.4545 | 13.4545 | 13.4545 | 13.4545 | 13.4545 | 13.4545 | 13.4545 |  | 24.6994 | 51.9423 | 59.0661 | 52.7359 | 52.7617 | 53.4896 | 55.4165 | 56.7031 | 57.9645 | 59.4405 | 60.8059 | 62.1333 | 62.2813 | 63.8313 | 62.6492 | 62.6492 | 62.6492 | 62.6492 | 62.6492 | 62.6492 | 62.6492 | 62.6492 | 62.6492 | 62.6492 | 62.6492 | 62.6492 | 62.6492 | 62.6492 | 62.6492 | 62.6492
95% | 17.3774 | 50.84 | 59.9429 | 52.4133 | 52.398 | 53.4325 | 54.568 | 56.9012 | 58.5781 | 59.4861 | 60.4775 | 61.3865 | 63.0319 | 65.075 | 64.9283 | 64.9283 | 64.9283 | 64.9283 | 64.9283 | 64.9283 | 64.9283 | 64.9283 | 64.9283 | 64.9283 | 64.9283 | 64.9283 | 64.9283 | 64.9283 | 64.9283 | 64.9283 |  | 34.9082 | 75.1439 | 85.6653 | 76.3161 | 76.3542 | 77.4292 | 80.2751 | 82.1753 | 84.0383 | 86.2183 | 88.2348 | 90.1953 | 90.4139 | 92.7031 | 90.9572 | 90.9572 | 90.9572 | 90.9572 | 90.9572 | 90.9572 | 90.9572 | 90.9572 | 90.9572 | 90.9572 | 90.9572 | 90.9572 | 90.9572 | 90.9572 | 90.9572 | 90.9572
90% | 24.555 | 82.5918 | 98.3797 | 85.3204 | 85.294 | 87.0881 | 89.0575 | 93.1042 | 96.0125 | 97.5874 | 99.3069 | 100.8833 | 103.7371 | 107.2806 | 107.0262 | 107.0262 | 107.0262 | 107.0262 | 107.0262 | 107.0262 | 107.0262 | 107.0262 | 107.0262 | 107.0262 | 107.0262 | 107.0262 | 107.0262 | 107.0262 | 107.0262 | 107.0262 |  | 134.6084 | 309.068 | 354.6878 | 314.1503 | 314.3154 | 318.9767 | 331.3164 | 339.5553 | 347.6334 | 357.0856 | 365.8289 | 374.3296 | 375.2773 | 385.2032 | 377.6333 | 377.6333 | 377.6333 | 377.6333 | 377.6333 | 377.6333 | 377.6333 | 377.6333 | 377.6333 | 377.6333 | 377.6333 | 377.6333 | 377.6333 | 377.6333 | 377.6333 | 377.6333
85% | 44.847 | 209.5458 | 254.3493 | 217.2893 | 217.2144 | 222.3058 | 227.8946 | 239.3784 | 247.6318 | 252.1009 | 256.9806 | 261.4544 | 269.5529 | 279.6088 | 278.8868 | 278.8868 | 278.8868 | 278.8868 | 278.8868 | 278.8868 | 278.8868 | 278.8868 | 278.8868 | 278.8868 | 278.8868 | 278.8868 | 278.8868 | 278.8868 | 278.8868 | 278.8868 |  | 102.4961 | 267.5254 | 310.6793 | 272.333 | 272.4892 | 276.8985 | 288.5712 | 296.3647 | 304.0063 | 312.9474 | 321.2182 | 329.2594 | 330.1559 | 339.5452 | 332.3845 | 332.3845 | 332.3845 | 332.3845 | 332.3845 | 332.3845 | 332.3845 | 332.3845 | 332.3845 | 332.3845 | 332.3845 | 332.3845 | 332.3845 | 332.3845 | 332.3845 | 332.3845
80% | 23.7465 | 253.802 | 316.3847 | 264.6184 | 264.5137 | 271.6255 | 279.432 | 295.4729 | 307.0016 | 313.244 | 320.0601 | 326.3092 | 337.6214 | 351.6678 | 350.6593 | 350.6593 | 350.6593 | 350.6593 | 350.6593 | 350.6593 | 350.6593 | 350.6593 | 350.6593 | 350.6593 | 350.6593 | 350.6593 | 350.6593 | 350.6593 | 350.6593 | 350.6593 |  | 52.1361 | 167.3947 | 197.5339 | 170.7524 | 170.8615 | 173.941 | 182.0934 | 187.5364 | 192.8734 | 199.118 | 204.8944 | 210.5105 | 211.1366 | 217.6942 | 212.6931 | 212.6931 | 212.6931 | 212.6931 | 212.6931 | 212.6931 | 212.6931 | 212.6931 | 212.6931 | 212.6931 | 212.6931 | 212.6931 | 212.6931 | 212.6931 | 212.6931 | 212.6931
75% | 0.18716 | 547.1351 | 710.2768 | 575.3313 | 575.0585 | 593.5976 | 613.9479 | 655.7635 | 685.8166 | 702.0896 | 719.8579 | 736.1481 | 765.637 | 802.2535 | 799.6244 | 799.6244 | 799.6244 | 799.6244 | 799.6244 | 799.6244 | 799.6244 | 799.6244 | 799.6244 | 799.6244 | 799.6244 | 799.6244 | 799.6244 | 799.6244 | 799.6244 | 799.6244 |  | 53.8635 | 259.5826 | 313.3765 | 265.5756 | 265.7703 | 271.2667 | 285.8175 | 295.5326 | 305.0582 | 316.2039 | 326.5139 | 336.5378 | 337.6553 | 349.3597 | 340.4334 | 340.4334 | 340.4334 | 340.4334 | 340.4334 | 340.4334 | 340.4334 | 340.4334 | 340.4334 | 340.4334 | 340.4334 | 340.4334 | 340.4334 | 340.4334 | 340.4334 | 340.4334
70% |  | 720.2141 | 1002.0732 | 768.9285 | 768.4572 | 800.4872 | 835.6462 | 907.8908 | 959.8134 | 987.9282 | 1018.6264 | 1046.7709 | 1097.7188 | 1160.9809 | 1156.4388 | 1156.4388 | 1156.4388 | 1156.4388 | 1156.4388 | 1156.4388 | 1156.4388 | 1156.4388 | 1156.4388 | 1156.4388 | 1156.4388 | 1156.4388 | 1156.4388 | 1156.4388 | 1156.4388 | 1156.4388 |  | 21.0605 | 391.6455 | 489.6437 | 402.5632 | 402.9179 | 412.9308 | 439.4385 | 457.1367 | 474.4899 | 494.7944 | 513.5764 | 531.8372 | 533.873 | 555.1953 | 538.934 | 538.934 | 538.934 | 538.934 | 538.934 | 538.934 | 538.934 | 538.934 | 538.934 | 538.934 | 538.934 | 538.934 | 538.934 | 538.934 | 538.934 | 538.934
65% |  | 1159.8257 | 1867.7211 | 1282.1729 | 1280.9892 | 1361.4333 | 1449.7359 | 1631.1799 | 1761.5847 | 1832.1956 | 1909.2947 | 1979.9804 | 2107.9371 | 2266.8214 | 2255.4136 | 2255.4136 | 2255.4136 | 2255.4136 | 2255.4136 | 2255.4136 | 2255.4136 | 2255.4136 | 2255.4136 | 2255.4136 | 2255.4136 | 2255.4136 | 2255.4136 | 2255.4136 | 2255.4136 | 2255.4136 |  |  | 375.3893 | 498.6861 | 389.1254 | 389.5717 | 402.1695 | 435.5202 | 457.7874 | 479.6203 | 505.1666 | 528.7972 | 551.7721 | 554.3335 | 581.1602 | 560.701 | 560.701 | 560.701 | 560.701 | 560.701 | 560.701 | 560.701 | 560.701 | 560.701 | 560.701 | 560.701 | 560.701 | 560.701 | 560.701 | 560.701 | 560.701
60% |  | 595.1039 | 1629.6346 | 773.7248 | 771.9945 | 889.5816 | 1018.6556 | 1283.8767 | 1474.4924 | 1577.706 | 1690.4037 | 1793.7266 | 1980.764 | 2213.009 | 2196.3339 | 2196.3339 | 2196.3339 | 2196.3339 | 2196.3339 | 2196.3339 | 2196.3339 | 2196.3339 | 2196.3339 | 2196.3339 | 2196.3339 | 2196.3339 | 2196.3339 | 2196.3339 | 2196.3339 | 2196.3339 |  |  | 374.3821 | 567.3189 | 395.8767 | 396.575 | 416.2883 | 468.476 | 503.3199 | 537.4844 | 577.4596 | 614.4372 | 650.3886 | 654.3967 | 696.3756 | 664.3607 | 664.3607 | 664.3607 | 664.3607 | 664.3607 | 664.3607 | 664.3607 | 664.3607 | 664.3607 | 664.3607 | 664.3607 | 664.3607 | 664.3607 | 664.3607 | 664.3607 | 664.3607
55% |  |  | 438.6107 | 10.8425 | 10.6025 | 32.9167 | 71.2285 | 193.8987 | 317.2695 | 395.942 | 491.1336 | 586.7647 | 779.7285 | 1041.6255 | 1022.7699 | 1022.7699 | 1022.7699 | 1022.7699 | 1022.7699 | 1022.7699 | 1022.7699 | 1022.7699 | 1022.7699 | 1022.7699 | 1022.7699 | 1022.7699 | 1022.7699 | 1022.7699 | 1022.7699 | 1022.7699 |  |  | 239.8473 | 609.6211 | 280.1679 | 281.5099 | 319.3921 | 419.6789 | 486.637 | 552.2894 | 629.108 | 700.1663 | 769.2526 | 776.9546 | 857.6236 | 796.1021 | 796.1021 | 796.1021 | 796.1021 | 796.1021 | 796.1021 | 796.1021 | 796.1021 | 796.1021 | 796.1021 | 796.1021 | 796.1021 | 796.1021 | 796.1021 | 796.1021 | 796.1021
50% | FY38: 17.1696; FY39: 14.2604; FY40: 14.2604; FY41: 14.2604; FY42: 14.2604; FY43: 14.2604; FY44: 14.2604; FY45: 14.2604; FY46: 14.2604; FY47: 14.2604; FY48: 14.2604; FY49: 14.2604; FY50: 14.2604; FY51: 14.2604; FY52: 14.2604; FY53: 14.2604; FY54: 14.2604 |  |  |  | 218.9141 | 0.10299 | 0.14546 | 4.3403 | 42.7762 | 89.8287 | 152.0029 | 244.2781 | 347.7848 | 464.6078 | 478.5991 | 636.5321 | 514.2106 | 514.2106 | 514.2106 | 514.2106 | 514.2106 | 514.2106 | 514.2106 | 514.2106 | 514.2106 | 514.2106 | 514.2106 | 514.2106 | 514.2106 | 514.2106 | 514.2106 | 514.2106
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 114.5088 | 3629.6513 | 6389.8148 | 4041.5537 | 4037.4312 | 4323.5877 | 4651.5163 | 5369.2902 | 5920.3653 | 6230.6288 | 6578.6917 | 6906.1591 | 7518.7979 | 8318.9765 | 8259.7962 | 8259.7962 | 8259.7962 | 8259.7962 | 8259.7962 | 8259.7962 | 8259.7962 | 8259.7962 | 8259.7962 | 8259.7962 | 8259.7962 | 8259.7962 | 8259.7962 | 8259.7962 | 8259.7962 | 8259.7962 | E @ R (MWh) | 463.1998 | 2592.9116 | 3797.0519 | 2701.901 | 2705.5131 | 2810.474 | 3115.6711 | 3340.8308 | 3577.6395 | 3874.2506 | 4166.7712 | 4467.3627 | 4501.8413 | 4874.3525 | 4588.3846 | 4588.3846 | 4588.3846 | 4588.3846 | 4588.3846 | 4588.3846 | 4588.3846 | 4588.3846 | 4588.3846 | 4588.3846 | 4588.3846 | 4588.3846 | 4588.3846 | 4588.3846 | 4588.3846 | 4588.3846
Option 4 Summer POE50 W E @ R (MWh) N 1 | 80.1561 | 2540.7559 | 4472.8704 | 2829.0876 | 2826.2018 | 3026.5114 | 3256.0614 | 3758.5032 | 4144.2557 | 4361.4401 | 4605.0842 | 4834.3114 | 5263.1585 | 5823.2835 | 5781.8573 | 5781.8573 | 5781.8573 | 5781.8573 | 5781.8573 | 5781.8573 | 5781.8573 | 5781.8573 | 5781.8573 | 5781.8573 | 5781.8573 | 5781.8573 | 5781.8573 | 5781.8573 | 5781.8573 | 5781.8573 | Option 4 Summer POE10 W E @ R (MWh) N 1 | 138.9599 | 777.8735 | 1139.1156 | 810.5703 | 811.6539 | 843.1422 | 934.7013 | 1002.2492 | 1073.2919 | 1162.2752 | 1250.0313 | 1340.2088 | 1350.5524 | 1462.3057 | 1376.5154 | 1376.5154 | 1376.5154 | 1376.5154 | 1376.5154 | 1376.5154 | 1376.5154 | 1376.5154 | 1376.5154 | 1376.5154 | 1376.5154 | 1376.5154 | 1376.5154 | 1376.5154 | 1376.5154 | 1376.5154
Option 5 - 4B LLG 2nd Tx + Switchroom + Two new feeders + OFR12 New Feeder
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | 0.52857 | 28.8388 | 36.1886 | 5.2779 | 6.2464 | 7.9245 | 11.7507 | 14.3064 | 17.55 | 19.2305 | 20.7048 | 17.9636 | 21.1619 | 26.1938 | 22.3637 | 22.3637 | 22.3637 | 22.3637 | 22.3637 | 22.3637 | 22.3637 | 22.3637 | 22.3637 | 22.3637 | 22.3637 | 22.3637 | 22.3637 | 22.3637 | 22.3637 | 22.3637 |  | 5.6789 | 33.6321 | 41.2692 | 10.2871 | 11.0285 | 12.6701 | 16.5561 | 18.6716 | 22.7137 | 35.0139 | 24.8583 | 22.8672 | 25.5395 | 31.3915 | 27.4193 | 27.4193 | 27.4193 | 27.4193 | 27.4193 | 27.4193 | 27.4193 | 27.4193 | 27.4193 | 27.4193 | 27.4193 | 27.4193 | 27.4193 | 27.4193 | 27.4193 | 27.4193
98% | 0.020606 | 33.3788 | 42.11 | 5.3898 | 6.5404 | 8.5339 | 13.0792 | 16.1152 | 19.9684 | 21.9647 | 23.7161 | 20.4597 | 24.2591 | 30.2367 | 25.6868 | 25.6868 | 25.6868 | 25.6868 | 25.6868 | 25.6868 | 25.6868 | 25.6868 | 25.6868 | 25.6868 | 25.6868 | 25.6868 | 25.6868 | 25.6868 | 25.6868 | 25.6868 |  | 5.8662 | 39.073 | 48.1454 | 11.3405 | 12.2212 | 14.1713 | 18.7877 | 21.3008 | 26.1025 | 40.7144 | 28.6502 | 26.285 | 29.4594 | 36.4112 | 31.6926 | 31.6926 | 31.6926 | 31.6926 | 31.6926 | 31.6926 | 31.6926 | 31.6926 | 31.6926 | 31.6926 | 31.6926 | 31.6926 | 31.6926 | 31.6926 | 31.6926 | 31.6926
97% |  | 64.3022 | 81.5872 | 8.8925 | 11.1703 | 15.1168 | 24.115 | 30.1255 | 37.7536 | 41.7057 | 45.1729 | 38.7263 | 46.2479 | 58.0818 | 49.0744 | 49.0744 | 49.0744 | 49.0744 | 49.0744 | 49.0744 | 49.0744 | 49.0744 | 49.0744 | 49.0744 | 49.0744 | 49.0744 | 49.0744 | 49.0744 | 49.0744 | 49.0744 |  | 9.8356 | 75.5748 | 93.5354 | 20.6729 | 22.4166 | 26.2771 | 35.4162 | 40.3912 | 49.8972 | 78.8244 | 54.941 | 50.2584 | 56.5429 | 70.3053 | 60.9639 | 60.9639 | 60.9639 | 60.9639 | 60.9639 | 60.9639 | 60.9639 | 60.9639 | 60.9639 | 60.9639 | 60.9639 | 60.9639 | 60.9639 | 60.9639 | 60.9639 | 60.9639
95% |  | 181.8568 | 232.914 | 18.185 | 24.9134 | 36.5706 | 63.1501 | 80.9041 | 103.4365 | 115.1101 | 125.3518 | 106.3094 | 128.5274 | 163.4826 | 136.8761 | 136.8761 | 136.8761 | 136.8761 | 136.8761 | 136.8761 | 136.8761 | 136.8761 | 136.8761 | 136.8761 | 136.8761 | 136.8761 | 136.8761 | 136.8761 | 136.8761 | 136.8761 |  | 20.9709 | 215.1544 | 268.2072 | 52.9827 | 58.1331 | 69.5366 | 96.5322 | 111.2275 | 139.3068 | 224.7531 | 154.2052 | 140.3737 | 158.9372 | 199.5892 | 171.9959 | 171.9959 | 171.9959 | 171.9959 | 171.9959 | 171.9959 | 171.9959 | 171.9959 | 171.9959 | 171.9959 | 171.9959 | 171.9959 | 171.9959 | 171.9959 | 171.9959 | 171.9959
90% |  | 893.0903 | 1174.5993 | 15.8515 | 36.7332 | 92.0405 | 238.589 | 336.4774 | 460.7119 | 525.0759 | 581.5444 | 476.5523 | 599.053 | 791.7823 | 645.0848 | 645.0848 | 645.0848 | 645.0848 | 645.0848 | 645.0848 | 645.0848 | 645.0848 | 645.0848 | 645.0848 | 645.0848 | 645.0848 | 645.0848 | 645.0848 | 645.0848 | 645.0848 |  | 23.4784 | 1076.68 | 1369.1919 | 182.5302 | 210.9275 | 273.8016 | 422.6443 | 503.6688 | 658.4866 | 1129.6033 | 740.6306 | 664.3692 | 766.7207 | 990.8594 | 838.721 | 838.721 | 838.721 | 838.721 | 838.721 | 838.721 | 838.721 | 838.721 | 838.721 | 838.721 | 838.721 | 838.721 | 838.721 | 838.721 | 838.721 | 838.721
85% |  | 1762.1242 | 2449.8304 |  |  | 0.53228 | 167.6397 | 402.3588 | 705.8547 | 863.0913 | 1001.0398 | 744.5516 | 1043.8121 | 1514.636 | 1156.2645 | 1156.2645 | 1156.2645 | 1156.2645 | 1156.2645 | 1156.2645 | 1156.2645 | 1156.2645 | 1156.2645 | 1156.2645 | 1156.2645 | 1156.2645 | 1156.2645 | 1156.2645 | 1156.2645 | 1156.2645 |  |  | 2210.6207 | 2925.2063 | 69.553 | 114.1454 | 249.2462 | 612.8584 | 810.7953 | 1189.0042 | 2339.9085 | 1389.6759 | 1203.375 | 1453.4123 | 2000.9671 | 1629.3038 | 1629.3038 | 1629.3038 | 1629.3038 | 1629.3038 | 1629.3038 | 1629.3038 | 1629.3038 | 1629.3038 | 1629.3038 | 1629.3038 | 1629.3038 | 1629.3038 | 1629.3038 | 1629.3038 | 1629.3038
80% |  | 2007.5732 | 3076.4726 |  |  |  |  | 50.4871 | 366.5029 | 610.2096 | 824.6224 | 425.9638 | 891.1033 | 1622.9032 | 1065.8877 | 1065.8877 | 1065.8877 | 1065.8877 | 1065.8877 | 1065.8877 | 1065.8877 | 1065.8877 | 1065.8877 | 1065.8877 | 1065.8877 | 1065.8877 | 1065.8877 | 1065.8877 | 1065.8877 | 1065.8877 |  |  | 2704.6698 | 3815.3477 |  |  | 0.7433 | 240.2914 | 528.9261 | 1116.7749 | 2905.6214 | 1428.6783 | 1139.1113 | 1527.7434 | 2378.8059 | 1801.131 | 1801.131 | 1801.131 | 1801.131 | 1801.131 | 1801.131 | 1801.131 | 1801.131 | 1801.131 | 1801.131 | 1801.131 | 1801.131 | 1801.131 | 1801.131 | 1801.131 | 1801.131
75% |  | 1303.991 | 2483.2854 | [6 empty] | 30.0486 | 120.6361 | 0.46718 | 160.5764 | 879.5926 | 291.4691 | 291.4691 | 291.4691 | 291.4691 | 291.4691 | 291.4691 | 291.4691 | 291.4691 | 291.4691 | 291.4691 | 291.4691 | 291.4691 | 291.4691 | 291.4691 | 291.4691 | 291.4691 |  |  | 2073.0831 | 3298.4708 |  |  |  |  | 11.3773 | 336.479 | 2294.7888 | 665.3083 | 357.2011 | 774.6048 | 1713.5643 | 1076.2276 | 1076.2276 | 1076.2276 | 1076.2276 | 1076.2276 | 1076.2276 | 1076.2276 | 1076.2276 | 1076.2276 | 1076.2276 | 1076.2276 | 1076.2276 | 1076.2276 | 1076.2276 | 1076.2276 | 1076.2276
70% | FY26: 329.0664; FY27: 1554.418; FY38: 75.0984 |  |  | 1113.6786 | 2430.2892 | [6 empty] | 1351.889 | 14.3375 |  | 39.4823 | 727.3957 | 171.2524 | 171.2524 | 171.2524 | 171.2524 | 171.2524 | 171.2524 | 171.2524 | 171.2524 | 171.2524 | 171.2524 | 171.2524 | 171.2524 | 171.2524 | 171.2524 | 171.2524 | 171.2524
65% | FY27: 357.6004 |  |  | 102.8871 | 1213.5217 | [6 empty] | 222.2257 |  |  |  | 5.2264
60% | [33 empty] | 76.5442
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0.54918 | 6604.2219 | 11489.0059 | 53.5966 | 85.6039 | 160.7186 | 518.3237 | 930.7746 | 1711.7782 | 2226.4364 | 2742.7883 | 1830.9939 | 2914.741 | 5162.0074 | 3392.7072 | 3392.7072 | 3392.7072 | 3392.7072 | 3392.7072 | 3392.7072 | 3392.7072 | 3392.7072 | 3392.7072 | 3392.7072 | 3392.7072 | 3392.7072 | 3392.7072 | 3392.7072 | 3392.7072 | 3392.7072 | E @ R (MWh) | 65.83 | 9645.0538 | 15579.729 | 347.3664 | 428.8724 | 646.4462 | 1443.0864 | 2046.3587 | 3538.765 | 10623.3425 | 4501.2853 | 3603.841 | 4832.4426 | 8154.5159 | 5808.7073 | 5808.7073 | 5808.7073 | 5808.7073 | 5808.7073 | 5808.7073 | 5808.7073 | 5808.7073 | 5808.7073 | 5808.7073 | 5808.7073 | 5808.7073 | 5808.7073 | 5808.7073 | 5808.7073 | 5808.7073
Option 5 Winter POE50 W E @ R (MWh) N 1 | 0.38442 | 4622.9553 | 8042.3041 | 37.5176 | 59.9227 | 112.503 | 362.8266 | 651.5422 | 1198.2447 | 1558.5055 | 1919.9518 | 1281.6957 | 2040.3187 | 3613.4052 | 2374.895 | 2374.895 | 2374.895 | 2374.895 | 2374.895 | 2374.895 | 2374.895 | 2374.895 | 2374.895 | 2374.895 | 2374.895 | 2374.895 | 2374.895 | 2374.895 | 2374.895 | 2374.895 | Option 5 Winter POE10 W E @ R (MWh) N 1 | 19.749 | 2893.5161 | 4673.9187 | 104.2099 | 128.6617 | 193.9339 | 432.9259 | 613.9076 | 1061.6295 | 3187.0027 | 1350.3856 | 1081.1523 | 1449.7328 | 2446.3548 | 1742.6122 | 1742.6122 | 1742.6122 | 1742.6122 | 1742.6122 | 1742.6122 | 1742.6122 | 1742.6122 | 1742.6122 | 1742.6122 | 1742.6122 | 1742.6122 | 1742.6122 | 1742.6122 | 1742.6122 | 1742.6122
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 26.6023 | 54.4041 | 61.674 | 28.4986 | 28.5249 | 29.2677 | 31.2342 | 32.5471 | 33.8344 | 35.3407 | 36.7341 | 38.0887 | 38.2397 | 39.8215 | 38.6152 | 38.6152 | 38.6152 | 38.6152 | 38.6152 | 38.6152 | 38.6152 | 38.6152 | 38.6152 | 38.6152 | 38.6152 | 38.6152 | 38.6152 | 38.6152 | 38.6152 | 38.6152
98% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 12.8254 | 26.5866 | 30.185 | 13.764 | 13.7771 | 14.1447 | 15.1181 | 15.7679 | 16.4051 | 17.1507 | 17.8404 | 18.5109 | 18.5857 | 19.3686 | 18.7715 | 18.7715 | 18.7715 | 18.7715 | 18.7715 | 18.7715 | 18.7715 | 18.7715 | 18.7715 | 18.7715 | 18.7715 | 18.7715 | 18.7715 | 18.7715 | 18.7715 | 18.7715
97% | 3.7957 | 10.5928 | 12.4418 | 4.3677 | 4.3646 | 4.5748 | 4.8054 | 5.2793 | 5.62 | 5.8044 | 6.0058 | 6.1904 | 6.5246 | 6.9397 | 6.9099 | 6.9099 | 6.9099 | 6.9099 | 6.9099 | 6.9099 | 6.9099 | 6.9099 | 6.9099 | 6.9099 | 6.9099 | 6.9099 | 6.9099 | 6.9099 | 6.9099 | 6.9099 |  | 24.6994 | 51.9423 | 59.0661 | 26.5575 | 26.5833 | 27.3112 | 29.2381 | 30.5247 | 31.7861 | 33.2621 | 34.6274 | 35.9549 | 36.1029 | 37.6529 | 36.4708 | 36.4708 | 36.4708 | 36.4708 | 36.4708 | 36.4708 | 36.4708 | 36.4708 | 36.4708 | 36.4708 | 36.4708 | 36.4708 | 36.4708 | 36.4708 | 36.4708 | 36.4708
95% | 17.3774 | 50.84 | 59.9429 | 20.1937 | 20.1784 | 21.2129 | 22.3484 | 24.6816 | 26.3585 | 27.2665 | 28.2579 | 29.1669 | 30.8123 | 32.8554 | 32.7087 | 32.7087 | 32.7087 | 32.7087 | 32.7087 | 32.7087 | 32.7087 | 32.7087 | 32.7087 | 32.7087 | 32.7087 | 32.7087 | 32.7087 | 32.7087 | 32.7087 | 32.7087 |  | 34.9082 | 75.1439 | 85.6653 | 37.6526 | 37.6907 | 38.7657 | 41.6116 | 43.5117 | 45.3748 | 47.5548 | 49.5712 | 51.5318 | 51.7503 | 54.0395 | 52.2937 | 52.2937 | 52.2937 | 52.2937 | 52.2937 | 52.2937 | 52.2937 | 52.2937 | 52.2937 | 52.2937 | 52.2937 | 52.2937 | 52.2937 | 52.2937 | 52.2937 | 52.2937
90% | 24.555 | 82.5918 | 98.3797 | 29.4396 | 29.4132 | 31.2073 | 33.1766 | 37.2233 | 40.1317 | 41.7065 | 43.426 | 45.0025 | 47.8562 | 51.3998 | 51.1453 | 51.1453 | 51.1453 | 51.1453 | 51.1453 | 51.1453 | 51.1453 | 51.1453 | 51.1453 | 51.1453 | 51.1453 | 51.1453 | 51.1453 | 51.1453 | 51.1453 | 51.1453 |  | 134.6084 | 309.068 | 354.6878 | 146.5077 | 146.6729 | 151.3341 | 163.6738 | 171.9127 | 179.9909 | 189.443 | 198.1863 | 206.687 | 207.6347 | 217.5606 | 209.9907 | 209.9907 | 209.9907 | 209.9907 | 209.9907 | 209.9907 | 209.9907 | 209.9907 | 209.9907 | 209.9907 | 209.9907 | 209.9907 | 209.9907 | 209.9907 | 209.9907 | 209.9907
85% | 44.847 | 209.5458 | 254.3493 | 58.7085 | 58.6336 | 63.725 | 69.3138 | 80.7975 | 89.051 | 93.5201 | 98.3998 | 102.8735 | 110.9721 | 121.028 | 120.306 | 120.306 | 120.306 | 120.306 | 120.306 | 120.306 | 120.306 | 120.306 | 120.306 | 120.306 | 120.306 | 120.306 | 120.306 | 120.306 | 120.306 | 120.306 |  | 102.4961 | 267.5254 | 310.6793 | 113.7522 | 113.9084 | 118.3177 | 129.9904 | 137.7839 | 145.4254 | 154.3666 | 162.6373 | 170.6786 | 171.575 | 180.9644 | 173.8037 | 173.8037 | 173.8037 | 173.8037 | 173.8037 | 173.8037 | 173.8037 | 173.8037 | 173.8037 | 173.8037 | 173.8037 | 173.8037 | 173.8037 | 173.8037 | 173.8037 | 173.8037
80% | 23.7465 | 253.802 | 316.3847 | 43.1086 | 43.004 | 50.1158 | 57.9223 | 73.9632 | 85.4918 | 91.7343 | 98.5504 | 104.7995 | 116.1117 | 130.1581 | 129.1496 | 129.1496 | 129.1496 | 129.1496 | 129.1496 | 129.1496 | 129.1496 | 129.1496 | 129.1496 | 129.1496 | 129.1496 | 129.1496 | 129.1496 | 129.1496 | 129.1496 | 129.1496 |  | 52.1361 | 167.3947 | 197.5339 | 59.9975 | 60.1066 | 63.1861 | 71.3385 | 76.7816 | 82.1185 | 88.3632 | 94.1395 | 99.7556 | 100.3817 | 106.9394 | 101.9382 | 101.9382 | 101.9382 | 101.9382 | 101.9382 | 101.9382 | 101.9382 | 101.9382 | 101.9382 | 101.9382 | 101.9382 | 101.9382 | 101.9382 | 101.9382 | 101.9382 | 101.9382
75% | 0.18716 | 547.1351 | 710.2768 | 14.1824 | 14.0488 | 24.5073 | 39.1499 | 78.3279 | 108.381 | 124.654 | 142.4223 | 158.7125 | 188.2014 | 224.8179 | 222.1889 | 222.1889 | 222.1889 | 222.1889 | 222.1889 | 222.1889 | 222.1889 | 222.1889 | 222.1889 | 222.1889 | 222.1889 | 222.1889 | 222.1889 | 222.1889 | 222.1889 | 222.1889 |  | 53.8635 | 259.5826 | 313.3765 | 67.8949 | 68.0896 | 73.586 | 88.1368 | 97.8519 | 107.3775 | 118.5233 | 128.8332 | 138.8571 | 139.9746 | 151.679 | 142.7527 | 142.7527 | 142.7527 | 142.7527 | 142.7527 | 142.7527 | 142.7527 | 142.7527 | 142.7527 | 142.7527 | 142.7527 | 142.7527 | 142.7527 | 142.7527 | 142.7527 | 142.7527
70% |  | 720.2141 | 1002.0732 |  |  |  |  | 1.6083 | 13.8432 | 25.3341 | 41.662 | 60.0148 | 101.217 | 163.3481 | 158.8059 | 158.8059 | 158.8059 | 158.8059 | 158.8059 | 158.8059 | 158.8059 | 158.8059 | 158.8059 | 158.8059 | 158.8059 | 158.8059 | 158.8059 | 158.8059 | 158.8059 | 158.8059 |  | 21.0605 | 391.6455 | 489.6437 | 42.4753 | 42.8214 | 52.8097 | 79.3173 | 97.0156 | 114.3687 | 134.6733 | 153.4553 | 171.7161 | 173.7519 | 195.0741 | 178.8129 | 178.8129 | 178.8129 | 178.8129 | 178.8129 | 178.8129 | 178.8129 | 178.8129 | 178.8129 | 178.8129 | 178.8129 | 178.8129 | 178.8129 | 178.8129 | 178.8129 | 178.8129
65% |  | 1159.8257 | 1867.7211 | [10 empty] | 7.4989 | 5.8515 | 5.8515 | 5.8515 | 5.8515 | 5.8515 | 5.8515 | 5.8515 | 5.8515 | 5.8515 | 5.8515 | 5.8515 | 5.8515 | 5.8515 | 5.8515 | 5.8515 | 5.8515 |  |  | 375.3893 | 498.6861 |  |  | 0.42732 | 8.0472 | 18.2374 | 32.018 | 52.7167 | 75.7092 | 98.684 | 101.2454 | 128.0721 | 107.6129 | 107.6129 | 107.6129 | 107.6129 | 107.6129 | 107.6129 | 107.6129 | 107.6129 | 107.6129 | 107.6129 | 107.6129 | 107.6129 | 107.6129 | 107.6129 | 107.6129 | 107.6129
60% | FY26: 595.1039; FY27: 1629.6346 |  |  | 374.3821 | 567.3189 | [7 empty] | 0.62619 | 6.4888 | 7.5168 | 22.6693 | 10.3924 | 10.3924 | 10.3924 | 10.3924 | 10.3924 | 10.3924 | 10.3924 | 10.3924 | 10.3924 | 10.3924 | 10.3924 | 10.3924 | 10.3924 | 10.3924 | 10.3924 | 10.3924
55% | FY27: 438.6107 |  |  | 239.8473 | 609.6211
50% | [33 empty] | 218.9141
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 114.5088 | 3629.6513 | 6389.8148 | 170.0005 | 169.6426 | 195.343 | 226.7164 | 301.8812 | 368.8772 | 410.0199 | 458.7241 | 506.76 | 601.6953 | 738.0459 | 727.0658 | 727.0658 | 727.0658 | 727.0658 | 727.0658 | 727.0658 | 727.0658 | 727.0658 | 727.0658 | 727.0658 | 727.0658 | 727.0658 | 727.0658 | 727.0658 | 727.0658 | 727.0658 | E @ R (MWh) | 463.1998 | 2592.9116 | 3797.0519 | 537.1005 | 538.1748 | 569.1502 | 657.7061 | 721.9344 | 788.6996 | 871.3943 | 952.3602 | 1036.9535 | 1046.7588 | 1153.8415 | 1071.4547 | 1071.4547 | 1071.4547 | 1071.4547 | 1071.4547 | 1071.4547 | 1071.4547 | 1071.4547 | 1071.4547 | 1071.4547 | 1071.4547 | 1071.4547 | 1071.4547 | 1071.4547 | 1071.4547 | 1071.4547
Option 5 Summer POE50 W E @ R (MWh) N 1 | 80.1561 | 2540.7559 | 4472.8704 | 119.0003 | 118.7498 | 136.7401 | 158.7015 | 211.3168 | 258.214 | 287.0139 | 321.1069 | 354.732 | 421.1867 | 516.6321 | 508.946 | 508.946 | 508.946 | 508.946 | 508.946 | 508.946 | 508.946 | 508.946 | 508.946 | 508.946 | 508.946 | 508.946 | 508.946 | 508.946 | 508.946 | 508.946 | Option 5 Summer POE10 W E @ R (MWh) N 1 | 138.9599 | 777.8735 | 1139.1156 | 161.1301 | 161.4524 | 170.7451 | 197.3118 | 216.5803 | 236.6099 | 261.4183 | 285.7081 | 311.086 | 314.0276 | 346.1524 | 321.4364 | 321.4364 | 321.4364 | 321.4364 | 321.4364 | 321.4364 | 321.4364 | 321.4364 | 321.4364 | 321.4364 | 321.4364 | 321.4364 | 321.4364 | 321.4364 | 321.4364 | 321.4364
Option 6 -
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | 0.52857 | 28.8388 | 36.1886 | 37.4366 | 38.4052 | 40.0833 | 43.9094 | 46.4652 | 49.7088 | 51.3892 | 52.8635 | 50.1223 | 53.3207 | 58.3526 | 54.5225 | 54.5225 | 54.5225 | 54.5225 | 54.5225 | 54.5225 | 54.5225 | 54.5225 | 54.5225 | 54.5225 | 54.5225 | 54.5225 | 54.5225 | 54.5225 | 54.5225 | 54.5225 |  | 5.6789 | 33.6321 | 41.2692 | 42.4458 | 43.1872 | 44.8288 | 48.7149 | 50.8303 | 54.8724 | 67.1726 | 57.0171 | 55.026 | 57.6982 | 63.5502 | 59.5781 | 59.5781 | 59.5781 | 59.5781 | 59.5781 | 59.5781 | 59.5781 | 59.5781 | 59.5781 | 59.5781 | 59.5781 | 59.5781 | 59.5781 | 59.5781 | 59.5781 | 59.5781
98% | 0.020606 | 33.3788 | 42.11 | 43.5925 | 44.7431 | 46.7365 | 51.2818 | 54.3179 | 58.1711 | 60.1673 | 61.9187 | 58.6624 | 62.4618 | 68.4394 | 63.8895 | 63.8895 | 63.8895 | 63.8895 | 63.8895 | 63.8895 | 63.8895 | 63.8895 | 63.8895 | 63.8895 | 63.8895 | 63.8895 | 63.8895 | 63.8895 | 63.8895 | 63.8895 |  | 5.8662 | 39.073 | 48.1454 | 49.5431 | 50.4239 | 52.374 | 56.9904 | 59.5034 | 64.3051 | 78.9171 | 66.8529 | 64.4876 | 67.6621 | 74.6138 | 69.8952 | 69.8952 | 69.8952 | 69.8952 | 69.8952 | 69.8952 | 69.8952 | 69.8952 | 69.8952 | 69.8952 | 69.8952 | 69.8952 | 69.8952 | 69.8952 | 69.8952 | 69.8952
97% |  | 64.3022 | 81.5872 | 84.5221 | 86.7999 | 90.7464 | 99.7446 | 105.7551 | 113.3832 | 117.3353 | 120.8025 | 114.3559 | 121.8775 | 133.7114 | 124.704 | 124.704 | 124.704 | 124.704 | 124.704 | 124.704 | 124.704 | 124.704 | 124.704 | 124.704 | 124.704 | 124.704 | 124.704 | 124.704 | 124.704 | 124.704 |  | 9.8356 | 75.5748 | 93.5354 | 96.3025 | 98.0462 | 101.9067 | 111.0458 | 116.0208 | 125.5268 | 154.454 | 130.5706 | 125.888 | 132.1725 | 145.9349 | 136.5934 | 136.5934 | 136.5934 | 136.5934 | 136.5934 | 136.5934 | 136.5934 | 136.5934 | 136.5934 | 136.5934 | 136.5934 | 136.5934 | 136.5934 | 136.5934 | 136.5934 | 136.5934
95% |  | 181.8568 | 232.914 | 241.5832 | 248.3116 | 259.9688 | 286.5483 | 304.3023 | 326.8347 | 338.5083 | 348.75 | 329.7076 | 351.9256 | 386.8808 | 360.2743 | 360.2743 | 360.2743 | 360.2743 | 360.2743 | 360.2743 | 360.2743 | 360.2743 | 360.2743 | 360.2743 | 360.2743 | 360.2743 | 360.2743 | 360.2743 | 360.2743 | 360.2743 |  | 20.9709 | 215.1544 | 268.2072 | 276.3809 | 281.5313 | 292.9348 | 319.9304 | 334.6257 | 362.705 | 448.1513 | 377.6034 | 363.7719 | 382.3354 | 422.9874 | 395.3941 | 395.3941 | 395.3941 | 395.3941 | 395.3941 | 395.3941 | 395.3941 | 395.3941 | 395.3941 | 395.3941 | 395.3941 | 395.3941 | 395.3941 | 395.3941 | 395.3941 | 395.3941
90% |  | 893.0903 | 1174.5993 | 1222.3975 | 1259.4956 | 1323.7687 | 1470.3172 | 1568.2056 | 1692.4401 | 1756.8041 | 1813.2726 | 1708.2805 | 1830.7812 | 2023.5105 | 1876.813 | 1876.813 | 1876.813 | 1876.813 | 1876.813 | 1876.813 | 1876.813 | 1876.813 | 1876.813 | 1876.813 | 1876.813 | 1876.813 | 1876.813 | 1876.813 | 1876.813 | 1876.813 |  | 23.4784 | 1076.68 | 1369.1919 | 1414.2584 | 1442.6557 | 1505.5298 | 1654.3725 | 1735.397 | 1890.2148 | 2361.3315 | 1972.3588 | 1896.0974 | 1998.4489 | 2222.5876 | 2070.4492 | 2070.4492 | 2070.4492 | 2070.4492 | 2070.4492 | 2070.4492 | 2070.4492 | 2070.4492 | 2070.4492 | 2070.4492 | 2070.4492 | 2070.4492 | 2070.4492 | 2070.4492 | 2070.4492 | 2070.4492
85% |  | 1762.1242 | 2449.8304 | 2566.598 | 2657.2259 | 2814.2407 | 3172.248 | 3411.3825 | 3714.8785 | 3872.1151 | 4010.0635 | 3753.5754 | 4052.8358 | 4523.6597 | 4165.2882 | 4165.2882 | 4165.2882 | 4165.2882 | 4165.2882 | 4165.2882 | 4165.2882 | 4165.2882 | 4165.2882 | 4165.2882 | 4165.2882 | 4165.2882 | 4165.2882 | 4165.2882 | 4165.2882 | 4165.2882 |  |  | 2210.6207 | 2925.2063 | 3035.3005 | 3104.6731 | 3258.27 | 3621.8821 | 3819.8191 | 4198.028 | 5348.9323 | 4398.6997 | 4212.3987 | 4462.436 | 5009.9908 | 4638.3275 | 4638.3275 | 4638.3275 | 4638.3275 | 4638.3275 | 4638.3275 | 4638.3275 | 4638.3275 | 4638.3275 | 4638.3275 | 4638.3275 | 4638.3275 | 4638.3275 | 4638.3275 | 4638.3275 | 4638.3275
80% |  | 2007.5732 | 3076.4726 | 3257.9641 | 3398.8267 | 3642.8742 | 4199.3237 | 4571.0097 | 5042.7323 | 5287.1246 | 5501.5374 | 5102.8788 | 5568.0182 | 6299.8181 | 5742.8026 | 5742.8026 | 5742.8026 | 5742.8026 | 5742.8026 | 5742.8026 | 5742.8026 | 5742.8026 | 5742.8026 | 5742.8026 | 5742.8026 | 5742.8026 | 5742.8026 | 5742.8026 | 5742.8026 | 5742.8026 |  |  | 2704.6698 | 3815.3477 | 3986.4666 | 4094.2922 | 4333.0273 | 4898.1884 | 5205.8411 | 5793.6899 | 7582.5364 | 6105.5932 | 5816.0263 | 6204.6584 | 7055.7208 | 6478.0459 | 6478.0459 | 6478.0459 | 6478.0459 | 6478.0459 | 6478.0459 | 6478.0459 | 6478.0459 | 6478.0459 | 6478.0459 | 6478.0459 | 6478.0459 | 6478.0459 | 6478.0459 | 6478.0459 | 6478.0459
75% |  | 1303.991 | 2483.2854 | 2683.5211 | 2838.9319 | 3108.1844 | 3722.1035 | 4132.1769 | 4652.6186 | 4922.2514 | 5158.8086 | 4718.9769 | 5232.1555 | 6039.5351 | 5424.9915 | 5424.9915 | 5424.9915 | 5424.9915 | 5424.9915 | 5424.9915 | 5424.9915 | 5424.9915 | 5424.9915 | 5424.9915 | 5424.9915 | 5424.9915 | 5424.9915 | 5424.9915 | 5424.9915 | 5424.9915 |  |  | 2073.0831 | 3298.4708 | 3487.2627 | 3606.2244 | 3869.6159 | 4493.1463 | 4832.5731 | 5481.1343 | 7454.7312 | 5825.2508 | 5505.7776 | 5934.5473 | 6873.5067 | 6236.17 | 6236.17 | 6236.17 | 6236.17 | 6236.17 | 6236.17 | 6236.17 | 6236.17 | 6236.17 | 6236.17 | 6236.17 | 6236.17 | 6236.17 | 6236.17 | 6236.17 | 6236.17
70% |  | 329.0664 | 1554.418 | 1769.5601 | 1936.5403 | 2225.837 | 2885.4588 | 3326.0597 | 3885.2453 | 4174.9507 | 4429.1182 | 3956.5436 | 4507.9253 | 5375.4095 | 4715.1168 | 4715.1168 | 4715.1168 | 4715.1168 | 4715.1168 | 4715.1168 | 4715.1168 | 4715.1168 | 4715.1168 | 4715.1168 | 4715.1168 | 4715.1168 | 4715.1168 | 4715.1168 | 4715.1168 | 4715.1168 |  |  | 1113.6786 | 2430.2892 | 2633.1355 | 2760.9532 | 3043.9527 | 3713.9012 | 4078.5963 | 4775.4391 | 6895.9587 | 5145.173 | 4801.917 | 5262.606 | 6271.4654 | 5586.6828 | 5586.6828 | 5586.6828 | 5586.6828 | 5586.6828 | 5586.6828 | 5586.6828 | 5586.6828 | 5586.6828 | 5586.6828 | 5586.6828 | 5586.6828 | 5586.6828 | 5586.6828 | 5586.6828 | 5586.6828
65% |  |  | 357.6004 | 534.3679 | 694.2568 | 998.0683 | 1693.1832 | 2157.4921 | 2746.7664 | 3052.0604 | 3319.9042 | 2821.9012 | 3402.9518 | 4317.1138 | 3621.2919 | 3621.2919 | 3621.2919 | 3621.2919 | 3621.2919 | 3621.2919 | 3621.2919 | 3621.2919 | 3621.2919 | 3621.2919 | 3621.2919 | 3621.2919 | 3621.2919 | 3621.2919 | 3621.2919 | 3621.2919 |  |  | 102.8871 | 1213.5217 | 1427.2829 | 1561.9782 | 1860.2054 | 2566.2027 | 2950.5214 | 3684.8601 | 5919.4811 | 4074.4887 | 3712.7627 | 4198.2405 | 5261.3849 | 4539.7553 | 4539.7553 | 4539.7553 | 4539.7553 | 4539.7553 | 4539.7553 | 4539.7553 | 4539.7553 | 4539.7553 | 4539.7553 | 4539.7553 | 4539.7553 | 4539.7553 | 4539.7553 | 4539.7553 | 4539.7553
60% | [5 empty] | 22.0281 | 310.8024 | 678.0302 | 1303.0236 | 1639.1146 | 1933.9776 | 1385.7376 | 2025.4028 | 3031.7826 | 2265.7684 | 2265.7684 | 2265.7684 | 2265.7684 | 2265.7684 | 2265.7684 | 2265.7684 | 2265.7684 | 2265.7684 | 2265.7684 | 2265.7684 | 2265.7684 | 2265.7684 | 2265.7684 | 2265.7684 | 2265.7684 |  |  |  | 76.5442 | 162.0907 | 231.6582 | 427.4699 | 1104.2451 | 1527.3326 | 2335.7491 | 4795.7916 | 2764.6822 | 2366.4664 | 2900.9178 | 4071.3088 | 3276.8835 | 3276.8835 | 3276.8835 | 3276.8835 | 3276.8835 | 3276.8835 | 3276.8835 | 3276.8835 | 3276.8835 | 3276.8835 | 3276.8835 | 3276.8835 | 3276.8835 | 3276.8835 | 3276.8835 | 3276.8835
55% | [8 empty] | 31.8697 | 126.1441 | 258.2709 | 49.3804 | 308.3505 | 1129.5587 | 460.0863 | 460.0863 | 460.0863 | 460.0863 | 460.0863 | 460.0863 | 460.0863 | 460.0863 | 460.0863 | 460.0863 | 460.0863 | 460.0863 | 460.0863 | 460.0863 | 460.0863 | 460.0863 | [7 empty] | 5.3153 | 88.0196 | 509.6432 | 3087.7799 | 864.8984 | 532.1518 | 995.8136 | 2281.8383 | 1398.09 | 1398.09 | 1398.09 | 1398.09 | 1398.09 | 1398.09 | 1398.09 | 1398.09 | 1398.09 | 1398.09 | 1398.09 | 1398.09 | 1398.09 | 1398.09 | 1398.09 | 1398.09
50% | [40 empty] | 614.3108 |  |  |  | 194.216 | 2.9117 | 2.9117 | 2.9117 | 2.9117 | 2.9117 | 2.9117 | 2.9117 | 2.9117 | 2.9117 | 2.9117 | 2.9117 | 2.9117 | 2.9117 | 2.9117 | 2.9117 | 2.9117
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0.54918 | 6604.2219 | 11489.0059 | 12441.5431 | 13203.537 | 14572.5364 | 17934.9211 | 20355.1972 | 23617.6722 | 25397.9652 | 27009.2878 | 24050.1225 | 27518.0067 | 33387.7721 | 28875.549 | 28875.549 | 28875.549 | 28875.549 | 28875.549 | 28875.549 | 28875.549 | 28875.549 | 28875.549 | 28875.549 | 28875.549 | 28875.549 | 28875.549 | 28875.549 | 28875.549 | 28875.549 | E @ R (MWh) | 65.83 | 9645.0538 | 15579.729 | 16610.4697 | 17275.6237 | 18790.1152 | 22593.9352 | 24799.0804 | 29276.1679 | 44809.5484 | 31783.1886 | 29452.7715 | 32597.5368 | 39949.1057 | 34888.7767 | 34888.7767 | 34888.7767 | 34888.7767 | 34888.7767 | 34888.7767 | 34888.7767 | 34888.7767 | 34888.7767 | 34888.7767 | 34888.7767 | 34888.7767 | 34888.7767 | 34888.7767 | 34888.7767 | 34888.7767
Option 6 Winter POE50 W E @ R (MWh) N 1 | 0.38442 | 4622.9553 | 8042.3041 | 8709.0802 | 9242.4759 | 10200.7755 | 12554.4447 | 14248.638 | 16532.3706 | 17778.5756 | 18906.5014 | 16835.0857 | 19262.6047 | 23371.4405 | 20212.8843 | 20212.8843 | 20212.8843 | 20212.8843 | 20212.8843 | 20212.8843 | 20212.8843 | 20212.8843 | 20212.8843 | 20212.8843 | 20212.8843 | 20212.8843 | 20212.8843 | 20212.8843 | 20212.8843 | 20212.8843 | Option 6 Winter POE10 W E @ R (MWh) N 1 | 19.749 | 2893.5161 | 4673.9187 | 4983.1409 | 5182.6871 | 5637.0346 | 6778.1806 | 7439.7241 | 8782.8504 | 13442.8645 | 9534.9566 | 8835.8314 | 9779.261 | 11984.7317 | 10466.633 | 10466.633 | 10466.633 | 10466.633 | 10466.633 | 10466.633 | 10466.633 | 10466.633 | 10466.633 | 10466.633 | 10466.633 | 10466.633 | 10466.633 | 10466.633 | 10466.633 | 10466.633
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 26.6023 | 54.4041 | 61.674 | 61.2344 | 61.2607 | 62.0035 | 63.97 | 65.2829 | 66.5702 | 68.0765 | 69.4698 | 70.8245 | 70.9755 | 72.5573 | 71.351 | 71.351 | 71.351 | 71.351 | 71.351 | 71.351 | 71.351 | 71.351 | 71.351 | 71.351 | 71.351 | 71.351 | 71.351 | 71.351 | 71.351 | 71.351
98% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 12.8254 | 26.5866 | 30.185 | 29.9674 | 29.9804 | 30.3481 | 31.3215 | 31.9713 | 32.6085 | 33.3541 | 34.0438 | 34.7143 | 34.789 | 35.572 | 34.9749 | 34.9749 | 34.9749 | 34.9749 | 34.9749 | 34.9749 | 34.9749 | 34.9749 | 34.9749 | 34.9749 | 34.9749 | 34.9749 | 34.9749 | 34.9749 | 34.9749 | 34.9749
97% | 3.7957 | 10.5928 | 12.4418 | 12.3872 | 12.3841 | 12.5942 | 12.8249 | 13.2988 | 13.6394 | 13.8238 | 14.0252 | 14.2099 | 14.5441 | 14.9591 | 14.9293 | 14.9293 | 14.9293 | 14.9293 | 14.9293 | 14.9293 | 14.9293 | 14.9293 | 14.9293 | 14.9293 | 14.9293 | 14.9293 | 14.9293 | 14.9293 | 14.9293 | 14.9293 |  | 24.6994 | 51.9423 | 59.0661 | 58.6353 | 58.6611 | 59.389 | 61.3159 | 62.6024 | 63.8639 | 65.3399 | 66.7052 | 68.0327 | 68.1807 | 69.7307 | 68.5486 | 68.5486 | 68.5486 | 68.5486 | 68.5486 | 68.5486 | 68.5486 | 68.5486 | 68.5486 | 68.5486 | 68.5486 | 68.5486 | 68.5486 | 68.5486 | 68.5486 | 68.5486
95% | 17.3774 | 50.84 | 59.9429 | 59.674 | 59.6588 | 60.6932 | 61.8287 | 64.162 | 65.8388 | 66.7468 | 67.7383 | 68.6472 | 70.2926 | 72.3358 | 72.1891 | 72.1891 | 72.1891 | 72.1891 | 72.1891 | 72.1891 | 72.1891 | 72.1891 | 72.1891 | 72.1891 | 72.1891 | 72.1891 | 72.1891 | 72.1891 | 72.1891 | 72.1891 |  | 34.9082 | 75.1439 | 85.6653 | 85.029 | 85.0671 | 86.1421 | 88.988 | 90.8882 | 92.7512 | 94.9312 | 96.9477 | 98.9082 | 99.1268 | 101.416 | 99.6701 | 99.6701 | 99.6701 | 99.6701 | 99.6701 | 99.6701 | 99.6701 | 99.6701 | 99.6701 | 99.6701 | 99.6701 | 99.6701 | 99.6701 | 99.6701 | 99.6701 | 99.6701
90% | 24.555 | 82.5918 | 98.3797 | 97.9133 | 97.8869 | 99.681 | 101.6504 | 105.6971 | 108.6054 | 110.1802 | 111.8997 | 113.4762 | 116.33 | 119.8735 | 119.6191 | 119.6191 | 119.6191 | 119.6191 | 119.6191 | 119.6191 | 119.6191 | 119.6191 | 119.6191 | 119.6191 | 119.6191 | 119.6191 | 119.6191 | 119.6191 | 119.6191 | 119.6191 |  | 134.6084 | 309.068 | 354.6878 | 351.9289 | 352.0941 | 356.7553 | 369.095 | 377.3339 | 385.4121 | 394.8642 | 403.6075 | 412.1082 | 413.0559 | 422.9818 | 415.4119 | 415.4119 | 415.4119 | 415.4119 | 415.4119 | 415.4119 | 415.4119 | 415.4119 | 415.4119 | 415.4119 | 415.4119 | 415.4119 | 415.4119 | 415.4119 | 415.4119 | 415.4119
85% | 44.847 | 209.5458 | 254.3493 | 253.0259 | 252.9509 | 258.0423 | 263.6311 | 275.1149 | 283.3684 | 287.8374 | 292.7171 | 297.1909 | 305.2894 | 315.3454 | 314.6234 | 314.6234 | 314.6234 | 314.6234 | 314.6234 | 314.6234 | 314.6234 | 314.6234 | 314.6234 | 314.6234 | 314.6234 | 314.6234 | 314.6234 | 314.6234 | 314.6234 | 314.6234 |  | 102.4961 | 267.5254 | 310.6793 | 308.0696 | 308.2258 | 312.635 | 324.3078 | 332.1012 | 339.7428 | 348.684 | 356.9547 | 364.9959 | 365.8924 | 375.2817 | 368.121 | 368.121 | 368.121 | 368.121 | 368.121 | 368.121 | 368.121 | 368.121 | 368.121 | 368.121 | 368.121 | 368.121 | 368.121 | 368.121 | 368.121 | 368.121
80% | 23.7465 | 253.802 | 316.3847 | 314.536 | 314.4314 | 321.5432 | 329.3497 | 345.3906 | 356.9192 | 363.1617 | 369.9778 | 376.2269 | 387.5391 | 401.5855 | 400.577 | 400.577 | 400.577 | 400.577 | 400.577 | 400.577 | 400.577 | 400.577 | 400.577 | 400.577 | 400.577 | 400.577 | 400.577 | 400.577 | 400.577 | 400.577 |  | 52.1361 | 167.3947 | 197.5339 | 195.7112 | 195.8203 | 198.8998 | 207.0522 | 212.4953 | 217.8322 | 224.0769 | 229.8532 | 235.4693 | 236.0954 | 242.6531 | 237.6519 | 237.6519 | 237.6519 | 237.6519 | 237.6519 | 237.6519 | 237.6519 | 237.6519 | 237.6519 | 237.6519 | 237.6519 | 237.6519 | 237.6519 | 237.6519 | 237.6519 | 237.6519
75% | 0.18716 | 547.1351 | 710.2768 | 705.4576 | 705.1848 | 723.724 | 744.0742 | 785.8898 | 815.9429 | 832.2159 | 849.9842 | 866.2744 | 895.7633 | 932.3798 | 929.7508 | 929.7508 | 929.7508 | 929.7508 | 929.7508 | 929.7508 | 929.7508 | 929.7508 | 929.7508 | 929.7508 | 929.7508 | 929.7508 | 929.7508 | 929.7508 | 929.7508 | 929.7508 |  | 53.8635 | 259.5826 | 313.3765 | 310.1233 | 310.3181 | 315.8145 | 330.3652 | 340.0803 | 349.6059 | 360.7517 | 371.0616 | 381.0855 | 382.203 | 393.9074 | 384.9811 | 384.9811 | 384.9811 | 384.9811 | 384.9811 | 384.9811 | 384.9811 | 384.9811 | 384.9811 | 384.9811 | 384.9811 | 384.9811 | 384.9811 | 384.9811 | 384.9811 | 384.9811
70% |  | 720.2141 | 1002.0732 | 993.7472 | 993.2758 | 1025.3059 | 1060.4649 | 1132.7095 | 1184.6321 | 1212.7469 | 1243.4451 | 1271.5896 | 1322.5375 | 1385.7996 | 1381.2574 | 1381.2574 | 1381.2574 | 1381.2574 | 1381.2574 | 1381.2574 | 1381.2574 | 1381.2574 | 1381.2574 | 1381.2574 | 1381.2574 | 1381.2574 | 1381.2574 | 1381.2574 | 1381.2574 | 1381.2574 |  | 21.0605 | 391.6455 | 489.6437 | 483.7172 | 484.0719 | 494.0849 | 520.5925 | 538.2908 | 555.6439 | 575.9484 | 594.7305 | 612.9912 | 615.027 | 636.3493 | 620.088 | 620.088 | 620.088 | 620.088 | 620.088 | 620.088 | 620.088 | 620.088 | 620.088 | 620.088 | 620.088 | 620.088 | 620.088 | 620.088 | 620.088 | 620.088
65% |  | 1159.8257 | 1867.7211 | 1846.81 | 1845.6263 | 1926.0704 | 2014.373 | 2195.817 | 2326.2218 | 2396.8327 | 2473.9318 | 2544.6175 | 2672.5742 | 2831.4585 | 2820.0507 | 2820.0507 | 2820.0507 | 2820.0507 | 2820.0507 | 2820.0507 | 2820.0507 | 2820.0507 | 2820.0507 | 2820.0507 | 2820.0507 | 2820.0507 | 2820.0507 | 2820.0507 | 2820.0507 | 2820.0507 |  |  | 375.3893 | 498.6861 | 491.2298 | 491.676 | 504.2739 | 537.6246 | 559.8917 | 581.7247 | 607.2709 | 630.9016 | 653.8765 | 656.4378 | 683.2646 | 662.8054 | 662.8054 | 662.8054 | 662.8054 | 662.8054 | 662.8054 | 662.8054 | 662.8054 | 662.8054 | 662.8054 | 662.8054 | 662.8054 | 662.8054 | 662.8054 | 662.8054 | 662.8054
60% |  | 595.1039 | 1629.6346 | 1599.0683 | 1597.338 | 1714.9251 | 1843.9992 | 2109.2202 | 2299.836 | 2403.0496 | 2515.7473 | 2619.0702 | 2806.1076 | 3038.3525 | 3021.6775 | 3021.6775 | 3021.6775 | 3021.6775 | 3021.6775 | 3021.6775 | 3021.6775 | 3021.6775 | 3021.6775 | 3021.6775 | 3021.6775 | 3021.6775 | 3021.6775 | 3021.6775 | 3021.6775 | 3021.6775 |  |  | 374.3821 | 567.3189 | 555.6511 | 556.3494 | 576.0627 | 628.2504 | 663.0943 | 697.2588 | 737.234 | 774.2116 | 810.1631 | 814.1711 | 856.15 | 824.1351 | 824.1351 | 824.1351 | 824.1351 | 824.1351 | 824.1351 | 824.1351 | 824.1351 | 824.1351 | 824.1351 | 824.1351 | 824.1351 | 824.1351 | 824.1351 | 824.1351 | 824.1351
55% |  |  | 438.6107 | 413.2466 | 411.832 | 513.1119 | 636.1403 | 924.2646 | 1139.8067 | 1256.5173 | 1383.9522 | 1500.7863 | 1712.2821 | 1974.8972 | 1956.0416 | 1956.0416 | 1956.0416 | 1956.0416 | 1956.0416 | 1956.0416 | 1956.0416 | 1956.0416 | 1956.0416 | 1956.0416 | 1956.0416 | 1956.0416 | 1956.0416 | 1956.0416 | 1956.0416 | 1956.0416 |  |  | 239.8473 | 609.6211 | 587.1995 | 588.5414 | 626.4237 | 726.7105 | 793.6685 | 859.321 | 936.1395 | 1007.1978 | 1076.2842 | 1083.9862 | 1164.6552 | 1103.1336 | 1103.1336 | 1103.1336 | 1103.1336 | 1103.1336 | 1103.1336 | 1103.1336 | 1103.1336 | 1103.1336 | 1103.1336 | 1103.1336 | 1103.1336 | 1103.1336 | 1103.1336 | 1103.1336 | 1103.1336
50% | [7 empty] | 3.4281 | 36.6085 | 68.9695 | 115.5831 | 168.4762 | 288.3744 | 479.2895 | 464.0651 | 464.0651 | 464.0651 | 464.0651 | 464.0651 | 464.0651 | 464.0651 | 464.0651 | 464.0651 | 464.0651 | 464.0651 | 464.0651 | 464.0651 | 464.0651 | 464.0651 | 464.0651 |  |  |  | 218.9141 | 191.3668 | 192.9659 | 240.7061 | 390.8095 | 509.6193 | 640.0757 | 807.8717 | 965.5671 | 1118.8862 | 1135.9788 | 1315.0026 | 1178.4715 | 1178.4715 | 1178.4715 | 1178.4715 | 1178.4715 | 1178.4715 | 1178.4715 | 1178.4715 | 1178.4715 | 1178.4715 | 1178.4715 | 1178.4715 | 1178.4715 | 1178.4715 | 1178.4715 | 1178.4715
45% | [40 empty] | 3.1349 | 28.4196 | 76.7087 | 83.5101 | 171.461 | 101.6343 | 101.6343 | 101.6343 | 101.6343 | 101.6343 | 101.6343 | 101.6343 | 101.6343 | 101.6343 | 101.6343 | 101.6343 | 101.6343 | 101.6343 | 101.6343 | 101.6343 | 101.6343
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 114.5088 | 3629.6513 | 6389.8148 | 6295.8662 | 6290.5691 | 6655.6913 | 7068.3364 | 7954.9925 | 8631.4193 | 9012.0818 | 9439.0017 | 9840.5652 | 10591.6343 | 11566.2763 | 11494.7808 | 11494.7808 | 11494.7808 | 11494.7808 | 11494.7808 | 11494.7808 | 11494.7808 | 11494.7808 | 11494.7808 | 11494.7808 | 11494.7808 | 11494.7808 | 11494.7808 | 11494.7808 | 11494.7808 | 11494.7808 | E @ R (MWh) | 463.1998 | 2592.9116 | 3797.0519 | 3709.8635 | 3715.0322 | 3863.5385 | 4280.4031 | 4577.3201 | 4882.411 | 5257.6779 | 5629.6718 | 6015.0485 | 6059.4299 | 6540.9827 | 6170.9785 | 6170.9785 | 6170.9785 | 6170.9785 | 6170.9785 | 6170.9785 | 6170.9785 | 6170.9785 | 6170.9785 | 6170.9785 | 6170.9785 | 6170.9785 | 6170.9785 | 6170.9785 | 6170.9785 | 6170.9785
Option 6 Summer POE50 W E @ R (MWh) N 1 | 80.1561 | 2540.7559 | 4472.8704 | 4407.1063 | 4403.3984 | 4658.9839 | 4947.8355 | 5568.4947 | 6041.9935 | 6308.4573 | 6607.3012 | 6888.3957 | 7414.144 | 8096.3934 | 8046.3465 | 8046.3465 | 8046.3465 | 8046.3465 | 8046.3465 | 8046.3465 | 8046.3465 | 8046.3465 | 8046.3465 | 8046.3465 | 8046.3465 | 8046.3465 | 8046.3465 | 8046.3465 | 8046.3465 | 8046.3465 | Option 6 Summer POE10 W E @ R (MWh) N 1 | 138.9599 | 777.8735 | 1139.1156 | 1112.959 | 1114.5097 | 1159.0616 | 1284.1209 | 1373.196 | 1464.7233 | 1577.3034 | 1688.9015 | 1804.5146 | 1817.829 | 1962.2948 | 1851.2936 | 1851.2936 | 1851.2936 | 1851.2936 | 1851.2936 | 1851.2936 | 1851.2936 | 1851.2936 | 1851.2936 | 1851.2936 | 1851.2936 | 1851.2936 | 1851.2936 | 1851.2936 | 1851.2936 | 1851.2936
Option 7 -
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | 0.52857 | 28.8388 | 36.1886 | 37.4366 | 38.4052 | 40.0833 | 43.9094 | 46.4652 | 49.7088 | 51.3892 | 52.8635 | 50.1223 | 53.3207 | 58.3526 | 54.5225 | 54.5225 | 54.5225 | 54.5225 | 54.5225 | 54.5225 | 54.5225 | 54.5225 | 54.5225 | 54.5225 | 54.5225 | 54.5225 | 54.5225 | 54.5225 | 54.5225 | 54.5225 |  | 5.6789 | 33.6321 | 41.2692 | 42.4458 | 43.1872 | 44.8288 | 48.7149 | 50.8303 | 54.8724 | 67.1726 | 57.0171 | 55.026 | 57.6982 | 63.5502 | 59.5781 | 59.5781 | 59.5781 | 59.5781 | 59.5781 | 59.5781 | 59.5781 | 59.5781 | 59.5781 | 59.5781 | 59.5781 | 59.5781 | 59.5781 | 59.5781 | 59.5781 | 59.5781
98% | 0.020606 | 33.3788 | 42.11 | 43.5925 | 44.7431 | 46.7365 | 51.2818 | 54.3179 | 58.1711 | 60.1673 | 61.9187 | 58.6624 | 62.4618 | 68.4394 | 63.8895 | 63.8895 | 63.8895 | 63.8895 | 63.8895 | 63.8895 | 63.8895 | 63.8895 | 63.8895 | 63.8895 | 63.8895 | 63.8895 | 63.8895 | 63.8895 | 63.8895 | 63.8895 |  | 5.8662 | 39.073 | 48.1454 | 49.5431 | 50.4239 | 52.374 | 56.9904 | 59.5034 | 64.3051 | 78.9171 | 66.8529 | 64.4876 | 67.6621 | 74.6138 | 69.8952 | 69.8952 | 69.8952 | 69.8952 | 69.8952 | 69.8952 | 69.8952 | 69.8952 | 69.8952 | 69.8952 | 69.8952 | 69.8952 | 69.8952 | 69.8952 | 69.8952 | 69.8952
97% |  | 64.3022 | 81.5872 | 84.5221 | 86.7999 | 90.7464 | 99.7446 | 105.7551 | 113.3832 | 117.3353 | 120.8025 | 114.3559 | 121.8775 | 133.7114 | 124.704 | 124.704 | 124.704 | 124.704 | 124.704 | 124.704 | 124.704 | 124.704 | 124.704 | 124.704 | 124.704 | 124.704 | 124.704 | 124.704 | 124.704 | 124.704 |  | 9.8356 | 75.5748 | 93.5354 | 96.3025 | 98.0462 | 101.9067 | 111.0458 | 116.0208 | 125.5268 | 154.454 | 130.5706 | 125.888 | 132.1725 | 145.9349 | 136.5934 | 136.5934 | 136.5934 | 136.5934 | 136.5934 | 136.5934 | 136.5934 | 136.5934 | 136.5934 | 136.5934 | 136.5934 | 136.5934 | 136.5934 | 136.5934 | 136.5934 | 136.5934
95% |  | 181.8568 | 232.914 | 241.5832 | 248.3116 | 259.9688 | 286.5483 | 304.3023 | 326.8347 | 338.5083 | 348.75 | 329.7076 | 351.9256 | 386.8808 | 360.2743 | 360.2743 | 360.2743 | 360.2743 | 360.2743 | 360.2743 | 360.2743 | 360.2743 | 360.2743 | 360.2743 | 360.2743 | 360.2743 | 360.2743 | 360.2743 | 360.2743 | 360.2743 |  | 20.9709 | 215.1544 | 268.2072 | 276.3809 | 281.5313 | 292.9348 | 319.9304 | 334.6257 | 362.705 | 448.1513 | 377.6034 | 363.7719 | 382.3354 | 422.9874 | 395.3941 | 395.3941 | 395.3941 | 395.3941 | 395.3941 | 395.3941 | 395.3941 | 395.3941 | 395.3941 | 395.3941 | 395.3941 | 395.3941 | 395.3941 | 395.3941 | 395.3941 | 395.3941
90% |  | 893.0903 | 1174.5993 | 1222.3975 | 1259.4956 | 1323.7687 | 1470.3172 | 1568.2056 | 1692.4401 | 1756.8041 | 1813.2726 | 1708.2805 | 1830.7812 | 2023.5105 | 1876.813 | 1876.813 | 1876.813 | 1876.813 | 1876.813 | 1876.813 | 1876.813 | 1876.813 | 1876.813 | 1876.813 | 1876.813 | 1876.813 | 1876.813 | 1876.813 | 1876.813 | 1876.813 |  | 23.4784 | 1076.68 | 1369.1919 | 1414.2584 | 1442.6557 | 1505.5298 | 1654.3725 | 1735.397 | 1890.2148 | 2361.3315 | 1972.3588 | 1896.0974 | 1998.4489 | 2222.5876 | 2070.4492 | 2070.4492 | 2070.4492 | 2070.4492 | 2070.4492 | 2070.4492 | 2070.4492 | 2070.4492 | 2070.4492 | 2070.4492 | 2070.4492 | 2070.4492 | 2070.4492 | 2070.4492 | 2070.4492 | 2070.4492
85% |  | 1762.1242 | 2449.8304 | 2566.598 | 2657.2259 | 2814.2407 | 3172.248 | 3411.3825 | 3714.8785 | 3872.1151 | 4010.0635 | 3753.5754 | 4052.8358 | 4523.6597 | 4165.2882 | 4165.2882 | 4165.2882 | 4165.2882 | 4165.2882 | 4165.2882 | 4165.2882 | 4165.2882 | 4165.2882 | 4165.2882 | 4165.2882 | 4165.2882 | 4165.2882 | 4165.2882 | 4165.2882 | 4165.2882 |  |  | 2210.6207 | 2925.2063 | 3035.3005 | 3104.6731 | 3258.27 | 3621.8821 | 3819.8191 | 4198.028 | 5348.9323 | 4398.6997 | 4212.3987 | 4462.436 | 5009.9908 | 4638.3275 | 4638.3275 | 4638.3275 | 4638.3275 | 4638.3275 | 4638.3275 | 4638.3275 | 4638.3275 | 4638.3275 | 4638.3275 | 4638.3275 | 4638.3275 | 4638.3275 | 4638.3275 | 4638.3275 | 4638.3275
80% |  | 2007.5732 | 3076.4726 | 3257.9641 | 3398.8267 | 3642.8742 | 4199.3237 | 4571.0097 | 5042.7323 | 5287.1246 | 5501.5374 | 5102.8788 | 5568.0182 | 6299.8181 | 5742.8026 | 5742.8026 | 5742.8026 | 5742.8026 | 5742.8026 | 5742.8026 | 5742.8026 | 5742.8026 | 5742.8026 | 5742.8026 | 5742.8026 | 5742.8026 | 5742.8026 | 5742.8026 | 5742.8026 | 5742.8026 |  |  | 2704.6698 | 3815.3477 | 3986.4666 | 4094.2922 | 4333.0273 | 4898.1884 | 5205.8411 | 5793.6899 | 7582.5364 | 6105.5932 | 5816.0263 | 6204.6584 | 7055.7208 | 6478.0459 | 6478.0459 | 6478.0459 | 6478.0459 | 6478.0459 | 6478.0459 | 6478.0459 | 6478.0459 | 6478.0459 | 6478.0459 | 6478.0459 | 6478.0459 | 6478.0459 | 6478.0459 | 6478.0459 | 6478.0459
75% |  | 1303.991 | 2483.2854 | 2683.5211 | 2838.9319 | 3108.1844 | 3722.1035 | 4132.1769 | 4652.6186 | 4922.2514 | 5158.8086 | 4718.9769 | 5232.1555 | 6039.5351 | 5424.9915 | 5424.9915 | 5424.9915 | 5424.9915 | 5424.9915 | 5424.9915 | 5424.9915 | 5424.9915 | 5424.9915 | 5424.9915 | 5424.9915 | 5424.9915 | 5424.9915 | 5424.9915 | 5424.9915 | 5424.9915 |  |  | 2073.0831 | 3298.4708 | 3487.2627 | 3606.2244 | 3869.6159 | 4493.1463 | 4832.5731 | 5481.1343 | 7454.7312 | 5825.2508 | 5505.7776 | 5934.5473 | 6873.5067 | 6236.17 | 6236.17 | 6236.17 | 6236.17 | 6236.17 | 6236.17 | 6236.17 | 6236.17 | 6236.17 | 6236.17 | 6236.17 | 6236.17 | 6236.17 | 6236.17 | 6236.17 | 6236.17
70% |  | 329.0664 | 1554.418 | 1769.5601 | 1936.5403 | 2225.837 | 2885.4588 | 3326.0597 | 3885.2453 | 4174.9507 | 4429.1182 | 3956.5436 | 4507.9253 | 5375.4095 | 4715.1168 | 4715.1168 | 4715.1168 | 4715.1168 | 4715.1168 | 4715.1168 | 4715.1168 | 4715.1168 | 4715.1168 | 4715.1168 | 4715.1168 | 4715.1168 | 4715.1168 | 4715.1168 | 4715.1168 | 4715.1168 |  |  | 1113.6786 | 2430.2892 | 2633.1355 | 2760.9532 | 3043.9527 | 3713.9012 | 4078.5963 | 4775.4391 | 6895.9587 | 5145.173 | 4801.917 | 5262.606 | 6271.4654 | 5586.6828 | 5586.6828 | 5586.6828 | 5586.6828 | 5586.6828 | 5586.6828 | 5586.6828 | 5586.6828 | 5586.6828 | 5586.6828 | 5586.6828 | 5586.6828 | 5586.6828 | 5586.6828 | 5586.6828 | 5586.6828
65% |  |  | 357.6004 | 534.3679 | 694.2568 | 998.0683 | 1693.1832 | 2157.4921 | 2746.7664 | 3052.0604 | 3319.9042 | 2821.9012 | 3402.9518 | 4317.1138 | 3621.2919 | 3621.2919 | 3621.2919 | 3621.2919 | 3621.2919 | 3621.2919 | 3621.2919 | 3621.2919 | 3621.2919 | 3621.2919 | 3621.2919 | 3621.2919 | 3621.2919 | 3621.2919 | 3621.2919 | 3621.2919 |  |  | 102.8871 | 1213.5217 | 1427.2829 | 1561.9782 | 1860.2054 | 2566.2027 | 2950.5214 | 3684.8601 | 5919.4811 | 4074.4887 | 3712.7627 | 4198.2405 | 5261.3849 | 4539.7553 | 4539.7553 | 4539.7553 | 4539.7553 | 4539.7553 | 4539.7553 | 4539.7553 | 4539.7553 | 4539.7553 | 4539.7553 | 4539.7553 | 4539.7553 | 4539.7553 | 4539.7553 | 4539.7553 | 4539.7553
60% | [5 empty] | 22.0281 | 310.8024 | 678.0302 | 1303.0236 | 1639.1146 | 1933.9776 | 1385.7376 | 2025.4028 | 3031.7826 | 2265.7684 | 2265.7684 | 2265.7684 | 2265.7684 | 2265.7684 | 2265.7684 | 2265.7684 | 2265.7684 | 2265.7684 | 2265.7684 | 2265.7684 | 2265.7684 | 2265.7684 | 2265.7684 | 2265.7684 | 2265.7684 |  |  |  | 76.5442 | 162.0907 | 231.6582 | 427.4699 | 1104.2451 | 1527.3326 | 2335.7491 | 4795.7916 | 2764.6822 | 2366.4664 | 2900.9178 | 4071.3088 | 3276.8835 | 3276.8835 | 3276.8835 | 3276.8835 | 3276.8835 | 3276.8835 | 3276.8835 | 3276.8835 | 3276.8835 | 3276.8835 | 3276.8835 | 3276.8835 | 3276.8835 | 3276.8835 | 3276.8835 | 3276.8835
55% | [8 empty] | 31.8697 | 126.1441 | 258.2709 | 49.3804 | 308.3505 | 1129.5587 | 460.0863 | 460.0863 | 460.0863 | 460.0863 | 460.0863 | 460.0863 | 460.0863 | 460.0863 | 460.0863 | 460.0863 | 460.0863 | 460.0863 | 460.0863 | 460.0863 | 460.0863 | 460.0863 | [7 empty] | 5.3153 | 88.0196 | 509.6432 | 3087.7799 | 864.8984 | 532.1518 | 995.8136 | 2281.8383 | 1398.09 | 1398.09 | 1398.09 | 1398.09 | 1398.09 | 1398.09 | 1398.09 | 1398.09 | 1398.09 | 1398.09 | 1398.09 | 1398.09 | 1398.09 | 1398.09 | 1398.09 | 1398.09
50% | [40 empty] | 614.3108 |  |  |  | 194.216 | 2.9117 | 2.9117 | 2.9117 | 2.9117 | 2.9117 | 2.9117 | 2.9117 | 2.9117 | 2.9117 | 2.9117 | 2.9117 | 2.9117 | 2.9117 | 2.9117 | 2.9117 | 2.9117
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0.54918 | 6604.2219 | 11489.0059 | 12441.5431 | 13203.537 | 14572.5364 | 17934.9211 | 20355.1972 | 23617.6722 | 25397.9652 | 27009.2878 | 24050.1225 | 27518.0067 | 33387.7721 | 28875.549 | 28875.549 | 28875.549 | 28875.549 | 28875.549 | 28875.549 | 28875.549 | 28875.549 | 28875.549 | 28875.549 | 28875.549 | 28875.549 | 28875.549 | 28875.549 | 28875.549 | 28875.549 | E @ R (MWh) | 65.83 | 9645.0538 | 15579.729 | 16610.4697 | 17275.6237 | 18790.1152 | 22593.9352 | 24799.0804 | 29276.1679 | 44809.5484 | 31783.1886 | 29452.7715 | 32597.5368 | 39949.1057 | 34888.7767 | 34888.7767 | 34888.7767 | 34888.7767 | 34888.7767 | 34888.7767 | 34888.7767 | 34888.7767 | 34888.7767 | 34888.7767 | 34888.7767 | 34888.7767 | 34888.7767 | 34888.7767 | 34888.7767 | 34888.7767
Option 7 Winter POE50 W E @ R (MWh) N 1 | 0.38442 | 4622.9553 | 8042.3041 | 8709.0802 | 9242.4759 | 10200.7755 | 12554.4447 | 14248.638 | 16532.3706 | 17778.5756 | 18906.5014 | 16835.0857 | 19262.6047 | 23371.4405 | 20212.8843 | 20212.8843 | 20212.8843 | 20212.8843 | 20212.8843 | 20212.8843 | 20212.8843 | 20212.8843 | 20212.8843 | 20212.8843 | 20212.8843 | 20212.8843 | 20212.8843 | 20212.8843 | 20212.8843 | 20212.8843 | Option 7 Winter POE10 W E @ R (MWh) N 1 | 19.749 | 2893.5161 | 4673.9187 | 4983.1409 | 5182.6871 | 5637.0346 | 6778.1806 | 7439.7241 | 8782.8504 | 13442.8645 | 9534.9566 | 8835.8314 | 9779.261 | 11984.7317 | 10466.633 | 10466.633 | 10466.633 | 10466.633 | 10466.633 | 10466.633 | 10466.633 | 10466.633 | 10466.633 | 10466.633 | 10466.633 | 10466.633 | 10466.633 | 10466.633 | 10466.633 | 10466.633
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 26.6023 | 54.4041 | 61.674 | 61.2344 | 61.2607 | 62.0035 | 63.97 | 65.2829 | 66.5702 | 68.0765 | 69.4698 | 70.8245 | 70.9755 | 72.5573 | 71.351 | 71.351 | 71.351 | 71.351 | 71.351 | 71.351 | 71.351 | 71.351 | 71.351 | 71.351 | 71.351 | 71.351 | 71.351 | 71.351 | 71.351 | 71.351
98% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 12.8254 | 26.5866 | 30.185 | 29.9674 | 29.9804 | 30.3481 | 31.3215 | 31.9713 | 32.6085 | 33.3541 | 34.0438 | 34.7143 | 34.789 | 35.572 | 34.9749 | 34.9749 | 34.9749 | 34.9749 | 34.9749 | 34.9749 | 34.9749 | 34.9749 | 34.9749 | 34.9749 | 34.9749 | 34.9749 | 34.9749 | 34.9749 | 34.9749 | 34.9749
97% | 3.7957 | 10.5928 | 12.4418 | 12.3872 | 12.3841 | 12.5942 | 12.8249 | 13.2988 | 13.6394 | 13.8238 | 14.0252 | 14.2099 | 14.5441 | 14.9591 | 14.9293 | 14.9293 | 14.9293 | 14.9293 | 14.9293 | 14.9293 | 14.9293 | 14.9293 | 14.9293 | 14.9293 | 14.9293 | 14.9293 | 14.9293 | 14.9293 | 14.9293 | 14.9293 |  | 24.6994 | 51.9423 | 59.0661 | 58.6353 | 58.6611 | 59.389 | 61.3159 | 62.6024 | 63.8639 | 65.3399 | 66.7052 | 68.0327 | 68.1807 | 69.7307 | 68.5486 | 68.5486 | 68.5486 | 68.5486 | 68.5486 | 68.5486 | 68.5486 | 68.5486 | 68.5486 | 68.5486 | 68.5486 | 68.5486 | 68.5486 | 68.5486 | 68.5486 | 68.5486
95% | 17.3774 | 50.84 | 59.9429 | 59.674 | 59.6588 | 60.6932 | 61.8287 | 64.162 | 65.8388 | 66.7468 | 67.7383 | 68.6472 | 70.2926 | 72.3358 | 72.1891 | 72.1891 | 72.1891 | 72.1891 | 72.1891 | 72.1891 | 72.1891 | 72.1891 | 72.1891 | 72.1891 | 72.1891 | 72.1891 | 72.1891 | 72.1891 | 72.1891 | 72.1891 |  | 34.9082 | 75.1439 | 85.6653 | 85.029 | 85.0671 | 86.1421 | 88.988 | 90.8882 | 92.7512 | 94.9312 | 96.9477 | 98.9082 | 99.1268 | 101.416 | 99.6701 | 99.6701 | 99.6701 | 99.6701 | 99.6701 | 99.6701 | 99.6701 | 99.6701 | 99.6701 | 99.6701 | 99.6701 | 99.6701 | 99.6701 | 99.6701 | 99.6701 | 99.6701
90% | 24.555 | 82.5918 | 98.3797 | 97.9133 | 97.8869 | 99.681 | 101.6504 | 105.6971 | 108.6054 | 110.1802 | 111.8997 | 113.4762 | 116.33 | 119.8735 | 119.6191 | 119.6191 | 119.6191 | 119.6191 | 119.6191 | 119.6191 | 119.6191 | 119.6191 | 119.6191 | 119.6191 | 119.6191 | 119.6191 | 119.6191 | 119.6191 | 119.6191 | 119.6191 |  | 134.6084 | 309.068 | 354.6878 | 351.9289 | 352.0941 | 356.7553 | 369.095 | 377.3339 | 385.4121 | 394.8642 | 403.6075 | 412.1082 | 413.0559 | 422.9818 | 415.4119 | 415.4119 | 415.4119 | 415.4119 | 415.4119 | 415.4119 | 415.4119 | 415.4119 | 415.4119 | 415.4119 | 415.4119 | 415.4119 | 415.4119 | 415.4119 | 415.4119 | 415.4119
85% | 44.847 | 209.5458 | 254.3493 | 253.0259 | 252.9509 | 258.0423 | 263.6311 | 275.1149 | 283.3684 | 287.8374 | 292.7171 | 297.1909 | 305.2894 | 315.3454 | 314.6234 | 314.6234 | 314.6234 | 314.6234 | 314.6234 | 314.6234 | 314.6234 | 314.6234 | 314.6234 | 314.6234 | 314.6234 | 314.6234 | 314.6234 | 314.6234 | 314.6234 | 314.6234 |  | 102.4961 | 267.5254 | 310.6793 | 308.0696 | 308.2258 | 312.635 | 324.3078 | 332.1012 | 339.7428 | 348.684 | 356.9547 | 364.9959 | 365.8924 | 375.2817 | 368.121 | 368.121 | 368.121 | 368.121 | 368.121 | 368.121 | 368.121 | 368.121 | 368.121 | 368.121 | 368.121 | 368.121 | 368.121 | 368.121 | 368.121 | 368.121
80% | 23.7465 | 253.802 | 316.3847 | 314.536 | 314.4314 | 321.5432 | 329.3497 | 345.3906 | 356.9192 | 363.1617 | 369.9778 | 376.2269 | 387.5391 | 401.5855 | 400.577 | 400.577 | 400.577 | 400.577 | 400.577 | 400.577 | 400.577 | 400.577 | 400.577 | 400.577 | 400.577 | 400.577 | 400.577 | 400.577 | 400.577 | 400.577 |  | 52.1361 | 167.3947 | 197.5339 | 195.7112 | 195.8203 | 198.8998 | 207.0522 | 212.4953 | 217.8322 | 224.0769 | 229.8532 | 235.4693 | 236.0954 | 242.6531 | 237.6519 | 237.6519 | 237.6519 | 237.6519 | 237.6519 | 237.6519 | 237.6519 | 237.6519 | 237.6519 | 237.6519 | 237.6519 | 237.6519 | 237.6519 | 237.6519 | 237.6519 | 237.6519
75% | 0.18716 | 547.1351 | 710.2768 | 705.4576 | 705.1848 | 723.724 | 744.0742 | 785.8898 | 815.9429 | 832.2159 | 849.9842 | 866.2744 | 895.7633 | 932.3798 | 929.7508 | 929.7508 | 929.7508 | 929.7508 | 929.7508 | 929.7508 | 929.7508 | 929.7508 | 929.7508 | 929.7508 | 929.7508 | 929.7508 | 929.7508 | 929.7508 | 929.7508 | 929.7508 |  | 53.8635 | 259.5826 | 313.3765 | 310.1233 | 310.3181 | 315.8145 | 330.3652 | 340.0803 | 349.6059 | 360.7517 | 371.0616 | 381.0855 | 382.203 | 393.9074 | 384.9811 | 384.9811 | 384.9811 | 384.9811 | 384.9811 | 384.9811 | 384.9811 | 384.9811 | 384.9811 | 384.9811 | 384.9811 | 384.9811 | 384.9811 | 384.9811 | 384.9811 | 384.9811
70% |  | 720.2141 | 1002.0732 | 993.7472 | 993.2758 | 1025.3059 | 1060.4649 | 1132.7095 | 1184.6321 | 1212.7469 | 1243.4451 | 1271.5896 | 1322.5375 | 1385.7996 | 1381.2574 | 1381.2574 | 1381.2574 | 1381.2574 | 1381.2574 | 1381.2574 | 1381.2574 | 1381.2574 | 1381.2574 | 1381.2574 | 1381.2574 | 1381.2574 | 1381.2574 | 1381.2574 | 1381.2574 | 1381.2574 |  | 21.0605 | 391.6455 | 489.6437 | 483.7172 | 484.0719 | 494.0849 | 520.5925 | 538.2908 | 555.6439 | 575.9484 | 594.7305 | 612.9912 | 615.027 | 636.3493 | 620.088 | 620.088 | 620.088 | 620.088 | 620.088 | 620.088 | 620.088 | 620.088 | 620.088 | 620.088 | 620.088 | 620.088 | 620.088 | 620.088 | 620.088 | 620.088
65% |  | 1159.8257 | 1867.7211 | 1846.81 | 1845.6263 | 1926.0704 | 2014.373 | 2195.817 | 2326.2218 | 2396.8327 | 2473.9318 | 2544.6175 | 2672.5742 | 2831.4585 | 2820.0507 | 2820.0507 | 2820.0507 | 2820.0507 | 2820.0507 | 2820.0507 | 2820.0507 | 2820.0507 | 2820.0507 | 2820.0507 | 2820.0507 | 2820.0507 | 2820.0507 | 2820.0507 | 2820.0507 | 2820.0507 |  |  | 375.3893 | 498.6861 | 491.2298 | 491.676 | 504.2739 | 537.6246 | 559.8917 | 581.7247 | 607.2709 | 630.9016 | 653.8765 | 656.4378 | 683.2646 | 662.8054 | 662.8054 | 662.8054 | 662.8054 | 662.8054 | 662.8054 | 662.8054 | 662.8054 | 662.8054 | 662.8054 | 662.8054 | 662.8054 | 662.8054 | 662.8054 | 662.8054 | 662.8054
60% |  | 595.1039 | 1629.6346 | 1599.0683 | 1597.338 | 1714.9251 | 1843.9992 | 2109.2202 | 2299.836 | 2403.0496 | 2515.7473 | 2619.0702 | 2806.1076 | 3038.3525 | 3021.6775 | 3021.6775 | 3021.6775 | 3021.6775 | 3021.6775 | 3021.6775 | 3021.6775 | 3021.6775 | 3021.6775 | 3021.6775 | 3021.6775 | 3021.6775 | 3021.6775 | 3021.6775 | 3021.6775 | 3021.6775 |  |  | 374.3821 | 567.3189 | 555.6511 | 556.3494 | 576.0627 | 628.2504 | 663.0943 | 697.2588 | 737.234 | 774.2116 | 810.1631 | 814.1711 | 856.15 | 824.1351 | 824.1351 | 824.1351 | 824.1351 | 824.1351 | 824.1351 | 824.1351 | 824.1351 | 824.1351 | 824.1351 | 824.1351 | 824.1351 | 824.1351 | 824.1351 | 824.1351 | 824.1351
55% |  |  | 438.6107 | 413.2466 | 411.832 | 513.1119 | 636.1403 | 924.2646 | 1139.8067 | 1256.5173 | 1383.9522 | 1500.7863 | 1712.2821 | 1974.8972 | 1956.0416 | 1956.0416 | 1956.0416 | 1956.0416 | 1956.0416 | 1956.0416 | 1956.0416 | 1956.0416 | 1956.0416 | 1956.0416 | 1956.0416 | 1956.0416 | 1956.0416 | 1956.0416 | 1956.0416 | 1956.0416 |  |  | 239.8473 | 609.6211 | 587.1995 | 588.5414 | 626.4237 | 726.7105 | 793.6685 | 859.321 | 936.1395 | 1007.1978 | 1076.2842 | 1083.9862 | 1164.6552 | 1103.1336 | 1103.1336 | 1103.1336 | 1103.1336 | 1103.1336 | 1103.1336 | 1103.1336 | 1103.1336 | 1103.1336 | 1103.1336 | 1103.1336 | 1103.1336 | 1103.1336 | 1103.1336 | 1103.1336 | 1103.1336
50% | [7 empty] | 3.4281 | 36.6085 | 68.9695 | 115.5831 | 168.4762 | 288.3744 | 479.2895 | 464.0651 | 464.0651 | 464.0651 | 464.0651 | 464.0651 | 464.0651 | 464.0651 | 464.0651 | 464.0651 | 464.0651 | 464.0651 | 464.0651 | 464.0651 | 464.0651 | 464.0651 | 464.0651 |  |  |  | 218.9141 | 191.3668 | 192.9659 | 240.7061 | 390.8095 | 509.6193 | 640.0757 | 807.8717 | 965.5671 | 1118.8862 | 1135.9788 | 1315.0026 | 1178.4715 | 1178.4715 | 1178.4715 | 1178.4715 | 1178.4715 | 1178.4715 | 1178.4715 | 1178.4715 | 1178.4715 | 1178.4715 | 1178.4715 | 1178.4715 | 1178.4715 | 1178.4715 | 1178.4715 | 1178.4715
45% | [40 empty] | 3.1349 | 28.4196 | 76.7087 | 83.5101 | 171.461 | 101.6343 | 101.6343 | 101.6343 | 101.6343 | 101.6343 | 101.6343 | 101.6343 | 101.6343 | 101.6343 | 101.6343 | 101.6343 | 101.6343 | 101.6343 | 101.6343 | 101.6343 | 101.6343
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 114.5088 | 3629.6513 | 6389.8148 | 6295.8662 | 6290.5691 | 6655.6913 | 7068.3364 | 7954.9925 | 8631.4193 | 9012.0818 | 9439.0017 | 9840.5652 | 10591.6343 | 11566.2763 | 11494.7808 | 11494.7808 | 11494.7808 | 11494.7808 | 11494.7808 | 11494.7808 | 11494.7808 | 11494.7808 | 11494.7808 | 11494.7808 | 11494.7808 | 11494.7808 | 11494.7808 | 11494.7808 | 11494.7808 | 11494.7808 | E @ R (MWh) | 463.1998 | 2592.9116 | 3797.0519 | 3709.8635 | 3715.0322 | 3863.5385 | 4280.4031 | 4577.3201 | 4882.411 | 5257.6779 | 5629.6718 | 6015.0485 | 6059.4299 | 6540.9827 | 6170.9785 | 6170.9785 | 6170.9785 | 6170.9785 | 6170.9785 | 6170.9785 | 6170.9785 | 6170.9785 | 6170.9785 | 6170.9785 | 6170.9785 | 6170.9785 | 6170.9785 | 6170.9785 | 6170.9785 | 6170.9785
Option 7 Summer POE50 W E @ R (MWh) N 1 | 80.1561 | 2540.7559 | 4472.8704 | 4407.1063 | 4403.3984 | 4658.9839 | 4947.8355 | 5568.4947 | 6041.9935 | 6308.4573 | 6607.3012 | 6888.3957 | 7414.144 | 8096.3934 | 8046.3465 | 8046.3465 | 8046.3465 | 8046.3465 | 8046.3465 | 8046.3465 | 8046.3465 | 8046.3465 | 8046.3465 | 8046.3465 | 8046.3465 | 8046.3465 | 8046.3465 | 8046.3465 | 8046.3465 | 8046.3465 | Option 7 Summer POE10 W E @ R (MWh) N 1 | 138.9599 | 777.8735 | 1139.1156 | 1112.959 | 1114.5097 | 1159.0616 | 1284.1209 | 1373.196 | 1464.7233 | 1577.3034 | 1688.9015 | 1804.5146 | 1817.829 | 1962.2948 | 1851.2936 | 1851.2936 | 1851.2936 | 1851.2936 | 1851.2936 | 1851.2936 | 1851.2936 | 1851.2936 | 1851.2936 | 1851.2936 | 1851.2936 | 1851.2936 | 1851.2936 | 1851.2936 | 1851.2936 | 1851.2936
Option 8 -
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | 0.52857 | 28.8388 | 36.1886 | 37.4366 | 38.4052 | 40.0833 | 43.9094 | 46.4652 | 49.7088 | 51.3892 | 52.8635 | 50.1223 | 53.3207 | 58.3526 | 54.5225 | 54.5225 | 54.5225 | 54.5225 | 54.5225 | 54.5225 | 54.5225 | 54.5225 | 54.5225 | 54.5225 | 54.5225 | 54.5225 | 54.5225 | 54.5225 | 54.5225 | 54.5225 |  | 5.6789 | 33.6321 | 41.2692 | 42.4458 | 43.1872 | 44.8288 | 48.7149 | 50.8303 | 54.8724 | 67.1726 | 57.0171 | 55.026 | 57.6982 | 63.5502 | 59.5781 | 59.5781 | 59.5781 | 59.5781 | 59.5781 | 59.5781 | 59.5781 | 59.5781 | 59.5781 | 59.5781 | 59.5781 | 59.5781 | 59.5781 | 59.5781 | 59.5781 | 59.5781
98% | 0.020606 | 33.3788 | 42.11 | 43.5925 | 44.7431 | 46.7365 | 51.2818 | 54.3179 | 58.1711 | 60.1673 | 61.9187 | 58.6624 | 62.4618 | 68.4394 | 63.8895 | 63.8895 | 63.8895 | 63.8895 | 63.8895 | 63.8895 | 63.8895 | 63.8895 | 63.8895 | 63.8895 | 63.8895 | 63.8895 | 63.8895 | 63.8895 | 63.8895 | 63.8895 |  | 5.8662 | 39.073 | 48.1454 | 49.5431 | 50.4239 | 52.374 | 56.9904 | 59.5034 | 64.3051 | 78.9171 | 66.8529 | 64.4876 | 67.6621 | 74.6138 | 69.8952 | 69.8952 | 69.8952 | 69.8952 | 69.8952 | 69.8952 | 69.8952 | 69.8952 | 69.8952 | 69.8952 | 69.8952 | 69.8952 | 69.8952 | 69.8952 | 69.8952 | 69.8952
97% |  | 64.3022 | 81.5872 | 84.5221 | 86.7999 | 90.7464 | 99.7446 | 105.7551 | 113.3832 | 117.3353 | 120.8025 | 114.3559 | 121.8775 | 133.7114 | 124.704 | 124.704 | 124.704 | 124.704 | 124.704 | 124.704 | 124.704 | 124.704 | 124.704 | 124.704 | 124.704 | 124.704 | 124.704 | 124.704 | 124.704 | 124.704 |  | 9.8356 | 75.5748 | 93.5354 | 96.3025 | 98.0462 | 101.9067 | 111.0458 | 116.0208 | 125.5268 | 154.454 | 130.5706 | 125.888 | 132.1725 | 145.9349 | 136.5934 | 136.5934 | 136.5934 | 136.5934 | 136.5934 | 136.5934 | 136.5934 | 136.5934 | 136.5934 | 136.5934 | 136.5934 | 136.5934 | 136.5934 | 136.5934 | 136.5934 | 136.5934
95% |  | 181.8568 | 232.914 | 241.5832 | 248.3116 | 259.9688 | 286.5483 | 304.3023 | 326.8347 | 338.5083 | 348.75 | 329.7076 | 351.9256 | 386.8808 | 360.2743 | 360.2743 | 360.2743 | 360.2743 | 360.2743 | 360.2743 | 360.2743 | 360.2743 | 360.2743 | 360.2743 | 360.2743 | 360.2743 | 360.2743 | 360.2743 | 360.2743 | 360.2743 |  | 20.9709 | 215.1544 | 268.2072 | 276.3809 | 281.5313 | 292.9348 | 319.9304 | 334.6257 | 362.705 | 448.1513 | 377.6034 | 363.7719 | 382.3354 | 422.9874 | 395.3941 | 395.3941 | 395.3941 | 395.3941 | 395.3941 | 395.3941 | 395.3941 | 395.3941 | 395.3941 | 395.3941 | 395.3941 | 395.3941 | 395.3941 | 395.3941 | 395.3941 | 395.3941
90% |  | 893.0903 | 1174.5993 | 1222.3975 | 1259.4956 | 1323.7687 | 1470.3172 | 1568.2056 | 1692.4401 | 1756.8041 | 1813.2726 | 1708.2805 | 1830.7812 | 2023.5105 | 1876.813 | 1876.813 | 1876.813 | 1876.813 | 1876.813 | 1876.813 | 1876.813 | 1876.813 | 1876.813 | 1876.813 | 1876.813 | 1876.813 | 1876.813 | 1876.813 | 1876.813 | 1876.813 |  | 23.4784 | 1076.68 | 1369.1919 | 1414.2584 | 1442.6557 | 1505.5298 | 1654.3725 | 1735.397 | 1890.2148 | 2361.3315 | 1972.3588 | 1896.0974 | 1998.4489 | 2222.5876 | 2070.4492 | 2070.4492 | 2070.4492 | 2070.4492 | 2070.4492 | 2070.4492 | 2070.4492 | 2070.4492 | 2070.4492 | 2070.4492 | 2070.4492 | 2070.4492 | 2070.4492 | 2070.4492 | 2070.4492 | 2070.4492
85% |  | 1762.1242 | 2449.8304 | 2566.598 | 2657.2259 | 2814.2407 | 3172.248 | 3411.3825 | 3714.8785 | 3872.1151 | 4010.0635 | 3753.5754 | 4052.8358 | 4523.6597 | 4165.2882 | 4165.2882 | 4165.2882 | 4165.2882 | 4165.2882 | 4165.2882 | 4165.2882 | 4165.2882 | 4165.2882 | 4165.2882 | 4165.2882 | 4165.2882 | 4165.2882 | 4165.2882 | 4165.2882 | 4165.2882 |  |  | 2210.6207 | 2925.2063 | 3035.3005 | 3104.6731 | 3258.27 | 3621.8821 | 3819.8191 | 4198.028 | 5348.9323 | 4398.6997 | 4212.3987 | 4462.436 | 5009.9908 | 4638.3275 | 4638.3275 | 4638.3275 | 4638.3275 | 4638.3275 | 4638.3275 | 4638.3275 | 4638.3275 | 4638.3275 | 4638.3275 | 4638.3275 | 4638.3275 | 4638.3275 | 4638.3275 | 4638.3275 | 4638.3275
80% |  | 2007.5732 | 3076.4726 | 3257.9641 | 3398.8267 | 3642.8742 | 4199.3237 | 4571.0097 | 5042.7323 | 5287.1246 | 5501.5374 | 5102.8788 | 5568.0182 | 6299.8181 | 5742.8026 | 5742.8026 | 5742.8026 | 5742.8026 | 5742.8026 | 5742.8026 | 5742.8026 | 5742.8026 | 5742.8026 | 5742.8026 | 5742.8026 | 5742.8026 | 5742.8026 | 5742.8026 | 5742.8026 | 5742.8026 |  |  | 2704.6698 | 3815.3477 | 3986.4666 | 4094.2922 | 4333.0273 | 4898.1884 | 5205.8411 | 5793.6899 | 7582.5364 | 6105.5932 | 5816.0263 | 6204.6584 | 7055.7208 | 6478.0459 | 6478.0459 | 6478.0459 | 6478.0459 | 6478.0459 | 6478.0459 | 6478.0459 | 6478.0459 | 6478.0459 | 6478.0459 | 6478.0459 | 6478.0459 | 6478.0459 | 6478.0459 | 6478.0459 | 6478.0459
75% |  | 1303.991 | 2483.2854 | 2683.5211 | 2838.9319 | 3108.1844 | 3722.1035 | 4132.1769 | 4652.6186 | 4922.2514 | 5158.8086 | 4718.9769 | 5232.1555 | 6039.5351 | 5424.9915 | 5424.9915 | 5424.9915 | 5424.9915 | 5424.9915 | 5424.9915 | 5424.9915 | 5424.9915 | 5424.9915 | 5424.9915 | 5424.9915 | 5424.9915 | 5424.9915 | 5424.9915 | 5424.9915 | 5424.9915 |  |  | 2073.0831 | 3298.4708 | 3487.2627 | 3606.2244 | 3869.6159 | 4493.1463 | 4832.5731 | 5481.1343 | 7454.7312 | 5825.2508 | 5505.7776 | 5934.5473 | 6873.5067 | 6236.17 | 6236.17 | 6236.17 | 6236.17 | 6236.17 | 6236.17 | 6236.17 | 6236.17 | 6236.17 | 6236.17 | 6236.17 | 6236.17 | 6236.17 | 6236.17 | 6236.17 | 6236.17
70% |  | 329.0664 | 1554.418 | 1769.5601 | 1936.5403 | 2225.837 | 2885.4588 | 3326.0597 | 3885.2453 | 4174.9507 | 4429.1182 | 3956.5436 | 4507.9253 | 5375.4095 | 4715.1168 | 4715.1168 | 4715.1168 | 4715.1168 | 4715.1168 | 4715.1168 | 4715.1168 | 4715.1168 | 4715.1168 | 4715.1168 | 4715.1168 | 4715.1168 | 4715.1168 | 4715.1168 | 4715.1168 | 4715.1168 |  |  | 1113.6786 | 2430.2892 | 2633.1355 | 2760.9532 | 3043.9527 | 3713.9012 | 4078.5963 | 4775.4391 | 6895.9587 | 5145.173 | 4801.917 | 5262.606 | 6271.4654 | 5586.6828 | 5586.6828 | 5586.6828 | 5586.6828 | 5586.6828 | 5586.6828 | 5586.6828 | 5586.6828 | 5586.6828 | 5586.6828 | 5586.6828 | 5586.6828 | 5586.6828 | 5586.6828 | 5586.6828 | 5586.6828
65% |  |  | 357.6004 | 534.3679 | 694.2568 | 998.0683 | 1693.1832 | 2157.4921 | 2746.7664 | 3052.0604 | 3319.9042 | 2821.9012 | 3402.9518 | 4317.1138 | 3621.2919 | 3621.2919 | 3621.2919 | 3621.2919 | 3621.2919 | 3621.2919 | 3621.2919 | 3621.2919 | 3621.2919 | 3621.2919 | 3621.2919 | 3621.2919 | 3621.2919 | 3621.2919 | 3621.2919 | 3621.2919 |  |  | 102.8871 | 1213.5217 | 1427.2829 | 1561.9782 | 1860.2054 | 2566.2027 | 2950.5214 | 3684.8601 | 5919.4811 | 4074.4887 | 3712.7627 | 4198.2405 | 5261.3849 | 4539.7553 | 4539.7553 | 4539.7553 | 4539.7553 | 4539.7553 | 4539.7553 | 4539.7553 | 4539.7553 | 4539.7553 | 4539.7553 | 4539.7553 | 4539.7553 | 4539.7553 | 4539.7553 | 4539.7553 | 4539.7553
60% | [5 empty] | 22.0281 | 310.8024 | 678.0302 | 1303.0236 | 1639.1146 | 1933.9776 | 1385.7376 | 2025.4028 | 3031.7826 | 2265.7684 | 2265.7684 | 2265.7684 | 2265.7684 | 2265.7684 | 2265.7684 | 2265.7684 | 2265.7684 | 2265.7684 | 2265.7684 | 2265.7684 | 2265.7684 | 2265.7684 | 2265.7684 | 2265.7684 | 2265.7684 |  |  |  | 76.5442 | 162.0907 | 231.6582 | 427.4699 | 1104.2451 | 1527.3326 | 2335.7491 | 4795.7916 | 2764.6822 | 2366.4664 | 2900.9178 | 4071.3088 | 3276.8835 | 3276.8835 | 3276.8835 | 3276.8835 | 3276.8835 | 3276.8835 | 3276.8835 | 3276.8835 | 3276.8835 | 3276.8835 | 3276.8835 | 3276.8835 | 3276.8835 | 3276.8835 | 3276.8835 | 3276.8835
55% | [8 empty] | 31.8697 | 126.1441 | 258.2709 | 49.3804 | 308.3505 | 1129.5587 | 460.0863 | 460.0863 | 460.0863 | 460.0863 | 460.0863 | 460.0863 | 460.0863 | 460.0863 | 460.0863 | 460.0863 | 460.0863 | 460.0863 | 460.0863 | 460.0863 | 460.0863 | 460.0863 | [7 empty] | 5.3153 | 88.0196 | 509.6432 | 3087.7799 | 864.8984 | 532.1518 | 995.8136 | 2281.8383 | 1398.09 | 1398.09 | 1398.09 | 1398.09 | 1398.09 | 1398.09 | 1398.09 | 1398.09 | 1398.09 | 1398.09 | 1398.09 | 1398.09 | 1398.09 | 1398.09 | 1398.09 | 1398.09
50% | [40 empty] | 614.3108 |  |  |  | 194.216 | 2.9117 | 2.9117 | 2.9117 | 2.9117 | 2.9117 | 2.9117 | 2.9117 | 2.9117 | 2.9117 | 2.9117 | 2.9117 | 2.9117 | 2.9117 | 2.9117 | 2.9117 | 2.9117
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0.54918 | 6604.2219 | 11489.0059 | 12441.5431 | 13203.537 | 14572.5364 | 17934.9211 | 20355.1972 | 23617.6722 | 25397.9652 | 27009.2878 | 24050.1225 | 27518.0067 | 33387.7721 | 28875.549 | 28875.549 | 28875.549 | 28875.549 | 28875.549 | 28875.549 | 28875.549 | 28875.549 | 28875.549 | 28875.549 | 28875.549 | 28875.549 | 28875.549 | 28875.549 | 28875.549 | 28875.549 | E @ R (MWh) | 65.83 | 9645.0538 | 15579.729 | 16610.4697 | 17275.6237 | 18790.1152 | 22593.9352 | 24799.0804 | 29276.1679 | 44809.5484 | 31783.1886 | 29452.7715 | 32597.5368 | 39949.1057 | 34888.7767 | 34888.7767 | 34888.7767 | 34888.7767 | 34888.7767 | 34888.7767 | 34888.7767 | 34888.7767 | 34888.7767 | 34888.7767 | 34888.7767 | 34888.7767 | 34888.7767 | 34888.7767 | 34888.7767 | 34888.7767
Option 8 Winter POE50 W E @ R (MWh) N 1 | 0.38442 | 4622.9553 | 8042.3041 | 8709.0802 | 9242.4759 | 10200.7755 | 12554.4447 | 14248.638 | 16532.3706 | 17778.5756 | 18906.5014 | 16835.0857 | 19262.6047 | 23371.4405 | 20212.8843 | 20212.8843 | 20212.8843 | 20212.8843 | 20212.8843 | 20212.8843 | 20212.8843 | 20212.8843 | 20212.8843 | 20212.8843 | 20212.8843 | 20212.8843 | 20212.8843 | 20212.8843 | 20212.8843 | 20212.8843 | Option 8 Winter POE10 W E @ R (MWh) N 1 | 19.749 | 2893.5161 | 4673.9187 | 4983.1409 | 5182.6871 | 5637.0346 | 6778.1806 | 7439.7241 | 8782.8504 | 13442.8645 | 9534.9566 | 8835.8314 | 9779.261 | 11984.7317 | 10466.633 | 10466.633 | 10466.633 | 10466.633 | 10466.633 | 10466.633 | 10466.633 | 10466.633 | 10466.633 | 10466.633 | 10466.633 | 10466.633 | 10466.633 | 10466.633 | 10466.633 | 10466.633
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 26.6023 | 54.4041 | 61.674 | 61.2344 | 61.2607 | 62.0035 | 63.97 | 65.2829 | 66.5702 | 68.0765 | 69.4698 | 70.8245 | 70.9755 | 72.5573 | 71.351 | 71.351 | 71.351 | 71.351 | 71.351 | 71.351 | 71.351 | 71.351 | 71.351 | 71.351 | 71.351 | 71.351 | 71.351 | 71.351 | 71.351 | 71.351
98% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 12.8254 | 26.5866 | 30.185 | 29.9674 | 29.9804 | 30.3481 | 31.3215 | 31.9713 | 32.6085 | 33.3541 | 34.0438 | 34.7143 | 34.789 | 35.572 | 34.9749 | 34.9749 | 34.9749 | 34.9749 | 34.9749 | 34.9749 | 34.9749 | 34.9749 | 34.9749 | 34.9749 | 34.9749 | 34.9749 | 34.9749 | 34.9749 | 34.9749 | 34.9749
97% | 3.7957 | 10.5928 | 12.4418 | 12.3872 | 12.3841 | 12.5942 | 12.8249 | 13.2988 | 13.6394 | 13.8238 | 14.0252 | 14.2099 | 14.5441 | 14.9591 | 14.9293 | 14.9293 | 14.9293 | 14.9293 | 14.9293 | 14.9293 | 14.9293 | 14.9293 | 14.9293 | 14.9293 | 14.9293 | 14.9293 | 14.9293 | 14.9293 | 14.9293 | 14.9293 |  | 24.6994 | 51.9423 | 59.0661 | 58.6353 | 58.6611 | 59.389 | 61.3159 | 62.6024 | 63.8639 | 65.3399 | 66.7052 | 68.0327 | 68.1807 | 69.7307 | 68.5486 | 68.5486 | 68.5486 | 68.5486 | 68.5486 | 68.5486 | 68.5486 | 68.5486 | 68.5486 | 68.5486 | 68.5486 | 68.5486 | 68.5486 | 68.5486 | 68.5486 | 68.5486
95% | 17.3774 | 50.84 | 59.9429 | 59.674 | 59.6588 | 60.6932 | 61.8287 | 64.162 | 65.8388 | 66.7468 | 67.7383 | 68.6472 | 70.2926 | 72.3358 | 72.1891 | 72.1891 | 72.1891 | 72.1891 | 72.1891 | 72.1891 | 72.1891 | 72.1891 | 72.1891 | 72.1891 | 72.1891 | 72.1891 | 72.1891 | 72.1891 | 72.1891 | 72.1891 |  | 34.9082 | 75.1439 | 85.6653 | 85.029 | 85.0671 | 86.1421 | 88.988 | 90.8882 | 92.7512 | 94.9312 | 96.9477 | 98.9082 | 99.1268 | 101.416 | 99.6701 | 99.6701 | 99.6701 | 99.6701 | 99.6701 | 99.6701 | 99.6701 | 99.6701 | 99.6701 | 99.6701 | 99.6701 | 99.6701 | 99.6701 | 99.6701 | 99.6701 | 99.6701
90% | 24.555 | 82.5918 | 98.3797 | 97.9133 | 97.8869 | 99.681 | 101.6504 | 105.6971 | 108.6054 | 110.1802 | 111.8997 | 113.4762 | 116.33 | 119.8735 | 119.6191 | 119.6191 | 119.6191 | 119.6191 | 119.6191 | 119.6191 | 119.6191 | 119.6191 | 119.6191 | 119.6191 | 119.6191 | 119.6191 | 119.6191 | 119.6191 | 119.6191 | 119.6191 |  | 134.6084 | 309.068 | 354.6878 | 351.9289 | 352.0941 | 356.7553 | 369.095 | 377.3339 | 385.4121 | 394.8642 | 403.6075 | 412.1082 | 413.0559 | 422.9818 | 415.4119 | 415.4119 | 415.4119 | 415.4119 | 415.4119 | 415.4119 | 415.4119 | 415.4119 | 415.4119 | 415.4119 | 415.4119 | 415.4119 | 415.4119 | 415.4119 | 415.4119 | 415.4119
85% | 44.847 | 209.5458 | 254.3493 | 253.0259 | 252.9509 | 258.0423 | 263.6311 | 275.1149 | 283.3684 | 287.8374 | 292.7171 | 297.1909 | 305.2894 | 315.3454 | 314.6234 | 314.6234 | 314.6234 | 314.6234 | 314.6234 | 314.6234 | 314.6234 | 314.6234 | 314.6234 | 314.6234 | 314.6234 | 314.6234 | 314.6234 | 314.6234 | 314.6234 | 314.6234 |  | 102.4961 | 267.5254 | 310.6793 | 308.0696 | 308.2258 | 312.635 | 324.3078 | 332.1012 | 339.7428 | 348.684 | 356.9547 | 364.9959 | 365.8924 | 375.2817 | 368.121 | 368.121 | 368.121 | 368.121 | 368.121 | 368.121 | 368.121 | 368.121 | 368.121 | 368.121 | 368.121 | 368.121 | 368.121 | 368.121 | 368.121 | 368.121
80% | 23.7465 | 253.802 | 316.3847 | 314.536 | 314.4314 | 321.5432 | 329.3497 | 345.3906 | 356.9192 | 363.1617 | 369.9778 | 376.2269 | 387.5391 | 401.5855 | 400.577 | 400.577 | 400.577 | 400.577 | 400.577 | 400.577 | 400.577 | 400.577 | 400.577 | 400.577 | 400.577 | 400.577 | 400.577 | 400.577 | 400.577 | 400.577 |  | 52.1361 | 167.3947 | 197.5339 | 195.7112 | 195.8203 | 198.8998 | 207.0522 | 212.4953 | 217.8322 | 224.0769 | 229.8532 | 235.4693 | 236.0954 | 242.6531 | 237.6519 | 237.6519 | 237.6519 | 237.6519 | 237.6519 | 237.6519 | 237.6519 | 237.6519 | 237.6519 | 237.6519 | 237.6519 | 237.6519 | 237.6519 | 237.6519 | 237.6519 | 237.6519
75% | 0.18716 | 547.1351 | 710.2768 | 705.4576 | 705.1848 | 723.724 | 744.0742 | 785.8898 | 815.9429 | 832.2159 | 849.9842 | 866.2744 | 895.7633 | 932.3798 | 929.7508 | 929.7508 | 929.7508 | 929.7508 | 929.7508 | 929.7508 | 929.7508 | 929.7508 | 929.7508 | 929.7508 | 929.7508 | 929.7508 | 929.7508 | 929.7508 | 929.7508 | 929.7508 |  | 53.8635 | 259.5826 | 313.3765 | 310.1233 | 310.3181 | 315.8145 | 330.3652 | 340.0803 | 349.6059 | 360.7517 | 371.0616 | 381.0855 | 382.203 | 393.9074 | 384.9811 | 384.9811 | 384.9811 | 384.9811 | 384.9811 | 384.9811 | 384.9811 | 384.9811 | 384.9811 | 384.9811 | 384.9811 | 384.9811 | 384.9811 | 384.9811 | 384.9811 | 384.9811
70% |  | 720.2141 | 1002.0732 | 993.7472 | 993.2758 | 1025.3059 | 1060.4649 | 1132.7095 | 1184.6321 | 1212.7469 | 1243.4451 | 1271.5896 | 1322.5375 | 1385.7996 | 1381.2574 | 1381.2574 | 1381.2574 | 1381.2574 | 1381.2574 | 1381.2574 | 1381.2574 | 1381.2574 | 1381.2574 | 1381.2574 | 1381.2574 | 1381.2574 | 1381.2574 | 1381.2574 | 1381.2574 | 1381.2574 |  | 21.0605 | 391.6455 | 489.6437 | 483.7172 | 484.0719 | 494.0849 | 520.5925 | 538.2908 | 555.6439 | 575.9484 | 594.7305 | 612.9912 | 615.027 | 636.3493 | 620.088 | 620.088 | 620.088 | 620.088 | 620.088 | 620.088 | 620.088 | 620.088 | 620.088 | 620.088 | 620.088 | 620.088 | 620.088 | 620.088 | 620.088 | 620.088
65% |  | 1159.8257 | 1867.7211 | 1846.81 | 1845.6263 | 1926.0704 | 2014.373 | 2195.817 | 2326.2218 | 2396.8327 | 2473.9318 | 2544.6175 | 2672.5742 | 2831.4585 | 2820.0507 | 2820.0507 | 2820.0507 | 2820.0507 | 2820.0507 | 2820.0507 | 2820.0507 | 2820.0507 | 2820.0507 | 2820.0507 | 2820.0507 | 2820.0507 | 2820.0507 | 2820.0507 | 2820.0507 | 2820.0507 |  |  | 375.3893 | 498.6861 | 491.2298 | 491.676 | 504.2739 | 537.6246 | 559.8917 | 581.7247 | 607.2709 | 630.9016 | 653.8765 | 656.4378 | 683.2646 | 662.8054 | 662.8054 | 662.8054 | 662.8054 | 662.8054 | 662.8054 | 662.8054 | 662.8054 | 662.8054 | 662.8054 | 662.8054 | 662.8054 | 662.8054 | 662.8054 | 662.8054 | 662.8054
60% |  | 595.1039 | 1629.6346 | 1599.0683 | 1597.338 | 1714.9251 | 1843.9992 | 2109.2202 | 2299.836 | 2403.0496 | 2515.7473 | 2619.0702 | 2806.1076 | 3038.3525 | 3021.6775 | 3021.6775 | 3021.6775 | 3021.6775 | 3021.6775 | 3021.6775 | 3021.6775 | 3021.6775 | 3021.6775 | 3021.6775 | 3021.6775 | 3021.6775 | 3021.6775 | 3021.6775 | 3021.6775 | 3021.6775 |  |  | 374.3821 | 567.3189 | 555.6511 | 556.3494 | 576.0627 | 628.2504 | 663.0943 | 697.2588 | 737.234 | 774.2116 | 810.1631 | 814.1711 | 856.15 | 824.1351 | 824.1351 | 824.1351 | 824.1351 | 824.1351 | 824.1351 | 824.1351 | 824.1351 | 824.1351 | 824.1351 | 824.1351 | 824.1351 | 824.1351 | 824.1351 | 824.1351 | 824.1351
55% |  |  | 438.6107 | 413.2466 | 411.832 | 513.1119 | 636.1403 | 924.2646 | 1139.8067 | 1256.5173 | 1383.9522 | 1500.7863 | 1712.2821 | 1974.8972 | 1956.0416 | 1956.0416 | 1956.0416 | 1956.0416 | 1956.0416 | 1956.0416 | 1956.0416 | 1956.0416 | 1956.0416 | 1956.0416 | 1956.0416 | 1956.0416 | 1956.0416 | 1956.0416 | 1956.0416 | 1956.0416 |  |  | 239.8473 | 609.6211 | 587.1995 | 588.5414 | 626.4237 | 726.7105 | 793.6685 | 859.321 | 936.1395 | 1007.1978 | 1076.2842 | 1083.9862 | 1164.6552 | 1103.1336 | 1103.1336 | 1103.1336 | 1103.1336 | 1103.1336 | 1103.1336 | 1103.1336 | 1103.1336 | 1103.1336 | 1103.1336 | 1103.1336 | 1103.1336 | 1103.1336 | 1103.1336 | 1103.1336 | 1103.1336
50% | [7 empty] | 3.4281 | 36.6085 | 68.9695 | 115.5831 | 168.4762 | 288.3744 | 479.2895 | 464.0651 | 464.0651 | 464.0651 | 464.0651 | 464.0651 | 464.0651 | 464.0651 | 464.0651 | 464.0651 | 464.0651 | 464.0651 | 464.0651 | 464.0651 | 464.0651 | 464.0651 | 464.0651 |  |  |  | 218.9141 | 191.3668 | 192.9659 | 240.7061 | 390.8095 | 509.6193 | 640.0757 | 807.8717 | 965.5671 | 1118.8862 | 1135.9788 | 1315.0026 | 1178.4715 | 1178.4715 | 1178.4715 | 1178.4715 | 1178.4715 | 1178.4715 | 1178.4715 | 1178.4715 | 1178.4715 | 1178.4715 | 1178.4715 | 1178.4715 | 1178.4715 | 1178.4715 | 1178.4715 | 1178.4715
45% | [40 empty] | 3.1349 | 28.4196 | 76.7087 | 83.5101 | 171.461 | 101.6343 | 101.6343 | 101.6343 | 101.6343 | 101.6343 | 101.6343 | 101.6343 | 101.6343 | 101.6343 | 101.6343 | 101.6343 | 101.6343 | 101.6343 | 101.6343 | 101.6343 | 101.6343
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 114.5088 | 3629.6513 | 6389.8148 | 6295.8662 | 6290.5691 | 6655.6913 | 7068.3364 | 7954.9925 | 8631.4193 | 9012.0818 | 9439.0017 | 9840.5652 | 10591.6343 | 11566.2763 | 11494.7808 | 11494.7808 | 11494.7808 | 11494.7808 | 11494.7808 | 11494.7808 | 11494.7808 | 11494.7808 | 11494.7808 | 11494.7808 | 11494.7808 | 11494.7808 | 11494.7808 | 11494.7808 | 11494.7808 | 11494.7808 | E @ R (MWh) | 463.1998 | 2592.9116 | 3797.0519 | 3709.8635 | 3715.0322 | 3863.5385 | 4280.4031 | 4577.3201 | 4882.411 | 5257.6779 | 5629.6718 | 6015.0485 | 6059.4299 | 6540.9827 | 6170.9785 | 6170.9785 | 6170.9785 | 6170.9785 | 6170.9785 | 6170.9785 | 6170.9785 | 6170.9785 | 6170.9785 | 6170.9785 | 6170.9785 | 6170.9785 | 6170.9785 | 6170.9785 | 6170.9785 | 6170.9785
Option 8 Summer POE50 W E @ R (MWh) N 1 | 80.1561 | 2540.7559 | 4472.8704 | 4407.1063 | 4403.3984 | 4658.9839 | 4947.8355 | 5568.4947 | 6041.9935 | 6308.4573 | 6607.3012 | 6888.3957 | 7414.144 | 8096.3934 | 8046.3465 | 8046.3465 | 8046.3465 | 8046.3465 | 8046.3465 | 8046.3465 | 8046.3465 | 8046.3465 | 8046.3465 | 8046.3465 | 8046.3465 | 8046.3465 | 8046.3465 | 8046.3465 | 8046.3465 | 8046.3465 | Option 8 Summer POE10 W E @ R (MWh) N 1 | 138.9599 | 777.8735 | 1139.1156 | 1112.959 | 1114.5097 | 1159.0616 | 1284.1209 | 1373.196 | 1464.7233 | 1577.3034 | 1688.9015 | 1804.5146 | 1817.829 | 1962.2948 | 1851.2936 | 1851.2936 | 1851.2936 | 1851.2936 | 1851.2936 | 1851.2936 | 1851.2936 | 1851.2936 | 1851.2936 | 1851.2936 | 1851.2936 | 1851.2936 | 1851.2936 | 1851.2936 | 1851.2936 | 1851.2936

## E@R N-2
Option 1 - Do Nothing / Base Case
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | 73.4908 | 101.8011 | 109.1509 | 110.3988 | 111.3674 | 113.0455 | 116.8717 | 119.4274 | 122.671 | 124.3515 | 125.8258 | 123.0846 | 126.2829 | 131.3148 | 127.4847 | 127.4847 | 127.4847 | 127.4847 | 127.4847 | 127.4847 | 127.4847 | 127.4847 | 127.4847 | 127.4847 | 127.4847 | 127.4847 | 127.4847 | 127.4847 | 127.4847 | 127.4847 |  | 78.6411 | 106.5944 | 114.2314 | 115.4081 | 116.1495 | 117.791 | 121.6771 | 123.7926 | 127.8346 | 140.1348 | 129.9793 | 127.9882 | 130.6605 | 136.5124 | 132.5403 | 132.5403 | 132.5403 | 132.5403 | 132.5403 | 132.5403 | 132.5403 | 132.5403 | 132.5403 | 132.5403 | 132.5403 | 132.5403 | 132.5403 | 132.5403 | 132.5403 | 132.5403
98% | 87.3027 | 120.9335 | 129.6647 | 131.1472 | 132.2978 | 134.2912 | 138.8365 | 141.8726 | 145.7258 | 147.722 | 149.4734 | 146.2171 | 150.0165 | 155.9941 | 151.4442 | 151.4442 | 151.4442 | 151.4442 | 151.4442 | 151.4442 | 151.4442 | 151.4442 | 151.4442 | 151.4442 | 151.4442 | 151.4442 | 151.4442 | 151.4442 | 151.4442 | 151.4442 |  | 93.4209 | 126.6277 | 135.7001 | 137.0978 | 137.9786 | 139.9286 | 144.5451 | 147.0581 | 151.8598 | 166.4717 | 154.4076 | 152.0423 | 155.2168 | 162.1685 | 157.4499 | 157.4499 | 157.4499 | 157.4499 | 157.4499 | 157.4499 | 157.4499 | 157.4499 | 157.4499 | 157.4499 | 157.4499 | 157.4499 | 157.4499 | 157.4499 | 157.4499 | 157.4499
97% | 172.8327 | 239.4116 | 256.6966 | 259.6314 | 261.9093 | 265.8557 | 274.854 | 280.8645 | 288.4926 | 292.4446 | 295.9119 | 289.4652 | 296.9869 | 308.8207 | 299.8133 | 299.8133 | 299.8133 | 299.8133 | 299.8133 | 299.8133 | 299.8133 | 299.8133 | 299.8133 | 299.8133 | 299.8133 | 299.8133 | 299.8133 | 299.8133 | 299.8133 | 299.8133 |  | 184.945 | 250.6842 | 268.6448 | 271.4119 | 273.1556 | 277.0161 | 286.1552 | 291.1302 | 300.6362 | 329.5634 | 305.68 | 300.9974 | 307.2819 | 321.0443 | 311.7028 | 311.7028 | 311.7028 | 311.7028 | 311.7028 | 311.7028 | 311.7028 | 311.7028 | 311.7028 | 311.7028 | 311.7028 | 311.7028 | 311.7028 | 311.7028 | 311.7028 | 311.7028
95% | 510.5211 | 707.185 | 758.2422 | 766.9113 | 773.6398 | 785.297 | 811.8764 | 829.6304 | 852.1628 | 863.8365 | 874.0782 | 855.0358 | 877.2537 | 912.2089 | 885.6025 | 885.6025 | 885.6025 | 885.6025 | 885.6025 | 885.6025 | 885.6025 | 885.6025 | 885.6025 | 885.6025 | 885.6025 | 885.6025 | 885.6025 | 885.6025 | 885.6025 | 885.6025 |  | 546.299 | 740.4826 | 793.5354 | 801.7091 | 806.8595 | 818.2629 | 845.2585 | 859.9539 | 888.0332 | 973.4795 | 902.9316 | 889.1001 | 907.6635 | 948.3155 | 920.7222 | 920.7222 | 920.7222 | 920.7222 | 920.7222 | 920.7222 | 920.7222 | 920.7222 | 920.7222 | 920.7222 | 920.7222 | 920.7222 | 920.7222 | 920.7222 | 920.7222 | 920.7222
90% | 2814.8088 | 3899.1347 | 4180.6436 | 4228.4418 | 4265.5399 | 4329.8131 | 4476.3615 | 4574.25 | 4698.4845 | 4762.8484 | 4819.3169 | 4714.3248 | 4836.8255 | 5029.5548 | 4882.8573 | 4882.8573 | 4882.8573 | 4882.8573 | 4882.8573 | 4882.8573 | 4882.8573 | 4882.8573 | 4882.8573 | 4882.8573 | 4882.8573 | 4882.8573 | 4882.8573 | 4882.8573 | 4882.8573 | 4882.8573 |  | 3012.0741 | 4082.7244 | 4375.2363 | 4420.3027 | 4448.7 | 4511.5741 | 4660.4169 | 4741.4413 | 4896.2592 | 5367.3759 | 4978.4031 | 4902.1418 | 5004.4932 | 5228.6319 | 5076.4935 | 5076.4935 | 5076.4935 | 5076.4935 | 5076.4935 | 5076.4935 | 5076.4935 | 5076.4935 | 5076.4935 | 5076.4935 | 5076.4935 | 5076.4935 | 5076.4935 | 5076.4935 | 5076.4935 | 5076.4935
85% | 6876.3763 | 9525.3066 | 10213.0129 | 10329.7805 | 10420.4084 | 10577.4231 | 10935.4305 | 11174.565 | 11478.0609 | 11635.2975 | 11773.246 | 11516.7578 | 11816.0183 | 12286.8422 | 11928.4707 | 11928.4707 | 11928.4707 | 11928.4707 | 11928.4707 | 11928.4707 | 11928.4707 | 11928.4707 | 11928.4707 | 11928.4707 | 11928.4707 | 11928.4707 | 11928.4707 | 11928.4707 | 11928.4707 | 11928.4707 |  | 7358.2813 | 9973.8032 | 10688.3888 | 10798.4829 | 10867.8555 | 11021.4524 | 11385.0646 | 11583.0015 | 11961.2104 | 13112.1147 | 12161.8821 | 11975.5812 | 12225.6185 | 12773.1733 | 12401.51 | 12401.51 | 12401.51 | 12401.51 | 12401.51 | 12401.51 | 12401.51 | 12401.51 | 12401.51 | 12401.51 | 12401.51 | 12401.51 | 12401.51 | 12401.51 | 12401.51 | 12401.51
80% | 10687.9274 | 14805.1503 | 15874.0497 | 16055.5412 | 16196.4038 | 16440.4513 | 16996.9008 | 17368.5868 | 17840.3094 | 18084.7017 | 18299.1145 | 17900.4559 | 18365.5953 | 19097.3952 | 18540.3797 | 18540.3797 | 18540.3797 | 18540.3797 | 18540.3797 | 18540.3797 | 18540.3797 | 18540.3797 | 18540.3797 | 18540.3797 | 18540.3797 | 18540.3797 | 18540.3797 | 18540.3797 | 18540.3797 | 18540.3797 |  | 11436.9506 | 15502.2469 | 16612.9248 | 16784.0437 | 16891.8693 | 17130.6044 | 17695.7655 | 18003.4182 | 18591.267 | 20380.1135 | 18903.1703 | 18613.6034 | 19002.2355 | 19853.298 | 19275.623 | 19275.623 | 19275.623 | 19275.623 | 19275.623 | 19275.623 | 19275.623 | 19275.623 | 19275.623 | 19275.623 | 19275.623 | 19275.623 | 19275.623 | 19275.623 | 19275.623 | 19275.623
75% | 11791.7667 | 16334.2127 | 17513.507 | 17713.7428 | 17869.1536 | 18138.406 | 18752.3252 | 19162.3985 | 19682.8403 | 19952.4731 | 20189.0303 | 19749.1986 | 20262.3772 | 21069.7567 | 20455.2132 | 20455.2132 | 20455.2132 | 20455.2132 | 20455.2132 | 20455.2132 | 20455.2132 | 20455.2132 | 20455.2132 | 20455.2132 | 20455.2132 | 20455.2132 | 20455.2132 | 20455.2132 | 20455.2132 | 20455.2132 |  | 12618.1483 | 17103.3048 | 18328.6925 | 18517.4844 | 18636.4461 | 18899.8376 | 19523.368 | 19862.7948 | 20511.356 | 22484.9529 | 20855.4725 | 20535.9993 | 20964.769 | 21903.7284 | 21266.3917 | 21266.3917 | 21266.3917 | 21266.3917 | 21266.3917 | 21266.3917 | 21266.3917 | 21266.3917 | 21266.3917 | 21266.3917 | 21266.3917 | 21266.3917 | 21266.3917 | 21266.3917 | 21266.3917 | 21266.3917
70% | 12669.5942 | 17550.1984 | 18817.2842 | 19032.4264 | 19199.4066 | 19488.7033 | 20148.3251 | 20588.926 | 21148.1115 | 21437.817 | 21691.9844 | 21219.4098 | 21770.7916 | 22638.2758 | 21977.983 | 21977.983 | 21977.983 | 21977.983 | 21977.983 | 21977.983 | 21977.983 | 21977.983 | 21977.983 | 21977.983 | 21977.983 | 21977.983 | 21977.983 | 21977.983 | 21977.983 | 21977.983 |  | 13557.495 | 18376.5449 | 19693.1554 | 19896.0018 | 20023.8195 | 20306.8189 | 20976.7675 | 21341.4626 | 22038.3054 | 24158.8249 | 22408.0393 | 22064.7832 | 22525.4722 | 23534.3317 | 22849.549 | 22849.549 | 22849.549 | 22849.549 | 22849.549 | 22849.549 | 22849.549 | 22849.549 | 22849.549 | 22849.549 | 22849.549 | 22849.549 | 22849.549 | 22849.549 | 22849.549 | 22849.549
65% | 13351.323 | 18494.5441 | 19829.8096 | 20056.5282 | 20232.4932 | 20537.3565 | 21232.4714 | 21696.7803 | 22286.0546 | 22591.3486 | 22859.1924 | 22361.1894 | 22942.24 | 23856.402 | 23160.5801 | 23160.5801 | 23160.5801 | 23160.5801 | 23160.5801 | 23160.5801 | 23160.5801 | 23160.5801 | 23160.5801 | 23160.5801 | 23160.5801 | 23160.5801 | 23160.5801 | 23160.5801 | 23160.5801 | 23160.5801 |  | 14287.0002 | 19365.3548 | 20752.8099 | 20966.571 | 21101.2664 | 21399.4935 | 22105.4909 | 22489.8096 | 23224.1482 | 25458.7693 | 23613.7769 | 23252.0508 | 23737.5287 | 24800.6731 | 24079.0435 | 24079.0435 | 24079.0435 | 24079.0435 | 24079.0435 | 24079.0435 | 24079.0435 | 24079.0435 | 24079.0435 | 24079.0435 | 24079.0435 | 24079.0435 | 24079.0435 | 24079.0435 | 24079.0435 | 24079.0435
60% | 14698.1621 | 20360.2151 | 21830.1779 | 22079.7671 | 22273.483 | 22609.0999 | 23374.3358 | 23885.4827 | 24534.2012 | 24870.2922 | 25165.1552 | 24616.9152 | 25256.5804 | 26262.9602 | 25496.946 | 25496.946 | 25496.946 | 25496.946 | 25496.946 | 25496.946 | 25496.946 | 25496.946 | 25496.946 | 25496.946 | 25496.946 | 25496.946 | 25496.946 | 25496.946 | 25496.946 | 25496.946 |  | 15728.2275 | 21318.8704 | 22846.2875 | 23081.6122 | 23229.8952 | 23558.2066 | 24335.4227 | 24758.5102 | 25566.9267 | 28026.9692 | 25995.8598 | 25597.644 | 26132.0954 | 27302.4864 | 26508.0611 | 26508.0611 | 26508.0611 | 26508.0611 | 26508.0611 | 26508.0611 | 26508.0611 | 26508.0611 | 26508.0611 | 26508.0611 | 26508.0611 | 26508.0611 | 26508.0611 | 26508.0611 | 26508.0611 | 26508.0611
55% | 16350.7821 | 22649.4603 | 24284.7017 | 24562.354 | 24777.8508 | 25151.2035 | 26002.4804 | 26571.0991 | 27292.7577 | 27666.6379 | 27994.6544 | 27384.7719 | 28096.3592 | 29215.8935 | 28363.7508 | 28363.7508 | 28363.7508 | 28363.7508 | 28363.7508 | 28363.7508 | 28363.7508 | 28363.7508 | 28363.7508 | 28363.7508 | 28363.7508 | 28363.7508 | 28363.7508 | 28363.7508 | 28363.7508 | 28363.7508 |  | 17496.6651 | 23715.9042 | 25415.0598 | 25676.8438 | 25841.7993 | 26207.0251 | 27071.6291 | 27542.2874 | 28441.6 | 31178.2427 | 28918.7611 | 28475.7711 | 29070.3146 | 30372.3011 | 29488.5529 | 29488.5529 | 29488.5529 | 29488.5529 | 29488.5529 | 29488.5529 | 29488.5529 | 29488.5529 | 29488.5529 | 29488.5529 | 29488.5529 | 29488.5529 | 29488.5529 | 29488.5529 | 29488.5529 | 29488.5529
50% | 16573.101 | 22957.4214 | 24614.8968 | 24896.3244 | 25114.7512 | 25493.1803 | 26356.0319 | 26932.3821 | 27663.8529 | 28042.8167 | 28375.2932 | 27757.1182 | 28478.3809 | 29613.1373 | 28749.4081 | 28749.4081 | 28749.4081 | 28749.4081 | 28749.4081 | 28749.4081 | 28749.4081 | 28749.4081 | 28749.4081 | 28749.4081 | 28749.4081 | 28749.4081 | 28749.4081 | 28749.4081 | 28749.4081 | 28749.4081 |  | 17734.5645 | 24038.3655 | 25760.6242 | 26025.9676 | 26193.1661 | 26563.3577 | 27439.7177 | 27916.7755 | 28828.3158 | 31602.1683 | 29311.9648 | 28862.9515 | 29465.579 | 30785.2684 | 29889.5039 | 29889.5039 | 29889.5039 | 29889.5039 | 29889.5039 | 29889.5039 | 29889.5039 | 29889.5039 | 29889.5039 | 29889.5039 | 29889.5039 | 29889.5039 | 29889.5039 | 29889.5039 | 29889.5039 | 29889.5039
45% | 12791.4633 | 17719.0143 | 18998.2882 | 19215.4999 | 19384.0862 | 19676.1657 | 20342.1324 | 20786.9714 | 21351.5358 | 21644.0279 | 21900.6402 | 21423.5199 | 21980.2054 | 22856.034 | 22189.3899 | 22189.3899 | 22189.3899 | 22189.3899 | 22189.3899 | 22189.3899 | 22189.3899 | 22189.3899 | 22189.3899 | 22189.3899 | 22189.3899 | 22189.3899 | 22189.3899 | 22189.3899 | 22189.3899 | 22189.3899 |  | 13687.9049 | 18553.3094 | 19882.5844 | 20087.382 | 20216.4292 | 20502.1508 | 21178.5436 | 21546.7467 | 22250.2924 | 24391.2093 | 22623.5828 | 22277.025 | 22742.1454 | 23760.7091 | 23069.3395 | 23069.3395 | 23069.3395 | 23069.3395 | 23069.3395 | 23069.3395 | 23069.3395 | 23069.3395 | 23069.3395 | 23069.3395 | 23069.3395 | 23069.3395 | 23069.3395 | 23069.3395 | 23069.3395 | 23069.3395
40% | 6284.3875 | 8705.2708 | 9333.7723 | 9440.4874 | 9523.3131 | 9666.8104 | 9993.9968 | 10212.5442 | 10489.9121 | 10633.6121 | 10759.6846 | 10525.2775 | 10798.7746 | 11229.0652 | 10901.546 | 10901.546 | 10901.546 | 10901.546 | 10901.546 | 10901.546 | 10901.546 | 10901.546 | 10901.546 | 10901.546 | 10901.546 | 10901.546 | 10901.546 | 10901.546 | 10901.546 | 10901.546 |  | 6724.8052 | 9115.1562 | 9768.223 | 9868.8391 | 9932.2394 | 10072.6131 | 10404.9218 | 10585.8183 | 10931.4671 | 11983.2898 | 11114.863 | 10944.6007 | 11173.1122 | 11673.5279 | 11333.8612 | 11333.8612 | 11333.8612 | 11333.8612 | 11333.8612 | 11333.8612 | 11333.8612 | 11333.8612 | 11333.8612 | 11333.8612 | 11333.8612 | 11333.8612 | 11333.8612 | 11333.8612 | 11333.8612 | 11333.8612
35% | 2348.7515 | 3253.5419 | 3488.4405 | 3528.3246 | 3559.2802 | 3612.9114 | 3735.1954 | 3816.8761 | 3920.5407 | 3974.2477 | 4021.3665 | 3933.7583 | 4035.9762 | 4196.7946 | 4074.3863 | 4074.3863 | 4074.3863 | 4074.3863 | 4074.3863 | 4074.3863 | 4074.3863 | 4074.3863 | 4074.3863 | 4074.3863 | 4074.3863 | 4074.3863 | 4074.3863 | 4074.3863 | 4074.3863 | 4074.3863 |  | 2513.3549 | 3406.7341 | 3650.8138 | 3688.4184 | 3712.1139 | 3764.5777 | 3888.7761 | 3956.3851 | 4085.5692 | 4478.6815 | 4154.1123 | 4090.4778 | 4175.8826 | 4362.9099 | 4235.9615 | 4235.9615 | 4235.9615 | 4235.9615 | 4235.9615 | 4235.9615 | 4235.9615 | 4235.9615 | 4235.9615 | 4235.9615 | 4235.9615 | 4235.9615 | 4235.9615 | 4235.9615 | 4235.9615 | 4235.9615
30% | 1171.4214 | 1622.6784 | 1739.8323 | 1759.7242 | 1775.163 | 1801.9112 | 1862.8993 | 1903.637 | 1955.3388 | 1982.1248 | 2005.6249 | 1961.931 | 2012.9114 | 2093.1183 | 2032.0682 | 2032.0682 | 2032.0682 | 2032.0682 | 2032.0682 | 2032.0682 | 2032.0682 | 2032.0682 | 2032.0682 | 2032.0682 | 2032.0682 | 2032.0682 | 2032.0682 | 2032.0682 | 2032.0682 | 2032.0682 |  | 1253.516 | 1699.0818 | 1820.8147 | 1839.5697 | 1851.3876 | 1877.5536 | 1939.4965 | 1973.2159 | 2037.6455 | 2233.7072 | 2071.8308 | 2040.0936 | 2082.6886 | 2175.967 | 2112.6525 | 2112.6525 | 2112.6525 | 2112.6525 | 2112.6525 | 2112.6525 | 2112.6525 | 2112.6525 | 2112.6525 | 2112.6525 | 2112.6525 | 2112.6525 | 2112.6525 | 2112.6525 | 2112.6525 | 2112.6525
25% | 690.592 | 956.6232 | 1025.6893 | 1037.4162 | 1046.5179 | 1062.2869 | 1098.2414 | 1122.2576 | 1152.7376 | 1168.5288 | 1182.3829 | 1156.6239 | 1186.6785 | 1233.9632 | 1197.9721 | 1197.9721 | 1197.9721 | 1197.9721 | 1197.9721 | 1197.9721 | 1197.9721 | 1197.9721 | 1197.9721 | 1197.9721 | 1197.9721 | 1197.9721 | 1197.9721 | 1197.9721 | 1197.9721 | 1197.9721 |  | 738.9896 | 1001.6655 | 1073.4311 | 1084.4878 | 1091.4549 | 1106.8806 | 1143.398 | 1163.2767 | 1201.2601 | 1316.845 | 1221.4135 | 1202.7034 | 1227.8145 | 1282.8053 | 1245.4793 | 1245.4793 | 1245.4793 | 1245.4793 | 1245.4793 | 1245.4793 | 1245.4793 | 1245.4793 | 1245.4793 | 1245.4793 | 1245.4793 | 1245.4793 | 1245.4793 | 1245.4793 | 1245.4793 | 1245.4793
20% | 348.989 | 483.4272 | 518.3296 | 524.2558 | 528.8553 | 536.8241 | 554.9937 | 567.1302 | 582.5332 | 590.5132 | 597.5144 | 584.4971 | 599.6851 | 623.5803 | 605.3923 | 605.3923 | 605.3923 | 605.3923 | 605.3923 | 605.3923 | 605.3923 | 605.3923 | 605.3923 | 605.3923 | 605.3923 | 605.3923 | 605.3923 | 605.3923 | 605.3923 | 605.3923 |  | 373.4466 | 506.1893 | 542.4558 | 548.0433 | 551.5641 | 559.3594 | 577.8134 | 587.8591 | 607.0539 | 665.4645 | 617.2384 | 607.7833 | 620.4731 | 648.2626 | 629.3999 | 629.3999 | 629.3999 | 629.3999 | 629.3999 | 629.3999 | 629.3999 | 629.3999 | 629.3999 | 629.3999 | 629.3999 | 629.3999 | 629.3999 | 629.3999 | 629.3999 | 629.3999
15% | 142.1807 | 196.9518 | 211.1713 | 213.5857 | 215.4596 | 218.7061 | 226.1085 | 231.053 | 237.3283 | 240.5795 | 243.4318 | 238.1285 | 244.3162 | 254.0512 | 246.6413 | 246.6413 | 246.6413 | 246.6413 | 246.6413 | 246.6413 | 246.6413 | 246.6413 | 246.6413 | 246.6413 | 246.6413 | 246.6413 | 246.6413 | 246.6413 | 246.6413 | 246.6413 |  | 152.1449 | 206.2253 | 221.0005 | 223.2769 | 224.7113 | 227.8872 | 235.4055 | 239.4982 | 247.3183 | 271.1152 | 251.4675 | 247.6154 | 252.7853 | 264.107 | 256.4222 | 256.4222 | 256.4222 | 256.4222 | 256.4222 | 256.4222 | 256.4222 | 256.4222 | 256.4222 | 256.4222 | 256.4222 | 256.4222 | 256.4222 | 256.4222 | 256.4222 | 256.4222
10% | 57.2416 | 79.2923 | 85.017 | 85.989 | 86.7435 | 88.0505 | 91.0307 | 93.0214 | 95.5478 | 96.8567 | 98.005 | 95.8699 | 98.3611 | 102.2804 | 99.2972 | 99.2972 | 99.2972 | 99.2972 | 99.2972 | 99.2972 | 99.2972 | 99.2972 | 99.2972 | 99.2972 | 99.2972 | 99.2972 | 99.2972 | 99.2972 | 99.2972 | 99.2972 |  | 61.2531 | 83.0258 | 88.9742 | 89.8907 | 90.4682 | 91.7468 | 94.7736 | 96.4213 | 99.5697 | 109.1503 | 101.2402 | 99.6893 | 101.7707 | 106.3288 | 103.2349 | 103.2349 | 103.2349 | 103.2349 | 103.2349 | 103.2349 | 103.2349 | 103.2349 | 103.2349 | 103.2349 | 103.2349 | 103.2349 | 103.2349 | 103.2349 | 103.2349 | 103.2349
5% | 48.7477 | 67.5263 | 72.4016 | 73.2294 | 73.8719 | 74.985 | 77.5229 | 79.2182 | 81.3697 | 82.4844 | 83.4623 | 81.644 | 83.7655 | 87.1033 | 84.5627 | 84.5627 | 84.5627 | 84.5627 | 84.5627 | 84.5627 | 84.5627 | 84.5627 | 84.5627 | 84.5627 | 84.5627 | 84.5627 | 84.5627 | 84.5627 | 84.5627 | 84.5627 |  | 52.164 | 70.7058 | 75.7716 | 76.5521 | 77.0439 | 78.1327 | 80.7104 | 82.1137 | 84.7948 | 92.9538 | 86.2174 | 84.8967 | 86.6693 | 90.551 | 87.9162 | 87.9162 | 87.9162 | 87.9162 | 87.9162 | 87.9162 | 87.9162 | 87.9162 | 87.9162 | 87.9162 | 87.9162 | 87.9162 | 87.9162 | 87.9162 | 87.9162 | 87.9162
9.992e-14% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E @ R (MWh) | 130541.7636 | 180829.3011 | 193884.7798 | 196101.5072 | 197821.9953 | 200802.7777 | 207599.2223 | 212138.9744 | 217900.5692 | 220885.5628 | 223504.3892 | 218635.1944 | 224316.3823 | 233254.5468 | 226451.1896 | 226451.1896 | 226451.1896 | 226451.1896 | 226451.1896 | 226451.1896 | 226451.1896 | 226451.1896 | 226451.1896 | 226451.1896 | 226451.1896 | 226451.1896 | 226451.1896 | 226451.1896 | 226451.1896 | 226451.1896 | E @ R (MWh) | 139690.2921 | 189343.6009 | 202909.3599 | 204999.3971 | 206316.373 | 209232.2711 | 216135.1177 | 219892.7708 | 227072.7236 | 248921.5973 | 230882.2942 | 227345.5395 | 232092.2705 | 242487.1014 | 235431.4111 | 235431.4111 | 235431.4111 | 235431.4111 | 235431.4111 | 235431.4111 | 235431.4111 | 235431.4111 | 235431.4111 | 235431.4111 | 235431.4111 | 235431.4111 | 235431.4111 | 235431.4111 | 235431.4111 | 235431.4111
Option 1 Winter POE50 W E @ R (MWh) N 2 | 91379.2345 | 126580.5108 | 135719.3459 | 137271.0551 | 138475.3967 | 140561.9444 | 145319.4556 | 148497.2821 | 152530.3985 | 154619.8939 | 156453.0725 | 153044.6361 | 157021.4676 | 163278.1828 | 158515.8327 | 158515.8327 | 158515.8327 | 158515.8327 | 158515.8327 | 158515.8327 | 158515.8327 | 158515.8327 | 158515.8327 | 158515.8327 | 158515.8327 | 158515.8327 | 158515.8327 | 158515.8327 | 158515.8327 | 158515.8327 | Option 1 Winter POE10 W E @ R (MWh) N 2 | 41907.0876 | 56803.0803 | 60872.808 | 61499.8191 | 61894.9119 | 62769.6813 | 64840.5353 | 65967.8312 | 68121.8171 | 74676.4792 | 69264.6882 | 68203.6618 | 69627.6812 | 72746.1304 | 70629.4233 | 70629.4233 | 70629.4233 | 70629.4233 | 70629.4233 | 70629.4233 | 70629.4233 | 70629.4233 | 70629.4233 | 70629.4233 | 70629.4233 | 70629.4233 | 70629.4233 | 70629.4233 | 70629.4233 | 70629.4233
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 94.6719 | 122.4737 | 129.7436 | 129.304 | 129.3303 | 130.0731 | 132.0395 | 133.3525 | 134.6398 | 136.1461 | 137.5394 | 138.8941 | 139.0451 | 140.6269 | 139.4206 | 139.4206 | 139.4206 | 139.4206 | 139.4206 | 139.4206 | 139.4206 | 139.4206 | 139.4206 | 139.4206 | 139.4206 | 139.4206 | 139.4206 | 139.4206 | 139.4206 | 139.4206
98% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 46.8602 | 60.6214 | 64.2198 | 64.0022 | 64.0152 | 64.3829 | 65.3562 | 66.0061 | 66.6433 | 67.3889 | 68.0786 | 68.7491 | 68.8238 | 69.6068 | 69.0097 | 69.0097 | 69.0097 | 69.0097 | 69.0097 | 69.0097 | 69.0097 | 69.0097 | 69.0097 | 69.0097 | 69.0097 | 69.0097 | 69.0097 | 69.0097 | 69.0097 | 69.0097
97% | 20.8131 | 27.6102 | 29.4592 | 29.4046 | 29.4015 | 29.6116 | 29.8423 | 30.3162 | 30.6568 | 30.8412 | 31.0426 | 31.2273 | 31.5615 | 31.9765 | 31.9467 | 31.9467 | 31.9467 | 31.9467 | 31.9467 | 31.9467 | 31.9467 | 31.9467 | 31.9467 | 31.9467 | 31.9467 | 31.9467 | 31.9467 | 31.9467 | 31.9467 | 31.9467 |  | 92.7689 | 120.0119 | 127.1357 | 126.7049 | 126.7307 | 127.4585 | 129.3855 | 130.672 | 131.9335 | 133.4095 | 134.7748 | 136.1022 | 136.2502 | 137.8002 | 136.6181 | 136.6181 | 136.6181 | 136.6181 | 136.6181 | 136.6181 | 136.6181 | 136.6181 | 136.6181 | 136.6181 | 136.6181 | 136.6181 | 136.6181 | 136.6181 | 136.6181 | 136.6181
95% | 102.4643 | 135.9269 | 145.0299 | 144.761 | 144.7458 | 145.7802 | 146.9157 | 149.2489 | 150.9258 | 151.8338 | 152.8252 | 153.7342 | 155.3796 | 157.4227 | 157.276 | 157.276 | 157.276 | 157.276 | 157.276 | 157.276 | 157.276 | 157.276 | 157.276 | 157.276 | 157.276 | 157.276 | 157.276 | 157.276 | 157.276 | 157.276 |  | 137.0126 | 177.2483 | 187.7696 | 187.1334 | 187.1714 | 188.2465 | 191.0924 | 192.9925 | 194.8556 | 197.0355 | 199.052 | 201.0125 | 201.2311 | 203.5203 | 201.7745 | 201.7745 | 201.7745 | 201.7745 | 201.7745 | 201.7745 | 201.7745 | 201.7745 | 201.7745 | 201.7745 | 201.7745 | 201.7745 | 201.7745 | 201.7745 | 201.7745 | 201.7745
90% | 177.7116 | 235.7483 | 251.5362 | 251.0698 | 251.0434 | 252.8375 | 254.8069 | 258.8536 | 261.762 | 263.3368 | 265.0563 | 266.6327 | 269.4865 | 273.03 | 272.7756 | 272.7756 | 272.7756 | 272.7756 | 272.7756 | 272.7756 | 272.7756 | 272.7756 | 272.7756 | 272.7756 | 272.7756 | 272.7756 | 272.7756 | 272.7756 | 272.7756 | 272.7756 |  | 594.078 | 768.5376 | 814.1574 | 811.3985 | 811.5637 | 816.2249 | 828.5646 | 836.8035 | 844.8817 | 854.3338 | 863.0771 | 871.5778 | 872.5255 | 882.4514 | 874.8815 | 874.8815 | 874.8815 | 874.8815 | 874.8815 | 874.8815 | 874.8815 | 874.8815 | 874.8815 | 874.8815 | 874.8815 | 874.8815 | 874.8815 | 874.8815 | 874.8815 | 874.8815
85% | 504.3166 | 669.0154 | 713.8189 | 712.4955 | 712.4205 | 717.5119 | 723.1007 | 734.5845 | 742.838 | 747.307 | 752.1867 | 756.6605 | 764.759 | 774.815 | 774.093 | 774.093 | 774.093 | 774.093 | 774.093 | 774.093 | 774.093 | 774.093 | 774.093 | 774.093 | 774.093 | 774.093 | 774.093 | 774.093 | 774.093 | 774.093 |  | 561.9657 | 726.995 | 770.1489 | 767.5392 | 767.6954 | 772.1046 | 783.7774 | 791.5709 | 799.2124 | 808.1536 | 816.4243 | 824.4655 | 825.362 | 834.7513 | 827.5906 | 827.5906 | 827.5906 | 827.5906 | 827.5906 | 827.5906 | 827.5906 | 827.5906 | 827.5906 | 827.5906 | 827.5906 | 827.5906 | 827.5906 | 827.5906 | 827.5906 | 827.5906
80% | 704.4422 | 934.4978 | 997.0804 | 995.2318 | 995.1271 | 1002.2389 | 1010.0454 | 1026.0863 | 1037.6149 | 1043.8574 | 1050.6735 | 1056.9226 | 1068.2348 | 1082.2812 | 1081.2727 | 1081.2727 | 1081.2727 | 1081.2727 | 1081.2727 | 1081.2727 | 1081.2727 | 1081.2727 | 1081.2727 | 1081.2727 | 1081.2727 | 1081.2727 | 1081.2727 | 1081.2727 | 1081.2727 | 1081.2727 |  | 392.484 | 507.7425 | 537.8818 | 536.0591 | 536.1682 | 539.2477 | 547.4001 | 552.8431 | 558.1801 | 564.4247 | 570.2011 | 575.8172 | 576.4433 | 583.0009 | 577.9998 | 577.9998 | 577.9998 | 577.9998 | 577.9998 | 577.9998 | 577.9998 | 577.9998 | 577.9998 | 577.9998 | 577.9998 | 577.9998 | 577.9998 | 577.9998 | 577.9998 | 577.9998
75% | 1836.3528 | 2436.0657 | 2599.2074 | 2594.3882 | 2594.1154 | 2612.6546 | 2633.0048 | 2674.8204 | 2704.8735 | 2721.1465 | 2738.9148 | 2755.205 | 2784.6939 | 2821.3104 | 2818.6814 | 2818.6814 | 2818.6814 | 2818.6814 | 2818.6814 | 2818.6814 | 2818.6814 | 2818.6814 | 2818.6814 | 2818.6814 | 2818.6814 | 2818.6814 | 2818.6814 | 2818.6814 | 2818.6814 | 2818.6814 |  | 700.5244 | 906.2435 | 960.0375 | 956.7843 | 956.979 | 962.4754 | 977.0262 | 986.7412 | 996.2669 | 1007.4126 | 1017.7226 | 1027.7464 | 1028.8639 | 1040.5683 | 1031.6421 | 1031.6421 | 1031.6421 | 1031.6421 | 1031.6421 | 1031.6421 | 1031.6421 | 1031.6421 | 1031.6421 | 1031.6421 | 1031.6421 | 1031.6421 | 1031.6421 | 1031.6421 | 1031.6421 | 1031.6421
70% | 3172.6584 | 4208.7797 | 4490.6388 | 4482.3127 | 4481.8414 | 4513.8714 | 4549.0304 | 4621.275 | 4673.1976 | 4701.3124 | 4732.0106 | 4760.1551 | 4811.103 | 4874.3651 | 4869.823 | 4869.823 | 4869.823 | 4869.823 | 4869.823 | 4869.823 | 4869.823 | 4869.823 | 4869.823 | 4869.823 | 4869.823 | 4869.823 | 4869.823 | 4869.823 | 4869.823 | 4869.823 |  | 1276.1675 | 1650.9325 | 1748.9307 | 1743.0043 | 1743.359 | 1753.372 | 1779.8796 | 1797.5778 | 1814.931 | 1835.2355 | 1854.0175 | 1872.2783 | 1874.3141 | 1895.6364 | 1879.3751 | 1879.3751 | 1879.3751 | 1879.3751 | 1879.3751 | 1879.3751 | 1879.3751 | 1879.3751 | 1879.3751 | 1879.3751 | 1879.3751 | 1879.3751 | 1879.3751 | 1879.3751 | 1879.3751 | 1879.3751
65% | 7968.2023 | 10570.444 | 11278.3393 | 11257.4282 | 11256.2445 | 11336.6886 | 11424.9912 | 11606.4352 | 11736.84 | 11807.4509 | 11884.55 | 11955.2357 | 12083.1924 | 12242.0767 | 12230.6689 | 12230.6689 | 12230.6689 | 12230.6689 | 12230.6689 | 12230.6689 | 12230.6689 | 12230.6689 | 12230.6689 | 12230.6689 | 12230.6689 | 12230.6689 | 12230.6689 | 12230.6689 | 12230.6689 | 12230.6689 |  | 1605.6162 | 2077.1285 | 2200.4254 | 2192.969 | 2193.4153 | 2206.0132 | 2239.3639 | 2261.631 | 2283.4639 | 2309.0102 | 2332.6409 | 2355.6158 | 2358.1771 | 2385.0038 | 2364.5446 | 2364.5446 | 2364.5446 | 2364.5446 | 2364.5446 | 2364.5446 | 2364.5446 | 2364.5446 | 2364.5446 | 2364.5446 | 2364.5446 | 2364.5446 | 2364.5446 | 2364.5446 | 2364.5446 | 2364.5446
60% | 11647.312 | 15451.0709 | 16485.8185 | 16455.2522 | 16453.5219 | 16571.109 | 16700.1831 | 16965.4041 | 17156.0199 | 17259.2335 | 17371.9312 | 17475.2541 | 17662.2915 | 17894.5364 | 17877.8614 | 17877.8614 | 17877.8614 | 17877.8614 | 17877.8614 | 17877.8614 | 17877.8614 | 17877.8614 | 17877.8614 | 17877.8614 | 17877.8614 | 17877.8614 | 17877.8614 | 17877.8614 | 17877.8614 | 17877.8614 |  | 2512.492 | 3250.3215 | 3443.2583 | 3431.5904 | 3432.2888 | 3452.0021 | 3504.1898 | 3539.0337 | 3573.1982 | 3613.1734 | 3650.151 | 3686.1024 | 3690.1105 | 3732.0893 | 3700.0745 | 3700.0745 | 3700.0745 | 3700.0745 | 3700.0745 | 3700.0745 | 3700.0745 | 3700.0745 | 3700.0745 | 3700.0745 | 3700.0745 | 3700.0745 | 3700.0745 | 3700.0745 | 3700.0745 | 3700.0745
55% | 13170.4015 | 17471.5683 | 18641.6273 | 18607.0639 | 18605.1073 | 18738.071 | 18884.0238 | 19183.9271 | 19399.4692 | 19516.1798 | 19643.6146 | 19760.4488 | 19971.9446 | 20234.5597 | 20215.7041 | 20215.7041 | 20215.7041 | 20215.7041 | 20215.7041 | 20215.7041 | 20215.7041 | 20215.7041 | 20215.7041 | 20215.7041 | 20215.7041 | 20215.7041 | 20215.7041 | 20215.7041 | 20215.7041 | 20215.7041 |  | 4828.1473 | 6246.0024 | 6616.7608 | 6594.3391 | 6595.6811 | 6633.5633 | 6733.8501 | 6800.8082 | 6866.4607 | 6943.2792 | 7014.3375 | 7083.4238 | 7091.1259 | 7171.7949 | 7110.2733 | 7110.2733 | 7110.2733 | 7110.2733 | 7110.2733 | 7110.2733 | 7110.2733 | 7110.2733 | 7110.2733 | 7110.2733 | 7110.2733 | 7110.2733 | 7110.2733 | 7110.2733 | 7110.2733 | 7110.2733
50% | 16911.4168 | 22434.3178 | 23936.7286 | 23892.3477 | 23889.8353 | 24060.567 | 24247.9772 | 24633.0672 | 24909.8334 | 25059.6953 | 25223.3277 | 25373.3483 | 25644.9189 | 25982.129 | 25957.9175 | 25957.9175 | 25957.9175 | 25957.9175 | 25957.9175 | 25957.9175 | 25957.9175 | 25957.9175 | 25957.9175 | 25957.9175 | 25957.9175 | 25957.9175 | 25957.9175 | 25957.9175 | 25957.9175 | 25957.9175 |  | 10714.812 | 13861.3711 | 14684.1724 | 14634.4134 | 14637.3915 | 14721.4613 | 14944.0217 | 15092.6176 | 15238.3161 | 15408.7947 | 15566.4901 | 15719.8092 | 15736.9019 | 15915.9256 | 15779.3945 | 15779.3945 | 15779.3945 | 15779.3945 | 15779.3945 | 15779.3945 | 15779.3945 | 15779.3945 | 15779.3945 | 15779.3945 | 15779.3945 | 15779.3945 | 15779.3945 | 15779.3945 | 15779.3945 | 15779.3945
45% | 22520.2713 | 29874.9022 | 31875.6039 | 31816.5035 | 31813.1579 | 32040.5146 | 32290.0814 | 32802.8907 | 33171.4494 | 33371.0147 | 33588.9175 | 33788.694 | 34150.3339 | 34599.3834 | 34567.1419 | 34567.1419 | 34567.1419 | 34567.1419 | 34567.1419 | 34567.1419 | 34567.1419 | 34567.1419 | 34567.1419 | 34567.1419 | 34567.1419 | 34567.1419 | 34567.1419 | 34567.1419 | 34567.1419 | 34567.1419 |  | 16236.3476 | 21004.3853 | 22251.1909 | 22175.7903 | 22180.3031 | 22307.6955 | 22644.9453 | 22870.1153 | 23090.8949 | 23349.2243 | 23588.1829 | 23820.5101 | 23846.4109 | 24117.6889 | 23910.8008 | 23910.8008 | 23910.8008 | 23910.8008 | 23910.8008 | 23910.8008 | 23910.8008 | 23910.8008 | 23910.8008 | 23910.8008 | 23910.8008 | 23910.8008 | 23910.8008 | 23910.8008 | 23910.8008 | 23910.8008
40% | 15794.9825 | 20953.2804 | 22356.5072 | 22315.0562 | 22312.7097 | 22472.1702 | 22647.2082 | 23006.8759 | 23265.371 | 23405.3395 | 23558.1694 | 23698.2861 | 23951.9286 | 24266.8772 | 24244.2641 | 24244.2641 | 24244.2641 | 24244.2641 | 24244.2641 | 24244.2641 | 24244.2641 | 24244.2641 | 24244.2641 | 24244.2641 | 24244.2641 | 24244.2641 | 24244.2641 | 24244.2641 | 24244.2641 | 24244.2641 |  | 16811.9908 | 21749.0744 | 23040.0842 | 22962.0103 | 22966.6831 | 23098.592 | 23447.7987 | 23680.9519 | 23909.559 | 24177.0472 | 24424.4778 | 24665.0419 | 24691.8611 | 24972.7569 | 24758.5339 | 24758.5339 | 24758.5339 | 24758.5339 | 24758.5339 | 24758.5339 | 24758.5339 | 24758.5339 | 24758.5339 | 24758.5339 | 24758.5339 | 24758.5339 | 24758.5339 | 24758.5339 | 24758.5339 | 24758.5339
35% | 8189.141 | 10863.5364 | 11591.06 | 11569.5691 | 11568.3525 | 11651.0272 | 11741.7782 | 11928.2532 | 12062.2738 | 12134.8425 | 12214.0795 | 12286.725 | 12418.2297 | 12581.5194 | 12569.7953 | 12569.7953 | 12569.7953 | 12569.7953 | 12569.7953 | 12569.7953 | 12569.7953 | 12569.7953 | 12569.7953 | 12569.7953 | 12569.7953 | 12569.7953 | 12569.7953 | 12569.7953 | 12569.7953 | 12569.7953 |  | 22897.8708 | 29622.1608 | 31380.5115 | 31274.1752 | 31280.5395 | 31460.199 | 31935.8172 | 32253.3711 | 32564.7331 | 32929.051 | 33266.0507 | 33593.6981 | 33630.2257 | 34012.8048 | 33721.0338 | 33721.0338 | 33721.0338 | 33721.0338 | 33721.0338 | 33721.0338 | 33721.0338 | 33721.0338 | 33721.0338 | 33721.0338 | 33721.0338 | 33721.0338 | 33721.0338 | 33721.0338 | 33721.0338 | 33721.0338
30% | 3808.7911 | 5052.6595 | 5391.0326 | 5381.0371 | 5380.4713 | 5418.9235 | 5461.132 | 5547.8621 | 5610.1954 | 5643.9473 | 5680.8006 | 5714.5882 | 5775.7514 | 5851.6979 | 5846.245 | 5846.245 | 5846.245 | 5846.245 | 5846.245 | 5846.245 | 5846.245 | 5846.245 | 5846.245 | 5846.245 | 5846.245 | 5846.245 | 5846.245 | 5846.245 | 5846.245 | 5846.245 |  | 21159.0479 | 27372.7075 | 28997.5323 | 28899.2709 | 28905.152 | 29071.1685 | 29510.6691 | 29804.1085 | 30091.8262 | 30428.4785 | 30739.887 | 31042.6535 | 31076.4072 | 31429.934 | 31160.3195 | 31160.3195 | 31160.3195 | 31160.3195 | 31160.3195 | 31160.3195 | 31160.3195 | 31160.3195 | 31160.3195 | 31160.3195 | 31160.3195 | 31160.3195 | 31160.3195 | 31160.3195 | 31160.3195 | 31160.3195
25% | 2600.5659 | 3449.8542 | 3680.8886 | 3674.0639 | 3673.6775 | 3699.9319 | 3728.7511 | 3787.9686 | 3830.5285 | 3853.5736 | 3878.7363 | 3901.8059 | 3943.5668 | 3995.4216 | 3991.6984 | 3991.6984 | 3991.6984 | 3991.6984 | 3991.6984 | 3991.6984 | 3991.6984 | 3991.6984 | 3991.6984 | 3991.6984 | 3991.6984 | 3991.6984 | 3991.6984 | 3991.6984 | 3991.6984 | 3991.6984 |  | 6103.1255 | 7895.3963 | 8364.0615 | 8335.719 | 8337.4153 | 8385.3012 | 8512.071 | 8596.7107 | 8679.7002 | 8776.8043 | 8866.6271 | 8953.9572 | 8963.6932 | 9065.6646 | 8987.8969 | 8987.8969 | 8987.8969 | 8987.8969 | 8987.8969 | 8987.8969 | 8987.8969 | 8987.8969 | 8987.8969 | 8987.8969 | 8987.8969 | 8987.8969 | 8987.8969 | 8987.8969 | 8987.8969 | 8987.8969
20% | 1575.389 | 2089.8768 | 2229.8344 | 2225.7001 | 2225.4661 | 2241.3706 | 2258.8289 | 2294.7021 | 2320.4843 | 2334.4448 | 2349.688 | 2363.6632 | 2388.9615 | 2420.3744 | 2418.119 | 2418.119 | 2418.119 | 2418.119 | 2418.119 | 2418.119 | 2418.119 | 2418.119 | 2418.119 | 2418.119 | 2418.119 | 2418.119 | 2418.119 | 2418.119 | 2418.119 | 2418.119 |  | 1637.7285 | 2118.6711 | 2244.4339 | 2236.8284 | 2237.2836 | 2250.1334 | 2284.1512 | 2306.8636 | 2329.1332 | 2355.1904 | 2379.2937 | 2402.7281 | 2405.3406 | 2432.7039 | 2411.8355 | 2411.8355 | 2411.8355 | 2411.8355 | 2411.8355 | 2411.8355 | 2411.8355 | 2411.8355 | 2411.8355 | 2411.8355 | 2411.8355 | 2411.8355 | 2411.8355 | 2411.8355 | 2411.8355 | 2411.8355
15% | 1008.6332 | 1338.0309 | 1427.6379 | 1424.9909 | 1424.8411 | 1435.0239 | 1446.2014 | 1469.169 | 1485.676 | 1494.614 | 1504.3734 | 1513.321 | 1529.518 | 1549.63 | 1548.1859 | 1548.1859 | 1548.1859 | 1548.1859 | 1548.1859 | 1548.1859 | 1548.1859 | 1548.1859 | 1548.1859 | 1548.1859 | 1548.1859 | 1548.1859 | 1548.1859 | 1548.1859 | 1548.1859 | 1548.1859 |  | 903.3078 | 1168.5771 | 1237.943 | 1233.7481 | 1233.9992 | 1241.0867 | 1259.8495 | 1272.3769 | 1284.6599 | 1299.032 | 1312.3265 | 1325.252 | 1326.693 | 1341.7855 | 1330.2753 | 1330.2753 | 1330.2753 | 1330.2753 | 1330.2753 | 1330.2753 | 1330.2753 | 1330.2753 | 1330.2753 | 1330.2753 | 1330.2753 | 1330.2753 | 1330.2753 | 1330.2753 | 1330.2753 | 1330.2753
10% | 675.0905 | 895.5604 | 955.5354 | 953.7638 | 953.6635 | 960.4789 | 967.9602 | 983.3327 | 994.381 | 1000.3634 | 1006.8954 | 1012.8841 | 1023.725 | 1037.1862 | 1036.2197 | 1036.2197 | 1036.2197 | 1036.2197 | 1036.2197 | 1036.2197 | 1036.2197 | 1036.2197 | 1036.2197 | 1036.2197 | 1036.2197 | 1036.2197 | 1036.2197 | 1036.2197 | 1036.2197 | 1036.2197 |  | 211.1088 | 273.1039 | 289.3152 | 288.3348 | 288.3935 | 290.0499 | 294.4349 | 297.3626 | 300.2332 | 303.5921 | 306.6991 | 309.7199 | 310.0566 | 313.5838 | 310.8938 | 310.8938 | 310.8938 | 310.8938 | 310.8938 | 310.8938 | 310.8938 | 310.8938 | 310.8938 | 310.8938 | 310.8938 | 310.8938 | 310.8938 | 310.8938 | 310.8938 | 310.8938
5% | 480.3015 | 637.1576 | 679.8276 | 678.5671 | 678.4957 | 683.3447 | 688.6673 | 699.6043 | 707.4647 | 711.721 | 716.3683 | 720.629 | 728.3419 | 737.919 | 737.2314 | 737.2314 | 737.2314 | 737.2314 | 737.2314 | 737.2314 | 737.2314 | 737.2314 | 737.2314 | 737.2314 | 737.2314 | 737.2314 | 737.2314 | 737.2314 | 737.2314 | 737.2314 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9.992e-14% | 42.1598 | 55.9283 | 59.6738 | 59.5631 | 59.5568 | 59.9825 | 60.4497 | 61.4097 | 62.0997 | 62.4733 | 62.8812 | 63.2552 | 63.9322 | 64.7729 | 64.7125 | 64.7125 | 64.7125 | 64.7125 | 64.7125 | 64.7125 | 64.7125 | 64.7125 | 64.7125 | 64.7125 | 64.7125 | 64.7125 | 64.7125 | 64.7125 | 64.7125 | 64.7125 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E @ R (MWh) | 112911.4176 | 149785.8315 | 159816.886 | 159520.5704 | 159503.7964 | 160643.7099 | 161894.98 | 164466.0868 | 166313.955 | 167314.5287 | 168407.043 | 169408.6762 | 171221.8548 | 173473.2847 | 173311.6334 | 173311.6334 | 173311.6334 | 173311.6334 | 173311.6334 | 173311.6334 | 173311.6334 | 173311.6334 | 173311.6334 | 173311.6334 | 173311.6334 | 173311.6334 | 173311.6334 | 173311.6334 | 173311.6334 | 173311.6334 | E @ R (MWh) | 109518.1284 | 141679.7064 | 150089.7144 | 149581.1188 | 149611.5589 | 150470.8515 | 152745.6837 | 154264.5107 | 155753.7228 | 157496.2176 | 159108.0516 | 160675.1553 | 160849.8627 | 162679.6988 | 161284.1885 | 161284.1885 | 161284.1885 | 161284.1885 | 161284.1885 | 161284.1885 | 161284.1885 | 161284.1885 | 161284.1885 | 161284.1885 | 161284.1885 | 161284.1885 | 161284.1885 | 161284.1885 | 161284.1885 | 161284.1885
Option 1 Summer POE50 W E @ R (MWh) N 2 | 79037.9923 | 104850.082 | 111871.8202 | 111664.3993 | 111652.6574 | 112450.5969 | 113326.486 | 115126.2607 | 116419.7685 | 117120.1701 | 117884.9301 | 118586.0733 | 119855.2983 | 121431.2993 | 121318.1434 | 121318.1434 | 121318.1434 | 121318.1434 | 121318.1434 | 121318.1434 | 121318.1434 | 121318.1434 | 121318.1434 | 121318.1434 | 121318.1434 | 121318.1434 | 121318.1434 | 121318.1434 | 121318.1434 | 121318.1434 | Option 1 Summer POE10 W E @ R (MWh) N 2 | 32855.4385 | 42503.9119 | 45026.9143 | 44874.3356 | 44883.4677 | 45141.2555 | 45823.7051 | 46279.3532 | 46726.1168 | 47248.8653 | 47732.4155 | 48202.5466 | 48254.9588 | 48803.9096 | 48385.2566 | 48385.2566 | 48385.2566 | 48385.2566 | 48385.2566 | 48385.2566 | 48385.2566 | 48385.2566 | 48385.2566 | 48385.2566 | 48385.2566 | 48385.2566 | 48385.2566 | 48385.2566 | 48385.2566 | 48385.2566
Option 2 - 1B New PHS ZSS + Three new feeders
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | 73.4908 | 101.8011 | 109.1509 | 81.8133 | 82.7819 | 84.46 | 88.2861 | 90.8419 | 94.0855 | 95.7659 | 97.2402 | 94.499 | 97.6974 | 102.7293 | 98.8992 | 98.8992 | 98.8992 | 98.8992 | 98.8992 | 98.8992 | 98.8992 | 98.8992 | 98.8992 | 98.8992 | 98.8992 | 98.8992 | 98.8992 | 98.8992 | 98.8992 | 98.8992 |  | 78.6411 | 106.5944 | 114.2314 | 86.8225 | 87.5639 | 89.2055 | 93.0916 | 95.207 | 99.2491 | 111.5493 | 101.3938 | 99.4027 | 102.0749 | 107.9269 | 103.9548 | 103.9548 | 103.9548 | 103.9548 | 103.9548 | 103.9548 | 103.9548 | 103.9548 | 103.9548 | 103.9548 | 103.9548 | 103.9548 | 103.9548 | 103.9548 | 103.9548 | 103.9548
98% | 87.3027 | 120.9335 | 129.6647 | 97.1893 | 98.3399 | 100.3333 | 104.8786 | 107.9147 | 111.7679 | 113.7641 | 115.5155 | 112.2591 | 116.0586 | 122.0362 | 117.4863 | 117.4863 | 117.4863 | 117.4863 | 117.4863 | 117.4863 | 117.4863 | 117.4863 | 117.4863 | 117.4863 | 117.4863 | 117.4863 | 117.4863 | 117.4863 | 117.4863 | 117.4863 |  | 93.4209 | 126.6277 | 135.7001 | 103.1399 | 104.0207 | 105.9707 | 110.5872 | 113.1002 | 117.9019 | 132.5138 | 120.4497 | 118.0844 | 121.2589 | 128.2106 | 123.492 | 123.492 | 123.492 | 123.492 | 123.492 | 123.492 | 123.492 | 123.492 | 123.492 | 123.492 | 123.492 | 123.492 | 123.492 | 123.492 | 123.492 | 123.492
97% | 172.8327 | 239.4116 | 256.6966 | 192.4051 | 194.683 | 198.6294 | 207.6277 | 213.6382 | 221.2663 | 225.2183 | 228.6856 | 222.2389 | 229.7606 | 241.5944 | 232.587 | 232.587 | 232.587 | 232.587 | 232.587 | 232.587 | 232.587 | 232.587 | 232.587 | 232.587 | 232.587 | 232.587 | 232.587 | 232.587 | 232.587 | 232.587 |  | 184.945 | 250.6842 | 268.6448 | 204.1856 | 205.9292 | 209.7898 | 218.9289 | 223.9039 | 233.4099 | 262.337 | 238.4537 | 233.7711 | 240.0556 | 253.818 | 244.4765 | 244.4765 | 244.4765 | 244.4765 | 244.4765 | 244.4765 | 244.4765 | 244.4765 | 244.4765 | 244.4765 | 244.4765 | 244.4765 | 244.4765 | 244.4765 | 244.4765 | 244.4765
95% | 510.5211 | 707.185 | 758.2422 | 568.3351 | 575.0636 | 586.7208 | 613.3003 | 631.0543 | 653.5866 | 665.2603 | 675.502 | 656.4596 | 678.6775 | 713.6328 | 687.0263 | 687.0263 | 687.0263 | 687.0263 | 687.0263 | 687.0263 | 687.0263 | 687.0263 | 687.0263 | 687.0263 | 687.0263 | 687.0263 | 687.0263 | 687.0263 | 687.0263 | 687.0263 |  | 546.299 | 740.4826 | 793.5354 | 603.1329 | 608.2833 | 619.6868 | 646.6823 | 661.3777 | 689.457 | 774.9033 | 704.3554 | 690.5239 | 709.0874 | 749.7393 | 722.146 | 722.146 | 722.146 | 722.146 | 722.146 | 722.146 | 722.146 | 722.146 | 722.146 | 722.146 | 722.146 | 722.146 | 722.146 | 722.146 | 722.146 | 722.146
90% | 2814.8088 | 3899.1347 | 4180.6436 | 3133.5723 | 3170.6704 | 3234.9435 | 3381.492 | 3479.3805 | 3603.6149 | 3667.9789 | 3724.4474 | 3619.4553 | 3741.956 | 3934.6853 | 3787.9878 | 3787.9878 | 3787.9878 | 3787.9878 | 3787.9878 | 3787.9878 | 3787.9878 | 3787.9878 | 3787.9878 | 3787.9878 | 3787.9878 | 3787.9878 | 3787.9878 | 3787.9878 | 3787.9878 | 3787.9878 |  | 3012.0741 | 4082.7244 | 4375.2363 | 3325.4332 | 3353.8305 | 3416.7046 | 3565.5474 | 3646.5718 | 3801.3897 | 4272.5064 | 3883.5336 | 3807.2723 | 3909.6237 | 4133.7624 | 3981.624 | 3981.624 | 3981.624 | 3981.624 | 3981.624 | 3981.624 | 3981.624 | 3981.624 | 3981.624 | 3981.624 | 3981.624 | 3981.624 | 3981.624 | 3981.624 | 3981.624 | 3981.624
85% | 6876.3763 | 9525.3066 | 10213.0129 | 7655.0927 | 7745.7206 | 7902.7353 | 8260.7427 | 8499.8772 | 8803.3732 | 8960.6097 | 9098.5582 | 8842.07 | 9141.3305 | 9612.1544 | 9253.7829 | 9253.7829 | 9253.7829 | 9253.7829 | 9253.7829 | 9253.7829 | 9253.7829 | 9253.7829 | 9253.7829 | 9253.7829 | 9253.7829 | 9253.7829 | 9253.7829 | 9253.7829 | 9253.7829 | 9253.7829 |  | 7358.2813 | 9973.8032 | 10688.3888 | 8123.7951 | 8193.1677 | 8346.7647 | 8710.3768 | 8908.3137 | 9286.5226 | 10437.427 | 9487.1944 | 9300.8934 | 9550.9307 | 10098.4855 | 9726.8222 | 9726.8222 | 9726.8222 | 9726.8222 | 9726.8222 | 9726.8222 | 9726.8222 | 9726.8222 | 9726.8222 | 9726.8222 | 9726.8222 | 9726.8222 | 9726.8222 | 9726.8222 | 9726.8222 | 9726.8222
80% | 10687.9274 | 14805.1503 | 15874.0497 | 11898.2835 | 12039.1461 | 12283.1935 | 12839.6431 | 13211.3291 | 13683.0517 | 13927.4439 | 14141.8568 | 13743.1981 | 14208.3376 | 14940.1375 | 14383.122 | 14383.122 | 14383.122 | 14383.122 | 14383.122 | 14383.122 | 14383.122 | 14383.122 | 14383.122 | 14383.122 | 14383.122 | 14383.122 | 14383.122 | 14383.122 | 14383.122 | 14383.122 |  | 11436.9506 | 15502.2469 | 16612.9248 | 12626.786 | 12734.6116 | 12973.3467 | 13538.5078 | 13846.1605 | 14434.0092 | 16222.8557 | 14745.9126 | 14456.3457 | 14844.9777 | 15696.0402 | 15118.3653 | 15118.3653 | 15118.3653 | 15118.3653 | 15118.3653 | 15118.3653 | 15118.3653 | 15118.3653 | 15118.3653 | 15118.3653 | 15118.3653 | 15118.3653 | 15118.3653 | 15118.3653 | 15118.3653 | 15118.3653
75% | 11791.7667 | 16334.2127 | 17513.507 | 13127.1273 | 13282.5381 | 13551.7905 | 14165.7097 | 14575.783 | 15096.2248 | 15365.8576 | 15602.4148 | 15162.5831 | 15675.7617 | 16483.1412 | 15868.5977 | 15868.5977 | 15868.5977 | 15868.5977 | 15868.5977 | 15868.5977 | 15868.5977 | 15868.5977 | 15868.5977 | 15868.5977 | 15868.5977 | 15868.5977 | 15868.5977 | 15868.5977 | 15868.5977 | 15868.5977 |  | 12618.1483 | 17103.3048 | 18328.6925 | 13930.8689 | 14049.8306 | 14313.2221 | 14936.7525 | 15276.1793 | 15924.7405 | 17898.3374 | 16268.8569 | 15949.3838 | 16378.1535 | 17317.1129 | 16679.7762 | 16679.7762 | 16679.7762 | 16679.7762 | 16679.7762 | 16679.7762 | 16679.7762 | 16679.7762 | 16679.7762 | 16679.7762 | 16679.7762 | 16679.7762 | 16679.7762 | 16679.7762 | 16679.7762 | 16679.7762
70% | 12669.5942 | 17550.1984 | 18817.2842 | 14104.3644 | 14271.3446 | 14560.6413 | 15220.2631 | 15660.864 | 16220.0496 | 16509.755 | 16763.9225 | 16291.3479 | 16842.7296 | 17710.2138 | 17049.9211 | 17049.9211 | 17049.9211 | 17049.9211 | 17049.9211 | 17049.9211 | 17049.9211 | 17049.9211 | 17049.9211 | 17049.9211 | 17049.9211 | 17049.9211 | 17049.9211 | 17049.9211 | 17049.9211 | 17049.9211 |  | 13557.495 | 18376.5449 | 19693.1554 | 14967.9398 | 15095.7575 | 15378.757 | 16048.7055 | 16413.4006 | 17110.2434 | 19230.763 | 17479.9773 | 17136.7213 | 17597.4103 | 18606.2697 | 17921.4871 | 17921.4871 | 17921.4871 | 17921.4871 | 17921.4871 | 17921.4871 | 17921.4871 | 17921.4871 | 17921.4871 | 17921.4871 | 17921.4871 | 17921.4871 | 17921.4871 | 17921.4871 | 17921.4871 | 17921.4871
65% | 13351.323 | 18494.5441 | 19829.8096 | 14863.2958 | 15039.2609 | 15344.1241 | 16039.239 | 16503.5479 | 17092.8222 | 17398.1162 | 17665.96 | 17167.957 | 17749.0076 | 18663.1696 | 17967.3477 | 17967.3477 | 17967.3477 | 17967.3477 | 17967.3477 | 17967.3477 | 17967.3477 | 17967.3477 | 17967.3477 | 17967.3477 | 17967.3477 | 17967.3477 | 17967.3477 | 17967.3477 | 17967.3477 | 17967.3477 |  | 14287.0002 | 19365.3548 | 20752.8099 | 15773.3386 | 15908.034 | 16206.2611 | 16912.2585 | 17296.5772 | 18030.9159 | 20265.5369 | 18420.5445 | 18058.8184 | 18544.2963 | 19607.4407 | 18885.8111 | 18885.8111 | 18885.8111 | 18885.8111 | 18885.8111 | 18885.8111 | 18885.8111 | 18885.8111 | 18885.8111 | 18885.8111 | 18885.8111 | 18885.8111 | 18885.8111 | 18885.8111 | 18885.8111 | 18885.8111
60% | 14698.1621 | 20360.2151 | 21830.1779 | 16362.6579 | 16556.3738 | 16891.9907 | 17657.2266 | 18168.3735 | 18817.0919 | 19153.183 | 19448.046 | 18899.806 | 19539.4712 | 20545.851 | 19779.8367 | 19779.8367 | 19779.8367 | 19779.8367 | 19779.8367 | 19779.8367 | 19779.8367 | 19779.8367 | 19779.8367 | 19779.8367 | 19779.8367 | 19779.8367 | 19779.8367 | 19779.8367 | 19779.8367 | 19779.8367 |  | 15728.2275 | 21318.8704 | 22846.2875 | 17364.503 | 17512.786 | 17841.0974 | 18618.3135 | 19041.401 | 19849.8175 | 22309.86 | 20278.7506 | 19880.5348 | 20414.9861 | 21585.3772 | 20790.9519 | 20790.9519 | 20790.9519 | 20790.9519 | 20790.9519 | 20790.9519 | 20790.9519 | 20790.9519 | 20790.9519 | 20790.9519 | 20790.9519 | 20790.9519 | 20790.9519 | 20790.9519 | 20790.9519 | 20790.9519
55% | 16350.7821 | 22649.4603 | 24284.7017 | 18202.4291 | 18417.9259 | 18791.2786 | 19642.5555 | 20211.1742 | 20932.8328 | 21306.713 | 21634.7296 | 21024.847 | 21736.4343 | 22855.9686 | 22003.8259 | 22003.8259 | 22003.8259 | 22003.8259 | 22003.8259 | 22003.8259 | 22003.8259 | 22003.8259 | 22003.8259 | 22003.8259 | 22003.8259 | 22003.8259 | 22003.8259 | 22003.8259 | 22003.8259 | 22003.8259 |  | 17496.6651 | 23715.9042 | 25415.0598 | 19316.9189 | 19481.8744 | 19847.1002 | 20711.7042 | 21182.3626 | 22081.6751 | 24818.3179 | 22558.8362 | 22115.8462 | 22710.3897 | 24012.3762 | 23128.628 | 23128.628 | 23128.628 | 23128.628 | 23128.628 | 23128.628 | 23128.628 | 23128.628 | 23128.628 | 23128.628 | 23128.628 | 23128.628 | 23128.628 | 23128.628 | 23128.628 | 23128.628
50% | 16573.101 | 22957.4214 | 24614.8968 | 18449.9246 | 18668.3514 | 19046.7806 | 19909.6321 | 20485.9823 | 21217.4531 | 21596.4169 | 21928.8935 | 21310.7185 | 22031.9811 | 23166.7375 | 22303.0084 | 22303.0084 | 22303.0084 | 22303.0084 | 22303.0084 | 22303.0084 | 22303.0084 | 22303.0084 | 22303.0084 | 22303.0084 | 22303.0084 | 22303.0084 | 22303.0084 | 22303.0084 | 22303.0084 | 22303.0084 |  | 17734.5645 | 24038.3655 | 25760.6242 | 19579.5679 | 19746.7663 | 20116.958 | 20993.3179 | 21470.3757 | 22381.916 | 25155.7685 | 22865.5651 | 22416.5517 | 23019.1792 | 24338.8686 | 23443.1042 | 23443.1042 | 23443.1042 | 23443.1042 | 23443.1042 | 23443.1042 | 23443.1042 | 23443.1042 | 23443.1042 | 23443.1042 | 23443.1042 | 23443.1042 | 23443.1042 | 23443.1042 | 23443.1042 | 23443.1042
45% | 12791.4633 | 17719.0143 | 18998.2882 | 14240.0347 | 14408.6211 | 14700.7006 | 15366.6673 | 15811.5063 | 16376.0707 | 16668.5628 | 16925.1751 | 16448.0548 | 17004.7403 | 17880.5688 | 17213.9248 | 17213.9248 | 17213.9248 | 17213.9248 | 17213.9248 | 17213.9248 | 17213.9248 | 17213.9248 | 17213.9248 | 17213.9248 | 17213.9248 | 17213.9248 | 17213.9248 | 17213.9248 | 17213.9248 | 17213.9248 |  | 13687.9049 | 18553.3094 | 19882.5844 | 15111.9169 | 15240.9641 | 15526.6857 | 16203.0785 | 16571.2816 | 17274.8273 | 19415.7442 | 17648.1177 | 17301.5599 | 17766.6803 | 18785.2439 | 18093.8744 | 18093.8744 | 18093.8744 | 18093.8744 | 18093.8744 | 18093.8744 | 18093.8744 | 18093.8744 | 18093.8744 | 18093.8744 | 18093.8744 | 18093.8744 | 18093.8744 | 18093.8744 | 18093.8744 | 18093.8744
40% | 6284.3875 | 8705.2708 | 9333.7723 | 6996.0641 | 7078.8898 | 7222.3871 | 7549.5735 | 7768.1209 | 8045.4888 | 8189.1888 | 8315.2613 | 8080.8542 | 8354.3513 | 8784.6419 | 8457.1227 | 8457.1227 | 8457.1227 | 8457.1227 | 8457.1227 | 8457.1227 | 8457.1227 | 8457.1227 | 8457.1227 | 8457.1227 | 8457.1227 | 8457.1227 | 8457.1227 | 8457.1227 | 8457.1227 | 8457.1227 |  | 6724.8052 | 9115.1562 | 9768.223 | 7424.4158 | 7487.8161 | 7628.1898 | 7960.4985 | 8141.395 | 8487.0438 | 9538.8665 | 8670.4397 | 8500.1774 | 8728.6889 | 9229.1046 | 8889.4379 | 8889.4379 | 8889.4379 | 8889.4379 | 8889.4379 | 8889.4379 | 8889.4379 | 8889.4379 | 8889.4379 | 8889.4379 | 8889.4379 | 8889.4379 | 8889.4379 | 8889.4379 | 8889.4379 | 8889.4379
35% | 2348.7515 | 3253.5419 | 3488.4405 | 2614.7363 | 2645.6919 | 2699.3231 | 2821.6071 | 2903.2878 | 3006.9524 | 3060.6594 | 3107.7782 | 3020.17 | 3122.3879 | 3283.2063 | 3160.798 | 3160.798 | 3160.798 | 3160.798 | 3160.798 | 3160.798 | 3160.798 | 3160.798 | 3160.798 | 3160.798 | 3160.798 | 3160.798 | 3160.798 | 3160.798 | 3160.798 | 3160.798 |  | 2513.3549 | 3406.7341 | 3650.8138 | 2774.8301 | 2798.5256 | 2850.9894 | 2975.1878 | 3042.7967 | 3171.9809 | 3565.0932 | 3240.524 | 3176.8895 | 3262.2943 | 3449.3216 | 3322.3732 | 3322.3732 | 3322.3732 | 3322.3732 | 3322.3732 | 3322.3732 | 3322.3732 | 3322.3732 | 3322.3732 | 3322.3732 | 3322.3732 | 3322.3732 | 3322.3732 | 3322.3732 | 3322.3732 | 3322.3732
30% | 1171.4214 | 1622.6784 | 1739.8323 | 1304.0792 | 1319.518 | 1346.2662 | 1407.2543 | 1447.992 | 1499.6939 | 1526.4798 | 1549.9799 | 1506.286 | 1557.2664 | 1637.4733 | 1576.4232 | 1576.4232 | 1576.4232 | 1576.4232 | 1576.4232 | 1576.4232 | 1576.4232 | 1576.4232 | 1576.4232 | 1576.4232 | 1576.4232 | 1576.4232 | 1576.4232 | 1576.4232 | 1576.4232 | 1576.4232 |  | 1253.516 | 1699.0818 | 1820.8147 | 1383.9247 | 1395.7426 | 1421.9086 | 1483.8515 | 1517.571 | 1582.0005 | 1778.0622 | 1616.1859 | 1584.4487 | 1627.0436 | 1720.322 | 1657.0075 | 1657.0075 | 1657.0075 | 1657.0075 | 1657.0075 | 1657.0075 | 1657.0075 | 1657.0075 | 1657.0075 | 1657.0075 | 1657.0075 | 1657.0075 | 1657.0075 | 1657.0075 | 1657.0075 | 1657.0075
25% | 690.592 | 956.6232 | 1025.6893 | 768.7982 | 777.9 | 793.6689 | 829.6235 | 853.6397 | 884.1196 | 899.9109 | 913.765 | 888.006 | 918.0606 | 965.3453 | 929.3541 | 929.3541 | 929.3541 | 929.3541 | 929.3541 | 929.3541 | 929.3541 | 929.3541 | 929.3541 | 929.3541 | 929.3541 | 929.3541 | 929.3541 | 929.3541 | 929.3541 | 929.3541 |  | 738.9896 | 1001.6655 | 1073.4311 | 815.8699 | 822.8369 | 838.2626 | 874.7801 | 894.6588 | 932.6422 | 1048.2271 | 952.7956 | 934.0854 | 959.1966 | 1014.1873 | 976.8613 | 976.8613 | 976.8613 | 976.8613 | 976.8613 | 976.8613 | 976.8613 | 976.8613 | 976.8613 | 976.8613 | 976.8613 | 976.8613 | 976.8613 | 976.8613 | 976.8613 | 976.8613
20% | 348.989 | 483.4272 | 518.3296 | 388.5103 | 393.1099 | 401.0787 | 419.2482 | 431.3847 | 446.7877 | 454.7678 | 461.7689 | 448.7517 | 463.9397 | 487.8349 | 469.6469 | 469.6469 | 469.6469 | 469.6469 | 469.6469 | 469.6469 | 469.6469 | 469.6469 | 469.6469 | 469.6469 | 469.6469 | 469.6469 | 469.6469 | 469.6469 | 469.6469 | 469.6469 |  | 373.4466 | 506.1893 | 542.4558 | 412.2979 | 415.8187 | 423.614 | 442.068 | 452.1137 | 471.3085 | 529.719 | 481.4929 | 472.0378 | 484.7277 | 512.5171 | 493.6545 | 493.6545 | 493.6545 | 493.6545 | 493.6545 | 493.6545 | 493.6545 | 493.6545 | 493.6545 | 493.6545 | 493.6545 | 493.6545 | 493.6545 | 493.6545 | 493.6545 | 493.6545
15% | 142.1807 | 196.9518 | 211.1713 | 158.282 | 160.1559 | 163.4024 | 170.8048 | 175.7493 | 182.0246 | 185.2758 | 188.1281 | 182.8248 | 189.0125 | 198.7476 | 191.3376 | 191.3376 | 191.3376 | 191.3376 | 191.3376 | 191.3376 | 191.3376 | 191.3376 | 191.3376 | 191.3376 | 191.3376 | 191.3376 | 191.3376 | 191.3376 | 191.3376 | 191.3376 |  | 152.1449 | 206.2253 | 221.0005 | 167.9732 | 169.4076 | 172.5835 | 180.1018 | 184.1945 | 192.0146 | 215.8115 | 196.1638 | 192.3117 | 197.4816 | 208.8033 | 201.1185 | 201.1185 | 201.1185 | 201.1185 | 201.1185 | 201.1185 | 201.1185 | 201.1185 | 201.1185 | 201.1185 | 201.1185 | 201.1185 | 201.1185 | 201.1185 | 201.1185 | 201.1185
10% | 57.2416 | 79.2923 | 85.017 | 63.7239 | 64.4783 | 65.7854 | 68.7656 | 70.7562 | 73.2826 | 74.5915 | 75.7399 | 73.6048 | 76.0959 | 80.0152 | 77.032 | 77.032 | 77.032 | 77.032 | 77.032 | 77.032 | 77.032 | 77.032 | 77.032 | 77.032 | 77.032 | 77.032 | 77.032 | 77.032 | 77.032 | 77.032 |  | 61.2531 | 83.0258 | 88.9742 | 67.6256 | 68.2031 | 69.4817 | 72.5085 | 74.1562 | 77.3046 | 86.8851 | 78.975 | 77.4242 | 79.5056 | 84.0637 | 80.9698 | 80.9698 | 80.9698 | 80.9698 | 80.9698 | 80.9698 | 80.9698 | 80.9698 | 80.9698 | 80.9698 | 80.9698 | 80.9698 | 80.9698 | 80.9698 | 80.9698 | 80.9698
5% | 48.7477 | 67.5263 | 72.4016 | 54.2681 | 54.9106 | 56.0237 | 58.5617 | 60.2569 | 62.4084 | 63.5231 | 64.5011 | 62.6828 | 64.8043 | 68.142 | 65.6015 | 65.6015 | 65.6015 | 65.6015 | 65.6015 | 65.6015 | 65.6015 | 65.6015 | 65.6015 | 65.6015 | 65.6015 | 65.6015 | 65.6015 | 65.6015 | 65.6015 | 65.6015 |  | 52.164 | 70.7058 | 75.7716 | 57.5908 | 58.0826 | 59.1715 | 61.7492 | 63.1524 | 65.8336 | 73.9925 | 67.2562 | 65.9354 | 67.708 | 71.5897 | 68.9549 | 68.9549 | 68.9549 | 68.9549 | 68.9549 | 68.9549 | 68.9549 | 68.9549 | 68.9549 | 68.9549 | 68.9549 | 68.9549 | 68.9549 | 68.9549 | 68.9549 | 68.9549
9.992e-14% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E @ R (MWh) | 130541.7636 | 180829.3011 | 193884.7798 | 145324.9874 | 147045.4755 | 150026.2579 | 156822.7025 | 161362.4545 | 167124.0494 | 170109.0429 | 172727.8694 | 167858.6746 | 173539.8625 | 182478.027 | 175674.6697 | 175674.6697 | 175674.6697 | 175674.6697 | 175674.6697 | 175674.6697 | 175674.6697 | 175674.6697 | 175674.6697 | 175674.6697 | 175674.6697 | 175674.6697 | 175674.6697 | 175674.6697 | 175674.6697 | 175674.6697 | E @ R (MWh) | 139690.2921 | 189343.6009 | 202909.3599 | 154222.8772 | 155539.8531 | 158455.7512 | 165358.5978 | 169116.2509 | 176296.2037 | 198145.0774 | 180105.7743 | 176569.0196 | 181315.7507 | 191710.5816 | 184654.8912 | 184654.8912 | 184654.8912 | 184654.8912 | 184654.8912 | 184654.8912 | 184654.8912 | 184654.8912 | 184654.8912 | 184654.8912 | 184654.8912 | 184654.8912 | 184654.8912 | 184654.8912 | 184654.8912 | 184654.8912
Option 2 Winter POE50 W E @ R (MWh) N 2 | 91379.2345 | 126580.5108 | 135719.3459 | 101727.4912 | 102931.8328 | 105018.3805 | 109775.8917 | 112953.7182 | 116986.8345 | 119076.33 | 120909.5086 | 117501.0722 | 121477.9037 | 127734.6189 | 122972.2688 | 122972.2688 | 122972.2688 | 122972.2688 | 122972.2688 | 122972.2688 | 122972.2688 | 122972.2688 | 122972.2688 | 122972.2688 | 122972.2688 | 122972.2688 | 122972.2688 | 122972.2688 | 122972.2688 | 122972.2688 | Option 2 Winter POE10 W E @ R (MWh) N 2 | 41907.0876 | 56803.0803 | 60872.808 | 46266.8632 | 46661.9559 | 47536.7254 | 49607.5793 | 50734.8753 | 52888.8611 | 59443.5232 | 54031.7323 | 52970.7059 | 54394.7252 | 57513.1745 | 55396.4674 | 55396.4674 | 55396.4674 | 55396.4674 | 55396.4674 | 55396.4674 | 55396.4674 | 55396.4674 | 55396.4674 | 55396.4674 | 55396.4674 | 55396.4674 | 55396.4674 | 55396.4674 | 55396.4674 | 55396.4674
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 94.6719 | 122.4737 | 129.7436 | 100.2055 | 100.2318 | 100.9746 | 102.941 | 104.254 | 105.5413 | 107.0476 | 108.4409 | 109.7956 | 109.9466 | 111.5284 | 110.3221 | 110.3221 | 110.3221 | 110.3221 | 110.3221 | 110.3221 | 110.3221 | 110.3221 | 110.3221 | 110.3221 | 110.3221 | 110.3221 | 110.3221 | 110.3221 | 110.3221 | 110.3221
98% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 46.8602 | 60.6214 | 64.2198 | 49.5992 | 49.6122 | 49.9799 | 50.9532 | 51.6031 | 52.2403 | 52.9859 | 53.6755 | 54.3461 | 54.4208 | 55.2038 | 54.6067 | 54.6067 | 54.6067 | 54.6067 | 54.6067 | 54.6067 | 54.6067 | 54.6067 | 54.6067 | 54.6067 | 54.6067 | 54.6067 | 54.6067 | 54.6067 | 54.6067 | 54.6067
97% | 20.8131 | 27.6102 | 29.4592 | 22.2762 | 22.2731 | 22.4832 | 22.7139 | 23.1878 | 23.5284 | 23.7128 | 23.9142 | 24.0989 | 24.4331 | 24.8481 | 24.8183 | 24.8183 | 24.8183 | 24.8183 | 24.8183 | 24.8183 | 24.8183 | 24.8183 | 24.8183 | 24.8183 | 24.8183 | 24.8183 | 24.8183 | 24.8183 | 24.8183 | 24.8183 |  | 92.7689 | 120.0119 | 127.1357 | 98.1913 | 98.2171 | 98.945 | 100.8719 | 102.1584 | 103.4199 | 104.8959 | 106.2612 | 107.5887 | 107.7366 | 109.2866 | 108.1045 | 108.1045 | 108.1045 | 108.1045 | 108.1045 | 108.1045 | 108.1045 | 108.1045 | 108.1045 | 108.1045 | 108.1045 | 108.1045 | 108.1045 | 108.1045 | 108.1045 | 108.1045
95% | 102.4643 | 135.9269 | 145.0299 | 109.6673 | 109.6521 | 110.6866 | 111.8221 | 114.1553 | 115.8322 | 116.7402 | 117.7316 | 118.6405 | 120.286 | 122.3291 | 122.1824 | 122.1824 | 122.1824 | 122.1824 | 122.1824 | 122.1824 | 122.1824 | 122.1824 | 122.1824 | 122.1824 | 122.1824 | 122.1824 | 122.1824 | 122.1824 | 122.1824 | 122.1824 |  | 137.0126 | 177.2483 | 187.7696 | 145.021 | 145.0591 | 146.1341 | 148.98 | 150.8801 | 152.7432 | 154.9232 | 156.9396 | 158.9002 | 159.1187 | 161.408 | 159.6621 | 159.6621 | 159.6621 | 159.6621 | 159.6621 | 159.6621 | 159.6621 | 159.6621 | 159.6621 | 159.6621 | 159.6621 | 159.6621 | 159.6621 | 159.6621 | 159.6621 | 159.6621
90% | 177.7116 | 235.7483 | 251.5362 | 190.2043 | 190.1779 | 191.972 | 193.9414 | 197.988 | 200.8964 | 202.4712 | 204.1907 | 205.7672 | 208.621 | 212.1645 | 211.9101 | 211.9101 | 211.9101 | 211.9101 | 211.9101 | 211.9101 | 211.9101 | 211.9101 | 211.9101 | 211.9101 | 211.9101 | 211.9101 | 211.9101 | 211.9101 | 211.9101 | 211.9101 |  | 594.078 | 768.5376 | 814.1574 | 628.8019 | 628.967 | 633.6283 | 645.968 | 654.2068 | 662.285 | 671.7372 | 680.4805 | 688.9812 | 689.9289 | 699.8548 | 692.2849 | 692.2849 | 692.2849 | 692.2849 | 692.2849 | 692.2849 | 692.2849 | 692.2849 | 692.2849 | 692.2849 | 692.2849 | 692.2849 | 692.2849 | 692.2849 | 692.2849 | 692.2849
85% | 504.3166 | 669.0154 | 713.8189 | 539.7689 | 539.694 | 544.7854 | 550.3742 | 561.858 | 570.1114 | 574.5805 | 579.4602 | 583.9339 | 592.0325 | 602.0884 | 601.3664 | 601.3664 | 601.3664 | 601.3664 | 601.3664 | 601.3664 | 601.3664 | 601.3664 | 601.3664 | 601.3664 | 601.3664 | 601.3664 | 601.3664 | 601.3664 | 601.3664 | 601.3664 |  | 561.9657 | 726.995 | 770.1489 | 594.8126 | 594.9688 | 599.3781 | 611.0508 | 618.8443 | 626.4858 | 635.427 | 643.6978 | 651.739 | 652.6354 | 662.0248 | 654.8641 | 654.8641 | 654.8641 | 654.8641 | 654.8641 | 654.8641 | 654.8641 | 654.8641 | 654.8641 | 654.8641 | 654.8641 | 654.8641 | 654.8641 | 654.8641 | 654.8641 | 654.8641
80% | 704.4422 | 934.4978 | 997.0804 | 753.9629 | 753.8583 | 760.9701 | 768.7766 | 784.8175 | 796.3461 | 802.5886 | 809.4047 | 815.6538 | 826.966 | 841.0124 | 840.0039 | 840.0039 | 840.0039 | 840.0039 | 840.0039 | 840.0039 | 840.0039 | 840.0039 | 840.0039 | 840.0039 | 840.0039 | 840.0039 | 840.0039 | 840.0039 | 840.0039 | 840.0039 |  | 392.484 | 507.7425 | 537.8818 | 415.4247 | 415.5338 | 418.6133 | 426.7657 | 432.2087 | 437.5457 | 443.7903 | 449.5667 | 455.1828 | 455.8089 | 462.3665 | 457.3654 | 457.3654 | 457.3654 | 457.3654 | 457.3654 | 457.3654 | 457.3654 | 457.3654 | 457.3654 | 457.3654 | 457.3654 | 457.3654 | 457.3654 | 457.3654 | 457.3654 | 457.3654
75% | 1836.3528 | 2436.0657 | 2599.2074 | 1965.4443 | 1965.1715 | 1983.7107 | 2004.0609 | 2045.8765 | 2075.9296 | 2092.2026 | 2109.9709 | 2126.2611 | 2155.75 | 2192.3665 | 2189.7374 | 2189.7374 | 2189.7374 | 2189.7374 | 2189.7374 | 2189.7374 | 2189.7374 | 2189.7374 | 2189.7374 | 2189.7374 | 2189.7374 | 2189.7374 | 2189.7374 | 2189.7374 | 2189.7374 | 2189.7374 |  | 700.5244 | 906.2435 | 960.0375 | 741.4701 | 741.6648 | 747.1612 | 761.712 | 771.4271 | 780.9527 | 792.0985 | 802.4084 | 812.4323 | 813.5498 | 825.2542 | 816.3279 | 816.3279 | 816.3279 | 816.3279 | 816.3279 | 816.3279 | 816.3279 | 816.3279 | 816.3279 | 816.3279 | 816.3279 | 816.3279 | 816.3279 | 816.3279 | 816.3279 | 816.3279
70% | 3172.6584 | 4208.7797 | 4490.6388 | 3395.6891 | 3395.2178 | 3427.2478 | 3462.4068 | 3534.6515 | 3586.5741 | 3614.6888 | 3645.387 | 3673.5316 | 3724.4794 | 3787.7416 | 3783.1994 | 3783.1994 | 3783.1994 | 3783.1994 | 3783.1994 | 3783.1994 | 3783.1994 | 3783.1994 | 3783.1994 | 3783.1994 | 3783.1994 | 3783.1994 | 3783.1994 | 3783.1994 | 3783.1994 | 3783.1994 |  | 1276.1675 | 1650.9325 | 1748.9307 | 1350.7597 | 1351.1144 | 1361.1274 | 1387.635 | 1405.3332 | 1422.6864 | 1442.9909 | 1461.7729 | 1480.0337 | 1482.0695 | 1503.3918 | 1487.1305 | 1487.1305 | 1487.1305 | 1487.1305 | 1487.1305 | 1487.1305 | 1487.1305 | 1487.1305 | 1487.1305 | 1487.1305 | 1487.1305 | 1487.1305 | 1487.1305 | 1487.1305 | 1487.1305 | 1487.1305
65% | 7968.2023 | 10570.444 | 11278.3393 | 8528.349 | 8527.1652 | 8607.6093 | 8695.912 | 8877.356 | 9007.7607 | 9078.3716 | 9155.4708 | 9226.1564 | 9354.1131 | 9512.9974 | 9501.5896 | 9501.5896 | 9501.5896 | 9501.5896 | 9501.5896 | 9501.5896 | 9501.5896 | 9501.5896 | 9501.5896 | 9501.5896 | 9501.5896 | 9501.5896 | 9501.5896 | 9501.5896 | 9501.5896 | 9501.5896 |  | 1605.6162 | 2077.1285 | 2200.4254 | 1699.4647 | 1699.9109 | 1712.5088 | 1745.8595 | 1768.1266 | 1789.9596 | 1815.5058 | 1839.1365 | 1862.1114 | 1864.6727 | 1891.4995 | 1871.0402 | 1871.0402 | 1871.0402 | 1871.0402 | 1871.0402 | 1871.0402 | 1871.0402 | 1871.0402 | 1871.0402 | 1871.0402 | 1871.0402 | 1871.0402 | 1871.0402 | 1871.0402 | 1871.0402 | 1871.0402
60% | 11647.312 | 15451.0709 | 16485.8185 | 12466.0917 | 12464.3614 | 12581.9486 | 12711.0226 | 12976.2436 | 13166.8594 | 13270.073 | 13382.7707 | 13486.0936 | 13673.131 | 13905.3759 | 13888.7009 | 13888.7009 | 13888.7009 | 13888.7009 | 13888.7009 | 13888.7009 | 13888.7009 | 13888.7009 | 13888.7009 | 13888.7009 | 13888.7009 | 13888.7009 | 13888.7009 | 13888.7009 | 13888.7009 | 13888.7009 |  | 2512.492 | 3250.3215 | 3443.2583 | 2659.3475 | 2660.0458 | 2679.7591 | 2731.9468 | 2766.7907 | 2800.9552 | 2840.9304 | 2877.908 | 2913.8595 | 2917.8675 | 2959.8464 | 2927.8315 | 2927.8315 | 2927.8315 | 2927.8315 | 2927.8315 | 2927.8315 | 2927.8315 | 2927.8315 | 2927.8315 | 2927.8315 | 2927.8315 | 2927.8315 | 2927.8315 | 2927.8315 | 2927.8315 | 2927.8315
55% | 13170.4015 | 17471.5683 | 18641.6273 | 14096.251 | 14094.2944 | 14227.2581 | 14373.2108 | 14673.1142 | 14888.6563 | 15005.3669 | 15132.8017 | 15249.6359 | 15461.1317 | 15723.7467 | 15704.8911 | 15704.8911 | 15704.8911 | 15704.8911 | 15704.8911 | 15704.8911 | 15704.8911 | 15704.8911 | 15704.8911 | 15704.8911 | 15704.8911 | 15704.8911 | 15704.8911 | 15704.8911 | 15704.8911 | 15704.8911 |  | 4828.1473 | 6246.0024 | 6616.7608 | 5110.3531 | 5111.6951 | 5149.5773 | 5249.8642 | 5316.8222 | 5382.4747 | 5459.2932 | 5530.3515 | 5599.4379 | 5607.1399 | 5687.8089 | 5626.2873 | 5626.2873 | 5626.2873 | 5626.2873 | 5626.2873 | 5626.2873 | 5626.2873 | 5626.2873 | 5626.2873 | 5626.2873 | 5626.2873 | 5626.2873 | 5626.2873 | 5626.2873 | 5626.2873 | 5626.2873
50% | 16911.4168 | 22434.3178 | 23936.7286 | 18100.2512 | 18097.7388 | 18268.4705 | 18455.8806 | 18840.9706 | 19117.7369 | 19267.5988 | 19431.2312 | 19581.2518 | 19852.8223 | 20190.0324 | 20165.821 | 20165.821 | 20165.821 | 20165.821 | 20165.821 | 20165.821 | 20165.821 | 20165.821 | 20165.821 | 20165.821 | 20165.821 | 20165.821 | 20165.821 | 20165.821 | 20165.821 | 20165.821 |  | 10714.812 | 13861.3711 | 14684.1724 | 11341.0941 | 11344.0722 | 11428.142 | 11650.7024 | 11799.2983 | 11944.9968 | 12115.4754 | 12273.1708 | 12426.4899 | 12443.5826 | 12622.6063 | 12486.0752 | 12486.0752 | 12486.0752 | 12486.0752 | 12486.0752 | 12486.0752 | 12486.0752 | 12486.0752 | 12486.0752 | 12486.0752 | 12486.0752 | 12486.0752 | 12486.0752 | 12486.0752 | 12486.0752 | 12486.0752
45% | 22520.2713 | 29874.9022 | 31875.6039 | 24103.3955 | 24100.0499 | 24327.4065 | 24576.9733 | 25089.7826 | 25458.3414 | 25657.9066 | 25875.8094 | 26075.5859 | 26437.2258 | 26886.2753 | 26854.0338 | 26854.0338 | 26854.0338 | 26854.0338 | 26854.0338 | 26854.0338 | 26854.0338 | 26854.0338 | 26854.0338 | 26854.0338 | 26854.0338 | 26854.0338 | 26854.0338 | 26854.0338 | 26854.0338 | 26854.0338 |  | 16236.3476 | 21004.3853 | 22251.1909 | 17185.3642 | 17189.877 | 17317.2694 | 17654.5192 | 17879.6892 | 18100.4688 | 18358.7982 | 18597.7568 | 18830.084 | 18855.9848 | 19127.2628 | 18920.3748 | 18920.3748 | 18920.3748 | 18920.3748 | 18920.3748 | 18920.3748 | 18920.3748 | 18920.3748 | 18920.3748 | 18920.3748 | 18920.3748 | 18920.3748 | 18920.3748 | 18920.3748 | 18920.3748 | 18920.3748
40% | 15794.9825 | 20953.2804 | 22356.5072 | 16905.3341 | 16902.9876 | 17062.4482 | 17237.4862 | 17597.1538 | 17855.6489 | 17995.6175 | 18148.4474 | 18288.5641 | 18542.2065 | 18857.1552 | 18834.542 | 18834.542 | 18834.542 | 18834.542 | 18834.542 | 18834.542 | 18834.542 | 18834.542 | 18834.542 | 18834.542 | 18834.542 | 18834.542 | 18834.542 | 18834.542 | 18834.542 | 18834.542 |  | 16811.9908 | 21749.0744 | 23040.0842 | 17794.6538 | 17799.3266 | 17931.2355 | 18280.4421 | 18513.5954 | 18742.2025 | 19009.6907 | 19257.1213 | 19497.6854 | 19524.5045 | 19805.4004 | 19591.1773 | 19591.1773 | 19591.1773 | 19591.1773 | 19591.1773 | 19591.1773 | 19591.1773 | 19591.1773 | 19591.1773 | 19591.1773 | 19591.1773 | 19591.1773 | 19591.1773 | 19591.1773 | 19591.1773 | 19591.1773
35% | 8189.141 | 10863.5364 | 11591.06 | 8764.8191 | 8763.6026 | 8846.2772 | 8937.0283 | 9123.5033 | 9257.5238 | 9330.0926 | 9409.3295 | 9481.9751 | 9613.4797 | 9776.7695 | 9765.0454 | 9765.0454 | 9765.0454 | 9765.0454 | 9765.0454 | 9765.0454 | 9765.0454 | 9765.0454 | 9765.0454 | 9765.0454 | 9765.0454 | 9765.0454 | 9765.0454 | 9765.0454 | 9765.0454 | 9765.0454 |  | 22897.8708 | 29622.1608 | 31380.5115 | 24236.2542 | 24242.6186 | 24422.2781 | 24897.8962 | 25215.4501 | 25526.8121 | 25891.1301 | 26228.1297 | 26555.7772 | 26592.3047 | 26974.8838 | 26683.1128 | 26683.1128 | 26683.1128 | 26683.1128 | 26683.1128 | 26683.1128 | 26683.1128 | 26683.1128 | 26683.1128 | 26683.1128 | 26683.1128 | 26683.1128 | 26683.1128 | 26683.1128 | 26683.1128 | 26683.1128
30% | 3808.7911 | 5052.6595 | 5391.0326 | 4076.5405 | 4075.9747 | 4114.4269 | 4156.6354 | 4243.3654 | 4305.6988 | 4339.4507 | 4376.304 | 4410.0916 | 4471.2548 | 4547.2013 | 4541.7484 | 4541.7484 | 4541.7484 | 4541.7484 | 4541.7484 | 4541.7484 | 4541.7484 | 4541.7484 | 4541.7484 | 4541.7484 | 4541.7484 | 4541.7484 | 4541.7484 | 4541.7484 | 4541.7484 | 4541.7484 |  | 21159.0479 | 27372.7075 | 28997.5323 | 22395.7969 | 22401.678 | 22567.6945 | 23007.1951 | 23300.6345 | 23588.3522 | 23925.0045 | 24236.413 | 24539.1795 | 24572.9332 | 24926.46 | 24656.8456 | 24656.8456 | 24656.8456 | 24656.8456 | 24656.8456 | 24656.8456 | 24656.8456 | 24656.8456 | 24656.8456 | 24656.8456 | 24656.8456 | 24656.8456 | 24656.8456 | 24656.8456 | 24656.8456 | 24656.8456
25% | 2600.5659 | 3449.8542 | 3680.8886 | 2783.3798 | 2782.9935 | 2809.2479 | 2838.067 | 2897.2845 | 2939.8445 | 2962.8896 | 2988.0523 | 3011.1218 | 3052.8828 | 3104.7375 | 3101.0144 | 3101.0144 | 3101.0144 | 3101.0144 | 3101.0144 | 3101.0144 | 3101.0144 | 3101.0144 | 3101.0144 | 3101.0144 | 3101.0144 | 3101.0144 | 3101.0144 | 3101.0144 | 3101.0144 | 3101.0144 |  | 6103.1255 | 7895.3963 | 8364.0615 | 6459.854 | 6461.5503 | 6509.4362 | 6636.2059 | 6720.8457 | 6803.8352 | 6900.9393 | 6990.7621 | 7078.0922 | 7087.8282 | 7189.7996 | 7112.0319 | 7112.0319 | 7112.0319 | 7112.0319 | 7112.0319 | 7112.0319 | 7112.0319 | 7112.0319 | 7112.0319 | 7112.0319 | 7112.0319 | 7112.0319 | 7112.0319 | 7112.0319 | 7112.0319 | 7112.0319
20% | 1575.389 | 2089.8768 | 2229.8344 | 1686.1353 | 1685.9013 | 1701.8058 | 1719.2641 | 1755.1373 | 1780.9195 | 1794.88 | 1810.1232 | 1824.0984 | 1849.3967 | 1880.8096 | 1878.5542 | 1878.5542 | 1878.5542 | 1878.5542 | 1878.5542 | 1878.5542 | 1878.5542 | 1878.5542 | 1878.5542 | 1878.5542 | 1878.5542 | 1878.5542 | 1878.5542 | 1878.5542 | 1878.5542 | 1878.5542 |  | 1637.7285 | 2118.6711 | 2244.4339 | 1733.4539 | 1733.9091 | 1746.759 | 1780.7767 | 1803.4891 | 1825.7587 | 1851.8159 | 1875.9192 | 1899.3536 | 1901.9662 | 1929.3294 | 1908.4611 | 1908.4611 | 1908.4611 | 1908.4611 | 1908.4611 | 1908.4611 | 1908.4611 | 1908.4611 | 1908.4611 | 1908.4611 | 1908.4611 | 1908.4611 | 1908.4611 | 1908.4611 | 1908.4611 | 1908.4611
15% | 1008.6332 | 1338.0309 | 1427.6379 | 1079.5378 | 1079.388 | 1089.5708 | 1100.7483 | 1123.7159 | 1140.2229 | 1149.161 | 1158.9203 | 1167.8679 | 1184.065 | 1204.1769 | 1202.7329 | 1202.7329 | 1202.7329 | 1202.7329 | 1202.7329 | 1202.7329 | 1202.7329 | 1202.7329 | 1202.7329 | 1202.7329 | 1202.7329 | 1202.7329 | 1202.7329 | 1202.7329 | 1202.7329 | 1202.7329 |  | 903.3078 | 1168.5771 | 1237.943 | 956.1062 | 956.3573 | 963.4448 | 982.2076 | 994.7349 | 1007.018 | 1021.3901 | 1034.6846 | 1047.6101 | 1049.0511 | 1064.1436 | 1052.6334 | 1052.6334 | 1052.6334 | 1052.6334 | 1052.6334 | 1052.6334 | 1052.6334 | 1052.6334 | 1052.6334 | 1052.6334 | 1052.6334 | 1052.6334 | 1052.6334 | 1052.6334 | 1052.6334 | 1052.6334
10% | 675.0905 | 895.5604 | 955.5354 | 722.5478 | 722.4475 | 729.263 | 736.7443 | 752.1168 | 763.165 | 769.1474 | 775.6795 | 781.6682 | 792.5091 | 805.9702 | 805.0037 | 805.0037 | 805.0037 | 805.0037 | 805.0037 | 805.0037 | 805.0037 | 805.0037 | 805.0037 | 805.0037 | 805.0037 | 805.0037 | 805.0037 | 805.0037 | 805.0037 | 805.0037 |  | 211.1088 | 273.1039 | 289.3152 | 223.4481 | 223.5068 | 225.1632 | 229.5482 | 232.4759 | 235.3465 | 238.7054 | 241.8124 | 244.8332 | 245.1699 | 248.6972 | 246.0071 | 246.0071 | 246.0071 | 246.0071 | 246.0071 | 246.0071 | 246.0071 | 246.0071 | 246.0071 | 246.0071 | 246.0071 | 246.0071 | 246.0071 | 246.0071 | 246.0071 | 246.0071
5% | 480.3015 | 637.1576 | 679.8276 | 514.0656 | 513.9943 | 518.8432 | 524.1659 | 535.1028 | 542.9633 | 547.2195 | 551.8668 | 556.1276 | 563.8405 | 573.4176 | 572.7299 | 572.7299 | 572.7299 | 572.7299 | 572.7299 | 572.7299 | 572.7299 | 572.7299 | 572.7299 | 572.7299 | 572.7299 | 572.7299 | 572.7299 | 572.7299 | 572.7299 | 572.7299 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9.992e-14% | 42.1598 | 55.9283 | 59.6738 | 45.1235 | 45.1173 | 45.5429 | 46.0101 | 46.9701 | 47.6601 | 48.0337 | 48.4416 | 48.8156 | 49.4927 | 50.3333 | 50.273 | 50.273 | 50.273 | 50.273 | 50.273 | 50.273 | 50.273 | 50.273 | 50.273 | 50.273 | 50.273 | 50.273 | 50.273 | 50.273 | 50.273 | 50.273 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E @ R (MWh) | 112911.4176 | 149785.8315 | 159816.886 | 120848.8352 | 120832.0611 | 121971.9746 | 123223.2448 | 125794.3515 | 127642.2198 | 128642.7935 | 129735.3077 | 130736.941 | 132550.1196 | 134801.5495 | 134639.8982 | 134639.8982 | 134639.8982 | 134639.8982 | 134639.8982 | 134639.8982 | 134639.8982 | 134639.8982 | 134639.8982 | 134639.8982 | 134639.8982 | 134639.8982 | 134639.8982 | 134639.8982 | 134639.8982 | 134639.8982 | E @ R (MWh) | 109518.1284 | 141679.7064 | 150089.7144 | 115919.4767 | 115949.9168 | 116809.2094 | 119084.0416 | 120602.8686 | 122092.0807 | 123834.5755 | 125446.4095 | 127013.5132 | 127188.2207 | 129018.0567 | 127622.5464 | 127622.5464 | 127622.5464 | 127622.5464 | 127622.5464 | 127622.5464 | 127622.5464 | 127622.5464 | 127622.5464 | 127622.5464 | 127622.5464 | 127622.5464 | 127622.5464 | 127622.5464 | 127622.5464 | 127622.5464
Option 2 Summer POE50 W E @ R (MWh) N 2 | 79037.9923 | 104850.082 | 111871.8202 | 84594.1846 | 84582.4428 | 85380.3823 | 86256.2713 | 88056.0461 | 89349.5539 | 90049.9554 | 90814.7154 | 91515.8587 | 92785.0837 | 94361.0846 | 94247.9288 | 94247.9288 | 94247.9288 | 94247.9288 | 94247.9288 | 94247.9288 | 94247.9288 | 94247.9288 | 94247.9288 | 94247.9288 | 94247.9288 | 94247.9288 | 94247.9288 | 94247.9288 | 94247.9288 | 94247.9288 | Option 2 Summer POE10 W E @ R (MWh) N 2 | 32855.4385 | 42503.9119 | 45026.9143 | 34775.843 | 34784.975 | 35042.7628 | 35725.2125 | 36180.8606 | 36627.6242 | 37150.3727 | 37633.9229 | 38104.054 | 38156.4662 | 38705.417 | 38286.7639 | 38286.7639 | 38286.7639 | 38286.7639 | 38286.7639 | 38286.7639 | 38286.7639 | 38286.7639 | 38286.7639 | 38286.7639 | 38286.7639 | 38286.7639 | 38286.7639 | 38286.7639 | 38286.7639 | 38286.7639
Option 3 - 2B PHM 3rd Tx + Switchroom + Two new feeders + OFR12 New Feeder
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | 73.4908 | 101.8011 | 109.1509 | 43.5292 | 44.4977 | 46.1758 | 50.002 | 52.5577 | 55.8013 | 57.4818 | 58.9561 | 56.2149 | 59.4132 | 64.4451 | 60.6151 | 60.6151 | 60.6151 | 60.6151 | 60.6151 | 60.6151 | 60.6151 | 60.6151 | 60.6151 | 60.6151 | 60.6151 | 60.6151 | 60.6151 | 60.6151 | 60.6151 | 60.6151 |  | 78.6411 | 106.5944 | 114.2314 | 48.5384 | 49.2798 | 50.9214 | 54.8074 | 56.9229 | 60.965 | 73.2652 | 63.1096 | 61.1185 | 63.7908 | 69.6428 | 65.6706 | 65.6706 | 65.6706 | 65.6706 | 65.6706 | 65.6706 | 65.6706 | 65.6706 | 65.6706 | 65.6706 | 65.6706 | 65.6706 | 65.6706 | 65.6706 | 65.6706 | 65.6706
98% | 87.3027 | 120.9335 | 129.6647 | 50.9036 | 52.0542 | 54.0476 | 58.5929 | 61.629 | 65.4822 | 67.4784 | 69.2298 | 65.9734 | 69.7729 | 75.7505 | 71.2006 | 71.2006 | 71.2006 | 71.2006 | 71.2006 | 71.2006 | 71.2006 | 71.2006 | 71.2006 | 71.2006 | 71.2006 | 71.2006 | 71.2006 | 71.2006 | 71.2006 | 71.2006 |  | 93.4209 | 126.6277 | 135.7001 | 56.8542 | 57.735 | 59.685 | 64.3015 | 66.8145 | 71.6162 | 86.2281 | 74.164 | 71.7987 | 74.9732 | 81.9249 | 77.2063 | 77.2063 | 77.2063 | 77.2063 | 77.2063 | 77.2063 | 77.2063 | 77.2063 | 77.2063 | 77.2063 | 77.2063 | 77.2063 | 77.2063 | 77.2063 | 77.2063 | 77.2063
97% | 172.8327 | 239.4116 | 256.6966 | 99.1442 | 101.4221 | 105.3685 | 114.3668 | 120.3773 | 128.0054 | 131.9574 | 135.4247 | 128.978 | 136.4997 | 148.3335 | 139.3261 | 139.3261 | 139.3261 | 139.3261 | 139.3261 | 139.3261 | 139.3261 | 139.3261 | 139.3261 | 139.3261 | 139.3261 | 139.3261 | 139.3261 | 139.3261 | 139.3261 | 139.3261 |  | 184.945 | 250.6842 | 268.6448 | 110.9247 | 112.6683 | 116.5289 | 125.668 | 130.643 | 140.149 | 169.0761 | 145.1927 | 140.5102 | 146.7947 | 160.5571 | 151.2156 | 151.2156 | 151.2156 | 151.2156 | 151.2156 | 151.2156 | 151.2156 | 151.2156 | 151.2156 | 151.2156 | 151.2156 | 151.2156 | 151.2156 | 151.2156 | 151.2156 | 151.2156
95% | 510.5211 | 707.185 | 758.2422 | 285.4497 | 292.1781 | 303.8353 | 330.4148 | 348.1688 | 370.7012 | 382.3748 | 392.6165 | 373.5741 | 395.7921 | 430.7473 | 404.1408 | 404.1408 | 404.1408 | 404.1408 | 404.1408 | 404.1408 | 404.1408 | 404.1408 | 404.1408 | 404.1408 | 404.1408 | 404.1408 | 404.1408 | 404.1408 | 404.1408 | 404.1408 |  | 546.299 | 740.4826 | 793.5354 | 320.2474 | 325.3978 | 336.8013 | 363.7969 | 378.4923 | 406.5715 | 492.0178 | 421.4699 | 407.6384 | 426.2019 | 466.8539 | 439.2606 | 439.2606 | 439.2606 | 439.2606 | 439.2606 | 439.2606 | 439.2606 | 439.2606 | 439.2606 | 439.2606 | 439.2606 | 439.2606 | 439.2606 | 439.2606 | 439.2606 | 439.2606
90% | 2814.8088 | 3899.1347 | 4180.6436 | 1473.4114 | 1510.5094 | 1574.7826 | 1721.331 | 1819.2195 | 1943.454 | 2007.818 | 2064.2865 | 1959.2944 | 2081.7951 | 2274.5244 | 2127.8269 | 2127.8269 | 2127.8269 | 2127.8269 | 2127.8269 | 2127.8269 | 2127.8269 | 2127.8269 | 2127.8269 | 2127.8269 | 2127.8269 | 2127.8269 | 2127.8269 | 2127.8269 | 2127.8269 | 2127.8269 |  | 3012.0741 | 4082.7244 | 4375.2363 | 1665.2723 | 1693.6696 | 1756.5437 | 1905.3864 | 1986.4109 | 2141.2287 | 2612.3454 | 2223.3727 | 2147.1113 | 2249.4628 | 2473.6015 | 2321.4631 | 2321.4631 | 2321.4631 | 2321.4631 | 2321.4631 | 2321.4631 | 2321.4631 | 2321.4631 | 2321.4631 | 2321.4631 | 2321.4631 | 2321.4631 | 2321.4631 | 2321.4631 | 2321.4631 | 2321.4631
85% | 6876.3763 | 9525.3066 | 10213.0129 | 3214.8475 | 3305.4754 | 3462.4901 | 3820.4975 | 4059.632 | 4363.1279 | 4520.3645 | 4658.313 | 4401.8248 | 4701.0853 | 5171.9092 | 4813.5377 | 4813.5377 | 4813.5377 | 4813.5377 | 4813.5377 | 4813.5377 | 4813.5377 | 4813.5377 | 4813.5377 | 4813.5377 | 4813.5377 | 4813.5377 | 4813.5377 | 4813.5377 | 4813.5377 | 4813.5377 |  | 7358.2813 | 9973.8032 | 10688.3888 | 3683.5499 | 3752.9225 | 3906.5194 | 4270.1316 | 4468.0685 | 4846.2774 | 5997.1817 | 5046.9491 | 4860.6482 | 5110.6855 | 5658.2403 | 5286.577 | 5286.577 | 5286.577 | 5286.577 | 5286.577 | 5286.577 | 5286.577 | 5286.577 | 5286.577 | 5286.577 | 5286.577 | 5286.577 | 5286.577 | 5286.577 | 5286.577 | 5286.577
80% | 10687.9274 | 14805.1503 | 15874.0497 | 4326.6009 | 4467.4635 | 4711.511 | 5267.9605 | 5639.6465 | 6111.3691 | 6355.7614 | 6570.1742 | 6171.5156 | 6636.655 | 7368.4549 | 6811.4394 | 6811.4394 | 6811.4394 | 6811.4394 | 6811.4394 | 6811.4394 | 6811.4394 | 6811.4394 | 6811.4394 | 6811.4394 | 6811.4394 | 6811.4394 | 6811.4394 | 6811.4394 | 6811.4394 | 6811.4394 |  | 11436.9506 | 15502.2469 | 16612.9248 | 5055.1034 | 5162.929 | 5401.6641 | 5966.8252 | 6274.4779 | 6862.3266 | 8651.1731 | 7174.23 | 6884.6631 | 7273.2952 | 8124.3576 | 7546.6827 | 7546.6827 | 7546.6827 | 7546.6827 | 7546.6827 | 7546.6827 | 7546.6827 | 7546.6827 | 7546.6827 | 7546.6827 | 7546.6827 | 7546.6827 | 7546.6827 | 7546.6827 | 7546.6827 | 7546.6827
75% | 11791.7667 | 16334.2127 | 17513.507 | 3938.5906 | 4094.0013 | 4363.2538 | 4977.1729 | 5387.2463 | 5907.688 | 6177.3209 | 6413.878 | 5974.0463 | 6487.2249 | 7294.6045 | 6680.0609 | 6680.0609 | 6680.0609 | 6680.0609 | 6680.0609 | 6680.0609 | 6680.0609 | 6680.0609 | 6680.0609 | 6680.0609 | 6680.0609 | 6680.0609 | 6680.0609 | 6680.0609 | 6680.0609 | 6680.0609 |  | 12618.1483 | 17103.3048 | 18328.6925 | 4742.3321 | 4861.2939 | 5124.6853 | 5748.2157 | 6087.6425 | 6736.2038 | 8709.8007 | 7080.3202 | 6760.8471 | 7189.6167 | 8128.5761 | 7491.2395 | 7491.2395 | 7491.2395 | 7491.2395 | 7491.2395 | 7491.2395 | 7491.2395 | 7491.2395 | 7491.2395 | 7491.2395 | 7491.2395 | 7491.2395 | 7491.2395 | 7491.2395 | 7491.2395 | 7491.2395
70% | 12669.5942 | 17550.1984 | 18817.2842 | 3211.0622 | 3378.0424 | 3667.3391 | 4326.9609 | 4767.5618 | 5326.7473 | 5616.4528 | 5870.6202 | 5398.0456 | 5949.4274 | 6816.9116 | 6156.6189 | 6156.6189 | 6156.6189 | 6156.6189 | 6156.6189 | 6156.6189 | 6156.6189 | 6156.6189 | 6156.6189 | 6156.6189 | 6156.6189 | 6156.6189 | 6156.6189 | 6156.6189 | 6156.6189 | 6156.6189 |  | 13557.495 | 18376.5449 | 19693.1554 | 4074.6376 | 4202.4553 | 4485.4547 | 5155.4033 | 5520.0984 | 6216.9412 | 8337.4607 | 6586.6751 | 6243.419 | 6704.1081 | 7712.9675 | 7028.1848 | 7028.1848 | 7028.1848 | 7028.1848 | 7028.1848 | 7028.1848 | 7028.1848 | 7028.1848 | 7028.1848 | 7028.1848 | 7028.1848 | 7028.1848 | 7028.1848 | 7028.1848 | 7028.1848 | 7028.1848
65% | 13351.323 | 18494.5441 | 19829.8096 | 2148.8302 | 2324.7953 | 2629.6586 | 3324.7735 | 3789.0824 | 4378.3567 | 4683.6507 | 4951.4944 | 4453.4914 | 5034.5421 | 5948.7041 | 5252.8822 | 5252.8822 | 5252.8822 | 5252.8822 | 5252.8822 | 5252.8822 | 5252.8822 | 5252.8822 | 5252.8822 | 5252.8822 | 5252.8822 | 5252.8822 | 5252.8822 | 5252.8822 | 5252.8822 | 5252.8822 |  | 14287.0002 | 19365.3548 | 20752.8099 | 3058.8731 | 3193.5685 | 3491.7956 | 4197.7929 | 4582.1116 | 5316.4503 | 7551.0713 | 5706.0789 | 5344.3529 | 5829.8308 | 6892.9752 | 6171.3456 | 6171.3456 | 6171.3456 | 6171.3456 | 6171.3456 | 6171.3456 | 6171.3456 | 6171.3456 | 6171.3456 | 6171.3456 | 6171.3456 | 6171.3456 | 6171.3456 | 6171.3456 | 6171.3456 | 6171.3456
60% | 14698.1621 | 20360.2151 | 21830.1779 | 791.0038 | 982.1797 | 1317.7966 | 2083.0325 | 2594.1794 | 3242.8979 | 3578.9889 | 3873.8519 | 3325.6119 | 3965.2771 | 4971.6569 | 4205.6427 | 4205.6427 | 4205.6427 | 4205.6427 | 4205.6427 | 4205.6427 | 4205.6427 | 4205.6427 | 4205.6427 | 4205.6427 | 4205.6427 | 4205.6427 | 4205.6427 | 4205.6427 | 4205.6427 | 4205.6427 |  | 15728.2275 | 21318.8704 | 22846.2875 | 1790.3089 | 1938.592 | 2266.9033 | 3044.1194 | 3467.2069 | 4275.6234 | 6735.6659 | 4704.5565 | 4306.3407 | 4840.7921 | 6011.1831 | 5216.7578 | 5216.7578 | 5216.7578 | 5216.7578 | 5216.7578 | 5216.7578 | 5216.7578 | 5216.7578 | 5216.7578 | 5216.7578 | 5216.7578 | 5216.7578 | 5216.7578 | 5216.7578 | 5216.7578 | 5216.7578
55% | 16350.7821 | 22649.4603 | 24284.7017 |  | 2.8246 | 57.1339 | 426.1445 | 849.6977 | 1547.9343 | 1921.8145 | 2249.8311 | 1639.9485 | 2351.5358 | 3471.0701 | 2618.9274 | 2618.9274 | 2618.9274 | 2618.9274 | 2618.9274 | 2618.9274 | 2618.9274 | 2618.9274 | 2618.9274 | 2618.9274 | 2618.9274 | 2618.9274 | 2618.9274 | 2618.9274 | 2618.9274 | 2618.9274 |  | 17496.6651 | 23715.9042 | 25415.0598 | 246.1412 | 331.4696 | 562.8318 | 1326.8057 | 1797.4641 | 2696.7766 | 5433.4194 | 3173.9377 | 2730.9477 | 3325.4912 | 4627.4777 | 3743.7295 | 3743.7295 | 3743.7295 | 3743.7295 | 3743.7295 | 3743.7295 | 3743.7295 | 3743.7295 | 3743.7295 | 3743.7295 | 3743.7295 | 3743.7295 | 3743.7295 | 3743.7295 | 3743.7295 | 3743.7295
50% | 16573.101 | 22957.4214 | 24614.8968 | [5 empty] | 30.529 | 119.2458 | 243.1596 | 47.0563 | 290.0774 | 1058.252 | 432.145 | 432.145 | 432.145 | 432.145 | 432.145 | 432.145 | 432.145 | 432.145 | 432.145 | 432.145 | 432.145 | 432.145 | 432.145 | 432.145 | 432.145 | 432.145 |  | 17734.5645 | 24038.3655 | 25760.6242 |  |  |  | 5.2896 | 83.4268 | 478.5238 | 3022.0708 | 810.8211 | 499.5863 | 933.2237 | 2205.1709 | 1311.6853 | 1311.6853 | 1311.6853 | 1311.6853 | 1311.6853 | 1311.6853 | 1311.6853 | 1311.6853 | 1311.6853 | 1311.6853 | 1311.6853 | 1311.6853 | 1311.6853 | 1311.6853 | 1311.6853 | 1311.6853
45% | FY25: 12791.4633; FY26: 17719.0143; FY27: 18998.2882 |  | 13687.9049 | 18553.3094 | 19882.5844 | [6 empty] | 326.2222 |  |  |  | 79.4931
40% | FY25: 6284.3875; FY26: 8705.2708; FY27: 9333.7723 |  | 6724.8052 | 9115.1562 | 9768.223
35% | FY25: 2348.7515; FY26: 3253.5419; FY27: 3488.4405 |  | 2513.3549 | 3406.7341 | 3650.8138
30% | FY25: 1171.4214; FY26: 1622.6784; FY27: 1739.8323 |  | 1253.516 | 1699.0818 | 1820.8147
25% | FY25: 690.592; FY26: 956.6232; FY27: 1025.6893 |  | 738.9896 | 1001.6655 | 1073.4311
20% | FY25: 348.989; FY26: 483.4272; FY27: 518.3296 |  | 373.4466 | 506.1893 | 542.4558
15% | FY25: 142.1807; FY26: 196.9518; FY27: 211.1713 |  | 152.1449 | 206.2253 | 221.0005
10% | FY25: 57.2416; FY26: 79.2923; FY27: 85.017 |  | 61.2531 | 83.0258 | 88.9742
5% | FY25: 48.7477; FY26: 67.5263; FY27: 72.4016 |  | 52.164 | 70.7058 | 75.7716
9.992e-14% | FY25: 0; FY26: 0; FY27: 0 |  | 0 | 0 | 0
E @ R (MWh) | 130541.7636 | 180829.3011 | 193884.7798 | 19583.3732 | 20555.4438 | 22293.393 | 26501.2499 | 29488.9982 | 33472.0944 | 35620.7099 | 37551.8361 | 33995.5753 | 38159.0979 | 45095.3641 | 39774.3636 | 39774.3636 | 39774.3636 | 39774.3636 | 39774.3636 | 39774.3636 | 39774.3636 | 39774.3636 | 39774.3636 | 39774.3636 | 39774.3636 | 39774.3636 | 39774.3636 | 39774.3636 | 39774.3636 | 39774.3636 | E @ R (MWh) | 139690.2921 | 189343.6009 | 202909.3599 | 24852.7833 | 25681.9812 | 27560.3346 | 32228.5437 | 34899.7802 | 40249.6535 | 58196.9985 | 43210.8776 | 40458.9821 | 44168.2665 | 52693.0217 | 46851.0183 | 46851.0183 | 46851.0183 | 46851.0183 | 46851.0183 | 46851.0183 | 46851.0183 | 46851.0183 | 46851.0183 | 46851.0183 | 46851.0183 | 46851.0183 | 46851.0183 | 46851.0183 | 46851.0183 | 46851.0183
Option 3 Winter POE50 W E @ R (MWh) N 2 | 91379.2345 | 126580.5108 | 135719.3459 | 13708.3613 | 14388.8107 | 15605.3751 | 18550.8749 | 20642.2988 | 23430.4661 | 24934.4969 | 26286.2852 | 23796.9027 | 26711.3686 | 31566.7548 | 27842.0545 | 27842.0545 | 27842.0545 | 27842.0545 | 27842.0545 | 27842.0545 | 27842.0545 | 27842.0545 | 27842.0545 | 27842.0545 | 27842.0545 | 27842.0545 | 27842.0545 | 27842.0545 | 27842.0545 | 27842.0545 | Option 3 Winter POE10 W E @ R (MWh) N 2 | 41907.0876 | 56803.0803 | 60872.808 | 7455.835 | 7704.5944 | 8268.1004 | 9668.5631 | 10469.9341 | 12074.8961 | 17459.0996 | 12963.2633 | 12137.6946 | 13250.48 | 15807.9065 | 14055.3055 | 14055.3055 | 14055.3055 | 14055.3055 | 14055.3055 | 14055.3055 | 14055.3055 | 14055.3055 | 14055.3055 | 14055.3055 | 14055.3055 | 14055.3055 | 14055.3055 | 14055.3055 | 14055.3055 | 14055.3055
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 94.6719 | 122.4737 | 129.7436 | 61.2344 | 61.2607 | 62.0035 | 63.97 | 65.2829 | 66.5702 | 68.0765 | 69.4698 | 70.8245 | 70.9755 | 72.5573 | 71.351 | 71.351 | 71.351 | 71.351 | 71.351 | 71.351 | 71.351 | 71.351 | 71.351 | 71.351 | 71.351 | 71.351 | 71.351 | 71.351 | 71.351 | 71.351
98% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 46.8602 | 60.6214 | 64.2198 | 29.9674 | 29.9804 | 30.3481 | 31.3215 | 31.9713 | 32.6085 | 33.3541 | 34.0438 | 34.7143 | 34.789 | 35.572 | 34.9749 | 34.9749 | 34.9749 | 34.9749 | 34.9749 | 34.9749 | 34.9749 | 34.9749 | 34.9749 | 34.9749 | 34.9749 | 34.9749 | 34.9749 | 34.9749 | 34.9749 | 34.9749
97% | 20.8131 | 27.6102 | 29.4592 | 12.3872 | 12.3841 | 12.5942 | 12.8249 | 13.2988 | 13.6394 | 13.8238 | 14.0252 | 14.2099 | 14.5441 | 14.9591 | 14.9293 | 14.9293 | 14.9293 | 14.9293 | 14.9293 | 14.9293 | 14.9293 | 14.9293 | 14.9293 | 14.9293 | 14.9293 | 14.9293 | 14.9293 | 14.9293 | 14.9293 | 14.9293 |  | 92.7689 | 120.0119 | 127.1357 | 58.6353 | 58.6611 | 59.389 | 61.3159 | 62.6024 | 63.8639 | 65.3399 | 66.7052 | 68.0327 | 68.1807 | 69.7307 | 68.5486 | 68.5486 | 68.5486 | 68.5486 | 68.5486 | 68.5486 | 68.5486 | 68.5486 | 68.5486 | 68.5486 | 68.5486 | 68.5486 | 68.5486 | 68.5486 | 68.5486 | 68.5486
95% | 102.4643 | 135.9269 | 145.0299 | 59.674 | 59.6588 | 60.6932 | 61.8287 | 64.162 | 65.8388 | 66.7468 | 67.7383 | 68.6472 | 70.2926 | 72.3358 | 72.1891 | 72.1891 | 72.1891 | 72.1891 | 72.1891 | 72.1891 | 72.1891 | 72.1891 | 72.1891 | 72.1891 | 72.1891 | 72.1891 | 72.1891 | 72.1891 | 72.1891 | 72.1891 |  | 137.0126 | 177.2483 | 187.7696 | 85.029 | 85.0671 | 86.1421 | 88.988 | 90.8882 | 92.7512 | 94.9312 | 96.9477 | 98.9082 | 99.1268 | 101.416 | 99.6701 | 99.6701 | 99.6701 | 99.6701 | 99.6701 | 99.6701 | 99.6701 | 99.6701 | 99.6701 | 99.6701 | 99.6701 | 99.6701 | 99.6701 | 99.6701 | 99.6701 | 99.6701
90% | 177.7116 | 235.7483 | 251.5362 | 97.9133 | 97.8869 | 99.681 | 101.6504 | 105.6971 | 108.6054 | 110.1802 | 111.8997 | 113.4762 | 116.33 | 119.8735 | 119.6191 | 119.6191 | 119.6191 | 119.6191 | 119.6191 | 119.6191 | 119.6191 | 119.6191 | 119.6191 | 119.6191 | 119.6191 | 119.6191 | 119.6191 | 119.6191 | 119.6191 | 119.6191 |  | 594.078 | 768.5376 | 814.1574 | 351.9289 | 352.0941 | 356.7553 | 369.095 | 377.3339 | 385.4121 | 394.8642 | 403.6075 | 412.1082 | 413.0559 | 422.9818 | 415.4119 | 415.4119 | 415.4119 | 415.4119 | 415.4119 | 415.4119 | 415.4119 | 415.4119 | 415.4119 | 415.4119 | 415.4119 | 415.4119 | 415.4119 | 415.4119 | 415.4119 | 415.4119
85% | 504.3166 | 669.0154 | 713.8189 | 253.0259 | 252.9509 | 258.0423 | 263.6311 | 275.1149 | 283.3684 | 287.8374 | 292.7171 | 297.1909 | 305.2894 | 315.3454 | 314.6234 | 314.6234 | 314.6234 | 314.6234 | 314.6234 | 314.6234 | 314.6234 | 314.6234 | 314.6234 | 314.6234 | 314.6234 | 314.6234 | 314.6234 | 314.6234 | 314.6234 | 314.6234 |  | 561.9657 | 726.995 | 770.1489 | 308.0696 | 308.2258 | 312.635 | 324.3078 | 332.1012 | 339.7428 | 348.684 | 356.9547 | 364.9959 | 365.8924 | 375.2817 | 368.121 | 368.121 | 368.121 | 368.121 | 368.121 | 368.121 | 368.121 | 368.121 | 368.121 | 368.121 | 368.121 | 368.121 | 368.121 | 368.121 | 368.121 | 368.121
80% | 704.4422 | 934.4978 | 997.0804 | 314.536 | 314.4314 | 321.5432 | 329.3497 | 345.3906 | 356.9192 | 363.1617 | 369.9778 | 376.2269 | 387.5391 | 401.5855 | 400.577 | 400.577 | 400.577 | 400.577 | 400.577 | 400.577 | 400.577 | 400.577 | 400.577 | 400.577 | 400.577 | 400.577 | 400.577 | 400.577 | 400.577 | 400.577 |  | 392.484 | 507.7425 | 537.8818 | 195.7112 | 195.8203 | 198.8998 | 207.0522 | 212.4953 | 217.8322 | 224.0769 | 229.8532 | 235.4693 | 236.0954 | 242.6531 | 237.6519 | 237.6519 | 237.6519 | 237.6519 | 237.6519 | 237.6519 | 237.6519 | 237.6519 | 237.6519 | 237.6519 | 237.6519 | 237.6519 | 237.6519 | 237.6519 | 237.6519 | 237.6519
75% | 1836.3528 | 2436.0657 | 2599.2074 | 705.4576 | 705.1848 | 723.724 | 744.0742 | 785.8898 | 815.9429 | 832.2159 | 849.9842 | 866.2744 | 895.7633 | 932.3798 | 929.7508 | 929.7508 | 929.7508 | 929.7508 | 929.7508 | 929.7508 | 929.7508 | 929.7508 | 929.7508 | 929.7508 | 929.7508 | 929.7508 | 929.7508 | 929.7508 | 929.7508 | 929.7508 |  | 700.5244 | 906.2435 | 960.0375 | 310.1233 | 310.3181 | 315.8145 | 330.3652 | 340.0803 | 349.6059 | 360.7517 | 371.0616 | 381.0855 | 382.203 | 393.9074 | 384.9811 | 384.9811 | 384.9811 | 384.9811 | 384.9811 | 384.9811 | 384.9811 | 384.9811 | 384.9811 | 384.9811 | 384.9811 | 384.9811 | 384.9811 | 384.9811 | 384.9811 | 384.9811
70% | 3172.6584 | 4208.7797 | 4490.6388 | 993.7472 | 993.2758 | 1025.3059 | 1060.4649 | 1132.7095 | 1184.6321 | 1212.7469 | 1243.4451 | 1271.5896 | 1322.5375 | 1385.7996 | 1381.2574 | 1381.2574 | 1381.2574 | 1381.2574 | 1381.2574 | 1381.2574 | 1381.2574 | 1381.2574 | 1381.2574 | 1381.2574 | 1381.2574 | 1381.2574 | 1381.2574 | 1381.2574 | 1381.2574 | 1381.2574 |  | 1276.1675 | 1650.9325 | 1748.9307 | 483.7172 | 484.0719 | 494.0849 | 520.5925 | 538.2908 | 555.6439 | 575.9484 | 594.7305 | 612.9912 | 615.027 | 636.3493 | 620.088 | 620.088 | 620.088 | 620.088 | 620.088 | 620.088 | 620.088 | 620.088 | 620.088 | 620.088 | 620.088 | 620.088 | 620.088 | 620.088 | 620.088 | 620.088
65% | 7968.2023 | 10570.444 | 11278.3393 | 1846.81 | 1845.6263 | 1926.0704 | 2014.373 | 2195.817 | 2326.2218 | 2396.8327 | 2473.9318 | 2544.6175 | 2672.5742 | 2831.4585 | 2820.0507 | 2820.0507 | 2820.0507 | 2820.0507 | 2820.0507 | 2820.0507 | 2820.0507 | 2820.0507 | 2820.0507 | 2820.0507 | 2820.0507 | 2820.0507 | 2820.0507 | 2820.0507 | 2820.0507 | 2820.0507 |  | 1605.6162 | 2077.1285 | 2200.4254 | 491.2298 | 491.676 | 504.2739 | 537.6246 | 559.8917 | 581.7247 | 607.2709 | 630.9016 | 653.8765 | 656.4378 | 683.2646 | 662.8054 | 662.8054 | 662.8054 | 662.8054 | 662.8054 | 662.8054 | 662.8054 | 662.8054 | 662.8054 | 662.8054 | 662.8054 | 662.8054 | 662.8054 | 662.8054 | 662.8054 | 662.8054
60% | 11647.312 | 15451.0709 | 16485.8185 | 1599.0683 | 1597.338 | 1714.9251 | 1843.9992 | 2109.2202 | 2299.836 | 2403.0496 | 2515.7473 | 2619.0702 | 2806.1076 | 3038.3525 | 3021.6775 | 3021.6775 | 3021.6775 | 3021.6775 | 3021.6775 | 3021.6775 | 3021.6775 | 3021.6775 | 3021.6775 | 3021.6775 | 3021.6775 | 3021.6775 | 3021.6775 | 3021.6775 | 3021.6775 | 3021.6775 |  | 2512.492 | 3250.3215 | 3443.2583 | 555.6511 | 556.3494 | 576.0627 | 628.2504 | 663.0943 | 697.2588 | 737.234 | 774.2116 | 810.1631 | 814.1711 | 856.15 | 824.1351 | 824.1351 | 824.1351 | 824.1351 | 824.1351 | 824.1351 | 824.1351 | 824.1351 | 824.1351 | 824.1351 | 824.1351 | 824.1351 | 824.1351 | 824.1351 | 824.1351 | 824.1351
55% | 13170.4015 | 17471.5683 | 18641.6273 | 413.2466 | 411.832 | 513.1119 | 636.1403 | 924.2646 | 1139.8067 | 1256.5173 | 1383.9522 | 1500.7863 | 1712.2821 | 1974.8972 | 1956.0416 | 1956.0416 | 1956.0416 | 1956.0416 | 1956.0416 | 1956.0416 | 1956.0416 | 1956.0416 | 1956.0416 | 1956.0416 | 1956.0416 | 1956.0416 | 1956.0416 | 1956.0416 | 1956.0416 | 1956.0416 |  | 4828.1473 | 6246.0024 | 6616.7608 | 587.1995 | 588.5414 | 626.4237 | 726.7105 | 793.6685 | 859.321 | 936.1395 | 1007.1978 | 1076.2842 | 1083.9862 | 1164.6552 | 1103.1336 | 1103.1336 | 1103.1336 | 1103.1336 | 1103.1336 | 1103.1336 | 1103.1336 | 1103.1336 | 1103.1336 | 1103.1336 | 1103.1336 | 1103.1336 | 1103.1336 | 1103.1336 | 1103.1336 | 1103.1336
50% | 16911.4168 | 22434.3178 | 23936.7286 |  |  |  |  | 3.4281 | 36.6085 | 68.9695 | 115.5831 | 168.4762 | 288.3744 | 479.2895 | 464.0651 | 464.0651 | 464.0651 | 464.0651 | 464.0651 | 464.0651 | 464.0651 | 464.0651 | 464.0651 | 464.0651 | 464.0651 | 464.0651 | 464.0651 | 464.0651 | 464.0651 | 464.0651 |  | 10714.812 | 13861.3711 | 14684.1724 | 191.3668 | 192.9659 | 240.7061 | 390.8095 | 509.6193 | 640.0757 | 807.8717 | 965.5671 | 1118.8862 | 1135.9788 | 1315.0026 | 1178.4715 | 1178.4715 | 1178.4715 | 1178.4715 | 1178.4715 | 1178.4715 | 1178.4715 | 1178.4715 | 1178.4715 | 1178.4715 | 1178.4715 | 1178.4715 | 1178.4715 | 1178.4715 | 1178.4715 | 1178.4715
45% | FY25: 22520.2713; FY26: 29874.9022; FY27: 31875.6039 |  | 16236.3476 | 21004.3853 | 22251.1909 | [6 empty] | 3.1349 | 28.4196 | 76.7087 | 83.5101 | 171.461 | 101.6343 | 101.6343 | 101.6343 | 101.6343 | 101.6343 | 101.6343 | 101.6343 | 101.6343 | 101.6343 | 101.6343 | 101.6343 | 101.6343 | 101.6343 | 101.6343 | 101.6343 | 101.6343
40% | FY25: 15794.9825; FY26: 20953.2804; FY27: 22356.5072 |  | 16811.9908 | 21749.0744 | 23040.0842
35% | FY25: 8189.141; FY26: 10863.5364; FY27: 11591.06 |  | 22897.8708 | 29622.1608 | 31380.5115
30% | FY25: 3808.7911; FY26: 5052.6595; FY27: 5391.0326 |  | 21159.0479 | 27372.7075 | 28997.5323
25% | FY25: 2600.5659; FY26: 3449.8542; FY27: 3680.8886 |  | 6103.1255 | 7895.3963 | 8364.0615
20% | FY25: 1575.389; FY26: 2089.8768; FY27: 2229.8344 |  | 1637.7285 | 2118.6711 | 2244.4339
15% | FY25: 1008.6332; FY26: 1338.0309; FY27: 1427.6379 |  | 903.3078 | 1168.5771 | 1237.943
10% | FY25: 675.0905; FY26: 895.5604; FY27: 955.5354 |  | 211.1088 | 273.1039 | 289.3152
5% | FY25: 480.3015; FY26: 637.1576; FY27: 679.8276 |  | 0 | 0 | 0
9.992e-14% | FY25: 42.1598; FY26: 55.9283; FY27: 59.6738 |  | 0 | 0 | 0
E @ R (MWh) | 112911.4176 | 149785.8315 | 159816.886 | 6295.8662 | 6290.5691 | 6655.6913 | 7068.3364 | 7954.9925 | 8631.4193 | 9012.0818 | 9439.0017 | 9840.5652 | 10591.6343 | 11566.2763 | 11494.7808 | 11494.7808 | 11494.7808 | 11494.7808 | 11494.7808 | 11494.7808 | 11494.7808 | 11494.7808 | 11494.7808 | 11494.7808 | 11494.7808 | 11494.7808 | 11494.7808 | 11494.7808 | 11494.7808 | 11494.7808 | E @ R (MWh) | 109518.1284 | 141679.7064 | 150089.7144 | 3709.8635 | 3715.0322 | 3863.5385 | 4280.4031 | 4577.3201 | 4882.411 | 5257.6779 | 5629.6718 | 6015.0485 | 6059.4299 | 6540.9827 | 6170.9785 | 6170.9785 | 6170.9785 | 6170.9785 | 6170.9785 | 6170.9785 | 6170.9785 | 6170.9785 | 6170.9785 | 6170.9785 | 6170.9785 | 6170.9785 | 6170.9785 | 6170.9785 | 6170.9785 | 6170.9785
Option 3 Summer POE50 W E @ R (MWh) N 2 | 79037.9923 | 104850.082 | 111871.8202 | 4407.1063 | 4403.3984 | 4658.9839 | 4947.8355 | 5568.4947 | 6041.9935 | 6308.4573 | 6607.3012 | 6888.3957 | 7414.144 | 8096.3934 | 8046.3465 | 8046.3465 | 8046.3465 | 8046.3465 | 8046.3465 | 8046.3465 | 8046.3465 | 8046.3465 | 8046.3465 | 8046.3465 | 8046.3465 | 8046.3465 | 8046.3465 | 8046.3465 | 8046.3465 | 8046.3465 | Option 3 Summer POE10 W E @ R (MWh) N 2 | 32855.4385 | 42503.9119 | 45026.9143 | 1112.959 | 1114.5097 | 1159.0616 | 1284.1209 | 1373.196 | 1464.7233 | 1577.3034 | 1688.9015 | 1804.5146 | 1817.829 | 1962.2948 | 1851.2936 | 1851.2936 | 1851.2936 | 1851.2936 | 1851.2936 | 1851.2936 | 1851.2936 | 1851.2936 | 1851.2936 | 1851.2936 | 1851.2936 | 1851.2936 | 1851.2936 | 1851.2936 | 1851.2936 | 1851.2936
Option 4 - 3B OFR 3rd Tx + Switchroom + Two new feeders + OFR12 New Feeder
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | 73.4908 | 101.8011 | 109.1509 | 104.4846 | 105.4532 | 107.1312 | 110.9574 | 113.5132 | 116.7568 | 118.4372 | 119.9115 | 117.1703 | 120.3687 | 125.4005 | 121.5705 | 121.5705 | 121.5705 | 121.5705 | 121.5705 | 121.5705 | 121.5705 | 121.5705 | 121.5705 | 121.5705 | 121.5705 | 121.5705 | 121.5705 | 121.5705 | 121.5705 | 121.5705 |  | 78.6411 | 106.5944 | 114.2314 | 109.4938 | 110.2352 | 111.8768 | 115.7629 | 117.8783 | 121.9204 | 134.2206 | 124.065 | 122.074 | 124.7462 | 130.5982 | 126.6261 | 126.6261 | 126.6261 | 126.6261 | 126.6261 | 126.6261 | 126.6261 | 126.6261 | 126.6261 | 126.6261 | 126.6261 | 126.6261 | 126.6261 | 126.6261 | 126.6261 | 126.6261
98% | 87.3027 | 120.9335 | 129.6647 | 124.1214 | 125.272 | 127.2655 | 131.8107 | 134.8468 | 138.7 | 140.6963 | 142.4477 | 139.1913 | 142.9907 | 148.9683 | 144.4184 | 144.4184 | 144.4184 | 144.4184 | 144.4184 | 144.4184 | 144.4184 | 144.4184 | 144.4184 | 144.4184 | 144.4184 | 144.4184 | 144.4184 | 144.4184 | 144.4184 | 144.4184 |  | 93.4209 | 126.6277 | 135.7001 | 130.072 | 130.9528 | 132.9029 | 137.5193 | 140.0323 | 144.8341 | 159.446 | 147.3818 | 145.0165 | 148.191 | 155.1428 | 150.4241 | 150.4241 | 150.4241 | 150.4241 | 150.4241 | 150.4241 | 150.4241 | 150.4241 | 150.4241 | 150.4241 | 150.4241 | 150.4241 | 150.4241 | 150.4241 | 150.4241 | 150.4241
97% | 172.8327 | 239.4116 | 256.6966 | 245.7225 | 248.0004 | 251.9469 | 260.9451 | 266.9556 | 274.5837 | 278.5358 | 282.003 | 275.5563 | 283.078 | 294.9118 | 285.9044 | 285.9044 | 285.9044 | 285.9044 | 285.9044 | 285.9044 | 285.9044 | 285.9044 | 285.9044 | 285.9044 | 285.9044 | 285.9044 | 285.9044 | 285.9044 | 285.9044 | 285.9044 |  | 184.945 | 250.6842 | 268.6448 | 257.503 | 259.2467 | 263.1072 | 272.2463 | 277.2213 | 286.7273 | 315.6545 | 291.7711 | 287.0885 | 293.373 | 307.1354 | 297.7939 | 297.7939 | 297.7939 | 297.7939 | 297.7939 | 297.7939 | 297.7939 | 297.7939 | 297.7939 | 297.7939 | 297.7939 | 297.7939 | 297.7939 | 297.7939 | 297.7939 | 297.7939
95% | 510.5211 | 707.185 | 758.2422 | 725.8266 | 732.555 | 744.2123 | 770.7917 | 788.5457 | 811.0781 | 822.7518 | 832.9934 | 813.951 | 836.169 | 871.1242 | 844.5177 | 844.5177 | 844.5177 | 844.5177 | 844.5177 | 844.5177 | 844.5177 | 844.5177 | 844.5177 | 844.5177 | 844.5177 | 844.5177 | 844.5177 | 844.5177 | 844.5177 | 844.5177 |  | 546.299 | 740.4826 | 793.5354 | 760.6243 | 765.7748 | 777.1782 | 804.1738 | 818.8692 | 846.9484 | 932.3947 | 861.8468 | 848.0154 | 866.5788 | 907.2308 | 879.6375 | 879.6375 | 879.6375 | 879.6375 | 879.6375 | 879.6375 | 879.6375 | 879.6375 | 879.6375 | 879.6375 | 879.6375 | 879.6375 | 879.6375 | 879.6375 | 879.6375 | 879.6375
90% | 2814.8088 | 3899.1347 | 4180.6436 | 4001.9171 | 4039.0152 | 4103.2883 | 4249.8368 | 4347.7252 | 4471.9597 | 4536.3237 | 4592.7922 | 4487.8001 | 4610.3008 | 4803.0301 | 4656.3326 | 4656.3326 | 4656.3326 | 4656.3326 | 4656.3326 | 4656.3326 | 4656.3326 | 4656.3326 | 4656.3326 | 4656.3326 | 4656.3326 | 4656.3326 | 4656.3326 | 4656.3326 | 4656.3326 | 4656.3326 |  | 3012.0741 | 4082.7244 | 4375.2363 | 4193.778 | 4222.1753 | 4285.0494 | 4433.8921 | 4514.9166 | 4669.7344 | 5140.8511 | 4751.8784 | 4675.617 | 4777.9685 | 5002.1072 | 4849.9688 | 4849.9688 | 4849.9688 | 4849.9688 | 4849.9688 | 4849.9688 | 4849.9688 | 4849.9688 | 4849.9688 | 4849.9688 | 4849.9688 | 4849.9688 | 4849.9688 | 4849.9688 | 4849.9688 | 4849.9688
85% | 6876.3763 | 9525.3066 | 10213.0129 | 9776.3968 | 9867.0247 | 10024.0394 | 10382.0468 | 10621.1813 | 10924.6773 | 11081.9138 | 11219.8623 | 10963.3741 | 11262.6346 | 11733.4585 | 11375.087 | 11375.087 | 11375.087 | 11375.087 | 11375.087 | 11375.087 | 11375.087 | 11375.087 | 11375.087 | 11375.087 | 11375.087 | 11375.087 | 11375.087 | 11375.087 | 11375.087 | 11375.087 |  | 7358.2813 | 9973.8032 | 10688.3888 | 10245.0992 | 10314.4718 | 10468.0688 | 10831.6809 | 11029.6178 | 11407.8267 | 12558.7311 | 11608.4985 | 11422.1975 | 11672.2348 | 12219.7896 | 11848.1263 | 11848.1263 | 11848.1263 | 11848.1263 | 11848.1263 | 11848.1263 | 11848.1263 | 11848.1263 | 11848.1263 | 11848.1263 | 11848.1263 | 11848.1263 | 11848.1263 | 11848.1263 | 11848.1263 | 11848.1263
80% | 10687.9274 | 14805.1503 | 15874.0497 | 15195.4189 | 15336.2815 | 15580.329 | 16136.7785 | 16508.4645 | 16980.1871 | 17224.5794 | 17438.9922 | 17040.3336 | 17505.473 | 18237.273 | 17680.2574 | 17680.2574 | 17680.2574 | 17680.2574 | 17680.2574 | 17680.2574 | 17680.2574 | 17680.2574 | 17680.2574 | 17680.2574 | 17680.2574 | 17680.2574 | 17680.2574 | 17680.2574 | 17680.2574 | 17680.2574 |  | 11436.9506 | 15502.2469 | 16612.9248 | 15923.9214 | 16031.747 | 16270.4822 | 16835.6432 | 17143.2959 | 17731.1447 | 19519.9912 | 18043.048 | 17753.4811 | 18142.1132 | 18993.1757 | 18415.5007 | 18415.5007 | 18415.5007 | 18415.5007 | 18415.5007 | 18415.5007 | 18415.5007 | 18415.5007 | 18415.5007 | 18415.5007 | 18415.5007 | 18415.5007 | 18415.5007 | 18415.5007 | 18415.5007 | 18415.5007
75% | 11791.7667 | 16334.2127 | 17513.507 | 16764.7879 | 16920.1986 | 17189.4511 | 17803.3703 | 18213.4436 | 18733.8853 | 19003.5182 | 19240.0754 | 18800.2436 | 19313.4223 | 20120.8018 | 19506.2582 | 19506.2582 | 19506.2582 | 19506.2582 | 19506.2582 | 19506.2582 | 19506.2582 | 19506.2582 | 19506.2582 | 19506.2582 | 19506.2582 | 19506.2582 | 19506.2582 | 19506.2582 | 19506.2582 | 19506.2582 |  | 12618.1483 | 17103.3048 | 18328.6925 | 17568.5295 | 17687.4912 | 17950.8827 | 18574.4131 | 18913.8398 | 19562.4011 | 21535.998 | 19906.5175 | 19587.0444 | 20015.814 | 20954.7735 | 20317.4368 | 20317.4368 | 20317.4368 | 20317.4368 | 20317.4368 | 20317.4368 | 20317.4368 | 20317.4368 | 20317.4368 | 20317.4368 | 20317.4368 | 20317.4368 | 20317.4368 | 20317.4368 | 20317.4368 | 20317.4368
70% | 12669.5942 | 17550.1984 | 18817.2842 | 18012.8274 | 18179.8075 | 18469.1043 | 19128.7261 | 19569.327 | 20128.5125 | 20418.2179 | 20672.3854 | 20199.8108 | 20751.1925 | 21618.6767 | 20958.384 | 20958.384 | 20958.384 | 20958.384 | 20958.384 | 20958.384 | 20958.384 | 20958.384 | 20958.384 | 20958.384 | 20958.384 | 20958.384 | 20958.384 | 20958.384 | 20958.384 | 20958.384 |  | 13557.495 | 18376.5449 | 19693.1554 | 18876.4028 | 19004.2205 | 19287.2199 | 19957.1685 | 20321.8635 | 21018.7063 | 23139.2259 | 21388.4402 | 21045.1842 | 21505.8732 | 22514.7326 | 21829.95 | 21829.95 | 21829.95 | 21829.95 | 21829.95 | 21829.95 | 21829.95 | 21829.95 | 21829.95 | 21829.95 | 21829.95 | 21829.95 | 21829.95 | 21829.95 | 21829.95 | 21829.95
65% | 13351.323 | 18494.5441 | 19829.8096 | 18982.0663 | 19158.0314 | 19462.8946 | 20158.0096 | 20622.3184 | 21211.5928 | 21516.8867 | 21784.7305 | 21286.7275 | 21867.7781 | 22781.9401 | 22086.1182 | 22086.1182 | 22086.1182 | 22086.1182 | 22086.1182 | 22086.1182 | 22086.1182 | 22086.1182 | 22086.1182 | 22086.1182 | 22086.1182 | 22086.1182 | 22086.1182 | 22086.1182 | 22086.1182 | 22086.1182 |  | 14287.0002 | 19365.3548 | 20752.8099 | 19892.1092 | 20026.8045 | 20325.0317 | 21031.029 | 21415.3477 | 22149.6864 | 24384.3074 | 22539.315 | 22177.589 | 22663.0669 | 23726.2112 | 23004.5816 | 23004.5816 | 23004.5816 | 23004.5816 | 23004.5816 | 23004.5816 | 23004.5816 | 23004.5816 | 23004.5816 | 23004.5816 | 23004.5816 | 23004.5816 | 23004.5816 | 23004.5816 | 23004.5816 | 23004.5816
60% | 14698.1621 | 20360.2151 | 21830.1779 | 20896.9169 | 21090.6328 | 21426.2497 | 22191.4856 | 22702.6325 | 23351.351 | 23687.442 | 23982.305 | 23434.065 | 24073.7302 | 25080.11 | 24314.0958 | 24314.0958 | 24314.0958 | 24314.0958 | 24314.0958 | 24314.0958 | 24314.0958 | 24314.0958 | 24314.0958 | 24314.0958 | 24314.0958 | 24314.0958 | 24314.0958 | 24314.0958 | 24314.0958 | 24314.0958 |  | 15728.2275 | 21318.8704 | 22846.2875 | 21898.7621 | 22047.0451 | 22375.3564 | 23152.5725 | 23575.66 | 24384.0765 | 26844.119 | 24813.0096 | 24414.7938 | 24949.2452 | 26119.6362 | 25325.2109 | 25325.2109 | 25325.2109 | 25325.2109 | 25325.2109 | 25325.2109 | 25325.2109 | 25325.2109 | 25325.2109 | 25325.2109 | 25325.2109 | 25325.2109 | 25325.2109 | 25325.2109 | 25325.2109 | 25325.2109
55% | 16350.7821 | 22649.4603 | 24284.7017 | 23246.5075 | 23462.0042 | 23835.357 | 24686.6338 | 25255.2526 | 25976.9112 | 26350.7914 | 26678.8079 | 26068.9254 | 26780.5127 | 27900.047 | 27047.9043 | 27047.9043 | 27047.9043 | 27047.9043 | 27047.9043 | 27047.9043 | 27047.9043 | 27047.9043 | 27047.9043 | 27047.9043 | 27047.9043 | 27047.9043 | 27047.9043 | 27047.9043 | 27047.9043 | 27047.9043 |  | 17496.6651 | 23715.9042 | 25415.0598 | 24360.9972 | 24525.9528 | 24891.1785 | 25755.7826 | 26226.4409 | 27125.7534 | 29862.3962 | 27602.9146 | 27159.9245 | 27754.4681 | 29056.4546 | 28172.7063 | 28172.7063 | 28172.7063 | 28172.7063 | 28172.7063 | 28172.7063 | 28172.7063 | 28172.7063 | 28172.7063 | 28172.7063 | 28172.7063 | 28172.7063 | 28172.7063 | 28172.7063 | 28172.7063 | 28172.7063
50% | 16573.101 | 22957.4214 | 24614.8968 | 23562.5865 | 23781.0133 | 24159.4424 | 25022.294 | 25598.6442 | 26330.115 | 26709.0788 | 27041.5553 | 26423.3803 | 27144.643 | 28279.3994 | 27415.6703 | 27415.6703 | 27415.6703 | 27415.6703 | 27415.6703 | 27415.6703 | 27415.6703 | 27415.6703 | 27415.6703 | 27415.6703 | 27415.6703 | 27415.6703 | 27415.6703 | 27415.6703 | 27415.6703 | 27415.6703 |  | 17734.5645 | 24038.3655 | 25760.6242 | 24692.2298 | 24859.4282 | 25229.6198 | 26105.9798 | 26583.0376 | 27494.5779 | 30268.4304 | 27978.227 | 27529.2136 | 28131.8411 | 29451.5305 | 28555.7661 | 28555.7661 | 28555.7661 | 28555.7661 | 28555.7661 | 28555.7661 | 28555.7661 | 28555.7661 | 28555.7661 | 28555.7661 | 28555.7661 | 28555.7661 | 28555.7661 | 28555.7661 | 28555.7661 | 28555.7661
45% | 12791.4633 | 17719.0143 | 18998.2882 | 18186.0933 | 18354.6796 | 18646.7591 | 19312.7258 | 19757.5649 | 20322.1292 | 20614.6213 | 20871.2336 | 20394.1133 | 20950.7988 | 21826.6274 | 21159.9833 | 21159.9833 | 21159.9833 | 21159.9833 | 21159.9833 | 21159.9833 | 21159.9833 | 21159.9833 | 21159.9833 | 21159.9833 | 21159.9833 | 21159.9833 | 21159.9833 | 21159.9833 | 21159.9833 | 21159.9833 |  | 13687.9049 | 18553.3094 | 19882.5844 | 19057.9754 | 19187.0226 | 19472.7442 | 20149.137 | 20517.3401 | 21220.8859 | 23361.8028 | 21594.1762 | 21247.6184 | 21712.7388 | 22731.3025 | 22039.9329 | 22039.9329 | 22039.9329 | 22039.9329 | 22039.9329 | 22039.9329 | 22039.9329 | 22039.9329 | 22039.9329 | 22039.9329 | 22039.9329 | 22039.9329 | 22039.9329 | 22039.9329 | 22039.9329 | 22039.9329
40% | 6284.3875 | 8705.2708 | 9333.7723 | 8934.7446 | 9017.5703 | 9161.0676 | 9488.254 | 9706.8014 | 9984.1693 | 10127.8694 | 10253.9418 | 10019.5348 | 10293.0318 | 10723.3224 | 10395.8032 | 10395.8032 | 10395.8032 | 10395.8032 | 10395.8032 | 10395.8032 | 10395.8032 | 10395.8032 | 10395.8032 | 10395.8032 | 10395.8032 | 10395.8032 | 10395.8032 | 10395.8032 | 10395.8032 | 10395.8032 |  | 6724.8052 | 9115.1562 | 9768.223 | 9363.0963 | 9426.4966 | 9566.8704 | 9899.179 | 10080.0756 | 10425.7244 | 11477.5471 | 10609.1202 | 10438.8579 | 10667.3695 | 11167.7852 | 10828.1184 | 10828.1184 | 10828.1184 | 10828.1184 | 10828.1184 | 10828.1184 | 10828.1184 | 10828.1184 | 10828.1184 | 10828.1184 | 10828.1184 | 10828.1184 | 10828.1184 | 10828.1184 | 10828.1184 | 10828.1184
35% | 2348.7515 | 3253.5419 | 3488.4405 | 3339.3063 | 3370.2619 | 3423.8932 | 3546.1771 | 3627.8579 | 3731.5224 | 3785.2294 | 3832.3482 | 3744.74 | 3846.9579 | 4007.7764 | 3885.3681 | 3885.3681 | 3885.3681 | 3885.3681 | 3885.3681 | 3885.3681 | 3885.3681 | 3885.3681 | 3885.3681 | 3885.3681 | 3885.3681 | 3885.3681 | 3885.3681 | 3885.3681 | 3885.3681 | 3885.3681 |  | 2513.3549 | 3406.7341 | 3650.8138 | 3499.4002 | 3523.0956 | 3575.5595 | 3699.7578 | 3767.3668 | 3896.5509 | 4289.6632 | 3965.094 | 3901.4595 | 3986.8643 | 4173.8916 | 4046.9432 | 4046.9432 | 4046.9432 | 4046.9432 | 4046.9432 | 4046.9432 | 4046.9432 | 4046.9432 | 4046.9432 | 4046.9432 | 4046.9432 | 4046.9432 | 4046.9432 | 4046.9432 | 4046.9432 | 4046.9432
30% | 1171.4214 | 1622.6784 | 1739.8323 | 1665.4528 | 1680.8916 | 1707.6398 | 1768.628 | 1809.3656 | 1861.0675 | 1887.8534 | 1911.3536 | 1867.6597 | 1918.64 | 1998.847 | 1937.7968 | 1937.7968 | 1937.7968 | 1937.7968 | 1937.7968 | 1937.7968 | 1937.7968 | 1937.7968 | 1937.7968 | 1937.7968 | 1937.7968 | 1937.7968 | 1937.7968 | 1937.7968 | 1937.7968 | 1937.7968 |  | 1253.516 | 1699.0818 | 1820.8147 | 1745.2983 | 1757.1163 | 1783.2822 | 1845.2251 | 1878.9446 | 1943.3741 | 2139.4358 | 1977.5595 | 1945.8223 | 1988.4172 | 2081.6956 | 2018.3811 | 2018.3811 | 2018.3811 | 2018.3811 | 2018.3811 | 2018.3811 | 2018.3811 | 2018.3811 | 2018.3811 | 2018.3811 | 2018.3811 | 2018.3811 | 2018.3811 | 2018.3811 | 2018.3811 | 2018.3811
25% | 690.592 | 956.6232 | 1025.6893 | 981.8401 | 990.9418 | 1006.7107 | 1042.6653 | 1066.6815 | 1097.1615 | 1112.9527 | 1126.8068 | 1101.0478 | 1131.1024 | 1178.3871 | 1142.396 | 1142.396 | 1142.396 | 1142.396 | 1142.396 | 1142.396 | 1142.396 | 1142.396 | 1142.396 | 1142.396 | 1142.396 | 1142.396 | 1142.396 | 1142.396 | 1142.396 | 1142.396 |  | 738.9896 | 1001.6655 | 1073.4311 | 1028.9117 | 1035.8788 | 1051.3044 | 1087.8219 | 1107.7006 | 1145.684 | 1261.2689 | 1165.8374 | 1147.1272 | 1172.2384 | 1227.2291 | 1189.9031 | 1189.9031 | 1189.9031 | 1189.9031 | 1189.9031 | 1189.9031 | 1189.9031 | 1189.9031 | 1189.9031 | 1189.9031 | 1189.9031 | 1189.9031 | 1189.9031 | 1189.9031 | 1189.9031 | 1189.9031
20% | 348.989 | 483.4272 | 518.3296 | 496.1705 | 500.7701 | 508.7388 | 526.9084 | 539.0449 | 554.4479 | 562.428 | 569.4291 | 556.4118 | 571.5999 | 595.4951 | 577.307 | 577.307 | 577.307 | 577.307 | 577.307 | 577.307 | 577.307 | 577.307 | 577.307 | 577.307 | 577.307 | 577.307 | 577.307 | 577.307 | 577.307 | 577.307 |  | 373.4466 | 506.1893 | 542.4558 | 519.958 | 523.4788 | 531.2742 | 549.7282 | 559.7738 | 578.9687 | 637.3792 | 589.1531 | 579.698 | 592.3879 | 620.1773 | 601.3147 | 601.3147 | 601.3147 | 601.3147 | 601.3147 | 601.3147 | 601.3147 | 601.3147 | 601.3147 | 601.3147 | 601.3147 | 601.3147 | 601.3147 | 601.3147 | 601.3147 | 601.3147
15% | 142.1807 | 196.9518 | 211.1713 | 202.1435 | 204.0174 | 207.264 | 214.6664 | 219.6109 | 225.8862 | 229.1373 | 231.9896 | 226.6863 | 232.874 | 242.6091 | 235.1992 | 235.1992 | 235.1992 | 235.1992 | 235.1992 | 235.1992 | 235.1992 | 235.1992 | 235.1992 | 235.1992 | 235.1992 | 235.1992 | 235.1992 | 235.1992 | 235.1992 | 235.1992 |  | 152.1449 | 206.2253 | 221.0005 | 211.8348 | 213.2692 | 216.445 | 223.9633 | 228.056 | 235.8761 | 259.673 | 240.0253 | 236.1733 | 241.3432 | 252.6648 | 244.9801 | 244.9801 | 244.9801 | 244.9801 | 244.9801 | 244.9801 | 244.9801 | 244.9801 | 244.9801 | 244.9801 | 244.9801 | 244.9801 | 244.9801 | 244.9801 | 244.9801 | 244.9801
10% | 57.2416 | 79.2923 | 85.017 | 81.3825 | 82.1369 | 83.4439 | 86.4241 | 88.4148 | 90.9412 | 92.2501 | 93.3984 | 91.2633 | 93.7545 | 97.6738 | 94.6906 | 94.6906 | 94.6906 | 94.6906 | 94.6906 | 94.6906 | 94.6906 | 94.6906 | 94.6906 | 94.6906 | 94.6906 | 94.6906 | 94.6906 | 94.6906 | 94.6906 | 94.6906 |  | 61.2531 | 83.0258 | 88.9742 | 85.2841 | 85.8616 | 87.1402 | 90.1671 | 91.8148 | 94.9631 | 104.5437 | 96.6336 | 95.0827 | 97.1641 | 101.7222 | 98.6283 | 98.6283 | 98.6283 | 98.6283 | 98.6283 | 98.6283 | 98.6283 | 98.6283 | 98.6283 | 98.6283 | 98.6283 | 98.6283 | 98.6283 | 98.6283 | 98.6283 | 98.6283
5% | 48.7477 | 67.5263 | 72.4016 | 69.3064 | 69.9488 | 71.0619 | 73.5999 | 75.2952 | 77.4467 | 78.5614 | 79.5393 | 77.721 | 79.8425 | 83.1803 | 80.6397 | 80.6397 | 80.6397 | 80.6397 | 80.6397 | 80.6397 | 80.6397 | 80.6397 | 80.6397 | 80.6397 | 80.6397 | 80.6397 | 80.6397 | 80.6397 | 80.6397 | 80.6397 |  | 52.164 | 70.7058 | 75.7716 | 72.6291 | 73.1209 | 74.2097 | 76.7874 | 78.1906 | 80.8718 | 89.0307 | 82.2944 | 80.9737 | 82.7462 | 86.6279 | 83.9932 | 83.9932 | 83.9932 | 83.9932 | 83.9932 | 83.9932 | 83.9932 | 83.9932 | 83.9932 | 83.9932 | 83.9932 | 83.9932 | 83.9932 | 83.9932 | 83.9932 | 83.9932
9.992e-14% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E @ R (MWh) | 130541.7636 | 180829.3011 | 193884.7798 | 185596.0204 | 187316.5085 | 190297.2908 | 197093.7355 | 201633.4875 | 207395.0823 | 210380.0759 | 212998.9024 | 208129.7076 | 213810.8955 | 222749.06 | 215945.7027 | 215945.7027 | 215945.7027 | 215945.7027 | 215945.7027 | 215945.7027 | 215945.7027 | 215945.7027 | 215945.7027 | 215945.7027 | 215945.7027 | 215945.7027 | 215945.7027 | 215945.7027 | 215945.7027 | 215945.7027 | E @ R (MWh) | 139690.2921 | 189343.6009 | 202909.3599 | 194493.9102 | 195810.8861 | 198726.7842 | 205629.6308 | 209387.2839 | 216567.2367 | 238416.1104 | 220376.8073 | 216840.0526 | 221586.7837 | 231981.6146 | 224925.9242 | 224925.9242 | 224925.9242 | 224925.9242 | 224925.9242 | 224925.9242 | 224925.9242 | 224925.9242 | 224925.9242 | 224925.9242 | 224925.9242 | 224925.9242 | 224925.9242 | 224925.9242 | 224925.9242 | 224925.9242
Option 4 Winter POE50 W E @ R (MWh) N 2 | 91379.2345 | 126580.5108 | 135719.3459 | 129917.2143 | 131121.5559 | 133208.1036 | 137965.6148 | 141143.4413 | 145176.5576 | 147266.0531 | 149099.2317 | 145690.7953 | 149667.6268 | 155924.342 | 151161.9919 | 151161.9919 | 151161.9919 | 151161.9919 | 151161.9919 | 151161.9919 | 151161.9919 | 151161.9919 | 151161.9919 | 151161.9919 | 151161.9919 | 151161.9919 | 151161.9919 | 151161.9919 | 151161.9919 | 151161.9919 | Option 4 Winter POE10 W E @ R (MWh) N 2 | 41907.0876 | 56803.0803 | 60872.808 | 58348.1731 | 58743.2658 | 59618.0353 | 61688.8892 | 62816.1852 | 64970.171 | 71524.8331 | 66113.0422 | 65052.0158 | 66476.0351 | 69594.4844 | 67477.7773 | 67477.7773 | 67477.7773 | 67477.7773 | 67477.7773 | 67477.7773 | 67477.7773 | 67477.7773 | 67477.7773 | 67477.7773 | 67477.7773 | 67477.7773 | 67477.7773 | 67477.7773 | 67477.7773 | 67477.7773
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 94.6719 | 122.4737 | 129.7436 | 123.2836 | 123.3099 | 124.0527 | 126.0192 | 127.3321 | 128.6194 | 130.1257 | 131.519 | 132.8737 | 133.0247 | 134.6065 | 133.4002 | 133.4002 | 133.4002 | 133.4002 | 133.4002 | 133.4002 | 133.4002 | 133.4002 | 133.4002 | 133.4002 | 133.4002 | 133.4002 | 133.4002 | 133.4002 | 133.4002 | 133.4002
98% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 46.8602 | 60.6214 | 64.2198 | 61.0223 | 61.0353 | 61.403 | 62.3763 | 63.0262 | 63.6634 | 64.409 | 65.0986 | 65.7691 | 65.8439 | 66.6268 | 66.0297 | 66.0297 | 66.0297 | 66.0297 | 66.0297 | 66.0297 | 66.0297 | 66.0297 | 66.0297 | 66.0297 | 66.0297 | 66.0297 | 66.0297 | 66.0297 | 66.0297 | 66.0297
97% | 20.8131 | 27.6102 | 29.4592 | 27.9297 | 27.9266 | 28.1368 | 28.3674 | 28.8413 | 29.182 | 29.3664 | 29.5678 | 29.7524 | 30.0866 | 30.5017 | 30.4719 | 30.4719 | 30.4719 | 30.4719 | 30.4719 | 30.4719 | 30.4719 | 30.4719 | 30.4719 | 30.4719 | 30.4719 | 30.4719 | 30.4719 | 30.4719 | 30.4719 | 30.4719 |  | 92.7689 | 120.0119 | 127.1357 | 120.8055 | 120.8313 | 121.5592 | 123.4861 | 124.7727 | 126.0341 | 127.5101 | 128.8754 | 130.2029 | 130.3509 | 131.9009 | 130.7188 | 130.7188 | 130.7188 | 130.7188 | 130.7188 | 130.7188 | 130.7188 | 130.7188 | 130.7188 | 130.7188 | 130.7188 | 130.7188 | 130.7188 | 130.7188 | 130.7188 | 130.7188
95% | 102.4643 | 135.9269 | 145.0299 | 137.5002 | 137.485 | 138.5194 | 139.6549 | 141.9882 | 143.6651 | 144.5731 | 145.5645 | 146.4734 | 148.1189 | 150.162 | 150.0153 | 150.0153 | 150.0153 | 150.0153 | 150.0153 | 150.0153 | 150.0153 | 150.0153 | 150.0153 | 150.0153 | 150.0153 | 150.0153 | 150.0153 | 150.0153 | 150.0153 | 150.0153 |  | 137.0126 | 177.2483 | 187.7696 | 178.4205 | 178.4585 | 179.5336 | 182.3795 | 184.2796 | 186.1427 | 188.3226 | 190.3391 | 192.2996 | 192.5182 | 194.8074 | 193.0616 | 193.0616 | 193.0616 | 193.0616 | 193.0616 | 193.0616 | 193.0616 | 193.0616 | 193.0616 | 193.0616 | 193.0616 | 193.0616 | 193.0616 | 193.0616 | 193.0616 | 193.0616
90% | 177.7116 | 235.7483 | 251.5362 | 238.477 | 238.4506 | 240.2447 | 242.214 | 246.2607 | 249.1691 | 250.7439 | 252.4634 | 254.0399 | 256.8936 | 260.4372 | 260.1827 | 260.1827 | 260.1827 | 260.1827 | 260.1827 | 260.1827 | 260.1827 | 260.1827 | 260.1827 | 260.1827 | 260.1827 | 260.1827 | 260.1827 | 260.1827 | 260.1827 | 260.1827 |  | 594.078 | 768.5376 | 814.1574 | 773.6199 | 773.7851 | 778.4463 | 790.786 | 799.0249 | 807.103 | 816.5552 | 825.2985 | 833.7992 | 834.7469 | 844.6728 | 837.1029 | 837.1029 | 837.1029 | 837.1029 | 837.1029 | 837.1029 | 837.1029 | 837.1029 | 837.1029 | 837.1029 | 837.1029 | 837.1029 | 837.1029 | 837.1029 | 837.1029 | 837.1029
85% | 504.3166 | 669.0154 | 713.8189 | 676.7589 | 676.684 | 681.7754 | 687.3642 | 698.848 | 707.1015 | 711.5705 | 716.4502 | 720.924 | 729.0225 | 739.0785 | 738.3564 | 738.3564 | 738.3564 | 738.3564 | 738.3564 | 738.3564 | 738.3564 | 738.3564 | 738.3564 | 738.3564 | 738.3564 | 738.3564 | 738.3564 | 738.3564 | 738.3564 | 738.3564 |  | 561.9657 | 726.995 | 770.1489 | 731.8026 | 731.9588 | 736.3681 | 748.0408 | 755.8343 | 763.4759 | 772.417 | 780.6878 | 788.729 | 789.6255 | 799.0148 | 791.8541 | 791.8541 | 791.8541 | 791.8541 | 791.8541 | 791.8541 | 791.8541 | 791.8541 | 791.8541 | 791.8541 | 791.8541 | 791.8541 | 791.8541 | 791.8541 | 791.8541 | 791.8541
80% | 704.4422 | 934.4978 | 997.0804 | 945.3141 | 945.2094 | 952.3212 | 960.1278 | 976.1686 | 987.6973 | 993.9397 | 1000.7558 | 1007.0049 | 1018.3171 | 1032.3636 | 1031.355 | 1031.355 | 1031.355 | 1031.355 | 1031.355 | 1031.355 | 1031.355 | 1031.355 | 1031.355 | 1031.355 | 1031.355 | 1031.355 | 1031.355 | 1031.355 | 1031.355 | 1031.355 |  | 392.484 | 507.7425 | 537.8818 | 511.1003 | 511.2093 | 514.2888 | 522.4412 | 527.8843 | 533.2212 | 539.4659 | 545.2423 | 550.8583 | 551.4844 | 558.0421 | 553.041 | 553.041 | 553.041 | 553.041 | 553.041 | 553.041 | 553.041 | 553.041 | 553.041 | 553.041 | 553.041 | 553.041 | 553.041 | 553.041 | 553.041 | 553.041
75% | 1836.3528 | 2436.0657 | 2599.2074 | 2464.2619 | 2463.9891 | 2482.5283 | 2502.8785 | 2544.6941 | 2574.7472 | 2591.0202 | 2608.7885 | 2625.0787 | 2654.5676 | 2691.1841 | 2688.555 | 2688.555 | 2688.555 | 2688.555 | 2688.555 | 2688.555 | 2688.555 | 2688.555 | 2688.555 | 2688.555 | 2688.555 | 2688.555 | 2688.555 | 2688.555 | 2688.555 | 2688.555 |  | 700.5244 | 906.2435 | 960.0375 | 912.2365 | 912.4312 | 917.9276 | 932.4784 | 942.1935 | 951.7191 | 962.8648 | 973.1748 | 983.1987 | 984.3162 | 996.0206 | 987.0943 | 987.0943 | 987.0943 | 987.0943 | 987.0943 | 987.0943 | 987.0943 | 987.0943 | 987.0943 | 987.0943 | 987.0943 | 987.0943 | 987.0943 | 987.0943 | 987.0943 | 987.0943
70% | 3172.6584 | 4208.7797 | 4490.6388 | 4257.494 | 4257.0227 | 4289.0527 | 4324.2117 | 4396.4564 | 4448.379 | 4476.4937 | 4507.1919 | 4535.3365 | 4586.2843 | 4649.5465 | 4645.0043 | 4645.0043 | 4645.0043 | 4645.0043 | 4645.0043 | 4645.0043 | 4645.0043 | 4645.0043 | 4645.0043 | 4645.0043 | 4645.0043 | 4645.0043 | 4645.0043 | 4645.0043 | 4645.0043 | 4645.0043 |  | 1276.1675 | 1650.9325 | 1748.9307 | 1661.8502 | 1662.2049 | 1672.2179 | 1698.7255 | 1716.4238 | 1733.7769 | 1754.0815 | 1772.8635 | 1791.1243 | 1793.16 | 1814.4823 | 1798.2211 | 1798.2211 | 1798.2211 | 1798.2211 | 1798.2211 | 1798.2211 | 1798.2211 | 1798.2211 | 1798.2211 | 1798.2211 | 1798.2211 | 1798.2211 | 1798.2211 | 1798.2211 | 1798.2211 | 1798.2211
65% | 7968.2023 | 10570.444 | 11278.3393 | 10692.7911 | 10691.6074 | 10772.0515 | 10860.3541 | 11041.7981 | 11172.2029 | 11242.8138 | 11319.9129 | 11390.5986 | 11518.5553 | 11677.4396 | 11666.0318 | 11666.0318 | 11666.0318 | 11666.0318 | 11666.0318 | 11666.0318 | 11666.0318 | 11666.0318 | 11666.0318 | 11666.0318 | 11666.0318 | 11666.0318 | 11666.0318 | 11666.0318 | 11666.0318 | 11666.0318 |  | 1605.6162 | 2077.1285 | 2200.4254 | 2090.8647 | 2091.311 | 2103.9088 | 2137.2595 | 2159.5266 | 2181.3596 | 2206.9058 | 2230.5365 | 2253.5114 | 2256.0727 | 2282.8995 | 2262.4403 | 2262.4403 | 2262.4403 | 2262.4403 | 2262.4403 | 2262.4403 | 2262.4403 | 2262.4403 | 2262.4403 | 2262.4403 | 2262.4403 | 2262.4403 | 2262.4403 | 2262.4403 | 2262.4403 | 2262.4403
60% | 11647.312 | 15451.0709 | 16485.8185 | 15629.9087 | 15628.1784 | 15745.7655 | 15874.8395 | 16140.0606 | 16330.6764 | 16433.89 | 16546.5876 | 16649.9105 | 16836.9479 | 17069.1929 | 17052.5178 | 17052.5178 | 17052.5178 | 17052.5178 | 17052.5178 | 17052.5178 | 17052.5178 | 17052.5178 | 17052.5178 | 17052.5178 | 17052.5178 | 17052.5178 | 17052.5178 | 17052.5178 | 17052.5178 | 17052.5178 |  | 2512.492 | 3250.3215 | 3443.2583 | 3271.816 | 3272.5144 | 3292.2277 | 3344.4154 | 3379.2593 | 3413.4238 | 3453.399 | 3490.3766 | 3526.328 | 3530.3361 | 3572.3149 | 3540.3001 | 3540.3001 | 3540.3001 | 3540.3001 | 3540.3001 | 3540.3001 | 3540.3001 | 3540.3001 | 3540.3001 | 3540.3001 | 3540.3001 | 3540.3001 | 3540.3001 | 3540.3001 | 3540.3001 | 3540.3001
55% | 13170.4015 | 17471.5683 | 18641.6273 | 17673.7923 | 17671.8357 | 17804.7994 | 17950.7521 | 18250.6554 | 18466.1976 | 18582.9081 | 18710.343 | 18827.1772 | 19038.673 | 19301.288 | 19282.4324 | 19282.4324 | 19282.4324 | 19282.4324 | 19282.4324 | 19282.4324 | 19282.4324 | 19282.4324 | 19282.4324 | 19282.4324 | 19282.4324 | 19282.4324 | 19282.4324 | 19282.4324 | 19282.4324 | 19282.4324 |  | 4828.1473 | 6246.0024 | 6616.7608 | 6287.3075 | 6288.6495 | 6326.5317 | 6426.8186 | 6493.7766 | 6559.4291 | 6636.2476 | 6707.3059 | 6776.3923 | 6784.0943 | 6864.7633 | 6803.2417 | 6803.2417 | 6803.2417 | 6803.2417 | 6803.2417 | 6803.2417 | 6803.2417 | 6803.2417 | 6803.2417 | 6803.2417 | 6803.2417 | 6803.2417 | 6803.2417 | 6803.2417 | 6803.2417 | 6803.2417
50% | 16911.4168 | 22434.3178 | 23936.7286 | 22693.9829 | 22691.4705 | 22862.2022 | 23049.6124 | 23434.7024 | 23711.4686 | 23861.3305 | 24024.9629 | 24174.9835 | 24446.5541 | 24783.7642 | 24759.5527 | 24759.5527 | 24759.5527 | 24759.5527 | 24759.5527 | 24759.5527 | 24759.5527 | 24759.5527 | 24759.5527 | 24759.5527 | 24759.5527 | 24759.5527 | 24759.5527 | 24759.5527 | 24759.5527 | 24759.5527 |  | 10714.812 | 13861.3711 | 14684.1724 | 13953.037 | 13956.0151 | 14040.0849 | 14262.6453 | 14411.2412 | 14556.9397 | 14727.4183 | 14885.1137 | 15038.4328 | 15055.5255 | 15234.5492 | 15098.0181 | 15098.0181 | 15098.0181 | 15098.0181 | 15098.0181 | 15098.0181 | 15098.0181 | 15098.0181 | 15098.0181 | 15098.0181 | 15098.0181 | 15098.0181 | 15098.0181 | 15098.0181 | 15098.0181 | 15098.0181
45% | 22520.2713 | 29874.9022 | 31875.6039 | 30220.6881 | 30217.3425 | 30444.6991 | 30694.2659 | 31207.0752 | 31575.634 | 31775.1992 | 31993.102 | 32192.8786 | 32554.5185 | 33003.5679 | 32971.3265 | 32971.3265 | 32971.3265 | 32971.3265 | 32971.3265 | 32971.3265 | 32971.3265 | 32971.3265 | 32971.3265 | 32971.3265 | 32971.3265 | 32971.3265 | 32971.3265 | 32971.3265 | 32971.3265 | 32971.3265 |  | 16236.3476 | 21004.3853 | 22251.1909 | 21143.2883 | 21147.8012 | 21275.1935 | 21612.4433 | 21837.6134 | 22058.3929 | 22316.7223 | 22555.6809 | 22788.0081 | 22813.909 | 23085.1869 | 22878.2989 | 22878.2989 | 22878.2989 | 22878.2989 | 22878.2989 | 22878.2989 | 22878.2989 | 22878.2989 | 22878.2989 | 22878.2989 | 22878.2989 | 22878.2989 | 22878.2989 | 22878.2989 | 22878.2989 | 22878.2989
40% | 15794.9825 | 20953.2804 | 22356.5072 | 21195.8033 | 21193.4568 | 21352.9174 | 21527.9554 | 21887.623 | 22146.1181 | 22286.0866 | 22438.9166 | 22579.0333 | 22832.6757 | 23147.6244 | 23125.0112 | 23125.0112 | 23125.0112 | 23125.0112 | 23125.0112 | 23125.0112 | 23125.0112 | 23125.0112 | 23125.0112 | 23125.0112 | 23125.0112 | 23125.0112 | 23125.0112 | 23125.0112 | 23125.0112 | 23125.0112 |  | 16811.9908 | 21749.0744 | 23040.0842 | 21892.902 | 21897.5749 | 22029.4838 | 22378.6904 | 22611.8437 | 22840.4508 | 23107.9389 | 23355.3696 | 23595.9337 | 23622.7528 | 23903.6487 | 23689.4256 | 23689.4256 | 23689.4256 | 23689.4256 | 23689.4256 | 23689.4256 | 23689.4256 | 23689.4256 | 23689.4256 | 23689.4256 | 23689.4256 | 23689.4256 | 23689.4256 | 23689.4256 | 23689.4256 | 23689.4256
35% | 8189.141 | 10863.5364 | 11591.06 | 10989.276 | 10988.0594 | 11070.7341 | 11161.4851 | 11347.9601 | 11481.9807 | 11554.5494 | 11633.7864 | 11706.4319 | 11837.9366 | 12001.2263 | 11989.5022 | 11989.5022 | 11989.5022 | 11989.5022 | 11989.5022 | 11989.5022 | 11989.5022 | 11989.5022 | 11989.5022 | 11989.5022 | 11989.5022 | 11989.5022 | 11989.5022 | 11989.5022 | 11989.5022 | 11989.5022 |  | 22897.8708 | 29622.1608 | 31380.5115 | 29818.0536 | 29824.418 | 30004.0774 | 30479.6956 | 30797.2495 | 31108.6115 | 31472.9295 | 31809.9291 | 32137.5766 | 32174.1041 | 32556.6832 | 32264.9122 | 32264.9122 | 32264.9122 | 32264.9122 | 32264.9122 | 32264.9122 | 32264.9122 | 32264.9122 | 32264.9122 | 32264.9122 | 32264.9122 | 32264.9122 | 32264.9122 | 32264.9122 | 32264.9122 | 32264.9122
30% | 3808.7911 | 5052.6595 | 5391.0326 | 5111.1413 | 5110.5754 | 5149.0276 | 5191.2362 | 5277.9662 | 5340.2995 | 5374.0514 | 5410.9047 | 5444.6924 | 5505.8555 | 5581.802 | 5576.3491 | 5576.3491 | 5576.3491 | 5576.3491 | 5576.3491 | 5576.3491 | 5576.3491 | 5576.3491 | 5576.3491 | 5576.3491 | 5576.3491 | 5576.3491 | 5576.3491 | 5576.3491 | 5576.3491 | 5576.3491 |  | 21159.0479 | 27372.7075 | 28997.5323 | 27553.7246 | 27559.6056 | 27725.6221 | 28165.1227 | 28458.5621 | 28746.2799 | 29082.9322 | 29394.3407 | 29697.1072 | 29730.8609 | 30084.3876 | 29814.7732 | 29814.7732 | 29814.7732 | 29814.7732 | 29814.7732 | 29814.7732 | 29814.7732 | 29814.7732 | 29814.7732 | 29814.7732 | 29814.7732 | 29814.7732 | 29814.7732 | 29814.7732 | 29814.7732 | 29814.7732
25% | 2600.5659 | 3449.8542 | 3680.8886 | 3489.7844 | 3489.3981 | 3515.6525 | 3544.4716 | 3603.6891 | 3646.2491 | 3669.2942 | 3694.4569 | 3717.5264 | 3759.2874 | 3811.1421 | 3807.419 | 3807.419 | 3807.419 | 3807.419 | 3807.419 | 3807.419 | 3807.419 | 3807.419 | 3807.419 | 3807.419 | 3807.419 | 3807.419 | 3807.419 | 3807.419 | 3807.419 | 3807.419 |  | 6103.1255 | 7895.3963 | 8364.0615 | 7947.609 | 7949.3053 | 7997.1912 | 8123.9609 | 8208.6007 | 8291.5902 | 8388.6943 | 8478.5171 | 8565.8472 | 8575.5832 | 8677.5546 | 8599.7869 | 8599.7869 | 8599.7869 | 8599.7869 | 8599.7869 | 8599.7869 | 8599.7869 | 8599.7869 | 8599.7869 | 8599.7869 | 8599.7869 | 8599.7869 | 8599.7869 | 8599.7869 | 8599.7869 | 8599.7869
20% | 1575.389 | 2089.8768 | 2229.8344 | 2114.066 | 2113.832 | 2129.7365 | 2147.1948 | 2183.068 | 2208.8502 | 2222.8107 | 2238.0539 | 2252.0291 | 2277.3274 | 2308.7403 | 2306.4849 | 2306.4849 | 2306.4849 | 2306.4849 | 2306.4849 | 2306.4849 | 2306.4849 | 2306.4849 | 2306.4849 | 2306.4849 | 2306.4849 | 2306.4849 | 2306.4849 | 2306.4849 | 2306.4849 | 2306.4849 |  | 1637.7285 | 2118.6711 | 2244.4339 | 2132.682 | 2133.1372 | 2145.987 | 2180.0047 | 2202.7172 | 2224.9868 | 2251.044 | 2275.1472 | 2298.5816 | 2301.1942 | 2328.5575 | 2307.6891 | 2307.6891 | 2307.6891 | 2307.6891 | 2307.6891 | 2307.6891 | 2307.6891 | 2307.6891 | 2307.6891 | 2307.6891 | 2307.6891 | 2307.6891 | 2307.6891 | 2307.6891 | 2307.6891 | 2307.6891
15% | 1008.6332 | 1338.0309 | 1427.6379 | 1353.5179 | 1353.368 | 1363.5508 | 1374.7284 | 1397.696 | 1414.2029 | 1423.141 | 1432.9004 | 1441.8479 | 1458.045 | 1478.1569 | 1476.7129 | 1476.7129 | 1476.7129 | 1476.7129 | 1476.7129 | 1476.7129 | 1476.7129 | 1476.7129 | 1476.7129 | 1476.7129 | 1476.7129 | 1476.7129 | 1476.7129 | 1476.7129 | 1476.7129 | 1476.7129 |  | 903.3078 | 1168.5771 | 1237.943 | 1176.305 | 1176.5561 | 1183.6435 | 1202.4064 | 1214.9337 | 1227.2167 | 1241.5889 | 1254.8833 | 1267.8088 | 1269.2498 | 1284.3423 | 1272.8321 | 1272.8321 | 1272.8321 | 1272.8321 | 1272.8321 | 1272.8321 | 1272.8321 | 1272.8321 | 1272.8321 | 1272.8321 | 1272.8321 | 1272.8321 | 1272.8321 | 1272.8321 | 1272.8321 | 1272.8321
10% | 675.0905 | 895.5604 | 955.5354 | 905.926 | 905.8257 | 912.6412 | 920.1224 | 935.4949 | 946.5432 | 952.5256 | 959.0577 | 965.0464 | 975.8872 | 989.3484 | 988.3819 | 988.3819 | 988.3819 | 988.3819 | 988.3819 | 988.3819 | 988.3819 | 988.3819 | 988.3819 | 988.3819 | 988.3819 | 988.3819 | 988.3819 | 988.3819 | 988.3819 | 988.3819 |  | 211.1088 | 273.1039 | 289.3152 | 274.91 | 274.9687 | 276.625 | 281.01 | 283.9378 | 286.8084 | 290.1673 | 293.2742 | 296.295 | 296.6318 | 300.159 | 297.469 | 297.469 | 297.469 | 297.469 | 297.469 | 297.469 | 297.469 | 297.469 | 297.469 | 297.469 | 297.469 | 297.469 | 297.469 | 297.469 | 297.469 | 297.469
5% | 480.3015 | 637.1576 | 679.8276 | 644.5323 | 644.461 | 649.3099 | 654.6326 | 665.5695 | 673.43 | 677.6862 | 682.3335 | 686.5942 | 694.3071 | 703.8842 | 703.1966 | 703.1966 | 703.1966 | 703.1966 | 703.1966 | 703.1966 | 703.1966 | 703.1966 | 703.1966 | 703.1966 | 703.1966 | 703.1966 | 703.1966 | 703.1966 | 703.1966 | 703.1966 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9.992e-14% | 42.1598 | 55.9283 | 59.6738 | 56.5756 | 56.5694 | 56.995 | 57.4622 | 58.4222 | 59.1122 | 59.4858 | 59.8937 | 60.2677 | 60.9447 | 61.7854 | 61.725 | 61.725 | 61.725 | 61.725 | 61.725 | 61.725 | 61.725 | 61.725 | 61.725 | 61.725 | 61.725 | 61.725 | 61.725 | 61.725 | 61.725 | 61.725 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E @ R (MWh) | 112911.4176 | 149785.8315 | 159816.886 | 151519.5217 | 151502.7477 | 152642.6612 | 153893.9313 | 156465.0381 | 158312.9064 | 159313.48 | 160405.9943 | 161407.6275 | 163220.8061 | 165472.236 | 165310.5848 | 165310.5848 | 165310.5848 | 165310.5848 | 165310.5848 | 165310.5848 | 165310.5848 | 165310.5848 | 165310.5848 | 165310.5848 | 165310.5848 | 165310.5848 | 165310.5848 | 165310.5848 | 165310.5848 | 165310.5848 | E @ R (MWh) | 109518.1284 | 141679.7064 | 150089.7144 | 142616.6411 | 142647.0812 | 143506.3738 | 145781.206 | 147300.033 | 148789.2451 | 150531.7399 | 152143.5739 | 153710.6776 | 153885.3851 | 155715.2211 | 154319.7109 | 154319.7109 | 154319.7109 | 154319.7109 | 154319.7109 | 154319.7109 | 154319.7109 | 154319.7109 | 154319.7109 | 154319.7109 | 154319.7109 | 154319.7109 | 154319.7109 | 154319.7109 | 154319.7109 | 154319.7109
Option 4 Summer POE50 W E @ R (MWh) N 2 | 79037.9923 | 104850.082 | 111871.8202 | 106063.6652 | 106051.9234 | 106849.8628 | 107725.7519 | 109525.5267 | 110819.0345 | 111519.436 | 112284.196 | 112985.3393 | 114254.5643 | 115830.5652 | 115717.4093 | 115717.4093 | 115717.4093 | 115717.4093 | 115717.4093 | 115717.4093 | 115717.4093 | 115717.4093 | 115717.4093 | 115717.4093 | 115717.4093 | 115717.4093 | 115717.4093 | 115717.4093 | 115717.4093 | 115717.4093 | Option 4 Summer POE10 W E @ R (MWh) N 2 | 32855.4385 | 42503.9119 | 45026.9143 | 42784.9923 | 42794.1244 | 43051.9121 | 43734.3618 | 44190.0099 | 44636.7735 | 45159.522 | 45643.0722 | 46113.2033 | 46165.6155 | 46714.5663 | 46295.9133 | 46295.9133 | 46295.9133 | 46295.9133 | 46295.9133 | 46295.9133 | 46295.9133 | 46295.9133 | 46295.9133 | 46295.9133 | 46295.9133 | 46295.9133 | 46295.9133 | 46295.9133 | 46295.9133 | 46295.9133
Option 5 - 4B LLG 2nd Tx + Switchroom + Two new feeders + OFR12 New Feeder
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | 73.4908 | 101.8011 | 109.1509 | 78.2401 | 79.2087 | 80.8868 | 84.7129 | 87.2687 | 90.5123 | 92.1927 | 93.667 | 90.9258 | 94.1242 | 99.1561 | 95.326 | 95.326 | 95.326 | 95.326 | 95.326 | 95.326 | 95.326 | 95.326 | 95.326 | 95.326 | 95.326 | 95.326 | 95.326 | 95.326 | 95.326 | 95.326 |  | 78.6411 | 106.5944 | 114.2314 | 83.2493 | 83.9907 | 85.6323 | 89.5184 | 91.6338 | 95.6759 | 107.9761 | 97.8206 | 95.8295 | 98.5017 | 104.3537 | 100.3816 | 100.3816 | 100.3816 | 100.3816 | 100.3816 | 100.3816 | 100.3816 | 100.3816 | 100.3816 | 100.3816 | 100.3816 | 100.3816 | 100.3816 | 100.3816 | 100.3816 | 100.3816
98% | 87.3027 | 120.9335 | 129.6647 | 92.9445 | 94.0951 | 96.0886 | 100.6339 | 103.6699 | 107.5231 | 109.5194 | 111.2708 | 108.0144 | 111.8138 | 117.7914 | 113.2415 | 113.2415 | 113.2415 | 113.2415 | 113.2415 | 113.2415 | 113.2415 | 113.2415 | 113.2415 | 113.2415 | 113.2415 | 113.2415 | 113.2415 | 113.2415 | 113.2415 | 113.2415 |  | 93.4209 | 126.6277 | 135.7001 | 98.8952 | 99.7759 | 101.726 | 106.3424 | 108.8554 | 113.6572 | 128.2691 | 116.2049 | 113.8396 | 117.0141 | 123.9659 | 119.2472 | 119.2472 | 119.2472 | 119.2472 | 119.2472 | 119.2472 | 119.2472 | 119.2472 | 119.2472 | 119.2472 | 119.2472 | 119.2472 | 119.2472 | 119.2472 | 119.2472 | 119.2472
97% | 172.8327 | 239.4116 | 256.6966 | 184.0018 | 186.2797 | 190.2261 | 199.2244 | 205.2349 | 212.863 | 216.815 | 220.2823 | 213.8356 | 221.3573 | 233.1911 | 224.1837 | 224.1837 | 224.1837 | 224.1837 | 224.1837 | 224.1837 | 224.1837 | 224.1837 | 224.1837 | 224.1837 | 224.1837 | 224.1837 | 224.1837 | 224.1837 | 224.1837 | 224.1837 |  | 184.945 | 250.6842 | 268.6448 | 195.7823 | 197.526 | 201.3865 | 210.5256 | 215.5006 | 225.0066 | 253.9338 | 230.0504 | 225.3678 | 231.6523 | 245.4147 | 236.0732 | 236.0732 | 236.0732 | 236.0732 | 236.0732 | 236.0732 | 236.0732 | 236.0732 | 236.0732 | 236.0732 | 236.0732 | 236.0732 | 236.0732 | 236.0732 | 236.0732 | 236.0732
95% | 510.5211 | 707.185 | 758.2422 | 543.5131 | 550.2416 | 561.8988 | 588.4782 | 606.2322 | 628.7646 | 640.4383 | 650.68 | 631.6376 | 653.8555 | 688.8108 | 662.2043 | 662.2043 | 662.2043 | 662.2043 | 662.2043 | 662.2043 | 662.2043 | 662.2043 | 662.2043 | 662.2043 | 662.2043 | 662.2043 | 662.2043 | 662.2043 | 662.2043 | 662.2043 |  | 546.299 | 740.4826 | 793.5354 | 578.3109 | 583.4613 | 594.8647 | 621.8603 | 636.5557 | 664.635 | 750.0813 | 679.5334 | 665.7019 | 684.2653 | 724.9173 | 697.324 | 697.324 | 697.324 | 697.324 | 697.324 | 697.324 | 697.324 | 697.324 | 697.324 | 697.324 | 697.324 | 697.324 | 697.324 | 697.324 | 697.324 | 697.324
90% | 2814.8088 | 3899.1347 | 4180.6436 | 2996.7136 | 3033.8117 | 3098.0849 | 3244.6333 | 3342.5218 | 3466.7563 | 3531.1202 | 3587.5887 | 3482.5966 | 3605.0973 | 3797.8266 | 3651.1291 | 3651.1291 | 3651.1291 | 3651.1291 | 3651.1291 | 3651.1291 | 3651.1291 | 3651.1291 | 3651.1291 | 3651.1291 | 3651.1291 | 3651.1291 | 3651.1291 | 3651.1291 | 3651.1291 | 3651.1291 |  | 3012.0741 | 4082.7244 | 4375.2363 | 3188.5745 | 3216.9718 | 3279.8459 | 3428.6887 | 3509.7131 | 3664.531 | 4135.6477 | 3746.6749 | 3670.4136 | 3772.765 | 3996.9037 | 3844.7653 | 3844.7653 | 3844.7653 | 3844.7653 | 3844.7653 | 3844.7653 | 3844.7653 | 3844.7653 | 3844.7653 | 3844.7653 | 3844.7653 | 3844.7653 | 3844.7653 | 3844.7653 | 3844.7653 | 3844.7653
85% | 6876.3763 | 9525.3066 | 10213.0129 | 7320.7567 | 7411.3846 | 7568.3994 | 7926.4067 | 8165.5413 | 8469.0372 | 8626.2738 | 8764.2222 | 8507.7341 | 8806.9945 | 9277.8184 | 8919.4469 | 8919.4469 | 8919.4469 | 8919.4469 | 8919.4469 | 8919.4469 | 8919.4469 | 8919.4469 | 8919.4469 | 8919.4469 | 8919.4469 | 8919.4469 | 8919.4469 | 8919.4469 | 8919.4469 | 8919.4469 |  | 7358.2813 | 9973.8032 | 10688.3888 | 7789.4592 | 7858.8318 | 8012.4287 | 8376.0408 | 8573.9778 | 8952.1867 | 10103.091 | 9152.8584 | 8966.5574 | 9216.5947 | 9764.1495 | 9392.4862 | 9392.4862 | 9392.4862 | 9392.4862 | 9392.4862 | 9392.4862 | 9392.4862 | 9392.4862 | 9392.4862 | 9392.4862 | 9392.4862 | 9392.4862 | 9392.4862 | 9392.4862 | 9392.4862 | 9392.4862
80% | 10687.9274 | 14805.1503 | 15874.0497 | 11378.6263 | 11519.4889 | 11763.5363 | 12319.9859 | 12691.6718 | 13163.3945 | 13407.7867 | 13622.1995 | 13223.5409 | 13688.6804 | 14420.4803 | 13863.4648 | 13863.4648 | 13863.4648 | 13863.4648 | 13863.4648 | 13863.4648 | 13863.4648 | 13863.4648 | 13863.4648 | 13863.4648 | 13863.4648 | 13863.4648 | 13863.4648 | 13863.4648 | 13863.4648 | 13863.4648 |  | 11436.9506 | 15502.2469 | 16612.9248 | 12107.1288 | 12214.9544 | 12453.6895 | 13018.8506 | 13326.5032 | 13914.352 | 15703.1985 | 14226.2554 | 13936.6884 | 14325.3205 | 15176.383 | 14598.7081 | 14598.7081 | 14598.7081 | 14598.7081 | 14598.7081 | 14598.7081 | 14598.7081 | 14598.7081 | 14598.7081 | 14598.7081 | 14598.7081 | 14598.7081 | 14598.7081 | 14598.7081 | 14598.7081 | 14598.7081
75% | 11791.7667 | 16334.2127 | 17513.507 | 12553.8004 | 12709.2111 | 12978.4636 | 13592.3827 | 14002.4561 | 14522.8978 | 14792.5307 | 15029.0878 | 14589.2561 | 15102.4347 | 15909.8143 | 15295.2707 | 15295.2707 | 15295.2707 | 15295.2707 | 15295.2707 | 15295.2707 | 15295.2707 | 15295.2707 | 15295.2707 | 15295.2707 | 15295.2707 | 15295.2707 | 15295.2707 | 15295.2707 | 15295.2707 | 15295.2707 |  | 12618.1483 | 17103.3048 | 18328.6925 | 13357.5419 | 13476.5037 | 13739.8952 | 14363.4255 | 14702.8523 | 15351.4136 | 17325.0105 | 15695.53 | 15376.0569 | 15804.8265 | 16743.786 | 16106.4493 | 16106.4493 | 16106.4493 | 16106.4493 | 16106.4493 | 16106.4493 | 16106.4493 | 16106.4493 | 16106.4493 | 16106.4493 | 16106.4493 | 16106.4493 | 16106.4493 | 16106.4493 | 16106.4493 | 16106.4493
70% | 12669.5942 | 17550.1984 | 18817.2842 | 13488.3567 | 13655.3369 | 13944.6336 | 14604.2554 | 15044.8563 | 15604.0418 | 15893.7473 | 16147.9147 | 15675.3401 | 16226.7219 | 17094.2061 | 16433.9133 | 16433.9133 | 16433.9133 | 16433.9133 | 16433.9133 | 16433.9133 | 16433.9133 | 16433.9133 | 16433.9133 | 16433.9133 | 16433.9133 | 16433.9133 | 16433.9133 | 16433.9133 | 16433.9133 | 16433.9133 |  | 13557.495 | 18376.5449 | 19693.1554 | 14351.9321 | 14479.7498 | 14762.7492 | 15432.6978 | 15797.3929 | 16494.2357 | 18614.7552 | 16863.9696 | 16520.7135 | 16981.4025 | 17990.262 | 17305.4793 | 17305.4793 | 17305.4793 | 17305.4793 | 17305.4793 | 17305.4793 | 17305.4793 | 17305.4793 | 17305.4793 | 17305.4793 | 17305.4793 | 17305.4793 | 17305.4793 | 17305.4793 | 17305.4793 | 17305.4793
65% | 13351.323 | 18494.5441 | 19829.8096 | 14214.1417 | 14390.1068 | 14694.9701 | 15390.085 | 15854.3938 | 16443.6682 | 16748.9622 | 17016.8059 | 16518.8029 | 17099.8535 | 18014.0155 | 17318.1936 | 17318.1936 | 17318.1936 | 17318.1936 | 17318.1936 | 17318.1936 | 17318.1936 | 17318.1936 | 17318.1936 | 17318.1936 | 17318.1936 | 17318.1936 | 17318.1936 | 17318.1936 | 17318.1936 | 17318.1936 |  | 14287.0002 | 19365.3548 | 20752.8099 | 15124.1846 | 15258.88 | 15557.1071 | 16263.1044 | 16647.4231 | 17381.7618 | 19616.3828 | 17771.3904 | 17409.6644 | 17895.1423 | 18958.2867 | 18236.6571 | 18236.6571 | 18236.6571 | 18236.6571 | 18236.6571 | 18236.6571 | 18236.6571 | 18236.6571 | 18236.6571 | 18236.6571 | 18236.6571 | 18236.6571 | 18236.6571 | 18236.6571 | 18236.6571 | 18236.6571
60% | 14698.1621 | 20360.2151 | 21830.1779 | 15648.0193 | 15841.7351 | 16177.352 | 16942.588 | 17453.7348 | 18102.4533 | 18438.5443 | 18733.4073 | 18185.1674 | 18824.8325 | 19831.2123 | 19065.1981 | 19065.1981 | 19065.1981 | 19065.1981 | 19065.1981 | 19065.1981 | 19065.1981 | 19065.1981 | 19065.1981 | 19065.1981 | 19065.1981 | 19065.1981 | 19065.1981 | 19065.1981 | 19065.1981 | 19065.1981 |  | 15728.2275 | 21318.8704 | 22846.2875 | 16649.8644 | 16798.1474 | 17126.4587 | 17903.6748 | 18326.7624 | 19135.1788 | 21595.2213 | 19564.1119 | 19165.8961 | 19700.3475 | 20870.7385 | 20076.3132 | 20076.3132 | 20076.3132 | 20076.3132 | 20076.3132 | 20076.3132 | 20076.3132 | 20076.3132 | 20076.3132 | 20076.3132 | 20076.3132 | 20076.3132 | 20076.3132 | 20076.3132 | 20076.3132 | 20076.3132
55% | 16350.7821 | 22649.4603 | 24284.7017 | 17407.4385 | 17622.9353 | 17996.288 | 18847.5649 | 19416.1836 | 20137.8422 | 20511.7224 | 20839.7389 | 20229.8564 | 20941.4437 | 22060.978 | 21208.8353 | 21208.8353 | 21208.8353 | 21208.8353 | 21208.8353 | 21208.8353 | 21208.8353 | 21208.8353 | 21208.8353 | 21208.8353 | 21208.8353 | 21208.8353 | 21208.8353 | 21208.8353 | 21208.8353 | 21208.8353 |  | 17496.6651 | 23715.9042 | 25415.0598 | 18521.9283 | 18686.8838 | 19052.1096 | 19916.7136 | 20387.3719 | 21286.6845 | 24023.3272 | 21763.8456 | 21320.8556 | 21915.3991 | 23217.3856 | 22333.6374 | 22333.6374 | 22333.6374 | 22333.6374 | 22333.6374 | 22333.6374 | 22333.6374 | 22333.6374 | 22333.6374 | 22333.6374 | 22333.6374 | 22333.6374 | 22333.6374 | 22333.6374 | 22333.6374 | 22333.6374
50% | 16573.101 | 22957.4214 | 24614.8968 | 17644.1246 | 17862.5515 | 18240.9806 | 19103.8322 | 19680.1823 | 20411.6532 | 20790.6169 | 21123.0935 | 20504.9185 | 21226.1812 | 22360.9376 | 21497.2084 | 21497.2084 | 21497.2084 | 21497.2084 | 21497.2084 | 21497.2084 | 21497.2084 | 21497.2084 | 21497.2084 | 21497.2084 | 21497.2084 | 21497.2084 | 21497.2084 | 21497.2084 | 21497.2084 | 21497.2084 |  | 17734.5645 | 24038.3655 | 25760.6242 | 18773.7679 | 18940.9663 | 19311.158 | 20187.518 | 20664.5757 | 21576.1161 | 24349.9685 | 22059.7651 | 21610.7518 | 22213.3792 | 23533.0687 | 22637.3042 | 22637.3042 | 22637.3042 | 22637.3042 | 22637.3042 | 22637.3042 | 22637.3042 | 22637.3042 | 22637.3042 | 22637.3042 | 22637.3042 | 22637.3042 | 22637.3042 | 22637.3042 | 22637.3042 | 22637.3042
45% | 12791.4633 | 17719.0143 | 18998.2882 | 13618.1016 | 13786.6879 | 14078.7674 | 14744.7341 | 15189.5732 | 15754.1376 | 16046.6297 | 16303.242 | 15826.1217 | 16382.8072 | 17258.6357 | 16591.9916 | 16591.9916 | 16591.9916 | 16591.9916 | 16591.9916 | 16591.9916 | 16591.9916 | 16591.9916 | 16591.9916 | 16591.9916 | 16591.9916 | 16591.9916 | 16591.9916 | 16591.9916 | 16591.9916 | 16591.9916 |  | 13687.9049 | 18553.3094 | 19882.5844 | 14489.9837 | 14619.0309 | 14904.7525 | 15581.1453 | 15949.3484 | 16652.8942 | 18793.8111 | 17026.1846 | 16679.6267 | 17144.7471 | 18163.3108 | 17471.9412 | 17471.9412 | 17471.9412 | 17471.9412 | 17471.9412 | 17471.9412 | 17471.9412 | 17471.9412 | 17471.9412 | 17471.9412 | 17471.9412 | 17471.9412 | 17471.9412 | 17471.9412 | 17471.9412 | 17471.9412
40% | 6284.3875 | 8705.2708 | 9333.7723 | 6690.5111 | 6773.3369 | 6916.8342 | 7244.0206 | 7462.568 | 7739.9359 | 7883.6359 | 8009.7084 | 7775.3013 | 8048.7984 | 8479.0889 | 8151.5697 | 8151.5697 | 8151.5697 | 8151.5697 | 8151.5697 | 8151.5697 | 8151.5697 | 8151.5697 | 8151.5697 | 8151.5697 | 8151.5697 | 8151.5697 | 8151.5697 | 8151.5697 | 8151.5697 | 8151.5697 |  | 6724.8052 | 9115.1562 | 9768.223 | 7118.8629 | 7182.2632 | 7322.6369 | 7654.9456 | 7835.8421 | 8181.4909 | 9233.3136 | 8364.8868 | 8194.6245 | 8423.136 | 8923.5517 | 8583.885 | 8583.885 | 8583.885 | 8583.885 | 8583.885 | 8583.885 | 8583.885 | 8583.885 | 8583.885 | 8583.885 | 8583.885 | 8583.885 | 8583.885 | 8583.885 | 8583.885 | 8583.885
35% | 2348.7515 | 3253.5419 | 3488.4405 | 2500.5378 | 2531.4934 | 2585.1246 | 2707.4085 | 2789.0893 | 2892.7538 | 2946.4609 | 2993.5797 | 2905.9715 | 3008.1893 | 3169.0078 | 3046.5995 | 3046.5995 | 3046.5995 | 3046.5995 | 3046.5995 | 3046.5995 | 3046.5995 | 3046.5995 | 3046.5995 | 3046.5995 | 3046.5995 | 3046.5995 | 3046.5995 | 3046.5995 | 3046.5995 | 3046.5995 |  | 2513.3549 | 3406.7341 | 3650.8138 | 2660.6316 | 2684.3271 | 2736.7909 | 2860.9892 | 2928.5982 | 3057.7823 | 3450.8947 | 3126.3254 | 3062.6909 | 3148.0957 | 3335.123 | 3208.1747 | 3208.1747 | 3208.1747 | 3208.1747 | 3208.1747 | 3208.1747 | 3208.1747 | 3208.1747 | 3208.1747 | 3208.1747 | 3208.1747 | 3208.1747 | 3208.1747 | 3208.1747 | 3208.1747 | 3208.1747
30% | 1171.4214 | 1622.6784 | 1739.8323 | 1247.1235 | 1262.5624 | 1289.3106 | 1350.2987 | 1391.0364 | 1442.7382 | 1469.5242 | 1493.0243 | 1449.3304 | 1500.3108 | 1580.5177 | 1519.4675 | 1519.4675 | 1519.4675 | 1519.4675 | 1519.4675 | 1519.4675 | 1519.4675 | 1519.4675 | 1519.4675 | 1519.4675 | 1519.4675 | 1519.4675 | 1519.4675 | 1519.4675 | 1519.4675 | 1519.4675 |  | 1253.516 | 1699.0818 | 1820.8147 | 1326.9691 | 1338.787 | 1364.9529 | 1426.8959 | 1460.6153 | 1525.0449 | 1721.1066 | 1559.2302 | 1527.493 | 1570.088 | 1663.3664 | 1600.0519 | 1600.0519 | 1600.0519 | 1600.0519 | 1600.0519 | 1600.0519 | 1600.0519 | 1600.0519 | 1600.0519 | 1600.0519 | 1600.0519 | 1600.0519 | 1600.0519 | 1600.0519 | 1600.0519 | 1600.0519
25% | 690.592 | 956.6232 | 1025.6893 | 735.221 | 744.3227 | 760.0917 | 796.0462 | 820.0624 | 850.5424 | 866.3336 | 880.1877 | 854.4287 | 884.4833 | 931.768 | 895.7769 | 895.7769 | 895.7769 | 895.7769 | 895.7769 | 895.7769 | 895.7769 | 895.7769 | 895.7769 | 895.7769 | 895.7769 | 895.7769 | 895.7769 | 895.7769 | 895.7769 | 895.7769 |  | 738.9896 | 1001.6655 | 1073.4311 | 782.2926 | 789.2597 | 804.6854 | 841.2028 | 861.0815 | 899.0649 | 1014.6498 | 919.2183 | 900.5082 | 925.6193 | 980.6101 | 943.2841 | 943.2841 | 943.2841 | 943.2841 | 943.2841 | 943.2841 | 943.2841 | 943.2841 | 943.2841 | 943.2841 | 943.2841 | 943.2841 | 943.2841 | 943.2841 | 943.2841 | 943.2841
20% | 348.989 | 483.4272 | 518.3296 | 371.5422 | 376.1417 | 384.1105 | 402.28 | 414.4166 | 429.8196 | 437.7996 | 444.8008 | 431.7835 | 446.9715 | 470.8667 | 452.6787 | 452.6787 | 452.6787 | 452.6787 | 452.6787 | 452.6787 | 452.6787 | 452.6787 | 452.6787 | 452.6787 | 452.6787 | 452.6787 | 452.6787 | 452.6787 | 452.6787 | 452.6787 |  | 373.4466 | 506.1893 | 542.4558 | 395.3297 | 398.8505 | 406.6458 | 425.0998 | 435.1455 | 454.3403 | 512.7509 | 464.5248 | 455.0696 | 467.7595 | 495.5489 | 476.6863 | 476.6863 | 476.6863 | 476.6863 | 476.6863 | 476.6863 | 476.6863 | 476.6863 | 476.6863 | 476.6863 | 476.6863 | 476.6863 | 476.6863 | 476.6863 | 476.6863 | 476.6863
15% | 142.1807 | 196.9518 | 211.1713 | 151.369 | 153.2429 | 156.4895 | 163.8919 | 168.8364 | 175.1117 | 178.3628 | 181.2151 | 175.9118 | 182.0995 | 191.8346 | 184.4247 | 184.4247 | 184.4247 | 184.4247 | 184.4247 | 184.4247 | 184.4247 | 184.4247 | 184.4247 | 184.4247 | 184.4247 | 184.4247 | 184.4247 | 184.4247 | 184.4247 | 184.4247 |  | 152.1449 | 206.2253 | 221.0005 | 161.0602 | 162.4946 | 165.6705 | 173.1888 | 177.2815 | 185.1016 | 208.8985 | 189.2508 | 185.3987 | 190.5687 | 201.8903 | 194.2055 | 194.2055 | 194.2055 | 194.2055 | 194.2055 | 194.2055 | 194.2055 | 194.2055 | 194.2055 | 194.2055 | 194.2055 | 194.2055 | 194.2055 | 194.2055 | 194.2055 | 194.2055
10% | 57.2416 | 79.2923 | 85.017 | 60.9408 | 61.6952 | 63.0023 | 65.9824 | 67.9731 | 70.4995 | 71.8084 | 72.9567 | 70.8216 | 73.3128 | 77.2321 | 74.2489 | 74.2489 | 74.2489 | 74.2489 | 74.2489 | 74.2489 | 74.2489 | 74.2489 | 74.2489 | 74.2489 | 74.2489 | 74.2489 | 74.2489 | 74.2489 | 74.2489 | 74.2489 |  | 61.2531 | 83.0258 | 88.9742 | 64.8424 | 65.4199 | 66.6985 | 69.7254 | 71.3731 | 74.5214 | 84.102 | 76.1919 | 74.6411 | 76.7225 | 81.2805 | 78.1866 | 78.1866 | 78.1866 | 78.1866 | 78.1866 | 78.1866 | 78.1866 | 78.1866 | 78.1866 | 78.1866 | 78.1866 | 78.1866 | 78.1866 | 78.1866 | 78.1866 | 78.1866
5% | 48.7477 | 67.5263 | 72.4016 | 51.898 | 52.5404 | 53.6535 | 56.1915 | 57.8868 | 60.0383 | 61.153 | 62.1309 | 60.3126 | 62.4341 | 65.7719 | 63.2313 | 63.2313 | 63.2313 | 63.2313 | 63.2313 | 63.2313 | 63.2313 | 63.2313 | 63.2313 | 63.2313 | 63.2313 | 63.2313 | 63.2313 | 63.2313 | 63.2313 | 63.2313 |  | 52.164 | 70.7058 | 75.7716 | 55.2207 | 55.7124 | 56.8013 | 59.379 | 60.7822 | 63.4634 | 71.6223 | 64.886 | 63.5653 | 65.3378 | 69.2195 | 66.5848 | 66.5848 | 66.5848 | 66.5848 | 66.5848 | 66.5848 | 66.5848 | 66.5848 | 66.5848 | 66.5848 | 66.5848 | 66.5848 | 66.5848 | 66.5848 | 66.5848 | 66.5848
9.992e-14% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E @ R (MWh) | 130541.7636 | 180829.3011 | 193884.7798 | 138977.9224 | 140698.4105 | 143679.1929 | 150475.6375 | 155015.3895 | 160776.9844 | 163761.9779 | 166380.8044 | 161511.6096 | 167192.7975 | 176130.962 | 169327.6047 | 169327.6047 | 169327.6047 | 169327.6047 | 169327.6047 | 169327.6047 | 169327.6047 | 169327.6047 | 169327.6047 | 169327.6047 | 169327.6047 | 169327.6047 | 169327.6047 | 169327.6047 | 169327.6047 | 169327.6047 | E @ R (MWh) | 139690.2921 | 189343.6009 | 202909.3599 | 147875.8122 | 149192.7881 | 152108.6862 | 159011.5328 | 162769.1859 | 169949.1387 | 191798.0124 | 173758.7093 | 170221.9546 | 174968.6857 | 185363.5166 | 178307.8262 | 178307.8262 | 178307.8262 | 178307.8262 | 178307.8262 | 178307.8262 | 178307.8262 | 178307.8262 | 178307.8262 | 178307.8262 | 178307.8262 | 178307.8262 | 178307.8262 | 178307.8262 | 178307.8262 | 178307.8262
Option 5 Winter POE50 W E @ R (MWh) N 2 | 91379.2345 | 126580.5108 | 135719.3459 | 97284.5457 | 98488.8873 | 100575.435 | 105332.9462 | 108510.7727 | 112543.8891 | 114633.3845 | 116466.5631 | 113058.1267 | 117034.9582 | 123291.6734 | 118529.3233 | 118529.3233 | 118529.3233 | 118529.3233 | 118529.3233 | 118529.3233 | 118529.3233 | 118529.3233 | 118529.3233 | 118529.3233 | 118529.3233 | 118529.3233 | 118529.3233 | 118529.3233 | 118529.3233 | 118529.3233 | Option 5 Winter POE10 W E @ R (MWh) N 2 | 41907.0876 | 56803.0803 | 60872.808 | 44362.7437 | 44757.8364 | 45632.6059 | 47703.4598 | 48830.7558 | 50984.7416 | 57539.4037 | 52127.6128 | 51066.5864 | 52490.6057 | 55609.055 | 53492.3479 | 53492.3479 | 53492.3479 | 53492.3479 | 53492.3479 | 53492.3479 | 53492.3479 | 53492.3479 | 53492.3479 | 53492.3479 | 53492.3479 | 53492.3479 | 53492.3479 | 53492.3479 | 53492.3479 | 53492.3479
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 94.6719 | 122.4737 | 129.7436 | 96.5682 | 96.5945 | 97.3373 | 99.3037 | 100.6167 | 101.904 | 103.4103 | 104.8036 | 106.1583 | 106.3093 | 107.8911 | 106.6848 | 106.6848 | 106.6848 | 106.6848 | 106.6848 | 106.6848 | 106.6848 | 106.6848 | 106.6848 | 106.6848 | 106.6848 | 106.6848 | 106.6848 | 106.6848 | 106.6848 | 106.6848
98% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 46.8602 | 60.6214 | 64.2198 | 47.7988 | 47.8118 | 48.1795 | 49.1529 | 49.8027 | 50.4399 | 51.1855 | 51.8752 | 52.5457 | 52.6204 | 53.4034 | 52.8063 | 52.8063 | 52.8063 | 52.8063 | 52.8063 | 52.8063 | 52.8063 | 52.8063 | 52.8063 | 52.8063 | 52.8063 | 52.8063 | 52.8063 | 52.8063 | 52.8063 | 52.8063
97% | 20.8131 | 27.6102 | 29.4592 | 21.3851 | 21.382 | 21.5922 | 21.8228 | 22.2967 | 22.6374 | 22.8218 | 23.0232 | 23.2078 | 23.542 | 23.957 | 23.9272 | 23.9272 | 23.9272 | 23.9272 | 23.9272 | 23.9272 | 23.9272 | 23.9272 | 23.9272 | 23.9272 | 23.9272 | 23.9272 | 23.9272 | 23.9272 | 23.9272 | 23.9272 |  | 92.7689 | 120.0119 | 127.1357 | 94.6271 | 94.6529 | 95.3808 | 97.3077 | 98.5942 | 99.8557 | 101.3317 | 102.697 | 104.0245 | 104.1724 | 105.7224 | 104.5403 | 104.5403 | 104.5403 | 104.5403 | 104.5403 | 104.5403 | 104.5403 | 104.5403 | 104.5403 | 104.5403 | 104.5403 | 104.5403 | 104.5403 | 104.5403 | 104.5403 | 104.5403
95% | 102.4643 | 135.9269 | 145.0299 | 105.2806 | 105.2654 | 106.2999 | 107.4353 | 109.7686 | 111.4455 | 112.3535 | 113.3449 | 114.2538 | 115.8993 | 117.9424 | 117.7957 | 117.7957 | 117.7957 | 117.7957 | 117.7957 | 117.7957 | 117.7957 | 117.7957 | 117.7957 | 117.7957 | 117.7957 | 117.7957 | 117.7957 | 117.7957 | 117.7957 | 117.7957 |  | 137.0126 | 177.2483 | 187.7696 | 139.7569 | 139.795 | 140.87 | 143.716 | 145.6161 | 147.4792 | 149.6591 | 151.6756 | 153.6361 | 153.8547 | 156.1439 | 154.3981 | 154.3981 | 154.3981 | 154.3981 | 154.3981 | 154.3981 | 154.3981 | 154.3981 | 154.3981 | 154.3981 | 154.3981 | 154.3981 | 154.3981 | 154.3981 | 154.3981 | 154.3981
90% | 177.7116 | 235.7483 | 251.5362 | 182.5961 | 182.5697 | 184.3638 | 186.3332 | 190.3799 | 193.2882 | 194.863 | 196.5825 | 198.159 | 201.0128 | 204.5563 | 204.3019 | 204.3019 | 204.3019 | 204.3019 | 204.3019 | 204.3019 | 204.3019 | 204.3019 | 204.3019 | 204.3019 | 204.3019 | 204.3019 | 204.3019 | 204.3019 | 204.3019 | 204.3019 |  | 594.078 | 768.5376 | 814.1574 | 605.9773 | 606.1425 | 610.8037 | 623.1434 | 631.3823 | 639.4605 | 648.9126 | 657.6559 | 666.1566 | 667.1043 | 677.0302 | 669.4603 | 669.4603 | 669.4603 | 669.4603 | 669.4603 | 669.4603 | 669.4603 | 669.4603 | 669.4603 | 669.4603 | 669.4603 | 669.4603 | 669.4603 | 669.4603 | 669.4603 | 669.4603
85% | 504.3166 | 669.0154 | 713.8189 | 518.1781 | 518.1032 | 523.1946 | 528.7834 | 540.2672 | 548.5206 | 552.9897 | 557.8694 | 562.3431 | 570.4417 | 580.4976 | 579.7756 | 579.7756 | 579.7756 | 579.7756 | 579.7756 | 579.7756 | 579.7756 | 579.7756 | 579.7756 | 579.7756 | 579.7756 | 579.7756 | 579.7756 | 579.7756 | 579.7756 | 579.7756 |  | 561.9657 | 726.995 | 770.1489 | 573.2218 | 573.378 | 577.7873 | 589.46 | 597.2535 | 604.895 | 613.8362 | 622.107 | 630.1482 | 631.0446 | 640.434 | 633.2733 | 633.2733 | 633.2733 | 633.2733 | 633.2733 | 633.2733 | 633.2733 | 633.2733 | 633.2733 | 633.2733 | 633.2733 | 633.2733 | 633.2733 | 633.2733 | 633.2733 | 633.2733
80% | 704.4422 | 934.4978 | 997.0804 | 723.8043 | 723.6997 | 730.8115 | 738.618 | 754.6589 | 766.1875 | 772.43 | 779.2461 | 785.4952 | 796.8074 | 810.8538 | 809.8453 | 809.8453 | 809.8453 | 809.8453 | 809.8453 | 809.8453 | 809.8453 | 809.8453 | 809.8453 | 809.8453 | 809.8453 | 809.8453 | 809.8453 | 809.8453 | 809.8453 | 809.8453 |  | 392.484 | 507.7425 | 537.8818 | 400.3454 | 400.4545 | 403.534 | 411.6864 | 417.1294 | 422.4664 | 428.711 | 434.4874 | 440.1035 | 440.7296 | 447.2872 | 442.2861 | 442.2861 | 442.2861 | 442.2861 | 442.2861 | 442.2861 | 442.2861 | 442.2861 | 442.2861 | 442.2861 | 442.2861 | 442.2861 | 442.2861 | 442.2861 | 442.2861 | 442.2861
75% | 1836.3528 | 2436.0657 | 2599.2074 | 1886.8263 | 1886.5535 | 1905.0927 | 1925.4429 | 1967.2585 | 1997.3116 | 2013.5846 | 2031.3529 | 2047.6431 | 2077.132 | 2113.7485 | 2111.1195 | 2111.1195 | 2111.1195 | 2111.1195 | 2111.1195 | 2111.1195 | 2111.1195 | 2111.1195 | 2111.1195 | 2111.1195 | 2111.1195 | 2111.1195 | 2111.1195 | 2111.1195 | 2111.1195 | 2111.1195 |  | 700.5244 | 906.2435 | 960.0375 | 714.5559 | 714.7506 | 720.247 | 734.7978 | 744.5128 | 754.0385 | 765.1842 | 775.4942 | 785.518 | 786.6355 | 798.3399 | 789.4137 | 789.4137 | 789.4137 | 789.4137 | 789.4137 | 789.4137 | 789.4137 | 789.4137 | 789.4137 | 789.4137 | 789.4137 | 789.4137 | 789.4137 | 789.4137 | 789.4137 | 789.4137
70% | 3172.6584 | 4208.7797 | 4490.6388 | 3259.8612 | 3259.3899 | 3291.4199 | 3326.5789 | 3398.8235 | 3450.7461 | 3478.8609 | 3509.5591 | 3537.7036 | 3588.6515 | 3651.9136 | 3647.3714 | 3647.3714 | 3647.3714 | 3647.3714 | 3647.3714 | 3647.3714 | 3647.3714 | 3647.3714 | 3647.3714 | 3647.3714 | 3647.3714 | 3647.3714 | 3647.3714 | 3647.3714 | 3647.3714 | 3647.3714 |  | 1276.1675 | 1650.9325 | 1748.9307 | 1301.7291 | 1302.0838 | 1312.0968 | 1338.6044 | 1356.3027 | 1373.6558 | 1393.9603 | 1412.7423 | 1431.0031 | 1433.0389 | 1454.3612 | 1438.0999 | 1438.0999 | 1438.0999 | 1438.0999 | 1438.0999 | 1438.0999 | 1438.0999 | 1438.0999 | 1438.0999 | 1438.0999 | 1438.0999 | 1438.0999 | 1438.0999 | 1438.0999 | 1438.0999 | 1438.0999
65% | 7968.2023 | 10570.444 | 11278.3393 | 8187.214 | 8186.0303 | 8266.4744 | 8354.777 | 8536.221 | 8666.6258 | 8737.2367 | 8814.3358 | 8885.0215 | 9012.9782 | 9171.8625 | 9160.4547 | 9160.4547 | 9160.4547 | 9160.4547 | 9160.4547 | 9160.4547 | 9160.4547 | 9160.4547 | 9160.4547 | 9160.4547 | 9160.4547 | 9160.4547 | 9160.4547 | 9160.4547 | 9160.4547 | 9160.4547 |  | 1605.6162 | 2077.1285 | 2200.4254 | 1637.7766 | 1638.2229 | 1650.8207 | 1684.1714 | 1706.4386 | 1728.2715 | 1753.8178 | 1777.4484 | 1800.4233 | 1802.9847 | 1829.8114 | 1809.3522 | 1809.3522 | 1809.3522 | 1809.3522 | 1809.3522 | 1809.3522 | 1809.3522 | 1809.3522 | 1809.3522 | 1809.3522 | 1809.3522 | 1809.3522 | 1809.3522 | 1809.3522 | 1809.3522 | 1809.3522
60% | 11647.312 | 15451.0709 | 16485.8185 | 11967.4467 | 11965.7164 | 12083.3035 | 12212.3775 | 12477.5986 | 12668.2144 | 12771.4279 | 12884.1256 | 12987.4485 | 13174.4859 | 13406.7309 | 13390.0558 | 13390.0558 | 13390.0558 | 13390.0558 | 13390.0558 | 13390.0558 | 13390.0558 | 13390.0558 | 13390.0558 | 13390.0558 | 13390.0558 | 13390.0558 | 13390.0558 | 13390.0558 | 13390.0558 | 13390.0558 |  | 2512.492 | 3250.3215 | 3443.2583 | 2562.8171 | 2563.5154 | 2583.2287 | 2635.4164 | 2670.2603 | 2704.4249 | 2744.4 | 2781.3776 | 2817.3291 | 2821.3371 | 2863.316 | 2831.3011 | 2831.3011 | 2831.3011 | 2831.3011 | 2831.3011 | 2831.3011 | 2831.3011 | 2831.3011 | 2831.3011 | 2831.3011 | 2831.3011 | 2831.3011 | 2831.3011 | 2831.3011 | 2831.3011 | 2831.3011
55% | 13170.4015 | 17471.5683 | 18641.6273 | 13532.3994 | 13530.4428 | 13663.4065 | 13809.3592 | 14109.2625 | 14324.8047 | 14441.5153 | 14568.9501 | 14685.7843 | 14897.2801 | 15159.8951 | 15141.0395 | 15141.0395 | 15141.0395 | 15141.0395 | 15141.0395 | 15141.0395 | 15141.0395 | 15141.0395 | 15141.0395 | 15141.0395 | 15141.0395 | 15141.0395 | 15141.0395 | 15141.0395 | 15141.0395 | 15141.0395 |  | 4828.1473 | 6246.0024 | 6616.7608 | 4924.8549 | 4926.1969 | 4964.0791 | 5064.3659 | 5131.324 | 5196.9764 | 5273.795 | 5344.8533 | 5413.9396 | 5421.6417 | 5502.3107 | 5440.7891 | 5440.7891 | 5440.7891 | 5440.7891 | 5440.7891 | 5440.7891 | 5440.7891 | 5440.7891 | 5440.7891 | 5440.7891 | 5440.7891 | 5440.7891 | 5440.7891 | 5440.7891 | 5440.7891 | 5440.7891
50% | 16911.4168 | 22434.3178 | 23936.7286 | 17376.2391 | 17373.7267 | 17544.4584 | 17731.8686 | 18116.9586 | 18393.7248 | 18543.5867 | 18707.2191 | 18857.2397 | 19128.8103 | 19466.0204 | 19441.8089 | 19441.8089 | 19441.8089 | 19441.8089 | 19441.8089 | 19441.8089 | 19441.8089 | 19441.8089 | 19441.8089 | 19441.8089 | 19441.8089 | 19441.8089 | 19441.8089 | 19441.8089 | 19441.8089 | 19441.8089 |  | 10714.812 | 13861.3711 | 14684.1724 | 10929.4292 | 10932.4073 | 11016.477 | 11239.0375 | 11387.6334 | 11533.3319 | 11703.8105 | 11861.5059 | 12014.825 | 12031.9176 | 12210.9414 | 12074.4103 | 12074.4103 | 12074.4103 | 12074.4103 | 12074.4103 | 12074.4103 | 12074.4103 | 12074.4103 | 12074.4103 | 12074.4103 | 12074.4103 | 12074.4103 | 12074.4103 | 12074.4103 | 12074.4103 | 12074.4103
45% | 22520.2713 | 29874.9022 | 31875.6039 | 23139.2569 | 23135.9113 | 23363.268 | 23612.8348 | 24125.6441 | 24494.2029 | 24693.7681 | 24911.6709 | 25111.4474 | 25473.0873 | 25922.1368 | 25889.8953 | 25889.8953 | 25889.8953 | 25889.8953 | 25889.8953 | 25889.8953 | 25889.8953 | 25889.8953 | 25889.8953 | 25889.8953 | 25889.8953 | 25889.8953 | 25889.8953 | 25889.8953 | 25889.8953 | 25889.8953 |  | 16236.3476 | 21004.3853 | 22251.1909 | 16561.5609 | 16566.0738 | 16693.4661 | 17030.7159 | 17255.886 | 17476.6656 | 17734.9949 | 17973.9535 | 18206.2807 | 18232.1816 | 18503.4595 | 18296.5715 | 18296.5715 | 18296.5715 | 18296.5715 | 18296.5715 | 18296.5715 | 18296.5715 | 18296.5715 | 18296.5715 | 18296.5715 | 18296.5715 | 18296.5715 | 18296.5715 | 18296.5715 | 18296.5715 | 18296.5715
40% | 15794.9825 | 20953.2804 | 22356.5072 | 16229.1189 | 16226.7724 | 16386.2329 | 16561.2709 | 16920.9386 | 17179.4337 | 17319.4022 | 17472.2321 | 17612.3489 | 17865.9913 | 18180.9399 | 18158.3268 | 18158.3268 | 18158.3268 | 18158.3268 | 18158.3268 | 18158.3268 | 18158.3268 | 18158.3268 | 18158.3268 | 18158.3268 | 18158.3268 | 18158.3268 | 18158.3268 | 18158.3268 | 18158.3268 | 18158.3268 |  | 16811.9908 | 21749.0744 | 23040.0842 | 17148.7342 | 17153.407 | 17285.3159 | 17634.5226 | 17867.6758 | 18096.2829 | 18363.7711 | 18611.2017 | 18851.7658 | 18878.585 | 19159.4808 | 18945.2578 | 18945.2578 | 18945.2578 | 18945.2578 | 18945.2578 | 18945.2578 | 18945.2578 | 18945.2578 | 18945.2578 | 18945.2578 | 18945.2578 | 18945.2578 | 18945.2578 | 18945.2578 | 18945.2578 | 18945.2578
35% | 8189.141 | 10863.5364 | 11591.06 | 8414.2254 | 8413.0088 | 8495.6835 | 8586.4345 | 8772.9095 | 8906.9301 | 8979.4988 | 9058.7358 | 9131.3813 | 9262.886 | 9426.1757 | 9414.4516 | 9414.4516 | 9414.4516 | 9414.4516 | 9414.4516 | 9414.4516 | 9414.4516 | 9414.4516 | 9414.4516 | 9414.4516 | 9414.4516 | 9414.4516 | 9414.4516 | 9414.4516 | 9414.4516 | 9414.4516 |  | 22897.8708 | 29622.1608 | 31380.5115 | 23356.5141 | 23362.8785 | 23542.5379 | 24018.1561 | 24335.71 | 24647.072 | 25011.39 | 25348.3896 | 25676.0371 | 25712.5646 | 26095.1437 | 25803.3727 | 25803.3727 | 25803.3727 | 25803.3727 | 25803.3727 | 25803.3727 | 25803.3727 | 25803.3727 | 25803.3727 | 25803.3727 | 25803.3727 | 25803.3727 | 25803.3727 | 25803.3727 | 25803.3727 | 25803.3727
30% | 3808.7911 | 5052.6595 | 5391.0326 | 3913.4784 | 3912.9126 | 3951.3648 | 3993.5734 | 4080.3034 | 4142.6367 | 4176.3886 | 4213.2419 | 4247.0296 | 4308.1927 | 4384.1392 | 4378.6863 | 4378.6863 | 4378.6863 | 4378.6863 | 4378.6863 | 4378.6863 | 4378.6863 | 4378.6863 | 4378.6863 | 4378.6863 | 4378.6863 | 4378.6863 | 4378.6863 | 4378.6863 | 4378.6863 | 4378.6863 |  | 21159.0479 | 27372.7075 | 28997.5323 | 21582.8627 | 21588.7438 | 21754.7602 | 22194.2608 | 22487.7002 | 22775.418 | 23112.0703 | 23423.4788 | 23726.2453 | 23759.999 | 24113.5257 | 23843.9113 | 23843.9113 | 23843.9113 | 23843.9113 | 23843.9113 | 23843.9113 | 23843.9113 | 23843.9113 | 23843.9113 | 23843.9113 | 23843.9113 | 23843.9113 | 23843.9113 | 23843.9113 | 23843.9113 | 23843.9113
25% | 2600.5659 | 3449.8542 | 3680.8886 | 2672.0443 | 2671.658 | 2697.9124 | 2726.7315 | 2785.949 | 2828.509 | 2851.5541 | 2876.7168 | 2899.7863 | 2941.5473 | 2993.402 | 2989.6789 | 2989.6789 | 2989.6789 | 2989.6789 | 2989.6789 | 2989.6789 | 2989.6789 | 2989.6789 | 2989.6789 | 2989.6789 | 2989.6789 | 2989.6789 | 2989.6789 | 2989.6789 | 2989.6789 | 2989.6789 |  | 6103.1255 | 7895.3963 | 8364.0615 | 6225.3708 | 6227.0672 | 6274.953 | 6401.7228 | 6486.3626 | 6569.352 | 6666.4562 | 6756.279 | 6843.6091 | 6853.345 | 6955.3165 | 6877.5487 | 6877.5487 | 6877.5487 | 6877.5487 | 6877.5487 | 6877.5487 | 6877.5487 | 6877.5487 | 6877.5487 | 6877.5487 | 6877.5487 | 6877.5487 | 6877.5487 | 6877.5487 | 6877.5487 | 6877.5487
20% | 1575.389 | 2089.8768 | 2229.8344 | 1618.6897 | 1618.4557 | 1634.3602 | 1651.8185 | 1687.6917 | 1713.4739 | 1727.4344 | 1742.6776 | 1756.6528 | 1781.9511 | 1813.364 | 1811.1086 | 1811.1086 | 1811.1086 | 1811.1086 | 1811.1086 | 1811.1086 | 1811.1086 | 1811.1086 | 1811.1086 | 1811.1086 | 1811.1086 | 1811.1086 | 1811.1086 | 1811.1086 | 1811.1086 | 1811.1086 |  | 1637.7285 | 2118.6711 | 2244.4339 | 1670.5321 | 1670.9873 | 1683.8372 | 1717.8549 | 1740.5673 | 1762.8369 | 1788.8941 | 1812.9974 | 1836.4318 | 1839.0444 | 1866.4076 | 1845.5392 | 1845.5392 | 1845.5392 | 1845.5392 | 1845.5392 | 1845.5392 | 1845.5392 | 1845.5392 | 1845.5392 | 1845.5392 | 1845.5392 | 1845.5392 | 1845.5392 | 1845.5392 | 1845.5392 | 1845.5392
15% | 1008.6332 | 1338.0309 | 1427.6379 | 1036.3562 | 1036.2064 | 1046.3892 | 1057.5667 | 1080.5343 | 1097.0412 | 1105.9793 | 1115.7387 | 1124.6863 | 1140.8833 | 1160.9953 | 1159.5512 | 1159.5512 | 1159.5512 | 1159.5512 | 1159.5512 | 1159.5512 | 1159.5512 | 1159.5512 | 1159.5512 | 1159.5512 | 1159.5512 | 1159.5512 | 1159.5512 | 1159.5512 | 1159.5512 | 1159.5512 |  | 903.3078 | 1168.5771 | 1237.943 | 921.401 | 921.6521 | 928.7395 | 947.5024 | 960.0297 | 972.3127 | 986.6849 | 999.9793 | 1012.9048 | 1014.3458 | 1029.4383 | 1017.9281 | 1017.9281 | 1017.9281 | 1017.9281 | 1017.9281 | 1017.9281 | 1017.9281 | 1017.9281 | 1017.9281 | 1017.9281 | 1017.9281 | 1017.9281 | 1017.9281 | 1017.9281 | 1017.9281 | 1017.9281
10% | 675.0905 | 895.5604 | 955.5354 | 693.6458 | 693.5455 | 700.361 | 707.8423 | 723.2148 | 734.2631 | 740.2454 | 746.7775 | 752.7662 | 763.6071 | 777.0682 | 776.1017 | 776.1017 | 776.1017 | 776.1017 | 776.1017 | 776.1017 | 776.1017 | 776.1017 | 776.1017 | 776.1017 | 776.1017 | 776.1017 | 776.1017 | 776.1017 | 776.1017 | 776.1017 |  | 211.1088 | 273.1039 | 289.3152 | 215.3373 | 215.396 | 217.0524 | 221.4374 | 224.3651 | 227.2357 | 230.5946 | 233.7016 | 236.7223 | 237.0591 | 240.5863 | 237.8963 | 237.8963 | 237.8963 | 237.8963 | 237.8963 | 237.8963 | 237.8963 | 237.8963 | 237.8963 | 237.8963 | 237.8963 | 237.8963 | 237.8963 | 237.8963 | 237.8963 | 237.8963
5% | 480.3015 | 637.1576 | 679.8276 | 493.503 | 493.4316 | 498.2806 | 503.6032 | 514.5401 | 522.4006 | 526.6568 | 531.3041 | 535.5649 | 543.2778 | 552.8549 | 552.1673 | 552.1673 | 552.1673 | 552.1673 | 552.1673 | 552.1673 | 552.1673 | 552.1673 | 552.1673 | 552.1673 | 552.1673 | 552.1673 | 552.1673 | 552.1673 | 552.1673 | 552.1673 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9.992e-14% | 42.1598 | 55.9283 | 59.6738 | 43.3186 | 43.3123 | 43.738 | 44.2052 | 45.1652 | 45.8552 | 46.2288 | 46.6367 | 47.0107 | 47.6877 | 48.5284 | 48.468 | 48.468 | 48.468 | 48.468 | 48.468 | 48.468 | 48.468 | 48.468 | 48.468 | 48.468 | 48.468 | 48.468 | 48.468 | 48.468 | 48.468 | 48.468 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E @ R (MWh) | 112911.4176 | 149785.8315 | 159816.886 | 116014.8683 | 115998.0942 | 117138.0077 | 118389.2779 | 120960.3846 | 122808.2529 | 123808.8266 | 124901.3408 | 125902.9741 | 127716.1527 | 129967.5826 | 129805.9313 | 129805.9313 | 129805.9313 | 129805.9313 | 129805.9313 | 129805.9313 | 129805.9313 | 129805.9313 | 129805.9313 | 129805.9313 | 129805.9313 | 129805.9313 | 129805.9313 | 129805.9313 | 129805.9313 | 129805.9313 | E @ R (MWh) | 109518.1284 | 141679.7064 | 150089.7144 | 111711.7715 | 111742.2116 | 112601.5042 | 114876.3363 | 116395.1634 | 117884.3755 | 119626.8702 | 121238.7043 | 122805.8079 | 122980.5154 | 124810.3514 | 123414.8412 | 123414.8412 | 123414.8412 | 123414.8412 | 123414.8412 | 123414.8412 | 123414.8412 | 123414.8412 | 123414.8412 | 123414.8412 | 123414.8412 | 123414.8412 | 123414.8412 | 123414.8412 | 123414.8412 | 123414.8412
Option 5 Summer POE50 W E @ R (MWh) N 2 | 79037.9923 | 104850.082 | 111871.8202 | 81210.4078 | 81198.666 | 81996.6054 | 82872.4945 | 84672.2692 | 85965.777 | 86666.1786 | 87430.9386 | 88132.0818 | 89401.3069 | 90977.3078 | 90864.1519 | 90864.1519 | 90864.1519 | 90864.1519 | 90864.1519 | 90864.1519 | 90864.1519 | 90864.1519 | 90864.1519 | 90864.1519 | 90864.1519 | 90864.1519 | 90864.1519 | 90864.1519 | 90864.1519 | 90864.1519 | Option 5 Summer POE10 W E @ R (MWh) N 2 | 32855.4385 | 42503.9119 | 45026.9143 | 33513.5314 | 33522.6635 | 33780.4512 | 34462.9009 | 34918.549 | 35365.3126 | 35888.0611 | 36371.6113 | 36841.7424 | 36894.1546 | 37443.1054 | 37024.4524 | 37024.4524 | 37024.4524 | 37024.4524 | 37024.4524 | 37024.4524 | 37024.4524 | 37024.4524 | 37024.4524 | 37024.4524 | 37024.4524 | 37024.4524 | 37024.4524 | 37024.4524 | 37024.4524 | 37024.4524
Option 6 -
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | 73.4908 | 101.8011 | 109.1509 | 110.3988 | 111.3674 | 113.0455 | 116.8717 | 119.4274 | 122.671 | 124.3515 | 125.8258 | 123.0846 | 126.2829 | 131.3148 | 127.4847 | 127.4847 | 127.4847 | 127.4847 | 127.4847 | 127.4847 | 127.4847 | 127.4847 | 127.4847 | 127.4847 | 127.4847 | 127.4847 | 127.4847 | 127.4847 | 127.4847 | 127.4847 |  | 78.6411 | 106.5944 | 114.2314 | 115.4081 | 116.1495 | 117.791 | 121.6771 | 123.7926 | 127.8346 | 140.1348 | 129.9793 | 127.9882 | 130.6605 | 136.5124 | 132.5403 | 132.5403 | 132.5403 | 132.5403 | 132.5403 | 132.5403 | 132.5403 | 132.5403 | 132.5403 | 132.5403 | 132.5403 | 132.5403 | 132.5403 | 132.5403 | 132.5403 | 132.5403
98% | 87.3027 | 120.9335 | 129.6647 | 131.1472 | 132.2978 | 134.2912 | 138.8365 | 141.8726 | 145.7258 | 147.722 | 149.4734 | 146.2171 | 150.0165 | 155.9941 | 151.4442 | 151.4442 | 151.4442 | 151.4442 | 151.4442 | 151.4442 | 151.4442 | 151.4442 | 151.4442 | 151.4442 | 151.4442 | 151.4442 | 151.4442 | 151.4442 | 151.4442 | 151.4442 |  | 93.4209 | 126.6277 | 135.7001 | 137.0978 | 137.9786 | 139.9286 | 144.5451 | 147.0581 | 151.8598 | 166.4717 | 154.4076 | 152.0423 | 155.2168 | 162.1685 | 157.4499 | 157.4499 | 157.4499 | 157.4499 | 157.4499 | 157.4499 | 157.4499 | 157.4499 | 157.4499 | 157.4499 | 157.4499 | 157.4499 | 157.4499 | 157.4499 | 157.4499 | 157.4499
97% | 172.8327 | 239.4116 | 256.6966 | 259.6314 | 261.9093 | 265.8557 | 274.854 | 280.8645 | 288.4926 | 292.4446 | 295.9119 | 289.4652 | 296.9869 | 308.8207 | 299.8133 | 299.8133 | 299.8133 | 299.8133 | 299.8133 | 299.8133 | 299.8133 | 299.8133 | 299.8133 | 299.8133 | 299.8133 | 299.8133 | 299.8133 | 299.8133 | 299.8133 | 299.8133 |  | 184.945 | 250.6842 | 268.6448 | 271.4119 | 273.1556 | 277.0161 | 286.1552 | 291.1302 | 300.6362 | 329.5634 | 305.68 | 300.9974 | 307.2819 | 321.0443 | 311.7028 | 311.7028 | 311.7028 | 311.7028 | 311.7028 | 311.7028 | 311.7028 | 311.7028 | 311.7028 | 311.7028 | 311.7028 | 311.7028 | 311.7028 | 311.7028 | 311.7028 | 311.7028
95% | 510.5211 | 707.185 | 758.2422 | 766.9113 | 773.6398 | 785.297 | 811.8764 | 829.6304 | 852.1628 | 863.8365 | 874.0782 | 855.0358 | 877.2537 | 912.2089 | 885.6025 | 885.6025 | 885.6025 | 885.6025 | 885.6025 | 885.6025 | 885.6025 | 885.6025 | 885.6025 | 885.6025 | 885.6025 | 885.6025 | 885.6025 | 885.6025 | 885.6025 | 885.6025 |  | 546.299 | 740.4826 | 793.5354 | 801.7091 | 806.8595 | 818.2629 | 845.2585 | 859.9539 | 888.0332 | 973.4795 | 902.9316 | 889.1001 | 907.6635 | 948.3155 | 920.7222 | 920.7222 | 920.7222 | 920.7222 | 920.7222 | 920.7222 | 920.7222 | 920.7222 | 920.7222 | 920.7222 | 920.7222 | 920.7222 | 920.7222 | 920.7222 | 920.7222 | 920.7222
90% | 2814.8088 | 3899.1347 | 4180.6436 | 4228.4418 | 4265.5399 | 4329.8131 | 4476.3615 | 4574.25 | 4698.4845 | 4762.8484 | 4819.3169 | 4714.3248 | 4836.8255 | 5029.5548 | 4882.8573 | 4882.8573 | 4882.8573 | 4882.8573 | 4882.8573 | 4882.8573 | 4882.8573 | 4882.8573 | 4882.8573 | 4882.8573 | 4882.8573 | 4882.8573 | 4882.8573 | 4882.8573 | 4882.8573 | 4882.8573 |  | 3012.0741 | 4082.7244 | 4375.2363 | 4420.3027 | 4448.7 | 4511.5741 | 4660.4169 | 4741.4413 | 4896.2592 | 5367.3759 | 4978.4031 | 4902.1418 | 5004.4932 | 5228.6319 | 5076.4935 | 5076.4935 | 5076.4935 | 5076.4935 | 5076.4935 | 5076.4935 | 5076.4935 | 5076.4935 | 5076.4935 | 5076.4935 | 5076.4935 | 5076.4935 | 5076.4935 | 5076.4935 | 5076.4935 | 5076.4935
85% | 6876.3763 | 9525.3066 | 10213.0129 | 10329.7805 | 10420.4084 | 10577.4231 | 10935.4305 | 11174.565 | 11478.0609 | 11635.2975 | 11773.246 | 11516.7578 | 11816.0183 | 12286.8422 | 11928.4707 | 11928.4707 | 11928.4707 | 11928.4707 | 11928.4707 | 11928.4707 | 11928.4707 | 11928.4707 | 11928.4707 | 11928.4707 | 11928.4707 | 11928.4707 | 11928.4707 | 11928.4707 | 11928.4707 | 11928.4707 |  | 7358.2813 | 9973.8032 | 10688.3888 | 10798.4829 | 10867.8555 | 11021.4524 | 11385.0646 | 11583.0015 | 11961.2104 | 13112.1147 | 12161.8821 | 11975.5812 | 12225.6185 | 12773.1733 | 12401.51 | 12401.51 | 12401.51 | 12401.51 | 12401.51 | 12401.51 | 12401.51 | 12401.51 | 12401.51 | 12401.51 | 12401.51 | 12401.51 | 12401.51 | 12401.51 | 12401.51 | 12401.51
80% | 10687.9274 | 14805.1503 | 15874.0497 | 16055.5412 | 16196.4038 | 16440.4513 | 16996.9008 | 17368.5868 | 17840.3094 | 18084.7017 | 18299.1145 | 17900.4559 | 18365.5953 | 19097.3952 | 18540.3797 | 18540.3797 | 18540.3797 | 18540.3797 | 18540.3797 | 18540.3797 | 18540.3797 | 18540.3797 | 18540.3797 | 18540.3797 | 18540.3797 | 18540.3797 | 18540.3797 | 18540.3797 | 18540.3797 | 18540.3797 |  | 11436.9506 | 15502.2469 | 16612.9248 | 16784.0437 | 16891.8693 | 17130.6044 | 17695.7655 | 18003.4182 | 18591.267 | 20380.1135 | 18903.1703 | 18613.6034 | 19002.2355 | 19853.298 | 19275.623 | 19275.623 | 19275.623 | 19275.623 | 19275.623 | 19275.623 | 19275.623 | 19275.623 | 19275.623 | 19275.623 | 19275.623 | 19275.623 | 19275.623 | 19275.623 | 19275.623 | 19275.623
75% | 11791.7667 | 16334.2127 | 17513.507 | 17713.7428 | 17869.1536 | 18138.406 | 18752.3252 | 19162.3985 | 19682.8403 | 19952.4731 | 20189.0303 | 19749.1986 | 20262.3772 | 21069.7567 | 20455.2132 | 20455.2132 | 20455.2132 | 20455.2132 | 20455.2132 | 20455.2132 | 20455.2132 | 20455.2132 | 20455.2132 | 20455.2132 | 20455.2132 | 20455.2132 | 20455.2132 | 20455.2132 | 20455.2132 | 20455.2132 |  | 12618.1483 | 17103.3048 | 18328.6925 | 18517.4844 | 18636.4461 | 18899.8376 | 19523.368 | 19862.7948 | 20511.356 | 22484.9529 | 20855.4725 | 20535.9993 | 20964.769 | 21903.7284 | 21266.3917 | 21266.3917 | 21266.3917 | 21266.3917 | 21266.3917 | 21266.3917 | 21266.3917 | 21266.3917 | 21266.3917 | 21266.3917 | 21266.3917 | 21266.3917 | 21266.3917 | 21266.3917 | 21266.3917 | 21266.3917
70% | 12669.5942 | 17550.1984 | 18817.2842 | 19032.4264 | 19199.4066 | 19488.7033 | 20148.3251 | 20588.926 | 21148.1115 | 21437.817 | 21691.9844 | 21219.4098 | 21770.7916 | 22638.2758 | 21977.983 | 21977.983 | 21977.983 | 21977.983 | 21977.983 | 21977.983 | 21977.983 | 21977.983 | 21977.983 | 21977.983 | 21977.983 | 21977.983 | 21977.983 | 21977.983 | 21977.983 | 21977.983 |  | 13557.495 | 18376.5449 | 19693.1554 | 19896.0018 | 20023.8195 | 20306.8189 | 20976.7675 | 21341.4626 | 22038.3054 | 24158.8249 | 22408.0393 | 22064.7832 | 22525.4722 | 23534.3317 | 22849.549 | 22849.549 | 22849.549 | 22849.549 | 22849.549 | 22849.549 | 22849.549 | 22849.549 | 22849.549 | 22849.549 | 22849.549 | 22849.549 | 22849.549 | 22849.549 | 22849.549 | 22849.549
65% | 13351.323 | 18494.5441 | 19829.8096 | 20056.5282 | 20232.4932 | 20537.3565 | 21232.4714 | 21696.7803 | 22286.0546 | 22591.3486 | 22859.1924 | 22361.1894 | 22942.24 | 23856.402 | 23160.5801 | 23160.5801 | 23160.5801 | 23160.5801 | 23160.5801 | 23160.5801 | 23160.5801 | 23160.5801 | 23160.5801 | 23160.5801 | 23160.5801 | 23160.5801 | 23160.5801 | 23160.5801 | 23160.5801 | 23160.5801 |  | 14287.0002 | 19365.3548 | 20752.8099 | 20966.571 | 21101.2664 | 21399.4935 | 22105.4909 | 22489.8096 | 23224.1482 | 25458.7693 | 23613.7769 | 23252.0508 | 23737.5287 | 24800.6731 | 24079.0435 | 24079.0435 | 24079.0435 | 24079.0435 | 24079.0435 | 24079.0435 | 24079.0435 | 24079.0435 | 24079.0435 | 24079.0435 | 24079.0435 | 24079.0435 | 24079.0435 | 24079.0435 | 24079.0435 | 24079.0435
60% | 14698.1621 | 20360.2151 | 21830.1779 | 22079.7671 | 22273.483 | 22609.0999 | 23374.3358 | 23885.4827 | 24534.2012 | 24870.2922 | 25165.1552 | 24616.9152 | 25256.5804 | 26262.9602 | 25496.946 | 25496.946 | 25496.946 | 25496.946 | 25496.946 | 25496.946 | 25496.946 | 25496.946 | 25496.946 | 25496.946 | 25496.946 | 25496.946 | 25496.946 | 25496.946 | 25496.946 | 25496.946 |  | 15728.2275 | 21318.8704 | 22846.2875 | 23081.6122 | 23229.8952 | 23558.2066 | 24335.4227 | 24758.5102 | 25566.9267 | 28026.9692 | 25995.8598 | 25597.644 | 26132.0954 | 27302.4864 | 26508.0611 | 26508.0611 | 26508.0611 | 26508.0611 | 26508.0611 | 26508.0611 | 26508.0611 | 26508.0611 | 26508.0611 | 26508.0611 | 26508.0611 | 26508.0611 | 26508.0611 | 26508.0611 | 26508.0611 | 26508.0611
55% | 16350.7821 | 22649.4603 | 24284.7017 | 24562.354 | 24777.8508 | 25151.2035 | 26002.4804 | 26571.0991 | 27292.7577 | 27666.6379 | 27994.6544 | 27384.7719 | 28096.3592 | 29215.8935 | 28363.7508 | 28363.7508 | 28363.7508 | 28363.7508 | 28363.7508 | 28363.7508 | 28363.7508 | 28363.7508 | 28363.7508 | 28363.7508 | 28363.7508 | 28363.7508 | 28363.7508 | 28363.7508 | 28363.7508 | 28363.7508 |  | 17496.6651 | 23715.9042 | 25415.0598 | 25676.8438 | 25841.7993 | 26207.0251 | 27071.6291 | 27542.2874 | 28441.6 | 31178.2427 | 28918.7611 | 28475.7711 | 29070.3146 | 30372.3011 | 29488.5529 | 29488.5529 | 29488.5529 | 29488.5529 | 29488.5529 | 29488.5529 | 29488.5529 | 29488.5529 | 29488.5529 | 29488.5529 | 29488.5529 | 29488.5529 | 29488.5529 | 29488.5529 | 29488.5529 | 29488.5529
50% | 16573.101 | 22957.4214 | 24614.8968 | 24896.3244 | 25114.7512 | 25493.1803 | 26356.0319 | 26932.3821 | 27663.8529 | 28042.8167 | 28375.2932 | 27757.1182 | 28478.3809 | 29613.1373 | 28749.4081 | 28749.4081 | 28749.4081 | 28749.4081 | 28749.4081 | 28749.4081 | 28749.4081 | 28749.4081 | 28749.4081 | 28749.4081 | 28749.4081 | 28749.4081 | 28749.4081 | 28749.4081 | 28749.4081 | 28749.4081 |  | 17734.5645 | 24038.3655 | 25760.6242 | 26025.9676 | 26193.1661 | 26563.3577 | 27439.7177 | 27916.7755 | 28828.3158 | 31602.1683 | 29311.9648 | 28862.9515 | 29465.579 | 30785.2684 | 29889.5039 | 29889.5039 | 29889.5039 | 29889.5039 | 29889.5039 | 29889.5039 | 29889.5039 | 29889.5039 | 29889.5039 | 29889.5039 | 29889.5039 | 29889.5039 | 29889.5039 | 29889.5039 | 29889.5039 | 29889.5039
45% | 12791.4633 | 17719.0143 | 18998.2882 | 19215.4999 | 19384.0862 | 19676.1657 | 20342.1324 | 20786.9714 | 21351.5358 | 21644.0279 | 21900.6402 | 21423.5199 | 21980.2054 | 22856.034 | 22189.3899 | 22189.3899 | 22189.3899 | 22189.3899 | 22189.3899 | 22189.3899 | 22189.3899 | 22189.3899 | 22189.3899 | 22189.3899 | 22189.3899 | 22189.3899 | 22189.3899 | 22189.3899 | 22189.3899 | 22189.3899 |  | 13687.9049 | 18553.3094 | 19882.5844 | 20087.382 | 20216.4292 | 20502.1508 | 21178.5436 | 21546.7467 | 22250.2924 | 24391.2093 | 22623.5828 | 22277.025 | 22742.1454 | 23760.7091 | 23069.3395 | 23069.3395 | 23069.3395 | 23069.3395 | 23069.3395 | 23069.3395 | 23069.3395 | 23069.3395 | 23069.3395 | 23069.3395 | 23069.3395 | 23069.3395 | 23069.3395 | 23069.3395 | 23069.3395 | 23069.3395
40% | 6284.3875 | 8705.2708 | 9333.7723 | 9440.4874 | 9523.3131 | 9666.8104 | 9993.9968 | 10212.5442 | 10489.9121 | 10633.6121 | 10759.6846 | 10525.2775 | 10798.7746 | 11229.0652 | 10901.546 | 10901.546 | 10901.546 | 10901.546 | 10901.546 | 10901.546 | 10901.546 | 10901.546 | 10901.546 | 10901.546 | 10901.546 | 10901.546 | 10901.546 | 10901.546 | 10901.546 | 10901.546 |  | 6724.8052 | 9115.1562 | 9768.223 | 9868.8391 | 9932.2394 | 10072.6131 | 10404.9218 | 10585.8183 | 10931.4671 | 11983.2898 | 11114.863 | 10944.6007 | 11173.1122 | 11673.5279 | 11333.8612 | 11333.8612 | 11333.8612 | 11333.8612 | 11333.8612 | 11333.8612 | 11333.8612 | 11333.8612 | 11333.8612 | 11333.8612 | 11333.8612 | 11333.8612 | 11333.8612 | 11333.8612 | 11333.8612 | 11333.8612
35% | 2348.7515 | 3253.5419 | 3488.4405 | 3528.3246 | 3559.2802 | 3612.9114 | 3735.1954 | 3816.8761 | 3920.5407 | 3974.2477 | 4021.3665 | 3933.7583 | 4035.9762 | 4196.7946 | 4074.3863 | 4074.3863 | 4074.3863 | 4074.3863 | 4074.3863 | 4074.3863 | 4074.3863 | 4074.3863 | 4074.3863 | 4074.3863 | 4074.3863 | 4074.3863 | 4074.3863 | 4074.3863 | 4074.3863 | 4074.3863 |  | 2513.3549 | 3406.7341 | 3650.8138 | 3688.4184 | 3712.1139 | 3764.5777 | 3888.7761 | 3956.3851 | 4085.5692 | 4478.6815 | 4154.1123 | 4090.4778 | 4175.8826 | 4362.9099 | 4235.9615 | 4235.9615 | 4235.9615 | 4235.9615 | 4235.9615 | 4235.9615 | 4235.9615 | 4235.9615 | 4235.9615 | 4235.9615 | 4235.9615 | 4235.9615 | 4235.9615 | 4235.9615 | 4235.9615 | 4235.9615
30% | 1171.4214 | 1622.6784 | 1739.8323 | 1759.7242 | 1775.163 | 1801.9112 | 1862.8993 | 1903.637 | 1955.3388 | 1982.1248 | 2005.6249 | 1961.931 | 2012.9114 | 2093.1183 | 2032.0682 | 2032.0682 | 2032.0682 | 2032.0682 | 2032.0682 | 2032.0682 | 2032.0682 | 2032.0682 | 2032.0682 | 2032.0682 | 2032.0682 | 2032.0682 | 2032.0682 | 2032.0682 | 2032.0682 | 2032.0682 |  | 1253.516 | 1699.0818 | 1820.8147 | 1839.5697 | 1851.3876 | 1877.5536 | 1939.4965 | 1973.2159 | 2037.6455 | 2233.7072 | 2071.8308 | 2040.0936 | 2082.6886 | 2175.967 | 2112.6525 | 2112.6525 | 2112.6525 | 2112.6525 | 2112.6525 | 2112.6525 | 2112.6525 | 2112.6525 | 2112.6525 | 2112.6525 | 2112.6525 | 2112.6525 | 2112.6525 | 2112.6525 | 2112.6525 | 2112.6525
25% | 690.592 | 956.6232 | 1025.6893 | 1037.4162 | 1046.5179 | 1062.2869 | 1098.2414 | 1122.2576 | 1152.7376 | 1168.5288 | 1182.3829 | 1156.6239 | 1186.6785 | 1233.9632 | 1197.9721 | 1197.9721 | 1197.9721 | 1197.9721 | 1197.9721 | 1197.9721 | 1197.9721 | 1197.9721 | 1197.9721 | 1197.9721 | 1197.9721 | 1197.9721 | 1197.9721 | 1197.9721 | 1197.9721 | 1197.9721 |  | 738.9896 | 1001.6655 | 1073.4311 | 1084.4878 | 1091.4549 | 1106.8806 | 1143.398 | 1163.2767 | 1201.2601 | 1316.845 | 1221.4135 | 1202.7034 | 1227.8145 | 1282.8053 | 1245.4793 | 1245.4793 | 1245.4793 | 1245.4793 | 1245.4793 | 1245.4793 | 1245.4793 | 1245.4793 | 1245.4793 | 1245.4793 | 1245.4793 | 1245.4793 | 1245.4793 | 1245.4793 | 1245.4793 | 1245.4793
20% | 348.989 | 483.4272 | 518.3296 | 524.2558 | 528.8553 | 536.8241 | 554.9937 | 567.1302 | 582.5332 | 590.5132 | 597.5144 | 584.4971 | 599.6851 | 623.5803 | 605.3923 | 605.3923 | 605.3923 | 605.3923 | 605.3923 | 605.3923 | 605.3923 | 605.3923 | 605.3923 | 605.3923 | 605.3923 | 605.3923 | 605.3923 | 605.3923 | 605.3923 | 605.3923 |  | 373.4466 | 506.1893 | 542.4558 | 548.0433 | 551.5641 | 559.3594 | 577.8134 | 587.8591 | 607.0539 | 665.4645 | 617.2384 | 607.7833 | 620.4731 | 648.2626 | 629.3999 | 629.3999 | 629.3999 | 629.3999 | 629.3999 | 629.3999 | 629.3999 | 629.3999 | 629.3999 | 629.3999 | 629.3999 | 629.3999 | 629.3999 | 629.3999 | 629.3999 | 629.3999
15% | 142.1807 | 196.9518 | 211.1713 | 213.5857 | 215.4596 | 218.7061 | 226.1085 | 231.053 | 237.3283 | 240.5795 | 243.4318 | 238.1285 | 244.3162 | 254.0512 | 246.6413 | 246.6413 | 246.6413 | 246.6413 | 246.6413 | 246.6413 | 246.6413 | 246.6413 | 246.6413 | 246.6413 | 246.6413 | 246.6413 | 246.6413 | 246.6413 | 246.6413 | 246.6413 |  | 152.1449 | 206.2253 | 221.0005 | 223.2769 | 224.7113 | 227.8872 | 235.4055 | 239.4982 | 247.3183 | 271.1152 | 251.4675 | 247.6154 | 252.7853 | 264.107 | 256.4222 | 256.4222 | 256.4222 | 256.4222 | 256.4222 | 256.4222 | 256.4222 | 256.4222 | 256.4222 | 256.4222 | 256.4222 | 256.4222 | 256.4222 | 256.4222 | 256.4222 | 256.4222
10% | 57.2416 | 79.2923 | 85.017 | 85.989 | 86.7435 | 88.0505 | 91.0307 | 93.0214 | 95.5478 | 96.8567 | 98.005 | 95.8699 | 98.3611 | 102.2804 | 99.2972 | 99.2972 | 99.2972 | 99.2972 | 99.2972 | 99.2972 | 99.2972 | 99.2972 | 99.2972 | 99.2972 | 99.2972 | 99.2972 | 99.2972 | 99.2972 | 99.2972 | 99.2972 |  | 61.2531 | 83.0258 | 88.9742 | 89.8907 | 90.4682 | 91.7468 | 94.7736 | 96.4213 | 99.5697 | 109.1503 | 101.2402 | 99.6893 | 101.7707 | 106.3288 | 103.2349 | 103.2349 | 103.2349 | 103.2349 | 103.2349 | 103.2349 | 103.2349 | 103.2349 | 103.2349 | 103.2349 | 103.2349 | 103.2349 | 103.2349 | 103.2349 | 103.2349 | 103.2349
5% | 48.7477 | 67.5263 | 72.4016 | 73.2294 | 73.8719 | 74.985 | 77.5229 | 79.2182 | 81.3697 | 82.4844 | 83.4623 | 81.644 | 83.7655 | 87.1033 | 84.5627 | 84.5627 | 84.5627 | 84.5627 | 84.5627 | 84.5627 | 84.5627 | 84.5627 | 84.5627 | 84.5627 | 84.5627 | 84.5627 | 84.5627 | 84.5627 | 84.5627 | 84.5627 |  | 52.164 | 70.7058 | 75.7716 | 76.5521 | 77.0439 | 78.1327 | 80.7104 | 82.1137 | 84.7948 | 92.9538 | 86.2174 | 84.8967 | 86.6693 | 90.551 | 87.9162 | 87.9162 | 87.9162 | 87.9162 | 87.9162 | 87.9162 | 87.9162 | 87.9162 | 87.9162 | 87.9162 | 87.9162 | 87.9162 | 87.9162 | 87.9162 | 87.9162 | 87.9162
9.992e-14% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E @ R (MWh) | 130541.7636 | 180829.3011 | 193884.7798 | 196101.5072 | 197821.9953 | 200802.7777 | 207599.2223 | 212138.9744 | 217900.5692 | 220885.5628 | 223504.3892 | 218635.1944 | 224316.3823 | 233254.5468 | 226451.1896 | 226451.1896 | 226451.1896 | 226451.1896 | 226451.1896 | 226451.1896 | 226451.1896 | 226451.1896 | 226451.1896 | 226451.1896 | 226451.1896 | 226451.1896 | 226451.1896 | 226451.1896 | 226451.1896 | 226451.1896 | E @ R (MWh) | 139690.2921 | 189343.6009 | 202909.3599 | 204999.3971 | 206316.373 | 209232.2711 | 216135.1177 | 219892.7708 | 227072.7236 | 248921.5973 | 230882.2942 | 227345.5395 | 232092.2705 | 242487.1014 | 235431.4111 | 235431.4111 | 235431.4111 | 235431.4111 | 235431.4111 | 235431.4111 | 235431.4111 | 235431.4111 | 235431.4111 | 235431.4111 | 235431.4111 | 235431.4111 | 235431.4111 | 235431.4111 | 235431.4111 | 235431.4111
Option 6 Winter POE50 W E @ R (MWh) N 2 | 91379.2345 | 126580.5108 | 135719.3459 | 137271.0551 | 138475.3967 | 140561.9444 | 145319.4556 | 148497.2821 | 152530.3985 | 154619.8939 | 156453.0725 | 153044.6361 | 157021.4676 | 163278.1828 | 158515.8327 | 158515.8327 | 158515.8327 | 158515.8327 | 158515.8327 | 158515.8327 | 158515.8327 | 158515.8327 | 158515.8327 | 158515.8327 | 158515.8327 | 158515.8327 | 158515.8327 | 158515.8327 | 158515.8327 | 158515.8327 | Option 6 Winter POE10 W E @ R (MWh) N 2 | 41907.0876 | 56803.0803 | 60872.808 | 61499.8191 | 61894.9119 | 62769.6813 | 64840.5353 | 65967.8312 | 68121.8171 | 74676.4792 | 69264.6882 | 68203.6618 | 69627.6812 | 72746.1304 | 70629.4233 | 70629.4233 | 70629.4233 | 70629.4233 | 70629.4233 | 70629.4233 | 70629.4233 | 70629.4233 | 70629.4233 | 70629.4233 | 70629.4233 | 70629.4233 | 70629.4233 | 70629.4233 | 70629.4233 | 70629.4233
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 94.6719 | 122.4737 | 129.7436 | 129.304 | 129.3303 | 130.0731 | 132.0395 | 133.3525 | 134.6398 | 136.1461 | 137.5394 | 138.8941 | 139.0451 | 140.6269 | 139.4206 | 139.4206 | 139.4206 | 139.4206 | 139.4206 | 139.4206 | 139.4206 | 139.4206 | 139.4206 | 139.4206 | 139.4206 | 139.4206 | 139.4206 | 139.4206 | 139.4206 | 139.4206
98% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 46.8602 | 60.6214 | 64.2198 | 64.0022 | 64.0152 | 64.3829 | 65.3562 | 66.0061 | 66.6433 | 67.3889 | 68.0786 | 68.7491 | 68.8238 | 69.6068 | 69.0097 | 69.0097 | 69.0097 | 69.0097 | 69.0097 | 69.0097 | 69.0097 | 69.0097 | 69.0097 | 69.0097 | 69.0097 | 69.0097 | 69.0097 | 69.0097 | 69.0097 | 69.0097
97% | 20.8131 | 27.6102 | 29.4592 | 29.4046 | 29.4015 | 29.6116 | 29.8423 | 30.3162 | 30.6568 | 30.8412 | 31.0426 | 31.2273 | 31.5615 | 31.9765 | 31.9467 | 31.9467 | 31.9467 | 31.9467 | 31.9467 | 31.9467 | 31.9467 | 31.9467 | 31.9467 | 31.9467 | 31.9467 | 31.9467 | 31.9467 | 31.9467 | 31.9467 | 31.9467 |  | 92.7689 | 120.0119 | 127.1357 | 126.7049 | 126.7307 | 127.4585 | 129.3855 | 130.672 | 131.9335 | 133.4095 | 134.7748 | 136.1022 | 136.2502 | 137.8002 | 136.6181 | 136.6181 | 136.6181 | 136.6181 | 136.6181 | 136.6181 | 136.6181 | 136.6181 | 136.6181 | 136.6181 | 136.6181 | 136.6181 | 136.6181 | 136.6181 | 136.6181 | 136.6181
95% | 102.4643 | 135.9269 | 145.0299 | 144.761 | 144.7458 | 145.7802 | 146.9157 | 149.2489 | 150.9258 | 151.8338 | 152.8252 | 153.7342 | 155.3796 | 157.4227 | 157.276 | 157.276 | 157.276 | 157.276 | 157.276 | 157.276 | 157.276 | 157.276 | 157.276 | 157.276 | 157.276 | 157.276 | 157.276 | 157.276 | 157.276 | 157.276 |  | 137.0126 | 177.2483 | 187.7696 | 187.1334 | 187.1714 | 188.2465 | 191.0924 | 192.9925 | 194.8556 | 197.0355 | 199.052 | 201.0125 | 201.2311 | 203.5203 | 201.7745 | 201.7745 | 201.7745 | 201.7745 | 201.7745 | 201.7745 | 201.7745 | 201.7745 | 201.7745 | 201.7745 | 201.7745 | 201.7745 | 201.7745 | 201.7745 | 201.7745 | 201.7745
90% | 177.7116 | 235.7483 | 251.5362 | 251.0698 | 251.0434 | 252.8375 | 254.8069 | 258.8536 | 261.762 | 263.3368 | 265.0563 | 266.6327 | 269.4865 | 273.03 | 272.7756 | 272.7756 | 272.7756 | 272.7756 | 272.7756 | 272.7756 | 272.7756 | 272.7756 | 272.7756 | 272.7756 | 272.7756 | 272.7756 | 272.7756 | 272.7756 | 272.7756 | 272.7756 |  | 594.078 | 768.5376 | 814.1574 | 811.3985 | 811.5637 | 816.2249 | 828.5646 | 836.8035 | 844.8817 | 854.3338 | 863.0771 | 871.5778 | 872.5255 | 882.4514 | 874.8815 | 874.8815 | 874.8815 | 874.8815 | 874.8815 | 874.8815 | 874.8815 | 874.8815 | 874.8815 | 874.8815 | 874.8815 | 874.8815 | 874.8815 | 874.8815 | 874.8815 | 874.8815
85% | 504.3166 | 669.0154 | 713.8189 | 712.4955 | 712.4205 | 717.5119 | 723.1007 | 734.5845 | 742.838 | 747.307 | 752.1867 | 756.6605 | 764.759 | 774.815 | 774.093 | 774.093 | 774.093 | 774.093 | 774.093 | 774.093 | 774.093 | 774.093 | 774.093 | 774.093 | 774.093 | 774.093 | 774.093 | 774.093 | 774.093 | 774.093 |  | 561.9657 | 726.995 | 770.1489 | 767.5392 | 767.6954 | 772.1046 | 783.7774 | 791.5709 | 799.2124 | 808.1536 | 816.4243 | 824.4655 | 825.362 | 834.7513 | 827.5906 | 827.5906 | 827.5906 | 827.5906 | 827.5906 | 827.5906 | 827.5906 | 827.5906 | 827.5906 | 827.5906 | 827.5906 | 827.5906 | 827.5906 | 827.5906 | 827.5906 | 827.5906
80% | 704.4422 | 934.4978 | 997.0804 | 995.2318 | 995.1271 | 1002.2389 | 1010.0454 | 1026.0863 | 1037.6149 | 1043.8574 | 1050.6735 | 1056.9226 | 1068.2348 | 1082.2812 | 1081.2727 | 1081.2727 | 1081.2727 | 1081.2727 | 1081.2727 | 1081.2727 | 1081.2727 | 1081.2727 | 1081.2727 | 1081.2727 | 1081.2727 | 1081.2727 | 1081.2727 | 1081.2727 | 1081.2727 | 1081.2727 |  | 392.484 | 507.7425 | 537.8818 | 536.0591 | 536.1682 | 539.2477 | 547.4001 | 552.8431 | 558.1801 | 564.4247 | 570.2011 | 575.8172 | 576.4433 | 583.0009 | 577.9998 | 577.9998 | 577.9998 | 577.9998 | 577.9998 | 577.9998 | 577.9998 | 577.9998 | 577.9998 | 577.9998 | 577.9998 | 577.9998 | 577.9998 | 577.9998 | 577.9998 | 577.9998
75% | 1836.3528 | 2436.0657 | 2599.2074 | 2594.3882 | 2594.1154 | 2612.6546 | 2633.0048 | 2674.8204 | 2704.8735 | 2721.1465 | 2738.9148 | 2755.205 | 2784.6939 | 2821.3104 | 2818.6814 | 2818.6814 | 2818.6814 | 2818.6814 | 2818.6814 | 2818.6814 | 2818.6814 | 2818.6814 | 2818.6814 | 2818.6814 | 2818.6814 | 2818.6814 | 2818.6814 | 2818.6814 | 2818.6814 | 2818.6814 |  | 700.5244 | 906.2435 | 960.0375 | 956.7843 | 956.979 | 962.4754 | 977.0262 | 986.7412 | 996.2669 | 1007.4126 | 1017.7226 | 1027.7464 | 1028.8639 | 1040.5683 | 1031.6421 | 1031.6421 | 1031.6421 | 1031.6421 | 1031.6421 | 1031.6421 | 1031.6421 | 1031.6421 | 1031.6421 | 1031.6421 | 1031.6421 | 1031.6421 | 1031.6421 | 1031.6421 | 1031.6421 | 1031.6421
70% | 3172.6584 | 4208.7797 | 4490.6388 | 4482.3127 | 4481.8414 | 4513.8714 | 4549.0304 | 4621.275 | 4673.1976 | 4701.3124 | 4732.0106 | 4760.1551 | 4811.103 | 4874.3651 | 4869.823 | 4869.823 | 4869.823 | 4869.823 | 4869.823 | 4869.823 | 4869.823 | 4869.823 | 4869.823 | 4869.823 | 4869.823 | 4869.823 | 4869.823 | 4869.823 | 4869.823 | 4869.823 |  | 1276.1675 | 1650.9325 | 1748.9307 | 1743.0043 | 1743.359 | 1753.372 | 1779.8796 | 1797.5778 | 1814.931 | 1835.2355 | 1854.0175 | 1872.2783 | 1874.3141 | 1895.6364 | 1879.3751 | 1879.3751 | 1879.3751 | 1879.3751 | 1879.3751 | 1879.3751 | 1879.3751 | 1879.3751 | 1879.3751 | 1879.3751 | 1879.3751 | 1879.3751 | 1879.3751 | 1879.3751 | 1879.3751 | 1879.3751
65% | 7968.2023 | 10570.444 | 11278.3393 | 11257.4282 | 11256.2445 | 11336.6886 | 11424.9912 | 11606.4352 | 11736.84 | 11807.4509 | 11884.55 | 11955.2357 | 12083.1924 | 12242.0767 | 12230.6689 | 12230.6689 | 12230.6689 | 12230.6689 | 12230.6689 | 12230.6689 | 12230.6689 | 12230.6689 | 12230.6689 | 12230.6689 | 12230.6689 | 12230.6689 | 12230.6689 | 12230.6689 | 12230.6689 | 12230.6689 |  | 1605.6162 | 2077.1285 | 2200.4254 | 2192.969 | 2193.4153 | 2206.0132 | 2239.3639 | 2261.631 | 2283.4639 | 2309.0102 | 2332.6409 | 2355.6158 | 2358.1771 | 2385.0038 | 2364.5446 | 2364.5446 | 2364.5446 | 2364.5446 | 2364.5446 | 2364.5446 | 2364.5446 | 2364.5446 | 2364.5446 | 2364.5446 | 2364.5446 | 2364.5446 | 2364.5446 | 2364.5446 | 2364.5446 | 2364.5446
60% | 11647.312 | 15451.0709 | 16485.8185 | 16455.2522 | 16453.5219 | 16571.109 | 16700.1831 | 16965.4041 | 17156.0199 | 17259.2335 | 17371.9312 | 17475.2541 | 17662.2915 | 17894.5364 | 17877.8614 | 17877.8614 | 17877.8614 | 17877.8614 | 17877.8614 | 17877.8614 | 17877.8614 | 17877.8614 | 17877.8614 | 17877.8614 | 17877.8614 | 17877.8614 | 17877.8614 | 17877.8614 | 17877.8614 | 17877.8614 |  | 2512.492 | 3250.3215 | 3443.2583 | 3431.5904 | 3432.2888 | 3452.0021 | 3504.1898 | 3539.0337 | 3573.1982 | 3613.1734 | 3650.151 | 3686.1024 | 3690.1105 | 3732.0893 | 3700.0745 | 3700.0745 | 3700.0745 | 3700.0745 | 3700.0745 | 3700.0745 | 3700.0745 | 3700.0745 | 3700.0745 | 3700.0745 | 3700.0745 | 3700.0745 | 3700.0745 | 3700.0745 | 3700.0745 | 3700.0745
55% | 13170.4015 | 17471.5683 | 18641.6273 | 18607.0639 | 18605.1073 | 18738.071 | 18884.0238 | 19183.9271 | 19399.4692 | 19516.1798 | 19643.6146 | 19760.4488 | 19971.9446 | 20234.5597 | 20215.7041 | 20215.7041 | 20215.7041 | 20215.7041 | 20215.7041 | 20215.7041 | 20215.7041 | 20215.7041 | 20215.7041 | 20215.7041 | 20215.7041 | 20215.7041 | 20215.7041 | 20215.7041 | 20215.7041 | 20215.7041 |  | 4828.1473 | 6246.0024 | 6616.7608 | 6594.3391 | 6595.6811 | 6633.5633 | 6733.8501 | 6800.8082 | 6866.4607 | 6943.2792 | 7014.3375 | 7083.4238 | 7091.1259 | 7171.7949 | 7110.2733 | 7110.2733 | 7110.2733 | 7110.2733 | 7110.2733 | 7110.2733 | 7110.2733 | 7110.2733 | 7110.2733 | 7110.2733 | 7110.2733 | 7110.2733 | 7110.2733 | 7110.2733 | 7110.2733 | 7110.2733
50% | 16911.4168 | 22434.3178 | 23936.7286 | 23892.3477 | 23889.8353 | 24060.567 | 24247.9772 | 24633.0672 | 24909.8334 | 25059.6953 | 25223.3277 | 25373.3483 | 25644.9189 | 25982.129 | 25957.9175 | 25957.9175 | 25957.9175 | 25957.9175 | 25957.9175 | 25957.9175 | 25957.9175 | 25957.9175 | 25957.9175 | 25957.9175 | 25957.9175 | 25957.9175 | 25957.9175 | 25957.9175 | 25957.9175 | 25957.9175 |  | 10714.812 | 13861.3711 | 14684.1724 | 14634.4134 | 14637.3915 | 14721.4613 | 14944.0217 | 15092.6176 | 15238.3161 | 15408.7947 | 15566.4901 | 15719.8092 | 15736.9019 | 15915.9256 | 15779.3945 | 15779.3945 | 15779.3945 | 15779.3945 | 15779.3945 | 15779.3945 | 15779.3945 | 15779.3945 | 15779.3945 | 15779.3945 | 15779.3945 | 15779.3945 | 15779.3945 | 15779.3945 | 15779.3945 | 15779.3945
45% | 22520.2713 | 29874.9022 | 31875.6039 | 31816.5035 | 31813.1579 | 32040.5146 | 32290.0814 | 32802.8907 | 33171.4494 | 33371.0147 | 33588.9175 | 33788.694 | 34150.3339 | 34599.3834 | 34567.1419 | 34567.1419 | 34567.1419 | 34567.1419 | 34567.1419 | 34567.1419 | 34567.1419 | 34567.1419 | 34567.1419 | 34567.1419 | 34567.1419 | 34567.1419 | 34567.1419 | 34567.1419 | 34567.1419 | 34567.1419 |  | 16236.3476 | 21004.3853 | 22251.1909 | 22175.7903 | 22180.3031 | 22307.6955 | 22644.9453 | 22870.1153 | 23090.8949 | 23349.2243 | 23588.1829 | 23820.5101 | 23846.4109 | 24117.6889 | 23910.8008 | 23910.8008 | 23910.8008 | 23910.8008 | 23910.8008 | 23910.8008 | 23910.8008 | 23910.8008 | 23910.8008 | 23910.8008 | 23910.8008 | 23910.8008 | 23910.8008 | 23910.8008 | 23910.8008 | 23910.8008
40% | 15794.9825 | 20953.2804 | 22356.5072 | 22315.0562 | 22312.7097 | 22472.1702 | 22647.2082 | 23006.8759 | 23265.371 | 23405.3395 | 23558.1694 | 23698.2861 | 23951.9286 | 24266.8772 | 24244.2641 | 24244.2641 | 24244.2641 | 24244.2641 | 24244.2641 | 24244.2641 | 24244.2641 | 24244.2641 | 24244.2641 | 24244.2641 | 24244.2641 | 24244.2641 | 24244.2641 | 24244.2641 | 24244.2641 | 24244.2641 |  | 16811.9908 | 21749.0744 | 23040.0842 | 22962.0103 | 22966.6831 | 23098.592 | 23447.7987 | 23680.9519 | 23909.559 | 24177.0472 | 24424.4778 | 24665.0419 | 24691.8611 | 24972.7569 | 24758.5339 | 24758.5339 | 24758.5339 | 24758.5339 | 24758.5339 | 24758.5339 | 24758.5339 | 24758.5339 | 24758.5339 | 24758.5339 | 24758.5339 | 24758.5339 | 24758.5339 | 24758.5339 | 24758.5339 | 24758.5339
35% | 8189.141 | 10863.5364 | 11591.06 | 11569.5691 | 11568.3525 | 11651.0272 | 11741.7782 | 11928.2532 | 12062.2738 | 12134.8425 | 12214.0795 | 12286.725 | 12418.2297 | 12581.5194 | 12569.7953 | 12569.7953 | 12569.7953 | 12569.7953 | 12569.7953 | 12569.7953 | 12569.7953 | 12569.7953 | 12569.7953 | 12569.7953 | 12569.7953 | 12569.7953 | 12569.7953 | 12569.7953 | 12569.7953 | 12569.7953 |  | 22897.8708 | 29622.1608 | 31380.5115 | 31274.1752 | 31280.5395 | 31460.199 | 31935.8172 | 32253.3711 | 32564.7331 | 32929.051 | 33266.0507 | 33593.6981 | 33630.2257 | 34012.8048 | 33721.0338 | 33721.0338 | 33721.0338 | 33721.0338 | 33721.0338 | 33721.0338 | 33721.0338 | 33721.0338 | 33721.0338 | 33721.0338 | 33721.0338 | 33721.0338 | 33721.0338 | 33721.0338 | 33721.0338 | 33721.0338
30% | 3808.7911 | 5052.6595 | 5391.0326 | 5381.0371 | 5380.4713 | 5418.9235 | 5461.132 | 5547.8621 | 5610.1954 | 5643.9473 | 5680.8006 | 5714.5882 | 5775.7514 | 5851.6979 | 5846.245 | 5846.245 | 5846.245 | 5846.245 | 5846.245 | 5846.245 | 5846.245 | 5846.245 | 5846.245 | 5846.245 | 5846.245 | 5846.245 | 5846.245 | 5846.245 | 5846.245 | 5846.245 |  | 21159.0479 | 27372.7075 | 28997.5323 | 28899.2709 | 28905.152 | 29071.1685 | 29510.6691 | 29804.1085 | 30091.8262 | 30428.4785 | 30739.887 | 31042.6535 | 31076.4072 | 31429.934 | 31160.3195 | 31160.3195 | 31160.3195 | 31160.3195 | 31160.3195 | 31160.3195 | 31160.3195 | 31160.3195 | 31160.3195 | 31160.3195 | 31160.3195 | 31160.3195 | 31160.3195 | 31160.3195 | 31160.3195 | 31160.3195
25% | 2600.5659 | 3449.8542 | 3680.8886 | 3674.0639 | 3673.6775 | 3699.9319 | 3728.7511 | 3787.9686 | 3830.5285 | 3853.5736 | 3878.7363 | 3901.8059 | 3943.5668 | 3995.4216 | 3991.6984 | 3991.6984 | 3991.6984 | 3991.6984 | 3991.6984 | 3991.6984 | 3991.6984 | 3991.6984 | 3991.6984 | 3991.6984 | 3991.6984 | 3991.6984 | 3991.6984 | 3991.6984 | 3991.6984 | 3991.6984 |  | 6103.1255 | 7895.3963 | 8364.0615 | 8335.719 | 8337.4153 | 8385.3012 | 8512.071 | 8596.7107 | 8679.7002 | 8776.8043 | 8866.6271 | 8953.9572 | 8963.6932 | 9065.6646 | 8987.8969 | 8987.8969 | 8987.8969 | 8987.8969 | 8987.8969 | 8987.8969 | 8987.8969 | 8987.8969 | 8987.8969 | 8987.8969 | 8987.8969 | 8987.8969 | 8987.8969 | 8987.8969 | 8987.8969 | 8987.8969
20% | 1575.389 | 2089.8768 | 2229.8344 | 2225.7001 | 2225.4661 | 2241.3706 | 2258.8289 | 2294.7021 | 2320.4843 | 2334.4448 | 2349.688 | 2363.6632 | 2388.9615 | 2420.3744 | 2418.119 | 2418.119 | 2418.119 | 2418.119 | 2418.119 | 2418.119 | 2418.119 | 2418.119 | 2418.119 | 2418.119 | 2418.119 | 2418.119 | 2418.119 | 2418.119 | 2418.119 | 2418.119 |  | 1637.7285 | 2118.6711 | 2244.4339 | 2236.8284 | 2237.2836 | 2250.1334 | 2284.1512 | 2306.8636 | 2329.1332 | 2355.1904 | 2379.2937 | 2402.7281 | 2405.3406 | 2432.7039 | 2411.8355 | 2411.8355 | 2411.8355 | 2411.8355 | 2411.8355 | 2411.8355 | 2411.8355 | 2411.8355 | 2411.8355 | 2411.8355 | 2411.8355 | 2411.8355 | 2411.8355 | 2411.8355 | 2411.8355 | 2411.8355
15% | 1008.6332 | 1338.0309 | 1427.6379 | 1424.9909 | 1424.8411 | 1435.0239 | 1446.2014 | 1469.169 | 1485.676 | 1494.614 | 1504.3734 | 1513.321 | 1529.518 | 1549.63 | 1548.1859 | 1548.1859 | 1548.1859 | 1548.1859 | 1548.1859 | 1548.1859 | 1548.1859 | 1548.1859 | 1548.1859 | 1548.1859 | 1548.1859 | 1548.1859 | 1548.1859 | 1548.1859 | 1548.1859 | 1548.1859 |  | 903.3078 | 1168.5771 | 1237.943 | 1233.7481 | 1233.9992 | 1241.0867 | 1259.8495 | 1272.3769 | 1284.6599 | 1299.032 | 1312.3265 | 1325.252 | 1326.693 | 1341.7855 | 1330.2753 | 1330.2753 | 1330.2753 | 1330.2753 | 1330.2753 | 1330.2753 | 1330.2753 | 1330.2753 | 1330.2753 | 1330.2753 | 1330.2753 | 1330.2753 | 1330.2753 | 1330.2753 | 1330.2753 | 1330.2753
10% | 675.0905 | 895.5604 | 955.5354 | 953.7638 | 953.6635 | 960.4789 | 967.9602 | 983.3327 | 994.381 | 1000.3634 | 1006.8954 | 1012.8841 | 1023.725 | 1037.1862 | 1036.2197 | 1036.2197 | 1036.2197 | 1036.2197 | 1036.2197 | 1036.2197 | 1036.2197 | 1036.2197 | 1036.2197 | 1036.2197 | 1036.2197 | 1036.2197 | 1036.2197 | 1036.2197 | 1036.2197 | 1036.2197 |  | 211.1088 | 273.1039 | 289.3152 | 288.3348 | 288.3935 | 290.0499 | 294.4349 | 297.3626 | 300.2332 | 303.5921 | 306.6991 | 309.7199 | 310.0566 | 313.5838 | 310.8938 | 310.8938 | 310.8938 | 310.8938 | 310.8938 | 310.8938 | 310.8938 | 310.8938 | 310.8938 | 310.8938 | 310.8938 | 310.8938 | 310.8938 | 310.8938 | 310.8938 | 310.8938
5% | 480.3015 | 637.1576 | 679.8276 | 678.5671 | 678.4957 | 683.3447 | 688.6673 | 699.6043 | 707.4647 | 711.721 | 716.3683 | 720.629 | 728.3419 | 737.919 | 737.2314 | 737.2314 | 737.2314 | 737.2314 | 737.2314 | 737.2314 | 737.2314 | 737.2314 | 737.2314 | 737.2314 | 737.2314 | 737.2314 | 737.2314 | 737.2314 | 737.2314 | 737.2314 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9.992e-14% | 42.1598 | 55.9283 | 59.6738 | 59.5631 | 59.5568 | 59.9825 | 60.4497 | 61.4097 | 62.0997 | 62.4733 | 62.8812 | 63.2552 | 63.9322 | 64.7729 | 64.7125 | 64.7125 | 64.7125 | 64.7125 | 64.7125 | 64.7125 | 64.7125 | 64.7125 | 64.7125 | 64.7125 | 64.7125 | 64.7125 | 64.7125 | 64.7125 | 64.7125 | 64.7125 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E @ R (MWh) | 112911.4176 | 149785.8315 | 159816.886 | 159520.5704 | 159503.7964 | 160643.7099 | 161894.98 | 164466.0868 | 166313.955 | 167314.5287 | 168407.043 | 169408.6762 | 171221.8548 | 173473.2847 | 173311.6334 | 173311.6334 | 173311.6334 | 173311.6334 | 173311.6334 | 173311.6334 | 173311.6334 | 173311.6334 | 173311.6334 | 173311.6334 | 173311.6334 | 173311.6334 | 173311.6334 | 173311.6334 | 173311.6334 | 173311.6334 | E @ R (MWh) | 109518.1284 | 141679.7064 | 150089.7144 | 149581.1188 | 149611.5589 | 150470.8515 | 152745.6837 | 154264.5107 | 155753.7228 | 157496.2176 | 159108.0516 | 160675.1553 | 160849.8627 | 162679.6988 | 161284.1885 | 161284.1885 | 161284.1885 | 161284.1885 | 161284.1885 | 161284.1885 | 161284.1885 | 161284.1885 | 161284.1885 | 161284.1885 | 161284.1885 | 161284.1885 | 161284.1885 | 161284.1885 | 161284.1885 | 161284.1885
Option 6 Summer POE50 W E @ R (MWh) N 2 | 79037.9923 | 104850.082 | 111871.8202 | 111664.3993 | 111652.6574 | 112450.5969 | 113326.486 | 115126.2607 | 116419.7685 | 117120.1701 | 117884.9301 | 118586.0733 | 119855.2983 | 121431.2993 | 121318.1434 | 121318.1434 | 121318.1434 | 121318.1434 | 121318.1434 | 121318.1434 | 121318.1434 | 121318.1434 | 121318.1434 | 121318.1434 | 121318.1434 | 121318.1434 | 121318.1434 | 121318.1434 | 121318.1434 | 121318.1434 | Option 6 Summer POE10 W E @ R (MWh) N 2 | 32855.4385 | 42503.9119 | 45026.9143 | 44874.3356 | 44883.4677 | 45141.2555 | 45823.7051 | 46279.3532 | 46726.1168 | 47248.8653 | 47732.4155 | 48202.5466 | 48254.9588 | 48803.9096 | 48385.2566 | 48385.2566 | 48385.2566 | 48385.2566 | 48385.2566 | 48385.2566 | 48385.2566 | 48385.2566 | 48385.2566 | 48385.2566 | 48385.2566 | 48385.2566 | 48385.2566 | 48385.2566 | 48385.2566 | 48385.2566
Option 7 -
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | 73.4908 | 101.8011 | 109.1509 | 110.3988 | 111.3674 | 113.0455 | 116.8717 | 119.4274 | 122.671 | 124.3515 | 125.8258 | 123.0846 | 126.2829 | 131.3148 | 127.4847 | 127.4847 | 127.4847 | 127.4847 | 127.4847 | 127.4847 | 127.4847 | 127.4847 | 127.4847 | 127.4847 | 127.4847 | 127.4847 | 127.4847 | 127.4847 | 127.4847 | 127.4847 |  | 78.6411 | 106.5944 | 114.2314 | 115.4081 | 116.1495 | 117.791 | 121.6771 | 123.7926 | 127.8346 | 140.1348 | 129.9793 | 127.9882 | 130.6605 | 136.5124 | 132.5403 | 132.5403 | 132.5403 | 132.5403 | 132.5403 | 132.5403 | 132.5403 | 132.5403 | 132.5403 | 132.5403 | 132.5403 | 132.5403 | 132.5403 | 132.5403 | 132.5403 | 132.5403
98% | 87.3027 | 120.9335 | 129.6647 | 131.1472 | 132.2978 | 134.2912 | 138.8365 | 141.8726 | 145.7258 | 147.722 | 149.4734 | 146.2171 | 150.0165 | 155.9941 | 151.4442 | 151.4442 | 151.4442 | 151.4442 | 151.4442 | 151.4442 | 151.4442 | 151.4442 | 151.4442 | 151.4442 | 151.4442 | 151.4442 | 151.4442 | 151.4442 | 151.4442 | 151.4442 |  | 93.4209 | 126.6277 | 135.7001 | 137.0978 | 137.9786 | 139.9286 | 144.5451 | 147.0581 | 151.8598 | 166.4717 | 154.4076 | 152.0423 | 155.2168 | 162.1685 | 157.4499 | 157.4499 | 157.4499 | 157.4499 | 157.4499 | 157.4499 | 157.4499 | 157.4499 | 157.4499 | 157.4499 | 157.4499 | 157.4499 | 157.4499 | 157.4499 | 157.4499 | 157.4499
97% | 172.8327 | 239.4116 | 256.6966 | 259.6314 | 261.9093 | 265.8557 | 274.854 | 280.8645 | 288.4926 | 292.4446 | 295.9119 | 289.4652 | 296.9869 | 308.8207 | 299.8133 | 299.8133 | 299.8133 | 299.8133 | 299.8133 | 299.8133 | 299.8133 | 299.8133 | 299.8133 | 299.8133 | 299.8133 | 299.8133 | 299.8133 | 299.8133 | 299.8133 | 299.8133 |  | 184.945 | 250.6842 | 268.6448 | 271.4119 | 273.1556 | 277.0161 | 286.1552 | 291.1302 | 300.6362 | 329.5634 | 305.68 | 300.9974 | 307.2819 | 321.0443 | 311.7028 | 311.7028 | 311.7028 | 311.7028 | 311.7028 | 311.7028 | 311.7028 | 311.7028 | 311.7028 | 311.7028 | 311.7028 | 311.7028 | 311.7028 | 311.7028 | 311.7028 | 311.7028
95% | 510.5211 | 707.185 | 758.2422 | 766.9113 | 773.6398 | 785.297 | 811.8764 | 829.6304 | 852.1628 | 863.8365 | 874.0782 | 855.0358 | 877.2537 | 912.2089 | 885.6025 | 885.6025 | 885.6025 | 885.6025 | 885.6025 | 885.6025 | 885.6025 | 885.6025 | 885.6025 | 885.6025 | 885.6025 | 885.6025 | 885.6025 | 885.6025 | 885.6025 | 885.6025 |  | 546.299 | 740.4826 | 793.5354 | 801.7091 | 806.8595 | 818.2629 | 845.2585 | 859.9539 | 888.0332 | 973.4795 | 902.9316 | 889.1001 | 907.6635 | 948.3155 | 920.7222 | 920.7222 | 920.7222 | 920.7222 | 920.7222 | 920.7222 | 920.7222 | 920.7222 | 920.7222 | 920.7222 | 920.7222 | 920.7222 | 920.7222 | 920.7222 | 920.7222 | 920.7222
90% | 2814.8088 | 3899.1347 | 4180.6436 | 4228.4418 | 4265.5399 | 4329.8131 | 4476.3615 | 4574.25 | 4698.4845 | 4762.8484 | 4819.3169 | 4714.3248 | 4836.8255 | 5029.5548 | 4882.8573 | 4882.8573 | 4882.8573 | 4882.8573 | 4882.8573 | 4882.8573 | 4882.8573 | 4882.8573 | 4882.8573 | 4882.8573 | 4882.8573 | 4882.8573 | 4882.8573 | 4882.8573 | 4882.8573 | 4882.8573 |  | 3012.0741 | 4082.7244 | 4375.2363 | 4420.3027 | 4448.7 | 4511.5741 | 4660.4169 | 4741.4413 | 4896.2592 | 5367.3759 | 4978.4031 | 4902.1418 | 5004.4932 | 5228.6319 | 5076.4935 | 5076.4935 | 5076.4935 | 5076.4935 | 5076.4935 | 5076.4935 | 5076.4935 | 5076.4935 | 5076.4935 | 5076.4935 | 5076.4935 | 5076.4935 | 5076.4935 | 5076.4935 | 5076.4935 | 5076.4935
85% | 6876.3763 | 9525.3066 | 10213.0129 | 10329.7805 | 10420.4084 | 10577.4231 | 10935.4305 | 11174.565 | 11478.0609 | 11635.2975 | 11773.246 | 11516.7578 | 11816.0183 | 12286.8422 | 11928.4707 | 11928.4707 | 11928.4707 | 11928.4707 | 11928.4707 | 11928.4707 | 11928.4707 | 11928.4707 | 11928.4707 | 11928.4707 | 11928.4707 | 11928.4707 | 11928.4707 | 11928.4707 | 11928.4707 | 11928.4707 |  | 7358.2813 | 9973.8032 | 10688.3888 | 10798.4829 | 10867.8555 | 11021.4524 | 11385.0646 | 11583.0015 | 11961.2104 | 13112.1147 | 12161.8821 | 11975.5812 | 12225.6185 | 12773.1733 | 12401.51 | 12401.51 | 12401.51 | 12401.51 | 12401.51 | 12401.51 | 12401.51 | 12401.51 | 12401.51 | 12401.51 | 12401.51 | 12401.51 | 12401.51 | 12401.51 | 12401.51 | 12401.51
80% | 10687.9274 | 14805.1503 | 15874.0497 | 16055.5412 | 16196.4038 | 16440.4513 | 16996.9008 | 17368.5868 | 17840.3094 | 18084.7017 | 18299.1145 | 17900.4559 | 18365.5953 | 19097.3952 | 18540.3797 | 18540.3797 | 18540.3797 | 18540.3797 | 18540.3797 | 18540.3797 | 18540.3797 | 18540.3797 | 18540.3797 | 18540.3797 | 18540.3797 | 18540.3797 | 18540.3797 | 18540.3797 | 18540.3797 | 18540.3797 |  | 11436.9506 | 15502.2469 | 16612.9248 | 16784.0437 | 16891.8693 | 17130.6044 | 17695.7655 | 18003.4182 | 18591.267 | 20380.1135 | 18903.1703 | 18613.6034 | 19002.2355 | 19853.298 | 19275.623 | 19275.623 | 19275.623 | 19275.623 | 19275.623 | 19275.623 | 19275.623 | 19275.623 | 19275.623 | 19275.623 | 19275.623 | 19275.623 | 19275.623 | 19275.623 | 19275.623 | 19275.623
75% | 11791.7667 | 16334.2127 | 17513.507 | 17713.7428 | 17869.1536 | 18138.406 | 18752.3252 | 19162.3985 | 19682.8403 | 19952.4731 | 20189.0303 | 19749.1986 | 20262.3772 | 21069.7567 | 20455.2132 | 20455.2132 | 20455.2132 | 20455.2132 | 20455.2132 | 20455.2132 | 20455.2132 | 20455.2132 | 20455.2132 | 20455.2132 | 20455.2132 | 20455.2132 | 20455.2132 | 20455.2132 | 20455.2132 | 20455.2132 |  | 12618.1483 | 17103.3048 | 18328.6925 | 18517.4844 | 18636.4461 | 18899.8376 | 19523.368 | 19862.7948 | 20511.356 | 22484.9529 | 20855.4725 | 20535.9993 | 20964.769 | 21903.7284 | 21266.3917 | 21266.3917 | 21266.3917 | 21266.3917 | 21266.3917 | 21266.3917 | 21266.3917 | 21266.3917 | 21266.3917 | 21266.3917 | 21266.3917 | 21266.3917 | 21266.3917 | 21266.3917 | 21266.3917 | 21266.3917
70% | 12669.5942 | 17550.1984 | 18817.2842 | 19032.4264 | 19199.4066 | 19488.7033 | 20148.3251 | 20588.926 | 21148.1115 | 21437.817 | 21691.9844 | 21219.4098 | 21770.7916 | 22638.2758 | 21977.983 | 21977.983 | 21977.983 | 21977.983 | 21977.983 | 21977.983 | 21977.983 | 21977.983 | 21977.983 | 21977.983 | 21977.983 | 21977.983 | 21977.983 | 21977.983 | 21977.983 | 21977.983 |  | 13557.495 | 18376.5449 | 19693.1554 | 19896.0018 | 20023.8195 | 20306.8189 | 20976.7675 | 21341.4626 | 22038.3054 | 24158.8249 | 22408.0393 | 22064.7832 | 22525.4722 | 23534.3317 | 22849.549 | 22849.549 | 22849.549 | 22849.549 | 22849.549 | 22849.549 | 22849.549 | 22849.549 | 22849.549 | 22849.549 | 22849.549 | 22849.549 | 22849.549 | 22849.549 | 22849.549 | 22849.549
65% | 13351.323 | 18494.5441 | 19829.8096 | 20056.5282 | 20232.4932 | 20537.3565 | 21232.4714 | 21696.7803 | 22286.0546 | 22591.3486 | 22859.1924 | 22361.1894 | 22942.24 | 23856.402 | 23160.5801 | 23160.5801 | 23160.5801 | 23160.5801 | 23160.5801 | 23160.5801 | 23160.5801 | 23160.5801 | 23160.5801 | 23160.5801 | 23160.5801 | 23160.5801 | 23160.5801 | 23160.5801 | 23160.5801 | 23160.5801 |  | 14287.0002 | 19365.3548 | 20752.8099 | 20966.571 | 21101.2664 | 21399.4935 | 22105.4909 | 22489.8096 | 23224.1482 | 25458.7693 | 23613.7769 | 23252.0508 | 23737.5287 | 24800.6731 | 24079.0435 | 24079.0435 | 24079.0435 | 24079.0435 | 24079.0435 | 24079.0435 | 24079.0435 | 24079.0435 | 24079.0435 | 24079.0435 | 24079.0435 | 24079.0435 | 24079.0435 | 24079.0435 | 24079.0435 | 24079.0435
60% | 14698.1621 | 20360.2151 | 21830.1779 | 22079.7671 | 22273.483 | 22609.0999 | 23374.3358 | 23885.4827 | 24534.2012 | 24870.2922 | 25165.1552 | 24616.9152 | 25256.5804 | 26262.9602 | 25496.946 | 25496.946 | 25496.946 | 25496.946 | 25496.946 | 25496.946 | 25496.946 | 25496.946 | 25496.946 | 25496.946 | 25496.946 | 25496.946 | 25496.946 | 25496.946 | 25496.946 | 25496.946 |  | 15728.2275 | 21318.8704 | 22846.2875 | 23081.6122 | 23229.8952 | 23558.2066 | 24335.4227 | 24758.5102 | 25566.9267 | 28026.9692 | 25995.8598 | 25597.644 | 26132.0954 | 27302.4864 | 26508.0611 | 26508.0611 | 26508.0611 | 26508.0611 | 26508.0611 | 26508.0611 | 26508.0611 | 26508.0611 | 26508.0611 | 26508.0611 | 26508.0611 | 26508.0611 | 26508.0611 | 26508.0611 | 26508.0611 | 26508.0611
55% | 16350.7821 | 22649.4603 | 24284.7017 | 24562.354 | 24777.8508 | 25151.2035 | 26002.4804 | 26571.0991 | 27292.7577 | 27666.6379 | 27994.6544 | 27384.7719 | 28096.3592 | 29215.8935 | 28363.7508 | 28363.7508 | 28363.7508 | 28363.7508 | 28363.7508 | 28363.7508 | 28363.7508 | 28363.7508 | 28363.7508 | 28363.7508 | 28363.7508 | 28363.7508 | 28363.7508 | 28363.7508 | 28363.7508 | 28363.7508 |  | 17496.6651 | 23715.9042 | 25415.0598 | 25676.8438 | 25841.7993 | 26207.0251 | 27071.6291 | 27542.2874 | 28441.6 | 31178.2427 | 28918.7611 | 28475.7711 | 29070.3146 | 30372.3011 | 29488.5529 | 29488.5529 | 29488.5529 | 29488.5529 | 29488.5529 | 29488.5529 | 29488.5529 | 29488.5529 | 29488.5529 | 29488.5529 | 29488.5529 | 29488.5529 | 29488.5529 | 29488.5529 | 29488.5529 | 29488.5529
50% | 16573.101 | 22957.4214 | 24614.8968 | 24896.3244 | 25114.7512 | 25493.1803 | 26356.0319 | 26932.3821 | 27663.8529 | 28042.8167 | 28375.2932 | 27757.1182 | 28478.3809 | 29613.1373 | 28749.4081 | 28749.4081 | 28749.4081 | 28749.4081 | 28749.4081 | 28749.4081 | 28749.4081 | 28749.4081 | 28749.4081 | 28749.4081 | 28749.4081 | 28749.4081 | 28749.4081 | 28749.4081 | 28749.4081 | 28749.4081 |  | 17734.5645 | 24038.3655 | 25760.6242 | 26025.9676 | 26193.1661 | 26563.3577 | 27439.7177 | 27916.7755 | 28828.3158 | 31602.1683 | 29311.9648 | 28862.9515 | 29465.579 | 30785.2684 | 29889.5039 | 29889.5039 | 29889.5039 | 29889.5039 | 29889.5039 | 29889.5039 | 29889.5039 | 29889.5039 | 29889.5039 | 29889.5039 | 29889.5039 | 29889.5039 | 29889.5039 | 29889.5039 | 29889.5039 | 29889.5039
45% | 12791.4633 | 17719.0143 | 18998.2882 | 19215.4999 | 19384.0862 | 19676.1657 | 20342.1324 | 20786.9714 | 21351.5358 | 21644.0279 | 21900.6402 | 21423.5199 | 21980.2054 | 22856.034 | 22189.3899 | 22189.3899 | 22189.3899 | 22189.3899 | 22189.3899 | 22189.3899 | 22189.3899 | 22189.3899 | 22189.3899 | 22189.3899 | 22189.3899 | 22189.3899 | 22189.3899 | 22189.3899 | 22189.3899 | 22189.3899 |  | 13687.9049 | 18553.3094 | 19882.5844 | 20087.382 | 20216.4292 | 20502.1508 | 21178.5436 | 21546.7467 | 22250.2924 | 24391.2093 | 22623.5828 | 22277.025 | 22742.1454 | 23760.7091 | 23069.3395 | 23069.3395 | 23069.3395 | 23069.3395 | 23069.3395 | 23069.3395 | 23069.3395 | 23069.3395 | 23069.3395 | 23069.3395 | 23069.3395 | 23069.3395 | 23069.3395 | 23069.3395 | 23069.3395 | 23069.3395
40% | 6284.3875 | 8705.2708 | 9333.7723 | 9440.4874 | 9523.3131 | 9666.8104 | 9993.9968 | 10212.5442 | 10489.9121 | 10633.6121 | 10759.6846 | 10525.2775 | 10798.7746 | 11229.0652 | 10901.546 | 10901.546 | 10901.546 | 10901.546 | 10901.546 | 10901.546 | 10901.546 | 10901.546 | 10901.546 | 10901.546 | 10901.546 | 10901.546 | 10901.546 | 10901.546 | 10901.546 | 10901.546 |  | 6724.8052 | 9115.1562 | 9768.223 | 9868.8391 | 9932.2394 | 10072.6131 | 10404.9218 | 10585.8183 | 10931.4671 | 11983.2898 | 11114.863 | 10944.6007 | 11173.1122 | 11673.5279 | 11333.8612 | 11333.8612 | 11333.8612 | 11333.8612 | 11333.8612 | 11333.8612 | 11333.8612 | 11333.8612 | 11333.8612 | 11333.8612 | 11333.8612 | 11333.8612 | 11333.8612 | 11333.8612 | 11333.8612 | 11333.8612
35% | 2348.7515 | 3253.5419 | 3488.4405 | 3528.3246 | 3559.2802 | 3612.9114 | 3735.1954 | 3816.8761 | 3920.5407 | 3974.2477 | 4021.3665 | 3933.7583 | 4035.9762 | 4196.7946 | 4074.3863 | 4074.3863 | 4074.3863 | 4074.3863 | 4074.3863 | 4074.3863 | 4074.3863 | 4074.3863 | 4074.3863 | 4074.3863 | 4074.3863 | 4074.3863 | 4074.3863 | 4074.3863 | 4074.3863 | 4074.3863 |  | 2513.3549 | 3406.7341 | 3650.8138 | 3688.4184 | 3712.1139 | 3764.5777 | 3888.7761 | 3956.3851 | 4085.5692 | 4478.6815 | 4154.1123 | 4090.4778 | 4175.8826 | 4362.9099 | 4235.9615 | 4235.9615 | 4235.9615 | 4235.9615 | 4235.9615 | 4235.9615 | 4235.9615 | 4235.9615 | 4235.9615 | 4235.9615 | 4235.9615 | 4235.9615 | 4235.9615 | 4235.9615 | 4235.9615 | 4235.9615
30% | 1171.4214 | 1622.6784 | 1739.8323 | 1759.7242 | 1775.163 | 1801.9112 | 1862.8993 | 1903.637 | 1955.3388 | 1982.1248 | 2005.6249 | 1961.931 | 2012.9114 | 2093.1183 | 2032.0682 | 2032.0682 | 2032.0682 | 2032.0682 | 2032.0682 | 2032.0682 | 2032.0682 | 2032.0682 | 2032.0682 | 2032.0682 | 2032.0682 | 2032.0682 | 2032.0682 | 2032.0682 | 2032.0682 | 2032.0682 |  | 1253.516 | 1699.0818 | 1820.8147 | 1839.5697 | 1851.3876 | 1877.5536 | 1939.4965 | 1973.2159 | 2037.6455 | 2233.7072 | 2071.8308 | 2040.0936 | 2082.6886 | 2175.967 | 2112.6525 | 2112.6525 | 2112.6525 | 2112.6525 | 2112.6525 | 2112.6525 | 2112.6525 | 2112.6525 | 2112.6525 | 2112.6525 | 2112.6525 | 2112.6525 | 2112.6525 | 2112.6525 | 2112.6525 | 2112.6525
25% | 690.592 | 956.6232 | 1025.6893 | 1037.4162 | 1046.5179 | 1062.2869 | 1098.2414 | 1122.2576 | 1152.7376 | 1168.5288 | 1182.3829 | 1156.6239 | 1186.6785 | 1233.9632 | 1197.9721 | 1197.9721 | 1197.9721 | 1197.9721 | 1197.9721 | 1197.9721 | 1197.9721 | 1197.9721 | 1197.9721 | 1197.9721 | 1197.9721 | 1197.9721 | 1197.9721 | 1197.9721 | 1197.9721 | 1197.9721 |  | 738.9896 | 1001.6655 | 1073.4311 | 1084.4878 | 1091.4549 | 1106.8806 | 1143.398 | 1163.2767 | 1201.2601 | 1316.845 | 1221.4135 | 1202.7034 | 1227.8145 | 1282.8053 | 1245.4793 | 1245.4793 | 1245.4793 | 1245.4793 | 1245.4793 | 1245.4793 | 1245.4793 | 1245.4793 | 1245.4793 | 1245.4793 | 1245.4793 | 1245.4793 | 1245.4793 | 1245.4793 | 1245.4793 | 1245.4793
20% | 348.989 | 483.4272 | 518.3296 | 524.2558 | 528.8553 | 536.8241 | 554.9937 | 567.1302 | 582.5332 | 590.5132 | 597.5144 | 584.4971 | 599.6851 | 623.5803 | 605.3923 | 605.3923 | 605.3923 | 605.3923 | 605.3923 | 605.3923 | 605.3923 | 605.3923 | 605.3923 | 605.3923 | 605.3923 | 605.3923 | 605.3923 | 605.3923 | 605.3923 | 605.3923 |  | 373.4466 | 506.1893 | 542.4558 | 548.0433 | 551.5641 | 559.3594 | 577.8134 | 587.8591 | 607.0539 | 665.4645 | 617.2384 | 607.7833 | 620.4731 | 648.2626 | 629.3999 | 629.3999 | 629.3999 | 629.3999 | 629.3999 | 629.3999 | 629.3999 | 629.3999 | 629.3999 | 629.3999 | 629.3999 | 629.3999 | 629.3999 | 629.3999 | 629.3999 | 629.3999
15% | 142.1807 | 196.9518 | 211.1713 | 213.5857 | 215.4596 | 218.7061 | 226.1085 | 231.053 | 237.3283 | 240.5795 | 243.4318 | 238.1285 | 244.3162 | 254.0512 | 246.6413 | 246.6413 | 246.6413 | 246.6413 | 246.6413 | 246.6413 | 246.6413 | 246.6413 | 246.6413 | 246.6413 | 246.6413 | 246.6413 | 246.6413 | 246.6413 | 246.6413 | 246.6413 |  | 152.1449 | 206.2253 | 221.0005 | 223.2769 | 224.7113 | 227.8872 | 235.4055 | 239.4982 | 247.3183 | 271.1152 | 251.4675 | 247.6154 | 252.7853 | 264.107 | 256.4222 | 256.4222 | 256.4222 | 256.4222 | 256.4222 | 256.4222 | 256.4222 | 256.4222 | 256.4222 | 256.4222 | 256.4222 | 256.4222 | 256.4222 | 256.4222 | 256.4222 | 256.4222
10% | 57.2416 | 79.2923 | 85.017 | 85.989 | 86.7435 | 88.0505 | 91.0307 | 93.0214 | 95.5478 | 96.8567 | 98.005 | 95.8699 | 98.3611 | 102.2804 | 99.2972 | 99.2972 | 99.2972 | 99.2972 | 99.2972 | 99.2972 | 99.2972 | 99.2972 | 99.2972 | 99.2972 | 99.2972 | 99.2972 | 99.2972 | 99.2972 | 99.2972 | 99.2972 |  | 61.2531 | 83.0258 | 88.9742 | 89.8907 | 90.4682 | 91.7468 | 94.7736 | 96.4213 | 99.5697 | 109.1503 | 101.2402 | 99.6893 | 101.7707 | 106.3288 | 103.2349 | 103.2349 | 103.2349 | 103.2349 | 103.2349 | 103.2349 | 103.2349 | 103.2349 | 103.2349 | 103.2349 | 103.2349 | 103.2349 | 103.2349 | 103.2349 | 103.2349 | 103.2349
5% | 48.7477 | 67.5263 | 72.4016 | 73.2294 | 73.8719 | 74.985 | 77.5229 | 79.2182 | 81.3697 | 82.4844 | 83.4623 | 81.644 | 83.7655 | 87.1033 | 84.5627 | 84.5627 | 84.5627 | 84.5627 | 84.5627 | 84.5627 | 84.5627 | 84.5627 | 84.5627 | 84.5627 | 84.5627 | 84.5627 | 84.5627 | 84.5627 | 84.5627 | 84.5627 |  | 52.164 | 70.7058 | 75.7716 | 76.5521 | 77.0439 | 78.1327 | 80.7104 | 82.1137 | 84.7948 | 92.9538 | 86.2174 | 84.8967 | 86.6693 | 90.551 | 87.9162 | 87.9162 | 87.9162 | 87.9162 | 87.9162 | 87.9162 | 87.9162 | 87.9162 | 87.9162 | 87.9162 | 87.9162 | 87.9162 | 87.9162 | 87.9162 | 87.9162 | 87.9162
9.992e-14% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E @ R (MWh) | 130541.7636 | 180829.3011 | 193884.7798 | 196101.5072 | 197821.9953 | 200802.7777 | 207599.2223 | 212138.9744 | 217900.5692 | 220885.5628 | 223504.3892 | 218635.1944 | 224316.3823 | 233254.5468 | 226451.1896 | 226451.1896 | 226451.1896 | 226451.1896 | 226451.1896 | 226451.1896 | 226451.1896 | 226451.1896 | 226451.1896 | 226451.1896 | 226451.1896 | 226451.1896 | 226451.1896 | 226451.1896 | 226451.1896 | 226451.1896 | E @ R (MWh) | 139690.2921 | 189343.6009 | 202909.3599 | 204999.3971 | 206316.373 | 209232.2711 | 216135.1177 | 219892.7708 | 227072.7236 | 248921.5973 | 230882.2942 | 227345.5395 | 232092.2705 | 242487.1014 | 235431.4111 | 235431.4111 | 235431.4111 | 235431.4111 | 235431.4111 | 235431.4111 | 235431.4111 | 235431.4111 | 235431.4111 | 235431.4111 | 235431.4111 | 235431.4111 | 235431.4111 | 235431.4111 | 235431.4111 | 235431.4111
Option 7 Winter POE50 W E @ R (MWh) N 2 | 91379.2345 | 126580.5108 | 135719.3459 | 137271.0551 | 138475.3967 | 140561.9444 | 145319.4556 | 148497.2821 | 152530.3985 | 154619.8939 | 156453.0725 | 153044.6361 | 157021.4676 | 163278.1828 | 158515.8327 | 158515.8327 | 158515.8327 | 158515.8327 | 158515.8327 | 158515.8327 | 158515.8327 | 158515.8327 | 158515.8327 | 158515.8327 | 158515.8327 | 158515.8327 | 158515.8327 | 158515.8327 | 158515.8327 | 158515.8327 | Option 7 Winter POE10 W E @ R (MWh) N 2 | 41907.0876 | 56803.0803 | 60872.808 | 61499.8191 | 61894.9119 | 62769.6813 | 64840.5353 | 65967.8312 | 68121.8171 | 74676.4792 | 69264.6882 | 68203.6618 | 69627.6812 | 72746.1304 | 70629.4233 | 70629.4233 | 70629.4233 | 70629.4233 | 70629.4233 | 70629.4233 | 70629.4233 | 70629.4233 | 70629.4233 | 70629.4233 | 70629.4233 | 70629.4233 | 70629.4233 | 70629.4233 | 70629.4233 | 70629.4233
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 94.6719 | 122.4737 | 129.7436 | 129.304 | 129.3303 | 130.0731 | 132.0395 | 133.3525 | 134.6398 | 136.1461 | 137.5394 | 138.8941 | 139.0451 | 140.6269 | 139.4206 | 139.4206 | 139.4206 | 139.4206 | 139.4206 | 139.4206 | 139.4206 | 139.4206 | 139.4206 | 139.4206 | 139.4206 | 139.4206 | 139.4206 | 139.4206 | 139.4206 | 139.4206
98% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 46.8602 | 60.6214 | 64.2198 | 64.0022 | 64.0152 | 64.3829 | 65.3562 | 66.0061 | 66.6433 | 67.3889 | 68.0786 | 68.7491 | 68.8238 | 69.6068 | 69.0097 | 69.0097 | 69.0097 | 69.0097 | 69.0097 | 69.0097 | 69.0097 | 69.0097 | 69.0097 | 69.0097 | 69.0097 | 69.0097 | 69.0097 | 69.0097 | 69.0097 | 69.0097
97% | 20.8131 | 27.6102 | 29.4592 | 29.4046 | 29.4015 | 29.6116 | 29.8423 | 30.3162 | 30.6568 | 30.8412 | 31.0426 | 31.2273 | 31.5615 | 31.9765 | 31.9467 | 31.9467 | 31.9467 | 31.9467 | 31.9467 | 31.9467 | 31.9467 | 31.9467 | 31.9467 | 31.9467 | 31.9467 | 31.9467 | 31.9467 | 31.9467 | 31.9467 | 31.9467 |  | 92.7689 | 120.0119 | 127.1357 | 126.7049 | 126.7307 | 127.4585 | 129.3855 | 130.672 | 131.9335 | 133.4095 | 134.7748 | 136.1022 | 136.2502 | 137.8002 | 136.6181 | 136.6181 | 136.6181 | 136.6181 | 136.6181 | 136.6181 | 136.6181 | 136.6181 | 136.6181 | 136.6181 | 136.6181 | 136.6181 | 136.6181 | 136.6181 | 136.6181 | 136.6181
95% | 102.4643 | 135.9269 | 145.0299 | 144.761 | 144.7458 | 145.7802 | 146.9157 | 149.2489 | 150.9258 | 151.8338 | 152.8252 | 153.7342 | 155.3796 | 157.4227 | 157.276 | 157.276 | 157.276 | 157.276 | 157.276 | 157.276 | 157.276 | 157.276 | 157.276 | 157.276 | 157.276 | 157.276 | 157.276 | 157.276 | 157.276 | 157.276 |  | 137.0126 | 177.2483 | 187.7696 | 187.1334 | 187.1714 | 188.2465 | 191.0924 | 192.9925 | 194.8556 | 197.0355 | 199.052 | 201.0125 | 201.2311 | 203.5203 | 201.7745 | 201.7745 | 201.7745 | 201.7745 | 201.7745 | 201.7745 | 201.7745 | 201.7745 | 201.7745 | 201.7745 | 201.7745 | 201.7745 | 201.7745 | 201.7745 | 201.7745 | 201.7745
90% | 177.7116 | 235.7483 | 251.5362 | 251.0698 | 251.0434 | 252.8375 | 254.8069 | 258.8536 | 261.762 | 263.3368 | 265.0563 | 266.6327 | 269.4865 | 273.03 | 272.7756 | 272.7756 | 272.7756 | 272.7756 | 272.7756 | 272.7756 | 272.7756 | 272.7756 | 272.7756 | 272.7756 | 272.7756 | 272.7756 | 272.7756 | 272.7756 | 272.7756 | 272.7756 |  | 594.078 | 768.5376 | 814.1574 | 811.3985 | 811.5637 | 816.2249 | 828.5646 | 836.8035 | 844.8817 | 854.3338 | 863.0771 | 871.5778 | 872.5255 | 882.4514 | 874.8815 | 874.8815 | 874.8815 | 874.8815 | 874.8815 | 874.8815 | 874.8815 | 874.8815 | 874.8815 | 874.8815 | 874.8815 | 874.8815 | 874.8815 | 874.8815 | 874.8815 | 874.8815
85% | 504.3166 | 669.0154 | 713.8189 | 712.4955 | 712.4205 | 717.5119 | 723.1007 | 734.5845 | 742.838 | 747.307 | 752.1867 | 756.6605 | 764.759 | 774.815 | 774.093 | 774.093 | 774.093 | 774.093 | 774.093 | 774.093 | 774.093 | 774.093 | 774.093 | 774.093 | 774.093 | 774.093 | 774.093 | 774.093 | 774.093 | 774.093 |  | 561.9657 | 726.995 | 770.1489 | 767.5392 | 767.6954 | 772.1046 | 783.7774 | 791.5709 | 799.2124 | 808.1536 | 816.4243 | 824.4655 | 825.362 | 834.7513 | 827.5906 | 827.5906 | 827.5906 | 827.5906 | 827.5906 | 827.5906 | 827.5906 | 827.5906 | 827.5906 | 827.5906 | 827.5906 | 827.5906 | 827.5906 | 827.5906 | 827.5906 | 827.5906
80% | 704.4422 | 934.4978 | 997.0804 | 995.2318 | 995.1271 | 1002.2389 | 1010.0454 | 1026.0863 | 1037.6149 | 1043.8574 | 1050.6735 | 1056.9226 | 1068.2348 | 1082.2812 | 1081.2727 | 1081.2727 | 1081.2727 | 1081.2727 | 1081.2727 | 1081.2727 | 1081.2727 | 1081.2727 | 1081.2727 | 1081.2727 | 1081.2727 | 1081.2727 | 1081.2727 | 1081.2727 | 1081.2727 | 1081.2727 |  | 392.484 | 507.7425 | 537.8818 | 536.0591 | 536.1682 | 539.2477 | 547.4001 | 552.8431 | 558.1801 | 564.4247 | 570.2011 | 575.8172 | 576.4433 | 583.0009 | 577.9998 | 577.9998 | 577.9998 | 577.9998 | 577.9998 | 577.9998 | 577.9998 | 577.9998 | 577.9998 | 577.9998 | 577.9998 | 577.9998 | 577.9998 | 577.9998 | 577.9998 | 577.9998
75% | 1836.3528 | 2436.0657 | 2599.2074 | 2594.3882 | 2594.1154 | 2612.6546 | 2633.0048 | 2674.8204 | 2704.8735 | 2721.1465 | 2738.9148 | 2755.205 | 2784.6939 | 2821.3104 | 2818.6814 | 2818.6814 | 2818.6814 | 2818.6814 | 2818.6814 | 2818.6814 | 2818.6814 | 2818.6814 | 2818.6814 | 2818.6814 | 2818.6814 | 2818.6814 | 2818.6814 | 2818.6814 | 2818.6814 | 2818.6814 |  | 700.5244 | 906.2435 | 960.0375 | 956.7843 | 956.979 | 962.4754 | 977.0262 | 986.7412 | 996.2669 | 1007.4126 | 1017.7226 | 1027.7464 | 1028.8639 | 1040.5683 | 1031.6421 | 1031.6421 | 1031.6421 | 1031.6421 | 1031.6421 | 1031.6421 | 1031.6421 | 1031.6421 | 1031.6421 | 1031.6421 | 1031.6421 | 1031.6421 | 1031.6421 | 1031.6421 | 1031.6421 | 1031.6421
70% | 3172.6584 | 4208.7797 | 4490.6388 | 4482.3127 | 4481.8414 | 4513.8714 | 4549.0304 | 4621.275 | 4673.1976 | 4701.3124 | 4732.0106 | 4760.1551 | 4811.103 | 4874.3651 | 4869.823 | 4869.823 | 4869.823 | 4869.823 | 4869.823 | 4869.823 | 4869.823 | 4869.823 | 4869.823 | 4869.823 | 4869.823 | 4869.823 | 4869.823 | 4869.823 | 4869.823 | 4869.823 |  | 1276.1675 | 1650.9325 | 1748.9307 | 1743.0043 | 1743.359 | 1753.372 | 1779.8796 | 1797.5778 | 1814.931 | 1835.2355 | 1854.0175 | 1872.2783 | 1874.3141 | 1895.6364 | 1879.3751 | 1879.3751 | 1879.3751 | 1879.3751 | 1879.3751 | 1879.3751 | 1879.3751 | 1879.3751 | 1879.3751 | 1879.3751 | 1879.3751 | 1879.3751 | 1879.3751 | 1879.3751 | 1879.3751 | 1879.3751
65% | 7968.2023 | 10570.444 | 11278.3393 | 11257.4282 | 11256.2445 | 11336.6886 | 11424.9912 | 11606.4352 | 11736.84 | 11807.4509 | 11884.55 | 11955.2357 | 12083.1924 | 12242.0767 | 12230.6689 | 12230.6689 | 12230.6689 | 12230.6689 | 12230.6689 | 12230.6689 | 12230.6689 | 12230.6689 | 12230.6689 | 12230.6689 | 12230.6689 | 12230.6689 | 12230.6689 | 12230.6689 | 12230.6689 | 12230.6689 |  | 1605.6162 | 2077.1285 | 2200.4254 | 2192.969 | 2193.4153 | 2206.0132 | 2239.3639 | 2261.631 | 2283.4639 | 2309.0102 | 2332.6409 | 2355.6158 | 2358.1771 | 2385.0038 | 2364.5446 | 2364.5446 | 2364.5446 | 2364.5446 | 2364.5446 | 2364.5446 | 2364.5446 | 2364.5446 | 2364.5446 | 2364.5446 | 2364.5446 | 2364.5446 | 2364.5446 | 2364.5446 | 2364.5446 | 2364.5446
60% | 11647.312 | 15451.0709 | 16485.8185 | 16455.2522 | 16453.5219 | 16571.109 | 16700.1831 | 16965.4041 | 17156.0199 | 17259.2335 | 17371.9312 | 17475.2541 | 17662.2915 | 17894.5364 | 17877.8614 | 17877.8614 | 17877.8614 | 17877.8614 | 17877.8614 | 17877.8614 | 17877.8614 | 17877.8614 | 17877.8614 | 17877.8614 | 17877.8614 | 17877.8614 | 17877.8614 | 17877.8614 | 17877.8614 | 17877.8614 |  | 2512.492 | 3250.3215 | 3443.2583 | 3431.5904 | 3432.2888 | 3452.0021 | 3504.1898 | 3539.0337 | 3573.1982 | 3613.1734 | 3650.151 | 3686.1024 | 3690.1105 | 3732.0893 | 3700.0745 | 3700.0745 | 3700.0745 | 3700.0745 | 3700.0745 | 3700.0745 | 3700.0745 | 3700.0745 | 3700.0745 | 3700.0745 | 3700.0745 | 3700.0745 | 3700.0745 | 3700.0745 | 3700.0745 | 3700.0745
55% | 13170.4015 | 17471.5683 | 18641.6273 | 18607.0639 | 18605.1073 | 18738.071 | 18884.0238 | 19183.9271 | 19399.4692 | 19516.1798 | 19643.6146 | 19760.4488 | 19971.9446 | 20234.5597 | 20215.7041 | 20215.7041 | 20215.7041 | 20215.7041 | 20215.7041 | 20215.7041 | 20215.7041 | 20215.7041 | 20215.7041 | 20215.7041 | 20215.7041 | 20215.7041 | 20215.7041 | 20215.7041 | 20215.7041 | 20215.7041 |  | 4828.1473 | 6246.0024 | 6616.7608 | 6594.3391 | 6595.6811 | 6633.5633 | 6733.8501 | 6800.8082 | 6866.4607 | 6943.2792 | 7014.3375 | 7083.4238 | 7091.1259 | 7171.7949 | 7110.2733 | 7110.2733 | 7110.2733 | 7110.2733 | 7110.2733 | 7110.2733 | 7110.2733 | 7110.2733 | 7110.2733 | 7110.2733 | 7110.2733 | 7110.2733 | 7110.2733 | 7110.2733 | 7110.2733 | 7110.2733
50% | 16911.4168 | 22434.3178 | 23936.7286 | 23892.3477 | 23889.8353 | 24060.567 | 24247.9772 | 24633.0672 | 24909.8334 | 25059.6953 | 25223.3277 | 25373.3483 | 25644.9189 | 25982.129 | 25957.9175 | 25957.9175 | 25957.9175 | 25957.9175 | 25957.9175 | 25957.9175 | 25957.9175 | 25957.9175 | 25957.9175 | 25957.9175 | 25957.9175 | 25957.9175 | 25957.9175 | 25957.9175 | 25957.9175 | 25957.9175 |  | 10714.812 | 13861.3711 | 14684.1724 | 14634.4134 | 14637.3915 | 14721.4613 | 14944.0217 | 15092.6176 | 15238.3161 | 15408.7947 | 15566.4901 | 15719.8092 | 15736.9019 | 15915.9256 | 15779.3945 | 15779.3945 | 15779.3945 | 15779.3945 | 15779.3945 | 15779.3945 | 15779.3945 | 15779.3945 | 15779.3945 | 15779.3945 | 15779.3945 | 15779.3945 | 15779.3945 | 15779.3945 | 15779.3945 | 15779.3945
45% | 22520.2713 | 29874.9022 | 31875.6039 | 31816.5035 | 31813.1579 | 32040.5146 | 32290.0814 | 32802.8907 | 33171.4494 | 33371.0147 | 33588.9175 | 33788.694 | 34150.3339 | 34599.3834 | 34567.1419 | 34567.1419 | 34567.1419 | 34567.1419 | 34567.1419 | 34567.1419 | 34567.1419 | 34567.1419 | 34567.1419 | 34567.1419 | 34567.1419 | 34567.1419 | 34567.1419 | 34567.1419 | 34567.1419 | 34567.1419 |  | 16236.3476 | 21004.3853 | 22251.1909 | 22175.7903 | 22180.3031 | 22307.6955 | 22644.9453 | 22870.1153 | 23090.8949 | 23349.2243 | 23588.1829 | 23820.5101 | 23846.4109 | 24117.6889 | 23910.8008 | 23910.8008 | 23910.8008 | 23910.8008 | 23910.8008 | 23910.8008 | 23910.8008 | 23910.8008 | 23910.8008 | 23910.8008 | 23910.8008 | 23910.8008 | 23910.8008 | 23910.8008 | 23910.8008 | 23910.8008
40% | 15794.9825 | 20953.2804 | 22356.5072 | 22315.0562 | 22312.7097 | 22472.1702 | 22647.2082 | 23006.8759 | 23265.371 | 23405.3395 | 23558.1694 | 23698.2861 | 23951.9286 | 24266.8772 | 24244.2641 | 24244.2641 | 24244.2641 | 24244.2641 | 24244.2641 | 24244.2641 | 24244.2641 | 24244.2641 | 24244.2641 | 24244.2641 | 24244.2641 | 24244.2641 | 24244.2641 | 24244.2641 | 24244.2641 | 24244.2641 |  | 16811.9908 | 21749.0744 | 23040.0842 | 22962.0103 | 22966.6831 | 23098.592 | 23447.7987 | 23680.9519 | 23909.559 | 24177.0472 | 24424.4778 | 24665.0419 | 24691.8611 | 24972.7569 | 24758.5339 | 24758.5339 | 24758.5339 | 24758.5339 | 24758.5339 | 24758.5339 | 24758.5339 | 24758.5339 | 24758.5339 | 24758.5339 | 24758.5339 | 24758.5339 | 24758.5339 | 24758.5339 | 24758.5339 | 24758.5339
35% | 8189.141 | 10863.5364 | 11591.06 | 11569.5691 | 11568.3525 | 11651.0272 | 11741.7782 | 11928.2532 | 12062.2738 | 12134.8425 | 12214.0795 | 12286.725 | 12418.2297 | 12581.5194 | 12569.7953 | 12569.7953 | 12569.7953 | 12569.7953 | 12569.7953 | 12569.7953 | 12569.7953 | 12569.7953 | 12569.7953 | 12569.7953 | 12569.7953 | 12569.7953 | 12569.7953 | 12569.7953 | 12569.7953 | 12569.7953 |  | 22897.8708 | 29622.1608 | 31380.5115 | 31274.1752 | 31280.5395 | 31460.199 | 31935.8172 | 32253.3711 | 32564.7331 | 32929.051 | 33266.0507 | 33593.6981 | 33630.2257 | 34012.8048 | 33721.0338 | 33721.0338 | 33721.0338 | 33721.0338 | 33721.0338 | 33721.0338 | 33721.0338 | 33721.0338 | 33721.0338 | 33721.0338 | 33721.0338 | 33721.0338 | 33721.0338 | 33721.0338 | 33721.0338 | 33721.0338
30% | 3808.7911 | 5052.6595 | 5391.0326 | 5381.0371 | 5380.4713 | 5418.9235 | 5461.132 | 5547.8621 | 5610.1954 | 5643.9473 | 5680.8006 | 5714.5882 | 5775.7514 | 5851.6979 | 5846.245 | 5846.245 | 5846.245 | 5846.245 | 5846.245 | 5846.245 | 5846.245 | 5846.245 | 5846.245 | 5846.245 | 5846.245 | 5846.245 | 5846.245 | 5846.245 | 5846.245 | 5846.245 |  | 21159.0479 | 27372.7075 | 28997.5323 | 28899.2709 | 28905.152 | 29071.1685 | 29510.6691 | 29804.1085 | 30091.8262 | 30428.4785 | 30739.887 | 31042.6535 | 31076.4072 | 31429.934 | 31160.3195 | 31160.3195 | 31160.3195 | 31160.3195 | 31160.3195 | 31160.3195 | 31160.3195 | 31160.3195 | 31160.3195 | 31160.3195 | 31160.3195 | 31160.3195 | 31160.3195 | 31160.3195 | 31160.3195 | 31160.3195
25% | 2600.5659 | 3449.8542 | 3680.8886 | 3674.0639 | 3673.6775 | 3699.9319 | 3728.7511 | 3787.9686 | 3830.5285 | 3853.5736 | 3878.7363 | 3901.8059 | 3943.5668 | 3995.4216 | 3991.6984 | 3991.6984 | 3991.6984 | 3991.6984 | 3991.6984 | 3991.6984 | 3991.6984 | 3991.6984 | 3991.6984 | 3991.6984 | 3991.6984 | 3991.6984 | 3991.6984 | 3991.6984 | 3991.6984 | 3991.6984 |  | 6103.1255 | 7895.3963 | 8364.0615 | 8335.719 | 8337.4153 | 8385.3012 | 8512.071 | 8596.7107 | 8679.7002 | 8776.8043 | 8866.6271 | 8953.9572 | 8963.6932 | 9065.6646 | 8987.8969 | 8987.8969 | 8987.8969 | 8987.8969 | 8987.8969 | 8987.8969 | 8987.8969 | 8987.8969 | 8987.8969 | 8987.8969 | 8987.8969 | 8987.8969 | 8987.8969 | 8987.8969 | 8987.8969 | 8987.8969
20% | 1575.389 | 2089.8768 | 2229.8344 | 2225.7001 | 2225.4661 | 2241.3706 | 2258.8289 | 2294.7021 | 2320.4843 | 2334.4448 | 2349.688 | 2363.6632 | 2388.9615 | 2420.3744 | 2418.119 | 2418.119 | 2418.119 | 2418.119 | 2418.119 | 2418.119 | 2418.119 | 2418.119 | 2418.119 | 2418.119 | 2418.119 | 2418.119 | 2418.119 | 2418.119 | 2418.119 | 2418.119 |  | 1637.7285 | 2118.6711 | 2244.4339 | 2236.8284 | 2237.2836 | 2250.1334 | 2284.1512 | 2306.8636 | 2329.1332 | 2355.1904 | 2379.2937 | 2402.7281 | 2405.3406 | 2432.7039 | 2411.8355 | 2411.8355 | 2411.8355 | 2411.8355 | 2411.8355 | 2411.8355 | 2411.8355 | 2411.8355 | 2411.8355 | 2411.8355 | 2411.8355 | 2411.8355 | 2411.8355 | 2411.8355 | 2411.8355 | 2411.8355
15% | 1008.6332 | 1338.0309 | 1427.6379 | 1424.9909 | 1424.8411 | 1435.0239 | 1446.2014 | 1469.169 | 1485.676 | 1494.614 | 1504.3734 | 1513.321 | 1529.518 | 1549.63 | 1548.1859 | 1548.1859 | 1548.1859 | 1548.1859 | 1548.1859 | 1548.1859 | 1548.1859 | 1548.1859 | 1548.1859 | 1548.1859 | 1548.1859 | 1548.1859 | 1548.1859 | 1548.1859 | 1548.1859 | 1548.1859 |  | 903.3078 | 1168.5771 | 1237.943 | 1233.7481 | 1233.9992 | 1241.0867 | 1259.8495 | 1272.3769 | 1284.6599 | 1299.032 | 1312.3265 | 1325.252 | 1326.693 | 1341.7855 | 1330.2753 | 1330.2753 | 1330.2753 | 1330.2753 | 1330.2753 | 1330.2753 | 1330.2753 | 1330.2753 | 1330.2753 | 1330.2753 | 1330.2753 | 1330.2753 | 1330.2753 | 1330.2753 | 1330.2753 | 1330.2753
10% | 675.0905 | 895.5604 | 955.5354 | 953.7638 | 953.6635 | 960.4789 | 967.9602 | 983.3327 | 994.381 | 1000.3634 | 1006.8954 | 1012.8841 | 1023.725 | 1037.1862 | 1036.2197 | 1036.2197 | 1036.2197 | 1036.2197 | 1036.2197 | 1036.2197 | 1036.2197 | 1036.2197 | 1036.2197 | 1036.2197 | 1036.2197 | 1036.2197 | 1036.2197 | 1036.2197 | 1036.2197 | 1036.2197 |  | 211.1088 | 273.1039 | 289.3152 | 288.3348 | 288.3935 | 290.0499 | 294.4349 | 297.3626 | 300.2332 | 303.5921 | 306.6991 | 309.7199 | 310.0566 | 313.5838 | 310.8938 | 310.8938 | 310.8938 | 310.8938 | 310.8938 | 310.8938 | 310.8938 | 310.8938 | 310.8938 | 310.8938 | 310.8938 | 310.8938 | 310.8938 | 310.8938 | 310.8938 | 310.8938
5% | 480.3015 | 637.1576 | 679.8276 | 678.5671 | 678.4957 | 683.3447 | 688.6673 | 699.6043 | 707.4647 | 711.721 | 716.3683 | 720.629 | 728.3419 | 737.919 | 737.2314 | 737.2314 | 737.2314 | 737.2314 | 737.2314 | 737.2314 | 737.2314 | 737.2314 | 737.2314 | 737.2314 | 737.2314 | 737.2314 | 737.2314 | 737.2314 | 737.2314 | 737.2314 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9.992e-14% | 42.1598 | 55.9283 | 59.6738 | 59.5631 | 59.5568 | 59.9825 | 60.4497 | 61.4097 | 62.0997 | 62.4733 | 62.8812 | 63.2552 | 63.9322 | 64.7729 | 64.7125 | 64.7125 | 64.7125 | 64.7125 | 64.7125 | 64.7125 | 64.7125 | 64.7125 | 64.7125 | 64.7125 | 64.7125 | 64.7125 | 64.7125 | 64.7125 | 64.7125 | 64.7125 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E @ R (MWh) | 112911.4176 | 149785.8315 | 159816.886 | 159520.5704 | 159503.7964 | 160643.7099 | 161894.98 | 164466.0868 | 166313.955 | 167314.5287 | 168407.043 | 169408.6762 | 171221.8548 | 173473.2847 | 173311.6334 | 173311.6334 | 173311.6334 | 173311.6334 | 173311.6334 | 173311.6334 | 173311.6334 | 173311.6334 | 173311.6334 | 173311.6334 | 173311.6334 | 173311.6334 | 173311.6334 | 173311.6334 | 173311.6334 | 173311.6334 | E @ R (MWh) | 109518.1284 | 141679.7064 | 150089.7144 | 149581.1188 | 149611.5589 | 150470.8515 | 152745.6837 | 154264.5107 | 155753.7228 | 157496.2176 | 159108.0516 | 160675.1553 | 160849.8627 | 162679.6988 | 161284.1885 | 161284.1885 | 161284.1885 | 161284.1885 | 161284.1885 | 161284.1885 | 161284.1885 | 161284.1885 | 161284.1885 | 161284.1885 | 161284.1885 | 161284.1885 | 161284.1885 | 161284.1885 | 161284.1885 | 161284.1885
Option 7 Summer POE50 W E @ R (MWh) N 2 | 79037.9923 | 104850.082 | 111871.8202 | 111664.3993 | 111652.6574 | 112450.5969 | 113326.486 | 115126.2607 | 116419.7685 | 117120.1701 | 117884.9301 | 118586.0733 | 119855.2983 | 121431.2993 | 121318.1434 | 121318.1434 | 121318.1434 | 121318.1434 | 121318.1434 | 121318.1434 | 121318.1434 | 121318.1434 | 121318.1434 | 121318.1434 | 121318.1434 | 121318.1434 | 121318.1434 | 121318.1434 | 121318.1434 | 121318.1434 | Option 7 Summer POE10 W E @ R (MWh) N 2 | 32855.4385 | 42503.9119 | 45026.9143 | 44874.3356 | 44883.4677 | 45141.2555 | 45823.7051 | 46279.3532 | 46726.1168 | 47248.8653 | 47732.4155 | 48202.5466 | 48254.9588 | 48803.9096 | 48385.2566 | 48385.2566 | 48385.2566 | 48385.2566 | 48385.2566 | 48385.2566 | 48385.2566 | 48385.2566 | 48385.2566 | 48385.2566 | 48385.2566 | 48385.2566 | 48385.2566 | 48385.2566 | 48385.2566 | 48385.2566
Option 8 -
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | 73.4908 | 101.8011 | 109.1509 | 110.3988 | 111.3674 | 113.0455 | 116.8717 | 119.4274 | 122.671 | 124.3515 | 125.8258 | 123.0846 | 126.2829 | 131.3148 | 127.4847 | 127.4847 | 127.4847 | 127.4847 | 127.4847 | 127.4847 | 127.4847 | 127.4847 | 127.4847 | 127.4847 | 127.4847 | 127.4847 | 127.4847 | 127.4847 | 127.4847 | 127.4847 |  | 78.6411 | 106.5944 | 114.2314 | 115.4081 | 116.1495 | 117.791 | 121.6771 | 123.7926 | 127.8346 | 140.1348 | 129.9793 | 127.9882 | 130.6605 | 136.5124 | 132.5403 | 132.5403 | 132.5403 | 132.5403 | 132.5403 | 132.5403 | 132.5403 | 132.5403 | 132.5403 | 132.5403 | 132.5403 | 132.5403 | 132.5403 | 132.5403 | 132.5403 | 132.5403
98% | 87.3027 | 120.9335 | 129.6647 | 131.1472 | 132.2978 | 134.2912 | 138.8365 | 141.8726 | 145.7258 | 147.722 | 149.4734 | 146.2171 | 150.0165 | 155.9941 | 151.4442 | 151.4442 | 151.4442 | 151.4442 | 151.4442 | 151.4442 | 151.4442 | 151.4442 | 151.4442 | 151.4442 | 151.4442 | 151.4442 | 151.4442 | 151.4442 | 151.4442 | 151.4442 |  | 93.4209 | 126.6277 | 135.7001 | 137.0978 | 137.9786 | 139.9286 | 144.5451 | 147.0581 | 151.8598 | 166.4717 | 154.4076 | 152.0423 | 155.2168 | 162.1685 | 157.4499 | 157.4499 | 157.4499 | 157.4499 | 157.4499 | 157.4499 | 157.4499 | 157.4499 | 157.4499 | 157.4499 | 157.4499 | 157.4499 | 157.4499 | 157.4499 | 157.4499 | 157.4499
97% | 172.8327 | 239.4116 | 256.6966 | 259.6314 | 261.9093 | 265.8557 | 274.854 | 280.8645 | 288.4926 | 292.4446 | 295.9119 | 289.4652 | 296.9869 | 308.8207 | 299.8133 | 299.8133 | 299.8133 | 299.8133 | 299.8133 | 299.8133 | 299.8133 | 299.8133 | 299.8133 | 299.8133 | 299.8133 | 299.8133 | 299.8133 | 299.8133 | 299.8133 | 299.8133 |  | 184.945 | 250.6842 | 268.6448 | 271.4119 | 273.1556 | 277.0161 | 286.1552 | 291.1302 | 300.6362 | 329.5634 | 305.68 | 300.9974 | 307.2819 | 321.0443 | 311.7028 | 311.7028 | 311.7028 | 311.7028 | 311.7028 | 311.7028 | 311.7028 | 311.7028 | 311.7028 | 311.7028 | 311.7028 | 311.7028 | 311.7028 | 311.7028 | 311.7028 | 311.7028
95% | 510.5211 | 707.185 | 758.2422 | 766.9113 | 773.6398 | 785.297 | 811.8764 | 829.6304 | 852.1628 | 863.8365 | 874.0782 | 855.0358 | 877.2537 | 912.2089 | 885.6025 | 885.6025 | 885.6025 | 885.6025 | 885.6025 | 885.6025 | 885.6025 | 885.6025 | 885.6025 | 885.6025 | 885.6025 | 885.6025 | 885.6025 | 885.6025 | 885.6025 | 885.6025 |  | 546.299 | 740.4826 | 793.5354 | 801.7091 | 806.8595 | 818.2629 | 845.2585 | 859.9539 | 888.0332 | 973.4795 | 902.9316 | 889.1001 | 907.6635 | 948.3155 | 920.7222 | 920.7222 | 920.7222 | 920.7222 | 920.7222 | 920.7222 | 920.7222 | 920.7222 | 920.7222 | 920.7222 | 920.7222 | 920.7222 | 920.7222 | 920.7222 | 920.7222 | 920.7222
90% | 2814.8088 | 3899.1347 | 4180.6436 | 4228.4418 | 4265.5399 | 4329.8131 | 4476.3615 | 4574.25 | 4698.4845 | 4762.8484 | 4819.3169 | 4714.3248 | 4836.8255 | 5029.5548 | 4882.8573 | 4882.8573 | 4882.8573 | 4882.8573 | 4882.8573 | 4882.8573 | 4882.8573 | 4882.8573 | 4882.8573 | 4882.8573 | 4882.8573 | 4882.8573 | 4882.8573 | 4882.8573 | 4882.8573 | 4882.8573 |  | 3012.0741 | 4082.7244 | 4375.2363 | 4420.3027 | 4448.7 | 4511.5741 | 4660.4169 | 4741.4413 | 4896.2592 | 5367.3759 | 4978.4031 | 4902.1418 | 5004.4932 | 5228.6319 | 5076.4935 | 5076.4935 | 5076.4935 | 5076.4935 | 5076.4935 | 5076.4935 | 5076.4935 | 5076.4935 | 5076.4935 | 5076.4935 | 5076.4935 | 5076.4935 | 5076.4935 | 5076.4935 | 5076.4935 | 5076.4935
85% | 6876.3763 | 9525.3066 | 10213.0129 | 10329.7805 | 10420.4084 | 10577.4231 | 10935.4305 | 11174.565 | 11478.0609 | 11635.2975 | 11773.246 | 11516.7578 | 11816.0183 | 12286.8422 | 11928.4707 | 11928.4707 | 11928.4707 | 11928.4707 | 11928.4707 | 11928.4707 | 11928.4707 | 11928.4707 | 11928.4707 | 11928.4707 | 11928.4707 | 11928.4707 | 11928.4707 | 11928.4707 | 11928.4707 | 11928.4707 |  | 7358.2813 | 9973.8032 | 10688.3888 | 10798.4829 | 10867.8555 | 11021.4524 | 11385.0646 | 11583.0015 | 11961.2104 | 13112.1147 | 12161.8821 | 11975.5812 | 12225.6185 | 12773.1733 | 12401.51 | 12401.51 | 12401.51 | 12401.51 | 12401.51 | 12401.51 | 12401.51 | 12401.51 | 12401.51 | 12401.51 | 12401.51 | 12401.51 | 12401.51 | 12401.51 | 12401.51 | 12401.51
80% | 10687.9274 | 14805.1503 | 15874.0497 | 16055.5412 | 16196.4038 | 16440.4513 | 16996.9008 | 17368.5868 | 17840.3094 | 18084.7017 | 18299.1145 | 17900.4559 | 18365.5953 | 19097.3952 | 18540.3797 | 18540.3797 | 18540.3797 | 18540.3797 | 18540.3797 | 18540.3797 | 18540.3797 | 18540.3797 | 18540.3797 | 18540.3797 | 18540.3797 | 18540.3797 | 18540.3797 | 18540.3797 | 18540.3797 | 18540.3797 |  | 11436.9506 | 15502.2469 | 16612.9248 | 16784.0437 | 16891.8693 | 17130.6044 | 17695.7655 | 18003.4182 | 18591.267 | 20380.1135 | 18903.1703 | 18613.6034 | 19002.2355 | 19853.298 | 19275.623 | 19275.623 | 19275.623 | 19275.623 | 19275.623 | 19275.623 | 19275.623 | 19275.623 | 19275.623 | 19275.623 | 19275.623 | 19275.623 | 19275.623 | 19275.623 | 19275.623 | 19275.623
75% | 11791.7667 | 16334.2127 | 17513.507 | 17713.7428 | 17869.1536 | 18138.406 | 18752.3252 | 19162.3985 | 19682.8403 | 19952.4731 | 20189.0303 | 19749.1986 | 20262.3772 | 21069.7567 | 20455.2132 | 20455.2132 | 20455.2132 | 20455.2132 | 20455.2132 | 20455.2132 | 20455.2132 | 20455.2132 | 20455.2132 | 20455.2132 | 20455.2132 | 20455.2132 | 20455.2132 | 20455.2132 | 20455.2132 | 20455.2132 |  | 12618.1483 | 17103.3048 | 18328.6925 | 18517.4844 | 18636.4461 | 18899.8376 | 19523.368 | 19862.7948 | 20511.356 | 22484.9529 | 20855.4725 | 20535.9993 | 20964.769 | 21903.7284 | 21266.3917 | 21266.3917 | 21266.3917 | 21266.3917 | 21266.3917 | 21266.3917 | 21266.3917 | 21266.3917 | 21266.3917 | 21266.3917 | 21266.3917 | 21266.3917 | 21266.3917 | 21266.3917 | 21266.3917 | 21266.3917
70% | 12669.5942 | 17550.1984 | 18817.2842 | 19032.4264 | 19199.4066 | 19488.7033 | 20148.3251 | 20588.926 | 21148.1115 | 21437.817 | 21691.9844 | 21219.4098 | 21770.7916 | 22638.2758 | 21977.983 | 21977.983 | 21977.983 | 21977.983 | 21977.983 | 21977.983 | 21977.983 | 21977.983 | 21977.983 | 21977.983 | 21977.983 | 21977.983 | 21977.983 | 21977.983 | 21977.983 | 21977.983 |  | 13557.495 | 18376.5449 | 19693.1554 | 19896.0018 | 20023.8195 | 20306.8189 | 20976.7675 | 21341.4626 | 22038.3054 | 24158.8249 | 22408.0393 | 22064.7832 | 22525.4722 | 23534.3317 | 22849.549 | 22849.549 | 22849.549 | 22849.549 | 22849.549 | 22849.549 | 22849.549 | 22849.549 | 22849.549 | 22849.549 | 22849.549 | 22849.549 | 22849.549 | 22849.549 | 22849.549 | 22849.549
65% | 13351.323 | 18494.5441 | 19829.8096 | 20056.5282 | 20232.4932 | 20537.3565 | 21232.4714 | 21696.7803 | 22286.0546 | 22591.3486 | 22859.1924 | 22361.1894 | 22942.24 | 23856.402 | 23160.5801 | 23160.5801 | 23160.5801 | 23160.5801 | 23160.5801 | 23160.5801 | 23160.5801 | 23160.5801 | 23160.5801 | 23160.5801 | 23160.5801 | 23160.5801 | 23160.5801 | 23160.5801 | 23160.5801 | 23160.5801 |  | 14287.0002 | 19365.3548 | 20752.8099 | 20966.571 | 21101.2664 | 21399.4935 | 22105.4909 | 22489.8096 | 23224.1482 | 25458.7693 | 23613.7769 | 23252.0508 | 23737.5287 | 24800.6731 | 24079.0435 | 24079.0435 | 24079.0435 | 24079.0435 | 24079.0435 | 24079.0435 | 24079.0435 | 24079.0435 | 24079.0435 | 24079.0435 | 24079.0435 | 24079.0435 | 24079.0435 | 24079.0435 | 24079.0435 | 24079.0435
60% | 14698.1621 | 20360.2151 | 21830.1779 | 22079.7671 | 22273.483 | 22609.0999 | 23374.3358 | 23885.4827 | 24534.2012 | 24870.2922 | 25165.1552 | 24616.9152 | 25256.5804 | 26262.9602 | 25496.946 | 25496.946 | 25496.946 | 25496.946 | 25496.946 | 25496.946 | 25496.946 | 25496.946 | 25496.946 | 25496.946 | 25496.946 | 25496.946 | 25496.946 | 25496.946 | 25496.946 | 25496.946 |  | 15728.2275 | 21318.8704 | 22846.2875 | 23081.6122 | 23229.8952 | 23558.2066 | 24335.4227 | 24758.5102 | 25566.9267 | 28026.9692 | 25995.8598 | 25597.644 | 26132.0954 | 27302.4864 | 26508.0611 | 26508.0611 | 26508.0611 | 26508.0611 | 26508.0611 | 26508.0611 | 26508.0611 | 26508.0611 | 26508.0611 | 26508.0611 | 26508.0611 | 26508.0611 | 26508.0611 | 26508.0611 | 26508.0611 | 26508.0611
55% | 16350.7821 | 22649.4603 | 24284.7017 | 24562.354 | 24777.8508 | 25151.2035 | 26002.4804 | 26571.0991 | 27292.7577 | 27666.6379 | 27994.6544 | 27384.7719 | 28096.3592 | 29215.8935 | 28363.7508 | 28363.7508 | 28363.7508 | 28363.7508 | 28363.7508 | 28363.7508 | 28363.7508 | 28363.7508 | 28363.7508 | 28363.7508 | 28363.7508 | 28363.7508 | 28363.7508 | 28363.7508 | 28363.7508 | 28363.7508 |  | 17496.6651 | 23715.9042 | 25415.0598 | 25676.8438 | 25841.7993 | 26207.0251 | 27071.6291 | 27542.2874 | 28441.6 | 31178.2427 | 28918.7611 | 28475.7711 | 29070.3146 | 30372.3011 | 29488.5529 | 29488.5529 | 29488.5529 | 29488.5529 | 29488.5529 | 29488.5529 | 29488.5529 | 29488.5529 | 29488.5529 | 29488.5529 | 29488.5529 | 29488.5529 | 29488.5529 | 29488.5529 | 29488.5529 | 29488.5529
50% | 16573.101 | 22957.4214 | 24614.8968 | 24896.3244 | 25114.7512 | 25493.1803 | 26356.0319 | 26932.3821 | 27663.8529 | 28042.8167 | 28375.2932 | 27757.1182 | 28478.3809 | 29613.1373 | 28749.4081 | 28749.4081 | 28749.4081 | 28749.4081 | 28749.4081 | 28749.4081 | 28749.4081 | 28749.4081 | 28749.4081 | 28749.4081 | 28749.4081 | 28749.4081 | 28749.4081 | 28749.4081 | 28749.4081 | 28749.4081 |  | 17734.5645 | 24038.3655 | 25760.6242 | 26025.9676 | 26193.1661 | 26563.3577 | 27439.7177 | 27916.7755 | 28828.3158 | 31602.1683 | 29311.9648 | 28862.9515 | 29465.579 | 30785.2684 | 29889.5039 | 29889.5039 | 29889.5039 | 29889.5039 | 29889.5039 | 29889.5039 | 29889.5039 | 29889.5039 | 29889.5039 | 29889.5039 | 29889.5039 | 29889.5039 | 29889.5039 | 29889.5039 | 29889.5039 | 29889.5039
45% | 12791.4633 | 17719.0143 | 18998.2882 | 19215.4999 | 19384.0862 | 19676.1657 | 20342.1324 | 20786.9714 | 21351.5358 | 21644.0279 | 21900.6402 | 21423.5199 | 21980.2054 | 22856.034 | 22189.3899 | 22189.3899 | 22189.3899 | 22189.3899 | 22189.3899 | 22189.3899 | 22189.3899 | 22189.3899 | 22189.3899 | 22189.3899 | 22189.3899 | 22189.3899 | 22189.3899 | 22189.3899 | 22189.3899 | 22189.3899 |  | 13687.9049 | 18553.3094 | 19882.5844 | 20087.382 | 20216.4292 | 20502.1508 | 21178.5436 | 21546.7467 | 22250.2924 | 24391.2093 | 22623.5828 | 22277.025 | 22742.1454 | 23760.7091 | 23069.3395 | 23069.3395 | 23069.3395 | 23069.3395 | 23069.3395 | 23069.3395 | 23069.3395 | 23069.3395 | 23069.3395 | 23069.3395 | 23069.3395 | 23069.3395 | 23069.3395 | 23069.3395 | 23069.3395 | 23069.3395
40% | 6284.3875 | 8705.2708 | 9333.7723 | 9440.4874 | 9523.3131 | 9666.8104 | 9993.9968 | 10212.5442 | 10489.9121 | 10633.6121 | 10759.6846 | 10525.2775 | 10798.7746 | 11229.0652 | 10901.546 | 10901.546 | 10901.546 | 10901.546 | 10901.546 | 10901.546 | 10901.546 | 10901.546 | 10901.546 | 10901.546 | 10901.546 | 10901.546 | 10901.546 | 10901.546 | 10901.546 | 10901.546 |  | 6724.8052 | 9115.1562 | 9768.223 | 9868.8391 | 9932.2394 | 10072.6131 | 10404.9218 | 10585.8183 | 10931.4671 | 11983.2898 | 11114.863 | 10944.6007 | 11173.1122 | 11673.5279 | 11333.8612 | 11333.8612 | 11333.8612 | 11333.8612 | 11333.8612 | 11333.8612 | 11333.8612 | 11333.8612 | 11333.8612 | 11333.8612 | 11333.8612 | 11333.8612 | 11333.8612 | 11333.8612 | 11333.8612 | 11333.8612
35% | 2348.7515 | 3253.5419 | 3488.4405 | 3528.3246 | 3559.2802 | 3612.9114 | 3735.1954 | 3816.8761 | 3920.5407 | 3974.2477 | 4021.3665 | 3933.7583 | 4035.9762 | 4196.7946 | 4074.3863 | 4074.3863 | 4074.3863 | 4074.3863 | 4074.3863 | 4074.3863 | 4074.3863 | 4074.3863 | 4074.3863 | 4074.3863 | 4074.3863 | 4074.3863 | 4074.3863 | 4074.3863 | 4074.3863 | 4074.3863 |  | 2513.3549 | 3406.7341 | 3650.8138 | 3688.4184 | 3712.1139 | 3764.5777 | 3888.7761 | 3956.3851 | 4085.5692 | 4478.6815 | 4154.1123 | 4090.4778 | 4175.8826 | 4362.9099 | 4235.9615 | 4235.9615 | 4235.9615 | 4235.9615 | 4235.9615 | 4235.9615 | 4235.9615 | 4235.9615 | 4235.9615 | 4235.9615 | 4235.9615 | 4235.9615 | 4235.9615 | 4235.9615 | 4235.9615 | 4235.9615
30% | 1171.4214 | 1622.6784 | 1739.8323 | 1759.7242 | 1775.163 | 1801.9112 | 1862.8993 | 1903.637 | 1955.3388 | 1982.1248 | 2005.6249 | 1961.931 | 2012.9114 | 2093.1183 | 2032.0682 | 2032.0682 | 2032.0682 | 2032.0682 | 2032.0682 | 2032.0682 | 2032.0682 | 2032.0682 | 2032.0682 | 2032.0682 | 2032.0682 | 2032.0682 | 2032.0682 | 2032.0682 | 2032.0682 | 2032.0682 |  | 1253.516 | 1699.0818 | 1820.8147 | 1839.5697 | 1851.3876 | 1877.5536 | 1939.4965 | 1973.2159 | 2037.6455 | 2233.7072 | 2071.8308 | 2040.0936 | 2082.6886 | 2175.967 | 2112.6525 | 2112.6525 | 2112.6525 | 2112.6525 | 2112.6525 | 2112.6525 | 2112.6525 | 2112.6525 | 2112.6525 | 2112.6525 | 2112.6525 | 2112.6525 | 2112.6525 | 2112.6525 | 2112.6525 | 2112.6525
25% | 690.592 | 956.6232 | 1025.6893 | 1037.4162 | 1046.5179 | 1062.2869 | 1098.2414 | 1122.2576 | 1152.7376 | 1168.5288 | 1182.3829 | 1156.6239 | 1186.6785 | 1233.9632 | 1197.9721 | 1197.9721 | 1197.9721 | 1197.9721 | 1197.9721 | 1197.9721 | 1197.9721 | 1197.9721 | 1197.9721 | 1197.9721 | 1197.9721 | 1197.9721 | 1197.9721 | 1197.9721 | 1197.9721 | 1197.9721 |  | 738.9896 | 1001.6655 | 1073.4311 | 1084.4878 | 1091.4549 | 1106.8806 | 1143.398 | 1163.2767 | 1201.2601 | 1316.845 | 1221.4135 | 1202.7034 | 1227.8145 | 1282.8053 | 1245.4793 | 1245.4793 | 1245.4793 | 1245.4793 | 1245.4793 | 1245.4793 | 1245.4793 | 1245.4793 | 1245.4793 | 1245.4793 | 1245.4793 | 1245.4793 | 1245.4793 | 1245.4793 | 1245.4793 | 1245.4793
20% | 348.989 | 483.4272 | 518.3296 | 524.2558 | 528.8553 | 536.8241 | 554.9937 | 567.1302 | 582.5332 | 590.5132 | 597.5144 | 584.4971 | 599.6851 | 623.5803 | 605.3923 | 605.3923 | 605.3923 | 605.3923 | 605.3923 | 605.3923 | 605.3923 | 605.3923 | 605.3923 | 605.3923 | 605.3923 | 605.3923 | 605.3923 | 605.3923 | 605.3923 | 605.3923 |  | 373.4466 | 506.1893 | 542.4558 | 548.0433 | 551.5641 | 559.3594 | 577.8134 | 587.8591 | 607.0539 | 665.4645 | 617.2384 | 607.7833 | 620.4731 | 648.2626 | 629.3999 | 629.3999 | 629.3999 | 629.3999 | 629.3999 | 629.3999 | 629.3999 | 629.3999 | 629.3999 | 629.3999 | 629.3999 | 629.3999 | 629.3999 | 629.3999 | 629.3999 | 629.3999
15% | 142.1807 | 196.9518 | 211.1713 | 213.5857 | 215.4596 | 218.7061 | 226.1085 | 231.053 | 237.3283 | 240.5795 | 243.4318 | 238.1285 | 244.3162 | 254.0512 | 246.6413 | 246.6413 | 246.6413 | 246.6413 | 246.6413 | 246.6413 | 246.6413 | 246.6413 | 246.6413 | 246.6413 | 246.6413 | 246.6413 | 246.6413 | 246.6413 | 246.6413 | 246.6413 |  | 152.1449 | 206.2253 | 221.0005 | 223.2769 | 224.7113 | 227.8872 | 235.4055 | 239.4982 | 247.3183 | 271.1152 | 251.4675 | 247.6154 | 252.7853 | 264.107 | 256.4222 | 256.4222 | 256.4222 | 256.4222 | 256.4222 | 256.4222 | 256.4222 | 256.4222 | 256.4222 | 256.4222 | 256.4222 | 256.4222 | 256.4222 | 256.4222 | 256.4222 | 256.4222
10% | 57.2416 | 79.2923 | 85.017 | 85.989 | 86.7435 | 88.0505 | 91.0307 | 93.0214 | 95.5478 | 96.8567 | 98.005 | 95.8699 | 98.3611 | 102.2804 | 99.2972 | 99.2972 | 99.2972 | 99.2972 | 99.2972 | 99.2972 | 99.2972 | 99.2972 | 99.2972 | 99.2972 | 99.2972 | 99.2972 | 99.2972 | 99.2972 | 99.2972 | 99.2972 |  | 61.2531 | 83.0258 | 88.9742 | 89.8907 | 90.4682 | 91.7468 | 94.7736 | 96.4213 | 99.5697 | 109.1503 | 101.2402 | 99.6893 | 101.7707 | 106.3288 | 103.2349 | 103.2349 | 103.2349 | 103.2349 | 103.2349 | 103.2349 | 103.2349 | 103.2349 | 103.2349 | 103.2349 | 103.2349 | 103.2349 | 103.2349 | 103.2349 | 103.2349 | 103.2349
5% | 48.7477 | 67.5263 | 72.4016 | 73.2294 | 73.8719 | 74.985 | 77.5229 | 79.2182 | 81.3697 | 82.4844 | 83.4623 | 81.644 | 83.7655 | 87.1033 | 84.5627 | 84.5627 | 84.5627 | 84.5627 | 84.5627 | 84.5627 | 84.5627 | 84.5627 | 84.5627 | 84.5627 | 84.5627 | 84.5627 | 84.5627 | 84.5627 | 84.5627 | 84.5627 |  | 52.164 | 70.7058 | 75.7716 | 76.5521 | 77.0439 | 78.1327 | 80.7104 | 82.1137 | 84.7948 | 92.9538 | 86.2174 | 84.8967 | 86.6693 | 90.551 | 87.9162 | 87.9162 | 87.9162 | 87.9162 | 87.9162 | 87.9162 | 87.9162 | 87.9162 | 87.9162 | 87.9162 | 87.9162 | 87.9162 | 87.9162 | 87.9162 | 87.9162 | 87.9162
9.992e-14% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E @ R (MWh) | 130541.7636 | 180829.3011 | 193884.7798 | 196101.5072 | 197821.9953 | 200802.7777 | 207599.2223 | 212138.9744 | 217900.5692 | 220885.5628 | 223504.3892 | 218635.1944 | 224316.3823 | 233254.5468 | 226451.1896 | 226451.1896 | 226451.1896 | 226451.1896 | 226451.1896 | 226451.1896 | 226451.1896 | 226451.1896 | 226451.1896 | 226451.1896 | 226451.1896 | 226451.1896 | 226451.1896 | 226451.1896 | 226451.1896 | 226451.1896 | E @ R (MWh) | 139690.2921 | 189343.6009 | 202909.3599 | 204999.3971 | 206316.373 | 209232.2711 | 216135.1177 | 219892.7708 | 227072.7236 | 248921.5973 | 230882.2942 | 227345.5395 | 232092.2705 | 242487.1014 | 235431.4111 | 235431.4111 | 235431.4111 | 235431.4111 | 235431.4111 | 235431.4111 | 235431.4111 | 235431.4111 | 235431.4111 | 235431.4111 | 235431.4111 | 235431.4111 | 235431.4111 | 235431.4111 | 235431.4111 | 235431.4111
Option 8 Winter POE50 W E @ R (MWh) N 2 | 91379.2345 | 126580.5108 | 135719.3459 | 137271.0551 | 138475.3967 | 140561.9444 | 145319.4556 | 148497.2821 | 152530.3985 | 154619.8939 | 156453.0725 | 153044.6361 | 157021.4676 | 163278.1828 | 158515.8327 | 158515.8327 | 158515.8327 | 158515.8327 | 158515.8327 | 158515.8327 | 158515.8327 | 158515.8327 | 158515.8327 | 158515.8327 | 158515.8327 | 158515.8327 | 158515.8327 | 158515.8327 | 158515.8327 | 158515.8327 | Option 8 Winter POE10 W E @ R (MWh) N 2 | 41907.0876 | 56803.0803 | 60872.808 | 61499.8191 | 61894.9119 | 62769.6813 | 64840.5353 | 65967.8312 | 68121.8171 | 74676.4792 | 69264.6882 | 68203.6618 | 69627.6812 | 72746.1304 | 70629.4233 | 70629.4233 | 70629.4233 | 70629.4233 | 70629.4233 | 70629.4233 | 70629.4233 | 70629.4233 | 70629.4233 | 70629.4233 | 70629.4233 | 70629.4233 | 70629.4233 | 70629.4233 | 70629.4233 | 70629.4233
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 94.6719 | 122.4737 | 129.7436 | 129.304 | 129.3303 | 130.0731 | 132.0395 | 133.3525 | 134.6398 | 136.1461 | 137.5394 | 138.8941 | 139.0451 | 140.6269 | 139.4206 | 139.4206 | 139.4206 | 139.4206 | 139.4206 | 139.4206 | 139.4206 | 139.4206 | 139.4206 | 139.4206 | 139.4206 | 139.4206 | 139.4206 | 139.4206 | 139.4206 | 139.4206
98% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 46.8602 | 60.6214 | 64.2198 | 64.0022 | 64.0152 | 64.3829 | 65.3562 | 66.0061 | 66.6433 | 67.3889 | 68.0786 | 68.7491 | 68.8238 | 69.6068 | 69.0097 | 69.0097 | 69.0097 | 69.0097 | 69.0097 | 69.0097 | 69.0097 | 69.0097 | 69.0097 | 69.0097 | 69.0097 | 69.0097 | 69.0097 | 69.0097 | 69.0097 | 69.0097
97% | 20.8131 | 27.6102 | 29.4592 | 29.4046 | 29.4015 | 29.6116 | 29.8423 | 30.3162 | 30.6568 | 30.8412 | 31.0426 | 31.2273 | 31.5615 | 31.9765 | 31.9467 | 31.9467 | 31.9467 | 31.9467 | 31.9467 | 31.9467 | 31.9467 | 31.9467 | 31.9467 | 31.9467 | 31.9467 | 31.9467 | 31.9467 | 31.9467 | 31.9467 | 31.9467 |  | 92.7689 | 120.0119 | 127.1357 | 126.7049 | 126.7307 | 127.4585 | 129.3855 | 130.672 | 131.9335 | 133.4095 | 134.7748 | 136.1022 | 136.2502 | 137.8002 | 136.6181 | 136.6181 | 136.6181 | 136.6181 | 136.6181 | 136.6181 | 136.6181 | 136.6181 | 136.6181 | 136.6181 | 136.6181 | 136.6181 | 136.6181 | 136.6181 | 136.6181 | 136.6181
95% | 102.4643 | 135.9269 | 145.0299 | 144.761 | 144.7458 | 145.7802 | 146.9157 | 149.2489 | 150.9258 | 151.8338 | 152.8252 | 153.7342 | 155.3796 | 157.4227 | 157.276 | 157.276 | 157.276 | 157.276 | 157.276 | 157.276 | 157.276 | 157.276 | 157.276 | 157.276 | 157.276 | 157.276 | 157.276 | 157.276 | 157.276 | 157.276 |  | 137.0126 | 177.2483 | 187.7696 | 187.1334 | 187.1714 | 188.2465 | 191.0924 | 192.9925 | 194.8556 | 197.0355 | 199.052 | 201.0125 | 201.2311 | 203.5203 | 201.7745 | 201.7745 | 201.7745 | 201.7745 | 201.7745 | 201.7745 | 201.7745 | 201.7745 | 201.7745 | 201.7745 | 201.7745 | 201.7745 | 201.7745 | 201.7745 | 201.7745 | 201.7745
90% | 177.7116 | 235.7483 | 251.5362 | 251.0698 | 251.0434 | 252.8375 | 254.8069 | 258.8536 | 261.762 | 263.3368 | 265.0563 | 266.6327 | 269.4865 | 273.03 | 272.7756 | 272.7756 | 272.7756 | 272.7756 | 272.7756 | 272.7756 | 272.7756 | 272.7756 | 272.7756 | 272.7756 | 272.7756 | 272.7756 | 272.7756 | 272.7756 | 272.7756 | 272.7756 |  | 594.078 | 768.5376 | 814.1574 | 811.3985 | 811.5637 | 816.2249 | 828.5646 | 836.8035 | 844.8817 | 854.3338 | 863.0771 | 871.5778 | 872.5255 | 882.4514 | 874.8815 | 874.8815 | 874.8815 | 874.8815 | 874.8815 | 874.8815 | 874.8815 | 874.8815 | 874.8815 | 874.8815 | 874.8815 | 874.8815 | 874.8815 | 874.8815 | 874.8815 | 874.8815
85% | 504.3166 | 669.0154 | 713.8189 | 712.4955 | 712.4205 | 717.5119 | 723.1007 | 734.5845 | 742.838 | 747.307 | 752.1867 | 756.6605 | 764.759 | 774.815 | 774.093 | 774.093 | 774.093 | 774.093 | 774.093 | 774.093 | 774.093 | 774.093 | 774.093 | 774.093 | 774.093 | 774.093 | 774.093 | 774.093 | 774.093 | 774.093 |  | 561.9657 | 726.995 | 770.1489 | 767.5392 | 767.6954 | 772.1046 | 783.7774 | 791.5709 | 799.2124 | 808.1536 | 816.4243 | 824.4655 | 825.362 | 834.7513 | 827.5906 | 827.5906 | 827.5906 | 827.5906 | 827.5906 | 827.5906 | 827.5906 | 827.5906 | 827.5906 | 827.5906 | 827.5906 | 827.5906 | 827.5906 | 827.5906 | 827.5906 | 827.5906
80% | 704.4422 | 934.4978 | 997.0804 | 995.2318 | 995.1271 | 1002.2389 | 1010.0454 | 1026.0863 | 1037.6149 | 1043.8574 | 1050.6735 | 1056.9226 | 1068.2348 | 1082.2812 | 1081.2727 | 1081.2727 | 1081.2727 | 1081.2727 | 1081.2727 | 1081.2727 | 1081.2727 | 1081.2727 | 1081.2727 | 1081.2727 | 1081.2727 | 1081.2727 | 1081.2727 | 1081.2727 | 1081.2727 | 1081.2727 |  | 392.484 | 507.7425 | 537.8818 | 536.0591 | 536.1682 | 539.2477 | 547.4001 | 552.8431 | 558.1801 | 564.4247 | 570.2011 | 575.8172 | 576.4433 | 583.0009 | 577.9998 | 577.9998 | 577.9998 | 577.9998 | 577.9998 | 577.9998 | 577.9998 | 577.9998 | 577.9998 | 577.9998 | 577.9998 | 577.9998 | 577.9998 | 577.9998 | 577.9998 | 577.9998
75% | 1836.3528 | 2436.0657 | 2599.2074 | 2594.3882 | 2594.1154 | 2612.6546 | 2633.0048 | 2674.8204 | 2704.8735 | 2721.1465 | 2738.9148 | 2755.205 | 2784.6939 | 2821.3104 | 2818.6814 | 2818.6814 | 2818.6814 | 2818.6814 | 2818.6814 | 2818.6814 | 2818.6814 | 2818.6814 | 2818.6814 | 2818.6814 | 2818.6814 | 2818.6814 | 2818.6814 | 2818.6814 | 2818.6814 | 2818.6814 |  | 700.5244 | 906.2435 | 960.0375 | 956.7843 | 956.979 | 962.4754 | 977.0262 | 986.7412 | 996.2669 | 1007.4126 | 1017.7226 | 1027.7464 | 1028.8639 | 1040.5683 | 1031.6421 | 1031.6421 | 1031.6421 | 1031.6421 | 1031.6421 | 1031.6421 | 1031.6421 | 1031.6421 | 1031.6421 | 1031.6421 | 1031.6421 | 1031.6421 | 1031.6421 | 1031.6421 | 1031.6421 | 1031.6421
70% | 3172.6584 | 4208.7797 | 4490.6388 | 4482.3127 | 4481.8414 | 4513.8714 | 4549.0304 | 4621.275 | 4673.1976 | 4701.3124 | 4732.0106 | 4760.1551 | 4811.103 | 4874.3651 | 4869.823 | 4869.823 | 4869.823 | 4869.823 | 4869.823 | 4869.823 | 4869.823 | 4869.823 | 4869.823 | 4869.823 | 4869.823 | 4869.823 | 4869.823 | 4869.823 | 4869.823 | 4869.823 |  | 1276.1675 | 1650.9325 | 1748.9307 | 1743.0043 | 1743.359 | 1753.372 | 1779.8796 | 1797.5778 | 1814.931 | 1835.2355 | 1854.0175 | 1872.2783 | 1874.3141 | 1895.6364 | 1879.3751 | 1879.3751 | 1879.3751 | 1879.3751 | 1879.3751 | 1879.3751 | 1879.3751 | 1879.3751 | 1879.3751 | 1879.3751 | 1879.3751 | 1879.3751 | 1879.3751 | 1879.3751 | 1879.3751 | 1879.3751
65% | 7968.2023 | 10570.444 | 11278.3393 | 11257.4282 | 11256.2445 | 11336.6886 | 11424.9912 | 11606.4352 | 11736.84 | 11807.4509 | 11884.55 | 11955.2357 | 12083.1924 | 12242.0767 | 12230.6689 | 12230.6689 | 12230.6689 | 12230.6689 | 12230.6689 | 12230.6689 | 12230.6689 | 12230.6689 | 12230.6689 | 12230.6689 | 12230.6689 | 12230.6689 | 12230.6689 | 12230.6689 | 12230.6689 | 12230.6689 |  | 1605.6162 | 2077.1285 | 2200.4254 | 2192.969 | 2193.4153 | 2206.0132 | 2239.3639 | 2261.631 | 2283.4639 | 2309.0102 | 2332.6409 | 2355.6158 | 2358.1771 | 2385.0038 | 2364.5446 | 2364.5446 | 2364.5446 | 2364.5446 | 2364.5446 | 2364.5446 | 2364.5446 | 2364.5446 | 2364.5446 | 2364.5446 | 2364.5446 | 2364.5446 | 2364.5446 | 2364.5446 | 2364.5446 | 2364.5446
60% | 11647.312 | 15451.0709 | 16485.8185 | 16455.2522 | 16453.5219 | 16571.109 | 16700.1831 | 16965.4041 | 17156.0199 | 17259.2335 | 17371.9312 | 17475.2541 | 17662.2915 | 17894.5364 | 17877.8614 | 17877.8614 | 17877.8614 | 17877.8614 | 17877.8614 | 17877.8614 | 17877.8614 | 17877.8614 | 17877.8614 | 17877.8614 | 17877.8614 | 17877.8614 | 17877.8614 | 17877.8614 | 17877.8614 | 17877.8614 |  | 2512.492 | 3250.3215 | 3443.2583 | 3431.5904 | 3432.2888 | 3452.0021 | 3504.1898 | 3539.0337 | 3573.1982 | 3613.1734 | 3650.151 | 3686.1024 | 3690.1105 | 3732.0893 | 3700.0745 | 3700.0745 | 3700.0745 | 3700.0745 | 3700.0745 | 3700.0745 | 3700.0745 | 3700.0745 | 3700.0745 | 3700.0745 | 3700.0745 | 3700.0745 | 3700.0745 | 3700.0745 | 3700.0745 | 3700.0745
55% | 13170.4015 | 17471.5683 | 18641.6273 | 18607.0639 | 18605.1073 | 18738.071 | 18884.0238 | 19183.9271 | 19399.4692 | 19516.1798 | 19643.6146 | 19760.4488 | 19971.9446 | 20234.5597 | 20215.7041 | 20215.7041 | 20215.7041 | 20215.7041 | 20215.7041 | 20215.7041 | 20215.7041 | 20215.7041 | 20215.7041 | 20215.7041 | 20215.7041 | 20215.7041 | 20215.7041 | 20215.7041 | 20215.7041 | 20215.7041 |  | 4828.1473 | 6246.0024 | 6616.7608 | 6594.3391 | 6595.6811 | 6633.5633 | 6733.8501 | 6800.8082 | 6866.4607 | 6943.2792 | 7014.3375 | 7083.4238 | 7091.1259 | 7171.7949 | 7110.2733 | 7110.2733 | 7110.2733 | 7110.2733 | 7110.2733 | 7110.2733 | 7110.2733 | 7110.2733 | 7110.2733 | 7110.2733 | 7110.2733 | 7110.2733 | 7110.2733 | 7110.2733 | 7110.2733 | 7110.2733
50% | 16911.4168 | 22434.3178 | 23936.7286 | 23892.3477 | 23889.8353 | 24060.567 | 24247.9772 | 24633.0672 | 24909.8334 | 25059.6953 | 25223.3277 | 25373.3483 | 25644.9189 | 25982.129 | 25957.9175 | 25957.9175 | 25957.9175 | 25957.9175 | 25957.9175 | 25957.9175 | 25957.9175 | 25957.9175 | 25957.9175 | 25957.9175 | 25957.9175 | 25957.9175 | 25957.9175 | 25957.9175 | 25957.9175 | 25957.9175 |  | 10714.812 | 13861.3711 | 14684.1724 | 14634.4134 | 14637.3915 | 14721.4613 | 14944.0217 | 15092.6176 | 15238.3161 | 15408.7947 | 15566.4901 | 15719.8092 | 15736.9019 | 15915.9256 | 15779.3945 | 15779.3945 | 15779.3945 | 15779.3945 | 15779.3945 | 15779.3945 | 15779.3945 | 15779.3945 | 15779.3945 | 15779.3945 | 15779.3945 | 15779.3945 | 15779.3945 | 15779.3945 | 15779.3945 | 15779.3945
45% | 22520.2713 | 29874.9022 | 31875.6039 | 31816.5035 | 31813.1579 | 32040.5146 | 32290.0814 | 32802.8907 | 33171.4494 | 33371.0147 | 33588.9175 | 33788.694 | 34150.3339 | 34599.3834 | 34567.1419 | 34567.1419 | 34567.1419 | 34567.1419 | 34567.1419 | 34567.1419 | 34567.1419 | 34567.1419 | 34567.1419 | 34567.1419 | 34567.1419 | 34567.1419 | 34567.1419 | 34567.1419 | 34567.1419 | 34567.1419 |  | 16236.3476 | 21004.3853 | 22251.1909 | 22175.7903 | 22180.3031 | 22307.6955 | 22644.9453 | 22870.1153 | 23090.8949 | 23349.2243 | 23588.1829 | 23820.5101 | 23846.4109 | 24117.6889 | 23910.8008 | 23910.8008 | 23910.8008 | 23910.8008 | 23910.8008 | 23910.8008 | 23910.8008 | 23910.8008 | 23910.8008 | 23910.8008 | 23910.8008 | 23910.8008 | 23910.8008 | 23910.8008 | 23910.8008 | 23910.8008
40% | 15794.9825 | 20953.2804 | 22356.5072 | 22315.0562 | 22312.7097 | 22472.1702 | 22647.2082 | 23006.8759 | 23265.371 | 23405.3395 | 23558.1694 | 23698.2861 | 23951.9286 | 24266.8772 | 24244.2641 | 24244.2641 | 24244.2641 | 24244.2641 | 24244.2641 | 24244.2641 | 24244.2641 | 24244.2641 | 24244.2641 | 24244.2641 | 24244.2641 | 24244.2641 | 24244.2641 | 24244.2641 | 24244.2641 | 24244.2641 |  | 16811.9908 | 21749.0744 | 23040.0842 | 22962.0103 | 22966.6831 | 23098.592 | 23447.7987 | 23680.9519 | 23909.559 | 24177.0472 | 24424.4778 | 24665.0419 | 24691.8611 | 24972.7569 | 24758.5339 | 24758.5339 | 24758.5339 | 24758.5339 | 24758.5339 | 24758.5339 | 24758.5339 | 24758.5339 | 24758.5339 | 24758.5339 | 24758.5339 | 24758.5339 | 24758.5339 | 24758.5339 | 24758.5339 | 24758.5339
35% | 8189.141 | 10863.5364 | 11591.06 | 11569.5691 | 11568.3525 | 11651.0272 | 11741.7782 | 11928.2532 | 12062.2738 | 12134.8425 | 12214.0795 | 12286.725 | 12418.2297 | 12581.5194 | 12569.7953 | 12569.7953 | 12569.7953 | 12569.7953 | 12569.7953 | 12569.7953 | 12569.7953 | 12569.7953 | 12569.7953 | 12569.7953 | 12569.7953 | 12569.7953 | 12569.7953 | 12569.7953 | 12569.7953 | 12569.7953 |  | 22897.8708 | 29622.1608 | 31380.5115 | 31274.1752 | 31280.5395 | 31460.199 | 31935.8172 | 32253.3711 | 32564.7331 | 32929.051 | 33266.0507 | 33593.6981 | 33630.2257 | 34012.8048 | 33721.0338 | 33721.0338 | 33721.0338 | 33721.0338 | 33721.0338 | 33721.0338 | 33721.0338 | 33721.0338 | 33721.0338 | 33721.0338 | 33721.0338 | 33721.0338 | 33721.0338 | 33721.0338 | 33721.0338 | 33721.0338
30% | 3808.7911 | 5052.6595 | 5391.0326 | 5381.0371 | 5380.4713 | 5418.9235 | 5461.132 | 5547.8621 | 5610.1954 | 5643.9473 | 5680.8006 | 5714.5882 | 5775.7514 | 5851.6979 | 5846.245 | 5846.245 | 5846.245 | 5846.245 | 5846.245 | 5846.245 | 5846.245 | 5846.245 | 5846.245 | 5846.245 | 5846.245 | 5846.245 | 5846.245 | 5846.245 | 5846.245 | 5846.245 |  | 21159.0479 | 27372.7075 | 28997.5323 | 28899.2709 | 28905.152 | 29071.1685 | 29510.6691 | 29804.1085 | 30091.8262 | 30428.4785 | 30739.887 | 31042.6535 | 31076.4072 | 31429.934 | 31160.3195 | 31160.3195 | 31160.3195 | 31160.3195 | 31160.3195 | 31160.3195 | 31160.3195 | 31160.3195 | 31160.3195 | 31160.3195 | 31160.3195 | 31160.3195 | 31160.3195 | 31160.3195 | 31160.3195 | 31160.3195
25% | 2600.5659 | 3449.8542 | 3680.8886 | 3674.0639 | 3673.6775 | 3699.9319 | 3728.7511 | 3787.9686 | 3830.5285 | 3853.5736 | 3878.7363 | 3901.8059 | 3943.5668 | 3995.4216 | 3991.6984 | 3991.6984 | 3991.6984 | 3991.6984 | 3991.6984 | 3991.6984 | 3991.6984 | 3991.6984 | 3991.6984 | 3991.6984 | 3991.6984 | 3991.6984 | 3991.6984 | 3991.6984 | 3991.6984 | 3991.6984 |  | 6103.1255 | 7895.3963 | 8364.0615 | 8335.719 | 8337.4153 | 8385.3012 | 8512.071 | 8596.7107 | 8679.7002 | 8776.8043 | 8866.6271 | 8953.9572 | 8963.6932 | 9065.6646 | 8987.8969 | 8987.8969 | 8987.8969 | 8987.8969 | 8987.8969 | 8987.8969 | 8987.8969 | 8987.8969 | 8987.8969 | 8987.8969 | 8987.8969 | 8987.8969 | 8987.8969 | 8987.8969 | 8987.8969 | 8987.8969
20% | 1575.389 | 2089.8768 | 2229.8344 | 2225.7001 | 2225.4661 | 2241.3706 | 2258.8289 | 2294.7021 | 2320.4843 | 2334.4448 | 2349.688 | 2363.6632 | 2388.9615 | 2420.3744 | 2418.119 | 2418.119 | 2418.119 | 2418.119 | 2418.119 | 2418.119 | 2418.119 | 2418.119 | 2418.119 | 2418.119 | 2418.119 | 2418.119 | 2418.119 | 2418.119 | 2418.119 | 2418.119 |  | 1637.7285 | 2118.6711 | 2244.4339 | 2236.8284 | 2237.2836 | 2250.1334 | 2284.1512 | 2306.8636 | 2329.1332 | 2355.1904 | 2379.2937 | 2402.7281 | 2405.3406 | 2432.7039 | 2411.8355 | 2411.8355 | 2411.8355 | 2411.8355 | 2411.8355 | 2411.8355 | 2411.8355 | 2411.8355 | 2411.8355 | 2411.8355 | 2411.8355 | 2411.8355 | 2411.8355 | 2411.8355 | 2411.8355 | 2411.8355
15% | 1008.6332 | 1338.0309 | 1427.6379 | 1424.9909 | 1424.8411 | 1435.0239 | 1446.2014 | 1469.169 | 1485.676 | 1494.614 | 1504.3734 | 1513.321 | 1529.518 | 1549.63 | 1548.1859 | 1548.1859 | 1548.1859 | 1548.1859 | 1548.1859 | 1548.1859 | 1548.1859 | 1548.1859 | 1548.1859 | 1548.1859 | 1548.1859 | 1548.1859 | 1548.1859 | 1548.1859 | 1548.1859 | 1548.1859 |  | 903.3078 | 1168.5771 | 1237.943 | 1233.7481 | 1233.9992 | 1241.0867 | 1259.8495 | 1272.3769 | 1284.6599 | 1299.032 | 1312.3265 | 1325.252 | 1326.693 | 1341.7855 | 1330.2753 | 1330.2753 | 1330.2753 | 1330.2753 | 1330.2753 | 1330.2753 | 1330.2753 | 1330.2753 | 1330.2753 | 1330.2753 | 1330.2753 | 1330.2753 | 1330.2753 | 1330.2753 | 1330.2753 | 1330.2753
10% | 675.0905 | 895.5604 | 955.5354 | 953.7638 | 953.6635 | 960.4789 | 967.9602 | 983.3327 | 994.381 | 1000.3634 | 1006.8954 | 1012.8841 | 1023.725 | 1037.1862 | 1036.2197 | 1036.2197 | 1036.2197 | 1036.2197 | 1036.2197 | 1036.2197 | 1036.2197 | 1036.2197 | 1036.2197 | 1036.2197 | 1036.2197 | 1036.2197 | 1036.2197 | 1036.2197 | 1036.2197 | 1036.2197 |  | 211.1088 | 273.1039 | 289.3152 | 288.3348 | 288.3935 | 290.0499 | 294.4349 | 297.3626 | 300.2332 | 303.5921 | 306.6991 | 309.7199 | 310.0566 | 313.5838 | 310.8938 | 310.8938 | 310.8938 | 310.8938 | 310.8938 | 310.8938 | 310.8938 | 310.8938 | 310.8938 | 310.8938 | 310.8938 | 310.8938 | 310.8938 | 310.8938 | 310.8938 | 310.8938
5% | 480.3015 | 637.1576 | 679.8276 | 678.5671 | 678.4957 | 683.3447 | 688.6673 | 699.6043 | 707.4647 | 711.721 | 716.3683 | 720.629 | 728.3419 | 737.919 | 737.2314 | 737.2314 | 737.2314 | 737.2314 | 737.2314 | 737.2314 | 737.2314 | 737.2314 | 737.2314 | 737.2314 | 737.2314 | 737.2314 | 737.2314 | 737.2314 | 737.2314 | 737.2314 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9.992e-14% | 42.1598 | 55.9283 | 59.6738 | 59.5631 | 59.5568 | 59.9825 | 60.4497 | 61.4097 | 62.0997 | 62.4733 | 62.8812 | 63.2552 | 63.9322 | 64.7729 | 64.7125 | 64.7125 | 64.7125 | 64.7125 | 64.7125 | 64.7125 | 64.7125 | 64.7125 | 64.7125 | 64.7125 | 64.7125 | 64.7125 | 64.7125 | 64.7125 | 64.7125 | 64.7125 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E @ R (MWh) | 112911.4176 | 149785.8315 | 159816.886 | 159520.5704 | 159503.7964 | 160643.7099 | 161894.98 | 164466.0868 | 166313.955 | 167314.5287 | 168407.043 | 169408.6762 | 171221.8548 | 173473.2847 | 173311.6334 | 173311.6334 | 173311.6334 | 173311.6334 | 173311.6334 | 173311.6334 | 173311.6334 | 173311.6334 | 173311.6334 | 173311.6334 | 173311.6334 | 173311.6334 | 173311.6334 | 173311.6334 | 173311.6334 | 173311.6334 | E @ R (MWh) | 109518.1284 | 141679.7064 | 150089.7144 | 149581.1188 | 149611.5589 | 150470.8515 | 152745.6837 | 154264.5107 | 155753.7228 | 157496.2176 | 159108.0516 | 160675.1553 | 160849.8627 | 162679.6988 | 161284.1885 | 161284.1885 | 161284.1885 | 161284.1885 | 161284.1885 | 161284.1885 | 161284.1885 | 161284.1885 | 161284.1885 | 161284.1885 | 161284.1885 | 161284.1885 | 161284.1885 | 161284.1885 | 161284.1885 | 161284.1885
Option 8 Summer POE50 W E @ R (MWh) N 2 | 79037.9923 | 104850.082 | 111871.8202 | 111664.3993 | 111652.6574 | 112450.5969 | 113326.486 | 115126.2607 | 116419.7685 | 117120.1701 | 117884.9301 | 118586.0733 | 119855.2983 | 121431.2993 | 121318.1434 | 121318.1434 | 121318.1434 | 121318.1434 | 121318.1434 | 121318.1434 | 121318.1434 | 121318.1434 | 121318.1434 | 121318.1434 | 121318.1434 | 121318.1434 | 121318.1434 | 121318.1434 | 121318.1434 | 121318.1434 | Option 8 Summer POE10 W E @ R (MWh) N 2 | 32855.4385 | 42503.9119 | 45026.9143 | 44874.3356 | 44883.4677 | 45141.2555 | 45823.7051 | 46279.3532 | 46726.1168 | 47248.8653 | 47732.4155 | 48202.5466 | 48254.9588 | 48803.9096 | 48385.2566 | 48385.2566 | 48385.2566 | 48385.2566 | 48385.2566 | 48385.2566 | 48385.2566 | 48385.2566 | 48385.2566 | 48385.2566 | 48385.2566 | 48385.2566 | 48385.2566 | 48385.2566 | 48385.2566 | 48385.2566

## POF N,N-1 & N-2 Risk
N-2 Method 1
| Asset name | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Tx 1 Pof | DS-PHM-TRNFMR-9000004393 | 0.01357% | 0.01357% | 0.01791% | 0.023% | 0.02887% | 0.03555% | 0.04308% | 0.0515% | 0.06084% | 0.07112% | 0.08238% | 0.09465% | 0.1079% | 0.1223% | 0.1378% | 0.1378% | 0.1378% | 0.1378% | 0.1378% | 0.1378% | 0.1378% | 0.1378% | 0.1378% | 0.1378% | 0.1378% | 0.1378% | 0.1378% | 0.1378% | 0.1378% | 0.1378%
Tx 2 Pof | DS-PHM-TRNFMR-9000007050 | 0.01357% | 0.01357% | 0.01791% | 0.023% | 0.02887% | 0.03555% | 0.04308% | 0.0515% | 0.06084% | 0.07112% | 0.08238% | 0.09465% | 0.1079% | 0.1223% | 0.1378% | 0.1378% | 0.1378% | 0.1378% | 0.1378% | 0.1378% | 0.1378% | 0.1378% | 0.1378% | 0.1378% | 0.1378% | 0.1378% | 0.1378% | 0.1378% | 0.1378% | 0.1378%
Tx 3 Pof | bar: FY25 to FY54
Tx 4 Pof
Tx 5 Pof
Total Tx Pof |  | 0.02714% | 0.02714% | 0.03583% | 0.046% | 0.05773% | 0.0711% | 0.08616% | 0.103% | 0.1217% | 0.1422% | 0.1648% | 0.1893% | 0.2159% | 0.2446% | 0.2755% | 0.2755% | 0.2755% | 0.2755% | 0.2755% | 0.2755% | 0.2755% | 0.2755% | 0.2755% | 0.2755% | 0.2755% | 0.2755% | 0.2755% | 0.2755% | 0.2755% | 0.2755%
N-1 Risk |  | 0.01047% | 0.01047% | 0.01382% | 0.01775% | 0.02227% | 0.02743% | 0.03324% | 0.03974% | 0.04694% | 0.05488% | 0.06356% | 0.07303% | 0.08329% | 0.09438% | 0.1063% | 0.1063% | 0.1063% | 0.1063% | 0.1063% | 0.1063% | 0.1063% | 0.1063% | 0.1063% | 0.1063% | 0.1063% | 0.1063% | 0.1063% | 0.1063% | 0.1063% | 0.1063%
N-2 Risk |  | 4.318e-07% | 4.318e-07% | 7.523e-07% | 1.24e-06% | 1.953e-06% | 2.962e-06% | 4.351e-06% | 6.217e-06% | 8.675e-06% | 1.186e-05% | 1.591e-05% | 2.1e-05% | 2.731e-05% | 3.507e-05% | 4.449e-05% | 4.449e-05% | 4.449e-05% | 4.449e-05% | 4.449e-05% | 4.449e-05% | 4.449e-05% | 4.449e-05% | 4.449e-05% | 4.449e-05% | 4.449e-05% | 4.449e-05% | 4.449e-05% | 4.449e-05% | 4.449e-05% | 4.449e-05%
N Risk |  | 99.99% | 99.99% | 99.99% | 99.98% | 99.98% | 99.97% | 99.97% | 99.96% | 99.95% | 99.95% | 99.94% | 99.93% | 99.92% | 99.91% | 99.89% | 99.89% | 99.89% | 99.89% | 99.89% | 99.89% | 99.89% | 99.89% | 99.89% | 99.89% | 99.89% | 99.89% | 99.89% | 99.89% | 99.89% | 99.89%

## Summary
Involuntary load shedding (NER 5.17.1(c)(4)(ii))
Option 1 - Do Nothing / Base Case | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Weighted Energy @ Risk (MWh) under N Conditions | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.047852 | 0.076147 | 0.70127 | 0.1746 | 0.1746 | 0.1746 | 0.1746 | 0.1746 | 0.1746 | 0.1746 | 0.1746 | 0.1746 | 0.1746 | 0.1746 | 0.1746 | 0.1746 | 0.1746 | 0.1746 | 0.1746
Weighted Energy @ Risk (MWh) under N-1 Conditions | 0.032901 | 1.3517 | 3.018 | 4.0487 | 5.2651 | 7.0314 | 10.0174 | 13.4078 | 18.1148 | 25.1158 | 27.4427 | 29.628 | 37.5617 | 50.3309 | 50.8438 | 50.8438 | 50.8438 | 50.8438 | 50.8438 | 50.8438 | 50.8438 | 50.8438 | 50.8438 | 50.8438 | 50.8438 | 50.8438 | 50.8438 | 50.8438 | 50.8438 | 50.8438
Weighted Energy @ Risk (MWh) under N-2 Conditions | 0.0012928 | 0.0017409 | 0.003241 | 0.0053666 | 0.0084883 | 0.013014 | 0.019541 | 0.028413 | 0.040455 | 0.056638 | 0.075614 | 0.099076 | 0.13103 | 0.17292 | 0.21559 | 0.21559 | 0.21559 | 0.21559 | 0.21559 | 0.21559 | 0.21559 | 0.21559 | 0.21559 | 0.21559 | 0.21559 | 0.21559 | 0.21559 | 0.21559 | 0.21559 | 0.21559
Total EUE (MWh) - Option 1 | 0.034194 | 1.3534 | 3.0212 | 4.0541 | 5.2736 | 7.0444 | 10.0369 | 13.4362 | 18.1553 | 25.1725 | 27.5183 | 29.7749 | 37.7689 | 51.2051 | 51.234 | 51.234 | 51.234 | 51.234 | 51.234 | 51.234 | 51.234 | 51.234 | 51.234 | 51.234 | 51.234 | 51.234 | 51.234 | 51.234 | 51.234 | 51.234
Cost of EUE ($) - Option 1 | 1320.0832 | 52250.2261 | 116638.2684 | 156512.078 | 203592.9757 | 271955.8559 | 387486.1996 | 518720.9803 | 700905.2416 | 971811.9987 | 1062374.4731 | 1149494.6633 | 1458110.3655 | 1976830.5821 | 1977946.3358 | 1977946.3358 | 1977946.3358 | 1977946.3358 | 1977946.3358 | 1977946.3358 | 1977946.3358 | 1977946.3358 | 1977946.3358 | 1977946.3358 | 1977946.3358 | 1977946.3358 | 1977946.3358 | 1977946.3358 | 1977946.3358 | 1977946.3358
Hours at Risk pA. (Hrs) (N) | 1.486 | 1.486 | 1.486 | 1.486 | 1.486 | 1.486 | 1.486 | 1.486 | 1.486 | 1.486 | 1.486 | 2.9986 | 2.9986 | 3.755 | 2.9986 | 2.9986 | 2.9986 | 2.9986 | 2.9986 | 2.9986 | 2.9986 | 2.9986 | 2.9986 | 2.9986 | 2.9986 | 2.9986 | 2.9986 | 2.9986 | 2.9986 | 2.9986
Option 2 - 1B New PHS ZSS + Three new feeders | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Weighted Energy @ Risk (MWh) under N Conditions | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Weighted Energy @ Risk (MWh) under N-1 Conditions | 0.032901 | 1.3517 | 3.018 | 0.18074 | 0.25205 | 0.39931 | 0.81822 | 1.3496 | 2.3539 | 4.61 | 4.2292 | 3.993 | 5.9995 | 10.2793 | 8.7712 | 8.7712 | 8.7712 | 8.7712 | 8.7712 | 8.7712 | 8.7712 | 8.7712 | 8.7712 | 8.7712 | 8.7712 | 8.7712 | 8.7712 | 8.7712 | 8.7712 | 8.7712
Weighted Energy @ Risk (MWh) under N-2 Conditions | 0.0012928 | 0.0017409 | 0.003241 | 0.0040422 | 0.0064022 | 0.0098503 | 0.014894 | 0.021773 | 0.031189 | 0.043974 | 0.058623 | 0.076648 | 0.10185 | 0.13546 | 0.16808 | 0.16808 | 0.16808 | 0.16808 | 0.16808 | 0.16808 | 0.16808 | 0.16808 | 0.16808 | 0.16808 | 0.16808 | 0.16808 | 0.16808 | 0.16808 | 0.16808 | 0.16808
Total EUE (MWh) - Option 2 | 0.034194 | 1.3534 | 3.0212 | 0.18478 | 0.25845 | 0.40916 | 0.83312 | 1.3714 | 2.385 | 4.6539 | 4.2878 | 4.0696 | 6.1013 | 10.4148 | 8.9393 | 8.9393 | 8.9393 | 8.9393 | 8.9393 | 8.9393 | 8.9393 | 8.9393 | 8.9393 | 8.9393 | 8.9393 | 8.9393 | 8.9393 | 8.9393 | 8.9393 | 8.9393
Cost of EUE ($) - Option 2 | 1320.0832 | 52250.2261 | 116638.2684 | 7133.6501 | 9977.7895 | 15795.9869 | 32163.4749 | 52943.0323 | 92077.5758 | 179670.2378 | 165534.714 | 157112.2705 | 235549.3122 | 402073.8496 | 345111.747 | 345111.747 | 345111.747 | 345111.747 | 345111.747 | 345111.747 | 345111.747 | 345111.747 | 345111.747 | 345111.747 | 345111.747 | 345111.747 | 345111.747 | 345111.747 | 345111.747 | 345111.747
Option 3 - 2B PHM 3rd Tx + Switchroom + Two new feeders + OFR12 New Feeder | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Weighted Energy @ Risk (MWh) under N Conditions | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Weighted Energy @ Risk (MWh) under N-1 Conditions | 0.032901 | 1.3517 | 3.018 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0001052 | 0.00037821 | 0.0010464 | 0.0012944 | 0.0029852 | 0.002001 | 0.002001 | 0.002001 | 0.002001 | 0.002001 | 0.002001 | 0.002001 | 0.002001 | 0.002001 | 0.002001 | 0.002001 | 0.002001 | 0.002001 | 0.002001 | 0.002001 | 0.002001
Weighted Energy @ Risk (MWh) under N-2 Conditions | 0.0012928 | 0.0017409 | 0.003241 | 0.00038758 | 0.00063093 | 0.0010283 | 0.0017479 | 0.0027597 | 0.0043468 | 0.0069231 | 0.0088106 | 0.010954 | 0.015688 | 0.023463 | 0.026917 | 0.026917 | 0.026917 | 0.026917 | 0.026917 | 0.026917 | 0.026917 | 0.026917 | 0.026917 | 0.026917 | 0.026917 | 0.026917 | 0.026917 | 0.026917 | 0.026917 | 0.026917
Total EUE (MWh) - Option 3 | 0.034194 | 1.3534 | 3.0212 | 0.00038758 | 0.00063093 | 0.0010283 | 0.0017479 | 0.0027597 | 0.0043468 | 0.0070283 | 0.0091888 | 0.012 | 0.016983 | 0.026449 | 0.028918 | 0.028918 | 0.028918 | 0.028918 | 0.028918 | 0.028918 | 0.028918 | 0.028918 | 0.028918 | 0.028918 | 0.028918 | 0.028918 | 0.028918 | 0.028918 | 0.028918 | 0.028918
Cost of EUE ($) - Option 3 | 1320.0832 | 52250.2261 | 116638.2684 | 14.9628 | 24.3577 | 39.6979 | 67.4814 | 106.5432 | 167.8132 | 271.3342 | 354.7438 | 463.2904 | 655.6296 | 1021.0799 | 1116.4194 | 1116.4194 | 1116.4194 | 1116.4194 | 1116.4194 | 1116.4194 | 1116.4194 | 1116.4194 | 1116.4194 | 1116.4194 | 1116.4194 | 1116.4194 | 1116.4194 | 1116.4194 | 1116.4194 | 1116.4194
Option 4 - 3B OFR 3rd Tx + Switchroom + Two new feeders + OFR12 New Feeder | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Weighted Energy @ Risk (MWh) under N Conditions | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Weighted Energy @ Risk (MWh) under N-1 Conditions | 0.032901 | 1.3517 | 3.018 | 2.7223 | 3.5703 | 4.8513 | 7.1468 | 9.7627 | 13.5125 | 19.3351 | 20.829 | 22.2112 | 28.6387 | 39.3622 | 39.0808 | 39.0808 | 39.0808 | 39.0808 | 39.0808 | 39.0808 | 39.0808 | 39.0808 | 39.0808 | 39.0808 | 39.0808 | 39.0808 | 39.0808 | 39.0808 | 39.0808 | 39.0808
Weighted Energy @ Risk (MWh) under N-2 Conditions | 0.0012928 | 0.0017409 | 0.003241 | 0.0050926 | 0.0080567 | 0.01236 | 0.01858 | 0.027039 | 0.038538 | 0.054018 | 0.072099 | 0.094436 | 0.12499 | 0.16517 | 0.20576 | 0.20576 | 0.20576 | 0.20576 | 0.20576 | 0.20576 | 0.20576 | 0.20576 | 0.20576 | 0.20576 | 0.20576 | 0.20576 | 0.20576 | 0.20576 | 0.20576 | 0.20576
Total EUE (MWh) - Option 4 | 0.034194 | 1.3534 | 3.0212 | 2.7274 | 3.5783 | 4.8637 | 7.1654 | 9.7897 | 13.5511 | 19.3891 | 20.9011 | 22.3056 | 28.7637 | 39.5273 | 39.2866 | 39.2866 | 39.2866 | 39.2866 | 39.2866 | 39.2866 | 39.2866 | 39.2866 | 39.2866 | 39.2866 | 39.2866 | 39.2866 | 39.2866 | 39.2866 | 39.2866 | 39.2866
Cost of EUE ($) - Option 4 | 1320.0832 | 52250.2261 | 116638.2684 | 105292.4874 | 138145.4813 | 187769.0884 | 276627.011 | 377943.6481 | 523155.2653 | 748537.4507 | 806911.6711 | 861134.2666 | 1110454.94 | 1525998.4082 | 1516703.5062 | 1516703.5062 | 1516703.5062 | 1516703.5062 | 1516703.5062 | 1516703.5062 | 1516703.5062 | 1516703.5062 | 1516703.5062 | 1516703.5062 | 1516703.5062 | 1516703.5062 | 1516703.5062 | 1516703.5062 | 1516703.5062 | 1516703.5062
Option 5 - 4B LLG 2nd Tx + Switchroom + Two new feeders + OFR12 New Feeder | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Weighted Energy @ Risk (MWh) under N Conditions | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Weighted Energy @ Risk (MWh) under N-1 Conditions | 0.032901 | 1.3517 | 3.018 | 0.094541 | 0.13047 | 0.20715 | 0.45632 | 0.79439 | 1.5077 | 3.343 | 2.862 | 2.5966 | 4.0993 | 7.5453 | 6.1197 | 6.1197 | 6.1197 | 6.1197 | 6.1197 | 6.1197 | 6.1197 | 6.1197 | 6.1197 | 6.1197 | 6.1197 | 6.1197 | 6.1197 | 6.1197 | 6.1197 | 6.1197
Weighted Energy @ Risk (MWh) under N-2 Conditions | 0.0012928 | 0.0017409 | 0.003241 | 0.0038767 | 0.0061414 | 0.0094548 | 0.014313 | 0.020943 | 0.030031 | 0.042391 | 0.056499 | 0.073844 | 0.098205 | 0.13078 | 0.16214 | 0.16214 | 0.16214 | 0.16214 | 0.16214 | 0.16214 | 0.16214 | 0.16214 | 0.16214 | 0.16214 | 0.16214 | 0.16214 | 0.16214 | 0.16214 | 0.16214 | 0.16214
Total EUE (MWh) - Option 5 | 0.034194 | 1.3534 | 3.0212 | 0.098418 | 0.13661 | 0.21661 | 0.47063 | 0.81534 | 1.5377 | 3.3854 | 2.9185 | 2.6705 | 4.1975 | 7.6761 | 6.2819 | 6.2819 | 6.2819 | 6.2819 | 6.2819 | 6.2819 | 6.2819 | 6.2819 | 6.2819 | 6.2819 | 6.2819 | 6.2819 | 6.2819 | 6.2819 | 6.2819 | 6.2819
Cost of EUE ($) - Option 5 | 1320.0832 | 52250.2261 | 116638.2684 | 3799.5266 | 5273.9129 | 8362.3501 | 18169.2034 | 31476.9528 | 59364.2087 | 130695.4072 | 112673.1267 | 103096.1951 | 162051.2298 | 296345.5513 | 242518.9268 | 242518.9268 | 242518.9268 | 242518.9268 | 242518.9268 | 242518.9268 | 242518.9268 | 242518.9268 | 242518.9268 | 242518.9268 | 242518.9268 | 242518.9268 | 242518.9268 | 242518.9268 | 242518.9268 | 242518.9268
Option 6 - | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Weighted Energy @ Risk (MWh) under N Conditions | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.047852 | 0.076147 | 0.70127 | 0.1746 | 0.1746 | 0.1746 | 0.1746 | 0.1746 | 0.1746 | 0.1746 | 0.1746 | 0.1746 | 0.1746 | 0.1746 | 0.1746 | 0.1746 | 0.1746 | 0.1746 | 0.1746
Weighted Energy @ Risk (MWh) under N-1 Conditions | 0.032901 | 1.3517 | 3.018 | 4.0487 | 5.2651 | 7.0314 | 10.0174 | 13.4078 | 18.1148 | 25.1158 | 27.4427 | 29.628 | 37.5617 | 50.3309 | 50.8438 | 50.8438 | 50.8438 | 50.8438 | 50.8438 | 50.8438 | 50.8438 | 50.8438 | 50.8438 | 50.8438 | 50.8438 | 50.8438 | 50.8438 | 50.8438 | 50.8438 | 50.8438
Weighted Energy @ Risk (MWh) under N-2 Conditions | 0.0012928 | 0.0017409 | 0.003241 | 0.0053666 | 0.0084883 | 0.013014 | 0.019541 | 0.028413 | 0.040455 | 0.056638 | 0.075614 | 0.099076 | 0.13103 | 0.17292 | 0.21559 | 0.21559 | 0.21559 | 0.21559 | 0.21559 | 0.21559 | 0.21559 | 0.21559 | 0.21559 | 0.21559 | 0.21559 | 0.21559 | 0.21559 | 0.21559 | 0.21559 | 0.21559
Total EUE (MWh) - Option 6 | 0.034194 | 1.3534 | 3.0212 | 4.0541 | 5.2736 | 7.0444 | 10.0369 | 13.4362 | 18.1553 | 25.1725 | 27.5183 | 29.7749 | 37.7689 | 51.2051 | 51.234 | 51.234 | 51.234 | 51.234 | 51.234 | 51.234 | 51.234 | 51.234 | 51.234 | 51.234 | 51.234 | 51.234 | 51.234 | 51.234 | 51.234 | 51.234
Cost of EUE ($) - Option 6 | 1320.0832 | 52250.2261 | 116638.2684 | 156512.078 | 203592.9757 | 271955.8559 | 387486.1996 | 518720.9803 | 700905.2416 | 971811.9987 | 1062374.4731 | 1149494.6633 | 1458110.3655 | 1976830.5821 | 1977946.3358 | 1977946.3358 | 1977946.3358 | 1977946.3358 | 1977946.3358 | 1977946.3358 | 1977946.3358 | 1977946.3358 | 1977946.3358 | 1977946.3358 | 1977946.3358 | 1977946.3358 | 1977946.3358 | 1977946.3358 | 1977946.3358 | 1977946.3358
Option 7 - | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Weighted Energy @ Risk (MWh) under N Conditions | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.047852 | 0.076147 | 0.70127 | 0.1746 | 0.1746 | 0.1746 | 0.1746 | 0.1746 | 0.1746 | 0.1746 | 0.1746 | 0.1746 | 0.1746 | 0.1746 | 0.1746 | 0.1746 | 0.1746 | 0.1746 | 0.1746
Weighted Energy @ Risk (MWh) under N-1 Conditions | 0.032901 | 1.3517 | 3.018 | 4.0487 | 5.2651 | 7.0314 | 10.0174 | 13.4078 | 18.1148 | 25.1158 | 27.4427 | 29.628 | 37.5617 | 50.3309 | 50.8438 | 50.8438 | 50.8438 | 50.8438 | 50.8438 | 50.8438 | 50.8438 | 50.8438 | 50.8438 | 50.8438 | 50.8438 | 50.8438 | 50.8438 | 50.8438 | 50.8438 | 50.8438
Weighted Energy @ Risk (MWh) under N-2 Conditions | 0.0012928 | 0.0017409 | 0.003241 | 0.0053666 | 0.0084883 | 0.013014 | 0.019541 | 0.028413 | 0.040455 | 0.056638 | 0.075614 | 0.099076 | 0.13103 | 0.17292 | 0.21559 | 0.21559 | 0.21559 | 0.21559 | 0.21559 | 0.21559 | 0.21559 | 0.21559 | 0.21559 | 0.21559 | 0.21559 | 0.21559 | 0.21559 | 0.21559 | 0.21559 | 0.21559
Total EUE (MWh) - Option 7 | 0.034194 | 1.3534 | 3.0212 | 4.0541 | 5.2736 | 7.0444 | 10.0369 | 13.4362 | 18.1553 | 25.1725 | 27.5183 | 29.7749 | 37.7689 | 51.2051 | 51.234 | 51.234 | 51.234 | 51.234 | 51.234 | 51.234 | 51.234 | 51.234 | 51.234 | 51.234 | 51.234 | 51.234 | 51.234 | 51.234 | 51.234 | 51.234
Cost of EUE ($) - Option 7 | 1320.0832 | 52250.2261 | 116638.2684 | 156512.078 | 203592.9757 | 271955.8559 | 387486.1996 | 518720.9803 | 700905.2416 | 971811.9987 | 1062374.4731 | 1149494.6633 | 1458110.3655 | 1976830.5821 | 1977946.3358 | 1977946.3358 | 1977946.3358 | 1977946.3358 | 1977946.3358 | 1977946.3358 | 1977946.3358 | 1977946.3358 | 1977946.3358 | 1977946.3358 | 1977946.3358 | 1977946.3358 | 1977946.3358 | 1977946.3358 | 1977946.3358 | 1977946.3358
Option 8 - | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Weighted Energy @ Risk (MWh) under N Conditions | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.047852 | 0.076147 | 0.70127 | 0.1746 | 0.1746 | 0.1746 | 0.1746 | 0.1746 | 0.1746 | 0.1746 | 0.1746 | 0.1746 | 0.1746 | 0.1746 | 0.1746 | 0.1746 | 0.1746 | 0.1746 | 0.1746
Weighted Energy @ Risk (MWh) under N-1 Conditions | 0.032901 | 1.3517 | 3.018 | 4.0487 | 5.2651 | 7.0314 | 10.0174 | 13.4078 | 18.1148 | 25.1158 | 27.4427 | 29.628 | 37.5617 | 50.3309 | 50.8438 | 50.8438 | 50.8438 | 50.8438 | 50.8438 | 50.8438 | 50.8438 | 50.8438 | 50.8438 | 50.8438 | 50.8438 | 50.8438 | 50.8438 | 50.8438 | 50.8438 | 50.8438
Weighted Energy @ Risk (MWh) under N-2 Conditions | 0.0012928 | 0.0017409 | 0.003241 | 0.0053666 | 0.0084883 | 0.013014 | 0.019541 | 0.028413 | 0.040455 | 0.056638 | 0.075614 | 0.099076 | 0.13103 | 0.17292 | 0.21559 | 0.21559 | 0.21559 | 0.21559 | 0.21559 | 0.21559 | 0.21559 | 0.21559 | 0.21559 | 0.21559 | 0.21559 | 0.21559 | 0.21559 | 0.21559 | 0.21559 | 0.21559
Total EUE (MWh) - Option 8 | 0.034194 | 1.3534 | 3.0212 | 4.0541 | 5.2736 | 7.0444 | 10.0369 | 13.4362 | 18.1553 | 25.1725 | 27.5183 | 29.7749 | 37.7689 | 51.2051 | 51.234 | 51.234 | 51.234 | 51.234 | 51.234 | 51.234 | 51.234 | 51.234 | 51.234 | 51.234 | 51.234 | 51.234 | 51.234 | 51.234 | 51.234 | 51.234
Cost of EUE ($) - Option 8 | 1320.0832 | 52250.2261 | 116638.2684 | 156512.078 | 203592.9757 | 271955.8559 | 387486.1996 | 518720.9803 | 700905.2416 | 971811.9987 | 1062374.4731 | 1149494.6633 | 1458110.3655 | 1976830.5821 | 1977946.3358 | 1977946.3358 | 1977946.3358 | 1977946.3358 | 1977946.3358 | 1977946.3358 | 1977946.3358 | 1977946.3358 | 1977946.3358 | 1977946.3358 | 1977946.3358 | 1977946.3358 | 1977946.3358 | 1977946.3358 | 1977946.3358 | 1977946.3358