## Info
Document description
This model Energy at Risk model has been developed to calculated Energy at Risk (EaR) in terms of Expected Unsureved Energy (EUE) and the cost of EUE. The modelling inputs, calculation steps and outputs are described in the 'Modelling Steps' tab. Further detail on EaR/EUE calculations can be found in AusNet's Network Planning Policy and Guidelines.
Tab # | Tab Name | Description | Source/ Inputs
0.1 | Modelling Steps | E@R model process flowchart and underlying equations | N/A
0.2 | Modelling Example & QA | Example E@R model calculations and data flow; also used to validate base case | N/A
0.3 | QA | Quality assurance and data validation | Entire workbook
1.1 | Output for AusNet's NPV Model | Aggregates Supply Risk ($M) and EUE (MWh) for input into AusNet’s NPV model | Summary tab
2.1 | Key Model Assumptions & Inputs | E@R model inputs and asset selection | Augmentation plans from RPs/EPCs, Embedded Generation DB, Demand Management DB
2.2 | Tx PoF | Transformer Probabilities of Failure | Provided by Asset Management Team
2.3 | Customer No. and Volume per Feeder | Customer consumption data | Provided by Finance Team
2.4 | AER VCR Rates (2024) | AER 2024 VCR rates | AER VCR Factsheet
2.5 | Forecast - Summer | Summer Forecast Data | Extract from Forecasting Toolbox
2.6 | Forecast- Winter | Winter Forecast Data | Extract from Forecasting Toolbox
2.7 | Ratings | Station Rating Data | AMS 20-101 / Provided by Asset mangement Team
2.8 | FT (Forecast & Transfers) | Forecast, transfer & PF inputs | Forecast Summer , Forecast Winter , NP Transfer Sheet, PF = avg. max demand PF across stations
2.9 | Load Duration Curves | Load duration curve data | LDC Tool; data sourced from PI SCADA Historian and AEMO
3.1 | Capacity N | Option N capacity calculated | FT Sheet, Ratings & Key Model Assumptions
3.2 | Capacity N-1 | Option N-1 capacity calculated | FT Sheet, Ratings & Key Model Assumptions
3.3 | Capacity N-1 | Option N-2 capacity calculated | FT Sheet, Ratings & Key Model Assumptions
3.4 | Demand | Calculates maximum demand | FT Sheet & Key Model Assumptions
3.5 | MD Weighted LDC | Maps maximum demand forecast to load duration curve | Demand Sheet & Load Duration Curve Sheet
3.6 | Locational VCR | Calculates tailored VCR by location using feeder energy mix and AER rates | AER VCR Rates (2024) & Customer No./Volume per Feeder
3.7 | E@R N | Calculates N EUE using capacity and demand inputs | MD Weighted LDC & Capacity N
3.8 | E@R N-1 | Calculates N-1 EUE using capacity and demand inputs | MD Weighted LDC & Capacity N-1
3.9 | E@R N-2 | Calculates N-2 EUE using capacity and demand inputs | MD Weighted LDC & Capacity N-2
4 | POF N,N-1 & N-2 Risk | Calculates Station N , N-1 & N-2 PoF's from Tx PoF Data & MTTR | TX PoF & Key Model Assumptions
4.1 | Summary | Collates weighted EUE and calculates supply risk | E@R & Locational VCR
Revision table
Date | Editted by | Change
2025-10-14 | HT | Draft Version 2.1
2025-10-20 | HT | Version 2.2
2025-11-10 | HT | Version 2.3 Example Page Update and General Refinements

## Modelling Steps
Eq1. Locational VCR |  | Data Inputs |  |  | Calculations |  |  |  |  | Outputs
|  |  | Customer No. and Vol per Feeder |  | Eq1.
Locational VCR
Eq2. Maximum Demand
AER Latetst VCR Rates
Eq3. Options & Do nothing Capacity
Eq6. & Eq7.
Load Forecast
[9 empty] | Summary Sheet | Output for AusNet's NPV Model
Eq4. Help Sheet | Re Name Forecasted LDC add Forecast MD to eq
Transfer Capacity
Eq2.
Eq5. Energy at Risk ( Option/ Do Nothing Capacity) |  |  |  |  | Options & Do Nothing Max Demand
Embeded Generation
Eq6. Weighted Expected Unserved Energy
[6 empty] | Eq.4 | Eq.5
Demand Mangement Capacity
[6 empty] | Forecasted LDC |  | Energy @ Risk Sheet
Eq7. Supply Risk
Load Duration Curves
|  |  | Asset Ratings |  | Eq3.
Options & Do Nothing Capacity
Planned & Proposed Works

## Modelling Steps Example & QA
End of Sheet
Data Inputs |  |  | Calculations | [12 empty] | Outputs
AER VCR Rates(2024 |  |  | Locational (Tailored VCR)
Category | Rate |  | Base case |  | Energy Usage (CY 2024 kWh) | Energy Usage (CY 2024 %) | Tailored VCR
Dec 24 AER VCR ($/kWh) - Res | 49.23 |  | Dec 24 AER VCR ($/kWh) - Res | 49.23 | 67934749.1441 | 34.06% | 16.7657
Dec 24 AER VCR ($/kWh) - Com | 34.39 |  | Dec 24 AER VCR ($/kWh) - Com | 34.39 | 101368150.4504 | 50.82% | 17.4756
Dec 24 AER VCR ($/kWh) - Ind | 33.49 |  | Dec 24 AER VCR ($/kWh) - Ind | 33.49 | 17726336.2671 | 8.886% | 2.976
Dec 24 AER VCR ($/kWh) - Agr | 22.25 |  | Dec 24 AER VCR ($/kWh) - Agr | 22.25 | 12451243.5083 | 6.242% | 1.3888
[5 empty] | 199480479.3698 |  | 38.6062
Customer No. and Vol per Feeder | [6 empty] | 38606.1513 | [8 empty] | Summary |  | Outputs for NPV model
COMMERCIAL | 101368150.4504 | [14 empty] | Year | 2031 | Year | 2031
[16 empty] | E@R MWh | 7.6375 | E@R MWh | 7.6375
RESIDENTL | 67934749.1441 | [14 empty] | cost of EUE ($) | 294855.058 | cost of EUE ($M) | 0.29486
FARM | 12451243.5083
INDUSTRIAL | 17726336.2671
Forecast (FCT)
Forecast | 2031
Summer POE50 | 75.0153
Summer POE10 | 81.1895
Winter POE50 | 73.2946
Winter POE10 | 76.2493
Transfer Capacity |  |  | Option Max Demand |  |  |  | MD Weighted LDC |  |  | E@R (N) |  | E@R (N-1) |  | E@R (N-2)
Year | 2031 |  | Forecast | 2031 |  |  | % of MD | Summer - AD - Hours | FY31 | % of MD | FY31 | % of MD | FY31 | % of MD | FY31
Capacity | 1.58 |  | Summer POE50 | 73.4353 |  |  | 100% | 0 | 73.4353 | 100% |  | 100% |  | 100%
|  |  | Summer POE10 | 79.6095 |  |  | 99% | 0 | 72.701 | 99% |  | 99% | 0 | 99% | 0
Embedded Generation |  |  | Winter POE50 | 71.7146 |  |  | 98% | 0 | 71.9666 | 98% |  | 98% | 0 | 98% | 0
|  |  | Winter POE10 | 74.6693 |  |  | 97% | 0.37816 | 71.2323 | 97% |  | 97% | 10.059 | 97% | 27.0764
Year | 2031 | [5 empty] | 95% | 2.269 | 69.7636 | 95% |  | 95% | 48.212 | 95% | 133.299
Capacity | 0 | [5 empty] | 90% | 5.6725 | 66.0918 | 90% |  | 90% | 78.0339 | 90% | 231.1905
[7 empty] | 85% | 15.8829 | 62.42 | 85% |  | 85% | 196.6114 | 85% | 656.081
Demand Mangement | [6 empty] | 80% | 31.0095 | 58.7483 | 80% |  | 80% | 235.7349 | 80% | 916.4306
[7 empty] | 75% | 72.9857 | 55.0765 | 75% |  | 75% | 500.0374 | 75% | 2388.968
Year | 2031 | [5 empty] | 70% | 150.5094 | 51.4047 | 70% |  | 70% | 638.8436 | 70% | 4127.4091
Capacity | 0 | [5 empty] | 65% | 359.6342 | 47.733 | 65% |  | 65% | 955.4618 | 65% | 10366.0801
[7 empty] | 60% | 689.7717 | 44.0612 | 60% |  | 60% | 335.7847 | 60% | 15152.3473
LDC | [6 empty] | 55% | 1095.5419 | 40.3894 | 55% |  | 55% |  | 55% | 17133.7814
[7 empty] | 50% | 1666.1918 | 36.7177 | 50% |  | 50% |  | 50% | 22000.5834
% of MD | Summer - AD - Duration % | Summer - AD - Hours |  |  |  |  | 45% | 2506.0947 | 33.0459 | 45% |  | 45% |  | 45% | 29297.3152
100% | 0% | 0 |  |  |  |  | 40% | 3164.4787 | 29.3741 | 40% |  | 40% |  | 40% | 20548.1797
99% | 0% | 0 |  |  |  |  | 35% | 3551.3408 | 25.7024 | 35% |  | 35% |  | 35% | 10653.506
98% | 0% | 0 |  |  |  |  | 30% | 3758.953 | 22.0306 | 30% |  | 30% |  | 30% | 4954.9738
97% | 0.00861% | 0.37816 |  |  |  |  | 25% | 3926.4798 | 18.3588 | 25% |  | 25% |  | 25% | 3383.1564
95% | 0.05166% | 2.269 |  |  |  |  | 20% | 4050.5177 | 14.6871 | 20% |  | 20% |  | 20% | 2049.4721
90% | 0.1292% | 5.6725 |  |  |  |  | 15% | 4152.622 | 11.0153 | 15% |  | 15% |  | 15% | 1312.162
85% | 0.3616% | 15.8829 |  |  |  |  | 10% | 4248.2976 | 7.3435 | 10% |  | 10% |  | 10% | 878.246
80% | 0.706% | 31.0095 |  |  |  |  | 5% | 4361.7469 | 3.6718 | 5% |  | 5% |  | 5% | 624.8391
75% | 1.662% | 72.9857 |  |  |  |  | 9.992e-14% | 4391.6218 | 7.3377e-14 | 9.992e-14% |  | 9.992e-14% |  | 9.992e-14% | 54.847
70% | 3.427% | 150.5094 | [7 empty] | Total E@R | 0 | Total E@R | 2998.7788 | Total E@R | 146889.9441
65% | 8.188% | 359.6342 | [7 empty] | Total WE@R | 0 | Total WE@R | 1.3921 | Total WE@R | 0.013387
60% | 15.71% | 689.7717 |  |  |  |  | MD Weighted LDC
55% | 24.94% | 1095.5419
50% | 37.94% | 1666.1918 |  |  |  |  | % of MD | Summer - MD - Hours | FY31
45% | 57.06% | 2506.0947 |  |  |  |  | 100% | 0 | 79.6095 | E@R (N) |  | E@R (N-1) |  | E@R (N-2)
40% | 72.05% | 3164.4787 |  |  |  |  | 99% | 1.5127 | 78.8134
35% | 80.86% | 3551.3408 |  |  |  |  | 98% | 2.269 | 78.0173 | % of MD | FY31 | % of MD | FY31 | % of MD | FY31
30% | 85.59% | 3758.953 |  |  |  |  | 97% | 3.7816 | 77.2212 | 100% |  | 100% |  | 100%
25% | 89.4% | 3926.4798 |  |  |  |  | 95% | 6.0506 | 75.629 | 99% |  | 99% | 51.7502 | 99% | 119.8198
20% | 92.22% | 4050.5177 |  |  |  |  | 90% | 16.2611 | 71.6485 | 98% |  | 98% | 25.273 | 98% | 59.3078
15% | 94.55% | 4152.622 |  |  |  |  | 85% | 26.4715 | 67.6681 | 97% |  | 97% | 49.3417 | 97% | 117.4113
10% | 96.73% | 4248.2976 |  |  |  |  | 80% | 34.0348 | 63.6876 | 95% |  | 95% | 71.3031 | 95% | 173.4075
5% | 99.31% | 4361.7469 |  |  |  |  | 75% | 48.405 | 59.7071 | 90% |  | 90% | 292.4144 | 90% | 751.884
9.992e-14% | 99.99% | 4391.6218 |  |  |  |  | 70% | 76.3892 | 55.7266 | 85% |  | 85% | 251.772 | 85% | 711.2416
[7 empty] | 65% | 114.2056 | 51.7462 | 80% |  | 80% | 156.3923 | 80% | 496.7402
[7 empty] | 60% | 178.1154 | 47.7657 | 75% |  | 75% | 239.945 | 75% | 886.6059
[7 empty] | 55% | 311.6074 | 43.7852 | 70% |  | 70% | 355.8711 | 70% | 1615.1582
LDC | [6 empty] | 50% | 636.0723 | 39.8047 | 65% |  | 65% | 330.3796 | 65% | 2032.1189
[7 empty] | 45% | 1179.4944 | 35.8243 | 60% |  | 60% | 303.9503 | 60% | 3179.8897
% of MD | Summer - MD - Duration % | Summer - MD - Hours |  |  |  |  | 40% | 1808.3816 | 31.8438 | 55% |  | 55% | 128.262 | 55% | 6110.6567
100% | 0% | 0 |  |  |  |  | 35% | 2779.1293 | 27.8633 | 50% |  | 50% |  | 50% | 13561.0066
99% | 0.03444% | 1.5127 |  |  |  |  | 30% | 3814.165 | 23.8828 | 45% |  | 45% |  | 45% | 20549.2377
98% | 0.05166% | 2.269 |  |  |  |  | 25% | 4166.9923 | 19.9024 | 40% |  | 40% |  | 40% | 21277.7899
97% | 0.0861% | 3.7816 |  |  |  |  | 20% | 4282.7105 | 15.9219 | 35% |  | 35% |  | 35% | 28980.2731
95% | 0.1378% | 6.0506 |  |  |  |  | 15% | 4364.7722 | 11.9414 | 30% |  | 30% |  | 30% | 26779.5636
90% | 0.3702% | 16.2611 |  |  |  |  | 10% | 4391.6218 | 7.9609 | 25% |  | 25% |  | 25% | 7724.3096
85% | 0.6027% | 26.4715 |  |  |  |  | 5% | 4391.6218 | 3.9805 | 20% |  | 20% |  | 20% | 2072.7613
80% | 0.7749% | 34.0348 |  |  |  |  | 9.992e-14% | 4391.6218 | 7.9546e-14 | 15% |  | 15% |  | 15% | 1143.255
75% | 1.102% | 48.405 | [7 empty] | 10% |  | 10% |  | 10% | 267.186
70% | 1.739% | 76.3892 | [7 empty] | 5% |  | 5% |  | 5% | 0
65% | 2.6% | 114.2056 | [7 empty] | 9.992e-14% |  | 9.992e-14% |  | 9.992e-14% | 0
60% | 4.055% | 178.1154 | [7 empty] | Total E@R | 0 | Total E@R | 2256.6548 | Total E@R | 138609.6244
55% | 7.095% | 311.6074 |  |  |  |  | MD Weighted LDC |  |  | Total WE@R | 0 | Total WE@R | 0.44897 | Total WE@R | 0.0054138
50% | 14.48% | 636.0723
45% | 26.86% | 1179.4944 |  |  |  |  | % of MD | Winter - AD - Hours | FY31
40% | 41.17% | 1808.3816 |  |  |  |  | 100% | 0 | 71.7146
35% | 63.28% | 2779.1293 |  |  |  |  | 99% | 1.486 | 70.9975 | E@R (N) |  | E@R (N-1) |  | E@R (N-2)
30% | 86.84% | 3814.165 |  |  |  |  | 98% | 3.2692 | 70.2804
25% | 94.88% | 4166.9923 |  |  |  |  | 97% | 6.8356 | 69.5632 | % of MD | FY31 | % of MD | FY31 | % of MD | FY31
20% | 97.51% | 4282.7105 |  |  |  |  | 95% | 17.5347 | 68.1289 | 100% |  | 100% |  | 100%
15% | 99.38% | 4364.7722 |  |  |  |  | 90% | 78.7576 | 64.5432 | 99% |  | 99% | 33.0724 | 99% | 106.0346
10% | 99.99% | 4391.6218 |  |  |  |  | 85% | 236.8672 | 60.9575 | 98% |  | 98% | 38.408 | 98% | 125.9627
5% | 99.99% | 4391.6218 |  |  |  |  | 80% | 497.5104 | 57.3717 | 97% |  | 97% | 74.2584 | 97% | 249.3678
9.992e-14% | 99.99% | 4391.6218 |  |  |  |  | 75% | 803.6248 | 53.786 | 95% |  | 95% | 211.266 | 95% | 736.5942
[7 empty] | 70% | 1155.2107 | 50.2003 | 90% |  | 90% | 1055.2409 | 90% | 4061.2852
[7 empty] | 65% | 1553.1596 | 46.6145 | 85% |  | 85% | 2158.2465 | 85% | 9921.4289
[7 empty] | 60% | 2026.2996 | 43.0288 | 80% |  | 80% | 2623.2647 | 80% | 15420.8418
LDC | [6 empty] | 55% | 2598.4068 | 39.4431 | 75% |  | 75% | 1983.2706 | 75% | 17013.4923
[7 empty] | 50% | 3233.5201 | 35.8573 | 70% |  | 70% | 1017.18 | 70% | 18280.0463
% of MD | Winter - AD (P50) - Duration % | Winter - AD - Hours |  |  |  |  | 45% | 3775.313 | 32.2716 | 65% |  | 65% | 67.1746 | 65% | 19263.6638
100% | 0% | 0 |  |  |  |  | 40% | 4072.8088 | 28.6859 | 60% |  | 60% |  | 60% | 21206.9211
99% | 0.03383% | 1.486 |  |  |  |  | 35% | 4198.821 | 25.1001 | 55% |  | 55% |  | 55% | 23591.3677
98% | 0.07443% | 3.2692 |  |  |  |  | 30% | 4271.3374 | 21.5144 | 50% |  | 50% |  | 50% | 23912.1357
97% | 0.1556% | 6.8356 |  |  |  |  | 25% | 4321.8611 | 17.9287 | 45% |  | 45% |  | 45% | 18455.8826
95% | 0.3992% | 17.5347 |  |  |  |  | 20% | 4353.067 | 14.3429 | 40% |  | 40% |  | 40% | 9067.2909
90% | 1.793% | 78.7576 |  |  |  |  | 15% | 4369.4129 | 10.7572 | 35% |  | 35% |  | 35% | 3388.8447
85% | 5.393% | 236.8672 |  |  |  |  | 10% | 4378.6261 | 7.1715 | 30% |  | 30% |  | 30% | 1690.1596
80% | 11.33% | 497.5104 |  |  |  |  | 5% | 4391.7028 | 3.5857 | 25% |  | 25% |  | 25% | 996.4056
75% | 18.3% | 803.6248 |  |  |  |  | 9.992e-14% | 4391.7028 | 7.1657e-14 | 20% |  | 20% |  | 20% | 503.5312
70% | 26.3% | 1155.2107 | [7 empty] | 15% |  | 15% |  | 15% | 205.1423
65% | 35.36% | 1553.1596 | [7 empty] | 10% |  | 10% |  | 10% | 82.5898
60% | 46.14% | 2026.2996 | [7 empty] | 5% |  | 5% |  | 5% | 70.3345
55% | 59.16% | 2598.4068 | [7 empty] | 9.992e-14% |  | 9.992e-14% |  | 9.992e-14% | 0
50% | 73.62% | 3233.5201 |  |  |  |  | MD Weighted LDC |  |  | Total E@R | 0 | Total E@R | 9261.3822 | Total E@R | 188349.3233
45% | 85.96% | 3775.313 | [7 empty] | Total WE@R | 0 | Total WE@R | 3.6529 | Total WE@R | 0.014584
40% | 92.73% | 4072.8088 |  |  |  |  | % of MD | Winter - MD - Hours | FY31
35% | 95.6% | 4198.821 |  |  |  |  | 100% | 0 | 74.6693 | E@R (N) |  | E@R (N) |  | E@R (N)
30% | 97.25% | 4271.3374 |  |  |  |  | 99% | 1.486 | 73.9226
25% | 98.4% | 4321.8611 |  |  |  |  | 98% | 3.2692 | 73.1759 | % of MD | FY31 | % of MD | FY31 | % of MD | FY31
20% | 99.11% | 4353.067 |  |  |  |  | 97% | 6.8356 | 72.4292 | 100% |  | 100% |  | 100%
15% | 99.49% | 4369.4129 |  |  |  |  | 95% | 17.5347 | 70.9358 | 99% |  | 99% | 37.4409 | 99% | 110.4032
10% | 99.7% | 4378.6261 |  |  |  |  | 90% | 78.7576 | 67.2023 | 98% |  | 98% | 43.5976 | 98% | 131.1523
5% | 99.99% | 4391.7028 |  |  |  |  | 85% | 236.8672 | 63.4689 | 97% |  | 97% | 84.5323 | 97% | 259.6417
9.992e-14% | 99.99% | 4391.7028 |  |  |  |  | 80% | 497.5104 | 59.7354 | 95% |  | 95% | 241.6134 | 95% | 766.9415
[7 empty] | 75% | 803.6248 | 56.0019 | 90% |  | 90% | 1222.564 | 90% | 4228.6083
[7 empty] | 70% | 1155.2107 | 52.2685 | 85% |  | 85% | 2567.0047 | 85% | 10330.1872
[7 empty] | 65% | 1553.1596 | 48.535 | 80% |  | 80% | 3258.5963 | 80% | 16056.1734
LDC | [6 empty] | 60% | 2026.2996 | 44.8016 | 75% |  | 75% | 2684.2186 | 75% | 17714.4402
[7 empty] | 55% | 2598.4068 | 41.0681 | 70% |  | 70% | 1770.3095 | 70% | 19033.1757
% of MD | Winter - MD (P10) - Duration % | Winter - MD - Hours |  |  |  |  | 50% | 3233.5201 | 37.3346 | 65% |  | 65% | 535.0416 | 65% | 20057.3178
100% | 0% | 0 |  |  |  |  | 45% | 3775.313 | 33.6012 | 60% |  | 60% |  | 60% | 22080.6365
99% | 0.03383% | 1.486 |  |  |  |  | 40% | 4072.8088 | 29.8677 | 55% |  | 55% |  | 55% | 24563.3211
98% | 0.07443% | 3.2692 |  |  |  |  | 35% | 4198.821 | 26.1342 | 50% |  | 50% |  | 50% | 24897.3046
97% | 0.1556% | 6.8356 |  |  |  |  | 30% | 4271.3374 | 22.4008 | 45% |  | 45% |  | 45% | 19216.2564
95% | 0.3992% | 17.5347 |  |  |  |  | 25% | 4321.8611 | 18.6673 | 40% |  | 40% |  | 40% | 9440.8591
90% | 1.793% | 78.7576 |  |  |  |  | 20% | 4353.067 | 14.9339 | 35% |  | 35% |  | 35% | 3528.4635
85% | 5.393% | 236.8672 |  |  |  |  | 15% | 4369.4129 | 11.2004 | 30% |  | 30% |  | 30% | 1759.7934
80% | 11.33% | 497.5104 |  |  |  |  | 10% | 4378.6261 | 7.4669 | 25% |  | 25% |  | 25% | 1037.457
75% | 18.3% | 803.6248 |  |  |  |  | 5% | 4391.7028 | 3.7335 | 20% |  | 20% |  | 20% | 524.2764
70% | 26.3% | 1155.2107 |  |  |  |  | 9.992e-14% | 4391.7028 | 7.461e-14 | 15% |  | 15% |  | 15% | 213.5941
65% | 35.36% | 1553.1596 | [7 empty] | 10% |  | 10% |  | 10% | 85.9924
60% | 46.14% | 2026.2996 | [7 empty] | 5% |  | 5% |  | 5% | 73.2323
55% | 59.16% | 2598.4068 | [7 empty] | 9.992e-14% |  | 9.992e-14% | 0 | 9.992e-14% | 0
50% | 73.62% | 3233.5201 | [7 empty] | Total E@R | 0 | Total E@R | 12444.9189 | Total E@R | 196109.2281
45% | 85.96% | 3775.313 | [7 empty] | Total WE@R | 0 | Total WE@R | 2.1037 | Total WE@R | 0.0065078
40% | 92.73% | 4072.8088
35% | 95.6% | 4198.821
30% | 97.25% | 4271.3374
25% | 98.4% | 4321.8611
20% | 99.11% | 4353.067
15% | 99.49% | 4369.4129
10% | 99.7% | 4378.6261
5% | 99.99% | 4391.7028
9.992e-14% | 99.99% | 4391.7028
Ratings (MVA) |  |  |  | Option Capacity
SCR (N) | 91.9 |  |  | Year | 2031
SCR (N-1) | 45 |  |  | SCR (N) | 91.9
SCR (N-2) | 0 |  |  | SCR (N-1) | 45
WCR (N) | 95.7 |  |  | SCR (N-2) | 0
WCR (N-1) | 49.1 |  |  | WCR (N) | 95.7
WCR (N-2) | 0 |  |  | WCR (N-1) | 49.1
|  |  |  | WCR (N-2) | 0
Planned Works
Year | 2031
Capacity (N) | 0
Capacity (N-1) | 0
Capacity (N-2) | 0
Power Factor
Value | 1
End of Sheet

## QA
Overall Status
Good
Number | Check Name | Status | Info
1 | Forecast | Good | Confirms POE10 forecast is higher than POE50
2 | Option Maximum Demand | Good | Confirms whether transfers, embedded generation, and demand management contribute to demand reduction when present
3 | EUE Base Case | Good | Confirms Do Nothing/Base Case EUE for FY31 is the same as the example / checks model in Modelling Steps Example Sheet
4 | Feeder Consumption | Good | Confirms if aggregated feeder energy consumption by customer category matches with total feeder energy consumption (excluding uncategorised consumption)

## Output for AusNet's NPV model
Involuntary load shedding (NER 5.17.1(c)(4)(ii))
Base Case
Cost
Option 1 - Do Nothing / Base Case | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Cost of EUE ($M) | 0.00072127 | 0.02973 | 0.079301 | 0.10845 | 0.14312 | 0.19644 | 0.29486 | 0.40694 | 0.57048 | 0.83062 | 0.8878 | 0.9404 | 1.2248 | 1.7072 | 1.682 | 1.682 | 1.682 | 1.682 | 1.682 | 1.682 | 1.682 | 1.682 | 1.682 | 1.682 | 1.682 | 1.682 | 1.682 | 1.682 | 1.682 | 1.682
Total EUE (MWh) | 0.018683 | 0.77009 | 2.0541 | 2.809 | 3.7072 | 5.0883 | 7.6375 | 10.5408 | 14.7769 | 21.5152 | 22.9963 | 24.3587 | 31.7253 | 44.2218 | 43.5677 | 43.5677 | 43.5677 | 43.5677 | 43.5677 | 43.5677 | 43.5677 | 43.5677 | 43.5677 | 43.5677 | 43.5677 | 43.5677 | 43.5677 | 43.5677 | 43.5677 | 43.5677
Residual Values
Option 2 - 1B New PHS ZSS + Three new feeders | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Cost of Avoided EUE ($M) | 0.00072127 | 0.02973 | 0.079301 | 0.0018452 | 0.0024559 | 0.0035995 | 0.0067205 | 0.011957 | 0.024702 | 0.076841 | 0.052735 | 0.046518 | 0.079577 | 0.17396 | 0.12751 | 0.12751 | 0.12751 | 0.12751 | 0.12751 | 0.12751 | 0.12751 | 0.12751 | 0.12751 | 0.12751 | 0.12751 | 0.12751 | 0.12751 | 0.12751 | 0.12751 | 0.12751
Total EUE (MWh) | 0.018683 | 0.77009 | 2.0541 | 0.047795 | 0.063615 | 0.093237 | 0.17408 | 0.30972 | 0.63984 | 1.9904 | 1.366 | 1.2049 | 2.0613 | 4.5059 | 3.3028 | 3.3028 | 3.3028 | 3.3028 | 3.3028 | 3.3028 | 3.3028 | 3.3028 | 3.3028 | 3.3028 | 3.3028 | 3.3028 | 3.3028 | 3.3028 | 3.3028 | 3.3028
Option 3 - 2B PHM 3rd Tx + Switchroom + Two new feeders + OFR12 New Feeder | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Cost of Avoided EUE ($M) | 0.00072127 | 0.02973 | 0.079301 | 1.7678e-05 | 2.9089e-05 | 4.8299e-05 | 8.5258e-05 | 0.00013745 | 0.00022241 | 0.0003681 | 0.00045944 | 0.00056132 | 0.00082073 | 0.0012673 | 0.0014213 | 0.0014213 | 0.0014213 | 0.0014213 | 0.0014213 | 0.0014213 | 0.0014213 | 0.0014213 | 0.0014213 | 0.0014213 | 0.0014213 | 0.0014213 | 0.0014213 | 0.0014213 | 0.0014213 | 0.0014213
Total EUE (MWh) | 0.018683 | 0.77009 | 2.0541 | 0.0004579 | 0.00075348 | 0.0012511 | 0.0022084 | 0.0035602 | 0.005761 | 0.0095348 | 0.011901 | 0.01454 | 0.021259 | 0.032825 | 0.036817 | 0.036817 | 0.036817 | 0.036817 | 0.036817 | 0.036817 | 0.036817 | 0.036817 | 0.036817 | 0.036817 | 0.036817 | 0.036817 | 0.036817 | 0.036817 | 0.036817 | 0.036817
Option 4 - 3B OFR 3rd Tx + Switchroom + Two new feeders + OFR12 New Feeder | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Cost of Avoided EUE ($M) | 0.00072127 | 0.02973 | 0.079301 | 0.060605 | 0.081282 | 0.11502 | 0.18333 | 0.26171 | 0.38244 | 0.58815 | 0.61312 | 0.63573 | 0.85208 | 1.2377 | 1.1864 | 1.1864 | 1.1864 | 1.1864 | 1.1864 | 1.1864 | 1.1864 | 1.1864 | 1.1864 | 1.1864 | 1.1864 | 1.1864 | 1.1864 | 1.1864 | 1.1864 | 1.1864
Total EUE (MWh) | 0.018683 | 0.77009 | 2.0541 | 1.5698 | 2.1054 | 2.9792 | 4.7488 | 6.7791 | 9.9062 | 15.2345 | 15.8814 | 16.467 | 22.0712 | 32.0594 | 30.7308 | 30.7308 | 30.7308 | 30.7308 | 30.7308 | 30.7308 | 30.7308 | 30.7308 | 30.7308 | 30.7308 | 30.7308 | 30.7308 | 30.7308 | 30.7308 | 30.7308 | 30.7308
Option 5 - 4B LLG 2nd Tx + Switchroom + Two new feeders + OFR12 New Feeder | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Cost of Avoided EUE ($M) | 0.00072127 | 0.02973 | 0.079301 | 0.0011918 | 0.0015962 | 0.0022783 | 0.003732 | 0.0061348 | 0.012445 | 0.048322 | 0.027519 | 0.025264 | 0.043132 | 0.10373 | 0.072008 | 0.072008 | 0.072008 | 0.072008 | 0.072008 | 0.072008 | 0.072008 | 0.072008 | 0.072008 | 0.072008 | 0.072008 | 0.072008 | 0.072008 | 0.072008 | 0.072008 | 0.072008
Total EUE (MWh) | 0.018683 | 0.77009 | 2.0541 | 0.030871 | 0.041345 | 0.059013 | 0.096668 | 0.15891 | 0.32235 | 1.2517 | 0.71281 | 0.6544 | 1.1172 | 2.687 | 1.8652 | 1.8652 | 1.8652 | 1.8652 | 1.8652 | 1.8652 | 1.8652 | 1.8652 | 1.8652 | 1.8652 | 1.8652 | 1.8652 | 1.8652 | 1.8652 | 1.8652 | 1.8652
Option 6 - | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Cost of Avoided EUE ($M) | 0.00072127 | 0.02973 | 0.079301 | 0.10845 | 0.14312 | 0.19644 | 0.29486 | 0.40694 | 0.57048 | 0.83062 | 0.8878 | 0.9404 | 1.2248 | 1.7072 | 1.682 | 1.682 | 1.682 | 1.682 | 1.682 | 1.682 | 1.682 | 1.682 | 1.682 | 1.682 | 1.682 | 1.682 | 1.682 | 1.682 | 1.682 | 1.682
Total EUE (MWh) | 0.018683 | 0.77009 | 2.0541 | 2.809 | 3.7072 | 5.0883 | 7.6375 | 10.5408 | 14.7769 | 21.5152 | 22.9963 | 24.3587 | 31.7253 | 44.2218 | 43.5677 | 43.5677 | 43.5677 | 43.5677 | 43.5677 | 43.5677 | 43.5677 | 43.5677 | 43.5677 | 43.5677 | 43.5677 | 43.5677 | 43.5677 | 43.5677 | 43.5677 | 43.5677
Option 7 - | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Cost of Avoided EUE ($M) | 0.00072127 | 0.02973 | 0.079301 | 0.10845 | 0.14312 | 0.19644 | 0.29486 | 0.40694 | 0.57048 | 0.83062 | 0.8878 | 0.9404 | 1.2248 | 1.7072 | 1.682 | 1.682 | 1.682 | 1.682 | 1.682 | 1.682 | 1.682 | 1.682 | 1.682 | 1.682 | 1.682 | 1.682 | 1.682 | 1.682 | 1.682 | 1.682
Total EUE (MWh) | 0.018683 | 0.77009 | 2.0541 | 2.809 | 3.7072 | 5.0883 | 7.6375 | 10.5408 | 14.7769 | 21.5152 | 22.9963 | 24.3587 | 31.7253 | 44.2218 | 43.5677 | 43.5677 | 43.5677 | 43.5677 | 43.5677 | 43.5677 | 43.5677 | 43.5677 | 43.5677 | 43.5677 | 43.5677 | 43.5677 | 43.5677 | 43.5677 | 43.5677 | 43.5677
Option 8 - | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Cost of Avoided EUE ($M) | 0.00072127 | 0.02973 | 0.079301 | 0.10845 | 0.14312 | 0.19644 | 0.29486 | 0.40694 | 0.57048 | 0.83062 | 0.8878 | 0.9404 | 1.2248 | 1.7072 | 1.682 | 1.682 | 1.682 | 1.682 | 1.682 | 1.682 | 1.682 | 1.682 | 1.682 | 1.682 | 1.682 | 1.682 | 1.682 | 1.682 | 1.682 | 1.682
Total EUE (MWh) | 0.018683 | 0.77009 | 2.0541 | 2.809 | 3.7072 | 5.0883 | 7.6375 | 10.5408 | 14.7769 | 21.5152 | 22.9963 | 24.3587 | 31.7253 | 44.2218 | 43.5677 | 43.5677 | 43.5677 | 43.5677 | 43.5677 | 43.5677 | 43.5677 | 43.5677 | 43.5677 | 43.5677 | 43.5677 | 43.5677 | 43.5677 | 43.5677 | 43.5677 | 43.5677

## Key Model Assumption & Inputs
Select ZSS & Region | PHM | Central | MTTR
Probability Weighting for 10% POE MDs | 30% |  |  | Central | North | East | For Analysis
Probability Weighting for 50% POE MDs | 70% |  | N-1 MTTR (years) | 0.3858 | 0.1418 | 0.3858 | 0.3858
First year of analysis | FY25 |  | N-2 MTTR (years) | 0.2344 | 0.049 | 0.2344 | 0.2344
Select Sensitivity Variant | Forecast Sensitivity
Base | 100% |  | PV Factor's |  |  | PoF Sensitvity
Options | Name |  | Summer | 1.33 |  | Varaint
Option 1 - Do Nothing / Base Case | Do Nothing / Base Case |  | Winter | 1.13 |  | High | 150%
Option 2 - 1B New PHS ZSS + Three new feeders | 1B New PHS ZSS + Three new feeders
Option 3 - 2B PHM 3rd Tx + Switchroom + Two new feeders + OFR12 New Feeder | 2B PHM 3rd Tx + Switchroom + Two new feeders + OFR12 New Feeder |  | Demand Response
Option 4 - 3B OFR 3rd Tx + Switchroom + Two new feeders + OFR12 New Feeder | 3B OFR 3rd Tx + Switchroom + Two new feeders + OFR12 New Feeder |  | Average Rate % | 20%
Option 5 - 4B LLG 2nd Tx + Switchroom + Two new feeders + OFR12 New Feeder | 4B LLG 2nd Tx + Switchroom + Two new feeders + OFR12 New Feeder
Option 6 -
Option 7 -
Option 8 -
Added Capacity (MVA) | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39
Added Capacity (MVA) Option 1 N | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 1 N-1 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 1 N-2 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 2 N | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 2 N-1 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 2 N-2 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 3 N |  |  |  | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45
Added Capacity (MVA) Option 3 N-1 |  |  |  | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45
Added Capacity (MVA) Option 3 N-2 |  |  |  | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45
Added Capacity (MVA) Option 4 N | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 4 N-1 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 4 N-2 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 5 N | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 5 N-1 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 5 N-2 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 6 N | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 6 N-1 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 6 N-2 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 7 N | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 7 N-1 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 7 N-2 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 8 N | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 8 N-1 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 8 N-2 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Embedded Generation (MVA) | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39
Avaliable Embedded Generation (MVA) Option 1 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Embedded Generation (MVA) Option 2 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Embedded Generation (MVA) Option 3 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Embedded Generation (MVA) Option 4 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Embedded Generation (MVA) Option 5 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Embedded Generation (MVA) Option 6 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Embedded Generation (MVA) Option 7 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Embedded Generation (MVA) Option 8 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Demand Management (MVA) | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39
Avaliable Demand Management (MVA) Option 1 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Demand Management (MVA) Option 2 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Demand Management (MVA) Option 3 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Demand Management (MVA) Option 4 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Demand Management (MVA) Option 5 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Demand Management (MVA) Option 6 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Demand Management (MVA) Option 7 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Demand Management (MVA) Option 8 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Transfers (MVA) | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39
Planned Transfers (MVA) Option 1 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Transfers (MVA) Option 2 |  |  |  | 19.3333 | 19.3333 | 19.3333 | 19.3333 | 19.3333 | 19.3333 | 19.3333 | 19.3333 | 19.3333 | 19.3333 | 19.3333 | 19.3333
Added Transfers (MVA) Option 3 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Transfers (MVA) Option 4 |  |  |  | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
Added Transfers (MVA) Option 5 |  |  |  | 21.75 | 21.75 | 21.75 | 21.75 | 21.75 | 21.75 | 21.75 | 21.75 | 21.75 | 21.75 | 21.75 | 21.75
Added Transfers (MVA) Option 6 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Transfers (MVA) Option 7 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Transfers (MVA) Option 8 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Block Loads Not in Forecast (MVA) | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39
Block Loads (MVA) | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Base | FY25: 100%
High | FY25: 110%
Low | FY25: 90%

## Tx PoF
Transformer Failure Rates for individual Transformers
[5 empty] | 10 | 8 | 10 | 6 | 8 | 6 | 6 | 10 | 6
Zone | arm_asset_id | floc | user_status | Age | Major Winding insulation | Accelerated cellulose Aging | Winding insulating liquid | Hot metal fault covered by paper | Chemical contamination, degradation | Physical & chemical contamination, degradation | Physical contamination | Short Circuit Concern | OLTC | WMA Health Score | WMA CS | WMA effective age | WMA Beta | WMA Eta | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WGI | 30192717 | DS-WGI-TRNFMR-9000004493 |  | 59 | 5 | 3 | 1 | 5 | 2 | 1 | 5 | 5 | 5 | 351.4286 | 4 | 60 | 3.5 | 82 | 1.976% | 1.976% | 2.058% | 2.142% | 2.227% | 2.315% | 2.405% | 2.496% | 2.59% | 2.686% | 2.783% | 2.883% | 2.985% | 3.089% | 3.195% | 3.303% | 3.413% | 3.525% | 3.639% | 3.755% | 3.873% | 3.994% | 4.116% | 4.241% | 4.368% | 4.497% | 4.628% | 4.761% | 4.897% | 5.034%
WGI | 30111322 | DS-WGI-TRNFMR-9000003147 |  | 59 | 5 | 5 | 1 | 3 | 2 | 1 | 4 | 5 | 5 | 348.5714 | 3 | 44 | 3.5 | 82 | 0.9218% | 0.9218% | 0.9742% | 1.028% | 1.084% | 1.142% | 1.201% | 1.262% | 1.325% | 1.39% | 1.457% | 1.525% | 1.596% | 1.668% | 1.742% | 1.818% | 1.896% | 1.976% | 2.058% | 2.142% | 2.227% | 2.315% | 2.405% | 2.496% | 2.59% | 2.686% | 2.783% | 2.883% | 2.985% | 3.089%
EPG | 30026486 | DS-EPG-TRNFMR-9000010175 |  | 45 | 5 | 3 | 2 | 1 | 2 | 1 | 4 | 5 | 5 | 322.8571 | 3 | 44 | 3.5 | 84.05 | 0.8458% | 0.8458% | 0.8939% | 0.9436% | 0.9949% | 1.048% | 1.102% | 1.159% | 1.216% | 1.276% | 1.337% | 1.4% | 1.465% | 1.531% | 1.599% | 1.669% | 1.741% | 1.814% | 1.889% | 1.966% | 2.045% | 2.125% | 2.208% | 2.292% | 2.378% | 2.466% | 2.556% | 2.648% | 2.741% | 2.837%
EPG | 30058367 | DS-EPG-TRNFMR-9000010174 |  | 45 | 5 | 3 | 2 | 1 | 2 | 1 | 4 | 5 | 5 | 322.8571 | 3 | 44 | 3.5 | 84.05 | 0.8458% | 0.8458% | 0.8939% | 0.9436% | 0.9949% | 1.048% | 1.102% | 1.159% | 1.216% | 1.276% | 1.337% | 1.4% | 1.465% | 1.531% | 1.599% | 1.669% | 1.741% | 1.814% | 1.889% | 1.966% | 2.045% | 2.125% | 2.208% | 2.292% | 2.378% | 2.466% | 2.556% | 2.648% | 2.741% | 2.837%
WGI | 30475971 | DS-WGI-TRNFMR-9000007146 |  | 49 | 5 | 5 | 1 | 1 | 1 | 1 | 2 | 5 | 1 | 268.5714 | 3 | 44 | 3.5 | 82 | 0.9218% | 0.9218% | 0.9742% | 1.028% | 1.084% | 1.142% | 1.201% | 1.262% | 1.325% | 1.39% | 1.457% | 1.525% | 1.596% | 1.668% | 1.742% | 1.818% | 1.896% | 1.976% | 2.058% | 2.142% | 2.227% | 2.315% | 2.405% | 2.496% | 2.59% | 2.686% | 2.783% | 2.883% | 2.985% | 3.089%
EPG | 30209984 | DS-EPG-TRNFMR-9000007095 |  | 24 | 3 | 3 | 1 | 3 | 2 | 1 | 4 | 3 | 3 | 251.4286 | 3 | 44 | 3.5 | 84.05 | 0.8458% | 0.8458% | 0.8939% | 0.9436% | 0.9949% | 1.048% | 1.102% | 1.159% | 1.216% | 1.276% | 1.337% | 1.4% | 1.465% | 1.531% | 1.599% | 1.669% | 1.741% | 1.814% | 1.889% | 1.966% | 2.045% | 2.125% | 2.208% | 2.292% | 2.378% | 2.466% | 2.556% | 2.648% | 2.741% | 2.837%
CLN | 30338702 | DS-CLN-TRNFMR-9000006730 |  | 21 | 3 | 2 | 2 | 3 | 1 | 1 | 3 | 3 | 2 | 225.7143 | 2 | 24 | 3.5 | 84.05 | 0.1909% | 0.1909% | 0.211% | 0.2322% | 0.2547% | 0.2785% | 0.3035% | 0.3298% | 0.3575% | 0.3865% | 0.4168% | 0.4486% | 0.4817% | 0.5162% | 0.5522% | 0.5897% | 0.6286% | 0.669% | 0.7109% | 0.7543% | 0.7993% | 0.8458% | 0.8939% | 0.9436% | 0.9949% | 1.048% | 1.102% | 1.159% | 1.216% | 1.276%
CRE | 30165029 | DS-CRE-TRNFMR-9000525811 |  | 13 | 3 | 2 | 1 | 3 | 2 | 1 | 4 | 2 | 2 | 217.1429 | 2 | 24 | 3.5 | 84.05 | 0.1909% | 0.1909% | 0.211% | 0.2322% | 0.2547% | 0.2785% | 0.3035% | 0.3298% | 0.3575% | 0.3865% | 0.4168% | 0.4486% | 0.4817% | 0.5162% | 0.5522% | 0.5897% | 0.6286% | 0.669% | 0.7109% | 0.7543% | 0.7993% | 0.8458% | 0.8939% | 0.9436% | 0.9949% | 1.048% | 1.102% | 1.159% | 1.216% | 1.276%
LLG | 30359074 | DS-LLG-TRNFMR-9000007796 |  | 20 | 1 | 2 | 1 | 2 | 1 | 1 | 5 | 3 | 2 | 191.4286 | 2 | 24 | 3.5 | 84.05 | 0.1909% | 0.1909% | 0.211% | 0.2322% | 0.2547% | 0.2785% | 0.3035% | 0.3298% | 0.3575% | 0.3865% | 0.4168% | 0.4486% | 0.4817% | 0.5162% | 0.5522% | 0.5897% | 0.6286% | 0.669% | 0.7109% | 0.7543% | 0.7993% | 0.8458% | 0.8939% | 0.9436% | 0.9949% | 1.048% | 1.102% | 1.159% | 1.216% | 1.276%
CRE | 30380287 | DS-CRE-TRNFMR-9000525810 |  | 13 | 2 | 2 | 1 | 1 | 2 | 1 | 3 | 2 | 2 | 177.1429 | 2 | 24 | 3.5 | 84.05 | 0.1909% | 0.1909% | 0.211% | 0.2322% | 0.2547% | 0.2785% | 0.3035% | 0.3298% | 0.3575% | 0.3865% | 0.4168% | 0.4486% | 0.4817% | 0.5162% | 0.5522% | 0.5897% | 0.6286% | 0.669% | 0.7109% | 0.7543% | 0.7993% | 0.8458% | 0.8939% | 0.9436% | 0.9949% | 1.048% | 1.102% | 1.159% | 1.216% | 1.276%
CLN | 30000439 | DS-CLN-TRNFMR-9000001306 |  | 19 | 2 | 2 | 1 | 1 | 1 | 1 | 3 | 2 | 2 | 165.7143 | 2 | 24 | 3.5 | 84.05 | 0.1909% | 0.1909% | 0.211% | 0.2322% | 0.2547% | 0.2785% | 0.3035% | 0.3298% | 0.3575% | 0.3865% | 0.4168% | 0.4486% | 0.4817% | 0.5162% | 0.5522% | 0.5897% | 0.6286% | 0.669% | 0.7109% | 0.7543% | 0.7993% | 0.8458% | 0.8939% | 0.9436% | 0.9949% | 1.048% | 1.102% | 1.159% | 1.216% | 1.276%
OFR | 30035965 | DS-OFR-TRNFMR-9000014181 |  | 16 | 2 | 2 | 1 | 1 | 1 | 1 | 3 | 2 | 2 | 165.7143 | 2 | 24 | 3.5 | 84.05 | 0.1909% | 0.1909% | 0.211% | 0.2322% | 0.2547% | 0.2785% | 0.3035% | 0.3298% | 0.3575% | 0.3865% | 0.4168% | 0.4486% | 0.4817% | 0.5162% | 0.5522% | 0.5897% | 0.6286% | 0.669% | 0.7109% | 0.7543% | 0.7993% | 0.8458% | 0.8939% | 0.9436% | 0.9949% | 1.048% | 1.102% | 1.159% | 1.216% | 1.276%
KLO | 30002764 | DS-KLO-TRNFMR-9000412348 |  | 15 | 1 | 2 | 1 | 1 | 1 | 1 | 4 | 2 | 2 | 160 | 2 | 24 | 3.5 | 84.05 | 0.1909% | 0.1909% | 0.211% | 0.2322% | 0.2547% | 0.2785% | 0.3035% | 0.3298% | 0.3575% | 0.3865% | 0.4168% | 0.4486% | 0.4817% | 0.5162% | 0.5522% | 0.5897% | 0.6286% | 0.669% | 0.7109% | 0.7543% | 0.7993% | 0.8458% | 0.8939% | 0.9436% | 0.9949% | 1.048% | 1.102% | 1.159% | 1.216% | 1.276%
OFR | 30221642 | DS-OFR-TRNFMR-9000016122 |  | 16 | 1 | 2 | 1 | 1 | 1 | 1 | 3 | 2 | 2 | 151.4286 | 2 | 24 | 3.5 | 84.05 | 0.1909% | 0.1909% | 0.211% | 0.2322% | 0.2547% | 0.2785% | 0.3035% | 0.3298% | 0.3575% | 0.3865% | 0.4168% | 0.4486% | 0.4817% | 0.5162% | 0.5522% | 0.5897% | 0.6286% | 0.669% | 0.7109% | 0.7543% | 0.7993% | 0.8458% | 0.8939% | 0.9436% | 0.9949% | 1.048% | 1.102% | 1.159% | 1.216% | 1.276%
KLO | 30208816 | DS-KLO-TRNFMR-9000412347 |  | 15 | 1 | 2 | 1 | 1 | 1 | 1 | 3 | 2 | 2 | 151.4286 | 2 | 24 | 3.5 | 84.05 | 0.1909% | 0.1909% | 0.211% | 0.2322% | 0.2547% | 0.2785% | 0.3035% | 0.3298% | 0.3575% | 0.3865% | 0.4168% | 0.4486% | 0.4817% | 0.5162% | 0.5522% | 0.5897% | 0.6286% | 0.669% | 0.7109% | 0.7543% | 0.7993% | 0.8458% | 0.8939% | 0.9436% | 0.9949% | 1.048% | 1.102% | 1.159% | 1.216% | 1.276%
PHM | 32944656 | DS-PHM-TRNFMR-9000004393 |  | 8 | 2 | 2 | 1 | 1 | 1 | 1 | 3 | 1 | 1 | 142.8571 | 1 | 8 | 3.5 | 84.05 | 0.01357% | 0.01357% | 0.01791% | 0.023% | 0.02887% | 0.03555% | 0.04308% | 0.0515% | 0.06084% | 0.07112% | 0.08238% | 0.09465% | 0.1079% | 0.1223% | 0.1378% | 0.1543% | 0.172% | 0.1909% | 0.211% | 0.2322% | 0.2547% | 0.2785% | 0.3035% | 0.3298% | 0.3575% | 0.3865% | 0.4168% | 0.4486% | 0.4817% | 0.5162%
PHM | 32944654 | DS-PHM-TRNFMR-9000007050 |  | 8 | 2 | 2 | 1 | 1 | 1 | 1 | 3 | 1 | 1 | 142.8571 | 1 | 8 | 3.5 | 84.05 | 0.01357% | 0.01357% | 0.01791% | 0.023% | 0.02887% | 0.03555% | 0.04308% | 0.0515% | 0.06084% | 0.07112% | 0.08238% | 0.09465% | 0.1079% | 0.1223% | 0.1378% | 0.1543% | 0.172% | 0.1909% | 0.211% | 0.2322% | 0.2547% | 0.2785% | 0.3035% | 0.3298% | 0.3575% | 0.3865% | 0.4168% | 0.4486% | 0.4817% | 0.5162%

## AER VCR Rates(2024)
Category | Rate | Notes
Dec 24 AER VCR ($/kWh) - Res | 49.23 | Vic Av Res
Dec 24 AER VCR ($/kWh) - Com | 34.39 | Vic Av Com
Dec 24 AER VCR ($/kWh) - Ind | 33.49 | Vic Av Ind
Dec 24 AER VCR ($/kWh) - Agr | 22.25 | Vic Av Agr

## Customer No. and Vol per Feeder
CUSTOMER_CLASS | Feeder | VOL | CUST_NO | ZSS | Customer mix received from AusNet Financial Planning & Strategy on 25/7/2025
COMMERCIAL | bra11 | 9860526.7854 | 168 | bra
COMMERCIAL | bge13 | 654988.62 | 45 | bge
COMMERCIAL | phi11 | 1878610.03 | 37 | phi
NCONUML | moe11 | 47447.48 | 18 | moe
NCONUML | drn13 | 27414.73 | 17 | drn
COMMERCIAL | smg34 | 5224461.8 | 1 | smg
FARM | wgl13 | 901266.5312 | 97 | wgl
FARM | msd2 | 2808295.5668 | 471 | msd
NCONUML | elm34 | 86758.8 | 34 | elm
| rwt36 | 703.54 | 2 | rwt
COMMERCIAL | lga41 | 1099100.22 | 2 | lga
| bdl33 | 4298.82 | 8 | bdl
NCONUML | smr14 | 27225.34 | 18 | smr
COMMERCIAL | cln24 | 4484028.8333 | 290 | cln
RESIDENTL | ofr14 | 13024383.6958 | 3554 | ofr
NCONUML | bdl43 | 100361.9983 | 38 | bdl
| ofr22 | 16469.09 | 22 | ofr
NCONUML | rwn33 | 8721.79 | 7 | rwn
LIGHTING | hpk12 | 342838 | 1 | hpk
COMMERCIAL | bra23 | 6262297.01 | 84 | bra
FARM | tt1 | 1865.76 | 1 | tt
LIGHTING | mfa14 | 787800.53 | 1 | mfa
RESIDENTL | brt22 | 9968534.1043 | 1376 | brt
RESIDENTL | mwl25 | 4092575.372 | 493 | mwl
NCONUML | wgi22 | 83961.44 | 23 | wgi
INDUSTRIAL | ldl22 | 4379901.5885 | 45 | ldl
RESIDENTL | phm22 | 3628742.5283 | 796 | phm
FARM | mfa23 | 2691321.6324 | 201 | mfa
NCONUML | rwn32 | 60415.37 | 23 | rwn
FARM | cre22 | 55644.16 | 17 | cre
RESIDENTL | elm24 | 17367685.5307 | 2999 | elm
COMMERCIAL | tt9 | 7181168.3052 | 213 | tt
COMMERCIAL | kms12 | 15257134.8455 | 395 | kms
NCONUML | cyn31 | 24759.23 | 14 | cyn
| llg12 | 26420.7189 | 15 | llg
LIGHTING | ruba22 | 247422.69 | 1 | ruba
RESIDENTL | wt12 | 10803758.701 | 2579 | wt
COMMERCIAL | bwn14 | 6975240.1 | 156 | bwn
NCONUML | bge12 | 37366.03 | 11 | bge
NCONUML | rwn24 | 30489.76 | 21 | rwn
FARM | sfs1 | 113380.09 | 9 | sfs
| bwr13 | 80076.52 | 46 | bwr
FARM | wt13 | 37228.86 | 3 | wt
FARM | cre23 | 226478.55 | 9 | cre
COMMERCIAL | rwn22 | 1886562.0146 | 72 | rwn
| tgn23 | 13898.1302 | 15 | tgn
FARM | ldl22 | 7887.95 | 1 | ldl
RESIDENTL | fgy21 | 7153989.4877 | 1047 | fgy
FARM | mjg11 | 735019.886 | 74 | mjg
| ldl14 | 17432.2687 | 11 | ldl
INDUSTRIAL | ldl24 | 64751.4 | 12 | ldl
| sle13 | 253.3245 | 2 | sle
FARM | moe21 | 6301170.9744 | 504 | moe
FARM | bge23 | 671977.1074 | 66 | bge
RESIDENTL | elm32 | 19949095.4752 | 2463 | elm
COMMERCIAL | ftr12 | 1975462.7263 | 113 | ftr
RESIDENTL | lyd12 | 6657897.88 | 1592 | lyd
RESIDENTL | epg31 | 11862355.3417 | 3027 | epg
NCONUML | ofr11 | 57102.89 | 18 | ofr
FARM | moe11 | 65350.2807 | 7 | moe
FARM | nla32 | 1181128.1259 | 84 | nla
FARM | smr24 | 4141783.4574 | 392 | smr
RESIDENTL | fgy13 | 7970231.1446 | 1518 | fgy
FARM | bdl41 | 1305847.5951 | 258 | bdl
NCONUML | elm23 | 62172.37 | 40 | elm
| elm22 | 20617.5429 | 26 | elm
NCONUML | cre21 | 58240.1 | 18 | cre
FARM | phm32 | 50851.13 | 8 | phm
INDUSTRIAL | lga21 | 208132.02 | 16 | lga
INDUSTRIAL | nrn13 | 39703.59 | 6 | nrn
RESIDENTL | hpk22 | 18949862.0449 | 4569 | hpk
NCONUML | cyn13 | 17637.49 | 6 | cyn
COMMERCIAL | cre31 | 14851829.6913 | 363 | cre
COMMERCIAL | epg32 | 5001490.9226 | 156 | epg
| phm32 | 41386.12 | 47 | phm
NCONUML | wo33 | 6875.31 | 2 | wo
FARM | wgl21 | 5056187.7677 | 366 | wgl
INDUSTRIAL | cre22 | 240829.25 | 4 | cre
RESIDENTL | wgi34 | 3671110.7601 | 570 | wgi
INDUSTRIAL | ldl12 | 10352583.7 | 7 | ldl
INDUSTRIAL | wyk12 | 149433.7 | 6 | wyk
INDUSTRIAL | cyn14 | 23200.151 | 3 | cyn
| wo11 | 4136.2425 | 3 | wo
| msd4 | 20521.76 | 37 | msd
FARM | mby12 | 52034.88 | 19 | mby
COMMERCIAL | rwt22 | 7145877.6761 | 143 | rwt
COMMERCIAL | wo12 | 23719023.8 | 1 | wo
RESIDENTL | wn2 | 17414453.5902 | 3500 | wn
COMMERCIAL | wots25 | 3483725.2811 | 72 | wots
RESIDENTL | bwr33 | 46024.67 | 2 | bwr
RESIDENTL | wn3 | 12349888.6736 | 2099 | wn
RESIDENTL | bn24 | 2992797.8263 | 559 | bn
| bra21 | 41455.7142 | 65 | bra
INDUSTRIAL | hpk14 | 16381.88 | 4 | hpk
RESIDENTL | epg32 | 14811809.1158 | 3829 | epg
COMMERCIAL | cln14 | 10141314.5039 | 129 | cln
FARM | smg31 | 14995.46 | 5 | smg
INDUSTRIAL | drn22 | 2117102.6666 | 12 | drn
NCONUML | drn12 | 43785.8374 | 16 | drn
INDUSTRIAL | fgy34 | 128392.6893 | 5 | fgy
NCONUML | fgy31 | 6707.46 | 4 | fgy
| wt8 | 7059.0655 | 13 | wt
| bwn12 | 6521.57 | 6 | bwn
COMMERCIAL | myt12 | 10774273.2986 | 307 | myt
COMMERCIAL | ldl21 | 5339830.9491 | 117 | ldl
| cln21 | 32425.72 | 66 | cln
INDUSTRIAL | fgy14 | 162921.94 | 7 | fgy
| tgn12 | 22490.11 | 3 | tgn
COMMERCIAL | epg12 | 8214339.5389 | 163 | epg
NCONUML | moe23 | 69334.91 | 17 | moe
FARM | cyn14 | 7715.15 | 1 | cyn
RESIDENTL | lyd14 | 10580841.4317 | 1203 | lyd
COMMERCIAL | smg23 | 21963007.1063 | 434 | smg
INDUSTRIAL | bra33 | 2076536.62 | 34 | bra
INDUSTRIAL | rwt14 | 2271244.55 | 44 | rwt
COMMERCIAL | lga14 | 2174194.9787 | 115 | lga
INDUSTRIAL | myt22 | 3176.32 | 3 | myt
FARM | cyn21 | 10230.57 | 2 | cyn
| klo24 | 65411.35 | 119 | klo
COMMERCIAL | brt21 | 6571769.7252 | 216 | brt
FARM | kms11 | 665243.0597 | 75 | kms
| elm34 | 25999.6869 | 33 | elm
INDUSTRIAL | mwl11 | 366139.79 | 15 | mwl
INDUSTRIAL | lyd14 | 80895.88 | 12 | lyd
LIGHTING | cpk11 | 1086.88 | 1 | cpk
NCONUML | fgy23 | 34402.31 | 12 | fgy
| bra32 | 15753.982 | 22 | bra
RESIDENTL | epg12 | 26391788.5687 | 6905 | epg
COMMERCIAL | cyn24 | 15647575.1097 | 304 | cyn
INDUSTRIAL | phm21 | 511727.73 | 19 | phm
NCONUML | ftr12 | 5424.58 | 5 | ftr
| bwa23 | 5447.575 | 8 | bwa
NCONUML | llg12 | 4182.92 | 3 | llg
COMMERCIAL | drn13 | 5299129.684 | 96 | drn
INDUSTRIAL | hpk21 | 31624.71 | 8 | hpk
INDUSTRIAL | wyk23 | 1500537.4334 | 28 | wyk
RESIDENTL | lga12 | 4152631.2896 | 644 | lga
RESIDENTL | cyn11 | 6009338.551 | 1440 | cyn
NCONUML | fgy24 | 70027.41 | 43 | fgy
| moe23 | 74726.3012 | 22 | moe
COMMERCIAL | elm24 | 3531802.26 | 46 | elm
LIGHTING | elm33 | 1000.47 | 1 | elm
RESIDENTL | smg23 | 6500499.5996 | 1411 | smg
FARM | msd4 | 1851245.0012 | 252 | msd
COMMERCIAL | lga24 | 21693950.3379 | 92 | lga
COMMERCIAL | ldl11 | 7360578.73 | 74 | ldl
NCONUML | rve13 | 29515.6981 | 24 | rve
COMMERCIAL | trc01 | 365242.5067 | 42 | trc
COMMERCIAL | wt15 | 1164715.6471 | 30 | wt
COMMERCIAL | bra14 | 811059.401 | 59 | bra
| ftr21 | 17034.7542 | 20 | ftr
RESIDENTL | bra23 | 7643359.408 | 1736 | bra
INDUSTRIAL | cpk11 | 59065.36 | 14 | cpk
INDUSTRIAL | hpk12 | 531460.54 | 46 | hpk
FARM | fgy23 | 137430.23 | 3 | fgy
INDUSTRIAL | tt4 | 77015.1997 | 16 | tt
FARM | cpk22 | 45399.86 | 6 | cpk
INDUSTRIAL | yn31 | 1004932.7745 | 6 | yn
FARM | myt22 | 1873055.6433 | 191 | myt
| cpk12 | 20188.43 | 32 | cpk
RESIDENTL | bwa22 | 6606654.3694 | 1106 | bwa
| mfa34 | 1434.55 | 6 | mfa
| nla31 | 4780.58 | 5 | nla
FARM | mdg1 | 36782.2 | 6 | mdg
RESIDENTL | mwl21 | 3605605.4081 | 859 | mwl
COMMERCIAL | phm33 | 14452041.4603 | 180 | phm
INDUSTRIAL | ofr23 | 154535.41 | 17 | ofr
INDUSTRIAL | elm21 | 177435.466 | 7 | elm
INDUSTRIAL | wt5 | 89.11 | 1 | wt
FARM | llg13 | 1917532.2118 | 152 | llg
INDUSTRIAL | klk21 | 41156.68 | 10 | klk
NCONUML | wt9 | 48247.64 | 17 | wt
FARM | mdi1 | 153288.2952 | 21 | mdi
INDUSTRIAL | nrn14 | 19245.31 | 5 | nrn
INDUSTRIAL | wgl12 | 500659.11 | 16 | wgl
FARM | fgy13 | 80534.51 | 6 | fgy
INDUSTRIAL | bwr14 | 1597974.48 | 1 | bwr
LIGHTING | bn11 | 103048.5 | 1 | bn
RESIDENTL | klo14 | 40411755.0117 | 10946 | klo
RESIDENTL | fgy33 | 9101921.8028 | 1763 | fgy
LIGHTING | cre31 | 2308168.51 | 1 | cre
RESIDENTL | wn5 | 8555201.9981 | 1156 | wn
COMMERCIAL | mfa22 | 5299491.9938 | 179 | mfa
COMMERCIAL | lyd11 | 3798691.89 | 62 | lyd
LIGHTING | bn24 | 2014.81 | 1 | bn
COMMERCIAL | cf1 | 9360587.4941 | 189 | cf
FARM | lga11 | 4665290.6529 | 555 | lga
RESIDENTL | lyd13 | 10895753.2364 | 2051 | lyd
NCONUML | cre33 | 35388.67 | 19 | cre
| smg32 | 685.05 | 3 | smg
INDUSTRIAL | cyn11 | 1966971.1028 | 55 | cyn
COMMERCIAL | wn2 | 10157994.9798 | 156 | wn
| phm21 | 32464.7212 | 22 | phm
| sfs1 | 13890.635 | 10 | sfs
NCONUML | tt12 | 15011.94 | 8 | tt
FARM | lga21 | 1065599.6961 | 147 | lga
| ldl12 | 52350.63 | 6 | ldl
INDUSTRIAL | smg31 | 231921 | 9 | smg
LIGHTING | myt12 | 813470.88 | 6 | myt
| smr24 | 66801.9 | 34 | smr
NCONUML | cre32 | 49453.4427 | 23 | cre
INDUSTRIAL | bdl44 | 2337630.2078 | 41 | bdl
| rve11 | 302066.1 | 12 | rve
FARM | wo31 | 3245.01 | 1 | wo
LIGHTING | ofr13 | 171706.2 | 2 | ofr
RESIDENTL | tt9 | 13181645.445 | 3553 | tt
COMMERCIAL | wgl11 | 13522117.9742 | 216 | wgl
COMMERCIAL | hpk24 | 15242696.9791 | 271 | hpk
COMMERCIAL | bwr34 | 12222544.1423 | 437 | bwr
NCONUML | nla34 | 19980.17 | 11 | nla
FARM | bwr24 | 9303.26 | 1 | bwr
| wgi23 | 15962.8799 | 36 | wgi
RESIDENTL | cln13 | 18593732.5659 | 6830 | cln
RESIDENTL | lga13 | 1879247.7046 | 295 | lga
RESIDENTL | cnr3 | 108696.4186 | 22 | cnr
| wgl12 | 112644.3661 | 43 | wgl
COMMERCIAL | cln12 | 8203266.5202 | 86 | cln
NCONUML | ofr21 | 100427.35 | 34 | ofr
RESIDENTL | drn24 | 10021102.8231 | 2473 | drn
COMMERCIAL | cyn31 | 1940881.6507 | 53 | cyn
NCONUML | ldl24 | 34534.3 | 19 | ldl
COMMERCIAL | ofr13 | 9302944.2987 | 197 | ofr
| wots13 | 58538.6484 | 32 | wots
| cpk23 | 23360.0808 | 24 | cpk
NCONUML | cln11 | 4587.8606 | 9 | cln
| wt15 | 51811.4 | 11 | wt
COMMERCIAL | epg24 | 26841528 | 1 | epg
FARM | drn22 | 329138.5031 | 52 | drn
| mfa31 | 16838.31 | 22 | mfa
COMMERCIAL | bra32 | 4055727.3404 | 158 | bra
COMMERCIAL | cpk21 | 14974774.5549 | 258 | cpk
INDUSTRIAL | myt21 | 335981.9667 | 19 | myt
FARM | nrn14 | 139044.47 | 14 | nrn
| wt5 | 22324.85 | 13 | wt
INDUSTRIAL | mfa23 | 139940.33 | 14 | mfa
FARM | wyk12 | 2634438.6357 | 233 | wyk
RESIDENTL | epg23 | 3653084.6682 | 932 | epg
COMMERCIAL | tgn11 | 2525258.71 | 85 | tgn
| wt13 | 22551.0062 | 37 | wt
| cyn13 | 10533.28 | 7 | cyn
INDUSTRIAL | fgy13 | 259435.94 | 2 | fgy
RESIDENTL | cln12 | 23908773.0216 | 6775 | cln
COMMERCIAL | brt22 | 9042592.2197 | 210 | brt
COMMERCIAL | rwt25 | 7526054.6961 | 146 | rwt
FARM | mfa31 | 218040.8355 | 21 | mfa
COMMERCIAL | cln22 | 3248277.4443 | 37 | cln
NCONUML | bdl33 | 22970.8 | 8 | bdl
COMMERCIAL | fgy12 | 74427.591 | 4 | fgy
RESIDENTL | mwl16 | 8188909.2298 | 1700 | mwl
INDUSTRIAL | moe25 | 612177.9824 | 16 | moe
COMMERCIAL | tt7 | 24970154.3491 | 341 | tt
INDUSTRIAL | bwr24 | 4118148.7987 | 125 | bwr
RESIDENTL | moe13 | 2791200.4315 | 357 | moe
FARM | wyk24 | 694188.3378 | 94 | wyk
NCONUML | wo14 | 36996.26 | 12 | wo
RESIDENTL | bra13 | 6470560.8911 | 1572 | bra
RESIDENTL | tt7 | 39398.92 | 9 | tt
FARM | epg34 | 15821.91 | 5 | epg
INDUSTRIAL | yn35 | 6582.38 | 2 | yn
NCONUML | bwa23 | 749.23 | 1 | bwa
FARM | sle13 | 1461316.56 | 213 | sle
COMMERCIAL | cpk13 | 4127340.5971 | 198 | cpk
INDUSTRIAL | ldl14 | 1064067.7426 | 16 | ldl
| rwt14 | 62105.3312 | 18 | rwt
LIGHTING | hpk13 | 14513.85 | 1 | hpk
RESIDENTL | klk22 | 940238.19 | 128 | klk
COMMERCIAL | mwl25 | 259300.06 | 16 | mwl
| mjg11 | 96977.3135 | 7 | mjg
RESIDENTL | hpk24 | 4867180.3451 | 1284 | hpk
FARM | ftr21 | 6703423.0704 | 705 | ftr
FARM | smr12 | 441800.25 | 44 | smr
FARM | bwr13 | 73574.54 | 13 | bwr
| ldl22 | 9241.11 | 9 | ldl
FARM | wo22 | 35676.335 | 7 | wo
NCONUML | moe12 | 9318.9 | 3 | moe
INDUSTRIAL | bdl31 | 1561951.6978 | 44 | bdl
COMMERCIAL | ofr14 | 8393968.2568 | 77 | ofr
NCONUML | tgn23 | 48562.71 | 16 | tgn
NCONUML | cyn21 | 25127.29 | 5 | cyn
FARM | phm34 | 22945.58 | 3 | phm
INDUSTRIAL | cyn33 | 36519.92 | 4 | cyn
LIGHTING | bm8b32 | 1070.04 | 1 | bmb
FARM | llg12 | 5311057.9488 | 488 | llg
NCONUML | rwt32 | 94072.85 | 46 | rwt
COMMERCIAL | myt11 | 912988.53 | 42 | myt
INDUSTRIAL | cpk22 | 129954.91 | 11 | cpk
| cre22 | 20388.051 | 33 | cre
RESIDENTL | ldl21 | 5451727.7741 | 1502 | ldl
FARM | bdl44 | 8189534.7866 | 736 | bdl
INDUSTRIAL | bn11 | 1899511.3657 | 45 | bn
INDUSTRIAL | wgi31 | 152399.6 | 19 | wgi
INDUSTRIAL | mdi1 | 16.0426 | 1 | mdi
| ofr11 | 90492.4817 | 79 | ofr
LIGHTING | kms11 | 547479.19 | 1 | kms
RESIDENTL | phi12 | 18738852.0082 | 4967 | phi
COMMERCIAL | bwr12 | 7897915.6022 | 287 | bwr
FARM | msd1 | 2520603.4144 | 354 | msd
COMMERCIAL | tgn44 | 4662112.18 | 89 | tgn
NCONUML | uwy1 | 29815.85 | 15 | uwy
NCONUML | lga22 | 54192.29 | 17 | lga
NCONUML | lga23 | 17186.13 | 6 | lga
INDUSTRIAL | hpk13 | 1952010.47 | 3 | hpk
FARM | drn23 | 391232.6382 | 58 | drn
FARM | ldl23 | 5910515.5529 | 453 | ldl
FARM | bdl31 | 55336.85 | 12 | bdl
RESIDENTL | bwr34 | 11176240.016 | 2984 | bwr
RESIDENTL | ofr13 | 5689359.8131 | 1445 | ofr
NCONUML | bra21 | 145563.002 | 72 | bra
COMMERCIAL | cf2 | 1114027.3697 | 138 | cf
RESIDENTL | bdl32 | 16368580.902 | 3124 | bdl
COMMERCIAL | smr22 | 10240657.5236 | 95 | smr
NCONUML | rve12 | 34563.18 | 21 | rve
COMMERCIAL | cnr3 | 208527.63 | 11 | cnr
| elm25 | 9741.0155 | 15 | elm
INDUSTRIAL | lyd13 | 30651.21 | 5 | lyd
INDUSTRIAL | mby12 | 279353.09 | 7 | mby
INDUSTRIAL | epg21 | 31298.6803 | 2 | epg
FARM | wgl12 | 7817936.5802 | 624 | wgl
COMMERCIAL | moe13 | 1401894.0174 | 82 | moe
RESIDENTL | lga14 | 7239522.4699 | 1158 | lga
RESIDENTL | epg35 | 308209.78 | 22 | epg
FARM | hpk14 | 29274.39 | 5 | hpk
LIGHTING | bn22 | 341591.58 | 1 | bn
NCONUML | bge11 | 85890.46 | 45 | bge
NCONUML | wt7 | 26985.19 | 18 | wt
| wo31 | 27869.149 | 41 | wo
INDUSTRIAL | elm32 | 759094.4258 | 68 | elm
NCONUML | cre23 | 95638.5 | 25 | cre
RESIDENTL | cln23 | 19292170.1488 | 4992 | cln
| lga21 | 17263.28 | 18 | lga
NCONUML | bwn12 | 35975.24 | 12 | bwn
| fgy31 | 1671.76 | 6 | fgy
NCONUML | ftr23 | 39743.6852 | 30 | ftr
NCONUML | smg21 | 9405.11 | 5 | smg
RESIDENTL | epg13 | 24819451.0174 | 7299 | epg
RESIDENTL | ruba22 | 5955886.59 | 1080 | ruba
INDUSTRIAL | bwr23 | 1917390.4058 | 110 | bwr
COMMERCIAL | bn23 | 4585306.9 | 117 | bn
| fgy24 | 60212.15 | 95 | fgy
LIGHTING | brt21 | 27441.26 | 1 | brt
COMMERCIAL | mby14 | 13812.56 | 3 | mby
RESIDENTL | drn21 | 15235611.8074 | 3585 | drn
RESIDENTL | nrn11 | 3368324.1063 | 703 | nrn
NCONUML | cln21 | 97183.1897 | 28 | cln
NCONUML | tgn12 | 26909.78 | 9 | tgn
FARM | moe22 | 48531.59 | 7 | moe
RESIDENTL | bra14 | 17287022.2386 | 4193 | bra
RESIDENTL | brt21 | 8587133.8204 | 1368 | brt
INDUSTRIAL | ldl23 | 2181365.61 | 45 | ldl
NCONUML | klo24 | 121410.57 | 41 | klo
INDUSTRIAL | wt8 | 22231.36 | 5 | wt
| bdl41 | 27628.4721 | 32 | bdl
COMMERCIAL | sle14 | 13227565.7623 | 343 | sle
| smr14 | 17300.3116 | 19 | smr
INDUSTRIAL | llg11 | 439641.21 | 9 | llg
| wgi22 | 13903.1 | 35 | wgi
NCONUML | moe22 | 34069.45 | 10 | moe
| ftr12 | 15921.46 | 17 | ftr
COMMERCIAL | epg11 | 902129.45 | 16 | epg
RESIDENTL | cpk13 | 21255549.7429 | 4974 | cpk
| fgy23 | 9273.25 | 10 | fgy
FARM | cyn12 | 9105.46 | 2 | cyn
INDUSTRIAL | rwn31 | 527467.66 | 22 | rwn
RESIDENTL | bm8b32 | 357081.227 | 62 | bmb
FARM | ruba22 | 1060033.1321 | 158 | ruba
INDUSTRIAL | cnr1 | 88077.93 | 3 | cnr
FARM | cpk12 | 972803.9358 | 91 | cpk
COMMERCIAL | wo14 | 14658340.7796 | 304 | wo
COMMERCIAL | tt5 | 6134357.4395 | 224 | tt
INDUSTRIAL | wo11 | 18559582.74 | 7 | wo
| wgl23 | 17798.7289 | 12 | wgl
NCONUML | cyn12 | 64730.9 | 21 | cyn
COMMERCIAL | bwr33 | 3515549.759 | 83 | bwr
COMMERCIAL | cyn22 | 10287381.4837 | 183 | cyn
COMMERCIAL | rwt32 | 5482054.6843 | 198 | rwt
INDUSTRIAL | nrn12 | 7260.73 | 2 | nrn
RESIDENTL | cln22 | 8137131.1146 | 3340 | cln
| kms12 | 36774.1343 | 44 | kms
| cyn24 | 12784.0842 | 11 | cyn
| smg33 | 11524.64 | 21 | smg
COMMERCIAL | rve11 | 18192998.0721 | 274 | rve
FARM | wt5 | 8146.48 | 2 | wt
INDUSTRIAL | bge23 | 983662.8538 | 7 | bge
| msd2 | 9983.6 | 13 | msd
| bra12 | 98134.87 | 2 | bra
RESIDENTL | hpk23 | 13762355.5073 | 3377 | hpk
COMMERCIAL | smr13 | 15057236.7589 | 394 | smr
INDUSTRIAL | rwt21 | 372221.49 | 45 | rwt
FARM | rve12 | 22362.86 | 5 | rve
NCONUML | fgy32 | 32042.28 | 18 | fgy
INDUSTRIAL | smr12 | 37387308.69 | 3 | smr
NCONUML | mfa34 | 19451.19 | 8 | mfa
FARM | wots13 | 4844280.0942 | 510 | wots
COMMERCIAL | drn21 | 3220798.94 | 52 | drn
INDUSTRIAL | wo31 | 765.77 | 1 | wo
| fgy32 | 8528.5063 | 10 | fgy
INDUSTRIAL | bwr32 | 3058614 | 72 | bwr
| elm23 | 20831.6 | 30 | elm
INDUSTRIAL | mwl12 | 574569.29 | 12 | mwl
RESIDENTL | cpk21 | 7771248.352 | 1679 | cpk
COMMERCIAL | wots11 | 6621581.9604 | 243 | wots
INDUSTRIAL | ftr21 | 313604.8 | 24 | ftr
NCONUML | lyd11 | 43059.75 | 9 | lyd
FARM | phm21 | 25361.56 | 3 | phm
INDUSTRIAL | wyk13 | 453974.55 | 15 | wyk
INDUSTRIAL | mdg1 | 21781.42 | 1 | mdg
INDUSTRIAL | tt1 | 7434378.9861 | 77 | tt
INDUSTRIAL | wgi34 | 1206209.57 | 8 | wgi
LIGHTING | wgi33 | 1050486.0487 | 2 | wgi
COMMERCIAL | wgl15 | 27996457.3831 | 596 | wgl
RESIDENTL | bge23 | 16900476.9279 | 2094 | bge
INDUSTRIAL | bwr13 | 2417661.2776 | 147 | bwr
NCONUML | epg23 | 28250.73 | 7 | epg
INDUSTRIAL | drn14 | 25996.95 | 2 | drn
RESIDENTL | drn14 | 23831050.9741 | 4399 | drn
RESIDENTL | rwt31 | 5842296.4371 | 1436 | rwt
COMMERCIAL | drn24 | 1717660.9 | 35 | drn
FARM | epg14 | 3614.72 | 1 | epg
RESIDENTL | smr13 | 11225814.5464 | 2447 | smr
COMMERCIAL | wots12 | 14359758.4732 | 371 | wots
COMMERCIAL | klk11 | 3080934.4269 | 114 | klk
NCONUML | mwl14 | 31252.61 | 13 | mwl
INDUSTRIAL | sle11 | 266690.1 | 32 | sle
NCONUML | epg31 | 41319.36 | 24 | epg
RESIDENTL | cf1 | 4176161.3871 | 493 | cf
INDUSTRIAL | phm34 | 816155.12 | 6 | phm
FARM | rwn34 | 20402.21 | 4 | rwn
| mby12 | 1524.95 | 3 | mby
RESIDENTL | wgi31 | 14866992.8529 | 3617 | wgi
RESIDENTL | wots25 | 16858284.9544 | 3532 | wots
RESIDENTL | cre33 | 21876811.5892 | 4235 | cre
RESIDENTL | fgy34 | 4606270.9018 | 975 | fgy
RESIDENTL | cyn32 | 15011504.2579 | 3573 | cyn
RESIDENTL | klk11 | 9194980.7775 | 1227 | klk
INDUSTRIAL | fgy33 | 1452360.19 | 13 | fgy
INDUSTRIAL | wgl13 | 6688610.4344 | 14 | wgl
| tgn41 | 12751.16 | 13 | tgn
COMMERCIAL | klk22 | 85830.78 | 8 | klk
| mby11 | 4292.69 | 12 | mby
FARM | drn12 | 9939.61 | 1 | drn
RESIDENTL | rwn24 | 15617115.6722 | 2794 | rwn
RESIDENTL | cre32 | 8053371.5554 | 2218 | cre
COMMERCIAL | bwn11 | 5920812.2037 | 76 | bwn
NCONUML | smg33 | 19709.42 | 12 | smg
INDUSTRIAL | mby11 | 90387.22 | 16 | mby
COMMERCIAL | tgn41 | 8173213.7745 | 338 | tgn
INDUSTRIAL | wn7 | 3582803.57 | 9 | wn
FARM | bwr23 | 29264.76 | 8 | bwr
RESIDENTL | bwn13 | 8026926.4045 | 1629 | bwn
FARM | wgi24 | 1757204.2906 | 142 | wgi
| rve13 | 21148.03 | 29 | rve
RESIDENTL | wgl21 | 23764201.6622 | 4642 | wgl
COMMERCIAL | wn1 | 22168293.2818 | 620 | wn
INDUSTRIAL | cyn32 | 738566.1077 | 85 | cyn
| hpk21 | 27858.58 | 57 | hpk
COMMERCIAL | klo11 | 2030116.61 | 11 | klo
INDUSTRIAL | bn22 | 260832.7234 | 23 | bn
| ofr24 | 25053.77 | 43 | ofr
| drn12 | 30292.1138 | 29 | drn
COMMERCIAL | smg22 | 18806077.0677 | 136 | smg
COMMERCIAL | bwa22 | 4509592.2057 | 144 | bwa
COMMERCIAL | drn12 | 15118769.4919 | 112 | drn
| ldl23 | 80304.9161 | 48 | ldl
| rwn32 | 14306.27 | 22 | rwn
| drn23 | 12868.4314 | 15 | drn
RESIDENTL | mwl22 | 12904194.2639 | 2809 | mwl
COMMERCIAL | tt6 | 3682930.1298 | 115 | tt
COMMERCIAL | bra24 | 3429037.1414 | 127 | bra
NCONUML | hpk11 | 112614.82 | 31 | hpk
RESIDENTL | mfa21 | 12551518.2306 | 1921 | mfa
RESIDENTL | bge22 | 19945240.9452 | 3164 | bge
| tt4 | 9710.0483 | 41 | tt
NCONUML | phm22 | 22255.8232 | 9 | phm
COMMERCIAL | fgy21 | 1241019.6707 | 34 | fgy
INDUSTRIAL | nla31 | 516137.35 | 16 | nla
FARM | wyk13 | 707273.0378 | 84 | wyk
NCONUML | elm25 | 44655.33 | 20 | elm
| ofr23 | 28214.1089 | 26 | ofr
INDUSTRIAL | ruba22 | 167892.49 | 8 | ruba
FARM | hpk21 | 3124.97 | 1 | hpk
FARM | wn4 | 999664.927 | 129 | wn
COMMERCIAL | wn6 | 8795190.5545 | 246 | wn
| cre23 | 50195.43 | 25 | cre
COMMERCIAL | bwr22 | 15914202.1636 | 269 | bwr
INDUSTRIAL | elm22 | 545216.4127 | 27 | elm
NCONUML | bwr32 | 46210.27 | 31 | bwr
COMMERCIAL | moe12 | 4799517.76 | 51 | moe
| drn22 | 43438.5 | 28 | drn
FARM | bn22 | 13032.09 | 3 | bn
FARM | ldl24 | 222231.4641 | 11 | ldl
| bdl31 | 24144.6762 | 16 | bdl
FARM | cpk11 | 227979.0877 | 18 | cpk
FARM | elm33 | 50441.5205 | 4 | elm
INDUSTRIAL | rve13 | 147824.4003 | 10 | rve
COMMERCIAL | uwy1 | 603856.89 | 33 | uwy
FARM | mfa21 | 13347321.3386 | 701 | mfa
RESIDENTL | wo14 | 1446838.665 | 266 | wo
NCONUML | rwt14 | 102266.96 | 37 | rwt
| kms11 | 9612.23 | 20 | kms
RESIDENTL | phi11 | 5828644.3864 | 1391 | phi
COMMERCIAL | tgn12 | 10174331.2835 | 242 | tgn
LIGHTING | drn21 | 522455.53 | 1 | drn
INDUSTRIAL | smr22 | 2060432.23 | 13 | smr
| moe21 | 19173.8011 | 29 | moe
NCONUML | fgy12 | 1668.8419 | 4 | fgy
COMMERCIAL | elm25 | 2590499.6378 | 73 | elm
| epg34 | 11737.1961 | 27 | epg
COMMERCIAL | cpk23 | 2022573.8223 | 44 | cpk
COMMERCIAL | sle31 | 4198591.4215 | 178 | sle
FARM | nrn13 | 23844.37 | 5 | nrn
FARM | elm26 | 83060.0495 | 12 | elm
INDUSTRIAL | rve12 | 67014.5 | 12 | rve
INDUSTRIAL | moe21 | 304282.5341 | 37 | moe
COMMERCIAL | ofr21 | 9424773.56 | 126 | ofr
FARM | wn3 | 4385381.9629 | 585 | wn
FARM | klk21 | 574949.1868 | 82 | klk
NCONUML | wyk13 | 97422.66 | 49 | wyk
FARM | bwn12 | 14573.05 | 3 | bwn
NCONUML | msd2 | 8161.26 | 6 | msd
COMMERCIAL | elm31 | 474386.1613 | 1 | elm
RESIDENTL | rwt35 | 12065.95 | 2 | rwt
RESIDENTL | wt6 | 15702930.1084 | 3397 | wt
RESIDENTL | cln24 | 3991370.9732 | 1090 | cln
COMMERCIAL | smg21 | 2744632.8687 | 43 | smg
| myt21 | 64545.94 | 22 | myt
RESIDENTL | lga22 | 9862202.3617 | 1608 | lga
INDUSTRIAL | cyn13 | 4447831.06 | 67 | cyn
COMMERCIAL | ruba12 | 6703349.3664 | 290 | ruba
| smr23 | 7378.7014 | 9 | smr
FARM | phi13 | 230339.12 | 15 | phi
RESIDENTL | wt11 | 8665012.8839 | 2213 | wt
RESIDENTL | bge13 | 9255563.8982 | 1458 | bge
COMMERCIAL | bge11 | 11367890.3817 | 330 | bge
COMMERCIAL | wgi23 | 2290528.82 | 95 | wgi
COMMERCIAL | epg35 | 29855241.8371 | 304 | epg
NCONUML | mwl23 | 55631.52 | 20 | mwl
RESIDENTL | tgn11 | 18615536.7391 | 4196 | tgn
RESIDENTL | klo24 | 35150523.3753 | 8219 | klo
| wgi32 | 32777.55 | 36 | wgi
| uwy1 | 1895.86 | 6 | uwy
COMMERCIAL | wots24 | 5008654.6646 | 265 | wots
INDUSTRIAL | phi13 | 601326.64 | 38 | phi
LIGHTING | cf1 | 76883.018 | 3 | cf
RESIDENTL | cre21 | 18876617.5647 | 4715 | cre
INDUSTRIAL | wo32 | 73086.25 | 1 | wo
COMMERCIAL | lga13 | 621321.4861 | 47 | lga
FARM | cnr2 | 245915.51 | 48 | cnr
COMMERCIAL | bge22 | 4521687.9575 | 100 | bge
INDUSTRIAL | cyn12 | 101425.5 | 5 | cyn
FARM | drn11 | 51881.33 | 8 | drn
INDUSTRIAL | wo23 | 212041.78 | 1 | wo
RESIDENTL | lga23 | 5064870.5947 | 821 | lga
RESIDENTL | bn12 | 3438265.7182 | 625 | bn
RESIDENTL | bra21 | 23268334.8963 | 5707 | bra
| bdl42 | 11198.42 | 14 | bdl
FARM | cnr1 | 2440.03 | 2 | cnr
| phm34 | 68320.3174 | 32 | phm
FARM | rwt31 | 12148.87 | 1 | rwt
| smg31 | 8879.89 | 17 | smg
LIGHTING | tgn11 | 1064655.8 | 1 | tgn
FARM | llg14 | 4195351.6172 | 347 | llg
FARM | mwl11 | 2401732.236 | 295 | mwl
INDUSTRIAL | brt22 | 103539.39 | 15 | brt
COMMERCIAL | mwl14 | 15268408.4249 | 139 | mwl
RESIDENTL | wn1 | 4757807.4084 | 1039 | wn
COMMERCIAL | wo33 | 4706642.85 | 27 | wo
| nrn14 | 10562.91 | 10 | nrn
RESIDENTL | wgl15 | 10836827.2608 | 2158 | wgl
RESIDENTL | mfa22 | 4069843.249 | 701 | mfa
NCONUML | wyk24 | 96009.71 | 32 | wyk
NCONUML | rwn34 | 17137.95 | 21 | rwn
NCONUML | rve11 | 32578.28 | 16 | rve
INDUSTRIAL | klk11 | 54511.69 | 7 | klk
RESIDENTL | tt2 | 73044.37 | 7 | tt
COMMERCIAL | rwn32 | 3002784.6794 | 97 | rwn
NCONUML | tt1 | 9612.49 | 4 | tt
NCONUML | bwr23 | 79898.93 | 30 | bwr
NCONUML | epg14 | 19866.64 | 14 | epg
| elm26 | 27328.755 | 32 | elm
INDUSTRIAL | bdl32 | 418697.92 | 34 | bdl
FARM | wt11 | 3746.97 | 1 | wt
NCONUML | ofr23 | 50364.93 | 30 | ofr
INDUSTRIAL | smg23 | 412547.84 | 9 | smg
LIGHTING | klo14 | 3058096.87 | 1 | klo
| nrn13 | 13473.67 | 22 | nrn
FARM | bra12 | 12444.91 | 1 | bra
COMMERCIAL | cre21 | 15222170.3645 | 489 | cre
INDUSTRIAL | wgi32 | 984365.53 | 33 | wgi
NCONUML | rwt25 | 118451.05 | 54 | rwt
INDUSTRIAL | mwe236 | 280541.09 | 16 | mwe
RESIDENTL | epg33 | 183201.2006 | 6 | epg
INDUSTRIAL | elm33 | 243571.284 | 12 | elm
RESIDENTL | ldl11 | 13512975.3636 | 2241 | ldl
| mwl12 | 15850.97 | 9 | mwl
INDUSTRIAL | fgy21 | 6595081.67 | 18 | fgy
LIGHTING | smr24 | 109914.08 | 1 | smr
RESIDENTL | rwt25 | 10768082.8154 | 2324 | rwt
INDUSTRIAL | rwt15 | 3409961.2906 | 83 | rwt
INDUSTRIAL | phi12 | 3418741.3516 | 25 | phi
INDUSTRIAL | bwa22 | 1592049.74 | 9 | bwa
NCONUML | wo22 | 90587.46 | 26 | wo
INDUSTRIAL | ldl21 | 599666.7 | 44 | ldl
INDUSTRIAL | wt6 | 1814.16 | 1 | wt
NCONUML | ofr22 | 9198.59 | 2 | ofr
INDUSTRIAL | bra13 | 1860337.5903 | 47 | bra
COMMERCIAL | fgy24 | 2616699.5517 | 109 | fgy
RESIDENTL | epg11 | 6094828.0666 | 1503 | epg
NCONUML | rwt36 | 1279.88 | 1 | rwt
RESIDENTL | bwn14 | 23184606.5946 | 3016 | bwn
COMMERCIAL | bra31 | 7996775.7312 | 141 | bra
| nla32 | 13550.62 | 15 | nla
FARM | brt11 | 223967.42 | 33 | brt
| hpk12 | 10433.13 | 13 | hpk
INDUSTRIAL | llg13 | 899195.7591 | 21 | llg
INDUSTRIAL | wgl21 | 1687828.17 | 29 | wgl
INDUSTRIAL | cnr2 | 615523.18 | 19 | cnr
INDUSTRIAL | mfa14 | 499885.98 | 5 | mfa
RESIDENTL | drn13 | 15714620.5428 | 2698 | drn
FARM | kms12 | 1180373.8068 | 156 | kms
COMMERCIAL | rwn24 | 15303994.2605 | 63 | rwn
NCONUML | wn4 | 65357.11 | 21 | wn
COMMERCIAL | rwn33 | 562037.42 | 22 | rwn
| moe22 | 3614.75 | 12 | moe
| wgl13 | 39374.2 | 44 | wgl
| moe11 | 8193.3901 | 21 | moe
COMMERCIAL | wt7 | 4475658.5866 | 198 | wt
NCONUML | bwr13 | 106489.72 | 46 | bwr
NCONUML | kms12 | 115620.45 | 45 | kms
NCONUML | cyn24 | 41312.6858 | 21 | cyn
COMMERCIAL | mwl13 | 8520395.3383 | 232 | mwl
COMMERCIAL | cyn32 | 10902527.7138 | 351 | cyn
INDUSTRIAL | tgn31 | 3050316.88 | 29 | tgn
| wo13 | 12961.22 | 9 | wo
NCONUML | bra12 | 30121.15 | 6 | bra
| mwl24 | 4141.68 | 3 | mwl
RESIDENTL | ftr22 | 5196242.6186 | 1010 | ftr
| cyn12 | 33132.831 | 28 | cyn
| mwl11 | 4217.9 | 11 | mwl
NCONUML | sle13 | 9744.3474 | 7 | sle
RESIDENTL | sle14 | 16027394.2978 | 4223 | sle
RESIDENTL | wgl23 | 5362246.1099 | 739 | wgl
COMMERCIAL | cre23 | 25513720.5265 | 132 | cre
RESIDENTL | bdl43 | 5886157.096 | 1122 | bdl
RESIDENTL | bge21 | 100743.92 | 11 | bge
RESIDENTL | smg22 | 10427736.14 | 2476 | smg
FARM | rwn31 | 347566.14 | 21 | rwn
INDUSTRIAL | bn12 | 8173831.79 | 6 | bn
| wgi24 | 27543.5394 | 32 | wgi
| mfa23 | 2828.28 | 3 | mfa
NCONUML | elm22 | 93887.89 | 42 | elm
INDUSTRIAL | wots13 | 2426481.9937 | 28 | wots
RESIDENTL | mwl13 | 9372820.2657 | 1896 | mwl
COMMERCIAL | epg31 | 8736205.1691 | 170 | epg
| bdl44 | 43009.9658 | 33 | bdl
COMMERCIAL | wgl24 | 14484234.4559 | 200 | wgl
INDUSTRIAL | wn3 | 1104797.78 | 30 | wn
| wgi33 | 38017.7186 | 28 | wgi
NCONUML | wo31 | 91536.41 | 24 | wo
FARM | ldl14 | 3990495.203 | 142 | ldl
NCONUML | wyk12 | 43139.17 | 24 | wyk
INDUSTRIAL | mwl15 | 15961047.4 | 1 | mwl
LIGHTING | bdl32 | 23514.52 | 1 | bdl
| rve12 | 15159.19 | 33 | rve
NCONUML | phm34 | 55440.25 | 17 | phm
COMMERCIAL | phm22 | 18761180.3018 | 732 | phm
RESIDENTL | cyn22 | 8715945.6121 | 2142 | cyn
FARM | fgy31 | 3345.68 | 2 | fgy
RESIDENTL | smr22 | 8159798.5324 | 1327 | smr
RESIDENTL | cyn23 | 7298806.6664 | 1621 | cyn
FARM | bdl42 | 2407309.4815 | 483 | bdl
| wyk23 | 31976.68 | 33 | wyk
INDUSTRIAL | rwn26 | 257525.5397 | 10 | rwn
NCONUML | bwn11 | 91006.47 | 23 | bwn
COMMERCIAL | cyn23 | 7883296.3431 | 299 | cyn
| moe15 | 19145.0797 | 16 | moe
| drn11 | 44271.4909 | 65 | drn
INDUSTRIAL | moe22 | 88009.47 | 4 | moe
NCONUML | mdg1 | 4146.1 | 9 | mdg
FARM | bra33 | 5568.67 | 1 | bra
LIGHTING | bwa22 | 75542.46 | 1 | bwa
NCONUML | hpk14 | 64164.68 | 20 | hpk
NCONUML |  | 262.3928 | 5 | #REF!
INDUSTRIAL | cln13 | 2016187.9013 | 2 | cln
FARM | ofr11 | 1184021.9516 | 51 | ofr
FARM | phm31 | 2011038.4476 | 90 | phm
NCONUML | elm21 | 62554.36 | 23 | elm
NCONUML | wt8 | 36862.33 | 14 | wt
NCONUML | cnr1 | 1922.85 | 2 | cnr
INDUSTRIAL | cre31 | 212230.18 | 2 | cre
COMMERCIAL | mfa34 | 8313764.4144 | 170 | mfa
INDUSTRIAL | tt5 | 637183.9506 | 23 | tt
INDUSTRIAL | llg14 | 1201432.9268 | 29 | llg
RESIDENTL | wo23 | 1549813.7708 | 361 | wo
| bwr23 | 25383.1703 | 47 | bwr
| sle11 | 3997.21 | 10 | sle
NCONUML | epg22 | 8538.04 | 7 | epg
NCONUML | bwr24 | 20744.02 | 14 | bwr
INDUSTRIAL | myt12 | 952524.23 | 20 | myt
| ftr23 | 53453.1274 | 33 | ftr
RESIDENTL | bra11 | 9331476.9371 | 2277 | bra
FARM | ldl13 | 3504918.0126 | 302 | ldl
| brt11 | 8693.81 | 14 | brt
INDUSTRIAL | phm31 | 91642.7039 | 2 | phm
COMMERCIAL | bdl43 | 22280533.2345 | 523 | bdl
FARM | moe23 | 4928404.5033 | 365 | moe
| klk21 | 7164.56 | 8 | klk
| wt7 | 8483.27 | 17 | wt
FARM | llg11 | 4501914.1562 | 365 | llg
LIGHTING | cf2 | 13221.322 | 1 | cf
| tgn31 | 23134.1673 | 13 | tgn
RESIDENTL | nla31 | 3471883.5329 | 742 | nla
COMMERCIAL | bdl31 | 6479518.62 | 206 | bdl
COMMERCIAL | smr23 | 799486.21 | 26 | smr
INDUSTRIAL | rve11 | 154936.16 | 21 | rve
RESIDENTL | bm8b33 | 130717.0048 | 17 | bmb
FARM | phi12 | 364625.9 | 40 | phi
INDUSTRIAL | klk22 | 5518.6 | 1 | klk
RESIDENTL | llg12 | 7619865.2998 | 1210 | llg
RESIDENTL | cln21 | 24090170.4832 | 5877 | cln
NCONUML | cpk11 | 17830.25 | 17 | cpk
COMMERCIAL | ruba22 | 3463594.5603 | 120 | ruba
NCONUML | brt22 | 9306.55 | 7 | brt
INDUSTRIAL | epg32 | 7635590.16 | 5 | epg
INDUSTRIAL | cln12 | 360384.55 | 1 | cln
COMMERCIAL | bwr13 | 10101102.0366 | 288 | bwr
COMMERCIAL | wo22 | 9017310.64 | 153 | wo
INDUSTRIAL | hpk24 | 9439809.63 | 31 | hpk
COMMERCIAL | cpk12 | 5057421.24 | 115 | cpk
| lyd14 | 55928.8081 | 17 | lyd
INDUSTRIAL | klo11 | 67703.26 | 1 | klo
RESIDENTL | ldl14 | 11349760.1474 | 1905 | ldl
LIGHTING | myt21 | 2294.9 | 1 | myt
RESIDENTL | rwn22 | 13452598.5118 | 2640 | rwn
COMMERCIAL | bm8b32 | 168652.4116 | 16 | bmb
INDUSTRIAL | bdl34 | 328519.77 | 31 | bdl
| tt12 | 16952.1045 | 5 | tt
RESIDENTL | wots24 | 6979604.5034 | 1172 | wots
INDUSTRIAL | wyk24 | 160679.33 | 16 | wyk
COMMERCIAL | klo12 | 12237846.22 | 9 | klo
RESIDENTL | wo33 | 232024.16 | 58 | wo
COMMERCIAL | bn24 | 3468313.5774 | 163 | bn
COMMERCIAL | lga12 | 9341312.33 | 61 | lga
| msd1 | 16071.3636 | 20 | msd
INDUSTRIAL | ofr24 | 300622.14 | 4 | ofr
INDUSTRIAL | bwn13 | 24333.45 | 4 | bwn
| tt1 | 26786.62 | 3 | tt
INDUSTRIAL | rwt31 | 22449174.23 | 3 | rwt
FARM | mfa14 | 28798.91 | 1 | mfa
| bwr32 | 10607.4826 | 52 | bwr
INDUSTRIAL | wn4 | 1120535.2101 | 54 | wn
RESIDENTL | bwr12 | 975012.274 | 199 | bwr
INDUSTRIAL | wgi24 | 1432383.73 | 33 | wgi
| llg13 | 135285.4952 | 24 | llg
| rwn34 | 10950.9 | 10 | rwn
FARM | elm34 | 16399.68 | 6 | elm
RESIDENTL | ruba12 | 12797333.4035 | 1890 | ruba
COMMERCIAL | hpk22 | 5875279.82 | 181 | hpk
| cln11 | 262675.9461 | 229 | cln
RESIDENTL | cf2 | 494427.3912 | 409 | cf
FARM | elm22 | 15544.2323 | 4 | elm
INDUSTRIAL | smg32 | 67645.78 | 1 | smg
FARM | bwa23 | 3495492.525 | 169 | bwa
NCONUML | phm24 | 66511.6 | 15 | phm
NCONUML | wgi23 | 35701.3 | 15 | wgi
NCONUML | epg35 | 18576.68 | 9 | epg
NCONUML | llg13 | 26801.83 | 12 | llg
LIGHTING | phi13 | 74566.47 | 1 | phi
| ldl24 | 28689.7774 | 48 | ldl
| bge11 | 41147.6131 | 30 | bge
RESIDENTL | ofr21 | 18456788.2346 | 4412 | ofr
INDUSTRIAL | ofr11 | 52339.71 | 6 | ofr
COMMERCIAL | nrn11 | 8254682.48 | 13 | nrn
FARM | moe15 | 1053275.4428 | 126 | moe
INDUSTRIAL | lyd12 | 15947.41 | 3 | lyd
INDUSTRIAL | wt10 | 5540.7 | 1 | wt
RESIDENTL | rwt21 | 965731.93 | 282 | rwt
FARM | wo13 | 51683.13 | 6 | wo
INDUSTRIAL | epg34 | 25722.81 | 2 | epg
COMMERCIAL | lys36 | 31611.41 | 1 | lys
RESIDENTL | wn6 | 17451542.0984 | 3750 | wn
NCONUML | hpk12 | 23613.79 | 7 | hpk
INDUSTRIAL | ruba24 | 189283.4035 | 13 | ruba
| nrn12 | 36108.6 | 9 | nrn
NCONUML | nla32 | 30069.03 | 18 | nla
COMMERCIAL | bm8b31 | 174913.9253 | 14 | bmb
| wo22 | 26321.2427 | 38 | wo
INDUSTRIAL | fgy31 | 4952.61 | 1 | fgy
RESIDENTL | cln14 | 25051991.2109 | 8311 | cln
RESIDENTL | lga24 | 3807672.9803 | 653 | lga
RESIDENTL | bra31 | 2624204.8049 | 649 | bra
COMMERCIAL | cln21 | 7282112.3749 | 104 | cln
COMMERCIAL | ftr23 | 8984637.4811 | 336 | ftr
RESIDENTL | klo13 | 97850.5847 | 89 | klo
INDUSTRIAL | ofr14 | 250.62 | 1 | ofr
FARM | mwl24 | 966080.4815 | 75 | mwl
NCONUML | bdl41 | 86032.0652 | 28 | bdl
INDUSTRIAL | epg13 | 201122.3196 | 20 | epg
COMMERCIAL | tgn23 | 6173474.1124 | 95 | tgn
| moe12 | 11374.0239 | 16 | moe
INDUSTRIAL | drn11 | 8297.91 | 2 | drn
| wn4 | 46461.2191 | 29 | wn
NCONUML | wgl13 | 85005.64 | 23 | wgl
INDUSTRIAL | ftr22 | 264831.3749 | 23 | ftr
NCONUML | mjg11 | 5653.43 | 3 | mjg
RESIDENTL | klo12 | 526.2 | 1 | klo
COMMERCIAL | cln11 | 18408618.7138 | 182 | cln
NCONUML | wo13 | 11132.69 | 4 | wo
COMMERCIAL | yn38 | 28127.08 | 5 | yn
NCONUML | mwl24 | 19701.6 | 5 | mwl
RESIDENTL | wots12 | 7880580.6899 | 1786 | wots
COMMERCIAL | tgn43 | 5598797.62 | 126 | tgn
NCONUML | mfa23 | 6277.17 | 3 | mfa
NCONUML | bra32 | 63005.82 | 38 | bra
FARM | bdl34 | 247623.03 | 51 | bdl
INDUSTRIAL | wn5 | 6299826.69 | 33 | wn
| mby13 | 155.9226 | 1 | mby
FARM | ofr23 | 2419763.5413 | 305 | ofr
NCONUML | cre22 | 86458.6773 | 42 | cre
NCONUML | hpk23 | 84001.53 | 23 | hpk
RESIDENTL | bra24 | 8260262.5707 | 1824 | bra
| cyn14 | 12637.7523 | 26 | cyn
LIGHTING | wgl11 | 2443513.25 | 2 | wgl
NCONUML | wgi24 | 69610.83 | 24 | wgi
COMMERCIAL | klo14 | 11961206.944 | 269 | klo
FARM | drn14 | 379625.3327 | 36 | drn
RESIDENTL | bwr22 | 1941843.629 | 510 | bwr
| llg14 | 42684.6726 | 22 | llg
INDUSTRIAL | drn21 | 709809.96 | 3 | drn
INDUSTRIAL | tgn42 | 199383.97 | 5 | tgn
RESIDENTL | sle32 | 6677118.757 | 1350 | sle
RESIDENTL | myt12 | 14552002.0991 | 2380 | myt
FARM | myt21 | 821475.54 | 124 | myt
| bn11 | 39921.12 | 40 | bn
NCONUML | mby12 | 15769.2 | 4 | mby
NCONUML | bdl44 | 1602.59 | 5 | bdl
COMMERCIAL | tt12 | 10810239.5174 | 467 | tt
NCONUML | wn7 | 7884.6 | 2 | wn
| bdl34 | 14430.17 | 36 | bdl
RESIDENTL | lyd11 | 11014119.7855 | 2574 | lyd
FARM | wyk23 | 2329152.6841 | 202 | wyk
| epg23 | 66262.7623 | 20 | epg
RESIDENTL | rwt32 | 15157646.1346 | 3808 | rwt
RESIDENTL | cre31 | 23125994.5084 | 5990 | cre
FARM | bn11 | 9012293.1298 | 1372 | bn
COMMERCIAL |  | 2470964.7554 | 79 | #REF!
INDUSTRIAL | kms11 | 3849512.37 | 9 | kms
RESIDENTL | sle31 | 15232222.0022 | 4728 | sle
RESIDENTL | myt11 | 3230941.4261 | 365 | myt
| wyk12 | 33744.4845 | 17 | wyk
| lga11 | 13750.1489 | 25 | lga
COMMERCIAL | cre33 | 14716025.8299 | 132 | cre
RESIDENTL | trc01 | 404888.8876 | 85 | trc
| moe25 | 10579.3743 | 23 | moe
NCONUML | msd1 | 8725.66 | 9 | msd
RESIDENTL | mwl14 | 1637810.9082 | 178 | mwl
FARM | wn5 | 10157746.9699 | 1090 | wn
INDUSTRIAL | bwr33 | 13101695.07 | 41 | bwr
NCONUML | ofr24 | 72292.73 | 18 | ofr
| mdg1 | 5594.13 | 4 | mdg
FARM | wgi33 | 86057.74 | 7 | wgi
RESIDENTL | rwt22 | 12512450.4989 | 3066 | rwt
RESIDENTL | cnr2 | 3844076.3719 | 1054 | cnr
| hpk14 | 17565.23 | 35 | hpk
NCONUML | drn23 | 37389.78 | 20 | drn
RESIDENTL | tgn44 | 11943542.7304 | 2804 | tgn
| tgn42 | 0 | 1 | tgn
NCONUML | rwt22 | 27503.296 | 22 | rwt
FARM | mwl16 | 172184.54 | 14 | mwl
COMMERCIAL | nla34 | 1413700.5844 | 93 | nla
| epg22 | 2049.9261 | 2 | epg
FARM | tgn41 | 3728231.4432 | 423 | tgn
COMMERCIAL | lga23 | 3382991.9134 | 119 | lga
NCONUML | sle31 | 61055.23 | 20 | sle
NCONUML | tgn44 | 66469.79 | 20 | tgn
| phm24 | 18272.6834 | 34 | phm
RESIDENTL | hpk11 | 16523367.4098 | 4141 | hpk
| hpk13 | 40054.7485 | 22 | hpk
| bwr24 | 10180.34 | 28 | bwr
COMMERCIAL | bdl33 | 34051046.7333 | 257 | bdl
COMMERCIAL | wt9 | 7035668.1433 | 128 | wt
NCONUML | wt15 | 16005.53 | 14 | wt
FARM | ruba24 | 730484.142 | 55 | ruba
NCONUML | cpk23 | 20021.69 | 18 | cpk
INDUSTRIAL | mwl21 | 320021.87 | 5 | mwl
COMMERCIAL | hpk23 | 12064171.7331 | 206 | hpk
INDUSTRIAL | wt11 | 2563605.84 | 2 | wt
RESIDENTL | wt15 | 8580853.2399 | 1947 | wt
| elm21 | 24345.52 | 16 | elm
INDUSTRIAL | mwl16 | 183545.9668 | 9 | mwl
FARM | rve13 | 9637.99 | 1 | rve
NCONUML | drn22 | 69938.3 | 27 | drn
NCONUML | bdl31 | 70697.58 | 29 | bdl
NCONUML | bwa24 | 1320.25 | 1 | bwa
COMMERCIAL | mwl23 | 10773058.8537 | 154 | mwl
COMMERCIAL | elm23 | 5093994.3825 | 95 | elm
FARM | smr23 | 1078615.6398 | 156 | smr
| cpk11 | 37835.6667 | 47 | cpk
INDUSTRIAL | bra14 | 14750.52 | 4 | bra
RESIDENTL | rwn33 | 5693275.4596 | 1153 | rwn
| bn22 | 41634.09 | 21 | bn
INDUSTRIAL | tt2 | 11531135.8238 | 100 | tt
INDUSTRIAL | wt12 | 3871876.0911 | 67 | wt
INDUSTRIAL | mwl22 | 292678.42 | 8 | mwl
RESIDENTL | bn23 | 8695284.412 | 1665 | bn
COMMERCIAL | cyn11 | 9621618.8569 | 233 | cyn
| cyn21 | 22400.14 | 28 | cyn
INDUSTRIAL | mjg11 | 1321804.29 | 13 | mjg
INDUSTRIAL | cf2 | 1970.494 | 2 | cf
RESIDENTL | tt5 | 6560032.4165 | 1633 | tt
COMMERCIAL | smr14 | 6818307.6657 | 239 | smr
COMMERCIAL | smg33 | 1348313.99 | 14 | smg
RESIDENTL | rwt15 | 11066767.0768 | 2454 | rwt
COMMERCIAL | cre32 | 14440881.1645 | 427 | cre
INDUSTRIAL | smr24 | 4639865.5557 | 45 | smr
COMMERCIAL | fgy23 | 10185283.97 | 98 | fgy
COMMERCIAL | hpk11 | 3476478.711 | 53 | hpk
| cre32 | 19011.64 | 13 | cre
NCONUML | wgl23 | 12760.41 | 6 | wgl
COMMERCIAL | nrn15 | 84419.81 | 3 | nrn
NCONUML | moe15 | 22748.39 | 11 | moe
RESIDENTL | tt12 | 86039.86 | 6 | tt
RESIDENTL | cyn31 | 8632445.7043 | 2077 | cyn
RESIDENTL | wgl24 | 16633542.8094 | 2715 | wgl
COMMERCIAL | wgi22 | 6881286.006 | 159 | wgi
INDUSTRIAL | smr13 | 992080.85 | 26 | smr
NCONUML | cpk12 | 17033.61 | 10 | cpk
NCONUML | ftr21 | 16597.26 | 11 | ftr
FARM | mwl12 | 18529.37 | 2 | mwl
INDUSTRIAL | epg33 | 1129768.4897 | 4 | epg
| wyk13 | 9658.4809 | 15 | wyk
LIGHTING | trc01 | 669938.2281 | 2 | trc
FARM | hpk13 | 2305.94 | 1 | hpk
RESIDENTL | tt6 | 19150788.3328 | 4695 | tt
FARM | tgn31 | 5369095.0164 | 562 | tgn
NCONUML | wgl24 | 11028.97 | 10 | wgl
INDUSTRIAL | brt11 | 82545.9018 | 12 | brt
LIGHTING | mby11 | 10728.24 | 1 | mby
NCONUML | myt21 | 24178.1 | 12 | myt
| wt10 | 6115.9374 | 5 | wt
RESIDENTL | bge12 | 9796026.1467 | 1789 | bge
FARM | myt11 | 2640136.7565 | 257 | myt
NCONUML | cyn11 | 21168.08 | 13 | cyn
INDUSTRIAL |  | 942329979.1078 | 12 | #REF!
INDUSTRIAL | elm34 | 168803.0667 | 15 | elm
| brt22 | 30486.3216 | 18 | brt
INDUSTRIAL | epg11 | 6777.42 | 2 | epg
RESIDENTL | elm34 | 19825611.7814 | 4189 | elm
COMMERCIAL | sle13 | 974523.8832 | 109 | sle
INDUSTRIAL | lga13 | 207007.5439 | 9 | lga
RESIDENTL | mwl23 | 3618535.6291 | 812 | mwl
| fgy14 | 28887.99 | 26 | fgy
COMMERCIAL | mby13 | 2521770.2974 | 71 | mby
| lga12 | 14720.56 | 12 | lga
RESIDENTL | cpk12 | 17343162.547 | 2927 | cpk
COMMERCIAL | wt5 | 19785711.5258 | 118 | wt
INDUSTRIAL | drn24 | 4643890.64 | 3 | drn
FARM | drn21 | 13254.24 | 1 | drn
NCONUML | mwl11 | 360.93 | 3 | mwl
RESIDENTL | epg34 | 15669683.4078 | 3862 | epg
NCONUML | wt10 | 27658.61 | 16 | wt
LIGHTING | rwt14 | 962126.36 | 3 | rwt
COMMERCIAL | drn23 | 5472888.3558 | 161 | drn
LIGHTING | bwn11 | 6340546.01 | 1 | bwn
INDUSTRIAL | sfs1 | 80102.39 | 5 | sfs
COMMERCIAL | phm34 | 4610839.9937 | 66 | phm
COMMERCIAL | mfa31 | 3803351.87 | 100 | mfa
INDUSTRIAL | rwt25 | 2203508.65 | 42 | rwt
| bwa22 | 41045.3074 | 24 | bwa
FARM | smr13 | 139441.5096 | 27 | smr
NCONUML | phi12 | 84007.84 | 24 | phi
| fgy21 | 10377.87 | 9 | fgy
NCONUML | rwt15 | 44056.974 | 28 | rwt
LIGHTING | nla34 | 5187.52 | 1 | nla
RESIDENTL | sfs1 | 6449039.4989 | 958 | sfs
RESIDENTL | msd4 | 16354350.3097 | 2395 | msd
INDUSTRIAL | phm33 | 724516.58 | 21 | phm
COMMERCIAL | wgl14 | 59932538.6 | 1 | wgl
COMMERCIAL | rwt31 | 3904134.109 | 54 | rwt
RESIDENTL | wt5 | 5466545.168 | 1335 | wt
FARM | ftr22 | 3872176.8459 | 271 | ftr
| wn5 | 51237.831 | 23 | wn
INDUSTRIAL | kms12 | 880994.04 | 26 | kms
NCONUML | rwt31 | 27889.28 | 18 | rwt
RESIDENTL | elm22 | 20622579.4478 | 3120 | elm
| bn24 | 7126.586 | 9 | bn
FARM | wots11 | 7572710.4051 | 689 | wots
INDUSTRIAL | myt11 | 122662.09 | 11 | myt
NCONUML | bdl32 | 81716.25 | 38 | bdl
NCONUML | cyn33 | 39860.39 | 20 | cyn
| lga13 | 7900.07 | 12 | lga
COMMERCIAL | wn7 | 705796.26 | 31 | wn
RESIDENTL | tgn23 | 12995258.1614 | 2157 | tgn
RESIDENTL | wgl12 | 18309192.1093 | 3011 | wgl
NCONUML | drn14 | 58816.42 | 20 | drn
INDUSTRIAL | tt9 | 1853761.73 | 4 | tt
RESIDENTL | kms12 | 23913269.0041 | 4277 | kms
COMMERCIAL | wgi33 | 13737748.8552 | 364 | wgi
COMMERCIAL | phm21 | 28428865.0993 | 838 | phm
FARM | sle32 | 5441049.7096 | 310 | sle
NCONUML | cyn32 | 58907.16 | 38 | cyn
INDUSTRIAL | msd2 | 165834.72 | 18 | msd
COMMERCIAL | bwr23 | 26845428.111 | 233 | bwr
RESIDENTL | msd2 | 5810770.2828 | 1153 | msd
FARM | klk11 | 2014936.8264 | 177 | klk
| wots12 | 13459.1171 | 22 | wots
INDUSTRIAL | rwn24 | 4339629.96 | 13 | rwn
INDUSTRIAL | tgn41 | 1853911.3546 | 62 | tgn
COMMERCIAL | smg32 | 6595824.87 | 22 | smg
| wgi34 | 86239.94 | 15 | wgi
RESIDENTL | bn22 | 13286130.4589 | 3118 | bn
RESIDENTL | mfa31 | 9237847.4317 | 2206 | mfa
COMMERCIAL | wgi34 | 9571334.08 | 60 | wgi
RESIDENTL | mdi1 | 176577.17 | 31 | mdi
NCONUML | rwn31 | 16738.19 | 15 | rwn
INDUSTRIAL | drn13 | 239296.9 | 11 | drn
INDUSTRIAL | bdl43 | 306419.52 | 21 | bdl
NCONUML | wo23 | 56204.51 | 16 | wo
COMMERCIAL | ftr21 | 2804675.8206 | 100 | ftr
COMMERCIAL | bwa23 | 206762.2501 | 23 | bwa
NCONUML | mfa21 | 28416.84 | 12 | mfa
| cln23 | 52144.7804 | 85 | cln
RESIDENTL | rve11 | 2276471.0008 | 508 | rve
COMMERCIAL | ofr24 | 6649904.8426 | 113 | ofr
NCONUML | phi13 | 105028.33 | 33 | phi
FARM | smg22 | 25054.15 | 4 | smg
FARM | bwn11 | 18419.1 | 1 | bwn
INDUSTRIAL | epg31 | 360181.3871 | 31 | epg
COMMERCIAL | fgy14 | 7872993.2117 | 231 | fgy
| ldl11 | 24480.7 | 22 | ldl
INDUSTRIAL | wgl24 | 939120.3004 | 39 | wgl
| phm22 | 31542.7748 | 10 | phm
COMMERCIAL | moe15 | 2469270.3666 | 172 | moe
| cnr3 | 100.0469 | 1 | cnr
RESIDENTL | bwn12 | 4456239.3509 | 1013 | bwn
COMMERCIAL | mwl24 | 5791496.4979 | 78 | mwl
COMMERCIAL | wo13 | 2493976.37 | 46 | wo
RESIDENTL | elm25 | 10534980.5572 | 2009 | elm
RESIDENTL | phm32 | 14466986.7977 | 3288 | phm
COMMERCIAL | ofr11 | 14130002.2904 | 224 | ofr
INDUSTRIAL | bge13 | 1057475.88 | 11 | bge
RESIDENTL | ofr22 | 7907197.5875 | 2174 | ofr
INDUSTRIAL | lga22 | 745287.81 | 44 | lga
FARM | hpk22 | 33600.65 | 5 | hpk
COMMERCIAL | epg23 | 63543126.9632 | 711 | epg
NCONUML | epg34 | 29379.47 | 21 | epg
| mwl23 | 14018.9088 | 10 | mwl
FARM | lyd14 | 350081.37 | 31 | lyd
| elm33 | 18371.0537 | 30 | elm
RESIDENTL | bwn11 | 14758921.2622 | 2984 | bwn
| cyn33 | 33636.86 | 37 | cyn
INDUSTRIAL | ldl13 | 1566146.5513 | 31 | ldl
NCONUML | smg32 | 19512.15 | 10 | smg
NCONUML | lga21 | 24931.49 | 9 | lga
RESIDENTL | mfa34 | 6438005.323 | 995 | mfa
COMMERCIAL | lga22 | 10229963.6597 | 340 | lga
COMMERCIAL | wgi31 | 4363035.5887 | 128 | wgi
| wt9 | 17175.83 | 21 | wt
INDUSTRIAL | mfa21 | 1292894.4886 | 57 | mfa
FARM | wgi32 | 343056.5273 | 19 | wgi
COMMERCIAL | bge21 | 44944.8 | 1 | bge
INDUSTRIAL | elm26 | 46289.86 | 5 | elm
NCONUML | msd4 | 12187.83 | 6 | msd
COMMERCIAL | bra21 | 14789918.5926 | 289 | bra
| cpk22 | 7305.07 | 12 | cpk
NCONUML | phm32 | 76324.09 | 20 | phm
NCONUML | sfs1 | 44865.78 | 10 | sfs
COMMERCIAL | lyd13 | 6072257.17 | 42 | lyd
FARM | cyn33 | 36456.98 | 4 | cyn
NCONUML | phm21 | 71428.0533 | 24 | phm
COMMERCIAL | sle32 | 5434267.6149 | 190 | sle
NCONUML | smg31 | 21751.86 | 17 | smg
NCONUML | wots11 | 25057.91 | 11 | wots
RESIDENTL | tgn43 | 15724147.9465 | 3608 | tgn
INDUSTRIAL | cyn21 | 9259443.95 | 23 | cyn
INDUSTRIAL | bn23 | 1923467.13 | 19 | bn
NCONUML | nrn14 | 79150.17 | 17 | nrn
NCONUML | cyn22 | 32483.16 | 10 | cyn
NCONUML | wgl12 | 47271.49 | 20 | wgl
COMMERCIAL | phm24 | 600129.57 | 25 | phm
NCONUML | lga11 | 25837.14 | 8 | lga
NCONUML | tgn41 | 7415.11 | 5 | tgn
RESIDENTL | wgl11 | 17118670.1537 | 3818 | wgl
RESIDENTL | wots11 | 15871220.8415 | 2910 | wots
| rwn31 | 40233.5106 | 27 | rwn
COMMERCIAL | elm32 | 8171019.0636 | 263 | elm
FARM | mby11 | 1335559.7721 | 187 | mby
INDUSTRIAL | mwl25 | 33119.15 | 8 | mwl
FARM | rwn26 | 5055.63 | 2 | rwn
| nla34 | 8234.98 | 10 | nla
RESIDENTL |  | 349105.8277 | 492 | #REF!
FARM | epg13 | 82815.8863 | 12 | epg
| wyk24 | 32167.14 | 30 | wyk
FARM | sle11 | 16862.17 | 6 | sle
COMMERCIAL | bm8b33 | 3349.12 | 2 | bmb
RESIDENTL | smg21 | 17914575.4009 | 3718 | smg
INDUSTRIAL | bdl42 | 622534.62 | 24 | bdl
| yn38 | 7519.7419 | 1 | yn
| phi13 | 28221.5917 | 27 | phi
| epg14 | 9258.9052 | 38 | epg
FARM | nla31 | 1791184.5035 | 140 | nla
INDUSTRIAL | wgi33 | 1188063.8119 | 37 | wgi
LIGHTING | phm33 | 4303153.65 | 2 | phm
RESIDENTL | phm33 | 12878778.4238 | 2134 | phm
COMMERCIAL | wgl23 | 3870974.8784 | 252 | wgl
NCONUML | wt5 | 58508.56 | 14 | wt
NCONUML | bwn14 | 81385.02 | 37 | bwn
NCONUML | mfa31 | 49958.93 | 14 | mfa
COMMERCIAL | bra12 | 23355928.37 | 122 | bra
NCONUML | wt13 | 98966.19 | 41 | wt
COMMERCIAL | klo24 | 13267963.2484 | 244 | klo
COMMERCIAL | bge12 | 6262328.83 | 64 | bge
COMMERCIAL | wn4 | 10511680.2174 | 332 | wn
INDUSTRIAL | tt6 | 2940006.87 | 14 | tt
FARM | cln13 | 4519.0334 | 1 | cln
RESIDENTL | bwa23 | 1839261.5711 | 259 | bwa
RESIDENTL | smr12 | 601661.7559 | 102 | smr
NCONUML | bra31 | 17155.48 | 11 | bra
FARM | cln22 | 84599.56 | 6 | cln
RESIDENTL | moe23 | 10757204.18 | 1872 | moe
FARM | bn23 | 4995698.9571 | 709 | bn
INDUSTRIAL | bwr12 | 7576207.2428 | 317 | bwr
COMMERCIAL | elm33 | 8652520.7547 | 229 | elm
RESIDENTL | tgn12 | 769554.192 | 239 | tgn
NCONUML | bn23 | 5729.17 | 9 | bn
| cyn11 | 35169.6447 | 13 | cyn
INDUSTRIAL | wots12 | 5742170.47 | 22 | wots
INDUSTRIAL | llg12 | 8080777.31 | 18 | llg
NCONUML | ofr14 | 11958.45 | 3 | ofr
RESIDENTL | rwn34 | 11161403.5989 | 1490 | rwn
RESIDENTL | fgy12 | 975691.3435 | 398 | fgy
COMMERCIAL | wyk24 | 11852940.7836 | 290 | wyk
COMMERCIAL | smr12 | 1199230.8 | 20 | smr
INDUSTRIAL | wgl11 | 590499.13 | 17 | wgl
INDUSTRIAL | moe13 | 8896507.14 | 13 | moe
INDUSTRIAL | wots11 | 14616083.73 | 22 | wots
NCONUML | epg13 | 4325.18 | 2 | epg
NCONUML | bn22 | 72789.04 | 38 | bn
RESIDENTL | bwr23 | 15381612.1105 | 3589 | bwr
NCONUML | cln13 | 19538.3161 | 10 | cln
COMMERCIAL | bwa24 | 4350900.07 | 4 | bwa
COMMERCIAL | bwr32 | 11258727.4704 | 251 | bwr
RESIDENTL | bra32 | 8710928.5985 | 2041 | bra
FARM | klo14 | 681766.459 | 92 | klo
INDUSTRIAL | tt7 | 9353368.9205 | 125 | tt
RESIDENTL | wo11 | 815896.564 | 156 | wo
LIGHTING | mwl24 | 803944.3 | 2 | mwl
COMMERCIAL | bwr24 | 7860784.794 | 262 | bwr
COMMERCIAL | drn14 | 5284276.4061 | 147 | drn
NCONUML | hpk24 | 27055.52 | 10 | hpk
| cyn32 | 34865.18 | 48 | cyn
| bra23 | 7974.72 | 25 | bra
RESIDENTL | rve13 | 16767421.4281 | 3587 | rve
COMMERCIAL | bwn13 | 11531398.8601 | 263 | bwn
FARM | cln23 | 76487.94 | 5 | cln
NCONUML | ruba24 | 1482.28 | 4 | ruba
COMMERCIAL | msd1 | 4448954.738 | 126 | msd
| phm31 | 2299.25 | 4 | phm
LIGHTING | wn1 | 677520.74 | 1 | wn
COMMERCIAL | wt8 | 2125517.5597 | 71 | wt
RESIDENTL | bdl33 | 5101200.3632 | 906 | bdl
COMMERCIAL | rwt21 | 33203170.5825 | 281 | rwt
FARM |  | 15223.9488 | 53 | #REF!
| fgy13 | 16173.63 | 19 | fgy
| wt11 | 14907.843 | 20 | wt
RESIDENTL | mwl24 | 4259131.5949 | 729 | mwl
INDUSTRIAL | bwn12 | 375603.57 | 33 | bwn
| lyd12 | 10355.6 | 16 | lyd
| lyd13 | 31235.27 | 24 | lyd
| elm32 | 28931.8643 | 22 | elm
RESIDENTL | ldl13 | 20183081.1078 | 3515 | ldl
COMMERCIAL | epg14 | 4722560.1631 | 66 | epg
FARM | epg32 | 616929.8369 | 16 | epg
| smg23 | 6841.4304 | 12 | smg
NCONUML | mwl16 | 31954.29 | 10 | mwl
COMMERCIAL | ofr22 | 3955299.41 | 63 | ofr
FARM | wgl24 | 9990463.449 | 886 | wgl
COMMERCIAL | llg14 | 8402501.0583 | 280 | llg
COMMERCIAL | wgi24 | 3234685.3433 | 136 | wgi
FARM | cnr3 | 47812.597 | 17 | cnr
| epg33 | 55263.0616 | 6 | epg
INDUSTRIAL | bra24 | 1115020.317 | 14 | bra
NCONUML | wgi33 | 84992.31 | 23 | wgi
FARM | rwt15 | 1849.17 | 1 | rwt
RESIDENTL | ldl12 | 620798.3677 | 119 | ldl
INDUSTRIAL | bwr22 | 8606432.4227 | 334 | bwr
FARM | cf2 | 2033.193 | 1 | cf
NCONUML | klo14 | 36515.49 | 28 | klo
INDUSTRIAL | trc01 | 31629.57 | 2 | trc
RESIDENTL | lga21 | 9412760.8279 | 1623 | lga
RESIDENTL | wt13 | 15834142.0313 | 3223 | wt
RESIDENTL | cyn13 | 3260017.5153 | 858 | cyn
INDUSTRIAL | ofr21 | 138382.59 | 9 | ofr
NCONUML | sle32 | 22407.43 | 13 | sle
COMMERCIAL | lyd12 | 210380 | 9 | lyd
NCONUML | wyk23 | 87622.06 | 45 | wyk
| fgy33 | 11652.67 | 18 | fgy
INDUSTRIAL | hpk22 | 98414.21 | 14 | hpk
NCONUML | sle11 | 59204.61 | 19 | sle
RESIDENTL | bwr13 | 20902397.8318 | 4170 | bwr
COMMERCIAL | rwn34 | 3999387.7688 | 144 | rwn
| hpk22 | 19671.58 | 41 | hpk
FARM | klk22 | 332413.14 | 10 | klk
INDUSTRIAL | wn1 | 2988984.92 | 20 | wn
NCONUML | rwn26 | 27156.61 | 25 | rwn
| bwr33 | 13120.641 | 3 | bwr
NCONUML | mby11 | 20114.34 | 7 | mby
RESIDENTL | smg33 | 11198068.0634 | 2626 | smg
FARM | bn12 | 813334.585 | 146 | bn
FARM | bdl32 | 1026406.0127 | 170 | bdl
FARM | drn24 | 15422429 | 2 | drn
LIGHTING | cre21 | 378603.77 | 3 | cre
RESIDENTL | smg32 | 834640.09 | 219 | smg
| wt12 | 39199.7023 | 19 | wt
FARM | bwn14 | 804408.7 | 76 | bwn
NCONUML | bwr33 | 16865.43 | 3 | bwr
INDUSTRIAL | rwn22 | 12871.85 | 4 | rwn
NCONUML | drn11 | 63307.01 | 20 | drn
INDUSTRIAL | mwl13 | 228128.43 | 11 | mwl
COMMERCIAL | elm22 | 6567142.5918 | 154 | elm
FARM | trc01 | 521142.3328 | 100 | trc
COMMERCIAL | rwt14 | 11855990.576 | 301 | rwt
INDUSTRIAL | sle14 | 1780526.4437 | 64 | sle
RESIDENTL | smr24 | 17064871.7804 | 2952 | smr
FARM | bwa22 | 1586063.9755 | 254 | bwa
NCONUML | tt4 | 37478.54 | 17 | tt
| tt9 | 28146.8116 | 74 | tt
COMMERCIAL | epg34 | 4040655.8363 | 65 | epg
FARM | nrn11 | 7816.07 | 2 | nrn
LIGHTING | cpk23 | 1632459.3 | 1 | cpk
RESIDENTL | fgy31 | 4476808.4262 | 913 | fgy
COMMERCIAL | fgy33 | 6399813.6929 | 132 | fgy
| cnr2 | 20535.9245 | 15 | cnr
INDUSTRIAL | sle32 | 10933678.58 | 25 | sle
| bra13 | 120577.89 | 18 | bra
RESIDENTL | wgi23 | 12118480.0079 | 2685 | wgi
INDUSTRIAL | wn6 | 922850.6842 | 19 | wn
LIGHTING | tgn44 | 752.53 | 1 | tgn
RESIDENTL | wt8 | 8250779.9392 | 1851 | wt
COMMERCIAL | moe25 | 5695010.3572 | 176 | moe
FARM | wgi34 | 4315044.5216 | 374 | wgi
INDUSTRIAL | fgy32 | 667572.7217 | 61 | fgy
NCONUML | wo32 | 55386.46 | 14 | wo
INDUSTRIAL | lys36 | 1267258.48 | 1 | lys
| bn12 | 10728.35 | 13 | bn
NCONUML | brt11 | 10828.27 | 7 | brt
| drn21 | 27694.76 | 39 | drn
| drn24 | 16030.7 | 26 | drn
RESIDENTL | cpk23 | 11646034.7633 | 2466 | cpk
RESIDENTL | wots13 | 7948103.7952 | 1344 | wots
FARM | wgl23 | 3908847.1376 | 390 | wgl
COMMERCIAL | wyk13 | 4417313.7071 | 191 | wyk
NCONUML | klk21 | 10664.54 | 6 | klk
INDUSTRIAL | smg22 | 31514.93 | 2 | smg
RESIDENTL | wgi22 | 12719214.8315 | 3088 | wgi
| cpk13 | 49314.0333 | 41 | cpk
COMMERCIAL | bdl41 | 11311068.2286 | 367 | bdl
NCONUML | nrn12 | 43208.48 | 18 | nrn
RESIDENTL | fgy23 | 5177398.3937 | 1023 | fgy
NCONUML | brt21 | 3240.29 | 5 | brt
NCONUML | tgn31 | 2100.01 | 7 | tgn
RESIDENTL | mjg11 | 6256821.3625 | 1064 | mjg
INDUSTRIAL | lga24 | 175905.212 | 21 | lga
COMMERCIAL | moe21 | 6644337.36 | 291 | moe
INDUSTRIAL | bwn14 | 326743.47 | 17 | bwn
INDUSTRIAL | phm22 | 15545673.5732 | 29 | phm
LIGHTING | klo24 | 2201282.63 | 3 | klo
FARM | epg12 | 13782.33 | 2 | epg
INDUSTRIAL | cln14 | 247.5387 | 1 | cln
FARM | bge13 | 383352.554 | 75 | bge
NCONUML | bra14 | 25509.54 | 26 | bra
RESIDENTL | fgy24 | 17189073.2659 | 3574 | fgy
NCONUML | lyd14 | 37348.84 | 18 | lyd
FARM | fgy21 | 91303 | 9 | fgy
INDUSTRIAL | elm24 | 6476.78 | 2 | elm
FARM | bra24 | 985.88 | 1 | bra
COMMERCIAL | ldl24 | 1420329.0926 | 55 | ldl
INDUSTRIAL | wots24 | 329358.8434 | 32 | wots
| moe13 | 6325.43 | 5 | moe
COMMERCIAL | cyn14 | 5422735.5047 | 221 | cyn
LIGHTING | smg21 | 4640189.26 | 4 | smg
COMMERCIAL | tgn42 | 24454733.755 | 420 | tgn
INDUSTRIAL | lga14 | 502652.15 | 16 | lga
INDUSTRIAL | cre33 | 377497.19 | 17 | cre
FARM | ldl11 | 223383.36 | 16 | ldl
INDUSTRIAL | bn24 | 28582582.13 | 34 | bn
COMMERCIAL | tt1 | 14308038.8686 | 155 | tt
| wn3 | 30735.58 | 33 | wn
NCONUML | ldl21 | 10778.31 | 7 | ldl
NCONUML | wt6 | 188781.23 | 35 | wt
RESIDENTL | elm23 | 20356024.4153 | 3325 | elm
COMMERCIAL | drn11 | 4003224.2127 | 79 | drn
COMMERCIAL | bra34 | 7850026.49 | 9 | bra
FARM | cyn32 | 3133.97 | 2 | cyn
FARM | cpk23 | 18946.87 | 2 | cpk
FARM | wt15 | 5251.96 | 1 | wt
NCONUML | wgi32 | 95036.63 | 31 | wgi
COMMERCIAL | phm32 | 13343791.1884 | 221 | phm
COMMERCIAL | epg22 | 38007492.3668 | 89 | epg
INDUSTRIAL | wgl15 | 1553419.6108 | 26 | wgl
FARM | phm33 | 7138587.5126 | 545 | phm
LIGHTING | bra32 | 1301740.84 | 1 | bra
COMMERCIAL | bra22 | 30448240 | 1 | bra
COMMERCIAL | msd4 | 11090376.2999 | 395 | msd
COMMERCIAL | lyd14 | 7038791.6959 | 51 | lyd
| phi12 | 701365.4285 | 34 | phi
| nrn11 | 5120.38 | 9 | nrn
INDUSTRIAL | smg21 | 777155.28 | 5 | smg
NCONUML | nla31 | 5002.08 | 5 | nla
RESIDENTL | wyk13 | 19583843.7522 | 3346 | wyk
RESIDENTL | tgn41 | 6800482.2089 | 1104 | tgn
COMMERCIAL | fgy34 | 7285642.6158 | 201 | fgy
FARM | wgl11 | 5210774.8775 | 355 | wgl
FARM | tgn11 | 616949.6887 | 82 | tgn
NCONUML | wn5 | 5268.61 | 9 | wn
NCONUML | bdl42 | 6088.6 | 9 | bdl
INDUSTRIAL | hpk23 | 515987.93 | 6 | hpk
FARM | tgn44 | 47621.17 | 6 | tgn
| smr13 | 35140.976 | 19 | smr
| wgi31 | 18377.08 | 37 | wgi
NCONUML | bwr34 | 85519.21 | 30 | bwr
| bdl32 | 24365.9844 | 40 | bdl
COMMERCIAL | fgy13 | 5672167.28 | 57 | fgy
INDUSTRIAL | sle31 | 621920.2305 | 85 | sle
NCONUML | cyn23 | 72679.67 | 24 | cyn
NCONUML | hpk22 | 92149.17 | 38 | hpk
RESIDENTL | cre23 | 13902510.3441 | 3180 | cre
COMMERCIAL | lga21 | 4415159.211 | 179 | lga
| cre33 | 51988.0123 | 70 | cre
INDUSTRIAL | bra32 | 800790.5812 | 33 | bra
| rwn26 | 43959.1499 | 36 | rwn
NCONUML | ftr22 | 27457.1971 | 11 | ftr
FARM | cyn23 | 28738.28 | 3 | cyn
FARM | wn2 | 2722540.844 | 262 | wn
FARM | wots25 | 1192605.1156 | 155 | wots
COMMERCIAL | lga11 | 2601951.4442 | 115 | lga
COMMERCIAL | cnr1 | 836269.15 | 40 | cnr
RESIDENTL | cre22 | 15737441.9951 | 3931 | cre
RESIDENTL | cyn24 | 3227627.7482 | 729 | cyn
| drn14 | 42739.5968 | 43 | drn
NCONUML | wgi34 | 240.62 | 2 | wgi
COMMERCIAL | mdi1 | 200221.43 | 4 | mdi
LIGHTING | lga22 | 290997.27 | 1 | lga
RESIDENTL | sle13 | 2426821.6594 | 1643 | sle
RESIDENTL | mby12 | 3267894.3821 | 609 | mby
FARM | wgi31 | 368672.79 | 43 | wgi
INDUSTRIAL | cyn24 | 15644182.2427 | 207 | cyn
| fgy34 | 3433.61 | 11 | fgy
RESIDENTL | bge11 | 15368827.4604 | 2654 | bge
RESIDENTL | ftr12 | 3825364.7454 | 636 | ftr
| mfa21 | 17049.39 | 26 | mfa
COMMERCIAL | wgi21 | 45541.7604 | 2 | wgi
INDUSTRIAL | wo14 | 2975508 | 24 | wo
COMMERCIAL | wgl12 | 5759083.9004 | 210 | wgl
INDUSTRIAL | moe23 | 765740.5661 | 26 | moe
COMMERCIAL | hpk14 | 5487941.7 | 85 | hpk
NCONUML | tt2 | 10017.24 | 3 | tt
INDUSTRIAL | cpk13 | 1507420.269 | 6 | cpk
INDUSTRIAL | lga41 | 52440142.6 | 1 | lga
NCONUML | elm26 | 60173.53 | 25 | elm
FARM | cf1 | 12492.747 | 1 | cf
RESIDENTL | bwr32 | 11435795.4629 | 2903 | bwr
NCONUML | cln23 | 19017.15 | 5 | cln
RESIDENTL | bdl41 | 18711766.0554 | 3582 | bdl
RESIDENTL | tt4 | 9918702.5206 | 2673 | tt
NCONUML | nrn13 | 44749.68 | 14 | nrn
NCONUML | mwl12 | 43601.75 | 11 | mwl
FARM | cln12 | 30466.72 | 1 | cln
INDUSTRIAL | cpk21 | 122110.94 | 5 | cpk
NCONUML | epg11 | 2275 | 2 | epg
FARM | brt22 | 1064314.9433 | 146 | brt
NCONUML | moe21 | 60919.67 | 15 | moe
RESIDENTL | ldl22 | 4948357.507 | 1104 | ldl
INDUSTRIAL | epg22 | 206880.17 | 13 | epg
NCONUML | cln12 | 55224.6632 | 17 | cln
| wo14 | 16653.0726 | 14 | wo
INDUSTRIAL | wo13 | 14774006.15 | 3 | wo
INDUSTRIAL | wgi22 | 729700.7 | 28 | wgi
COMMERCIAL | msd2 | 2629949.014 | 87 | msd
NCONUML | ldl22 | 11421.24 | 5 | ldl
RESIDENTL | wo22 | 17812297.6729 | 4125 | wo
FARM | mwl25 | 2028215.2676 | 224 | mwl
| cln14 | 46492.03 | 68 | cln
INDUSTRIAL | smr14 | 413387.45 | 34 | smr
FARM | rwn33 | 39914.72 | 5 | rwn
NCONUML | tt7 | 28203.83 | 11 | tt
INDUSTRIAL | lga11 | 317451.8284 | 16 | lga
INDUSTRIAL | tt12 | 6074893.6495 | 86 | tt
INDUSTRIAL | rwn32 | 87972.96 | 1 | rwn
RESIDENTL | myt21 | 10899844.0445 | 1487 | myt
RESIDENTL | cyn14 | 9596207.6734 | 2758 | cyn
RESIDENTL | kms11 | 9874885.3712 | 1972 | kms
COMMERCIAL | wo32 | 9961950.2687 | 147 | wo
NCONUML | hpk21 | 96497.83 | 40 | hpk
FARM | mwl13 | 248036.6173 | 7 | mwl
RESIDENTL | smr23 | 3447913.5369 | 523 | smr
INDUSTRIAL | nla32 | 1443086.18 | 25 | nla
| rwt32 | 35174.87 | 36 | rwt
INDUSTRIAL | moe11 | 65970.59 | 6 | moe
INDUSTRIAL | wo33 | 33298223.9508 | 7 | wo
INDUSTRIAL | bra31 | 2919.84 | 1 | bra
RESIDENTL | moe15 | 9740983.6859 | 1552 | moe
RESIDENTL | moe12 | 4538532.291 | 887 | moe
INDUSTRIAL | bdl41 | 1328921.5447 | 34 | bdl
NCONUML | tt6 | 36560.52 | 20 | tt
RESIDENTL | uwy1 | 6496143.3356 | 1032 | uwy
RESIDENTL | wgi32 | 16438958.2366 | 3917 | wgi
COMMERCIAL | rwn31 | 2125446.8547 | 72 | rwn
| ldl13 | 45979.2126 | 34 | ldl
LIGHTING | hpk23 | 2010173.36 | 1 | hpk
RESIDENTL | fgy14 | 9703108.5669 | 2483 | fgy
FARM | rwn24 | 30208.83 | 4 | rwn
COMMERCIAL | wo23 | 11409957.4027 | 304 | wo
| myt12 | 115131.3847 | 34 | myt
| bge13 | 13458.3255 | 19 | bge
| sle32 | 15918.6359 | 20 | sle
FARM | epg11 | 14625.27 | 2 | epg
NCONUML | mwl21 | 34561.25 | 17 | mwl
COMMERCIAL | nrn12 | 21654160.6835 | 271 | nrn
COMMERCIAL | llg13 | 15983000.2277 | 99 | llg
| lga22 | 14116.8478 | 12 | lga
FARM | hpk11 | 14620.89 | 5 | hpk
RESIDENTL | ofr11 | 25072251.243 | 5672 | ofr
FARM | ftr12 | 9732520.1395 | 879 | ftr
RESIDENTL | epg21 | 580054.4394 | 151 | epg
FARM | bge22 | 343097.1961 | 60 | bge
COMMERCIAL | sfs1 | 1879673.1771 | 124 | sfs
| cln24 | 61460.6675 | 37 | cln
NCONUML | smg22 | 48204.28 | 25 | smg
RESIDENTL | phm34 | 11301839.7716 | 2904 | phm
RESIDENTL | phm31 | 2762476.4376 | 550 | phm
NCONUML | smr13 | 69764.68 | 26 | smr
RESIDENTL | wyk12 | 12357178.5976 | 1789 | wyk
INDUSTRIAL | sle13 | 125251.914 | 47 | sle
FARM | phm24 | 689286.43 | 52 | phm
| cre31 | 63798.4484 | 85 | cre
INDUSTRIAL | bge12 | 121322.77 | 7 | bge
FARM | wots12 | 5076.62 | 1 | wots
NCONUML | cf1 | 1922.85 | 2 | cf
RESIDENTL | wo31 | 20016820.444 | 4554 | wo
FARM | smr22 | 1275801.32 | 154 | smr
FARM | lga22 | 1443457.6222 | 105 | lga
COMMERCIAL | mwl22 | 10003347.9587 | 192 | mwl
FARM | bn24 | 2239563.0749 | 370 | bn
NCONUML | wots25 | 45798.68 | 13 | wots
NCONUML | wgi31 | 79233.36 | 21 | wgi
FARM | epg23 | 30049.96 | 2 | epg
NCONUML | klk11 | 24723.1 | 13 | klk
| mwl14 | 3593.32 | 2 | mwl
RESIDENTL | mdg1 | 4384126.608 | 684 | mdg
RESIDENTL | nrn14 | 9562152.1887 | 1877 | nrn
LIGHTING | msd4 | 139319.89 | 1 | msd
LIGHTING | sfs1 | 1558457.9 | 1 | sfs
| klo14 | 120043.1087 | 185 | klo
RESIDENTL | hpk14 | 17025183.7337 | 3944 | hpk
FARM | lga12 | 4046898.7707 | 351 | lga
COMMERCIAL | ldl14 | 12475957.7156 | 266 | ldl
RESIDENTL | bn11 | 14382992.5485 | 2912 | bn
COMMERCIAL | bdl34 | 6213094.4744 | 204 | bdl
FARM | lyd11 | 23799.7 | 3 | lyd
| mwl22 | 10189.434 | 23 | mwl
NCONUML | cf2 | 120.31 | 1 | cf
| epg32 | 18473.04 | 31 | epg
RESIDENTL | bdl34 | 21922135.2151 | 5106 | bdl
COMMERCIAL | rwn26 | 3719056.4225 | 81 | rwn
INDUSTRIAL | mby13 | 219583.33 | 2 | mby
NCONUML | fgy33 | 40029.49 | 14 | fgy
| ftr22 | 13372.1897 | 14 | ftr
NCONUML | mwl13 | 53127.87 | 17 | mwl
INDUSTRIAL | rwt32 | 132361.99 | 4 | rwt
COMMERCIAL | phm23 | 17053480.4 | 2 | phm
COMMERCIAL | bra13 | 19208526.3529 | 181 | bra
FARM | wn1 | 37241.96 | 7 | wn
FARM | bm8b33 | 1540.9 | 2 | bmb
COMMERCIAL | wt10 | 13883699.3972 | 155 | wt
INDUSTRIAL | uwy1 | 90405.23 | 3 | uwy
RESIDENTL | ldl23 | 26005181.5029 | 4084 | ldl
FARM | klo24 | 194259.84 | 22 | klo
| hpk11 | 33718.6052 | 42 | hpk
NCONUML | phm33 | 47915.862 | 19 | phm
FARM | wn6 | 4543418.3442 | 605 | wn
COMMERCIAL | cyn21 | 3633643.5973 | 195 | cyn
INDUSTRIAL | wo22 | 393144.5 | 11 | wo
RESIDENTL | tgn42 | 795534.2193 | 223 | tgn
INDUSTRIAL | mwl23 | 715134.0252 | 54 | mwl
| rwt22 | 26934.55 | 52 | rwt
COMMERCIAL | phm31 | 4117822.4369 | 32 | phm
RESIDENTL | epg22 | 39578.43 | 14 | epg
RESIDENTL | nla32 | 6559402.1513 | 1220 | nla
RESIDENTL | myt22 | 1017937.6841 | 120 | myt
| wgl15 | 30619.4 | 19 | wgl
LIGHTING | mjg11 | 68938.73 | 1 | mjg
COMMERCIAL | phi12 | 2400712.314 | 73 | phi
COMMERCIAL | rwt36 | 2264519.95 | 43 | rwt
INDUSTRIAL | wgi23 | 157973.74 | 15 | wgi
NCONUML | elm24 | 74942.52 | 25 | elm
RESIDENTL | wt10 | 3332972.5881 | 860 | wt
NCONUML | ruba22 | 360.93 | 3 | ruba
FARM | phi11 | 82538.05 | 19 | phi
| bra11 | 11169.2884 | 32 | bra
INDUSTRIAL | moe15 | 1465208.8927 | 46 | moe
| tt5 | 13084.5535 | 33 | tt
LIGHTING | elm34 | 2971413.79 | 6 | elm
FARM | rwt25 | 33966.32 | 4 | rwt
RESIDENTL | moe11 | 9711471.9521 | 1967 | moe
INDUSTRIAL | rwt22 | 12240.297 | 2 | rwt
FARM | tgn23 | 1979366.6929 | 215 | tgn
COMMERCIAL | elm34 | 4840398.0166 | 153 | elm
NCONUML | phi11 | 19831.48 | 5 | phi
NCONUML | bra13 | 31922.03 | 14 | bra
RESIDENTL | mwl11 | 7113484.1589 | 1047 | mwl
| sle14 | 9929.5555 | 28 | sle
COMMERCIAL | cpk11 | 7316179.79 | 51 | cpk
| cyn31 | 5192.9 | 11 | cyn
NCONUML | epg12 | 1563.57 | 9 | epg
| epg11 | 4794.77 | 9 | epg
INDUSTRIAL | bwa23 | 17470876.21 | 8 | bwa
FARM | cln21 | 792.83 | 1 | cln
COMMERCIAL | wn3 | 8489705.5245 | 275 | wn
COMMERCIAL | bwn12 | 29123057.9665 | 274 | bwn
NCONUML | bra23 | 28962.5293 | 21 | bra
| bge12 | 5967.8256 | 14 | bge
INDUSTRIAL | tgn12 | 464065.58 | 15 | tgn
LIGHTING | fgy31 | 1047083.29 | 1 | fgy
NCONUML | moe25 | 63582.44 | 18 | moe
NCONUML | fgy21 | 30728.13 | 12 | fgy
INDUSTRIAL | lyd11 | 151654.68 | 9 | lyd
FARM | bwn13 | 5960.02 | 1 | bwn
RESIDENTL | lga11 | 6965787.8425 | 1044 | lga
NCONUML | bwr22 | 31744.79 | 14 | bwr
COMMERCIAL | llg12 | 3977405.3306 | 115 | llg
COMMERCIAL | mfa21 | 3716072.0048 | 197 | mfa
INDUSTRIAL | phm32 | 1008.48 | 1 | phm
COMMERCIAL | nrn13 | 3605622.38 | 41 | nrn
FARM | cyn22 | 1131.4275 | 1 | cyn
INDUSTRIAL | ftr23 | 1828762.8842 | 76 | ftr
INDUSTRIAL | mfa31 | 463955.39 | 14 | mfa
INDUSTRIAL | bge11 | 395339.98 | 10 | bge
RESIDENTL | wo13 | 2691801.805 | 586 | wo
RESIDENTL | llg11 | 4969161.4408 | 709 | llg
| cpk21 | 8908.612 | 12 | cpk
INDUSTRIAL | cre23 | 238715.04 | 8 | cre
COMMERCIAL | epg33 | 43303826.6612 | 357 | epg
FARM | ofr21 | 60907.55 | 6 | ofr
COMMERCIAL | cpk22 | 8802072.7366 | 32 | cpk
NCONUML | bra24 | 34184.91 | 27 | bra
NCONUML | wn6 | 84222.69 | 35 | wn
FARM | mfa22 | 15017348.1505 | 702 | mfa
FARM | lga24 | 2675198.7919 | 323 | lga
COMMERCIAL | phi13 | 13565764.588 | 480 | phi
FARM | lga13 | 6142984.8245 | 572 | lga
NCONUML | wn2 | 74469.51 | 25 | wn
COMMERCIAL | wyk23 | 9043742.9219 | 306 | wyk
INDUSTRIAL | cyn31 | 110897.03 | 2 | cyn
RESIDENTL | wt7 | 9398293.9689 | 2293 | wt
COMMERCIAL | rwt15 | 2407529.701 | 118 | rwt
| wots11 | 29868.01 | 43 | wots
COMMERCIAL | wt12 | 9788397.4198 | 246 | wt
FARM | wots24 | 5049980.8194 | 706 | wots
COMMERCIAL | ftr22 | 3919173.7529 | 139 | ftr
INDUSTRIAL | ruba12 | 859698.6565 | 35 | ruba
| wots25 | 37134.4365 | 43 | wots
RESIDENTL | ofr24 | 14317680.0438 | 3420 | ofr
COMMERCIAL | bdl32 | 9327480.3168 | 349 | bdl
NCONUML | trc01 | 2600.11 | 1 | trc
RESIDENTL | wgi33 | 15074294.4922 | 2906 | wgi
RESIDENTL | wyk24 | 16651462.561 | 3130 | wyk
NCONUML | wn1 | 109135.95 | 32 | wn
NCONUML | fgy34 | 69468.4 | 26 | fgy
| tgn43 | 23585.3 | 37 | tgn
| bwn11 | 22540.96 | 33 | bwn
COMMERCIAL | bn11 | 11469939.8143 | 448 | bn
RESIDENTL | wn7 | 334597.06 | 81 | wn
FARM | lga23 | 6580772.0568 | 604 | lga
RESIDENTL | mby13 | 1114988.13 | 129 | mby
INDUSTRIAL | moe12 | 309363.05 | 10 | moe
NCONUML | wgl21 | 72341.71 | 26 | wgl
| rwn22 | 13422.17 | 20 | rwn
FARM | ofr13 | 1726.88 | 2 | ofr
INDUSTRIAL | smg33 | 3791.86 | 1 | smg
COMMERCIAL | cnr2 | 2241662.7301 | 123 | cnr
NCONUML | bwn13 | 114734.08 | 27 | bwn
INDUSTRIAL | tgn43 | 8336.37 | 2 | tgn
NCONUML | bra33 | 54640.5039 | 38 | bra
LIGHTING | drn23 | 137376.82 | 1 | drn
COMMERCIAL | wt11 | 6045415.4763 | 137 | wt
| wo23 | 3425.76 | 13 | wo
RESIDENTL | drn11 | 23689909.4015 | 5897 | drn
RESIDENTL | bra33 | 17227071.6094 | 3920 | bra
FARM | cre21 | 1165190.53 | 9 | cre
| wo32 | 20472.5797 | 26 | wo
NCONUML | mfa22 | 12133.93 | 8 | mfa
COMMERCIAL | fgy32 | 10874129.2215 | 316 | fgy
INDUSTRIAL | bdl33 | 6444229.03 | 34 | bdl
NCONUML | cnr3 | 880.96 | 3 | cnr
COMMERCIAL | bwr14 | 64319.73 | 1 | bwr
NCONUML | ldl11 | 15379.88 | 9 | ldl
FARM | bdl33 | 333127.23 | 48 | bdl
INDUSTRIAL | elm23 | 351538.3612 | 12 | elm
NCONUML | lga14 | 16509.29 | 6 | lga
NCONUML | rwt21 | 45520.76 | 13 | rwt
INDUSTRIAL | mwl24 | 3823292.43 | 15 | mwl
RESIDENTL | epg14 | 8906284.5994 | 2218 | epg
NCONUML | drn21 | 11559.57 | 6 | drn
FARM | ldl21 | 4274.77 | 1 | ldl
| lga14 | 13272.15 | 11 | lga
LIGHTING | wo22 | 1145144.2306 | 3 | wo
LIGHTING | bdl33 | 755365.47 | 1 | bdl
INDUSTRIAL | lga12 | 340570.559 | 7 | lga
RESIDENTL | ofr23 | 20573594.8025 | 3065 | ofr
LIGHTING | tgn12 | 393.8997 | 1 | tgn
RESIDENTL | fgy32 | 4718000.0914 | 1180 | fgy
COMMERCIAL | moe11 | 6876107.6583 | 169 | moe
COMMERCIAL | wgl13 | 16726185.3211 | 289 | wgl
COMMERCIAL | cre22 | 19152716.1468 | 212 | cre
RESIDENTL | drn12 | 16081122.8597 | 3986 | drn
COMMERCIAL | mfa23 | 8005013.26 | 78 | mfa
| cln13 | 39224.5517 | 61 | cln
INDUSTRIAL | mfa22 | 1793714.26 | 36 | mfa
LIGHTING | smr23 | 37560.88 | 1 | smr
RESIDENTL | rwn32 | 6727398.7344 | 1603 | rwn
FARM | lga14 | 4550189.1065 | 436 | lga
| cln12 | 24735.6225 | 51 | cln
COMMERCIAL | kms11 | 4936701.5866 | 120 | kms
RESIDENTL | smr14 | 10997106.9114 | 1697 | smr
| epg13 | 194183.3358 | 102 | epg
| brt21 | 9723.1397 | 7 | brt
INDUSTRIAL | drn12 | 10032.09 | 2 | drn
| tt7 | 34871.95 | 3 | tt
INDUSTRIAL | wots25 | 7153785.931 | 7 | wots
FARM | tgn43 | 14451.81 | 2 | tgn
NCONUML | ldl14 | 38917.21 | 26 | ldl
INDUSTRIAL | brt21 | 238786.6 | 10 | brt
| llg11 | 8477.8 | 10 | llg
RESIDENTL | wgi24 | 12721878.952 | 3596 | wgi
RESIDENTL | cyn21 | 10508542.767 | 2257 | cyn
INDUSTRIAL | bra11 | 3982632.29 | 3 | bra
INDUSTRIAL | phi11 | 184139.3994 | 13 | phi
| hpk24 | 8609.4373 | 14 | hpk
NCONUML | ldl13 | 24965.12 | 22 | ldl
RESIDENTL | hpk21 | 20637351.8958 | 5254 | hpk
RESIDENTL | wgl13 | 19626090.0794 | 4751 | wgl
COMMERCIAL | elm21 | 12124007.57 | 258 | elm
COMMERCIAL | wt13 | 23168272.4303 | 498 | wt
| hpk23 | 55023.71 | 41 | hpk
COMMERCIAL | mdg1 | 1157212.0402 | 52 | mdg
NCONUML | wt11 | 64055.27 | 25 | wt
NCONUML | phm31 | 9383.328 | 4 | phm
COMMERCIAL | bge23 | 4904566.2339 | 176 | bge
NCONUML | smg23 | 17942.69 | 11 | smg
| mwl16 | 4764.4783 | 12 | mwl
COMMERCIAL | hpk12 | 20352329.5415 | 361 | hpk
RESIDENTL | ruba24 | 4395729.6843 | 894 | ruba
COMMERCIAL | nla32 | 3390681.6399 | 175 | nla
NCONUML | lyd12 | 44439.84 | 9 | lyd
| cln22 | 289385.5413 | 85 | cln
NCONUML | cpk21 | 53769.1 | 26 | cpk
| ruba22 | 8482.6526 | 15 | ruba
COMMERCIAL | myt22 | 191990.12 | 18 | myt
RESIDENTL | mby11 | 5261006.6685 | 922 | mby
RESIDENTL | rwn26 | 21195116.3973 | 2454 | rwn
| rwt31 | 14608.62 | 19 | rwt
INDUSTRIAL | epg35 | 1615230.05 | 4 | epg
| bge23 | 30837.693 | 28 | bge
NCONUML | bdl34 | 70291.97 | 25 | bdl
NCONUML | ofr13 | 30258.73 | 11 | ofr
| klk11 | 25230.2094 | 21 | klk
NCONUML | bn12 | 1241.66 | 2 | bn
COMMERCIAL | wgi32 | 5461052.6827 | 195 | wgi
NCONUML | ldl12 | 45990.38 | 14 | ldl
INDUSTRIAL | bra23 | 3394433.4433 | 42 | bra
| wo33 | 4138.8 | 1 | wo
NCONUML | myt12 | 33269.22 | 16 | myt
INDUSTRIAL | ldl11 | 1468879.69 | 10 | ldl
RESIDENTL | msd1 | 8481569.4252 | 1750 | msd
NCONUML | bn11 | 57126.91 | 28 | bn
INDUSTRIAL | ftr12 | 2824402.5 | 31 | ftr
INDUSTRIAL | hpk11 | 29483.41 | 8 | hpk
NCONUML | epg33 | 5589.26 | 2 | epg
COMMERCIAL | wo31 | 10532525.1457 | 139 | wo
| wgl21 | 38182.04 | 53 | wgl
| bge22 | 25062.3495 | 31 | bge
RESIDENTL | tt1 | 171030.69 | 8 | tt
INDUSTRIAL | bwr34 | 134229.36 | 26 | bwr
COMMERCIAL | bra33 | 14409139.6368 | 303 | bra
COMMERCIAL | bdl44 | 4495186.894 | 197 | bdl
| bwn13 | 12482.8878 | 14 | bwn
NCONUML | wn3 | 40552.61 | 16 | wn
NCONUML | smr24 | 41055.27 | 16 | smr
INDUSTRIAL | mwl14 | 4499194.0326 | 50 | mwl
| wots24 | 36833.8626 | 36 | wots
NCONUML | wt12 | 74491.29 | 36 | wt
COMMERCIAL | smg31 | 17181337.4 | 81 | smg
FARM | lyd13 | 146611.14 | 18 | lyd
NCONUML | wots12 | 53576.05 | 15 | wots
INDUSTRIAL | fgy12 | 30820.7097 | 2 | fgy
FARM | myt12 | 4025860.4278 | 600 | myt
INDUSTRIAL | cyn22 | 204983.76 | 12 | cyn
COMMERCIAL | cyn33 | 3196035.4476 | 122 | cyn
COMMERCIAL | mby12 | 1853426.4391 | 89 | mby
NCONUML | tgn43 | 111938.06 | 34 | tgn
NCONUML | wo11 | 17571.55 | 5 | wo
INDUSTRIAL | epg12 | 1405424.52 | 3 | epg
| cf2 | 30699.57 | 2 | cf
COMMERCIAL | llg11 | 3213282.749 | 85 | llg
LIGHTING | rwn24 | 1936572.72 | 3 | rwn
INDUSTRIAL | cln24 | 15633.29 | 3 | cln
FARM | sle31 | 4999785.6618 | 315 | sle
INDUSTRIAL | cf1 | 129164.746 | 4 | cf
| ruba12 | 126134.0367 | 24 | ruba
| bwr12 | 18318.3952 | 15 | bwr
FARM | elm32 | 382389.8968 | 32 | elm
| ofr21 | 113717.1 | 52 | ofr
INDUSTRIAL | wn2 | 282430.54 | 13 | wn
NCONUML | bge22 | 82280.88 | 49 | bge
NCONUML | cnr2 | 33661.17 | 17 | cnr
NCONUML | wots13 | 10386.18 | 6 | wots
FARM | elm24 | 39172.3194 | 4 | elm
COMMERCIAL | nrn14 | 6896476.1265 | 116 | nrn
NCONUML | ruba12 | 27603.68 | 16 | ruba
NCONUML | hpk13 | 50290.3 | 16 | hpk
NCONUML | bra11 | 44798.92 | 35 | bra
| rwt21 | 23376.2409 | 6 | rwt
RESIDENTL | drn23 | 20613814.4846 | 2434 | drn
RESIDENTL | rwt36 | 2676215.9999 | 821 | rwt
RESIDENTL | llg13 | 6857833.0372 | 1230 | llg
COMMERCIAL | wyk12 | 4295149.2844 | 131 | wyk
INDUSTRIAL | ofr13 | 1622296.11 | 21 | ofr
| bra14 | 30334.7783 | 42 | bra
INDUSTRIAL | tgn11 | 3321263.75 | 18 | tgn
LIGHTING | mby13 | 9944.78 | 1 | mby
RESIDENTL | cln11 | 39284605.9906 | 12154 | cln
COMMERCIAL | drn22 | 10741065.2473 | 246 | drn
RESIDENTL | wo32 | 11244170.0715 | 2343 | wo
| bra33 | 27895.4569 | 47 | bra
COMMERCIAL | epg21 | 21867278.1603 | 75 | epg
INDUSTRIAL | cre21 | 293542.6 | 2 | cre
RESIDENTL | bwr24 | 1834966.95 | 415 | bwr
RESIDENTL | hpk13 | 8888406.848 | 2283 | hpk
NCONUML | moe13 | 240.62 | 2 | moe
RESIDENTL | mwl12 | 3605926.3697 | 887 | mwl
| elm24 | 29520.3106 | 27 | elm
COMMERCIAL | tgn31 | 5251765.7474 | 163 | tgn
| rwt25 | 17882.0217 | 23 | rwt
RESIDENTL | moe21 | 9438147.1697 | 1978 | moe
COMMERCIAL | mjg11 | 16973320.0649 | 258 | mjg
COMMERCIAL | moe22 | 1619971.835 | 34 | moe
NCONUML | cpk13 | 44472.2623 | 32 | cpk
| phi11 | 13149.9006 | 9 | phi
FARM | cyn11 | 2814.65 | 1 | cyn
FARM | cyn24 | 25049.8 | 2 | cyn
FARM | drn13 | 379220.8035 | 25 | drn
COMMERCIAL | mwe236 | 663523.2 | 21 | mwe
INDUSTRIAL | phm24 | 35612.08 | 4 | phm
INDUSTRIAL | bge22 | 36211.2493 | 9 | bge
RESIDENTL | cnr1 | 478523.9112 | 104 | cnr
| lga24 | 10918.35 | 11 | lga
NCONUML | sle14 | 98131.7526 | 34 | sle
NCONUML | tt5 | 14462.54 | 12 | tt
| epg12 | 53720.6497 | 70 | epg
NCONUML | kms11 | 42647.24 | 13 | kms
FARM | elm23 | 38507.8 | 8 | elm
COMMERCIAL | cyn12 | 12045879.7132 | 241 | cyn
INDUSTRIAL | fgy23 | 1420677.79 | 11 | fgy
COMMERCIAL | mfa14 | 259168.13 | 17 | mfa
| bra31 | 49797.7422 | 13 | bra
COMMERCIAL | mwl12 | 1780079.4127 | 78 | mwl
| bwr22 | 2405.71 | 25 | bwr
INDUSTRIAL | fgy24 | 415478.9 | 15 | fgy
COMMERCIAL | hpk13 | 9763023.5697 | 134 | hpk
| cyn22 | 22272.33 | 22 | cyn
| ldl21 | 13369.5383 | 42 | ldl
| wt6 | 17591.4373 | 23 | wt
RESIDENTL | wn4 | 11276854.4814 | 2349 | wn
FARM | mwl14 | 451834.7532 | 54 | mwl
RESIDENTL | bm8b31 | 357131.6719 | 111 | bmb
NCONUML | cyn14 | 48577.9677 | 22 | cyn
FARM | cre32 | 5136.47 | 1 | cre
FARM | bwr34 | 4550.33 | 1 | bwr
RESIDENTL | llg14 | 14855712.1657 | 2170 | llg
FARM | smg33 | 29400.19 | 7 | smg
RESIDENTL | drn22 | 21996972.8148 | 3999 | drn
NCONUML | elm32 | 42948.38 | 25 | elm
INDUSTRIAL | klo14 | 587332.99 | 17 | klo
| tgn11 | 22256.53 | 32 | tgn
INDUSTRIAL | tgn44 | 4536032.57 | 9 | tgn
COMMERCIAL | ldl23 | 15994398.5627 | 272 | ldl
| wn6 | 146062.0009 | 59 | wn
COMMERCIAL | tt2 | 18806104.6367 | 399 | tt
COMMERCIAL | brt11 | 4047117.81 | 129 | brt
NCONUML | llg14 | 65195.01 | 40 | llg
FARM | fgy24 | 95940.3 | 9 | fgy
NCONUML | fgy14 | 61562.37 | 33 | fgy
COMMERCIAL | rve12 | 3272242.91 | 54 | rve
INDUSTRIAL | cpk23 | 208291.634 | 5 | cpk
| lga23 | 41697.3391 | 21 | lga
INDUSTRIAL | yn38 | 642769.3081 | 6 | yn
COMMERCIAL | bwa21 | 7920817.52 | 6 | bwa
INDUSTRIAL | elm25 | 2097.04 | 1 | elm
COMMERCIAL | wots13 | 3416108.1488 | 213 | wots
FARM | wgi22 | 191494.2501 | 24 | wgi
NCONUML | fgy13 | 27847.71 | 7 | fgy
| bra24 | 9840.15 | 27 | bra
FARM | ofr14 | 100163.6258 | 21 | ofr
NCONUML | nrn11 | 16820.36 | 5 | nrn
RESIDENTL | smg31 | 12434679.8443 | 2879 | smg
COMMERCIAL | smr24 | 15083854.4686 | 348 | smr
| lyd11 | 12152.66 | 25 | lyd
INDUSTRIAL | bra12 | 1282907.1727 | 55 | bra
FARM | wgl15 | 3297105.6723 | 233 | wgl
INDUSTRIAL | msd1 | 544058.7154 | 15 | msd
| epg31 | 13971.3347 | 31 | epg
INDUSTRIAL | wgl23 | 572354.5027 | 44 | wgl
INDUSTRIAL | cpk12 | 343353.79 | 14 | cpk
INDUSTRIAL | mfa34 | 4790944.63 | 37 | mfa
| wn2 | 65478.1843 | 60 | wn
INDUSTRIAL | drn23 | 222019.33 | 21 | drn
| klo11 | 24997.4 | 1 | klo
COMMERCIAL | cyn13 | 11562540.4133 | 213 | cyn
| tgn44 | 15598.29 | 27 | tgn
| wn1 | 5093 | 9 | wn
NCONUML | wots24 | 22958.48 | 11 | wots
RESIDENTL | ftr21 | 5974099.1685 | 1654 | ftr
NCONUML | wgl11 | 116770.29 | 32 | wgl
FARM | phm22 | 2513172.8482 | 159 | phm
| mfa22 | 25912.0235 | 15 | mfa
| tt2 | 5693.01 | 1 | tt
RESIDENTL | cyn12 | 11384819.6049 | 2642 | cyn
COMMERCIAL | mby11 | 1920906.95 | 83 | mby
RESIDENTL | bdl42 | 7579399.6648 | 1528 | bdl
COMMERCIAL | sle11 | 16789466.3124 | 430 | sle
COMMERCIAL | bdl42 | 3935066.2305 | 228 | bdl
NCONUML | rwn22 | 25304.89 | 19 | rwn
INDUSTRIAL | cre32 | 1414910.91 | 33 | cre
INDUSTRIAL | bwn11 | 121807.37 | 8 | bwn
NCONUML | smr22 | 29006.3 | 13 | smr
RESIDENTL | phm24 | 12991887.5254 | 2975 | phm
RESIDENTL | phm21 | 5600884.0097 | 1319 | phm
NCONUML | ldl23 | 93357.12 | 44 | ldl
RESIDENTL | ldl24 | 19255310.9766 | 3964 | ldl
INDUSTRIAL | bra21 | 9682528.358 | 10 | bra
| sle31 | 21276.5675 | 34 | sle
| myt11 | 11671.01 | 10 | myt
RESIDENTL | elm21 | 10927220.6891 | 2208 | elm
COMMERCIAL | epg13 | 13081700.0195 | 121 | epg
COMMERCIAL | hpk21 | 6771211.022 | 80 | hpk
NCONUML | bwr12 | 55323.1848 | 22 | bwr
| trc01 | 7370.1419 | 1 | trc
| epg35 | 12733.43 | 3 | epg
INDUSTRIAL | bge21 | 30163.23 | 3 | bge
RESIDENTL | tgn31 | 10330935.5842 | 1504 | tgn
COMMERCIAL | moe23 | 8180066.6029 | 204 | moe
FARM | bra21 | 5211.11 | 2 | bra
LIGHTING | llg12 | 9573.66 | 1 | llg
RESIDENTL | bdl31 | 18828777.9984 | 3534 | bdl
COMMERCIAL | nla31 | 1365542.8767 | 73 | nla
INDUSTRIAL | klo24 | 421040.3606 | 14 | klo
FARM | bdl43 | 35833.9 | 4 | bdl
FARM | cyn31 | 3324.08 | 1 | cyn
FARM | sle14 | 508528.62 | 59 | sle
FARM | fgy34 | 3609.3 | 1 | fgy
RESIDENTL | elm26 | 19204314.084 | 3128 | elm
COMMERCIAL | ldl13 | 4974121.0157 | 271 | ldl
NCONUML | tgn42 | 32526.3 | 9 | tgn
RESIDENTL | nrn13 | 11128338.9236 | 2708 | nrn
| drn13 | 33230.29 | 35 | drn
RESIDENTL | mfa14 | 15628.16 | 8 | mfa
RESIDENTL | rwt14 | 5266292.5405 | 1232 | rwt
FARM | ftr23 | 7584335.745 | 587 | ftr
FARM | moe12 | 2890738.1544 | 266 | moe
RESIDENTL | klk21 | 6022162.144 | 692 | klk
COMMERCIAL | bn22 | 11917129.8815 | 407 | bn
COMMERCIAL | cln13 | 10498926.3291 | 102 | cln
INDUSTRIAL | cln11 | 955300.36 | 11 | cln
FARM | bge11 | 1450445.3683 | 132 | bge
| mwl25 | 368.2898 | 2 | mwl
| rwn33 | 13688.96 | 19 | rwn
| bdl43 | 33766.9817 | 15 | bdl
NCONUML | cln14 | 95979.5703 | 31 | cln
NCONUML | lga24 | 7306.35 | 4 | lga
| bn23 | 36133.4118 | 23 | bn
| ofr14 | 18460.3638 | 32 | ofr
FARM | wo14 | 29381.84 | 3 | wo
FARM | cln24 | 15169.45 | 1 | cln
FARM | smg21 | 2813.13 | 1 | smg
FARM | uwy1 | 50419.26 | 6 | uwy
RESIDENTL | cpk11 | 18255270.9798 | 3705 | cpk
INDUSTRIAL | rwn34 | 151721.8975 | 12 | rwn
FARM | mfa34 | 8352796.4311 | 398 | mfa
INDUSTRIAL | cyn23 | 283668.3977 | 39 | cyn
COMMERCIAL | cln23 | 7919442.4187 | 94 | cln
| rwn24 | 145239.1574 | 36 | rwn
INDUSTRIAL | cln21 | 91173.7471 | 8 | cln
INDUSTRIAL | wots23 | 9771996.01 | 2 | wots
COMMERCIAL | ofr23 | 7962081.4442 | 137 | ofr
FARM | cln11 | 5358747.3528 | 175 | cln
INDUSTRIAL | epg23 | 1603069.098 | 49 | epg
NCONUML | elm33 | 106570.09 | 33 | elm
| tt6 | 16214.4725 | 50 | tt
NCONUML | lga12 | 120.31 | 1 | lga
RESIDENTL | moe25 | 15202048.016 | 3044 | moe
RESIDENTL | moe22 | 6183768.6959 | 1343 | moe
RESIDENTL | mfa23 | 1535883.9368 | 206 | mfa
FARM | rwn22 | 76017.25 | 13 | rwn
COMMERCIAL | fgy31 | 26687.08 | 5 | fgy
RESIDENTL | elm33 | 17751529.9107 | 3238 | elm
COMMERCIAL | ldl22 | 7642772.3181 | 272 | ldl
NCONUML | llg11 | 13058.17 | 7 | llg
| ruba24 | 72607.09 | 10 | ruba
FARM | rwt32 | 21924.18 | 3 | rwt
FARM | ruba12 | 5735958.293 | 534 | ruba
FARM | brt21 | 526055.8565 | 65 | brt
| rwt15 | 24735.76 | 50 | rwt
NCONUML | bge13 | 40077 | 45 | bge
COMMERCIAL | klk21 | 1344972.0506 | 75 | klk
INDUSTRIAL | msd4 | 532825.24 | 27 | msd
| mwl21 | 2371.576 | 7 | mwl
RESIDENTL | wt9 | 13126762.7947 | 2901 | wt
FARM | wgi23 | 957555.9102 | 143 | wgi
| wgl24 | 12928.4076 | 27 | wgl
NCONUML | tgn11 | 50804.93 | 14 | tgn
LIGHTING | hpk22 | 402155.12 | 2 | hpk
INDUSTRIAL | wt13 | 198794.34 | 24 | wt
LIGHTING | wots24 | 69082.45 | 1 | wots
| ofr13 | 25120.5182 | 29 | ofr
| cre21 | 98632.2224 | 69 | cre
| smg22 | 13378.71 | 23 | smg
COMMERCIAL | tt4 | 4770691.1401 | 169 | tt
COMMERCIAL | elm26 | 2765254.86 | 47 | elm
NCONUML | bwa22 | 120.31 | 1 | bwa
| cyn23 | 386495.78 | 52 | cyn
INDUSTRIAL | nla34 | 227255.6563 | 13 | nla
FARM | mwl22 | 63.01 | 1 | mwl
| cf1 | 5771.13 | 3 | cf
NCONUML | cpk22 | 15413.02 | 10 | cpk
NCONUML | lyd13 | 28195.47 | 10 | lyd
NCONUML | cre31 | 35482.06 | 18 | cre
COMMERCIAL | wo11 | 6006584.4175 | 54 | wo
INDUSTRIAL | wt7 | 2382042.5333 | 25 | wt
| bwr34 | 19530.96 | 64 | bwr
NCONUML | bge23 | 57838.96 | 34 | bge
INDUSTRIAL | tgn23 | 187420.5 | 24 | tgn
RESIDENTL | cyn33 | 17836008.3498 | 3662 | cyn
RESIDENTL | nla34 | 7124747.0562 | 1408 | nla
| wgl11 | 21820.8596 | 38 | wgl
COMMERCIAL | bn12 | 3658135.6563 | 31 | bn
| mwl13 | 7054.2121 | 17 | mwl
COMMERCIAL | rwt26 | 65754589.65 | 1 | rwt
FARM | wt9 | 2789.4 | 1 | wt
RESIDENTL | bdl44 | 10906570.4152 | 1766 | bdl
FARM | cre33 | 2156267.3416 | 81 | cre
COMMERCIAL | wgl21 | 7364849.9167 | 150 | wgl
COMMERCIAL | wn5 | 3727109.367 | 208 | wn
NCONUML | mwl22 | 81020 | 27 | mwl
NCONUML | bn24 | 14677.57 | 9 | bn
| smr22 | 9887.67 | 15 | smr
|  | 8782.36 | 2 | #REF!
RESIDENTL | sle11 | 5311421.2716 | 1344 | sle
RESIDENTL | nw13 | 126364.0108 | 18 | nw
RESIDENTL | ftr23 | 12909653.9148 | 2620 | ftr
COMMERCIAL | mwl11 | 1278518.3133 | 72 | mwl
LIGHTING | llg13 | 66328.6913 | 1 | llg
NCONUML | klk22 | 2600.11 | 1 | klk
RESIDENTL | wyk23 | 22445865.182 | 3391 | wyk
COMMERCIAL | wt6 | 6354339.6482 | 191 | wt
RESIDENTL | brt11 | 6592458.6386 | 1001 | brt
NCONUML | tt9 | 66916.75 | 41 | tt
FARM | smr14 | 4406259.38 | 487 | smr
NCONUML | epg32 | 55568.91 | 13 | epg
RESIDENTL | rwn31 | 17135173.2235 | 2210 | rwn
| phm33 | 20993.1171 | 27 | phm
NCONUML | myt11 | 6079.5 | 6 | myt
RESIDENTL | nrn12 | 2807836.1314 | 591 | nrn
COMMERCIAL | mwl16 | 411566.3345 | 42 | mwl
INDUSTRIAL | lga23 | 1068068.6578 | 23 | lga
COMMERCIAL | ldl12 | 15390056.6509 | 380 | ldl
FARM | nla34 | 624678.3932 | 78 | nla
COMMERCIAL | rve13 | 1685040.429 | 44 | rve
NCONUML | drn24 | 11009.3526 | 4 | drn
COMMERCIAL | myt21 | 6919383.7104 | 251 | myt
FARM | moe13 | 3478506.4958 | 306 | moe
COMMERCIAL | mwl21 | 9182796.6603 | 240 | mwl
NCONUML | wgl15 | 97647.0301 | 36 | wgl
| bwn14 | 31300.22 | 31 | bwn
RESIDENTL | cpk22 | 8203984.593 | 1482 | cpk
RESIDENTL | rve12 | 17634581.2748 | 3656 | rve
RESIDENTL | phi13 | 17016004.0328 | 4317 | phi
RESIDENTL | hpk12 | 5058413.1519 | 1238 | hpk
COMMERCIAL | ruba24 | 4555190.3466 | 105 | ruba
FARM | cln14 | 51639.06 | 13 | cln
INDUSTRIAL | wt9 | 148098.11 | 5 | wt
| smg21 | 44014.37 | 27 | smg
INDUSTRIAL | smr23 | 883845.12 | 6 | smr

## Forecast - Summer
Forecasting Application - 13/10/2025
asset_type | asset | extremum | scenario | demand_year | season | poe | customer_count | pv_capacity | value | forecast_round | unit | region
zone_sub | cln | maximum |  | 2022 | Summer | 50 | 38619 | 72.2578 | 77.9086 | 202503 | MVA | central
zone_sub | cln | maximum |  | 2022 | Summer | 10 | 38619 | 72.2578 | 91.3183 | 202503 | MVA | central
zone_sub | cln | maximum |  | 2023 | Summer | 10 | 41429 | 81.3604 | 97.5884 | 202503 | MVA | central
zone_sub | cln | maximum |  | 2023 | Summer | 50 | 41429 | 81.3604 | 83.3369 | 202503 | MVA | central
zone_sub | cln | maximum |  | 2024 | Summer | 10 | 44846 | 94.6588 | 104.9463 | 202503 | MVA | central
zone_sub | cln | maximum |  | 2024 | Summer | 50 | 44846 | 94.6588 | 89.7351 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2025 | Summer | 10 |  |  | 119.6766 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2025 | Summer | 50 |  |  | 104.3341 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2026 | Summer | 10 |  |  | 124.2514 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2026 | Summer | 50 |  |  | 108.3435 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2027 | Summer | 10 |  |  | 128.0364 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2027 | Summer | 50 |  |  | 111.4611 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2028 | Summer | 10 |  |  | 131.3686 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2028 | Summer | 50 |  |  | 115.2173 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2029 | Summer | 10 |  |  | 136.7682 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2029 | Summer | 50 |  |  | 119.0984 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2030 | Summer | 10 |  |  | 141.634 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2030 | Summer | 50 |  |  | 123.2461 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2031 | Summer | 10 |  |  | 148.4809 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2031 | Summer | 50 |  |  | 128.0275 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2032 | Summer | 10 |  |  | 155.6302 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2032 | Summer | 50 |  |  | 133.6994 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2033 | Summer | 10 |  |  | 161.4365 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2033 | Summer | 50 |  |  | 139.0092 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2034 | Summer | 10 |  |  | 166.8996 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2034 | Summer | 50 |  |  | 144.6013 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2035 | Summer | 10 |  |  | 175.1342 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2035 | Summer | 50 |  |  | 154.2938 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2036 | Summer | 10 |  |  | 181.0486 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2036 | Summer | 50 |  |  | 157.43 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2037 | Summer | 10 |  |  | 187.0195 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2037 | Summer | 50 |  |  | 163.5566 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2038 | Summer | 10 |  |  | 193.3671 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2038 | Summer | 50 |  |  | 168.1999 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2039 | Summer | 10 |  |  | 192.0421 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2039 | Summer | 50 |  |  | 167.0472 | 202503 | MVA | central
zone_sub | cre | maximum |  | 2022 | Summer | 10 | 24937 | 39.5122 | 71.3044 | 202503 | MVA | central
zone_sub | cre | maximum |  | 2022 | Summer | 50 | 24937 | 39.5122 | 64.1683 | 202503 | MVA | central
zone_sub | cre | maximum |  | 2023 | Summer | 10 | 25835 | 43.8704 | 73.6781 | 202503 | MVA | central
zone_sub | cre | maximum |  | 2023 | Summer | 50 | 25835 | 43.8704 | 65.8328 | 202503 | MVA | central
zone_sub | cre | maximum |  | 2024 | Summer | 10 | 26314 | 48.9572 | 74.7994 | 202503 | MVA | central
zone_sub | cre | maximum |  | 2024 | Summer | 50 | 26314 | 48.9572 | 66.0879 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2025 | Summer | 10 |  |  | 89.8342 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2025 | Summer | 50 |  |  | 80.6612 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2026 | Summer | 10 |  |  | 90.653 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2026 | Summer | 50 |  |  | 81.4056 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2027 | Summer | 10 |  |  | 89.7773 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2027 | Summer | 50 |  |  | 80.6131 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2028 | Summer | 10 |  |  | 94.9573 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2028 | Summer | 50 |  |  | 85.9509 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2029 | Summer | 10 |  |  | 94.8385 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2029 | Summer | 50 |  |  | 85.6114 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2030 | Summer | 10 |  |  | 96.1186 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2030 | Summer | 50 |  |  | 85.7941 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2031 | Summer | 10 |  |  | 97.2062 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2031 | Summer | 50 |  |  | 86.4866 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2032 | Summer | 10 |  |  | 98.0786 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2032 | Summer | 50 |  |  | 87.2925 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2033 | Summer | 10 |  |  | 98.8781 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2033 | Summer | 50 |  |  | 88.2343 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2034 | Summer | 10 |  |  | 99.6475 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2034 | Summer | 50 |  |  | 88.9575 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2035 | Summer | 10 |  |  | 99.2707 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2035 | Summer | 50 |  |  | 89.8044 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2036 | Summer | 10 |  |  | 99.9981 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2036 | Summer | 50 |  |  | 89.5675 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2037 | Summer | 10 |  |  | 101.1509 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2037 | Summer | 50 |  |  | 90.5821 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2038 | Summer | 10 |  |  | 101.3208 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2038 | Summer | 50 |  |  | 90.3196 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2039 | Summer | 10 |  |  | 99.6095 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2039 | Summer | 50 |  |  | 88.5146 | 202503 | MVA | central
zone_sub | epg | maximum |  | 2022 | Summer | 10 | 29371 | 40.0067 | 87.2498 | 202503 | MVA | central
zone_sub | epg | maximum |  | 2022 | Summer | 50 | 29371 | 40.0067 | 72.9666 | 202503 | MVA | central
zone_sub | epg | maximum |  | 2023 | Summer | 10 | 30422 | 45.1511 | 90.3071 | 202503 | MVA | central
zone_sub | epg | maximum |  | 2023 | Summer | 50 | 30422 | 45.1511 | 75.7012 | 202503 | MVA | central
zone_sub | epg | maximum |  | 2024 | Summer | 10 | 32118 | 51.557 | 95.8895 | 202503 | MVA | central
zone_sub | epg | maximum |  | 2024 | Summer | 50 | 32118 | 51.557 | 79.9844 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2025 | Summer | 10 |  |  | 109.0669 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2025 | Summer | 50 |  |  | 92.5622 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2026 | Summer | 10 |  |  | 118.5447 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2026 | Summer | 50 |  |  | 101.6723 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2027 | Summer | 10 |  |  | 121.4869 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2027 | Summer | 50 |  |  | 104.4042 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2028 | Summer | 10 |  |  | 119.8786 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2028 | Summer | 50 |  |  | 102.6031 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2029 | Summer | 10 |  |  | 121.9204 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2029 | Summer | 50 |  |  | 105.5757 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2030 | Summer | 10 |  |  | 124.6444 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2030 | Summer | 50 |  |  | 106.371 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2031 | Summer | 10 |  |  | 127.5507 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2031 | Summer | 50 |  |  | 110.1341 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2032 | Summer | 10 |  |  | 131.8742 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2032 | Summer | 50 |  |  | 112.2581 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2033 | Summer | 10 |  |  | 136.3355 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2033 | Summer | 50 |  |  | 113.9316 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2034 | Summer | 10 |  |  | 140.9437 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2034 | Summer | 50 |  |  | 117.5793 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2035 | Summer | 10 |  |  | 144.5914 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2035 | Summer | 50 |  |  | 120.4726 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2036 | Summer | 50 |  |  | 128.0797 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2036 | Summer | 10 |  |  | 149.6115 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2037 | Summer | 10 |  |  | 152.9797 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2037 | Summer | 50 |  |  | 129.922 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2038 | Summer | 10 |  |  | 155.1715 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2038 | Summer | 50 |  |  | 132.5568 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2039 | Summer | 10 |  |  | 152.1644 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2039 | Summer | 50 |  |  | 125.7761 | 202503 | MVA | central
zone_sub | klo | maximum |  | 2022 | Summer | 10 | 14879 | 23.0226 | 53.5677 | 202503 | MVA | central
zone_sub | klo | maximum |  | 2022 | Summer | 50 | 14879 | 23.0226 | 41.9423 | 202503 | MVA | central
zone_sub | klo | maximum |  | 2023 | Summer | 10 | 17175 | 27.7177 | 61.121 | 202503 | MVA | central
zone_sub | klo | maximum |  | 2023 | Summer | 50 | 17175 | 27.7177 | 48.3019 | 202503 | MVA | central
zone_sub | klo | maximum |  | 2024 | Summer | 10 | 19951 | 34.2052 | 70.1897 | 202503 | MVA | central
zone_sub | klo | maximum |  | 2024 | Summer | 50 | 19951 | 34.2052 | 55.7613 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2025 | Summer | 10 |  |  | 83.6879 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2025 | Summer | 50 |  |  | 68.2523 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2026 | Summer | 10 |  |  | 94.1984 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2026 | Summer | 50 |  |  | 77.9353 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2027 | Summer | 10 |  |  | 102.4436 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2027 | Summer | 50 |  |  | 84.7194 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2028 | Summer | 10 |  |  | 118.3247 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2028 | Summer | 50 |  |  | 99.6669 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2029 | Summer | 10 |  |  | 126.3487 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2029 | Summer | 50 |  |  | 106.8624 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2030 | Summer | 10 |  |  | 135.5692 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2030 | Summer | 50 |  |  | 115.5707 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2031 | Summer | 10 |  |  | 148.561 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2031 | Summer | 50 |  |  | 127.0156 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2032 | Summer | 10 |  |  | 164.8827 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2032 | Summer | 50 |  |  | 137.8179 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2033 | Summer | 10 |  |  | 180.5841 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2033 | Summer | 50 |  |  | 151.2391 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2034 | Summer | 10 |  |  | 196.9964 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2034 | Summer | 50 |  |  | 164.8814 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2035 | Summer | 10 |  |  | 212.9758 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2035 | Summer | 50 |  |  | 181.5355 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2036 | Summer | 10 |  |  | 230.0573 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2036 | Summer | 50 |  |  | 195.8954 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2037 | Summer | 10 |  |  | 248.4456 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2037 | Summer | 50 |  |  | 212.2991 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2038 | Summer | 10 |  |  | 266.5409 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2038 | Summer | 50 |  |  | 225.6959 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2039 | Summer | 10 |  |  | 272.6357 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2039 | Summer | 50 |  |  | 228.9049 | 202503 | MVA | central
zone_sub | ofr | maximum |  | 2022 | Summer | 10 | 23246 | 35.5119 | 59.9776 | 202503 | MVA | central
zone_sub | ofr | maximum |  | 2022 | Summer | 50 | 23246 | 35.5119 | 53.856 | 202503 | MVA | central
zone_sub | ofr | maximum |  | 2023 | Summer | 10 | 24109 | 39.5748 | 62.0639 | 202503 | MVA | central
zone_sub | ofr | maximum |  | 2023 | Summer | 50 | 24109 | 39.5748 | 55.451 | 202503 | MVA | central
zone_sub | ofr | maximum |  | 2024 | Summer | 10 | 24997 | 44.4669 | 64.073 | 202503 | MVA | central
zone_sub | ofr | maximum |  | 2024 | Summer | 50 | 24997 | 44.4669 | 56.9594 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2025 | Summer | 10 |  |  | 69.589 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2025 | Summer | 50 |  |  | 61.9907 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2026 | Summer | 10 |  |  | 76.597 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2026 | Summer | 50 |  |  | 68.9791 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2027 | Summer | 10 |  |  | 81.5678 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2027 | Summer | 50 |  |  | 74.0072 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2028 | Summer | 10 |  |  | 84.5283 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2028 | Summer | 50 |  |  | 76.6284 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2029 | Summer | 10 |  |  | 86.8984 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2029 | Summer | 50 |  |  | 78.9811 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2030 | Summer | 10 |  |  | 88.8048 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2030 | Summer | 50 |  |  | 80.4506 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2031 | Summer | 10 |  |  | 90.6365 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2031 | Summer | 50 |  |  | 82.1352 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2032 | Summer | 10 |  |  | 92.2256 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2032 | Summer | 50 |  |  | 83.4813 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2033 | Summer | 10 |  |  | 92.9929 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2033 | Summer | 50 |  |  | 84.3346 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2034 | Summer | 10 |  |  | 94.1573 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2034 | Summer | 50 |  |  | 86.446 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2035 | Summer | 10 |  |  | 95.4952 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2035 | Summer | 50 |  |  | 87.894 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2036 | Summer | 10 |  |  | 96.8516 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2036 | Summer | 50 |  |  | 88.627 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2037 | Summer | 10 |  |  | 98.5806 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2037 | Summer | 50 |  |  | 90.0391 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2038 | Summer | 10 |  |  | 98.8168 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2038 | Summer | 50 |  |  | 89.5765 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2039 | Summer | 10 |  |  | 97.8239 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2039 | Summer | 50 |  |  | 88.3981 | 202503 | MVA | central
zone_sub | phm | maximum |  | 2022 | Summer | 50 | 16270 | 23.521 | 51.4174 | 202503 | MVA | central
zone_sub | phm | maximum |  | 2022 | Summer | 10 | 16270 | 23.521 | 56.9097 | 202503 | MVA | central
zone_sub | phm | maximum |  | 2023 | Summer | 10 | 16562 | 25.5412 | 57.758 | 202503 | MVA | central
zone_sub | phm | maximum |  | 2023 | Summer | 50 | 16562 | 25.5412 | 52.1386 | 202503 | MVA | central
zone_sub | phm | maximum |  | 2024 | Summer | 10 | 16854 | 27.7496 | 58.7282 | 202503 | MVA | central
zone_sub | phm | maximum |  | 2024 | Summer | 50 | 16854 | 27.7496 | 52.8621 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2025 | Summer | 10 |  |  | 75.5207 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2025 | Summer | 50 |  |  | 69.621 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2026 | Summer | 10 |  |  | 79.8845 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2026 | Summer | 50 |  |  | 74.1527 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2027 | Summer | 10 |  |  | 79.6008 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2027 | Summer | 50 |  |  | 73.9998 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2028 | Summer | 10 |  |  | 79.5894 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2028 | Summer | 50 |  |  | 73.965 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2029 | Summer | 10 |  |  | 80.0199 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2029 | Summer | 50 |  |  | 74.4648 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2030 | Summer | 10 |  |  | 81.1895 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2030 | Summer | 50 |  |  | 75.0153 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2031 | Summer | 10 |  |  | 81.9552 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2031 | Summer | 50 |  |  | 76.1566 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2032 | Summer | 10 |  |  | 82.7146 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2032 | Summer | 50 |  |  | 76.9783 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2033 | Summer | 10 |  |  | 83.6062 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2033 | Summer | 50 |  |  | 77.4148 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2034 | Summer | 10 |  |  | 84.4206 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2034 | Summer | 50 |  |  | 77.8841 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2035 | Summer | 10 |  |  | 85.2206 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2035 | Summer | 50 |  |  | 78.3211 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2036 | Summer | 10 |  |  | 85.2937 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2036 | Summer | 50 |  |  | 79.127 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2037 | Summer | 10 |  |  | 86.2309 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2037 | Summer | 50 |  |  | 80.1321 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2038 | Summer | 10 |  |  | 85.4841 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2038 | Summer | 50 |  |  | 80.0404 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2039 | Summer | 10 |  |  | 79.3417 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2039 | Summer | 50 |  |  | 73.3195 | 202503 | MVA | central
zone_sub | llg | maximum |  | 2022 | Summer | 10 | 7174 | 11.5134 | 25.3928 | 202503 | MVA | central
zone_sub | llg | maximum |  | 2022 | Summer | 50 | 7174 | 11.5134 | 23.4346 | 202503 | MVA | central
zone_sub | llg | maximum |  | 2023 | Summer | 10 | 7235 | 12.7349 | 25.4543 | 202503 | MVA | central
zone_sub | llg | maximum |  | 2023 | Summer | 50 | 7235 | 12.7349 | 23.4406 | 202503 | MVA | central
zone_sub | llg | maximum |  | 2024 | Summer | 10 | 7295 | 13.7538 | 25.544 | 202503 | MVA | central
zone_sub | llg | maximum |  | 2024 | Summer | 50 | 7295 | 13.7538 | 23.5081 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2025 | Summer | 10 |  |  | 28.7312 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2025 | Summer | 50 |  |  | 26.0976 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2026 | Summer | 10 |  |  | 33.0834 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2026 | Summer | 50 |  |  | 30.4575 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2027 | Summer | 10 |  |  | 33.0249 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2027 | Summer | 50 |  |  | 30.4247 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2028 | Summer | 10 |  |  | 33.0633 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2028 | Summer | 50 |  |  | 30.3952 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2029 | Summer | 10 |  |  | 33.1822 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2029 | Summer | 50 |  |  | 30.8677 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2030 | Summer | 10 |  |  | 33.5865 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2030 | Summer | 50 |  |  | 31.5616 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2031 | Summer | 10 |  |  | 33.8573 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2031 | Summer | 50 |  |  | 32.037 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2032 | Summer | 10 |  |  | 34.0794 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2032 | Summer | 50 |  |  | 31.4591 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2033 | Summer | 10 |  |  | 34.1121 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2033 | Summer | 50 |  |  | 31.5166 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2034 | Summer | 10 |  |  | 34.3124 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2034 | Summer | 50 |  |  | 31.792 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2035 | Summer | 10 |  |  | 34.3834 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2035 | Summer | 50 |  |  | 32.8827 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2036 | Summer | 10 |  |  | 34.3832 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2036 | Summer | 50 |  |  | 31.8492 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2037 | Summer | 10 |  |  | 34.3374 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2037 | Summer | 50 |  |  | 31.7885 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2038 | Summer | 10 |  |  | 34.3276 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2038 | Summer | 50 |  |  | 31.7234 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2039 | Summer | 10 |  |  | 32.6827 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2039 | Summer | 50 |  |  | 30.3101 | 202503 | MVA | central
zone_sub | wgi | maximum |  | 2022 | Summer | 10 | 21696 | 27.3902 | 50.299 | 202503 | MVA | east
zone_sub | wgi | maximum |  | 2022 | Summer | 50 | 21696 | 27.3902 | 41.2414 | 202503 | MVA | east
zone_sub | wgi | maximum |  | 2023 | Summer | 10 | 22045 | 30.4273 | 50.6919 | 202503 | MVA | east
zone_sub | wgi | maximum |  | 2023 | Summer | 50 | 22045 | 30.4273 | 41.4384 | 202503 | MVA | east
zone_sub | wgi | maximum |  | 2024 | Summer | 10 | 22388 | 33.5461 | 51.0465 | 202503 | MVA | east
zone_sub | wgi | maximum |  | 2024 | Summer | 50 | 22388 | 33.5461 | 41.5121 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2025 | Summer | 10 |  |  | 54.5057 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2025 | Summer | 50 |  |  | 44.6075 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2026 | Summer | 10 |  |  | 54.6012 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2026 | Summer | 50 |  |  | 44.9185 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2027 | Summer | 10 |  |  | 54.4983 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2027 | Summer | 50 |  |  | 44.7661 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2028 | Summer | 10 |  |  | 54.5247 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2028 | Summer | 50 |  |  | 44.911 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2029 | Summer | 10 |  |  | 54.7136 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2029 | Summer | 50 |  |  | 44.9706 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2030 | Summer | 10 |  |  | 55.0965 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2030 | Summer | 50 |  |  | 45.1615 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2031 | Summer | 10 |  |  | 55.7707 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2031 | Summer | 50 |  |  | 45.5541 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2032 | Summer | 50 |  |  | 45.8843 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2032 | Summer | 10 |  |  | 56.122 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2033 | Summer | 10 |  |  | 56.3761 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2033 | Summer | 50 |  |  | 46.0363 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2034 | Summer | 10 |  |  | 56.7608 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2034 | Summer | 50 |  |  | 45.9008 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2035 | Summer | 10 |  |  | 57.2519 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2035 | Summer | 50 |  |  | 46.4689 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2036 | Summer | 10 |  |  | 57.8457 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2036 | Summer | 50 |  |  | 46.559 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2037 | Summer | 10 |  |  | 58.1569 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2037 | Summer | 50 |  |  | 46.4523 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2038 | Summer | 10 |  |  | 58.056 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2038 | Summer | 50 |  |  | 46.6661 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2039 | Summer | 10 |  |  | 56.811 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2039 | Summer | 50 |  |  | 45.5652 | 202503 | MVA | east

## Forecast- Winter
Forecasting Application - 13/10/2025
asset_type | asset | extremum | scenario | demand_year | season | poe | customer_count | pv_capacity | value | forecast_round | unit | region
zone_sub | cln | maximum |  | 2022 | Winter | 10 | 38619 | 72.2578 | 63.0362 | 202503 | MVA | central
zone_sub | cln | maximum |  | 2022 | Winter | 50 | 38619 | 72.2578 | 58.8161 | 202503 | MVA | central
zone_sub | cln | maximum |  | 2023 | Winter | 10 | 41429 | 81.3604 | 67.9918 | 202503 | MVA | central
zone_sub | cln | maximum |  | 2023 | Winter | 50 | 41429 | 81.3604 | 63.4647 | 202503 | MVA | central
zone_sub | cln | maximum |  | 2024 | Winter | 10 | 44846 | 94.6588 | 74.018 | 202503 | MVA | central
zone_sub | cln | maximum |  | 2024 | Winter | 50 | 44846 | 94.6588 | 69.1182 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2025 | Winter | 10 |  |  | 89.4372 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2025 | Winter | 50 |  |  | 84.5179 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2026 | Winter | 10 |  |  | 93.2911 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2026 | Winter | 50 |  |  | 88.1502 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2027 | Winter | 10 |  |  | 98.0701 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2027 | Winter | 50 |  |  | 92.8679 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2028 | Winter | 10 |  |  | 102.5171 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2028 | Winter | 50 |  |  | 97.437 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2029 | Winter | 10 |  |  | 107.2692 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2029 | Winter | 50 |  |  | 101.4753 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2030 | Winter | 10 |  |  | 112.2902 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2030 | Winter | 50 |  |  | 107.1286 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2031 | Winter | 10 |  |  | 119.5588 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2031 | Winter | 50 |  |  | 113.3315 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2032 | Winter | 10 |  |  | 125.8642 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2032 | Winter | 50 |  |  | 119.6901 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2033 | Winter | 10 |  |  | 131.807 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2033 | Winter | 50 |  |  | 125.9989 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2034 | Winter | 10 |  |  | 137.993 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2034 | Winter | 50 |  |  | 131.579 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2035 | Winter | 10 |  |  | 145.465 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2035 | Winter | 50 |  |  | 137.6925 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2036 | Winter | 10 |  |  | 147.8036 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2036 | Winter | 50 |  |  | 139.8743 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2037 | Winter | 10 |  |  | 155.8793 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2037 | Winter | 50 |  |  | 147.8441 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2038 | Winter | 10 |  |  | 163.4009 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2038 | Winter | 50 |  |  | 156.1056 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2039 | Winter | 10 |  |  | 133.5693 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2039 | Winter | 50 |  |  | 127.2077 | 202503 | MVA | central
zone_sub | cre | maximum |  | 2022 | Winter | 10 | 24937 | 39.5122 | 50.635 | 202503 | MVA | central
zone_sub | cre | maximum |  | 2022 | Winter | 50 | 24937 | 39.5122 | 48.3881 | 202503 | MVA | central
zone_sub | cre | maximum |  | 2023 | Winter | 10 | 25835 | 43.8704 | 52.4586 | 202503 | MVA | central
zone_sub | cre | maximum |  | 2023 | Winter | 50 | 25835 | 43.8704 | 50.1308 | 202503 | MVA | central
zone_sub | cre | maximum |  | 2024 | Winter | 10 | 26314 | 48.9572 | 53.4328 | 202503 | MVA | central
zone_sub | cre | maximum |  | 2024 | Winter | 50 | 26314 | 48.9572 | 51.0617 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2025 | Winter | 10 |  |  | 68.4471 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2025 | Winter | 50 |  |  | 65.7336 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2026 | Winter | 10 |  |  | 69.4459 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2026 | Winter | 50 |  |  | 66.605 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2027 | Winter | 10 |  |  | 69.249 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2027 | Winter | 50 |  |  | 66.728 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2028 | Winter | 10 |  |  | 74.3386 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2028 | Winter | 50 |  |  | 72.0847 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2029 | Winter | 10 |  |  | 74.5773 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2029 | Winter | 50 |  |  | 72.2361 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2030 | Winter | 10 |  |  | 76.3193 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2030 | Winter | 50 |  |  | 74.0669 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2031 | Winter | 10 |  |  | 77.7248 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2031 | Winter | 50 |  |  | 75.6012 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2032 | Winter | 10 |  |  | 79.2116 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2032 | Winter | 50 |  |  | 76.7507 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2033 | Winter | 10 |  |  | 79.7367 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2033 | Winter | 50 |  |  | 77.8762 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2034 | Winter | 10 |  |  | 80.3545 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2034 | Winter | 50 |  |  | 78.6625 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2035 | Winter | 10 |  |  | 81.081 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2035 | Winter | 50 |  |  | 79.0014 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2036 | Winter | 10 |  |  | 80.0375 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2036 | Winter | 50 |  |  | 78.1499 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2037 | Winter | 10 |  |  | 83.4116 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2037 | Winter | 50 |  |  | 80.9567 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2038 | Winter | 10 |  |  | 84.3767 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2038 | Winter | 50 |  |  | 81.4995 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2039 | Winter | 10 |  |  | 72.4681 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2039 | Winter | 50 |  |  | 69.0004 | 202503 | MVA | central
zone_sub | epg | maximum |  | 2022 | Winter | 10 | 29371 | 40.0067 | 65.9271 | 202503 | MVA | central
zone_sub | epg | maximum |  | 2022 | Winter | 50 | 29371 | 40.0067 | 59.4269 | 202503 | MVA | central
zone_sub | epg | maximum |  | 2023 | Winter | 10 | 30422 | 45.1511 | 68.3101 | 202503 | MVA | central
zone_sub | epg | maximum |  | 2023 | Winter | 50 | 30422 | 45.1511 | 61.7598 | 202503 | MVA | central
zone_sub | epg | maximum |  | 2024 | Winter | 50 | 32118 | 51.557 | 65.5719 | 202503 | MVA | central
zone_sub | epg | maximum |  | 2024 | Winter | 10 | 32118 | 51.557 | 72.1952 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2025 | Winter | 10 |  |  | 85.9871 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2025 | Winter | 50 |  |  | 79.3939 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2026 | Winter | 10 |  |  | 95.0802 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2026 | Winter | 50 |  |  | 89.3565 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2027 | Winter | 10 |  |  | 100.5082 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2027 | Winter | 50 |  |  | 92.7492 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2028 | Winter | 10 |  |  | 99.8778 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2028 | Winter | 50 |  |  | 93.3308 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2029 | Winter | 10 |  |  | 103.1049 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2029 | Winter | 50 |  |  | 96.5577 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2030 | Winter | 10 |  |  | 109.1359 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2030 | Winter | 50 |  |  | 102.3455 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2031 | Winter | 10 |  |  | 112.51 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2031 | Winter | 50 |  |  | 104.2867 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2032 | Winter | 10 |  |  | 121.7799 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2032 | Winter | 50 |  |  | 114.0182 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2033 | Winter | 10 |  |  | 127.6696 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2033 | Winter | 50 |  |  | 119.7255 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2034 | Winter | 10 |  |  | 133.3287 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2034 | Winter | 50 |  |  | 125.5482 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2035 | Winter | 10 |  |  | 135.1129 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2035 | Winter | 50 |  |  | 126.6853 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2036 | Winter | 10 |  |  | 142.2751 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2036 | Winter | 50 |  |  | 134.3407 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2037 | Winter | 10 |  |  | 149.629 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2037 | Winter | 50 |  |  | 142.1357 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2038 | Winter | 10 |  |  | 150.109 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2038 | Winter | 50 |  |  | 141.9626 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2039 | Winter | 10 |  |  | 116.0207 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2039 | Winter | 50 |  |  | 101.3122 | 202503 | MVA | central
zone_sub | klo | maximum |  | 2022 | Winter | 10 | 14879 | 23.0226 | 48.7862 | 202503 | MVA | central
zone_sub | klo | maximum |  | 2022 | Winter | 50 | 14879 | 23.0226 | 43.3886 | 202503 | MVA | central
zone_sub | klo | maximum |  | 2023 | Winter | 10 | 17175 | 27.7177 | 56.3067 | 202503 | MVA | central
zone_sub | klo | maximum |  | 2023 | Winter | 50 | 17175 | 27.7177 | 50.077 | 202503 | MVA | central
zone_sub | klo | maximum |  | 2024 | Winter | 10 | 19951 | 34.2052 | 65.4015 | 202503 | MVA | central
zone_sub | klo | maximum |  | 2024 | Winter | 50 | 19951 | 34.2052 | 58.1655 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2025 | Winter | 10 |  |  | 79.8942 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2025 | Winter | 50 |  |  | 72.3119 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2026 | Winter | 10 |  |  | 92.3723 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2026 | Winter | 50 |  |  | 83.7626 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2027 | Winter | 10 |  |  | 102.9502 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2027 | Winter | 50 |  |  | 93.3778 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2028 | Winter | 10 |  |  | 120.3965 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2028 | Winter | 50 |  |  | 109.8362 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2029 | Winter | 10 |  |  | 129.7211 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2029 | Winter | 50 |  |  | 118.6301 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2030 | Winter | 10 |  |  | 142.5707 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2030 | Winter | 50 |  |  | 129.8167 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2031 | Winter | 10 |  |  | 159.4027 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2031 | Winter | 50 |  |  | 143.8497 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2032 | Winter | 10 |  |  | 178.8568 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2032 | Winter | 50 |  |  | 161.743 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2033 | Winter | 10 |  |  | 196.8658 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2033 | Winter | 50 |  |  | 178.8635 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2034 | Winter | 10 |  |  | 214.3536 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2034 | Winter | 50 |  |  | 194.8729 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2035 | Winter | 10 |  |  | 235.0946 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2035 | Winter | 50 |  |  | 213.0243 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2036 | Winter | 10 |  |  | 246.5584 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2036 | Winter | 50 |  |  | 225.0657 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2037 | Winter | 10 |  |  | 273.2503 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2037 | Winter | 50 |  |  | 249.8153 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2038 | Winter | 10 |  |  | 298.8878 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2038 | Winter | 50 |  |  | 271.7276 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2039 | Winter | 10 |  |  | 252.4111 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2039 | Winter | 50 |  |  | 227.0702 | 202503 | MVA | central
zone_sub | llg | maximum |  | 2022 | Winter | 10 | 7174 | 11.5134 | 22.426 | 202503 | MVA | central
zone_sub | llg | maximum |  | 2022 | Winter | 50 | 7174 | 11.5134 | 20.2322 | 202503 | MVA | central
zone_sub | llg | maximum |  | 2023 | Winter | 10 | 7235 | 12.7349 | 22.5982 | 202503 | MVA | central
zone_sub | llg | maximum |  | 2023 | Winter | 50 | 7235 | 12.7349 | 20.4035 | 202503 | MVA | central
zone_sub | llg | maximum |  | 2024 | Winter | 10 | 7295 | 13.7538 | 22.7705 | 202503 | MVA | central
zone_sub | llg | maximum |  | 2024 | Winter | 50 | 7295 | 13.7538 | 20.5738 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2025 | Winter | 10 |  |  | 26.1225 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2025 | Winter | 50 |  |  | 23.9159 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2026 | Winter | 10 |  |  | 30.6829 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2026 | Winter | 50 |  |  | 28.4398 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2027 | Winter | 10 |  |  | 31.049 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2027 | Winter | 50 |  |  | 28.8402 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2028 | Winter | 10 |  |  | 31.3064 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2028 | Winter | 50 |  |  | 29.108 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2029 | Winter | 10 |  |  | 31.5714 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2029 | Winter | 50 |  |  | 29.4846 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2030 | Winter | 10 |  |  | 32.5932 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2030 | Winter | 50 |  |  | 30.3426 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2031 | Winter | 10 |  |  | 33.1905 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2031 | Winter | 50 |  |  | 31.0163 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2032 | Winter | 10 |  |  | 33.8014 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2032 | Winter | 50 |  |  | 31.6154 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2033 | Winter | 10 |  |  | 34.0793 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2033 | Winter | 50 |  |  | 31.8255 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2034 | Winter | 10 |  |  | 34.2253 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2034 | Winter | 50 |  |  | 32.0656 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2035 | Winter | 10 |  |  | 33.7185 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2035 | Winter | 50 |  |  | 31.7299 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2036 | Winter | 10 |  |  | 33.9832 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2036 | Winter | 50 |  |  | 31.9069 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2037 | Winter | 10 |  |  | 34.9987 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2037 | Winter | 50 |  |  | 32.7389 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2038 | Winter | 10 |  |  | 34.5209 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2038 | Winter | 50 |  |  | 32.3709 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2039 | Winter | 10 |  |  | 28.3277 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2039 | Winter | 50 |  |  | 26.2847 | 202503 | MVA | central
zone_sub | ofr | maximum |  | 2022 | Winter | 10 | 23246 | 35.5119 | 49.8939 | 202503 | MVA | central
zone_sub | ofr | maximum |  | 2022 | Winter | 50 | 23246 | 35.5119 | 46.8764 | 202503 | MVA | central
zone_sub | ofr | maximum |  | 2023 | Winter | 10 | 24109 | 39.5748 | 51.7437 | 202503 | MVA | central
zone_sub | ofr | maximum |  | 2023 | Winter | 50 | 24109 | 39.5748 | 48.6149 | 202503 | MVA | central
zone_sub | ofr | maximum |  | 2024 | Winter | 10 | 24997 | 44.4669 | 53.6497 | 202503 | MVA | central
zone_sub | ofr | maximum |  | 2024 | Winter | 50 | 24997 | 44.4669 | 50.4065 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2025 | Winter | 10 |  |  | 59.4536 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2025 | Winter | 50 |  |  | 56.1183 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2026 | Winter | 10 |  |  | 66.5595 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2026 | Winter | 50 |  |  | 63.2802 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2027 | Winter | 10 |  |  | 72.8129 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2027 | Winter | 50 |  |  | 69.3039 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2028 | Winter | 10 |  |  | 76.0509 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2028 | Winter | 50 |  |  | 72.5305 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2029 | Winter | 10 |  |  | 78.6773 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2029 | Winter | 50 |  |  | 74.8582 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2030 | Winter | 10 |  |  | 81.1629 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2030 | Winter | 50 |  |  | 77.5373 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2031 | Winter | 10 |  |  | 83.2732 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2031 | Winter | 50 |  |  | 79.5294 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2032 | Winter | 10 |  |  | 85.4834 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2032 | Winter | 50 |  |  | 81.7407 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2033 | Winter | 10 |  |  | 86.4197 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2033 | Winter | 50 |  |  | 82.8706 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2034 | Winter | 10 |  |  | 87.7259 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2034 | Winter | 50 |  |  | 83.8526 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2035 | Winter | 10 |  |  | 90.1815 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2035 | Winter | 50 |  |  | 86.3425 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2036 | Winter | 10 |  |  | 89.3155 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2036 | Winter | 50 |  |  | 84.7668 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2037 | Winter | 10 |  |  | 92.5351 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2037 | Winter | 50 |  |  | 88.8524 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2038 | Winter | 10 |  |  | 94.3753 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2038 | Winter | 50 |  |  | 94.1939 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2039 | Winter | 10 |  |  | 80.6717 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2039 | Winter | 50 |  |  | 77.1549 | 202503 | MVA | central
zone_sub | phm | maximum |  | 2022 | Winter | 10 | 16270 | 23.521 | 48.1658 | 202503 | MVA | central
zone_sub | phm | maximum |  | 2022 | Winter | 50 | 16270 | 23.521 | 45.1092 | 202503 | MVA | central
zone_sub | phm | maximum |  | 2023 | Winter | 10 | 16562 | 25.5412 | 49.0318 | 202503 | MVA | central
zone_sub | phm | maximum |  | 2023 | Winter | 50 | 16562 | 25.5412 | 45.9202 | 202503 | MVA | central
zone_sub | phm | maximum |  | 2024 | Winter | 10 | 16854 | 27.7496 | 49.8978 | 202503 | MVA | central
zone_sub | phm | maximum |  | 2024 | Winter | 50 | 16854 | 27.7496 | 46.7311 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2025 | Winter | 10 |  |  | 67.0847 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2025 | Winter | 50 |  |  | 64.1376 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2026 | Winter | 10 |  |  | 71.7531 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2026 | Winter | 50 |  |  | 68.6294 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2027 | Winter | 10 |  |  | 72.4584 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2027 | Winter | 50 |  |  | 69.3785 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2028 | Winter | 10 |  |  | 72.887 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2028 | Winter | 50 |  |  | 69.9467 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2029 | Winter | 10 |  |  | 73.8781 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2029 | Winter | 50 |  |  | 70.9603 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2030 | Winter | 10 |  |  | 76.2493 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2030 | Winter | 50 |  |  | 73.2946 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2031 | Winter | 10 |  |  | 77.5227 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2031 | Winter | 50 |  |  | 74.8388 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2032 | Winter | 10 |  |  | 79.9897 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2032 | Winter | 50 |  |  | 76.8149 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2033 | Winter | 10 |  |  | 87.5343 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2033 | Winter | 50 |  |  | 77.8299 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2034 | Winter | 10 |  |  | 81.2629 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2034 | Winter | 50 |  |  | 78.7091 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2035 | Winter | 10 |  |  | 80.0205 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2035 | Winter | 50 |  |  | 77.0055 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2036 | Winter | 10 |  |  | 81.6454 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2036 | Winter | 50 |  |  | 78.9538 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2037 | Winter | 10 |  |  | 85.2253 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2037 | Winter | 50 |  |  | 82.0295 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2038 | Winter | 10 |  |  | 82.7648 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2038 | Winter | 50 |  |  | 79.6564 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2039 | Winter | 10 |  |  | 67.0558 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2039 | Winter | 50 |  |  | 63.9852 | 202503 | MVA | central
zone_sub | wgi | maximum |  | 2022 | Winter | 10 | 21696 | 27.3902 | 41.941 | 202503 | MVA | east
zone_sub | wgi | maximum |  | 2022 | Winter | 50 | 21696 | 27.3902 | 38.234 | 202503 | MVA | east
zone_sub | wgi | maximum |  | 2023 | Winter | 10 | 22045 | 30.4273 | 42.6315 | 202503 | MVA | east
zone_sub | wgi | maximum |  | 2023 | Winter | 50 | 22045 | 30.4273 | 38.883 | 202503 | MVA | east
zone_sub | wgi | maximum |  | 2024 | Winter | 10 | 22388 | 33.5461 | 43.3126 | 202503 | MVA | east
zone_sub | wgi | maximum |  | 2024 | Winter | 50 | 22388 | 33.5461 | 39.5207 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2025 | Winter | 10 |  |  | 47.2482 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2025 | Winter | 50 |  |  | 43.6466 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2026 | Winter | 10 |  |  | 47.6557 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2026 | Winter | 50 |  |  | 44.0841 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2027 | Winter | 10 |  |  | 49.0622 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2027 | Winter | 50 |  |  | 44.625 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2028 | Winter | 10 |  |  | 49.028 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2028 | Winter | 50 |  |  | 45.3431 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2029 | Winter | 10 |  |  | 49.3373 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2029 | Winter | 50 |  |  | 46.0239 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2030 | Winter | 10 |  |  | 50.5469 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2030 | Winter | 50 |  |  | 47.2137 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2031 | Winter | 10 |  |  | 54.0224 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2031 | Winter | 50 |  |  | 50.206 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2032 | Winter | 10 |  |  | 55.4565 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2032 | Winter | 50 |  |  | 51.8155 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2033 | Winter | 10 |  |  | 54.099 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2033 | Winter | 50 |  |  | 50.6413 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2034 | Winter | 10 |  |  | 57.8491 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2034 | Winter | 50 |  |  | 54.2764 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2035 | Winter | 10 |  |  | 56.2746 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2035 | Winter | 50 |  |  | 54.9313 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2036 | Winter | 10 |  |  | 57.6913 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2036 | Winter | 50 |  |  | 55.4021 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2037 | Winter | 10 |  |  | 58.7122 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2037 | Winter | 50 |  |  | 57.6212 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2038 | Winter | 10 |  |  | 58.2928 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2038 | Winter | 50 |  |  | 57.9824 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2039 | Winter | 10 |  |  | 49.2493 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2039 | Winter | 50 |  |  | 45.4578 | 202503 | MVA | east

## Ratings
STATION OUTPUT RATING (TRANSFORMER SUMMATION) SUMMARY
|  |  | Station N Rating |  | Station N-1 Rating |  | Station N-2 Rating
|  |  | SCR | WCR | SCR | WCR | SCR | WCR | Remarks | Remarks | Bus Target | Station Cap Bank
S/S Name | No. TX | Name Plate MVA | MVA | MVA | MVA | MVA | MVA | MVA | For N-1 Ratings | N-2 | Voltage kV | MVAr
CLN_Old | 2 | 66 | 87.3 | 95.3 | 44.6 | 48.9 | 0 | 0 | Loss of T1 |  | 22 | 12
CLN | 3 | 99 | 130.95 | 142.95 | 89.2 | 97.8 | 44.6 | 48.9
CRE | 2 | 66 | 84.3 | 93.8 | 41.1 | 46.3 | 0 | 0 | Loss of T2 or T3 |  | 22 | 12
EPG | 3 | 99 | 123.1 | 139.9 | 87.8 | 98.1 | 43.9 | 49.05 | Loss of T3 | Using Highest value | 22
KLO | 2 | 66 | 97.5 | 97.5 | 49.1 | 49.1 | 0 | 0 | Loss of T1 or T2 |  | 22.44 | 6
LLG | 1 | 33 | 47.4 | 48.3 | 0 | 0 | 0 | 0 | N rating only |  | 22 | 4
OFR | 2 | 66 | 93.2 | 93.2 | 45.2 | 48 | 0 | 0 | Loss of T1 or T2 |  | 22 | 6
PHM | 2 | 66 | 91.9 | 95.7 | 45 | 49.1 | 0 | 0 | Loss of T1 or T2 |  | 22 | 12
WGI | 3 | 40.5 | 55.8 | 56.8 | 35.3 | 36.1 | 17.65 | 18.05

## Power Factor
asset_type | asset | PF
zone_sub | cln | 1
zone_sub | cre | 1
zone_sub | cyn | 1
zone_sub | epg | 1
zone_sub | klo | 0.99
zone_sub | llg | 0.99
zone_sub | ofr | 1
zone_sub | phm | 1
zone_sub | wgi | 0.99

## FT
Forecast tool (MVA) |  | Forecast Capacity & Transfers
ZSS |  | PHM
Summer
[5 empty] | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads
DY (Apr 1 to Mar 30) |  | 2022/23 | 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2028/29 | 2029/30 | 2030/31 | 2031/32 | 2032/33 | 2033/34 | 2034/35 | 2035/36 | 2036/37 | 2037/38 | 2038/39
DY (Apr 1 to Mar 30) |  | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038
FY (Jul 1 to Jun 30) |  | 2022/23 | 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2028/29 | 2029/30 | 2030/31 | 2031/32 | 2032/33 | 2033/34 | 2034/35 | 2035/36 | 2036/37 | 2037/38 | 2038/39
FY (Jul 1 to Jun 30) |  |  |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39
Summer POE50 | 50 |  |  | 52.8621 | 69.621 | 74.1527 | 73.9998 | 73.965 | 74.4648 | 75.0153 | 76.1566 | 76.9783 | 77.4148 | 77.8841 | 78.3211 | 79.127 | 80.1321 | 80.0404
Summer POE10 | 10 |  |  | 58.7282 | 75.5207 | 79.8845 | 79.6008 | 79.5894 | 80.0199 | 81.1895 | 81.9552 | 82.7146 | 83.6062 | 84.4206 | 85.2206 | 85.2937 | 86.2309 | 85.4841
Winter
[5 empty] | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads
DM (Apr 1 to Mar 30) |  |  |  | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2028/29 | 2029/30 | 2030/31 | 2031/32 | 2032/33 | 2033/34 | 2034/35 | 2035/36 | 2036/37 | 2037/38 | 2038/39
DY (Apr 1 to Mar 30) |  |  |  | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038
FY (Jul 1 to Jun 30) |  |  |  | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2028/29 | 2029/30 | 2030/31 | 2031/32 | 2032/33 | 2033/34 | 2034/35 | 2035/36 | 2036/37 | 2037/38 | 2038/39
FY (Jul 1 to Jun 30) |  |  |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39
Winter POE50 | 50 |  |  | 46.7311 | 64.1376 | 68.6294 | 69.3785 | 69.9467 | 70.9603 | 73.2946 | 74.8388 | 76.8149 | 77.8299 | 78.7091 | 77.0055 | 78.9538 | 82.0295 | 79.6564
Winter POE10 | 10 |  |  | 49.8978 | 67.0847 | 71.7531 | 72.4584 | 72.887 | 73.8781 | 76.2493 | 77.5227 | 79.9897 | 87.5343 | 81.2629 | 80.0205 | 81.6454 | 85.2253 | 82.7648
Transfers (MVA)
|  | Feeder | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39
|  | PHM | 1.7 | 1.7 | 1.67 | 1.65 | 1.62 | 1.6 | 1.58 | 1.55 | 1.53 | 1.51 | 1.48 | 1.46 | 1.44 | 1.42 | 1.4
|  | PowerFactor | 1

## Load Duration Curves
Station
PHM
POE10
[6 empty] | Stations | KLO |  | EPG |  | CRE |  | CLN |  | PHM |  | OFR |  | LLG |  | WGI
| % of MD | Winter - MD (P10) - Duration % | Winter - MD - Hours | Summer - MD - Duration % | Summer - MD - Hours | %MD | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration %
| 100% | 0% | 0 | 0% | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| 99% | 0.03383% | 1.486 | 0.03444% | 1.5127 | 99% | 0.01722% | 0.02707% | 0% | 0.04737% | 0% | 0% | 0.00861% | 0.01353% | 0.03444% | 0.03383% | 0.01722% | 0.0203% | 0.02583% | 0.006767% | 0% | 0.006767%
| 98% | 0.07443% | 3.2692 | 0.05166% | 2.269 | 98% | 0.01722% | 0.07443% | 0.00861% | 0.08797% | 0.02583% | 0.01353% | 0.02583% | 0.0203% | 0.05166% | 0.07443% | 0.02583% | 0.0812% | 0.04305% | 0.0203% | 0% | 0.006767%
| 97% | 0.1556% | 6.8356 | 0.0861% | 3.7816 | 97% | 0.02583% | 0.09474% | 0.02583% | 0.1421% | 0.04305% | 0.02707% | 0.05166% | 0.03383% | 0.0861% | 0.1556% | 0.04305% | 0.1083% | 0.05166% | 0.04737% | 0.00861% | 0.006767%
| 95% | 0.3992% | 17.5347 | 0.1378% | 6.0506 | 95% | 0.05166% | 0.1895% | 0.09471% | 0.3519% | 0.0861% | 0.08797% | 0.1033% | 0.05413% | 0.1378% | 0.3992% | 0.07749% | 0.1759% | 0.09471% | 0.09474% | 0.00861% | 0.03383%
| 90% | 1.793% | 78.7576 | 0.3702% | 16.2611 | 90% | 0.0861% | 0.9135% | 0.1894% | 1.786% | 0.1894% | 0.7579% | 0.1808% | 0.07443% | 0.3702% | 1.793% | 0.2066% | 0.8932% | 0.353% | 0.2639% | 0.01722% | 0.1962%
| 85% | 5.393% | 236.8672 | 0.6027% | 26.4715 | 85% | 0.1205% | 2.355% | 0.353% | 4.588% | 0.2669% | 2.761% | 0.3272% | 0.318% | 0.6027% | 5.393% | 0.3702% | 2.68% | 0.7147% | 0.7443% | 0.02583% | 0.9135%
| 80% | 11.33% | 497.5104 | 0.7749% | 34.0348 | 80% | 0.31% | 5.616% | 0.6458% | 8.885% | 0.4219% | 6.787% | 0.4477% | 0.9406% | 0.7749% | 11.33% | 0.5683% | 6.11% | 1.317% | 1.915% | 0.06027% | 2.118%
| 75% | 18.3% | 803.6248 | 1.102% | 48.405 | 75% | 0.4822% | 9.995% | 0.9988% | 14.05% | 0.5338% | 11.76% | 0.5855% | 2.876% | 1.102% | 18.3% | 0.7491% | 10.38% | 2.764% | 4.601% | 0.07749% | 4.486%
| 70% | 26.3% | 1155.2107 | 1.739% | 76.3892 | 70% | 0.7491% | 14.12% | 1.498% | 19.88% | 0.8438% | 17.56% | 0.7921% | 7.376% | 1.739% | 26.3% | 0.9557% | 15.73% | 6.225% | 8.837% | 0.1292% | 8.607%
| 65% | 35.36% | 1553.1596 | 2.6% | 114.2056 | 65% | 1.154% | 18.84% | 2.265% | 27.11% | 1.102% | 25.21% | 1.05% | 12.51% | 2.6% | 35.36% | 1.541% | 22.03% | 12.05% | 15.25% | 0.1464% | 14.03%
| 60% | 46.14% | 2026.2996 | 4.055% | 178.1154 | 60% | 1.602% | 25.14% | 3.203% | 35.21% | 1.627% | 33.62% | 1.748% | 18.2% | 4.055% | 46.14% | 2.247% | 29.44% | 20.92% | 25.15% | 0.2583% | 21.29%
| 55% | 59.16% | 2598.4068 | 7.095% | 311.6074 | 55% | 2.411% | 33.56% | 4.357% | 45.33% | 2.48% | 42.68% | 2.419% | 25.42% | 7.095% | 59.16% | 3.496% | 37.5% | 33.11% | 37.15% | 0.8094% | 29.85%
| 50% | 73.62% | 3233.5201 | 14.48% | 636.0723 | 50% | 4.598% | 44.25% | 6.303% | 58.26% | 3.84% | 54.87% | 4.064% | 34.04% | 14.48% | 73.62% | 5.881% | 47.91% | 47.93% | 51.32% | 2.17% | 39.4%
| 45% | 85.96% | 3775.313 | 26.86% | 1179.4944 | 45% | 9.592% | 58.98% | 10.8% | 69.36% | 6.535% | 71.48% | 8.378% | 45.63% | 26.86% | 85.96% | 11.13% | 62.3% | 62.8% | 65.85% | 4.753% | 49.36%
| 40% | 92.73% | 4072.8088 | 41.17% | 1808.3816 | 40% | 19.83% | 71.65% | 21.2% | 75.98% | 14.01% | 84.31% | 16.88% | 65.51% | 41.17% | 92.73% | 21.13% | 79.32% | 76.24% | 79.08% | 8.662% | 59.42%
| 35% | 95.6% | 4198.821 | 63.28% | 2779.1293 | 35% | 37.74% | 78.94% | 37.58% | 85.16% | 27.53% | 88.52% | 26.59% | 78.66% | 63.28% | 95.6% | 34.85% | 87.21% | 86.9% | 88.41% | 15.86% | 68.26%
| 30% | 97.25% | 4271.3374 | 86.84% | 3814.165 | 30% | 66.82% | 83.24% | 57.09% | 93.38% | 49.73% | 90.98% | 45.59% | 83.41% | 86.84% | 97.25% | 59.02% | 90.02% | 92.6% | 93.97% | 28.71% | 75.35%
| 25% | 98.4% | 4321.8611 | 94.88% | 4166.9923 | 25% | 77.33% | 87.43% | 77.75% | 96.1% | 81.07% | 93.44% | 72.26% | 87.95% | 94.88% | 98.4% | 83.32% | 92.46% | 96.47% | 96.66% | 44.75% | 80.55%
| 20% | 99.11% | 4353.067 | 97.51% | 4282.7105 | 20% | 85.59% | 92.06% | 96.84% | 97.65% | 89.22% | 95.65% | 79.18% | 93.87% | 97.51% | 99.11% | 91.2% | 94.84% | 98.65% | 98.41% | 56.7% | 84.95%
| 15% | 99.49% | 4369.4129 | 99.38% | 4364.7722 | 15% | 96.14% | 98.9% | 99.64% | 98.65% | 96.11% | 97.43% | 86.26% | 99.55% | 99.38% | 99.49% | 97.48% | 97.23% | 99.31% | 99.14% | 68.25% | 89.03%
| 10% | 99.7% | 4378.6261 | 99.99% | 4391.6218 | 10% | 99.99% | 99.99% | 99.99% | 99.16% | 99.9% | 98.78% | 98.3% | 99.6% | 99.99% | 99.7% | 99.99% | 99.59% | 99.63% | 99.41% | 79.5% | 92.79%
| 5% | 99.99% | 4391.7028 | 99.99% | 4391.6218 | 5% | 99.99% | 99.99% | 99.99% | 99.49% | 99.99% | 99.76% | 99.99% | 99.61% | 99.99% | 99.99% | 99.99% | 99.99% | 99.68% | 99.6% | 90.07% | 96.81%
| 9.992e-14% | 99.99% | 4391.7028 | 99.99% | 4391.6218 | 0% | 99.99% | 99.99% | 99.99% | 99.99% | 99.99% | 99.99% | 99.99% | 99.63% | 99.99% | 99.99% | 99.99% | 99.99% | 99.71% | 99.63% | 99.99% | 99.99%
POE 50
[6 empty] | Stations | KLO |  | EPG |  | CRE |  | CLN |  | PHM |  | OFR |  | LLG |  | WGI
| % of MD | Winter - AD (P50) - Duration % | Winter - AD - Hours | Summer - AD - Duration % | Summer - AD - Hours | %MD | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration %
| 100% | 0% | 0 | 0% | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| 99% | 0.03383% | 1.486 | 0% | 0 | 99% | 0.03444% | 0.02707% | 0.04305% | 0.04737% | 0% | 0% | 0% | 0.01353% | 0% | 0.03383% | 0% | 0.0203% | 0.00861% | 0.006767% | 0.00861% | 0.006767%
| 98% | 0.07443% | 3.2692 | 0% | 0 | 98% | 0.05166% | 0.07443% | 0.07749% | 0.08797% | 0% | 0.01353% | 0.00861% | 0.0203% | 0% | 0.07443% | 0.00861% | 0.0812% | 0.00861% | 0.0203% | 0.00861% | 0.006767%
| 97% | 0.1556% | 6.8356 | 0.00861% | 0.37816 | 97% | 0.06888% | 0.09474% | 0.07749% | 0.1421% | 0.02583% | 0.02707% | 0.01722% | 0.03383% | 0.00861% | 0.1556% | 0.01722% | 0.1083% | 0.01722% | 0.0406% | 0.00861% | 0.006767%
| 95% | 0.3992% | 17.5347 | 0.05166% | 2.269 | 95% | 0.0861% | 0.1895% | 0.1378% | 0.3519% | 0.04305% | 0.08797% | 0.02583% | 0.05413% | 0.05166% | 0.3992% | 0.04305% | 0.1759% | 0.01722% | 0.1015% | 0.01722% | 0.03383%
| 90% | 1.793% | 78.7576 | 0.1292% | 5.6725 | 90% | 0.1292% | 0.9135% | 0.2583% | 1.786% | 0.1119% | 0.7579% | 0.1033% | 0.07443% | 0.1292% | 1.793% | 0.1033% | 0.8932% | 0.0861% | 0.3451% | 0.2066% | 0.1962%
| 85% | 5.393% | 236.8672 | 0.3616% | 15.8829 | 85% | 0.2497% | 2.355% | 0.465% | 4.588% | 0.2755% | 2.761% | 0.1808% | 0.318% | 0.3616% | 5.393% | 0.2066% | 2.68% | 0.31% | 0.9% | 0.9213% | 0.9135%
| 80% | 11.33% | 497.5104 | 0.706% | 31.0095 | 80% | 0.4133% | 5.616% | 0.7835% | 8.885% | 0.6113% | 6.787% | 0.2669% | 0.9406% | 0.706% | 11.33% | 0.6286% | 6.11% | 0.8008% | 2.517% | 2.153% | 2.118%
| 75% | 18.3% | 803.6248 | 1.662% | 72.9857 | 75% | 0.8352% | 9.995% | 1.257% | 14.05% | 0.9902% | 11.76% | 0.4047% | 2.876% | 1.662% | 18.3% | 1.309% | 10.38% | 1.834% | 5.562% | 4.486% | 4.486%
| 70% | 26.3% | 1155.2107 | 3.427% | 150.5094 | 70% | 1.619% | 14.12% | 2.101% | 19.88% | 1.911% | 17.56% | 0.8008% | 7.376% | 3.427% | 26.3% | 2.419% | 15.73% | 4.374% | 10.11% | 7.672% | 8.607%
| 65% | 35.36% | 1553.1596 | 8.188% | 359.6342 | 65% | 3.057% | 18.84% | 4.288% | 27.11% | 3.504% | 25.21% | 1.352% | 12.51% | 8.188% | 35.36% | 4.598% | 22.03% | 9.179% | 17.54% | 11.87% | 14.03%
| 60% | 46.14% | 2026.2996 | 15.71% | 689.7717 | 60% | 5.528% | 25.14% | 9.342% | 35.21% | 7.758% | 33.62% | 3.573% | 18.2% | 15.71% | 46.14% | 9.17% | 29.44% | 16.83% | 27.53% | 18.5% | 21.29%
| 55% | 59.16% | 2598.4068 | 24.94% | 1095.5419 | 55% | 11.8% | 33.56% | 17.61% | 45.33% | 16.05% | 42.68% | 8.283% | 25.42% | 24.94% | 59.16% | 14.93% | 37.5% | 27.43% | 40.02% | 27.37% | 29.85%
| 50% | 73.62% | 3233.5201 | 37.94% | 1666.1918 | 50% | 21.47% | 44.25% | 28.46% | 58.26% | 24.85% | 54.87% | 17.57% | 34.04% | 37.94% | 73.62% | 22.35% | 47.91% | 40.6% | 54.15% | 38.39% | 39.4%
| 45% | 85.96% | 3775.313 | 57.06% | 2506.0947 | 45% | 35.07% | 58.98% | 42.44% | 69.36% | 37.15% | 71.48% | 28.59% | 45.63% | 57.06% | 85.96% | 36.95% | 62.3% | 53.97% | 68.39% | 48.48% | 49.36%
| 40% | 92.73% | 4072.8088 | 72.05% | 3164.4787 | 40% | 60.78% | 71.65% | 63.35% | 75.98% | 61.17% | 84.31% | 46.88% | 65.51% | 72.05% | 92.73% | 55.62% | 79.32% | 65.21% | 80.79% | 56.57% | 59.42%
| 35% | 95.6% | 4198.821 | 80.86% | 3551.3408 | 35% | 70.59% | 78.94% | 76.04% | 85.16% | 71.05% | 88.52% | 69.68% | 78.66% | 80.86% | 95.6% | 68.46% | 87.21% | 75.09% | 89.43% | 63.94% | 68.26%
| 30% | 97.25% | 4271.3374 | 85.59% | 3758.953 | 30% | 76.73% | 83.24% | 80.97% | 93.38% | 75.06% | 90.98% | 76.64% | 83.41% | 85.59% | 97.25% | 74.6% | 90.02% | 81.51% | 94.17% | 70.48% | 75.35%
| 25% | 98.4% | 4321.8611 | 89.4% | 3926.4798 | 25% | 83.08% | 87.43% | 85.41% | 96.1% | 78.56% | 93.44% | 83.93% | 87.95% | 89.4% | 98.4% | 78.93% | 92.46% | 86.44% | 96.81% | 76.48% | 80.55%
| 20% | 99.11% | 4353.067 | 92.22% | 4050.5177 | 20% | 91.12% | 92.06% | 89.28% | 97.65% | 81.79% | 95.65% | 91.73% | 93.87% | 92.22% | 99.11% | 84.56% | 94.84% | 90.52% | 98.48% | 81.71% | 84.95%
| 15% | 99.49% | 4369.4129 | 94.55% | 4152.622 | 15% | 99.18% | 98.9% | 92.61% | 98.65% | 86.18% | 97.43% | 98.93% | 99.55% | 94.55% | 99.49% | 92.06% | 97.23% | 93.75% | 99.28% | 86.58% | 89.03%
| 10% | 99.7% | 4378.6261 | 96.73% | 4248.2976 | 10% | 99.99% | 99.99% | 95.16% | 99.16% | 91.73% | 98.78% | 99.75% | 99.6% | 96.73% | 99.7% | 99.06% | 99.59% | 96.19% | 99.59% | 91.64% | 92.79%
| 5% | 99.99% | 4391.7028 | 99.31% | 4361.7469 | 5% | 99.99% | 99.99% | 97.15% | 99.49% | 97.84% | 99.76% | 99.99% | 99.61% | 99.31% | 99.99% | 99.99% | 99.99% | 98.14% | 99.77% | 96.54% | 96.81%
| 9.992e-14% | 99.99% | 4391.7028 | 99.99% | 4391.6218 | 0% | 99.99% | 99.99% | 99.99% | 99.99% | 99.99% | 99.99% | 99.99% | 99.63% | 99.99% | 99.99% | 99.99% | 99.99% | 99.78% | 99.99% | 99.99% | 99.99%
POE10
|  | Summer | Winter
| Year | 2019/2020 | 2023
| Start | 2024-10-01 | 2024-04-01
| End | 2025-04-01 | 2024-10-01
| Days | 183 | 183
| Hours | 4392 | 4392
POE50
|  | Summer | Winter
| Year | 2023/2024 | 2023
| Start | 2023-10-01 | 2024-04-01
| End | 2024-04-01 | 2024-10-01
| Days | 183 | 183
| Hours | 4392 | 4392

## Capacity N
Option 1 - Do Nothing / Base Case - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N Rating (MVA) - Option 1 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7
SCR N Rating (MVA) - Option 1 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9
Planned Additional Capacity (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2 - 1B New PHS ZSS + Three new feeders - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N Rating (MVA) - Option 2 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7
SCR N Rating (MVA) - Option 2 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 - 2B PHM 3rd Tx + Switchroom + Two new feeders + OFR12 New Feeder - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N Rating (MVA) - Option 3 | 95.7 | 95.7 | 95.7 | 140.7 | 140.7 | 140.7 | 140.7 | 140.7 | 140.7 | 140.7 | 140.7 | 140.7 | 140.7 | 140.7 | 140.7 | 140.7 | 140.7 | 140.7 | 140.7 | 140.7 | 140.7 | 140.7 | 140.7 | 140.7 | 140.7 | 140.7 | 140.7 | 140.7 | 140.7 | 140.7
SCR N Rating (MVA) - Option 3 | 91.9 | 91.9 | 91.9 | 136.9 | 136.9 | 136.9 | 136.9 | 136.9 | 136.9 | 136.9 | 136.9 | 136.9 | 136.9 | 136.9 | 136.9 | 136.9 | 136.9 | 136.9 | 136.9 | 136.9 | 136.9 | 136.9 | 136.9 | 136.9 | 136.9 | 136.9 | 136.9 | 136.9 | 136.9 | 136.9
Capacity Added (MVA) | 0 | 0 | 0 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45
Option 4 - 3B OFR 3rd Tx + Switchroom + Two new feeders + OFR12 New Feeder - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N Rating (MVA) - Option 4 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7
SCR N Rating (MVA) - Option 4 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 - 4B LLG 2nd Tx + Switchroom + Two new feeders + OFR12 New Feeder - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N Rating (MVA) - Option 5 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7
SCR N Rating (MVA) - Option 5 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 6 - - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N Rating (MVA) - Option 6 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7
SCR N Rating (MVA) - Option 6 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 7 - - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N Rating (MVA) - Option 7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7
SCR N Rating (MVA) - Option 7 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 8 - - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N Rating (MVA) - Option 8 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7
SCR N Rating (MVA) - Option 8 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Capacity N-1
Option 1 - Do Nothing / Base Case - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-1 Rating (MVA) - Option 1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1
SCR N-1 Rating (MVA) - Option 1 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45
Planned Additional Capacity (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2 - 1B New PHS ZSS + Three new feeders - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-1 Rating (MVA) - Option 2 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1
SCR N-1 Rating (MVA) - Option 2 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 - 2B PHM 3rd Tx + Switchroom + Two new feeders + OFR12 New Feeder - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-1 Rating (MVA) - Option 3 | 49.1 | 49.1 | 49.1 | 94.1 | 94.1 | 94.1 | 94.1 | 94.1 | 94.1 | 94.1 | 94.1 | 94.1 | 94.1 | 94.1 | 94.1 | 94.1 | 94.1 | 94.1 | 94.1 | 94.1 | 94.1 | 94.1 | 94.1 | 94.1 | 94.1 | 94.1 | 94.1 | 94.1 | 94.1 | 94.1
SCR N-1 Rating (MVA) - Option 3 | 45 | 45 | 45 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90
Capacity Added (MVA) | 0 | 0 | 0 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45
Option 4 - 3B OFR 3rd Tx + Switchroom + Two new feeders + OFR12 New Feeder - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-1 Rating (MVA) - Option 4 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1
SCR N-1 Rating (MVA) - Option 4 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 - 4B LLG 2nd Tx + Switchroom + Two new feeders + OFR12 New Feeder - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-1 Rating (MVA) - Option 5 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1
SCR N-1 Rating (MVA) - Option 5 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 6 - - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-1 Rating (MVA) - Option 6 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1
SCR N-1 Rating (MVA) - Option 6 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 7 - - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-1 Rating (MVA) - Option 7 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1
SCR N-1 Rating (MVA) - Option 7 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 8 - - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-1 Rating (MVA) - Option 8 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1
SCR N-1 Rating (MVA) - Option 8 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Capacity N-2
Option 1 - Do Nothing / Base Case - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-2 Rating (MVA) - Option 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCR N-2 Rating (MVA) - Option 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Planned Additional Capacity (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2 - 1B New PHS ZSS + Three new feeders - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-2 Rating (MVA) - Option 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCR N-2 Rating (MVA) - Option 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 - 2B PHM 3rd Tx + Switchroom + Two new feeders + OFR12 New Feeder - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-2 Rating (MVA) - Option 3 | 0 | 0 | 0 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45
SCR N-2 Rating (MVA) - Option 3 | 0 | 0 | 0 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45
Capacity Added (MVA) | 0 | 0 | 0 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45
Option 4 - 3B OFR 3rd Tx + Switchroom + Two new feeders + OFR12 New Feeder - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-2 Rating (MVA) - Option 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCR N-2 Rating (MVA) - Option 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 - 4B LLG 2nd Tx + Switchroom + Two new feeders + OFR12 New Feeder - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-2 Rating (MVA) - Option 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCR N-2 Rating (MVA) - Option 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 6 - - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-2 Rating (MVA) - Option 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCR N-2 Rating (MVA) - Option 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 7 - - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-2 Rating (MVA) - Option 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCR N-2 Rating (MVA) - Option 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 8 - - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-2 Rating (MVA) - Option 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCR N-2 Rating (MVA) - Option 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Demand
Option 1 - Do Nothing / Base Case
Winter Season | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Maximum Demand (MVA) - P50 | 46.7311 | 64.1376 | 68.6294 | 69.3785 | 69.9467 | 70.9603 | 73.2946 | 74.8388 | 76.8149 | 77.8299 | 78.7091 | 77.0055 | 78.9538 | 82.0295 | 79.6564 | 79.6564 | 79.6564 | 79.6564 | 79.6564 | 79.6564 | 79.6564 | 79.6564 | 79.6564 | 79.6564 | 79.6564 | 79.6564 | 79.6564 | 79.6564 | 79.6564 | 79.6564
Maximum Demand (MVA) - P10 | 49.8978 | 67.0847 | 71.7531 | 72.4584 | 72.887 | 73.8781 | 76.2493 | 77.5227 | 79.9897 | 87.5343 | 81.2629 | 80.0205 | 81.6454 | 85.2253 | 82.7648 | 82.7648 | 82.7648 | 82.7648 | 82.7648 | 82.7648 | 82.7648 | 82.7648 | 82.7648 | 82.7648 | 82.7648 | 82.7648 | 82.7648 | 82.7648 | 82.7648 | 82.7648
Block loads (MVA) not in the forecast | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Available Transfers (MVA) | 1.7 | 1.7 | 1.67 | 1.65 | 1.62 | 1.6 | 1.58 | 1.55 | 1.53 | 1.51 | 1.48 | 1.46 | 1.44 | 1.42 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4
Demand management (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Embedded generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Maximum Demand (MVA) - Option 1 Winter POE50 | 45.0311 | 62.4376 | 66.9594 | 67.7285 | 68.3267 | 69.3603 | 71.7146 | 73.2888 | 75.2849 | 76.3199 | 77.2291 | 75.5455 | 77.5138 | 80.6095 | 78.2564 | 78.2564 | 78.2564 | 78.2564 | 78.2564 | 78.2564 | 78.2564 | 78.2564 | 78.2564 | 78.2564 | 78.2564 | 78.2564 | 78.2564 | 78.2564 | 78.2564 | 78.2564
Total Maximum Demand (MVA) - Option 1 Winter POE10 | 48.1978 | 65.3847 | 70.0831 | 70.8084 | 71.267 | 72.2781 | 74.6693 | 75.9727 | 78.4597 | 86.0243 | 79.7829 | 78.5605 | 80.2054 | 83.8053 | 81.3648 | 81.3648 | 81.3648 | 81.3648 | 81.3648 | 81.3648 | 81.3648 | 81.3648 | 81.3648 | 81.3648 | 81.3648 | 81.3648 | 81.3648 | 81.3648 | 81.3648 | 81.3648
Summer Season | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Maximum Demand (MVA) - P50 | 52.8621 | 69.621 | 74.1527 | 73.9998 | 73.965 | 74.4648 | 75.0153 | 76.1566 | 76.9783 | 77.4148 | 77.8841 | 78.3211 | 79.127 | 80.1321 | 80.0404 | 80.0404 | 80.0404 | 80.0404 | 80.0404 | 80.0404 | 80.0404 | 80.0404 | 80.0404 | 80.0404 | 80.0404 | 80.0404 | 80.0404 | 80.0404 | 80.0404 | 80.0404
Maximum Demand (MVA) - P10 | 58.7282 | 75.5207 | 79.8845 | 79.6008 | 79.5894 | 80.0199 | 81.1895 | 81.9552 | 82.7146 | 83.6062 | 84.4206 | 85.2206 | 85.2937 | 86.2309 | 85.4841 | 85.4841 | 85.4841 | 85.4841 | 85.4841 | 85.4841 | 85.4841 | 85.4841 | 85.4841 | 85.4841 | 85.4841 | 85.4841 | 85.4841 | 85.4841 | 85.4841 | 85.4841
Block loads (MVA) not in the forecast | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Available Transfers (MVA) | 1.7 | 1.7 | 1.67 | 1.65 | 1.62 | 1.6 | 1.58 | 1.55 | 1.53 | 1.51 | 1.48 | 1.46 | 1.44 | 1.42 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4
Demand management (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Embedded generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Maximum Demand (MVA) - Option 1 Summer POE50 | 51.1621 | 67.921 | 72.4827 | 72.3498 | 72.345 | 72.8648 | 73.4353 | 74.6066 | 75.4483 | 75.9048 | 76.4041 | 76.8611 | 77.687 | 78.7121 | 78.6404 | 78.6404 | 78.6404 | 78.6404 | 78.6404 | 78.6404 | 78.6404 | 78.6404 | 78.6404 | 78.6404 | 78.6404 | 78.6404 | 78.6404 | 78.6404 | 78.6404 | 78.6404
Total Maximum Demand (MVA) - Option 1 Summer POE10 | 57.0282 | 73.8207 | 78.2145 | 77.9508 | 77.9694 | 78.4199 | 79.6095 | 80.4052 | 81.1846 | 82.0962 | 82.9406 | 83.7606 | 83.8537 | 84.8109 | 84.0841 | 84.0841 | 84.0841 | 84.0841 | 84.0841 | 84.0841 | 84.0841 | 84.0841 | 84.0841 | 84.0841 | 84.0841 | 84.0841 | 84.0841 | 84.0841 | 84.0841 | 84.0841
Option 2 - 1B New PHS ZSS + Three new feeders
Year | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Added Transfers (MVA) | 0 | 0 | 0 | 19.3333 | 19.3333 | 19.3333 | 19.3333 | 19.3333 | 19.3333 | 19.3333 | 19.3333 | 19.3333 | 19.3333 | 19.3333 | 19.3333 | 19.3333 | 19.3333 | 19.3333 | 19.3333 | 19.3333 | 19.3333 | 19.3333 | 19.3333 | 19.3333 | 19.3333 | 19.3333 | 19.3333 | 19.3333 | 19.3333 | 19.3333
Added Demand management (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Added Embedded generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Maximum Demand (MVA) - Option 2 Winter POE50 | 45.0311 | 62.4376 | 66.9594 | 48.3951 | 48.9934 | 50.027 | 52.3813 | 53.9554 | 55.9516 | 56.9866 | 57.8958 | 56.2122 | 58.1805 | 61.2762 | 58.9231 | 58.9231 | 58.9231 | 58.9231 | 58.9231 | 58.9231 | 58.9231 | 58.9231 | 58.9231 | 58.9231 | 58.9231 | 58.9231 | 58.9231 | 58.9231 | 58.9231 | 58.9231
Total Maximum Demand (MVA) - Option 2 Winter POE10 | 48.1978 | 65.3847 | 70.0831 | 51.475 | 51.9336 | 52.9448 | 55.3359 | 56.6393 | 59.1264 | 66.691 | 60.4496 | 59.2272 | 60.8721 | 64.4719 | 62.0315 | 62.0315 | 62.0315 | 62.0315 | 62.0315 | 62.0315 | 62.0315 | 62.0315 | 62.0315 | 62.0315 | 62.0315 | 62.0315 | 62.0315 | 62.0315 | 62.0315 | 62.0315
Total Maximum Demand (MVA) - Option 2 Summer POE50 | 51.1621 | 67.921 | 72.4827 | 53.0165 | 53.0116 | 53.5315 | 54.102 | 55.2733 | 56.1149 | 56.5715 | 57.0707 | 57.5278 | 58.3537 | 59.3787 | 59.3071 | 59.3071 | 59.3071 | 59.3071 | 59.3071 | 59.3071 | 59.3071 | 59.3071 | 59.3071 | 59.3071 | 59.3071 | 59.3071 | 59.3071 | 59.3071 | 59.3071 | 59.3071
Total Maximum Demand (MVA) - Option 2 Summer POE10 | 57.0282 | 73.8207 | 78.2145 | 58.6175 | 58.6361 | 59.0866 | 60.2762 | 61.0719 | 61.8513 | 62.7629 | 63.6072 | 64.4273 | 64.5203 | 65.4775 | 64.7507 | 64.7507 | 64.7507 | 64.7507 | 64.7507 | 64.7507 | 64.7507 | 64.7507 | 64.7507 | 64.7507 | 64.7507 | 64.7507 | 64.7507 | 64.7507 | 64.7507 | 64.7507
Option 3 - 2B PHM 3rd Tx + Switchroom + Two new feeders + OFR12 New Feeder
Year | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Added Transfers (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Added Demand management (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Added Embedded generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Maximum Demand (MVA) - Option 3 Winter POE50 | 45.0311 | 62.4376 | 66.9594 | 67.7285 | 68.3267 | 69.3603 | 71.7146 | 73.2888 | 75.2849 | 76.3199 | 77.2291 | 75.5455 | 77.5138 | 80.6095 | 78.2564 | 78.2564 | 78.2564 | 78.2564 | 78.2564 | 78.2564 | 78.2564 | 78.2564 | 78.2564 | 78.2564 | 78.2564 | 78.2564 | 78.2564 | 78.2564 | 78.2564 | 78.2564
Total Maximum Demand (MVA) - Option 3 Winter POE10 | 48.1978 | 65.3847 | 70.0831 | 70.8084 | 71.267 | 72.2781 | 74.6693 | 75.9727 | 78.4597 | 86.0243 | 79.7829 | 78.5605 | 80.2054 | 83.8053 | 81.3648 | 81.3648 | 81.3648 | 81.3648 | 81.3648 | 81.3648 | 81.3648 | 81.3648 | 81.3648 | 81.3648 | 81.3648 | 81.3648 | 81.3648 | 81.3648 | 81.3648 | 81.3648
Total Maximum Demand (MVA) - Option 3 Summer POE50 | 51.1621 | 67.921 | 72.4827 | 72.3498 | 72.345 | 72.8648 | 73.4353 | 74.6066 | 75.4483 | 75.9048 | 76.4041 | 76.8611 | 77.687 | 78.7121 | 78.6404 | 78.6404 | 78.6404 | 78.6404 | 78.6404 | 78.6404 | 78.6404 | 78.6404 | 78.6404 | 78.6404 | 78.6404 | 78.6404 | 78.6404 | 78.6404 | 78.6404 | 78.6404
Total Maximum Demand (MVA) - Option 3 Summer POE10 | 57.0282 | 73.8207 | 78.2145 | 77.9508 | 77.9694 | 78.4199 | 79.6095 | 80.4052 | 81.1846 | 82.0962 | 82.9406 | 83.7606 | 83.8537 | 84.8109 | 84.0841 | 84.0841 | 84.0841 | 84.0841 | 84.0841 | 84.0841 | 84.0841 | 84.0841 | 84.0841 | 84.0841 | 84.0841 | 84.0841 | 84.0841 | 84.0841 | 84.0841 | 84.0841
Option 4 - 3B OFR 3rd Tx + Switchroom + Two new feeders + OFR12 New Feeder
Year | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Added Transfers (MVA) | 0 | 0 | 0 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
Added Demand management (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Added Embedded generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Maximum Demand (MVA) - Option 4 Winter POE50 | 45.0311 | 62.4376 | 66.9594 | 63.7285 | 64.3267 | 65.3603 | 67.7146 | 69.2888 | 71.2849 | 72.3199 | 73.2291 | 71.5455 | 73.5138 | 76.6095 | 74.2564 | 74.2564 | 74.2564 | 74.2564 | 74.2564 | 74.2564 | 74.2564 | 74.2564 | 74.2564 | 74.2564 | 74.2564 | 74.2564 | 74.2564 | 74.2564 | 74.2564 | 74.2564
Total Maximum Demand (MVA) - Option 4 Winter POE10 | 48.1978 | 65.3847 | 70.0831 | 66.8084 | 67.267 | 68.2781 | 70.6693 | 71.9727 | 74.4597 | 82.0243 | 75.7829 | 74.5605 | 76.2054 | 79.8053 | 77.3648 | 77.3648 | 77.3648 | 77.3648 | 77.3648 | 77.3648 | 77.3648 | 77.3648 | 77.3648 | 77.3648 | 77.3648 | 77.3648 | 77.3648 | 77.3648 | 77.3648 | 77.3648
Total Maximum Demand (MVA) - Option 4 Summer POE50 | 51.1621 | 67.921 | 72.4827 | 68.3498 | 68.345 | 68.8648 | 69.4353 | 70.6066 | 71.4483 | 71.9048 | 72.4041 | 72.8611 | 73.687 | 74.7121 | 74.6404 | 74.6404 | 74.6404 | 74.6404 | 74.6404 | 74.6404 | 74.6404 | 74.6404 | 74.6404 | 74.6404 | 74.6404 | 74.6404 | 74.6404 | 74.6404 | 74.6404 | 74.6404
Total Maximum Demand (MVA) - Option 4 Summer POE10 | 57.0282 | 73.8207 | 78.2145 | 73.9508 | 73.9694 | 74.4199 | 75.6095 | 76.4052 | 77.1846 | 78.0962 | 78.9406 | 79.7606 | 79.8537 | 80.8109 | 80.0841 | 80.0841 | 80.0841 | 80.0841 | 80.0841 | 80.0841 | 80.0841 | 80.0841 | 80.0841 | 80.0841 | 80.0841 | 80.0841 | 80.0841 | 80.0841 | 80.0841 | 80.0841
Option 5 - 4B LLG 2nd Tx + Switchroom + Two new feeders + OFR12 New Feeder
Year | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Added Transfers (MVA) | 0 | 0 | 0 | 21.75 | 21.75 | 21.75 | 21.75 | 21.75 | 21.75 | 21.75 | 21.75 | 21.75 | 21.75 | 21.75 | 21.75 | 21.75 | 21.75 | 21.75 | 21.75 | 21.75 | 21.75 | 21.75 | 21.75 | 21.75 | 21.75 | 21.75 | 21.75 | 21.75 | 21.75 | 21.75
Added Demand management (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Added Embedded generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Maximum Demand (MVA) - Option 5 Winter POE50 | 45.0311 | 62.4376 | 66.9594 | 45.9785 | 46.5767 | 47.6103 | 49.9646 | 51.5388 | 53.5349 | 54.5699 | 55.4791 | 53.7955 | 55.7638 | 58.8595 | 56.5064 | 56.5064 | 56.5064 | 56.5064 | 56.5064 | 56.5064 | 56.5064 | 56.5064 | 56.5064 | 56.5064 | 56.5064 | 56.5064 | 56.5064 | 56.5064 | 56.5064 | 56.5064
Total Maximum Demand (MVA) - Option 5 Winter POE10 | 48.1978 | 65.3847 | 70.0831 | 49.0584 | 49.517 | 50.5281 | 52.9193 | 54.2227 | 56.7097 | 64.2743 | 58.0329 | 56.8105 | 58.4554 | 62.0553 | 59.6148 | 59.6148 | 59.6148 | 59.6148 | 59.6148 | 59.6148 | 59.6148 | 59.6148 | 59.6148 | 59.6148 | 59.6148 | 59.6148 | 59.6148 | 59.6148 | 59.6148 | 59.6148
Total Maximum Demand (MVA) - Option 5 Summer POE50 | 51.1621 | 67.921 | 72.4827 | 50.5998 | 50.595 | 51.1148 | 51.6853 | 52.8566 | 53.6983 | 54.1548 | 54.6541 | 55.1111 | 55.937 | 56.9621 | 56.8904 | 56.8904 | 56.8904 | 56.8904 | 56.8904 | 56.8904 | 56.8904 | 56.8904 | 56.8904 | 56.8904 | 56.8904 | 56.8904 | 56.8904 | 56.8904 | 56.8904 | 56.8904
Total Maximum Demand (MVA) - Option 5 Summer POE10 | 57.0282 | 73.8207 | 78.2145 | 56.2008 | 56.2194 | 56.6699 | 57.8595 | 58.6552 | 59.4346 | 60.3462 | 61.1906 | 62.0106 | 62.1037 | 63.0609 | 62.3341 | 62.3341 | 62.3341 | 62.3341 | 62.3341 | 62.3341 | 62.3341 | 62.3341 | 62.3341 | 62.3341 | 62.3341 | 62.3341 | 62.3341 | 62.3341 | 62.3341 | 62.3341
Option 6 -
Year | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Added Transfers (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Added Demand management (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Added Embedded generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Maximum Demand (MVA) - Option 6 Winter POE50 | 45.0311 | 62.4376 | 66.9594 | 67.7285 | 68.3267 | 69.3603 | 71.7146 | 73.2888 | 75.2849 | 76.3199 | 77.2291 | 75.5455 | 77.5138 | 80.6095 | 78.2564 | 78.2564 | 78.2564 | 78.2564 | 78.2564 | 78.2564 | 78.2564 | 78.2564 | 78.2564 | 78.2564 | 78.2564 | 78.2564 | 78.2564 | 78.2564 | 78.2564 | 78.2564
Total Maximum Demand (MVA) - Option 6 Winter POE10 | 48.1978 | 65.3847 | 70.0831 | 70.8084 | 71.267 | 72.2781 | 74.6693 | 75.9727 | 78.4597 | 86.0243 | 79.7829 | 78.5605 | 80.2054 | 83.8053 | 81.3648 | 81.3648 | 81.3648 | 81.3648 | 81.3648 | 81.3648 | 81.3648 | 81.3648 | 81.3648 | 81.3648 | 81.3648 | 81.3648 | 81.3648 | 81.3648 | 81.3648 | 81.3648
Total Maximum Demand (MVA) - Option 6 Summer POE50 | 51.1621 | 67.921 | 72.4827 | 72.3498 | 72.345 | 72.8648 | 73.4353 | 74.6066 | 75.4483 | 75.9048 | 76.4041 | 76.8611 | 77.687 | 78.7121 | 78.6404 | 78.6404 | 78.6404 | 78.6404 | 78.6404 | 78.6404 | 78.6404 | 78.6404 | 78.6404 | 78.6404 | 78.6404 | 78.6404 | 78.6404 | 78.6404 | 78.6404 | 78.6404
Total Maximum Demand (MVA) - Option 6 Summer POE10 | 57.0282 | 73.8207 | 78.2145 | 77.9508 | 77.9694 | 78.4199 | 79.6095 | 80.4052 | 81.1846 | 82.0962 | 82.9406 | 83.7606 | 83.8537 | 84.8109 | 84.0841 | 84.0841 | 84.0841 | 84.0841 | 84.0841 | 84.0841 | 84.0841 | 84.0841 | 84.0841 | 84.0841 | 84.0841 | 84.0841 | 84.0841 | 84.0841 | 84.0841 | 84.0841
Option 7 -
Year | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Added Transfers (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Added Demand management (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Added Embedded generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Maximum Demand (MVA) - Option 7 Winter POE50 | 45.0311 | 62.4376 | 66.9594 | 67.7285 | 68.3267 | 69.3603 | 71.7146 | 73.2888 | 75.2849 | 76.3199 | 77.2291 | 75.5455 | 77.5138 | 80.6095 | 78.2564 | 78.2564 | 78.2564 | 78.2564 | 78.2564 | 78.2564 | 78.2564 | 78.2564 | 78.2564 | 78.2564 | 78.2564 | 78.2564 | 78.2564 | 78.2564 | 78.2564 | 78.2564
Total Maximum Demand (MVA) - Option 7 Winter POE10 | 48.1978 | 65.3847 | 70.0831 | 70.8084 | 71.267 | 72.2781 | 74.6693 | 75.9727 | 78.4597 | 86.0243 | 79.7829 | 78.5605 | 80.2054 | 83.8053 | 81.3648 | 81.3648 | 81.3648 | 81.3648 | 81.3648 | 81.3648 | 81.3648 | 81.3648 | 81.3648 | 81.3648 | 81.3648 | 81.3648 | 81.3648 | 81.3648 | 81.3648 | 81.3648
Total Maximum Demand (MVA) - Option 7 Summer POE50 | 51.1621 | 67.921 | 72.4827 | 72.3498 | 72.345 | 72.8648 | 73.4353 | 74.6066 | 75.4483 | 75.9048 | 76.4041 | 76.8611 | 77.687 | 78.7121 | 78.6404 | 78.6404 | 78.6404 | 78.6404 | 78.6404 | 78.6404 | 78.6404 | 78.6404 | 78.6404 | 78.6404 | 78.6404 | 78.6404 | 78.6404 | 78.6404 | 78.6404 | 78.6404
Total Maximum Demand (MVA) - Option 7 Summer POE10 | 57.0282 | 73.8207 | 78.2145 | 77.9508 | 77.9694 | 78.4199 | 79.6095 | 80.4052 | 81.1846 | 82.0962 | 82.9406 | 83.7606 | 83.8537 | 84.8109 | 84.0841 | 84.0841 | 84.0841 | 84.0841 | 84.0841 | 84.0841 | 84.0841 | 84.0841 | 84.0841 | 84.0841 | 84.0841 | 84.0841 | 84.0841 | 84.0841 | 84.0841 | 84.0841
Option 8 -
Year | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Added Transfers (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Added Demand management (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Added Embedded generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Maximum Demand (MVA) - Option 8 Winter POE50 | 45.0311 | 62.4376 | 66.9594 | 67.7285 | 68.3267 | 69.3603 | 71.7146 | 73.2888 | 75.2849 | 76.3199 | 77.2291 | 75.5455 | 77.5138 | 80.6095 | 78.2564 | 78.2564 | 78.2564 | 78.2564 | 78.2564 | 78.2564 | 78.2564 | 78.2564 | 78.2564 | 78.2564 | 78.2564 | 78.2564 | 78.2564 | 78.2564 | 78.2564 | 78.2564
Total Maximum Demand (MVA) - Option 8 Winter POE10 | 48.1978 | 65.3847 | 70.0831 | 70.8084 | 71.267 | 72.2781 | 74.6693 | 75.9727 | 78.4597 | 86.0243 | 79.7829 | 78.5605 | 80.2054 | 83.8053 | 81.3648 | 81.3648 | 81.3648 | 81.3648 | 81.3648 | 81.3648 | 81.3648 | 81.3648 | 81.3648 | 81.3648 | 81.3648 | 81.3648 | 81.3648 | 81.3648 | 81.3648 | 81.3648
Total Maximum Demand (MVA) - Option 8 Summer POE50 | 51.1621 | 67.921 | 72.4827 | 72.3498 | 72.345 | 72.8648 | 73.4353 | 74.6066 | 75.4483 | 75.9048 | 76.4041 | 76.8611 | 77.687 | 78.7121 | 78.6404 | 78.6404 | 78.6404 | 78.6404 | 78.6404 | 78.6404 | 78.6404 | 78.6404 | 78.6404 | 78.6404 | 78.6404 | 78.6404 | 78.6404 | 78.6404 | 78.6404 | 78.6404
Total Maximum Demand (MVA) - Option 8 Summer POE10 | 57.0282 | 73.8207 | 78.2145 | 77.9508 | 77.9694 | 78.4199 | 79.6095 | 80.4052 | 81.1846 | 82.0962 | 82.9406 | 83.7606 | 83.8537 | 84.8109 | 84.0841 | 84.0841 | 84.0841 | 84.0841 | 84.0841 | 84.0841 | 84.0841 | 84.0841 | 84.0841 | 84.0841 | 84.0841 | 84.0841 | 84.0841 | 84.0841 | 84.0841 | 84.0841

## Forecasted LDC
Option 1 - Do Nothing / Base Case
Winter Season | [31 empty] | Winter Season
P50 | [31 empty] | P10
% of MD | Winter - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Winter - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 45.0311 | 62.4376 | 66.9594 | 67.7285 | 68.3267 | 69.3603 | 71.7146 | 73.2888 | 75.2849 | 76.3199 | 77.2291 | 75.5455 | 77.5138 | 80.6095 | 78.2564 | 78.2564 | 78.2564 | 78.2564 | 78.2564 | 78.2564 | 78.2564 | 78.2564 | 78.2564 | 78.2564 | 78.2564 | 78.2564 | 78.2564 | 78.2564 | 78.2564 | 78.2564 | 100% | 0 | 48.1978 | 65.3847 | 70.0831 | 70.8084 | 71.267 | 72.2781 | 74.6693 | 75.9727 | 78.4597 | 86.0243 | 79.7829 | 78.5605 | 80.2054 | 83.8053 | 81.3648 | 81.3648 | 81.3648 | 81.3648 | 81.3648 | 81.3648 | 81.3648 | 81.3648 | 81.3648 | 81.3648 | 81.3648 | 81.3648 | 81.3648 | 81.3648 | 81.3648 | 81.3648
99% | 1.486 | 44.5808 | 61.8132 | 66.2898 | 67.0512 | 67.6435 | 68.6667 | 70.9975 | 72.5559 | 74.532 | 75.5567 | 76.4569 | 74.7901 | 76.7387 | 79.8034 | 77.4739 | 77.4739 | 77.4739 | 77.4739 | 77.4739 | 77.4739 | 77.4739 | 77.4739 | 77.4739 | 77.4739 | 77.4739 | 77.4739 | 77.4739 | 77.4739 | 77.4739 | 77.4739 | 99% | 1.486 | 47.7158 | 64.7309 | 69.3823 | 70.1003 | 70.5543 | 71.5553 | 73.9226 | 75.2129 | 77.6751 | 85.1641 | 78.9851 | 77.7749 | 79.4033 | 82.9672 | 80.5512 | 80.5512 | 80.5512 | 80.5512 | 80.5512 | 80.5512 | 80.5512 | 80.5512 | 80.5512 | 80.5512 | 80.5512 | 80.5512 | 80.5512 | 80.5512 | 80.5512 | 80.5512
98% | 3.2692 | 44.1305 | 61.1889 | 65.6202 | 66.3739 | 66.9602 | 67.9731 | 70.2804 | 71.823 | 73.7792 | 74.7935 | 75.6846 | 74.0346 | 75.9636 | 78.9973 | 76.6913 | 76.6913 | 76.6913 | 76.6913 | 76.6913 | 76.6913 | 76.6913 | 76.6913 | 76.6913 | 76.6913 | 76.6913 | 76.6913 | 76.6913 | 76.6913 | 76.6913 | 76.6913 | 98% | 3.2692 | 47.2338 | 64.0771 | 68.6815 | 69.3922 | 69.8416 | 70.8325 | 73.1759 | 74.4532 | 76.8905 | 84.3038 | 78.1873 | 76.9893 | 78.6013 | 82.1292 | 79.7375 | 79.7375 | 79.7375 | 79.7375 | 79.7375 | 79.7375 | 79.7375 | 79.7375 | 79.7375 | 79.7375 | 79.7375 | 79.7375 | 79.7375 | 79.7375 | 79.7375 | 79.7375
97% | 6.8356 | 43.6802 | 60.5645 | 64.9506 | 65.6966 | 66.2769 | 67.2795 | 69.5632 | 71.0901 | 73.0263 | 74.0303 | 74.9123 | 73.2792 | 75.1884 | 78.1912 | 75.9087 | 75.9087 | 75.9087 | 75.9087 | 75.9087 | 75.9087 | 75.9087 | 75.9087 | 75.9087 | 75.9087 | 75.9087 | 75.9087 | 75.9087 | 75.9087 | 75.9087 | 75.9087 | 97% | 6.8356 | 46.7518 | 63.4232 | 67.9806 | 68.6841 | 69.129 | 70.1097 | 72.4292 | 73.6935 | 76.1059 | 83.4436 | 77.3894 | 76.2037 | 77.7992 | 81.2911 | 78.9239 | 78.9239 | 78.9239 | 78.9239 | 78.9239 | 78.9239 | 78.9239 | 78.9239 | 78.9239 | 78.9239 | 78.9239 | 78.9239 | 78.9239 | 78.9239 | 78.9239 | 78.9239
95% | 17.5347 | 42.7796 | 59.3157 | 63.6114 | 64.342 | 64.9104 | 65.8923 | 68.1289 | 69.6243 | 71.5207 | 72.5039 | 73.3677 | 71.7683 | 73.6382 | 76.579 | 74.3436 | 74.3436 | 74.3436 | 74.3436 | 74.3436 | 74.3436 | 74.3436 | 74.3436 | 74.3436 | 74.3436 | 74.3436 | 74.3436 | 74.3436 | 74.3436 | 74.3436 | 74.3436 | 95% | 17.5347 | 45.7879 | 62.1155 | 66.579 | 67.268 | 67.7036 | 68.6642 | 70.9358 | 72.174 | 74.5368 | 81.7231 | 75.7938 | 74.6325 | 76.1951 | 79.615 | 77.2966 | 77.2966 | 77.2966 | 77.2966 | 77.2966 | 77.2966 | 77.2966 | 77.2966 | 77.2966 | 77.2966 | 77.2966 | 77.2966 | 77.2966 | 77.2966 | 77.2966 | 77.2966
90% | 78.7576 | 40.528 | 56.1939 | 60.2634 | 60.9556 | 61.4941 | 62.4243 | 64.5432 | 65.9599 | 67.7564 | 68.6879 | 69.5062 | 67.991 | 69.7625 | 72.5486 | 70.4308 | 70.4308 | 70.4308 | 70.4308 | 70.4308 | 70.4308 | 70.4308 | 70.4308 | 70.4308 | 70.4308 | 70.4308 | 70.4308 | 70.4308 | 70.4308 | 70.4308 | 70.4308 | 90% | 78.7576 | 43.378 | 58.8463 | 63.0748 | 63.7275 | 64.1403 | 65.0503 | 67.2023 | 68.3754 | 70.6138 | 77.4219 | 71.8046 | 70.7045 | 72.1848 | 75.4247 | 73.2283 | 73.2283 | 73.2283 | 73.2283 | 73.2283 | 73.2283 | 73.2283 | 73.2283 | 73.2283 | 73.2283 | 73.2283 | 73.2283 | 73.2283 | 73.2283 | 73.2283 | 73.2283
85% | 236.8672 | 38.2764 | 53.072 | 56.9155 | 57.5692 | 58.0777 | 58.9563 | 60.9575 | 62.2954 | 63.9922 | 64.8719 | 65.6448 | 64.2137 | 65.8868 | 68.5181 | 66.518 | 66.518 | 66.518 | 66.518 | 66.518 | 66.518 | 66.518 | 66.518 | 66.518 | 66.518 | 66.518 | 66.518 | 66.518 | 66.518 | 66.518 | 66.518 | 85% | 236.8672 | 40.9681 | 55.577 | 59.5707 | 60.1871 | 60.5769 | 61.4364 | 63.4689 | 64.5768 | 66.6908 | 73.1207 | 67.8155 | 66.7765 | 68.1746 | 71.2345 | 69.1601 | 69.1601 | 69.1601 | 69.1601 | 69.1601 | 69.1601 | 69.1601 | 69.1601 | 69.1601 | 69.1601 | 69.1601 | 69.1601 | 69.1601 | 69.1601 | 69.1601 | 69.1601
80% | 497.5104 | 36.0249 | 49.9501 | 53.5675 | 54.1828 | 54.6614 | 55.4882 | 57.3717 | 58.631 | 60.2279 | 61.056 | 61.7833 | 60.4364 | 62.0111 | 64.4876 | 62.6051 | 62.6051 | 62.6051 | 62.6051 | 62.6051 | 62.6051 | 62.6051 | 62.6051 | 62.6051 | 62.6051 | 62.6051 | 62.6051 | 62.6051 | 62.6051 | 62.6051 | 62.6051 | 80% | 497.5104 | 38.5582 | 52.3078 | 56.0665 | 56.6467 | 57.0136 | 57.8225 | 59.7354 | 60.7781 | 62.7678 | 68.8195 | 63.8263 | 62.8484 | 64.1643 | 67.0442 | 65.0919 | 65.0919 | 65.0919 | 65.0919 | 65.0919 | 65.0919 | 65.0919 | 65.0919 | 65.0919 | 65.0919 | 65.0919 | 65.0919 | 65.0919 | 65.0919 | 65.0919 | 65.0919
75% | 803.6248 | 33.7733 | 46.8282 | 50.2195 | 50.7964 | 51.245 | 52.0202 | 53.786 | 54.9666 | 56.4637 | 57.24 | 57.9219 | 56.6592 | 58.1354 | 60.4571 | 58.6923 | 58.6923 | 58.6923 | 58.6923 | 58.6923 | 58.6923 | 58.6923 | 58.6923 | 58.6923 | 58.6923 | 58.6923 | 58.6923 | 58.6923 | 58.6923 | 58.6923 | 58.6923 | 75% | 803.6248 | 36.1483 | 49.0386 | 52.5623 | 53.1063 | 53.4502 | 54.2086 | 56.0019 | 56.9795 | 58.8448 | 64.5182 | 59.8372 | 58.9204 | 60.154 | 62.8539 | 61.0236 | 61.0236 | 61.0236 | 61.0236 | 61.0236 | 61.0236 | 61.0236 | 61.0236 | 61.0236 | 61.0236 | 61.0236 | 61.0236 | 61.0236 | 61.0236 | 61.0236 | 61.0236
70% | 1155.2107 | 31.5218 | 43.7063 | 46.8715 | 47.4099 | 47.8287 | 48.5522 | 50.2003 | 51.3021 | 52.6994 | 53.424 | 54.0604 | 52.8819 | 54.2597 | 56.4267 | 54.7795 | 54.7795 | 54.7795 | 54.7795 | 54.7795 | 54.7795 | 54.7795 | 54.7795 | 54.7795 | 54.7795 | 54.7795 | 54.7795 | 54.7795 | 54.7795 | 54.7795 | 54.7795 | 70% | 1155.2107 | 33.7384 | 45.7693 | 49.0582 | 49.5659 | 49.8869 | 50.5947 | 52.2685 | 53.1809 | 54.9218 | 60.217 | 55.8481 | 54.9924 | 56.1438 | 58.6637 | 56.9554 | 56.9554 | 56.9554 | 56.9554 | 56.9554 | 56.9554 | 56.9554 | 56.9554 | 56.9554 | 56.9554 | 56.9554 | 56.9554 | 56.9554 | 56.9554 | 56.9554 | 56.9554
65% | 1553.1596 | 29.2702 | 40.5844 | 43.5236 | 44.0235 | 44.4124 | 45.0842 | 46.6145 | 47.6377 | 48.9352 | 49.608 | 50.1989 | 49.1046 | 50.384 | 52.3962 | 50.8667 | 50.8667 | 50.8667 | 50.8667 | 50.8667 | 50.8667 | 50.8667 | 50.8667 | 50.8667 | 50.8667 | 50.8667 | 50.8667 | 50.8667 | 50.8667 | 50.8667 | 50.8667 | 65% | 1553.1596 | 31.3286 | 42.5001 | 45.554 | 46.0254 | 46.3235 | 46.9808 | 48.535 | 49.3822 | 50.9988 | 55.9158 | 51.8589 | 51.0643 | 52.1335 | 54.4734 | 52.8871 | 52.8871 | 52.8871 | 52.8871 | 52.8871 | 52.8871 | 52.8871 | 52.8871 | 52.8871 | 52.8871 | 52.8871 | 52.8871 | 52.8871 | 52.8871 | 52.8871 | 52.8871
60% | 2026.2996 | 27.0187 | 37.4626 | 40.1756 | 40.6371 | 40.996 | 41.6162 | 43.0288 | 43.9733 | 45.1709 | 45.792 | 46.3375 | 45.3273 | 46.5083 | 48.3657 | 46.9539 | 46.9539 | 46.9539 | 46.9539 | 46.9539 | 46.9539 | 46.9539 | 46.9539 | 46.9539 | 46.9539 | 46.9539 | 46.9539 | 46.9539 | 46.9539 | 46.9539 | 46.9539 | 60% | 2026.2996 | 28.9187 | 39.2308 | 42.0499 | 42.485 | 42.7602 | 43.3669 | 44.8016 | 45.5836 | 47.0758 | 51.6146 | 47.8698 | 47.1363 | 48.1232 | 50.2832 | 48.8189 | 48.8189 | 48.8189 | 48.8189 | 48.8189 | 48.8189 | 48.8189 | 48.8189 | 48.8189 | 48.8189 | 48.8189 | 48.8189 | 48.8189 | 48.8189 | 48.8189 | 48.8189
55% | 2598.4068 | 24.7671 | 34.3407 | 36.8276 | 37.2507 | 37.5797 | 38.1482 | 39.4431 | 40.3088 | 41.4067 | 41.976 | 42.476 | 41.55 | 42.6326 | 44.3352 | 43.041 | 43.041 | 43.041 | 43.041 | 43.041 | 43.041 | 43.041 | 43.041 | 43.041 | 43.041 | 43.041 | 43.041 | 43.041 | 43.041 | 43.041 | 43.041 | 55% | 2598.4068 | 26.5088 | 35.9616 | 38.5457 | 38.9446 | 39.1968 | 39.753 | 41.0681 | 41.785 | 43.1529 | 47.3134 | 43.8806 | 43.2083 | 44.113 | 46.0929 | 44.7507 | 44.7507 | 44.7507 | 44.7507 | 44.7507 | 44.7507 | 44.7507 | 44.7507 | 44.7507 | 44.7507 | 44.7507 | 44.7507 | 44.7507 | 44.7507 | 44.7507 | 44.7507
50% | 3233.5201 | 22.5156 | 31.2188 | 33.4797 | 33.8642 | 34.1634 | 34.6802 | 35.8573 | 36.6444 | 37.6424 | 38.16 | 38.6146 | 37.7728 | 38.7569 | 40.3048 | 39.1282 | 39.1282 | 39.1282 | 39.1282 | 39.1282 | 39.1282 | 39.1282 | 39.1282 | 39.1282 | 39.1282 | 39.1282 | 39.1282 | 39.1282 | 39.1282 | 39.1282 | 39.1282 | 50% | 3233.5201 | 24.0989 | 32.6924 | 35.0416 | 35.4042 | 35.6335 | 36.139 | 37.3346 | 37.9863 | 39.2299 | 43.0122 | 39.8915 | 39.2803 | 40.1027 | 41.9026 | 40.6824 | 40.6824 | 40.6824 | 40.6824 | 40.6824 | 40.6824 | 40.6824 | 40.6824 | 40.6824 | 40.6824 | 40.6824 | 40.6824 | 40.6824 | 40.6824 | 40.6824 | 40.6824
45% | 3775.313 | 20.264 | 28.0969 | 30.1317 | 30.4778 | 30.747 | 31.2121 | 32.2716 | 32.9799 | 33.8782 | 34.344 | 34.7531 | 33.9955 | 34.8812 | 36.2743 | 35.2154 | 35.2154 | 35.2154 | 35.2154 | 35.2154 | 35.2154 | 35.2154 | 35.2154 | 35.2154 | 35.2154 | 35.2154 | 35.2154 | 35.2154 | 35.2154 | 35.2154 | 35.2154 | 45% | 3775.313 | 21.689 | 29.4231 | 31.5374 | 31.8638 | 32.0701 | 32.5251 | 33.6012 | 34.1877 | 35.3069 | 38.7109 | 35.9023 | 35.3522 | 36.0924 | 37.7124 | 36.6142 | 36.6142 | 36.6142 | 36.6142 | 36.6142 | 36.6142 | 36.6142 | 36.6142 | 36.6142 | 36.6142 | 36.6142 | 36.6142 | 36.6142 | 36.6142 | 36.6142 | 36.6142
40% | 4072.8088 | 18.0124 | 24.975 | 26.7837 | 27.0914 | 27.3307 | 27.7441 | 28.6859 | 29.3155 | 30.114 | 30.528 | 30.8917 | 30.2182 | 31.0055 | 32.2438 | 31.3026 | 31.3026 | 31.3026 | 31.3026 | 31.3026 | 31.3026 | 31.3026 | 31.3026 | 31.3026 | 31.3026 | 31.3026 | 31.3026 | 31.3026 | 31.3026 | 31.3026 | 31.3026 | 40% | 4072.8088 | 19.2791 | 26.1539 | 28.0332 | 28.3234 | 28.5068 | 28.9112 | 29.8677 | 30.3891 | 31.3839 | 34.4097 | 31.9132 | 31.4242 | 32.0822 | 33.5221 | 32.5459 | 32.5459 | 32.5459 | 32.5459 | 32.5459 | 32.5459 | 32.5459 | 32.5459 | 32.5459 | 32.5459 | 32.5459 | 32.5459 | 32.5459 | 32.5459 | 32.5459 | 32.5459
35% | 4198.821 | 15.7609 | 21.8532 | 23.4358 | 23.705 | 23.9144 | 24.2761 | 25.1001 | 25.6511 | 26.3497 | 26.712 | 27.0302 | 26.4409 | 27.1298 | 28.2133 | 27.3897 | 27.3897 | 27.3897 | 27.3897 | 27.3897 | 27.3897 | 27.3897 | 27.3897 | 27.3897 | 27.3897 | 27.3897 | 27.3897 | 27.3897 | 27.3897 | 27.3897 | 27.3897 | 35% | 4198.821 | 16.8692 | 22.8847 | 24.5291 | 24.7829 | 24.9434 | 25.2973 | 26.1342 | 26.5904 | 27.4609 | 30.1085 | 27.924 | 27.4962 | 28.0719 | 29.3318 | 28.4777 | 28.4777 | 28.4777 | 28.4777 | 28.4777 | 28.4777 | 28.4777 | 28.4777 | 28.4777 | 28.4777 | 28.4777 | 28.4777 | 28.4777 | 28.4777 | 28.4777 | 28.4777
30% | 4271.3374 | 13.5093 | 18.7313 | 20.0878 | 20.3185 | 20.498 | 20.8081 | 21.5144 | 21.9866 | 22.5855 | 22.896 | 23.1687 | 22.6637 | 23.2542 | 24.1829 | 23.4769 | 23.4769 | 23.4769 | 23.4769 | 23.4769 | 23.4769 | 23.4769 | 23.4769 | 23.4769 | 23.4769 | 23.4769 | 23.4769 | 23.4769 | 23.4769 | 23.4769 | 23.4769 | 30% | 4271.3374 | 14.4593 | 19.6154 | 21.0249 | 21.2425 | 21.3801 | 21.6834 | 22.4008 | 22.7918 | 23.5379 | 25.8073 | 23.9349 | 23.5682 | 24.0616 | 25.1416 | 24.4094 | 24.4094 | 24.4094 | 24.4094 | 24.4094 | 24.4094 | 24.4094 | 24.4094 | 24.4094 | 24.4094 | 24.4094 | 24.4094 | 24.4094 | 24.4094 | 24.4094 | 24.4094
25% | 4321.8611 | 11.2578 | 15.6094 | 16.7398 | 16.9321 | 17.0817 | 17.3401 | 17.9287 | 18.3222 | 18.8212 | 19.08 | 19.3073 | 18.8864 | 19.3785 | 20.1524 | 19.5641 | 19.5641 | 19.5641 | 19.5641 | 19.5641 | 19.5641 | 19.5641 | 19.5641 | 19.5641 | 19.5641 | 19.5641 | 19.5641 | 19.5641 | 19.5641 | 19.5641 | 19.5641 | 25% | 4321.8611 | 12.0494 | 16.3462 | 17.5208 | 17.7021 | 17.8167 | 18.0695 | 18.6673 | 18.9932 | 19.6149 | 21.5061 | 19.9457 | 19.6401 | 20.0513 | 20.9513 | 20.3412 | 20.3412 | 20.3412 | 20.3412 | 20.3412 | 20.3412 | 20.3412 | 20.3412 | 20.3412 | 20.3412 | 20.3412 | 20.3412 | 20.3412 | 20.3412 | 20.3412 | 20.3412
20% | 4353.067 | 9.0062 | 12.4875 | 13.3919 | 13.5457 | 13.6653 | 13.8721 | 14.3429 | 14.6578 | 15.057 | 15.264 | 15.4458 | 15.1091 | 15.5028 | 16.1219 | 15.6513 | 15.6513 | 15.6513 | 15.6513 | 15.6513 | 15.6513 | 15.6513 | 15.6513 | 15.6513 | 15.6513 | 15.6513 | 15.6513 | 15.6513 | 15.6513 | 15.6513 | 15.6513 | 20% | 4353.067 | 9.6396 | 13.0769 | 14.0166 | 14.1617 | 14.2534 | 14.4556 | 14.9339 | 15.1945 | 15.6919 | 17.2049 | 15.9566 | 15.7121 | 16.0411 | 16.7611 | 16.273 | 16.273 | 16.273 | 16.273 | 16.273 | 16.273 | 16.273 | 16.273 | 16.273 | 16.273 | 16.273 | 16.273 | 16.273 | 16.273 | 16.273 | 16.273
15% | 4369.4129 | 6.7547 | 9.3656 | 10.0439 | 10.1593 | 10.249 | 10.404 | 10.7572 | 10.9933 | 11.2927 | 11.448 | 11.5844 | 11.3318 | 11.6271 | 12.0914 | 11.7385 | 11.7385 | 11.7385 | 11.7385 | 11.7385 | 11.7385 | 11.7385 | 11.7385 | 11.7385 | 11.7385 | 11.7385 | 11.7385 | 11.7385 | 11.7385 | 11.7385 | 11.7385 | 15% | 4369.4129 | 7.2297 | 9.8077 | 10.5125 | 10.6213 | 10.69 | 10.8417 | 11.2004 | 11.3959 | 11.769 | 12.9036 | 11.9674 | 11.7841 | 12.0308 | 12.5708 | 12.2047 | 12.2047 | 12.2047 | 12.2047 | 12.2047 | 12.2047 | 12.2047 | 12.2047 | 12.2047 | 12.2047 | 12.2047 | 12.2047 | 12.2047 | 12.2047 | 12.2047 | 12.2047
10% | 4378.6261 | 4.5031 | 6.2438 | 6.6959 | 6.7728 | 6.8327 | 6.936 | 7.1715 | 7.3289 | 7.5285 | 7.632 | 7.7229 | 7.5546 | 7.7514 | 8.061 | 7.8256 | 7.8256 | 7.8256 | 7.8256 | 7.8256 | 7.8256 | 7.8256 | 7.8256 | 7.8256 | 7.8256 | 7.8256 | 7.8256 | 7.8256 | 7.8256 | 7.8256 | 7.8256 | 10% | 4378.6261 | 4.8198 | 6.5385 | 7.0083 | 7.0808 | 7.1267 | 7.2278 | 7.4669 | 7.5973 | 7.846 | 8.6024 | 7.9783 | 7.8561 | 8.0205 | 8.3805 | 8.1365 | 8.1365 | 8.1365 | 8.1365 | 8.1365 | 8.1365 | 8.1365 | 8.1365 | 8.1365 | 8.1365 | 8.1365 | 8.1365 | 8.1365 | 8.1365 | 8.1365 | 8.1365
5% | 4391.7028 | 2.2516 | 3.1219 | 3.348 | 3.3864 | 3.4163 | 3.468 | 3.5857 | 3.6644 | 3.7642 | 3.816 | 3.8615 | 3.7773 | 3.8757 | 4.0305 | 3.9128 | 3.9128 | 3.9128 | 3.9128 | 3.9128 | 3.9128 | 3.9128 | 3.9128 | 3.9128 | 3.9128 | 3.9128 | 3.9128 | 3.9128 | 3.9128 | 3.9128 | 3.9128 | 5% | 4391.7028 | 2.4099 | 3.2692 | 3.5042 | 3.5404 | 3.5633 | 3.6139 | 3.7335 | 3.7986 | 3.923 | 4.3012 | 3.9891 | 3.928 | 4.0103 | 4.1903 | 4.0682 | 4.0682 | 4.0682 | 4.0682 | 4.0682 | 4.0682 | 4.0682 | 4.0682 | 4.0682 | 4.0682 | 4.0682 | 4.0682 | 4.0682 | 4.0682 | 4.0682 | 4.0682
9.992e-14% | 4391.7028 | 4.4995e-14 | 6.2388e-14 | 6.6906e-14 | 6.7674e-14 | 6.8272e-14 | 6.9305e-14 | 7.1657e-14 | 7.323e-14 | 7.5225e-14 | 7.6259e-14 | 7.7167e-14 | 7.5485e-14 | 7.7452e-14 | 8.0545e-14 | 7.8194e-14 | 7.8194e-14 | 7.8194e-14 | 7.8194e-14 | 7.8194e-14 | 7.8194e-14 | 7.8194e-14 | 7.8194e-14 | 7.8194e-14 | 7.8194e-14 | 7.8194e-14 | 7.8194e-14 | 7.8194e-14 | 7.8194e-14 | 7.8194e-14 | 7.8194e-14 | 9.992e-14% | 4391.7028 | 4.8159e-14 | 6.5332e-14 | 7.0027e-14 | 7.0752e-14 | 7.121e-14 | 7.222e-14 | 7.461e-14 | 7.5912e-14 | 7.8397e-14 | 8.5956e-14 | 7.9719e-14 | 7.8498e-14 | 8.0141e-14 | 8.3738e-14 | 8.13e-14 | 8.13e-14 | 8.13e-14 | 8.13e-14 | 8.13e-14 | 8.13e-14 | 8.13e-14 | 8.13e-14 | 8.13e-14 | 8.13e-14 | 8.13e-14 | 8.13e-14 | 8.13e-14 | 8.13e-14 | 8.13e-14 | 8.13e-14
Summer Season | [31 empty] | Summer Season
P50 | [31 empty] | P10
% of MD | Summer - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Summer - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 51.1621 | 67.921 | 72.4827 | 72.3498 | 72.345 | 72.8648 | 73.4353 | 74.6066 | 75.4483 | 75.9048 | 76.4041 | 76.8611 | 77.687 | 78.7121 | 78.6404 | 78.6404 | 78.6404 | 78.6404 | 78.6404 | 78.6404 | 78.6404 | 78.6404 | 78.6404 | 78.6404 | 78.6404 | 78.6404 | 78.6404 | 78.6404 | 78.6404 | 78.6404 | 100% | 0 | 57.0282 | 73.8207 | 78.2145 | 77.9508 | 77.9694 | 78.4199 | 79.6095 | 80.4052 | 81.1846 | 82.0962 | 82.9406 | 83.7606 | 83.8537 | 84.8109 | 84.0841 | 84.0841 | 84.0841 | 84.0841 | 84.0841 | 84.0841 | 84.0841 | 84.0841 | 84.0841 | 84.0841 | 84.0841 | 84.0841 | 84.0841 | 84.0841 | 84.0841 | 84.0841
99% | 0 | 50.6505 | 67.2418 | 71.7579 | 71.6263 | 71.6215 | 72.1362 | 72.701 | 73.8605 | 74.6938 | 75.1458 | 75.64 | 76.0925 | 76.9101 | 77.9249 | 77.854 | 77.854 | 77.854 | 77.854 | 77.854 | 77.854 | 77.854 | 77.854 | 77.854 | 77.854 | 77.854 | 77.854 | 77.854 | 77.854 | 77.854 | 77.854 | 99% | 1.5127 | 56.4579 | 73.0825 | 77.4324 | 77.1713 | 77.1897 | 77.6357 | 78.8134 | 79.6012 | 80.3728 | 81.2753 | 82.1112 | 82.923 | 83.0151 | 83.9628 | 83.2432 | 83.2432 | 83.2432 | 83.2432 | 83.2432 | 83.2432 | 83.2432 | 83.2432 | 83.2432 | 83.2432 | 83.2432 | 83.2432 | 83.2432 | 83.2432 | 83.2432 | 83.2432
98% | 0 | 50.1389 | 66.5626 | 71.033 | 70.9028 | 70.8981 | 71.4075 | 71.9666 | 73.1145 | 73.9393 | 74.3867 | 74.876 | 75.3239 | 76.1333 | 77.1378 | 77.0676 | 77.0676 | 77.0676 | 77.0676 | 77.0676 | 77.0676 | 77.0676 | 77.0676 | 77.0676 | 77.0676 | 77.0676 | 77.0676 | 77.0676 | 77.0676 | 77.0676 | 77.0676 | 98% | 2.269 | 55.8876 | 72.3443 | 76.6503 | 76.3918 | 76.41 | 76.8515 | 78.0173 | 78.7971 | 79.5609 | 80.4543 | 81.2818 | 82.0854 | 82.1766 | 83.1147 | 82.4024 | 82.4024 | 82.4024 | 82.4024 | 82.4024 | 82.4024 | 82.4024 | 82.4024 | 82.4024 | 82.4024 | 82.4024 | 82.4024 | 82.4024 | 82.4024 | 82.4024 | 82.4024
97% | 0.37816 | 49.6272 | 65.8834 | 70.3082 | 70.1794 | 70.1746 | 70.6789 | 71.2323 | 72.3684 | 73.1848 | 73.6277 | 74.112 | 74.5553 | 75.3564 | 76.3507 | 76.2812 | 76.2812 | 76.2812 | 76.2812 | 76.2812 | 76.2812 | 76.2812 | 76.2812 | 76.2812 | 76.2812 | 76.2812 | 76.2812 | 76.2812 | 76.2812 | 76.2812 | 76.2812 | 97% | 3.7816 | 55.3173 | 71.6061 | 75.8681 | 75.6123 | 75.6303 | 76.0673 | 77.2212 | 77.9931 | 78.7491 | 79.6334 | 80.4523 | 81.2478 | 81.338 | 82.2666 | 81.5615 | 81.5615 | 81.5615 | 81.5615 | 81.5615 | 81.5615 | 81.5615 | 81.5615 | 81.5615 | 81.5615 | 81.5615 | 81.5615 | 81.5615 | 81.5615 | 81.5615 | 81.5615
95% | 2.269 | 48.604 | 64.5249 | 68.8586 | 68.7324 | 68.7277 | 69.2216 | 69.7636 | 70.8763 | 71.6758 | 72.1096 | 72.5839 | 73.0181 | 73.8027 | 74.7765 | 74.7084 | 74.7084 | 74.7084 | 74.7084 | 74.7084 | 74.7084 | 74.7084 | 74.7084 | 74.7084 | 74.7084 | 74.7084 | 74.7084 | 74.7084 | 74.7084 | 74.7084 | 74.7084 | 95% | 6.0506 | 54.1768 | 70.1297 | 74.3038 | 74.0533 | 74.071 | 74.4989 | 75.629 | 76.385 | 77.1254 | 77.9914 | 78.7935 | 79.5726 | 79.661 | 80.5703 | 79.8799 | 79.8799 | 79.8799 | 79.8799 | 79.8799 | 79.8799 | 79.8799 | 79.8799 | 79.8799 | 79.8799 | 79.8799 | 79.8799 | 79.8799 | 79.8799 | 79.8799 | 79.8799
90% | 5.6725 | 46.0459 | 61.1289 | 65.2344 | 65.1149 | 65.1105 | 65.5784 | 66.0918 | 67.1459 | 67.9034 | 68.3143 | 68.7637 | 69.175 | 69.9183 | 70.8409 | 70.7764 | 70.7764 | 70.7764 | 70.7764 | 70.7764 | 70.7764 | 70.7764 | 70.7764 | 70.7764 | 70.7764 | 70.7764 | 70.7764 | 70.7764 | 70.7764 | 70.7764 | 70.7764 | 90% | 16.2611 | 51.3254 | 66.4386 | 70.3931 | 70.1557 | 70.1725 | 70.5779 | 71.6485 | 72.3647 | 73.0662 | 73.8866 | 74.6465 | 75.3846 | 75.4683 | 76.3298 | 75.6757 | 75.6757 | 75.6757 | 75.6757 | 75.6757 | 75.6757 | 75.6757 | 75.6757 | 75.6757 | 75.6757 | 75.6757 | 75.6757 | 75.6757 | 75.6757 | 75.6757 | 75.6757
85% | 15.8829 | 43.4878 | 57.7328 | 61.6103 | 61.4974 | 61.4932 | 61.9351 | 62.42 | 63.4156 | 64.131 | 64.5191 | 64.9435 | 65.332 | 66.034 | 66.9053 | 66.8444 | 66.8444 | 66.8444 | 66.8444 | 66.8444 | 66.8444 | 66.8444 | 66.8444 | 66.8444 | 66.8444 | 66.8444 | 66.8444 | 66.8444 | 66.8444 | 66.8444 | 66.8444 | 85% | 26.4715 | 48.4739 | 62.7476 | 66.4824 | 66.2582 | 66.274 | 66.6569 | 67.6681 | 68.3445 | 69.0069 | 69.7818 | 70.4995 | 71.1965 | 71.2756 | 72.0892 | 71.4715 | 71.4715 | 71.4715 | 71.4715 | 71.4715 | 71.4715 | 71.4715 | 71.4715 | 71.4715 | 71.4715 | 71.4715 | 71.4715 | 71.4715 | 71.4715 | 71.4715 | 71.4715
80% | 31.0095 | 40.9297 | 54.3368 | 57.9862 | 57.8799 | 57.876 | 58.2919 | 58.7483 | 59.6853 | 60.3586 | 60.7239 | 61.1233 | 61.4889 | 62.1496 | 62.9697 | 62.9123 | 62.9123 | 62.9123 | 62.9123 | 62.9123 | 62.9123 | 62.9123 | 62.9123 | 62.9123 | 62.9123 | 62.9123 | 62.9123 | 62.9123 | 62.9123 | 62.9123 | 62.9123 | 80% | 34.0348 | 45.6225 | 59.0566 | 62.5716 | 62.3606 | 62.3755 | 62.7359 | 63.6876 | 64.3242 | 64.9477 | 65.677 | 66.3524 | 67.0085 | 67.0829 | 67.8487 | 67.2672 | 67.2672 | 67.2672 | 67.2672 | 67.2672 | 67.2672 | 67.2672 | 67.2672 | 67.2672 | 67.2672 | 67.2672 | 67.2672 | 67.2672 | 67.2672 | 67.2672 | 67.2672
75% | 72.9857 | 38.3716 | 50.9407 | 54.362 | 54.2624 | 54.2587 | 54.6486 | 55.0765 | 55.955 | 56.5862 | 56.9286 | 57.3031 | 57.6458 | 58.2653 | 59.0341 | 58.9803 | 58.9803 | 58.9803 | 58.9803 | 58.9803 | 58.9803 | 58.9803 | 58.9803 | 58.9803 | 58.9803 | 58.9803 | 58.9803 | 58.9803 | 58.9803 | 58.9803 | 58.9803 | 75% | 48.405 | 42.7711 | 55.3655 | 58.6609 | 58.4631 | 58.4771 | 58.8149 | 59.7071 | 60.3039 | 60.8885 | 61.5722 | 62.2054 | 62.8205 | 62.8902 | 63.6082 | 63.063 | 63.063 | 63.063 | 63.063 | 63.063 | 63.063 | 63.063 | 63.063 | 63.063 | 63.063 | 63.063 | 63.063 | 63.063 | 63.063 | 63.063 | 63.063
70% | 150.5094 | 35.8135 | 47.5447 | 50.7379 | 50.6449 | 50.6415 | 51.0054 | 51.4047 | 52.2246 | 52.8138 | 53.1334 | 53.4829 | 53.8028 | 54.3809 | 55.0984 | 55.0483 | 55.0483 | 55.0483 | 55.0483 | 55.0483 | 55.0483 | 55.0483 | 55.0483 | 55.0483 | 55.0483 | 55.0483 | 55.0483 | 55.0483 | 55.0483 | 55.0483 | 55.0483 | 70% | 76.3892 | 39.9197 | 51.6745 | 54.7502 | 54.5656 | 54.5786 | 54.8939 | 55.7266 | 56.2837 | 56.8292 | 57.4674 | 58.0584 | 58.6324 | 58.6976 | 59.3676 | 58.8588 | 58.8588 | 58.8588 | 58.8588 | 58.8588 | 58.8588 | 58.8588 | 58.8588 | 58.8588 | 58.8588 | 58.8588 | 58.8588 | 58.8588 | 58.8588 | 58.8588 | 58.8588
65% | 359.6342 | 33.2554 | 44.1486 | 47.1138 | 47.0274 | 47.0242 | 47.3621 | 47.733 | 48.4943 | 49.0414 | 49.3381 | 49.6627 | 49.9597 | 50.4966 | 51.1628 | 51.1163 | 51.1163 | 51.1163 | 51.1163 | 51.1163 | 51.1163 | 51.1163 | 51.1163 | 51.1163 | 51.1163 | 51.1163 | 51.1163 | 51.1163 | 51.1163 | 51.1163 | 51.1163 | 65% | 114.2056 | 37.0683 | 47.9835 | 50.8395 | 50.668 | 50.6801 | 50.9729 | 51.7462 | 52.2634 | 52.77 | 53.3626 | 53.9114 | 54.4444 | 54.5049 | 55.1271 | 54.6546 | 54.6546 | 54.6546 | 54.6546 | 54.6546 | 54.6546 | 54.6546 | 54.6546 | 54.6546 | 54.6546 | 54.6546 | 54.6546 | 54.6546 | 54.6546 | 54.6546 | 54.6546
60% | 689.7717 | 30.6973 | 40.7526 | 43.4896 | 43.4099 | 43.407 | 43.7189 | 44.0612 | 44.764 | 45.269 | 45.5429 | 45.8424 | 46.1167 | 46.6122 | 47.2272 | 47.1843 | 47.1843 | 47.1843 | 47.1843 | 47.1843 | 47.1843 | 47.1843 | 47.1843 | 47.1843 | 47.1843 | 47.1843 | 47.1843 | 47.1843 | 47.1843 | 47.1843 | 47.1843 | 60% | 178.1154 | 34.2169 | 44.2924 | 46.9287 | 46.7705 | 46.7817 | 47.0519 | 47.7657 | 48.2431 | 48.7108 | 49.2577 | 49.7643 | 50.2564 | 50.3122 | 50.8865 | 50.4504 | 50.4504 | 50.4504 | 50.4504 | 50.4504 | 50.4504 | 50.4504 | 50.4504 | 50.4504 | 50.4504 | 50.4504 | 50.4504 | 50.4504 | 50.4504 | 50.4504 | 50.4504
55% | 1095.5419 | 28.1392 | 37.3565 | 39.8655 | 39.7924 | 39.7897 | 40.0757 | 40.3894 | 41.0336 | 41.4965 | 41.7476 | 42.0222 | 42.2736 | 42.7279 | 43.2916 | 43.2522 | 43.2522 | 43.2522 | 43.2522 | 43.2522 | 43.2522 | 43.2522 | 43.2522 | 43.2522 | 43.2522 | 43.2522 | 43.2522 | 43.2522 | 43.2522 | 43.2522 | 43.2522 | 55% | 311.6074 | 31.3655 | 40.6014 | 43.018 | 42.8729 | 42.8832 | 43.131 | 43.7852 | 44.2229 | 44.6515 | 45.1529 | 45.6173 | 46.0683 | 46.1195 | 46.646 | 46.2462 | 46.2462 | 46.2462 | 46.2462 | 46.2462 | 46.2462 | 46.2462 | 46.2462 | 46.2462 | 46.2462 | 46.2462 | 46.2462 | 46.2462 | 46.2462 | 46.2462 | 46.2462
50% | 1666.1918 | 25.581 | 33.9605 | 36.2413 | 36.1749 | 36.1725 | 36.4324 | 36.7177 | 37.3033 | 37.7241 | 37.9524 | 38.202 | 38.4306 | 38.8435 | 39.356 | 39.3202 | 39.3202 | 39.3202 | 39.3202 | 39.3202 | 39.3202 | 39.3202 | 39.3202 | 39.3202 | 39.3202 | 39.3202 | 39.3202 | 39.3202 | 39.3202 | 39.3202 | 39.3202 | 50% | 636.0723 | 28.5141 | 36.9103 | 39.1073 | 38.9754 | 38.9847 | 39.21 | 39.8047 | 40.2026 | 40.5923 | 41.0481 | 41.4703 | 41.8803 | 41.9268 | 42.4054 | 42.042 | 42.042 | 42.042 | 42.042 | 42.042 | 42.042 | 42.042 | 42.042 | 42.042 | 42.042 | 42.042 | 42.042 | 42.042 | 42.042 | 42.042 | 42.042
45% | 2506.0947 | 23.0229 | 30.5644 | 32.6172 | 32.5574 | 32.5552 | 32.7892 | 33.0459 | 33.573 | 33.9517 | 34.1572 | 34.3818 | 34.5875 | 34.9592 | 35.4204 | 35.3882 | 35.3882 | 35.3882 | 35.3882 | 35.3882 | 35.3882 | 35.3882 | 35.3882 | 35.3882 | 35.3882 | 35.3882 | 35.3882 | 35.3882 | 35.3882 | 35.3882 | 35.3882 | 45% | 1179.4944 | 25.6627 | 33.2193 | 35.1965 | 35.0779 | 35.0862 | 35.289 | 35.8243 | 36.1824 | 36.5331 | 36.9433 | 37.3233 | 37.6923 | 37.7341 | 38.1649 | 37.8378 | 37.8378 | 37.8378 | 37.8378 | 37.8378 | 37.8378 | 37.8378 | 37.8378 | 37.8378 | 37.8378 | 37.8378 | 37.8378 | 37.8378 | 37.8378 | 37.8378 | 37.8378
40% | 3164.4787 | 20.4648 | 27.1684 | 28.9931 | 28.9399 | 28.938 | 29.1459 | 29.3741 | 29.8426 | 30.1793 | 30.3619 | 30.5616 | 30.7444 | 31.0748 | 31.4848 | 31.4562 | 31.4562 | 31.4562 | 31.4562 | 31.4562 | 31.4562 | 31.4562 | 31.4562 | 31.4562 | 31.4562 | 31.4562 | 31.4562 | 31.4562 | 31.4562 | 31.4562 | 31.4562 | 40% | 1808.3816 | 22.8113 | 29.5283 | 31.2858 | 31.1803 | 31.1878 | 31.368 | 31.8438 | 32.1621 | 32.4738 | 32.8385 | 33.1762 | 33.5042 | 33.5415 | 33.9244 | 33.6336 | 33.6336 | 33.6336 | 33.6336 | 33.6336 | 33.6336 | 33.6336 | 33.6336 | 33.6336 | 33.6336 | 33.6336 | 33.6336 | 33.6336 | 33.6336 | 33.6336 | 33.6336
35% | 3551.3408 | 17.9067 | 23.7723 | 25.3689 | 25.3224 | 25.3207 | 25.5027 | 25.7024 | 26.1123 | 26.4069 | 26.5667 | 26.7414 | 26.9014 | 27.1905 | 27.5492 | 27.5241 | 27.5241 | 27.5241 | 27.5241 | 27.5241 | 27.5241 | 27.5241 | 27.5241 | 27.5241 | 27.5241 | 27.5241 | 27.5241 | 27.5241 | 27.5241 | 27.5241 | 27.5241 | 35% | 2779.1293 | 19.9599 | 25.8372 | 27.3751 | 27.2828 | 27.2893 | 27.447 | 27.8633 | 28.1418 | 28.4146 | 28.7337 | 29.0292 | 29.3162 | 29.3488 | 29.6838 | 29.4294 | 29.4294 | 29.4294 | 29.4294 | 29.4294 | 29.4294 | 29.4294 | 29.4294 | 29.4294 | 29.4294 | 29.4294 | 29.4294 | 29.4294 | 29.4294 | 29.4294 | 29.4294
30% | 3758.953 | 15.3486 | 20.3763 | 21.7448 | 21.705 | 21.7035 | 21.8595 | 22.0306 | 22.382 | 22.6345 | 22.7714 | 22.9212 | 23.0583 | 23.3061 | 23.6136 | 23.5921 | 23.5921 | 23.5921 | 23.5921 | 23.5921 | 23.5921 | 23.5921 | 23.5921 | 23.5921 | 23.5921 | 23.5921 | 23.5921 | 23.5921 | 23.5921 | 23.5921 | 23.5921 | 30% | 3814.165 | 17.1085 | 22.1462 | 23.4644 | 23.3852 | 23.3908 | 23.526 | 23.8828 | 24.1216 | 24.3554 | 24.6289 | 24.8822 | 25.1282 | 25.1561 | 25.4433 | 25.2252 | 25.2252 | 25.2252 | 25.2252 | 25.2252 | 25.2252 | 25.2252 | 25.2252 | 25.2252 | 25.2252 | 25.2252 | 25.2252 | 25.2252 | 25.2252 | 25.2252 | 25.2252
25% | 3926.4798 | 12.7905 | 16.9802 | 18.1207 | 18.0875 | 18.0862 | 18.2162 | 18.3588 | 18.6517 | 18.8621 | 18.9762 | 19.101 | 19.2153 | 19.4218 | 19.678 | 19.6601 | 19.6601 | 19.6601 | 19.6601 | 19.6601 | 19.6601 | 19.6601 | 19.6601 | 19.6601 | 19.6601 | 19.6601 | 19.6601 | 19.6601 | 19.6601 | 19.6601 | 19.6601 | 25% | 4166.9923 | 14.257 | 18.4552 | 19.5536 | 19.4877 | 19.4924 | 19.605 | 19.9024 | 20.1013 | 20.2962 | 20.5241 | 20.7351 | 20.9402 | 20.9634 | 21.2027 | 21.021 | 21.021 | 21.021 | 21.021 | 21.021 | 21.021 | 21.021 | 21.021 | 21.021 | 21.021 | 21.021 | 21.021 | 21.021 | 21.021 | 21.021 | 21.021
20% | 4050.5177 | 10.2324 | 13.5842 | 14.4965 | 14.47 | 14.469 | 14.573 | 14.6871 | 14.9213 | 15.0897 | 15.181 | 15.2808 | 15.3722 | 15.5374 | 15.7424 | 15.7281 | 15.7281 | 15.7281 | 15.7281 | 15.7281 | 15.7281 | 15.7281 | 15.7281 | 15.7281 | 15.7281 | 15.7281 | 15.7281 | 15.7281 | 15.7281 | 15.7281 | 15.7281 | 20% | 4282.7105 | 11.4056 | 14.7641 | 15.6429 | 15.5902 | 15.5939 | 15.684 | 15.9219 | 16.081 | 16.2369 | 16.4192 | 16.5881 | 16.7521 | 16.7707 | 16.9622 | 16.8168 | 16.8168 | 16.8168 | 16.8168 | 16.8168 | 16.8168 | 16.8168 | 16.8168 | 16.8168 | 16.8168 | 16.8168 | 16.8168 | 16.8168 | 16.8168 | 16.8168 | 16.8168
15% | 4152.622 | 7.6743 | 10.1881 | 10.8724 | 10.8525 | 10.8517 | 10.9297 | 11.0153 | 11.191 | 11.3172 | 11.3857 | 11.4606 | 11.5292 | 11.6531 | 11.8068 | 11.7961 | 11.7961 | 11.7961 | 11.7961 | 11.7961 | 11.7961 | 11.7961 | 11.7961 | 11.7961 | 11.7961 | 11.7961 | 11.7961 | 11.7961 | 11.7961 | 11.7961 | 11.7961 | 15% | 4364.7722 | 8.5542 | 11.0731 | 11.7322 | 11.6926 | 11.6954 | 11.763 | 11.9414 | 12.0608 | 12.1777 | 12.3144 | 12.4411 | 12.5641 | 12.578 | 12.7216 | 12.6126 | 12.6126 | 12.6126 | 12.6126 | 12.6126 | 12.6126 | 12.6126 | 12.6126 | 12.6126 | 12.6126 | 12.6126 | 12.6126 | 12.6126 | 12.6126 | 12.6126 | 12.6126
10% | 4248.2976 | 5.1162 | 6.7921 | 7.2483 | 7.235 | 7.2345 | 7.2865 | 7.3435 | 7.4607 | 7.5448 | 7.5905 | 7.6404 | 7.6861 | 7.7687 | 7.8712 | 7.864 | 7.864 | 7.864 | 7.864 | 7.864 | 7.864 | 7.864 | 7.864 | 7.864 | 7.864 | 7.864 | 7.864 | 7.864 | 7.864 | 7.864 | 7.864 | 10% | 4391.6218 | 5.7028 | 7.3821 | 7.8215 | 7.7951 | 7.7969 | 7.842 | 7.9609 | 8.0405 | 8.1185 | 8.2096 | 8.2941 | 8.3761 | 8.3854 | 8.4811 | 8.4084 | 8.4084 | 8.4084 | 8.4084 | 8.4084 | 8.4084 | 8.4084 | 8.4084 | 8.4084 | 8.4084 | 8.4084 | 8.4084 | 8.4084 | 8.4084 | 8.4084 | 8.4084
5% | 4361.7469 | 2.5581 | 3.396 | 3.6241 | 3.6175 | 3.6172 | 3.6432 | 3.6718 | 3.7303 | 3.7724 | 3.7952 | 3.8202 | 3.8431 | 3.8844 | 3.9356 | 3.932 | 3.932 | 3.932 | 3.932 | 3.932 | 3.932 | 3.932 | 3.932 | 3.932 | 3.932 | 3.932 | 3.932 | 3.932 | 3.932 | 3.932 | 3.932 | 5% | 4391.6218 | 2.8514 | 3.691 | 3.9107 | 3.8975 | 3.8985 | 3.921 | 3.9805 | 4.0203 | 4.0592 | 4.1048 | 4.147 | 4.188 | 4.1927 | 4.2405 | 4.2042 | 4.2042 | 4.2042 | 4.2042 | 4.2042 | 4.2042 | 4.2042 | 4.2042 | 4.2042 | 4.2042 | 4.2042 | 4.2042 | 4.2042 | 4.2042 | 4.2042 | 4.2042
9.992e-14% | 4391.6218 | 5.1121e-14 | 6.7867e-14 | 7.2425e-14 | 7.2292e-14 | 7.2287e-14 | 7.2807e-14 | 7.3377e-14 | 7.4547e-14 | 7.5388e-14 | 7.5844e-14 | 7.6343e-14 | 7.68e-14 | 7.7625e-14 | 7.8649e-14 | 7.8578e-14 | 7.8578e-14 | 7.8578e-14 | 7.8578e-14 | 7.8578e-14 | 7.8578e-14 | 7.8578e-14 | 7.8578e-14 | 7.8578e-14 | 7.8578e-14 | 7.8578e-14 | 7.8578e-14 | 7.8578e-14 | 7.8578e-14 | 7.8578e-14 | 7.8578e-14 | 9.992e-14% | 4391.6218 | 5.6983e-14 | 7.3762e-14 | 7.8152e-14 | 7.7889e-14 | 7.7907e-14 | 7.8357e-14 | 7.9546e-14 | 8.0341e-14 | 8.112e-14 | 8.2031e-14 | 8.2874e-14 | 8.3694e-14 | 8.3787e-14 | 8.4743e-14 | 8.4017e-14 | 8.4017e-14 | 8.4017e-14 | 8.4017e-14 | 8.4017e-14 | 8.4017e-14 | 8.4017e-14 | 8.4017e-14 | 8.4017e-14 | 8.4017e-14 | 8.4017e-14 | 8.4017e-14 | 8.4017e-14 | 8.4017e-14 | 8.4017e-14 | 8.4017e-14
Option 2
Winter Season | [31 empty] | Winter Season
P50 | [31 empty] | P10
% of MD | Winter - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Winter - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 45.0311 | 62.4376 | 66.9594 | 48.3951 | 48.9934 | 50.027 | 52.3813 | 53.9554 | 55.9516 | 56.9866 | 57.8958 | 56.2122 | 58.1805 | 61.2762 | 58.9231 | 58.9231 | 58.9231 | 58.9231 | 58.9231 | 58.9231 | 58.9231 | 58.9231 | 58.9231 | 58.9231 | 58.9231 | 58.9231 | 58.9231 | 58.9231 | 58.9231 | 58.9231 | 100% | 0 | 48.1978 | 65.3847 | 70.0831 | 51.475 | 51.9336 | 52.9448 | 55.3359 | 56.6393 | 59.1264 | 66.691 | 60.4496 | 59.2272 | 60.8721 | 64.4719 | 62.0315 | 62.0315 | 62.0315 | 62.0315 | 62.0315 | 62.0315 | 62.0315 | 62.0315 | 62.0315 | 62.0315 | 62.0315 | 62.0315 | 62.0315 | 62.0315 | 62.0315 | 62.0315
99% | 1.486 | 44.5808 | 61.8132 | 66.2898 | 47.9112 | 48.5035 | 49.5267 | 51.8575 | 53.4159 | 55.392 | 56.4167 | 57.3169 | 55.6501 | 57.5987 | 60.6634 | 58.3339 | 58.3339 | 58.3339 | 58.3339 | 58.3339 | 58.3339 | 58.3339 | 58.3339 | 58.3339 | 58.3339 | 58.3339 | 58.3339 | 58.3339 | 58.3339 | 58.3339 | 58.3339 | 99% | 1.486 | 47.7158 | 64.7309 | 69.3823 | 50.9603 | 51.4143 | 52.4153 | 54.7826 | 56.0729 | 58.5351 | 66.0241 | 59.8451 | 58.6349 | 60.2633 | 63.8272 | 61.4112 | 61.4112 | 61.4112 | 61.4112 | 61.4112 | 61.4112 | 61.4112 | 61.4112 | 61.4112 | 61.4112 | 61.4112 | 61.4112 | 61.4112 | 61.4112 | 61.4112 | 61.4112
98% | 3.2692 | 44.1305 | 61.1889 | 65.6202 | 47.4272 | 48.0135 | 49.0264 | 51.3337 | 52.8763 | 54.8325 | 55.8469 | 56.7379 | 55.088 | 57.0169 | 60.0507 | 57.7446 | 57.7446 | 57.7446 | 57.7446 | 57.7446 | 57.7446 | 57.7446 | 57.7446 | 57.7446 | 57.7446 | 57.7446 | 57.7446 | 57.7446 | 57.7446 | 57.7446 | 57.7446 | 98% | 3.2692 | 47.2338 | 64.0771 | 68.6815 | 50.4455 | 50.895 | 51.8859 | 54.2292 | 55.5065 | 57.9439 | 65.3572 | 59.2406 | 58.0427 | 59.6546 | 63.1825 | 60.7909 | 60.7909 | 60.7909 | 60.7909 | 60.7909 | 60.7909 | 60.7909 | 60.7909 | 60.7909 | 60.7909 | 60.7909 | 60.7909 | 60.7909 | 60.7909 | 60.7909 | 60.7909
97% | 6.8356 | 43.6802 | 60.5645 | 64.9506 | 46.9433 | 47.5236 | 48.5262 | 50.8099 | 52.3368 | 54.273 | 55.277 | 56.1589 | 54.5258 | 56.4351 | 59.4379 | 57.1554 | 57.1554 | 57.1554 | 57.1554 | 57.1554 | 57.1554 | 57.1554 | 57.1554 | 57.1554 | 57.1554 | 57.1554 | 57.1554 | 57.1554 | 57.1554 | 57.1554 | 57.1554 | 97% | 6.8356 | 46.7518 | 63.4232 | 67.9806 | 49.9308 | 50.3756 | 51.3564 | 53.6758 | 54.9401 | 57.3526 | 64.6903 | 58.6361 | 57.4504 | 59.0459 | 62.5378 | 60.1706 | 60.1706 | 60.1706 | 60.1706 | 60.1706 | 60.1706 | 60.1706 | 60.1706 | 60.1706 | 60.1706 | 60.1706 | 60.1706 | 60.1706 | 60.1706 | 60.1706 | 60.1706
95% | 17.5347 | 42.7796 | 59.3157 | 63.6114 | 45.9754 | 46.5437 | 47.5256 | 49.7622 | 51.2577 | 53.154 | 54.1373 | 55.001 | 53.4016 | 55.2715 | 58.2124 | 55.9769 | 55.9769 | 55.9769 | 55.9769 | 55.9769 | 55.9769 | 55.9769 | 55.9769 | 55.9769 | 55.9769 | 55.9769 | 55.9769 | 55.9769 | 55.9769 | 55.9769 | 55.9769 | 95% | 17.5347 | 45.7879 | 62.1155 | 66.579 | 48.9013 | 49.337 | 50.2975 | 52.5691 | 53.8074 | 56.1701 | 63.3564 | 57.4271 | 56.2658 | 57.8285 | 61.2483 | 58.9299 | 58.9299 | 58.9299 | 58.9299 | 58.9299 | 58.9299 | 58.9299 | 58.9299 | 58.9299 | 58.9299 | 58.9299 | 58.9299 | 58.9299 | 58.9299 | 58.9299 | 58.9299
90% | 78.7576 | 40.528 | 56.1939 | 60.2634 | 43.5556 | 44.0941 | 45.0243 | 47.1432 | 48.5599 | 50.3564 | 51.2879 | 52.1062 | 50.591 | 52.3625 | 55.1486 | 53.0308 | 53.0308 | 53.0308 | 53.0308 | 53.0308 | 53.0308 | 53.0308 | 53.0308 | 53.0308 | 53.0308 | 53.0308 | 53.0308 | 53.0308 | 53.0308 | 53.0308 | 53.0308 | 90% | 78.7576 | 43.378 | 58.8463 | 63.0748 | 46.3275 | 46.7403 | 47.6503 | 49.8023 | 50.9754 | 53.2138 | 60.0219 | 54.4046 | 53.3045 | 54.7848 | 58.0247 | 55.8283 | 55.8283 | 55.8283 | 55.8283 | 55.8283 | 55.8283 | 55.8283 | 55.8283 | 55.8283 | 55.8283 | 55.8283 | 55.8283 | 55.8283 | 55.8283 | 55.8283 | 55.8283
85% | 236.8672 | 38.2764 | 53.072 | 56.9155 | 41.1359 | 41.6444 | 42.5229 | 44.5241 | 45.8621 | 47.5588 | 48.4386 | 49.2114 | 47.7804 | 49.4534 | 52.0848 | 50.0846 | 50.0846 | 50.0846 | 50.0846 | 50.0846 | 50.0846 | 50.0846 | 50.0846 | 50.0846 | 50.0846 | 50.0846 | 50.0846 | 50.0846 | 50.0846 | 50.0846 | 50.0846 | 85% | 236.8672 | 40.9681 | 55.577 | 59.5707 | 43.7538 | 44.1436 | 45.003 | 47.0355 | 48.1434 | 50.2574 | 56.6873 | 51.3822 | 50.3431 | 51.7412 | 54.8011 | 52.7268 | 52.7268 | 52.7268 | 52.7268 | 52.7268 | 52.7268 | 52.7268 | 52.7268 | 52.7268 | 52.7268 | 52.7268 | 52.7268 | 52.7268 | 52.7268 | 52.7268 | 52.7268
80% | 497.5104 | 36.0249 | 49.9501 | 53.5675 | 38.7161 | 39.1947 | 40.0216 | 41.9051 | 43.1643 | 44.7613 | 45.5893 | 46.3166 | 44.9698 | 46.5444 | 49.0209 | 47.1385 | 47.1385 | 47.1385 | 47.1385 | 47.1385 | 47.1385 | 47.1385 | 47.1385 | 47.1385 | 47.1385 | 47.1385 | 47.1385 | 47.1385 | 47.1385 | 47.1385 | 47.1385 | 80% | 497.5104 | 38.5582 | 52.3078 | 56.0665 | 41.18 | 41.5469 | 42.3558 | 44.2687 | 45.3115 | 47.3011 | 53.3528 | 48.3597 | 47.3818 | 48.6976 | 51.5775 | 49.6252 | 49.6252 | 49.6252 | 49.6252 | 49.6252 | 49.6252 | 49.6252 | 49.6252 | 49.6252 | 49.6252 | 49.6252 | 49.6252 | 49.6252 | 49.6252 | 49.6252 | 49.6252
75% | 803.6248 | 33.7733 | 46.8282 | 50.2195 | 36.2964 | 36.745 | 37.5202 | 39.286 | 40.4666 | 41.9637 | 42.74 | 43.4219 | 42.1592 | 43.6354 | 45.9571 | 44.1923 | 44.1923 | 44.1923 | 44.1923 | 44.1923 | 44.1923 | 44.1923 | 44.1923 | 44.1923 | 44.1923 | 44.1923 | 44.1923 | 44.1923 | 44.1923 | 44.1923 | 44.1923 | 75% | 803.6248 | 36.1483 | 49.0386 | 52.5623 | 38.6063 | 38.9502 | 39.7086 | 41.5019 | 42.4795 | 44.3448 | 50.0182 | 45.3372 | 44.4204 | 45.654 | 48.3539 | 46.5236 | 46.5236 | 46.5236 | 46.5236 | 46.5236 | 46.5236 | 46.5236 | 46.5236 | 46.5236 | 46.5236 | 46.5236 | 46.5236 | 46.5236 | 46.5236 | 46.5236 | 46.5236
70% | 1155.2107 | 31.5218 | 43.7063 | 46.8715 | 33.8766 | 34.2954 | 35.0189 | 36.6669 | 37.7688 | 39.1661 | 39.8906 | 40.5271 | 39.3485 | 40.7264 | 42.8933 | 41.2462 | 41.2462 | 41.2462 | 41.2462 | 41.2462 | 41.2462 | 41.2462 | 41.2462 | 41.2462 | 41.2462 | 41.2462 | 41.2462 | 41.2462 | 41.2462 | 41.2462 | 41.2462 | 70% | 1155.2107 | 33.7384 | 45.7693 | 49.0582 | 36.0325 | 36.3535 | 37.0613 | 38.7351 | 39.6475 | 41.3885 | 46.6837 | 42.3147 | 41.459 | 42.6104 | 45.1304 | 43.422 | 43.422 | 43.422 | 43.422 | 43.422 | 43.422 | 43.422 | 43.422 | 43.422 | 43.422 | 43.422 | 43.422 | 43.422 | 43.422 | 43.422 | 43.422
65% | 1553.1596 | 29.2702 | 40.5844 | 43.5236 | 31.4568 | 31.8457 | 32.5175 | 34.0479 | 35.071 | 36.3685 | 37.0413 | 37.6323 | 36.5379 | 37.8173 | 39.8295 | 38.3 | 38.3 | 38.3 | 38.3 | 38.3 | 38.3 | 38.3 | 38.3 | 38.3 | 38.3 | 38.3 | 38.3 | 38.3 | 38.3 | 38.3 | 38.3 | 65% | 1553.1596 | 31.3286 | 42.5001 | 45.554 | 33.4588 | 33.7569 | 34.4141 | 35.9684 | 36.8156 | 38.4322 | 43.3491 | 39.2922 | 38.4977 | 39.5668 | 41.9068 | 40.3205 | 40.3205 | 40.3205 | 40.3205 | 40.3205 | 40.3205 | 40.3205 | 40.3205 | 40.3205 | 40.3205 | 40.3205 | 40.3205 | 40.3205 | 40.3205 | 40.3205 | 40.3205
60% | 2026.2996 | 27.0187 | 37.4626 | 40.1756 | 29.0371 | 29.396 | 30.0162 | 31.4288 | 32.3733 | 33.5709 | 34.192 | 34.7375 | 33.7273 | 34.9083 | 36.7657 | 35.3539 | 35.3539 | 35.3539 | 35.3539 | 35.3539 | 35.3539 | 35.3539 | 35.3539 | 35.3539 | 35.3539 | 35.3539 | 35.3539 | 35.3539 | 35.3539 | 35.3539 | 35.3539 | 60% | 2026.2996 | 28.9187 | 39.2308 | 42.0499 | 30.885 | 31.1602 | 31.7669 | 33.2016 | 33.9836 | 35.4758 | 40.0146 | 36.2698 | 35.5363 | 36.5232 | 38.6832 | 37.2189 | 37.2189 | 37.2189 | 37.2189 | 37.2189 | 37.2189 | 37.2189 | 37.2189 | 37.2189 | 37.2189 | 37.2189 | 37.2189 | 37.2189 | 37.2189 | 37.2189 | 37.2189
55% | 2598.4068 | 24.7671 | 34.3407 | 36.8276 | 26.6173 | 26.9464 | 27.5148 | 28.8097 | 29.6755 | 30.7734 | 31.3426 | 31.8427 | 30.9167 | 31.9993 | 33.7019 | 32.4077 | 32.4077 | 32.4077 | 32.4077 | 32.4077 | 32.4077 | 32.4077 | 32.4077 | 32.4077 | 32.4077 | 32.4077 | 32.4077 | 32.4077 | 32.4077 | 32.4077 | 32.4077 | 55% | 2598.4068 | 26.5088 | 35.9616 | 38.5457 | 28.3113 | 28.5635 | 29.1196 | 30.4348 | 31.1516 | 32.5195 | 36.68 | 33.2473 | 32.575 | 33.4796 | 35.4596 | 34.1173 | 34.1173 | 34.1173 | 34.1173 | 34.1173 | 34.1173 | 34.1173 | 34.1173 | 34.1173 | 34.1173 | 34.1173 | 34.1173 | 34.1173 | 34.1173 | 34.1173 | 34.1173
50% | 3233.5201 | 22.5156 | 31.2188 | 33.4797 | 24.1976 | 24.4967 | 25.0135 | 26.1907 | 26.9777 | 27.9758 | 28.4933 | 28.9479 | 28.1061 | 29.0903 | 30.6381 | 29.4615 | 29.4615 | 29.4615 | 29.4615 | 29.4615 | 29.4615 | 29.4615 | 29.4615 | 29.4615 | 29.4615 | 29.4615 | 29.4615 | 29.4615 | 29.4615 | 29.4615 | 29.4615 | 50% | 3233.5201 | 24.0989 | 32.6924 | 35.0416 | 25.7375 | 25.9668 | 26.4724 | 27.668 | 28.3197 | 29.5632 | 33.3455 | 30.2248 | 29.6136 | 30.436 | 32.236 | 31.0157 | 31.0157 | 31.0157 | 31.0157 | 31.0157 | 31.0157 | 31.0157 | 31.0157 | 31.0157 | 31.0157 | 31.0157 | 31.0157 | 31.0157 | 31.0157 | 31.0157 | 31.0157
45% | 3775.313 | 20.264 | 28.0969 | 30.1317 | 21.7778 | 22.047 | 22.5121 | 23.5716 | 24.2799 | 25.1782 | 25.644 | 26.0531 | 25.2955 | 26.1812 | 27.5743 | 26.5154 | 26.5154 | 26.5154 | 26.5154 | 26.5154 | 26.5154 | 26.5154 | 26.5154 | 26.5154 | 26.5154 | 26.5154 | 26.5154 | 26.5154 | 26.5154 | 26.5154 | 26.5154 | 45% | 3775.313 | 21.689 | 29.4231 | 31.5374 | 23.1638 | 23.3701 | 23.8251 | 24.9012 | 25.4877 | 26.6069 | 30.0109 | 27.2023 | 26.6522 | 27.3924 | 29.0124 | 27.9142 | 27.9142 | 27.9142 | 27.9142 | 27.9142 | 27.9142 | 27.9142 | 27.9142 | 27.9142 | 27.9142 | 27.9142 | 27.9142 | 27.9142 | 27.9142 | 27.9142 | 27.9142
40% | 4072.8088 | 18.0124 | 24.975 | 26.7837 | 19.3581 | 19.5974 | 20.0108 | 20.9525 | 21.5822 | 22.3806 | 22.7946 | 23.1583 | 22.4849 | 23.2722 | 24.5105 | 23.5692 | 23.5692 | 23.5692 | 23.5692 | 23.5692 | 23.5692 | 23.5692 | 23.5692 | 23.5692 | 23.5692 | 23.5692 | 23.5692 | 23.5692 | 23.5692 | 23.5692 | 23.5692 | 40% | 4072.8088 | 19.2791 | 26.1539 | 28.0332 | 20.59 | 20.7735 | 21.1779 | 22.1344 | 22.6557 | 23.6506 | 26.6764 | 24.1798 | 23.6909 | 24.3488 | 25.7888 | 24.8126 | 24.8126 | 24.8126 | 24.8126 | 24.8126 | 24.8126 | 24.8126 | 24.8126 | 24.8126 | 24.8126 | 24.8126 | 24.8126 | 24.8126 | 24.8126 | 24.8126 | 24.8126
35% | 4198.821 | 15.7609 | 21.8532 | 23.4358 | 16.9383 | 17.1477 | 17.5094 | 18.3335 | 18.8844 | 19.583 | 19.9453 | 20.2635 | 19.6743 | 20.3632 | 21.4467 | 20.6231 | 20.6231 | 20.6231 | 20.6231 | 20.6231 | 20.6231 | 20.6231 | 20.6231 | 20.6231 | 20.6231 | 20.6231 | 20.6231 | 20.6231 | 20.6231 | 20.6231 | 20.6231 | 35% | 4198.821 | 16.8692 | 22.8847 | 24.5291 | 18.0163 | 18.1768 | 18.5307 | 19.3676 | 19.8238 | 20.6942 | 23.3418 | 21.1574 | 20.7295 | 21.3052 | 22.5652 | 21.711 | 21.711 | 21.711 | 21.711 | 21.711 | 21.711 | 21.711 | 21.711 | 21.711 | 21.711 | 21.711 | 21.711 | 21.711 | 21.711 | 21.711 | 21.711
30% | 4271.3374 | 13.5093 | 18.7313 | 20.0878 | 14.5185 | 14.698 | 15.0081 | 15.7144 | 16.1866 | 16.7855 | 17.096 | 17.3687 | 16.8637 | 17.4542 | 18.3829 | 17.6769 | 17.6769 | 17.6769 | 17.6769 | 17.6769 | 17.6769 | 17.6769 | 17.6769 | 17.6769 | 17.6769 | 17.6769 | 17.6769 | 17.6769 | 17.6769 | 17.6769 | 17.6769 | 30% | 4271.3374 | 14.4593 | 19.6154 | 21.0249 | 15.4425 | 15.5801 | 15.8834 | 16.6008 | 16.9918 | 17.7379 | 20.0073 | 18.1349 | 17.7682 | 18.2616 | 19.3416 | 18.6094 | 18.6094 | 18.6094 | 18.6094 | 18.6094 | 18.6094 | 18.6094 | 18.6094 | 18.6094 | 18.6094 | 18.6094 | 18.6094 | 18.6094 | 18.6094 | 18.6094 | 18.6094
25% | 4321.8611 | 11.2578 | 15.6094 | 16.7398 | 12.0988 | 12.2483 | 12.5067 | 13.0953 | 13.4889 | 13.9879 | 14.2467 | 14.474 | 14.0531 | 14.5451 | 15.319 | 14.7308 | 14.7308 | 14.7308 | 14.7308 | 14.7308 | 14.7308 | 14.7308 | 14.7308 | 14.7308 | 14.7308 | 14.7308 | 14.7308 | 14.7308 | 14.7308 | 14.7308 | 14.7308 | 25% | 4321.8611 | 12.0494 | 16.3462 | 17.5208 | 12.8688 | 12.9834 | 13.2362 | 13.834 | 14.1598 | 14.7816 | 16.6727 | 15.1124 | 14.8068 | 15.218 | 16.118 | 15.5079 | 15.5079 | 15.5079 | 15.5079 | 15.5079 | 15.5079 | 15.5079 | 15.5079 | 15.5079 | 15.5079 | 15.5079 | 15.5079 | 15.5079 | 15.5079 | 15.5079 | 15.5079
20% | 4353.067 | 9.0062 | 12.4875 | 13.3919 | 9.679 | 9.7987 | 10.0054 | 10.4763 | 10.7911 | 11.1903 | 11.3973 | 11.5792 | 11.2424 | 11.6361 | 12.2552 | 11.7846 | 11.7846 | 11.7846 | 11.7846 | 11.7846 | 11.7846 | 11.7846 | 11.7846 | 11.7846 | 11.7846 | 11.7846 | 11.7846 | 11.7846 | 11.7846 | 11.7846 | 11.7846 | 20% | 4353.067 | 9.6396 | 13.0769 | 14.0166 | 10.295 | 10.3867 | 10.589 | 11.0672 | 11.3279 | 11.8253 | 13.3382 | 12.0899 | 11.8454 | 12.1744 | 12.8944 | 12.4063 | 12.4063 | 12.4063 | 12.4063 | 12.4063 | 12.4063 | 12.4063 | 12.4063 | 12.4063 | 12.4063 | 12.4063 | 12.4063 | 12.4063 | 12.4063 | 12.4063 | 12.4063
15% | 4369.4129 | 6.7547 | 9.3656 | 10.0439 | 7.2593 | 7.349 | 7.504 | 7.8572 | 8.0933 | 8.3927 | 8.548 | 8.6844 | 8.4318 | 8.7271 | 9.1914 | 8.8385 | 8.8385 | 8.8385 | 8.8385 | 8.8385 | 8.8385 | 8.8385 | 8.8385 | 8.8385 | 8.8385 | 8.8385 | 8.8385 | 8.8385 | 8.8385 | 8.8385 | 8.8385 | 15% | 4369.4129 | 7.2297 | 9.8077 | 10.5125 | 7.7213 | 7.79 | 7.9417 | 8.3004 | 8.4959 | 8.869 | 10.0036 | 9.0674 | 8.8841 | 9.1308 | 9.6708 | 9.3047 | 9.3047 | 9.3047 | 9.3047 | 9.3047 | 9.3047 | 9.3047 | 9.3047 | 9.3047 | 9.3047 | 9.3047 | 9.3047 | 9.3047 | 9.3047 | 9.3047 | 9.3047
10% | 4378.6261 | 4.5031 | 6.2438 | 6.6959 | 4.8395 | 4.8993 | 5.0027 | 5.2381 | 5.3955 | 5.5952 | 5.6987 | 5.7896 | 5.6212 | 5.8181 | 6.1276 | 5.8923 | 5.8923 | 5.8923 | 5.8923 | 5.8923 | 5.8923 | 5.8923 | 5.8923 | 5.8923 | 5.8923 | 5.8923 | 5.8923 | 5.8923 | 5.8923 | 5.8923 | 5.8923 | 10% | 4378.6261 | 4.8198 | 6.5385 | 7.0083 | 5.1475 | 5.1934 | 5.2945 | 5.5336 | 5.6639 | 5.9126 | 6.6691 | 6.045 | 5.9227 | 6.0872 | 6.4472 | 6.2031 | 6.2031 | 6.2031 | 6.2031 | 6.2031 | 6.2031 | 6.2031 | 6.2031 | 6.2031 | 6.2031 | 6.2031 | 6.2031 | 6.2031 | 6.2031 | 6.2031 | 6.2031
5% | 4391.7028 | 2.2516 | 3.1219 | 3.348 | 2.4198 | 2.4497 | 2.5013 | 2.6191 | 2.6978 | 2.7976 | 2.8493 | 2.8948 | 2.8106 | 2.909 | 3.0638 | 2.9462 | 2.9462 | 2.9462 | 2.9462 | 2.9462 | 2.9462 | 2.9462 | 2.9462 | 2.9462 | 2.9462 | 2.9462 | 2.9462 | 2.9462 | 2.9462 | 2.9462 | 2.9462 | 5% | 4391.7028 | 2.4099 | 3.2692 | 3.5042 | 2.5738 | 2.5967 | 2.6472 | 2.7668 | 2.832 | 2.9563 | 3.3345 | 3.0225 | 2.9614 | 3.0436 | 3.2236 | 3.1016 | 3.1016 | 3.1016 | 3.1016 | 3.1016 | 3.1016 | 3.1016 | 3.1016 | 3.1016 | 3.1016 | 3.1016 | 3.1016 | 3.1016 | 3.1016 | 3.1016 | 3.1016
9.992e-14% | 4391.7028 | 4.4995e-14 | 6.2388e-14 | 6.6906e-14 | 4.8356e-14 | 4.8954e-14 | 4.9987e-14 | 5.2339e-14 | 5.3912e-14 | 5.5907e-14 | 5.6941e-14 | 5.785e-14 | 5.6167e-14 | 5.8134e-14 | 6.1227e-14 | 5.8876e-14 | 5.8876e-14 | 5.8876e-14 | 5.8876e-14 | 5.8876e-14 | 5.8876e-14 | 5.8876e-14 | 5.8876e-14 | 5.8876e-14 | 5.8876e-14 | 5.8876e-14 | 5.8876e-14 | 5.8876e-14 | 5.8876e-14 | 5.8876e-14 | 5.8876e-14 | 9.992e-14% | 4391.7028 | 4.8159e-14 | 6.5332e-14 | 7.0027e-14 | 5.1434e-14 | 5.1892e-14 | 5.2902e-14 | 5.5292e-14 | 5.6594e-14 | 5.9079e-14 | 6.6638e-14 | 6.0401e-14 | 5.918e-14 | 6.0823e-14 | 6.442e-14 | 6.1982e-14 | 6.1982e-14 | 6.1982e-14 | 6.1982e-14 | 6.1982e-14 | 6.1982e-14 | 6.1982e-14 | 6.1982e-14 | 6.1982e-14 | 6.1982e-14 | 6.1982e-14 | 6.1982e-14 | 6.1982e-14 | 6.1982e-14 | 6.1982e-14 | 6.1982e-14
Summer Season | [31 empty] | Summer Season
P50 | [31 empty] | P10
% of MD | Summer - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Summer - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 51.1621 | 67.921 | 72.4827 | 53.0165 | 53.0116 | 53.5315 | 54.102 | 55.2733 | 56.1149 | 56.5715 | 57.0707 | 57.5278 | 58.3537 | 59.3787 | 59.3071 | 59.3071 | 59.3071 | 59.3071 | 59.3071 | 59.3071 | 59.3071 | 59.3071 | 59.3071 | 59.3071 | 59.3071 | 59.3071 | 59.3071 | 59.3071 | 59.3071 | 59.3071 | 100% | 0 | 57.0282 | 73.8207 | 78.2145 | 58.6175 | 58.6361 | 59.0866 | 60.2762 | 61.0719 | 61.8513 | 62.7629 | 63.6072 | 64.4273 | 64.5203 | 65.4775 | 64.7507 | 64.7507 | 64.7507 | 64.7507 | 64.7507 | 64.7507 | 64.7507 | 64.7507 | 64.7507 | 64.7507 | 64.7507 | 64.7507 | 64.7507 | 64.7507 | 64.7507 | 64.7507
99% | 0 | 50.6505 | 67.2418 | 71.7579 | 52.4863 | 52.4815 | 52.9962 | 53.561 | 54.7205 | 55.5538 | 56.0058 | 56.5 | 56.9525 | 57.7701 | 58.7849 | 58.714 | 58.714 | 58.714 | 58.714 | 58.714 | 58.714 | 58.714 | 58.714 | 58.714 | 58.714 | 58.714 | 58.714 | 58.714 | 58.714 | 58.714 | 58.714 | 99% | 1.5127 | 56.4579 | 73.0825 | 77.4324 | 58.0313 | 58.0497 | 58.4957 | 59.6734 | 60.4612 | 61.2328 | 62.1353 | 62.9712 | 63.783 | 63.8751 | 64.8228 | 64.1032 | 64.1032 | 64.1032 | 64.1032 | 64.1032 | 64.1032 | 64.1032 | 64.1032 | 64.1032 | 64.1032 | 64.1032 | 64.1032 | 64.1032 | 64.1032 | 64.1032 | 64.1032
98% | 0 | 50.1389 | 66.5626 | 71.033 | 51.9562 | 51.9514 | 52.4609 | 53.02 | 54.1678 | 54.9926 | 55.4401 | 55.9293 | 56.3772 | 57.1866 | 58.1912 | 58.1209 | 58.1209 | 58.1209 | 58.1209 | 58.1209 | 58.1209 | 58.1209 | 58.1209 | 58.1209 | 58.1209 | 58.1209 | 58.1209 | 58.1209 | 58.1209 | 58.1209 | 58.1209 | 98% | 2.269 | 55.8876 | 72.3443 | 76.6503 | 57.4451 | 57.4634 | 57.9048 | 59.0706 | 59.8505 | 60.6143 | 61.5077 | 62.3351 | 63.1387 | 63.2299 | 64.168 | 63.4557 | 63.4557 | 63.4557 | 63.4557 | 63.4557 | 63.4557 | 63.4557 | 63.4557 | 63.4557 | 63.4557 | 63.4557 | 63.4557 | 63.4557 | 63.4557 | 63.4557 | 63.4557
97% | 0.37816 | 49.6272 | 65.8834 | 70.3082 | 51.426 | 51.4213 | 51.9256 | 52.479 | 53.6151 | 54.4315 | 54.8743 | 55.3586 | 55.802 | 56.6031 | 57.5974 | 57.5279 | 57.5279 | 57.5279 | 57.5279 | 57.5279 | 57.5279 | 57.5279 | 57.5279 | 57.5279 | 57.5279 | 57.5279 | 57.5279 | 57.5279 | 57.5279 | 57.5279 | 57.5279 | 97% | 3.7816 | 55.3173 | 71.6061 | 75.8681 | 56.859 | 56.877 | 57.314 | 58.4679 | 59.2397 | 59.9957 | 60.88 | 61.699 | 62.4945 | 62.5847 | 63.5132 | 62.8082 | 62.8082 | 62.8082 | 62.8082 | 62.8082 | 62.8082 | 62.8082 | 62.8082 | 62.8082 | 62.8082 | 62.8082 | 62.8082 | 62.8082 | 62.8082 | 62.8082 | 62.8082
95% | 2.269 | 48.604 | 64.5249 | 68.8586 | 50.3657 | 50.361 | 50.8549 | 51.3969 | 52.5096 | 53.3092 | 53.7429 | 54.2172 | 54.6514 | 55.436 | 56.4098 | 56.3417 | 56.3417 | 56.3417 | 56.3417 | 56.3417 | 56.3417 | 56.3417 | 56.3417 | 56.3417 | 56.3417 | 56.3417 | 56.3417 | 56.3417 | 56.3417 | 56.3417 | 56.3417 | 95% | 6.0506 | 54.1768 | 70.1297 | 74.3038 | 55.6866 | 55.7043 | 56.1322 | 57.2623 | 58.0183 | 58.7587 | 59.6248 | 60.4269 | 61.2059 | 61.2943 | 62.2037 | 61.5132 | 61.5132 | 61.5132 | 61.5132 | 61.5132 | 61.5132 | 61.5132 | 61.5132 | 61.5132 | 61.5132 | 61.5132 | 61.5132 | 61.5132 | 61.5132 | 61.5132 | 61.5132
90% | 5.6725 | 46.0459 | 61.1289 | 65.2344 | 47.7149 | 47.7105 | 48.1784 | 48.6918 | 49.7459 | 50.5034 | 50.9143 | 51.3637 | 51.775 | 52.5183 | 53.4409 | 53.3764 | 53.3764 | 53.3764 | 53.3764 | 53.3764 | 53.3764 | 53.3764 | 53.3764 | 53.3764 | 53.3764 | 53.3764 | 53.3764 | 53.3764 | 53.3764 | 53.3764 | 53.3764 | 90% | 16.2611 | 51.3254 | 66.4386 | 70.3931 | 52.7557 | 52.7725 | 53.1779 | 54.2485 | 54.9647 | 55.6662 | 56.4866 | 57.2465 | 57.9846 | 58.0683 | 58.9298 | 58.2757 | 58.2757 | 58.2757 | 58.2757 | 58.2757 | 58.2757 | 58.2757 | 58.2757 | 58.2757 | 58.2757 | 58.2757 | 58.2757 | 58.2757 | 58.2757 | 58.2757 | 58.2757
85% | 15.8829 | 43.4878 | 57.7328 | 61.6103 | 45.064 | 45.0599 | 45.5018 | 45.9867 | 46.9823 | 47.6977 | 48.0858 | 48.5101 | 48.8986 | 49.6006 | 50.4719 | 50.411 | 50.411 | 50.411 | 50.411 | 50.411 | 50.411 | 50.411 | 50.411 | 50.411 | 50.411 | 50.411 | 50.411 | 50.411 | 50.411 | 50.411 | 50.411 | 85% | 26.4715 | 48.4739 | 62.7476 | 66.4824 | 49.8249 | 49.8407 | 50.2236 | 51.2347 | 51.9111 | 52.5736 | 53.3485 | 54.0661 | 54.7632 | 54.8423 | 55.6559 | 55.0381 | 55.0381 | 55.0381 | 55.0381 | 55.0381 | 55.0381 | 55.0381 | 55.0381 | 55.0381 | 55.0381 | 55.0381 | 55.0381 | 55.0381 | 55.0381 | 55.0381 | 55.0381
80% | 31.0095 | 40.9297 | 54.3368 | 57.9862 | 42.4132 | 42.4093 | 42.8252 | 43.2816 | 44.2186 | 44.8919 | 45.2572 | 45.6566 | 46.0222 | 46.6829 | 47.503 | 47.4457 | 47.4457 | 47.4457 | 47.4457 | 47.4457 | 47.4457 | 47.4457 | 47.4457 | 47.4457 | 47.4457 | 47.4457 | 47.4457 | 47.4457 | 47.4457 | 47.4457 | 47.4457 | 80% | 34.0348 | 45.6225 | 59.0566 | 62.5716 | 46.894 | 46.9089 | 47.2693 | 48.2209 | 48.8575 | 49.481 | 50.2103 | 50.8858 | 51.5418 | 51.6163 | 52.382 | 51.8006 | 51.8006 | 51.8006 | 51.8006 | 51.8006 | 51.8006 | 51.8006 | 51.8006 | 51.8006 | 51.8006 | 51.8006 | 51.8006 | 51.8006 | 51.8006 | 51.8006 | 51.8006
75% | 72.9857 | 38.3716 | 50.9407 | 54.362 | 39.7624 | 39.7587 | 40.1486 | 40.5765 | 41.455 | 42.0862 | 42.4286 | 42.8031 | 43.1458 | 43.7653 | 44.5341 | 44.4803 | 44.4803 | 44.4803 | 44.4803 | 44.4803 | 44.4803 | 44.4803 | 44.4803 | 44.4803 | 44.4803 | 44.4803 | 44.4803 | 44.4803 | 44.4803 | 44.4803 | 44.4803 | 75% | 48.405 | 42.7711 | 55.3655 | 58.6609 | 43.9631 | 43.9771 | 44.3149 | 45.2071 | 45.8039 | 46.3885 | 47.0722 | 47.7054 | 48.3205 | 48.3902 | 49.1082 | 48.563 | 48.563 | 48.563 | 48.563 | 48.563 | 48.563 | 48.563 | 48.563 | 48.563 | 48.563 | 48.563 | 48.563 | 48.563 | 48.563 | 48.563 | 48.563
70% | 150.5094 | 35.8135 | 47.5447 | 50.7379 | 37.1116 | 37.1081 | 37.4721 | 37.8714 | 38.6913 | 39.2804 | 39.6 | 39.9495 | 40.2695 | 40.8476 | 41.5651 | 41.515 | 41.515 | 41.515 | 41.515 | 41.515 | 41.515 | 41.515 | 41.515 | 41.515 | 41.515 | 41.515 | 41.515 | 41.515 | 41.515 | 41.515 | 41.515 | 70% | 76.3892 | 39.9197 | 51.6745 | 54.7502 | 41.0322 | 41.0453 | 41.3606 | 42.1933 | 42.7503 | 43.2959 | 43.934 | 44.5251 | 45.0991 | 45.1642 | 45.8343 | 45.3255 | 45.3255 | 45.3255 | 45.3255 | 45.3255 | 45.3255 | 45.3255 | 45.3255 | 45.3255 | 45.3255 | 45.3255 | 45.3255 | 45.3255 | 45.3255 | 45.3255 | 45.3255
65% | 359.6342 | 33.2554 | 44.1486 | 47.1138 | 34.4607 | 34.4576 | 34.7955 | 35.1663 | 35.9276 | 36.4747 | 36.7715 | 37.096 | 37.3931 | 37.9299 | 38.5962 | 38.5496 | 38.5496 | 38.5496 | 38.5496 | 38.5496 | 38.5496 | 38.5496 | 38.5496 | 38.5496 | 38.5496 | 38.5496 | 38.5496 | 38.5496 | 38.5496 | 38.5496 | 38.5496 | 65% | 114.2056 | 37.0683 | 47.9835 | 50.8395 | 38.1014 | 38.1135 | 38.4063 | 39.1795 | 39.6967 | 40.2033 | 40.7959 | 41.3447 | 41.8777 | 41.9382 | 42.5604 | 42.088 | 42.088 | 42.088 | 42.088 | 42.088 | 42.088 | 42.088 | 42.088 | 42.088 | 42.088 | 42.088 | 42.088 | 42.088 | 42.088 | 42.088 | 42.088
60% | 689.7717 | 30.6973 | 40.7526 | 43.4896 | 31.8099 | 31.807 | 32.1189 | 32.4612 | 33.164 | 33.669 | 33.9429 | 34.2424 | 34.5167 | 35.0122 | 35.6272 | 35.5843 | 35.5843 | 35.5843 | 35.5843 | 35.5843 | 35.5843 | 35.5843 | 35.5843 | 35.5843 | 35.5843 | 35.5843 | 35.5843 | 35.5843 | 35.5843 | 35.5843 | 35.5843 | 60% | 178.1154 | 34.2169 | 44.2924 | 46.9287 | 35.1705 | 35.1817 | 35.4519 | 36.1657 | 36.6431 | 37.1108 | 37.6577 | 38.1643 | 38.6564 | 38.7122 | 39.2865 | 38.8504 | 38.8504 | 38.8504 | 38.8504 | 38.8504 | 38.8504 | 38.8504 | 38.8504 | 38.8504 | 38.8504 | 38.8504 | 38.8504 | 38.8504 | 38.8504 | 38.8504 | 38.8504
55% | 1095.5419 | 28.1392 | 37.3565 | 39.8655 | 29.1591 | 29.1564 | 29.4423 | 29.7561 | 30.4003 | 30.8632 | 31.1143 | 31.3889 | 31.6403 | 32.0945 | 32.6583 | 32.6189 | 32.6189 | 32.6189 | 32.6189 | 32.6189 | 32.6189 | 32.6189 | 32.6189 | 32.6189 | 32.6189 | 32.6189 | 32.6189 | 32.6189 | 32.6189 | 32.6189 | 32.6189 | 55% | 311.6074 | 31.3655 | 40.6014 | 43.018 | 32.2396 | 32.2499 | 32.4976 | 33.1519 | 33.5895 | 34.0182 | 34.5196 | 34.984 | 35.435 | 35.4862 | 36.0127 | 35.6129 | 35.6129 | 35.6129 | 35.6129 | 35.6129 | 35.6129 | 35.6129 | 35.6129 | 35.6129 | 35.6129 | 35.6129 | 35.6129 | 35.6129 | 35.6129 | 35.6129 | 35.6129
50% | 1666.1918 | 25.581 | 33.9605 | 36.2413 | 26.5083 | 26.5058 | 26.7658 | 27.051 | 27.6366 | 28.0575 | 28.2857 | 28.5354 | 28.7639 | 29.1768 | 29.6894 | 29.6535 | 29.6535 | 29.6535 | 29.6535 | 29.6535 | 29.6535 | 29.6535 | 29.6535 | 29.6535 | 29.6535 | 29.6535 | 29.6535 | 29.6535 | 29.6535 | 29.6535 | 29.6535 | 50% | 636.0723 | 28.5141 | 36.9103 | 39.1073 | 29.3087 | 29.318 | 29.5433 | 30.1381 | 30.536 | 30.9256 | 31.3815 | 31.8036 | 32.2136 | 32.2602 | 32.7388 | 32.3754 | 32.3754 | 32.3754 | 32.3754 | 32.3754 | 32.3754 | 32.3754 | 32.3754 | 32.3754 | 32.3754 | 32.3754 | 32.3754 | 32.3754 | 32.3754 | 32.3754 | 32.3754
45% | 2506.0947 | 23.0229 | 30.5644 | 32.6172 | 23.8574 | 23.8552 | 24.0892 | 24.3459 | 24.873 | 25.2517 | 25.4572 | 25.6818 | 25.8875 | 26.2592 | 26.7204 | 26.6882 | 26.6882 | 26.6882 | 26.6882 | 26.6882 | 26.6882 | 26.6882 | 26.6882 | 26.6882 | 26.6882 | 26.6882 | 26.6882 | 26.6882 | 26.6882 | 26.6882 | 26.6882 | 45% | 1179.4944 | 25.6627 | 33.2193 | 35.1965 | 26.3779 | 26.3862 | 26.589 | 27.1243 | 27.4824 | 27.8331 | 28.2433 | 28.6233 | 28.9923 | 29.0341 | 29.4649 | 29.1378 | 29.1378 | 29.1378 | 29.1378 | 29.1378 | 29.1378 | 29.1378 | 29.1378 | 29.1378 | 29.1378 | 29.1378 | 29.1378 | 29.1378 | 29.1378 | 29.1378 | 29.1378
40% | 3164.4787 | 20.4648 | 27.1684 | 28.9931 | 21.2066 | 21.2046 | 21.4126 | 21.6408 | 22.1093 | 22.446 | 22.6286 | 22.8283 | 23.0111 | 23.3415 | 23.7515 | 23.7228 | 23.7228 | 23.7228 | 23.7228 | 23.7228 | 23.7228 | 23.7228 | 23.7228 | 23.7228 | 23.7228 | 23.7228 | 23.7228 | 23.7228 | 23.7228 | 23.7228 | 23.7228 | 40% | 1808.3816 | 22.8113 | 29.5283 | 31.2858 | 23.447 | 23.4544 | 23.6346 | 24.1105 | 24.4288 | 24.7405 | 25.1052 | 25.4429 | 25.7709 | 25.8081 | 26.191 | 25.9003 | 25.9003 | 25.9003 | 25.9003 | 25.9003 | 25.9003 | 25.9003 | 25.9003 | 25.9003 | 25.9003 | 25.9003 | 25.9003 | 25.9003 | 25.9003 | 25.9003 | 25.9003
35% | 3551.3408 | 17.9067 | 23.7723 | 25.3689 | 18.5558 | 18.5541 | 18.736 | 18.9357 | 19.3456 | 19.6402 | 19.8 | 19.9748 | 20.1347 | 20.4238 | 20.7826 | 20.7575 | 20.7575 | 20.7575 | 20.7575 | 20.7575 | 20.7575 | 20.7575 | 20.7575 | 20.7575 | 20.7575 | 20.7575 | 20.7575 | 20.7575 | 20.7575 | 20.7575 | 20.7575 | 35% | 2779.1293 | 19.9599 | 25.8372 | 27.3751 | 20.5161 | 20.5226 | 20.6803 | 21.0967 | 21.3752 | 21.648 | 21.967 | 22.2625 | 22.5495 | 22.5821 | 22.9171 | 22.6628 | 22.6628 | 22.6628 | 22.6628 | 22.6628 | 22.6628 | 22.6628 | 22.6628 | 22.6628 | 22.6628 | 22.6628 | 22.6628 | 22.6628 | 22.6628 | 22.6628 | 22.6628
30% | 3758.953 | 15.3486 | 20.3763 | 21.7448 | 15.905 | 15.9035 | 16.0595 | 16.2306 | 16.582 | 16.8345 | 16.9714 | 17.1212 | 17.2583 | 17.5061 | 17.8136 | 17.7921 | 17.7921 | 17.7921 | 17.7921 | 17.7921 | 17.7921 | 17.7921 | 17.7921 | 17.7921 | 17.7921 | 17.7921 | 17.7921 | 17.7921 | 17.7921 | 17.7921 | 17.7921 | 30% | 3814.165 | 17.1085 | 22.1462 | 23.4644 | 17.5852 | 17.5908 | 17.726 | 18.0828 | 18.3216 | 18.5554 | 18.8289 | 19.0822 | 19.3282 | 19.3561 | 19.6433 | 19.4252 | 19.4252 | 19.4252 | 19.4252 | 19.4252 | 19.4252 | 19.4252 | 19.4252 | 19.4252 | 19.4252 | 19.4252 | 19.4252 | 19.4252 | 19.4252 | 19.4252 | 19.4252
25% | 3926.4798 | 12.7905 | 16.9802 | 18.1207 | 13.2541 | 13.2529 | 13.3829 | 13.5255 | 13.8183 | 14.0287 | 14.1429 | 14.2677 | 14.3819 | 14.5884 | 14.8447 | 14.8268 | 14.8268 | 14.8268 | 14.8268 | 14.8268 | 14.8268 | 14.8268 | 14.8268 | 14.8268 | 14.8268 | 14.8268 | 14.8268 | 14.8268 | 14.8268 | 14.8268 | 14.8268 | 25% | 4166.9923 | 14.257 | 18.4552 | 19.5536 | 14.6544 | 14.659 | 14.7716 | 15.069 | 15.268 | 15.4628 | 15.6907 | 15.9018 | 16.1068 | 16.1301 | 16.3694 | 16.1877 | 16.1877 | 16.1877 | 16.1877 | 16.1877 | 16.1877 | 16.1877 | 16.1877 | 16.1877 | 16.1877 | 16.1877 | 16.1877 | 16.1877 | 16.1877 | 16.1877 | 16.1877
20% | 4050.5177 | 10.2324 | 13.5842 | 14.4965 | 10.6033 | 10.6023 | 10.7063 | 10.8204 | 11.0547 | 11.223 | 11.3143 | 11.4141 | 11.5056 | 11.6707 | 11.8757 | 11.8614 | 11.8614 | 11.8614 | 11.8614 | 11.8614 | 11.8614 | 11.8614 | 11.8614 | 11.8614 | 11.8614 | 11.8614 | 11.8614 | 11.8614 | 11.8614 | 11.8614 | 11.8614 | 20% | 4282.7105 | 11.4056 | 14.7641 | 15.6429 | 11.7235 | 11.7272 | 11.8173 | 12.0552 | 12.2144 | 12.3703 | 12.5526 | 12.7214 | 12.8855 | 12.9041 | 13.0955 | 12.9501 | 12.9501 | 12.9501 | 12.9501 | 12.9501 | 12.9501 | 12.9501 | 12.9501 | 12.9501 | 12.9501 | 12.9501 | 12.9501 | 12.9501 | 12.9501 | 12.9501 | 12.9501
15% | 4152.622 | 7.6743 | 10.1881 | 10.8724 | 7.9525 | 7.9517 | 8.0297 | 8.1153 | 8.291 | 8.4172 | 8.4857 | 8.5606 | 8.6292 | 8.7531 | 8.9068 | 8.8961 | 8.8961 | 8.8961 | 8.8961 | 8.8961 | 8.8961 | 8.8961 | 8.8961 | 8.8961 | 8.8961 | 8.8961 | 8.8961 | 8.8961 | 8.8961 | 8.8961 | 8.8961 | 15% | 4364.7722 | 8.5542 | 11.0731 | 11.7322 | 8.7926 | 8.7954 | 8.863 | 9.0414 | 9.1608 | 9.2777 | 9.4144 | 9.5411 | 9.6641 | 9.678 | 9.8216 | 9.7126 | 9.7126 | 9.7126 | 9.7126 | 9.7126 | 9.7126 | 9.7126 | 9.7126 | 9.7126 | 9.7126 | 9.7126 | 9.7126 | 9.7126 | 9.7126 | 9.7126 | 9.7126
10% | 4248.2976 | 5.1162 | 6.7921 | 7.2483 | 5.3017 | 5.3012 | 5.3532 | 5.4102 | 5.5273 | 5.6115 | 5.6571 | 5.7071 | 5.7528 | 5.8354 | 5.9379 | 5.9307 | 5.9307 | 5.9307 | 5.9307 | 5.9307 | 5.9307 | 5.9307 | 5.9307 | 5.9307 | 5.9307 | 5.9307 | 5.9307 | 5.9307 | 5.9307 | 5.9307 | 5.9307 | 10% | 4391.6218 | 5.7028 | 7.3821 | 7.8215 | 5.8617 | 5.8636 | 5.9087 | 6.0276 | 6.1072 | 6.1851 | 6.2763 | 6.3607 | 6.4427 | 6.452 | 6.5478 | 6.4751 | 6.4751 | 6.4751 | 6.4751 | 6.4751 | 6.4751 | 6.4751 | 6.4751 | 6.4751 | 6.4751 | 6.4751 | 6.4751 | 6.4751 | 6.4751 | 6.4751 | 6.4751
5% | 4361.7469 | 2.5581 | 3.396 | 3.6241 | 2.6508 | 2.6506 | 2.6766 | 2.7051 | 2.7637 | 2.8057 | 2.8286 | 2.8535 | 2.8764 | 2.9177 | 2.9689 | 2.9654 | 2.9654 | 2.9654 | 2.9654 | 2.9654 | 2.9654 | 2.9654 | 2.9654 | 2.9654 | 2.9654 | 2.9654 | 2.9654 | 2.9654 | 2.9654 | 2.9654 | 2.9654 | 5% | 4391.6218 | 2.8514 | 3.691 | 3.9107 | 2.9309 | 2.9318 | 2.9543 | 3.0138 | 3.0536 | 3.0926 | 3.1381 | 3.1804 | 3.2214 | 3.226 | 3.2739 | 3.2375 | 3.2375 | 3.2375 | 3.2375 | 3.2375 | 3.2375 | 3.2375 | 3.2375 | 3.2375 | 3.2375 | 3.2375 | 3.2375 | 3.2375 | 3.2375 | 3.2375 | 3.2375
9.992e-14% | 4391.6218 | 5.1121e-14 | 6.7867e-14 | 7.2425e-14 | 5.2974e-14 | 5.2969e-14 | 5.3489e-14 | 5.4059e-14 | 5.5229e-14 | 5.607e-14 | 5.6526e-14 | 5.7025e-14 | 5.7482e-14 | 5.8307e-14 | 5.9331e-14 | 5.926e-14 | 5.926e-14 | 5.926e-14 | 5.926e-14 | 5.926e-14 | 5.926e-14 | 5.926e-14 | 5.926e-14 | 5.926e-14 | 5.926e-14 | 5.926e-14 | 5.926e-14 | 5.926e-14 | 5.926e-14 | 5.926e-14 | 5.926e-14 | 9.992e-14% | 4391.6218 | 5.6983e-14 | 7.3762e-14 | 7.8152e-14 | 5.8571e-14 | 5.8589e-14 | 5.9039e-14 | 6.0228e-14 | 6.1023e-14 | 6.1802e-14 | 6.2713e-14 | 6.3556e-14 | 6.4376e-14 | 6.4469e-14 | 6.5425e-14 | 6.4699e-14 | 6.4699e-14 | 6.4699e-14 | 6.4699e-14 | 6.4699e-14 | 6.4699e-14 | 6.4699e-14 | 6.4699e-14 | 6.4699e-14 | 6.4699e-14 | 6.4699e-14 | 6.4699e-14 | 6.4699e-14 | 6.4699e-14 | 6.4699e-14 | 6.4699e-14
Option 3
Winter Season | [31 empty] | Winter Season
P50 | [31 empty] | P10
% of MD | Winter - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Winter - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 45.0311 | 62.4376 | 66.9594 | 67.7285 | 68.3267 | 69.3603 | 71.7146 | 73.2888 | 75.2849 | 76.3199 | 77.2291 | 75.5455 | 77.5138 | 80.6095 | 78.2564 | 78.2564 | 78.2564 | 78.2564 | 78.2564 | 78.2564 | 78.2564 | 78.2564 | 78.2564 | 78.2564 | 78.2564 | 78.2564 | 78.2564 | 78.2564 | 78.2564 | 78.2564 | 100% | 0 | 48.1978 | 65.3847 | 70.0831 | 70.8084 | 71.267 | 72.2781 | 74.6693 | 75.9727 | 78.4597 | 86.0243 | 79.7829 | 78.5605 | 80.2054 | 83.8053 | 81.3648 | 81.3648 | 81.3648 | 81.3648 | 81.3648 | 81.3648 | 81.3648 | 81.3648 | 81.3648 | 81.3648 | 81.3648 | 81.3648 | 81.3648 | 81.3648 | 81.3648 | 81.3648
99% | 1.486 | 44.5808 | 61.8132 | 66.2898 | 67.0512 | 67.6435 | 68.6667 | 70.9975 | 72.5559 | 74.532 | 75.5567 | 76.4569 | 74.7901 | 76.7387 | 79.8034 | 77.4739 | 77.4739 | 77.4739 | 77.4739 | 77.4739 | 77.4739 | 77.4739 | 77.4739 | 77.4739 | 77.4739 | 77.4739 | 77.4739 | 77.4739 | 77.4739 | 77.4739 | 77.4739 | 99% | 1.486 | 47.7158 | 64.7309 | 69.3823 | 70.1003 | 70.5543 | 71.5553 | 73.9226 | 75.2129 | 77.6751 | 85.1641 | 78.9851 | 77.7749 | 79.4033 | 82.9672 | 80.5512 | 80.5512 | 80.5512 | 80.5512 | 80.5512 | 80.5512 | 80.5512 | 80.5512 | 80.5512 | 80.5512 | 80.5512 | 80.5512 | 80.5512 | 80.5512 | 80.5512 | 80.5512
98% | 3.2692 | 44.1305 | 61.1889 | 65.6202 | 66.3739 | 66.9602 | 67.9731 | 70.2804 | 71.823 | 73.7792 | 74.7935 | 75.6846 | 74.0346 | 75.9636 | 78.9973 | 76.6913 | 76.6913 | 76.6913 | 76.6913 | 76.6913 | 76.6913 | 76.6913 | 76.6913 | 76.6913 | 76.6913 | 76.6913 | 76.6913 | 76.6913 | 76.6913 | 76.6913 | 76.6913 | 98% | 3.2692 | 47.2338 | 64.0771 | 68.6815 | 69.3922 | 69.8416 | 70.8325 | 73.1759 | 74.4532 | 76.8905 | 84.3038 | 78.1873 | 76.9893 | 78.6013 | 82.1292 | 79.7375 | 79.7375 | 79.7375 | 79.7375 | 79.7375 | 79.7375 | 79.7375 | 79.7375 | 79.7375 | 79.7375 | 79.7375 | 79.7375 | 79.7375 | 79.7375 | 79.7375 | 79.7375
97% | 6.8356 | 43.6802 | 60.5645 | 64.9506 | 65.6966 | 66.2769 | 67.2795 | 69.5632 | 71.0901 | 73.0263 | 74.0303 | 74.9123 | 73.2792 | 75.1884 | 78.1912 | 75.9087 | 75.9087 | 75.9087 | 75.9087 | 75.9087 | 75.9087 | 75.9087 | 75.9087 | 75.9087 | 75.9087 | 75.9087 | 75.9087 | 75.9087 | 75.9087 | 75.9087 | 75.9087 | 97% | 6.8356 | 46.7518 | 63.4232 | 67.9806 | 68.6841 | 69.129 | 70.1097 | 72.4292 | 73.6935 | 76.1059 | 83.4436 | 77.3894 | 76.2037 | 77.7992 | 81.2911 | 78.9239 | 78.9239 | 78.9239 | 78.9239 | 78.9239 | 78.9239 | 78.9239 | 78.9239 | 78.9239 | 78.9239 | 78.9239 | 78.9239 | 78.9239 | 78.9239 | 78.9239 | 78.9239
95% | 17.5347 | 42.7796 | 59.3157 | 63.6114 | 64.342 | 64.9104 | 65.8923 | 68.1289 | 69.6243 | 71.5207 | 72.5039 | 73.3677 | 71.7683 | 73.6382 | 76.579 | 74.3436 | 74.3436 | 74.3436 | 74.3436 | 74.3436 | 74.3436 | 74.3436 | 74.3436 | 74.3436 | 74.3436 | 74.3436 | 74.3436 | 74.3436 | 74.3436 | 74.3436 | 74.3436 | 95% | 17.5347 | 45.7879 | 62.1155 | 66.579 | 67.268 | 67.7036 | 68.6642 | 70.9358 | 72.174 | 74.5368 | 81.7231 | 75.7938 | 74.6325 | 76.1951 | 79.615 | 77.2966 | 77.2966 | 77.2966 | 77.2966 | 77.2966 | 77.2966 | 77.2966 | 77.2966 | 77.2966 | 77.2966 | 77.2966 | 77.2966 | 77.2966 | 77.2966 | 77.2966 | 77.2966
90% | 78.7576 | 40.528 | 56.1939 | 60.2634 | 60.9556 | 61.4941 | 62.4243 | 64.5432 | 65.9599 | 67.7564 | 68.6879 | 69.5062 | 67.991 | 69.7625 | 72.5486 | 70.4308 | 70.4308 | 70.4308 | 70.4308 | 70.4308 | 70.4308 | 70.4308 | 70.4308 | 70.4308 | 70.4308 | 70.4308 | 70.4308 | 70.4308 | 70.4308 | 70.4308 | 70.4308 | 90% | 78.7576 | 43.378 | 58.8463 | 63.0748 | 63.7275 | 64.1403 | 65.0503 | 67.2023 | 68.3754 | 70.6138 | 77.4219 | 71.8046 | 70.7045 | 72.1848 | 75.4247 | 73.2283 | 73.2283 | 73.2283 | 73.2283 | 73.2283 | 73.2283 | 73.2283 | 73.2283 | 73.2283 | 73.2283 | 73.2283 | 73.2283 | 73.2283 | 73.2283 | 73.2283 | 73.2283
85% | 236.8672 | 38.2764 | 53.072 | 56.9155 | 57.5692 | 58.0777 | 58.9563 | 60.9575 | 62.2954 | 63.9922 | 64.8719 | 65.6448 | 64.2137 | 65.8868 | 68.5181 | 66.518 | 66.518 | 66.518 | 66.518 | 66.518 | 66.518 | 66.518 | 66.518 | 66.518 | 66.518 | 66.518 | 66.518 | 66.518 | 66.518 | 66.518 | 66.518 | 85% | 236.8672 | 40.9681 | 55.577 | 59.5707 | 60.1871 | 60.5769 | 61.4364 | 63.4689 | 64.5768 | 66.6908 | 73.1207 | 67.8155 | 66.7765 | 68.1746 | 71.2345 | 69.1601 | 69.1601 | 69.1601 | 69.1601 | 69.1601 | 69.1601 | 69.1601 | 69.1601 | 69.1601 | 69.1601 | 69.1601 | 69.1601 | 69.1601 | 69.1601 | 69.1601 | 69.1601
80% | 497.5104 | 36.0249 | 49.9501 | 53.5675 | 54.1828 | 54.6614 | 55.4882 | 57.3717 | 58.631 | 60.2279 | 61.056 | 61.7833 | 60.4364 | 62.0111 | 64.4876 | 62.6051 | 62.6051 | 62.6051 | 62.6051 | 62.6051 | 62.6051 | 62.6051 | 62.6051 | 62.6051 | 62.6051 | 62.6051 | 62.6051 | 62.6051 | 62.6051 | 62.6051 | 62.6051 | 80% | 497.5104 | 38.5582 | 52.3078 | 56.0665 | 56.6467 | 57.0136 | 57.8225 | 59.7354 | 60.7781 | 62.7678 | 68.8195 | 63.8263 | 62.8484 | 64.1643 | 67.0442 | 65.0919 | 65.0919 | 65.0919 | 65.0919 | 65.0919 | 65.0919 | 65.0919 | 65.0919 | 65.0919 | 65.0919 | 65.0919 | 65.0919 | 65.0919 | 65.0919 | 65.0919 | 65.0919
75% | 803.6248 | 33.7733 | 46.8282 | 50.2195 | 50.7964 | 51.245 | 52.0202 | 53.786 | 54.9666 | 56.4637 | 57.24 | 57.9219 | 56.6592 | 58.1354 | 60.4571 | 58.6923 | 58.6923 | 58.6923 | 58.6923 | 58.6923 | 58.6923 | 58.6923 | 58.6923 | 58.6923 | 58.6923 | 58.6923 | 58.6923 | 58.6923 | 58.6923 | 58.6923 | 58.6923 | 75% | 803.6248 | 36.1483 | 49.0386 | 52.5623 | 53.1063 | 53.4502 | 54.2086 | 56.0019 | 56.9795 | 58.8448 | 64.5182 | 59.8372 | 58.9204 | 60.154 | 62.8539 | 61.0236 | 61.0236 | 61.0236 | 61.0236 | 61.0236 | 61.0236 | 61.0236 | 61.0236 | 61.0236 | 61.0236 | 61.0236 | 61.0236 | 61.0236 | 61.0236 | 61.0236 | 61.0236
70% | 1155.2107 | 31.5218 | 43.7063 | 46.8715 | 47.4099 | 47.8287 | 48.5522 | 50.2003 | 51.3021 | 52.6994 | 53.424 | 54.0604 | 52.8819 | 54.2597 | 56.4267 | 54.7795 | 54.7795 | 54.7795 | 54.7795 | 54.7795 | 54.7795 | 54.7795 | 54.7795 | 54.7795 | 54.7795 | 54.7795 | 54.7795 | 54.7795 | 54.7795 | 54.7795 | 54.7795 | 70% | 1155.2107 | 33.7384 | 45.7693 | 49.0582 | 49.5659 | 49.8869 | 50.5947 | 52.2685 | 53.1809 | 54.9218 | 60.217 | 55.8481 | 54.9924 | 56.1438 | 58.6637 | 56.9554 | 56.9554 | 56.9554 | 56.9554 | 56.9554 | 56.9554 | 56.9554 | 56.9554 | 56.9554 | 56.9554 | 56.9554 | 56.9554 | 56.9554 | 56.9554 | 56.9554 | 56.9554
65% | 1553.1596 | 29.2702 | 40.5844 | 43.5236 | 44.0235 | 44.4124 | 45.0842 | 46.6145 | 47.6377 | 48.9352 | 49.608 | 50.1989 | 49.1046 | 50.384 | 52.3962 | 50.8667 | 50.8667 | 50.8667 | 50.8667 | 50.8667 | 50.8667 | 50.8667 | 50.8667 | 50.8667 | 50.8667 | 50.8667 | 50.8667 | 50.8667 | 50.8667 | 50.8667 | 50.8667 | 65% | 1553.1596 | 31.3286 | 42.5001 | 45.554 | 46.0254 | 46.3235 | 46.9808 | 48.535 | 49.3822 | 50.9988 | 55.9158 | 51.8589 | 51.0643 | 52.1335 | 54.4734 | 52.8871 | 52.8871 | 52.8871 | 52.8871 | 52.8871 | 52.8871 | 52.8871 | 52.8871 | 52.8871 | 52.8871 | 52.8871 | 52.8871 | 52.8871 | 52.8871 | 52.8871 | 52.8871
60% | 2026.2996 | 27.0187 | 37.4626 | 40.1756 | 40.6371 | 40.996 | 41.6162 | 43.0288 | 43.9733 | 45.1709 | 45.792 | 46.3375 | 45.3273 | 46.5083 | 48.3657 | 46.9539 | 46.9539 | 46.9539 | 46.9539 | 46.9539 | 46.9539 | 46.9539 | 46.9539 | 46.9539 | 46.9539 | 46.9539 | 46.9539 | 46.9539 | 46.9539 | 46.9539 | 46.9539 | 60% | 2026.2996 | 28.9187 | 39.2308 | 42.0499 | 42.485 | 42.7602 | 43.3669 | 44.8016 | 45.5836 | 47.0758 | 51.6146 | 47.8698 | 47.1363 | 48.1232 | 50.2832 | 48.8189 | 48.8189 | 48.8189 | 48.8189 | 48.8189 | 48.8189 | 48.8189 | 48.8189 | 48.8189 | 48.8189 | 48.8189 | 48.8189 | 48.8189 | 48.8189 | 48.8189 | 48.8189
55% | 2598.4068 | 24.7671 | 34.3407 | 36.8276 | 37.2507 | 37.5797 | 38.1482 | 39.4431 | 40.3088 | 41.4067 | 41.976 | 42.476 | 41.55 | 42.6326 | 44.3352 | 43.041 | 43.041 | 43.041 | 43.041 | 43.041 | 43.041 | 43.041 | 43.041 | 43.041 | 43.041 | 43.041 | 43.041 | 43.041 | 43.041 | 43.041 | 43.041 | 55% | 2598.4068 | 26.5088 | 35.9616 | 38.5457 | 38.9446 | 39.1968 | 39.753 | 41.0681 | 41.785 | 43.1529 | 47.3134 | 43.8806 | 43.2083 | 44.113 | 46.0929 | 44.7507 | 44.7507 | 44.7507 | 44.7507 | 44.7507 | 44.7507 | 44.7507 | 44.7507 | 44.7507 | 44.7507 | 44.7507 | 44.7507 | 44.7507 | 44.7507 | 44.7507 | 44.7507
50% | 3233.5201 | 22.5156 | 31.2188 | 33.4797 | 33.8642 | 34.1634 | 34.6802 | 35.8573 | 36.6444 | 37.6424 | 38.16 | 38.6146 | 37.7728 | 38.7569 | 40.3048 | 39.1282 | 39.1282 | 39.1282 | 39.1282 | 39.1282 | 39.1282 | 39.1282 | 39.1282 | 39.1282 | 39.1282 | 39.1282 | 39.1282 | 39.1282 | 39.1282 | 39.1282 | 39.1282 | 50% | 3233.5201 | 24.0989 | 32.6924 | 35.0416 | 35.4042 | 35.6335 | 36.139 | 37.3346 | 37.9863 | 39.2299 | 43.0122 | 39.8915 | 39.2803 | 40.1027 | 41.9026 | 40.6824 | 40.6824 | 40.6824 | 40.6824 | 40.6824 | 40.6824 | 40.6824 | 40.6824 | 40.6824 | 40.6824 | 40.6824 | 40.6824 | 40.6824 | 40.6824 | 40.6824 | 40.6824
45% | 3775.313 | 20.264 | 28.0969 | 30.1317 | 30.4778 | 30.747 | 31.2121 | 32.2716 | 32.9799 | 33.8782 | 34.344 | 34.7531 | 33.9955 | 34.8812 | 36.2743 | 35.2154 | 35.2154 | 35.2154 | 35.2154 | 35.2154 | 35.2154 | 35.2154 | 35.2154 | 35.2154 | 35.2154 | 35.2154 | 35.2154 | 35.2154 | 35.2154 | 35.2154 | 35.2154 | 45% | 3775.313 | 21.689 | 29.4231 | 31.5374 | 31.8638 | 32.0701 | 32.5251 | 33.6012 | 34.1877 | 35.3069 | 38.7109 | 35.9023 | 35.3522 | 36.0924 | 37.7124 | 36.6142 | 36.6142 | 36.6142 | 36.6142 | 36.6142 | 36.6142 | 36.6142 | 36.6142 | 36.6142 | 36.6142 | 36.6142 | 36.6142 | 36.6142 | 36.6142 | 36.6142 | 36.6142
40% | 4072.8088 | 18.0124 | 24.975 | 26.7837 | 27.0914 | 27.3307 | 27.7441 | 28.6859 | 29.3155 | 30.114 | 30.528 | 30.8917 | 30.2182 | 31.0055 | 32.2438 | 31.3026 | 31.3026 | 31.3026 | 31.3026 | 31.3026 | 31.3026 | 31.3026 | 31.3026 | 31.3026 | 31.3026 | 31.3026 | 31.3026 | 31.3026 | 31.3026 | 31.3026 | 31.3026 | 40% | 4072.8088 | 19.2791 | 26.1539 | 28.0332 | 28.3234 | 28.5068 | 28.9112 | 29.8677 | 30.3891 | 31.3839 | 34.4097 | 31.9132 | 31.4242 | 32.0822 | 33.5221 | 32.5459 | 32.5459 | 32.5459 | 32.5459 | 32.5459 | 32.5459 | 32.5459 | 32.5459 | 32.5459 | 32.5459 | 32.5459 | 32.5459 | 32.5459 | 32.5459 | 32.5459 | 32.5459
35% | 4198.821 | 15.7609 | 21.8532 | 23.4358 | 23.705 | 23.9144 | 24.2761 | 25.1001 | 25.6511 | 26.3497 | 26.712 | 27.0302 | 26.4409 | 27.1298 | 28.2133 | 27.3897 | 27.3897 | 27.3897 | 27.3897 | 27.3897 | 27.3897 | 27.3897 | 27.3897 | 27.3897 | 27.3897 | 27.3897 | 27.3897 | 27.3897 | 27.3897 | 27.3897 | 27.3897 | 35% | 4198.821 | 16.8692 | 22.8847 | 24.5291 | 24.7829 | 24.9434 | 25.2973 | 26.1342 | 26.5904 | 27.4609 | 30.1085 | 27.924 | 27.4962 | 28.0719 | 29.3318 | 28.4777 | 28.4777 | 28.4777 | 28.4777 | 28.4777 | 28.4777 | 28.4777 | 28.4777 | 28.4777 | 28.4777 | 28.4777 | 28.4777 | 28.4777 | 28.4777 | 28.4777 | 28.4777
30% | 4271.3374 | 13.5093 | 18.7313 | 20.0878 | 20.3185 | 20.498 | 20.8081 | 21.5144 | 21.9866 | 22.5855 | 22.896 | 23.1687 | 22.6637 | 23.2542 | 24.1829 | 23.4769 | 23.4769 | 23.4769 | 23.4769 | 23.4769 | 23.4769 | 23.4769 | 23.4769 | 23.4769 | 23.4769 | 23.4769 | 23.4769 | 23.4769 | 23.4769 | 23.4769 | 23.4769 | 30% | 4271.3374 | 14.4593 | 19.6154 | 21.0249 | 21.2425 | 21.3801 | 21.6834 | 22.4008 | 22.7918 | 23.5379 | 25.8073 | 23.9349 | 23.5682 | 24.0616 | 25.1416 | 24.4094 | 24.4094 | 24.4094 | 24.4094 | 24.4094 | 24.4094 | 24.4094 | 24.4094 | 24.4094 | 24.4094 | 24.4094 | 24.4094 | 24.4094 | 24.4094 | 24.4094 | 24.4094
25% | 4321.8611 | 11.2578 | 15.6094 | 16.7398 | 16.9321 | 17.0817 | 17.3401 | 17.9287 | 18.3222 | 18.8212 | 19.08 | 19.3073 | 18.8864 | 19.3785 | 20.1524 | 19.5641 | 19.5641 | 19.5641 | 19.5641 | 19.5641 | 19.5641 | 19.5641 | 19.5641 | 19.5641 | 19.5641 | 19.5641 | 19.5641 | 19.5641 | 19.5641 | 19.5641 | 19.5641 | 25% | 4321.8611 | 12.0494 | 16.3462 | 17.5208 | 17.7021 | 17.8167 | 18.0695 | 18.6673 | 18.9932 | 19.6149 | 21.5061 | 19.9457 | 19.6401 | 20.0513 | 20.9513 | 20.3412 | 20.3412 | 20.3412 | 20.3412 | 20.3412 | 20.3412 | 20.3412 | 20.3412 | 20.3412 | 20.3412 | 20.3412 | 20.3412 | 20.3412 | 20.3412 | 20.3412 | 20.3412
20% | 4353.067 | 9.0062 | 12.4875 | 13.3919 | 13.5457 | 13.6653 | 13.8721 | 14.3429 | 14.6578 | 15.057 | 15.264 | 15.4458 | 15.1091 | 15.5028 | 16.1219 | 15.6513 | 15.6513 | 15.6513 | 15.6513 | 15.6513 | 15.6513 | 15.6513 | 15.6513 | 15.6513 | 15.6513 | 15.6513 | 15.6513 | 15.6513 | 15.6513 | 15.6513 | 15.6513 | 20% | 4353.067 | 9.6396 | 13.0769 | 14.0166 | 14.1617 | 14.2534 | 14.4556 | 14.9339 | 15.1945 | 15.6919 | 17.2049 | 15.9566 | 15.7121 | 16.0411 | 16.7611 | 16.273 | 16.273 | 16.273 | 16.273 | 16.273 | 16.273 | 16.273 | 16.273 | 16.273 | 16.273 | 16.273 | 16.273 | 16.273 | 16.273 | 16.273 | 16.273
15% | 4369.4129 | 6.7547 | 9.3656 | 10.0439 | 10.1593 | 10.249 | 10.404 | 10.7572 | 10.9933 | 11.2927 | 11.448 | 11.5844 | 11.3318 | 11.6271 | 12.0914 | 11.7385 | 11.7385 | 11.7385 | 11.7385 | 11.7385 | 11.7385 | 11.7385 | 11.7385 | 11.7385 | 11.7385 | 11.7385 | 11.7385 | 11.7385 | 11.7385 | 11.7385 | 11.7385 | 15% | 4369.4129 | 7.2297 | 9.8077 | 10.5125 | 10.6213 | 10.69 | 10.8417 | 11.2004 | 11.3959 | 11.769 | 12.9036 | 11.9674 | 11.7841 | 12.0308 | 12.5708 | 12.2047 | 12.2047 | 12.2047 | 12.2047 | 12.2047 | 12.2047 | 12.2047 | 12.2047 | 12.2047 | 12.2047 | 12.2047 | 12.2047 | 12.2047 | 12.2047 | 12.2047 | 12.2047
10% | 4378.6261 | 4.5031 | 6.2438 | 6.6959 | 6.7728 | 6.8327 | 6.936 | 7.1715 | 7.3289 | 7.5285 | 7.632 | 7.7229 | 7.5546 | 7.7514 | 8.061 | 7.8256 | 7.8256 | 7.8256 | 7.8256 | 7.8256 | 7.8256 | 7.8256 | 7.8256 | 7.8256 | 7.8256 | 7.8256 | 7.8256 | 7.8256 | 7.8256 | 7.8256 | 7.8256 | 10% | 4378.6261 | 4.8198 | 6.5385 | 7.0083 | 7.0808 | 7.1267 | 7.2278 | 7.4669 | 7.5973 | 7.846 | 8.6024 | 7.9783 | 7.8561 | 8.0205 | 8.3805 | 8.1365 | 8.1365 | 8.1365 | 8.1365 | 8.1365 | 8.1365 | 8.1365 | 8.1365 | 8.1365 | 8.1365 | 8.1365 | 8.1365 | 8.1365 | 8.1365 | 8.1365 | 8.1365
5% | 4391.7028 | 2.2516 | 3.1219 | 3.348 | 3.3864 | 3.4163 | 3.468 | 3.5857 | 3.6644 | 3.7642 | 3.816 | 3.8615 | 3.7773 | 3.8757 | 4.0305 | 3.9128 | 3.9128 | 3.9128 | 3.9128 | 3.9128 | 3.9128 | 3.9128 | 3.9128 | 3.9128 | 3.9128 | 3.9128 | 3.9128 | 3.9128 | 3.9128 | 3.9128 | 3.9128 | 5% | 4391.7028 | 2.4099 | 3.2692 | 3.5042 | 3.5404 | 3.5633 | 3.6139 | 3.7335 | 3.7986 | 3.923 | 4.3012 | 3.9891 | 3.928 | 4.0103 | 4.1903 | 4.0682 | 4.0682 | 4.0682 | 4.0682 | 4.0682 | 4.0682 | 4.0682 | 4.0682 | 4.0682 | 4.0682 | 4.0682 | 4.0682 | 4.0682 | 4.0682 | 4.0682 | 4.0682
9.992e-14% | 4391.7028 | 4.4995e-14 | 6.2388e-14 | 6.6906e-14 | 6.7674e-14 | 6.8272e-14 | 6.9305e-14 | 7.1657e-14 | 7.323e-14 | 7.5225e-14 | 7.6259e-14 | 7.7167e-14 | 7.5485e-14 | 7.7452e-14 | 8.0545e-14 | 7.8194e-14 | 7.8194e-14 | 7.8194e-14 | 7.8194e-14 | 7.8194e-14 | 7.8194e-14 | 7.8194e-14 | 7.8194e-14 | 7.8194e-14 | 7.8194e-14 | 7.8194e-14 | 7.8194e-14 | 7.8194e-14 | 7.8194e-14 | 7.8194e-14 | 7.8194e-14 | 9.992e-14% | 4391.7028 | 4.8159e-14 | 6.5332e-14 | 7.0027e-14 | 7.0752e-14 | 7.121e-14 | 7.222e-14 | 7.461e-14 | 7.5912e-14 | 7.8397e-14 | 8.5956e-14 | 7.9719e-14 | 7.8498e-14 | 8.0141e-14 | 8.3738e-14 | 8.13e-14 | 8.13e-14 | 8.13e-14 | 8.13e-14 | 8.13e-14 | 8.13e-14 | 8.13e-14 | 8.13e-14 | 8.13e-14 | 8.13e-14 | 8.13e-14 | 8.13e-14 | 8.13e-14 | 8.13e-14 | 8.13e-14 | 8.13e-14
Summer Season | [31 empty] | Summer Season
P50 | [31 empty] | P10
% of MD | Summer - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Summer - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 51.1621 | 67.921 | 72.4827 | 72.3498 | 72.345 | 72.8648 | 73.4353 | 74.6066 | 75.4483 | 75.9048 | 76.4041 | 76.8611 | 77.687 | 78.7121 | 78.6404 | 78.6404 | 78.6404 | 78.6404 | 78.6404 | 78.6404 | 78.6404 | 78.6404 | 78.6404 | 78.6404 | 78.6404 | 78.6404 | 78.6404 | 78.6404 | 78.6404 | 78.6404 | 100% | 0 | 57.0282 | 73.8207 | 78.2145 | 77.9508 | 77.9694 | 78.4199 | 79.6095 | 80.4052 | 81.1846 | 82.0962 | 82.9406 | 83.7606 | 83.8537 | 84.8109 | 84.0841 | 84.0841 | 84.0841 | 84.0841 | 84.0841 | 84.0841 | 84.0841 | 84.0841 | 84.0841 | 84.0841 | 84.0841 | 84.0841 | 84.0841 | 84.0841 | 84.0841 | 84.0841
99% | 0 | 50.6505 | 67.2418 | 71.7579 | 71.6263 | 71.6215 | 72.1362 | 72.701 | 73.8605 | 74.6938 | 75.1458 | 75.64 | 76.0925 | 76.9101 | 77.9249 | 77.854 | 77.854 | 77.854 | 77.854 | 77.854 | 77.854 | 77.854 | 77.854 | 77.854 | 77.854 | 77.854 | 77.854 | 77.854 | 77.854 | 77.854 | 77.854 | 99% | 1.5127 | 56.4579 | 73.0825 | 77.4324 | 77.1713 | 77.1897 | 77.6357 | 78.8134 | 79.6012 | 80.3728 | 81.2753 | 82.1112 | 82.923 | 83.0151 | 83.9628 | 83.2432 | 83.2432 | 83.2432 | 83.2432 | 83.2432 | 83.2432 | 83.2432 | 83.2432 | 83.2432 | 83.2432 | 83.2432 | 83.2432 | 83.2432 | 83.2432 | 83.2432 | 83.2432
98% | 0 | 50.1389 | 66.5626 | 71.033 | 70.9028 | 70.8981 | 71.4075 | 71.9666 | 73.1145 | 73.9393 | 74.3867 | 74.876 | 75.3239 | 76.1333 | 77.1378 | 77.0676 | 77.0676 | 77.0676 | 77.0676 | 77.0676 | 77.0676 | 77.0676 | 77.0676 | 77.0676 | 77.0676 | 77.0676 | 77.0676 | 77.0676 | 77.0676 | 77.0676 | 77.0676 | 98% | 2.269 | 55.8876 | 72.3443 | 76.6503 | 76.3918 | 76.41 | 76.8515 | 78.0173 | 78.7971 | 79.5609 | 80.4543 | 81.2818 | 82.0854 | 82.1766 | 83.1147 | 82.4024 | 82.4024 | 82.4024 | 82.4024 | 82.4024 | 82.4024 | 82.4024 | 82.4024 | 82.4024 | 82.4024 | 82.4024 | 82.4024 | 82.4024 | 82.4024 | 82.4024 | 82.4024
97% | 0.37816 | 49.6272 | 65.8834 | 70.3082 | 70.1794 | 70.1746 | 70.6789 | 71.2323 | 72.3684 | 73.1848 | 73.6277 | 74.112 | 74.5553 | 75.3564 | 76.3507 | 76.2812 | 76.2812 | 76.2812 | 76.2812 | 76.2812 | 76.2812 | 76.2812 | 76.2812 | 76.2812 | 76.2812 | 76.2812 | 76.2812 | 76.2812 | 76.2812 | 76.2812 | 76.2812 | 97% | 3.7816 | 55.3173 | 71.6061 | 75.8681 | 75.6123 | 75.6303 | 76.0673 | 77.2212 | 77.9931 | 78.7491 | 79.6334 | 80.4523 | 81.2478 | 81.338 | 82.2666 | 81.5615 | 81.5615 | 81.5615 | 81.5615 | 81.5615 | 81.5615 | 81.5615 | 81.5615 | 81.5615 | 81.5615 | 81.5615 | 81.5615 | 81.5615 | 81.5615 | 81.5615 | 81.5615
95% | 2.269 | 48.604 | 64.5249 | 68.8586 | 68.7324 | 68.7277 | 69.2216 | 69.7636 | 70.8763 | 71.6758 | 72.1096 | 72.5839 | 73.0181 | 73.8027 | 74.7765 | 74.7084 | 74.7084 | 74.7084 | 74.7084 | 74.7084 | 74.7084 | 74.7084 | 74.7084 | 74.7084 | 74.7084 | 74.7084 | 74.7084 | 74.7084 | 74.7084 | 74.7084 | 74.7084 | 95% | 6.0506 | 54.1768 | 70.1297 | 74.3038 | 74.0533 | 74.071 | 74.4989 | 75.629 | 76.385 | 77.1254 | 77.9914 | 78.7935 | 79.5726 | 79.661 | 80.5703 | 79.8799 | 79.8799 | 79.8799 | 79.8799 | 79.8799 | 79.8799 | 79.8799 | 79.8799 | 79.8799 | 79.8799 | 79.8799 | 79.8799 | 79.8799 | 79.8799 | 79.8799 | 79.8799
90% | 5.6725 | 46.0459 | 61.1289 | 65.2344 | 65.1149 | 65.1105 | 65.5784 | 66.0918 | 67.1459 | 67.9034 | 68.3143 | 68.7637 | 69.175 | 69.9183 | 70.8409 | 70.7764 | 70.7764 | 70.7764 | 70.7764 | 70.7764 | 70.7764 | 70.7764 | 70.7764 | 70.7764 | 70.7764 | 70.7764 | 70.7764 | 70.7764 | 70.7764 | 70.7764 | 70.7764 | 90% | 16.2611 | 51.3254 | 66.4386 | 70.3931 | 70.1557 | 70.1725 | 70.5779 | 71.6485 | 72.3647 | 73.0662 | 73.8866 | 74.6465 | 75.3846 | 75.4683 | 76.3298 | 75.6757 | 75.6757 | 75.6757 | 75.6757 | 75.6757 | 75.6757 | 75.6757 | 75.6757 | 75.6757 | 75.6757 | 75.6757 | 75.6757 | 75.6757 | 75.6757 | 75.6757 | 75.6757
85% | 15.8829 | 43.4878 | 57.7328 | 61.6103 | 61.4974 | 61.4932 | 61.9351 | 62.42 | 63.4156 | 64.131 | 64.5191 | 64.9435 | 65.332 | 66.034 | 66.9053 | 66.8444 | 66.8444 | 66.8444 | 66.8444 | 66.8444 | 66.8444 | 66.8444 | 66.8444 | 66.8444 | 66.8444 | 66.8444 | 66.8444 | 66.8444 | 66.8444 | 66.8444 | 66.8444 | 85% | 26.4715 | 48.4739 | 62.7476 | 66.4824 | 66.2582 | 66.274 | 66.6569 | 67.6681 | 68.3445 | 69.0069 | 69.7818 | 70.4995 | 71.1965 | 71.2756 | 72.0892 | 71.4715 | 71.4715 | 71.4715 | 71.4715 | 71.4715 | 71.4715 | 71.4715 | 71.4715 | 71.4715 | 71.4715 | 71.4715 | 71.4715 | 71.4715 | 71.4715 | 71.4715 | 71.4715
80% | 31.0095 | 40.9297 | 54.3368 | 57.9862 | 57.8799 | 57.876 | 58.2919 | 58.7483 | 59.6853 | 60.3586 | 60.7239 | 61.1233 | 61.4889 | 62.1496 | 62.9697 | 62.9123 | 62.9123 | 62.9123 | 62.9123 | 62.9123 | 62.9123 | 62.9123 | 62.9123 | 62.9123 | 62.9123 | 62.9123 | 62.9123 | 62.9123 | 62.9123 | 62.9123 | 62.9123 | 80% | 34.0348 | 45.6225 | 59.0566 | 62.5716 | 62.3606 | 62.3755 | 62.7359 | 63.6876 | 64.3242 | 64.9477 | 65.677 | 66.3524 | 67.0085 | 67.0829 | 67.8487 | 67.2672 | 67.2672 | 67.2672 | 67.2672 | 67.2672 | 67.2672 | 67.2672 | 67.2672 | 67.2672 | 67.2672 | 67.2672 | 67.2672 | 67.2672 | 67.2672 | 67.2672 | 67.2672
75% | 72.9857 | 38.3716 | 50.9407 | 54.362 | 54.2624 | 54.2587 | 54.6486 | 55.0765 | 55.955 | 56.5862 | 56.9286 | 57.3031 | 57.6458 | 58.2653 | 59.0341 | 58.9803 | 58.9803 | 58.9803 | 58.9803 | 58.9803 | 58.9803 | 58.9803 | 58.9803 | 58.9803 | 58.9803 | 58.9803 | 58.9803 | 58.9803 | 58.9803 | 58.9803 | 58.9803 | 75% | 48.405 | 42.7711 | 55.3655 | 58.6609 | 58.4631 | 58.4771 | 58.8149 | 59.7071 | 60.3039 | 60.8885 | 61.5722 | 62.2054 | 62.8205 | 62.8902 | 63.6082 | 63.063 | 63.063 | 63.063 | 63.063 | 63.063 | 63.063 | 63.063 | 63.063 | 63.063 | 63.063 | 63.063 | 63.063 | 63.063 | 63.063 | 63.063 | 63.063
70% | 150.5094 | 35.8135 | 47.5447 | 50.7379 | 50.6449 | 50.6415 | 51.0054 | 51.4047 | 52.2246 | 52.8138 | 53.1334 | 53.4829 | 53.8028 | 54.3809 | 55.0984 | 55.0483 | 55.0483 | 55.0483 | 55.0483 | 55.0483 | 55.0483 | 55.0483 | 55.0483 | 55.0483 | 55.0483 | 55.0483 | 55.0483 | 55.0483 | 55.0483 | 55.0483 | 55.0483 | 70% | 76.3892 | 39.9197 | 51.6745 | 54.7502 | 54.5656 | 54.5786 | 54.8939 | 55.7266 | 56.2837 | 56.8292 | 57.4674 | 58.0584 | 58.6324 | 58.6976 | 59.3676 | 58.8588 | 58.8588 | 58.8588 | 58.8588 | 58.8588 | 58.8588 | 58.8588 | 58.8588 | 58.8588 | 58.8588 | 58.8588 | 58.8588 | 58.8588 | 58.8588 | 58.8588 | 58.8588
65% | 359.6342 | 33.2554 | 44.1486 | 47.1138 | 47.0274 | 47.0242 | 47.3621 | 47.733 | 48.4943 | 49.0414 | 49.3381 | 49.6627 | 49.9597 | 50.4966 | 51.1628 | 51.1163 | 51.1163 | 51.1163 | 51.1163 | 51.1163 | 51.1163 | 51.1163 | 51.1163 | 51.1163 | 51.1163 | 51.1163 | 51.1163 | 51.1163 | 51.1163 | 51.1163 | 51.1163 | 65% | 114.2056 | 37.0683 | 47.9835 | 50.8395 | 50.668 | 50.6801 | 50.9729 | 51.7462 | 52.2634 | 52.77 | 53.3626 | 53.9114 | 54.4444 | 54.5049 | 55.1271 | 54.6546 | 54.6546 | 54.6546 | 54.6546 | 54.6546 | 54.6546 | 54.6546 | 54.6546 | 54.6546 | 54.6546 | 54.6546 | 54.6546 | 54.6546 | 54.6546 | 54.6546 | 54.6546
60% | 689.7717 | 30.6973 | 40.7526 | 43.4896 | 43.4099 | 43.407 | 43.7189 | 44.0612 | 44.764 | 45.269 | 45.5429 | 45.8424 | 46.1167 | 46.6122 | 47.2272 | 47.1843 | 47.1843 | 47.1843 | 47.1843 | 47.1843 | 47.1843 | 47.1843 | 47.1843 | 47.1843 | 47.1843 | 47.1843 | 47.1843 | 47.1843 | 47.1843 | 47.1843 | 47.1843 | 60% | 178.1154 | 34.2169 | 44.2924 | 46.9287 | 46.7705 | 46.7817 | 47.0519 | 47.7657 | 48.2431 | 48.7108 | 49.2577 | 49.7643 | 50.2564 | 50.3122 | 50.8865 | 50.4504 | 50.4504 | 50.4504 | 50.4504 | 50.4504 | 50.4504 | 50.4504 | 50.4504 | 50.4504 | 50.4504 | 50.4504 | 50.4504 | 50.4504 | 50.4504 | 50.4504 | 50.4504
55% | 1095.5419 | 28.1392 | 37.3565 | 39.8655 | 39.7924 | 39.7897 | 40.0757 | 40.3894 | 41.0336 | 41.4965 | 41.7476 | 42.0222 | 42.2736 | 42.7279 | 43.2916 | 43.2522 | 43.2522 | 43.2522 | 43.2522 | 43.2522 | 43.2522 | 43.2522 | 43.2522 | 43.2522 | 43.2522 | 43.2522 | 43.2522 | 43.2522 | 43.2522 | 43.2522 | 43.2522 | 55% | 311.6074 | 31.3655 | 40.6014 | 43.018 | 42.8729 | 42.8832 | 43.131 | 43.7852 | 44.2229 | 44.6515 | 45.1529 | 45.6173 | 46.0683 | 46.1195 | 46.646 | 46.2462 | 46.2462 | 46.2462 | 46.2462 | 46.2462 | 46.2462 | 46.2462 | 46.2462 | 46.2462 | 46.2462 | 46.2462 | 46.2462 | 46.2462 | 46.2462 | 46.2462 | 46.2462
50% | 1666.1918 | 25.581 | 33.9605 | 36.2413 | 36.1749 | 36.1725 | 36.4324 | 36.7177 | 37.3033 | 37.7241 | 37.9524 | 38.202 | 38.4306 | 38.8435 | 39.356 | 39.3202 | 39.3202 | 39.3202 | 39.3202 | 39.3202 | 39.3202 | 39.3202 | 39.3202 | 39.3202 | 39.3202 | 39.3202 | 39.3202 | 39.3202 | 39.3202 | 39.3202 | 39.3202 | 50% | 636.0723 | 28.5141 | 36.9103 | 39.1073 | 38.9754 | 38.9847 | 39.21 | 39.8047 | 40.2026 | 40.5923 | 41.0481 | 41.4703 | 41.8803 | 41.9268 | 42.4054 | 42.042 | 42.042 | 42.042 | 42.042 | 42.042 | 42.042 | 42.042 | 42.042 | 42.042 | 42.042 | 42.042 | 42.042 | 42.042 | 42.042 | 42.042 | 42.042
45% | 2506.0947 | 23.0229 | 30.5644 | 32.6172 | 32.5574 | 32.5552 | 32.7892 | 33.0459 | 33.573 | 33.9517 | 34.1572 | 34.3818 | 34.5875 | 34.9592 | 35.4204 | 35.3882 | 35.3882 | 35.3882 | 35.3882 | 35.3882 | 35.3882 | 35.3882 | 35.3882 | 35.3882 | 35.3882 | 35.3882 | 35.3882 | 35.3882 | 35.3882 | 35.3882 | 35.3882 | 45% | 1179.4944 | 25.6627 | 33.2193 | 35.1965 | 35.0779 | 35.0862 | 35.289 | 35.8243 | 36.1824 | 36.5331 | 36.9433 | 37.3233 | 37.6923 | 37.7341 | 38.1649 | 37.8378 | 37.8378 | 37.8378 | 37.8378 | 37.8378 | 37.8378 | 37.8378 | 37.8378 | 37.8378 | 37.8378 | 37.8378 | 37.8378 | 37.8378 | 37.8378 | 37.8378 | 37.8378
40% | 3164.4787 | 20.4648 | 27.1684 | 28.9931 | 28.9399 | 28.938 | 29.1459 | 29.3741 | 29.8426 | 30.1793 | 30.3619 | 30.5616 | 30.7444 | 31.0748 | 31.4848 | 31.4562 | 31.4562 | 31.4562 | 31.4562 | 31.4562 | 31.4562 | 31.4562 | 31.4562 | 31.4562 | 31.4562 | 31.4562 | 31.4562 | 31.4562 | 31.4562 | 31.4562 | 31.4562 | 40% | 1808.3816 | 22.8113 | 29.5283 | 31.2858 | 31.1803 | 31.1878 | 31.368 | 31.8438 | 32.1621 | 32.4738 | 32.8385 | 33.1762 | 33.5042 | 33.5415 | 33.9244 | 33.6336 | 33.6336 | 33.6336 | 33.6336 | 33.6336 | 33.6336 | 33.6336 | 33.6336 | 33.6336 | 33.6336 | 33.6336 | 33.6336 | 33.6336 | 33.6336 | 33.6336 | 33.6336
35% | 3551.3408 | 17.9067 | 23.7723 | 25.3689 | 25.3224 | 25.3207 | 25.5027 | 25.7024 | 26.1123 | 26.4069 | 26.5667 | 26.7414 | 26.9014 | 27.1905 | 27.5492 | 27.5241 | 27.5241 | 27.5241 | 27.5241 | 27.5241 | 27.5241 | 27.5241 | 27.5241 | 27.5241 | 27.5241 | 27.5241 | 27.5241 | 27.5241 | 27.5241 | 27.5241 | 27.5241 | 35% | 2779.1293 | 19.9599 | 25.8372 | 27.3751 | 27.2828 | 27.2893 | 27.447 | 27.8633 | 28.1418 | 28.4146 | 28.7337 | 29.0292 | 29.3162 | 29.3488 | 29.6838 | 29.4294 | 29.4294 | 29.4294 | 29.4294 | 29.4294 | 29.4294 | 29.4294 | 29.4294 | 29.4294 | 29.4294 | 29.4294 | 29.4294 | 29.4294 | 29.4294 | 29.4294 | 29.4294
30% | 3758.953 | 15.3486 | 20.3763 | 21.7448 | 21.705 | 21.7035 | 21.8595 | 22.0306 | 22.382 | 22.6345 | 22.7714 | 22.9212 | 23.0583 | 23.3061 | 23.6136 | 23.5921 | 23.5921 | 23.5921 | 23.5921 | 23.5921 | 23.5921 | 23.5921 | 23.5921 | 23.5921 | 23.5921 | 23.5921 | 23.5921 | 23.5921 | 23.5921 | 23.5921 | 23.5921 | 30% | 3814.165 | 17.1085 | 22.1462 | 23.4644 | 23.3852 | 23.3908 | 23.526 | 23.8828 | 24.1216 | 24.3554 | 24.6289 | 24.8822 | 25.1282 | 25.1561 | 25.4433 | 25.2252 | 25.2252 | 25.2252 | 25.2252 | 25.2252 | 25.2252 | 25.2252 | 25.2252 | 25.2252 | 25.2252 | 25.2252 | 25.2252 | 25.2252 | 25.2252 | 25.2252 | 25.2252
25% | 3926.4798 | 12.7905 | 16.9802 | 18.1207 | 18.0875 | 18.0862 | 18.2162 | 18.3588 | 18.6517 | 18.8621 | 18.9762 | 19.101 | 19.2153 | 19.4218 | 19.678 | 19.6601 | 19.6601 | 19.6601 | 19.6601 | 19.6601 | 19.6601 | 19.6601 | 19.6601 | 19.6601 | 19.6601 | 19.6601 | 19.6601 | 19.6601 | 19.6601 | 19.6601 | 19.6601 | 25% | 4166.9923 | 14.257 | 18.4552 | 19.5536 | 19.4877 | 19.4924 | 19.605 | 19.9024 | 20.1013 | 20.2962 | 20.5241 | 20.7351 | 20.9402 | 20.9634 | 21.2027 | 21.021 | 21.021 | 21.021 | 21.021 | 21.021 | 21.021 | 21.021 | 21.021 | 21.021 | 21.021 | 21.021 | 21.021 | 21.021 | 21.021 | 21.021 | 21.021
20% | 4050.5177 | 10.2324 | 13.5842 | 14.4965 | 14.47 | 14.469 | 14.573 | 14.6871 | 14.9213 | 15.0897 | 15.181 | 15.2808 | 15.3722 | 15.5374 | 15.7424 | 15.7281 | 15.7281 | 15.7281 | 15.7281 | 15.7281 | 15.7281 | 15.7281 | 15.7281 | 15.7281 | 15.7281 | 15.7281 | 15.7281 | 15.7281 | 15.7281 | 15.7281 | 15.7281 | 20% | 4282.7105 | 11.4056 | 14.7641 | 15.6429 | 15.5902 | 15.5939 | 15.684 | 15.9219 | 16.081 | 16.2369 | 16.4192 | 16.5881 | 16.7521 | 16.7707 | 16.9622 | 16.8168 | 16.8168 | 16.8168 | 16.8168 | 16.8168 | 16.8168 | 16.8168 | 16.8168 | 16.8168 | 16.8168 | 16.8168 | 16.8168 | 16.8168 | 16.8168 | 16.8168 | 16.8168
15% | 4152.622 | 7.6743 | 10.1881 | 10.8724 | 10.8525 | 10.8517 | 10.9297 | 11.0153 | 11.191 | 11.3172 | 11.3857 | 11.4606 | 11.5292 | 11.6531 | 11.8068 | 11.7961 | 11.7961 | 11.7961 | 11.7961 | 11.7961 | 11.7961 | 11.7961 | 11.7961 | 11.7961 | 11.7961 | 11.7961 | 11.7961 | 11.7961 | 11.7961 | 11.7961 | 11.7961 | 15% | 4364.7722 | 8.5542 | 11.0731 | 11.7322 | 11.6926 | 11.6954 | 11.763 | 11.9414 | 12.0608 | 12.1777 | 12.3144 | 12.4411 | 12.5641 | 12.578 | 12.7216 | 12.6126 | 12.6126 | 12.6126 | 12.6126 | 12.6126 | 12.6126 | 12.6126 | 12.6126 | 12.6126 | 12.6126 | 12.6126 | 12.6126 | 12.6126 | 12.6126 | 12.6126 | 12.6126
10% | 4248.2976 | 5.1162 | 6.7921 | 7.2483 | 7.235 | 7.2345 | 7.2865 | 7.3435 | 7.4607 | 7.5448 | 7.5905 | 7.6404 | 7.6861 | 7.7687 | 7.8712 | 7.864 | 7.864 | 7.864 | 7.864 | 7.864 | 7.864 | 7.864 | 7.864 | 7.864 | 7.864 | 7.864 | 7.864 | 7.864 | 7.864 | 7.864 | 7.864 | 10% | 4391.6218 | 5.7028 | 7.3821 | 7.8215 | 7.7951 | 7.7969 | 7.842 | 7.9609 | 8.0405 | 8.1185 | 8.2096 | 8.2941 | 8.3761 | 8.3854 | 8.4811 | 8.4084 | 8.4084 | 8.4084 | 8.4084 | 8.4084 | 8.4084 | 8.4084 | 8.4084 | 8.4084 | 8.4084 | 8.4084 | 8.4084 | 8.4084 | 8.4084 | 8.4084 | 8.4084
5% | 4361.7469 | 2.5581 | 3.396 | 3.6241 | 3.6175 | 3.6172 | 3.6432 | 3.6718 | 3.7303 | 3.7724 | 3.7952 | 3.8202 | 3.8431 | 3.8844 | 3.9356 | 3.932 | 3.932 | 3.932 | 3.932 | 3.932 | 3.932 | 3.932 | 3.932 | 3.932 | 3.932 | 3.932 | 3.932 | 3.932 | 3.932 | 3.932 | 3.932 | 5% | 4391.6218 | 2.8514 | 3.691 | 3.9107 | 3.8975 | 3.8985 | 3.921 | 3.9805 | 4.0203 | 4.0592 | 4.1048 | 4.147 | 4.188 | 4.1927 | 4.2405 | 4.2042 | 4.2042 | 4.2042 | 4.2042 | 4.2042 | 4.2042 | 4.2042 | 4.2042 | 4.2042 | 4.2042 | 4.2042 | 4.2042 | 4.2042 | 4.2042 | 4.2042 | 4.2042
9.992e-14% | 4391.6218 | 5.1121e-14 | 6.7867e-14 | 7.2425e-14 | 7.2292e-14 | 7.2287e-14 | 7.2807e-14 | 7.3377e-14 | 7.4547e-14 | 7.5388e-14 | 7.5844e-14 | 7.6343e-14 | 7.68e-14 | 7.7625e-14 | 7.8649e-14 | 7.8578e-14 | 7.8578e-14 | 7.8578e-14 | 7.8578e-14 | 7.8578e-14 | 7.8578e-14 | 7.8578e-14 | 7.8578e-14 | 7.8578e-14 | 7.8578e-14 | 7.8578e-14 | 7.8578e-14 | 7.8578e-14 | 7.8578e-14 | 7.8578e-14 | 7.8578e-14 | 9.992e-14% | 4391.6218 | 5.6983e-14 | 7.3762e-14 | 7.8152e-14 | 7.7889e-14 | 7.7907e-14 | 7.8357e-14 | 7.9546e-14 | 8.0341e-14 | 8.112e-14 | 8.2031e-14 | 8.2874e-14 | 8.3694e-14 | 8.3787e-14 | 8.4743e-14 | 8.4017e-14 | 8.4017e-14 | 8.4017e-14 | 8.4017e-14 | 8.4017e-14 | 8.4017e-14 | 8.4017e-14 | 8.4017e-14 | 8.4017e-14 | 8.4017e-14 | 8.4017e-14 | 8.4017e-14 | 8.4017e-14 | 8.4017e-14 | 8.4017e-14 | 8.4017e-14
Option 4
Winter Season | [31 empty] | Winter Season
P50 | [31 empty] | P10
% of MD | Winter - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Winter - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 45.0311 | 62.4376 | 66.9594 | 63.7285 | 64.3267 | 65.3603 | 67.7146 | 69.2888 | 71.2849 | 72.3199 | 73.2291 | 71.5455 | 73.5138 | 76.6095 | 74.2564 | 74.2564 | 74.2564 | 74.2564 | 74.2564 | 74.2564 | 74.2564 | 74.2564 | 74.2564 | 74.2564 | 74.2564 | 74.2564 | 74.2564 | 74.2564 | 74.2564 | 74.2564 | 100% | 0 | 48.1978 | 65.3847 | 70.0831 | 66.8084 | 67.267 | 68.2781 | 70.6693 | 71.9727 | 74.4597 | 82.0243 | 75.7829 | 74.5605 | 76.2054 | 79.8053 | 77.3648 | 77.3648 | 77.3648 | 77.3648 | 77.3648 | 77.3648 | 77.3648 | 77.3648 | 77.3648 | 77.3648 | 77.3648 | 77.3648 | 77.3648 | 77.3648 | 77.3648 | 77.3648
99% | 1.486 | 44.5808 | 61.8132 | 66.2898 | 63.0912 | 63.6835 | 64.7067 | 67.0375 | 68.5959 | 70.572 | 71.5967 | 72.4969 | 70.8301 | 72.7787 | 75.8434 | 73.5139 | 73.5139 | 73.5139 | 73.5139 | 73.5139 | 73.5139 | 73.5139 | 73.5139 | 73.5139 | 73.5139 | 73.5139 | 73.5139 | 73.5139 | 73.5139 | 73.5139 | 73.5139 | 99% | 1.486 | 47.7158 | 64.7309 | 69.3823 | 66.1403 | 66.5943 | 67.5953 | 69.9626 | 71.2529 | 73.7151 | 81.2041 | 75.0251 | 73.8149 | 75.4433 | 79.0072 | 76.5912 | 76.5912 | 76.5912 | 76.5912 | 76.5912 | 76.5912 | 76.5912 | 76.5912 | 76.5912 | 76.5912 | 76.5912 | 76.5912 | 76.5912 | 76.5912 | 76.5912 | 76.5912
98% | 3.2692 | 44.1305 | 61.1889 | 65.6202 | 62.4539 | 63.0402 | 64.0531 | 66.3604 | 67.903 | 69.8592 | 70.8735 | 71.7646 | 70.1146 | 72.0436 | 75.0773 | 72.7713 | 72.7713 | 72.7713 | 72.7713 | 72.7713 | 72.7713 | 72.7713 | 72.7713 | 72.7713 | 72.7713 | 72.7713 | 72.7713 | 72.7713 | 72.7713 | 72.7713 | 72.7713 | 98% | 3.2692 | 47.2338 | 64.0771 | 68.6815 | 65.4722 | 65.9216 | 66.9125 | 69.2559 | 70.5332 | 72.9705 | 80.3838 | 74.2673 | 73.0693 | 74.6813 | 78.2092 | 75.8175 | 75.8175 | 75.8175 | 75.8175 | 75.8175 | 75.8175 | 75.8175 | 75.8175 | 75.8175 | 75.8175 | 75.8175 | 75.8175 | 75.8175 | 75.8175 | 75.8175 | 75.8175
97% | 6.8356 | 43.6802 | 60.5645 | 64.9506 | 61.8166 | 62.3969 | 63.3995 | 65.6832 | 67.2101 | 69.1463 | 70.1503 | 71.0323 | 69.3992 | 71.3084 | 74.3112 | 72.0287 | 72.0287 | 72.0287 | 72.0287 | 72.0287 | 72.0287 | 72.0287 | 72.0287 | 72.0287 | 72.0287 | 72.0287 | 72.0287 | 72.0287 | 72.0287 | 72.0287 | 72.0287 | 97% | 6.8356 | 46.7518 | 63.4232 | 67.9806 | 64.8041 | 65.249 | 66.2297 | 68.5492 | 69.8135 | 72.2259 | 79.5636 | 73.5094 | 72.3237 | 73.9192 | 77.4111 | 75.0439 | 75.0439 | 75.0439 | 75.0439 | 75.0439 | 75.0439 | 75.0439 | 75.0439 | 75.0439 | 75.0439 | 75.0439 | 75.0439 | 75.0439 | 75.0439 | 75.0439 | 75.0439
95% | 17.5347 | 42.7796 | 59.3157 | 63.6114 | 60.542 | 61.1104 | 62.0923 | 64.3289 | 65.8243 | 67.7207 | 68.7039 | 69.5677 | 67.9683 | 69.8382 | 72.779 | 70.5436 | 70.5436 | 70.5436 | 70.5436 | 70.5436 | 70.5436 | 70.5436 | 70.5436 | 70.5436 | 70.5436 | 70.5436 | 70.5436 | 70.5436 | 70.5436 | 70.5436 | 70.5436 | 95% | 17.5347 | 45.7879 | 62.1155 | 66.579 | 63.468 | 63.9036 | 64.8642 | 67.1358 | 68.374 | 70.7368 | 77.9231 | 71.9938 | 70.8325 | 72.3951 | 75.815 | 73.4966 | 73.4966 | 73.4966 | 73.4966 | 73.4966 | 73.4966 | 73.4966 | 73.4966 | 73.4966 | 73.4966 | 73.4966 | 73.4966 | 73.4966 | 73.4966 | 73.4966 | 73.4966
90% | 78.7576 | 40.528 | 56.1939 | 60.2634 | 57.3556 | 57.8941 | 58.8243 | 60.9432 | 62.3599 | 64.1564 | 65.0879 | 65.9062 | 64.391 | 66.1625 | 68.9486 | 66.8308 | 66.8308 | 66.8308 | 66.8308 | 66.8308 | 66.8308 | 66.8308 | 66.8308 | 66.8308 | 66.8308 | 66.8308 | 66.8308 | 66.8308 | 66.8308 | 66.8308 | 66.8308 | 90% | 78.7576 | 43.378 | 58.8463 | 63.0748 | 60.1275 | 60.5403 | 61.4503 | 63.6023 | 64.7754 | 67.0138 | 73.8219 | 68.2046 | 67.1045 | 68.5848 | 71.8247 | 69.6283 | 69.6283 | 69.6283 | 69.6283 | 69.6283 | 69.6283 | 69.6283 | 69.6283 | 69.6283 | 69.6283 | 69.6283 | 69.6283 | 69.6283 | 69.6283 | 69.6283 | 69.6283
85% | 236.8672 | 38.2764 | 53.072 | 56.9155 | 54.1692 | 54.6777 | 55.5563 | 57.5575 | 58.8954 | 60.5922 | 61.4719 | 62.2448 | 60.8137 | 62.4868 | 65.1181 | 63.118 | 63.118 | 63.118 | 63.118 | 63.118 | 63.118 | 63.118 | 63.118 | 63.118 | 63.118 | 63.118 | 63.118 | 63.118 | 63.118 | 63.118 | 63.118 | 85% | 236.8672 | 40.9681 | 55.577 | 59.5707 | 56.7871 | 57.1769 | 58.0364 | 60.0689 | 61.1768 | 63.2908 | 69.7207 | 64.4155 | 63.3765 | 64.7746 | 67.8345 | 65.7601 | 65.7601 | 65.7601 | 65.7601 | 65.7601 | 65.7601 | 65.7601 | 65.7601 | 65.7601 | 65.7601 | 65.7601 | 65.7601 | 65.7601 | 65.7601 | 65.7601 | 65.7601
80% | 497.5104 | 36.0249 | 49.9501 | 53.5675 | 50.9828 | 51.4614 | 52.2882 | 54.1717 | 55.431 | 57.0279 | 57.856 | 58.5833 | 57.2364 | 58.8111 | 61.2876 | 59.4051 | 59.4051 | 59.4051 | 59.4051 | 59.4051 | 59.4051 | 59.4051 | 59.4051 | 59.4051 | 59.4051 | 59.4051 | 59.4051 | 59.4051 | 59.4051 | 59.4051 | 59.4051 | 80% | 497.5104 | 38.5582 | 52.3078 | 56.0665 | 53.4467 | 53.8136 | 54.6225 | 56.5354 | 57.5781 | 59.5678 | 65.6195 | 60.6263 | 59.6484 | 60.9643 | 63.8442 | 61.8919 | 61.8919 | 61.8919 | 61.8919 | 61.8919 | 61.8919 | 61.8919 | 61.8919 | 61.8919 | 61.8919 | 61.8919 | 61.8919 | 61.8919 | 61.8919 | 61.8919 | 61.8919
75% | 803.6248 | 33.7733 | 46.8282 | 50.2195 | 47.7964 | 48.245 | 49.0202 | 50.786 | 51.9666 | 53.4637 | 54.24 | 54.9219 | 53.6592 | 55.1354 | 57.4571 | 55.6923 | 55.6923 | 55.6923 | 55.6923 | 55.6923 | 55.6923 | 55.6923 | 55.6923 | 55.6923 | 55.6923 | 55.6923 | 55.6923 | 55.6923 | 55.6923 | 55.6923 | 55.6923 | 75% | 803.6248 | 36.1483 | 49.0386 | 52.5623 | 50.1063 | 50.4502 | 51.2086 | 53.0019 | 53.9795 | 55.8448 | 61.5182 | 56.8372 | 55.9204 | 57.154 | 59.8539 | 58.0236 | 58.0236 | 58.0236 | 58.0236 | 58.0236 | 58.0236 | 58.0236 | 58.0236 | 58.0236 | 58.0236 | 58.0236 | 58.0236 | 58.0236 | 58.0236 | 58.0236 | 58.0236
70% | 1155.2107 | 31.5218 | 43.7063 | 46.8715 | 44.6099 | 45.0287 | 45.7522 | 47.4003 | 48.5021 | 49.8994 | 50.624 | 51.2604 | 50.0819 | 51.4597 | 53.6267 | 51.9795 | 51.9795 | 51.9795 | 51.9795 | 51.9795 | 51.9795 | 51.9795 | 51.9795 | 51.9795 | 51.9795 | 51.9795 | 51.9795 | 51.9795 | 51.9795 | 51.9795 | 51.9795 | 70% | 1155.2107 | 33.7384 | 45.7693 | 49.0582 | 46.7659 | 47.0869 | 47.7947 | 49.4685 | 50.3809 | 52.1218 | 57.417 | 53.0481 | 52.1924 | 53.3438 | 55.8637 | 54.1554 | 54.1554 | 54.1554 | 54.1554 | 54.1554 | 54.1554 | 54.1554 | 54.1554 | 54.1554 | 54.1554 | 54.1554 | 54.1554 | 54.1554 | 54.1554 | 54.1554 | 54.1554
65% | 1553.1596 | 29.2702 | 40.5844 | 43.5236 | 41.4235 | 41.8124 | 42.4842 | 44.0145 | 45.0377 | 46.3352 | 47.008 | 47.5989 | 46.5046 | 47.784 | 49.7962 | 48.2667 | 48.2667 | 48.2667 | 48.2667 | 48.2667 | 48.2667 | 48.2667 | 48.2667 | 48.2667 | 48.2667 | 48.2667 | 48.2667 | 48.2667 | 48.2667 | 48.2667 | 48.2667 | 65% | 1553.1596 | 31.3286 | 42.5001 | 45.554 | 43.4254 | 43.7235 | 44.3808 | 45.935 | 46.7822 | 48.3988 | 53.3158 | 49.2589 | 48.4643 | 49.5335 | 51.8734 | 50.2871 | 50.2871 | 50.2871 | 50.2871 | 50.2871 | 50.2871 | 50.2871 | 50.2871 | 50.2871 | 50.2871 | 50.2871 | 50.2871 | 50.2871 | 50.2871 | 50.2871 | 50.2871
60% | 2026.2996 | 27.0187 | 37.4626 | 40.1756 | 38.2371 | 38.596 | 39.2162 | 40.6288 | 41.5733 | 42.7709 | 43.392 | 43.9375 | 42.9273 | 44.1083 | 45.9657 | 44.5539 | 44.5539 | 44.5539 | 44.5539 | 44.5539 | 44.5539 | 44.5539 | 44.5539 | 44.5539 | 44.5539 | 44.5539 | 44.5539 | 44.5539 | 44.5539 | 44.5539 | 44.5539 | 60% | 2026.2996 | 28.9187 | 39.2308 | 42.0499 | 40.085 | 40.3602 | 40.9669 | 42.4016 | 43.1836 | 44.6758 | 49.2146 | 45.4698 | 44.7363 | 45.7232 | 47.8832 | 46.4189 | 46.4189 | 46.4189 | 46.4189 | 46.4189 | 46.4189 | 46.4189 | 46.4189 | 46.4189 | 46.4189 | 46.4189 | 46.4189 | 46.4189 | 46.4189 | 46.4189 | 46.4189
55% | 2598.4068 | 24.7671 | 34.3407 | 36.8276 | 35.0507 | 35.3797 | 35.9482 | 37.2431 | 38.1088 | 39.2067 | 39.776 | 40.276 | 39.35 | 40.4326 | 42.1352 | 40.841 | 40.841 | 40.841 | 40.841 | 40.841 | 40.841 | 40.841 | 40.841 | 40.841 | 40.841 | 40.841 | 40.841 | 40.841 | 40.841 | 40.841 | 40.841 | 55% | 2598.4068 | 26.5088 | 35.9616 | 38.5457 | 36.7446 | 36.9968 | 37.553 | 38.8681 | 39.585 | 40.9529 | 45.1134 | 41.6806 | 41.0083 | 41.913 | 43.8929 | 42.5507 | 42.5507 | 42.5507 | 42.5507 | 42.5507 | 42.5507 | 42.5507 | 42.5507 | 42.5507 | 42.5507 | 42.5507 | 42.5507 | 42.5507 | 42.5507 | 42.5507 | 42.5507
50% | 3233.5201 | 22.5156 | 31.2188 | 33.4797 | 31.8642 | 32.1634 | 32.6802 | 33.8573 | 34.6444 | 35.6424 | 36.16 | 36.6146 | 35.7728 | 36.7569 | 38.3048 | 37.1282 | 37.1282 | 37.1282 | 37.1282 | 37.1282 | 37.1282 | 37.1282 | 37.1282 | 37.1282 | 37.1282 | 37.1282 | 37.1282 | 37.1282 | 37.1282 | 37.1282 | 37.1282 | 50% | 3233.5201 | 24.0989 | 32.6924 | 35.0416 | 33.4042 | 33.6335 | 34.139 | 35.3346 | 35.9863 | 37.2299 | 41.0122 | 37.8915 | 37.2803 | 38.1027 | 39.9026 | 38.6824 | 38.6824 | 38.6824 | 38.6824 | 38.6824 | 38.6824 | 38.6824 | 38.6824 | 38.6824 | 38.6824 | 38.6824 | 38.6824 | 38.6824 | 38.6824 | 38.6824 | 38.6824
45% | 3775.313 | 20.264 | 28.0969 | 30.1317 | 28.6778 | 28.947 | 29.4121 | 30.4716 | 31.1799 | 32.0782 | 32.544 | 32.9531 | 32.1955 | 33.0812 | 34.4743 | 33.4154 | 33.4154 | 33.4154 | 33.4154 | 33.4154 | 33.4154 | 33.4154 | 33.4154 | 33.4154 | 33.4154 | 33.4154 | 33.4154 | 33.4154 | 33.4154 | 33.4154 | 33.4154 | 45% | 3775.313 | 21.689 | 29.4231 | 31.5374 | 30.0638 | 30.2701 | 30.7251 | 31.8012 | 32.3877 | 33.5069 | 36.9109 | 34.1023 | 33.5522 | 34.2924 | 35.9124 | 34.8142 | 34.8142 | 34.8142 | 34.8142 | 34.8142 | 34.8142 | 34.8142 | 34.8142 | 34.8142 | 34.8142 | 34.8142 | 34.8142 | 34.8142 | 34.8142 | 34.8142 | 34.8142
40% | 4072.8088 | 18.0124 | 24.975 | 26.7837 | 25.4914 | 25.7307 | 26.1441 | 27.0859 | 27.7155 | 28.514 | 28.928 | 29.2917 | 28.6182 | 29.4055 | 30.6438 | 29.7026 | 29.7026 | 29.7026 | 29.7026 | 29.7026 | 29.7026 | 29.7026 | 29.7026 | 29.7026 | 29.7026 | 29.7026 | 29.7026 | 29.7026 | 29.7026 | 29.7026 | 29.7026 | 40% | 4072.8088 | 19.2791 | 26.1539 | 28.0332 | 26.7234 | 26.9068 | 27.3112 | 28.2677 | 28.7891 | 29.7839 | 32.8097 | 30.3132 | 29.8242 | 30.4822 | 31.9221 | 30.9459 | 30.9459 | 30.9459 | 30.9459 | 30.9459 | 30.9459 | 30.9459 | 30.9459 | 30.9459 | 30.9459 | 30.9459 | 30.9459 | 30.9459 | 30.9459 | 30.9459 | 30.9459
35% | 4198.821 | 15.7609 | 21.8532 | 23.4358 | 22.305 | 22.5144 | 22.8761 | 23.7001 | 24.2511 | 24.9497 | 25.312 | 25.6302 | 25.0409 | 25.7298 | 26.8133 | 25.9897 | 25.9897 | 25.9897 | 25.9897 | 25.9897 | 25.9897 | 25.9897 | 25.9897 | 25.9897 | 25.9897 | 25.9897 | 25.9897 | 25.9897 | 25.9897 | 25.9897 | 25.9897 | 35% | 4198.821 | 16.8692 | 22.8847 | 24.5291 | 23.3829 | 23.5434 | 23.8973 | 24.7342 | 25.1904 | 26.0609 | 28.7085 | 26.524 | 26.0962 | 26.6719 | 27.9318 | 27.0777 | 27.0777 | 27.0777 | 27.0777 | 27.0777 | 27.0777 | 27.0777 | 27.0777 | 27.0777 | 27.0777 | 27.0777 | 27.0777 | 27.0777 | 27.0777 | 27.0777 | 27.0777
30% | 4271.3374 | 13.5093 | 18.7313 | 20.0878 | 19.1185 | 19.298 | 19.6081 | 20.3144 | 20.7866 | 21.3855 | 21.696 | 21.9687 | 21.4637 | 22.0542 | 22.9829 | 22.2769 | 22.2769 | 22.2769 | 22.2769 | 22.2769 | 22.2769 | 22.2769 | 22.2769 | 22.2769 | 22.2769 | 22.2769 | 22.2769 | 22.2769 | 22.2769 | 22.2769 | 22.2769 | 30% | 4271.3374 | 14.4593 | 19.6154 | 21.0249 | 20.0425 | 20.1801 | 20.4834 | 21.2008 | 21.5918 | 22.3379 | 24.6073 | 22.7349 | 22.3682 | 22.8616 | 23.9416 | 23.2094 | 23.2094 | 23.2094 | 23.2094 | 23.2094 | 23.2094 | 23.2094 | 23.2094 | 23.2094 | 23.2094 | 23.2094 | 23.2094 | 23.2094 | 23.2094 | 23.2094 | 23.2094
25% | 4321.8611 | 11.2578 | 15.6094 | 16.7398 | 15.9321 | 16.0817 | 16.3401 | 16.9287 | 17.3222 | 17.8212 | 18.08 | 18.3073 | 17.8864 | 18.3785 | 19.1524 | 18.5641 | 18.5641 | 18.5641 | 18.5641 | 18.5641 | 18.5641 | 18.5641 | 18.5641 | 18.5641 | 18.5641 | 18.5641 | 18.5641 | 18.5641 | 18.5641 | 18.5641 | 18.5641 | 25% | 4321.8611 | 12.0494 | 16.3462 | 17.5208 | 16.7021 | 16.8167 | 17.0695 | 17.6673 | 17.9932 | 18.6149 | 20.5061 | 18.9457 | 18.6401 | 19.0513 | 19.9513 | 19.3412 | 19.3412 | 19.3412 | 19.3412 | 19.3412 | 19.3412 | 19.3412 | 19.3412 | 19.3412 | 19.3412 | 19.3412 | 19.3412 | 19.3412 | 19.3412 | 19.3412 | 19.3412
20% | 4353.067 | 9.0062 | 12.4875 | 13.3919 | 12.7457 | 12.8653 | 13.0721 | 13.5429 | 13.8578 | 14.257 | 14.464 | 14.6458 | 14.3091 | 14.7028 | 15.3219 | 14.8513 | 14.8513 | 14.8513 | 14.8513 | 14.8513 | 14.8513 | 14.8513 | 14.8513 | 14.8513 | 14.8513 | 14.8513 | 14.8513 | 14.8513 | 14.8513 | 14.8513 | 14.8513 | 20% | 4353.067 | 9.6396 | 13.0769 | 14.0166 | 13.3617 | 13.4534 | 13.6556 | 14.1339 | 14.3945 | 14.8919 | 16.4049 | 15.1566 | 14.9121 | 15.2411 | 15.9611 | 15.473 | 15.473 | 15.473 | 15.473 | 15.473 | 15.473 | 15.473 | 15.473 | 15.473 | 15.473 | 15.473 | 15.473 | 15.473 | 15.473 | 15.473 | 15.473
15% | 4369.4129 | 6.7547 | 9.3656 | 10.0439 | 9.5593 | 9.649 | 9.804 | 10.1572 | 10.3933 | 10.6927 | 10.848 | 10.9844 | 10.7318 | 11.0271 | 11.4914 | 11.1385 | 11.1385 | 11.1385 | 11.1385 | 11.1385 | 11.1385 | 11.1385 | 11.1385 | 11.1385 | 11.1385 | 11.1385 | 11.1385 | 11.1385 | 11.1385 | 11.1385 | 11.1385 | 15% | 4369.4129 | 7.2297 | 9.8077 | 10.5125 | 10.0213 | 10.09 | 10.2417 | 10.6004 | 10.7959 | 11.169 | 12.3036 | 11.3674 | 11.1841 | 11.4308 | 11.9708 | 11.6047 | 11.6047 | 11.6047 | 11.6047 | 11.6047 | 11.6047 | 11.6047 | 11.6047 | 11.6047 | 11.6047 | 11.6047 | 11.6047 | 11.6047 | 11.6047 | 11.6047 | 11.6047
10% | 4378.6261 | 4.5031 | 6.2438 | 6.6959 | 6.3728 | 6.4327 | 6.536 | 6.7715 | 6.9289 | 7.1285 | 7.232 | 7.3229 | 7.1546 | 7.3514 | 7.661 | 7.4256 | 7.4256 | 7.4256 | 7.4256 | 7.4256 | 7.4256 | 7.4256 | 7.4256 | 7.4256 | 7.4256 | 7.4256 | 7.4256 | 7.4256 | 7.4256 | 7.4256 | 7.4256 | 10% | 4378.6261 | 4.8198 | 6.5385 | 7.0083 | 6.6808 | 6.7267 | 6.8278 | 7.0669 | 7.1973 | 7.446 | 8.2024 | 7.5783 | 7.4561 | 7.6205 | 7.9805 | 7.7365 | 7.7365 | 7.7365 | 7.7365 | 7.7365 | 7.7365 | 7.7365 | 7.7365 | 7.7365 | 7.7365 | 7.7365 | 7.7365 | 7.7365 | 7.7365 | 7.7365 | 7.7365
5% | 4391.7028 | 2.2516 | 3.1219 | 3.348 | 3.1864 | 3.2163 | 3.268 | 3.3857 | 3.4644 | 3.5642 | 3.616 | 3.6615 | 3.5773 | 3.6757 | 3.8305 | 3.7128 | 3.7128 | 3.7128 | 3.7128 | 3.7128 | 3.7128 | 3.7128 | 3.7128 | 3.7128 | 3.7128 | 3.7128 | 3.7128 | 3.7128 | 3.7128 | 3.7128 | 3.7128 | 5% | 4391.7028 | 2.4099 | 3.2692 | 3.5042 | 3.3404 | 3.3633 | 3.4139 | 3.5335 | 3.5986 | 3.723 | 4.1012 | 3.7891 | 3.728 | 3.8103 | 3.9903 | 3.8682 | 3.8682 | 3.8682 | 3.8682 | 3.8682 | 3.8682 | 3.8682 | 3.8682 | 3.8682 | 3.8682 | 3.8682 | 3.8682 | 3.8682 | 3.8682 | 3.8682 | 3.8682
9.992e-14% | 4391.7028 | 4.4995e-14 | 6.2388e-14 | 6.6906e-14 | 6.3678e-14 | 6.4275e-14 | 6.5308e-14 | 6.7661e-14 | 6.9233e-14 | 7.1228e-14 | 7.2262e-14 | 7.3171e-14 | 7.1488e-14 | 7.3455e-14 | 7.6548e-14 | 7.4197e-14 | 7.4197e-14 | 7.4197e-14 | 7.4197e-14 | 7.4197e-14 | 7.4197e-14 | 7.4197e-14 | 7.4197e-14 | 7.4197e-14 | 7.4197e-14 | 7.4197e-14 | 7.4197e-14 | 7.4197e-14 | 7.4197e-14 | 7.4197e-14 | 7.4197e-14 | 9.992e-14% | 4391.7028 | 4.8159e-14 | 6.5332e-14 | 7.0027e-14 | 6.6755e-14 | 6.7213e-14 | 6.8224e-14 | 7.0613e-14 | 7.1915e-14 | 7.44e-14 | 8.1959e-14 | 7.5722e-14 | 7.4501e-14 | 7.6144e-14 | 7.9741e-14 | 7.7303e-14 | 7.7303e-14 | 7.7303e-14 | 7.7303e-14 | 7.7303e-14 | 7.7303e-14 | 7.7303e-14 | 7.7303e-14 | 7.7303e-14 | 7.7303e-14 | 7.7303e-14 | 7.7303e-14 | 7.7303e-14 | 7.7303e-14 | 7.7303e-14 | 7.7303e-14
Summer Season | [31 empty] | Summer Season
P50 | [31 empty] | P10
% of MD | Summer - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Summer - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 51.1621 | 67.921 | 72.4827 | 68.3498 | 68.345 | 68.8648 | 69.4353 | 70.6066 | 71.4483 | 71.9048 | 72.4041 | 72.8611 | 73.687 | 74.7121 | 74.6404 | 74.6404 | 74.6404 | 74.6404 | 74.6404 | 74.6404 | 74.6404 | 74.6404 | 74.6404 | 74.6404 | 74.6404 | 74.6404 | 74.6404 | 74.6404 | 74.6404 | 74.6404 | 100% | 0 | 57.0282 | 73.8207 | 78.2145 | 73.9508 | 73.9694 | 74.4199 | 75.6095 | 76.4052 | 77.1846 | 78.0962 | 78.9406 | 79.7606 | 79.8537 | 80.8109 | 80.0841 | 80.0841 | 80.0841 | 80.0841 | 80.0841 | 80.0841 | 80.0841 | 80.0841 | 80.0841 | 80.0841 | 80.0841 | 80.0841 | 80.0841 | 80.0841 | 80.0841 | 80.0841
99% | 0 | 50.6505 | 67.2418 | 71.7579 | 67.6663 | 67.6615 | 68.1762 | 68.741 | 69.9005 | 70.7338 | 71.1858 | 71.68 | 72.1325 | 72.9501 | 73.9649 | 73.894 | 73.894 | 73.894 | 73.894 | 73.894 | 73.894 | 73.894 | 73.894 | 73.894 | 73.894 | 73.894 | 73.894 | 73.894 | 73.894 | 73.894 | 73.894 | 99% | 1.5127 | 56.4579 | 73.0825 | 77.4324 | 73.2113 | 73.2297 | 73.6757 | 74.8534 | 75.6412 | 76.4128 | 77.3153 | 78.1512 | 78.963 | 79.0551 | 80.0028 | 79.2832 | 79.2832 | 79.2832 | 79.2832 | 79.2832 | 79.2832 | 79.2832 | 79.2832 | 79.2832 | 79.2832 | 79.2832 | 79.2832 | 79.2832 | 79.2832 | 79.2832 | 79.2832
98% | 0 | 50.1389 | 66.5626 | 71.033 | 66.9828 | 66.9781 | 67.4875 | 68.0466 | 69.1945 | 70.0193 | 70.4667 | 70.956 | 71.4039 | 72.2133 | 73.2178 | 73.1476 | 73.1476 | 73.1476 | 73.1476 | 73.1476 | 73.1476 | 73.1476 | 73.1476 | 73.1476 | 73.1476 | 73.1476 | 73.1476 | 73.1476 | 73.1476 | 73.1476 | 73.1476 | 98% | 2.269 | 55.8876 | 72.3443 | 76.6503 | 72.4718 | 72.49 | 72.9315 | 74.0973 | 74.8771 | 75.6409 | 76.5343 | 77.3618 | 78.1654 | 78.2566 | 79.1947 | 78.4824 | 78.4824 | 78.4824 | 78.4824 | 78.4824 | 78.4824 | 78.4824 | 78.4824 | 78.4824 | 78.4824 | 78.4824 | 78.4824 | 78.4824 | 78.4824 | 78.4824 | 78.4824
97% | 0.37816 | 49.6272 | 65.8834 | 70.3082 | 66.2994 | 66.2946 | 66.7989 | 67.3523 | 68.4884 | 69.3048 | 69.7477 | 70.232 | 70.6753 | 71.4764 | 72.4707 | 72.4012 | 72.4012 | 72.4012 | 72.4012 | 72.4012 | 72.4012 | 72.4012 | 72.4012 | 72.4012 | 72.4012 | 72.4012 | 72.4012 | 72.4012 | 72.4012 | 72.4012 | 72.4012 | 97% | 3.7816 | 55.3173 | 71.6061 | 75.8681 | 71.7323 | 71.7503 | 72.1873 | 73.3412 | 74.1131 | 74.8691 | 75.7534 | 76.5723 | 77.3678 | 77.458 | 78.3866 | 77.6815 | 77.6815 | 77.6815 | 77.6815 | 77.6815 | 77.6815 | 77.6815 | 77.6815 | 77.6815 | 77.6815 | 77.6815 | 77.6815 | 77.6815 | 77.6815 | 77.6815 | 77.6815
95% | 2.269 | 48.604 | 64.5249 | 68.8586 | 64.9324 | 64.9277 | 65.4216 | 65.9636 | 67.0763 | 67.8758 | 68.3096 | 68.7839 | 69.2181 | 70.0027 | 70.9765 | 70.9084 | 70.9084 | 70.9084 | 70.9084 | 70.9084 | 70.9084 | 70.9084 | 70.9084 | 70.9084 | 70.9084 | 70.9084 | 70.9084 | 70.9084 | 70.9084 | 70.9084 | 70.9084 | 95% | 6.0506 | 54.1768 | 70.1297 | 74.3038 | 70.2533 | 70.271 | 70.6989 | 71.829 | 72.585 | 73.3254 | 74.1914 | 74.9935 | 75.7726 | 75.861 | 76.7703 | 76.0799 | 76.0799 | 76.0799 | 76.0799 | 76.0799 | 76.0799 | 76.0799 | 76.0799 | 76.0799 | 76.0799 | 76.0799 | 76.0799 | 76.0799 | 76.0799 | 76.0799 | 76.0799
90% | 5.6725 | 46.0459 | 61.1289 | 65.2344 | 61.5149 | 61.5105 | 61.9784 | 62.4918 | 63.5459 | 64.3034 | 64.7143 | 65.1637 | 65.575 | 66.3183 | 67.2409 | 67.1764 | 67.1764 | 67.1764 | 67.1764 | 67.1764 | 67.1764 | 67.1764 | 67.1764 | 67.1764 | 67.1764 | 67.1764 | 67.1764 | 67.1764 | 67.1764 | 67.1764 | 67.1764 | 90% | 16.2611 | 51.3254 | 66.4386 | 70.3931 | 66.5557 | 66.5725 | 66.9779 | 68.0485 | 68.7647 | 69.4662 | 70.2866 | 71.0465 | 71.7846 | 71.8683 | 72.7298 | 72.0757 | 72.0757 | 72.0757 | 72.0757 | 72.0757 | 72.0757 | 72.0757 | 72.0757 | 72.0757 | 72.0757 | 72.0757 | 72.0757 | 72.0757 | 72.0757 | 72.0757 | 72.0757
85% | 15.8829 | 43.4878 | 57.7328 | 61.6103 | 58.0974 | 58.0932 | 58.5351 | 59.02 | 60.0156 | 60.731 | 61.1191 | 61.5435 | 61.932 | 62.634 | 63.5053 | 63.4444 | 63.4444 | 63.4444 | 63.4444 | 63.4444 | 63.4444 | 63.4444 | 63.4444 | 63.4444 | 63.4444 | 63.4444 | 63.4444 | 63.4444 | 63.4444 | 63.4444 | 63.4444 | 85% | 26.4715 | 48.4739 | 62.7476 | 66.4824 | 62.8582 | 62.874 | 63.2569 | 64.2681 | 64.9445 | 65.6069 | 66.3818 | 67.0995 | 67.7965 | 67.8756 | 68.6892 | 68.0715 | 68.0715 | 68.0715 | 68.0715 | 68.0715 | 68.0715 | 68.0715 | 68.0715 | 68.0715 | 68.0715 | 68.0715 | 68.0715 | 68.0715 | 68.0715 | 68.0715 | 68.0715
80% | 31.0095 | 40.9297 | 54.3368 | 57.9862 | 54.6799 | 54.676 | 55.0919 | 55.5483 | 56.4853 | 57.1586 | 57.5239 | 57.9233 | 58.2889 | 58.9496 | 59.7697 | 59.7123 | 59.7123 | 59.7123 | 59.7123 | 59.7123 | 59.7123 | 59.7123 | 59.7123 | 59.7123 | 59.7123 | 59.7123 | 59.7123 | 59.7123 | 59.7123 | 59.7123 | 59.7123 | 80% | 34.0348 | 45.6225 | 59.0566 | 62.5716 | 59.1606 | 59.1755 | 59.5359 | 60.4876 | 61.1242 | 61.7477 | 62.477 | 63.1524 | 63.8085 | 63.8829 | 64.6487 | 64.0672 | 64.0672 | 64.0672 | 64.0672 | 64.0672 | 64.0672 | 64.0672 | 64.0672 | 64.0672 | 64.0672 | 64.0672 | 64.0672 | 64.0672 | 64.0672 | 64.0672 | 64.0672
75% | 72.9857 | 38.3716 | 50.9407 | 54.362 | 51.2624 | 51.2587 | 51.6486 | 52.0765 | 52.955 | 53.5862 | 53.9286 | 54.3031 | 54.6458 | 55.2653 | 56.0341 | 55.9803 | 55.9803 | 55.9803 | 55.9803 | 55.9803 | 55.9803 | 55.9803 | 55.9803 | 55.9803 | 55.9803 | 55.9803 | 55.9803 | 55.9803 | 55.9803 | 55.9803 | 55.9803 | 75% | 48.405 | 42.7711 | 55.3655 | 58.6609 | 55.4631 | 55.4771 | 55.8149 | 56.7071 | 57.3039 | 57.8885 | 58.5722 | 59.2054 | 59.8205 | 59.8902 | 60.6082 | 60.063 | 60.063 | 60.063 | 60.063 | 60.063 | 60.063 | 60.063 | 60.063 | 60.063 | 60.063 | 60.063 | 60.063 | 60.063 | 60.063 | 60.063 | 60.063
70% | 150.5094 | 35.8135 | 47.5447 | 50.7379 | 47.8449 | 47.8415 | 48.2054 | 48.6047 | 49.4246 | 50.0138 | 50.3334 | 50.6829 | 51.0028 | 51.5809 | 52.2984 | 52.2483 | 52.2483 | 52.2483 | 52.2483 | 52.2483 | 52.2483 | 52.2483 | 52.2483 | 52.2483 | 52.2483 | 52.2483 | 52.2483 | 52.2483 | 52.2483 | 52.2483 | 52.2483 | 70% | 76.3892 | 39.9197 | 51.6745 | 54.7502 | 51.7656 | 51.7786 | 52.0939 | 52.9266 | 53.4837 | 54.0292 | 54.6674 | 55.2584 | 55.8324 | 55.8976 | 56.5676 | 56.0588 | 56.0588 | 56.0588 | 56.0588 | 56.0588 | 56.0588 | 56.0588 | 56.0588 | 56.0588 | 56.0588 | 56.0588 | 56.0588 | 56.0588 | 56.0588 | 56.0588 | 56.0588
65% | 359.6342 | 33.2554 | 44.1486 | 47.1138 | 44.4274 | 44.4242 | 44.7621 | 45.133 | 45.8943 | 46.4414 | 46.7381 | 47.0627 | 47.3597 | 47.8966 | 48.5628 | 48.5163 | 48.5163 | 48.5163 | 48.5163 | 48.5163 | 48.5163 | 48.5163 | 48.5163 | 48.5163 | 48.5163 | 48.5163 | 48.5163 | 48.5163 | 48.5163 | 48.5163 | 48.5163 | 65% | 114.2056 | 37.0683 | 47.9835 | 50.8395 | 48.068 | 48.0801 | 48.3729 | 49.1462 | 49.6634 | 50.17 | 50.7626 | 51.3114 | 51.8444 | 51.9049 | 52.5271 | 52.0546 | 52.0546 | 52.0546 | 52.0546 | 52.0546 | 52.0546 | 52.0546 | 52.0546 | 52.0546 | 52.0546 | 52.0546 | 52.0546 | 52.0546 | 52.0546 | 52.0546 | 52.0546
60% | 689.7717 | 30.6973 | 40.7526 | 43.4896 | 41.0099 | 41.007 | 41.3189 | 41.6612 | 42.364 | 42.869 | 43.1429 | 43.4424 | 43.7167 | 44.2122 | 44.8272 | 44.7843 | 44.7843 | 44.7843 | 44.7843 | 44.7843 | 44.7843 | 44.7843 | 44.7843 | 44.7843 | 44.7843 | 44.7843 | 44.7843 | 44.7843 | 44.7843 | 44.7843 | 44.7843 | 60% | 178.1154 | 34.2169 | 44.2924 | 46.9287 | 44.3705 | 44.3817 | 44.6519 | 45.3657 | 45.8431 | 46.3108 | 46.8577 | 47.3643 | 47.8564 | 47.9122 | 48.4865 | 48.0504 | 48.0504 | 48.0504 | 48.0504 | 48.0504 | 48.0504 | 48.0504 | 48.0504 | 48.0504 | 48.0504 | 48.0504 | 48.0504 | 48.0504 | 48.0504 | 48.0504 | 48.0504
55% | 1095.5419 | 28.1392 | 37.3565 | 39.8655 | 37.5924 | 37.5897 | 37.8757 | 38.1894 | 38.8336 | 39.2965 | 39.5476 | 39.8222 | 40.0736 | 40.5279 | 41.0916 | 41.0522 | 41.0522 | 41.0522 | 41.0522 | 41.0522 | 41.0522 | 41.0522 | 41.0522 | 41.0522 | 41.0522 | 41.0522 | 41.0522 | 41.0522 | 41.0522 | 41.0522 | 41.0522 | 55% | 311.6074 | 31.3655 | 40.6014 | 43.018 | 40.6729 | 40.6832 | 40.931 | 41.5852 | 42.0229 | 42.4515 | 42.9529 | 43.4173 | 43.8683 | 43.9195 | 44.446 | 44.0462 | 44.0462 | 44.0462 | 44.0462 | 44.0462 | 44.0462 | 44.0462 | 44.0462 | 44.0462 | 44.0462 | 44.0462 | 44.0462 | 44.0462 | 44.0462 | 44.0462 | 44.0462
50% | 1666.1918 | 25.581 | 33.9605 | 36.2413 | 34.1749 | 34.1725 | 34.4324 | 34.7177 | 35.3033 | 35.7241 | 35.9524 | 36.202 | 36.4306 | 36.8435 | 37.356 | 37.3202 | 37.3202 | 37.3202 | 37.3202 | 37.3202 | 37.3202 | 37.3202 | 37.3202 | 37.3202 | 37.3202 | 37.3202 | 37.3202 | 37.3202 | 37.3202 | 37.3202 | 37.3202 | 50% | 636.0723 | 28.5141 | 36.9103 | 39.1073 | 36.9754 | 36.9847 | 37.21 | 37.8047 | 38.2026 | 38.5923 | 39.0481 | 39.4703 | 39.8803 | 39.9268 | 40.4054 | 40.042 | 40.042 | 40.042 | 40.042 | 40.042 | 40.042 | 40.042 | 40.042 | 40.042 | 40.042 | 40.042 | 40.042 | 40.042 | 40.042 | 40.042 | 40.042
45% | 2506.0947 | 23.0229 | 30.5644 | 32.6172 | 30.7574 | 30.7552 | 30.9892 | 31.2459 | 31.773 | 32.1517 | 32.3572 | 32.5818 | 32.7875 | 33.1592 | 33.6204 | 33.5882 | 33.5882 | 33.5882 | 33.5882 | 33.5882 | 33.5882 | 33.5882 | 33.5882 | 33.5882 | 33.5882 | 33.5882 | 33.5882 | 33.5882 | 33.5882 | 33.5882 | 33.5882 | 45% | 1179.4944 | 25.6627 | 33.2193 | 35.1965 | 33.2779 | 33.2862 | 33.489 | 34.0243 | 34.3824 | 34.7331 | 35.1433 | 35.5233 | 35.8923 | 35.9341 | 36.3649 | 36.0378 | 36.0378 | 36.0378 | 36.0378 | 36.0378 | 36.0378 | 36.0378 | 36.0378 | 36.0378 | 36.0378 | 36.0378 | 36.0378 | 36.0378 | 36.0378 | 36.0378 | 36.0378
40% | 3164.4787 | 20.4648 | 27.1684 | 28.9931 | 27.3399 | 27.338 | 27.5459 | 27.7741 | 28.2426 | 28.5793 | 28.7619 | 28.9616 | 29.1444 | 29.4748 | 29.8848 | 29.8562 | 29.8562 | 29.8562 | 29.8562 | 29.8562 | 29.8562 | 29.8562 | 29.8562 | 29.8562 | 29.8562 | 29.8562 | 29.8562 | 29.8562 | 29.8562 | 29.8562 | 29.8562 | 40% | 1808.3816 | 22.8113 | 29.5283 | 31.2858 | 29.5803 | 29.5878 | 29.768 | 30.2438 | 30.5621 | 30.8738 | 31.2385 | 31.5762 | 31.9042 | 31.9415 | 32.3244 | 32.0336 | 32.0336 | 32.0336 | 32.0336 | 32.0336 | 32.0336 | 32.0336 | 32.0336 | 32.0336 | 32.0336 | 32.0336 | 32.0336 | 32.0336 | 32.0336 | 32.0336 | 32.0336
35% | 3551.3408 | 17.9067 | 23.7723 | 25.3689 | 23.9224 | 23.9207 | 24.1027 | 24.3024 | 24.7123 | 25.0069 | 25.1667 | 25.3414 | 25.5014 | 25.7905 | 26.1492 | 26.1241 | 26.1241 | 26.1241 | 26.1241 | 26.1241 | 26.1241 | 26.1241 | 26.1241 | 26.1241 | 26.1241 | 26.1241 | 26.1241 | 26.1241 | 26.1241 | 26.1241 | 26.1241 | 35% | 2779.1293 | 19.9599 | 25.8372 | 27.3751 | 25.8828 | 25.8893 | 26.047 | 26.4633 | 26.7418 | 27.0146 | 27.3337 | 27.6292 | 27.9162 | 27.9488 | 28.2838 | 28.0294 | 28.0294 | 28.0294 | 28.0294 | 28.0294 | 28.0294 | 28.0294 | 28.0294 | 28.0294 | 28.0294 | 28.0294 | 28.0294 | 28.0294 | 28.0294 | 28.0294 | 28.0294
30% | 3758.953 | 15.3486 | 20.3763 | 21.7448 | 20.505 | 20.5035 | 20.6595 | 20.8306 | 21.182 | 21.4345 | 21.5714 | 21.7212 | 21.8583 | 22.1061 | 22.4136 | 22.3921 | 22.3921 | 22.3921 | 22.3921 | 22.3921 | 22.3921 | 22.3921 | 22.3921 | 22.3921 | 22.3921 | 22.3921 | 22.3921 | 22.3921 | 22.3921 | 22.3921 | 22.3921 | 30% | 3814.165 | 17.1085 | 22.1462 | 23.4644 | 22.1852 | 22.1908 | 22.326 | 22.6828 | 22.9216 | 23.1554 | 23.4289 | 23.6822 | 23.9282 | 23.9561 | 24.2433 | 24.0252 | 24.0252 | 24.0252 | 24.0252 | 24.0252 | 24.0252 | 24.0252 | 24.0252 | 24.0252 | 24.0252 | 24.0252 | 24.0252 | 24.0252 | 24.0252 | 24.0252 | 24.0252
25% | 3926.4798 | 12.7905 | 16.9802 | 18.1207 | 17.0875 | 17.0862 | 17.2162 | 17.3588 | 17.6517 | 17.8621 | 17.9762 | 18.101 | 18.2153 | 18.4218 | 18.678 | 18.6601 | 18.6601 | 18.6601 | 18.6601 | 18.6601 | 18.6601 | 18.6601 | 18.6601 | 18.6601 | 18.6601 | 18.6601 | 18.6601 | 18.6601 | 18.6601 | 18.6601 | 18.6601 | 25% | 4166.9923 | 14.257 | 18.4552 | 19.5536 | 18.4877 | 18.4924 | 18.605 | 18.9024 | 19.1013 | 19.2962 | 19.5241 | 19.7351 | 19.9402 | 19.9634 | 20.2027 | 20.021 | 20.021 | 20.021 | 20.021 | 20.021 | 20.021 | 20.021 | 20.021 | 20.021 | 20.021 | 20.021 | 20.021 | 20.021 | 20.021 | 20.021 | 20.021
20% | 4050.5177 | 10.2324 | 13.5842 | 14.4965 | 13.67 | 13.669 | 13.773 | 13.8871 | 14.1213 | 14.2897 | 14.381 | 14.4808 | 14.5722 | 14.7374 | 14.9424 | 14.9281 | 14.9281 | 14.9281 | 14.9281 | 14.9281 | 14.9281 | 14.9281 | 14.9281 | 14.9281 | 14.9281 | 14.9281 | 14.9281 | 14.9281 | 14.9281 | 14.9281 | 14.9281 | 20% | 4282.7105 | 11.4056 | 14.7641 | 15.6429 | 14.7902 | 14.7939 | 14.884 | 15.1219 | 15.281 | 15.4369 | 15.6192 | 15.7881 | 15.9521 | 15.9707 | 16.1622 | 16.0168 | 16.0168 | 16.0168 | 16.0168 | 16.0168 | 16.0168 | 16.0168 | 16.0168 | 16.0168 | 16.0168 | 16.0168 | 16.0168 | 16.0168 | 16.0168 | 16.0168 | 16.0168
15% | 4152.622 | 7.6743 | 10.1881 | 10.8724 | 10.2525 | 10.2517 | 10.3297 | 10.4153 | 10.591 | 10.7172 | 10.7857 | 10.8606 | 10.9292 | 11.0531 | 11.2068 | 11.1961 | 11.1961 | 11.1961 | 11.1961 | 11.1961 | 11.1961 | 11.1961 | 11.1961 | 11.1961 | 11.1961 | 11.1961 | 11.1961 | 11.1961 | 11.1961 | 11.1961 | 11.1961 | 15% | 4364.7722 | 8.5542 | 11.0731 | 11.7322 | 11.0926 | 11.0954 | 11.163 | 11.3414 | 11.4608 | 11.5777 | 11.7144 | 11.8411 | 11.9641 | 11.978 | 12.1216 | 12.0126 | 12.0126 | 12.0126 | 12.0126 | 12.0126 | 12.0126 | 12.0126 | 12.0126 | 12.0126 | 12.0126 | 12.0126 | 12.0126 | 12.0126 | 12.0126 | 12.0126 | 12.0126
10% | 4248.2976 | 5.1162 | 6.7921 | 7.2483 | 6.835 | 6.8345 | 6.8865 | 6.9435 | 7.0607 | 7.1448 | 7.1905 | 7.2404 | 7.2861 | 7.3687 | 7.4712 | 7.464 | 7.464 | 7.464 | 7.464 | 7.464 | 7.464 | 7.464 | 7.464 | 7.464 | 7.464 | 7.464 | 7.464 | 7.464 | 7.464 | 7.464 | 7.464 | 10% | 4391.6218 | 5.7028 | 7.3821 | 7.8215 | 7.3951 | 7.3969 | 7.442 | 7.5609 | 7.6405 | 7.7185 | 7.8096 | 7.8941 | 7.9761 | 7.9854 | 8.0811 | 8.0084 | 8.0084 | 8.0084 | 8.0084 | 8.0084 | 8.0084 | 8.0084 | 8.0084 | 8.0084 | 8.0084 | 8.0084 | 8.0084 | 8.0084 | 8.0084 | 8.0084 | 8.0084
5% | 4361.7469 | 2.5581 | 3.396 | 3.6241 | 3.4175 | 3.4172 | 3.4432 | 3.4718 | 3.5303 | 3.5724 | 3.5952 | 3.6202 | 3.6431 | 3.6844 | 3.7356 | 3.732 | 3.732 | 3.732 | 3.732 | 3.732 | 3.732 | 3.732 | 3.732 | 3.732 | 3.732 | 3.732 | 3.732 | 3.732 | 3.732 | 3.732 | 3.732 | 5% | 4391.6218 | 2.8514 | 3.691 | 3.9107 | 3.6975 | 3.6985 | 3.721 | 3.7805 | 3.8203 | 3.8592 | 3.9048 | 3.947 | 3.988 | 3.9927 | 4.0405 | 4.0042 | 4.0042 | 4.0042 | 4.0042 | 4.0042 | 4.0042 | 4.0042 | 4.0042 | 4.0042 | 4.0042 | 4.0042 | 4.0042 | 4.0042 | 4.0042 | 4.0042 | 4.0042
9.992e-14% | 4391.6218 | 5.1121e-14 | 6.7867e-14 | 7.2425e-14 | 6.8295e-14 | 6.829e-14 | 6.881e-14 | 6.938e-14 | 7.055e-14 | 7.1391e-14 | 7.1847e-14 | 7.2346e-14 | 7.2803e-14 | 7.3628e-14 | 7.4652e-14 | 7.4581e-14 | 7.4581e-14 | 7.4581e-14 | 7.4581e-14 | 7.4581e-14 | 7.4581e-14 | 7.4581e-14 | 7.4581e-14 | 7.4581e-14 | 7.4581e-14 | 7.4581e-14 | 7.4581e-14 | 7.4581e-14 | 7.4581e-14 | 7.4581e-14 | 7.4581e-14 | 9.992e-14% | 4391.6218 | 5.6983e-14 | 7.3762e-14 | 7.8152e-14 | 7.3892e-14 | 7.391e-14 | 7.436e-14 | 7.5549e-14 | 7.6344e-14 | 7.7123e-14 | 7.8034e-14 | 7.8877e-14 | 7.9697e-14 | 7.979e-14 | 8.0746e-14 | 8.002e-14 | 8.002e-14 | 8.002e-14 | 8.002e-14 | 8.002e-14 | 8.002e-14 | 8.002e-14 | 8.002e-14 | 8.002e-14 | 8.002e-14 | 8.002e-14 | 8.002e-14 | 8.002e-14 | 8.002e-14 | 8.002e-14 | 8.002e-14
Option 5
Winter Season | [31 empty] | Winter Season
P50 | [31 empty] | P10
% of MD | Winter - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Winter - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 45.0311 | 62.4376 | 66.9594 | 45.9785 | 46.5767 | 47.6103 | 49.9646 | 51.5388 | 53.5349 | 54.5699 | 55.4791 | 53.7955 | 55.7638 | 58.8595 | 56.5064 | 56.5064 | 56.5064 | 56.5064 | 56.5064 | 56.5064 | 56.5064 | 56.5064 | 56.5064 | 56.5064 | 56.5064 | 56.5064 | 56.5064 | 56.5064 | 56.5064 | 56.5064 | 100% | 0 | 48.1978 | 65.3847 | 70.0831 | 49.0584 | 49.517 | 50.5281 | 52.9193 | 54.2227 | 56.7097 | 64.2743 | 58.0329 | 56.8105 | 58.4554 | 62.0553 | 59.6148 | 59.6148 | 59.6148 | 59.6148 | 59.6148 | 59.6148 | 59.6148 | 59.6148 | 59.6148 | 59.6148 | 59.6148 | 59.6148 | 59.6148 | 59.6148 | 59.6148 | 59.6148
99% | 1.486 | 44.5808 | 61.8132 | 66.2898 | 45.5187 | 46.111 | 47.1342 | 49.465 | 51.0234 | 52.9995 | 54.0242 | 54.9244 | 53.2576 | 55.2062 | 58.2709 | 55.9414 | 55.9414 | 55.9414 | 55.9414 | 55.9414 | 55.9414 | 55.9414 | 55.9414 | 55.9414 | 55.9414 | 55.9414 | 55.9414 | 55.9414 | 55.9414 | 55.9414 | 55.9414 | 99% | 1.486 | 47.7158 | 64.7309 | 69.3823 | 48.5678 | 49.0218 | 50.0228 | 52.3901 | 53.6804 | 56.1426 | 63.6316 | 57.4526 | 56.2424 | 57.8708 | 61.4347 | 59.0187 | 59.0187 | 59.0187 | 59.0187 | 59.0187 | 59.0187 | 59.0187 | 59.0187 | 59.0187 | 59.0187 | 59.0187 | 59.0187 | 59.0187 | 59.0187 | 59.0187 | 59.0187
98% | 3.2692 | 44.1305 | 61.1889 | 65.6202 | 45.0589 | 45.6452 | 46.6581 | 48.9654 | 50.508 | 52.4642 | 53.4785 | 54.3696 | 52.7196 | 54.6486 | 57.6823 | 55.3763 | 55.3763 | 55.3763 | 55.3763 | 55.3763 | 55.3763 | 55.3763 | 55.3763 | 55.3763 | 55.3763 | 55.3763 | 55.3763 | 55.3763 | 55.3763 | 55.3763 | 55.3763 | 98% | 3.2692 | 47.2338 | 64.0771 | 68.6815 | 48.0772 | 48.5266 | 49.5175 | 51.8609 | 53.1382 | 55.5755 | 62.9888 | 56.8723 | 55.6743 | 57.2863 | 60.8142 | 58.4225 | 58.4225 | 58.4225 | 58.4225 | 58.4225 | 58.4225 | 58.4225 | 58.4225 | 58.4225 | 58.4225 | 58.4225 | 58.4225 | 58.4225 | 58.4225 | 58.4225 | 58.4225
97% | 6.8356 | 43.6802 | 60.5645 | 64.9506 | 44.5991 | 45.1794 | 46.182 | 48.4657 | 49.9926 | 51.9288 | 52.9328 | 53.8148 | 52.1817 | 54.0909 | 57.0937 | 54.8112 | 54.8112 | 54.8112 | 54.8112 | 54.8112 | 54.8112 | 54.8112 | 54.8112 | 54.8112 | 54.8112 | 54.8112 | 54.8112 | 54.8112 | 54.8112 | 54.8112 | 54.8112 | 97% | 6.8356 | 46.7518 | 63.4232 | 67.9806 | 47.5866 | 48.0315 | 49.0122 | 51.3317 | 52.596 | 55.0084 | 62.3461 | 56.2919 | 55.1062 | 56.7017 | 60.1936 | 57.8264 | 57.8264 | 57.8264 | 57.8264 | 57.8264 | 57.8264 | 57.8264 | 57.8264 | 57.8264 | 57.8264 | 57.8264 | 57.8264 | 57.8264 | 57.8264 | 57.8264 | 57.8264
95% | 17.5347 | 42.7796 | 59.3157 | 63.6114 | 43.6795 | 44.2479 | 45.2298 | 47.4664 | 48.9618 | 50.8582 | 51.8414 | 52.7052 | 51.1058 | 52.9757 | 55.9165 | 53.6811 | 53.6811 | 53.6811 | 53.6811 | 53.6811 | 53.6811 | 53.6811 | 53.6811 | 53.6811 | 53.6811 | 53.6811 | 53.6811 | 53.6811 | 53.6811 | 53.6811 | 53.6811 | 95% | 17.5347 | 45.7879 | 62.1155 | 66.579 | 46.6055 | 47.0411 | 48.0017 | 50.2733 | 51.5115 | 53.8743 | 61.0606 | 55.1313 | 53.97 | 55.5326 | 58.9525 | 56.6341 | 56.6341 | 56.6341 | 56.6341 | 56.6341 | 56.6341 | 56.6341 | 56.6341 | 56.6341 | 56.6341 | 56.6341 | 56.6341 | 56.6341 | 56.6341 | 56.6341 | 56.6341
90% | 78.7576 | 40.528 | 56.1939 | 60.2634 | 41.3806 | 41.9191 | 42.8493 | 44.9682 | 46.3849 | 48.1814 | 49.1129 | 49.9312 | 48.416 | 50.1875 | 52.9736 | 50.8558 | 50.8558 | 50.8558 | 50.8558 | 50.8558 | 50.8558 | 50.8558 | 50.8558 | 50.8558 | 50.8558 | 50.8558 | 50.8558 | 50.8558 | 50.8558 | 50.8558 | 50.8558 | 90% | 78.7576 | 43.378 | 58.8463 | 63.0748 | 44.1525 | 44.5653 | 45.4753 | 47.6273 | 48.8004 | 51.0388 | 57.8469 | 52.2296 | 51.1295 | 52.6098 | 55.8497 | 53.6533 | 53.6533 | 53.6533 | 53.6533 | 53.6533 | 53.6533 | 53.6533 | 53.6533 | 53.6533 | 53.6533 | 53.6533 | 53.6533 | 53.6533 | 53.6533 | 53.6533 | 53.6533
85% | 236.8672 | 38.2764 | 53.072 | 56.9155 | 39.0817 | 39.5902 | 40.4688 | 42.47 | 43.8079 | 45.5047 | 46.3844 | 47.1573 | 45.7262 | 47.3993 | 50.0306 | 48.0305 | 48.0305 | 48.0305 | 48.0305 | 48.0305 | 48.0305 | 48.0305 | 48.0305 | 48.0305 | 48.0305 | 48.0305 | 48.0305 | 48.0305 | 48.0305 | 48.0305 | 48.0305 | 85% | 236.8672 | 40.9681 | 55.577 | 59.5707 | 41.6996 | 42.0894 | 42.9489 | 44.9814 | 46.0893 | 48.2033 | 54.6332 | 49.328 | 48.289 | 49.6871 | 52.747 | 50.6726 | 50.6726 | 50.6726 | 50.6726 | 50.6726 | 50.6726 | 50.6726 | 50.6726 | 50.6726 | 50.6726 | 50.6726 | 50.6726 | 50.6726 | 50.6726 | 50.6726 | 50.6726
80% | 497.5104 | 36.0249 | 49.9501 | 53.5675 | 36.7828 | 37.2614 | 38.0882 | 39.9717 | 41.231 | 42.8279 | 43.656 | 44.3833 | 43.0364 | 44.6111 | 47.0876 | 45.2051 | 45.2051 | 45.2051 | 45.2051 | 45.2051 | 45.2051 | 45.2051 | 45.2051 | 45.2051 | 45.2051 | 45.2051 | 45.2051 | 45.2051 | 45.2051 | 45.2051 | 45.2051 | 80% | 497.5104 | 38.5582 | 52.3078 | 56.0665 | 39.2467 | 39.6136 | 40.4225 | 42.3354 | 43.3781 | 45.3678 | 51.4195 | 46.4263 | 45.4484 | 46.7643 | 49.6442 | 47.6919 | 47.6919 | 47.6919 | 47.6919 | 47.6919 | 47.6919 | 47.6919 | 47.6919 | 47.6919 | 47.6919 | 47.6919 | 47.6919 | 47.6919 | 47.6919 | 47.6919 | 47.6919
75% | 803.6248 | 33.7733 | 46.8282 | 50.2195 | 34.4839 | 34.9325 | 35.7077 | 37.4735 | 38.6541 | 40.1512 | 40.9275 | 41.6094 | 40.3467 | 41.8229 | 44.1446 | 42.3798 | 42.3798 | 42.3798 | 42.3798 | 42.3798 | 42.3798 | 42.3798 | 42.3798 | 42.3798 | 42.3798 | 42.3798 | 42.3798 | 42.3798 | 42.3798 | 42.3798 | 42.3798 | 75% | 803.6248 | 36.1483 | 49.0386 | 52.5623 | 36.7938 | 37.1377 | 37.8961 | 39.6894 | 40.667 | 42.5323 | 48.2057 | 43.5247 | 42.6079 | 43.8415 | 46.5414 | 44.7111 | 44.7111 | 44.7111 | 44.7111 | 44.7111 | 44.7111 | 44.7111 | 44.7111 | 44.7111 | 44.7111 | 44.7111 | 44.7111 | 44.7111 | 44.7111 | 44.7111 | 44.7111
70% | 1155.2107 | 31.5218 | 43.7063 | 46.8715 | 32.1849 | 32.6037 | 33.3272 | 34.9753 | 36.0771 | 37.4744 | 38.199 | 38.8354 | 37.6569 | 39.0347 | 41.2017 | 39.5545 | 39.5545 | 39.5545 | 39.5545 | 39.5545 | 39.5545 | 39.5545 | 39.5545 | 39.5545 | 39.5545 | 39.5545 | 39.5545 | 39.5545 | 39.5545 | 39.5545 | 39.5545 | 70% | 1155.2107 | 33.7384 | 45.7693 | 49.0582 | 34.3409 | 34.6619 | 35.3697 | 37.0435 | 37.9559 | 39.6968 | 44.992 | 40.6231 | 39.7674 | 40.9188 | 43.4387 | 41.7304 | 41.7304 | 41.7304 | 41.7304 | 41.7304 | 41.7304 | 41.7304 | 41.7304 | 41.7304 | 41.7304 | 41.7304 | 41.7304 | 41.7304 | 41.7304 | 41.7304 | 41.7304
65% | 1553.1596 | 29.2702 | 40.5844 | 43.5236 | 29.886 | 30.2749 | 30.9467 | 32.477 | 33.5002 | 34.7977 | 35.4705 | 36.0614 | 34.9671 | 36.2465 | 38.2587 | 36.7292 | 36.7292 | 36.7292 | 36.7292 | 36.7292 | 36.7292 | 36.7292 | 36.7292 | 36.7292 | 36.7292 | 36.7292 | 36.7292 | 36.7292 | 36.7292 | 36.7292 | 36.7292 | 65% | 1553.1596 | 31.3286 | 42.5001 | 45.554 | 31.8879 | 32.186 | 32.8433 | 34.3975 | 35.2447 | 36.8613 | 41.7783 | 37.7214 | 36.9268 | 37.996 | 40.3359 | 38.7496 | 38.7496 | 38.7496 | 38.7496 | 38.7496 | 38.7496 | 38.7496 | 38.7496 | 38.7496 | 38.7496 | 38.7496 | 38.7496 | 38.7496 | 38.7496 | 38.7496 | 38.7496
60% | 2026.2996 | 27.0187 | 37.4626 | 40.1756 | 27.5871 | 27.946 | 28.5662 | 29.9788 | 30.9233 | 32.1209 | 32.742 | 33.2875 | 32.2773 | 33.4583 | 35.3157 | 33.9039 | 33.9039 | 33.9039 | 33.9039 | 33.9039 | 33.9039 | 33.9039 | 33.9039 | 33.9039 | 33.9039 | 33.9039 | 33.9039 | 33.9039 | 33.9039 | 33.9039 | 33.9039 | 60% | 2026.2996 | 28.9187 | 39.2308 | 42.0499 | 29.435 | 29.7102 | 30.3169 | 31.7516 | 32.5336 | 34.0258 | 38.5646 | 34.8198 | 34.0863 | 35.0732 | 37.2332 | 35.7689 | 35.7689 | 35.7689 | 35.7689 | 35.7689 | 35.7689 | 35.7689 | 35.7689 | 35.7689 | 35.7689 | 35.7689 | 35.7689 | 35.7689 | 35.7689 | 35.7689 | 35.7689
55% | 2598.4068 | 24.7671 | 34.3407 | 36.8276 | 25.2882 | 25.6172 | 26.1857 | 27.4806 | 28.3463 | 29.4442 | 30.0135 | 30.5135 | 29.5875 | 30.6701 | 32.3727 | 31.0785 | 31.0785 | 31.0785 | 31.0785 | 31.0785 | 31.0785 | 31.0785 | 31.0785 | 31.0785 | 31.0785 | 31.0785 | 31.0785 | 31.0785 | 31.0785 | 31.0785 | 31.0785 | 55% | 2598.4068 | 26.5088 | 35.9616 | 38.5457 | 26.9821 | 27.2343 | 27.7905 | 29.1056 | 29.8225 | 31.1904 | 35.3509 | 31.9181 | 31.2458 | 32.1505 | 34.1304 | 32.7882 | 32.7882 | 32.7882 | 32.7882 | 32.7882 | 32.7882 | 32.7882 | 32.7882 | 32.7882 | 32.7882 | 32.7882 | 32.7882 | 32.7882 | 32.7882 | 32.7882 | 32.7882
50% | 3233.5201 | 22.5156 | 31.2188 | 33.4797 | 22.9892 | 23.2884 | 23.8052 | 24.9823 | 25.7694 | 26.7674 | 27.285 | 27.7396 | 26.8978 | 27.8819 | 29.4298 | 28.2532 | 28.2532 | 28.2532 | 28.2532 | 28.2532 | 28.2532 | 28.2532 | 28.2532 | 28.2532 | 28.2532 | 28.2532 | 28.2532 | 28.2532 | 28.2532 | 28.2532 | 28.2532 | 50% | 3233.5201 | 24.0989 | 32.6924 | 35.0416 | 24.5292 | 24.7585 | 25.264 | 26.4596 | 27.1113 | 28.3549 | 32.1372 | 29.0165 | 28.4053 | 29.2277 | 31.0276 | 29.8074 | 29.8074 | 29.8074 | 29.8074 | 29.8074 | 29.8074 | 29.8074 | 29.8074 | 29.8074 | 29.8074 | 29.8074 | 29.8074 | 29.8074 | 29.8074 | 29.8074 | 29.8074
45% | 3775.313 | 20.264 | 28.0969 | 30.1317 | 20.6903 | 20.9595 | 21.4246 | 22.4841 | 23.1924 | 24.0907 | 24.5565 | 24.9656 | 24.208 | 25.0937 | 26.4868 | 25.4279 | 25.4279 | 25.4279 | 25.4279 | 25.4279 | 25.4279 | 25.4279 | 25.4279 | 25.4279 | 25.4279 | 25.4279 | 25.4279 | 25.4279 | 25.4279 | 25.4279 | 25.4279 | 45% | 3775.313 | 21.689 | 29.4231 | 31.5374 | 22.0763 | 22.2826 | 22.7376 | 23.8137 | 24.4002 | 25.5194 | 28.9234 | 26.1148 | 25.5647 | 26.3049 | 27.9249 | 26.8267 | 26.8267 | 26.8267 | 26.8267 | 26.8267 | 26.8267 | 26.8267 | 26.8267 | 26.8267 | 26.8267 | 26.8267 | 26.8267 | 26.8267 | 26.8267 | 26.8267 | 26.8267
40% | 4072.8088 | 18.0124 | 24.975 | 26.7837 | 18.3914 | 18.6307 | 19.0441 | 19.9859 | 20.6155 | 21.414 | 21.828 | 22.1917 | 21.5182 | 22.3055 | 23.5438 | 22.6026 | 22.6026 | 22.6026 | 22.6026 | 22.6026 | 22.6026 | 22.6026 | 22.6026 | 22.6026 | 22.6026 | 22.6026 | 22.6026 | 22.6026 | 22.6026 | 22.6026 | 22.6026 | 40% | 4072.8088 | 19.2791 | 26.1539 | 28.0332 | 19.6234 | 19.8068 | 20.2112 | 21.1677 | 21.6891 | 22.6839 | 25.7097 | 23.2132 | 22.7242 | 23.3822 | 24.8221 | 23.8459 | 23.8459 | 23.8459 | 23.8459 | 23.8459 | 23.8459 | 23.8459 | 23.8459 | 23.8459 | 23.8459 | 23.8459 | 23.8459 | 23.8459 | 23.8459 | 23.8459 | 23.8459
35% | 4198.821 | 15.7609 | 21.8532 | 23.4358 | 16.0925 | 16.3019 | 16.6636 | 17.4876 | 18.0386 | 18.7372 | 19.0995 | 19.4177 | 18.8284 | 19.5173 | 20.6008 | 19.7772 | 19.7772 | 19.7772 | 19.7772 | 19.7772 | 19.7772 | 19.7772 | 19.7772 | 19.7772 | 19.7772 | 19.7772 | 19.7772 | 19.7772 | 19.7772 | 19.7772 | 19.7772 | 35% | 4198.821 | 16.8692 | 22.8847 | 24.5291 | 17.1704 | 17.3309 | 17.6848 | 18.5217 | 18.9779 | 19.8484 | 22.496 | 20.3115 | 19.8837 | 20.4594 | 21.7193 | 20.8652 | 20.8652 | 20.8652 | 20.8652 | 20.8652 | 20.8652 | 20.8652 | 20.8652 | 20.8652 | 20.8652 | 20.8652 | 20.8652 | 20.8652 | 20.8652 | 20.8652 | 20.8652
30% | 4271.3374 | 13.5093 | 18.7313 | 20.0878 | 13.7935 | 13.973 | 14.2831 | 14.9894 | 15.4616 | 16.0605 | 16.371 | 16.6437 | 16.1387 | 16.7292 | 17.6579 | 16.9519 | 16.9519 | 16.9519 | 16.9519 | 16.9519 | 16.9519 | 16.9519 | 16.9519 | 16.9519 | 16.9519 | 16.9519 | 16.9519 | 16.9519 | 16.9519 | 16.9519 | 16.9519 | 30% | 4271.3374 | 14.4593 | 19.6154 | 21.0249 | 14.7175 | 14.8551 | 15.1584 | 15.8758 | 16.2668 | 17.0129 | 19.2823 | 17.4099 | 17.0432 | 17.5366 | 18.6166 | 17.8844 | 17.8844 | 17.8844 | 17.8844 | 17.8844 | 17.8844 | 17.8844 | 17.8844 | 17.8844 | 17.8844 | 17.8844 | 17.8844 | 17.8844 | 17.8844 | 17.8844 | 17.8844
25% | 4321.8611 | 11.2578 | 15.6094 | 16.7398 | 11.4946 | 11.6442 | 11.9026 | 12.4912 | 12.8847 | 13.3837 | 13.6425 | 13.8698 | 13.4489 | 13.941 | 14.7149 | 14.1266 | 14.1266 | 14.1266 | 14.1266 | 14.1266 | 14.1266 | 14.1266 | 14.1266 | 14.1266 | 14.1266 | 14.1266 | 14.1266 | 14.1266 | 14.1266 | 14.1266 | 14.1266 | 25% | 4321.8611 | 12.0494 | 16.3462 | 17.5208 | 12.2646 | 12.3792 | 12.632 | 13.2298 | 13.5557 | 14.1774 | 16.0686 | 14.5082 | 14.2026 | 14.6138 | 15.5138 | 14.9037 | 14.9037 | 14.9037 | 14.9037 | 14.9037 | 14.9037 | 14.9037 | 14.9037 | 14.9037 | 14.9037 | 14.9037 | 14.9037 | 14.9037 | 14.9037 | 14.9037 | 14.9037
20% | 4353.067 | 9.0062 | 12.4875 | 13.3919 | 9.1957 | 9.3153 | 9.5221 | 9.9929 | 10.3078 | 10.707 | 10.914 | 11.0958 | 10.7591 | 11.1528 | 11.7719 | 11.3013 | 11.3013 | 11.3013 | 11.3013 | 11.3013 | 11.3013 | 11.3013 | 11.3013 | 11.3013 | 11.3013 | 11.3013 | 11.3013 | 11.3013 | 11.3013 | 11.3013 | 11.3013 | 20% | 4353.067 | 9.6396 | 13.0769 | 14.0166 | 9.8117 | 9.9034 | 10.1056 | 10.5839 | 10.8445 | 11.3419 | 12.8549 | 11.6066 | 11.3621 | 11.6911 | 12.4111 | 11.923 | 11.923 | 11.923 | 11.923 | 11.923 | 11.923 | 11.923 | 11.923 | 11.923 | 11.923 | 11.923 | 11.923 | 11.923 | 11.923 | 11.923 | 11.923
15% | 4369.4129 | 6.7547 | 9.3656 | 10.0439 | 6.8968 | 6.9865 | 7.1415 | 7.4947 | 7.7308 | 8.0302 | 8.1855 | 8.3219 | 8.0693 | 8.3646 | 8.8289 | 8.476 | 8.476 | 8.476 | 8.476 | 8.476 | 8.476 | 8.476 | 8.476 | 8.476 | 8.476 | 8.476 | 8.476 | 8.476 | 8.476 | 8.476 | 8.476 | 15% | 4369.4129 | 7.2297 | 9.8077 | 10.5125 | 7.3588 | 7.4275 | 7.5792 | 7.9379 | 8.1334 | 8.5065 | 9.6411 | 8.7049 | 8.5216 | 8.7683 | 9.3083 | 8.9422 | 8.9422 | 8.9422 | 8.9422 | 8.9422 | 8.9422 | 8.9422 | 8.9422 | 8.9422 | 8.9422 | 8.9422 | 8.9422 | 8.9422 | 8.9422 | 8.9422 | 8.9422
10% | 4378.6261 | 4.5031 | 6.2438 | 6.6959 | 4.5978 | 4.6577 | 4.761 | 4.9965 | 5.1539 | 5.3535 | 5.457 | 5.5479 | 5.3796 | 5.5764 | 5.886 | 5.6506 | 5.6506 | 5.6506 | 5.6506 | 5.6506 | 5.6506 | 5.6506 | 5.6506 | 5.6506 | 5.6506 | 5.6506 | 5.6506 | 5.6506 | 5.6506 | 5.6506 | 5.6506 | 10% | 4378.6261 | 4.8198 | 6.5385 | 7.0083 | 4.9058 | 4.9517 | 5.0528 | 5.2919 | 5.4223 | 5.671 | 6.4274 | 5.8033 | 5.6811 | 5.8455 | 6.2055 | 5.9615 | 5.9615 | 5.9615 | 5.9615 | 5.9615 | 5.9615 | 5.9615 | 5.9615 | 5.9615 | 5.9615 | 5.9615 | 5.9615 | 5.9615 | 5.9615 | 5.9615 | 5.9615
5% | 4391.7028 | 2.2516 | 3.1219 | 3.348 | 2.2989 | 2.3288 | 2.3805 | 2.4982 | 2.5769 | 2.6767 | 2.7285 | 2.774 | 2.6898 | 2.7882 | 2.943 | 2.8253 | 2.8253 | 2.8253 | 2.8253 | 2.8253 | 2.8253 | 2.8253 | 2.8253 | 2.8253 | 2.8253 | 2.8253 | 2.8253 | 2.8253 | 2.8253 | 2.8253 | 2.8253 | 5% | 4391.7028 | 2.4099 | 3.2692 | 3.5042 | 2.4529 | 2.4758 | 2.5264 | 2.646 | 2.7111 | 2.8355 | 3.2137 | 2.9016 | 2.8405 | 2.9228 | 3.1028 | 2.9807 | 2.9807 | 2.9807 | 2.9807 | 2.9807 | 2.9807 | 2.9807 | 2.9807 | 2.9807 | 2.9807 | 2.9807 | 2.9807 | 2.9807 | 2.9807 | 2.9807 | 2.9807
9.992e-14% | 4391.7028 | 4.4995e-14 | 6.2388e-14 | 6.6906e-14 | 4.5942e-14 | 4.6539e-14 | 4.7572e-14 | 4.9925e-14 | 5.1498e-14 | 5.3492e-14 | 5.4526e-14 | 5.5435e-14 | 5.3753e-14 | 5.5719e-14 | 5.8812e-14 | 5.6461e-14 | 5.6461e-14 | 5.6461e-14 | 5.6461e-14 | 5.6461e-14 | 5.6461e-14 | 5.6461e-14 | 5.6461e-14 | 5.6461e-14 | 5.6461e-14 | 5.6461e-14 | 5.6461e-14 | 5.6461e-14 | 5.6461e-14 | 5.6461e-14 | 5.6461e-14 | 9.992e-14% | 4391.7028 | 4.8159e-14 | 6.5332e-14 | 7.0027e-14 | 4.9019e-14 | 4.9477e-14 | 5.0488e-14 | 5.2877e-14 | 5.4179e-14 | 5.6664e-14 | 6.4223e-14 | 5.7987e-14 | 5.6765e-14 | 5.8409e-14 | 6.2006e-14 | 5.9567e-14 | 5.9567e-14 | 5.9567e-14 | 5.9567e-14 | 5.9567e-14 | 5.9567e-14 | 5.9567e-14 | 5.9567e-14 | 5.9567e-14 | 5.9567e-14 | 5.9567e-14 | 5.9567e-14 | 5.9567e-14 | 5.9567e-14 | 5.9567e-14 | 5.9567e-14
Summer Season | [31 empty] | Summer Season
P50 | [31 empty] | P10
% of MD | Summer - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Summer - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 51.1621 | 67.921 | 72.4827 | 50.5998 | 50.595 | 51.1148 | 51.6853 | 52.8566 | 53.6983 | 54.1548 | 54.6541 | 55.1111 | 55.937 | 56.9621 | 56.8904 | 56.8904 | 56.8904 | 56.8904 | 56.8904 | 56.8904 | 56.8904 | 56.8904 | 56.8904 | 56.8904 | 56.8904 | 56.8904 | 56.8904 | 56.8904 | 56.8904 | 56.8904 | 100% | 0 | 57.0282 | 73.8207 | 78.2145 | 56.2008 | 56.2194 | 56.6699 | 57.8595 | 58.6552 | 59.4346 | 60.3462 | 61.1906 | 62.0106 | 62.1037 | 63.0609 | 62.3341 | 62.3341 | 62.3341 | 62.3341 | 62.3341 | 62.3341 | 62.3341 | 62.3341 | 62.3341 | 62.3341 | 62.3341 | 62.3341 | 62.3341 | 62.3341 | 62.3341 | 62.3341
99% | 0 | 50.6505 | 67.2418 | 71.7579 | 50.0938 | 50.089 | 50.6037 | 51.1685 | 52.328 | 53.1613 | 53.6133 | 54.1075 | 54.56 | 55.3776 | 56.3924 | 56.3215 | 56.3215 | 56.3215 | 56.3215 | 56.3215 | 56.3215 | 56.3215 | 56.3215 | 56.3215 | 56.3215 | 56.3215 | 56.3215 | 56.3215 | 56.3215 | 56.3215 | 56.3215 | 99% | 1.5127 | 56.4579 | 73.0825 | 77.4324 | 55.6388 | 55.6572 | 56.1032 | 57.2809 | 58.0687 | 58.8403 | 59.7428 | 60.5787 | 61.3905 | 61.4826 | 62.4303 | 61.7107 | 61.7107 | 61.7107 | 61.7107 | 61.7107 | 61.7107 | 61.7107 | 61.7107 | 61.7107 | 61.7107 | 61.7107 | 61.7107 | 61.7107 | 61.7107 | 61.7107 | 61.7107
98% | 0 | 50.1389 | 66.5626 | 71.033 | 49.5878 | 49.5831 | 50.0925 | 50.6516 | 51.7995 | 52.6243 | 53.0717 | 53.561 | 54.0089 | 54.8183 | 55.8228 | 55.7526 | 55.7526 | 55.7526 | 55.7526 | 55.7526 | 55.7526 | 55.7526 | 55.7526 | 55.7526 | 55.7526 | 55.7526 | 55.7526 | 55.7526 | 55.7526 | 55.7526 | 55.7526 | 98% | 2.269 | 55.8876 | 72.3443 | 76.6503 | 55.0768 | 55.095 | 55.5365 | 56.7023 | 57.4821 | 58.2459 | 59.1393 | 59.9668 | 60.7704 | 60.8616 | 61.7997 | 61.0874 | 61.0874 | 61.0874 | 61.0874 | 61.0874 | 61.0874 | 61.0874 | 61.0874 | 61.0874 | 61.0874 | 61.0874 | 61.0874 | 61.0874 | 61.0874 | 61.0874 | 61.0874
97% | 0.37816 | 49.6272 | 65.8834 | 70.3082 | 49.0819 | 49.0771 | 49.5814 | 50.1348 | 51.2709 | 52.0873 | 52.5302 | 53.0145 | 53.4578 | 54.2589 | 55.2532 | 55.1837 | 55.1837 | 55.1837 | 55.1837 | 55.1837 | 55.1837 | 55.1837 | 55.1837 | 55.1837 | 55.1837 | 55.1837 | 55.1837 | 55.1837 | 55.1837 | 55.1837 | 55.1837 | 97% | 3.7816 | 55.3173 | 71.6061 | 75.8681 | 54.5148 | 54.5328 | 54.9698 | 56.1237 | 56.8956 | 57.6516 | 58.5359 | 59.3548 | 60.1503 | 60.2405 | 61.1691 | 60.464 | 60.464 | 60.464 | 60.464 | 60.464 | 60.464 | 60.464 | 60.464 | 60.464 | 60.464 | 60.464 | 60.464 | 60.464 | 60.464 | 60.464 | 60.464
95% | 2.269 | 48.604 | 64.5249 | 68.8586 | 48.0699 | 48.0652 | 48.5591 | 49.1011 | 50.2138 | 51.0133 | 51.4471 | 51.9214 | 52.3556 | 53.1402 | 54.114 | 54.0459 | 54.0459 | 54.0459 | 54.0459 | 54.0459 | 54.0459 | 54.0459 | 54.0459 | 54.0459 | 54.0459 | 54.0459 | 54.0459 | 54.0459 | 54.0459 | 54.0459 | 54.0459 | 95% | 6.0506 | 54.1768 | 70.1297 | 74.3038 | 53.3908 | 53.4085 | 53.8364 | 54.9665 | 55.7225 | 56.4629 | 57.3289 | 58.131 | 58.9101 | 58.9985 | 59.9078 | 59.2174 | 59.2174 | 59.2174 | 59.2174 | 59.2174 | 59.2174 | 59.2174 | 59.2174 | 59.2174 | 59.2174 | 59.2174 | 59.2174 | 59.2174 | 59.2174 | 59.2174 | 59.2174
90% | 5.6725 | 46.0459 | 61.1289 | 65.2344 | 45.5399 | 45.5355 | 46.0034 | 46.5168 | 47.5709 | 48.3284 | 48.7393 | 49.1887 | 49.6 | 50.3433 | 51.2659 | 51.2014 | 51.2014 | 51.2014 | 51.2014 | 51.2014 | 51.2014 | 51.2014 | 51.2014 | 51.2014 | 51.2014 | 51.2014 | 51.2014 | 51.2014 | 51.2014 | 51.2014 | 51.2014 | 90% | 16.2611 | 51.3254 | 66.4386 | 70.3931 | 50.5807 | 50.5975 | 51.0029 | 52.0735 | 52.7897 | 53.4912 | 54.3116 | 55.0715 | 55.8096 | 55.8933 | 56.7548 | 56.1007 | 56.1007 | 56.1007 | 56.1007 | 56.1007 | 56.1007 | 56.1007 | 56.1007 | 56.1007 | 56.1007 | 56.1007 | 56.1007 | 56.1007 | 56.1007 | 56.1007 | 56.1007
85% | 15.8829 | 43.4878 | 57.7328 | 61.6103 | 43.0099 | 43.0057 | 43.4476 | 43.9325 | 44.9281 | 45.6435 | 46.0316 | 46.456 | 46.8445 | 47.5465 | 48.4178 | 48.3569 | 48.3569 | 48.3569 | 48.3569 | 48.3569 | 48.3569 | 48.3569 | 48.3569 | 48.3569 | 48.3569 | 48.3569 | 48.3569 | 48.3569 | 48.3569 | 48.3569 | 48.3569 | 85% | 26.4715 | 48.4739 | 62.7476 | 66.4824 | 47.7707 | 47.7865 | 48.1694 | 49.1806 | 49.857 | 50.5194 | 51.2943 | 52.012 | 52.709 | 52.7881 | 53.6017 | 52.984 | 52.984 | 52.984 | 52.984 | 52.984 | 52.984 | 52.984 | 52.984 | 52.984 | 52.984 | 52.984 | 52.984 | 52.984 | 52.984 | 52.984 | 52.984
80% | 31.0095 | 40.9297 | 54.3368 | 57.9862 | 40.4799 | 40.476 | 40.8919 | 41.3483 | 42.2853 | 42.9586 | 43.3239 | 43.7233 | 44.0889 | 44.7496 | 45.5697 | 45.5123 | 45.5123 | 45.5123 | 45.5123 | 45.5123 | 45.5123 | 45.5123 | 45.5123 | 45.5123 | 45.5123 | 45.5123 | 45.5123 | 45.5123 | 45.5123 | 45.5123 | 45.5123 | 80% | 34.0348 | 45.6225 | 59.0566 | 62.5716 | 44.9606 | 44.9755 | 45.3359 | 46.2876 | 46.9242 | 47.5477 | 48.277 | 48.9524 | 49.6085 | 49.6829 | 50.4487 | 49.8672 | 49.8672 | 49.8672 | 49.8672 | 49.8672 | 49.8672 | 49.8672 | 49.8672 | 49.8672 | 49.8672 | 49.8672 | 49.8672 | 49.8672 | 49.8672 | 49.8672 | 49.8672
75% | 72.9857 | 38.3716 | 50.9407 | 54.362 | 37.9499 | 37.9462 | 38.3361 | 38.764 | 39.6425 | 40.2737 | 40.6161 | 40.9906 | 41.3333 | 41.9528 | 42.7216 | 42.6678 | 42.6678 | 42.6678 | 42.6678 | 42.6678 | 42.6678 | 42.6678 | 42.6678 | 42.6678 | 42.6678 | 42.6678 | 42.6678 | 42.6678 | 42.6678 | 42.6678 | 42.6678 | 75% | 48.405 | 42.7711 | 55.3655 | 58.6609 | 42.1506 | 42.1646 | 42.5024 | 43.3946 | 43.9914 | 44.576 | 45.2597 | 45.8929 | 46.508 | 46.5777 | 47.2957 | 46.7505 | 46.7505 | 46.7505 | 46.7505 | 46.7505 | 46.7505 | 46.7505 | 46.7505 | 46.7505 | 46.7505 | 46.7505 | 46.7505 | 46.7505 | 46.7505 | 46.7505 | 46.7505
70% | 150.5094 | 35.8135 | 47.5447 | 50.7379 | 35.4199 | 35.4165 | 35.7804 | 36.1797 | 36.9996 | 37.5888 | 37.9084 | 38.2579 | 38.5778 | 39.1559 | 39.8734 | 39.8233 | 39.8233 | 39.8233 | 39.8233 | 39.8233 | 39.8233 | 39.8233 | 39.8233 | 39.8233 | 39.8233 | 39.8233 | 39.8233 | 39.8233 | 39.8233 | 39.8233 | 39.8233 | 70% | 76.3892 | 39.9197 | 51.6745 | 54.7502 | 39.3406 | 39.3536 | 39.6689 | 40.5016 | 41.0587 | 41.6042 | 42.2424 | 42.8334 | 43.4074 | 43.4726 | 44.1426 | 43.6338 | 43.6338 | 43.6338 | 43.6338 | 43.6338 | 43.6338 | 43.6338 | 43.6338 | 43.6338 | 43.6338 | 43.6338 | 43.6338 | 43.6338 | 43.6338 | 43.6338 | 43.6338
65% | 359.6342 | 33.2554 | 44.1486 | 47.1138 | 32.8899 | 32.8867 | 33.2246 | 33.5955 | 34.3568 | 34.9039 | 35.2006 | 35.5252 | 35.8222 | 36.3591 | 37.0253 | 36.9788 | 36.9788 | 36.9788 | 36.9788 | 36.9788 | 36.9788 | 36.9788 | 36.9788 | 36.9788 | 36.9788 | 36.9788 | 36.9788 | 36.9788 | 36.9788 | 36.9788 | 36.9788 | 65% | 114.2056 | 37.0683 | 47.9835 | 50.8395 | 36.5305 | 36.5426 | 36.8354 | 37.6087 | 38.1259 | 38.6325 | 39.2251 | 39.7739 | 40.3069 | 40.3674 | 40.9896 | 40.5171 | 40.5171 | 40.5171 | 40.5171 | 40.5171 | 40.5171 | 40.5171 | 40.5171 | 40.5171 | 40.5171 | 40.5171 | 40.5171 | 40.5171 | 40.5171 | 40.5171 | 40.5171
60% | 689.7717 | 30.6973 | 40.7526 | 43.4896 | 30.3599 | 30.357 | 30.6689 | 31.0112 | 31.714 | 32.219 | 32.4929 | 32.7924 | 33.0667 | 33.5622 | 34.1772 | 34.1343 | 34.1343 | 34.1343 | 34.1343 | 34.1343 | 34.1343 | 34.1343 | 34.1343 | 34.1343 | 34.1343 | 34.1343 | 34.1343 | 34.1343 | 34.1343 | 34.1343 | 34.1343 | 60% | 178.1154 | 34.2169 | 44.2924 | 46.9287 | 33.7205 | 33.7317 | 34.0019 | 34.7157 | 35.1931 | 35.6608 | 36.2077 | 36.7143 | 37.2064 | 37.2622 | 37.8365 | 37.4004 | 37.4004 | 37.4004 | 37.4004 | 37.4004 | 37.4004 | 37.4004 | 37.4004 | 37.4004 | 37.4004 | 37.4004 | 37.4004 | 37.4004 | 37.4004 | 37.4004 | 37.4004
55% | 1095.5419 | 28.1392 | 37.3565 | 39.8655 | 27.8299 | 27.8272 | 28.1132 | 28.4269 | 29.0711 | 29.534 | 29.7851 | 30.0597 | 30.3111 | 30.7654 | 31.3291 | 31.2897 | 31.2897 | 31.2897 | 31.2897 | 31.2897 | 31.2897 | 31.2897 | 31.2897 | 31.2897 | 31.2897 | 31.2897 | 31.2897 | 31.2897 | 31.2897 | 31.2897 | 31.2897 | 55% | 311.6074 | 31.3655 | 40.6014 | 43.018 | 30.9104 | 30.9207 | 31.1685 | 31.8227 | 32.2604 | 32.689 | 33.1904 | 33.6548 | 34.1058 | 34.157 | 34.6835 | 34.2837 | 34.2837 | 34.2837 | 34.2837 | 34.2837 | 34.2837 | 34.2837 | 34.2837 | 34.2837 | 34.2837 | 34.2837 | 34.2837 | 34.2837 | 34.2837 | 34.2837 | 34.2837
50% | 1666.1918 | 25.581 | 33.9605 | 36.2413 | 25.2999 | 25.2975 | 25.5574 | 25.8427 | 26.4283 | 26.8491 | 27.0774 | 27.327 | 27.5556 | 27.9685 | 28.481 | 28.4452 | 28.4452 | 28.4452 | 28.4452 | 28.4452 | 28.4452 | 28.4452 | 28.4452 | 28.4452 | 28.4452 | 28.4452 | 28.4452 | 28.4452 | 28.4452 | 28.4452 | 28.4452 | 50% | 636.0723 | 28.5141 | 36.9103 | 39.1073 | 28.1004 | 28.1097 | 28.335 | 28.9297 | 29.3276 | 29.7173 | 30.1731 | 30.5953 | 31.0053 | 31.0518 | 31.5304 | 31.167 | 31.167 | 31.167 | 31.167 | 31.167 | 31.167 | 31.167 | 31.167 | 31.167 | 31.167 | 31.167 | 31.167 | 31.167 | 31.167 | 31.167 | 31.167
45% | 2506.0947 | 23.0229 | 30.5644 | 32.6172 | 22.7699 | 22.7677 | 23.0017 | 23.2584 | 23.7855 | 24.1642 | 24.3697 | 24.5943 | 24.8 | 25.1717 | 25.6329 | 25.6007 | 25.6007 | 25.6007 | 25.6007 | 25.6007 | 25.6007 | 25.6007 | 25.6007 | 25.6007 | 25.6007 | 25.6007 | 25.6007 | 25.6007 | 25.6007 | 25.6007 | 25.6007 | 45% | 1179.4944 | 25.6627 | 33.2193 | 35.1965 | 25.2904 | 25.2987 | 25.5015 | 26.0368 | 26.3949 | 26.7456 | 27.1558 | 27.5358 | 27.9048 | 27.9466 | 28.3774 | 28.0503 | 28.0503 | 28.0503 | 28.0503 | 28.0503 | 28.0503 | 28.0503 | 28.0503 | 28.0503 | 28.0503 | 28.0503 | 28.0503 | 28.0503 | 28.0503 | 28.0503 | 28.0503
40% | 3164.4787 | 20.4648 | 27.1684 | 28.9931 | 20.2399 | 20.238 | 20.4459 | 20.6741 | 21.1426 | 21.4793 | 21.6619 | 21.8616 | 22.0444 | 22.3748 | 22.7848 | 22.7562 | 22.7562 | 22.7562 | 22.7562 | 22.7562 | 22.7562 | 22.7562 | 22.7562 | 22.7562 | 22.7562 | 22.7562 | 22.7562 | 22.7562 | 22.7562 | 22.7562 | 22.7562 | 40% | 1808.3816 | 22.8113 | 29.5283 | 31.2858 | 22.4803 | 22.4878 | 22.668 | 23.1438 | 23.4621 | 23.7738 | 24.1385 | 24.4762 | 24.8042 | 24.8415 | 25.2244 | 24.9336 | 24.9336 | 24.9336 | 24.9336 | 24.9336 | 24.9336 | 24.9336 | 24.9336 | 24.9336 | 24.9336 | 24.9336 | 24.9336 | 24.9336 | 24.9336 | 24.9336 | 24.9336
35% | 3551.3408 | 17.9067 | 23.7723 | 25.3689 | 17.7099 | 17.7082 | 17.8902 | 18.0899 | 18.4998 | 18.7944 | 18.9542 | 19.1289 | 19.2889 | 19.578 | 19.9367 | 19.9116 | 19.9116 | 19.9116 | 19.9116 | 19.9116 | 19.9116 | 19.9116 | 19.9116 | 19.9116 | 19.9116 | 19.9116 | 19.9116 | 19.9116 | 19.9116 | 19.9116 | 19.9116 | 35% | 2779.1293 | 19.9599 | 25.8372 | 27.3751 | 19.6703 | 19.6768 | 19.8345 | 20.2508 | 20.5293 | 20.8021 | 21.1212 | 21.4167 | 21.7037 | 21.7363 | 22.0713 | 21.8169 | 21.8169 | 21.8169 | 21.8169 | 21.8169 | 21.8169 | 21.8169 | 21.8169 | 21.8169 | 21.8169 | 21.8169 | 21.8169 | 21.8169 | 21.8169 | 21.8169 | 21.8169
30% | 3758.953 | 15.3486 | 20.3763 | 21.7448 | 15.18 | 15.1785 | 15.3345 | 15.5056 | 15.857 | 16.1095 | 16.2464 | 16.3962 | 16.5333 | 16.7811 | 17.0886 | 17.0671 | 17.0671 | 17.0671 | 17.0671 | 17.0671 | 17.0671 | 17.0671 | 17.0671 | 17.0671 | 17.0671 | 17.0671 | 17.0671 | 17.0671 | 17.0671 | 17.0671 | 17.0671 | 30% | 3814.165 | 17.1085 | 22.1462 | 23.4644 | 16.8602 | 16.8658 | 17.001 | 17.3578 | 17.5966 | 17.8304 | 18.1039 | 18.3572 | 18.6032 | 18.6311 | 18.9183 | 18.7002 | 18.7002 | 18.7002 | 18.7002 | 18.7002 | 18.7002 | 18.7002 | 18.7002 | 18.7002 | 18.7002 | 18.7002 | 18.7002 | 18.7002 | 18.7002 | 18.7002 | 18.7002
25% | 3926.4798 | 12.7905 | 16.9802 | 18.1207 | 12.65 | 12.6487 | 12.7787 | 12.9213 | 13.2142 | 13.4246 | 13.5387 | 13.6635 | 13.7778 | 13.9843 | 14.2405 | 14.2226 | 14.2226 | 14.2226 | 14.2226 | 14.2226 | 14.2226 | 14.2226 | 14.2226 | 14.2226 | 14.2226 | 14.2226 | 14.2226 | 14.2226 | 14.2226 | 14.2226 | 14.2226 | 25% | 4166.9923 | 14.257 | 18.4552 | 19.5536 | 14.0502 | 14.0549 | 14.1675 | 14.4649 | 14.6638 | 14.8587 | 15.0866 | 15.2976 | 15.5027 | 15.5259 | 15.7652 | 15.5835 | 15.5835 | 15.5835 | 15.5835 | 15.5835 | 15.5835 | 15.5835 | 15.5835 | 15.5835 | 15.5835 | 15.5835 | 15.5835 | 15.5835 | 15.5835 | 15.5835 | 15.5835
20% | 4050.5177 | 10.2324 | 13.5842 | 14.4965 | 10.12 | 10.119 | 10.223 | 10.3371 | 10.5713 | 10.7397 | 10.831 | 10.9308 | 11.0222 | 11.1874 | 11.3924 | 11.3781 | 11.3781 | 11.3781 | 11.3781 | 11.3781 | 11.3781 | 11.3781 | 11.3781 | 11.3781 | 11.3781 | 11.3781 | 11.3781 | 11.3781 | 11.3781 | 11.3781 | 11.3781 | 20% | 4282.7105 | 11.4056 | 14.7641 | 15.6429 | 11.2402 | 11.2439 | 11.334 | 11.5719 | 11.731 | 11.8869 | 12.0692 | 12.2381 | 12.4021 | 12.4207 | 12.6122 | 12.4668 | 12.4668 | 12.4668 | 12.4668 | 12.4668 | 12.4668 | 12.4668 | 12.4668 | 12.4668 | 12.4668 | 12.4668 | 12.4668 | 12.4668 | 12.4668 | 12.4668 | 12.4668
15% | 4152.622 | 7.6743 | 10.1881 | 10.8724 | 7.59 | 7.5892 | 7.6672 | 7.7528 | 7.9285 | 8.0547 | 8.1232 | 8.1981 | 8.2667 | 8.3906 | 8.5443 | 8.5336 | 8.5336 | 8.5336 | 8.5336 | 8.5336 | 8.5336 | 8.5336 | 8.5336 | 8.5336 | 8.5336 | 8.5336 | 8.5336 | 8.5336 | 8.5336 | 8.5336 | 8.5336 | 15% | 4364.7722 | 8.5542 | 11.0731 | 11.7322 | 8.4301 | 8.4329 | 8.5005 | 8.6789 | 8.7983 | 8.9152 | 9.0519 | 9.1786 | 9.3016 | 9.3155 | 9.4591 | 9.3501 | 9.3501 | 9.3501 | 9.3501 | 9.3501 | 9.3501 | 9.3501 | 9.3501 | 9.3501 | 9.3501 | 9.3501 | 9.3501 | 9.3501 | 9.3501 | 9.3501 | 9.3501
10% | 4248.2976 | 5.1162 | 6.7921 | 7.2483 | 5.06 | 5.0595 | 5.1115 | 5.1685 | 5.2857 | 5.3698 | 5.4155 | 5.4654 | 5.5111 | 5.5937 | 5.6962 | 5.689 | 5.689 | 5.689 | 5.689 | 5.689 | 5.689 | 5.689 | 5.689 | 5.689 | 5.689 | 5.689 | 5.689 | 5.689 | 5.689 | 5.689 | 5.689 | 10% | 4391.6218 | 5.7028 | 7.3821 | 7.8215 | 5.6201 | 5.6219 | 5.667 | 5.7859 | 5.8655 | 5.9435 | 6.0346 | 6.1191 | 6.2011 | 6.2104 | 6.3061 | 6.2334 | 6.2334 | 6.2334 | 6.2334 | 6.2334 | 6.2334 | 6.2334 | 6.2334 | 6.2334 | 6.2334 | 6.2334 | 6.2334 | 6.2334 | 6.2334 | 6.2334 | 6.2334
5% | 4361.7469 | 2.5581 | 3.396 | 3.6241 | 2.53 | 2.5297 | 2.5557 | 2.5843 | 2.6428 | 2.6849 | 2.7077 | 2.7327 | 2.7556 | 2.7969 | 2.8481 | 2.8445 | 2.8445 | 2.8445 | 2.8445 | 2.8445 | 2.8445 | 2.8445 | 2.8445 | 2.8445 | 2.8445 | 2.8445 | 2.8445 | 2.8445 | 2.8445 | 2.8445 | 2.8445 | 5% | 4391.6218 | 2.8514 | 3.691 | 3.9107 | 2.81 | 2.811 | 2.8335 | 2.893 | 2.9328 | 2.9717 | 3.0173 | 3.0595 | 3.1005 | 3.1052 | 3.153 | 3.1167 | 3.1167 | 3.1167 | 3.1167 | 3.1167 | 3.1167 | 3.1167 | 3.1167 | 3.1167 | 3.1167 | 3.1167 | 3.1167 | 3.1167 | 3.1167 | 3.1167 | 3.1167
9.992e-14% | 4391.6218 | 5.1121e-14 | 6.7867e-14 | 7.2425e-14 | 5.0559e-14 | 5.0555e-14 | 5.1074e-14 | 5.1644e-14 | 5.2814e-14 | 5.3655e-14 | 5.4112e-14 | 5.461e-14 | 5.5067e-14 | 5.5892e-14 | 5.6917e-14 | 5.6845e-14 | 5.6845e-14 | 5.6845e-14 | 5.6845e-14 | 5.6845e-14 | 5.6845e-14 | 5.6845e-14 | 5.6845e-14 | 5.6845e-14 | 5.6845e-14 | 5.6845e-14 | 5.6845e-14 | 5.6845e-14 | 5.6845e-14 | 5.6845e-14 | 5.6845e-14 | 9.992e-14% | 4391.6218 | 5.6983e-14 | 7.3762e-14 | 7.8152e-14 | 5.6156e-14 | 5.6174e-14 | 5.6625e-14 | 5.7813e-14 | 5.8608e-14 | 5.9387e-14 | 6.0298e-14 | 6.1142e-14 | 6.1961e-14 | 6.2054e-14 | 6.301e-14 | 6.2284e-14 | 6.2284e-14 | 6.2284e-14 | 6.2284e-14 | 6.2284e-14 | 6.2284e-14 | 6.2284e-14 | 6.2284e-14 | 6.2284e-14 | 6.2284e-14 | 6.2284e-14 | 6.2284e-14 | 6.2284e-14 | 6.2284e-14 | 6.2284e-14 | 6.2284e-14
Option 6
Winter Season | [31 empty] | Winter Season
P50 | [31 empty] | P10
% of MD | Winter - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Winter - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 45.0311 | 62.4376 | 66.9594 | 67.7285 | 68.3267 | 69.3603 | 71.7146 | 73.2888 | 75.2849 | 76.3199 | 77.2291 | 75.5455 | 77.5138 | 80.6095 | 78.2564 | 78.2564 | 78.2564 | 78.2564 | 78.2564 | 78.2564 | 78.2564 | 78.2564 | 78.2564 | 78.2564 | 78.2564 | 78.2564 | 78.2564 | 78.2564 | 78.2564 | 78.2564 | 100% | 0 | 48.1978 | 65.3847 | 70.0831 | 70.8084 | 71.267 | 72.2781 | 74.6693 | 75.9727 | 78.4597 | 86.0243 | 79.7829 | 78.5605 | 80.2054 | 83.8053 | 81.3648 | 81.3648 | 81.3648 | 81.3648 | 81.3648 | 81.3648 | 81.3648 | 81.3648 | 81.3648 | 81.3648 | 81.3648 | 81.3648 | 81.3648 | 81.3648 | 81.3648 | 81.3648
99% | 1.486 | 44.5808 | 61.8132 | 66.2898 | 67.0512 | 67.6435 | 68.6667 | 70.9975 | 72.5559 | 74.532 | 75.5567 | 76.4569 | 74.7901 | 76.7387 | 79.8034 | 77.4739 | 77.4739 | 77.4739 | 77.4739 | 77.4739 | 77.4739 | 77.4739 | 77.4739 | 77.4739 | 77.4739 | 77.4739 | 77.4739 | 77.4739 | 77.4739 | 77.4739 | 77.4739 | 99% | 1.486 | 47.7158 | 64.7309 | 69.3823 | 70.1003 | 70.5543 | 71.5553 | 73.9226 | 75.2129 | 77.6751 | 85.1641 | 78.9851 | 77.7749 | 79.4033 | 82.9672 | 80.5512 | 80.5512 | 80.5512 | 80.5512 | 80.5512 | 80.5512 | 80.5512 | 80.5512 | 80.5512 | 80.5512 | 80.5512 | 80.5512 | 80.5512 | 80.5512 | 80.5512 | 80.5512
98% | 3.2692 | 44.1305 | 61.1889 | 65.6202 | 66.3739 | 66.9602 | 67.9731 | 70.2804 | 71.823 | 73.7792 | 74.7935 | 75.6846 | 74.0346 | 75.9636 | 78.9973 | 76.6913 | 76.6913 | 76.6913 | 76.6913 | 76.6913 | 76.6913 | 76.6913 | 76.6913 | 76.6913 | 76.6913 | 76.6913 | 76.6913 | 76.6913 | 76.6913 | 76.6913 | 76.6913 | 98% | 3.2692 | 47.2338 | 64.0771 | 68.6815 | 69.3922 | 69.8416 | 70.8325 | 73.1759 | 74.4532 | 76.8905 | 84.3038 | 78.1873 | 76.9893 | 78.6013 | 82.1292 | 79.7375 | 79.7375 | 79.7375 | 79.7375 | 79.7375 | 79.7375 | 79.7375 | 79.7375 | 79.7375 | 79.7375 | 79.7375 | 79.7375 | 79.7375 | 79.7375 | 79.7375 | 79.7375
97% | 6.8356 | 43.6802 | 60.5645 | 64.9506 | 65.6966 | 66.2769 | 67.2795 | 69.5632 | 71.0901 | 73.0263 | 74.0303 | 74.9123 | 73.2792 | 75.1884 | 78.1912 | 75.9087 | 75.9087 | 75.9087 | 75.9087 | 75.9087 | 75.9087 | 75.9087 | 75.9087 | 75.9087 | 75.9087 | 75.9087 | 75.9087 | 75.9087 | 75.9087 | 75.9087 | 75.9087 | 97% | 6.8356 | 46.7518 | 63.4232 | 67.9806 | 68.6841 | 69.129 | 70.1097 | 72.4292 | 73.6935 | 76.1059 | 83.4436 | 77.3894 | 76.2037 | 77.7992 | 81.2911 | 78.9239 | 78.9239 | 78.9239 | 78.9239 | 78.9239 | 78.9239 | 78.9239 | 78.9239 | 78.9239 | 78.9239 | 78.9239 | 78.9239 | 78.9239 | 78.9239 | 78.9239 | 78.9239
95% | 17.5347 | 42.7796 | 59.3157 | 63.6114 | 64.342 | 64.9104 | 65.8923 | 68.1289 | 69.6243 | 71.5207 | 72.5039 | 73.3677 | 71.7683 | 73.6382 | 76.579 | 74.3436 | 74.3436 | 74.3436 | 74.3436 | 74.3436 | 74.3436 | 74.3436 | 74.3436 | 74.3436 | 74.3436 | 74.3436 | 74.3436 | 74.3436 | 74.3436 | 74.3436 | 74.3436 | 95% | 17.5347 | 45.7879 | 62.1155 | 66.579 | 67.268 | 67.7036 | 68.6642 | 70.9358 | 72.174 | 74.5368 | 81.7231 | 75.7938 | 74.6325 | 76.1951 | 79.615 | 77.2966 | 77.2966 | 77.2966 | 77.2966 | 77.2966 | 77.2966 | 77.2966 | 77.2966 | 77.2966 | 77.2966 | 77.2966 | 77.2966 | 77.2966 | 77.2966 | 77.2966 | 77.2966
90% | 78.7576 | 40.528 | 56.1939 | 60.2634 | 60.9556 | 61.4941 | 62.4243 | 64.5432 | 65.9599 | 67.7564 | 68.6879 | 69.5062 | 67.991 | 69.7625 | 72.5486 | 70.4308 | 70.4308 | 70.4308 | 70.4308 | 70.4308 | 70.4308 | 70.4308 | 70.4308 | 70.4308 | 70.4308 | 70.4308 | 70.4308 | 70.4308 | 70.4308 | 70.4308 | 70.4308 | 90% | 78.7576 | 43.378 | 58.8463 | 63.0748 | 63.7275 | 64.1403 | 65.0503 | 67.2023 | 68.3754 | 70.6138 | 77.4219 | 71.8046 | 70.7045 | 72.1848 | 75.4247 | 73.2283 | 73.2283 | 73.2283 | 73.2283 | 73.2283 | 73.2283 | 73.2283 | 73.2283 | 73.2283 | 73.2283 | 73.2283 | 73.2283 | 73.2283 | 73.2283 | 73.2283 | 73.2283
85% | 236.8672 | 38.2764 | 53.072 | 56.9155 | 57.5692 | 58.0777 | 58.9563 | 60.9575 | 62.2954 | 63.9922 | 64.8719 | 65.6448 | 64.2137 | 65.8868 | 68.5181 | 66.518 | 66.518 | 66.518 | 66.518 | 66.518 | 66.518 | 66.518 | 66.518 | 66.518 | 66.518 | 66.518 | 66.518 | 66.518 | 66.518 | 66.518 | 66.518 | 85% | 236.8672 | 40.9681 | 55.577 | 59.5707 | 60.1871 | 60.5769 | 61.4364 | 63.4689 | 64.5768 | 66.6908 | 73.1207 | 67.8155 | 66.7765 | 68.1746 | 71.2345 | 69.1601 | 69.1601 | 69.1601 | 69.1601 | 69.1601 | 69.1601 | 69.1601 | 69.1601 | 69.1601 | 69.1601 | 69.1601 | 69.1601 | 69.1601 | 69.1601 | 69.1601 | 69.1601
80% | 497.5104 | 36.0249 | 49.9501 | 53.5675 | 54.1828 | 54.6614 | 55.4882 | 57.3717 | 58.631 | 60.2279 | 61.056 | 61.7833 | 60.4364 | 62.0111 | 64.4876 | 62.6051 | 62.6051 | 62.6051 | 62.6051 | 62.6051 | 62.6051 | 62.6051 | 62.6051 | 62.6051 | 62.6051 | 62.6051 | 62.6051 | 62.6051 | 62.6051 | 62.6051 | 62.6051 | 80% | 497.5104 | 38.5582 | 52.3078 | 56.0665 | 56.6467 | 57.0136 | 57.8225 | 59.7354 | 60.7781 | 62.7678 | 68.8195 | 63.8263 | 62.8484 | 64.1643 | 67.0442 | 65.0919 | 65.0919 | 65.0919 | 65.0919 | 65.0919 | 65.0919 | 65.0919 | 65.0919 | 65.0919 | 65.0919 | 65.0919 | 65.0919 | 65.0919 | 65.0919 | 65.0919 | 65.0919
75% | 803.6248 | 33.7733 | 46.8282 | 50.2195 | 50.7964 | 51.245 | 52.0202 | 53.786 | 54.9666 | 56.4637 | 57.24 | 57.9219 | 56.6592 | 58.1354 | 60.4571 | 58.6923 | 58.6923 | 58.6923 | 58.6923 | 58.6923 | 58.6923 | 58.6923 | 58.6923 | 58.6923 | 58.6923 | 58.6923 | 58.6923 | 58.6923 | 58.6923 | 58.6923 | 58.6923 | 75% | 803.6248 | 36.1483 | 49.0386 | 52.5623 | 53.1063 | 53.4502 | 54.2086 | 56.0019 | 56.9795 | 58.8448 | 64.5182 | 59.8372 | 58.9204 | 60.154 | 62.8539 | 61.0236 | 61.0236 | 61.0236 | 61.0236 | 61.0236 | 61.0236 | 61.0236 | 61.0236 | 61.0236 | 61.0236 | 61.0236 | 61.0236 | 61.0236 | 61.0236 | 61.0236 | 61.0236
70% | 1155.2107 | 31.5218 | 43.7063 | 46.8715 | 47.4099 | 47.8287 | 48.5522 | 50.2003 | 51.3021 | 52.6994 | 53.424 | 54.0604 | 52.8819 | 54.2597 | 56.4267 | 54.7795 | 54.7795 | 54.7795 | 54.7795 | 54.7795 | 54.7795 | 54.7795 | 54.7795 | 54.7795 | 54.7795 | 54.7795 | 54.7795 | 54.7795 | 54.7795 | 54.7795 | 54.7795 | 70% | 1155.2107 | 33.7384 | 45.7693 | 49.0582 | 49.5659 | 49.8869 | 50.5947 | 52.2685 | 53.1809 | 54.9218 | 60.217 | 55.8481 | 54.9924 | 56.1438 | 58.6637 | 56.9554 | 56.9554 | 56.9554 | 56.9554 | 56.9554 | 56.9554 | 56.9554 | 56.9554 | 56.9554 | 56.9554 | 56.9554 | 56.9554 | 56.9554 | 56.9554 | 56.9554 | 56.9554
65% | 1553.1596 | 29.2702 | 40.5844 | 43.5236 | 44.0235 | 44.4124 | 45.0842 | 46.6145 | 47.6377 | 48.9352 | 49.608 | 50.1989 | 49.1046 | 50.384 | 52.3962 | 50.8667 | 50.8667 | 50.8667 | 50.8667 | 50.8667 | 50.8667 | 50.8667 | 50.8667 | 50.8667 | 50.8667 | 50.8667 | 50.8667 | 50.8667 | 50.8667 | 50.8667 | 50.8667 | 65% | 1553.1596 | 31.3286 | 42.5001 | 45.554 | 46.0254 | 46.3235 | 46.9808 | 48.535 | 49.3822 | 50.9988 | 55.9158 | 51.8589 | 51.0643 | 52.1335 | 54.4734 | 52.8871 | 52.8871 | 52.8871 | 52.8871 | 52.8871 | 52.8871 | 52.8871 | 52.8871 | 52.8871 | 52.8871 | 52.8871 | 52.8871 | 52.8871 | 52.8871 | 52.8871 | 52.8871
60% | 2026.2996 | 27.0187 | 37.4626 | 40.1756 | 40.6371 | 40.996 | 41.6162 | 43.0288 | 43.9733 | 45.1709 | 45.792 | 46.3375 | 45.3273 | 46.5083 | 48.3657 | 46.9539 | 46.9539 | 46.9539 | 46.9539 | 46.9539 | 46.9539 | 46.9539 | 46.9539 | 46.9539 | 46.9539 | 46.9539 | 46.9539 | 46.9539 | 46.9539 | 46.9539 | 46.9539 | 60% | 2026.2996 | 28.9187 | 39.2308 | 42.0499 | 42.485 | 42.7602 | 43.3669 | 44.8016 | 45.5836 | 47.0758 | 51.6146 | 47.8698 | 47.1363 | 48.1232 | 50.2832 | 48.8189 | 48.8189 | 48.8189 | 48.8189 | 48.8189 | 48.8189 | 48.8189 | 48.8189 | 48.8189 | 48.8189 | 48.8189 | 48.8189 | 48.8189 | 48.8189 | 48.8189 | 48.8189
55% | 2598.4068 | 24.7671 | 34.3407 | 36.8276 | 37.2507 | 37.5797 | 38.1482 | 39.4431 | 40.3088 | 41.4067 | 41.976 | 42.476 | 41.55 | 42.6326 | 44.3352 | 43.041 | 43.041 | 43.041 | 43.041 | 43.041 | 43.041 | 43.041 | 43.041 | 43.041 | 43.041 | 43.041 | 43.041 | 43.041 | 43.041 | 43.041 | 43.041 | 55% | 2598.4068 | 26.5088 | 35.9616 | 38.5457 | 38.9446 | 39.1968 | 39.753 | 41.0681 | 41.785 | 43.1529 | 47.3134 | 43.8806 | 43.2083 | 44.113 | 46.0929 | 44.7507 | 44.7507 | 44.7507 | 44.7507 | 44.7507 | 44.7507 | 44.7507 | 44.7507 | 44.7507 | 44.7507 | 44.7507 | 44.7507 | 44.7507 | 44.7507 | 44.7507 | 44.7507
50% | 3233.5201 | 22.5156 | 31.2188 | 33.4797 | 33.8642 | 34.1634 | 34.6802 | 35.8573 | 36.6444 | 37.6424 | 38.16 | 38.6146 | 37.7728 | 38.7569 | 40.3048 | 39.1282 | 39.1282 | 39.1282 | 39.1282 | 39.1282 | 39.1282 | 39.1282 | 39.1282 | 39.1282 | 39.1282 | 39.1282 | 39.1282 | 39.1282 | 39.1282 | 39.1282 | 39.1282 | 50% | 3233.5201 | 24.0989 | 32.6924 | 35.0416 | 35.4042 | 35.6335 | 36.139 | 37.3346 | 37.9863 | 39.2299 | 43.0122 | 39.8915 | 39.2803 | 40.1027 | 41.9026 | 40.6824 | 40.6824 | 40.6824 | 40.6824 | 40.6824 | 40.6824 | 40.6824 | 40.6824 | 40.6824 | 40.6824 | 40.6824 | 40.6824 | 40.6824 | 40.6824 | 40.6824 | 40.6824
45% | 3775.313 | 20.264 | 28.0969 | 30.1317 | 30.4778 | 30.747 | 31.2121 | 32.2716 | 32.9799 | 33.8782 | 34.344 | 34.7531 | 33.9955 | 34.8812 | 36.2743 | 35.2154 | 35.2154 | 35.2154 | 35.2154 | 35.2154 | 35.2154 | 35.2154 | 35.2154 | 35.2154 | 35.2154 | 35.2154 | 35.2154 | 35.2154 | 35.2154 | 35.2154 | 35.2154 | 45% | 3775.313 | 21.689 | 29.4231 | 31.5374 | 31.8638 | 32.0701 | 32.5251 | 33.6012 | 34.1877 | 35.3069 | 38.7109 | 35.9023 | 35.3522 | 36.0924 | 37.7124 | 36.6142 | 36.6142 | 36.6142 | 36.6142 | 36.6142 | 36.6142 | 36.6142 | 36.6142 | 36.6142 | 36.6142 | 36.6142 | 36.6142 | 36.6142 | 36.6142 | 36.6142 | 36.6142
40% | 4072.8088 | 18.0124 | 24.975 | 26.7837 | 27.0914 | 27.3307 | 27.7441 | 28.6859 | 29.3155 | 30.114 | 30.528 | 30.8917 | 30.2182 | 31.0055 | 32.2438 | 31.3026 | 31.3026 | 31.3026 | 31.3026 | 31.3026 | 31.3026 | 31.3026 | 31.3026 | 31.3026 | 31.3026 | 31.3026 | 31.3026 | 31.3026 | 31.3026 | 31.3026 | 31.3026 | 40% | 4072.8088 | 19.2791 | 26.1539 | 28.0332 | 28.3234 | 28.5068 | 28.9112 | 29.8677 | 30.3891 | 31.3839 | 34.4097 | 31.9132 | 31.4242 | 32.0822 | 33.5221 | 32.5459 | 32.5459 | 32.5459 | 32.5459 | 32.5459 | 32.5459 | 32.5459 | 32.5459 | 32.5459 | 32.5459 | 32.5459 | 32.5459 | 32.5459 | 32.5459 | 32.5459 | 32.5459
35% | 4198.821 | 15.7609 | 21.8532 | 23.4358 | 23.705 | 23.9144 | 24.2761 | 25.1001 | 25.6511 | 26.3497 | 26.712 | 27.0302 | 26.4409 | 27.1298 | 28.2133 | 27.3897 | 27.3897 | 27.3897 | 27.3897 | 27.3897 | 27.3897 | 27.3897 | 27.3897 | 27.3897 | 27.3897 | 27.3897 | 27.3897 | 27.3897 | 27.3897 | 27.3897 | 27.3897 | 35% | 4198.821 | 16.8692 | 22.8847 | 24.5291 | 24.7829 | 24.9434 | 25.2973 | 26.1342 | 26.5904 | 27.4609 | 30.1085 | 27.924 | 27.4962 | 28.0719 | 29.3318 | 28.4777 | 28.4777 | 28.4777 | 28.4777 | 28.4777 | 28.4777 | 28.4777 | 28.4777 | 28.4777 | 28.4777 | 28.4777 | 28.4777 | 28.4777 | 28.4777 | 28.4777 | 28.4777
30% | 4271.3374 | 13.5093 | 18.7313 | 20.0878 | 20.3185 | 20.498 | 20.8081 | 21.5144 | 21.9866 | 22.5855 | 22.896 | 23.1687 | 22.6637 | 23.2542 | 24.1829 | 23.4769 | 23.4769 | 23.4769 | 23.4769 | 23.4769 | 23.4769 | 23.4769 | 23.4769 | 23.4769 | 23.4769 | 23.4769 | 23.4769 | 23.4769 | 23.4769 | 23.4769 | 23.4769 | 30% | 4271.3374 | 14.4593 | 19.6154 | 21.0249 | 21.2425 | 21.3801 | 21.6834 | 22.4008 | 22.7918 | 23.5379 | 25.8073 | 23.9349 | 23.5682 | 24.0616 | 25.1416 | 24.4094 | 24.4094 | 24.4094 | 24.4094 | 24.4094 | 24.4094 | 24.4094 | 24.4094 | 24.4094 | 24.4094 | 24.4094 | 24.4094 | 24.4094 | 24.4094 | 24.4094 | 24.4094
25% | 4321.8611 | 11.2578 | 15.6094 | 16.7398 | 16.9321 | 17.0817 | 17.3401 | 17.9287 | 18.3222 | 18.8212 | 19.08 | 19.3073 | 18.8864 | 19.3785 | 20.1524 | 19.5641 | 19.5641 | 19.5641 | 19.5641 | 19.5641 | 19.5641 | 19.5641 | 19.5641 | 19.5641 | 19.5641 | 19.5641 | 19.5641 | 19.5641 | 19.5641 | 19.5641 | 19.5641 | 25% | 4321.8611 | 12.0494 | 16.3462 | 17.5208 | 17.7021 | 17.8167 | 18.0695 | 18.6673 | 18.9932 | 19.6149 | 21.5061 | 19.9457 | 19.6401 | 20.0513 | 20.9513 | 20.3412 | 20.3412 | 20.3412 | 20.3412 | 20.3412 | 20.3412 | 20.3412 | 20.3412 | 20.3412 | 20.3412 | 20.3412 | 20.3412 | 20.3412 | 20.3412 | 20.3412 | 20.3412
20% | 4353.067 | 9.0062 | 12.4875 | 13.3919 | 13.5457 | 13.6653 | 13.8721 | 14.3429 | 14.6578 | 15.057 | 15.264 | 15.4458 | 15.1091 | 15.5028 | 16.1219 | 15.6513 | 15.6513 | 15.6513 | 15.6513 | 15.6513 | 15.6513 | 15.6513 | 15.6513 | 15.6513 | 15.6513 | 15.6513 | 15.6513 | 15.6513 | 15.6513 | 15.6513 | 15.6513 | 20% | 4353.067 | 9.6396 | 13.0769 | 14.0166 | 14.1617 | 14.2534 | 14.4556 | 14.9339 | 15.1945 | 15.6919 | 17.2049 | 15.9566 | 15.7121 | 16.0411 | 16.7611 | 16.273 | 16.273 | 16.273 | 16.273 | 16.273 | 16.273 | 16.273 | 16.273 | 16.273 | 16.273 | 16.273 | 16.273 | 16.273 | 16.273 | 16.273 | 16.273
15% | 4369.4129 | 6.7547 | 9.3656 | 10.0439 | 10.1593 | 10.249 | 10.404 | 10.7572 | 10.9933 | 11.2927 | 11.448 | 11.5844 | 11.3318 | 11.6271 | 12.0914 | 11.7385 | 11.7385 | 11.7385 | 11.7385 | 11.7385 | 11.7385 | 11.7385 | 11.7385 | 11.7385 | 11.7385 | 11.7385 | 11.7385 | 11.7385 | 11.7385 | 11.7385 | 11.7385 | 15% | 4369.4129 | 7.2297 | 9.8077 | 10.5125 | 10.6213 | 10.69 | 10.8417 | 11.2004 | 11.3959 | 11.769 | 12.9036 | 11.9674 | 11.7841 | 12.0308 | 12.5708 | 12.2047 | 12.2047 | 12.2047 | 12.2047 | 12.2047 | 12.2047 | 12.2047 | 12.2047 | 12.2047 | 12.2047 | 12.2047 | 12.2047 | 12.2047 | 12.2047 | 12.2047 | 12.2047
10% | 4378.6261 | 4.5031 | 6.2438 | 6.6959 | 6.7728 | 6.8327 | 6.936 | 7.1715 | 7.3289 | 7.5285 | 7.632 | 7.7229 | 7.5546 | 7.7514 | 8.061 | 7.8256 | 7.8256 | 7.8256 | 7.8256 | 7.8256 | 7.8256 | 7.8256 | 7.8256 | 7.8256 | 7.8256 | 7.8256 | 7.8256 | 7.8256 | 7.8256 | 7.8256 | 7.8256 | 10% | 4378.6261 | 4.8198 | 6.5385 | 7.0083 | 7.0808 | 7.1267 | 7.2278 | 7.4669 | 7.5973 | 7.846 | 8.6024 | 7.9783 | 7.8561 | 8.0205 | 8.3805 | 8.1365 | 8.1365 | 8.1365 | 8.1365 | 8.1365 | 8.1365 | 8.1365 | 8.1365 | 8.1365 | 8.1365 | 8.1365 | 8.1365 | 8.1365 | 8.1365 | 8.1365 | 8.1365
5% | 4391.7028 | 2.2516 | 3.1219 | 3.348 | 3.3864 | 3.4163 | 3.468 | 3.5857 | 3.6644 | 3.7642 | 3.816 | 3.8615 | 3.7773 | 3.8757 | 4.0305 | 3.9128 | 3.9128 | 3.9128 | 3.9128 | 3.9128 | 3.9128 | 3.9128 | 3.9128 | 3.9128 | 3.9128 | 3.9128 | 3.9128 | 3.9128 | 3.9128 | 3.9128 | 3.9128 | 5% | 4391.7028 | 2.4099 | 3.2692 | 3.5042 | 3.5404 | 3.5633 | 3.6139 | 3.7335 | 3.7986 | 3.923 | 4.3012 | 3.9891 | 3.928 | 4.0103 | 4.1903 | 4.0682 | 4.0682 | 4.0682 | 4.0682 | 4.0682 | 4.0682 | 4.0682 | 4.0682 | 4.0682 | 4.0682 | 4.0682 | 4.0682 | 4.0682 | 4.0682 | 4.0682 | 4.0682
9.992e-14% | 4391.7028 | 4.4995e-14 | 6.2388e-14 | 6.6906e-14 | 6.7674e-14 | 6.8272e-14 | 6.9305e-14 | 7.1657e-14 | 7.323e-14 | 7.5225e-14 | 7.6259e-14 | 7.7167e-14 | 7.5485e-14 | 7.7452e-14 | 8.0545e-14 | 7.8194e-14 | 7.8194e-14 | 7.8194e-14 | 7.8194e-14 | 7.8194e-14 | 7.8194e-14 | 7.8194e-14 | 7.8194e-14 | 7.8194e-14 | 7.8194e-14 | 7.8194e-14 | 7.8194e-14 | 7.8194e-14 | 7.8194e-14 | 7.8194e-14 | 7.8194e-14 | 9.992e-14% | 4391.7028 | 4.8159e-14 | 6.5332e-14 | 7.0027e-14 | 7.0752e-14 | 7.121e-14 | 7.222e-14 | 7.461e-14 | 7.5912e-14 | 7.8397e-14 | 8.5956e-14 | 7.9719e-14 | 7.8498e-14 | 8.0141e-14 | 8.3738e-14 | 8.13e-14 | 8.13e-14 | 8.13e-14 | 8.13e-14 | 8.13e-14 | 8.13e-14 | 8.13e-14 | 8.13e-14 | 8.13e-14 | 8.13e-14 | 8.13e-14 | 8.13e-14 | 8.13e-14 | 8.13e-14 | 8.13e-14 | 8.13e-14
Summer Season | [31 empty] | Summer Season
P50 | [31 empty] | P10
% of MD | Summer - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Summer - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 51.1621 | 67.921 | 72.4827 | 72.3498 | 72.345 | 72.8648 | 73.4353 | 74.6066 | 75.4483 | 75.9048 | 76.4041 | 76.8611 | 77.687 | 78.7121 | 78.6404 | 78.6404 | 78.6404 | 78.6404 | 78.6404 | 78.6404 | 78.6404 | 78.6404 | 78.6404 | 78.6404 | 78.6404 | 78.6404 | 78.6404 | 78.6404 | 78.6404 | 78.6404 | 100% | 0 | 57.0282 | 73.8207 | 78.2145 | 77.9508 | 77.9694 | 78.4199 | 79.6095 | 80.4052 | 81.1846 | 82.0962 | 82.9406 | 83.7606 | 83.8537 | 84.8109 | 84.0841 | 84.0841 | 84.0841 | 84.0841 | 84.0841 | 84.0841 | 84.0841 | 84.0841 | 84.0841 | 84.0841 | 84.0841 | 84.0841 | 84.0841 | 84.0841 | 84.0841 | 84.0841
99% | 0 | 50.6505 | 67.2418 | 71.7579 | 71.6263 | 71.6215 | 72.1362 | 72.701 | 73.8605 | 74.6938 | 75.1458 | 75.64 | 76.0925 | 76.9101 | 77.9249 | 77.854 | 77.854 | 77.854 | 77.854 | 77.854 | 77.854 | 77.854 | 77.854 | 77.854 | 77.854 | 77.854 | 77.854 | 77.854 | 77.854 | 77.854 | 77.854 | 99% | 1.5127 | 56.4579 | 73.0825 | 77.4324 | 77.1713 | 77.1897 | 77.6357 | 78.8134 | 79.6012 | 80.3728 | 81.2753 | 82.1112 | 82.923 | 83.0151 | 83.9628 | 83.2432 | 83.2432 | 83.2432 | 83.2432 | 83.2432 | 83.2432 | 83.2432 | 83.2432 | 83.2432 | 83.2432 | 83.2432 | 83.2432 | 83.2432 | 83.2432 | 83.2432 | 83.2432
98% | 0 | 50.1389 | 66.5626 | 71.033 | 70.9028 | 70.8981 | 71.4075 | 71.9666 | 73.1145 | 73.9393 | 74.3867 | 74.876 | 75.3239 | 76.1333 | 77.1378 | 77.0676 | 77.0676 | 77.0676 | 77.0676 | 77.0676 | 77.0676 | 77.0676 | 77.0676 | 77.0676 | 77.0676 | 77.0676 | 77.0676 | 77.0676 | 77.0676 | 77.0676 | 77.0676 | 98% | 2.269 | 55.8876 | 72.3443 | 76.6503 | 76.3918 | 76.41 | 76.8515 | 78.0173 | 78.7971 | 79.5609 | 80.4543 | 81.2818 | 82.0854 | 82.1766 | 83.1147 | 82.4024 | 82.4024 | 82.4024 | 82.4024 | 82.4024 | 82.4024 | 82.4024 | 82.4024 | 82.4024 | 82.4024 | 82.4024 | 82.4024 | 82.4024 | 82.4024 | 82.4024 | 82.4024
97% | 0.37816 | 49.6272 | 65.8834 | 70.3082 | 70.1794 | 70.1746 | 70.6789 | 71.2323 | 72.3684 | 73.1848 | 73.6277 | 74.112 | 74.5553 | 75.3564 | 76.3507 | 76.2812 | 76.2812 | 76.2812 | 76.2812 | 76.2812 | 76.2812 | 76.2812 | 76.2812 | 76.2812 | 76.2812 | 76.2812 | 76.2812 | 76.2812 | 76.2812 | 76.2812 | 76.2812 | 97% | 3.7816 | 55.3173 | 71.6061 | 75.8681 | 75.6123 | 75.6303 | 76.0673 | 77.2212 | 77.9931 | 78.7491 | 79.6334 | 80.4523 | 81.2478 | 81.338 | 82.2666 | 81.5615 | 81.5615 | 81.5615 | 81.5615 | 81.5615 | 81.5615 | 81.5615 | 81.5615 | 81.5615 | 81.5615 | 81.5615 | 81.5615 | 81.5615 | 81.5615 | 81.5615 | 81.5615
95% | 2.269 | 48.604 | 64.5249 | 68.8586 | 68.7324 | 68.7277 | 69.2216 | 69.7636 | 70.8763 | 71.6758 | 72.1096 | 72.5839 | 73.0181 | 73.8027 | 74.7765 | 74.7084 | 74.7084 | 74.7084 | 74.7084 | 74.7084 | 74.7084 | 74.7084 | 74.7084 | 74.7084 | 74.7084 | 74.7084 | 74.7084 | 74.7084 | 74.7084 | 74.7084 | 74.7084 | 95% | 6.0506 | 54.1768 | 70.1297 | 74.3038 | 74.0533 | 74.071 | 74.4989 | 75.629 | 76.385 | 77.1254 | 77.9914 | 78.7935 | 79.5726 | 79.661 | 80.5703 | 79.8799 | 79.8799 | 79.8799 | 79.8799 | 79.8799 | 79.8799 | 79.8799 | 79.8799 | 79.8799 | 79.8799 | 79.8799 | 79.8799 | 79.8799 | 79.8799 | 79.8799 | 79.8799
90% | 5.6725 | 46.0459 | 61.1289 | 65.2344 | 65.1149 | 65.1105 | 65.5784 | 66.0918 | 67.1459 | 67.9034 | 68.3143 | 68.7637 | 69.175 | 69.9183 | 70.8409 | 70.7764 | 70.7764 | 70.7764 | 70.7764 | 70.7764 | 70.7764 | 70.7764 | 70.7764 | 70.7764 | 70.7764 | 70.7764 | 70.7764 | 70.7764 | 70.7764 | 70.7764 | 70.7764 | 90% | 16.2611 | 51.3254 | 66.4386 | 70.3931 | 70.1557 | 70.1725 | 70.5779 | 71.6485 | 72.3647 | 73.0662 | 73.8866 | 74.6465 | 75.3846 | 75.4683 | 76.3298 | 75.6757 | 75.6757 | 75.6757 | 75.6757 | 75.6757 | 75.6757 | 75.6757 | 75.6757 | 75.6757 | 75.6757 | 75.6757 | 75.6757 | 75.6757 | 75.6757 | 75.6757 | 75.6757
85% | 15.8829 | 43.4878 | 57.7328 | 61.6103 | 61.4974 | 61.4932 | 61.9351 | 62.42 | 63.4156 | 64.131 | 64.5191 | 64.9435 | 65.332 | 66.034 | 66.9053 | 66.8444 | 66.8444 | 66.8444 | 66.8444 | 66.8444 | 66.8444 | 66.8444 | 66.8444 | 66.8444 | 66.8444 | 66.8444 | 66.8444 | 66.8444 | 66.8444 | 66.8444 | 66.8444 | 85% | 26.4715 | 48.4739 | 62.7476 | 66.4824 | 66.2582 | 66.274 | 66.6569 | 67.6681 | 68.3445 | 69.0069 | 69.7818 | 70.4995 | 71.1965 | 71.2756 | 72.0892 | 71.4715 | 71.4715 | 71.4715 | 71.4715 | 71.4715 | 71.4715 | 71.4715 | 71.4715 | 71.4715 | 71.4715 | 71.4715 | 71.4715 | 71.4715 | 71.4715 | 71.4715 | 71.4715
80% | 31.0095 | 40.9297 | 54.3368 | 57.9862 | 57.8799 | 57.876 | 58.2919 | 58.7483 | 59.6853 | 60.3586 | 60.7239 | 61.1233 | 61.4889 | 62.1496 | 62.9697 | 62.9123 | 62.9123 | 62.9123 | 62.9123 | 62.9123 | 62.9123 | 62.9123 | 62.9123 | 62.9123 | 62.9123 | 62.9123 | 62.9123 | 62.9123 | 62.9123 | 62.9123 | 62.9123 | 80% | 34.0348 | 45.6225 | 59.0566 | 62.5716 | 62.3606 | 62.3755 | 62.7359 | 63.6876 | 64.3242 | 64.9477 | 65.677 | 66.3524 | 67.0085 | 67.0829 | 67.8487 | 67.2672 | 67.2672 | 67.2672 | 67.2672 | 67.2672 | 67.2672 | 67.2672 | 67.2672 | 67.2672 | 67.2672 | 67.2672 | 67.2672 | 67.2672 | 67.2672 | 67.2672 | 67.2672
75% | 72.9857 | 38.3716 | 50.9407 | 54.362 | 54.2624 | 54.2587 | 54.6486 | 55.0765 | 55.955 | 56.5862 | 56.9286 | 57.3031 | 57.6458 | 58.2653 | 59.0341 | 58.9803 | 58.9803 | 58.9803 | 58.9803 | 58.9803 | 58.9803 | 58.9803 | 58.9803 | 58.9803 | 58.9803 | 58.9803 | 58.9803 | 58.9803 | 58.9803 | 58.9803 | 58.9803 | 75% | 48.405 | 42.7711 | 55.3655 | 58.6609 | 58.4631 | 58.4771 | 58.8149 | 59.7071 | 60.3039 | 60.8885 | 61.5722 | 62.2054 | 62.8205 | 62.8902 | 63.6082 | 63.063 | 63.063 | 63.063 | 63.063 | 63.063 | 63.063 | 63.063 | 63.063 | 63.063 | 63.063 | 63.063 | 63.063 | 63.063 | 63.063 | 63.063 | 63.063
70% | 150.5094 | 35.8135 | 47.5447 | 50.7379 | 50.6449 | 50.6415 | 51.0054 | 51.4047 | 52.2246 | 52.8138 | 53.1334 | 53.4829 | 53.8028 | 54.3809 | 55.0984 | 55.0483 | 55.0483 | 55.0483 | 55.0483 | 55.0483 | 55.0483 | 55.0483 | 55.0483 | 55.0483 | 55.0483 | 55.0483 | 55.0483 | 55.0483 | 55.0483 | 55.0483 | 55.0483 | 70% | 76.3892 | 39.9197 | 51.6745 | 54.7502 | 54.5656 | 54.5786 | 54.8939 | 55.7266 | 56.2837 | 56.8292 | 57.4674 | 58.0584 | 58.6324 | 58.6976 | 59.3676 | 58.8588 | 58.8588 | 58.8588 | 58.8588 | 58.8588 | 58.8588 | 58.8588 | 58.8588 | 58.8588 | 58.8588 | 58.8588 | 58.8588 | 58.8588 | 58.8588 | 58.8588 | 58.8588
65% | 359.6342 | 33.2554 | 44.1486 | 47.1138 | 47.0274 | 47.0242 | 47.3621 | 47.733 | 48.4943 | 49.0414 | 49.3381 | 49.6627 | 49.9597 | 50.4966 | 51.1628 | 51.1163 | 51.1163 | 51.1163 | 51.1163 | 51.1163 | 51.1163 | 51.1163 | 51.1163 | 51.1163 | 51.1163 | 51.1163 | 51.1163 | 51.1163 | 51.1163 | 51.1163 | 51.1163 | 65% | 114.2056 | 37.0683 | 47.9835 | 50.8395 | 50.668 | 50.6801 | 50.9729 | 51.7462 | 52.2634 | 52.77 | 53.3626 | 53.9114 | 54.4444 | 54.5049 | 55.1271 | 54.6546 | 54.6546 | 54.6546 | 54.6546 | 54.6546 | 54.6546 | 54.6546 | 54.6546 | 54.6546 | 54.6546 | 54.6546 | 54.6546 | 54.6546 | 54.6546 | 54.6546 | 54.6546
60% | 689.7717 | 30.6973 | 40.7526 | 43.4896 | 43.4099 | 43.407 | 43.7189 | 44.0612 | 44.764 | 45.269 | 45.5429 | 45.8424 | 46.1167 | 46.6122 | 47.2272 | 47.1843 | 47.1843 | 47.1843 | 47.1843 | 47.1843 | 47.1843 | 47.1843 | 47.1843 | 47.1843 | 47.1843 | 47.1843 | 47.1843 | 47.1843 | 47.1843 | 47.1843 | 47.1843 | 60% | 178.1154 | 34.2169 | 44.2924 | 46.9287 | 46.7705 | 46.7817 | 47.0519 | 47.7657 | 48.2431 | 48.7108 | 49.2577 | 49.7643 | 50.2564 | 50.3122 | 50.8865 | 50.4504 | 50.4504 | 50.4504 | 50.4504 | 50.4504 | 50.4504 | 50.4504 | 50.4504 | 50.4504 | 50.4504 | 50.4504 | 50.4504 | 50.4504 | 50.4504 | 50.4504 | 50.4504
55% | 1095.5419 | 28.1392 | 37.3565 | 39.8655 | 39.7924 | 39.7897 | 40.0757 | 40.3894 | 41.0336 | 41.4965 | 41.7476 | 42.0222 | 42.2736 | 42.7279 | 43.2916 | 43.2522 | 43.2522 | 43.2522 | 43.2522 | 43.2522 | 43.2522 | 43.2522 | 43.2522 | 43.2522 | 43.2522 | 43.2522 | 43.2522 | 43.2522 | 43.2522 | 43.2522 | 43.2522 | 55% | 311.6074 | 31.3655 | 40.6014 | 43.018 | 42.8729 | 42.8832 | 43.131 | 43.7852 | 44.2229 | 44.6515 | 45.1529 | 45.6173 | 46.0683 | 46.1195 | 46.646 | 46.2462 | 46.2462 | 46.2462 | 46.2462 | 46.2462 | 46.2462 | 46.2462 | 46.2462 | 46.2462 | 46.2462 | 46.2462 | 46.2462 | 46.2462 | 46.2462 | 46.2462 | 46.2462
50% | 1666.1918 | 25.581 | 33.9605 | 36.2413 | 36.1749 | 36.1725 | 36.4324 | 36.7177 | 37.3033 | 37.7241 | 37.9524 | 38.202 | 38.4306 | 38.8435 | 39.356 | 39.3202 | 39.3202 | 39.3202 | 39.3202 | 39.3202 | 39.3202 | 39.3202 | 39.3202 | 39.3202 | 39.3202 | 39.3202 | 39.3202 | 39.3202 | 39.3202 | 39.3202 | 39.3202 | 50% | 636.0723 | 28.5141 | 36.9103 | 39.1073 | 38.9754 | 38.9847 | 39.21 | 39.8047 | 40.2026 | 40.5923 | 41.0481 | 41.4703 | 41.8803 | 41.9268 | 42.4054 | 42.042 | 42.042 | 42.042 | 42.042 | 42.042 | 42.042 | 42.042 | 42.042 | 42.042 | 42.042 | 42.042 | 42.042 | 42.042 | 42.042 | 42.042 | 42.042
45% | 2506.0947 | 23.0229 | 30.5644 | 32.6172 | 32.5574 | 32.5552 | 32.7892 | 33.0459 | 33.573 | 33.9517 | 34.1572 | 34.3818 | 34.5875 | 34.9592 | 35.4204 | 35.3882 | 35.3882 | 35.3882 | 35.3882 | 35.3882 | 35.3882 | 35.3882 | 35.3882 | 35.3882 | 35.3882 | 35.3882 | 35.3882 | 35.3882 | 35.3882 | 35.3882 | 35.3882 | 45% | 1179.4944 | 25.6627 | 33.2193 | 35.1965 | 35.0779 | 35.0862 | 35.289 | 35.8243 | 36.1824 | 36.5331 | 36.9433 | 37.3233 | 37.6923 | 37.7341 | 38.1649 | 37.8378 | 37.8378 | 37.8378 | 37.8378 | 37.8378 | 37.8378 | 37.8378 | 37.8378 | 37.8378 | 37.8378 | 37.8378 | 37.8378 | 37.8378 | 37.8378 | 37.8378 | 37.8378
40% | 3164.4787 | 20.4648 | 27.1684 | 28.9931 | 28.9399 | 28.938 | 29.1459 | 29.3741 | 29.8426 | 30.1793 | 30.3619 | 30.5616 | 30.7444 | 31.0748 | 31.4848 | 31.4562 | 31.4562 | 31.4562 | 31.4562 | 31.4562 | 31.4562 | 31.4562 | 31.4562 | 31.4562 | 31.4562 | 31.4562 | 31.4562 | 31.4562 | 31.4562 | 31.4562 | 31.4562 | 40% | 1808.3816 | 22.8113 | 29.5283 | 31.2858 | 31.1803 | 31.1878 | 31.368 | 31.8438 | 32.1621 | 32.4738 | 32.8385 | 33.1762 | 33.5042 | 33.5415 | 33.9244 | 33.6336 | 33.6336 | 33.6336 | 33.6336 | 33.6336 | 33.6336 | 33.6336 | 33.6336 | 33.6336 | 33.6336 | 33.6336 | 33.6336 | 33.6336 | 33.6336 | 33.6336 | 33.6336
35% | 3551.3408 | 17.9067 | 23.7723 | 25.3689 | 25.3224 | 25.3207 | 25.5027 | 25.7024 | 26.1123 | 26.4069 | 26.5667 | 26.7414 | 26.9014 | 27.1905 | 27.5492 | 27.5241 | 27.5241 | 27.5241 | 27.5241 | 27.5241 | 27.5241 | 27.5241 | 27.5241 | 27.5241 | 27.5241 | 27.5241 | 27.5241 | 27.5241 | 27.5241 | 27.5241 | 27.5241 | 35% | 2779.1293 | 19.9599 | 25.8372 | 27.3751 | 27.2828 | 27.2893 | 27.447 | 27.8633 | 28.1418 | 28.4146 | 28.7337 | 29.0292 | 29.3162 | 29.3488 | 29.6838 | 29.4294 | 29.4294 | 29.4294 | 29.4294 | 29.4294 | 29.4294 | 29.4294 | 29.4294 | 29.4294 | 29.4294 | 29.4294 | 29.4294 | 29.4294 | 29.4294 | 29.4294 | 29.4294
30% | 3758.953 | 15.3486 | 20.3763 | 21.7448 | 21.705 | 21.7035 | 21.8595 | 22.0306 | 22.382 | 22.6345 | 22.7714 | 22.9212 | 23.0583 | 23.3061 | 23.6136 | 23.5921 | 23.5921 | 23.5921 | 23.5921 | 23.5921 | 23.5921 | 23.5921 | 23.5921 | 23.5921 | 23.5921 | 23.5921 | 23.5921 | 23.5921 | 23.5921 | 23.5921 | 23.5921 | 30% | 3814.165 | 17.1085 | 22.1462 | 23.4644 | 23.3852 | 23.3908 | 23.526 | 23.8828 | 24.1216 | 24.3554 | 24.6289 | 24.8822 | 25.1282 | 25.1561 | 25.4433 | 25.2252 | 25.2252 | 25.2252 | 25.2252 | 25.2252 | 25.2252 | 25.2252 | 25.2252 | 25.2252 | 25.2252 | 25.2252 | 25.2252 | 25.2252 | 25.2252 | 25.2252 | 25.2252
25% | 3926.4798 | 12.7905 | 16.9802 | 18.1207 | 18.0875 | 18.0862 | 18.2162 | 18.3588 | 18.6517 | 18.8621 | 18.9762 | 19.101 | 19.2153 | 19.4218 | 19.678 | 19.6601 | 19.6601 | 19.6601 | 19.6601 | 19.6601 | 19.6601 | 19.6601 | 19.6601 | 19.6601 | 19.6601 | 19.6601 | 19.6601 | 19.6601 | 19.6601 | 19.6601 | 19.6601 | 25% | 4166.9923 | 14.257 | 18.4552 | 19.5536 | 19.4877 | 19.4924 | 19.605 | 19.9024 | 20.1013 | 20.2962 | 20.5241 | 20.7351 | 20.9402 | 20.9634 | 21.2027 | 21.021 | 21.021 | 21.021 | 21.021 | 21.021 | 21.021 | 21.021 | 21.021 | 21.021 | 21.021 | 21.021 | 21.021 | 21.021 | 21.021 | 21.021 | 21.021
20% | 4050.5177 | 10.2324 | 13.5842 | 14.4965 | 14.47 | 14.469 | 14.573 | 14.6871 | 14.9213 | 15.0897 | 15.181 | 15.2808 | 15.3722 | 15.5374 | 15.7424 | 15.7281 | 15.7281 | 15.7281 | 15.7281 | 15.7281 | 15.7281 | 15.7281 | 15.7281 | 15.7281 | 15.7281 | 15.7281 | 15.7281 | 15.7281 | 15.7281 | 15.7281 | 15.7281 | 20% | 4282.7105 | 11.4056 | 14.7641 | 15.6429 | 15.5902 | 15.5939 | 15.684 | 15.9219 | 16.081 | 16.2369 | 16.4192 | 16.5881 | 16.7521 | 16.7707 | 16.9622 | 16.8168 | 16.8168 | 16.8168 | 16.8168 | 16.8168 | 16.8168 | 16.8168 | 16.8168 | 16.8168 | 16.8168 | 16.8168 | 16.8168 | 16.8168 | 16.8168 | 16.8168 | 16.8168
15% | 4152.622 | 7.6743 | 10.1881 | 10.8724 | 10.8525 | 10.8517 | 10.9297 | 11.0153 | 11.191 | 11.3172 | 11.3857 | 11.4606 | 11.5292 | 11.6531 | 11.8068 | 11.7961 | 11.7961 | 11.7961 | 11.7961 | 11.7961 | 11.7961 | 11.7961 | 11.7961 | 11.7961 | 11.7961 | 11.7961 | 11.7961 | 11.7961 | 11.7961 | 11.7961 | 11.7961 | 15% | 4364.7722 | 8.5542 | 11.0731 | 11.7322 | 11.6926 | 11.6954 | 11.763 | 11.9414 | 12.0608 | 12.1777 | 12.3144 | 12.4411 | 12.5641 | 12.578 | 12.7216 | 12.6126 | 12.6126 | 12.6126 | 12.6126 | 12.6126 | 12.6126 | 12.6126 | 12.6126 | 12.6126 | 12.6126 | 12.6126 | 12.6126 | 12.6126 | 12.6126 | 12.6126 | 12.6126
10% | 4248.2976 | 5.1162 | 6.7921 | 7.2483 | 7.235 | 7.2345 | 7.2865 | 7.3435 | 7.4607 | 7.5448 | 7.5905 | 7.6404 | 7.6861 | 7.7687 | 7.8712 | 7.864 | 7.864 | 7.864 | 7.864 | 7.864 | 7.864 | 7.864 | 7.864 | 7.864 | 7.864 | 7.864 | 7.864 | 7.864 | 7.864 | 7.864 | 7.864 | 10% | 4391.6218 | 5.7028 | 7.3821 | 7.8215 | 7.7951 | 7.7969 | 7.842 | 7.9609 | 8.0405 | 8.1185 | 8.2096 | 8.2941 | 8.3761 | 8.3854 | 8.4811 | 8.4084 | 8.4084 | 8.4084 | 8.4084 | 8.4084 | 8.4084 | 8.4084 | 8.4084 | 8.4084 | 8.4084 | 8.4084 | 8.4084 | 8.4084 | 8.4084 | 8.4084 | 8.4084
5% | 4361.7469 | 2.5581 | 3.396 | 3.6241 | 3.6175 | 3.6172 | 3.6432 | 3.6718 | 3.7303 | 3.7724 | 3.7952 | 3.8202 | 3.8431 | 3.8844 | 3.9356 | 3.932 | 3.932 | 3.932 | 3.932 | 3.932 | 3.932 | 3.932 | 3.932 | 3.932 | 3.932 | 3.932 | 3.932 | 3.932 | 3.932 | 3.932 | 3.932 | 5% | 4391.6218 | 2.8514 | 3.691 | 3.9107 | 3.8975 | 3.8985 | 3.921 | 3.9805 | 4.0203 | 4.0592 | 4.1048 | 4.147 | 4.188 | 4.1927 | 4.2405 | 4.2042 | 4.2042 | 4.2042 | 4.2042 | 4.2042 | 4.2042 | 4.2042 | 4.2042 | 4.2042 | 4.2042 | 4.2042 | 4.2042 | 4.2042 | 4.2042 | 4.2042 | 4.2042
9.992e-14% | 4391.6218 | 5.1121e-14 | 6.7867e-14 | 7.2425e-14 | 7.2292e-14 | 7.2287e-14 | 7.2807e-14 | 7.3377e-14 | 7.4547e-14 | 7.5388e-14 | 7.5844e-14 | 7.6343e-14 | 7.68e-14 | 7.7625e-14 | 7.8649e-14 | 7.8578e-14 | 7.8578e-14 | 7.8578e-14 | 7.8578e-14 | 7.8578e-14 | 7.8578e-14 | 7.8578e-14 | 7.8578e-14 | 7.8578e-14 | 7.8578e-14 | 7.8578e-14 | 7.8578e-14 | 7.8578e-14 | 7.8578e-14 | 7.8578e-14 | 7.8578e-14 | 9.992e-14% | 4391.6218 | 5.6983e-14 | 7.3762e-14 | 7.8152e-14 | 7.7889e-14 | 7.7907e-14 | 7.8357e-14 | 7.9546e-14 | 8.0341e-14 | 8.112e-14 | 8.2031e-14 | 8.2874e-14 | 8.3694e-14 | 8.3787e-14 | 8.4743e-14 | 8.4017e-14 | 8.4017e-14 | 8.4017e-14 | 8.4017e-14 | 8.4017e-14 | 8.4017e-14 | 8.4017e-14 | 8.4017e-14 | 8.4017e-14 | 8.4017e-14 | 8.4017e-14 | 8.4017e-14 | 8.4017e-14 | 8.4017e-14 | 8.4017e-14 | 8.4017e-14
Option 7
Winter Season | [31 empty] | Winter Season
P50 | [31 empty] | P10
% of MD | Winter - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Winter - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 45.0311 | 62.4376 | 66.9594 | 67.7285 | 68.3267 | 69.3603 | 71.7146 | 73.2888 | 75.2849 | 76.3199 | 77.2291 | 75.5455 | 77.5138 | 80.6095 | 78.2564 | 78.2564 | 78.2564 | 78.2564 | 78.2564 | 78.2564 | 78.2564 | 78.2564 | 78.2564 | 78.2564 | 78.2564 | 78.2564 | 78.2564 | 78.2564 | 78.2564 | 78.2564 | 100% | 0 | 48.1978 | 65.3847 | 70.0831 | 70.8084 | 71.267 | 72.2781 | 74.6693 | 75.9727 | 78.4597 | 86.0243 | 79.7829 | 78.5605 | 80.2054 | 83.8053 | 81.3648 | 81.3648 | 81.3648 | 81.3648 | 81.3648 | 81.3648 | 81.3648 | 81.3648 | 81.3648 | 81.3648 | 81.3648 | 81.3648 | 81.3648 | 81.3648 | 81.3648 | 81.3648
99% | 1.486 | 44.5808 | 61.8132 | 66.2898 | 67.0512 | 67.6435 | 68.6667 | 70.9975 | 72.5559 | 74.532 | 75.5567 | 76.4569 | 74.7901 | 76.7387 | 79.8034 | 77.4739 | 77.4739 | 77.4739 | 77.4739 | 77.4739 | 77.4739 | 77.4739 | 77.4739 | 77.4739 | 77.4739 | 77.4739 | 77.4739 | 77.4739 | 77.4739 | 77.4739 | 77.4739 | 99% | 1.486 | 47.7158 | 64.7309 | 69.3823 | 70.1003 | 70.5543 | 71.5553 | 73.9226 | 75.2129 | 77.6751 | 85.1641 | 78.9851 | 77.7749 | 79.4033 | 82.9672 | 80.5512 | 80.5512 | 80.5512 | 80.5512 | 80.5512 | 80.5512 | 80.5512 | 80.5512 | 80.5512 | 80.5512 | 80.5512 | 80.5512 | 80.5512 | 80.5512 | 80.5512 | 80.5512
98% | 3.2692 | 44.1305 | 61.1889 | 65.6202 | 66.3739 | 66.9602 | 67.9731 | 70.2804 | 71.823 | 73.7792 | 74.7935 | 75.6846 | 74.0346 | 75.9636 | 78.9973 | 76.6913 | 76.6913 | 76.6913 | 76.6913 | 76.6913 | 76.6913 | 76.6913 | 76.6913 | 76.6913 | 76.6913 | 76.6913 | 76.6913 | 76.6913 | 76.6913 | 76.6913 | 76.6913 | 98% | 3.2692 | 47.2338 | 64.0771 | 68.6815 | 69.3922 | 69.8416 | 70.8325 | 73.1759 | 74.4532 | 76.8905 | 84.3038 | 78.1873 | 76.9893 | 78.6013 | 82.1292 | 79.7375 | 79.7375 | 79.7375 | 79.7375 | 79.7375 | 79.7375 | 79.7375 | 79.7375 | 79.7375 | 79.7375 | 79.7375 | 79.7375 | 79.7375 | 79.7375 | 79.7375 | 79.7375
97% | 6.8356 | 43.6802 | 60.5645 | 64.9506 | 65.6966 | 66.2769 | 67.2795 | 69.5632 | 71.0901 | 73.0263 | 74.0303 | 74.9123 | 73.2792 | 75.1884 | 78.1912 | 75.9087 | 75.9087 | 75.9087 | 75.9087 | 75.9087 | 75.9087 | 75.9087 | 75.9087 | 75.9087 | 75.9087 | 75.9087 | 75.9087 | 75.9087 | 75.9087 | 75.9087 | 75.9087 | 97% | 6.8356 | 46.7518 | 63.4232 | 67.9806 | 68.6841 | 69.129 | 70.1097 | 72.4292 | 73.6935 | 76.1059 | 83.4436 | 77.3894 | 76.2037 | 77.7992 | 81.2911 | 78.9239 | 78.9239 | 78.9239 | 78.9239 | 78.9239 | 78.9239 | 78.9239 | 78.9239 | 78.9239 | 78.9239 | 78.9239 | 78.9239 | 78.9239 | 78.9239 | 78.9239 | 78.9239
95% | 17.5347 | 42.7796 | 59.3157 | 63.6114 | 64.342 | 64.9104 | 65.8923 | 68.1289 | 69.6243 | 71.5207 | 72.5039 | 73.3677 | 71.7683 | 73.6382 | 76.579 | 74.3436 | 74.3436 | 74.3436 | 74.3436 | 74.3436 | 74.3436 | 74.3436 | 74.3436 | 74.3436 | 74.3436 | 74.3436 | 74.3436 | 74.3436 | 74.3436 | 74.3436 | 74.3436 | 95% | 17.5347 | 45.7879 | 62.1155 | 66.579 | 67.268 | 67.7036 | 68.6642 | 70.9358 | 72.174 | 74.5368 | 81.7231 | 75.7938 | 74.6325 | 76.1951 | 79.615 | 77.2966 | 77.2966 | 77.2966 | 77.2966 | 77.2966 | 77.2966 | 77.2966 | 77.2966 | 77.2966 | 77.2966 | 77.2966 | 77.2966 | 77.2966 | 77.2966 | 77.2966 | 77.2966
90% | 78.7576 | 40.528 | 56.1939 | 60.2634 | 60.9556 | 61.4941 | 62.4243 | 64.5432 | 65.9599 | 67.7564 | 68.6879 | 69.5062 | 67.991 | 69.7625 | 72.5486 | 70.4308 | 70.4308 | 70.4308 | 70.4308 | 70.4308 | 70.4308 | 70.4308 | 70.4308 | 70.4308 | 70.4308 | 70.4308 | 70.4308 | 70.4308 | 70.4308 | 70.4308 | 70.4308 | 90% | 78.7576 | 43.378 | 58.8463 | 63.0748 | 63.7275 | 64.1403 | 65.0503 | 67.2023 | 68.3754 | 70.6138 | 77.4219 | 71.8046 | 70.7045 | 72.1848 | 75.4247 | 73.2283 | 73.2283 | 73.2283 | 73.2283 | 73.2283 | 73.2283 | 73.2283 | 73.2283 | 73.2283 | 73.2283 | 73.2283 | 73.2283 | 73.2283 | 73.2283 | 73.2283 | 73.2283
85% | 236.8672 | 38.2764 | 53.072 | 56.9155 | 57.5692 | 58.0777 | 58.9563 | 60.9575 | 62.2954 | 63.9922 | 64.8719 | 65.6448 | 64.2137 | 65.8868 | 68.5181 | 66.518 | 66.518 | 66.518 | 66.518 | 66.518 | 66.518 | 66.518 | 66.518 | 66.518 | 66.518 | 66.518 | 66.518 | 66.518 | 66.518 | 66.518 | 66.518 | 85% | 236.8672 | 40.9681 | 55.577 | 59.5707 | 60.1871 | 60.5769 | 61.4364 | 63.4689 | 64.5768 | 66.6908 | 73.1207 | 67.8155 | 66.7765 | 68.1746 | 71.2345 | 69.1601 | 69.1601 | 69.1601 | 69.1601 | 69.1601 | 69.1601 | 69.1601 | 69.1601 | 69.1601 | 69.1601 | 69.1601 | 69.1601 | 69.1601 | 69.1601 | 69.1601 | 69.1601
80% | 497.5104 | 36.0249 | 49.9501 | 53.5675 | 54.1828 | 54.6614 | 55.4882 | 57.3717 | 58.631 | 60.2279 | 61.056 | 61.7833 | 60.4364 | 62.0111 | 64.4876 | 62.6051 | 62.6051 | 62.6051 | 62.6051 | 62.6051 | 62.6051 | 62.6051 | 62.6051 | 62.6051 | 62.6051 | 62.6051 | 62.6051 | 62.6051 | 62.6051 | 62.6051 | 62.6051 | 80% | 497.5104 | 38.5582 | 52.3078 | 56.0665 | 56.6467 | 57.0136 | 57.8225 | 59.7354 | 60.7781 | 62.7678 | 68.8195 | 63.8263 | 62.8484 | 64.1643 | 67.0442 | 65.0919 | 65.0919 | 65.0919 | 65.0919 | 65.0919 | 65.0919 | 65.0919 | 65.0919 | 65.0919 | 65.0919 | 65.0919 | 65.0919 | 65.0919 | 65.0919 | 65.0919 | 65.0919
75% | 803.6248 | 33.7733 | 46.8282 | 50.2195 | 50.7964 | 51.245 | 52.0202 | 53.786 | 54.9666 | 56.4637 | 57.24 | 57.9219 | 56.6592 | 58.1354 | 60.4571 | 58.6923 | 58.6923 | 58.6923 | 58.6923 | 58.6923 | 58.6923 | 58.6923 | 58.6923 | 58.6923 | 58.6923 | 58.6923 | 58.6923 | 58.6923 | 58.6923 | 58.6923 | 58.6923 | 75% | 803.6248 | 36.1483 | 49.0386 | 52.5623 | 53.1063 | 53.4502 | 54.2086 | 56.0019 | 56.9795 | 58.8448 | 64.5182 | 59.8372 | 58.9204 | 60.154 | 62.8539 | 61.0236 | 61.0236 | 61.0236 | 61.0236 | 61.0236 | 61.0236 | 61.0236 | 61.0236 | 61.0236 | 61.0236 | 61.0236 | 61.0236 | 61.0236 | 61.0236 | 61.0236 | 61.0236
70% | 1155.2107 | 31.5218 | 43.7063 | 46.8715 | 47.4099 | 47.8287 | 48.5522 | 50.2003 | 51.3021 | 52.6994 | 53.424 | 54.0604 | 52.8819 | 54.2597 | 56.4267 | 54.7795 | 54.7795 | 54.7795 | 54.7795 | 54.7795 | 54.7795 | 54.7795 | 54.7795 | 54.7795 | 54.7795 | 54.7795 | 54.7795 | 54.7795 | 54.7795 | 54.7795 | 54.7795 | 70% | 1155.2107 | 33.7384 | 45.7693 | 49.0582 | 49.5659 | 49.8869 | 50.5947 | 52.2685 | 53.1809 | 54.9218 | 60.217 | 55.8481 | 54.9924 | 56.1438 | 58.6637 | 56.9554 | 56.9554 | 56.9554 | 56.9554 | 56.9554 | 56.9554 | 56.9554 | 56.9554 | 56.9554 | 56.9554 | 56.9554 | 56.9554 | 56.9554 | 56.9554 | 56.9554 | 56.9554
65% | 1553.1596 | 29.2702 | 40.5844 | 43.5236 | 44.0235 | 44.4124 | 45.0842 | 46.6145 | 47.6377 | 48.9352 | 49.608 | 50.1989 | 49.1046 | 50.384 | 52.3962 | 50.8667 | 50.8667 | 50.8667 | 50.8667 | 50.8667 | 50.8667 | 50.8667 | 50.8667 | 50.8667 | 50.8667 | 50.8667 | 50.8667 | 50.8667 | 50.8667 | 50.8667 | 50.8667 | 65% | 1553.1596 | 31.3286 | 42.5001 | 45.554 | 46.0254 | 46.3235 | 46.9808 | 48.535 | 49.3822 | 50.9988 | 55.9158 | 51.8589 | 51.0643 | 52.1335 | 54.4734 | 52.8871 | 52.8871 | 52.8871 | 52.8871 | 52.8871 | 52.8871 | 52.8871 | 52.8871 | 52.8871 | 52.8871 | 52.8871 | 52.8871 | 52.8871 | 52.8871 | 52.8871 | 52.8871
60% | 2026.2996 | 27.0187 | 37.4626 | 40.1756 | 40.6371 | 40.996 | 41.6162 | 43.0288 | 43.9733 | 45.1709 | 45.792 | 46.3375 | 45.3273 | 46.5083 | 48.3657 | 46.9539 | 46.9539 | 46.9539 | 46.9539 | 46.9539 | 46.9539 | 46.9539 | 46.9539 | 46.9539 | 46.9539 | 46.9539 | 46.9539 | 46.9539 | 46.9539 | 46.9539 | 46.9539 | 60% | 2026.2996 | 28.9187 | 39.2308 | 42.0499 | 42.485 | 42.7602 | 43.3669 | 44.8016 | 45.5836 | 47.0758 | 51.6146 | 47.8698 | 47.1363 | 48.1232 | 50.2832 | 48.8189 | 48.8189 | 48.8189 | 48.8189 | 48.8189 | 48.8189 | 48.8189 | 48.8189 | 48.8189 | 48.8189 | 48.8189 | 48.8189 | 48.8189 | 48.8189 | 48.8189 | 48.8189
55% | 2598.4068 | 24.7671 | 34.3407 | 36.8276 | 37.2507 | 37.5797 | 38.1482 | 39.4431 | 40.3088 | 41.4067 | 41.976 | 42.476 | 41.55 | 42.6326 | 44.3352 | 43.041 | 43.041 | 43.041 | 43.041 | 43.041 | 43.041 | 43.041 | 43.041 | 43.041 | 43.041 | 43.041 | 43.041 | 43.041 | 43.041 | 43.041 | 43.041 | 55% | 2598.4068 | 26.5088 | 35.9616 | 38.5457 | 38.9446 | 39.1968 | 39.753 | 41.0681 | 41.785 | 43.1529 | 47.3134 | 43.8806 | 43.2083 | 44.113 | 46.0929 | 44.7507 | 44.7507 | 44.7507 | 44.7507 | 44.7507 | 44.7507 | 44.7507 | 44.7507 | 44.7507 | 44.7507 | 44.7507 | 44.7507 | 44.7507 | 44.7507 | 44.7507 | 44.7507
50% | 3233.5201 | 22.5156 | 31.2188 | 33.4797 | 33.8642 | 34.1634 | 34.6802 | 35.8573 | 36.6444 | 37.6424 | 38.16 | 38.6146 | 37.7728 | 38.7569 | 40.3048 | 39.1282 | 39.1282 | 39.1282 | 39.1282 | 39.1282 | 39.1282 | 39.1282 | 39.1282 | 39.1282 | 39.1282 | 39.1282 | 39.1282 | 39.1282 | 39.1282 | 39.1282 | 39.1282 | 50% | 3233.5201 | 24.0989 | 32.6924 | 35.0416 | 35.4042 | 35.6335 | 36.139 | 37.3346 | 37.9863 | 39.2299 | 43.0122 | 39.8915 | 39.2803 | 40.1027 | 41.9026 | 40.6824 | 40.6824 | 40.6824 | 40.6824 | 40.6824 | 40.6824 | 40.6824 | 40.6824 | 40.6824 | 40.6824 | 40.6824 | 40.6824 | 40.6824 | 40.6824 | 40.6824 | 40.6824
45% | 3775.313 | 20.264 | 28.0969 | 30.1317 | 30.4778 | 30.747 | 31.2121 | 32.2716 | 32.9799 | 33.8782 | 34.344 | 34.7531 | 33.9955 | 34.8812 | 36.2743 | 35.2154 | 35.2154 | 35.2154 | 35.2154 | 35.2154 | 35.2154 | 35.2154 | 35.2154 | 35.2154 | 35.2154 | 35.2154 | 35.2154 | 35.2154 | 35.2154 | 35.2154 | 35.2154 | 45% | 3775.313 | 21.689 | 29.4231 | 31.5374 | 31.8638 | 32.0701 | 32.5251 | 33.6012 | 34.1877 | 35.3069 | 38.7109 | 35.9023 | 35.3522 | 36.0924 | 37.7124 | 36.6142 | 36.6142 | 36.6142 | 36.6142 | 36.6142 | 36.6142 | 36.6142 | 36.6142 | 36.6142 | 36.6142 | 36.6142 | 36.6142 | 36.6142 | 36.6142 | 36.6142 | 36.6142
40% | 4072.8088 | 18.0124 | 24.975 | 26.7837 | 27.0914 | 27.3307 | 27.7441 | 28.6859 | 29.3155 | 30.114 | 30.528 | 30.8917 | 30.2182 | 31.0055 | 32.2438 | 31.3026 | 31.3026 | 31.3026 | 31.3026 | 31.3026 | 31.3026 | 31.3026 | 31.3026 | 31.3026 | 31.3026 | 31.3026 | 31.3026 | 31.3026 | 31.3026 | 31.3026 | 31.3026 | 40% | 4072.8088 | 19.2791 | 26.1539 | 28.0332 | 28.3234 | 28.5068 | 28.9112 | 29.8677 | 30.3891 | 31.3839 | 34.4097 | 31.9132 | 31.4242 | 32.0822 | 33.5221 | 32.5459 | 32.5459 | 32.5459 | 32.5459 | 32.5459 | 32.5459 | 32.5459 | 32.5459 | 32.5459 | 32.5459 | 32.5459 | 32.5459 | 32.5459 | 32.5459 | 32.5459 | 32.5459
35% | 4198.821 | 15.7609 | 21.8532 | 23.4358 | 23.705 | 23.9144 | 24.2761 | 25.1001 | 25.6511 | 26.3497 | 26.712 | 27.0302 | 26.4409 | 27.1298 | 28.2133 | 27.3897 | 27.3897 | 27.3897 | 27.3897 | 27.3897 | 27.3897 | 27.3897 | 27.3897 | 27.3897 | 27.3897 | 27.3897 | 27.3897 | 27.3897 | 27.3897 | 27.3897 | 27.3897 | 35% | 4198.821 | 16.8692 | 22.8847 | 24.5291 | 24.7829 | 24.9434 | 25.2973 | 26.1342 | 26.5904 | 27.4609 | 30.1085 | 27.924 | 27.4962 | 28.0719 | 29.3318 | 28.4777 | 28.4777 | 28.4777 | 28.4777 | 28.4777 | 28.4777 | 28.4777 | 28.4777 | 28.4777 | 28.4777 | 28.4777 | 28.4777 | 28.4777 | 28.4777 | 28.4777 | 28.4777
30% | 4271.3374 | 13.5093 | 18.7313 | 20.0878 | 20.3185 | 20.498 | 20.8081 | 21.5144 | 21.9866 | 22.5855 | 22.896 | 23.1687 | 22.6637 | 23.2542 | 24.1829 | 23.4769 | 23.4769 | 23.4769 | 23.4769 | 23.4769 | 23.4769 | 23.4769 | 23.4769 | 23.4769 | 23.4769 | 23.4769 | 23.4769 | 23.4769 | 23.4769 | 23.4769 | 23.4769 | 30% | 4271.3374 | 14.4593 | 19.6154 | 21.0249 | 21.2425 | 21.3801 | 21.6834 | 22.4008 | 22.7918 | 23.5379 | 25.8073 | 23.9349 | 23.5682 | 24.0616 | 25.1416 | 24.4094 | 24.4094 | 24.4094 | 24.4094 | 24.4094 | 24.4094 | 24.4094 | 24.4094 | 24.4094 | 24.4094 | 24.4094 | 24.4094 | 24.4094 | 24.4094 | 24.4094 | 24.4094
25% | 4321.8611 | 11.2578 | 15.6094 | 16.7398 | 16.9321 | 17.0817 | 17.3401 | 17.9287 | 18.3222 | 18.8212 | 19.08 | 19.3073 | 18.8864 | 19.3785 | 20.1524 | 19.5641 | 19.5641 | 19.5641 | 19.5641 | 19.5641 | 19.5641 | 19.5641 | 19.5641 | 19.5641 | 19.5641 | 19.5641 | 19.5641 | 19.5641 | 19.5641 | 19.5641 | 19.5641 | 25% | 4321.8611 | 12.0494 | 16.3462 | 17.5208 | 17.7021 | 17.8167 | 18.0695 | 18.6673 | 18.9932 | 19.6149 | 21.5061 | 19.9457 | 19.6401 | 20.0513 | 20.9513 | 20.3412 | 20.3412 | 20.3412 | 20.3412 | 20.3412 | 20.3412 | 20.3412 | 20.3412 | 20.3412 | 20.3412 | 20.3412 | 20.3412 | 20.3412 | 20.3412 | 20.3412 | 20.3412
20% | 4353.067 | 9.0062 | 12.4875 | 13.3919 | 13.5457 | 13.6653 | 13.8721 | 14.3429 | 14.6578 | 15.057 | 15.264 | 15.4458 | 15.1091 | 15.5028 | 16.1219 | 15.6513 | 15.6513 | 15.6513 | 15.6513 | 15.6513 | 15.6513 | 15.6513 | 15.6513 | 15.6513 | 15.6513 | 15.6513 | 15.6513 | 15.6513 | 15.6513 | 15.6513 | 15.6513 | 20% | 4353.067 | 9.6396 | 13.0769 | 14.0166 | 14.1617 | 14.2534 | 14.4556 | 14.9339 | 15.1945 | 15.6919 | 17.2049 | 15.9566 | 15.7121 | 16.0411 | 16.7611 | 16.273 | 16.273 | 16.273 | 16.273 | 16.273 | 16.273 | 16.273 | 16.273 | 16.273 | 16.273 | 16.273 | 16.273 | 16.273 | 16.273 | 16.273 | 16.273
15% | 4369.4129 | 6.7547 | 9.3656 | 10.0439 | 10.1593 | 10.249 | 10.404 | 10.7572 | 10.9933 | 11.2927 | 11.448 | 11.5844 | 11.3318 | 11.6271 | 12.0914 | 11.7385 | 11.7385 | 11.7385 | 11.7385 | 11.7385 | 11.7385 | 11.7385 | 11.7385 | 11.7385 | 11.7385 | 11.7385 | 11.7385 | 11.7385 | 11.7385 | 11.7385 | 11.7385 | 15% | 4369.4129 | 7.2297 | 9.8077 | 10.5125 | 10.6213 | 10.69 | 10.8417 | 11.2004 | 11.3959 | 11.769 | 12.9036 | 11.9674 | 11.7841 | 12.0308 | 12.5708 | 12.2047 | 12.2047 | 12.2047 | 12.2047 | 12.2047 | 12.2047 | 12.2047 | 12.2047 | 12.2047 | 12.2047 | 12.2047 | 12.2047 | 12.2047 | 12.2047 | 12.2047 | 12.2047
10% | 4378.6261 | 4.5031 | 6.2438 | 6.6959 | 6.7728 | 6.8327 | 6.936 | 7.1715 | 7.3289 | 7.5285 | 7.632 | 7.7229 | 7.5546 | 7.7514 | 8.061 | 7.8256 | 7.8256 | 7.8256 | 7.8256 | 7.8256 | 7.8256 | 7.8256 | 7.8256 | 7.8256 | 7.8256 | 7.8256 | 7.8256 | 7.8256 | 7.8256 | 7.8256 | 7.8256 | 10% | 4378.6261 | 4.8198 | 6.5385 | 7.0083 | 7.0808 | 7.1267 | 7.2278 | 7.4669 | 7.5973 | 7.846 | 8.6024 | 7.9783 | 7.8561 | 8.0205 | 8.3805 | 8.1365 | 8.1365 | 8.1365 | 8.1365 | 8.1365 | 8.1365 | 8.1365 | 8.1365 | 8.1365 | 8.1365 | 8.1365 | 8.1365 | 8.1365 | 8.1365 | 8.1365 | 8.1365
5% | 4391.7028 | 2.2516 | 3.1219 | 3.348 | 3.3864 | 3.4163 | 3.468 | 3.5857 | 3.6644 | 3.7642 | 3.816 | 3.8615 | 3.7773 | 3.8757 | 4.0305 | 3.9128 | 3.9128 | 3.9128 | 3.9128 | 3.9128 | 3.9128 | 3.9128 | 3.9128 | 3.9128 | 3.9128 | 3.9128 | 3.9128 | 3.9128 | 3.9128 | 3.9128 | 3.9128 | 5% | 4391.7028 | 2.4099 | 3.2692 | 3.5042 | 3.5404 | 3.5633 | 3.6139 | 3.7335 | 3.7986 | 3.923 | 4.3012 | 3.9891 | 3.928 | 4.0103 | 4.1903 | 4.0682 | 4.0682 | 4.0682 | 4.0682 | 4.0682 | 4.0682 | 4.0682 | 4.0682 | 4.0682 | 4.0682 | 4.0682 | 4.0682 | 4.0682 | 4.0682 | 4.0682 | 4.0682
9.992e-14% | 4391.7028 | 4.4995e-14 | 6.2388e-14 | 6.6906e-14 | 6.7674e-14 | 6.8272e-14 | 6.9305e-14 | 7.1657e-14 | 7.323e-14 | 7.5225e-14 | 7.6259e-14 | 7.7167e-14 | 7.5485e-14 | 7.7452e-14 | 8.0545e-14 | 7.8194e-14 | 7.8194e-14 | 7.8194e-14 | 7.8194e-14 | 7.8194e-14 | 7.8194e-14 | 7.8194e-14 | 7.8194e-14 | 7.8194e-14 | 7.8194e-14 | 7.8194e-14 | 7.8194e-14 | 7.8194e-14 | 7.8194e-14 | 7.8194e-14 | 7.8194e-14 | 9.992e-14% | 4391.7028 | 4.8159e-14 | 6.5332e-14 | 7.0027e-14 | 7.0752e-14 | 7.121e-14 | 7.222e-14 | 7.461e-14 | 7.5912e-14 | 7.8397e-14 | 8.5956e-14 | 7.9719e-14 | 7.8498e-14 | 8.0141e-14 | 8.3738e-14 | 8.13e-14 | 8.13e-14 | 8.13e-14 | 8.13e-14 | 8.13e-14 | 8.13e-14 | 8.13e-14 | 8.13e-14 | 8.13e-14 | 8.13e-14 | 8.13e-14 | 8.13e-14 | 8.13e-14 | 8.13e-14 | 8.13e-14 | 8.13e-14
Summer Season | [31 empty] | Summer Season
P50 | [31 empty] | P10
% of MD | Summer - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Summer - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 51.1621 | 67.921 | 72.4827 | 72.3498 | 72.345 | 72.8648 | 73.4353 | 74.6066 | 75.4483 | 75.9048 | 76.4041 | 76.8611 | 77.687 | 78.7121 | 78.6404 | 78.6404 | 78.6404 | 78.6404 | 78.6404 | 78.6404 | 78.6404 | 78.6404 | 78.6404 | 78.6404 | 78.6404 | 78.6404 | 78.6404 | 78.6404 | 78.6404 | 78.6404 | 100% | 0 | 57.0282 | 73.8207 | 78.2145 | 77.9508 | 77.9694 | 78.4199 | 79.6095 | 80.4052 | 81.1846 | 82.0962 | 82.9406 | 83.7606 | 83.8537 | 84.8109 | 84.0841 | 84.0841 | 84.0841 | 84.0841 | 84.0841 | 84.0841 | 84.0841 | 84.0841 | 84.0841 | 84.0841 | 84.0841 | 84.0841 | 84.0841 | 84.0841 | 84.0841 | 84.0841
99% | 0 | 50.6505 | 67.2418 | 71.7579 | 71.6263 | 71.6215 | 72.1362 | 72.701 | 73.8605 | 74.6938 | 75.1458 | 75.64 | 76.0925 | 76.9101 | 77.9249 | 77.854 | 77.854 | 77.854 | 77.854 | 77.854 | 77.854 | 77.854 | 77.854 | 77.854 | 77.854 | 77.854 | 77.854 | 77.854 | 77.854 | 77.854 | 77.854 | 99% | 1.5127 | 56.4579 | 73.0825 | 77.4324 | 77.1713 | 77.1897 | 77.6357 | 78.8134 | 79.6012 | 80.3728 | 81.2753 | 82.1112 | 82.923 | 83.0151 | 83.9628 | 83.2432 | 83.2432 | 83.2432 | 83.2432 | 83.2432 | 83.2432 | 83.2432 | 83.2432 | 83.2432 | 83.2432 | 83.2432 | 83.2432 | 83.2432 | 83.2432 | 83.2432 | 83.2432
98% | 0 | 50.1389 | 66.5626 | 71.033 | 70.9028 | 70.8981 | 71.4075 | 71.9666 | 73.1145 | 73.9393 | 74.3867 | 74.876 | 75.3239 | 76.1333 | 77.1378 | 77.0676 | 77.0676 | 77.0676 | 77.0676 | 77.0676 | 77.0676 | 77.0676 | 77.0676 | 77.0676 | 77.0676 | 77.0676 | 77.0676 | 77.0676 | 77.0676 | 77.0676 | 77.0676 | 98% | 2.269 | 55.8876 | 72.3443 | 76.6503 | 76.3918 | 76.41 | 76.8515 | 78.0173 | 78.7971 | 79.5609 | 80.4543 | 81.2818 | 82.0854 | 82.1766 | 83.1147 | 82.4024 | 82.4024 | 82.4024 | 82.4024 | 82.4024 | 82.4024 | 82.4024 | 82.4024 | 82.4024 | 82.4024 | 82.4024 | 82.4024 | 82.4024 | 82.4024 | 82.4024 | 82.4024
97% | 0.37816 | 49.6272 | 65.8834 | 70.3082 | 70.1794 | 70.1746 | 70.6789 | 71.2323 | 72.3684 | 73.1848 | 73.6277 | 74.112 | 74.5553 | 75.3564 | 76.3507 | 76.2812 | 76.2812 | 76.2812 | 76.2812 | 76.2812 | 76.2812 | 76.2812 | 76.2812 | 76.2812 | 76.2812 | 76.2812 | 76.2812 | 76.2812 | 76.2812 | 76.2812 | 76.2812 | 97% | 3.7816 | 55.3173 | 71.6061 | 75.8681 | 75.6123 | 75.6303 | 76.0673 | 77.2212 | 77.9931 | 78.7491 | 79.6334 | 80.4523 | 81.2478 | 81.338 | 82.2666 | 81.5615 | 81.5615 | 81.5615 | 81.5615 | 81.5615 | 81.5615 | 81.5615 | 81.5615 | 81.5615 | 81.5615 | 81.5615 | 81.5615 | 81.5615 | 81.5615 | 81.5615 | 81.5615
95% | 2.269 | 48.604 | 64.5249 | 68.8586 | 68.7324 | 68.7277 | 69.2216 | 69.7636 | 70.8763 | 71.6758 | 72.1096 | 72.5839 | 73.0181 | 73.8027 | 74.7765 | 74.7084 | 74.7084 | 74.7084 | 74.7084 | 74.7084 | 74.7084 | 74.7084 | 74.7084 | 74.7084 | 74.7084 | 74.7084 | 74.7084 | 74.7084 | 74.7084 | 74.7084 | 74.7084 | 95% | 6.0506 | 54.1768 | 70.1297 | 74.3038 | 74.0533 | 74.071 | 74.4989 | 75.629 | 76.385 | 77.1254 | 77.9914 | 78.7935 | 79.5726 | 79.661 | 80.5703 | 79.8799 | 79.8799 | 79.8799 | 79.8799 | 79.8799 | 79.8799 | 79.8799 | 79.8799 | 79.8799 | 79.8799 | 79.8799 | 79.8799 | 79.8799 | 79.8799 | 79.8799 | 79.8799
90% | 5.6725 | 46.0459 | 61.1289 | 65.2344 | 65.1149 | 65.1105 | 65.5784 | 66.0918 | 67.1459 | 67.9034 | 68.3143 | 68.7637 | 69.175 | 69.9183 | 70.8409 | 70.7764 | 70.7764 | 70.7764 | 70.7764 | 70.7764 | 70.7764 | 70.7764 | 70.7764 | 70.7764 | 70.7764 | 70.7764 | 70.7764 | 70.7764 | 70.7764 | 70.7764 | 70.7764 | 90% | 16.2611 | 51.3254 | 66.4386 | 70.3931 | 70.1557 | 70.1725 | 70.5779 | 71.6485 | 72.3647 | 73.0662 | 73.8866 | 74.6465 | 75.3846 | 75.4683 | 76.3298 | 75.6757 | 75.6757 | 75.6757 | 75.6757 | 75.6757 | 75.6757 | 75.6757 | 75.6757 | 75.6757 | 75.6757 | 75.6757 | 75.6757 | 75.6757 | 75.6757 | 75.6757 | 75.6757
85% | 15.8829 | 43.4878 | 57.7328 | 61.6103 | 61.4974 | 61.4932 | 61.9351 | 62.42 | 63.4156 | 64.131 | 64.5191 | 64.9435 | 65.332 | 66.034 | 66.9053 | 66.8444 | 66.8444 | 66.8444 | 66.8444 | 66.8444 | 66.8444 | 66.8444 | 66.8444 | 66.8444 | 66.8444 | 66.8444 | 66.8444 | 66.8444 | 66.8444 | 66.8444 | 66.8444 | 85% | 26.4715 | 48.4739 | 62.7476 | 66.4824 | 66.2582 | 66.274 | 66.6569 | 67.6681 | 68.3445 | 69.0069 | 69.7818 | 70.4995 | 71.1965 | 71.2756 | 72.0892 | 71.4715 | 71.4715 | 71.4715 | 71.4715 | 71.4715 | 71.4715 | 71.4715 | 71.4715 | 71.4715 | 71.4715 | 71.4715 | 71.4715 | 71.4715 | 71.4715 | 71.4715 | 71.4715
80% | 31.0095 | 40.9297 | 54.3368 | 57.9862 | 57.8799 | 57.876 | 58.2919 | 58.7483 | 59.6853 | 60.3586 | 60.7239 | 61.1233 | 61.4889 | 62.1496 | 62.9697 | 62.9123 | 62.9123 | 62.9123 | 62.9123 | 62.9123 | 62.9123 | 62.9123 | 62.9123 | 62.9123 | 62.9123 | 62.9123 | 62.9123 | 62.9123 | 62.9123 | 62.9123 | 62.9123 | 80% | 34.0348 | 45.6225 | 59.0566 | 62.5716 | 62.3606 | 62.3755 | 62.7359 | 63.6876 | 64.3242 | 64.9477 | 65.677 | 66.3524 | 67.0085 | 67.0829 | 67.8487 | 67.2672 | 67.2672 | 67.2672 | 67.2672 | 67.2672 | 67.2672 | 67.2672 | 67.2672 | 67.2672 | 67.2672 | 67.2672 | 67.2672 | 67.2672 | 67.2672 | 67.2672 | 67.2672
75% | 72.9857 | 38.3716 | 50.9407 | 54.362 | 54.2624 | 54.2587 | 54.6486 | 55.0765 | 55.955 | 56.5862 | 56.9286 | 57.3031 | 57.6458 | 58.2653 | 59.0341 | 58.9803 | 58.9803 | 58.9803 | 58.9803 | 58.9803 | 58.9803 | 58.9803 | 58.9803 | 58.9803 | 58.9803 | 58.9803 | 58.9803 | 58.9803 | 58.9803 | 58.9803 | 58.9803 | 75% | 48.405 | 42.7711 | 55.3655 | 58.6609 | 58.4631 | 58.4771 | 58.8149 | 59.7071 | 60.3039 | 60.8885 | 61.5722 | 62.2054 | 62.8205 | 62.8902 | 63.6082 | 63.063 | 63.063 | 63.063 | 63.063 | 63.063 | 63.063 | 63.063 | 63.063 | 63.063 | 63.063 | 63.063 | 63.063 | 63.063 | 63.063 | 63.063 | 63.063
70% | 150.5094 | 35.8135 | 47.5447 | 50.7379 | 50.6449 | 50.6415 | 51.0054 | 51.4047 | 52.2246 | 52.8138 | 53.1334 | 53.4829 | 53.8028 | 54.3809 | 55.0984 | 55.0483 | 55.0483 | 55.0483 | 55.0483 | 55.0483 | 55.0483 | 55.0483 | 55.0483 | 55.0483 | 55.0483 | 55.0483 | 55.0483 | 55.0483 | 55.0483 | 55.0483 | 55.0483 | 70% | 76.3892 | 39.9197 | 51.6745 | 54.7502 | 54.5656 | 54.5786 | 54.8939 | 55.7266 | 56.2837 | 56.8292 | 57.4674 | 58.0584 | 58.6324 | 58.6976 | 59.3676 | 58.8588 | 58.8588 | 58.8588 | 58.8588 | 58.8588 | 58.8588 | 58.8588 | 58.8588 | 58.8588 | 58.8588 | 58.8588 | 58.8588 | 58.8588 | 58.8588 | 58.8588 | 58.8588
65% | 359.6342 | 33.2554 | 44.1486 | 47.1138 | 47.0274 | 47.0242 | 47.3621 | 47.733 | 48.4943 | 49.0414 | 49.3381 | 49.6627 | 49.9597 | 50.4966 | 51.1628 | 51.1163 | 51.1163 | 51.1163 | 51.1163 | 51.1163 | 51.1163 | 51.1163 | 51.1163 | 51.1163 | 51.1163 | 51.1163 | 51.1163 | 51.1163 | 51.1163 | 51.1163 | 51.1163 | 65% | 114.2056 | 37.0683 | 47.9835 | 50.8395 | 50.668 | 50.6801 | 50.9729 | 51.7462 | 52.2634 | 52.77 | 53.3626 | 53.9114 | 54.4444 | 54.5049 | 55.1271 | 54.6546 | 54.6546 | 54.6546 | 54.6546 | 54.6546 | 54.6546 | 54.6546 | 54.6546 | 54.6546 | 54.6546 | 54.6546 | 54.6546 | 54.6546 | 54.6546 | 54.6546 | 54.6546
60% | 689.7717 | 30.6973 | 40.7526 | 43.4896 | 43.4099 | 43.407 | 43.7189 | 44.0612 | 44.764 | 45.269 | 45.5429 | 45.8424 | 46.1167 | 46.6122 | 47.2272 | 47.1843 | 47.1843 | 47.1843 | 47.1843 | 47.1843 | 47.1843 | 47.1843 | 47.1843 | 47.1843 | 47.1843 | 47.1843 | 47.1843 | 47.1843 | 47.1843 | 47.1843 | 47.1843 | 60% | 178.1154 | 34.2169 | 44.2924 | 46.9287 | 46.7705 | 46.7817 | 47.0519 | 47.7657 | 48.2431 | 48.7108 | 49.2577 | 49.7643 | 50.2564 | 50.3122 | 50.8865 | 50.4504 | 50.4504 | 50.4504 | 50.4504 | 50.4504 | 50.4504 | 50.4504 | 50.4504 | 50.4504 | 50.4504 | 50.4504 | 50.4504 | 50.4504 | 50.4504 | 50.4504 | 50.4504
55% | 1095.5419 | 28.1392 | 37.3565 | 39.8655 | 39.7924 | 39.7897 | 40.0757 | 40.3894 | 41.0336 | 41.4965 | 41.7476 | 42.0222 | 42.2736 | 42.7279 | 43.2916 | 43.2522 | 43.2522 | 43.2522 | 43.2522 | 43.2522 | 43.2522 | 43.2522 | 43.2522 | 43.2522 | 43.2522 | 43.2522 | 43.2522 | 43.2522 | 43.2522 | 43.2522 | 43.2522 | 55% | 311.6074 | 31.3655 | 40.6014 | 43.018 | 42.8729 | 42.8832 | 43.131 | 43.7852 | 44.2229 | 44.6515 | 45.1529 | 45.6173 | 46.0683 | 46.1195 | 46.646 | 46.2462 | 46.2462 | 46.2462 | 46.2462 | 46.2462 | 46.2462 | 46.2462 | 46.2462 | 46.2462 | 46.2462 | 46.2462 | 46.2462 | 46.2462 | 46.2462 | 46.2462 | 46.2462
50% | 1666.1918 | 25.581 | 33.9605 | 36.2413 | 36.1749 | 36.1725 | 36.4324 | 36.7177 | 37.3033 | 37.7241 | 37.9524 | 38.202 | 38.4306 | 38.8435 | 39.356 | 39.3202 | 39.3202 | 39.3202 | 39.3202 | 39.3202 | 39.3202 | 39.3202 | 39.3202 | 39.3202 | 39.3202 | 39.3202 | 39.3202 | 39.3202 | 39.3202 | 39.3202 | 39.3202 | 50% | 636.0723 | 28.5141 | 36.9103 | 39.1073 | 38.9754 | 38.9847 | 39.21 | 39.8047 | 40.2026 | 40.5923 | 41.0481 | 41.4703 | 41.8803 | 41.9268 | 42.4054 | 42.042 | 42.042 | 42.042 | 42.042 | 42.042 | 42.042 | 42.042 | 42.042 | 42.042 | 42.042 | 42.042 | 42.042 | 42.042 | 42.042 | 42.042 | 42.042
45% | 2506.0947 | 23.0229 | 30.5644 | 32.6172 | 32.5574 | 32.5552 | 32.7892 | 33.0459 | 33.573 | 33.9517 | 34.1572 | 34.3818 | 34.5875 | 34.9592 | 35.4204 | 35.3882 | 35.3882 | 35.3882 | 35.3882 | 35.3882 | 35.3882 | 35.3882 | 35.3882 | 35.3882 | 35.3882 | 35.3882 | 35.3882 | 35.3882 | 35.3882 | 35.3882 | 35.3882 | 45% | 1179.4944 | 25.6627 | 33.2193 | 35.1965 | 35.0779 | 35.0862 | 35.289 | 35.8243 | 36.1824 | 36.5331 | 36.9433 | 37.3233 | 37.6923 | 37.7341 | 38.1649 | 37.8378 | 37.8378 | 37.8378 | 37.8378 | 37.8378 | 37.8378 | 37.8378 | 37.8378 | 37.8378 | 37.8378 | 37.8378 | 37.8378 | 37.8378 | 37.8378 | 37.8378 | 37.8378
40% | 3164.4787 | 20.4648 | 27.1684 | 28.9931 | 28.9399 | 28.938 | 29.1459 | 29.3741 | 29.8426 | 30.1793 | 30.3619 | 30.5616 | 30.7444 | 31.0748 | 31.4848 | 31.4562 | 31.4562 | 31.4562 | 31.4562 | 31.4562 | 31.4562 | 31.4562 | 31.4562 | 31.4562 | 31.4562 | 31.4562 | 31.4562 | 31.4562 | 31.4562 | 31.4562 | 31.4562 | 40% | 1808.3816 | 22.8113 | 29.5283 | 31.2858 | 31.1803 | 31.1878 | 31.368 | 31.8438 | 32.1621 | 32.4738 | 32.8385 | 33.1762 | 33.5042 | 33.5415 | 33.9244 | 33.6336 | 33.6336 | 33.6336 | 33.6336 | 33.6336 | 33.6336 | 33.6336 | 33.6336 | 33.6336 | 33.6336 | 33.6336 | 33.6336 | 33.6336 | 33.6336 | 33.6336 | 33.6336
35% | 3551.3408 | 17.9067 | 23.7723 | 25.3689 | 25.3224 | 25.3207 | 25.5027 | 25.7024 | 26.1123 | 26.4069 | 26.5667 | 26.7414 | 26.9014 | 27.1905 | 27.5492 | 27.5241 | 27.5241 | 27.5241 | 27.5241 | 27.5241 | 27.5241 | 27.5241 | 27.5241 | 27.5241 | 27.5241 | 27.5241 | 27.5241 | 27.5241 | 27.5241 | 27.5241 | 27.5241 | 35% | 2779.1293 | 19.9599 | 25.8372 | 27.3751 | 27.2828 | 27.2893 | 27.447 | 27.8633 | 28.1418 | 28.4146 | 28.7337 | 29.0292 | 29.3162 | 29.3488 | 29.6838 | 29.4294 | 29.4294 | 29.4294 | 29.4294 | 29.4294 | 29.4294 | 29.4294 | 29.4294 | 29.4294 | 29.4294 | 29.4294 | 29.4294 | 29.4294 | 29.4294 | 29.4294 | 29.4294
30% | 3758.953 | 15.3486 | 20.3763 | 21.7448 | 21.705 | 21.7035 | 21.8595 | 22.0306 | 22.382 | 22.6345 | 22.7714 | 22.9212 | 23.0583 | 23.3061 | 23.6136 | 23.5921 | 23.5921 | 23.5921 | 23.5921 | 23.5921 | 23.5921 | 23.5921 | 23.5921 | 23.5921 | 23.5921 | 23.5921 | 23.5921 | 23.5921 | 23.5921 | 23.5921 | 23.5921 | 30% | 3814.165 | 17.1085 | 22.1462 | 23.4644 | 23.3852 | 23.3908 | 23.526 | 23.8828 | 24.1216 | 24.3554 | 24.6289 | 24.8822 | 25.1282 | 25.1561 | 25.4433 | 25.2252 | 25.2252 | 25.2252 | 25.2252 | 25.2252 | 25.2252 | 25.2252 | 25.2252 | 25.2252 | 25.2252 | 25.2252 | 25.2252 | 25.2252 | 25.2252 | 25.2252 | 25.2252
25% | 3926.4798 | 12.7905 | 16.9802 | 18.1207 | 18.0875 | 18.0862 | 18.2162 | 18.3588 | 18.6517 | 18.8621 | 18.9762 | 19.101 | 19.2153 | 19.4218 | 19.678 | 19.6601 | 19.6601 | 19.6601 | 19.6601 | 19.6601 | 19.6601 | 19.6601 | 19.6601 | 19.6601 | 19.6601 | 19.6601 | 19.6601 | 19.6601 | 19.6601 | 19.6601 | 19.6601 | 25% | 4166.9923 | 14.257 | 18.4552 | 19.5536 | 19.4877 | 19.4924 | 19.605 | 19.9024 | 20.1013 | 20.2962 | 20.5241 | 20.7351 | 20.9402 | 20.9634 | 21.2027 | 21.021 | 21.021 | 21.021 | 21.021 | 21.021 | 21.021 | 21.021 | 21.021 | 21.021 | 21.021 | 21.021 | 21.021 | 21.021 | 21.021 | 21.021 | 21.021
20% | 4050.5177 | 10.2324 | 13.5842 | 14.4965 | 14.47 | 14.469 | 14.573 | 14.6871 | 14.9213 | 15.0897 | 15.181 | 15.2808 | 15.3722 | 15.5374 | 15.7424 | 15.7281 | 15.7281 | 15.7281 | 15.7281 | 15.7281 | 15.7281 | 15.7281 | 15.7281 | 15.7281 | 15.7281 | 15.7281 | 15.7281 | 15.7281 | 15.7281 | 15.7281 | 15.7281 | 20% | 4282.7105 | 11.4056 | 14.7641 | 15.6429 | 15.5902 | 15.5939 | 15.684 | 15.9219 | 16.081 | 16.2369 | 16.4192 | 16.5881 | 16.7521 | 16.7707 | 16.9622 | 16.8168 | 16.8168 | 16.8168 | 16.8168 | 16.8168 | 16.8168 | 16.8168 | 16.8168 | 16.8168 | 16.8168 | 16.8168 | 16.8168 | 16.8168 | 16.8168 | 16.8168 | 16.8168
15% | 4152.622 | 7.6743 | 10.1881 | 10.8724 | 10.8525 | 10.8517 | 10.9297 | 11.0153 | 11.191 | 11.3172 | 11.3857 | 11.4606 | 11.5292 | 11.6531 | 11.8068 | 11.7961 | 11.7961 | 11.7961 | 11.7961 | 11.7961 | 11.7961 | 11.7961 | 11.7961 | 11.7961 | 11.7961 | 11.7961 | 11.7961 | 11.7961 | 11.7961 | 11.7961 | 11.7961 | 15% | 4364.7722 | 8.5542 | 11.0731 | 11.7322 | 11.6926 | 11.6954 | 11.763 | 11.9414 | 12.0608 | 12.1777 | 12.3144 | 12.4411 | 12.5641 | 12.578 | 12.7216 | 12.6126 | 12.6126 | 12.6126 | 12.6126 | 12.6126 | 12.6126 | 12.6126 | 12.6126 | 12.6126 | 12.6126 | 12.6126 | 12.6126 | 12.6126 | 12.6126 | 12.6126 | 12.6126
10% | 4248.2976 | 5.1162 | 6.7921 | 7.2483 | 7.235 | 7.2345 | 7.2865 | 7.3435 | 7.4607 | 7.5448 | 7.5905 | 7.6404 | 7.6861 | 7.7687 | 7.8712 | 7.864 | 7.864 | 7.864 | 7.864 | 7.864 | 7.864 | 7.864 | 7.864 | 7.864 | 7.864 | 7.864 | 7.864 | 7.864 | 7.864 | 7.864 | 7.864 | 10% | 4391.6218 | 5.7028 | 7.3821 | 7.8215 | 7.7951 | 7.7969 | 7.842 | 7.9609 | 8.0405 | 8.1185 | 8.2096 | 8.2941 | 8.3761 | 8.3854 | 8.4811 | 8.4084 | 8.4084 | 8.4084 | 8.4084 | 8.4084 | 8.4084 | 8.4084 | 8.4084 | 8.4084 | 8.4084 | 8.4084 | 8.4084 | 8.4084 | 8.4084 | 8.4084 | 8.4084
5% | 4361.7469 | 2.5581 | 3.396 | 3.6241 | 3.6175 | 3.6172 | 3.6432 | 3.6718 | 3.7303 | 3.7724 | 3.7952 | 3.8202 | 3.8431 | 3.8844 | 3.9356 | 3.932 | 3.932 | 3.932 | 3.932 | 3.932 | 3.932 | 3.932 | 3.932 | 3.932 | 3.932 | 3.932 | 3.932 | 3.932 | 3.932 | 3.932 | 3.932 | 5% | 4391.6218 | 2.8514 | 3.691 | 3.9107 | 3.8975 | 3.8985 | 3.921 | 3.9805 | 4.0203 | 4.0592 | 4.1048 | 4.147 | 4.188 | 4.1927 | 4.2405 | 4.2042 | 4.2042 | 4.2042 | 4.2042 | 4.2042 | 4.2042 | 4.2042 | 4.2042 | 4.2042 | 4.2042 | 4.2042 | 4.2042 | 4.2042 | 4.2042 | 4.2042 | 4.2042
9.992e-14% | 4391.6218 | 5.1121e-14 | 6.7867e-14 | 7.2425e-14 | 7.2292e-14 | 7.2287e-14 | 7.2807e-14 | 7.3377e-14 | 7.4547e-14 | 7.5388e-14 | 7.5844e-14 | 7.6343e-14 | 7.68e-14 | 7.7625e-14 | 7.8649e-14 | 7.8578e-14 | 7.8578e-14 | 7.8578e-14 | 7.8578e-14 | 7.8578e-14 | 7.8578e-14 | 7.8578e-14 | 7.8578e-14 | 7.8578e-14 | 7.8578e-14 | 7.8578e-14 | 7.8578e-14 | 7.8578e-14 | 7.8578e-14 | 7.8578e-14 | 7.8578e-14 | 9.992e-14% | 4391.6218 | 5.6983e-14 | 7.3762e-14 | 7.8152e-14 | 7.7889e-14 | 7.7907e-14 | 7.8357e-14 | 7.9546e-14 | 8.0341e-14 | 8.112e-14 | 8.2031e-14 | 8.2874e-14 | 8.3694e-14 | 8.3787e-14 | 8.4743e-14 | 8.4017e-14 | 8.4017e-14 | 8.4017e-14 | 8.4017e-14 | 8.4017e-14 | 8.4017e-14 | 8.4017e-14 | 8.4017e-14 | 8.4017e-14 | 8.4017e-14 | 8.4017e-14 | 8.4017e-14 | 8.4017e-14 | 8.4017e-14 | 8.4017e-14 | 8.4017e-14
Option 8
Winter Season | [31 empty] | Winter Season
P50 | [31 empty] | P10
% of MD | Winter - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Winter - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 45.0311 | 62.4376 | 66.9594 | 67.7285 | 68.3267 | 69.3603 | 71.7146 | 73.2888 | 75.2849 | 76.3199 | 77.2291 | 75.5455 | 77.5138 | 80.6095 | 78.2564 | 78.2564 | 78.2564 | 78.2564 | 78.2564 | 78.2564 | 78.2564 | 78.2564 | 78.2564 | 78.2564 | 78.2564 | 78.2564 | 78.2564 | 78.2564 | 78.2564 | 78.2564 | 100% | 0 | 48.1978 | 65.3847 | 70.0831 | 70.8084 | 71.267 | 72.2781 | 74.6693 | 75.9727 | 78.4597 | 86.0243 | 79.7829 | 78.5605 | 80.2054 | 83.8053 | 81.3648 | 81.3648 | 81.3648 | 81.3648 | 81.3648 | 81.3648 | 81.3648 | 81.3648 | 81.3648 | 81.3648 | 81.3648 | 81.3648 | 81.3648 | 81.3648 | 81.3648 | 81.3648
99% | 1.486 | 44.5808 | 61.8132 | 66.2898 | 67.0512 | 67.6435 | 68.6667 | 70.9975 | 72.5559 | 74.532 | 75.5567 | 76.4569 | 74.7901 | 76.7387 | 79.8034 | 77.4739 | 77.4739 | 77.4739 | 77.4739 | 77.4739 | 77.4739 | 77.4739 | 77.4739 | 77.4739 | 77.4739 | 77.4739 | 77.4739 | 77.4739 | 77.4739 | 77.4739 | 77.4739 | 99% | 1.486 | 47.7158 | 64.7309 | 69.3823 | 70.1003 | 70.5543 | 71.5553 | 73.9226 | 75.2129 | 77.6751 | 85.1641 | 78.9851 | 77.7749 | 79.4033 | 82.9672 | 80.5512 | 80.5512 | 80.5512 | 80.5512 | 80.5512 | 80.5512 | 80.5512 | 80.5512 | 80.5512 | 80.5512 | 80.5512 | 80.5512 | 80.5512 | 80.5512 | 80.5512 | 80.5512
98% | 3.2692 | 44.1305 | 61.1889 | 65.6202 | 66.3739 | 66.9602 | 67.9731 | 70.2804 | 71.823 | 73.7792 | 74.7935 | 75.6846 | 74.0346 | 75.9636 | 78.9973 | 76.6913 | 76.6913 | 76.6913 | 76.6913 | 76.6913 | 76.6913 | 76.6913 | 76.6913 | 76.6913 | 76.6913 | 76.6913 | 76.6913 | 76.6913 | 76.6913 | 76.6913 | 76.6913 | 98% | 3.2692 | 47.2338 | 64.0771 | 68.6815 | 69.3922 | 69.8416 | 70.8325 | 73.1759 | 74.4532 | 76.8905 | 84.3038 | 78.1873 | 76.9893 | 78.6013 | 82.1292 | 79.7375 | 79.7375 | 79.7375 | 79.7375 | 79.7375 | 79.7375 | 79.7375 | 79.7375 | 79.7375 | 79.7375 | 79.7375 | 79.7375 | 79.7375 | 79.7375 | 79.7375 | 79.7375
97% | 6.8356 | 43.6802 | 60.5645 | 64.9506 | 65.6966 | 66.2769 | 67.2795 | 69.5632 | 71.0901 | 73.0263 | 74.0303 | 74.9123 | 73.2792 | 75.1884 | 78.1912 | 75.9087 | 75.9087 | 75.9087 | 75.9087 | 75.9087 | 75.9087 | 75.9087 | 75.9087 | 75.9087 | 75.9087 | 75.9087 | 75.9087 | 75.9087 | 75.9087 | 75.9087 | 75.9087 | 97% | 6.8356 | 46.7518 | 63.4232 | 67.9806 | 68.6841 | 69.129 | 70.1097 | 72.4292 | 73.6935 | 76.1059 | 83.4436 | 77.3894 | 76.2037 | 77.7992 | 81.2911 | 78.9239 | 78.9239 | 78.9239 | 78.9239 | 78.9239 | 78.9239 | 78.9239 | 78.9239 | 78.9239 | 78.9239 | 78.9239 | 78.9239 | 78.9239 | 78.9239 | 78.9239 | 78.9239
95% | 17.5347 | 42.7796 | 59.3157 | 63.6114 | 64.342 | 64.9104 | 65.8923 | 68.1289 | 69.6243 | 71.5207 | 72.5039 | 73.3677 | 71.7683 | 73.6382 | 76.579 | 74.3436 | 74.3436 | 74.3436 | 74.3436 | 74.3436 | 74.3436 | 74.3436 | 74.3436 | 74.3436 | 74.3436 | 74.3436 | 74.3436 | 74.3436 | 74.3436 | 74.3436 | 74.3436 | 95% | 17.5347 | 45.7879 | 62.1155 | 66.579 | 67.268 | 67.7036 | 68.6642 | 70.9358 | 72.174 | 74.5368 | 81.7231 | 75.7938 | 74.6325 | 76.1951 | 79.615 | 77.2966 | 77.2966 | 77.2966 | 77.2966 | 77.2966 | 77.2966 | 77.2966 | 77.2966 | 77.2966 | 77.2966 | 77.2966 | 77.2966 | 77.2966 | 77.2966 | 77.2966 | 77.2966
90% | 78.7576 | 40.528 | 56.1939 | 60.2634 | 60.9556 | 61.4941 | 62.4243 | 64.5432 | 65.9599 | 67.7564 | 68.6879 | 69.5062 | 67.991 | 69.7625 | 72.5486 | 70.4308 | 70.4308 | 70.4308 | 70.4308 | 70.4308 | 70.4308 | 70.4308 | 70.4308 | 70.4308 | 70.4308 | 70.4308 | 70.4308 | 70.4308 | 70.4308 | 70.4308 | 70.4308 | 90% | 78.7576 | 43.378 | 58.8463 | 63.0748 | 63.7275 | 64.1403 | 65.0503 | 67.2023 | 68.3754 | 70.6138 | 77.4219 | 71.8046 | 70.7045 | 72.1848 | 75.4247 | 73.2283 | 73.2283 | 73.2283 | 73.2283 | 73.2283 | 73.2283 | 73.2283 | 73.2283 | 73.2283 | 73.2283 | 73.2283 | 73.2283 | 73.2283 | 73.2283 | 73.2283 | 73.2283
85% | 236.8672 | 38.2764 | 53.072 | 56.9155 | 57.5692 | 58.0777 | 58.9563 | 60.9575 | 62.2954 | 63.9922 | 64.8719 | 65.6448 | 64.2137 | 65.8868 | 68.5181 | 66.518 | 66.518 | 66.518 | 66.518 | 66.518 | 66.518 | 66.518 | 66.518 | 66.518 | 66.518 | 66.518 | 66.518 | 66.518 | 66.518 | 66.518 | 66.518 | 85% | 236.8672 | 40.9681 | 55.577 | 59.5707 | 60.1871 | 60.5769 | 61.4364 | 63.4689 | 64.5768 | 66.6908 | 73.1207 | 67.8155 | 66.7765 | 68.1746 | 71.2345 | 69.1601 | 69.1601 | 69.1601 | 69.1601 | 69.1601 | 69.1601 | 69.1601 | 69.1601 | 69.1601 | 69.1601 | 69.1601 | 69.1601 | 69.1601 | 69.1601 | 69.1601 | 69.1601
80% | 497.5104 | 36.0249 | 49.9501 | 53.5675 | 54.1828 | 54.6614 | 55.4882 | 57.3717 | 58.631 | 60.2279 | 61.056 | 61.7833 | 60.4364 | 62.0111 | 64.4876 | 62.6051 | 62.6051 | 62.6051 | 62.6051 | 62.6051 | 62.6051 | 62.6051 | 62.6051 | 62.6051 | 62.6051 | 62.6051 | 62.6051 | 62.6051 | 62.6051 | 62.6051 | 62.6051 | 80% | 497.5104 | 38.5582 | 52.3078 | 56.0665 | 56.6467 | 57.0136 | 57.8225 | 59.7354 | 60.7781 | 62.7678 | 68.8195 | 63.8263 | 62.8484 | 64.1643 | 67.0442 | 65.0919 | 65.0919 | 65.0919 | 65.0919 | 65.0919 | 65.0919 | 65.0919 | 65.0919 | 65.0919 | 65.0919 | 65.0919 | 65.0919 | 65.0919 | 65.0919 | 65.0919 | 65.0919
75% | 803.6248 | 33.7733 | 46.8282 | 50.2195 | 50.7964 | 51.245 | 52.0202 | 53.786 | 54.9666 | 56.4637 | 57.24 | 57.9219 | 56.6592 | 58.1354 | 60.4571 | 58.6923 | 58.6923 | 58.6923 | 58.6923 | 58.6923 | 58.6923 | 58.6923 | 58.6923 | 58.6923 | 58.6923 | 58.6923 | 58.6923 | 58.6923 | 58.6923 | 58.6923 | 58.6923 | 75% | 803.6248 | 36.1483 | 49.0386 | 52.5623 | 53.1063 | 53.4502 | 54.2086 | 56.0019 | 56.9795 | 58.8448 | 64.5182 | 59.8372 | 58.9204 | 60.154 | 62.8539 | 61.0236 | 61.0236 | 61.0236 | 61.0236 | 61.0236 | 61.0236 | 61.0236 | 61.0236 | 61.0236 | 61.0236 | 61.0236 | 61.0236 | 61.0236 | 61.0236 | 61.0236 | 61.0236
70% | 1155.2107 | 31.5218 | 43.7063 | 46.8715 | 47.4099 | 47.8287 | 48.5522 | 50.2003 | 51.3021 | 52.6994 | 53.424 | 54.0604 | 52.8819 | 54.2597 | 56.4267 | 54.7795 | 54.7795 | 54.7795 | 54.7795 | 54.7795 | 54.7795 | 54.7795 | 54.7795 | 54.7795 | 54.7795 | 54.7795 | 54.7795 | 54.7795 | 54.7795 | 54.7795 | 54.7795 | 70% | 1155.2107 | 33.7384 | 45.7693 | 49.0582 | 49.5659 | 49.8869 | 50.5947 | 52.2685 | 53.1809 | 54.9218 | 60.217 | 55.8481 | 54.9924 | 56.1438 | 58.6637 | 56.9554 | 56.9554 | 56.9554 | 56.9554 | 56.9554 | 56.9554 | 56.9554 | 56.9554 | 56.9554 | 56.9554 | 56.9554 | 56.9554 | 56.9554 | 56.9554 | 56.9554 | 56.9554
65% | 1553.1596 | 29.2702 | 40.5844 | 43.5236 | 44.0235 | 44.4124 | 45.0842 | 46.6145 | 47.6377 | 48.9352 | 49.608 | 50.1989 | 49.1046 | 50.384 | 52.3962 | 50.8667 | 50.8667 | 50.8667 | 50.8667 | 50.8667 | 50.8667 | 50.8667 | 50.8667 | 50.8667 | 50.8667 | 50.8667 | 50.8667 | 50.8667 | 50.8667 | 50.8667 | 50.8667 | 65% | 1553.1596 | 31.3286 | 42.5001 | 45.554 | 46.0254 | 46.3235 | 46.9808 | 48.535 | 49.3822 | 50.9988 | 55.9158 | 51.8589 | 51.0643 | 52.1335 | 54.4734 | 52.8871 | 52.8871 | 52.8871 | 52.8871 | 52.8871 | 52.8871 | 52.8871 | 52.8871 | 52.8871 | 52.8871 | 52.8871 | 52.8871 | 52.8871 | 52.8871 | 52.8871 | 52.8871
60% | 2026.2996 | 27.0187 | 37.4626 | 40.1756 | 40.6371 | 40.996 | 41.6162 | 43.0288 | 43.9733 | 45.1709 | 45.792 | 46.3375 | 45.3273 | 46.5083 | 48.3657 | 46.9539 | 46.9539 | 46.9539 | 46.9539 | 46.9539 | 46.9539 | 46.9539 | 46.9539 | 46.9539 | 46.9539 | 46.9539 | 46.9539 | 46.9539 | 46.9539 | 46.9539 | 46.9539 | 60% | 2026.2996 | 28.9187 | 39.2308 | 42.0499 | 42.485 | 42.7602 | 43.3669 | 44.8016 | 45.5836 | 47.0758 | 51.6146 | 47.8698 | 47.1363 | 48.1232 | 50.2832 | 48.8189 | 48.8189 | 48.8189 | 48.8189 | 48.8189 | 48.8189 | 48.8189 | 48.8189 | 48.8189 | 48.8189 | 48.8189 | 48.8189 | 48.8189 | 48.8189 | 48.8189 | 48.8189
55% | 2598.4068 | 24.7671 | 34.3407 | 36.8276 | 37.2507 | 37.5797 | 38.1482 | 39.4431 | 40.3088 | 41.4067 | 41.976 | 42.476 | 41.55 | 42.6326 | 44.3352 | 43.041 | 43.041 | 43.041 | 43.041 | 43.041 | 43.041 | 43.041 | 43.041 | 43.041 | 43.041 | 43.041 | 43.041 | 43.041 | 43.041 | 43.041 | 43.041 | 55% | 2598.4068 | 26.5088 | 35.9616 | 38.5457 | 38.9446 | 39.1968 | 39.753 | 41.0681 | 41.785 | 43.1529 | 47.3134 | 43.8806 | 43.2083 | 44.113 | 46.0929 | 44.7507 | 44.7507 | 44.7507 | 44.7507 | 44.7507 | 44.7507 | 44.7507 | 44.7507 | 44.7507 | 44.7507 | 44.7507 | 44.7507 | 44.7507 | 44.7507 | 44.7507 | 44.7507
50% | 3233.5201 | 22.5156 | 31.2188 | 33.4797 | 33.8642 | 34.1634 | 34.6802 | 35.8573 | 36.6444 | 37.6424 | 38.16 | 38.6146 | 37.7728 | 38.7569 | 40.3048 | 39.1282 | 39.1282 | 39.1282 | 39.1282 | 39.1282 | 39.1282 | 39.1282 | 39.1282 | 39.1282 | 39.1282 | 39.1282 | 39.1282 | 39.1282 | 39.1282 | 39.1282 | 39.1282 | 50% | 3233.5201 | 24.0989 | 32.6924 | 35.0416 | 35.4042 | 35.6335 | 36.139 | 37.3346 | 37.9863 | 39.2299 | 43.0122 | 39.8915 | 39.2803 | 40.1027 | 41.9026 | 40.6824 | 40.6824 | 40.6824 | 40.6824 | 40.6824 | 40.6824 | 40.6824 | 40.6824 | 40.6824 | 40.6824 | 40.6824 | 40.6824 | 40.6824 | 40.6824 | 40.6824 | 40.6824
45% | 3775.313 | 20.264 | 28.0969 | 30.1317 | 30.4778 | 30.747 | 31.2121 | 32.2716 | 32.9799 | 33.8782 | 34.344 | 34.7531 | 33.9955 | 34.8812 | 36.2743 | 35.2154 | 35.2154 | 35.2154 | 35.2154 | 35.2154 | 35.2154 | 35.2154 | 35.2154 | 35.2154 | 35.2154 | 35.2154 | 35.2154 | 35.2154 | 35.2154 | 35.2154 | 35.2154 | 45% | 3775.313 | 21.689 | 29.4231 | 31.5374 | 31.8638 | 32.0701 | 32.5251 | 33.6012 | 34.1877 | 35.3069 | 38.7109 | 35.9023 | 35.3522 | 36.0924 | 37.7124 | 36.6142 | 36.6142 | 36.6142 | 36.6142 | 36.6142 | 36.6142 | 36.6142 | 36.6142 | 36.6142 | 36.6142 | 36.6142 | 36.6142 | 36.6142 | 36.6142 | 36.6142 | 36.6142
40% | 4072.8088 | 18.0124 | 24.975 | 26.7837 | 27.0914 | 27.3307 | 27.7441 | 28.6859 | 29.3155 | 30.114 | 30.528 | 30.8917 | 30.2182 | 31.0055 | 32.2438 | 31.3026 | 31.3026 | 31.3026 | 31.3026 | 31.3026 | 31.3026 | 31.3026 | 31.3026 | 31.3026 | 31.3026 | 31.3026 | 31.3026 | 31.3026 | 31.3026 | 31.3026 | 31.3026 | 40% | 4072.8088 | 19.2791 | 26.1539 | 28.0332 | 28.3234 | 28.5068 | 28.9112 | 29.8677 | 30.3891 | 31.3839 | 34.4097 | 31.9132 | 31.4242 | 32.0822 | 33.5221 | 32.5459 | 32.5459 | 32.5459 | 32.5459 | 32.5459 | 32.5459 | 32.5459 | 32.5459 | 32.5459 | 32.5459 | 32.5459 | 32.5459 | 32.5459 | 32.5459 | 32.5459 | 32.5459
35% | 4198.821 | 15.7609 | 21.8532 | 23.4358 | 23.705 | 23.9144 | 24.2761 | 25.1001 | 25.6511 | 26.3497 | 26.712 | 27.0302 | 26.4409 | 27.1298 | 28.2133 | 27.3897 | 27.3897 | 27.3897 | 27.3897 | 27.3897 | 27.3897 | 27.3897 | 27.3897 | 27.3897 | 27.3897 | 27.3897 | 27.3897 | 27.3897 | 27.3897 | 27.3897 | 27.3897 | 35% | 4198.821 | 16.8692 | 22.8847 | 24.5291 | 24.7829 | 24.9434 | 25.2973 | 26.1342 | 26.5904 | 27.4609 | 30.1085 | 27.924 | 27.4962 | 28.0719 | 29.3318 | 28.4777 | 28.4777 | 28.4777 | 28.4777 | 28.4777 | 28.4777 | 28.4777 | 28.4777 | 28.4777 | 28.4777 | 28.4777 | 28.4777 | 28.4777 | 28.4777 | 28.4777 | 28.4777
30% | 4271.3374 | 13.5093 | 18.7313 | 20.0878 | 20.3185 | 20.498 | 20.8081 | 21.5144 | 21.9866 | 22.5855 | 22.896 | 23.1687 | 22.6637 | 23.2542 | 24.1829 | 23.4769 | 23.4769 | 23.4769 | 23.4769 | 23.4769 | 23.4769 | 23.4769 | 23.4769 | 23.4769 | 23.4769 | 23.4769 | 23.4769 | 23.4769 | 23.4769 | 23.4769 | 23.4769 | 30% | 4271.3374 | 14.4593 | 19.6154 | 21.0249 | 21.2425 | 21.3801 | 21.6834 | 22.4008 | 22.7918 | 23.5379 | 25.8073 | 23.9349 | 23.5682 | 24.0616 | 25.1416 | 24.4094 | 24.4094 | 24.4094 | 24.4094 | 24.4094 | 24.4094 | 24.4094 | 24.4094 | 24.4094 | 24.4094 | 24.4094 | 24.4094 | 24.4094 | 24.4094 | 24.4094 | 24.4094
25% | 4321.8611 | 11.2578 | 15.6094 | 16.7398 | 16.9321 | 17.0817 | 17.3401 | 17.9287 | 18.3222 | 18.8212 | 19.08 | 19.3073 | 18.8864 | 19.3785 | 20.1524 | 19.5641 | 19.5641 | 19.5641 | 19.5641 | 19.5641 | 19.5641 | 19.5641 | 19.5641 | 19.5641 | 19.5641 | 19.5641 | 19.5641 | 19.5641 | 19.5641 | 19.5641 | 19.5641 | 25% | 4321.8611 | 12.0494 | 16.3462 | 17.5208 | 17.7021 | 17.8167 | 18.0695 | 18.6673 | 18.9932 | 19.6149 | 21.5061 | 19.9457 | 19.6401 | 20.0513 | 20.9513 | 20.3412 | 20.3412 | 20.3412 | 20.3412 | 20.3412 | 20.3412 | 20.3412 | 20.3412 | 20.3412 | 20.3412 | 20.3412 | 20.3412 | 20.3412 | 20.3412 | 20.3412 | 20.3412
20% | 4353.067 | 9.0062 | 12.4875 | 13.3919 | 13.5457 | 13.6653 | 13.8721 | 14.3429 | 14.6578 | 15.057 | 15.264 | 15.4458 | 15.1091 | 15.5028 | 16.1219 | 15.6513 | 15.6513 | 15.6513 | 15.6513 | 15.6513 | 15.6513 | 15.6513 | 15.6513 | 15.6513 | 15.6513 | 15.6513 | 15.6513 | 15.6513 | 15.6513 | 15.6513 | 15.6513 | 20% | 4353.067 | 9.6396 | 13.0769 | 14.0166 | 14.1617 | 14.2534 | 14.4556 | 14.9339 | 15.1945 | 15.6919 | 17.2049 | 15.9566 | 15.7121 | 16.0411 | 16.7611 | 16.273 | 16.273 | 16.273 | 16.273 | 16.273 | 16.273 | 16.273 | 16.273 | 16.273 | 16.273 | 16.273 | 16.273 | 16.273 | 16.273 | 16.273 | 16.273
15% | 4369.4129 | 6.7547 | 9.3656 | 10.0439 | 10.1593 | 10.249 | 10.404 | 10.7572 | 10.9933 | 11.2927 | 11.448 | 11.5844 | 11.3318 | 11.6271 | 12.0914 | 11.7385 | 11.7385 | 11.7385 | 11.7385 | 11.7385 | 11.7385 | 11.7385 | 11.7385 | 11.7385 | 11.7385 | 11.7385 | 11.7385 | 11.7385 | 11.7385 | 11.7385 | 11.7385 | 15% | 4369.4129 | 7.2297 | 9.8077 | 10.5125 | 10.6213 | 10.69 | 10.8417 | 11.2004 | 11.3959 | 11.769 | 12.9036 | 11.9674 | 11.7841 | 12.0308 | 12.5708 | 12.2047 | 12.2047 | 12.2047 | 12.2047 | 12.2047 | 12.2047 | 12.2047 | 12.2047 | 12.2047 | 12.2047 | 12.2047 | 12.2047 | 12.2047 | 12.2047 | 12.2047 | 12.2047
10% | 4378.6261 | 4.5031 | 6.2438 | 6.6959 | 6.7728 | 6.8327 | 6.936 | 7.1715 | 7.3289 | 7.5285 | 7.632 | 7.7229 | 7.5546 | 7.7514 | 8.061 | 7.8256 | 7.8256 | 7.8256 | 7.8256 | 7.8256 | 7.8256 | 7.8256 | 7.8256 | 7.8256 | 7.8256 | 7.8256 | 7.8256 | 7.8256 | 7.8256 | 7.8256 | 7.8256 | 10% | 4378.6261 | 4.8198 | 6.5385 | 7.0083 | 7.0808 | 7.1267 | 7.2278 | 7.4669 | 7.5973 | 7.846 | 8.6024 | 7.9783 | 7.8561 | 8.0205 | 8.3805 | 8.1365 | 8.1365 | 8.1365 | 8.1365 | 8.1365 | 8.1365 | 8.1365 | 8.1365 | 8.1365 | 8.1365 | 8.1365 | 8.1365 | 8.1365 | 8.1365 | 8.1365 | 8.1365
5% | 4391.7028 | 2.2516 | 3.1219 | 3.348 | 3.3864 | 3.4163 | 3.468 | 3.5857 | 3.6644 | 3.7642 | 3.816 | 3.8615 | 3.7773 | 3.8757 | 4.0305 | 3.9128 | 3.9128 | 3.9128 | 3.9128 | 3.9128 | 3.9128 | 3.9128 | 3.9128 | 3.9128 | 3.9128 | 3.9128 | 3.9128 | 3.9128 | 3.9128 | 3.9128 | 3.9128 | 5% | 4391.7028 | 2.4099 | 3.2692 | 3.5042 | 3.5404 | 3.5633 | 3.6139 | 3.7335 | 3.7986 | 3.923 | 4.3012 | 3.9891 | 3.928 | 4.0103 | 4.1903 | 4.0682 | 4.0682 | 4.0682 | 4.0682 | 4.0682 | 4.0682 | 4.0682 | 4.0682 | 4.0682 | 4.0682 | 4.0682 | 4.0682 | 4.0682 | 4.0682 | 4.0682 | 4.0682
9.992e-14% | 4391.7028 | 4.4995e-14 | 6.2388e-14 | 6.6906e-14 | 6.7674e-14 | 6.8272e-14 | 6.9305e-14 | 7.1657e-14 | 7.323e-14 | 7.5225e-14 | 7.6259e-14 | 7.7167e-14 | 7.5485e-14 | 7.7452e-14 | 8.0545e-14 | 7.8194e-14 | 7.8194e-14 | 7.8194e-14 | 7.8194e-14 | 7.8194e-14 | 7.8194e-14 | 7.8194e-14 | 7.8194e-14 | 7.8194e-14 | 7.8194e-14 | 7.8194e-14 | 7.8194e-14 | 7.8194e-14 | 7.8194e-14 | 7.8194e-14 | 7.8194e-14 | 9.992e-14% | 4391.7028 | 4.8159e-14 | 6.5332e-14 | 7.0027e-14 | 7.0752e-14 | 7.121e-14 | 7.222e-14 | 7.461e-14 | 7.5912e-14 | 7.8397e-14 | 8.5956e-14 | 7.9719e-14 | 7.8498e-14 | 8.0141e-14 | 8.3738e-14 | 8.13e-14 | 8.13e-14 | 8.13e-14 | 8.13e-14 | 8.13e-14 | 8.13e-14 | 8.13e-14 | 8.13e-14 | 8.13e-14 | 8.13e-14 | 8.13e-14 | 8.13e-14 | 8.13e-14 | 8.13e-14 | 8.13e-14 | 8.13e-14
Summer Season | [31 empty] | Summer Season
P50 | [31 empty] | P10
% of MD | Summer - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Summer - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 51.1621 | 67.921 | 72.4827 | 72.3498 | 72.345 | 72.8648 | 73.4353 | 74.6066 | 75.4483 | 75.9048 | 76.4041 | 76.8611 | 77.687 | 78.7121 | 78.6404 | 78.6404 | 78.6404 | 78.6404 | 78.6404 | 78.6404 | 78.6404 | 78.6404 | 78.6404 | 78.6404 | 78.6404 | 78.6404 | 78.6404 | 78.6404 | 78.6404 | 78.6404 | 100% | 0 | 57.0282 | 73.8207 | 78.2145 | 77.9508 | 77.9694 | 78.4199 | 79.6095 | 80.4052 | 81.1846 | 82.0962 | 82.9406 | 83.7606 | 83.8537 | 84.8109 | 84.0841 | 84.0841 | 84.0841 | 84.0841 | 84.0841 | 84.0841 | 84.0841 | 84.0841 | 84.0841 | 84.0841 | 84.0841 | 84.0841 | 84.0841 | 84.0841 | 84.0841 | 84.0841
99% | 0 | 50.6505 | 67.2418 | 71.7579 | 71.6263 | 71.6215 | 72.1362 | 72.701 | 73.8605 | 74.6938 | 75.1458 | 75.64 | 76.0925 | 76.9101 | 77.9249 | 77.854 | 77.854 | 77.854 | 77.854 | 77.854 | 77.854 | 77.854 | 77.854 | 77.854 | 77.854 | 77.854 | 77.854 | 77.854 | 77.854 | 77.854 | 77.854 | 99% | 1.5127 | 56.4579 | 73.0825 | 77.4324 | 77.1713 | 77.1897 | 77.6357 | 78.8134 | 79.6012 | 80.3728 | 81.2753 | 82.1112 | 82.923 | 83.0151 | 83.9628 | 83.2432 | 83.2432 | 83.2432 | 83.2432 | 83.2432 | 83.2432 | 83.2432 | 83.2432 | 83.2432 | 83.2432 | 83.2432 | 83.2432 | 83.2432 | 83.2432 | 83.2432 | 83.2432
98% | 0 | 50.1389 | 66.5626 | 71.033 | 70.9028 | 70.8981 | 71.4075 | 71.9666 | 73.1145 | 73.9393 | 74.3867 | 74.876 | 75.3239 | 76.1333 | 77.1378 | 77.0676 | 77.0676 | 77.0676 | 77.0676 | 77.0676 | 77.0676 | 77.0676 | 77.0676 | 77.0676 | 77.0676 | 77.0676 | 77.0676 | 77.0676 | 77.0676 | 77.0676 | 77.0676 | 98% | 2.269 | 55.8876 | 72.3443 | 76.6503 | 76.3918 | 76.41 | 76.8515 | 78.0173 | 78.7971 | 79.5609 | 80.4543 | 81.2818 | 82.0854 | 82.1766 | 83.1147 | 82.4024 | 82.4024 | 82.4024 | 82.4024 | 82.4024 | 82.4024 | 82.4024 | 82.4024 | 82.4024 | 82.4024 | 82.4024 | 82.4024 | 82.4024 | 82.4024 | 82.4024 | 82.4024
97% | 0.37816 | 49.6272 | 65.8834 | 70.3082 | 70.1794 | 70.1746 | 70.6789 | 71.2323 | 72.3684 | 73.1848 | 73.6277 | 74.112 | 74.5553 | 75.3564 | 76.3507 | 76.2812 | 76.2812 | 76.2812 | 76.2812 | 76.2812 | 76.2812 | 76.2812 | 76.2812 | 76.2812 | 76.2812 | 76.2812 | 76.2812 | 76.2812 | 76.2812 | 76.2812 | 76.2812 | 97% | 3.7816 | 55.3173 | 71.6061 | 75.8681 | 75.6123 | 75.6303 | 76.0673 | 77.2212 | 77.9931 | 78.7491 | 79.6334 | 80.4523 | 81.2478 | 81.338 | 82.2666 | 81.5615 | 81.5615 | 81.5615 | 81.5615 | 81.5615 | 81.5615 | 81.5615 | 81.5615 | 81.5615 | 81.5615 | 81.5615 | 81.5615 | 81.5615 | 81.5615 | 81.5615 | 81.5615
95% | 2.269 | 48.604 | 64.5249 | 68.8586 | 68.7324 | 68.7277 | 69.2216 | 69.7636 | 70.8763 | 71.6758 | 72.1096 | 72.5839 | 73.0181 | 73.8027 | 74.7765 | 74.7084 | 74.7084 | 74.7084 | 74.7084 | 74.7084 | 74.7084 | 74.7084 | 74.7084 | 74.7084 | 74.7084 | 74.7084 | 74.7084 | 74.7084 | 74.7084 | 74.7084 | 74.7084 | 95% | 6.0506 | 54.1768 | 70.1297 | 74.3038 | 74.0533 | 74.071 | 74.4989 | 75.629 | 76.385 | 77.1254 | 77.9914 | 78.7935 | 79.5726 | 79.661 | 80.5703 | 79.8799 | 79.8799 | 79.8799 | 79.8799 | 79.8799 | 79.8799 | 79.8799 | 79.8799 | 79.8799 | 79.8799 | 79.8799 | 79.8799 | 79.8799 | 79.8799 | 79.8799 | 79.8799
90% | 5.6725 | 46.0459 | 61.1289 | 65.2344 | 65.1149 | 65.1105 | 65.5784 | 66.0918 | 67.1459 | 67.9034 | 68.3143 | 68.7637 | 69.175 | 69.9183 | 70.8409 | 70.7764 | 70.7764 | 70.7764 | 70.7764 | 70.7764 | 70.7764 | 70.7764 | 70.7764 | 70.7764 | 70.7764 | 70.7764 | 70.7764 | 70.7764 | 70.7764 | 70.7764 | 70.7764 | 90% | 16.2611 | 51.3254 | 66.4386 | 70.3931 | 70.1557 | 70.1725 | 70.5779 | 71.6485 | 72.3647 | 73.0662 | 73.8866 | 74.6465 | 75.3846 | 75.4683 | 76.3298 | 75.6757 | 75.6757 | 75.6757 | 75.6757 | 75.6757 | 75.6757 | 75.6757 | 75.6757 | 75.6757 | 75.6757 | 75.6757 | 75.6757 | 75.6757 | 75.6757 | 75.6757 | 75.6757
85% | 15.8829 | 43.4878 | 57.7328 | 61.6103 | 61.4974 | 61.4932 | 61.9351 | 62.42 | 63.4156 | 64.131 | 64.5191 | 64.9435 | 65.332 | 66.034 | 66.9053 | 66.8444 | 66.8444 | 66.8444 | 66.8444 | 66.8444 | 66.8444 | 66.8444 | 66.8444 | 66.8444 | 66.8444 | 66.8444 | 66.8444 | 66.8444 | 66.8444 | 66.8444 | 66.8444 | 85% | 26.4715 | 48.4739 | 62.7476 | 66.4824 | 66.2582 | 66.274 | 66.6569 | 67.6681 | 68.3445 | 69.0069 | 69.7818 | 70.4995 | 71.1965 | 71.2756 | 72.0892 | 71.4715 | 71.4715 | 71.4715 | 71.4715 | 71.4715 | 71.4715 | 71.4715 | 71.4715 | 71.4715 | 71.4715 | 71.4715 | 71.4715 | 71.4715 | 71.4715 | 71.4715 | 71.4715
80% | 31.0095 | 40.9297 | 54.3368 | 57.9862 | 57.8799 | 57.876 | 58.2919 | 58.7483 | 59.6853 | 60.3586 | 60.7239 | 61.1233 | 61.4889 | 62.1496 | 62.9697 | 62.9123 | 62.9123 | 62.9123 | 62.9123 | 62.9123 | 62.9123 | 62.9123 | 62.9123 | 62.9123 | 62.9123 | 62.9123 | 62.9123 | 62.9123 | 62.9123 | 62.9123 | 62.9123 | 80% | 34.0348 | 45.6225 | 59.0566 | 62.5716 | 62.3606 | 62.3755 | 62.7359 | 63.6876 | 64.3242 | 64.9477 | 65.677 | 66.3524 | 67.0085 | 67.0829 | 67.8487 | 67.2672 | 67.2672 | 67.2672 | 67.2672 | 67.2672 | 67.2672 | 67.2672 | 67.2672 | 67.2672 | 67.2672 | 67.2672 | 67.2672 | 67.2672 | 67.2672 | 67.2672 | 67.2672
75% | 72.9857 | 38.3716 | 50.9407 | 54.362 | 54.2624 | 54.2587 | 54.6486 | 55.0765 | 55.955 | 56.5862 | 56.9286 | 57.3031 | 57.6458 | 58.2653 | 59.0341 | 58.9803 | 58.9803 | 58.9803 | 58.9803 | 58.9803 | 58.9803 | 58.9803 | 58.9803 | 58.9803 | 58.9803 | 58.9803 | 58.9803 | 58.9803 | 58.9803 | 58.9803 | 58.9803 | 75% | 48.405 | 42.7711 | 55.3655 | 58.6609 | 58.4631 | 58.4771 | 58.8149 | 59.7071 | 60.3039 | 60.8885 | 61.5722 | 62.2054 | 62.8205 | 62.8902 | 63.6082 | 63.063 | 63.063 | 63.063 | 63.063 | 63.063 | 63.063 | 63.063 | 63.063 | 63.063 | 63.063 | 63.063 | 63.063 | 63.063 | 63.063 | 63.063 | 63.063
70% | 150.5094 | 35.8135 | 47.5447 | 50.7379 | 50.6449 | 50.6415 | 51.0054 | 51.4047 | 52.2246 | 52.8138 | 53.1334 | 53.4829 | 53.8028 | 54.3809 | 55.0984 | 55.0483 | 55.0483 | 55.0483 | 55.0483 | 55.0483 | 55.0483 | 55.0483 | 55.0483 | 55.0483 | 55.0483 | 55.0483 | 55.0483 | 55.0483 | 55.0483 | 55.0483 | 55.0483 | 70% | 76.3892 | 39.9197 | 51.6745 | 54.7502 | 54.5656 | 54.5786 | 54.8939 | 55.7266 | 56.2837 | 56.8292 | 57.4674 | 58.0584 | 58.6324 | 58.6976 | 59.3676 | 58.8588 | 58.8588 | 58.8588 | 58.8588 | 58.8588 | 58.8588 | 58.8588 | 58.8588 | 58.8588 | 58.8588 | 58.8588 | 58.8588 | 58.8588 | 58.8588 | 58.8588 | 58.8588
65% | 359.6342 | 33.2554 | 44.1486 | 47.1138 | 47.0274 | 47.0242 | 47.3621 | 47.733 | 48.4943 | 49.0414 | 49.3381 | 49.6627 | 49.9597 | 50.4966 | 51.1628 | 51.1163 | 51.1163 | 51.1163 | 51.1163 | 51.1163 | 51.1163 | 51.1163 | 51.1163 | 51.1163 | 51.1163 | 51.1163 | 51.1163 | 51.1163 | 51.1163 | 51.1163 | 51.1163 | 65% | 114.2056 | 37.0683 | 47.9835 | 50.8395 | 50.668 | 50.6801 | 50.9729 | 51.7462 | 52.2634 | 52.77 | 53.3626 | 53.9114 | 54.4444 | 54.5049 | 55.1271 | 54.6546 | 54.6546 | 54.6546 | 54.6546 | 54.6546 | 54.6546 | 54.6546 | 54.6546 | 54.6546 | 54.6546 | 54.6546 | 54.6546 | 54.6546 | 54.6546 | 54.6546 | 54.6546
60% | 689.7717 | 30.6973 | 40.7526 | 43.4896 | 43.4099 | 43.407 | 43.7189 | 44.0612 | 44.764 | 45.269 | 45.5429 | 45.8424 | 46.1167 | 46.6122 | 47.2272 | 47.1843 | 47.1843 | 47.1843 | 47.1843 | 47.1843 | 47.1843 | 47.1843 | 47.1843 | 47.1843 | 47.1843 | 47.1843 | 47.1843 | 47.1843 | 47.1843 | 47.1843 | 47.1843 | 60% | 178.1154 | 34.2169 | 44.2924 | 46.9287 | 46.7705 | 46.7817 | 47.0519 | 47.7657 | 48.2431 | 48.7108 | 49.2577 | 49.7643 | 50.2564 | 50.3122 | 50.8865 | 50.4504 | 50.4504 | 50.4504 | 50.4504 | 50.4504 | 50.4504 | 50.4504 | 50.4504 | 50.4504 | 50.4504 | 50.4504 | 50.4504 | 50.4504 | 50.4504 | 50.4504 | 50.4504
55% | 1095.5419 | 28.1392 | 37.3565 | 39.8655 | 39.7924 | 39.7897 | 40.0757 | 40.3894 | 41.0336 | 41.4965 | 41.7476 | 42.0222 | 42.2736 | 42.7279 | 43.2916 | 43.2522 | 43.2522 | 43.2522 | 43.2522 | 43.2522 | 43.2522 | 43.2522 | 43.2522 | 43.2522 | 43.2522 | 43.2522 | 43.2522 | 43.2522 | 43.2522 | 43.2522 | 43.2522 | 55% | 311.6074 | 31.3655 | 40.6014 | 43.018 | 42.8729 | 42.8832 | 43.131 | 43.7852 | 44.2229 | 44.6515 | 45.1529 | 45.6173 | 46.0683 | 46.1195 | 46.646 | 46.2462 | 46.2462 | 46.2462 | 46.2462 | 46.2462 | 46.2462 | 46.2462 | 46.2462 | 46.2462 | 46.2462 | 46.2462 | 46.2462 | 46.2462 | 46.2462 | 46.2462 | 46.2462
50% | 1666.1918 | 25.581 | 33.9605 | 36.2413 | 36.1749 | 36.1725 | 36.4324 | 36.7177 | 37.3033 | 37.7241 | 37.9524 | 38.202 | 38.4306 | 38.8435 | 39.356 | 39.3202 | 39.3202 | 39.3202 | 39.3202 | 39.3202 | 39.3202 | 39.3202 | 39.3202 | 39.3202 | 39.3202 | 39.3202 | 39.3202 | 39.3202 | 39.3202 | 39.3202 | 39.3202 | 50% | 636.0723 | 28.5141 | 36.9103 | 39.1073 | 38.9754 | 38.9847 | 39.21 | 39.8047 | 40.2026 | 40.5923 | 41.0481 | 41.4703 | 41.8803 | 41.9268 | 42.4054 | 42.042 | 42.042 | 42.042 | 42.042 | 42.042 | 42.042 | 42.042 | 42.042 | 42.042 | 42.042 | 42.042 | 42.042 | 42.042 | 42.042 | 42.042 | 42.042
45% | 2506.0947 | 23.0229 | 30.5644 | 32.6172 | 32.5574 | 32.5552 | 32.7892 | 33.0459 | 33.573 | 33.9517 | 34.1572 | 34.3818 | 34.5875 | 34.9592 | 35.4204 | 35.3882 | 35.3882 | 35.3882 | 35.3882 | 35.3882 | 35.3882 | 35.3882 | 35.3882 | 35.3882 | 35.3882 | 35.3882 | 35.3882 | 35.3882 | 35.3882 | 35.3882 | 35.3882 | 45% | 1179.4944 | 25.6627 | 33.2193 | 35.1965 | 35.0779 | 35.0862 | 35.289 | 35.8243 | 36.1824 | 36.5331 | 36.9433 | 37.3233 | 37.6923 | 37.7341 | 38.1649 | 37.8378 | 37.8378 | 37.8378 | 37.8378 | 37.8378 | 37.8378 | 37.8378 | 37.8378 | 37.8378 | 37.8378 | 37.8378 | 37.8378 | 37.8378 | 37.8378 | 37.8378 | 37.8378
40% | 3164.4787 | 20.4648 | 27.1684 | 28.9931 | 28.9399 | 28.938 | 29.1459 | 29.3741 | 29.8426 | 30.1793 | 30.3619 | 30.5616 | 30.7444 | 31.0748 | 31.4848 | 31.4562 | 31.4562 | 31.4562 | 31.4562 | 31.4562 | 31.4562 | 31.4562 | 31.4562 | 31.4562 | 31.4562 | 31.4562 | 31.4562 | 31.4562 | 31.4562 | 31.4562 | 31.4562 | 40% | 1808.3816 | 22.8113 | 29.5283 | 31.2858 | 31.1803 | 31.1878 | 31.368 | 31.8438 | 32.1621 | 32.4738 | 32.8385 | 33.1762 | 33.5042 | 33.5415 | 33.9244 | 33.6336 | 33.6336 | 33.6336 | 33.6336 | 33.6336 | 33.6336 | 33.6336 | 33.6336 | 33.6336 | 33.6336 | 33.6336 | 33.6336 | 33.6336 | 33.6336 | 33.6336 | 33.6336
35% | 3551.3408 | 17.9067 | 23.7723 | 25.3689 | 25.3224 | 25.3207 | 25.5027 | 25.7024 | 26.1123 | 26.4069 | 26.5667 | 26.7414 | 26.9014 | 27.1905 | 27.5492 | 27.5241 | 27.5241 | 27.5241 | 27.5241 | 27.5241 | 27.5241 | 27.5241 | 27.5241 | 27.5241 | 27.5241 | 27.5241 | 27.5241 | 27.5241 | 27.5241 | 27.5241 | 27.5241 | 35% | 2779.1293 | 19.9599 | 25.8372 | 27.3751 | 27.2828 | 27.2893 | 27.447 | 27.8633 | 28.1418 | 28.4146 | 28.7337 | 29.0292 | 29.3162 | 29.3488 | 29.6838 | 29.4294 | 29.4294 | 29.4294 | 29.4294 | 29.4294 | 29.4294 | 29.4294 | 29.4294 | 29.4294 | 29.4294 | 29.4294 | 29.4294 | 29.4294 | 29.4294 | 29.4294 | 29.4294
30% | 3758.953 | 15.3486 | 20.3763 | 21.7448 | 21.705 | 21.7035 | 21.8595 | 22.0306 | 22.382 | 22.6345 | 22.7714 | 22.9212 | 23.0583 | 23.3061 | 23.6136 | 23.5921 | 23.5921 | 23.5921 | 23.5921 | 23.5921 | 23.5921 | 23.5921 | 23.5921 | 23.5921 | 23.5921 | 23.5921 | 23.5921 | 23.5921 | 23.5921 | 23.5921 | 23.5921 | 30% | 3814.165 | 17.1085 | 22.1462 | 23.4644 | 23.3852 | 23.3908 | 23.526 | 23.8828 | 24.1216 | 24.3554 | 24.6289 | 24.8822 | 25.1282 | 25.1561 | 25.4433 | 25.2252 | 25.2252 | 25.2252 | 25.2252 | 25.2252 | 25.2252 | 25.2252 | 25.2252 | 25.2252 | 25.2252 | 25.2252 | 25.2252 | 25.2252 | 25.2252 | 25.2252 | 25.2252
25% | 3926.4798 | 12.7905 | 16.9802 | 18.1207 | 18.0875 | 18.0862 | 18.2162 | 18.3588 | 18.6517 | 18.8621 | 18.9762 | 19.101 | 19.2153 | 19.4218 | 19.678 | 19.6601 | 19.6601 | 19.6601 | 19.6601 | 19.6601 | 19.6601 | 19.6601 | 19.6601 | 19.6601 | 19.6601 | 19.6601 | 19.6601 | 19.6601 | 19.6601 | 19.6601 | 19.6601 | 25% | 4166.9923 | 14.257 | 18.4552 | 19.5536 | 19.4877 | 19.4924 | 19.605 | 19.9024 | 20.1013 | 20.2962 | 20.5241 | 20.7351 | 20.9402 | 20.9634 | 21.2027 | 21.021 | 21.021 | 21.021 | 21.021 | 21.021 | 21.021 | 21.021 | 21.021 | 21.021 | 21.021 | 21.021 | 21.021 | 21.021 | 21.021 | 21.021 | 21.021
20% | 4050.5177 | 10.2324 | 13.5842 | 14.4965 | 14.47 | 14.469 | 14.573 | 14.6871 | 14.9213 | 15.0897 | 15.181 | 15.2808 | 15.3722 | 15.5374 | 15.7424 | 15.7281 | 15.7281 | 15.7281 | 15.7281 | 15.7281 | 15.7281 | 15.7281 | 15.7281 | 15.7281 | 15.7281 | 15.7281 | 15.7281 | 15.7281 | 15.7281 | 15.7281 | 15.7281 | 20% | 4282.7105 | 11.4056 | 14.7641 | 15.6429 | 15.5902 | 15.5939 | 15.684 | 15.9219 | 16.081 | 16.2369 | 16.4192 | 16.5881 | 16.7521 | 16.7707 | 16.9622 | 16.8168 | 16.8168 | 16.8168 | 16.8168 | 16.8168 | 16.8168 | 16.8168 | 16.8168 | 16.8168 | 16.8168 | 16.8168 | 16.8168 | 16.8168 | 16.8168 | 16.8168 | 16.8168
15% | 4152.622 | 7.6743 | 10.1881 | 10.8724 | 10.8525 | 10.8517 | 10.9297 | 11.0153 | 11.191 | 11.3172 | 11.3857 | 11.4606 | 11.5292 | 11.6531 | 11.8068 | 11.7961 | 11.7961 | 11.7961 | 11.7961 | 11.7961 | 11.7961 | 11.7961 | 11.7961 | 11.7961 | 11.7961 | 11.7961 | 11.7961 | 11.7961 | 11.7961 | 11.7961 | 11.7961 | 15% | 4364.7722 | 8.5542 | 11.0731 | 11.7322 | 11.6926 | 11.6954 | 11.763 | 11.9414 | 12.0608 | 12.1777 | 12.3144 | 12.4411 | 12.5641 | 12.578 | 12.7216 | 12.6126 | 12.6126 | 12.6126 | 12.6126 | 12.6126 | 12.6126 | 12.6126 | 12.6126 | 12.6126 | 12.6126 | 12.6126 | 12.6126 | 12.6126 | 12.6126 | 12.6126 | 12.6126
10% | 4248.2976 | 5.1162 | 6.7921 | 7.2483 | 7.235 | 7.2345 | 7.2865 | 7.3435 | 7.4607 | 7.5448 | 7.5905 | 7.6404 | 7.6861 | 7.7687 | 7.8712 | 7.864 | 7.864 | 7.864 | 7.864 | 7.864 | 7.864 | 7.864 | 7.864 | 7.864 | 7.864 | 7.864 | 7.864 | 7.864 | 7.864 | 7.864 | 7.864 | 10% | 4391.6218 | 5.7028 | 7.3821 | 7.8215 | 7.7951 | 7.7969 | 7.842 | 7.9609 | 8.0405 | 8.1185 | 8.2096 | 8.2941 | 8.3761 | 8.3854 | 8.4811 | 8.4084 | 8.4084 | 8.4084 | 8.4084 | 8.4084 | 8.4084 | 8.4084 | 8.4084 | 8.4084 | 8.4084 | 8.4084 | 8.4084 | 8.4084 | 8.4084 | 8.4084 | 8.4084
5% | 4361.7469 | 2.5581 | 3.396 | 3.6241 | 3.6175 | 3.6172 | 3.6432 | 3.6718 | 3.7303 | 3.7724 | 3.7952 | 3.8202 | 3.8431 | 3.8844 | 3.9356 | 3.932 | 3.932 | 3.932 | 3.932 | 3.932 | 3.932 | 3.932 | 3.932 | 3.932 | 3.932 | 3.932 | 3.932 | 3.932 | 3.932 | 3.932 | 3.932 | 5% | 4391.6218 | 2.8514 | 3.691 | 3.9107 | 3.8975 | 3.8985 | 3.921 | 3.9805 | 4.0203 | 4.0592 | 4.1048 | 4.147 | 4.188 | 4.1927 | 4.2405 | 4.2042 | 4.2042 | 4.2042 | 4.2042 | 4.2042 | 4.2042 | 4.2042 | 4.2042 | 4.2042 | 4.2042 | 4.2042 | 4.2042 | 4.2042 | 4.2042 | 4.2042 | 4.2042
9.992e-14% | 4391.6218 | 5.1121e-14 | 6.7867e-14 | 7.2425e-14 | 7.2292e-14 | 7.2287e-14 | 7.2807e-14 | 7.3377e-14 | 7.4547e-14 | 7.5388e-14 | 7.5844e-14 | 7.6343e-14 | 7.68e-14 | 7.7625e-14 | 7.8649e-14 | 7.8578e-14 | 7.8578e-14 | 7.8578e-14 | 7.8578e-14 | 7.8578e-14 | 7.8578e-14 | 7.8578e-14 | 7.8578e-14 | 7.8578e-14 | 7.8578e-14 | 7.8578e-14 | 7.8578e-14 | 7.8578e-14 | 7.8578e-14 | 7.8578e-14 | 7.8578e-14 | 9.992e-14% | 4391.6218 | 5.6983e-14 | 7.3762e-14 | 7.8152e-14 | 7.7889e-14 | 7.7907e-14 | 7.8357e-14 | 7.9546e-14 | 8.0341e-14 | 8.112e-14 | 8.2031e-14 | 8.2874e-14 | 8.3694e-14 | 8.3787e-14 | 8.4743e-14 | 8.4017e-14 | 8.4017e-14 | 8.4017e-14 | 8.4017e-14 | 8.4017e-14 | 8.4017e-14 | 8.4017e-14 | 8.4017e-14 | 8.4017e-14 | 8.4017e-14 | 8.4017e-14 | 8.4017e-14 | 8.4017e-14 | 8.4017e-14 | 8.4017e-14 | 8.4017e-14

## Locational VCR
Base case |  | Energy Usage (CY 2024 kWh) | Energy Usage (CY 2024 %) | Tailored VCR
Dec 24 AER VCR ($/kWh) - Res | 49.23 | 67934749.1441 | 34.06% | 16.7657
Dec 24 AER VCR ($/kWh) - Com | 34.39 | 101368150.4504 | 50.82% | 17.4756
Dec 24 AER VCR ($/kWh) - Ind | 33.49 | 17726336.2671 | 8.886% | 2.976
Dec 24 AER VCR ($/kWh) - Agr | 22.25 | 12451243.5083 | 6.242% | 1.3888
|  | 199480479.3698 |  | 38.6062 | KW/h
|  |  |  | 38606.1513 | MW/h

## E@R N
Option 1 - Do Nothing / Base Case
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99%
98%
97%
95%
90%
85%
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1 Winter POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 1 Winter POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99
98%
97%
95%
90%
85%
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1 Summer POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 1 Summer POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2 - 1B New PHS ZSS + Three new feeders
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99%
98%
97%
95%
90%
85%
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2 Winter POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 2 Winter POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99
98%
97%
95%
90%
85%
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2 Summer POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 2 Summer POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 - 2B PHM 3rd Tx + Switchroom + Two new feeders + OFR12 New Feeder
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99%
98%
97%
95%
90%
85%
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 Winter POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 3 Winter POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99
98%
97%
95%
90%
85%
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 Summer POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 3 Summer POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 - 3B OFR 3rd Tx + Switchroom + Two new feeders + OFR12 New Feeder
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99%
98%
97%
95%
90%
85%
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 Winter POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 4 Winter POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99
98%
97%
95%
90%
85%
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 Summer POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 4 Summer POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 - 4B LLG 2nd Tx + Switchroom + Two new feeders + OFR12 New Feeder
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99%
98%
97%
95%
90%
85%
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 Winter POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 5 Winter POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99
98%
97%
95%
90%
85%
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 Summer POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 5 Summer POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 6 -
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99%
98%
97%
95%
90%
85%
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 6 Winter POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 6 Winter POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99
98%
97%
95%
90%
85%
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 6 Summer POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 6 Summer POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 7 -
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99%
98%
97%
95%
90%
85%
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 7 Winter POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 7 Winter POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99
98%
97%
95%
90%
85%
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 7 Summer POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 7 Summer POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 8 -
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99%
98%
97%
95%
90%
85%
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 8 Winter POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 8 Winter POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99
98%
97%
95%
90%
85%
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 8 Summer POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 8 Summer POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## E@R N-1
Option 1 - Do Nothing / Base Case
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% |  | 19.3557 | 26.0414 | 27.1786 | 28.0631 | 29.5913 | 33.0724 | 35.3998 | 38.3512 | 39.8816 | 41.2259 | 38.7366 | 41.6468 | 46.224 | 42.7448 | 42.7448 | 42.7448 | 42.7448 | 42.7448 | 42.7448 | 42.7448 | 42.7448 | 42.7448 | 42.7448 | 42.7448 | 42.7448 | 42.7448 | 42.7448 | 42.7448 | 42.7448 |  |  | 23.7132 | 30.66 | 31.7324 | 32.4104 | 33.9055 | 37.4409 | 39.3681 | 43.0454 | 54.2301 | 45.0018 | 43.1944 | 45.6265 | 50.9491 | 47.3408 | 47.3408 | 47.3408 | 47.3408 | 47.3408 | 47.3408 | 47.3408 | 47.3408 | 47.3408 | 47.3408 | 47.3408 | 47.3408 | 47.3408 | 47.3408 | 47.3408 | 47.3408
98% |  | 22.1134 | 30.0556 | 31.4065 | 32.4573 | 34.2728 | 38.408 | 41.1729 | 44.679 | 46.497 | 48.0939 | 45.1368 | 48.594 | 54.0314 | 49.8983 | 49.8983 | 49.8983 | 49.8983 | 49.8983 | 49.8983 | 49.8983 | 49.8983 | 49.8983 | 49.8983 | 49.8983 | 49.8983 | 49.8983 | 49.8983 | 49.8983 | 49.8983 |  |  | 27.2899 | 35.5423 | 36.8162 | 37.6217 | 39.3977 | 43.5976 | 45.887 | 50.2554 | 63.5422 | 52.5795 | 50.4324 | 53.3215 | 59.6445 | 55.358 | 55.358 | 55.358 | 55.358 | 55.358 | 55.358 | 55.358 | 55.358 | 55.358 | 55.358 | 55.358 | 55.358 | 55.358 | 55.358 | 55.358 | 55.358
97% |  | 42.0001 | 57.7232 | 60.3976 | 62.4779 | 66.0719 | 74.2584 | 79.732 | 86.673 | 90.2721 | 93.4336 | 87.5793 | 94.4235 | 105.1879 | 97.0056 | 97.0056 | 97.0056 | 97.0056 | 97.0056 | 97.0056 | 97.0056 | 97.0056 | 97.0056 | 97.0056 | 97.0056 | 97.0056 | 97.0056 | 97.0056 | 97.0056 | 97.0056 |  |  | 52.248 | 68.5852 | 71.1071 | 72.7018 | 76.2177 | 84.5323 | 89.0645 | 97.7126 | 124.0163 | 102.3136 | 98.0631 | 103.7826 | 116.3002 | 107.8143 | 107.8143 | 107.8143 | 107.8143 | 107.8143 | 107.8143 | 107.8143 | 107.8143 | 107.8143 | 107.8143 | 107.8143 | 107.8143 | 107.8143 | 107.8143 | 107.8143 | 107.8143
95% |  | 115.9799 | 162.4236 | 170.3233 | 176.4681 | 187.0842 | 211.266 | 227.434 | 247.9367 | 258.5678 | 267.9064 | 250.6138 | 270.8306 | 302.6268 | 278.4578 | 278.4578 | 278.4578 | 278.4578 | 278.4578 | 278.4578 | 278.4578 | 278.4578 | 278.4578 | 278.4578 | 278.4578 | 278.4578 | 278.4578 | 278.4578 | 278.4578 | 278.4578 |  |  | 146.2505 | 194.5083 | 201.9576 | 206.6678 | 217.0533 | 241.6134 | 255.0008 | 280.5461 | 358.2432 | 294.1368 | 281.5814 | 298.4759 | 335.451 | 310.3848 | 310.3848 | 310.3848 | 310.3848 | 310.3848 | 310.3848 | 310.3848 | 310.3848 | 310.3848 | 310.3848 | 310.3848 | 310.3848 | 310.3848 | 310.3848 | 310.3848 | 310.3848
90% |  | 529.8714 | 785.9431 | 829.499 | 863.379 | 921.9121 | 1055.2409 | 1144.3849 | 1257.4283 | 1316.044 | 1367.5334 | 1272.189 | 1383.6562 | 1558.9677 | 1425.7093 | 1425.7093 | 1425.7093 | 1425.7093 | 1425.7093 | 1425.7093 | 1425.7093 | 1425.7093 | 1425.7093 | 1425.7093 | 1425.7093 | 1425.7093 | 1425.7093 | 1425.7093 | 1425.7093 | 1425.7093 |  |  | 696.7712 | 962.8455 | 1003.918 | 1029.8882 | 1087.1494 | 1222.564 | 1296.377 | 1437.2235 | 1865.6143 | 1512.1572 | 1442.9317 | 1536.0814 | 1739.9469 | 1601.7422 | 1601.7422 | 1601.7422 | 1601.7422 | 1601.7422 | 1601.7422 | 1601.7422 | 1601.7422 | 1601.7422 | 1601.7422 | 1601.7422 | 1601.7422 | 1601.7422 | 1601.7422 | 1601.7422 | 1601.7422
85% |  | 874.8065 | 1500.3713 | 1606.7752 | 1689.5415 | 1832.5337 | 2158.2465 | 2376.0188 | 2652.1757 | 2795.3696 | 2921.1546 | 2688.2351 | 2960.5416 | 3388.8149 | 3063.2741 | 3063.2741 | 3063.2741 | 3063.2741 | 3063.2741 | 3063.2741 | 3063.2741 | 3063.2741 | 3063.2741 | 3063.2741 | 3063.2741 | 3063.2741 | 3063.2741 | 3063.2741 | 3063.2741 | 3063.2741 |  |  | 1282.5306 | 1932.5312 | 2032.8683 | 2096.3116 | 2236.1967 | 2567.0047 | 2747.3247 | 3091.4025 | 4137.9307 | 3274.4602 | 3105.3472 | 3332.9054 | 3830.934 | 3493.3099 | 3493.3099 | 3493.3099 | 3493.3099 | 3493.3099 | 3493.3099 | 3493.3099 | 3493.3099 | 3493.3099 | 3493.3099 | 3493.3099 | 3493.3099 | 3493.3099 | 3493.3099 | 3493.3099 | 3493.3099
80% |  | 628.4185 | 1600.7316 | 1766.1149 | 1894.7582 | 2117.0105 | 2623.2647 | 2961.7475 | 3390.9772 | 3613.543 | 3809.0501 | 3447.0242 | 3870.2692 | 4535.9328 | 4029.946 | 4029.946 | 4029.946 | 4029.946 | 4029.946 | 4029.946 | 4029.946 | 4029.946 | 4029.946 | 4029.946 | 4029.946 | 4029.946 | 4029.946 | 4029.946 | 4029.946 | 4029.946 |  |  | 1262.1427 | 2272.4362 | 2428.3899 | 2526.9996 | 2744.4225 | 3258.5963 | 3538.867 | 4073.6659 | 5700.2809 | 4358.1918 | 4095.3401 | 4449.033 | 5223.1171 | 4698.349 | 4698.349 | 4698.349 | 4698.349 | 4698.349 | 4698.349 | 4698.349 | 4698.349 | 4698.349 | 4698.349 | 4698.349 | 4698.349 | 4698.349 | 4698.349 | 4698.349 | 4698.349
75% |  | 35.4297 | 855.1312 | 1037.5951 | 1179.5246 | 1424.7309 | 1983.2706 | 2356.7115 | 2830.2717 | 3075.8238 | 3291.5228 | 2892.1072 | 3359.0645 | 4093.4773 | 3535.2326 | 3535.2326 | 3535.2326 | 3535.2326 | 3535.2326 | 3535.2326 | 3535.2326 | 3535.2326 | 3535.2326 | 3535.2326 | 3535.2326 | 3535.2326 | 3535.2326 | 3535.2326 | 3535.2326 | 3535.2326 |  |  | 481.7498 | 1596.2089 | 1768.2692 | 1877.0633 | 2116.9414 | 2684.2186 | 2993.4354 | 3583.4678 | 5378.0782 | 3897.3793 | 3607.3806 | 3997.6025 | 4851.6333 | 4272.6677 | 4272.6677 | 4272.6677 | 4272.6677 | 4272.6677 | 4272.6677 | 4272.6677 | 4272.6677 | 4272.6677 | 4272.6677 | 4272.6677 | 4272.6677 | 4272.6677 | 4272.6677 | 4272.6677 | 4272.6677
70% |  |  | 65.8085 | 149.3801 | 236.763 | 432.2706 | 1017.18 | 1418.4215 | 1927.2354 | 2191.0675 | 2422.824 | 1993.6741 | 2495.3937 | 3284.4792 | 2684.6765 | 2684.6765 | 2684.6765 | 2684.6765 | 2684.6765 | 2684.6765 | 2684.6765 | 2684.6765 | 2684.6765 | 2684.6765 | 2684.6765 | 2684.6765 | 2684.6765 | 2684.6765 | 2684.6765 | 2684.6765 |  |  |  | 601.3916 | 786.1731 | 903.0662 | 1160.8019 | 1770.3095 | 2102.5457 | 2736.5026 | 4664.7111 | 3073.7829 | 2762.1954 | 3181.4671 | 4099.0755 | 3477.0093 | 3477.0093 | 3477.0093 | 3477.0093 | 3477.0093 | 3477.0093 | 3477.0093 | 3477.0093 | 3477.0093 | 3477.0093 | 3477.0093 | 3477.0093 | 3477.0093 | 3477.0093 | 3477.0093 | 3477.0093
65% | [6 empty] | 67.1746 | 263.316 | 684.8354 | 961.4279 | 1205.6548 | 753.4132 | 1282.1294 | 2113.6742 | 1481.5972 | 1481.5972 | 1481.5972 | 1481.5972 | 1481.5972 | 1481.5972 | 1481.5972 | 1481.5972 | 1481.5972 | 1481.5972 | 1481.5972 | 1481.5972 | 1481.5972 | 1481.5972 | 1481.5972 | 1481.5972 |  |  |  |  | 12.1974 | 34.5742 | 123.0009 | 535.0416 | 868.1429 | 1536.2119 | 3568.1739 | 1891.6407 | 1563.2873 | 2005.1192 | 2972.1025 | 2316.564 | 2316.564 | 2316.564 | 2316.564 | 2316.564 | 2316.564 | 2316.564 | 2316.564 | 2316.564 | 2316.564 | 2316.564 | 2316.564 | 2316.564 | 2316.564 | 2316.564 | 2316.564
60% | [9 empty] | 15.996 | 73.9877 | 0.0013268 | 100.6328 | 637.7145 | 188.7046 | 188.7046 | 188.7046 | 188.7046 | 188.7046 | 188.7046 | 188.7046 | 188.7046 | 188.7046 | 188.7046 | 188.7046 | 188.7046 | 188.7046 | 188.7046 | 188.7046 | 188.7046 | [8 empty] | 4.9606 | 217.4281 | 2207.292 | 451.391 | 232.3927 | 542.8433 | 1551.0908 | 834.0186 | 834.0186 | 834.0186 | 834.0186 | 834.0186 | 834.0186 | 834.0186 | 834.0186 | 834.0186 | 834.0186 | 834.0186 | 834.0186 | 834.0186 | 834.0186 | 834.0186 | 834.0186
55% | [40 empty] | 420.5237 |  |  |  | 95.5636
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 2267.9753 | 5084.2295 | 5678.6703 | 6163.4327 | 7045.478 | 9261.3822 | 10904.3389 | 13160.5637 | 14404.4901 | 15542.3873 | 13468.7106 | 15907.1825 | 20121.1305 | 16877.247 | 16877.247 | 16877.247 | 16877.247 | 16877.247 | 16877.247 | 16877.247 | 16877.247 | 16877.247 | 16877.247 | 16877.247 | 16877.247 | 16877.247 | 16877.247 | 16877.247 | 16877.247 | E @ R (MWh) | 0 | 3972.6958 | 7694.7094 | 8373.4293 | 8817.3048 | 9835.0869 | 12444.9189 | 13980.9735 | 17147.4619 | 28542.6368 | 18953.035 | 17282.1464 | 19546.2584 | 24925.8084 | 21214.5583 | 21214.5583 | 21214.5583 | 21214.5583 | 21214.5583 | 21214.5583 | 21214.5583 | 21214.5583 | 21214.5583 | 21214.5583 | 21214.5583 | 21214.5583 | 21214.5583 | 21214.5583 | 21214.5583 | 21214.5583
Option 1 Winter POE50 W E @ R (MWh) N 1 | 0 | 1587.5827 | 3558.9606 | 3975.0692 | 4314.4029 | 4931.8346 | 6482.9675 | 7633.0372 | 9212.3946 | 10083.1431 | 10879.6711 | 9428.0974 | 11135.0277 | 14084.7914 | 11814.0729 | 11814.0729 | 11814.0729 | 11814.0729 | 11814.0729 | 11814.0729 | 11814.0729 | 11814.0729 | 11814.0729 | 11814.0729 | 11814.0729 | 11814.0729 | 11814.0729 | 11814.0729 | 11814.0729 | 11814.0729 | Option 1 Winter POE10 W E @ R (MWh) N 1 | 0 | 1191.8087 | 2308.4128 | 2512.0288 | 2645.1914 | 2950.5261 | 3733.4757 | 4194.2921 | 5144.2386 | 8562.791 | 5685.9105 | 5184.6439 | 5863.8775 | 7477.7425 | 6364.3675 | 6364.3675 | 6364.3675 | 6364.3675 | 6364.3675 | 6364.3675 | 6364.3675 | 6364.3675 | 6364.3675 | 6364.3675 | 6364.3675 | 6364.3675 | 6364.3675 | 6364.3675 | 6364.3675 | 6364.3675
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 17.7632 | 43.0375 | 49.6507 | 49.2537 | 49.2817 | 49.9598 | 51.7502 | 52.9479 | 54.1209 | 55.493 | 56.7638 | 57.998 | 58.138 | 59.5788 | 58.4848 | 58.4848 | 58.4848 | 58.4848 | 58.4848 | 58.4848 | 58.4848 | 58.4848 | 58.4848 | 58.4848 | 58.4848 | 58.4848 | 58.4848 | 58.4848 | 58.4848 | 58.4848
98% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 8.4503 | 20.9604 | 24.2338 | 24.0373 | 24.0512 | 24.3868 | 25.273 | 25.8658 | 26.4464 | 27.1256 | 27.7546 | 28.3655 | 28.4348 | 29.1479 | 28.6065 | 28.6065 | 28.6065 | 28.6065 | 28.6065 | 28.6065 | 28.6065 | 28.6065 | 28.6065 | 28.6065 | 28.6065 | 28.6065 | 28.6065 | 28.6065 | 28.6065 | 28.6065
97% | 1.8466 | 8.0258 | 9.7077 | 9.6587 | 9.6569 | 9.8486 | 10.059 | 10.4908 | 10.8011 | 10.9695 | 11.1536 | 11.3221 | 11.6266 | 12.0045 | 11.9781 | 11.9781 | 11.9781 | 11.9781 | 11.9781 | 11.9781 | 11.9781 | 11.9781 | 11.9781 | 11.9781 | 11.9781 | 11.9781 | 11.9781 | 11.9781 | 11.9781 | 11.9781 |  | 16.0379 | 40.8042 | 47.2844 | 46.8955 | 46.9229 | 47.5873 | 49.3417 | 50.5154 | 51.6648 | 53.0093 | 54.2545 | 55.464 | 55.6012 | 57.013 | 55.941 | 55.941 | 55.941 | 55.941 | 55.941 | 55.941 | 55.941 | 55.941 | 55.941 | 55.941 | 55.941 | 55.941 | 55.941 | 55.941 | 55.941 | 55.941
95% | 7.7819 | 38.2025 | 46.4828 | 46.2417 | 46.2328 | 47.1765 | 48.212 | 50.3381 | 51.8658 | 52.6946 | 53.6008 | 54.4305 | 55.9296 | 57.7903 | 57.6602 | 57.6602 | 57.6602 | 57.6602 | 57.6602 | 57.6602 | 57.6602 | 57.6602 | 57.6602 | 57.6602 | 57.6602 | 57.6602 | 57.6602 | 57.6602 | 57.6602 | 57.6602 |  | 22.1159 | 58.6938 | 68.2646 | 67.6901 | 67.7307 | 68.712 | 71.3031 | 73.0364 | 74.7341 | 76.7198 | 78.559 | 80.3452 | 80.5479 | 82.6329 | 81.0498 | 81.0498 | 81.0498 | 81.0498 | 81.0498 | 81.0498 | 81.0498 | 81.0498 | 81.0498 | 81.0498 | 81.0498 | 81.0498 | 81.0498 | 81.0498 | 81.0498 | 81.0498
90% | 7.9129 | 60.6736 | 75.0348 | 74.6165 | 74.6011 | 76.2379 | 78.0339 | 81.7213 | 84.371 | 85.8084 | 87.3801 | 88.819 | 91.4191 | 94.6462 | 94.4206 | 94.4206 | 94.4206 | 94.4206 | 94.4206 | 94.4206 | 94.4206 | 94.4206 | 94.4206 | 94.4206 | 94.4206 | 94.4206 | 94.4206 | 94.4206 | 94.4206 | 94.4206 |  | 79.1417 | 237.7413 | 279.2396 | 276.7487 | 276.9246 | 281.1792 | 292.4144 | 299.93 | 307.291 | 315.901 | 323.8752 | 331.6203 | 332.499 | 341.5397 | 334.6752 | 334.6752 | 334.6752 | 334.6752 | 334.6752 | 334.6752 | 334.6752 | 334.6752 | 334.6752 | 334.6752 | 334.6752 | 334.6752 | 334.6752 | 334.6752 | 334.6752 | 334.6752
85% | 2.1831 | 147.3455 | 188.1003 | 186.9134 | 186.8697 | 191.5145 | 196.6114 | 207.0756 | 214.595 | 218.674 | 223.1344 | 227.2178 | 234.5963 | 243.7543 | 243.1142 | 243.1142 | 243.1142 | 243.1142 | 243.1142 | 243.1142 | 243.1142 | 243.1142 | 243.1142 | 243.1142 | 243.1142 | 243.1142 | 243.1142 | 243.1142 | 243.1142 | 243.1142 |  | 50.0275 | 200.0542 | 239.3094 | 236.9532 | 237.1195 | 241.1442 | 251.772 | 258.8814 | 265.8444 | 273.989 | 281.5323 | 288.8587 | 289.6899 | 298.2419 | 291.7484 | 291.7484 | 291.7484 | 291.7484 | 291.7484 | 291.7484 | 291.7484 | 291.7484 | 291.7484 | 291.7484 | 291.7484 | 291.7484 | 291.7484 | 291.7484 | 291.7484 | 291.7484
80% |  | 166.9191 | 223.8464 | 222.1885 | 222.1274 | 228.6154 | 235.7349 | 250.3515 | 260.8548 | 266.5525 | 272.783 | 278.4866 | 288.7932 | 301.5853 | 300.6912 | 300.6912 | 300.6912 | 300.6912 | 300.6912 | 300.6912 | 300.6912 | 300.6912 | 300.6912 | 300.6912 | 300.6912 | 300.6912 | 300.6912 | 300.6912 | 300.6912 | 300.6912 |  | 15.4914 | 120.2719 | 147.6883 | 146.0426 | 146.1588 | 148.9697 | 156.3923 | 161.3576 | 166.2207 | 171.909 | 177.1773 | 182.2941 | 182.8747 | 188.8475 | 184.3124 | 184.3124 | 184.3124 | 184.3124 | 184.3124 | 184.3124 | 184.3124 | 184.3124 | 184.3124 | 184.3124 | 184.3124 | 184.3124 | 184.3124 | 184.3124 | 184.3124 | 184.3124
75% |  | 320.647 | 469.0463 | 464.7244 | 464.5651 | 481.4781 | 500.0374 | 538.1403 | 565.5205 | 580.3733 | 596.615 | 611.4834 | 638.3507 | 671.6975 | 669.3666 | 669.3666 | 669.3666 | 669.3666 | 669.3666 | 669.3666 | 669.3666 | 669.3666 | 669.3666 | 669.3666 | 669.3666 | 669.3666 | 669.3666 | 669.3666 | 669.3666 | 669.3666 |  | 0.97657 | 175.4756 | 224.4096 | 221.4724 | 221.6798 | 226.6968 | 239.945 | 248.8073 | 257.4872 | 267.6399 | 277.043 | 286.1758 | 287.212 | 297.8726 | 289.7781 | 289.7781 | 289.7781 | 289.7781 | 289.7781 | 289.7781 | 289.7781 | 289.7781 | 289.7781 | 289.7781 | 289.7781 | 289.7781 | 289.7781 | 289.7781 | 289.7781 | 289.7781
70% |  | 328.9116 | 585.3005 | 577.8335 | 577.5583 | 606.7787 | 638.8436 | 704.6738 | 751.9784 | 777.6395 | 805.7002 | 831.3883 | 877.8068 | 935.42 | 931.3929 | 931.3929 | 931.3929 | 931.3929 | 931.3929 | 931.3929 | 931.3929 | 931.3929 | 931.3929 | 931.3929 | 931.3929 | 931.3929 | 931.3929 | 931.3929 | 931.3929 | 931.3929 |  |  | 238.4252 | 327.5698 | 322.219 | 322.5968 | 331.7364 | 355.8711 | 372.0158 | 387.8282 | 406.3238 | 423.4537 | 440.0913 | 441.9789 | 461.3997 | 446.6536 | 446.6536 | 446.6536 | 446.6536 | 446.6536 | 446.6536 | 446.6536 | 446.6536 | 446.6536 | 446.6536 | 446.6536 | 446.6536 | 446.6536 | 446.6536 | 446.6536 | 446.6536
65% |  | 199.3768 | 820.987 | 802.2336 | 801.5424 | 874.9301 | 955.4618 | 1120.7959 | 1239.6024 | 1304.0507 | 1374.5258 | 1439.0422 | 1555.6231 | 1700.32 | 1690.2059 | 1690.2059 | 1690.2059 | 1690.2059 | 1690.2059 | 1690.2059 | 1690.2059 | 1690.2059 | 1690.2059 | 1690.2059 | 1690.2059 | 1690.2059 | 1690.2059 | 1690.2059 | 1690.2059 | 1690.2059 |  |  | 182.6144 | 294.7721 | 288.04 | 288.5153 | 300.0144 | 330.3796 | 350.692 | 370.5866 | 393.8569 | 415.4089 | 436.3416 | 438.7165 | 463.1508 | 444.598 | 444.598 | 444.598 | 444.598 | 444.598 | 444.598 | 444.598 | 444.598 | 444.598 | 444.598 | 444.598 | 444.598 | 444.598 | 444.598 | 444.598 | 444.598
60% |  |  | 203.5024 | 187.5582 | 186.9825 | 252.8081 | 335.7847 | 540.3015 | 711.4984 | 805.7041 | 908.7192 | 1003.0243 | 1173.4335 | 1384.9404 | 1370.1564 | 1370.1564 | 1370.1564 | 1370.1564 | 1370.1564 | 1370.1564 | 1370.1564 | 1370.1564 | 1370.1564 | 1370.1564 | 1370.1564 | 1370.1564 | 1370.1564 | 1370.1564 | 1370.1564 | 1370.1564 |  |  | 77.0598 | 248.2313 | 237.6968 | 238.4405 | 256.4344 | 303.9503 | 335.7356 | 366.8668 | 403.2805 | 437.0055 | 469.7612 | 473.4775 | 511.7128 | 482.681 | 482.681 | 482.681 | 482.681 | 482.681 | 482.681 | 482.681 | 482.681 | 482.681 | 482.681 | 482.681 | 482.681 | 482.681 | 482.681 | 482.681 | 482.681
55% | [8 empty] | 3.8903 | 15.7556 | 37.6919 | 65.8304 | 135.7599 | 255.725 | 246.1724 | 246.1724 | 246.1724 | 246.1724 | 246.1724 | 246.1724 | 246.1724 | 246.1724 | 246.1724 | 246.1724 | 246.1724 | 246.1724 | 246.1724 | 246.1724 | 246.1724 | 246.1724 |  |  |  | 63.4905 | 53.6808 | 54.3475 | 71.6739 | 128.262 | 174.6238 | 226.4176 | 294.3956 | 359.2034 | 422.1487 | 429.2901 | 502.7651 | 446.976 | 446.976 | 446.976 | 446.976 | 446.976 | 446.976 | 446.976 | 446.976 | 446.976 | 446.976 | 446.976 | 446.976 | 446.976 | 446.976 | 446.976 | 446.976
50% | [40 empty] | 0.92441 | 14.9076 | 44.2124 | 48.4954 | 103.6497 | 59.9312 | 59.9312 | 59.9312 | 59.9312 | 59.9312 | 59.9312 | 59.9312 | 59.9312 | 59.9312 | 59.9312 | 59.9312 | 59.9312 | 59.9312 | 59.9312 | 59.9312 | 59.9312
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 19.7244 | 1270.1019 | 2622.0083 | 2571.9686 | 2570.1362 | 2769.3877 | 2998.7788 | 3503.8889 | 3894.9777 | 4118.2221 | 4371.3041 | 4611.0446 | 5063.3387 | 5657.8836 | 5615.1586 | 5615.1586 | 5615.1586 | 5615.1586 | 5615.1586 | 5615.1586 | 5615.1586 | 5615.1586 | 5615.1586 | 5615.1586 | 5615.1586 | 5615.1586 | 5615.1586 | 5615.1586 | 5615.1586 | 5615.1586 | E @ R (MWh) | 210.0044 | 1395.1384 | 2014.1441 | 1970.7302 | 1973.7695 | 2048.4946 | 2256.6548 | 2404.4088 | 2555.5088 | 2740.5678 | 2926.9386 | 3123.6769 | 3146.9559 | 3397.5525 | 3205.4359 | 3205.4359 | 3205.4359 | 3205.4359 | 3205.4359 | 3205.4359 | 3205.4359 | 3205.4359 | 3205.4359 | 3205.4359 | 3205.4359 | 3205.4359 | 3205.4359 | 3205.4359 | 3205.4359 | 3205.4359
Option 1 Summer POE50 W E @ R (MWh) N 1 | 13.8071 | 889.0713 | 1835.4058 | 1800.378 | 1799.0954 | 1938.5714 | 2099.1452 | 2452.7222 | 2726.4844 | 2882.7555 | 3059.9129 | 3227.7312 | 3544.3371 | 3960.5185 | 3930.611 | 3930.611 | 3930.611 | 3930.611 | 3930.611 | 3930.611 | 3930.611 | 3930.611 | 3930.611 | 3930.611 | 3930.611 | 3930.611 | 3930.611 | 3930.611 | 3930.611 | 3930.611 | Option 1 Summer POE10 W E @ R (MWh) N 1 | 63.0013 | 418.5415 | 604.2432 | 591.2191 | 592.1308 | 614.5484 | 676.9964 | 721.3226 | 766.6526 | 822.1703 | 878.0816 | 937.1031 | 944.0868 | 1019.2657 | 961.6308 | 961.6308 | 961.6308 | 961.6308 | 961.6308 | 961.6308 | 961.6308 | 961.6308 | 961.6308 | 961.6308 | 961.6308 | 961.6308 | 961.6308 | 961.6308 | 961.6308 | 961.6308
Option 2 - 1B New PHS ZSS + Three new feeders
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% |  | 19.3557 | 26.0414 |  |  | 1.0058 | 4.4868 | 6.8142 | 9.7657 | 11.296 | 12.6403 | 10.151 | 13.0613 | 17.6384 | 14.1592 | 14.1592 | 14.1592 | 14.1592 | 14.1592 | 14.1592 | 14.1592 | 14.1592 | 14.1592 | 14.1592 | 14.1592 | 14.1592 | 14.1592 | 14.1592 | 14.1592 | 14.1592 |  |  | 23.7132 | 30.66 | 3.1468 | 3.8249 | 5.3199 | 8.8554 | 10.7826 | 14.4599 | 25.6446 | 16.4163 | 14.6089 | 17.0409 | 22.3636 | 18.7552 | 18.7552 | 18.7552 | 18.7552 | 18.7552 | 18.7552 | 18.7552 | 18.7552 | 18.7552 | 18.7552 | 18.7552 | 18.7552 | 18.7552 | 18.7552 | 18.7552 | 18.7552
98% |  | 22.1134 | 30.0556 |  |  | 0.32451 | 4.4501 | 7.215 | 10.7211 | 12.5391 | 14.136 | 11.1789 | 14.6361 | 20.0735 | 15.9404 | 15.9404 | 15.9404 | 15.9404 | 15.9404 | 15.9404 | 15.9404 | 15.9404 | 15.9404 | 15.9404 | 15.9404 | 15.9404 | 15.9404 | 15.9404 | 15.9404 | 15.9404 |  |  | 27.2899 | 35.5423 | 2.8583 | 3.6638 | 5.4398 | 9.6397 | 11.9291 | 16.2975 | 29.5842 | 18.6216 | 16.4745 | 19.3636 | 25.6866 | 21.4001 | 21.4001 | 21.4001 | 21.4001 | 21.4001 | 21.4001 | 21.4001 | 21.4001 | 21.4001 | 21.4001 | 21.4001 | 21.4001 | 21.4001 | 21.4001 | 21.4001 | 21.4001
97% |  | 42.0001 | 57.7232 |  |  |  | 7.0321 | 12.5057 | 19.4467 | 23.0457 | 26.2073 | 20.353 | 27.1972 | 37.9616 | 29.7793 | 29.7793 | 29.7793 | 29.7793 | 29.7793 | 29.7793 | 29.7793 | 29.7793 | 29.7793 | 29.7793 | 29.7793 | 29.7793 | 29.7793 | 29.7793 | 29.7793 | 29.7793 |  |  | 52.248 | 68.5852 | 3.8808 | 5.4754 | 8.9913 | 17.306 | 21.8382 | 30.4863 | 56.79 | 35.0873 | 30.8368 | 36.5563 | 49.0739 | 40.588 | 40.588 | 40.588 | 40.588 | 40.588 | 40.588 | 40.588 | 40.588 | 40.588 | 40.588 | 40.588 | 40.588 | 40.588 | 40.588 | 40.588 | 40.588
95% |  | 115.9799 | 162.4236 |  |  |  | 12.6899 | 28.8579 | 49.3605 | 59.9916 | 69.3303 | 52.0377 | 72.2544 | 104.0506 | 79.8816 | 79.8816 | 79.8816 | 79.8816 | 79.8816 | 79.8816 | 79.8816 | 79.8816 | 79.8816 | 79.8816 | 79.8816 | 79.8816 | 79.8816 | 79.8816 | 79.8816 | 79.8816 |  |  | 146.2505 | 194.5083 | 3.5866 | 8.0916 | 18.4771 | 43.0372 | 56.4246 | 81.9699 | 159.6671 | 95.5606 | 83.0052 | 99.8998 | 136.8748 | 111.8086 | 111.8086 | 111.8086 | 111.8086 | 111.8086 | 111.8086 | 111.8086 | 111.8086 | 111.8086 | 111.8086 | 111.8086 | 111.8086 | 111.8086 | 111.8086 | 111.8086 | 111.8086
90% |  | 529.8714 | 785.9431 |  |  |  | 5.126 | 52.8255 | 162.5588 | 221.1744 | 272.6639 | 177.3195 | 288.7867 | 464.0982 | 330.8398 | 330.8398 | 330.8398 | 330.8398 | 330.8398 | 330.8398 | 330.8398 | 330.8398 | 330.8398 | 330.8398 | 330.8398 | 330.8398 | 330.8398 | 330.8398 | 330.8398 | 330.8398 |  |  | 696.7712 | 962.8455 |  | 0.66189 | 16.5828 | 127.6945 | 201.5075 | 342.354 | 770.7448 | 417.2877 | 348.0622 | 441.2119 | 645.0773 | 506.8726 | 506.8726 | 506.8726 | 506.8726 | 506.8726 | 506.8726 | 506.8726 | 506.8726 | 506.8726 | 506.8726 | 506.8726 | 506.8726 | 506.8726 | 506.8726 | 506.8726 | 506.8726
85% |  | 874.8065 | 1500.3713 | [5 empty] | 44.6074 | 132.8184 | 246.4668 | 62.5282 | 285.8538 | 714.1271 | 388.5864 | 388.5864 | 388.5864 | 388.5864 | 388.5864 | 388.5864 | 388.5864 | 388.5864 | 388.5864 | 388.5864 | 388.5864 | 388.5864 | 388.5864 | 388.5864 | 388.5864 | 388.5864 |  |  | 1282.5306 | 1932.5312 |  |  |  | 14.0941 | 98.1803 | 416.7148 | 1463.2429 | 599.7724 | 430.6595 | 658.2176 | 1156.2463 | 818.6221 | 818.6221 | 818.6221 | 818.6221 | 818.6221 | 818.6221 | 818.6221 | 818.6221 | 818.6221 | 818.6221 | 818.6221 | 818.6221 | 818.6221 | 818.6221 | 818.6221 | 818.6221
80% |  | 628.4185 | 1600.7316 | [7 empty] | 0.55909 |  | 5.5961 | 378.9409 | 42.8847 | 42.8847 | 42.8847 | 42.8847 | 42.8847 | 42.8847 | 42.8847 | 42.8847 | 42.8847 | 42.8847 | 42.8847 | 42.8847 | 42.8847 | 42.8847 | 42.8847 | 42.8847 |  |  | 1262.1427 | 2272.4362 | [5 empty] | 59.0563 | 1543.0232 | 224.5658 | 68.0069 | 298.7071 | 1065.8594 | 541.0913 | 541.0913 | 541.0913 | 541.0913 | 541.0913 | 541.0913 | 541.0913 | 541.0913 | 541.0913 | 541.0913 | 541.0913 | 541.0913 | 541.0913 | 541.0913 | 541.0913 | 541.0913
75% | FY26: 35.4297; FY27: 855.1312 |  |  | 481.7498 | 1596.2089 | [6 empty] | 791.4627 |  |  |  | 291.445 | 13.6119 | 13.6119 | 13.6119 | 13.6119 | 13.6119 | 13.6119 | 13.6119 | 13.6119 | 13.6119 | 13.6119 | 13.6119 | 13.6119 | 13.6119 | 13.6119 | 13.6119 | 13.6119
70% | FY27: 65.8085 |  |  |  | 601.3916 | [6 empty] | 44.4503
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 2267.9753 | 5084.2295 | 0 | 0 | 1.3303 | 33.7849 | 108.2183 | 296.46 | 460.8653 | 642.0037 | 333.5683 | 707.3857 | 1736.8902 | 902.0714 | 902.0714 | 902.0714 | 902.0714 | 902.0714 | 902.0714 | 902.0714 | 902.0714 | 902.0714 | 902.0714 | 902.0714 | 902.0714 | 902.0714 | 902.0714 | 902.0714 | 902.0714 | E @ R (MWh) | 0 | 3972.6958 | 7694.7094 | 13.4726 | 21.7177 | 54.8109 | 220.6268 | 400.6622 | 961.3387 | 4884.6098 | 1407.3118 | 991.654 | 1570.9973 | 3392.6268 | 2072.7498 | 2072.7498 | 2072.7498 | 2072.7498 | 2072.7498 | 2072.7498 | 2072.7498 | 2072.7498 | 2072.7498 | 2072.7498 | 2072.7498 | 2072.7498 | 2072.7498 | 2072.7498 | 2072.7498 | 2072.7498
Option 2 Winter POE50 W E @ R (MWh) N 1 | 0 | 1587.5827 | 3558.9606 | 0 | 0 | 0.93121 | 23.6495 | 75.7528 | 207.522 | 322.6057 | 449.4026 | 233.4978 | 495.17 | 1215.8232 | 631.45 | 631.45 | 631.45 | 631.45 | 631.45 | 631.45 | 631.45 | 631.45 | 631.45 | 631.45 | 631.45 | 631.45 | 631.45 | 631.45 | 631.45 | 631.45 | Option 2 Winter POE10 W E @ R (MWh) N 1 | 0 | 1191.8087 | 2308.4128 | 4.0418 | 6.5153 | 16.4433 | 66.188 | 120.1987 | 288.4016 | 1465.3829 | 422.1935 | 297.4962 | 471.2992 | 1017.788 | 621.8249 | 621.8249 | 621.8249 | 621.8249 | 621.8249 | 621.8249 | 621.8249 | 621.8249 | 621.8249 | 621.8249 | 621.8249 | 621.8249 | 621.8249 | 621.8249 | 621.8249 | 621.8249
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 17.7632 | 43.0375 | 49.6507 | 20.1552 | 20.1833 | 20.8613 | 22.6517 | 23.8494 | 25.0224 | 26.3945 | 27.6653 | 28.8995 | 29.0396 | 30.4803 | 29.3864 | 29.3864 | 29.3864 | 29.3864 | 29.3864 | 29.3864 | 29.3864 | 29.3864 | 29.3864 | 29.3864 | 29.3864 | 29.3864 | 29.3864 | 29.3864 | 29.3864 | 29.3864
98% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 8.4503 | 20.9604 | 24.2338 | 9.6343 | 9.6481 | 9.9837 | 10.87 | 11.4628 | 12.0434 | 12.7226 | 13.3516 | 13.9625 | 14.0318 | 14.7449 | 14.2034 | 14.2034 | 14.2034 | 14.2034 | 14.2034 | 14.2034 | 14.2034 | 14.2034 | 14.2034 | 14.2034 | 14.2034 | 14.2034 | 14.2034 | 14.2034 | 14.2034 | 14.2034
97% | 1.8466 | 8.0258 | 9.7077 | 2.5303 | 2.5285 | 2.7202 | 2.9306 | 3.3624 | 3.6727 | 3.8411 | 4.0252 | 4.1937 | 4.4982 | 4.8762 | 4.8497 | 4.8497 | 4.8497 | 4.8497 | 4.8497 | 4.8497 | 4.8497 | 4.8497 | 4.8497 | 4.8497 | 4.8497 | 4.8497 | 4.8497 | 4.8497 | 4.8497 | 4.8497 |  | 16.0379 | 40.8042 | 47.2844 | 18.3819 | 18.4093 | 19.0737 | 20.8282 | 22.0018 | 23.1512 | 24.4957 | 25.741 | 26.9504 | 27.0876 | 28.4994 | 27.4274 | 27.4274 | 27.4274 | 27.4274 | 27.4274 | 27.4274 | 27.4274 | 27.4274 | 27.4274 | 27.4274 | 27.4274 | 27.4274 | 27.4274 | 27.4274 | 27.4274 | 27.4274
95% | 7.7819 | 38.2025 | 46.4828 | 11.148 | 11.1391 | 12.0828 | 13.1184 | 15.2444 | 16.7722 | 17.6009 | 18.5072 | 19.3368 | 20.836 | 22.6966 | 22.5666 | 22.5666 | 22.5666 | 22.5666 | 22.5666 | 22.5666 | 22.5666 | 22.5666 | 22.5666 | 22.5666 | 22.5666 | 22.5666 | 22.5666 | 22.5666 | 22.5666 | 22.5666 |  | 22.1159 | 58.6938 | 68.2646 | 25.5778 | 25.6183 | 26.5996 | 29.1907 | 30.9241 | 32.6217 | 34.6075 | 36.4466 | 38.2328 | 38.4355 | 40.5206 | 38.9374 | 38.9374 | 38.9374 | 38.9374 | 38.9374 | 38.9374 | 38.9374 | 38.9374 | 38.9374 | 38.9374 | 38.9374 | 38.9374 | 38.9374 | 38.9374 | 38.9374 | 38.9374
90% | 7.9129 | 60.6736 | 75.0348 | 13.751 | 13.7356 | 15.3723 | 17.1684 | 20.8558 | 23.5054 | 24.9428 | 26.5146 | 27.9535 | 30.5535 | 33.7806 | 33.5551 | 33.5551 | 33.5551 | 33.5551 | 33.5551 | 33.5551 | 33.5551 | 33.5551 | 33.5551 | 33.5551 | 33.5551 | 33.5551 | 33.5551 | 33.5551 | 33.5551 | 33.5551 |  | 79.1417 | 237.7413 | 279.2396 | 94.1521 | 94.328 | 98.5826 | 109.8178 | 117.3334 | 124.6943 | 133.3043 | 141.2786 | 149.0237 | 149.9024 | 158.9431 | 152.0786 | 152.0786 | 152.0786 | 152.0786 | 152.0786 | 152.0786 | 152.0786 | 152.0786 | 152.0786 | 152.0786 | 152.0786 | 152.0786 | 152.0786 | 152.0786 | 152.0786 | 152.0786
85% | 2.1831 | 147.3455 | 188.1003 | 14.1869 | 14.1431 | 18.7879 | 23.8849 | 34.3491 | 41.8685 | 45.9475 | 50.4079 | 54.4912 | 61.8698 | 71.0278 | 70.3877 | 70.3877 | 70.3877 | 70.3877 | 70.3877 | 70.3877 | 70.3877 | 70.3877 | 70.3877 | 70.3877 | 70.3877 | 70.3877 | 70.3877 | 70.3877 | 70.3877 | 70.3877 |  | 50.0275 | 200.0542 | 239.3094 | 64.2266 | 64.393 | 68.4176 | 79.0455 | 86.1548 | 93.1179 | 101.2625 | 108.8057 | 116.1322 | 116.9634 | 125.5154 | 119.0219 | 119.0219 | 119.0219 | 119.0219 | 119.0219 | 119.0219 | 119.0219 | 119.0219 | 119.0219 | 119.0219 | 119.0219 | 119.0219 | 119.0219 | 119.0219 | 119.0219 | 119.0219
80% |  | 166.9191 | 223.8464 | 0.0117 | 0.010229 | 0.71148 | 2.7221 | 10.7536 | 19.6175 | 25.2837 | 31.5142 | 37.2178 | 47.5244 | 60.3165 | 59.4224 | 59.4224 | 59.4224 | 59.4224 | 59.4224 | 59.4224 | 59.4224 | 59.4224 | 59.4224 | 59.4224 | 59.4224 | 59.4224 | 59.4224 | 59.4224 | 59.4224 | 59.4224 |  | 15.4914 | 120.2719 | 147.6883 | 25.4082 | 25.5244 | 28.3353 | 35.7579 | 40.7232 | 45.5863 | 51.2746 | 56.5429 | 61.6597 | 62.2403 | 68.2131 | 63.678 | 63.678 | 63.678 | 63.678 | 63.678 | 63.678 | 63.678 | 63.678 | 63.678 | 63.678 | 63.678 | 63.678 | 63.678 | 63.678 | 63.678 | 63.678
75% |  | 320.647 | 469.0463 | [6 empty] | 0.4908 | 3.1709 | 7.6247 | 20.3738 | 44.2884 | 42.3342 | 42.3342 | 42.3342 | 42.3342 | 42.3342 | 42.3342 | 42.3342 | 42.3342 | 42.3342 | 42.3342 | 42.3342 | 42.3342 | 42.3342 | 42.3342 | 42.3342 | 42.3342 |  | 0.97657 | 175.4756 | 224.4096 | 8.794 | 8.9301 | 12.524 | 24.6309 | 33.4931 | 42.173 | 52.3258 | 61.7289 | 70.8617 | 71.8979 | 82.5585 | 74.4639 | 74.4639 | 74.4639 | 74.4639 | 74.4639 | 74.4639 | 74.4639 | 74.4639 | 74.4639 | 74.4639 | 74.4639 | 74.4639 | 74.4639 | 74.4639 | 74.4639 | 74.4639
70% | FY26: 328.9116; FY27: 585.3005 |  |  | 238.4252 | 327.5698 |  |  |  | 0.19916 | 2.9615 | 8.7224 | 19.1455 | 32.2015 | 47.8467 | 49.7343 | 69.1551 | 54.409 | 54.409 | 54.409 | 54.409 | 54.409 | 54.409 | 54.409 | 54.409 | 54.409 | 54.409 | 54.409 | 54.409 | 54.409 | 54.409 | 54.409 | 54.409
65% | FY26: 199.3768; FY27: 820.987 |  |  | 182.6144 | 294.7721 | [8 empty] | 0.057639 | 0.15807 | 4.0199 | 0.61882 | 0.61882 | 0.61882 | 0.61882 | 0.61882 | 0.61882 | 0.61882 | 0.61882 | 0.61882 | 0.61882 | 0.61882 | 0.61882 | 0.61882 | 0.61882 | 0.61882 | 0.61882
60% | FY27: 203.5024 |  |  | 77.0598 | 248.2313
55% | [33 empty] | 63.4905
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 19.7244 | 1270.1019 | 2622.0083 | 41.6279 | 41.5566 | 49.6748 | 59.8243 | 84.5653 | 105.4363 | 118.1068 | 134.1399 | 150.8178 | 185.6556 | 236.9861 | 233.1157 | 233.1157 | 233.1157 | 233.1157 | 233.1157 | 233.1157 | 233.1157 | 233.1157 | 233.1157 | 233.1157 | 233.1157 | 233.1157 | 233.1157 | 233.1157 | 233.1157 | 233.1157 | E @ R (MWh) | 210.0044 | 1395.1384 | 2014.1441 | 266.3301 | 267.0345 | 284.3779 | 332.9917 | 368.904 | 407.1327 | 455.533 | 503.7619 | 553.6268 | 559.4907 | 622.6502 | 574.2248 | 574.2248 | 574.2248 | 574.2248 | 574.2248 | 574.2248 | 574.2248 | 574.2248 | 574.2248 | 574.2248 | 574.2248 | 574.2248 | 574.2248 | 574.2248 | 574.2248 | 574.2248
Option 2 Summer POE50 W E @ R (MWh) N 1 | 13.8071 | 889.0713 | 1835.4058 | 29.1395 | 29.0896 | 34.7723 | 41.877 | 59.1957 | 73.8054 | 82.6748 | 93.898 | 105.5724 | 129.9589 | 165.8903 | 163.181 | 163.181 | 163.181 | 163.181 | 163.181 | 163.181 | 163.181 | 163.181 | 163.181 | 163.181 | 163.181 | 163.181 | 163.181 | 163.181 | 163.181 | 163.181 | Option 2 Summer POE10 W E @ R (MWh) N 1 | 63.0013 | 418.5415 | 604.2432 | 79.899 | 80.1104 | 85.3134 | 99.8975 | 110.6712 | 122.1398 | 136.6599 | 151.1286 | 166.0881 | 167.8472 | 186.7951 | 172.2674 | 172.2674 | 172.2674 | 172.2674 | 172.2674 | 172.2674 | 172.2674 | 172.2674 | 172.2674 | 172.2674 | 172.2674 | 172.2674 | 172.2674 | 172.2674 | 172.2674 | 172.2674
Option 3 - 2B PHM 3rd Tx + Switchroom + Two new feeders + OFR12 New Feeder
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | FY26: 19.3557; FY27: 26.0414 |  |  | 23.7132 | 30.66
98% | FY26: 22.1134; FY27: 30.0556 |  |  | 27.2899 | 35.5423
97% | FY26: 42.0001; FY27: 57.7232 |  |  | 52.248 | 68.5852
95% | FY26: 115.9799; FY27: 162.4236 |  |  | 146.2505 | 194.5083
90% | FY26: 529.8714; FY27: 785.9431 |  |  | 696.7712 | 962.8455
85% | FY26: 874.8065; FY27: 1500.3713 |  |  | 1282.5306 | 1932.5312
80% | FY26: 628.4185; FY27: 1600.7316 |  |  | 1262.1427 | 2272.4362
75% | FY26: 35.4297; FY27: 855.1312 |  |  | 481.7498 | 1596.2089
70% | FY27: 65.8085 |  |  |  | 601.3916
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 2267.9753 | 5084.2295 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 3972.6958 | 7694.7094 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 Winter POE50 W E @ R (MWh) N 1 | 0 | 1587.5827 | 3558.9606 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 3 Winter POE10 W E @ R (MWh) N 1 | 0 | 1191.8087 | 2308.4128 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | FY25: 0; FY26: 0; FY27: 0 |  | 17.7632 | 43.0375 | 49.6507
98% | FY25: 0; FY26: 0; FY27: 0 |  | 8.4503 | 20.9604 | 24.2338
97% | FY25: 1.8466; FY26: 8.0258; FY27: 9.7077 |  | 16.0379 | 40.8042 | 47.2844
95% | FY25: 7.7819; FY26: 38.2025; FY27: 46.4828 |  | 22.1159 | 58.6938 | 68.2646
90% | FY25: 7.9129; FY26: 60.6736; FY27: 75.0348 |  | 79.1417 | 237.7413 | 279.2396
85% | FY25: 2.1831; FY26: 147.3455; FY27: 188.1003 |  | 50.0275 | 200.0542 | 239.3094
80% | FY26: 166.9191; FY27: 223.8464 |  | 15.4914 | 120.2719 | 147.6883
75% | FY26: 320.647; FY27: 469.0463 |  | 0.97657 | 175.4756 | 224.4096
70% | FY26: 328.9116; FY27: 585.3005 |  |  | 238.4252 | 327.5698
65% | FY26: 199.3768; FY27: 820.987 |  |  | 182.6144 | 294.7721
60% | FY27: 203.5024 |  |  | 77.0598 | 248.2313
55% | [33 empty] | 63.4905
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 19.7244 | 1270.1019 | 2622.0083 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 210.0044 | 1395.1384 | 2014.1441 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 Summer POE50 W E @ R (MWh) N 1 | 13.8071 | 889.0713 | 1835.4058 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 3 Summer POE10 W E @ R (MWh) N 1 | 63.0013 | 418.5415 | 604.2432 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 - 3B OFR 3rd Tx + Switchroom + Two new feeders + OFR12 New Feeder
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% |  | 19.3557 | 26.0414 | 21.2643 | 22.1489 | 23.6771 | 27.1581 | 29.4855 | 32.4369 | 33.9673 | 35.3116 | 32.8223 | 35.7326 | 40.3097 | 36.8305 | 36.8305 | 36.8305 | 36.8305 | 36.8305 | 36.8305 | 36.8305 | 36.8305 | 36.8305 | 36.8305 | 36.8305 | 36.8305 | 36.8305 | 36.8305 | 36.8305 | 36.8305 |  |  | 23.7132 | 30.66 | 25.8181 | 26.4962 | 27.9912 | 31.5267 | 33.4538 | 37.1312 | 48.3159 | 39.0876 | 37.2802 | 39.7122 | 45.0348 | 41.4265 | 41.4265 | 41.4265 | 41.4265 | 41.4265 | 41.4265 | 41.4265 | 41.4265 | 41.4265 | 41.4265 | 41.4265 | 41.4265 | 41.4265 | 41.4265 | 41.4265 | 41.4265
98% |  | 22.1134 | 30.0556 | 24.3808 | 25.4316 | 27.247 | 31.3823 | 34.1471 | 37.6532 | 39.4712 | 41.0682 | 38.111 | 41.5682 | 47.0056 | 42.8725 | 42.8725 | 42.8725 | 42.8725 | 42.8725 | 42.8725 | 42.8725 | 42.8725 | 42.8725 | 42.8725 | 42.8725 | 42.8725 | 42.8725 | 42.8725 | 42.8725 | 42.8725 |  |  | 27.2899 | 35.5423 | 29.7905 | 30.5959 | 32.3719 | 36.5719 | 38.8612 | 43.2296 | 56.5164 | 45.5537 | 43.4067 | 46.2958 | 52.6187 | 48.3323 | 48.3323 | 48.3323 | 48.3323 | 48.3323 | 48.3323 | 48.3323 | 48.3323 | 48.3323 | 48.3323 | 48.3323 | 48.3323 | 48.3323 | 48.3323 | 48.3323 | 48.3323
97% |  | 42.0001 | 57.7232 | 46.4887 | 48.569 | 52.163 | 60.3495 | 65.8231 | 72.7641 | 76.3632 | 79.5247 | 73.6704 | 80.5146 | 91.279 | 83.0968 | 83.0968 | 83.0968 | 83.0968 | 83.0968 | 83.0968 | 83.0968 | 83.0968 | 83.0968 | 83.0968 | 83.0968 | 83.0968 | 83.0968 | 83.0968 | 83.0968 | 83.0968 |  |  | 52.248 | 68.5852 | 57.1983 | 58.7929 | 62.3088 | 70.6234 | 75.1556 | 83.8037 | 110.1075 | 88.4048 | 84.1542 | 89.8737 | 102.3913 | 93.9054 | 93.9054 | 93.9054 | 93.9054 | 93.9054 | 93.9054 | 93.9054 | 93.9054 | 93.9054 | 93.9054 | 93.9054 | 93.9054 | 93.9054 | 93.9054 | 93.9054 | 93.9054
95% |  | 115.9799 | 162.4236 | 129.2386 | 135.3834 | 145.9995 | 170.1813 | 186.3493 | 206.852 | 217.4831 | 226.8217 | 209.5291 | 229.7459 | 261.5421 | 237.373 | 237.373 | 237.373 | 237.373 | 237.373 | 237.373 | 237.373 | 237.373 | 237.373 | 237.373 | 237.373 | 237.373 | 237.373 | 237.373 | 237.373 | 237.373 |  |  | 146.2505 | 194.5083 | 160.8729 | 165.5831 | 175.9685 | 200.5286 | 213.9161 | 239.4614 | 317.1585 | 253.0521 | 240.4967 | 257.3912 | 294.3662 | 269.3001 | 269.3001 | 269.3001 | 269.3001 | 269.3001 | 269.3001 | 269.3001 | 269.3001 | 269.3001 | 269.3001 | 269.3001 | 269.3001 | 269.3001 | 269.3001 | 269.3001 | 269.3001
90% |  | 529.8714 | 785.9431 | 602.9743 | 636.8542 | 695.3874 | 828.7162 | 917.8602 | 1030.9036 | 1089.5192 | 1141.0087 | 1045.6643 | 1157.1315 | 1332.4429 | 1199.1846 | 1199.1846 | 1199.1846 | 1199.1846 | 1199.1846 | 1199.1846 | 1199.1846 | 1199.1846 | 1199.1846 | 1199.1846 | 1199.1846 | 1199.1846 | 1199.1846 | 1199.1846 | 1199.1846 | 1199.1846 |  |  | 696.7712 | 962.8455 | 777.3933 | 803.3635 | 860.6247 | 996.0393 | 1069.8523 | 1210.6988 | 1639.0896 | 1285.6325 | 1216.407 | 1309.5567 | 1513.4221 | 1375.2174 | 1375.2174 | 1375.2174 | 1375.2174 | 1375.2174 | 1375.2174 | 1375.2174 | 1375.2174 | 1375.2174 | 1375.2174 | 1375.2174 | 1375.2174 | 1375.2174 | 1375.2174 | 1375.2174 | 1375.2174
85% |  | 874.8065 | 1500.3713 | 1053.3915 | 1136.1578 | 1279.15 | 1604.8628 | 1822.6351 | 2098.7921 | 2241.9859 | 2367.7709 | 2134.8514 | 2407.1579 | 2835.4312 | 2509.8905 | 2509.8905 | 2509.8905 | 2509.8905 | 2509.8905 | 2509.8905 | 2509.8905 | 2509.8905 | 2509.8905 | 2509.8905 | 2509.8905 | 2509.8905 | 2509.8905 | 2509.8905 | 2509.8905 | 2509.8905 |  |  | 1282.5306 | 1932.5312 | 1479.4846 | 1542.9279 | 1682.813 | 2013.6211 | 2193.941 | 2538.0189 | 3584.547 | 2721.0765 | 2551.9636 | 2779.5217 | 3277.5504 | 2939.9262 | 2939.9262 | 2939.9262 | 2939.9262 | 2939.9262 | 2939.9262 | 2939.9262 | 2939.9262 | 2939.9262 | 2939.9262 | 2939.9262 | 2939.9262 | 2939.9262 | 2939.9262 | 2939.9262 | 2939.9262
80% |  | 628.4185 | 1600.7316 | 905.9926 | 1034.6359 | 1256.8882 | 1763.1424 | 2101.6252 | 2530.8549 | 2753.4207 | 2948.9279 | 2586.9019 | 3010.1469 | 3675.8105 | 3169.8237 | 3169.8237 | 3169.8237 | 3169.8237 | 3169.8237 | 3169.8237 | 3169.8237 | 3169.8237 | 3169.8237 | 3169.8237 | 3169.8237 | 3169.8237 | 3169.8237 | 3169.8237 | 3169.8237 | 3169.8237 |  |  | 1262.1427 | 2272.4362 | 1568.2676 | 1666.8773 | 1884.3002 | 2398.474 | 2678.7447 | 3213.5436 | 4840.1586 | 3498.0695 | 3235.2178 | 3588.9107 | 4362.9948 | 3838.2267 | 3838.2267 | 3838.2267 | 3838.2267 | 3838.2267 | 3838.2267 | 3838.2267 | 3838.2267 | 3838.2267 | 3838.2267 | 3838.2267 | 3838.2267 | 3838.2267 | 3838.2267 | 3838.2267 | 3838.2267
75% |  | 35.4297 | 855.1312 | 170.274 | 265.3536 | 476.074 | 1034.3156 | 1407.7566 | 1881.3168 | 2126.8689 | 2342.5679 | 1943.1522 | 2410.1096 | 3144.5223 | 2586.2777 | 2586.2777 | 2586.2777 | 2586.2777 | 2586.2777 | 2586.2777 | 2586.2777 | 2586.2777 | 2586.2777 | 2586.2777 | 2586.2777 | 2586.2777 | 2586.2777 | 2586.2777 | 2586.2777 | 2586.2777 |  |  | 481.7498 | 1596.2089 | 819.3143 | 928.1083 | 1167.9865 | 1735.2636 | 2044.4804 | 2634.5129 | 4429.1233 | 2948.4244 | 2658.4256 | 3048.6476 | 3902.6784 | 3323.7127 | 3323.7127 | 3323.7127 | 3323.7127 | 3323.7127 | 3323.7127 | 3323.7127 | 3323.7127 | 3323.7127 | 3323.7127 | 3323.7127 | 3323.7127 | 3323.7127 | 3323.7127 | 3323.7127 | 3323.7127
70% |  |  | 65.8085 |  |  |  | 147.5899 | 416.9599 | 907.6364 | 1171.4684 | 1403.2249 | 974.0751 | 1475.7947 | 2264.8802 | 1665.0775 | 1665.0775 | 1665.0775 | 1665.0775 | 1665.0775 | 1665.0775 | 1665.0775 | 1665.0775 | 1665.0775 | 1665.0775 | 1665.0775 | 1665.0775 | 1665.0775 | 1665.0775 | 1665.0775 | 1665.0775 |  |  |  | 601.3916 | 53.2898 | 95.2888 | 228.9422 | 750.7105 | 1082.9466 | 1716.9035 | 3645.112 | 2054.1839 | 1742.5964 | 2161.8681 | 3079.4764 | 2457.4102 | 2457.4102 | 2457.4102 | 2457.4102 | 2457.4102 | 2457.4102 | 2457.4102 | 2457.4102 | 2457.4102 | 2457.4102 | 2457.4102 | 2457.4102 | 2457.4102 | 2457.4102 | 2457.4102 | 2457.4102
65% | [8 empty] | 35.6769 | 127.7952 | 253.6368 | 53.6243 | 301.4174 | 1039.2123 | 444.3507 | 444.3507 | 444.3507 | 444.3507 | 444.3507 | 444.3507 | 444.3507 | 444.3507 | 444.3507 | 444.3507 | 444.3507 | 444.3507 | 444.3507 | 444.3507 | 444.3507 | 444.3507 | [7 empty] | 7.6459 | 90.7117 | 488.0255 | 2493.7121 | 817.1788 | 510.3907 | 930.6573 | 1897.6406 | 1242.1021 | 1242.1021 | 1242.1021 | 1242.1021 | 1242.1021 | 1242.1021 | 1242.1021 | 1242.1021 | 1242.1021 | 1242.1021 | 1242.1021 | 1242.1021 | 1242.1021 | 1242.1021 | 1242.1021 | 1242.1021
60% | FY38: 29.9333 | [10 empty] | 1024.4419 | 1.5765 |  | 11.6677 | 456.0267 | 86.1886 | 86.1886 | 86.1886 | 86.1886 | 86.1886 | 86.1886 | 86.1886 | 86.1886 | 86.1886 | 86.1886 | 86.1886 | 86.1886 | 86.1886 | 86.1886 | 86.1886 | 86.1886
55% | [40 empty] | 0.91586
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 2267.9753 | 5084.2295 | 2954.0047 | 3304.5343 | 3956.5861 | 5667.6982 | 6982.6421 | 8834.8869 | 9878.3431 | 10839.8632 | 9092.4021 | 11149.3194 | 14762.3692 | 11974.7776 | 11974.7776 | 11974.7776 | 11974.7776 | 11974.7776 | 11974.7776 | 11974.7776 | 11974.7776 | 11974.7776 | 11974.7776 | 11974.7776 | 11974.7776 | 11974.7776 | 11974.7776 | 11974.7776 | 11974.7776 | E @ R (MWh) | 0 | 3972.6958 | 7694.7094 | 4971.4293 | 5318.0339 | 6123.307 | 8241.0048 | 9522.0635 | 12205.329 | 22189.1986 | 13752.2403 | 12320.3388 | 14264.1026 | 18984.2005 | 15715.7482 | 15715.7482 | 15715.7482 | 15715.7482 | 15715.7482 | 15715.7482 | 15715.7482 | 15715.7482 | 15715.7482 | 15715.7482 | 15715.7482 | 15715.7482 | 15715.7482 | 15715.7482 | 15715.7482 | 15715.7482
Option 4 Winter POE50 W E @ R (MWh) N 1 | 0 | 1587.5827 | 3558.9606 | 2067.8033 | 2313.174 | 2769.6103 | 3967.3887 | 4887.8494 | 6184.4208 | 6914.8402 | 7587.9043 | 6364.6814 | 7804.5236 | 10333.6584 | 8382.3443 | 8382.3443 | 8382.3443 | 8382.3443 | 8382.3443 | 8382.3443 | 8382.3443 | 8382.3443 | 8382.3443 | 8382.3443 | 8382.3443 | 8382.3443 | 8382.3443 | 8382.3443 | 8382.3443 | 8382.3443 | Option 4 Winter POE10 W E @ R (MWh) N 1 | 0 | 1191.8087 | 2308.4128 | 1491.4288 | 1595.4102 | 1836.9921 | 2472.3014 | 2856.6191 | 3661.5987 | 6656.7596 | 4125.6721 | 3696.1016 | 4279.2308 | 5695.2602 | 4714.7245 | 4714.7245 | 4714.7245 | 4714.7245 | 4714.7245 | 4714.7245 | 4714.7245 | 4714.7245 | 4714.7245 | 4714.7245 | 4714.7245 | 4714.7245 | 4714.7245 | 4714.7245 | 4714.7245 | 4714.7245
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 17.7632 | 43.0375 | 49.6507 | 43.2333 | 43.2614 | 43.9394 | 45.7298 | 46.9275 | 48.1005 | 49.4726 | 50.7434 | 51.9776 | 52.1177 | 53.5584 | 52.4645 | 52.4645 | 52.4645 | 52.4645 | 52.4645 | 52.4645 | 52.4645 | 52.4645 | 52.4645 | 52.4645 | 52.4645 | 52.4645 | 52.4645 | 52.4645 | 52.4645 | 52.4645
98% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 8.4503 | 20.9604 | 24.2338 | 21.0574 | 21.0712 | 21.4068 | 22.293 | 22.8859 | 23.4665 | 24.1456 | 24.7746 | 25.3856 | 25.4549 | 26.168 | 25.6265 | 25.6265 | 25.6265 | 25.6265 | 25.6265 | 25.6265 | 25.6265 | 25.6265 | 25.6265 | 25.6265 | 25.6265 | 25.6265 | 25.6265 | 25.6265 | 25.6265 | 25.6265
97% | 1.8466 | 8.0258 | 9.7077 | 8.1839 | 8.1821 | 8.3738 | 8.5841 | 9.016 | 9.3263 | 9.4946 | 9.6787 | 9.8472 | 10.1518 | 10.5297 | 10.5033 | 10.5033 | 10.5033 | 10.5033 | 10.5033 | 10.5033 | 10.5033 | 10.5033 | 10.5033 | 10.5033 | 10.5033 | 10.5033 | 10.5033 | 10.5033 | 10.5033 | 10.5033 |  | 16.0379 | 40.8042 | 47.2844 | 40.9961 | 41.0236 | 41.6879 | 43.4424 | 44.616 | 45.7654 | 47.11 | 48.3552 | 49.5646 | 49.7018 | 51.1136 | 50.0417 | 50.0417 | 50.0417 | 50.0417 | 50.0417 | 50.0417 | 50.0417 | 50.0417 | 50.0417 | 50.0417 | 50.0417 | 50.0417 | 50.0417 | 50.0417 | 50.0417 | 50.0417
95% | 7.7819 | 38.2025 | 46.4828 | 38.9809 | 38.972 | 39.9157 | 40.9513 | 43.0773 | 44.6051 | 45.4338 | 46.3401 | 47.1697 | 48.6688 | 50.5295 | 50.3995 | 50.3995 | 50.3995 | 50.3995 | 50.3995 | 50.3995 | 50.3995 | 50.3995 | 50.3995 | 50.3995 | 50.3995 | 50.3995 | 50.3995 | 50.3995 | 50.3995 | 50.3995 |  | 22.1159 | 58.6938 | 68.2646 | 58.9772 | 59.0178 | 59.999 | 62.5902 | 64.3235 | 66.0212 | 68.0069 | 69.8461 | 71.6323 | 71.835 | 73.92 | 72.3369 | 72.3369 | 72.3369 | 72.3369 | 72.3369 | 72.3369 | 72.3369 | 72.3369 | 72.3369 | 72.3369 | 72.3369 | 72.3369 | 72.3369 | 72.3369 | 72.3369 | 72.3369
90% | 7.9129 | 60.6736 | 75.0348 | 62.0237 | 62.0082 | 63.645 | 65.441 | 69.1284 | 71.7781 | 73.2155 | 74.7873 | 76.2261 | 78.8262 | 82.0533 | 81.8277 | 81.8277 | 81.8277 | 81.8277 | 81.8277 | 81.8277 | 81.8277 | 81.8277 | 81.8277 | 81.8277 | 81.8277 | 81.8277 | 81.8277 | 81.8277 | 81.8277 | 81.8277 |  | 79.1417 | 237.7413 | 279.2396 | 238.9701 | 239.146 | 243.4006 | 254.6358 | 262.1514 | 269.5124 | 278.1224 | 286.0966 | 293.8417 | 294.7204 | 303.7611 | 296.8966 | 296.8966 | 296.8966 | 296.8966 | 296.8966 | 296.8966 | 296.8966 | 296.8966 | 296.8966 | 296.8966 | 296.8966 | 296.8966 | 296.8966 | 296.8966 | 296.8966 | 296.8966
85% | 2.1831 | 147.3455 | 188.1003 | 151.1769 | 151.1331 | 155.7779 | 160.8749 | 171.3391 | 178.8585 | 182.9375 | 187.3979 | 191.4812 | 198.8598 | 208.0178 | 207.3777 | 207.3777 | 207.3777 | 207.3777 | 207.3777 | 207.3777 | 207.3777 | 207.3777 | 207.3777 | 207.3777 | 207.3777 | 207.3777 | 207.3777 | 207.3777 | 207.3777 | 207.3777 |  | 50.0275 | 200.0542 | 239.3094 | 201.2166 | 201.383 | 205.4076 | 216.0355 | 223.1448 | 230.1079 | 238.2525 | 245.7957 | 253.1222 | 253.9534 | 262.5054 | 256.0119 | 256.0119 | 256.0119 | 256.0119 | 256.0119 | 256.0119 | 256.0119 | 256.0119 | 256.0119 | 256.0119 | 256.0119 | 256.0119 | 256.0119 | 256.0119 | 256.0119 | 256.0119
80% |  | 166.9191 | 223.8464 | 172.2708 | 172.2097 | 178.6977 | 185.8172 | 200.4339 | 210.9371 | 216.6348 | 222.8653 | 228.569 | 238.8755 | 251.6677 | 250.7735 | 250.7735 | 250.7735 | 250.7735 | 250.7735 | 250.7735 | 250.7735 | 250.7735 | 250.7735 | 250.7735 | 250.7735 | 250.7735 | 250.7735 | 250.7735 | 250.7735 | 250.7735 |  | 15.4914 | 120.2719 | 147.6883 | 121.0838 | 121.2 | 124.0109 | 131.4335 | 136.3987 | 141.2618 | 146.9501 | 152.2184 | 157.3353 | 157.9158 | 163.8887 | 159.3535 | 159.3535 | 159.3535 | 159.3535 | 159.3535 | 159.3535 | 159.3535 | 159.3535 | 159.3535 | 159.3535 | 159.3535 | 159.3535 | 159.3535 | 159.3535 | 159.3535 | 159.3535
75% |  | 320.647 | 469.0463 | 334.5981 | 334.4388 | 351.3517 | 369.9111 | 408.014 | 435.3941 | 450.2469 | 466.4886 | 481.3571 | 508.2243 | 541.5712 | 539.2403 | 539.2403 | 539.2403 | 539.2403 | 539.2403 | 539.2403 | 539.2403 | 539.2403 | 539.2403 | 539.2403 | 539.2403 | 539.2403 | 539.2403 | 539.2403 | 539.2403 | 539.2403 |  | 0.97657 | 175.4756 | 224.4096 | 176.9247 | 177.132 | 182.149 | 195.3973 | 204.2595 | 212.9394 | 223.0922 | 232.4952 | 241.6281 | 242.6642 | 253.3249 | 245.2303 | 245.2303 | 245.2303 | 245.2303 | 245.2303 | 245.2303 | 245.2303 | 245.2303 | 245.2303 | 245.2303 | 245.2303 | 245.2303 | 245.2303 | 245.2303 | 245.2303 | 245.2303
70% |  | 328.9116 | 585.3005 | 353.0148 | 352.7396 | 381.96 | 414.025 | 479.8552 | 527.1597 | 552.8208 | 580.8815 | 606.5697 | 652.9881 | 710.6013 | 706.5743 | 706.5743 | 706.5743 | 706.5743 | 706.5743 | 706.5743 | 706.5743 | 706.5743 | 706.5743 | 706.5743 | 706.5743 | 706.5743 | 706.5743 | 706.5743 | 706.5743 | 706.5743 |  |  | 238.4252 | 327.5698 | 241.0649 | 241.4427 | 250.5823 | 274.7171 | 290.8617 | 306.6742 | 325.1697 | 342.2996 | 358.9372 | 360.8248 | 380.2456 | 365.4995 | 365.4995 | 365.4995 | 365.4995 | 365.4995 | 365.4995 | 365.4995 | 365.4995 | 365.4995 | 365.4995 | 365.4995 | 365.4995 | 365.4995 | 365.4995 | 365.4995 | 365.4995
65% |  | 199.3768 | 820.987 | 247.6281 | 247.0495 | 312.011 | 390.8248 | 556.1588 | 674.9653 | 739.4136 | 809.8887 | 874.4051 | 990.986 | 1135.6829 | 1125.5689 | 1125.5689 | 1125.5689 | 1125.5689 | 1125.5689 | 1125.5689 | 1125.5689 | 1125.5689 | 1125.5689 | 1125.5689 | 1125.5689 | 1125.5689 | 1125.5689 | 1125.5689 | 1125.5689 | 1125.5689 |  |  | 182.6144 | 294.7721 | 185.9357 | 186.411 | 197.91 | 228.2752 | 248.5877 | 268.4822 | 291.7525 | 313.3046 | 334.2372 | 336.6121 | 361.0465 | 342.4936 | 342.4936 | 342.4936 | 342.4936 | 342.4936 | 342.4936 | 342.4936 | 342.4936 | 342.4936 | 342.4936 | 342.4936 | 342.4936 | 342.4936 | 342.4936 | 342.4936 | 342.4936
60% |  |  | 203.5024 |  |  |  | 0.84072 | 37.3946 | 95.9955 | 138.7082 | 193.9916 | 252.3037 | 375.8955 | 560.9157 | 546.8717 | 546.8717 | 546.8717 | 546.8717 | 546.8717 | 546.8717 | 546.8717 | 546.8717 | 546.8717 | 546.8717 | 546.8717 | 546.8717 | 546.8717 | 546.8717 | 546.8717 | 546.8717 |  |  | 77.0598 | 248.2313 | 81.3471 | 81.9696 | 97.7003 | 144.1759 | 175.9612 | 207.0924 | 243.5061 | 277.2311 | 309.9868 | 313.7031 | 351.9383 | 322.9065 | 322.9065 | 322.9065 | 322.9065 | 322.9065 | 322.9065 | 322.9065 | 322.9065 | 322.9065 | 322.9065 | 322.9065 | 322.9065 | 322.9065 | 322.9065 | 322.9065 | 322.9065
55% | [33 empty] | 63.4905 |  |  |  | 2.3611 | 12.4204 | 29.7152 | 58.9928 | 94.5309 | 136.551 | 141.7751 | 200.8038 | 155.1077 | 155.1077 | 155.1077 | 155.1077 | 155.1077 | 155.1077 | 155.1077 | 155.1077 | 155.1077 | 155.1077 | 155.1077 | 155.1077 | 155.1077 | 155.1077 | 155.1077 | 155.1077
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 19.7244 | 1270.1019 | 2622.0083 | 1367.8771 | 1366.7331 | 1491.7328 | 1637.2701 | 1974.4173 | 2249.0198 | 2408.9058 | 2592.3198 | 2767.9288 | 3103.476 | 3551.5691 | 3519.1368 | 3519.1368 | 3519.1368 | 3519.1368 | 3519.1368 | 3519.1368 | 3519.1368 | 3519.1368 | 3519.1368 | 3519.1368 | 3519.1368 | 3519.1368 | 3519.1368 | 3519.1368 | 3519.1368 | 3519.1368 | E @ R (MWh) | 210.0044 | 1395.1384 | 2014.1441 | 1410.807 | 1413.0583 | 1468.194 | 1621.0867 | 1732.5383 | 1849.1393 | 1994.5735 | 2137.6914 | 2284.1997 | 2301.2784 | 2482.2743 | 2343.9692 | 2343.9692 | 2343.9692 | 2343.9692 | 2343.9692 | 2343.9692 | 2343.9692 | 2343.9692 | 2343.9692 | 2343.9692 | 2343.9692 | 2343.9692 | 2343.9692 | 2343.9692 | 2343.9692 | 2343.9692
Option 4 Summer POE50 W E @ R (MWh) N 1 | 13.8071 | 889.0713 | 1835.4058 | 957.514 | 956.7132 | 1044.213 | 1146.0891 | 1382.0921 | 1574.3138 | 1686.2341 | 1814.6239 | 1937.5502 | 2172.4332 | 2486.0984 | 2463.3958 | 2463.3958 | 2463.3958 | 2463.3958 | 2463.3958 | 2463.3958 | 2463.3958 | 2463.3958 | 2463.3958 | 2463.3958 | 2463.3958 | 2463.3958 | 2463.3958 | 2463.3958 | 2463.3958 | 2463.3958 | Option 4 Summer POE10 W E @ R (MWh) N 1 | 63.0013 | 418.5415 | 604.2432 | 423.2421 | 423.9175 | 440.4582 | 486.326 | 519.7615 | 554.7418 | 598.372 | 641.3074 | 685.2599 | 690.3835 | 744.6823 | 703.1908 | 703.1908 | 703.1908 | 703.1908 | 703.1908 | 703.1908 | 703.1908 | 703.1908 | 703.1908 | 703.1908 | 703.1908 | 703.1908 | 703.1908 | 703.1908 | 703.1908 | 703.1908
Option 5 - 4B LLG 2nd Tx + Switchroom + Two new feeders + OFR12 New Feeder
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% |  | 19.3557 | 26.0414 |  |  |  | 0.91363 | 3.2411 | 6.1925 | 7.7228 | 9.0672 | 6.5778 | 9.4881 | 14.0652 | 10.586 | 10.586 | 10.586 | 10.586 | 10.586 | 10.586 | 10.586 | 10.586 | 10.586 | 10.586 | 10.586 | 10.586 | 10.586 | 10.586 | 10.586 | 10.586 |  |  | 23.7132 | 30.66 |  | 0.26088 | 1.7467 | 5.2822 | 7.2094 | 10.8867 | 22.0714 | 12.8431 | 11.0357 | 13.4677 | 18.7904 | 15.182 | 15.182 | 15.182 | 15.182 | 15.182 | 15.182 | 15.182 | 15.182 | 15.182 | 15.182 | 15.182 | 15.182 | 15.182 | 15.182 | 15.182 | 15.182
98% |  | 22.1134 | 30.0556 |  |  |  | 0.23774 | 2.9702 | 6.4763 | 8.2943 | 9.8913 | 6.9341 | 10.3913 | 15.8287 | 11.6956 | 11.6956 | 11.6956 | 11.6956 | 11.6956 | 11.6956 | 11.6956 | 11.6956 | 11.6956 | 11.6956 | 11.6956 | 11.6956 | 11.6956 | 11.6956 | 11.6956 | 11.6956 |  |  | 27.2899 | 35.5423 |  |  | 1.195 | 5.395 | 7.6843 | 12.0528 | 25.3395 | 14.3769 | 12.2298 | 15.1189 | 21.4419 | 17.1554 | 17.1554 | 17.1554 | 17.1554 | 17.1554 | 17.1554 | 17.1554 | 17.1554 | 17.1554 | 17.1554 | 17.1554 | 17.1554 | 17.1554 | 17.1554 | 17.1554 | 17.1554
97% |  | 42.0001 | 57.7232 |  |  |  |  | 4.1024 | 11.0434 | 14.6425 | 17.804 | 11.9497 | 18.7939 | 29.5583 | 21.376 | 21.376 | 21.376 | 21.376 | 21.376 | 21.376 | 21.376 | 21.376 | 21.376 | 21.376 | 21.376 | 21.376 | 21.376 | 21.376 | 21.376 | 21.376 |  |  | 52.248 | 68.5852 |  |  | 0.61524 | 8.9027 | 13.4349 | 22.083 | 48.3867 | 26.6841 | 22.4335 | 28.153 | 40.6706 | 32.1847 | 32.1847 | 32.1847 | 32.1847 | 32.1847 | 32.1847 | 32.1847 | 32.1847 | 32.1847 | 32.1847 | 32.1847 | 32.1847 | 32.1847 | 32.1847 | 32.1847 | 32.1847
95% |  | 115.9799 | 162.4236 |  |  |  |  | 4.1349 | 24.5385 | 35.1696 | 44.5082 | 27.2156 | 47.4324 | 79.2286 | 55.0596 | 55.0596 | 55.0596 | 55.0596 | 55.0596 | 55.0596 | 55.0596 | 55.0596 | 55.0596 | 55.0596 | 55.0596 | 55.0596 | 55.0596 | 55.0596 | 55.0596 | 55.0596 |  |  | 146.2505 | 194.5083 |  |  |  | 18.2152 | 31.6026 | 57.1479 | 134.845 | 70.7386 | 58.1832 | 75.0777 | 112.0528 | 86.9866 | 86.9866 | 86.9866 | 86.9866 | 86.9866 | 86.9866 | 86.9866 | 86.9866 | 86.9866 | 86.9866 | 86.9866 | 86.9866 | 86.9866 | 86.9866 | 86.9866 | 86.9866
90% |  | 529.8714 | 785.9431 | [5 empty] | 35.35 | 84.3158 | 135.8052 | 45.7855 | 151.928 | 327.2395 | 193.9811 | 193.9811 | 193.9811 | 193.9811 | 193.9811 | 193.9811 | 193.9811 | 193.9811 | 193.9811 | 193.9811 | 193.9811 | 193.9811 | 193.9811 | 193.9811 | 193.9811 | 193.9811 |  |  | 696.7712 | 962.8455 |  |  |  | 15.9263 | 65.6624 | 205.4953 | 633.8861 | 280.429 | 211.2035 | 304.3532 | 508.2187 | 370.014 | 370.014 | 370.014 | 370.014 | 370.014 | 370.014 | 370.014 | 370.014 | 370.014 | 370.014 | 370.014 | 370.014 | 370.014 | 370.014 | 370.014 | 370.014
85% |  | 874.8065 | 1500.3713 | [6 empty] | 0.0048549 | 19.6912 |  | 33.5299 | 379.7911 | 86.2582 | 86.2582 | 86.2582 | 86.2582 | 86.2582 | 86.2582 | 86.2582 | 86.2582 | 86.2582 | 86.2582 | 86.2582 | 86.2582 | 86.2582 | 86.2582 | 86.2582 | 86.2582 |  |  | 1282.5306 | 1932.5312 | [5 empty] | 104.7977 | 1128.907 | 265.4365 | 114.6305 | 323.8817 | 821.9103 | 484.2861 | 484.2861 | 484.2861 | 484.2861 | 484.2861 | 484.2861 | 484.2861 | 484.2861 | 484.2861 | 484.2861 | 484.2861 | 484.2861 | 484.2861 | 484.2861 | 484.2861 | 484.2861
80% | FY26: 628.4185; FY27: 1600.7316; FY38: 38.3481 |  |  | 1262.1427 | 2272.4362 | [6 empty] | 1023.366 | 2.3345 |  | 15.3679 | 546.2021 | 108.1264 | 108.1264 | 108.1264 | 108.1264 | 108.1264 | 108.1264 | 108.1264 | 108.1264 | 108.1264 | 108.1264 | 108.1264 | 108.1264 | 108.1264 | 108.1264 | 108.1264 | 108.1264
75% | FY26: 35.4297; FY27: 855.1312 |  |  | 481.7498 | 1596.2089 | [6 empty] | 256.2227 |  |  |  | 14.6097
70% | FY27: 65.8085 |  |  |  | 601.3916
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 2267.9753 | 5084.2295 | 0 | 0 | 0 | 1.1514 | 14.4486 | 83.6007 | 150.1498 | 236.767 | 98.4628 | 271.5637 | 884.0595 | 378.9566 | 378.9566 | 378.9566 | 378.9566 | 378.9566 | 378.9566 | 378.9566 | 378.9566 | 378.9566 | 378.9566 | 378.9566 | 378.9566 | 378.9566 | 378.9566 | 378.9566 | 378.9566 | E @ R (MWh) | 0 | 3972.6958 | 7694.7094 | 0 | 0.26088 | 3.557 | 53.7213 | 125.5936 | 412.4634 | 3273.0245 | 672.8426 | 429.7162 | 775.4201 | 2083.8964 | 1113.9352 | 1113.9352 | 1113.9352 | 1113.9352 | 1113.9352 | 1113.9352 | 1113.9352 | 1113.9352 | 1113.9352 | 1113.9352 | 1113.9352 | 1113.9352 | 1113.9352 | 1113.9352 | 1113.9352 | 1113.9352
Option 5 Winter POE50 W E @ R (MWh) N 1 | 0 | 1587.5827 | 3558.9606 | 0 | 0 | 0 | 0.80595 | 10.114 | 58.5205 | 105.1049 | 165.7369 | 68.924 | 190.0946 | 618.8416 | 265.2696 | 265.2696 | 265.2696 | 265.2696 | 265.2696 | 265.2696 | 265.2696 | 265.2696 | 265.2696 | 265.2696 | 265.2696 | 265.2696 | 265.2696 | 265.2696 | 265.2696 | 265.2696 | Option 5 Winter POE10 W E @ R (MWh) N 1 | 0 | 1191.8087 | 2308.4128 | 0 | 0.078263 | 1.0671 | 16.1164 | 37.6781 | 123.739 | 981.9073 | 201.8528 | 128.9149 | 232.626 | 625.1689 | 334.1806 | 334.1806 | 334.1806 | 334.1806 | 334.1806 | 334.1806 | 334.1806 | 334.1806 | 334.1806 | 334.1806 | 334.1806 | 334.1806 | 334.1806 | 334.1806 | 334.1806 | 334.1806
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 17.7632 | 43.0375 | 49.6507 | 16.5179 | 16.5459 | 17.224 | 19.0144 | 20.2121 | 21.3851 | 22.7572 | 24.028 | 25.2622 | 25.4023 | 26.843 | 25.749 | 25.749 | 25.749 | 25.749 | 25.749 | 25.749 | 25.749 | 25.749 | 25.749 | 25.749 | 25.749 | 25.749 | 25.749 | 25.749 | 25.749 | 25.749
98% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 8.4503 | 20.9604 | 24.2338 | 7.8339 | 7.8478 | 8.1834 | 9.0696 | 9.6624 | 10.243 | 10.9222 | 11.5512 | 12.1621 | 12.2314 | 12.9445 | 12.4031 | 12.4031 | 12.4031 | 12.4031 | 12.4031 | 12.4031 | 12.4031 | 12.4031 | 12.4031 | 12.4031 | 12.4031 | 12.4031 | 12.4031 | 12.4031 | 12.4031 | 12.4031
97% | 1.8466 | 8.0258 | 9.7077 | 1.6393 | 1.6375 | 1.8292 | 2.0395 | 2.4714 | 2.7817 | 2.95 | 3.1341 | 3.3026 | 3.6072 | 3.9851 | 3.9587 | 3.9587 | 3.9587 | 3.9587 | 3.9587 | 3.9587 | 3.9587 | 3.9587 | 3.9587 | 3.9587 | 3.9587 | 3.9587 | 3.9587 | 3.9587 | 3.9587 | 3.9587 |  | 16.0379 | 40.8042 | 47.2844 | 14.8177 | 14.8451 | 15.5095 | 17.264 | 18.4376 | 19.587 | 20.9315 | 22.1768 | 23.3862 | 23.5234 | 24.9352 | 23.8632 | 23.8632 | 23.8632 | 23.8632 | 23.8632 | 23.8632 | 23.8632 | 23.8632 | 23.8632 | 23.8632 | 23.8632 | 23.8632 | 23.8632 | 23.8632 | 23.8632 | 23.8632
95% | 7.7819 | 38.2025 | 46.4828 | 6.7613 | 6.7524 | 7.6961 | 8.7317 | 10.8577 | 12.3855 | 13.2142 | 14.1205 | 14.9501 | 16.4492 | 18.3099 | 18.1799 | 18.1799 | 18.1799 | 18.1799 | 18.1799 | 18.1799 | 18.1799 | 18.1799 | 18.1799 | 18.1799 | 18.1799 | 18.1799 | 18.1799 | 18.1799 | 18.1799 | 18.1799 |  | 22.1159 | 58.6938 | 68.2646 | 20.3137 | 20.3543 | 21.3355 | 23.9267 | 25.66 | 27.3577 | 29.3434 | 31.1825 | 32.9688 | 33.1714 | 35.2565 | 33.6733 | 33.6733 | 33.6733 | 33.6733 | 33.6733 | 33.6733 | 33.6733 | 33.6733 | 33.6733 | 33.6733 | 33.6733 | 33.6733 | 33.6733 | 33.6733 | 33.6733 | 33.6733
90% | 7.9129 | 60.6736 | 75.0348 | 6.1428 | 6.1274 | 7.7641 | 9.5602 | 13.2476 | 15.8973 | 17.3346 | 18.9064 | 20.3453 | 22.9453 | 26.1725 | 25.9469 | 25.9469 | 25.9469 | 25.9469 | 25.9469 | 25.9469 | 25.9469 | 25.9469 | 25.9469 | 25.9469 | 25.9469 | 25.9469 | 25.9469 | 25.9469 | 25.9469 | 25.9469 |  | 79.1417 | 237.7413 | 279.2396 | 71.3275 | 71.5034 | 75.758 | 86.9932 | 94.5088 | 101.8698 | 110.4798 | 118.454 | 126.1991 | 127.0778 | 136.1185 | 129.254 | 129.254 | 129.254 | 129.254 | 129.254 | 129.254 | 129.254 | 129.254 | 129.254 | 129.254 | 129.254 | 129.254 | 129.254 | 129.254 | 129.254 | 129.254
85% | 2.1831 | 147.3455 | 188.1003 | 0.58811 | 0.57861 | 2.011 | 4.5451 | 12.7682 | 20.2776 | 24.3566 | 28.8171 | 32.9004 | 40.2789 | 49.437 | 48.7968 | 48.7968 | 48.7968 | 48.7968 | 48.7968 | 48.7968 | 48.7968 | 48.7968 | 48.7968 | 48.7968 | 48.7968 | 48.7968 | 48.7968 | 48.7968 | 48.7968 | 48.7968 |  | 50.0275 | 200.0542 | 239.3094 | 42.6358 | 42.8022 | 46.8268 | 57.4546 | 64.564 | 71.5271 | 79.6717 | 87.2149 | 94.5413 | 95.3726 | 103.9246 | 97.4311 | 97.4311 | 97.4311 | 97.4311 | 97.4311 | 97.4311 | 97.4311 | 97.4311 | 97.4311 | 97.4311 | 97.4311 | 97.4311 | 97.4311 | 97.4311 | 97.4311 | 97.4311
80% |  | 166.9191 | 223.8464 | [5 empty] | 1.1665 | 2.9725 | 5.8671 | 9.3376 | 17.5353 | 30.1579 | 29.2638 | 29.2638 | 29.2638 | 29.2638 | 29.2638 | 29.2638 | 29.2638 | 29.2638 | 29.2638 | 29.2638 | 29.2638 | 29.2638 | 29.2638 | 29.2638 | 29.2638 | 29.2638 |  | 15.4914 | 120.2719 | 147.6883 | 10.331 | 10.4459 | 13.256 | 20.6786 | 25.6439 | 30.507 | 36.1953 | 41.4635 | 46.5804 | 47.161 | 53.1338 | 48.5987 | 48.5987 | 48.5987 | 48.5987 | 48.5987 | 48.5987 | 48.5987 | 48.5987 | 48.5987 | 48.5987 | 48.5987 | 48.5987 | 48.5987 | 48.5987 | 48.5987 | 48.5987
75% |  | 320.647 | 469.0463 | [10 empty] | 2.3913 | 1.9367 | 1.9367 | 1.9367 | 1.9367 | 1.9367 | 1.9367 | 1.9367 | 1.9367 | 1.9367 | 1.9367 | 1.9367 | 1.9367 | 1.9367 | 1.9367 | 1.9367 | 1.9367 |  | 0.97657 | 175.4756 | 224.4096 |  |  | 0.28616 | 4.1176 | 9.071 | 15.6935 | 25.4115 | 34.8146 | 43.9474 | 44.9836 | 55.6442 | 47.5497 | 47.5497 | 47.5497 | 47.5497 | 47.5497 | 47.5497 | 47.5497 | 47.5497 | 47.5497 | 47.5497 | 47.5497 | 47.5497 | 47.5497 | 47.5497 | 47.5497 | 47.5497
70% | FY26: 328.9116; FY27: 585.3005 |  |  | 238.4252 | 327.5698 | [6 empty] | 0.31272 | 3.6463 | 10.2618 | 11.2167 | 23.3866 | 13.7573 | 13.7573 | 13.7573 | 13.7573 | 13.7573 | 13.7573 | 13.7573 | 13.7573 | 13.7573 | 13.7573 | 13.7573 | 13.7573 | 13.7573 | 13.7573 | 13.7573 | 13.7573
65% | FY26: 199.3768; FY27: 820.987 |  |  | 182.6144 | 294.7721
60% | FY27: 203.5024 |  |  | 77.0598 | 248.2313
55% | [33 empty] | 63.4905
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 19.7244 | 1270.1019 | 2622.0083 | 15.1315 | 15.0959 | 19.3004 | 24.8765 | 39.3449 | 52.5086 | 60.828 | 70.8452 | 80.8361 | 100.816 | 130.4537 | 128.0828 | 128.0828 | 128.0828 | 128.0828 | 128.0828 | 128.0828 | 128.0828 | 128.0828 | 128.0828 | 128.0828 | 128.0828 | 128.0828 | 128.0828 | 128.0828 | 128.0828 | 128.0828 | E @ R (MWh) | 210.0044 | 1395.1384 | 2014.1441 | 183.7776 | 184.3446 | 198.3794 | 238.5187 | 267.7597 | 298.1702 | 336.0253 | 374.5318 | 415.3095 | 420.1402 | 472.187 | 432.2794 | 432.2794 | 432.2794 | 432.2794 | 432.2794 | 432.2794 | 432.2794 | 432.2794 | 432.2794 | 432.2794 | 432.2794 | 432.2794 | 432.2794 | 432.2794 | 432.2794 | 432.2794
Option 5 Summer POE50 W E @ R (MWh) N 1 | 13.8071 | 889.0713 | 1835.4058 | 10.592 | 10.5671 | 13.5103 | 17.4135 | 27.5414 | 36.756 | 42.5796 | 49.5916 | 56.5853 | 70.5712 | 91.3176 | 89.658 | 89.658 | 89.658 | 89.658 | 89.658 | 89.658 | 89.658 | 89.658 | 89.658 | 89.658 | 89.658 | 89.658 | 89.658 | 89.658 | 89.658 | 89.658 | Option 5 Summer POE10 W E @ R (MWh) N 1 | 63.0013 | 418.5415 | 604.2432 | 55.1333 | 55.3034 | 59.5138 | 71.5556 | 80.3279 | 89.4511 | 100.8076 | 112.3595 | 124.5928 | 126.0421 | 141.6561 | 129.6838 | 129.6838 | 129.6838 | 129.6838 | 129.6838 | 129.6838 | 129.6838 | 129.6838 | 129.6838 | 129.6838 | 129.6838 | 129.6838 | 129.6838 | 129.6838 | 129.6838 | 129.6838
Option 6 -
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% |  | 19.3557 | 26.0414 | 27.1786 | 28.0631 | 29.5913 | 33.0724 | 35.3998 | 38.3512 | 39.8816 | 41.2259 | 38.7366 | 41.6468 | 46.224 | 42.7448 | 42.7448 | 42.7448 | 42.7448 | 42.7448 | 42.7448 | 42.7448 | 42.7448 | 42.7448 | 42.7448 | 42.7448 | 42.7448 | 42.7448 | 42.7448 | 42.7448 | 42.7448 |  |  | 23.7132 | 30.66 | 31.7324 | 32.4104 | 33.9055 | 37.4409 | 39.3681 | 43.0454 | 54.2301 | 45.0018 | 43.1944 | 45.6265 | 50.9491 | 47.3408 | 47.3408 | 47.3408 | 47.3408 | 47.3408 | 47.3408 | 47.3408 | 47.3408 | 47.3408 | 47.3408 | 47.3408 | 47.3408 | 47.3408 | 47.3408 | 47.3408 | 47.3408
98% |  | 22.1134 | 30.0556 | 31.4065 | 32.4573 | 34.2728 | 38.408 | 41.1729 | 44.679 | 46.497 | 48.0939 | 45.1368 | 48.594 | 54.0314 | 49.8983 | 49.8983 | 49.8983 | 49.8983 | 49.8983 | 49.8983 | 49.8983 | 49.8983 | 49.8983 | 49.8983 | 49.8983 | 49.8983 | 49.8983 | 49.8983 | 49.8983 | 49.8983 |  |  | 27.2899 | 35.5423 | 36.8162 | 37.6217 | 39.3977 | 43.5976 | 45.887 | 50.2554 | 63.5422 | 52.5795 | 50.4324 | 53.3215 | 59.6445 | 55.358 | 55.358 | 55.358 | 55.358 | 55.358 | 55.358 | 55.358 | 55.358 | 55.358 | 55.358 | 55.358 | 55.358 | 55.358 | 55.358 | 55.358 | 55.358
97% |  | 42.0001 | 57.7232 | 60.3976 | 62.4779 | 66.0719 | 74.2584 | 79.732 | 86.673 | 90.2721 | 93.4336 | 87.5793 | 94.4235 | 105.1879 | 97.0056 | 97.0056 | 97.0056 | 97.0056 | 97.0056 | 97.0056 | 97.0056 | 97.0056 | 97.0056 | 97.0056 | 97.0056 | 97.0056 | 97.0056 | 97.0056 | 97.0056 | 97.0056 |  |  | 52.248 | 68.5852 | 71.1071 | 72.7018 | 76.2177 | 84.5323 | 89.0645 | 97.7126 | 124.0163 | 102.3136 | 98.0631 | 103.7826 | 116.3002 | 107.8143 | 107.8143 | 107.8143 | 107.8143 | 107.8143 | 107.8143 | 107.8143 | 107.8143 | 107.8143 | 107.8143 | 107.8143 | 107.8143 | 107.8143 | 107.8143 | 107.8143 | 107.8143
95% |  | 115.9799 | 162.4236 | 170.3233 | 176.4681 | 187.0842 | 211.266 | 227.434 | 247.9367 | 258.5678 | 267.9064 | 250.6138 | 270.8306 | 302.6268 | 278.4578 | 278.4578 | 278.4578 | 278.4578 | 278.4578 | 278.4578 | 278.4578 | 278.4578 | 278.4578 | 278.4578 | 278.4578 | 278.4578 | 278.4578 | 278.4578 | 278.4578 | 278.4578 |  |  | 146.2505 | 194.5083 | 201.9576 | 206.6678 | 217.0533 | 241.6134 | 255.0008 | 280.5461 | 358.2432 | 294.1368 | 281.5814 | 298.4759 | 335.451 | 310.3848 | 310.3848 | 310.3848 | 310.3848 | 310.3848 | 310.3848 | 310.3848 | 310.3848 | 310.3848 | 310.3848 | 310.3848 | 310.3848 | 310.3848 | 310.3848 | 310.3848 | 310.3848
90% |  | 529.8714 | 785.9431 | 829.499 | 863.379 | 921.9121 | 1055.2409 | 1144.3849 | 1257.4283 | 1316.044 | 1367.5334 | 1272.189 | 1383.6562 | 1558.9677 | 1425.7093 | 1425.7093 | 1425.7093 | 1425.7093 | 1425.7093 | 1425.7093 | 1425.7093 | 1425.7093 | 1425.7093 | 1425.7093 | 1425.7093 | 1425.7093 | 1425.7093 | 1425.7093 | 1425.7093 | 1425.7093 |  |  | 696.7712 | 962.8455 | 1003.918 | 1029.8882 | 1087.1494 | 1222.564 | 1296.377 | 1437.2235 | 1865.6143 | 1512.1572 | 1442.9317 | 1536.0814 | 1739.9469 | 1601.7422 | 1601.7422 | 1601.7422 | 1601.7422 | 1601.7422 | 1601.7422 | 1601.7422 | 1601.7422 | 1601.7422 | 1601.7422 | 1601.7422 | 1601.7422 | 1601.7422 | 1601.7422 | 1601.7422 | 1601.7422
85% |  | 874.8065 | 1500.3713 | 1606.7752 | 1689.5415 | 1832.5337 | 2158.2465 | 2376.0188 | 2652.1757 | 2795.3696 | 2921.1546 | 2688.2351 | 2960.5416 | 3388.8149 | 3063.2741 | 3063.2741 | 3063.2741 | 3063.2741 | 3063.2741 | 3063.2741 | 3063.2741 | 3063.2741 | 3063.2741 | 3063.2741 | 3063.2741 | 3063.2741 | 3063.2741 | 3063.2741 | 3063.2741 | 3063.2741 |  |  | 1282.5306 | 1932.5312 | 2032.8683 | 2096.3116 | 2236.1967 | 2567.0047 | 2747.3247 | 3091.4025 | 4137.9307 | 3274.4602 | 3105.3472 | 3332.9054 | 3830.934 | 3493.3099 | 3493.3099 | 3493.3099 | 3493.3099 | 3493.3099 | 3493.3099 | 3493.3099 | 3493.3099 | 3493.3099 | 3493.3099 | 3493.3099 | 3493.3099 | 3493.3099 | 3493.3099 | 3493.3099 | 3493.3099
80% |  | 628.4185 | 1600.7316 | 1766.1149 | 1894.7582 | 2117.0105 | 2623.2647 | 2961.7475 | 3390.9772 | 3613.543 | 3809.0501 | 3447.0242 | 3870.2692 | 4535.9328 | 4029.946 | 4029.946 | 4029.946 | 4029.946 | 4029.946 | 4029.946 | 4029.946 | 4029.946 | 4029.946 | 4029.946 | 4029.946 | 4029.946 | 4029.946 | 4029.946 | 4029.946 | 4029.946 |  |  | 1262.1427 | 2272.4362 | 2428.3899 | 2526.9996 | 2744.4225 | 3258.5963 | 3538.867 | 4073.6659 | 5700.2809 | 4358.1918 | 4095.3401 | 4449.033 | 5223.1171 | 4698.349 | 4698.349 | 4698.349 | 4698.349 | 4698.349 | 4698.349 | 4698.349 | 4698.349 | 4698.349 | 4698.349 | 4698.349 | 4698.349 | 4698.349 | 4698.349 | 4698.349 | 4698.349
75% |  | 35.4297 | 855.1312 | 1037.5951 | 1179.5246 | 1424.7309 | 1983.2706 | 2356.7115 | 2830.2717 | 3075.8238 | 3291.5228 | 2892.1072 | 3359.0645 | 4093.4773 | 3535.2326 | 3535.2326 | 3535.2326 | 3535.2326 | 3535.2326 | 3535.2326 | 3535.2326 | 3535.2326 | 3535.2326 | 3535.2326 | 3535.2326 | 3535.2326 | 3535.2326 | 3535.2326 | 3535.2326 | 3535.2326 |  |  | 481.7498 | 1596.2089 | 1768.2692 | 1877.0633 | 2116.9414 | 2684.2186 | 2993.4354 | 3583.4678 | 5378.0782 | 3897.3793 | 3607.3806 | 3997.6025 | 4851.6333 | 4272.6677 | 4272.6677 | 4272.6677 | 4272.6677 | 4272.6677 | 4272.6677 | 4272.6677 | 4272.6677 | 4272.6677 | 4272.6677 | 4272.6677 | 4272.6677 | 4272.6677 | 4272.6677 | 4272.6677 | 4272.6677
70% |  |  | 65.8085 | 149.3801 | 236.763 | 432.2706 | 1017.18 | 1418.4215 | 1927.2354 | 2191.0675 | 2422.824 | 1993.6741 | 2495.3937 | 3284.4792 | 2684.6765 | 2684.6765 | 2684.6765 | 2684.6765 | 2684.6765 | 2684.6765 | 2684.6765 | 2684.6765 | 2684.6765 | 2684.6765 | 2684.6765 | 2684.6765 | 2684.6765 | 2684.6765 | 2684.6765 | 2684.6765 |  |  |  | 601.3916 | 786.1731 | 903.0662 | 1160.8019 | 1770.3095 | 2102.5457 | 2736.5026 | 4664.7111 | 3073.7829 | 2762.1954 | 3181.4671 | 4099.0755 | 3477.0093 | 3477.0093 | 3477.0093 | 3477.0093 | 3477.0093 | 3477.0093 | 3477.0093 | 3477.0093 | 3477.0093 | 3477.0093 | 3477.0093 | 3477.0093 | 3477.0093 | 3477.0093 | 3477.0093 | 3477.0093
65% | [6 empty] | 67.1746 | 263.316 | 684.8354 | 961.4279 | 1205.6548 | 753.4132 | 1282.1294 | 2113.6742 | 1481.5972 | 1481.5972 | 1481.5972 | 1481.5972 | 1481.5972 | 1481.5972 | 1481.5972 | 1481.5972 | 1481.5972 | 1481.5972 | 1481.5972 | 1481.5972 | 1481.5972 | 1481.5972 | 1481.5972 | 1481.5972 |  |  |  |  | 12.1974 | 34.5742 | 123.0009 | 535.0416 | 868.1429 | 1536.2119 | 3568.1739 | 1891.6407 | 1563.2873 | 2005.1192 | 2972.1025 | 2316.564 | 2316.564 | 2316.564 | 2316.564 | 2316.564 | 2316.564 | 2316.564 | 2316.564 | 2316.564 | 2316.564 | 2316.564 | 2316.564 | 2316.564 | 2316.564 | 2316.564 | 2316.564
60% | [9 empty] | 15.996 | 73.9877 | 0.0013268 | 100.6328 | 637.7145 | 188.7046 | 188.7046 | 188.7046 | 188.7046 | 188.7046 | 188.7046 | 188.7046 | 188.7046 | 188.7046 | 188.7046 | 188.7046 | 188.7046 | 188.7046 | 188.7046 | 188.7046 | 188.7046 | [8 empty] | 4.9606 | 217.4281 | 2207.292 | 451.391 | 232.3927 | 542.8433 | 1551.0908 | 834.0186 | 834.0186 | 834.0186 | 834.0186 | 834.0186 | 834.0186 | 834.0186 | 834.0186 | 834.0186 | 834.0186 | 834.0186 | 834.0186 | 834.0186 | 834.0186 | 834.0186 | 834.0186
55% | [40 empty] | 420.5237 |  |  |  | 95.5636
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 2267.9753 | 5084.2295 | 5678.6703 | 6163.4327 | 7045.478 | 9261.3822 | 10904.3389 | 13160.5637 | 14404.4901 | 15542.3873 | 13468.7106 | 15907.1825 | 20121.1305 | 16877.247 | 16877.247 | 16877.247 | 16877.247 | 16877.247 | 16877.247 | 16877.247 | 16877.247 | 16877.247 | 16877.247 | 16877.247 | 16877.247 | 16877.247 | 16877.247 | 16877.247 | 16877.247 | E @ R (MWh) | 0 | 3972.6958 | 7694.7094 | 8373.4293 | 8817.3048 | 9835.0869 | 12444.9189 | 13980.9735 | 17147.4619 | 28542.6368 | 18953.035 | 17282.1464 | 19546.2584 | 24925.8084 | 21214.5583 | 21214.5583 | 21214.5583 | 21214.5583 | 21214.5583 | 21214.5583 | 21214.5583 | 21214.5583 | 21214.5583 | 21214.5583 | 21214.5583 | 21214.5583 | 21214.5583 | 21214.5583 | 21214.5583 | 21214.5583
Option 6 Winter POE50 W E @ R (MWh) N 1 | 0 | 1587.5827 | 3558.9606 | 3975.0692 | 4314.4029 | 4931.8346 | 6482.9675 | 7633.0372 | 9212.3946 | 10083.1431 | 10879.6711 | 9428.0974 | 11135.0277 | 14084.7914 | 11814.0729 | 11814.0729 | 11814.0729 | 11814.0729 | 11814.0729 | 11814.0729 | 11814.0729 | 11814.0729 | 11814.0729 | 11814.0729 | 11814.0729 | 11814.0729 | 11814.0729 | 11814.0729 | 11814.0729 | 11814.0729 | Option 6 Winter POE10 W E @ R (MWh) N 1 | 0 | 1191.8087 | 2308.4128 | 2512.0288 | 2645.1914 | 2950.5261 | 3733.4757 | 4194.2921 | 5144.2386 | 8562.791 | 5685.9105 | 5184.6439 | 5863.8775 | 7477.7425 | 6364.3675 | 6364.3675 | 6364.3675 | 6364.3675 | 6364.3675 | 6364.3675 | 6364.3675 | 6364.3675 | 6364.3675 | 6364.3675 | 6364.3675 | 6364.3675 | 6364.3675 | 6364.3675 | 6364.3675 | 6364.3675
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 17.7632 | 43.0375 | 49.6507 | 49.2537 | 49.2817 | 49.9598 | 51.7502 | 52.9479 | 54.1209 | 55.493 | 56.7638 | 57.998 | 58.138 | 59.5788 | 58.4848 | 58.4848 | 58.4848 | 58.4848 | 58.4848 | 58.4848 | 58.4848 | 58.4848 | 58.4848 | 58.4848 | 58.4848 | 58.4848 | 58.4848 | 58.4848 | 58.4848 | 58.4848
98% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 8.4503 | 20.9604 | 24.2338 | 24.0373 | 24.0512 | 24.3868 | 25.273 | 25.8658 | 26.4464 | 27.1256 | 27.7546 | 28.3655 | 28.4348 | 29.1479 | 28.6065 | 28.6065 | 28.6065 | 28.6065 | 28.6065 | 28.6065 | 28.6065 | 28.6065 | 28.6065 | 28.6065 | 28.6065 | 28.6065 | 28.6065 | 28.6065 | 28.6065 | 28.6065
97% | 1.8466 | 8.0258 | 9.7077 | 9.6587 | 9.6569 | 9.8486 | 10.059 | 10.4908 | 10.8011 | 10.9695 | 11.1536 | 11.3221 | 11.6266 | 12.0045 | 11.9781 | 11.9781 | 11.9781 | 11.9781 | 11.9781 | 11.9781 | 11.9781 | 11.9781 | 11.9781 | 11.9781 | 11.9781 | 11.9781 | 11.9781 | 11.9781 | 11.9781 | 11.9781 |  | 16.0379 | 40.8042 | 47.2844 | 46.8955 | 46.9229 | 47.5873 | 49.3417 | 50.5154 | 51.6648 | 53.0093 | 54.2545 | 55.464 | 55.6012 | 57.013 | 55.941 | 55.941 | 55.941 | 55.941 | 55.941 | 55.941 | 55.941 | 55.941 | 55.941 | 55.941 | 55.941 | 55.941 | 55.941 | 55.941 | 55.941 | 55.941
95% | 7.7819 | 38.2025 | 46.4828 | 46.2417 | 46.2328 | 47.1765 | 48.212 | 50.3381 | 51.8658 | 52.6946 | 53.6008 | 54.4305 | 55.9296 | 57.7903 | 57.6602 | 57.6602 | 57.6602 | 57.6602 | 57.6602 | 57.6602 | 57.6602 | 57.6602 | 57.6602 | 57.6602 | 57.6602 | 57.6602 | 57.6602 | 57.6602 | 57.6602 | 57.6602 |  | 22.1159 | 58.6938 | 68.2646 | 67.6901 | 67.7307 | 68.712 | 71.3031 | 73.0364 | 74.7341 | 76.7198 | 78.559 | 80.3452 | 80.5479 | 82.6329 | 81.0498 | 81.0498 | 81.0498 | 81.0498 | 81.0498 | 81.0498 | 81.0498 | 81.0498 | 81.0498 | 81.0498 | 81.0498 | 81.0498 | 81.0498 | 81.0498 | 81.0498 | 81.0498
90% | 7.9129 | 60.6736 | 75.0348 | 74.6165 | 74.6011 | 76.2379 | 78.0339 | 81.7213 | 84.371 | 85.8084 | 87.3801 | 88.819 | 91.4191 | 94.6462 | 94.4206 | 94.4206 | 94.4206 | 94.4206 | 94.4206 | 94.4206 | 94.4206 | 94.4206 | 94.4206 | 94.4206 | 94.4206 | 94.4206 | 94.4206 | 94.4206 | 94.4206 | 94.4206 |  | 79.1417 | 237.7413 | 279.2396 | 276.7487 | 276.9246 | 281.1792 | 292.4144 | 299.93 | 307.291 | 315.901 | 323.8752 | 331.6203 | 332.499 | 341.5397 | 334.6752 | 334.6752 | 334.6752 | 334.6752 | 334.6752 | 334.6752 | 334.6752 | 334.6752 | 334.6752 | 334.6752 | 334.6752 | 334.6752 | 334.6752 | 334.6752 | 334.6752 | 334.6752
85% | 2.1831 | 147.3455 | 188.1003 | 186.9134 | 186.8697 | 191.5145 | 196.6114 | 207.0756 | 214.595 | 218.674 | 223.1344 | 227.2178 | 234.5963 | 243.7543 | 243.1142 | 243.1142 | 243.1142 | 243.1142 | 243.1142 | 243.1142 | 243.1142 | 243.1142 | 243.1142 | 243.1142 | 243.1142 | 243.1142 | 243.1142 | 243.1142 | 243.1142 | 243.1142 |  | 50.0275 | 200.0542 | 239.3094 | 236.9532 | 237.1195 | 241.1442 | 251.772 | 258.8814 | 265.8444 | 273.989 | 281.5323 | 288.8587 | 289.6899 | 298.2419 | 291.7484 | 291.7484 | 291.7484 | 291.7484 | 291.7484 | 291.7484 | 291.7484 | 291.7484 | 291.7484 | 291.7484 | 291.7484 | 291.7484 | 291.7484 | 291.7484 | 291.7484 | 291.7484
80% |  | 166.9191 | 223.8464 | 222.1885 | 222.1274 | 228.6154 | 235.7349 | 250.3515 | 260.8548 | 266.5525 | 272.783 | 278.4866 | 288.7932 | 301.5853 | 300.6912 | 300.6912 | 300.6912 | 300.6912 | 300.6912 | 300.6912 | 300.6912 | 300.6912 | 300.6912 | 300.6912 | 300.6912 | 300.6912 | 300.6912 | 300.6912 | 300.6912 | 300.6912 |  | 15.4914 | 120.2719 | 147.6883 | 146.0426 | 146.1588 | 148.9697 | 156.3923 | 161.3576 | 166.2207 | 171.909 | 177.1773 | 182.2941 | 182.8747 | 188.8475 | 184.3124 | 184.3124 | 184.3124 | 184.3124 | 184.3124 | 184.3124 | 184.3124 | 184.3124 | 184.3124 | 184.3124 | 184.3124 | 184.3124 | 184.3124 | 184.3124 | 184.3124 | 184.3124
75% |  | 320.647 | 469.0463 | 464.7244 | 464.5651 | 481.4781 | 500.0374 | 538.1403 | 565.5205 | 580.3733 | 596.615 | 611.4834 | 638.3507 | 671.6975 | 669.3666 | 669.3666 | 669.3666 | 669.3666 | 669.3666 | 669.3666 | 669.3666 | 669.3666 | 669.3666 | 669.3666 | 669.3666 | 669.3666 | 669.3666 | 669.3666 | 669.3666 | 669.3666 |  | 0.97657 | 175.4756 | 224.4096 | 221.4724 | 221.6798 | 226.6968 | 239.945 | 248.8073 | 257.4872 | 267.6399 | 277.043 | 286.1758 | 287.212 | 297.8726 | 289.7781 | 289.7781 | 289.7781 | 289.7781 | 289.7781 | 289.7781 | 289.7781 | 289.7781 | 289.7781 | 289.7781 | 289.7781 | 289.7781 | 289.7781 | 289.7781 | 289.7781 | 289.7781
70% |  | 328.9116 | 585.3005 | 577.8335 | 577.5583 | 606.7787 | 638.8436 | 704.6738 | 751.9784 | 777.6395 | 805.7002 | 831.3883 | 877.8068 | 935.42 | 931.3929 | 931.3929 | 931.3929 | 931.3929 | 931.3929 | 931.3929 | 931.3929 | 931.3929 | 931.3929 | 931.3929 | 931.3929 | 931.3929 | 931.3929 | 931.3929 | 931.3929 | 931.3929 |  |  | 238.4252 | 327.5698 | 322.219 | 322.5968 | 331.7364 | 355.8711 | 372.0158 | 387.8282 | 406.3238 | 423.4537 | 440.0913 | 441.9789 | 461.3997 | 446.6536 | 446.6536 | 446.6536 | 446.6536 | 446.6536 | 446.6536 | 446.6536 | 446.6536 | 446.6536 | 446.6536 | 446.6536 | 446.6536 | 446.6536 | 446.6536 | 446.6536 | 446.6536
65% |  | 199.3768 | 820.987 | 802.2336 | 801.5424 | 874.9301 | 955.4618 | 1120.7959 | 1239.6024 | 1304.0507 | 1374.5258 | 1439.0422 | 1555.6231 | 1700.32 | 1690.2059 | 1690.2059 | 1690.2059 | 1690.2059 | 1690.2059 | 1690.2059 | 1690.2059 | 1690.2059 | 1690.2059 | 1690.2059 | 1690.2059 | 1690.2059 | 1690.2059 | 1690.2059 | 1690.2059 | 1690.2059 |  |  | 182.6144 | 294.7721 | 288.04 | 288.5153 | 300.0144 | 330.3796 | 350.692 | 370.5866 | 393.8569 | 415.4089 | 436.3416 | 438.7165 | 463.1508 | 444.598 | 444.598 | 444.598 | 444.598 | 444.598 | 444.598 | 444.598 | 444.598 | 444.598 | 444.598 | 444.598 | 444.598 | 444.598 | 444.598 | 444.598 | 444.598
60% |  |  | 203.5024 | 187.5582 | 186.9825 | 252.8081 | 335.7847 | 540.3015 | 711.4984 | 805.7041 | 908.7192 | 1003.0243 | 1173.4335 | 1384.9404 | 1370.1564 | 1370.1564 | 1370.1564 | 1370.1564 | 1370.1564 | 1370.1564 | 1370.1564 | 1370.1564 | 1370.1564 | 1370.1564 | 1370.1564 | 1370.1564 | 1370.1564 | 1370.1564 | 1370.1564 | 1370.1564 |  |  | 77.0598 | 248.2313 | 237.6968 | 238.4405 | 256.4344 | 303.9503 | 335.7356 | 366.8668 | 403.2805 | 437.0055 | 469.7612 | 473.4775 | 511.7128 | 482.681 | 482.681 | 482.681 | 482.681 | 482.681 | 482.681 | 482.681 | 482.681 | 482.681 | 482.681 | 482.681 | 482.681 | 482.681 | 482.681 | 482.681 | 482.681
55% | [8 empty] | 3.8903 | 15.7556 | 37.6919 | 65.8304 | 135.7599 | 255.725 | 246.1724 | 246.1724 | 246.1724 | 246.1724 | 246.1724 | 246.1724 | 246.1724 | 246.1724 | 246.1724 | 246.1724 | 246.1724 | 246.1724 | 246.1724 | 246.1724 | 246.1724 | 246.1724 |  |  |  | 63.4905 | 53.6808 | 54.3475 | 71.6739 | 128.262 | 174.6238 | 226.4176 | 294.3956 | 359.2034 | 422.1487 | 429.2901 | 502.7651 | 446.976 | 446.976 | 446.976 | 446.976 | 446.976 | 446.976 | 446.976 | 446.976 | 446.976 | 446.976 | 446.976 | 446.976 | 446.976 | 446.976 | 446.976 | 446.976
50% | [40 empty] | 0.92441 | 14.9076 | 44.2124 | 48.4954 | 103.6497 | 59.9312 | 59.9312 | 59.9312 | 59.9312 | 59.9312 | 59.9312 | 59.9312 | 59.9312 | 59.9312 | 59.9312 | 59.9312 | 59.9312 | 59.9312 | 59.9312 | 59.9312 | 59.9312
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 19.7244 | 1270.1019 | 2622.0083 | 2571.9686 | 2570.1362 | 2769.3877 | 2998.7788 | 3503.8889 | 3894.9777 | 4118.2221 | 4371.3041 | 4611.0446 | 5063.3387 | 5657.8836 | 5615.1586 | 5615.1586 | 5615.1586 | 5615.1586 | 5615.1586 | 5615.1586 | 5615.1586 | 5615.1586 | 5615.1586 | 5615.1586 | 5615.1586 | 5615.1586 | 5615.1586 | 5615.1586 | 5615.1586 | 5615.1586 | E @ R (MWh) | 210.0044 | 1395.1384 | 2014.1441 | 1970.7302 | 1973.7695 | 2048.4946 | 2256.6548 | 2404.4088 | 2555.5088 | 2740.5678 | 2926.9386 | 3123.6769 | 3146.9559 | 3397.5525 | 3205.4359 | 3205.4359 | 3205.4359 | 3205.4359 | 3205.4359 | 3205.4359 | 3205.4359 | 3205.4359 | 3205.4359 | 3205.4359 | 3205.4359 | 3205.4359 | 3205.4359 | 3205.4359 | 3205.4359 | 3205.4359
Option 6 Summer POE50 W E @ R (MWh) N 1 | 13.8071 | 889.0713 | 1835.4058 | 1800.378 | 1799.0954 | 1938.5714 | 2099.1452 | 2452.7222 | 2726.4844 | 2882.7555 | 3059.9129 | 3227.7312 | 3544.3371 | 3960.5185 | 3930.611 | 3930.611 | 3930.611 | 3930.611 | 3930.611 | 3930.611 | 3930.611 | 3930.611 | 3930.611 | 3930.611 | 3930.611 | 3930.611 | 3930.611 | 3930.611 | 3930.611 | 3930.611 | Option 6 Summer POE10 W E @ R (MWh) N 1 | 63.0013 | 418.5415 | 604.2432 | 591.2191 | 592.1308 | 614.5484 | 676.9964 | 721.3226 | 766.6526 | 822.1703 | 878.0816 | 937.1031 | 944.0868 | 1019.2657 | 961.6308 | 961.6308 | 961.6308 | 961.6308 | 961.6308 | 961.6308 | 961.6308 | 961.6308 | 961.6308 | 961.6308 | 961.6308 | 961.6308 | 961.6308 | 961.6308 | 961.6308 | 961.6308
Option 7 -
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% |  | 19.3557 | 26.0414 | 27.1786 | 28.0631 | 29.5913 | 33.0724 | 35.3998 | 38.3512 | 39.8816 | 41.2259 | 38.7366 | 41.6468 | 46.224 | 42.7448 | 42.7448 | 42.7448 | 42.7448 | 42.7448 | 42.7448 | 42.7448 | 42.7448 | 42.7448 | 42.7448 | 42.7448 | 42.7448 | 42.7448 | 42.7448 | 42.7448 | 42.7448 |  |  | 23.7132 | 30.66 | 31.7324 | 32.4104 | 33.9055 | 37.4409 | 39.3681 | 43.0454 | 54.2301 | 45.0018 | 43.1944 | 45.6265 | 50.9491 | 47.3408 | 47.3408 | 47.3408 | 47.3408 | 47.3408 | 47.3408 | 47.3408 | 47.3408 | 47.3408 | 47.3408 | 47.3408 | 47.3408 | 47.3408 | 47.3408 | 47.3408 | 47.3408
98% |  | 22.1134 | 30.0556 | 31.4065 | 32.4573 | 34.2728 | 38.408 | 41.1729 | 44.679 | 46.497 | 48.0939 | 45.1368 | 48.594 | 54.0314 | 49.8983 | 49.8983 | 49.8983 | 49.8983 | 49.8983 | 49.8983 | 49.8983 | 49.8983 | 49.8983 | 49.8983 | 49.8983 | 49.8983 | 49.8983 | 49.8983 | 49.8983 | 49.8983 |  |  | 27.2899 | 35.5423 | 36.8162 | 37.6217 | 39.3977 | 43.5976 | 45.887 | 50.2554 | 63.5422 | 52.5795 | 50.4324 | 53.3215 | 59.6445 | 55.358 | 55.358 | 55.358 | 55.358 | 55.358 | 55.358 | 55.358 | 55.358 | 55.358 | 55.358 | 55.358 | 55.358 | 55.358 | 55.358 | 55.358 | 55.358
97% |  | 42.0001 | 57.7232 | 60.3976 | 62.4779 | 66.0719 | 74.2584 | 79.732 | 86.673 | 90.2721 | 93.4336 | 87.5793 | 94.4235 | 105.1879 | 97.0056 | 97.0056 | 97.0056 | 97.0056 | 97.0056 | 97.0056 | 97.0056 | 97.0056 | 97.0056 | 97.0056 | 97.0056 | 97.0056 | 97.0056 | 97.0056 | 97.0056 | 97.0056 |  |  | 52.248 | 68.5852 | 71.1071 | 72.7018 | 76.2177 | 84.5323 | 89.0645 | 97.7126 | 124.0163 | 102.3136 | 98.0631 | 103.7826 | 116.3002 | 107.8143 | 107.8143 | 107.8143 | 107.8143 | 107.8143 | 107.8143 | 107.8143 | 107.8143 | 107.8143 | 107.8143 | 107.8143 | 107.8143 | 107.8143 | 107.8143 | 107.8143 | 107.8143
95% |  | 115.9799 | 162.4236 | 170.3233 | 176.4681 | 187.0842 | 211.266 | 227.434 | 247.9367 | 258.5678 | 267.9064 | 250.6138 | 270.8306 | 302.6268 | 278.4578 | 278.4578 | 278.4578 | 278.4578 | 278.4578 | 278.4578 | 278.4578 | 278.4578 | 278.4578 | 278.4578 | 278.4578 | 278.4578 | 278.4578 | 278.4578 | 278.4578 | 278.4578 |  |  | 146.2505 | 194.5083 | 201.9576 | 206.6678 | 217.0533 | 241.6134 | 255.0008 | 280.5461 | 358.2432 | 294.1368 | 281.5814 | 298.4759 | 335.451 | 310.3848 | 310.3848 | 310.3848 | 310.3848 | 310.3848 | 310.3848 | 310.3848 | 310.3848 | 310.3848 | 310.3848 | 310.3848 | 310.3848 | 310.3848 | 310.3848 | 310.3848 | 310.3848
90% |  | 529.8714 | 785.9431 | 829.499 | 863.379 | 921.9121 | 1055.2409 | 1144.3849 | 1257.4283 | 1316.044 | 1367.5334 | 1272.189 | 1383.6562 | 1558.9677 | 1425.7093 | 1425.7093 | 1425.7093 | 1425.7093 | 1425.7093 | 1425.7093 | 1425.7093 | 1425.7093 | 1425.7093 | 1425.7093 | 1425.7093 | 1425.7093 | 1425.7093 | 1425.7093 | 1425.7093 | 1425.7093 |  |  | 696.7712 | 962.8455 | 1003.918 | 1029.8882 | 1087.1494 | 1222.564 | 1296.377 | 1437.2235 | 1865.6143 | 1512.1572 | 1442.9317 | 1536.0814 | 1739.9469 | 1601.7422 | 1601.7422 | 1601.7422 | 1601.7422 | 1601.7422 | 1601.7422 | 1601.7422 | 1601.7422 | 1601.7422 | 1601.7422 | 1601.7422 | 1601.7422 | 1601.7422 | 1601.7422 | 1601.7422 | 1601.7422
85% |  | 874.8065 | 1500.3713 | 1606.7752 | 1689.5415 | 1832.5337 | 2158.2465 | 2376.0188 | 2652.1757 | 2795.3696 | 2921.1546 | 2688.2351 | 2960.5416 | 3388.8149 | 3063.2741 | 3063.2741 | 3063.2741 | 3063.2741 | 3063.2741 | 3063.2741 | 3063.2741 | 3063.2741 | 3063.2741 | 3063.2741 | 3063.2741 | 3063.2741 | 3063.2741 | 3063.2741 | 3063.2741 | 3063.2741 |  |  | 1282.5306 | 1932.5312 | 2032.8683 | 2096.3116 | 2236.1967 | 2567.0047 | 2747.3247 | 3091.4025 | 4137.9307 | 3274.4602 | 3105.3472 | 3332.9054 | 3830.934 | 3493.3099 | 3493.3099 | 3493.3099 | 3493.3099 | 3493.3099 | 3493.3099 | 3493.3099 | 3493.3099 | 3493.3099 | 3493.3099 | 3493.3099 | 3493.3099 | 3493.3099 | 3493.3099 | 3493.3099 | 3493.3099
80% |  | 628.4185 | 1600.7316 | 1766.1149 | 1894.7582 | 2117.0105 | 2623.2647 | 2961.7475 | 3390.9772 | 3613.543 | 3809.0501 | 3447.0242 | 3870.2692 | 4535.9328 | 4029.946 | 4029.946 | 4029.946 | 4029.946 | 4029.946 | 4029.946 | 4029.946 | 4029.946 | 4029.946 | 4029.946 | 4029.946 | 4029.946 | 4029.946 | 4029.946 | 4029.946 | 4029.946 |  |  | 1262.1427 | 2272.4362 | 2428.3899 | 2526.9996 | 2744.4225 | 3258.5963 | 3538.867 | 4073.6659 | 5700.2809 | 4358.1918 | 4095.3401 | 4449.033 | 5223.1171 | 4698.349 | 4698.349 | 4698.349 | 4698.349 | 4698.349 | 4698.349 | 4698.349 | 4698.349 | 4698.349 | 4698.349 | 4698.349 | 4698.349 | 4698.349 | 4698.349 | 4698.349 | 4698.349
75% |  | 35.4297 | 855.1312 | 1037.5951 | 1179.5246 | 1424.7309 | 1983.2706 | 2356.7115 | 2830.2717 | 3075.8238 | 3291.5228 | 2892.1072 | 3359.0645 | 4093.4773 | 3535.2326 | 3535.2326 | 3535.2326 | 3535.2326 | 3535.2326 | 3535.2326 | 3535.2326 | 3535.2326 | 3535.2326 | 3535.2326 | 3535.2326 | 3535.2326 | 3535.2326 | 3535.2326 | 3535.2326 | 3535.2326 |  |  | 481.7498 | 1596.2089 | 1768.2692 | 1877.0633 | 2116.9414 | 2684.2186 | 2993.4354 | 3583.4678 | 5378.0782 | 3897.3793 | 3607.3806 | 3997.6025 | 4851.6333 | 4272.6677 | 4272.6677 | 4272.6677 | 4272.6677 | 4272.6677 | 4272.6677 | 4272.6677 | 4272.6677 | 4272.6677 | 4272.6677 | 4272.6677 | 4272.6677 | 4272.6677 | 4272.6677 | 4272.6677 | 4272.6677
70% |  |  | 65.8085 | 149.3801 | 236.763 | 432.2706 | 1017.18 | 1418.4215 | 1927.2354 | 2191.0675 | 2422.824 | 1993.6741 | 2495.3937 | 3284.4792 | 2684.6765 | 2684.6765 | 2684.6765 | 2684.6765 | 2684.6765 | 2684.6765 | 2684.6765 | 2684.6765 | 2684.6765 | 2684.6765 | 2684.6765 | 2684.6765 | 2684.6765 | 2684.6765 | 2684.6765 | 2684.6765 |  |  |  | 601.3916 | 786.1731 | 903.0662 | 1160.8019 | 1770.3095 | 2102.5457 | 2736.5026 | 4664.7111 | 3073.7829 | 2762.1954 | 3181.4671 | 4099.0755 | 3477.0093 | 3477.0093 | 3477.0093 | 3477.0093 | 3477.0093 | 3477.0093 | 3477.0093 | 3477.0093 | 3477.0093 | 3477.0093 | 3477.0093 | 3477.0093 | 3477.0093 | 3477.0093 | 3477.0093 | 3477.0093
65% | [6 empty] | 67.1746 | 263.316 | 684.8354 | 961.4279 | 1205.6548 | 753.4132 | 1282.1294 | 2113.6742 | 1481.5972 | 1481.5972 | 1481.5972 | 1481.5972 | 1481.5972 | 1481.5972 | 1481.5972 | 1481.5972 | 1481.5972 | 1481.5972 | 1481.5972 | 1481.5972 | 1481.5972 | 1481.5972 | 1481.5972 | 1481.5972 |  |  |  |  | 12.1974 | 34.5742 | 123.0009 | 535.0416 | 868.1429 | 1536.2119 | 3568.1739 | 1891.6407 | 1563.2873 | 2005.1192 | 2972.1025 | 2316.564 | 2316.564 | 2316.564 | 2316.564 | 2316.564 | 2316.564 | 2316.564 | 2316.564 | 2316.564 | 2316.564 | 2316.564 | 2316.564 | 2316.564 | 2316.564 | 2316.564 | 2316.564
60% | [9 empty] | 15.996 | 73.9877 | 0.0013268 | 100.6328 | 637.7145 | 188.7046 | 188.7046 | 188.7046 | 188.7046 | 188.7046 | 188.7046 | 188.7046 | 188.7046 | 188.7046 | 188.7046 | 188.7046 | 188.7046 | 188.7046 | 188.7046 | 188.7046 | 188.7046 | [8 empty] | 4.9606 | 217.4281 | 2207.292 | 451.391 | 232.3927 | 542.8433 | 1551.0908 | 834.0186 | 834.0186 | 834.0186 | 834.0186 | 834.0186 | 834.0186 | 834.0186 | 834.0186 | 834.0186 | 834.0186 | 834.0186 | 834.0186 | 834.0186 | 834.0186 | 834.0186 | 834.0186
55% | [40 empty] | 420.5237 |  |  |  | 95.5636
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 2267.9753 | 5084.2295 | 5678.6703 | 6163.4327 | 7045.478 | 9261.3822 | 10904.3389 | 13160.5637 | 14404.4901 | 15542.3873 | 13468.7106 | 15907.1825 | 20121.1305 | 16877.247 | 16877.247 | 16877.247 | 16877.247 | 16877.247 | 16877.247 | 16877.247 | 16877.247 | 16877.247 | 16877.247 | 16877.247 | 16877.247 | 16877.247 | 16877.247 | 16877.247 | 16877.247 | E @ R (MWh) | 0 | 3972.6958 | 7694.7094 | 8373.4293 | 8817.3048 | 9835.0869 | 12444.9189 | 13980.9735 | 17147.4619 | 28542.6368 | 18953.035 | 17282.1464 | 19546.2584 | 24925.8084 | 21214.5583 | 21214.5583 | 21214.5583 | 21214.5583 | 21214.5583 | 21214.5583 | 21214.5583 | 21214.5583 | 21214.5583 | 21214.5583 | 21214.5583 | 21214.5583 | 21214.5583 | 21214.5583 | 21214.5583 | 21214.5583
Option 7 Winter POE50 W E @ R (MWh) N 1 | 0 | 1587.5827 | 3558.9606 | 3975.0692 | 4314.4029 | 4931.8346 | 6482.9675 | 7633.0372 | 9212.3946 | 10083.1431 | 10879.6711 | 9428.0974 | 11135.0277 | 14084.7914 | 11814.0729 | 11814.0729 | 11814.0729 | 11814.0729 | 11814.0729 | 11814.0729 | 11814.0729 | 11814.0729 | 11814.0729 | 11814.0729 | 11814.0729 | 11814.0729 | 11814.0729 | 11814.0729 | 11814.0729 | 11814.0729 | Option 7 Winter POE10 W E @ R (MWh) N 1 | 0 | 1191.8087 | 2308.4128 | 2512.0288 | 2645.1914 | 2950.5261 | 3733.4757 | 4194.2921 | 5144.2386 | 8562.791 | 5685.9105 | 5184.6439 | 5863.8775 | 7477.7425 | 6364.3675 | 6364.3675 | 6364.3675 | 6364.3675 | 6364.3675 | 6364.3675 | 6364.3675 | 6364.3675 | 6364.3675 | 6364.3675 | 6364.3675 | 6364.3675 | 6364.3675 | 6364.3675 | 6364.3675 | 6364.3675
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 17.7632 | 43.0375 | 49.6507 | 49.2537 | 49.2817 | 49.9598 | 51.7502 | 52.9479 | 54.1209 | 55.493 | 56.7638 | 57.998 | 58.138 | 59.5788 | 58.4848 | 58.4848 | 58.4848 | 58.4848 | 58.4848 | 58.4848 | 58.4848 | 58.4848 | 58.4848 | 58.4848 | 58.4848 | 58.4848 | 58.4848 | 58.4848 | 58.4848 | 58.4848
98% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 8.4503 | 20.9604 | 24.2338 | 24.0373 | 24.0512 | 24.3868 | 25.273 | 25.8658 | 26.4464 | 27.1256 | 27.7546 | 28.3655 | 28.4348 | 29.1479 | 28.6065 | 28.6065 | 28.6065 | 28.6065 | 28.6065 | 28.6065 | 28.6065 | 28.6065 | 28.6065 | 28.6065 | 28.6065 | 28.6065 | 28.6065 | 28.6065 | 28.6065 | 28.6065
97% | 1.8466 | 8.0258 | 9.7077 | 9.6587 | 9.6569 | 9.8486 | 10.059 | 10.4908 | 10.8011 | 10.9695 | 11.1536 | 11.3221 | 11.6266 | 12.0045 | 11.9781 | 11.9781 | 11.9781 | 11.9781 | 11.9781 | 11.9781 | 11.9781 | 11.9781 | 11.9781 | 11.9781 | 11.9781 | 11.9781 | 11.9781 | 11.9781 | 11.9781 | 11.9781 |  | 16.0379 | 40.8042 | 47.2844 | 46.8955 | 46.9229 | 47.5873 | 49.3417 | 50.5154 | 51.6648 | 53.0093 | 54.2545 | 55.464 | 55.6012 | 57.013 | 55.941 | 55.941 | 55.941 | 55.941 | 55.941 | 55.941 | 55.941 | 55.941 | 55.941 | 55.941 | 55.941 | 55.941 | 55.941 | 55.941 | 55.941 | 55.941
95% | 7.7819 | 38.2025 | 46.4828 | 46.2417 | 46.2328 | 47.1765 | 48.212 | 50.3381 | 51.8658 | 52.6946 | 53.6008 | 54.4305 | 55.9296 | 57.7903 | 57.6602 | 57.6602 | 57.6602 | 57.6602 | 57.6602 | 57.6602 | 57.6602 | 57.6602 | 57.6602 | 57.6602 | 57.6602 | 57.6602 | 57.6602 | 57.6602 | 57.6602 | 57.6602 |  | 22.1159 | 58.6938 | 68.2646 | 67.6901 | 67.7307 | 68.712 | 71.3031 | 73.0364 | 74.7341 | 76.7198 | 78.559 | 80.3452 | 80.5479 | 82.6329 | 81.0498 | 81.0498 | 81.0498 | 81.0498 | 81.0498 | 81.0498 | 81.0498 | 81.0498 | 81.0498 | 81.0498 | 81.0498 | 81.0498 | 81.0498 | 81.0498 | 81.0498 | 81.0498
90% | 7.9129 | 60.6736 | 75.0348 | 74.6165 | 74.6011 | 76.2379 | 78.0339 | 81.7213 | 84.371 | 85.8084 | 87.3801 | 88.819 | 91.4191 | 94.6462 | 94.4206 | 94.4206 | 94.4206 | 94.4206 | 94.4206 | 94.4206 | 94.4206 | 94.4206 | 94.4206 | 94.4206 | 94.4206 | 94.4206 | 94.4206 | 94.4206 | 94.4206 | 94.4206 |  | 79.1417 | 237.7413 | 279.2396 | 276.7487 | 276.9246 | 281.1792 | 292.4144 | 299.93 | 307.291 | 315.901 | 323.8752 | 331.6203 | 332.499 | 341.5397 | 334.6752 | 334.6752 | 334.6752 | 334.6752 | 334.6752 | 334.6752 | 334.6752 | 334.6752 | 334.6752 | 334.6752 | 334.6752 | 334.6752 | 334.6752 | 334.6752 | 334.6752 | 334.6752
85% | 2.1831 | 147.3455 | 188.1003 | 186.9134 | 186.8697 | 191.5145 | 196.6114 | 207.0756 | 214.595 | 218.674 | 223.1344 | 227.2178 | 234.5963 | 243.7543 | 243.1142 | 243.1142 | 243.1142 | 243.1142 | 243.1142 | 243.1142 | 243.1142 | 243.1142 | 243.1142 | 243.1142 | 243.1142 | 243.1142 | 243.1142 | 243.1142 | 243.1142 | 243.1142 |  | 50.0275 | 200.0542 | 239.3094 | 236.9532 | 237.1195 | 241.1442 | 251.772 | 258.8814 | 265.8444 | 273.989 | 281.5323 | 288.8587 | 289.6899 | 298.2419 | 291.7484 | 291.7484 | 291.7484 | 291.7484 | 291.7484 | 291.7484 | 291.7484 | 291.7484 | 291.7484 | 291.7484 | 291.7484 | 291.7484 | 291.7484 | 291.7484 | 291.7484 | 291.7484
80% |  | 166.9191 | 223.8464 | 222.1885 | 222.1274 | 228.6154 | 235.7349 | 250.3515 | 260.8548 | 266.5525 | 272.783 | 278.4866 | 288.7932 | 301.5853 | 300.6912 | 300.6912 | 300.6912 | 300.6912 | 300.6912 | 300.6912 | 300.6912 | 300.6912 | 300.6912 | 300.6912 | 300.6912 | 300.6912 | 300.6912 | 300.6912 | 300.6912 | 300.6912 |  | 15.4914 | 120.2719 | 147.6883 | 146.0426 | 146.1588 | 148.9697 | 156.3923 | 161.3576 | 166.2207 | 171.909 | 177.1773 | 182.2941 | 182.8747 | 188.8475 | 184.3124 | 184.3124 | 184.3124 | 184.3124 | 184.3124 | 184.3124 | 184.3124 | 184.3124 | 184.3124 | 184.3124 | 184.3124 | 184.3124 | 184.3124 | 184.3124 | 184.3124 | 184.3124
75% |  | 320.647 | 469.0463 | 464.7244 | 464.5651 | 481.4781 | 500.0374 | 538.1403 | 565.5205 | 580.3733 | 596.615 | 611.4834 | 638.3507 | 671.6975 | 669.3666 | 669.3666 | 669.3666 | 669.3666 | 669.3666 | 669.3666 | 669.3666 | 669.3666 | 669.3666 | 669.3666 | 669.3666 | 669.3666 | 669.3666 | 669.3666 | 669.3666 | 669.3666 |  | 0.97657 | 175.4756 | 224.4096 | 221.4724 | 221.6798 | 226.6968 | 239.945 | 248.8073 | 257.4872 | 267.6399 | 277.043 | 286.1758 | 287.212 | 297.8726 | 289.7781 | 289.7781 | 289.7781 | 289.7781 | 289.7781 | 289.7781 | 289.7781 | 289.7781 | 289.7781 | 289.7781 | 289.7781 | 289.7781 | 289.7781 | 289.7781 | 289.7781 | 289.7781
70% |  | 328.9116 | 585.3005 | 577.8335 | 577.5583 | 606.7787 | 638.8436 | 704.6738 | 751.9784 | 777.6395 | 805.7002 | 831.3883 | 877.8068 | 935.42 | 931.3929 | 931.3929 | 931.3929 | 931.3929 | 931.3929 | 931.3929 | 931.3929 | 931.3929 | 931.3929 | 931.3929 | 931.3929 | 931.3929 | 931.3929 | 931.3929 | 931.3929 | 931.3929 |  |  | 238.4252 | 327.5698 | 322.219 | 322.5968 | 331.7364 | 355.8711 | 372.0158 | 387.8282 | 406.3238 | 423.4537 | 440.0913 | 441.9789 | 461.3997 | 446.6536 | 446.6536 | 446.6536 | 446.6536 | 446.6536 | 446.6536 | 446.6536 | 446.6536 | 446.6536 | 446.6536 | 446.6536 | 446.6536 | 446.6536 | 446.6536 | 446.6536 | 446.6536
65% |  | 199.3768 | 820.987 | 802.2336 | 801.5424 | 874.9301 | 955.4618 | 1120.7959 | 1239.6024 | 1304.0507 | 1374.5258 | 1439.0422 | 1555.6231 | 1700.32 | 1690.2059 | 1690.2059 | 1690.2059 | 1690.2059 | 1690.2059 | 1690.2059 | 1690.2059 | 1690.2059 | 1690.2059 | 1690.2059 | 1690.2059 | 1690.2059 | 1690.2059 | 1690.2059 | 1690.2059 | 1690.2059 |  |  | 182.6144 | 294.7721 | 288.04 | 288.5153 | 300.0144 | 330.3796 | 350.692 | 370.5866 | 393.8569 | 415.4089 | 436.3416 | 438.7165 | 463.1508 | 444.598 | 444.598 | 444.598 | 444.598 | 444.598 | 444.598 | 444.598 | 444.598 | 444.598 | 444.598 | 444.598 | 444.598 | 444.598 | 444.598 | 444.598 | 444.598
60% |  |  | 203.5024 | 187.5582 | 186.9825 | 252.8081 | 335.7847 | 540.3015 | 711.4984 | 805.7041 | 908.7192 | 1003.0243 | 1173.4335 | 1384.9404 | 1370.1564 | 1370.1564 | 1370.1564 | 1370.1564 | 1370.1564 | 1370.1564 | 1370.1564 | 1370.1564 | 1370.1564 | 1370.1564 | 1370.1564 | 1370.1564 | 1370.1564 | 1370.1564 | 1370.1564 | 1370.1564 |  |  | 77.0598 | 248.2313 | 237.6968 | 238.4405 | 256.4344 | 303.9503 | 335.7356 | 366.8668 | 403.2805 | 437.0055 | 469.7612 | 473.4775 | 511.7128 | 482.681 | 482.681 | 482.681 | 482.681 | 482.681 | 482.681 | 482.681 | 482.681 | 482.681 | 482.681 | 482.681 | 482.681 | 482.681 | 482.681 | 482.681 | 482.681
55% | [8 empty] | 3.8903 | 15.7556 | 37.6919 | 65.8304 | 135.7599 | 255.725 | 246.1724 | 246.1724 | 246.1724 | 246.1724 | 246.1724 | 246.1724 | 246.1724 | 246.1724 | 246.1724 | 246.1724 | 246.1724 | 246.1724 | 246.1724 | 246.1724 | 246.1724 | 246.1724 |  |  |  | 63.4905 | 53.6808 | 54.3475 | 71.6739 | 128.262 | 174.6238 | 226.4176 | 294.3956 | 359.2034 | 422.1487 | 429.2901 | 502.7651 | 446.976 | 446.976 | 446.976 | 446.976 | 446.976 | 446.976 | 446.976 | 446.976 | 446.976 | 446.976 | 446.976 | 446.976 | 446.976 | 446.976 | 446.976 | 446.976
50% | [40 empty] | 0.92441 | 14.9076 | 44.2124 | 48.4954 | 103.6497 | 59.9312 | 59.9312 | 59.9312 | 59.9312 | 59.9312 | 59.9312 | 59.9312 | 59.9312 | 59.9312 | 59.9312 | 59.9312 | 59.9312 | 59.9312 | 59.9312 | 59.9312 | 59.9312
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 19.7244 | 1270.1019 | 2622.0083 | 2571.9686 | 2570.1362 | 2769.3877 | 2998.7788 | 3503.8889 | 3894.9777 | 4118.2221 | 4371.3041 | 4611.0446 | 5063.3387 | 5657.8836 | 5615.1586 | 5615.1586 | 5615.1586 | 5615.1586 | 5615.1586 | 5615.1586 | 5615.1586 | 5615.1586 | 5615.1586 | 5615.1586 | 5615.1586 | 5615.1586 | 5615.1586 | 5615.1586 | 5615.1586 | 5615.1586 | E @ R (MWh) | 210.0044 | 1395.1384 | 2014.1441 | 1970.7302 | 1973.7695 | 2048.4946 | 2256.6548 | 2404.4088 | 2555.5088 | 2740.5678 | 2926.9386 | 3123.6769 | 3146.9559 | 3397.5525 | 3205.4359 | 3205.4359 | 3205.4359 | 3205.4359 | 3205.4359 | 3205.4359 | 3205.4359 | 3205.4359 | 3205.4359 | 3205.4359 | 3205.4359 | 3205.4359 | 3205.4359 | 3205.4359 | 3205.4359 | 3205.4359
Option 7 Summer POE50 W E @ R (MWh) N 1 | 13.8071 | 889.0713 | 1835.4058 | 1800.378 | 1799.0954 | 1938.5714 | 2099.1452 | 2452.7222 | 2726.4844 | 2882.7555 | 3059.9129 | 3227.7312 | 3544.3371 | 3960.5185 | 3930.611 | 3930.611 | 3930.611 | 3930.611 | 3930.611 | 3930.611 | 3930.611 | 3930.611 | 3930.611 | 3930.611 | 3930.611 | 3930.611 | 3930.611 | 3930.611 | 3930.611 | 3930.611 | Option 7 Summer POE10 W E @ R (MWh) N 1 | 63.0013 | 418.5415 | 604.2432 | 591.2191 | 592.1308 | 614.5484 | 676.9964 | 721.3226 | 766.6526 | 822.1703 | 878.0816 | 937.1031 | 944.0868 | 1019.2657 | 961.6308 | 961.6308 | 961.6308 | 961.6308 | 961.6308 | 961.6308 | 961.6308 | 961.6308 | 961.6308 | 961.6308 | 961.6308 | 961.6308 | 961.6308 | 961.6308 | 961.6308 | 961.6308
Option 8 -
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% |  | 19.3557 | 26.0414 | 27.1786 | 28.0631 | 29.5913 | 33.0724 | 35.3998 | 38.3512 | 39.8816 | 41.2259 | 38.7366 | 41.6468 | 46.224 | 42.7448 | 42.7448 | 42.7448 | 42.7448 | 42.7448 | 42.7448 | 42.7448 | 42.7448 | 42.7448 | 42.7448 | 42.7448 | 42.7448 | 42.7448 | 42.7448 | 42.7448 | 42.7448 |  |  | 23.7132 | 30.66 | 31.7324 | 32.4104 | 33.9055 | 37.4409 | 39.3681 | 43.0454 | 54.2301 | 45.0018 | 43.1944 | 45.6265 | 50.9491 | 47.3408 | 47.3408 | 47.3408 | 47.3408 | 47.3408 | 47.3408 | 47.3408 | 47.3408 | 47.3408 | 47.3408 | 47.3408 | 47.3408 | 47.3408 | 47.3408 | 47.3408 | 47.3408
98% |  | 22.1134 | 30.0556 | 31.4065 | 32.4573 | 34.2728 | 38.408 | 41.1729 | 44.679 | 46.497 | 48.0939 | 45.1368 | 48.594 | 54.0314 | 49.8983 | 49.8983 | 49.8983 | 49.8983 | 49.8983 | 49.8983 | 49.8983 | 49.8983 | 49.8983 | 49.8983 | 49.8983 | 49.8983 | 49.8983 | 49.8983 | 49.8983 | 49.8983 |  |  | 27.2899 | 35.5423 | 36.8162 | 37.6217 | 39.3977 | 43.5976 | 45.887 | 50.2554 | 63.5422 | 52.5795 | 50.4324 | 53.3215 | 59.6445 | 55.358 | 55.358 | 55.358 | 55.358 | 55.358 | 55.358 | 55.358 | 55.358 | 55.358 | 55.358 | 55.358 | 55.358 | 55.358 | 55.358 | 55.358 | 55.358
97% |  | 42.0001 | 57.7232 | 60.3976 | 62.4779 | 66.0719 | 74.2584 | 79.732 | 86.673 | 90.2721 | 93.4336 | 87.5793 | 94.4235 | 105.1879 | 97.0056 | 97.0056 | 97.0056 | 97.0056 | 97.0056 | 97.0056 | 97.0056 | 97.0056 | 97.0056 | 97.0056 | 97.0056 | 97.0056 | 97.0056 | 97.0056 | 97.0056 | 97.0056 |  |  | 52.248 | 68.5852 | 71.1071 | 72.7018 | 76.2177 | 84.5323 | 89.0645 | 97.7126 | 124.0163 | 102.3136 | 98.0631 | 103.7826 | 116.3002 | 107.8143 | 107.8143 | 107.8143 | 107.8143 | 107.8143 | 107.8143 | 107.8143 | 107.8143 | 107.8143 | 107.8143 | 107.8143 | 107.8143 | 107.8143 | 107.8143 | 107.8143 | 107.8143
95% |  | 115.9799 | 162.4236 | 170.3233 | 176.4681 | 187.0842 | 211.266 | 227.434 | 247.9367 | 258.5678 | 267.9064 | 250.6138 | 270.8306 | 302.6268 | 278.4578 | 278.4578 | 278.4578 | 278.4578 | 278.4578 | 278.4578 | 278.4578 | 278.4578 | 278.4578 | 278.4578 | 278.4578 | 278.4578 | 278.4578 | 278.4578 | 278.4578 | 278.4578 |  |  | 146.2505 | 194.5083 | 201.9576 | 206.6678 | 217.0533 | 241.6134 | 255.0008 | 280.5461 | 358.2432 | 294.1368 | 281.5814 | 298.4759 | 335.451 | 310.3848 | 310.3848 | 310.3848 | 310.3848 | 310.3848 | 310.3848 | 310.3848 | 310.3848 | 310.3848 | 310.3848 | 310.3848 | 310.3848 | 310.3848 | 310.3848 | 310.3848 | 310.3848
90% |  | 529.8714 | 785.9431 | 829.499 | 863.379 | 921.9121 | 1055.2409 | 1144.3849 | 1257.4283 | 1316.044 | 1367.5334 | 1272.189 | 1383.6562 | 1558.9677 | 1425.7093 | 1425.7093 | 1425.7093 | 1425.7093 | 1425.7093 | 1425.7093 | 1425.7093 | 1425.7093 | 1425.7093 | 1425.7093 | 1425.7093 | 1425.7093 | 1425.7093 | 1425.7093 | 1425.7093 | 1425.7093 |  |  | 696.7712 | 962.8455 | 1003.918 | 1029.8882 | 1087.1494 | 1222.564 | 1296.377 | 1437.2235 | 1865.6143 | 1512.1572 | 1442.9317 | 1536.0814 | 1739.9469 | 1601.7422 | 1601.7422 | 1601.7422 | 1601.7422 | 1601.7422 | 1601.7422 | 1601.7422 | 1601.7422 | 1601.7422 | 1601.7422 | 1601.7422 | 1601.7422 | 1601.7422 | 1601.7422 | 1601.7422 | 1601.7422
85% |  | 874.8065 | 1500.3713 | 1606.7752 | 1689.5415 | 1832.5337 | 2158.2465 | 2376.0188 | 2652.1757 | 2795.3696 | 2921.1546 | 2688.2351 | 2960.5416 | 3388.8149 | 3063.2741 | 3063.2741 | 3063.2741 | 3063.2741 | 3063.2741 | 3063.2741 | 3063.2741 | 3063.2741 | 3063.2741 | 3063.2741 | 3063.2741 | 3063.2741 | 3063.2741 | 3063.2741 | 3063.2741 | 3063.2741 |  |  | 1282.5306 | 1932.5312 | 2032.8683 | 2096.3116 | 2236.1967 | 2567.0047 | 2747.3247 | 3091.4025 | 4137.9307 | 3274.4602 | 3105.3472 | 3332.9054 | 3830.934 | 3493.3099 | 3493.3099 | 3493.3099 | 3493.3099 | 3493.3099 | 3493.3099 | 3493.3099 | 3493.3099 | 3493.3099 | 3493.3099 | 3493.3099 | 3493.3099 | 3493.3099 | 3493.3099 | 3493.3099 | 3493.3099
80% |  | 628.4185 | 1600.7316 | 1766.1149 | 1894.7582 | 2117.0105 | 2623.2647 | 2961.7475 | 3390.9772 | 3613.543 | 3809.0501 | 3447.0242 | 3870.2692 | 4535.9328 | 4029.946 | 4029.946 | 4029.946 | 4029.946 | 4029.946 | 4029.946 | 4029.946 | 4029.946 | 4029.946 | 4029.946 | 4029.946 | 4029.946 | 4029.946 | 4029.946 | 4029.946 | 4029.946 |  |  | 1262.1427 | 2272.4362 | 2428.3899 | 2526.9996 | 2744.4225 | 3258.5963 | 3538.867 | 4073.6659 | 5700.2809 | 4358.1918 | 4095.3401 | 4449.033 | 5223.1171 | 4698.349 | 4698.349 | 4698.349 | 4698.349 | 4698.349 | 4698.349 | 4698.349 | 4698.349 | 4698.349 | 4698.349 | 4698.349 | 4698.349 | 4698.349 | 4698.349 | 4698.349 | 4698.349
75% |  | 35.4297 | 855.1312 | 1037.5951 | 1179.5246 | 1424.7309 | 1983.2706 | 2356.7115 | 2830.2717 | 3075.8238 | 3291.5228 | 2892.1072 | 3359.0645 | 4093.4773 | 3535.2326 | 3535.2326 | 3535.2326 | 3535.2326 | 3535.2326 | 3535.2326 | 3535.2326 | 3535.2326 | 3535.2326 | 3535.2326 | 3535.2326 | 3535.2326 | 3535.2326 | 3535.2326 | 3535.2326 | 3535.2326 |  |  | 481.7498 | 1596.2089 | 1768.2692 | 1877.0633 | 2116.9414 | 2684.2186 | 2993.4354 | 3583.4678 | 5378.0782 | 3897.3793 | 3607.3806 | 3997.6025 | 4851.6333 | 4272.6677 | 4272.6677 | 4272.6677 | 4272.6677 | 4272.6677 | 4272.6677 | 4272.6677 | 4272.6677 | 4272.6677 | 4272.6677 | 4272.6677 | 4272.6677 | 4272.6677 | 4272.6677 | 4272.6677 | 4272.6677
70% |  |  | 65.8085 | 149.3801 | 236.763 | 432.2706 | 1017.18 | 1418.4215 | 1927.2354 | 2191.0675 | 2422.824 | 1993.6741 | 2495.3937 | 3284.4792 | 2684.6765 | 2684.6765 | 2684.6765 | 2684.6765 | 2684.6765 | 2684.6765 | 2684.6765 | 2684.6765 | 2684.6765 | 2684.6765 | 2684.6765 | 2684.6765 | 2684.6765 | 2684.6765 | 2684.6765 | 2684.6765 |  |  |  | 601.3916 | 786.1731 | 903.0662 | 1160.8019 | 1770.3095 | 2102.5457 | 2736.5026 | 4664.7111 | 3073.7829 | 2762.1954 | 3181.4671 | 4099.0755 | 3477.0093 | 3477.0093 | 3477.0093 | 3477.0093 | 3477.0093 | 3477.0093 | 3477.0093 | 3477.0093 | 3477.0093 | 3477.0093 | 3477.0093 | 3477.0093 | 3477.0093 | 3477.0093 | 3477.0093 | 3477.0093
65% | [6 empty] | 67.1746 | 263.316 | 684.8354 | 961.4279 | 1205.6548 | 753.4132 | 1282.1294 | 2113.6742 | 1481.5972 | 1481.5972 | 1481.5972 | 1481.5972 | 1481.5972 | 1481.5972 | 1481.5972 | 1481.5972 | 1481.5972 | 1481.5972 | 1481.5972 | 1481.5972 | 1481.5972 | 1481.5972 | 1481.5972 | 1481.5972 |  |  |  |  | 12.1974 | 34.5742 | 123.0009 | 535.0416 | 868.1429 | 1536.2119 | 3568.1739 | 1891.6407 | 1563.2873 | 2005.1192 | 2972.1025 | 2316.564 | 2316.564 | 2316.564 | 2316.564 | 2316.564 | 2316.564 | 2316.564 | 2316.564 | 2316.564 | 2316.564 | 2316.564 | 2316.564 | 2316.564 | 2316.564 | 2316.564 | 2316.564
60% | [9 empty] | 15.996 | 73.9877 | 0.0013268 | 100.6328 | 637.7145 | 188.7046 | 188.7046 | 188.7046 | 188.7046 | 188.7046 | 188.7046 | 188.7046 | 188.7046 | 188.7046 | 188.7046 | 188.7046 | 188.7046 | 188.7046 | 188.7046 | 188.7046 | 188.7046 | [8 empty] | 4.9606 | 217.4281 | 2207.292 | 451.391 | 232.3927 | 542.8433 | 1551.0908 | 834.0186 | 834.0186 | 834.0186 | 834.0186 | 834.0186 | 834.0186 | 834.0186 | 834.0186 | 834.0186 | 834.0186 | 834.0186 | 834.0186 | 834.0186 | 834.0186 | 834.0186 | 834.0186
55% | [40 empty] | 420.5237 |  |  |  | 95.5636
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 2267.9753 | 5084.2295 | 5678.6703 | 6163.4327 | 7045.478 | 9261.3822 | 10904.3389 | 13160.5637 | 14404.4901 | 15542.3873 | 13468.7106 | 15907.1825 | 20121.1305 | 16877.247 | 16877.247 | 16877.247 | 16877.247 | 16877.247 | 16877.247 | 16877.247 | 16877.247 | 16877.247 | 16877.247 | 16877.247 | 16877.247 | 16877.247 | 16877.247 | 16877.247 | 16877.247 | E @ R (MWh) | 0 | 3972.6958 | 7694.7094 | 8373.4293 | 8817.3048 | 9835.0869 | 12444.9189 | 13980.9735 | 17147.4619 | 28542.6368 | 18953.035 | 17282.1464 | 19546.2584 | 24925.8084 | 21214.5583 | 21214.5583 | 21214.5583 | 21214.5583 | 21214.5583 | 21214.5583 | 21214.5583 | 21214.5583 | 21214.5583 | 21214.5583 | 21214.5583 | 21214.5583 | 21214.5583 | 21214.5583 | 21214.5583 | 21214.5583
Option 8 Winter POE50 W E @ R (MWh) N 1 | 0 | 1587.5827 | 3558.9606 | 3975.0692 | 4314.4029 | 4931.8346 | 6482.9675 | 7633.0372 | 9212.3946 | 10083.1431 | 10879.6711 | 9428.0974 | 11135.0277 | 14084.7914 | 11814.0729 | 11814.0729 | 11814.0729 | 11814.0729 | 11814.0729 | 11814.0729 | 11814.0729 | 11814.0729 | 11814.0729 | 11814.0729 | 11814.0729 | 11814.0729 | 11814.0729 | 11814.0729 | 11814.0729 | 11814.0729 | Option 8 Winter POE10 W E @ R (MWh) N 1 | 0 | 1191.8087 | 2308.4128 | 2512.0288 | 2645.1914 | 2950.5261 | 3733.4757 | 4194.2921 | 5144.2386 | 8562.791 | 5685.9105 | 5184.6439 | 5863.8775 | 7477.7425 | 6364.3675 | 6364.3675 | 6364.3675 | 6364.3675 | 6364.3675 | 6364.3675 | 6364.3675 | 6364.3675 | 6364.3675 | 6364.3675 | 6364.3675 | 6364.3675 | 6364.3675 | 6364.3675 | 6364.3675 | 6364.3675
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 17.7632 | 43.0375 | 49.6507 | 49.2537 | 49.2817 | 49.9598 | 51.7502 | 52.9479 | 54.1209 | 55.493 | 56.7638 | 57.998 | 58.138 | 59.5788 | 58.4848 | 58.4848 | 58.4848 | 58.4848 | 58.4848 | 58.4848 | 58.4848 | 58.4848 | 58.4848 | 58.4848 | 58.4848 | 58.4848 | 58.4848 | 58.4848 | 58.4848 | 58.4848
98% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 8.4503 | 20.9604 | 24.2338 | 24.0373 | 24.0512 | 24.3868 | 25.273 | 25.8658 | 26.4464 | 27.1256 | 27.7546 | 28.3655 | 28.4348 | 29.1479 | 28.6065 | 28.6065 | 28.6065 | 28.6065 | 28.6065 | 28.6065 | 28.6065 | 28.6065 | 28.6065 | 28.6065 | 28.6065 | 28.6065 | 28.6065 | 28.6065 | 28.6065 | 28.6065
97% | 1.8466 | 8.0258 | 9.7077 | 9.6587 | 9.6569 | 9.8486 | 10.059 | 10.4908 | 10.8011 | 10.9695 | 11.1536 | 11.3221 | 11.6266 | 12.0045 | 11.9781 | 11.9781 | 11.9781 | 11.9781 | 11.9781 | 11.9781 | 11.9781 | 11.9781 | 11.9781 | 11.9781 | 11.9781 | 11.9781 | 11.9781 | 11.9781 | 11.9781 | 11.9781 |  | 16.0379 | 40.8042 | 47.2844 | 46.8955 | 46.9229 | 47.5873 | 49.3417 | 50.5154 | 51.6648 | 53.0093 | 54.2545 | 55.464 | 55.6012 | 57.013 | 55.941 | 55.941 | 55.941 | 55.941 | 55.941 | 55.941 | 55.941 | 55.941 | 55.941 | 55.941 | 55.941 | 55.941 | 55.941 | 55.941 | 55.941 | 55.941
95% | 7.7819 | 38.2025 | 46.4828 | 46.2417 | 46.2328 | 47.1765 | 48.212 | 50.3381 | 51.8658 | 52.6946 | 53.6008 | 54.4305 | 55.9296 | 57.7903 | 57.6602 | 57.6602 | 57.6602 | 57.6602 | 57.6602 | 57.6602 | 57.6602 | 57.6602 | 57.6602 | 57.6602 | 57.6602 | 57.6602 | 57.6602 | 57.6602 | 57.6602 | 57.6602 |  | 22.1159 | 58.6938 | 68.2646 | 67.6901 | 67.7307 | 68.712 | 71.3031 | 73.0364 | 74.7341 | 76.7198 | 78.559 | 80.3452 | 80.5479 | 82.6329 | 81.0498 | 81.0498 | 81.0498 | 81.0498 | 81.0498 | 81.0498 | 81.0498 | 81.0498 | 81.0498 | 81.0498 | 81.0498 | 81.0498 | 81.0498 | 81.0498 | 81.0498 | 81.0498
90% | 7.9129 | 60.6736 | 75.0348 | 74.6165 | 74.6011 | 76.2379 | 78.0339 | 81.7213 | 84.371 | 85.8084 | 87.3801 | 88.819 | 91.4191 | 94.6462 | 94.4206 | 94.4206 | 94.4206 | 94.4206 | 94.4206 | 94.4206 | 94.4206 | 94.4206 | 94.4206 | 94.4206 | 94.4206 | 94.4206 | 94.4206 | 94.4206 | 94.4206 | 94.4206 |  | 79.1417 | 237.7413 | 279.2396 | 276.7487 | 276.9246 | 281.1792 | 292.4144 | 299.93 | 307.291 | 315.901 | 323.8752 | 331.6203 | 332.499 | 341.5397 | 334.6752 | 334.6752 | 334.6752 | 334.6752 | 334.6752 | 334.6752 | 334.6752 | 334.6752 | 334.6752 | 334.6752 | 334.6752 | 334.6752 | 334.6752 | 334.6752 | 334.6752 | 334.6752
85% | 2.1831 | 147.3455 | 188.1003 | 186.9134 | 186.8697 | 191.5145 | 196.6114 | 207.0756 | 214.595 | 218.674 | 223.1344 | 227.2178 | 234.5963 | 243.7543 | 243.1142 | 243.1142 | 243.1142 | 243.1142 | 243.1142 | 243.1142 | 243.1142 | 243.1142 | 243.1142 | 243.1142 | 243.1142 | 243.1142 | 243.1142 | 243.1142 | 243.1142 | 243.1142 |  | 50.0275 | 200.0542 | 239.3094 | 236.9532 | 237.1195 | 241.1442 | 251.772 | 258.8814 | 265.8444 | 273.989 | 281.5323 | 288.8587 | 289.6899 | 298.2419 | 291.7484 | 291.7484 | 291.7484 | 291.7484 | 291.7484 | 291.7484 | 291.7484 | 291.7484 | 291.7484 | 291.7484 | 291.7484 | 291.7484 | 291.7484 | 291.7484 | 291.7484 | 291.7484
80% |  | 166.9191 | 223.8464 | 222.1885 | 222.1274 | 228.6154 | 235.7349 | 250.3515 | 260.8548 | 266.5525 | 272.783 | 278.4866 | 288.7932 | 301.5853 | 300.6912 | 300.6912 | 300.6912 | 300.6912 | 300.6912 | 300.6912 | 300.6912 | 300.6912 | 300.6912 | 300.6912 | 300.6912 | 300.6912 | 300.6912 | 300.6912 | 300.6912 | 300.6912 |  | 15.4914 | 120.2719 | 147.6883 | 146.0426 | 146.1588 | 148.9697 | 156.3923 | 161.3576 | 166.2207 | 171.909 | 177.1773 | 182.2941 | 182.8747 | 188.8475 | 184.3124 | 184.3124 | 184.3124 | 184.3124 | 184.3124 | 184.3124 | 184.3124 | 184.3124 | 184.3124 | 184.3124 | 184.3124 | 184.3124 | 184.3124 | 184.3124 | 184.3124 | 184.3124
75% |  | 320.647 | 469.0463 | 464.7244 | 464.5651 | 481.4781 | 500.0374 | 538.1403 | 565.5205 | 580.3733 | 596.615 | 611.4834 | 638.3507 | 671.6975 | 669.3666 | 669.3666 | 669.3666 | 669.3666 | 669.3666 | 669.3666 | 669.3666 | 669.3666 | 669.3666 | 669.3666 | 669.3666 | 669.3666 | 669.3666 | 669.3666 | 669.3666 | 669.3666 |  | 0.97657 | 175.4756 | 224.4096 | 221.4724 | 221.6798 | 226.6968 | 239.945 | 248.8073 | 257.4872 | 267.6399 | 277.043 | 286.1758 | 287.212 | 297.8726 | 289.7781 | 289.7781 | 289.7781 | 289.7781 | 289.7781 | 289.7781 | 289.7781 | 289.7781 | 289.7781 | 289.7781 | 289.7781 | 289.7781 | 289.7781 | 289.7781 | 289.7781 | 289.7781
70% |  | 328.9116 | 585.3005 | 577.8335 | 577.5583 | 606.7787 | 638.8436 | 704.6738 | 751.9784 | 777.6395 | 805.7002 | 831.3883 | 877.8068 | 935.42 | 931.3929 | 931.3929 | 931.3929 | 931.3929 | 931.3929 | 931.3929 | 931.3929 | 931.3929 | 931.3929 | 931.3929 | 931.3929 | 931.3929 | 931.3929 | 931.3929 | 931.3929 | 931.3929 |  |  | 238.4252 | 327.5698 | 322.219 | 322.5968 | 331.7364 | 355.8711 | 372.0158 | 387.8282 | 406.3238 | 423.4537 | 440.0913 | 441.9789 | 461.3997 | 446.6536 | 446.6536 | 446.6536 | 446.6536 | 446.6536 | 446.6536 | 446.6536 | 446.6536 | 446.6536 | 446.6536 | 446.6536 | 446.6536 | 446.6536 | 446.6536 | 446.6536 | 446.6536
65% |  | 199.3768 | 820.987 | 802.2336 | 801.5424 | 874.9301 | 955.4618 | 1120.7959 | 1239.6024 | 1304.0507 | 1374.5258 | 1439.0422 | 1555.6231 | 1700.32 | 1690.2059 | 1690.2059 | 1690.2059 | 1690.2059 | 1690.2059 | 1690.2059 | 1690.2059 | 1690.2059 | 1690.2059 | 1690.2059 | 1690.2059 | 1690.2059 | 1690.2059 | 1690.2059 | 1690.2059 | 1690.2059 |  |  | 182.6144 | 294.7721 | 288.04 | 288.5153 | 300.0144 | 330.3796 | 350.692 | 370.5866 | 393.8569 | 415.4089 | 436.3416 | 438.7165 | 463.1508 | 444.598 | 444.598 | 444.598 | 444.598 | 444.598 | 444.598 | 444.598 | 444.598 | 444.598 | 444.598 | 444.598 | 444.598 | 444.598 | 444.598 | 444.598 | 444.598
60% |  |  | 203.5024 | 187.5582 | 186.9825 | 252.8081 | 335.7847 | 540.3015 | 711.4984 | 805.7041 | 908.7192 | 1003.0243 | 1173.4335 | 1384.9404 | 1370.1564 | 1370.1564 | 1370.1564 | 1370.1564 | 1370.1564 | 1370.1564 | 1370.1564 | 1370.1564 | 1370.1564 | 1370.1564 | 1370.1564 | 1370.1564 | 1370.1564 | 1370.1564 | 1370.1564 | 1370.1564 |  |  | 77.0598 | 248.2313 | 237.6968 | 238.4405 | 256.4344 | 303.9503 | 335.7356 | 366.8668 | 403.2805 | 437.0055 | 469.7612 | 473.4775 | 511.7128 | 482.681 | 482.681 | 482.681 | 482.681 | 482.681 | 482.681 | 482.681 | 482.681 | 482.681 | 482.681 | 482.681 | 482.681 | 482.681 | 482.681 | 482.681 | 482.681
55% | [8 empty] | 3.8903 | 15.7556 | 37.6919 | 65.8304 | 135.7599 | 255.725 | 246.1724 | 246.1724 | 246.1724 | 246.1724 | 246.1724 | 246.1724 | 246.1724 | 246.1724 | 246.1724 | 246.1724 | 246.1724 | 246.1724 | 246.1724 | 246.1724 | 246.1724 | 246.1724 |  |  |  | 63.4905 | 53.6808 | 54.3475 | 71.6739 | 128.262 | 174.6238 | 226.4176 | 294.3956 | 359.2034 | 422.1487 | 429.2901 | 502.7651 | 446.976 | 446.976 | 446.976 | 446.976 | 446.976 | 446.976 | 446.976 | 446.976 | 446.976 | 446.976 | 446.976 | 446.976 | 446.976 | 446.976 | 446.976 | 446.976
50% | [40 empty] | 0.92441 | 14.9076 | 44.2124 | 48.4954 | 103.6497 | 59.9312 | 59.9312 | 59.9312 | 59.9312 | 59.9312 | 59.9312 | 59.9312 | 59.9312 | 59.9312 | 59.9312 | 59.9312 | 59.9312 | 59.9312 | 59.9312 | 59.9312 | 59.9312
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 19.7244 | 1270.1019 | 2622.0083 | 2571.9686 | 2570.1362 | 2769.3877 | 2998.7788 | 3503.8889 | 3894.9777 | 4118.2221 | 4371.3041 | 4611.0446 | 5063.3387 | 5657.8836 | 5615.1586 | 5615.1586 | 5615.1586 | 5615.1586 | 5615.1586 | 5615.1586 | 5615.1586 | 5615.1586 | 5615.1586 | 5615.1586 | 5615.1586 | 5615.1586 | 5615.1586 | 5615.1586 | 5615.1586 | 5615.1586 | E @ R (MWh) | 210.0044 | 1395.1384 | 2014.1441 | 1970.7302 | 1973.7695 | 2048.4946 | 2256.6548 | 2404.4088 | 2555.5088 | 2740.5678 | 2926.9386 | 3123.6769 | 3146.9559 | 3397.5525 | 3205.4359 | 3205.4359 | 3205.4359 | 3205.4359 | 3205.4359 | 3205.4359 | 3205.4359 | 3205.4359 | 3205.4359 | 3205.4359 | 3205.4359 | 3205.4359 | 3205.4359 | 3205.4359 | 3205.4359 | 3205.4359
Option 8 Summer POE50 W E @ R (MWh) N 1 | 13.8071 | 889.0713 | 1835.4058 | 1800.378 | 1799.0954 | 1938.5714 | 2099.1452 | 2452.7222 | 2726.4844 | 2882.7555 | 3059.9129 | 3227.7312 | 3544.3371 | 3960.5185 | 3930.611 | 3930.611 | 3930.611 | 3930.611 | 3930.611 | 3930.611 | 3930.611 | 3930.611 | 3930.611 | 3930.611 | 3930.611 | 3930.611 | 3930.611 | 3930.611 | 3930.611 | 3930.611 | Option 8 Summer POE10 W E @ R (MWh) N 1 | 63.0013 | 418.5415 | 604.2432 | 591.2191 | 592.1308 | 614.5484 | 676.9964 | 721.3226 | 766.6526 | 822.1703 | 878.0816 | 937.1031 | 944.0868 | 1019.2657 | 961.6308 | 961.6308 | 961.6308 | 961.6308 | 961.6308 | 961.6308 | 961.6308 | 961.6308 | 961.6308 | 961.6308 | 961.6308 | 961.6308 | 961.6308 | 961.6308 | 961.6308 | 961.6308

## E@R N-2
Option 1 - Do Nothing / Base Case
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | 66.5813 | 92.3179 | 99.0036 | 100.1408 | 101.0254 | 102.5536 | 106.0346 | 108.362 | 111.3134 | 112.8438 | 114.1881 | 111.6988 | 114.6091 | 119.1862 | 115.707 | 115.707 | 115.707 | 115.707 | 115.707 | 115.707 | 115.707 | 115.707 | 115.707 | 115.707 | 115.707 | 115.707 | 115.707 | 115.707 | 115.707 | 115.707 |  | 71.2634 | 96.6755 | 103.6223 | 104.6946 | 105.3727 | 106.8677 | 110.4032 | 112.3303 | 116.0076 | 127.1923 | 117.9641 | 116.1567 | 118.5887 | 123.9113 | 120.303 | 120.303 | 120.303 | 120.303 | 120.303 | 120.303 | 120.303 | 120.303 | 120.303 | 120.303 | 120.303 | 120.303 | 120.303 | 120.303 | 120.303 | 120.303
98% | 79.0946 | 109.6681 | 117.6103 | 118.9612 | 120.012 | 121.8275 | 125.9627 | 128.7276 | 132.2337 | 134.0516 | 135.6486 | 132.6915 | 136.1487 | 141.586 | 137.453 | 137.453 | 137.453 | 137.453 | 137.453 | 137.453 | 137.453 | 137.453 | 137.453 | 137.453 | 137.453 | 137.453 | 137.453 | 137.453 | 137.453 | 137.453 |  | 84.6567 | 114.8446 | 123.097 | 124.3709 | 125.1764 | 126.9524 | 131.1523 | 133.4417 | 137.8101 | 151.0968 | 140.1342 | 137.9871 | 140.8762 | 147.1992 | 142.9127 | 142.9127 | 142.9127 | 142.9127 | 142.9127 | 142.9127 | 142.9127 | 142.9127 | 142.9127 | 142.9127 | 142.9127 | 142.9127 | 142.9127 | 142.9127 | 142.9127 | 142.9127
97% | 156.5832 | 217.1095 | 232.8326 | 235.507 | 237.5873 | 241.1813 | 249.3678 | 254.8414 | 261.7824 | 265.3814 | 268.543 | 262.6887 | 269.5329 | 280.2972 | 272.115 | 272.115 | 272.115 | 272.115 | 272.115 | 272.115 | 272.115 | 272.115 | 272.115 | 272.115 | 272.115 | 272.115 | 272.115 | 272.115 | 272.115 | 272.115 |  | 167.5944 | 227.3573 | 243.6946 | 246.2165 | 247.8111 | 251.327 | 259.6417 | 264.1739 | 272.822 | 299.1257 | 277.423 | 273.1725 | 278.892 | 291.4096 | 282.9237 | 282.9237 | 282.9237 | 282.9237 | 282.9237 | 282.9237 | 282.9237 | 282.9237 | 282.9237 | 282.9237 | 282.9237 | 282.9237 | 282.9237 | 282.9237 | 282.9237 | 282.9237
95% | 462.5227 | 641.3081 | 687.7517 | 695.6514 | 701.7962 | 712.4124 | 736.5942 | 752.7622 | 773.2648 | 783.8959 | 793.2346 | 775.942 | 796.1588 | 827.9549 | 803.7859 | 803.7859 | 803.7859 | 803.7859 | 803.7859 | 803.7859 | 803.7859 | 803.7859 | 803.7859 | 803.7859 | 803.7859 | 803.7859 | 803.7859 | 803.7859 | 803.7859 | 803.7859 |  | 495.0481 | 671.5786 | 719.8364 | 727.2857 | 731.996 | 742.3814 | 766.9415 | 780.329 | 805.8742 | 883.5714 | 819.4649 | 806.9095 | 823.8041 | 860.7791 | 835.7129 | 835.7129 | 835.7129 | 835.7129 | 835.7129 | 835.7129 | 835.7129 | 835.7129 | 835.7129 | 835.7129 | 835.7129 | 835.7129 | 835.7129 | 835.7129 | 835.7129 | 835.7129
90% | 2550.165 | 3535.9158 | 3791.9875 | 3835.5434 | 3869.4233 | 3927.9564 | 4061.2852 | 4150.4292 | 4263.4726 | 4322.0883 | 4373.5777 | 4278.2333 | 4389.7006 | 4565.012 | 4431.7536 | 4431.7536 | 4431.7536 | 4431.7536 | 4431.7536 | 4431.7536 | 4431.7536 | 4431.7536 | 4431.7536 | 4431.7536 | 4431.7536 | 4431.7536 | 4431.7536 | 4431.7536 | 4431.7536 | 4431.7536 |  | 2729.4971 | 3702.8155 | 3968.8899 | 4009.9623 | 4035.9325 | 4093.1938 | 4228.6083 | 4302.4214 | 4443.2678 | 4871.6587 | 4518.2015 | 4448.976 | 4542.1258 | 4745.9912 | 4607.7865 | 4607.7865 | 4607.7865 | 4607.7865 | 4607.7865 | 4607.7865 | 4607.7865 | 4607.7865 | 4607.7865 | 4607.7865 | 4607.7865 | 4607.7865 | 4607.7865 | 4607.7865 | 4607.7865 | 4607.7865
85% | 6229.8705 | 8637.9889 | 9263.5537 | 9369.9577 | 9452.724 | 9595.7162 | 9921.4289 | 10139.2013 | 10415.3582 | 10558.5521 | 10684.3371 | 10451.4176 | 10723.7241 | 11151.9973 | 10826.4566 | 10826.4566 | 10826.4566 | 10826.4566 | 10826.4566 | 10826.4566 | 10826.4566 | 10826.4566 | 10826.4566 | 10826.4566 | 10826.4566 | 10826.4566 | 10826.4566 | 10826.4566 | 10826.4566 | 10826.4566 |  | 6667.9659 | 9045.7131 | 9695.7136 | 9796.0508 | 9859.4941 | 9999.3792 | 10330.1872 | 10510.5072 | 10854.585 | 11901.1132 | 11037.6427 | 10868.5297 | 11096.0879 | 11594.1165 | 11256.4923 | 11256.4923 | 11256.4923 | 11256.4923 | 11256.4923 | 11256.4923 | 11256.4923 | 11256.4923 | 11256.4923 | 11256.4923 | 11256.4923 | 11256.4923 | 11256.4923 | 11256.4923 | 11256.4923 | 11256.4923
80% | 9683.0656 | 13425.9956 | 14398.3087 | 14563.692 | 14692.3353 | 14914.5876 | 15420.8418 | 15759.3246 | 16188.5543 | 16411.1201 | 16606.6272 | 16244.6013 | 16667.8463 | 17333.5099 | 16827.5231 | 16827.5231 | 16827.5231 | 16827.5231 | 16827.5231 | 16827.5231 | 16827.5231 | 16827.5231 | 16827.5231 | 16827.5231 | 16827.5231 | 16827.5231 | 16827.5231 | 16827.5231 | 16827.5231 | 16827.5231 |  | 10363.9958 | 14059.7198 | 15070.0133 | 15225.967 | 15324.5767 | 15541.9996 | 16056.1734 | 16336.4441 | 16871.243 | 18497.858 | 17155.7689 | 16892.9172 | 17246.6101 | 18020.6942 | 17495.9261 | 17495.9261 | 17495.9261 | 17495.9261 | 17495.9261 | 17495.9261 | 17495.9261 | 17495.9261 | 17495.9261 | 17495.9261 | 17495.9261 | 17495.9261 | 17495.9261 | 17495.9261 | 17495.9261 | 17495.9261
75% | 10683.1238 | 14812.6201 | 15885.3529 | 16067.8168 | 16209.7463 | 16454.9526 | 17013.4923 | 17386.9332 | 17860.4934 | 18106.0455 | 18321.7445 | 17922.3288 | 18389.2862 | 19123.699 | 18565.4543 | 18565.4543 | 18565.4543 | 18565.4543 | 18565.4543 | 18565.4543 | 18565.4543 | 18565.4543 | 18565.4543 | 18565.4543 | 18565.4543 | 18565.4543 | 18565.4543 | 18565.4543 | 18565.4543 | 18565.4543 |  | 11434.3798 | 15511.7948 | 16626.4305 | 16798.4909 | 16907.2849 | 17147.1631 | 17714.4402 | 18023.6571 | 18613.6895 | 20408.2999 | 18927.601 | 18637.6022 | 19027.8242 | 19881.855 | 19302.8894 | 19302.8894 | 19302.8894 | 19302.8894 | 19302.8894 | 19302.8894 | 19302.8894 | 19302.8894 | 19302.8894 | 19302.8894 | 19302.8894 | 19302.8894 | 19302.8894 | 19302.8894 | 19302.8894 | 19302.8894
70% | 11478.4193 | 15915.3323 | 17067.9236 | 17263.9709 | 17416.4662 | 17679.9267 | 18280.0463 | 18681.2877 | 19190.1017 | 19453.9337 | 19685.6902 | 19256.5404 | 19758.26 | 20547.3454 | 19947.5428 | 19947.5428 | 19947.5428 | 19947.5428 | 19947.5428 | 19947.5428 | 19947.5428 | 19947.5428 | 19947.5428 | 19947.5428 | 19947.5428 | 19947.5428 | 19947.5428 | 19947.5428 | 19947.5428 | 19947.5428 |  | 12285.6019 | 16666.5563 | 17864.1701 | 18049.0394 | 18165.9325 | 18423.6682 | 19033.1757 | 19365.4119 | 19999.3688 | 21927.5773 | 20336.6492 | 20025.0617 | 20444.3333 | 21361.9417 | 20739.8755 | 20739.8755 | 20739.8755 | 20739.8755 | 20739.8755 | 20739.8755 | 20739.8755 | 20739.8755 | 20739.8755 | 20739.8755 | 20739.8755 | 20739.8755 | 20739.8755 | 20739.8755 | 20739.8755 | 20739.8755
65% | 12096.053 | 16771.7086 | 17986.3189 | 18192.9151 | 18353.6159 | 18631.2528 | 19263.6638 | 19686.4953 | 20222.6877 | 20500.7161 | 20744.943 | 20292.7014 | 20821.4176 | 21652.9624 | 21020.8854 | 21020.8854 | 21020.8854 | 21020.8854 | 21020.8854 | 21020.8854 | 21020.8854 | 21020.8854 | 21020.8854 | 21020.8854 | 21020.8854 | 21020.8854 | 21020.8854 | 21020.8854 | 21020.8854 | 21020.8854 |  | 12946.6687 | 17563.3547 | 18825.4101 | 19020.2268 | 19143.4097 | 19415.0137 | 20057.3178 | 20407.431 | 21075.5001 | 23107.4621 | 21430.9289 | 21102.5754 | 21544.4074 | 22511.3907 | 21855.8521 | 21855.8521 | 21855.8521 | 21855.8521 | 21855.8521 | 21855.8521 | 21855.8521 | 21855.8521 | 21855.8521 | 21855.8521 | 21855.8521 | 21855.8521 | 21855.8521 | 21855.8521 | 21855.8521 | 21855.8521
60% | 13316.2645 | 18463.5854 | 19800.7217 | 20028.1587 | 20205.0705 | 20510.7145 | 21206.9211 | 21672.4066 | 22262.6883 | 22568.7633 | 22837.627 | 22339.7647 | 22921.8162 | 23837.2445 | 23141.4056 | 23141.4056 | 23141.4056 | 23141.4056 | 23141.4056 | 23141.4056 | 23141.4056 | 23141.4056 | 23141.4056 | 23141.4056 | 23141.4056 | 23141.4056 | 23141.4056 | 23141.4056 | 23141.4056 | 23141.4056 |  | 14252.6876 | 19335.0902 | 20724.4577 | 20938.927 | 21074.5362 | 21373.5387 | 22080.6365 | 22466.068 | 23201.5297 | 25438.4696 | 23592.813 | 23231.3363 | 23717.7389 | 24782.2684 | 24060.6012 | 24060.6012 | 24060.6012 | 24060.6012 | 24060.6012 | 24060.6012 | 24060.6012 | 24060.6012 | 24060.6012 | 24060.6012 | 24060.6012 | 24060.6012 | 24060.6012 | 24060.6012 | 24060.6012 | 24060.6012
55% | 14813.5078 | 20539.579 | 22027.0592 | 22280.0685 | 22476.8718 | 22816.8815 | 23591.3677 | 24109.191 | 24765.8423 | 25106.3315 | 25405.4256 | 24851.585 | 25499.0807 | 26517.4372 | 25743.3602 | 25743.3602 | 25743.3602 | 25743.3602 | 25743.3602 | 25743.3602 | 25743.3602 | 25743.3602 | 25743.3602 | 25743.3602 | 25743.3602 | 25743.3602 | 25743.3602 | 25743.3602 | 25743.3602 | 25743.3602 |  | 15855.2197 | 21509.0734 | 23054.6574 | 23293.241 | 23444.0977 | 23776.7193 | 24563.3211 | 24992.0894 | 25810.2444 | 28298.6996 | 26245.5225 | 25843.4024 | 26384.4947 | 27568.7169 | 26765.9075 | 26765.9075 | 26765.9075 | 26765.9075 | 26765.9075 | 26765.9075 | 26765.9075 | 26765.9075 | 26765.9075 | 26765.9075 | 26765.9075 | 26765.9075 | 26765.9075 | 26765.9075 | 26765.9075 | 26765.9075
50% | 15014.9247 | 20818.8523 | 22326.5575 | 22583.007 | 22782.4862 | 23127.1189 | 23912.1357 | 24436.9997 | 25102.5795 | 25447.6982 | 25750.859 | 25189.488 | 25845.7876 | 26877.9905 | 26093.3885 | 26093.3885 | 26093.3885 | 26093.3885 | 26093.3885 | 26093.3885 | 26093.3885 | 26093.3885 | 26093.3885 | 26093.3885 | 26093.3885 | 26093.3885 | 26093.3885 | 26093.3885 | 26093.3885 | 26093.3885 |  | 16070.8005 | 21801.5288 | 23368.1279 | 23609.9554 | 23762.8633 | 24100.0075 | 24897.3046 | 25331.9028 | 26161.1821 | 28683.4724 | 26602.3787 | 26194.791 | 26743.2404 | 27943.5643 | 27129.8392 | 27129.8392 | 27129.8392 | 27129.8392 | 27129.8392 | 27129.8392 | 27129.8392 | 27129.8392 | 27129.8392 | 27129.8392 | 27129.8392 | 27129.8392 | 27129.8392 | 27129.8392 | 27129.8392 | 27129.8392
45% | 11588.8305 | 16068.4223 | 17232.1005 | 17430.0335 | 17583.9957 | 17849.9904 | 18455.8826 | 18860.9836 | 19374.6918 | 19641.0617 | 19875.0474 | 19441.7696 | 19948.3153 | 20744.9909 | 20139.4188 | 20139.4188 | 20139.4188 | 20139.4188 | 20139.4188 | 20139.4188 | 20139.4188 | 20139.4188 | 20139.4188 | 20139.4188 | 20139.4188 | 20139.4188 | 20139.4188 | 20139.4188 | 20139.4188 | 20139.4188 |  | 12403.7774 | 16826.8724 | 18036.0061 | 18222.6536 | 18340.6711 | 18600.8859 | 19216.2564 | 19551.6884 | 20191.7433 | 22138.4993 | 20532.268 | 20217.6833 | 20640.988 | 21567.4228 | 20939.373 | 20939.373 | 20939.373 | 20939.373 | 20939.373 | 20939.373 | 20939.373 | 20939.373 | 20939.373 | 20939.373 | 20939.373 | 20939.373 | 20939.373 | 20939.373 | 20939.373 | 20939.373
40% | 5693.5395 | 7894.3425 | 8466.0523 | 8563.2959 | 8638.9368 | 8769.6188 | 9067.2909 | 9266.3151 | 9518.6977 | 9649.5639 | 9764.5201 | 9551.6527 | 9800.5162 | 10191.9194 | 9894.4045 | 9894.4045 | 9894.4045 | 9894.4045 | 9894.4045 | 9894.4045 | 9894.4045 | 9894.4045 | 9894.4045 | 9894.4045 | 9894.4045 | 9894.4045 | 9894.4045 | 9894.4045 | 9894.4045 | 9894.4045 |  | 6093.9192 | 8266.9656 | 8861.0075 | 8952.7065 | 9010.688 | 9138.5304 | 9440.8591 | 9605.6552 | 9920.1113 | 10876.5437 | 10087.4095 | 9932.8555 | 10140.8232 | 10595.9764 | 10287.4184 | 10287.4184 | 10287.4184 | 10287.4184 | 10287.4184 | 10287.4184 | 10287.4184 | 10287.4184 | 10287.4184 | 10287.4184 | 10287.4184 | 10287.4184 | 10287.4184 | 10287.4184 | 10287.4184 | 10287.4184
35% | 2127.9257 | 2950.4624 | 3164.1354 | 3200.4796 | 3228.75 | 3277.5916 | 3388.8447 | 3463.2288 | 3557.5552 | 3606.4657 | 3649.4298 | 3569.872 | 3662.8832 | 3809.1677 | 3697.9734 | 3697.9734 | 3697.9734 | 3697.9734 | 3697.9734 | 3697.9734 | 3697.9734 | 3697.9734 | 3697.9734 | 3697.9734 | 3697.9734 | 3697.9734 | 3697.9734 | 3697.9734 | 3697.9734 | 3697.9734 |  | 2277.5652 | 3089.728 | 3311.7475 | 3346.0195 | 3367.6897 | 3415.47 | 3528.4635 | 3590.0551 | 3707.5811 | 4065.0419 | 3770.1078 | 3712.3442 | 3790.0708 | 3960.1816 | 3844.8599 | 3844.8599 | 3844.8599 | 3844.8599 | 3844.8599 | 3844.8599 | 3844.8599 | 3844.8599 | 3844.8599 | 3844.8599 | 3844.8599 | 3844.8599 | 3844.8599 | 3844.8599 | 3844.8599 | 3844.8599
30% | 1061.2862 | 1471.5199 | 1578.0877 | 1596.2141 | 1610.3137 | 1634.673 | 1690.1596 | 1727.2581 | 1774.3027 | 1798.6964 | 1820.1244 | 1780.4456 | 1826.8342 | 1899.7925 | 1844.3351 | 1844.3351 | 1844.3351 | 1844.3351 | 1844.3351 | 1844.3351 | 1844.3351 | 1844.3351 | 1844.3351 | 1844.3351 | 1844.3351 | 1844.3351 | 1844.3351 | 1844.3351 | 1844.3351 | 1844.3351 |  | 1135.9177 | 1540.9775 | 1651.708 | 1668.8009 | 1679.6088 | 1703.4388 | 1759.7934 | 1790.5117 | 1849.1269 | 2027.4077 | 1880.3116 | 1851.5025 | 1890.268 | 1975.1094 | 1917.5936 | 1917.5936 | 1917.5936 | 1917.5936 | 1917.5936 | 1917.5936 | 1917.5936 | 1917.5936 | 1917.5936 | 1917.5936 | 1917.5936 | 1917.5936 | 1917.5936 | 1917.5936 | 1917.5936 | 1917.5936
25% | 625.6637 | 867.5102 | 930.3354 | 941.0215 | 949.3337 | 963.6944 | 996.4056 | 1018.2764 | 1046.0107 | 1060.3916 | 1073.0242 | 1049.6322 | 1076.9798 | 1119.9911 | 1087.2972 | 1087.2972 | 1087.2972 | 1087.2972 | 1087.2972 | 1087.2972 | 1087.2972 | 1087.2972 | 1087.2972 | 1087.2972 | 1087.2972 | 1087.2972 | 1087.2972 | 1087.2972 | 1087.2972 | 1087.2972 |  | 669.6615 | 908.4578 | 973.7371 | 983.8139 | 990.1855 | 1004.2341 | 1037.457 | 1055.5665 | 1090.1221 | 1195.2246 | 1108.5065 | 1091.5226 | 1114.3762 | 1164.393 | 1130.4855 | 1130.4855 | 1130.4855 | 1130.4855 | 1130.4855 | 1130.4855 | 1130.4855 | 1130.4855 | 1130.4855 | 1130.4855 | 1130.4855 | 1130.4855 | 1130.4855 | 1130.4855 | 1130.4855 | 1130.4855
20% | 316.1776 | 438.3942 | 470.1428 | 475.543 | 479.7435 | 487.0006 | 503.5312 | 514.5835 | 528.599 | 535.8664 | 542.2502 | 530.4291 | 544.2492 | 565.9848 | 549.463 | 549.463 | 549.463 | 549.463 | 549.463 | 549.463 | 549.463 | 549.463 | 549.463 | 549.463 | 549.463 | 549.463 | 549.463 | 549.463 | 549.463 | 549.463 |  | 338.4118 | 459.0869 | 492.0757 | 497.168 | 500.3879 | 507.4873 | 524.2764 | 533.428 | 550.8906 | 604.0039 | 560.1811 | 551.5983 | 563.1473 | 588.4232 | 571.2881 | 571.2881 | 571.2881 | 571.2881 | 571.2881 | 571.2881 | 571.2881 | 571.2881 | 571.2881 | 571.2881 | 571.2881 | 571.2881 | 571.2881 | 571.2881 | 571.2881 | 571.2881
15% | 128.8131 | 178.605 | 191.5396 | 193.7397 | 195.4511 | 198.4077 | 205.1423 | 209.6451 | 215.3552 | 218.3159 | 220.9167 | 216.1007 | 221.7311 | 230.5864 | 223.8553 | 223.8553 | 223.8553 | 223.8553 | 223.8553 | 223.8553 | 223.8553 | 223.8553 | 223.8553 | 223.8553 | 223.8553 | 223.8553 | 223.8553 | 223.8553 | 223.8553 | 223.8553 |  | 137.8715 | 187.0354 | 200.4753 | 202.5499 | 203.8617 | 206.7541 | 213.5941 | 217.3225 | 224.4369 | 246.0756 | 228.2219 | 224.7252 | 229.4304 | 239.728 | 232.747 | 232.747 | 232.747 | 232.747 | 232.747 | 232.747 | 232.747 | 232.747 | 232.747 | 232.747 | 232.747 | 232.747 | 232.747 | 232.747 | 232.747 | 232.747
10% | 51.8598 | 71.9059 | 77.1134 | 77.9991 | 78.6881 | 79.8784 | 82.5898 | 84.4026 | 86.7014 | 87.8934 | 88.9405 | 87.0016 | 89.2684 | 92.8335 | 90.1236 | 90.1236 | 90.1236 | 90.1236 | 90.1236 | 90.1236 | 90.1236 | 90.1236 | 90.1236 | 90.1236 | 90.1236 | 90.1236 | 90.1236 | 90.1236 | 90.1236 | 90.1236 |  | 55.5067 | 75.3 | 80.7108 | 81.5461 | 82.0742 | 83.2387 | 85.9924 | 87.4935 | 90.3577 | 99.0694 | 91.8816 | 90.4738 | 92.3681 | 96.5139 | 93.7033 | 93.7033 | 93.7033 | 93.7033 | 93.7033 | 93.7033 | 93.7033 | 93.7033 | 93.7033 | 93.7033 | 93.7033 | 93.7033 | 93.7033 | 93.7033 | 93.7033 | 93.7033
5% | 44.1645 | 61.236 | 65.6707 | 66.425 | 67.0118 | 68.0255 | 70.3345 | 71.8783 | 73.8361 | 74.8512 | 75.7429 | 74.0917 | 76.0221 | 79.0582 | 76.7504 | 76.7504 | 76.7504 | 76.7504 | 76.7504 | 76.7504 | 76.7504 | 76.7504 | 76.7504 | 76.7504 | 76.7504 | 76.7504 | 76.7504 | 76.7504 | 76.7504 | 76.7504 |  | 47.2702 | 64.1264 | 68.7344 | 69.4457 | 69.8954 | 70.8871 | 73.2323 | 74.5106 | 76.9498 | 84.3688 | 78.2475 | 77.0487 | 78.6618 | 82.1924 | 79.799 | 79.799 | 79.799 | 79.799 | 79.799 | 79.799 | 79.799 | 79.799 | 79.799 | 79.799 | 79.799 | 79.799 | 79.799 | 79.799 | 79.799 | 79.799
9.992e-14% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E @ R (MWh) | 118268.4368 | 163984.3799 | 175860.1598 | 177880.1417 | 179451.3847 | 182165.962 | 188349.3233 | 192483.5334 | 197726.1221 | 200444.5279 | 202832.442 | 198410.6765 | 203580.168 | 211710.5473 | 205530.4523 | 205530.4523 | 205530.4523 | 205530.4523 | 205530.4523 | 205530.4523 | 205530.4523 | 205530.4523 | 205530.4523 | 205530.4523 | 205530.4523 | 205530.4523 | 205530.4523 | 205530.4523 | 205530.4523 | 205530.4523 | E @ R (MWh) | 126585.2808 | 171724.6525 | 184064.3234 | 185969.1325 | 187173.5461 | 189829.1378 | 196109.2281 | 199532.4392 | 206064.4443 | 225931.832 | 209539.6283 | 206329.172 | 210649.1573 | 220103.7788 | 213694.29 | 213694.29 | 213694.29 | 213694.29 | 213694.29 | 213694.29 | 213694.29 | 213694.29 | 213694.29 | 213694.29 | 213694.29 | 213694.29 | 213694.29 | 213694.29 | 213694.29 | 213694.29
Option 1 Winter POE50 W E @ R (MWh) N 2 | 82787.9057 | 114789.066 | 123102.1118 | 124516.0992 | 125615.9693 | 127516.1734 | 131844.5263 | 134738.4734 | 138408.2855 | 140311.1695 | 141982.7094 | 138887.4736 | 142506.1176 | 148197.3831 | 143871.3166 | 143871.3166 | 143871.3166 | 143871.3166 | 143871.3166 | 143871.3166 | 143871.3166 | 143871.3166 | 143871.3166 | 143871.3166 | 143871.3166 | 143871.3166 | 143871.3166 | 143871.3166 | 143871.3166 | 143871.3166 | Option 1 Winter POE10 W E @ R (MWh) N 2 | 37975.5842 | 51517.3957 | 55219.297 | 55790.7397 | 56152.0638 | 56948.7413 | 58832.7684 | 59859.7318 | 61819.3333 | 67779.5496 | 62861.8885 | 61898.7516 | 63194.7472 | 66031.1336 | 64108.287 | 64108.287 | 64108.287 | 64108.287 | 64108.287 | 64108.287 | 64108.287 | 64108.287 | 64108.287 | 64108.287 | 64108.287 | 64108.287 | 64108.287 | 64108.287 | 64108.287 | 64108.287
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 85.8327 | 111.1071 | 117.7202 | 117.3233 | 117.3513 | 118.0293 | 119.8198 | 121.0174 | 122.1905 | 123.5626 | 124.8333 | 126.0676 | 126.2076 | 127.6483 | 126.5544 | 126.5544 | 126.5544 | 126.5544 | 126.5544 | 126.5544 | 126.5544 | 126.5544 | 126.5544 | 126.5544 | 126.5544 | 126.5544 | 126.5544 | 126.5544 | 126.5544 | 126.5544
98% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 42.4851 | 54.9952 | 58.2686 | 58.0721 | 58.0859 | 58.4216 | 59.3078 | 59.9006 | 60.4812 | 61.1604 | 61.7894 | 62.4003 | 62.4696 | 63.1827 | 62.6413 | 62.6413 | 62.6413 | 62.6413 | 62.6413 | 62.6413 | 62.6413 | 62.6413 | 62.6413 | 62.6413 | 62.6413 | 62.6413 | 62.6413 | 62.6413 | 62.6413 | 62.6413
97% | 18.864 | 25.0432 | 26.7251 | 26.6761 | 26.6743 | 26.866 | 27.0764 | 27.5082 | 27.8185 | 27.9869 | 28.171 | 28.3395 | 28.644 | 29.0219 | 28.9955 | 28.9955 | 28.9955 | 28.9955 | 28.9955 | 28.9955 | 28.9955 | 28.9955 | 28.9955 | 28.9955 | 28.9955 | 28.9955 | 28.9955 | 28.9955 | 28.9955 | 28.9955 |  | 84.1075 | 108.8738 | 115.354 | 114.965 | 114.9925 | 115.6569 | 117.4113 | 118.5849 | 119.7344 | 121.0789 | 122.3241 | 123.5336 | 123.6708 | 125.0825 | 124.0106 | 124.0106 | 124.0106 | 124.0106 | 124.0106 | 124.0106 | 124.0106 | 124.0106 | 124.0106 | 124.0106 | 124.0106 | 124.0106 | 124.0106 | 124.0106 | 124.0106 | 124.0106
95% | 92.8689 | 123.2894 | 131.5698 | 131.3286 | 131.3197 | 132.2634 | 133.299 | 135.4251 | 136.9528 | 137.7816 | 138.6878 | 139.5174 | 141.0166 | 142.8772 | 142.7472 | 142.7472 | 142.7472 | 142.7472 | 142.7472 | 142.7472 | 142.7472 | 142.7472 | 142.7472 | 142.7472 | 142.7472 | 142.7472 | 142.7472 | 142.7472 | 142.7472 | 142.7472 |  | 124.2203 | 160.7982 | 170.369 | 169.7945 | 169.8351 | 170.8163 | 173.4075 | 175.1408 | 176.8385 | 178.8242 | 180.6633 | 182.4496 | 182.6522 | 184.7373 | 183.1541 | 183.1541 | 183.1541 | 183.1541 | 183.1541 | 183.1541 | 183.1541 | 183.1541 | 183.1541 | 183.1541 | 183.1541 | 183.1541 | 183.1541 | 183.1541 | 183.1541 | 183.1541
90% | 161.0694 | 213.8301 | 228.1913 | 227.7731 | 227.7577 | 229.3944 | 231.1905 | 234.8778 | 237.5275 | 238.9649 | 240.5367 | 241.9755 | 244.5756 | 247.8027 | 247.5772 | 247.5772 | 247.5772 | 247.5772 | 247.5772 | 247.5772 | 247.5772 | 247.5772 | 247.5772 | 247.5772 | 247.5772 | 247.5772 | 247.5772 | 247.5772 | 247.5772 | 247.5772 |  | 538.6113 | 697.2109 | 738.7092 | 736.2183 | 736.3942 | 740.6488 | 751.884 | 759.3996 | 766.7606 | 775.3706 | 783.3448 | 791.0899 | 791.9686 | 801.0093 | 794.1448 | 794.1448 | 794.1448 | 794.1448 | 794.1448 | 794.1448 | 794.1448 | 794.1448 | 794.1448 | 794.1448 | 794.1448 | 794.1448 | 794.1448 | 794.1448 | 794.1448 | 794.1448
85% | 457.0889 | 606.8151 | 647.57 | 646.383 | 646.3393 | 650.9841 | 656.081 | 666.5452 | 674.0646 | 678.1436 | 682.6041 | 686.6874 | 694.0659 | 703.2239 | 702.5838 | 702.5838 | 702.5838 | 702.5838 | 702.5838 | 702.5838 | 702.5838 | 702.5838 | 702.5838 | 702.5838 | 702.5838 | 702.5838 | 702.5838 | 702.5838 | 702.5838 | 702.5838 |  | 509.4971 | 659.5238 | 698.779 | 696.4228 | 696.5891 | 700.6138 | 711.2416 | 718.351 | 725.3141 | 733.4587 | 741.0019 | 748.3283 | 749.1595 | 757.7115 | 751.218 | 751.218 | 751.218 | 751.218 | 751.218 | 751.218 | 751.218 | 751.218 | 751.218 | 751.218 | 751.218 | 751.218 | 751.218 | 751.218 | 751.218 | 751.218
80% | 638.4734 | 847.6148 | 904.5422 | 902.8842 | 902.8231 | 909.3111 | 916.4306 | 931.0473 | 941.5505 | 947.2482 | 953.4787 | 959.1824 | 969.4889 | 982.2811 | 981.3869 | 981.3869 | 981.3869 | 981.3869 | 981.3869 | 981.3869 | 981.3869 | 981.3869 | 981.3869 | 981.3869 | 981.3869 | 981.3869 | 981.3869 | 981.3869 | 981.3869 | 981.3869 |  | 355.8393 | 460.6198 | 488.0361 | 486.3905 | 486.5067 | 489.3176 | 496.7402 | 501.7054 | 506.5685 | 512.2568 | 517.5251 | 522.642 | 523.2225 | 529.1954 | 524.6602 | 524.6602 | 524.6602 | 524.6602 | 524.6602 | 524.6602 | 524.6602 | 524.6602 | 524.6602 | 524.6602 | 524.6602 | 524.6602 | 524.6602 | 524.6602 | 524.6602 | 524.6602
75% | 1664.3841 | 2209.5776 | 2357.9769 | 2353.655 | 2353.4957 | 2370.4087 | 2388.968 | 2427.0709 | 2454.4511 | 2469.3039 | 2485.5456 | 2500.414 | 2527.2813 | 2560.6281 | 2558.2972 | 2558.2972 | 2558.2972 | 2558.2972 | 2558.2972 | 2558.2972 | 2558.2972 | 2558.2972 | 2558.2972 | 2558.2972 | 2558.2972 | 2558.2972 | 2558.2972 | 2558.2972 | 2558.2972 | 2558.2972 |  | 635.1192 | 822.1366 | 871.0705 | 868.1333 | 868.3407 | 873.3577 | 886.6059 | 895.4682 | 904.1481 | 914.3008 | 923.7039 | 932.8368 | 933.8729 | 944.5335 | 936.439 | 936.439 | 936.439 | 936.439 | 936.439 | 936.439 | 936.439 | 936.439 | 936.439 | 936.439 | 936.439 | 936.439 | 936.439 | 936.439 | 936.439 | 936.439
70% | 2875.5487 | 3817.4772 | 4073.866 | 4066.399 | 4066.1238 | 4095.3442 | 4127.4091 | 4193.2394 | 4240.5439 | 4266.205 | 4294.2657 | 4319.9539 | 4366.3723 | 4423.9855 | 4419.9585 | 4419.9585 | 4419.9585 | 4419.9585 | 4419.9585 | 4419.9585 | 4419.9585 | 4419.9585 | 4419.9585 | 4419.9585 | 4419.9585 | 4419.9585 | 4419.9585 | 4419.9585 | 4419.9585 | 4419.9585 |  | 1157.0168 | 1497.7123 | 1586.8569 | 1581.5061 | 1581.8839 | 1591.0234 | 1615.1582 | 1631.3028 | 1647.1153 | 1665.6109 | 1682.7407 | 1699.3783 | 1701.266 | 1720.6867 | 1705.9407 | 1705.9407 | 1705.9407 | 1705.9407 | 1705.9407 | 1705.9407 | 1705.9407 | 1705.9407 | 1705.9407 | 1705.9407 | 1705.9407 | 1705.9407 | 1705.9407 | 1705.9407 | 1705.9407 | 1705.9407
65% | 7222.0048 | 9587.679 | 10231.6052 | 10212.8518 | 10212.1606 | 10285.5483 | 10366.0801 | 10531.4141 | 10650.2206 | 10714.6689 | 10785.1441 | 10849.6604 | 10966.2413 | 11110.9382 | 11100.8242 | 11100.8242 | 11100.8242 | 11100.8242 | 11100.8242 | 11100.8242 | 11100.8242 | 11100.8242 | 11100.8242 | 11100.8242 | 11100.8242 | 11100.8242 | 11100.8242 | 11100.8242 | 11100.8242 | 11100.8242 |  | 1455.7061 | 1884.3537 | 1996.5114 | 1989.7793 | 1990.2546 | 2001.7536 | 2032.1189 | 2052.4313 | 2072.3259 | 2095.5961 | 2117.1482 | 2138.0809 | 2140.4558 | 2164.8901 | 2146.3373 | 2146.3373 | 2146.3373 | 2146.3373 | 2146.3373 | 2146.3373 | 2146.3373 | 2146.3373 | 2146.3373 | 2146.3373 | 2146.3373 | 2146.3373 | 2146.3373 | 2146.3373 | 2146.3373 | 2146.3373
60% | 10556.5772 | 14014.5398 | 14955.7822 | 14928.3698 | 14927.3596 | 15034.6321 | 15152.3473 | 15394.0201 | 15567.6823 | 15661.888 | 15764.9032 | 15859.2082 | 16029.6174 | 16241.1243 | 16226.3403 | 16226.3403 | 16226.3403 | 16226.3403 | 16226.3403 | 16226.3403 | 16226.3403 | 16226.3403 | 16226.3403 | 16226.3403 | 16226.3403 | 16226.3403 | 16226.3403 | 16226.3403 | 16226.3403 | 16226.3403 |  | 2277.9105 | 2948.6646 | 3124.1707 | 3113.6361 | 3114.3799 | 3132.3737 | 3179.8897 | 3211.675 | 3242.8062 | 3279.2199 | 3312.9449 | 3345.7006 | 3349.4169 | 3387.6521 | 3358.6203 | 3358.6203 | 3358.6203 | 3358.6203 | 3358.6203 | 3358.6203 | 3358.6203 | 3358.6203 | 3358.6203 | 3358.6203 | 3358.6203 | 3358.6203 | 3358.6203 | 3358.6203 | 3358.6203 | 3358.6203
55% | 11937.0341 | 15847.1857 | 16911.512 | 16880.515 | 16879.3726 | 17000.6729 | 17133.7814 | 17407.0571 | 17603.4287 | 17709.9534 | 17826.4396 | 17933.0767 | 18125.7699 | 18364.935 | 18348.2178 | 18348.2178 | 18348.2178 | 18348.2178 | 18348.2178 | 18348.2178 | 18348.2178 | 18348.2178 | 18348.2178 | 18348.2178 | 18348.2178 | 18348.2178 | 18348.2178 | 18348.2178 | 18348.2178 | 18348.2178 |  | 4377.3623 | 5666.3214 | 6003.5838 | 5983.3401 | 5984.7694 | 6019.3473 | 6110.6567 | 6171.737 | 6231.5606 | 6301.5352 | 6366.343 | 6429.2884 | 6436.4298 | 6509.9048 | 6454.1156 | 6454.1156 | 6454.1156 | 6454.1156 | 6454.1156 | 6454.1156 | 6454.1156 | 6454.1156 | 6454.1156 | 6454.1156 | 6454.1156 | 6454.1156 | 6454.1156 | 6454.1156 | 6454.1156 | 6454.1156
50% | 15327.7148 | 20348.5339 | 21715.179 | 21675.3774 | 21673.9105 | 21829.6658 | 22000.5834 | 22351.4823 | 22603.6327 | 22740.4155 | 22889.9893 | 23026.9163 | 23274.3434 | 23581.4427 | 23559.977 | 23559.977 | 23559.977 | 23559.977 | 23559.977 | 23559.977 | 23559.977 | 23559.977 | 23559.977 | 23559.977 | 23559.977 | 23559.977 | 23559.977 | 23559.977 | 23559.977 | 23559.977 |  | 9714.4123 | 12574.9205 | 13323.3863 | 13278.4606 | 13281.6325 | 13358.3693 | 13561.0066 | 13696.5584 | 13829.3213 | 13984.6116 | 14128.4356 | 14268.1263 | 14283.9748 | 14447.0334 | 14323.224 | 14323.224 | 14323.224 | 14323.224 | 14323.224 | 14323.224 | 14323.224 | 14323.224 | 14323.224 | 14323.224 | 14323.224 | 14323.224 | 14323.224 | 14323.224 | 14323.224 | 14323.224
45% | 20411.3174 | 27097.3455 | 28917.2533 | 28864.251 | 28862.2976 | 29069.7109 | 29297.3152 | 29764.5935 | 30100.3723 | 30282.5206 | 30481.7021 | 30664.0425 | 30993.5314 | 31402.4836 | 31373.8985 | 31373.8985 | 31373.8985 | 31373.8985 | 31373.8985 | 31373.8985 | 31373.8985 | 31373.8985 | 31373.8985 | 31373.8985 | 31373.8985 | 31373.8985 | 31373.8985 | 31373.8985 | 31373.8985 | 31373.8985 |  | 14720.4239 | 19055.0036 | 20189.1672 | 20121.0905 | 20125.8971 | 20242.1776 | 20549.2377 | 20754.6417 | 20955.8197 | 21191.1339 | 21409.073 | 21620.7489 | 21644.7644 | 21891.85 | 21704.2393 | 21704.2393 | 21704.2393 | 21704.2393 | 21704.2393 | 21704.2393 | 21704.2393 | 21704.2393 | 21704.2393 | 21704.2393 | 21704.2393 | 21704.2393 | 21704.2393 | 21704.2393 | 21704.2393 | 21704.2393
40% | 14315.8312 | 19005.1929 | 20281.6168 | 20244.4427 | 20243.0727 | 20388.5455 | 20548.1797 | 20875.9135 | 21111.4178 | 21239.1706 | 21378.87 | 21506.7576 | 21737.8504 | 22024.6761 | 22004.6275 | 22004.6275 | 22004.6275 | 22004.6275 | 22004.6275 | 22004.6275 | 22004.6275 | 22004.6275 | 22004.6275 | 22004.6275 | 22004.6275 | 22004.6275 | 22004.6275 | 22004.6275 | 22004.6275 | 22004.6275 |  | 15242.3215 | 19730.5793 | 20904.9535 | 20834.4632 | 20839.4402 | 20959.8434 | 21277.7899 | 21490.4763 | 21698.7869 | 21942.444 | 22168.1098 | 22387.2904 | 22412.1574 | 22668.0032 | 22473.741 | 22473.741 | 22473.741 | 22473.741 | 22473.741 | 22473.741 | 22473.741 | 22473.741 | 22473.741 | 22473.741 | 22473.741 | 22473.741 | 22473.741 | 22473.741 | 22473.741 | 22473.741
35% | 7422.2532 | 9853.5218 | 10515.3025 | 10496.0291 | 10495.3188 | 10570.7413 | 10653.506 | 10823.4244 | 10945.5251 | 11011.7604 | 11084.1896 | 11150.4949 | 11270.3083 | 11419.0173 | 11408.6228 | 11408.6228 | 11408.6228 | 11408.6228 | 11408.6228 | 11408.6228 | 11408.6228 | 11408.6228 | 11408.6228 | 11408.6228 | 11408.6228 | 11408.6228 | 11408.6228 | 11408.6228 | 11408.6228 | 11408.6228 |  | 20759.9869 | 26872.9779 | 28472.4713 | 28376.4638 | 28383.2424 | 28547.2311 | 28980.2731 | 29269.9512 | 29553.6695 | 29885.5295 | 30192.8856 | 30491.4088 | 30525.2776 | 30873.7386 | 30609.1541 | 30609.1541 | 30609.1541 | 30609.1541 | 30609.1541 | 30609.1541 | 30609.1541 | 30609.1541 | 30609.1541 | 30609.1541 | 30609.1541 | 30609.1541 | 30609.1541 | 30609.1541 | 30609.1541 | 30609.1541
30% | 3452.1096 | 4582.899 | 4890.695 | 4881.7308 | 4881.4005 | 4916.4797 | 4954.9738 | 5034.0033 | 5090.7926 | 5121.5988 | 5155.2859 | 5186.1246 | 5241.8501 | 5311.0151 | 5306.1806 | 5306.1806 | 5306.1806 | 5306.1806 | 5306.1806 | 5306.1806 | 5306.1806 | 5306.1806 | 5306.1806 | 5306.1806 | 5306.1806 | 5306.1806 | 5306.1806 | 5306.1806 | 5306.1806 | 5306.1806 |  | 19183.5111 | 24832.2926 | 26310.3234 | 26221.6065 | 26227.8703 | 26379.406 | 26779.5636 | 27047.2441 | 27309.4173 | 27616.0765 | 27900.0925 | 28175.9464 | 28207.2432 | 28529.2428 | 28284.7504 | 28284.7504 | 28284.7504 | 28284.7504 | 28284.7504 | 28284.7504 | 28284.7504 | 28284.7504 | 28284.7504 | 28284.7504 | 28284.7504 | 28284.7504 | 28284.7504 | 28284.7504 | 28284.7504 | 28284.7504
25% | 2357.031 | 3129.1112 | 3339.2681 | 3333.1476 | 3332.922 | 3356.8734 | 3383.1564 | 3437.1161 | 3475.8908 | 3496.9246 | 3519.9255 | 3540.9815 | 3579.0298 | 3626.2542 | 3622.9533 | 3622.9533 | 3622.9533 | 3622.9533 | 3622.9533 | 3622.9533 | 3622.9533 | 3622.9533 | 3622.9533 | 3622.9533 | 3622.9533 | 3622.9533 | 3622.9533 | 3622.9533 | 3622.9533 | 3622.9533 |  | 5533.3008 | 7162.6379 | 7588.9618 | 7563.3722 | 7565.179 | 7608.888 | 7724.3096 | 7801.5195 | 7877.1409 | 7965.5938 | 8047.5155 | 8127.0829 | 8136.1102 | 8228.9879 | 8158.4664 | 8158.4664 | 8158.4664 | 8158.4664 | 8158.4664 | 8158.4664 | 8158.4664 | 8158.4664 | 8158.4664 | 8158.4664 | 8158.4664 | 8158.4664 | 8158.4664 | 8158.4664 | 8158.4664 | 8158.4664
20% | 1427.8587 | 1895.5749 | 2022.8852 | 2019.1774 | 2019.0408 | 2033.5502 | 2049.4721 | 2082.1602 | 2105.6494 | 2118.3914 | 2132.325 | 2145.0805 | 2168.1297 | 2196.7376 | 2194.738 | 2194.738 | 2194.738 | 2194.738 | 2194.738 | 2194.738 | 2194.738 | 2194.738 | 2194.738 | 2194.738 | 2194.738 | 2194.738 | 2194.738 | 2194.738 | 2194.738 | 2194.738 |  | 1484.8203 | 1922.0408 | 2036.4417 | 2029.5749 | 2030.0597 | 2041.7887 | 2072.7613 | 2093.48 | 2113.7724 | 2137.5081 | 2159.4912 | 2180.8425 | 2183.2649 | 2208.1879 | 2189.264 | 2189.264 | 2189.264 | 2189.264 | 2189.264 | 2189.264 | 2189.264 | 2189.264 | 2189.264 | 2189.264 | 2189.264 | 2189.264 | 2189.264 | 2189.264 | 2189.264 | 2189.264
15% | 914.1778 | 1213.6303 | 1295.1399 | 1292.766 | 1292.6786 | 1301.9681 | 1312.162 | 1333.0904 | 1348.1292 | 1356.2872 | 1365.2081 | 1373.3747 | 1388.1318 | 1406.4479 | 1405.1676 | 1405.1676 | 1405.1676 | 1405.1676 | 1405.1676 | 1405.1676 | 1405.1676 | 1405.1676 | 1405.1676 | 1405.1676 | 1405.1676 | 1405.1676 | 1405.1676 | 1405.1676 | 1405.1676 | 1405.1676 |  | 818.9695 | 1060.1234 | 1123.2225 | 1119.4351 | 1119.7025 | 1126.1718 | 1143.255 | 1154.6827 | 1165.8752 | 1178.9669 | 1191.0919 | 1202.8685 | 1204.2046 | 1217.9511 | 1207.5134 | 1207.5134 | 1207.5134 | 1207.5134 | 1207.5134 | 1207.5134 | 1207.5134 | 1207.5134 | 1207.5134 | 1207.5134 | 1207.5134 | 1207.5134 | 1207.5134 | 1207.5134 | 1207.5134 | 1207.5134
10% | 611.8703 | 812.2975 | 866.8529 | 865.264 | 865.2055 | 871.4231 | 878.246 | 892.2536 | 902.3193 | 907.7795 | 913.7504 | 919.2164 | 929.0935 | 941.3527 | 940.4958 | 940.4958 | 940.4958 | 940.4958 | 940.4958 | 940.4958 | 940.4958 | 940.4958 | 940.4958 | 940.4958 | 940.4958 | 940.4958 | 940.4958 | 940.4958 | 940.4958 | 940.4958 |  | 191.3984 | 247.7576 | 262.5043 | 261.6191 | 261.6816 | 263.1935 | 267.186 | 269.8567 | 272.4725 | 275.5321 | 278.3658 | 281.118 | 281.4303 | 284.643 | 282.2036 | 282.2036 | 282.2036 | 282.2036 | 282.2036 | 282.2036 | 282.2036 | 282.2036 | 282.2036 | 282.2036 | 282.2036 | 282.2036 | 282.2036 | 282.2036 | 282.2036 | 282.2036
5% | 435.3228 | 577.9192 | 616.7333 | 615.6029 | 615.5612 | 619.9848 | 624.8391 | 634.805 | 641.9663 | 645.8511 | 650.0991 | 653.988 | 661.0151 | 669.7371 | 669.1274 | 669.1274 | 669.1274 | 669.1274 | 669.1274 | 669.1274 | 669.1274 | 669.1274 | 669.1274 | 669.1274 | 669.1274 | 669.1274 | 669.1274 | 669.1274 | 669.1274 | 669.1274 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9.992e-14% | 38.2117 | 50.7285 | 54.1355 | 54.0363 | 54.0326 | 54.4209 | 54.847 | 55.7218 | 56.3504 | 56.6914 | 57.0643 | 57.4056 | 58.0224 | 58.788 | 58.7345 | 58.7345 | 58.7345 | 58.7345 | 58.7345 | 58.7345 | 58.7345 | 58.7345 | 58.7345 | 58.7345 | 58.7345 | 58.7345 | 58.7345 | 58.7345 | 58.7345 | 58.7345 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E @ R (MWh) | 102337.6118 | 135859.8063 | 144984.402 | 144718.661 | 144708.8672 | 145748.789 | 146889.9441 | 149232.7692 | 150916.2863 | 151829.5355 | 152828.1856 | 153742.3981 | 155394.3791 | 157444.7704 | 157301.4516 | 157301.4516 | 157301.4516 | 157301.4516 | 157301.4516 | 157301.4516 | 157301.4516 | 157301.4516 | 157301.4516 | 157301.4516 | 157301.4516 | 157301.4516 | 157301.4516 | 157301.4516 | 157301.4516 | 157301.4516 | E @ R (MWh) | 99292.8528 | 128530.651 | 136180.8614 | 135721.6674 | 135754.0887 | 136538.4294 | 138609.6244 | 139995.1247 | 141352.1196 | 142939.3714 | 144409.4236 | 145837.2289 | 145999.2196 | 147665.8725 | 146400.3925 | 146400.3925 | 146400.3925 | 146400.3925 | 146400.3925 | 146400.3925 | 146400.3925 | 146400.3925 | 146400.3925 | 146400.3925 | 146400.3925 | 146400.3925 | 146400.3925 | 146400.3925 | 146400.3925 | 146400.3925
Option 1 Summer POE50 W E @ R (MWh) N 2 | 71636.3283 | 95101.8644 | 101489.0814 | 101303.0627 | 101296.207 | 102024.1523 | 102822.9609 | 104462.9384 | 105641.4004 | 106280.6749 | 106979.7299 | 107619.6787 | 108776.0654 | 110211.3393 | 110111.0161 | 110111.0161 | 110111.0161 | 110111.0161 | 110111.0161 | 110111.0161 | 110111.0161 | 110111.0161 | 110111.0161 | 110111.0161 | 110111.0161 | 110111.0161 | 110111.0161 | 110111.0161 | 110111.0161 | 110111.0161 | Option 1 Summer POE10 W E @ R (MWh) N 2 | 29787.8558 | 38559.1953 | 40854.2584 | 40716.5002 | 40726.2266 | 40961.5288 | 41582.8873 | 41998.5374 | 42405.6359 | 42881.8114 | 43322.8271 | 43751.1687 | 43799.7659 | 44299.7618 | 43920.1178 | 43920.1178 | 43920.1178 | 43920.1178 | 43920.1178 | 43920.1178 | 43920.1178 | 43920.1178 | 43920.1178 | 43920.1178 | 43920.1178 | 43920.1178 | 43920.1178 | 43920.1178 | 43920.1178 | 43920.1178
Option 2 - 1B New PHS ZSS + Three new feeders
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | 66.5813 | 92.3179 | 99.0036 | 71.5552 | 72.4398 | 73.968 | 77.4491 | 79.7765 | 82.7279 | 84.2583 | 85.6026 | 83.1133 | 86.0235 | 90.6007 | 87.1215 | 87.1215 | 87.1215 | 87.1215 | 87.1215 | 87.1215 | 87.1215 | 87.1215 | 87.1215 | 87.1215 | 87.1215 | 87.1215 | 87.1215 | 87.1215 | 87.1215 | 87.1215 |  | 71.2634 | 96.6755 | 103.6223 | 76.1091 | 76.7871 | 78.2821 | 81.8176 | 83.7448 | 87.4221 | 98.6068 | 89.3785 | 87.5711 | 90.0031 | 95.3258 | 91.7175 | 91.7175 | 91.7175 | 91.7175 | 91.7175 | 91.7175 | 91.7175 | 91.7175 | 91.7175 | 91.7175 | 91.7175 | 91.7175 | 91.7175 | 91.7175 | 91.7175 | 91.7175
98% | 79.0946 | 109.6681 | 117.6103 | 85.0033 | 86.0541 | 87.8696 | 92.0048 | 94.7697 | 98.2758 | 100.0937 | 101.6907 | 98.7336 | 102.1908 | 107.6281 | 103.4951 | 103.4951 | 103.4951 | 103.4951 | 103.4951 | 103.4951 | 103.4951 | 103.4951 | 103.4951 | 103.4951 | 103.4951 | 103.4951 | 103.4951 | 103.4951 | 103.4951 | 103.4951 |  | 84.6567 | 114.8446 | 123.097 | 90.413 | 91.2185 | 92.9945 | 97.1944 | 99.4838 | 103.8522 | 117.1389 | 106.1763 | 104.0292 | 106.9183 | 113.2413 | 108.9548 | 108.9548 | 108.9548 | 108.9548 | 108.9548 | 108.9548 | 108.9548 | 108.9548 | 108.9548 | 108.9548 | 108.9548 | 108.9548 | 108.9548 | 108.9548 | 108.9548 | 108.9548
97% | 156.5832 | 217.1095 | 232.8326 | 168.2807 | 170.361 | 173.955 | 182.1415 | 187.6151 | 194.5561 | 198.1551 | 201.3166 | 195.4624 | 202.3066 | 213.0709 | 204.8887 | 204.8887 | 204.8887 | 204.8887 | 204.8887 | 204.8887 | 204.8887 | 204.8887 | 204.8887 | 204.8887 | 204.8887 | 204.8887 | 204.8887 | 204.8887 | 204.8887 | 204.8887 |  | 167.5944 | 227.3573 | 243.6946 | 178.9902 | 180.5848 | 184.1007 | 192.4153 | 196.9476 | 205.5957 | 231.8994 | 210.1967 | 205.9462 | 211.6657 | 224.1833 | 215.6973 | 215.6973 | 215.6973 | 215.6973 | 215.6973 | 215.6973 | 215.6973 | 215.6973 | 215.6973 | 215.6973 | 215.6973 | 215.6973 | 215.6973 | 215.6973 | 215.6973 | 215.6973
95% | 462.5227 | 641.3081 | 687.7517 | 497.0752 | 503.22 | 513.8362 | 538.018 | 554.186 | 574.6887 | 585.3198 | 594.6584 | 577.3658 | 597.5826 | 629.3788 | 605.2097 | 605.2097 | 605.2097 | 605.2097 | 605.2097 | 605.2097 | 605.2097 | 605.2097 | 605.2097 | 605.2097 | 605.2097 | 605.2097 | 605.2097 | 605.2097 | 605.2097 | 605.2097 |  | 495.0481 | 671.5786 | 719.8364 | 528.7096 | 533.4198 | 543.8052 | 568.3653 | 581.7528 | 607.2981 | 684.9952 | 620.8888 | 608.3334 | 625.2279 | 662.2029 | 637.1368 | 637.1368 | 637.1368 | 637.1368 | 637.1368 | 637.1368 | 637.1368 | 637.1368 | 637.1368 | 637.1368 | 637.1368 | 637.1368 | 637.1368 | 637.1368 | 637.1368 | 637.1368
90% | 2550.165 | 3535.9158 | 3791.9875 | 2740.6738 | 2774.5538 | 2833.0869 | 2966.4157 | 3055.5597 | 3168.6031 | 3227.2188 | 3278.7082 | 3183.3638 | 3294.8311 | 3470.1425 | 3336.8841 | 3336.8841 | 3336.8841 | 3336.8841 | 3336.8841 | 3336.8841 | 3336.8841 | 3336.8841 | 3336.8841 | 3336.8841 | 3336.8841 | 3336.8841 | 3336.8841 | 3336.8841 | 3336.8841 | 3336.8841 |  | 2729.4971 | 3702.8155 | 3968.8899 | 2915.0928 | 2941.063 | 2998.3243 | 3133.7388 | 3207.5519 | 3348.3983 | 3776.7892 | 3423.332 | 3354.1065 | 3447.2563 | 3651.1217 | 3512.917 | 3512.917 | 3512.917 | 3512.917 | 3512.917 | 3512.917 | 3512.917 | 3512.917 | 3512.917 | 3512.917 | 3512.917 | 3512.917 | 3512.917 | 3512.917 | 3512.917 | 3512.917
85% | 6229.8705 | 8637.9889 | 9263.5537 | 6695.2699 | 6778.0362 | 6921.0284 | 7246.7412 | 7464.5135 | 7740.6704 | 7883.8643 | 8009.6493 | 7776.7298 | 8049.0363 | 8477.3095 | 8151.7688 | 8151.7688 | 8151.7688 | 8151.7688 | 8151.7688 | 8151.7688 | 8151.7688 | 8151.7688 | 8151.7688 | 8151.7688 | 8151.7688 | 8151.7688 | 8151.7688 | 8151.7688 | 8151.7688 | 8151.7688 |  | 6667.9659 | 9045.7131 | 9695.7136 | 7121.363 | 7184.8063 | 7324.6914 | 7655.4994 | 7835.8194 | 8179.8972 | 9226.4254 | 8362.9549 | 8193.8419 | 8421.4001 | 8919.4287 | 8581.8045 | 8581.8045 | 8581.8045 | 8581.8045 | 8581.8045 | 8581.8045 | 8581.8045 | 8581.8045 | 8581.8045 | 8581.8045 | 8581.8045 | 8581.8045 | 8581.8045 | 8581.8045 | 8581.8045 | 8581.8045
80% | 9683.0656 | 13425.9956 | 14398.3087 | 10406.4342 | 10535.0776 | 10757.3299 | 11263.5841 | 11602.0669 | 12031.2966 | 12253.8623 | 12449.3695 | 12087.3435 | 12510.5886 | 13176.2522 | 12670.2654 | 12670.2654 | 12670.2654 | 12670.2654 | 12670.2654 | 12670.2654 | 12670.2654 | 12670.2654 | 12670.2654 | 12670.2654 | 12670.2654 | 12670.2654 | 12670.2654 | 12670.2654 | 12670.2654 | 12670.2654 |  | 10363.9958 | 14059.7198 | 15070.0133 | 11068.7092 | 11167.3189 | 11384.7419 | 11898.9156 | 12179.1863 | 12713.9853 | 14340.6003 | 12998.5112 | 12735.6595 | 13089.3523 | 13863.4365 | 13338.6684 | 13338.6684 | 13338.6684 | 13338.6684 | 13338.6684 | 13338.6684 | 13338.6684 | 13338.6684 | 13338.6684 | 13338.6684 | 13338.6684 | 13338.6684 | 13338.6684 | 13338.6684 | 13338.6684 | 13338.6684
75% | 10683.1238 | 14812.6201 | 15885.3529 | 11481.2012 | 11623.1308 | 11868.3371 | 12426.8767 | 12800.3177 | 13273.8779 | 13519.43 | 13735.129 | 13335.7133 | 13802.6707 | 14537.0834 | 13978.8388 | 13978.8388 | 13978.8388 | 13978.8388 | 13978.8388 | 13978.8388 | 13978.8388 | 13978.8388 | 13978.8388 | 13978.8388 | 13978.8388 | 13978.8388 | 13978.8388 | 13978.8388 | 13978.8388 | 13978.8388 |  | 11434.3798 | 15511.7948 | 16626.4305 | 12211.8754 | 12320.6694 | 12560.5476 | 13127.8247 | 13437.0415 | 14027.074 | 15821.6844 | 14340.9855 | 14050.9867 | 14441.2087 | 15295.2395 | 14716.2738 | 14716.2738 | 14716.2738 | 14716.2738 | 14716.2738 | 14716.2738 | 14716.2738 | 14716.2738 | 14716.2738 | 14716.2738 | 14716.2738 | 14716.2738 | 14716.2738 | 14716.2738 | 14716.2738 | 14716.2738
70% | 11478.4193 | 15915.3323 | 17067.9236 | 12335.9089 | 12488.4042 | 12751.8647 | 13351.9844 | 13753.2258 | 14262.0397 | 14525.8718 | 14757.6283 | 14328.4785 | 14830.198 | 15619.2835 | 15019.4808 | 15019.4808 | 15019.4808 | 15019.4808 | 15019.4808 | 15019.4808 | 15019.4808 | 15019.4808 | 15019.4808 | 15019.4808 | 15019.4808 | 15019.4808 | 15019.4808 | 15019.4808 | 15019.4808 | 15019.4808 |  | 12285.6019 | 16666.5563 | 17864.1701 | 13120.9774 | 13237.8705 | 13495.6062 | 14105.1138 | 14437.35 | 15071.3069 | 16999.5154 | 15408.5872 | 15096.9997 | 15516.2714 | 16433.8798 | 15811.8136 | 15811.8136 | 15811.8136 | 15811.8136 | 15811.8136 | 15811.8136 | 15811.8136 | 15811.8136 | 15811.8136 | 15811.8136 | 15811.8136 | 15811.8136 | 15811.8136 | 15811.8136 | 15811.8136 | 15811.8136
65% | 12096.053 | 16771.7086 | 17986.3189 | 12999.6827 | 13160.3836 | 13438.0204 | 14070.4314 | 14493.2629 | 15029.4553 | 15307.4837 | 15551.7106 | 15099.469 | 15628.1852 | 16459.73 | 15827.653 | 15827.653 | 15827.653 | 15827.653 | 15827.653 | 15827.653 | 15827.653 | 15827.653 | 15827.653 | 15827.653 | 15827.653 | 15827.653 | 15827.653 | 15827.653 | 15827.653 | 15827.653 |  | 12946.6687 | 17563.3547 | 18825.4101 | 13826.9944 | 13950.1773 | 14221.7813 | 14864.0854 | 15214.1986 | 15882.2677 | 17914.2297 | 16237.6965 | 15909.343 | 16351.175 | 17318.1583 | 16662.6197 | 16662.6197 | 16662.6197 | 16662.6197 | 16662.6197 | 16662.6197 | 16662.6197 | 16662.6197 | 16662.6197 | 16662.6197 | 16662.6197 | 16662.6197 | 16662.6197 | 16662.6197 | 16662.6197 | 16662.6197
60% | 13316.2645 | 18463.5854 | 19800.7217 | 14311.0495 | 14487.9613 | 14793.6052 | 15489.8119 | 15955.2974 | 16545.5791 | 16851.6541 | 17120.5178 | 16622.6555 | 17204.707 | 18120.1353 | 17424.2964 | 17424.2964 | 17424.2964 | 17424.2964 | 17424.2964 | 17424.2964 | 17424.2964 | 17424.2964 | 17424.2964 | 17424.2964 | 17424.2964 | 17424.2964 | 17424.2964 | 17424.2964 | 17424.2964 | 17424.2964 |  | 14252.6876 | 19335.0902 | 20724.4577 | 15221.8178 | 15357.427 | 15656.4295 | 16363.5272 | 16748.9588 | 17484.4205 | 19721.3604 | 17875.7038 | 17514.2271 | 18000.6296 | 19065.1592 | 18343.492 | 18343.492 | 18343.492 | 18343.492 | 18343.492 | 18343.492 | 18343.492 | 18343.492 | 18343.492 | 18343.492 | 18343.492 | 18343.492 | 18343.492 | 18343.492 | 18343.492 | 18343.492
55% | 14813.5078 | 20539.579 | 22027.0592 | 15920.1436 | 16116.9469 | 16456.9566 | 17231.4428 | 17749.2661 | 18405.9174 | 18746.4066 | 19045.5007 | 18491.6601 | 19139.1558 | 20157.5124 | 19383.4353 | 19383.4353 | 19383.4353 | 19383.4353 | 19383.4353 | 19383.4353 | 19383.4353 | 19383.4353 | 19383.4353 | 19383.4353 | 19383.4353 | 19383.4353 | 19383.4353 | 19383.4353 | 19383.4353 | 19383.4353 |  | 15855.2197 | 21509.0734 | 23054.6574 | 16933.3161 | 17084.1728 | 17416.7944 | 18203.3962 | 18632.1646 | 19450.3195 | 21938.7747 | 19885.5977 | 19483.4775 | 20024.5698 | 21208.792 | 20405.9826 | 20405.9826 | 20405.9826 | 20405.9826 | 20405.9826 | 20405.9826 | 20405.9826 | 20405.9826 | 20405.9826 | 20405.9826 | 20405.9826 | 20405.9826 | 20405.9826 | 20405.9826 | 20405.9826 | 20405.9826
50% | 15014.9247 | 20818.8523 | 22326.5575 | 16136.6072 | 16336.0864 | 16680.7192 | 17465.7359 | 17990.6 | 18656.1797 | 19001.2985 | 19304.4593 | 18743.0882 | 19399.3878 | 20431.5908 | 19646.9887 | 19646.9887 | 19646.9887 | 19646.9887 | 19646.9887 | 19646.9887 | 19646.9887 | 19646.9887 | 19646.9887 | 19646.9887 | 19646.9887 | 19646.9887 | 19646.9887 | 19646.9887 | 19646.9887 | 19646.9887 |  | 16070.8005 | 21801.5288 | 23368.1279 | 17163.5557 | 17316.4636 | 17653.6077 | 18450.9048 | 18885.5031 | 19714.7824 | 22237.0727 | 20155.9789 | 19748.3912 | 20296.8406 | 21497.1645 | 20683.4394 | 20683.4394 | 20683.4394 | 20683.4394 | 20683.4394 | 20683.4394 | 20683.4394 | 20683.4394 | 20683.4394 | 20683.4394 | 20683.4394 | 20683.4394 | 20683.4394 | 20683.4394 | 20683.4394 | 20683.4394
45% | 11588.8305 | 16068.4223 | 17232.1005 | 12454.5684 | 12608.5306 | 12874.5253 | 13480.4175 | 13885.5185 | 14399.2267 | 14665.5965 | 14899.5823 | 14466.3045 | 14972.8501 | 15769.5258 | 15163.9536 | 15163.9536 | 15163.9536 | 15163.9536 | 15163.9536 | 15163.9536 | 15163.9536 | 15163.9536 | 15163.9536 | 15163.9536 | 15163.9536 | 15163.9536 | 15163.9536 | 15163.9536 | 15163.9536 | 15163.9536 |  | 12403.7774 | 16826.8724 | 18036.0061 | 13247.1885 | 13365.206 | 13625.4208 | 14240.7913 | 14576.2232 | 15216.2782 | 17163.0342 | 15556.8029 | 15242.2182 | 15665.5228 | 16591.9577 | 15963.9078 | 15963.9078 | 15963.9078 | 15963.9078 | 15963.9078 | 15963.9078 | 15963.9078 | 15963.9078 | 15963.9078 | 15963.9078 | 15963.9078 | 15963.9078 | 15963.9078 | 15963.9078 | 15963.9078 | 15963.9078
40% | 5693.5395 | 7894.3425 | 8466.0523 | 6118.8726 | 6194.5135 | 6325.1955 | 6622.8676 | 6821.8918 | 7074.2744 | 7205.1406 | 7320.0968 | 7107.2294 | 7356.0929 | 7747.4961 | 7449.9812 | 7449.9812 | 7449.9812 | 7449.9812 | 7449.9812 | 7449.9812 | 7449.9812 | 7449.9812 | 7449.9812 | 7449.9812 | 7449.9812 | 7449.9812 | 7449.9812 | 7449.9812 | 7449.9812 | 7449.9812 |  | 6093.9192 | 8266.9656 | 8861.0075 | 6508.2832 | 6566.2647 | 6694.1071 | 6996.4358 | 7161.2319 | 7475.688 | 8432.1204 | 7642.9862 | 7488.4322 | 7696.3999 | 8151.5531 | 7842.9951 | 7842.9951 | 7842.9951 | 7842.9951 | 7842.9951 | 7842.9951 | 7842.9951 | 7842.9951 | 7842.9951 | 7842.9951 | 7842.9951 | 7842.9951 | 7842.9951 | 7842.9951 | 7842.9951 | 7842.9951
35% | 2127.9257 | 2950.4624 | 3164.1354 | 2286.8913 | 2315.1617 | 2364.0033 | 2475.2564 | 2549.6405 | 2643.9669 | 2692.8774 | 2735.8415 | 2656.2836 | 2749.2949 | 2895.5794 | 2784.3851 | 2784.3851 | 2784.3851 | 2784.3851 | 2784.3851 | 2784.3851 | 2784.3851 | 2784.3851 | 2784.3851 | 2784.3851 | 2784.3851 | 2784.3851 | 2784.3851 | 2784.3851 | 2784.3851 | 2784.3851 |  | 2277.5652 | 3089.728 | 3311.7475 | 2432.4312 | 2454.1014 | 2501.8817 | 2614.8752 | 2676.4668 | 2793.9928 | 3151.4536 | 2856.5195 | 2798.7559 | 2876.4825 | 3046.5933 | 2931.2716 | 2931.2716 | 2931.2716 | 2931.2716 | 2931.2716 | 2931.2716 | 2931.2716 | 2931.2716 | 2931.2716 | 2931.2716 | 2931.2716 | 2931.2716 | 2931.2716 | 2931.2716 | 2931.2716 | 2931.2716
30% | 1061.2862 | 1471.5199 | 1578.0877 | 1140.5691 | 1154.6687 | 1179.028 | 1234.5147 | 1271.6131 | 1318.6577 | 1343.0514 | 1364.4795 | 1324.8006 | 1371.1892 | 1444.1475 | 1388.6902 | 1388.6902 | 1388.6902 | 1388.6902 | 1388.6902 | 1388.6902 | 1388.6902 | 1388.6902 | 1388.6902 | 1388.6902 | 1388.6902 | 1388.6902 | 1388.6902 | 1388.6902 | 1388.6902 | 1388.6902 |  | 1135.9177 | 1540.9775 | 1651.708 | 1213.1559 | 1223.9638 | 1247.7938 | 1304.1485 | 1334.8668 | 1393.482 | 1571.7627 | 1424.6666 | 1395.8575 | 1434.623 | 1519.4644 | 1461.9487 | 1461.9487 | 1461.9487 | 1461.9487 | 1461.9487 | 1461.9487 | 1461.9487 | 1461.9487 | 1461.9487 | 1461.9487 | 1461.9487 | 1461.9487 | 1461.9487 | 1461.9487 | 1461.9487 | 1461.9487
25% | 625.6637 | 867.5102 | 930.3354 | 672.4036 | 680.7158 | 695.0764 | 727.7876 | 749.6584 | 777.3928 | 791.7737 | 804.4062 | 781.0142 | 808.3619 | 851.3732 | 818.6793 | 818.6793 | 818.6793 | 818.6793 | 818.6793 | 818.6793 | 818.6793 | 818.6793 | 818.6793 | 818.6793 | 818.6793 | 818.6793 | 818.6793 | 818.6793 | 818.6793 | 818.6793 |  | 669.6615 | 908.4578 | 973.7371 | 715.196 | 721.5675 | 735.6162 | 768.8391 | 786.9486 | 821.5042 | 926.6066 | 839.8886 | 822.9046 | 845.7582 | 895.7751 | 861.8676 | 861.8676 | 861.8676 | 861.8676 | 861.8676 | 861.8676 | 861.8676 | 861.8676 | 861.8676 | 861.8676 | 861.8676 | 861.8676 | 861.8676 | 861.8676 | 861.8676 | 861.8676
20% | 316.1776 | 438.3942 | 470.1428 | 339.7975 | 343.9981 | 351.2552 | 367.7857 | 378.8381 | 392.8536 | 400.1209 | 406.5048 | 394.6837 | 408.5037 | 430.2394 | 413.7176 | 413.7176 | 413.7176 | 413.7176 | 413.7176 | 413.7176 | 413.7176 | 413.7176 | 413.7176 | 413.7176 | 413.7176 | 413.7176 | 413.7176 | 413.7176 | 413.7176 | 413.7176 |  | 338.4118 | 459.0869 | 492.0757 | 361.4226 | 364.6424 | 371.7419 | 388.531 | 397.6826 | 415.1452 | 468.2584 | 424.4357 | 415.8529 | 427.4019 | 452.6778 | 435.5427 | 435.5427 | 435.5427 | 435.5427 | 435.5427 | 435.5427 | 435.5427 | 435.5427 | 435.5427 | 435.5427 | 435.5427 | 435.5427 | 435.5427 | 435.5427 | 435.5427 | 435.5427
15% | 128.8131 | 178.605 | 191.5396 | 138.436 | 140.1474 | 143.104 | 149.8386 | 154.3414 | 160.0515 | 163.0122 | 165.613 | 160.797 | 166.4274 | 175.2827 | 168.5516 | 168.5516 | 168.5516 | 168.5516 | 168.5516 | 168.5516 | 168.5516 | 168.5516 | 168.5516 | 168.5516 | 168.5516 | 168.5516 | 168.5516 | 168.5516 | 168.5516 | 168.5516 |  | 137.8715 | 187.0354 | 200.4753 | 147.2462 | 148.558 | 151.4504 | 158.2904 | 162.0188 | 169.1332 | 190.772 | 172.9182 | 169.4215 | 174.1267 | 184.4243 | 177.4433 | 177.4433 | 177.4433 | 177.4433 | 177.4433 | 177.4433 | 177.4433 | 177.4433 | 177.4433 | 177.4433 | 177.4433 | 177.4433 | 177.4433 | 177.4433 | 177.4433 | 177.4433
10% | 51.8598 | 71.9059 | 77.1134 | 55.734 | 56.423 | 57.6133 | 60.3246 | 62.1375 | 64.4363 | 65.6283 | 66.6754 | 64.7365 | 67.0033 | 70.5684 | 67.8584 | 67.8584 | 67.8584 | 67.8584 | 67.8584 | 67.8584 | 67.8584 | 67.8584 | 67.8584 | 67.8584 | 67.8584 | 67.8584 | 67.8584 | 67.8584 | 67.8584 | 67.8584 |  | 55.5067 | 75.3 | 80.7108 | 59.2809 | 59.8091 | 60.9735 | 63.7273 | 65.2284 | 68.0926 | 76.8043 | 69.6164 | 68.2087 | 70.103 | 74.2487 | 71.4382 | 71.4382 | 71.4382 | 71.4382 | 71.4382 | 71.4382 | 71.4382 | 71.4382 | 71.4382 | 71.4382 | 71.4382 | 71.4382 | 71.4382 | 71.4382 | 71.4382 | 71.4382
5% | 44.1645 | 61.236 | 65.6707 | 47.4638 | 48.0505 | 49.0642 | 51.3732 | 52.9171 | 54.8748 | 55.8899 | 56.7816 | 55.1304 | 57.0608 | 60.0969 | 57.7891 | 57.7891 | 57.7891 | 57.7891 | 57.7891 | 57.7891 | 57.7891 | 57.7891 | 57.7891 | 57.7891 | 57.7891 | 57.7891 | 57.7891 | 57.7891 | 57.7891 | 57.7891 |  | 47.2702 | 64.1264 | 68.7344 | 50.4844 | 50.9342 | 51.9258 | 54.271 | 55.5493 | 57.9885 | 65.4075 | 59.2863 | 58.0874 | 59.7006 | 63.2312 | 60.8377 | 60.8377 | 60.8377 | 60.8377 | 60.8377 | 60.8377 | 60.8377 | 60.8377 | 60.8377 | 60.8377 | 60.8377 | 60.8377 | 60.8377 | 60.8377 | 60.8377 | 60.8377
9.992e-14% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E @ R (MWh) | 118268.4368 | 163984.3799 | 175860.1598 | 127103.6219 | 128674.8648 | 131389.4422 | 137572.8034 | 141707.0136 | 146949.6023 | 149668.008 | 152055.9222 | 147634.1566 | 152803.6482 | 160934.0275 | 154753.9325 | 154753.9325 | 154753.9325 | 154753.9325 | 154753.9325 | 154753.9325 | 154753.9325 | 154753.9325 | 154753.9325 | 154753.9325 | 154753.9325 | 154753.9325 | 154753.9325 | 154753.9325 | 154753.9325 | 154753.9325 | E @ R (MWh) | 126585.2808 | 171724.6525 | 184064.3234 | 135192.6126 | 136397.0263 | 139052.6179 | 145332.7083 | 148755.9194 | 155287.9244 | 175155.3121 | 158763.1085 | 155552.6521 | 159872.6374 | 169327.2589 | 162917.7702 | 162917.7702 | 162917.7702 | 162917.7702 | 162917.7702 | 162917.7702 | 162917.7702 | 162917.7702 | 162917.7702 | 162917.7702 | 162917.7702 | 162917.7702 | 162917.7702 | 162917.7702 | 162917.7702 | 162917.7702
Option 2 Winter POE50 W E @ R (MWh) N 2 | 82787.9057 | 114789.066 | 123102.1118 | 88972.5353 | 90072.4054 | 91972.6095 | 96300.9624 | 99194.9095 | 102864.7216 | 104767.6056 | 106439.1455 | 103343.9097 | 106962.5537 | 112653.8192 | 108327.7527 | 108327.7527 | 108327.7527 | 108327.7527 | 108327.7527 | 108327.7527 | 108327.7527 | 108327.7527 | 108327.7527 | 108327.7527 | 108327.7527 | 108327.7527 | 108327.7527 | 108327.7527 | 108327.7527 | 108327.7527 | Option 2 Winter POE10 W E @ R (MWh) N 2 | 37975.5842 | 51517.3957 | 55219.297 | 40557.7838 | 40919.1079 | 41715.7854 | 43599.8125 | 44626.7758 | 46586.3773 | 52546.5936 | 47628.9325 | 46665.7956 | 47961.7912 | 50798.1777 | 48875.331 | 48875.331 | 48875.331 | 48875.331 | 48875.331 | 48875.331 | 48875.331 | 48875.331 | 48875.331 | 48875.331 | 48875.331 | 48875.331 | 48875.331 | 48875.331 | 48875.331 | 48875.331
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 85.8327 | 111.1071 | 117.7202 | 88.2248 | 88.2528 | 88.9308 | 90.7213 | 91.919 | 93.092 | 94.4641 | 95.7348 | 96.9691 | 97.1091 | 98.5499 | 97.4559 | 97.4559 | 97.4559 | 97.4559 | 97.4559 | 97.4559 | 97.4559 | 97.4559 | 97.4559 | 97.4559 | 97.4559 | 97.4559 | 97.4559 | 97.4559 | 97.4559 | 97.4559
98% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 42.4851 | 54.9952 | 58.2686 | 43.6691 | 43.6829 | 44.0185 | 44.9047 | 45.4976 | 46.0782 | 46.7573 | 47.3863 | 47.9973 | 48.0666 | 48.7797 | 48.2382 | 48.2382 | 48.2382 | 48.2382 | 48.2382 | 48.2382 | 48.2382 | 48.2382 | 48.2382 | 48.2382 | 48.2382 | 48.2382 | 48.2382 | 48.2382 | 48.2382 | 48.2382
97% | 18.864 | 25.0432 | 26.7251 | 19.5477 | 19.5459 | 19.7376 | 19.948 | 20.3798 | 20.6901 | 20.8585 | 21.0426 | 21.2111 | 21.5156 | 21.8935 | 21.8671 | 21.8671 | 21.8671 | 21.8671 | 21.8671 | 21.8671 | 21.8671 | 21.8671 | 21.8671 | 21.8671 | 21.8671 | 21.8671 | 21.8671 | 21.8671 | 21.8671 | 21.8671 |  | 84.1075 | 108.8738 | 115.354 | 86.4514 | 86.4789 | 87.1433 | 88.8977 | 90.0713 | 91.2208 | 92.5653 | 93.8105 | 95.02 | 95.1572 | 96.569 | 95.497 | 95.497 | 95.497 | 95.497 | 95.497 | 95.497 | 95.497 | 95.497 | 95.497 | 95.497 | 95.497 | 95.497 | 95.497 | 95.497 | 95.497 | 95.497
95% | 92.8689 | 123.2894 | 131.5698 | 96.235 | 96.2261 | 97.1698 | 98.2054 | 100.3314 | 101.8592 | 102.6879 | 103.5942 | 104.4238 | 105.9229 | 107.7836 | 107.6535 | 107.6535 | 107.6535 | 107.6535 | 107.6535 | 107.6535 | 107.6535 | 107.6535 | 107.6535 | 107.6535 | 107.6535 | 107.6535 | 107.6535 | 107.6535 | 107.6535 | 107.6535 |  | 124.2203 | 160.7982 | 170.369 | 127.6821 | 127.7227 | 128.7039 | 131.2951 | 133.0284 | 134.7261 | 136.7118 | 138.5509 | 140.3372 | 140.5399 | 142.6249 | 141.0417 | 141.0417 | 141.0417 | 141.0417 | 141.0417 | 141.0417 | 141.0417 | 141.0417 | 141.0417 | 141.0417 | 141.0417 | 141.0417 | 141.0417 | 141.0417 | 141.0417 | 141.0417
90% | 161.0694 | 213.8301 | 228.1913 | 166.9075 | 166.8921 | 168.5288 | 170.3249 | 174.0123 | 176.662 | 178.0993 | 179.6711 | 181.11 | 183.7101 | 186.9372 | 186.7116 | 186.7116 | 186.7116 | 186.7116 | 186.7116 | 186.7116 | 186.7116 | 186.7116 | 186.7116 | 186.7116 | 186.7116 | 186.7116 | 186.7116 | 186.7116 | 186.7116 | 186.7116 |  | 538.6113 | 697.2109 | 738.7092 | 553.6217 | 553.7976 | 558.0522 | 569.2874 | 576.803 | 584.1639 | 592.7739 | 600.7482 | 608.4933 | 609.372 | 618.4127 | 611.5482 | 611.5482 | 611.5482 | 611.5482 | 611.5482 | 611.5482 | 611.5482 | 611.5482 | 611.5482 | 611.5482 | 611.5482 | 611.5482 | 611.5482 | 611.5482 | 611.5482 | 611.5482
85% | 457.0889 | 606.8151 | 647.57 | 473.6565 | 473.6127 | 478.2575 | 483.3545 | 493.8187 | 501.3381 | 505.4171 | 509.8775 | 513.9608 | 521.3394 | 530.4974 | 529.8573 | 529.8573 | 529.8573 | 529.8573 | 529.8573 | 529.8573 | 529.8573 | 529.8573 | 529.8573 | 529.8573 | 529.8573 | 529.8573 | 529.8573 | 529.8573 | 529.8573 | 529.8573 |  | 509.4971 | 659.5238 | 698.779 | 523.6962 | 523.8626 | 527.8872 | 538.5151 | 545.6244 | 552.5875 | 560.7321 | 568.2753 | 575.6018 | 576.433 | 584.985 | 578.4915 | 578.4915 | 578.4915 | 578.4915 | 578.4915 | 578.4915 | 578.4915 | 578.4915 | 578.4915 | 578.4915 | 578.4915 | 578.4915 | 578.4915 | 578.4915 | 578.4915 | 578.4915
80% | 638.4734 | 847.6148 | 904.5422 | 661.6154 | 661.5543 | 668.0423 | 675.1618 | 689.7784 | 700.2817 | 705.9794 | 712.2099 | 717.9135 | 728.2201 | 741.0122 | 740.1181 | 740.1181 | 740.1181 | 740.1181 | 740.1181 | 740.1181 | 740.1181 | 740.1181 | 740.1181 | 740.1181 | 740.1181 | 740.1181 | 740.1181 | 740.1181 | 740.1181 | 740.1181 |  | 355.8393 | 460.6198 | 488.0361 | 365.7561 | 365.8723 | 368.6831 | 376.1058 | 381.071 | 385.9341 | 391.6224 | 396.8907 | 402.0076 | 402.5881 | 408.561 | 404.0258 | 404.0258 | 404.0258 | 404.0258 | 404.0258 | 404.0258 | 404.0258 | 404.0258 | 404.0258 | 404.0258 | 404.0258 | 404.0258 | 404.0258 | 404.0258 | 404.0258 | 404.0258
75% | 1664.3841 | 2209.5776 | 2357.9769 | 1724.7111 | 1724.5518 | 1741.4647 | 1760.0241 | 1798.127 | 1825.5071 | 1840.3599 | 1856.6016 | 1871.4701 | 1898.3373 | 1931.6842 | 1929.3533 | 1929.3533 | 1929.3533 | 1929.3533 | 1929.3533 | 1929.3533 | 1929.3533 | 1929.3533 | 1929.3533 | 1929.3533 | 1929.3533 | 1929.3533 | 1929.3533 | 1929.3533 | 1929.3533 | 1929.3533 |  | 635.1192 | 822.1366 | 871.0705 | 652.8192 | 653.0266 | 658.0436 | 671.2918 | 680.154 | 688.834 | 698.9867 | 708.3898 | 717.5226 | 718.5588 | 729.2194 | 721.1249 | 721.1249 | 721.1249 | 721.1249 | 721.1249 | 721.1249 | 721.1249 | 721.1249 | 721.1249 | 721.1249 | 721.1249 | 721.1249 | 721.1249 | 721.1249 | 721.1249 | 721.1249
70% | 2875.5487 | 3817.4772 | 4073.866 | 2979.7755 | 2979.5003 | 3008.7207 | 3040.7856 | 3106.6158 | 3153.9204 | 3179.5814 | 3207.6422 | 3233.3303 | 3279.7487 | 3337.362 | 3333.3349 | 3333.3349 | 3333.3349 | 3333.3349 | 3333.3349 | 3333.3349 | 3333.3349 | 3333.3349 | 3333.3349 | 3333.3349 | 3333.3349 | 3333.3349 | 3333.3349 | 3333.3349 | 3333.3349 | 3333.3349 |  | 1157.0168 | 1497.7123 | 1586.8569 | 1189.2615 | 1189.6393 | 1198.7788 | 1222.9136 | 1239.0582 | 1254.8707 | 1273.3663 | 1290.4961 | 1307.1337 | 1309.0214 | 1328.4421 | 1313.696 | 1313.696 | 1313.696 | 1313.696 | 1313.696 | 1313.696 | 1313.696 | 1313.696 | 1313.696 | 1313.696 | 1313.696 | 1313.696 | 1313.696 | 1313.696 | 1313.696 | 1313.696
65% | 7222.0048 | 9587.679 | 10231.6052 | 7483.7725 | 7483.0813 | 7556.469 | 7637.0008 | 7802.3349 | 7921.1413 | 7985.5897 | 8056.0648 | 8120.5811 | 8237.162 | 8381.8589 | 8371.7449 | 8371.7449 | 8371.7449 | 8371.7449 | 8371.7449 | 8371.7449 | 8371.7449 | 8371.7449 | 8371.7449 | 8371.7449 | 8371.7449 | 8371.7449 | 8371.7449 | 8371.7449 | 8371.7449 | 8371.7449 |  | 1455.7061 | 1884.3537 | 1996.5114 | 1496.2749 | 1496.7502 | 1508.2492 | 1538.6145 | 1558.9269 | 1578.8215 | 1602.0918 | 1623.6438 | 1644.5765 | 1646.9514 | 1671.3857 | 1652.8329 | 1652.8329 | 1652.8329 | 1652.8329 | 1652.8329 | 1652.8329 | 1652.8329 | 1652.8329 | 1652.8329 | 1652.8329 | 1652.8329 | 1652.8329 | 1652.8329 | 1652.8329 | 1652.8329 | 1652.8329
60% | 10556.5772 | 14014.5398 | 14955.7822 | 10939.2093 | 10938.1991 | 11045.4716 | 11163.1868 | 11404.8596 | 11578.5218 | 11672.7275 | 11775.7427 | 11870.0477 | 12040.4569 | 12251.9638 | 12237.1798 | 12237.1798 | 12237.1798 | 12237.1798 | 12237.1798 | 12237.1798 | 12237.1798 | 12237.1798 | 12237.1798 | 12237.1798 | 12237.1798 | 12237.1798 | 12237.1798 | 12237.1798 | 12237.1798 | 12237.1798 |  | 2277.9105 | 2948.6646 | 3124.1707 | 2341.3932 | 2342.1369 | 2360.1308 | 2407.6467 | 2439.432 | 2470.5632 | 2506.9769 | 2540.7019 | 2573.4576 | 2577.1739 | 2615.4092 | 2586.3774 | 2586.3774 | 2586.3774 | 2586.3774 | 2586.3774 | 2586.3774 | 2586.3774 | 2586.3774 | 2586.3774 | 2586.3774 | 2586.3774 | 2586.3774 | 2586.3774 | 2586.3774 | 2586.3774 | 2586.3774
55% | 11937.0341 | 15847.1857 | 16911.512 | 12369.7021 | 12368.5597 | 12489.86 | 12622.9685 | 12896.2442 | 13092.6158 | 13199.1405 | 13315.6267 | 13422.2638 | 13614.9569 | 13854.1221 | 13837.4049 | 13837.4049 | 13837.4049 | 13837.4049 | 13837.4049 | 13837.4049 | 13837.4049 | 13837.4049 | 13837.4049 | 13837.4049 | 13837.4049 | 13837.4049 | 13837.4049 | 13837.4049 | 13837.4049 | 13837.4049 |  | 4377.3623 | 5666.3214 | 6003.5838 | 4499.3541 | 4500.7834 | 4535.3613 | 4626.6707 | 4687.751 | 4747.5747 | 4817.5492 | 4882.357 | 4945.3024 | 4952.4438 | 5025.9188 | 4970.1297 | 4970.1297 | 4970.1297 | 4970.1297 | 4970.1297 | 4970.1297 | 4970.1297 | 4970.1297 | 4970.1297 | 4970.1297 | 4970.1297 | 4970.1297 | 4970.1297 | 4970.1297 | 4970.1297 | 4970.1297
50% | 15327.7148 | 20348.5339 | 21715.179 | 15883.2809 | 15881.814 | 16037.5693 | 16208.4869 | 16559.3858 | 16811.5362 | 16948.319 | 17097.8927 | 17234.8198 | 17482.2469 | 17789.3462 | 17767.8805 | 17767.8805 | 17767.8805 | 17767.8805 | 17767.8805 | 17767.8805 | 17767.8805 | 17767.8805 | 17767.8805 | 17767.8805 | 17767.8805 | 17767.8805 | 17767.8805 | 17767.8805 | 17767.8805 | 17767.8805 |  | 9714.4123 | 12574.9205 | 13323.3863 | 9985.1413 | 9988.3132 | 10065.05 | 10267.6873 | 10403.2391 | 10536.002 | 10691.2923 | 10835.1163 | 10974.807 | 10990.6555 | 11153.7141 | 11029.9047 | 11029.9047 | 11029.9047 | 11029.9047 | 11029.9047 | 11029.9047 | 11029.9047 | 11029.9047 | 11029.9047 | 11029.9047 | 11029.9047 | 11029.9047 | 11029.9047 | 11029.9047 | 11029.9047 | 11029.9047
45% | 20411.3174 | 27097.3455 | 28917.2533 | 21151.143 | 21149.1896 | 21356.6028 | 21584.2071 | 22051.4854 | 22387.2642 | 22569.4125 | 22768.594 | 22950.9344 | 23280.4233 | 23689.3755 | 23660.7905 | 23660.7905 | 23660.7905 | 23660.7905 | 23660.7905 | 23660.7905 | 23660.7905 | 23660.7905 | 23660.7905 | 23660.7905 | 23660.7905 | 23660.7905 | 23660.7905 | 23660.7905 | 23660.7905 | 23660.7905 |  | 14720.4239 | 19055.0036 | 20189.1672 | 15130.6644 | 15135.471 | 15251.7516 | 15558.8116 | 15764.2156 | 15965.3936 | 16200.7079 | 16418.6469 | 16630.3228 | 16654.3383 | 16901.424 | 16713.8133 | 16713.8133 | 16713.8133 | 16713.8133 | 16713.8133 | 16713.8133 | 16713.8133 | 16713.8133 | 16713.8133 | 16713.8133 | 16713.8133 | 16713.8133 | 16713.8133 | 16713.8133 | 16713.8133 | 16713.8133
40% | 14315.8312 | 19005.1929 | 20281.6168 | 14834.7207 | 14833.3506 | 14978.8235 | 15138.4577 | 15466.1915 | 15701.6957 | 15829.4486 | 15969.148 | 16097.0356 | 16328.1284 | 16614.9541 | 16594.9054 | 16594.9054 | 16594.9054 | 16594.9054 | 16594.9054 | 16594.9054 | 16594.9054 | 16594.9054 | 16594.9054 | 16594.9054 | 16594.9054 | 16594.9054 | 16594.9054 | 16594.9054 | 16594.9054 | 16594.9054 |  | 15242.3215 | 19730.5793 | 20904.9535 | 15667.1067 | 15672.0837 | 15792.4868 | 16110.4334 | 16323.1198 | 16531.4304 | 16775.0874 | 17000.7533 | 17219.9339 | 17244.8009 | 17500.6467 | 17306.3844 | 17306.3844 | 17306.3844 | 17306.3844 | 17306.3844 | 17306.3844 | 17306.3844 | 17306.3844 | 17306.3844 | 17306.3844 | 17306.3844 | 17306.3844 | 17306.3844 | 17306.3844 | 17306.3844 | 17306.3844
35% | 7422.2532 | 9853.5218 | 10515.3025 | 7691.2791 | 7690.5688 | 7765.9914 | 7848.7561 | 8018.6745 | 8140.7751 | 8207.0105 | 8279.4397 | 8345.7449 | 8465.5583 | 8614.2673 | 8603.8728 | 8603.8728 | 8603.8728 | 8603.8728 | 8603.8728 | 8603.8728 | 8603.8728 | 8603.8728 | 8603.8728 | 8603.8728 | 8603.8728 | 8603.8728 | 8603.8728 | 8603.8728 | 8603.8728 | 8603.8728 |  | 20759.9869 | 26872.9779 | 28472.4713 | 21338.5428 | 21345.3214 | 21509.3101 | 21942.3521 | 22232.0303 | 22515.7485 | 22847.6086 | 23154.9646 | 23453.4879 | 23487.3566 | 23835.8177 | 23571.2332 | 23571.2332 | 23571.2332 | 23571.2332 | 23571.2332 | 23571.2332 | 23571.2332 | 23571.2332 | 23571.2332 | 23571.2332 | 23571.2332 | 23571.2332 | 23571.2332 | 23571.2332 | 23571.2332 | 23571.2332
30% | 3452.1096 | 4582.899 | 4890.695 | 3577.2342 | 3576.9039 | 3611.9831 | 3650.4772 | 3729.5067 | 3786.296 | 3817.1022 | 3850.7893 | 3881.628 | 3937.3535 | 4006.5185 | 4001.684 | 4001.684 | 4001.684 | 4001.684 | 4001.684 | 4001.684 | 4001.684 | 4001.684 | 4001.684 | 4001.684 | 4001.684 | 4001.684 | 4001.684 | 4001.684 | 4001.684 | 4001.684 |  | 19183.5111 | 24832.2926 | 26310.3234 | 19718.1325 | 19724.3963 | 19875.932 | 20276.0896 | 20543.7701 | 20805.9434 | 21112.6025 | 21396.6185 | 21672.4724 | 21703.7693 | 22025.7688 | 21781.2764 | 21781.2764 | 21781.2764 | 21781.2764 | 21781.2764 | 21781.2764 | 21781.2764 | 21781.2764 | 21781.2764 | 21781.2764 | 21781.2764 | 21781.2764 | 21781.2764 | 21781.2764 | 21781.2764 | 21781.2764
25% | 2357.031 | 3129.1112 | 3339.2681 | 2442.4636 | 2442.238 | 2466.1894 | 2492.4724 | 2546.4321 | 2585.2067 | 2606.2406 | 2629.2414 | 2650.2975 | 2688.3458 | 2735.5702 | 2732.2693 | 2732.2693 | 2732.2693 | 2732.2693 | 2732.2693 | 2732.2693 | 2732.2693 | 2732.2693 | 2732.2693 | 2732.2693 | 2732.2693 | 2732.2693 | 2732.2693 | 2732.2693 | 2732.2693 | 2732.2693 |  | 5533.3008 | 7162.6379 | 7588.9618 | 5687.5072 | 5689.314 | 5733.023 | 5848.4446 | 5925.6545 | 6001.2759 | 6089.7288 | 6171.6505 | 6251.2179 | 6260.2452 | 6353.1229 | 6282.6014 | 6282.6014 | 6282.6014 | 6282.6014 | 6282.6014 | 6282.6014 | 6282.6014 | 6282.6014 | 6282.6014 | 6282.6014 | 6282.6014 | 6282.6014 | 6282.6014 | 6282.6014 | 6282.6014 | 6282.6014
20% | 1427.8587 | 1895.5749 | 2022.8852 | 1479.6126 | 1479.476 | 1493.9854 | 1509.9073 | 1542.5954 | 1566.0846 | 1578.8266 | 1592.7602 | 1605.5157 | 1628.5649 | 1657.1728 | 1655.1732 | 1655.1732 | 1655.1732 | 1655.1732 | 1655.1732 | 1655.1732 | 1655.1732 | 1655.1732 | 1655.1732 | 1655.1732 | 1655.1732 | 1655.1732 | 1655.1732 | 1655.1732 | 1655.1732 | 1655.1732 |  | 1484.8203 | 1922.0408 | 2036.4417 | 1526.2004 | 1526.6852 | 1538.4142 | 1569.3868 | 1590.1055 | 1610.3979 | 1634.1336 | 1656.1167 | 1677.468 | 1679.8904 | 1704.8134 | 1685.8895 | 1685.8895 | 1685.8895 | 1685.8895 | 1685.8895 | 1685.8895 | 1685.8895 | 1685.8895 | 1685.8895 | 1685.8895 | 1685.8895 | 1685.8895 | 1685.8895 | 1685.8895 | 1685.8895 | 1685.8895
15% | 914.1778 | 1213.6303 | 1295.1399 | 947.313 | 947.2255 | 956.5151 | 966.709 | 987.6373 | 1002.6761 | 1010.8341 | 1019.755 | 1027.9217 | 1042.6787 | 1060.9948 | 1059.7145 | 1059.7145 | 1059.7145 | 1059.7145 | 1059.7145 | 1059.7145 | 1059.7145 | 1059.7145 | 1059.7145 | 1059.7145 | 1059.7145 | 1059.7145 | 1059.7145 | 1059.7145 | 1059.7145 | 1059.7145 |  | 818.9695 | 1060.1234 | 1123.2225 | 841.7932 | 842.0606 | 848.5299 | 865.6131 | 877.0407 | 888.2333 | 901.325 | 913.45 | 925.2265 | 926.5626 | 940.3092 | 929.8715 | 929.8715 | 929.8715 | 929.8715 | 929.8715 | 929.8715 | 929.8715 | 929.8715 | 929.8715 | 929.8715 | 929.8715 | 929.8715 | 929.8715 | 929.8715 | 929.8715 | 929.8715
10% | 611.8703 | 812.2975 | 866.8529 | 634.0481 | 633.9895 | 640.2072 | 647.0301 | 661.0377 | 671.1033 | 676.5636 | 682.5345 | 688.0005 | 697.8776 | 710.1367 | 709.2798 | 709.2798 | 709.2798 | 709.2798 | 709.2798 | 709.2798 | 709.2798 | 709.2798 | 709.2798 | 709.2798 | 709.2798 | 709.2798 | 709.2798 | 709.2798 | 709.2798 | 709.2798 |  | 191.3984 | 247.7576 | 262.5043 | 196.7324 | 196.7949 | 198.3068 | 202.2993 | 204.97 | 207.5858 | 210.6454 | 213.4791 | 216.2314 | 216.5436 | 219.7563 | 217.3169 | 217.3169 | 217.3169 | 217.3169 | 217.3169 | 217.3169 | 217.3169 | 217.3169 | 217.3169 | 217.3169 | 217.3169 | 217.3169 | 217.3169 | 217.3169 | 217.3169 | 217.3169
5% | 435.3228 | 577.9192 | 616.7333 | 451.1014 | 451.0598 | 455.4834 | 460.3376 | 470.3035 | 477.4648 | 481.3496 | 485.5976 | 489.4865 | 496.5137 | 505.2356 | 504.626 | 504.626 | 504.626 | 504.626 | 504.626 | 504.626 | 504.626 | 504.626 | 504.626 | 504.626 | 504.626 | 504.626 | 504.626 | 504.626 | 504.626 | 504.626 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9.992e-14% | 38.2117 | 50.7285 | 54.1355 | 39.5967 | 39.593 | 39.9813 | 40.4074 | 41.2822 | 41.9108 | 42.2518 | 42.6247 | 42.966 | 43.5829 | 44.3485 | 44.2949 | 44.2949 | 44.2949 | 44.2949 | 44.2949 | 44.2949 | 44.2949 | 44.2949 | 44.2949 | 44.2949 | 44.2949 | 44.2949 | 44.2949 | 44.2949 | 44.2949 | 44.2949 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E @ R (MWh) | 102337.6118 | 135859.8063 | 144984.402 | 106046.9258 | 106037.132 | 107077.0538 | 108218.2089 | 110561.034 | 112244.5511 | 113157.8003 | 114156.4504 | 115070.6629 | 116722.6439 | 118773.0352 | 118629.7164 | 118629.7164 | 118629.7164 | 118629.7164 | 118629.7164 | 118629.7164 | 118629.7164 | 118629.7164 | 118629.7164 | 118629.7164 | 118629.7164 | 118629.7164 | 118629.7164 | 118629.7164 | 118629.7164 | 118629.7164 | E @ R (MWh) | 99292.8528 | 128530.651 | 136180.8614 | 102060.0253 | 102092.4466 | 102876.7874 | 104947.9823 | 106333.4827 | 107690.4775 | 109277.7293 | 110747.7815 | 112175.5869 | 112337.5775 | 114004.2305 | 112738.7505 | 112738.7505 | 112738.7505 | 112738.7505 | 112738.7505 | 112738.7505 | 112738.7505 | 112738.7505 | 112738.7505 | 112738.7505 | 112738.7505 | 112738.7505 | 112738.7505 | 112738.7505 | 112738.7505 | 112738.7505
Option 2 Summer POE50 W E @ R (MWh) N 2 | 71636.3283 | 95101.8644 | 101489.0814 | 74232.8481 | 74225.9924 | 74953.9377 | 75752.7463 | 77392.7238 | 78571.1858 | 79210.4602 | 79909.5153 | 80549.464 | 81705.8507 | 83141.1247 | 83040.8014 | 83040.8014 | 83040.8014 | 83040.8014 | 83040.8014 | 83040.8014 | 83040.8014 | 83040.8014 | 83040.8014 | 83040.8014 | 83040.8014 | 83040.8014 | 83040.8014 | 83040.8014 | 83040.8014 | 83040.8014 | Option 2 Summer POE10 W E @ R (MWh) N 2 | 29787.8558 | 38559.1953 | 40854.2584 | 30618.0076 | 30627.734 | 30863.0362 | 31484.3947 | 31900.0448 | 32307.1433 | 32783.3188 | 33224.3344 | 33652.6761 | 33701.2733 | 34201.2691 | 33821.6251 | 33821.6251 | 33821.6251 | 33821.6251 | 33821.6251 | 33821.6251 | 33821.6251 | 33821.6251 | 33821.6251 | 33821.6251 | 33821.6251 | 33821.6251 | 33821.6251 | 33821.6251 | 33821.6251 | 33821.6251
Option 3 - 2B PHM 3rd Tx + Switchroom + Two new feeders + OFR12 New Feeder
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | 66.5813 | 92.3179 | 99.0036 | 33.2711 | 34.1557 | 35.6839 | 39.1649 | 41.4924 | 44.4438 | 45.9741 | 47.3185 | 44.8292 | 47.7394 | 52.3166 | 48.8374 | 48.8374 | 48.8374 | 48.8374 | 48.8374 | 48.8374 | 48.8374 | 48.8374 | 48.8374 | 48.8374 | 48.8374 | 48.8374 | 48.8374 | 48.8374 | 48.8374 | 48.8374 |  | 71.2634 | 96.6755 | 103.6223 | 37.825 | 38.503 | 39.998 | 43.5335 | 45.4607 | 49.138 | 60.3227 | 51.0944 | 49.287 | 51.719 | 57.0417 | 53.4333 | 53.4333 | 53.4333 | 53.4333 | 53.4333 | 53.4333 | 53.4333 | 53.4333 | 53.4333 | 53.4333 | 53.4333 | 53.4333 | 53.4333 | 53.4333 | 53.4333 | 53.4333
98% | 79.0946 | 109.6681 | 117.6103 | 38.7176 | 39.7684 | 41.5839 | 45.7191 | 48.484 | 51.9901 | 53.808 | 55.405 | 52.4479 | 55.9051 | 61.3424 | 57.2094 | 57.2094 | 57.2094 | 57.2094 | 57.2094 | 57.2094 | 57.2094 | 57.2094 | 57.2094 | 57.2094 | 57.2094 | 57.2094 | 57.2094 | 57.2094 | 57.2094 | 57.2094 |  | 84.6567 | 114.8446 | 123.097 | 44.1273 | 44.9328 | 46.7088 | 50.9087 | 53.1981 | 57.5665 | 70.8532 | 59.8906 | 57.7435 | 60.6326 | 66.9556 | 62.6691 | 62.6691 | 62.6691 | 62.6691 | 62.6691 | 62.6691 | 62.6691 | 62.6691 | 62.6691 | 62.6691 | 62.6691 | 62.6691 | 62.6691 | 62.6691 | 62.6691 | 62.6691
97% | 156.5832 | 217.1095 | 232.8326 | 75.0198 | 77.1001 | 80.6941 | 88.8806 | 94.3542 | 101.2952 | 104.8942 | 108.0557 | 102.2015 | 109.0457 | 119.81 | 111.6278 | 111.6278 | 111.6278 | 111.6278 | 111.6278 | 111.6278 | 111.6278 | 111.6278 | 111.6278 | 111.6278 | 111.6278 | 111.6278 | 111.6278 | 111.6278 | 111.6278 | 111.6278 |  | 167.5944 | 227.3573 | 243.6946 | 85.7293 | 87.3239 | 90.8398 | 99.1544 | 103.6867 | 112.3348 | 138.6385 | 116.9358 | 112.6853 | 118.4048 | 130.9224 | 122.4364 | 122.4364 | 122.4364 | 122.4364 | 122.4364 | 122.4364 | 122.4364 | 122.4364 | 122.4364 | 122.4364 | 122.4364 | 122.4364 | 122.4364 | 122.4364 | 122.4364 | 122.4364
95% | 462.5227 | 641.3081 | 687.7517 | 214.1898 | 220.3346 | 230.9507 | 255.1325 | 271.3005 | 291.8032 | 302.4343 | 311.7729 | 294.4803 | 314.6971 | 346.4933 | 322.3243 | 322.3243 | 322.3243 | 322.3243 | 322.3243 | 322.3243 | 322.3243 | 322.3243 | 322.3243 | 322.3243 | 322.3243 | 322.3243 | 322.3243 | 322.3243 | 322.3243 | 322.3243 |  | 495.0481 | 671.5786 | 719.8364 | 245.8241 | 250.5343 | 260.9198 | 285.4799 | 298.8673 | 324.4126 | 402.1097 | 338.0033 | 325.4479 | 342.3424 | 379.3175 | 354.2513 | 354.2513 | 354.2513 | 354.2513 | 354.2513 | 354.2513 | 354.2513 | 354.2513 | 354.2513 | 354.2513 | 354.2513 | 354.2513 | 354.2513 | 354.2513 | 354.2513 | 354.2513
90% | 2550.165 | 3535.9158 | 3791.9875 | 1080.5129 | 1114.3929 | 1172.926 | 1306.2548 | 1395.3988 | 1508.4422 | 1567.0578 | 1618.5473 | 1523.2029 | 1634.6701 | 1809.9816 | 1676.7232 | 1676.7232 | 1676.7232 | 1676.7232 | 1676.7232 | 1676.7232 | 1676.7232 | 1676.7232 | 1676.7232 | 1676.7232 | 1676.7232 | 1676.7232 | 1676.7232 | 1676.7232 | 1676.7232 | 1676.7232 |  | 2729.4971 | 3702.8155 | 3968.8899 | 1254.9319 | 1280.9021 | 1338.1633 | 1473.5779 | 1547.3909 | 1688.2374 | 2116.6282 | 1763.1711 | 1693.9456 | 1787.0953 | 1990.9607 | 1852.756 | 1852.756 | 1852.756 | 1852.756 | 1852.756 | 1852.756 | 1852.756 | 1852.756 | 1852.756 | 1852.756 | 1852.756 | 1852.756 | 1852.756 | 1852.756 | 1852.756 | 1852.756
85% | 6229.8705 | 8637.9889 | 9263.5537 | 2255.0247 | 2337.7909 | 2480.7832 | 2806.4959 | 3024.2683 | 3300.4252 | 3443.6191 | 3569.4041 | 3336.4846 | 3608.791 | 4037.0643 | 3711.5236 | 3711.5236 | 3711.5236 | 3711.5236 | 3711.5236 | 3711.5236 | 3711.5236 | 3711.5236 | 3711.5236 | 3711.5236 | 3711.5236 | 3711.5236 | 3711.5236 | 3711.5236 | 3711.5236 | 3711.5236 |  | 6667.9659 | 9045.7131 | 9695.7136 | 2681.1178 | 2744.5611 | 2884.4462 | 3215.2542 | 3395.5742 | 3739.652 | 4786.1802 | 3922.7097 | 3753.5967 | 3981.1549 | 4479.1835 | 4141.5593 | 4141.5593 | 4141.5593 | 4141.5593 | 4141.5593 | 4141.5593 | 4141.5593 | 4141.5593 | 4141.5593 | 4141.5593 | 4141.5593 | 4141.5593 | 4141.5593 | 4141.5593 | 4141.5593 | 4141.5593
80% | 9683.0656 | 13425.9956 | 14398.3087 | 2834.7517 | 2963.395 | 3185.6473 | 3691.9015 | 4030.3843 | 4459.614 | 4682.1797 | 4877.6869 | 4515.661 | 4938.906 | 5604.5696 | 5098.5828 | 5098.5828 | 5098.5828 | 5098.5828 | 5098.5828 | 5098.5828 | 5098.5828 | 5098.5828 | 5098.5828 | 5098.5828 | 5098.5828 | 5098.5828 | 5098.5828 | 5098.5828 | 5098.5828 | 5098.5828 |  | 10363.9958 | 14059.7198 | 15070.0133 | 3497.0267 | 3595.6364 | 3813.0593 | 4327.233 | 4607.5037 | 5142.3027 | 6768.9177 | 5426.8286 | 5163.9769 | 5517.6697 | 6291.7539 | 5766.9858 | 5766.9858 | 5766.9858 | 5766.9858 | 5766.9858 | 5766.9858 | 5766.9858 | 5766.9858 | 5766.9858 | 5766.9858 | 5766.9858 | 5766.9858 | 5766.9858 | 5766.9858 | 5766.9858 | 5766.9858
75% | 10683.1238 | 14812.6201 | 15885.3529 | 2292.6645 | 2434.594 | 2679.8003 | 3238.34 | 3611.781 | 4085.3412 | 4330.8933 | 4546.5923 | 4147.1766 | 4614.1339 | 5348.5467 | 4790.3021 | 4790.3021 | 4790.3021 | 4790.3021 | 4790.3021 | 4790.3021 | 4790.3021 | 4790.3021 | 4790.3021 | 4790.3021 | 4790.3021 | 4790.3021 | 4790.3021 | 4790.3021 | 4790.3021 | 4790.3021 |  | 11434.3798 | 15511.7948 | 16626.4305 | 3023.3387 | 3132.1327 | 3372.0108 | 3939.288 | 4248.5048 | 4838.5373 | 6633.1476 | 5152.4488 | 4862.45 | 5252.6719 | 6106.7027 | 5527.7371 | 5527.7371 | 5527.7371 | 5527.7371 | 5527.7371 | 5527.7371 | 5527.7371 | 5527.7371 | 5527.7371 | 5527.7371 | 5527.7371 | 5527.7371 | 5527.7371 | 5527.7371 | 5527.7371 | 5527.7371
70% | 11478.4193 | 15915.3323 | 17067.9236 | 1442.6067 | 1595.102 | 1858.5625 | 2458.6821 | 2859.9236 | 3368.7375 | 3632.5695 | 3864.326 | 3435.1762 | 3936.8958 | 4725.9813 | 4126.1786 | 4126.1786 | 4126.1786 | 4126.1786 | 4126.1786 | 4126.1786 | 4126.1786 | 4126.1786 | 4126.1786 | 4126.1786 | 4126.1786 | 4126.1786 | 4126.1786 | 4126.1786 | 4126.1786 | 4126.1786 |  | 12285.6019 | 16666.5563 | 17864.1701 | 2227.6752 | 2344.5683 | 2602.304 | 3211.8116 | 3544.0477 | 4178.0046 | 6106.2131 | 4515.285 | 4203.6975 | 4622.9692 | 5540.5775 | 4918.5113 | 4918.5113 | 4918.5113 | 4918.5113 | 4918.5113 | 4918.5113 | 4918.5113 | 4918.5113 | 4918.5113 | 4918.5113 | 4918.5113 | 4918.5113 | 4918.5113 | 4918.5113 | 4918.5113 | 4918.5113
65% | 12096.053 | 16771.7086 | 17986.3189 | 341.2438 | 466.0293 | 723.5548 | 1355.9659 | 1778.7974 | 2314.9898 | 2593.0181 | 2837.2451 | 2385.0034 | 2913.7197 | 3745.2644 | 3113.1874 | 3113.1874 | 3113.1874 | 3113.1874 | 3113.1874 | 3113.1874 | 3113.1874 | 3113.1874 | 3113.1874 | 3113.1874 | 3113.1874 | 3113.1874 | 3113.1874 | 3113.1874 | 3113.1874 | 3113.1874 |  | 12946.6687 | 17563.3547 | 18825.4101 | 1112.5289 | 1235.7118 | 1507.3158 | 2149.6199 | 2499.7331 | 3167.8021 | 5199.7642 | 3523.231 | 3194.8775 | 3636.7094 | 4603.6927 | 3948.1542 | 3948.1542 | 3948.1542 | 3948.1542 | 3948.1542 | 3948.1542 | 3948.1542 | 3948.1542 | 3948.1542 | 3948.1542 | 3948.1542 | 3948.1542 | 3948.1542 | 3948.1542 | 3948.1542 | 3948.1542
60% | 13316.2645 | 18463.5854 | 19800.7217 |  |  | 0.48365 | 171.9766 | 449.1607 | 971.385 | 1277.46 | 1546.3238 | 1048.4614 | 1630.5129 | 2545.9413 | 1850.1024 | 1850.1024 | 1850.1024 | 1850.1024 | 1850.1024 | 1850.1024 | 1850.1024 | 1850.1024 | 1850.1024 | 1850.1024 | 1850.1024 | 1850.1024 | 1850.1024 | 1850.1024 | 1850.1024 | 1850.1024 |  | 14252.6876 | 19335.0902 | 20724.4577 | 70.264 | 116.2969 | 256.8306 | 791.8285 | 1174.7647 | 1910.2264 | 4147.1663 | 2301.5098 | 1940.033 | 2426.4356 | 3490.9651 | 2769.2979 | 2769.2979 | 2769.2979 | 2769.2979 | 2769.2979 | 2769.2979 | 2769.2979 | 2769.2979 | 2769.2979 | 2769.2979 | 2769.2979 | 2769.2979 | 2769.2979 | 2769.2979 | 2769.2979 | 2769.2979
55% | 14813.5078 | 20539.579 | 22027.0592 | [5 empty] | 2.2205 | 47.0164 | 132.5181 | 8.1139 | 167.9103 | 803.9778 | 279.088 | 279.088 | 279.088 | 279.088 | 279.088 | 279.088 | 279.088 | 279.088 | 279.088 | 279.088 | 279.088 | 279.088 | 279.088 | 279.088 | 279.088 | 279.088 |  | 15855.2197 | 21509.0734 | 23054.6574 |  |  |  |  | 25.6474 | 314.2101 | 2553.8762 | 590.5515 | 332.3582 | 695.7965 | 1823.8935 | 1025.4557 | 1025.4557 | 1025.4557 | 1025.4557 | 1025.4557 | 1025.4557 | 1025.4557 | 1025.4557 | 1025.4557 | 1025.4557 | 1025.4557 | 1025.4557 | 1025.4557 | 1025.4557 | 1025.4557 | 1025.4557
50% | FY25: 15014.9247; FY26: 20818.8523; FY27: 22326.5575 |  | 16070.8005 | 21801.5288 | 23368.1279 | [6 empty] | 395.1133 |  |  |  | 90.5185
45% | FY25: 11588.8305; FY26: 16068.4223; FY27: 17232.1005 |  | 12403.7774 | 16826.8724 | 18036.0061
40% | FY25: 5693.5395; FY26: 7894.3425; FY27: 8466.0523 |  | 6093.9192 | 8266.9656 | 8861.0075
35% | FY25: 2127.9257; FY26: 2950.4624; FY27: 3164.1354 |  | 2277.5652 | 3089.728 | 3311.7475
30% | FY25: 1061.2862; FY26: 1471.5199; FY27: 1578.0877 |  | 1135.9177 | 1540.9775 | 1651.708
25% | FY25: 625.6637; FY26: 867.5102; FY27: 930.3354 |  | 669.6615 | 908.4578 | 973.7371
20% | FY25: 316.1776; FY26: 438.3942; FY27: 470.1428 |  | 338.4118 | 459.0869 | 492.0757
15% | FY25: 128.8131; FY26: 178.605; FY27: 191.5396 |  | 137.8715 | 187.0354 | 200.4753
10% | FY25: 51.8598; FY26: 71.9059; FY27: 77.1134 |  | 55.5067 | 75.3 | 80.7108
5% | FY25: 44.1645; FY26: 61.236; FY27: 65.6707 |  | 47.2702 | 64.1264 | 68.7344
9.992e-14% | FY25: 0; FY26: 0; FY27: 0 |  | 0 | 0 | 0
E @ R (MWh) | 118268.4368 | 163984.3799 | 175860.1598 | 10608.0025 | 11282.6629 | 12490.6702 | 15458.514 | 17605.3449 | 20500.6875 | 22080.9247 | 23515.1957 | 20893.2388 | 23972.9271 | 29201.2892 | 25185.6869 | 25185.6869 | 25185.6869 | 25185.6869 | 25185.6869 | 25185.6869 | 25185.6869 | 25185.6869 | 25185.6869 | 25185.6869 | 25185.6869 | 25185.6869 | 25185.6869 | 25185.6869 | 25185.6869 | 25185.6869 | E @ R (MWh) | 126585.2808 | 171724.6525 | 184064.3234 | 14280.3887 | 14871.1032 | 16212.5964 | 19587.6896 | 21544.3792 | 25522.4245 | 39378.9311 | 27761.6594 | 25690.0991 | 28493.6014 | 35052.4853 | 30543.2476 | 30543.2476 | 30543.2476 | 30543.2476 | 30543.2476 | 30543.2476 | 30543.2476 | 30543.2476 | 30543.2476 | 30543.2476 | 30543.2476 | 30543.2476 | 30543.2476 | 30543.2476 | 30543.2476 | 30543.2476
Option 3 Winter POE50 W E @ R (MWh) N 2 | 82787.9057 | 114789.066 | 123102.1118 | 7425.6018 | 7897.864 | 8743.4692 | 10820.9598 | 12323.7415 | 14350.4812 | 15456.6473 | 16460.637 | 14625.2671 | 16781.0489 | 20440.9025 | 17629.9808 | 17629.9808 | 17629.9808 | 17629.9808 | 17629.9808 | 17629.9808 | 17629.9808 | 17629.9808 | 17629.9808 | 17629.9808 | 17629.9808 | 17629.9808 | 17629.9808 | 17629.9808 | 17629.9808 | 17629.9808 | Option 3 Winter POE10 W E @ R (MWh) N 2 | 37975.5842 | 51517.3957 | 55219.297 | 4284.1166 | 4461.331 | 4863.7789 | 5876.3069 | 6463.3138 | 7656.7273 | 11813.6793 | 8328.4978 | 7707.0297 | 8548.0804 | 10515.7456 | 9162.9743 | 9162.9743 | 9162.9743 | 9162.9743 | 9162.9743 | 9162.9743 | 9162.9743 | 9162.9743 | 9162.9743 | 9162.9743 | 9162.9743 | 9162.9743 | 9162.9743 | 9162.9743 | 9162.9743 | 9162.9743
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 85.8327 | 111.1071 | 117.7202 | 49.2537 | 49.2817 | 49.9598 | 51.7502 | 52.9479 | 54.1209 | 55.493 | 56.7638 | 57.998 | 58.138 | 59.5788 | 58.4848 | 58.4848 | 58.4848 | 58.4848 | 58.4848 | 58.4848 | 58.4848 | 58.4848 | 58.4848 | 58.4848 | 58.4848 | 58.4848 | 58.4848 | 58.4848 | 58.4848 | 58.4848
98% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 42.4851 | 54.9952 | 58.2686 | 24.0373 | 24.0512 | 24.3868 | 25.273 | 25.8658 | 26.4464 | 27.1256 | 27.7546 | 28.3655 | 28.4348 | 29.1479 | 28.6065 | 28.6065 | 28.6065 | 28.6065 | 28.6065 | 28.6065 | 28.6065 | 28.6065 | 28.6065 | 28.6065 | 28.6065 | 28.6065 | 28.6065 | 28.6065 | 28.6065 | 28.6065
97% | 18.864 | 25.0432 | 26.7251 | 9.6587 | 9.6569 | 9.8486 | 10.059 | 10.4908 | 10.8011 | 10.9695 | 11.1536 | 11.3221 | 11.6266 | 12.0045 | 11.9781 | 11.9781 | 11.9781 | 11.9781 | 11.9781 | 11.9781 | 11.9781 | 11.9781 | 11.9781 | 11.9781 | 11.9781 | 11.9781 | 11.9781 | 11.9781 | 11.9781 | 11.9781 |  | 84.1075 | 108.8738 | 115.354 | 46.8955 | 46.9229 | 47.5873 | 49.3417 | 50.5154 | 51.6648 | 53.0093 | 54.2545 | 55.464 | 55.6012 | 57.013 | 55.941 | 55.941 | 55.941 | 55.941 | 55.941 | 55.941 | 55.941 | 55.941 | 55.941 | 55.941 | 55.941 | 55.941 | 55.941 | 55.941 | 55.941 | 55.941
95% | 92.8689 | 123.2894 | 131.5698 | 46.2417 | 46.2328 | 47.1765 | 48.212 | 50.3381 | 51.8658 | 52.6946 | 53.6008 | 54.4305 | 55.9296 | 57.7903 | 57.6602 | 57.6602 | 57.6602 | 57.6602 | 57.6602 | 57.6602 | 57.6602 | 57.6602 | 57.6602 | 57.6602 | 57.6602 | 57.6602 | 57.6602 | 57.6602 | 57.6602 | 57.6602 |  | 124.2203 | 160.7982 | 170.369 | 67.6901 | 67.7307 | 68.712 | 71.3031 | 73.0364 | 74.7341 | 76.7198 | 78.559 | 80.3452 | 80.5479 | 82.6329 | 81.0498 | 81.0498 | 81.0498 | 81.0498 | 81.0498 | 81.0498 | 81.0498 | 81.0498 | 81.0498 | 81.0498 | 81.0498 | 81.0498 | 81.0498 | 81.0498 | 81.0498 | 81.0498
90% | 161.0694 | 213.8301 | 228.1913 | 74.6165 | 74.6011 | 76.2379 | 78.0339 | 81.7213 | 84.371 | 85.8084 | 87.3801 | 88.819 | 91.4191 | 94.6462 | 94.4206 | 94.4206 | 94.4206 | 94.4206 | 94.4206 | 94.4206 | 94.4206 | 94.4206 | 94.4206 | 94.4206 | 94.4206 | 94.4206 | 94.4206 | 94.4206 | 94.4206 | 94.4206 |  | 538.6113 | 697.2109 | 738.7092 | 276.7487 | 276.9246 | 281.1792 | 292.4144 | 299.93 | 307.291 | 315.901 | 323.8752 | 331.6203 | 332.499 | 341.5397 | 334.6752 | 334.6752 | 334.6752 | 334.6752 | 334.6752 | 334.6752 | 334.6752 | 334.6752 | 334.6752 | 334.6752 | 334.6752 | 334.6752 | 334.6752 | 334.6752 | 334.6752 | 334.6752
85% | 457.0889 | 606.8151 | 647.57 | 186.9134 | 186.8697 | 191.5145 | 196.6114 | 207.0756 | 214.595 | 218.674 | 223.1344 | 227.2178 | 234.5963 | 243.7543 | 243.1142 | 243.1142 | 243.1142 | 243.1142 | 243.1142 | 243.1142 | 243.1142 | 243.1142 | 243.1142 | 243.1142 | 243.1142 | 243.1142 | 243.1142 | 243.1142 | 243.1142 | 243.1142 |  | 509.4971 | 659.5238 | 698.779 | 236.9532 | 237.1195 | 241.1442 | 251.772 | 258.8814 | 265.8444 | 273.989 | 281.5323 | 288.8587 | 289.6899 | 298.2419 | 291.7484 | 291.7484 | 291.7484 | 291.7484 | 291.7484 | 291.7484 | 291.7484 | 291.7484 | 291.7484 | 291.7484 | 291.7484 | 291.7484 | 291.7484 | 291.7484 | 291.7484 | 291.7484
80% | 638.4734 | 847.6148 | 904.5422 | 222.1885 | 222.1274 | 228.6154 | 235.7349 | 250.3515 | 260.8548 | 266.5525 | 272.783 | 278.4866 | 288.7932 | 301.5853 | 300.6912 | 300.6912 | 300.6912 | 300.6912 | 300.6912 | 300.6912 | 300.6912 | 300.6912 | 300.6912 | 300.6912 | 300.6912 | 300.6912 | 300.6912 | 300.6912 | 300.6912 | 300.6912 |  | 355.8393 | 460.6198 | 488.0361 | 146.0426 | 146.1588 | 148.9697 | 156.3923 | 161.3576 | 166.2207 | 171.909 | 177.1773 | 182.2941 | 182.8747 | 188.8475 | 184.3124 | 184.3124 | 184.3124 | 184.3124 | 184.3124 | 184.3124 | 184.3124 | 184.3124 | 184.3124 | 184.3124 | 184.3124 | 184.3124 | 184.3124 | 184.3124 | 184.3124 | 184.3124
75% | 1664.3841 | 2209.5776 | 2357.9769 | 464.7244 | 464.5651 | 481.4781 | 500.0374 | 538.1403 | 565.5205 | 580.3733 | 596.615 | 611.4834 | 638.3507 | 671.6975 | 669.3666 | 669.3666 | 669.3666 | 669.3666 | 669.3666 | 669.3666 | 669.3666 | 669.3666 | 669.3666 | 669.3666 | 669.3666 | 669.3666 | 669.3666 | 669.3666 | 669.3666 | 669.3666 |  | 635.1192 | 822.1366 | 871.0705 | 221.4724 | 221.6798 | 226.6968 | 239.945 | 248.8073 | 257.4872 | 267.6399 | 277.043 | 286.1758 | 287.212 | 297.8726 | 289.7781 | 289.7781 | 289.7781 | 289.7781 | 289.7781 | 289.7781 | 289.7781 | 289.7781 | 289.7781 | 289.7781 | 289.7781 | 289.7781 | 289.7781 | 289.7781 | 289.7781 | 289.7781
70% | 2875.5487 | 3817.4772 | 4073.866 | 577.8335 | 577.5583 | 606.7787 | 638.8436 | 704.6738 | 751.9784 | 777.6395 | 805.7002 | 831.3883 | 877.8068 | 935.42 | 931.3929 | 931.3929 | 931.3929 | 931.3929 | 931.3929 | 931.3929 | 931.3929 | 931.3929 | 931.3929 | 931.3929 | 931.3929 | 931.3929 | 931.3929 | 931.3929 | 931.3929 | 931.3929 |  | 1157.0168 | 1497.7123 | 1586.8569 | 322.219 | 322.5968 | 331.7364 | 355.8711 | 372.0158 | 387.8282 | 406.3238 | 423.4537 | 440.0913 | 441.9789 | 461.3997 | 446.6536 | 446.6536 | 446.6536 | 446.6536 | 446.6536 | 446.6536 | 446.6536 | 446.6536 | 446.6536 | 446.6536 | 446.6536 | 446.6536 | 446.6536 | 446.6536 | 446.6536 | 446.6536
65% | 7222.0048 | 9587.679 | 10231.6052 | 802.2336 | 801.5424 | 874.9301 | 955.4618 | 1120.7959 | 1239.6024 | 1304.0507 | 1374.5258 | 1439.0422 | 1555.6231 | 1700.32 | 1690.2059 | 1690.2059 | 1690.2059 | 1690.2059 | 1690.2059 | 1690.2059 | 1690.2059 | 1690.2059 | 1690.2059 | 1690.2059 | 1690.2059 | 1690.2059 | 1690.2059 | 1690.2059 | 1690.2059 | 1690.2059 |  | 1455.7061 | 1884.3537 | 1996.5114 | 288.04 | 288.5153 | 300.0144 | 330.3796 | 350.692 | 370.5866 | 393.8569 | 415.4089 | 436.3416 | 438.7165 | 463.1508 | 444.598 | 444.598 | 444.598 | 444.598 | 444.598 | 444.598 | 444.598 | 444.598 | 444.598 | 444.598 | 444.598 | 444.598 | 444.598 | 444.598 | 444.598 | 444.598
60% | 10556.5772 | 14014.5398 | 14955.7822 | 187.5582 | 186.9825 | 252.8081 | 335.7847 | 540.3015 | 711.4984 | 805.7041 | 908.7192 | 1003.0243 | 1173.4335 | 1384.9404 | 1370.1564 | 1370.1564 | 1370.1564 | 1370.1564 | 1370.1564 | 1370.1564 | 1370.1564 | 1370.1564 | 1370.1564 | 1370.1564 | 1370.1564 | 1370.1564 | 1370.1564 | 1370.1564 | 1370.1564 | 1370.1564 |  | 2277.9105 | 2948.6646 | 3124.1707 | 237.6968 | 238.4405 | 256.4344 | 303.9503 | 335.7356 | 366.8668 | 403.2805 | 437.0055 | 469.7612 | 473.4775 | 511.7128 | 482.681 | 482.681 | 482.681 | 482.681 | 482.681 | 482.681 | 482.681 | 482.681 | 482.681 | 482.681 | 482.681 | 482.681 | 482.681 | 482.681 | 482.681 | 482.681
55% | 11937.0341 | 15847.1857 | 16911.512 | [5 empty] | 3.8903 | 15.7556 | 37.6919 | 65.8304 | 135.7599 | 255.725 | 246.1724 | 246.1724 | 246.1724 | 246.1724 | 246.1724 | 246.1724 | 246.1724 | 246.1724 | 246.1724 | 246.1724 | 246.1724 | 246.1724 | 246.1724 | 246.1724 | 246.1724 | 246.1724 |  | 4377.3623 | 5666.3214 | 6003.5838 | 53.6808 | 54.3475 | 71.6739 | 128.262 | 174.6238 | 226.4176 | 294.3956 | 359.2034 | 422.1487 | 429.2901 | 502.7651 | 446.976 | 446.976 | 446.976 | 446.976 | 446.976 | 446.976 | 446.976 | 446.976 | 446.976 | 446.976 | 446.976 | 446.976 | 446.976 | 446.976 | 446.976 | 446.976
50% | FY25: 15327.7148; FY26: 20348.5339; FY27: 21715.179 |  | 9714.4123 | 12574.9205 | 13323.3863 | [6 empty] | 0.92441 | 14.9076 | 44.2124 | 48.4954 | 103.6497 | 59.9312 | 59.9312 | 59.9312 | 59.9312 | 59.9312 | 59.9312 | 59.9312 | 59.9312 | 59.9312 | 59.9312 | 59.9312 | 59.9312 | 59.9312 | 59.9312 | 59.9312 | 59.9312
45% | FY25: 20411.3174; FY26: 27097.3455; FY27: 28917.2533 |  | 14720.4239 | 19055.0036 | 20189.1672
40% | FY25: 14315.8312; FY26: 19005.1929; FY27: 20281.6168 |  | 15242.3215 | 19730.5793 | 20904.9535
35% | FY25: 7422.2532; FY26: 9853.5218; FY27: 10515.3025 |  | 20759.9869 | 26872.9779 | 28472.4713
30% | FY25: 3452.1096; FY26: 4582.899; FY27: 4890.695 |  | 19183.5111 | 24832.2926 | 26310.3234
25% | FY25: 2357.031; FY26: 3129.1112; FY27: 3339.2681 |  | 5533.3008 | 7162.6379 | 7588.9618
20% | FY25: 1427.8587; FY26: 1895.5749; FY27: 2022.8852 |  | 1484.8203 | 1922.0408 | 2036.4417
15% | FY25: 914.1778; FY26: 1213.6303; FY27: 1295.1399 |  | 818.9695 | 1060.1234 | 1123.2225
10% | FY25: 611.8703; FY26: 812.2975; FY27: 866.8529 |  | 191.3984 | 247.7576 | 262.5043
5% | FY25: 435.3228; FY26: 577.9192; FY27: 616.7333 |  | 0 | 0 | 0
9.992e-14% | FY25: 38.2117; FY26: 50.7285; FY27: 54.1355 |  | 0 | 0 | 0
E @ R (MWh) | 102337.6118 | 135859.8063 | 144984.402 | 2571.9686 | 2570.1362 | 2769.3877 | 2998.7788 | 3503.8889 | 3894.9777 | 4118.2221 | 4371.3041 | 4611.0446 | 5063.3387 | 5657.8836 | 5615.1586 | 5615.1586 | 5615.1586 | 5615.1586 | 5615.1586 | 5615.1586 | 5615.1586 | 5615.1586 | 5615.1586 | 5615.1586 | 5615.1586 | 5615.1586 | 5615.1586 | 5615.1586 | 5615.1586 | 5615.1586 | E @ R (MWh) | 99292.8528 | 128530.651 | 136180.8614 | 1970.7302 | 1973.7695 | 2048.4946 | 2256.6548 | 2404.4088 | 2555.5088 | 2740.5678 | 2926.9386 | 3123.6769 | 3146.9559 | 3397.5525 | 3205.4359 | 3205.4359 | 3205.4359 | 3205.4359 | 3205.4359 | 3205.4359 | 3205.4359 | 3205.4359 | 3205.4359 | 3205.4359 | 3205.4359 | 3205.4359 | 3205.4359 | 3205.4359 | 3205.4359 | 3205.4359
Option 3 Summer POE50 W E @ R (MWh) N 2 | 71636.3283 | 95101.8644 | 101489.0814 | 1800.378 | 1799.0954 | 1938.5714 | 2099.1452 | 2452.7222 | 2726.4844 | 2882.7555 | 3059.9129 | 3227.7312 | 3544.3371 | 3960.5185 | 3930.611 | 3930.611 | 3930.611 | 3930.611 | 3930.611 | 3930.611 | 3930.611 | 3930.611 | 3930.611 | 3930.611 | 3930.611 | 3930.611 | 3930.611 | 3930.611 | 3930.611 | 3930.611 | Option 3 Summer POE10 W E @ R (MWh) N 2 | 29787.8558 | 38559.1953 | 40854.2584 | 591.2191 | 592.1308 | 614.5484 | 676.9964 | 721.3226 | 766.6526 | 822.1703 | 878.0816 | 937.1031 | 944.0868 | 1019.2657 | 961.6308 | 961.6308 | 961.6308 | 961.6308 | 961.6308 | 961.6308 | 961.6308 | 961.6308 | 961.6308 | 961.6308 | 961.6308 | 961.6308 | 961.6308 | 961.6308 | 961.6308 | 961.6308
Option 4 - 3B OFR 3rd Tx + Switchroom + Two new feeders + OFR12 New Feeder
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | 66.5813 | 92.3179 | 99.0036 | 94.2265 | 95.1111 | 96.6393 | 100.1204 | 102.4478 | 105.3992 | 106.9296 | 108.2739 | 105.7846 | 108.6948 | 113.272 | 109.7928 | 109.7928 | 109.7928 | 109.7928 | 109.7928 | 109.7928 | 109.7928 | 109.7928 | 109.7928 | 109.7928 | 109.7928 | 109.7928 | 109.7928 | 109.7928 | 109.7928 | 109.7928 |  | 71.2634 | 96.6755 | 103.6223 | 98.7804 | 99.4584 | 100.9534 | 104.4889 | 106.4161 | 110.0934 | 121.2781 | 112.0498 | 110.2424 | 112.6744 | 117.9971 | 114.3888 | 114.3888 | 114.3888 | 114.3888 | 114.3888 | 114.3888 | 114.3888 | 114.3888 | 114.3888 | 114.3888 | 114.3888 | 114.3888 | 114.3888 | 114.3888 | 114.3888 | 114.3888
98% | 79.0946 | 109.6681 | 117.6103 | 111.9355 | 112.9863 | 114.8017 | 118.9369 | 121.7018 | 125.2079 | 127.0259 | 128.6228 | 125.6657 | 129.1229 | 134.5603 | 130.4272 | 130.4272 | 130.4272 | 130.4272 | 130.4272 | 130.4272 | 130.4272 | 130.4272 | 130.4272 | 130.4272 | 130.4272 | 130.4272 | 130.4272 | 130.4272 | 130.4272 | 130.4272 |  | 84.6567 | 114.8446 | 123.097 | 117.3451 | 118.1506 | 119.9266 | 124.1265 | 126.4159 | 130.7843 | 144.0711 | 133.1084 | 130.9614 | 133.8504 | 140.1734 | 135.8869 | 135.8869 | 135.8869 | 135.8869 | 135.8869 | 135.8869 | 135.8869 | 135.8869 | 135.8869 | 135.8869 | 135.8869 | 135.8869 | 135.8869 | 135.8869 | 135.8869 | 135.8869
97% | 156.5832 | 217.1095 | 232.8326 | 221.5981 | 223.6784 | 227.2724 | 235.4589 | 240.9325 | 247.8735 | 251.4725 | 254.6341 | 248.7798 | 255.624 | 266.3884 | 258.2061 | 258.2061 | 258.2061 | 258.2061 | 258.2061 | 258.2061 | 258.2061 | 258.2061 | 258.2061 | 258.2061 | 258.2061 | 258.2061 | 258.2061 | 258.2061 | 258.2061 | 258.2061 |  | 167.5944 | 227.3573 | 243.6946 | 232.3076 | 233.9022 | 237.4181 | 245.7328 | 250.265 | 258.9131 | 285.2168 | 263.5141 | 259.2636 | 264.9831 | 277.5007 | 269.0148 | 269.0148 | 269.0148 | 269.0148 | 269.0148 | 269.0148 | 269.0148 | 269.0148 | 269.0148 | 269.0148 | 269.0148 | 269.0148 | 269.0148 | 269.0148 | 269.0148 | 269.0148
95% | 462.5227 | 641.3081 | 687.7517 | 654.5667 | 660.7115 | 671.3276 | 695.5094 | 711.6775 | 732.1801 | 742.8112 | 752.1498 | 734.8573 | 755.074 | 786.8702 | 762.7012 | 762.7012 | 762.7012 | 762.7012 | 762.7012 | 762.7012 | 762.7012 | 762.7012 | 762.7012 | 762.7012 | 762.7012 | 762.7012 | 762.7012 | 762.7012 | 762.7012 | 762.7012 |  | 495.0481 | 671.5786 | 719.8364 | 686.201 | 690.9112 | 701.2967 | 725.8568 | 739.2442 | 764.7895 | 842.4866 | 778.3802 | 765.8248 | 782.7193 | 819.6944 | 794.6282 | 794.6282 | 794.6282 | 794.6282 | 794.6282 | 794.6282 | 794.6282 | 794.6282 | 794.6282 | 794.6282 | 794.6282 | 794.6282 | 794.6282 | 794.6282 | 794.6282 | 794.6282
90% | 2550.165 | 3535.9158 | 3791.9875 | 3609.0186 | 3642.8986 | 3701.4317 | 3834.7605 | 3923.9045 | 4036.9479 | 4095.5636 | 4147.053 | 4051.7086 | 4163.1759 | 4338.4873 | 4205.2289 | 4205.2289 | 4205.2289 | 4205.2289 | 4205.2289 | 4205.2289 | 4205.2289 | 4205.2289 | 4205.2289 | 4205.2289 | 4205.2289 | 4205.2289 | 4205.2289 | 4205.2289 | 4205.2289 | 4205.2289 |  | 2729.4971 | 3702.8155 | 3968.8899 | 3783.4376 | 3809.4078 | 3866.669 | 4002.0836 | 4075.8966 | 4216.7431 | 4645.134 | 4291.6768 | 4222.4513 | 4315.601 | 4519.4665 | 4381.2618 | 4381.2618 | 4381.2618 | 4381.2618 | 4381.2618 | 4381.2618 | 4381.2618 | 4381.2618 | 4381.2618 | 4381.2618 | 4381.2618 | 4381.2618 | 4381.2618 | 4381.2618 | 4381.2618 | 4381.2618
85% | 6229.8705 | 8637.9889 | 9263.5537 | 8816.574 | 8899.3403 | 9042.3325 | 9368.0453 | 9585.8176 | 9861.9745 | 10005.1684 | 10130.9534 | 9898.0339 | 10170.3404 | 10598.6136 | 10273.0729 | 10273.0729 | 10273.0729 | 10273.0729 | 10273.0729 | 10273.0729 | 10273.0729 | 10273.0729 | 10273.0729 | 10273.0729 | 10273.0729 | 10273.0729 | 10273.0729 | 10273.0729 | 10273.0729 | 10273.0729 |  | 6667.9659 | 9045.7131 | 9695.7136 | 9242.6671 | 9306.1104 | 9445.9955 | 9776.8035 | 9957.1235 | 10301.2013 | 11347.7295 | 10484.259 | 10315.146 | 10542.7042 | 11040.7328 | 10703.1086 | 10703.1086 | 10703.1086 | 10703.1086 | 10703.1086 | 10703.1086 | 10703.1086 | 10703.1086 | 10703.1086 | 10703.1086 | 10703.1086 | 10703.1086 | 10703.1086 | 10703.1086 | 10703.1086 | 10703.1086
80% | 9683.0656 | 13425.9956 | 14398.3087 | 13703.5697 | 13832.213 | 14054.4653 | 14560.7195 | 14899.2023 | 15328.432 | 15550.9978 | 15746.505 | 15384.479 | 15807.724 | 16473.3876 | 15967.4008 | 15967.4008 | 15967.4008 | 15967.4008 | 15967.4008 | 15967.4008 | 15967.4008 | 15967.4008 | 15967.4008 | 15967.4008 | 15967.4008 | 15967.4008 | 15967.4008 | 15967.4008 | 15967.4008 | 15967.4008 |  | 10363.9958 | 14059.7198 | 15070.0133 | 14365.8447 | 14464.4544 | 14681.8773 | 15196.0511 | 15476.3218 | 16011.1207 | 17637.7357 | 16295.6466 | 16032.7949 | 16386.4878 | 17160.5719 | 16635.8038 | 16635.8038 | 16635.8038 | 16635.8038 | 16635.8038 | 16635.8038 | 16635.8038 | 16635.8038 | 16635.8038 | 16635.8038 | 16635.8038 | 16635.8038 | 16635.8038 | 16635.8038 | 16635.8038 | 16635.8038
75% | 10683.1238 | 14812.6201 | 15885.3529 | 15118.8618 | 15260.7913 | 15505.9977 | 16064.5373 | 16437.9783 | 16911.5385 | 17157.0906 | 17372.7896 | 16973.3739 | 17440.3313 | 18174.744 | 17616.4994 | 17616.4994 | 17616.4994 | 17616.4994 | 17616.4994 | 17616.4994 | 17616.4994 | 17616.4994 | 17616.4994 | 17616.4994 | 17616.4994 | 17616.4994 | 17616.4994 | 17616.4994 | 17616.4994 | 17616.4994 |  | 11434.3798 | 15511.7948 | 16626.4305 | 15849.536 | 15958.33 | 16198.2082 | 16765.4853 | 17074.7021 | 17664.7346 | 19459.345 | 17978.6461 | 17688.6473 | 18078.8692 | 18932.9001 | 18353.9344 | 18353.9344 | 18353.9344 | 18353.9344 | 18353.9344 | 18353.9344 | 18353.9344 | 18353.9344 | 18353.9344 | 18353.9344 | 18353.9344 | 18353.9344 | 18353.9344 | 18353.9344 | 18353.9344 | 18353.9344
70% | 11478.4193 | 15915.3323 | 17067.9236 | 16244.3718 | 16396.8672 | 16660.3276 | 17260.4473 | 17661.6887 | 18170.5027 | 18434.3347 | 18666.0912 | 18236.9414 | 18738.661 | 19527.7464 | 18927.9438 | 18927.9438 | 18927.9438 | 18927.9438 | 18927.9438 | 18927.9438 | 18927.9438 | 18927.9438 | 18927.9438 | 18927.9438 | 18927.9438 | 18927.9438 | 18927.9438 | 18927.9438 | 18927.9438 | 18927.9438 |  | 12285.6019 | 16666.5563 | 17864.1701 | 17029.4404 | 17146.3335 | 17404.0691 | 18013.5767 | 18345.8129 | 18979.7698 | 20907.9783 | 19317.0501 | 19005.4627 | 19424.7343 | 20342.3427 | 19720.2765 | 19720.2765 | 19720.2765 | 19720.2765 | 19720.2765 | 19720.2765 | 19720.2765 | 19720.2765 | 19720.2765 | 19720.2765 | 19720.2765 | 19720.2765 | 19720.2765 | 19720.2765 | 19720.2765 | 19720.2765
65% | 12096.053 | 16771.7086 | 17986.3189 | 17118.4532 | 17279.1541 | 17556.7909 | 18189.2019 | 18612.0335 | 19148.2258 | 19426.2542 | 19670.4811 | 19218.2395 | 19746.9557 | 20578.5005 | 19946.4235 | 19946.4235 | 19946.4235 | 19946.4235 | 19946.4235 | 19946.4235 | 19946.4235 | 19946.4235 | 19946.4235 | 19946.4235 | 19946.4235 | 19946.4235 | 19946.4235 | 19946.4235 | 19946.4235 | 19946.4235 |  | 12946.6687 | 17563.3547 | 18825.4101 | 17945.7649 | 18068.9478 | 18340.5518 | 18982.856 | 19332.9692 | 20001.0382 | 22033.0003 | 20356.467 | 20028.1136 | 20469.9455 | 21436.9288 | 20781.3903 | 20781.3903 | 20781.3903 | 20781.3903 | 20781.3903 | 20781.3903 | 20781.3903 | 20781.3903 | 20781.3903 | 20781.3903 | 20781.3903 | 20781.3903 | 20781.3903 | 20781.3903 | 20781.3903 | 20781.3903
60% | 13316.2645 | 18463.5854 | 19800.7217 | 18845.3085 | 19022.2203 | 19327.8643 | 20024.0709 | 20489.5564 | 21079.8381 | 21385.9131 | 21654.7769 | 21156.9145 | 21738.966 | 22654.3944 | 21958.5555 | 21958.5555 | 21958.5555 | 21958.5555 | 21958.5555 | 21958.5555 | 21958.5555 | 21958.5555 | 21958.5555 | 21958.5555 | 21958.5555 | 21958.5555 | 21958.5555 | 21958.5555 | 21958.5555 | 21958.5555 |  | 14252.6876 | 19335.0902 | 20724.4577 | 19756.0768 | 19891.686 | 20190.6885 | 20897.7863 | 21283.2178 | 22018.6795 | 24255.6195 | 22409.9629 | 22048.4861 | 22534.8887 | 23599.4182 | 22877.751 | 22877.751 | 22877.751 | 22877.751 | 22877.751 | 22877.751 | 22877.751 | 22877.751 | 22877.751 | 22877.751 | 22877.751 | 22877.751 | 22877.751 | 22877.751 | 22877.751 | 22877.751
55% | 14813.5078 | 20539.579 | 22027.0592 | 20964.222 | 21161.0253 | 21501.035 | 22275.5211 | 22793.3445 | 23449.9958 | 23790.485 | 24089.579 | 23535.7385 | 24183.2342 | 25201.5907 | 24427.5136 | 24427.5136 | 24427.5136 | 24427.5136 | 24427.5136 | 24427.5136 | 24427.5136 | 24427.5136 | 24427.5136 | 24427.5136 | 24427.5136 | 24427.5136 | 24427.5136 | 24427.5136 | 24427.5136 | 24427.5136 |  | 15855.2197 | 21509.0734 | 23054.6574 | 21977.3945 | 22128.2512 | 22460.8727 | 23247.4745 | 23676.2429 | 24494.3979 | 26982.853 | 24929.676 | 24527.5559 | 25068.6481 | 26252.8704 | 25450.061 | 25450.061 | 25450.061 | 25450.061 | 25450.061 | 25450.061 | 25450.061 | 25450.061 | 25450.061 | 25450.061 | 25450.061 | 25450.061 | 25450.061 | 25450.061 | 25450.061 | 25450.061
50% | 15014.9247 | 20818.8523 | 22326.5575 | 21249.2691 | 21448.7483 | 21793.381 | 22578.3978 | 23103.2619 | 23768.8416 | 24113.9604 | 24417.1211 | 23855.7501 | 24512.0497 | 25544.2527 | 24759.6506 | 24759.6506 | 24759.6506 | 24759.6506 | 24759.6506 | 24759.6506 | 24759.6506 | 24759.6506 | 24759.6506 | 24759.6506 | 24759.6506 | 24759.6506 | 24759.6506 | 24759.6506 | 24759.6506 | 24759.6506 |  | 16070.8005 | 21801.5288 | 23368.1279 | 22276.2175 | 22429.1255 | 22766.2696 | 23563.5667 | 23998.165 | 24827.4442 | 27349.7345 | 25268.6408 | 24861.0531 | 25409.5025 | 26609.8264 | 25796.1013 | 25796.1013 | 25796.1013 | 25796.1013 | 25796.1013 | 25796.1013 | 25796.1013 | 25796.1013 | 25796.1013 | 25796.1013 | 25796.1013 | 25796.1013 | 25796.1013 | 25796.1013 | 25796.1013 | 25796.1013
45% | 11588.8305 | 16068.4223 | 17232.1005 | 16400.6269 | 16554.5891 | 16820.5838 | 17426.476 | 17831.577 | 18345.2853 | 18611.6551 | 18845.6409 | 18412.363 | 18918.9087 | 19715.5844 | 19110.0122 | 19110.0122 | 19110.0122 | 19110.0122 | 19110.0122 | 19110.0122 | 19110.0122 | 19110.0122 | 19110.0122 | 19110.0122 | 19110.0122 | 19110.0122 | 19110.0122 | 19110.0122 | 19110.0122 | 19110.0122 |  | 12403.7774 | 16826.8724 | 18036.0061 | 17193.247 | 17311.2645 | 17571.4794 | 18186.8498 | 18522.2818 | 19162.3367 | 21109.0927 | 19502.8614 | 19188.2768 | 19611.5814 | 20538.0163 | 19909.9664 | 19909.9664 | 19909.9664 | 19909.9664 | 19909.9664 | 19909.9664 | 19909.9664 | 19909.9664 | 19909.9664 | 19909.9664 | 19909.9664 | 19909.9664 | 19909.9664 | 19909.9664 | 19909.9664 | 19909.9664
40% | 5693.5395 | 7894.3425 | 8466.0523 | 8057.5531 | 8133.1941 | 8263.876 | 8561.5481 | 8760.5724 | 9012.9549 | 9143.8212 | 9258.7773 | 9045.9099 | 9294.7735 | 9686.1766 | 9388.6618 | 9388.6618 | 9388.6618 | 9388.6618 | 9388.6618 | 9388.6618 | 9388.6618 | 9388.6618 | 9388.6618 | 9388.6618 | 9388.6618 | 9388.6618 | 9388.6618 | 9388.6618 | 9388.6618 | 9388.6618 |  | 6093.9192 | 8266.9656 | 8861.0075 | 8446.9638 | 8504.9452 | 8632.7876 | 8935.1163 | 9099.9125 | 9414.3686 | 10370.8009 | 9581.6668 | 9427.1128 | 9635.0804 | 10090.2336 | 9781.6756 | 9781.6756 | 9781.6756 | 9781.6756 | 9781.6756 | 9781.6756 | 9781.6756 | 9781.6756 | 9781.6756 | 9781.6756 | 9781.6756 | 9781.6756 | 9781.6756 | 9781.6756 | 9781.6756 | 9781.6756
35% | 2127.9257 | 2950.4624 | 3164.1354 | 3011.4614 | 3039.7317 | 3088.5733 | 3199.8264 | 3274.2105 | 3368.5369 | 3417.4474 | 3460.4116 | 3380.8537 | 3473.8649 | 3620.1495 | 3508.9551 | 3508.9551 | 3508.9551 | 3508.9551 | 3508.9551 | 3508.9551 | 3508.9551 | 3508.9551 | 3508.9551 | 3508.9551 | 3508.9551 | 3508.9551 | 3508.9551 | 3508.9551 | 3508.9551 | 3508.9551 |  | 2277.5652 | 3089.728 | 3311.7475 | 3157.0012 | 3178.6714 | 3226.4517 | 3339.4452 | 3401.0368 | 3518.5629 | 3876.0236 | 3581.0895 | 3523.3259 | 3601.0526 | 3771.1633 | 3655.8416 | 3655.8416 | 3655.8416 | 3655.8416 | 3655.8416 | 3655.8416 | 3655.8416 | 3655.8416 | 3655.8416 | 3655.8416 | 3655.8416 | 3655.8416 | 3655.8416 | 3655.8416 | 3655.8416 | 3655.8416
30% | 1061.2862 | 1471.5199 | 1578.0877 | 1501.9427 | 1516.0423 | 1540.4016 | 1595.8883 | 1632.9868 | 1680.0313 | 1704.425 | 1725.8531 | 1686.1742 | 1732.5628 | 1805.5211 | 1750.0638 | 1750.0638 | 1750.0638 | 1750.0638 | 1750.0638 | 1750.0638 | 1750.0638 | 1750.0638 | 1750.0638 | 1750.0638 | 1750.0638 | 1750.0638 | 1750.0638 | 1750.0638 | 1750.0638 | 1750.0638 |  | 1135.9177 | 1540.9775 | 1651.708 | 1574.5295 | 1585.3374 | 1609.1674 | 1665.5221 | 1696.2404 | 1754.8556 | 1933.1363 | 1786.0403 | 1757.2311 | 1795.9967 | 1880.8381 | 1823.3223 | 1823.3223 | 1823.3223 | 1823.3223 | 1823.3223 | 1823.3223 | 1823.3223 | 1823.3223 | 1823.3223 | 1823.3223 | 1823.3223 | 1823.3223 | 1823.3223 | 1823.3223 | 1823.3223 | 1823.3223
25% | 625.6637 | 867.5102 | 930.3354 | 885.4454 | 893.7576 | 908.1182 | 940.8295 | 962.7003 | 990.4346 | 1004.8155 | 1017.4481 | 994.056 | 1021.4037 | 1064.415 | 1031.7211 | 1031.7211 | 1031.7211 | 1031.7211 | 1031.7211 | 1031.7211 | 1031.7211 | 1031.7211 | 1031.7211 | 1031.7211 | 1031.7211 | 1031.7211 | 1031.7211 | 1031.7211 | 1031.7211 | 1031.7211 |  | 669.6615 | 908.4578 | 973.7371 | 928.2378 | 934.6094 | 948.658 | 981.8809 | 999.9904 | 1034.546 | 1139.6485 | 1052.9304 | 1035.9465 | 1058.8 | 1108.8169 | 1074.9094 | 1074.9094 | 1074.9094 | 1074.9094 | 1074.9094 | 1074.9094 | 1074.9094 | 1074.9094 | 1074.9094 | 1074.9094 | 1074.9094 | 1074.9094 | 1074.9094 | 1074.9094 | 1074.9094 | 1074.9094
20% | 316.1776 | 438.3942 | 470.1428 | 447.4577 | 451.6582 | 458.9154 | 475.4459 | 486.4983 | 500.5137 | 507.7811 | 514.1649 | 502.3438 | 516.1639 | 537.8996 | 521.3778 | 521.3778 | 521.3778 | 521.3778 | 521.3778 | 521.3778 | 521.3778 | 521.3778 | 521.3778 | 521.3778 | 521.3778 | 521.3778 | 521.3778 | 521.3778 | 521.3778 | 521.3778 |  | 338.4118 | 459.0869 | 492.0757 | 469.0827 | 472.3026 | 479.402 | 496.1912 | 505.3427 | 522.8053 | 575.9186 | 532.0959 | 523.5131 | 535.0621 | 560.3379 | 543.2029 | 543.2029 | 543.2029 | 543.2029 | 543.2029 | 543.2029 | 543.2029 | 543.2029 | 543.2029 | 543.2029 | 543.2029 | 543.2029 | 543.2029 | 543.2029 | 543.2029 | 543.2029
15% | 128.8131 | 178.605 | 191.5396 | 182.2976 | 184.0089 | 186.9655 | 193.7002 | 198.203 | 203.913 | 206.8738 | 209.4746 | 204.6586 | 210.289 | 219.1443 | 212.4132 | 212.4132 | 212.4132 | 212.4132 | 212.4132 | 212.4132 | 212.4132 | 212.4132 | 212.4132 | 212.4132 | 212.4132 | 212.4132 | 212.4132 | 212.4132 | 212.4132 | 212.4132 |  | 137.8715 | 187.0354 | 200.4753 | 191.1078 | 192.4196 | 195.3119 | 202.152 | 205.8804 | 212.9948 | 234.6335 | 216.7798 | 213.2831 | 217.9882 | 228.2858 | 221.3049 | 221.3049 | 221.3049 | 221.3049 | 221.3049 | 221.3049 | 221.3049 | 221.3049 | 221.3049 | 221.3049 | 221.3049 | 221.3049 | 221.3049 | 221.3049 | 221.3049 | 221.3049
10% | 51.8598 | 71.9059 | 77.1134 | 73.3925 | 74.0815 | 75.2718 | 77.9832 | 79.796 | 82.0948 | 83.2868 | 84.3339 | 82.395 | 84.6618 | 88.2269 | 85.517 | 85.517 | 85.517 | 85.517 | 85.517 | 85.517 | 85.517 | 85.517 | 85.517 | 85.517 | 85.517 | 85.517 | 85.517 | 85.517 | 85.517 | 85.517 |  | 55.5067 | 75.3 | 80.7108 | 76.9395 | 77.4676 | 78.6321 | 81.3859 | 82.8869 | 85.7511 | 94.4628 | 87.275 | 85.8672 | 87.7615 | 91.9073 | 89.0968 | 89.0968 | 89.0968 | 89.0968 | 89.0968 | 89.0968 | 89.0968 | 89.0968 | 89.0968 | 89.0968 | 89.0968 | 89.0968 | 89.0968 | 89.0968 | 89.0968 | 89.0968
5% | 44.1645 | 61.236 | 65.6707 | 62.502 | 63.0888 | 64.1025 | 66.4115 | 67.9553 | 69.913 | 70.9282 | 71.8199 | 70.1687 | 72.0991 | 75.1352 | 72.8274 | 72.8274 | 72.8274 | 72.8274 | 72.8274 | 72.8274 | 72.8274 | 72.8274 | 72.8274 | 72.8274 | 72.8274 | 72.8274 | 72.8274 | 72.8274 | 72.8274 | 72.8274 |  | 47.2702 | 64.1264 | 68.7344 | 65.5227 | 65.9724 | 66.9641 | 69.3092 | 70.5876 | 73.0268 | 80.4458 | 74.3245 | 73.1256 | 74.7388 | 78.2694 | 75.876 | 75.876 | 75.876 | 75.876 | 75.876 | 75.876 | 75.876 | 75.876 | 75.876 | 75.876 | 75.876 | 75.876 | 75.876 | 75.876 | 75.876 | 75.876
9.992e-14% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E @ R (MWh) | 118268.4368 | 163984.3799 | 175860.1598 | 167374.6549 | 168945.8978 | 171660.4752 | 177843.8364 | 181978.0466 | 187220.6353 | 189939.041 | 192326.9551 | 187905.1896 | 193074.6811 | 201205.0605 | 195024.9655 | 195024.9655 | 195024.9655 | 195024.9655 | 195024.9655 | 195024.9655 | 195024.9655 | 195024.9655 | 195024.9655 | 195024.9655 | 195024.9655 | 195024.9655 | 195024.9655 | 195024.9655 | 195024.9655 | 195024.9655 | E @ R (MWh) | 126585.2808 | 171724.6525 | 184064.3234 | 175463.6456 | 176668.0593 | 179323.6509 | 185603.7413 | 189026.9524 | 195558.9574 | 215426.3451 | 199034.1414 | 195823.6851 | 200143.6704 | 209598.2919 | 203188.8031 | 203188.8031 | 203188.8031 | 203188.8031 | 203188.8031 | 203188.8031 | 203188.8031 | 203188.8031 | 203188.8031 | 203188.8031 | 203188.8031 | 203188.8031 | 203188.8031 | 203188.8031 | 203188.8031 | 203188.8031
Option 4 Winter POE50 W E @ R (MWh) N 2 | 82787.9057 | 114789.066 | 123102.1118 | 117162.2584 | 118262.1284 | 120162.3326 | 124490.6855 | 127384.6326 | 131054.4447 | 132957.3287 | 134628.8686 | 131533.6327 | 135152.2768 | 140843.5423 | 136517.4758 | 136517.4758 | 136517.4758 | 136517.4758 | 136517.4758 | 136517.4758 | 136517.4758 | 136517.4758 | 136517.4758 | 136517.4758 | 136517.4758 | 136517.4758 | 136517.4758 | 136517.4758 | 136517.4758 | 136517.4758 | Option 4 Winter POE10 W E @ R (MWh) N 2 | 37975.5842 | 51517.3957 | 55219.297 | 52639.0937 | 53000.4178 | 53797.0953 | 55681.1224 | 56708.0857 | 58667.6872 | 64627.9035 | 59710.2424 | 58747.1055 | 60043.1011 | 62879.4876 | 60956.6409 | 60956.6409 | 60956.6409 | 60956.6409 | 60956.6409 | 60956.6409 | 60956.6409 | 60956.6409 | 60956.6409 | 60956.6409 | 60956.6409 | 60956.6409 | 60956.6409 | 60956.6409 | 60956.6409 | 60956.6409
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 85.8327 | 111.1071 | 117.7202 | 111.3029 | 111.3309 | 112.009 | 113.7994 | 114.9971 | 116.1701 | 117.5422 | 118.813 | 120.0472 | 120.1872 | 121.628 | 120.534 | 120.534 | 120.534 | 120.534 | 120.534 | 120.534 | 120.534 | 120.534 | 120.534 | 120.534 | 120.534 | 120.534 | 120.534 | 120.534 | 120.534 | 120.534
98% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 42.4851 | 54.9952 | 58.2686 | 55.0921 | 55.106 | 55.4416 | 56.3278 | 56.9207 | 57.5013 | 58.1804 | 58.8094 | 59.4204 | 59.4897 | 60.2028 | 59.6613 | 59.6613 | 59.6613 | 59.6613 | 59.6613 | 59.6613 | 59.6613 | 59.6613 | 59.6613 | 59.6613 | 59.6613 | 59.6613 | 59.6613 | 59.6613 | 59.6613 | 59.6613
97% | 18.864 | 25.0432 | 26.7251 | 25.2013 | 25.1995 | 25.3912 | 25.6015 | 26.0334 | 26.3437 | 26.512 | 26.6961 | 26.8646 | 27.1691 | 27.5471 | 27.5207 | 27.5207 | 27.5207 | 27.5207 | 27.5207 | 27.5207 | 27.5207 | 27.5207 | 27.5207 | 27.5207 | 27.5207 | 27.5207 | 27.5207 | 27.5207 | 27.5207 | 27.5207 |  | 84.1075 | 108.8738 | 115.354 | 109.0657 | 109.0931 | 109.7575 | 111.512 | 112.6856 | 113.835 | 115.1795 | 116.4248 | 117.6342 | 117.7714 | 119.1832 | 118.1112 | 118.1112 | 118.1112 | 118.1112 | 118.1112 | 118.1112 | 118.1112 | 118.1112 | 118.1112 | 118.1112 | 118.1112 | 118.1112 | 118.1112 | 118.1112 | 118.1112 | 118.1112
95% | 92.8689 | 123.2894 | 131.5698 | 124.0679 | 124.059 | 125.0027 | 126.0382 | 128.1643 | 129.6921 | 130.5208 | 131.4271 | 132.2567 | 133.7558 | 135.6165 | 135.4864 | 135.4864 | 135.4864 | 135.4864 | 135.4864 | 135.4864 | 135.4864 | 135.4864 | 135.4864 | 135.4864 | 135.4864 | 135.4864 | 135.4864 | 135.4864 | 135.4864 | 135.4864 |  | 124.2203 | 160.7982 | 170.369 | 161.0816 | 161.1222 | 162.1034 | 164.6946 | 166.4279 | 168.1256 | 170.1113 | 171.9504 | 173.7367 | 173.9393 | 176.0244 | 174.4412 | 174.4412 | 174.4412 | 174.4412 | 174.4412 | 174.4412 | 174.4412 | 174.4412 | 174.4412 | 174.4412 | 174.4412 | 174.4412 | 174.4412 | 174.4412 | 174.4412 | 174.4412
90% | 161.0694 | 213.8301 | 228.1913 | 215.1802 | 215.1648 | 216.8015 | 218.5976 | 222.285 | 224.9347 | 226.372 | 227.9438 | 229.3827 | 231.9827 | 235.2099 | 234.9843 | 234.9843 | 234.9843 | 234.9843 | 234.9843 | 234.9843 | 234.9843 | 234.9843 | 234.9843 | 234.9843 | 234.9843 | 234.9843 | 234.9843 | 234.9843 | 234.9843 | 234.9843 |  | 538.6113 | 697.2109 | 738.7092 | 698.4397 | 698.6156 | 702.8702 | 714.1054 | 721.621 | 728.982 | 737.592 | 745.5662 | 753.3113 | 754.19 | 763.2307 | 756.3662 | 756.3662 | 756.3662 | 756.3662 | 756.3662 | 756.3662 | 756.3662 | 756.3662 | 756.3662 | 756.3662 | 756.3662 | 756.3662 | 756.3662 | 756.3662 | 756.3662 | 756.3662
85% | 457.0889 | 606.8151 | 647.57 | 610.6465 | 610.6028 | 615.2475 | 620.3445 | 630.8087 | 638.3281 | 642.4071 | 646.8675 | 650.9508 | 658.3294 | 667.4874 | 666.8473 | 666.8473 | 666.8473 | 666.8473 | 666.8473 | 666.8473 | 666.8473 | 666.8473 | 666.8473 | 666.8473 | 666.8473 | 666.8473 | 666.8473 | 666.8473 | 666.8473 | 666.8473 |  | 509.4971 | 659.5238 | 698.779 | 660.6862 | 660.8526 | 664.8772 | 675.5051 | 682.6144 | 689.5775 | 697.7221 | 705.2653 | 712.5918 | 713.423 | 721.975 | 715.4815 | 715.4815 | 715.4815 | 715.4815 | 715.4815 | 715.4815 | 715.4815 | 715.4815 | 715.4815 | 715.4815 | 715.4815 | 715.4815 | 715.4815 | 715.4815 | 715.4815 | 715.4815
80% | 638.4734 | 847.6148 | 904.5422 | 852.9665 | 852.9054 | 859.3934 | 866.5129 | 881.1296 | 891.6329 | 897.3305 | 903.561 | 909.2647 | 919.5712 | 932.3634 | 931.4692 | 931.4692 | 931.4692 | 931.4692 | 931.4692 | 931.4692 | 931.4692 | 931.4692 | 931.4692 | 931.4692 | 931.4692 | 931.4692 | 931.4692 | 931.4692 | 931.4692 | 931.4692 |  | 355.8393 | 460.6198 | 488.0361 | 461.4317 | 461.5478 | 464.3587 | 471.7813 | 476.7466 | 481.6097 | 487.298 | 492.5663 | 497.6831 | 498.2637 | 504.2365 | 499.7014 | 499.7014 | 499.7014 | 499.7014 | 499.7014 | 499.7014 | 499.7014 | 499.7014 | 499.7014 | 499.7014 | 499.7014 | 499.7014 | 499.7014 | 499.7014 | 499.7014 | 499.7014
75% | 1664.3841 | 2209.5776 | 2357.9769 | 2223.5287 | 2223.3694 | 2240.2823 | 2258.8417 | 2296.9446 | 2324.3247 | 2339.1775 | 2355.4192 | 2370.2877 | 2397.1549 | 2430.5018 | 2428.1709 | 2428.1709 | 2428.1709 | 2428.1709 | 2428.1709 | 2428.1709 | 2428.1709 | 2428.1709 | 2428.1709 | 2428.1709 | 2428.1709 | 2428.1709 | 2428.1709 | 2428.1709 | 2428.1709 | 2428.1709 |  | 635.1192 | 822.1366 | 871.0705 | 823.5856 | 823.793 | 828.8099 | 842.0582 | 850.9204 | 859.6003 | 869.7531 | 879.1562 | 888.289 | 889.3252 | 899.9858 | 891.8912 | 891.8912 | 891.8912 | 891.8912 | 891.8912 | 891.8912 | 891.8912 | 891.8912 | 891.8912 | 891.8912 | 891.8912 | 891.8912 | 891.8912 | 891.8912 | 891.8912 | 891.8912
70% | 2875.5487 | 3817.4772 | 4073.866 | 3841.5804 | 3841.3052 | 3870.5256 | 3902.5905 | 3968.4207 | 4015.7253 | 4041.3863 | 4069.447 | 4095.1352 | 4141.5536 | 4199.1669 | 4195.1398 | 4195.1398 | 4195.1398 | 4195.1398 | 4195.1398 | 4195.1398 | 4195.1398 | 4195.1398 | 4195.1398 | 4195.1398 | 4195.1398 | 4195.1398 | 4195.1398 | 4195.1398 | 4195.1398 | 4195.1398 |  | 1157.0168 | 1497.7123 | 1586.8569 | 1500.352 | 1500.7298 | 1509.8694 | 1534.0041 | 1550.1488 | 1565.9612 | 1584.4568 | 1601.5867 | 1618.2243 | 1620.1119 | 1639.5327 | 1624.7866 | 1624.7866 | 1624.7866 | 1624.7866 | 1624.7866 | 1624.7866 | 1624.7866 | 1624.7866 | 1624.7866 | 1624.7866 | 1624.7866 | 1624.7866 | 1624.7866 | 1624.7866 | 1624.7866 | 1624.7866
65% | 7222.0048 | 9587.679 | 10231.6052 | 9648.2147 | 9647.5235 | 9720.9112 | 9801.443 | 9966.777 | 10085.5835 | 10150.0318 | 10220.507 | 10285.0233 | 10401.6042 | 10546.3011 | 10536.1871 | 10536.1871 | 10536.1871 | 10536.1871 | 10536.1871 | 10536.1871 | 10536.1871 | 10536.1871 | 10536.1871 | 10536.1871 | 10536.1871 | 10536.1871 | 10536.1871 | 10536.1871 | 10536.1871 | 10536.1871 |  | 1455.7061 | 1884.3537 | 1996.5114 | 1887.6749 | 1888.1503 | 1899.6493 | 1930.0145 | 1950.327 | 1970.2215 | 1993.4918 | 2015.0438 | 2035.9765 | 2038.3514 | 2062.7858 | 2044.2329 | 2044.2329 | 2044.2329 | 2044.2329 | 2044.2329 | 2044.2329 | 2044.2329 | 2044.2329 | 2044.2329 | 2044.2329 | 2044.2329 | 2044.2329 | 2044.2329 | 2044.2329 | 2044.2329 | 2044.2329
60% | 10556.5772 | 14014.5398 | 14955.7822 | 14103.0263 | 14102.016 | 14209.2885 | 14327.0037 | 14568.6765 | 14742.3387 | 14836.5444 | 14939.5596 | 15033.8647 | 15204.2738 | 15415.7807 | 15400.9968 | 15400.9968 | 15400.9968 | 15400.9968 | 15400.9968 | 15400.9968 | 15400.9968 | 15400.9968 | 15400.9968 | 15400.9968 | 15400.9968 | 15400.9968 | 15400.9968 | 15400.9968 | 15400.9968 | 15400.9968 |  | 2277.9105 | 2948.6646 | 3124.1707 | 2953.8617 | 2954.6055 | 2972.5993 | 3020.1153 | 3051.9005 | 3083.0318 | 3119.4455 | 3153.1704 | 3185.9262 | 3189.6425 | 3227.8777 | 3198.8459 | 3198.8459 | 3198.8459 | 3198.8459 | 3198.8459 | 3198.8459 | 3198.8459 | 3198.8459 | 3198.8459 | 3198.8459 | 3198.8459 | 3198.8459 | 3198.8459 | 3198.8459 | 3198.8459 | 3198.8459
55% | 11937.0341 | 15847.1857 | 16911.512 | 15947.2433 | 15946.1009 | 16067.4012 | 16200.5098 | 16473.7855 | 16670.1571 | 16776.6818 | 16893.168 | 16999.8051 | 17192.4982 | 17431.6634 | 17414.9461 | 17414.9461 | 17414.9461 | 17414.9461 | 17414.9461 | 17414.9461 | 17414.9461 | 17414.9461 | 17414.9461 | 17414.9461 | 17414.9461 | 17414.9461 | 17414.9461 | 17414.9461 | 17414.9461 | 17414.9461 |  | 4377.3623 | 5666.3214 | 6003.5838 | 5676.3085 | 5677.7378 | 5712.3157 | 5803.6251 | 5864.7054 | 5924.5291 | 5994.5036 | 6059.3114 | 6122.2568 | 6129.3982 | 6202.8732 | 6147.084 | 6147.084 | 6147.084 | 6147.084 | 6147.084 | 6147.084 | 6147.084 | 6147.084 | 6147.084 | 6147.084 | 6147.084 | 6147.084 | 6147.084 | 6147.084 | 6147.084 | 6147.084
50% | 15327.7148 | 20348.5339 | 21715.179 | 20477.0126 | 20475.5457 | 20631.301 | 20802.2186 | 21153.1175 | 21405.2679 | 21542.0507 | 21691.6245 | 21828.5515 | 22075.9786 | 22383.0779 | 22361.6122 | 22361.6122 | 22361.6122 | 22361.6122 | 22361.6122 | 22361.6122 | 22361.6122 | 22361.6122 | 22361.6122 | 22361.6122 | 22361.6122 | 22361.6122 | 22361.6122 | 22361.6122 | 22361.6122 | 22361.6122 |  | 9714.4123 | 12574.9205 | 13323.3863 | 12597.0842 | 12600.2561 | 12676.9929 | 12879.6302 | 13015.182 | 13147.9449 | 13303.2352 | 13447.0592 | 13586.7499 | 13602.5984 | 13765.657 | 13641.8476 | 13641.8476 | 13641.8476 | 13641.8476 | 13641.8476 | 13641.8476 | 13641.8476 | 13641.8476 | 13641.8476 | 13641.8476 | 13641.8476 | 13641.8476 | 13641.8476 | 13641.8476 | 13641.8476 | 13641.8476
45% | 20411.3174 | 27097.3455 | 28917.2533 | 27268.4356 | 27266.4822 | 27473.8954 | 27701.4997 | 28168.778 | 28504.5568 | 28686.7051 | 28885.8866 | 29068.227 | 29397.716 | 29806.6681 | 29778.0831 | 29778.0831 | 29778.0831 | 29778.0831 | 29778.0831 | 29778.0831 | 29778.0831 | 29778.0831 | 29778.0831 | 29778.0831 | 29778.0831 | 29778.0831 | 29778.0831 | 29778.0831 | 29778.0831 | 29778.0831 |  | 14720.4239 | 19055.0036 | 20189.1672 | 19088.5886 | 19093.3951 | 19209.6757 | 19516.7357 | 19722.1398 | 19923.3178 | 20158.632 | 20376.571 | 20588.2469 | 20612.2624 | 20859.3481 | 20671.7374 | 20671.7374 | 20671.7374 | 20671.7374 | 20671.7374 | 20671.7374 | 20671.7374 | 20671.7374 | 20671.7374 | 20671.7374 | 20671.7374 | 20671.7374 | 20671.7374 | 20671.7374 | 20671.7374 | 20671.7374
40% | 14315.8312 | 19005.1929 | 20281.6168 | 19125.1899 | 19123.8198 | 19269.2927 | 19428.9269 | 19756.6606 | 19992.1649 | 20119.9178 | 20259.6172 | 20387.5048 | 20618.5976 | 20905.4233 | 20885.3746 | 20885.3746 | 20885.3746 | 20885.3746 | 20885.3746 | 20885.3746 | 20885.3746 | 20885.3746 | 20885.3746 | 20885.3746 | 20885.3746 | 20885.3746 | 20885.3746 | 20885.3746 | 20885.3746 | 20885.3746 |  | 15242.3215 | 19730.5793 | 20904.9535 | 19765.355 | 19770.332 | 19890.7351 | 20208.6817 | 20421.3681 | 20629.6787 | 20873.3357 | 21099.0016 | 21318.1822 | 21343.0492 | 21598.895 | 21404.6327 | 21404.6327 | 21404.6327 | 21404.6327 | 21404.6327 | 21404.6327 | 21404.6327 | 21404.6327 | 21404.6327 | 21404.6327 | 21404.6327 | 21404.6327 | 21404.6327 | 21404.6327 | 21404.6327 | 21404.6327
35% | 7422.2532 | 9853.5218 | 10515.3025 | 9915.736 | 9915.0257 | 9990.4482 | 10073.2129 | 10243.1313 | 10365.232 | 10431.4673 | 10503.8965 | 10570.2018 | 10690.0152 | 10838.7242 | 10828.3297 | 10828.3297 | 10828.3297 | 10828.3297 | 10828.3297 | 10828.3297 | 10828.3297 | 10828.3297 | 10828.3297 | 10828.3297 | 10828.3297 | 10828.3297 | 10828.3297 | 10828.3297 | 10828.3297 | 10828.3297 |  | 20759.9869 | 26872.9779 | 28472.4713 | 26920.3422 | 26927.1208 | 27091.1095 | 27524.1515 | 27813.8297 | 28097.5479 | 28429.4079 | 28736.764 | 29035.2872 | 29069.156 | 29417.617 | 29153.0326 | 29153.0326 | 29153.0326 | 29153.0326 | 29153.0326 | 29153.0326 | 29153.0326 | 29153.0326 | 29153.0326 | 29153.0326 | 29153.0326 | 29153.0326 | 29153.0326 | 29153.0326 | 29153.0326 | 29153.0326
30% | 3452.1096 | 4582.899 | 4890.695 | 4611.835 | 4611.5046 | 4646.5838 | 4685.0779 | 4764.1074 | 4820.8968 | 4851.703 | 4885.39 | 4916.2287 | 4971.9543 | 5041.1192 | 5036.2847 | 5036.2847 | 5036.2847 | 5036.2847 | 5036.2847 | 5036.2847 | 5036.2847 | 5036.2847 | 5036.2847 | 5036.2847 | 5036.2847 | 5036.2847 | 5036.2847 | 5036.2847 | 5036.2847 | 5036.2847 |  | 19183.5111 | 24832.2926 | 26310.3234 | 24876.0601 | 24882.324 | 25033.8597 | 25434.0173 | 25701.6978 | 25963.871 | 26270.5302 | 26554.5462 | 26830.4001 | 26861.6969 | 27183.6965 | 26939.204 | 26939.204 | 26939.204 | 26939.204 | 26939.204 | 26939.204 | 26939.204 | 26939.204 | 26939.204 | 26939.204 | 26939.204 | 26939.204 | 26939.204 | 26939.204 | 26939.204 | 26939.204
25% | 2357.031 | 3129.1112 | 3339.2681 | 3148.8681 | 3148.6426 | 3172.594 | 3198.8769 | 3252.8367 | 3291.6113 | 3312.6452 | 3335.646 | 3356.7021 | 3394.7503 | 3441.9748 | 3438.6739 | 3438.6739 | 3438.6739 | 3438.6739 | 3438.6739 | 3438.6739 | 3438.6739 | 3438.6739 | 3438.6739 | 3438.6739 | 3438.6739 | 3438.6739 | 3438.6739 | 3438.6739 | 3438.6739 | 3438.6739 |  | 5533.3008 | 7162.6379 | 7588.9618 | 7175.2622 | 7177.069 | 7220.778 | 7336.1996 | 7413.4095 | 7489.0309 | 7577.4838 | 7659.4055 | 7738.9729 | 7748.0002 | 7840.8779 | 7770.3564 | 7770.3564 | 7770.3564 | 7770.3564 | 7770.3564 | 7770.3564 | 7770.3564 | 7770.3564 | 7770.3564 | 7770.3564 | 7770.3564 | 7770.3564 | 7770.3564 | 7770.3564 | 7770.3564 | 7770.3564
20% | 1427.8587 | 1895.5749 | 2022.8852 | 1907.5433 | 1907.4067 | 1921.9161 | 1937.838 | 1970.5261 | 1994.0153 | 2006.7574 | 2020.6909 | 2033.4464 | 2056.4956 | 2085.1035 | 2083.1039 | 2083.1039 | 2083.1039 | 2083.1039 | 2083.1039 | 2083.1039 | 2083.1039 | 2083.1039 | 2083.1039 | 2083.1039 | 2083.1039 | 2083.1039 | 2083.1039 | 2083.1039 | 2083.1039 | 2083.1039 |  | 1484.8203 | 1922.0408 | 2036.4417 | 1925.4284 | 1925.9133 | 1937.6423 | 1968.6148 | 1989.3335 | 2009.6259 | 2033.3616 | 2055.3447 | 2076.696 | 2079.1184 | 2104.0415 | 2085.1176 | 2085.1176 | 2085.1176 | 2085.1176 | 2085.1176 | 2085.1176 | 2085.1176 | 2085.1176 | 2085.1176 | 2085.1176 | 2085.1176 | 2085.1176 | 2085.1176 | 2085.1176 | 2085.1176 | 2085.1176
15% | 914.1778 | 1213.6303 | 1295.1399 | 1221.293 | 1221.2055 | 1230.4951 | 1240.689 | 1261.6173 | 1276.6561 | 1284.8142 | 1293.7351 | 1301.9017 | 1316.6588 | 1334.9748 | 1333.6946 | 1333.6946 | 1333.6946 | 1333.6946 | 1333.6946 | 1333.6946 | 1333.6946 | 1333.6946 | 1333.6946 | 1333.6946 | 1333.6946 | 1333.6946 | 1333.6946 | 1333.6946 | 1333.6946 | 1333.6946 |  | 818.9695 | 1060.1234 | 1123.2225 | 1061.9919 | 1062.2594 | 1068.7286 | 1085.8119 | 1097.2395 | 1108.432 | 1121.5237 | 1133.6487 | 1145.4253 | 1146.7614 | 1160.508 | 1150.0703 | 1150.0703 | 1150.0703 | 1150.0703 | 1150.0703 | 1150.0703 | 1150.0703 | 1150.0703 | 1150.0703 | 1150.0703 | 1150.0703 | 1150.0703 | 1150.0703 | 1150.0703 | 1150.0703 | 1150.0703
10% | 611.8703 | 812.2975 | 866.8529 | 817.4263 | 817.3677 | 823.5853 | 830.4082 | 844.4158 | 854.4815 | 859.9418 | 865.9126 | 871.3786 | 881.2557 | 893.5149 | 892.658 | 892.658 | 892.658 | 892.658 | 892.658 | 892.658 | 892.658 | 892.658 | 892.658 | 892.658 | 892.658 | 892.658 | 892.658 | 892.658 | 892.658 | 892.658 |  | 191.3984 | 247.7576 | 262.5043 | 248.1943 | 248.2568 | 249.7687 | 253.7612 | 256.4319 | 259.0476 | 262.1073 | 264.9409 | 267.6932 | 268.0055 | 271.2181 | 268.7788 | 268.7788 | 268.7788 | 268.7788 | 268.7788 | 268.7788 | 268.7788 | 268.7788 | 268.7788 | 268.7788 | 268.7788 | 268.7788 | 268.7788 | 268.7788 | 268.7788 | 268.7788
5% | 435.3228 | 577.9192 | 616.7333 | 581.5681 | 581.5264 | 585.95 | 590.8043 | 600.7702 | 607.9315 | 611.8163 | 616.0643 | 619.9532 | 626.9804 | 635.7023 | 635.0927 | 635.0927 | 635.0927 | 635.0927 | 635.0927 | 635.0927 | 635.0927 | 635.0927 | 635.0927 | 635.0927 | 635.0927 | 635.0927 | 635.0927 | 635.0927 | 635.0927 | 635.0927 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9.992e-14% | 38.2117 | 50.7285 | 54.1355 | 51.0488 | 51.0451 | 51.4334 | 51.8595 | 52.7343 | 53.3629 | 53.7039 | 54.0768 | 54.4181 | 55.0349 | 55.8005 | 55.747 | 55.747 | 55.747 | 55.747 | 55.747 | 55.747 | 55.747 | 55.747 | 55.747 | 55.747 | 55.747 | 55.747 | 55.747 | 55.747 | 55.747 | 55.747 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E @ R (MWh) | 102337.6118 | 135859.8063 | 144984.402 | 136717.6124 | 136707.8185 | 137747.7403 | 138888.8955 | 141231.7205 | 142915.2376 | 143828.4869 | 144827.1369 | 145741.3494 | 147393.3305 | 149443.7218 | 149300.4029 | 149300.4029 | 149300.4029 | 149300.4029 | 149300.4029 | 149300.4029 | 149300.4029 | 149300.4029 | 149300.4029 | 149300.4029 | 149300.4029 | 149300.4029 | 149300.4029 | 149300.4029 | 149300.4029 | 149300.4029 | E @ R (MWh) | 99292.8528 | 128530.651 | 136180.8614 | 128757.1897 | 128789.611 | 129573.9518 | 131645.1467 | 133030.6471 | 134387.6419 | 135974.8937 | 137444.9459 | 138872.7513 | 139034.7419 | 140701.3949 | 139435.9149 | 139435.9149 | 139435.9149 | 139435.9149 | 139435.9149 | 139435.9149 | 139435.9149 | 139435.9149 | 139435.9149 | 139435.9149 | 139435.9149 | 139435.9149 | 139435.9149 | 139435.9149 | 139435.9149 | 139435.9149
Option 4 Summer POE50 W E @ R (MWh) N 2 | 71636.3283 | 95101.8644 | 101489.0814 | 95702.3287 | 95695.4729 | 96423.4182 | 97222.2268 | 98862.2044 | 100040.6663 | 100679.9408 | 101378.9959 | 102018.9446 | 103175.3313 | 104610.6052 | 104510.282 | 104510.282 | 104510.282 | 104510.282 | 104510.282 | 104510.282 | 104510.282 | 104510.282 | 104510.282 | 104510.282 | 104510.282 | 104510.282 | 104510.282 | 104510.282 | 104510.282 | 104510.282 | Option 4 Summer POE10 W E @ R (MWh) N 2 | 29787.8558 | 38559.1953 | 40854.2584 | 38627.1569 | 38636.8833 | 38872.1855 | 39493.544 | 39909.1941 | 40316.2926 | 40792.4681 | 41233.4838 | 41661.8254 | 41710.4226 | 42210.4185 | 41830.7745 | 41830.7745 | 41830.7745 | 41830.7745 | 41830.7745 | 41830.7745 | 41830.7745 | 41830.7745 | 41830.7745 | 41830.7745 | 41830.7745 | 41830.7745 | 41830.7745 | 41830.7745 | 41830.7745 | 41830.7745
Option 5 - 4B LLG 2nd Tx + Switchroom + Two new feeders + OFR12 New Feeder
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | 66.5813 | 92.3179 | 99.0036 | 67.9821 | 68.8666 | 70.3948 | 73.8759 | 76.2033 | 79.1547 | 80.6851 | 82.0294 | 79.5401 | 82.4503 | 87.0275 | 83.5483 | 83.5483 | 83.5483 | 83.5483 | 83.5483 | 83.5483 | 83.5483 | 83.5483 | 83.5483 | 83.5483 | 83.5483 | 83.5483 | 83.5483 | 83.5483 | 83.5483 | 83.5483 |  | 71.2634 | 96.6755 | 103.6223 | 72.5359 | 73.2139 | 74.709 | 78.2444 | 80.1716 | 83.8489 | 95.0336 | 85.8053 | 83.9979 | 86.43 | 91.7526 | 88.1443 | 88.1443 | 88.1443 | 88.1443 | 88.1443 | 88.1443 | 88.1443 | 88.1443 | 88.1443 | 88.1443 | 88.1443 | 88.1443 | 88.1443 | 88.1443 | 88.1443 | 88.1443
98% | 79.0946 | 109.6681 | 117.6103 | 80.7586 | 81.8094 | 83.6248 | 87.7601 | 90.5249 | 94.031 | 95.849 | 97.446 | 94.4888 | 97.946 | 103.3834 | 99.2503 | 99.2503 | 99.2503 | 99.2503 | 99.2503 | 99.2503 | 99.2503 | 99.2503 | 99.2503 | 99.2503 | 99.2503 | 99.2503 | 99.2503 | 99.2503 | 99.2503 | 99.2503 |  | 84.6567 | 114.8446 | 123.097 | 86.1683 | 86.9737 | 88.7497 | 92.9497 | 95.239 | 99.6074 | 112.8942 | 101.9316 | 99.7845 | 102.6736 | 108.9966 | 104.7101 | 104.7101 | 104.7101 | 104.7101 | 104.7101 | 104.7101 | 104.7101 | 104.7101 | 104.7101 | 104.7101 | 104.7101 | 104.7101 | 104.7101 | 104.7101 | 104.7101 | 104.7101
97% | 156.5832 | 217.1095 | 232.8326 | 159.8774 | 161.9577 | 165.5517 | 173.7382 | 179.2118 | 186.1528 | 189.7518 | 192.9134 | 187.0591 | 193.9033 | 204.6676 | 196.4854 | 196.4854 | 196.4854 | 196.4854 | 196.4854 | 196.4854 | 196.4854 | 196.4854 | 196.4854 | 196.4854 | 196.4854 | 196.4854 | 196.4854 | 196.4854 | 196.4854 | 196.4854 |  | 167.5944 | 227.3573 | 243.6946 | 170.5869 | 172.1815 | 175.6974 | 184.0121 | 188.5443 | 197.1924 | 223.4961 | 201.7934 | 197.5429 | 203.2624 | 215.78 | 207.2941 | 207.2941 | 207.2941 | 207.2941 | 207.2941 | 207.2941 | 207.2941 | 207.2941 | 207.2941 | 207.2941 | 207.2941 | 207.2941 | 207.2941 | 207.2941 | 207.2941 | 207.2941
95% | 462.5227 | 641.3081 | 687.7517 | 472.2532 | 478.398 | 489.0142 | 513.196 | 529.364 | 549.8666 | 560.4977 | 569.8364 | 552.5438 | 572.7606 | 604.5567 | 580.3877 | 580.3877 | 580.3877 | 580.3877 | 580.3877 | 580.3877 | 580.3877 | 580.3877 | 580.3877 | 580.3877 | 580.3877 | 580.3877 | 580.3877 | 580.3877 | 580.3877 | 580.3877 |  | 495.0481 | 671.5786 | 719.8364 | 503.8875 | 508.5978 | 518.9832 | 543.5433 | 556.9308 | 582.476 | 660.1732 | 596.0667 | 583.5113 | 600.4059 | 637.3809 | 612.3147 | 612.3147 | 612.3147 | 612.3147 | 612.3147 | 612.3147 | 612.3147 | 612.3147 | 612.3147 | 612.3147 | 612.3147 | 612.3147 | 612.3147 | 612.3147 | 612.3147 | 612.3147
90% | 2550.165 | 3535.9158 | 3791.9875 | 2603.8152 | 2637.6951 | 2696.2282 | 2829.557 | 2918.701 | 3031.7444 | 3090.3601 | 3141.8495 | 3046.5051 | 3157.9724 | 3333.2838 | 3200.0254 | 3200.0254 | 3200.0254 | 3200.0254 | 3200.0254 | 3200.0254 | 3200.0254 | 3200.0254 | 3200.0254 | 3200.0254 | 3200.0254 | 3200.0254 | 3200.0254 | 3200.0254 | 3200.0254 | 3200.0254 |  | 2729.4971 | 3702.8155 | 3968.8899 | 2778.2341 | 2804.2043 | 2861.4656 | 2996.8801 | 3070.6932 | 3211.5396 | 3639.9305 | 3286.4733 | 3217.2478 | 3310.3976 | 3514.263 | 3376.0583 | 3376.0583 | 3376.0583 | 3376.0583 | 3376.0583 | 3376.0583 | 3376.0583 | 3376.0583 | 3376.0583 | 3376.0583 | 3376.0583 | 3376.0583 | 3376.0583 | 3376.0583 | 3376.0583 | 3376.0583
85% | 6229.8705 | 8637.9889 | 9263.5537 | 6360.9339 | 6443.7002 | 6586.6924 | 6912.4052 | 7130.1775 | 7406.3344 | 7549.5283 | 7675.3133 | 7442.3938 | 7714.7003 | 8142.9736 | 7817.4329 | 7817.4329 | 7817.4329 | 7817.4329 | 7817.4329 | 7817.4329 | 7817.4329 | 7817.4329 | 7817.4329 | 7817.4329 | 7817.4329 | 7817.4329 | 7817.4329 | 7817.4329 | 7817.4329 | 7817.4329 |  | 6667.9659 | 9045.7131 | 9695.7136 | 6787.027 | 6850.4703 | 6990.3554 | 7321.1635 | 7501.4834 | 7845.5612 | 8892.0894 | 8028.6189 | 7859.506 | 8087.0641 | 8585.0928 | 8247.4686 | 8247.4686 | 8247.4686 | 8247.4686 | 8247.4686 | 8247.4686 | 8247.4686 | 8247.4686 | 8247.4686 | 8247.4686 | 8247.4686 | 8247.4686 | 8247.4686 | 8247.4686 | 8247.4686 | 8247.4686
80% | 9683.0656 | 13425.9956 | 14398.3087 | 9886.777 | 10015.4204 | 10237.6727 | 10743.9269 | 11082.4096 | 11511.6394 | 11734.2051 | 11929.7123 | 11567.6863 | 11990.9313 | 12656.595 | 12150.6082 | 12150.6082 | 12150.6082 | 12150.6082 | 12150.6082 | 12150.6082 | 12150.6082 | 12150.6082 | 12150.6082 | 12150.6082 | 12150.6082 | 12150.6082 | 12150.6082 | 12150.6082 | 12150.6082 | 12150.6082 |  | 10363.9958 | 14059.7198 | 15070.0133 | 10549.052 | 10647.6617 | 10865.0846 | 11379.2584 | 11659.5291 | 12194.328 | 13820.9431 | 12478.8539 | 12216.0023 | 12569.6951 | 13343.7792 | 12819.0112 | 12819.0112 | 12819.0112 | 12819.0112 | 12819.0112 | 12819.0112 | 12819.0112 | 12819.0112 | 12819.0112 | 12819.0112 | 12819.0112 | 12819.0112 | 12819.0112 | 12819.0112 | 12819.0112 | 12819.0112
75% | 10683.1238 | 14812.6201 | 15885.3529 | 10907.8743 | 11049.8038 | 11295.0101 | 11853.5498 | 12226.9908 | 12700.551 | 12946.1031 | 13161.8021 | 12762.3864 | 13229.3438 | 13963.7565 | 13405.5119 | 13405.5119 | 13405.5119 | 13405.5119 | 13405.5119 | 13405.5119 | 13405.5119 | 13405.5119 | 13405.5119 | 13405.5119 | 13405.5119 | 13405.5119 | 13405.5119 | 13405.5119 | 13405.5119 | 13405.5119 |  | 11434.3798 | 15511.7948 | 16626.4305 | 11638.5485 | 11747.3425 | 11987.2206 | 12554.4978 | 12863.7146 | 13453.7471 | 15248.3574 | 13767.6586 | 13477.6598 | 13867.8817 | 14721.9126 | 14142.9469 | 14142.9469 | 14142.9469 | 14142.9469 | 14142.9469 | 14142.9469 | 14142.9469 | 14142.9469 | 14142.9469 | 14142.9469 | 14142.9469 | 14142.9469 | 14142.9469 | 14142.9469 | 14142.9469 | 14142.9469
70% | 11478.4193 | 15915.3323 | 17067.9236 | 11719.9012 | 11872.3965 | 12135.857 | 12735.9766 | 13137.218 | 13646.032 | 13909.864 | 14141.6205 | 13712.4707 | 14214.1903 | 15003.2757 | 14403.4731 | 14403.4731 | 14403.4731 | 14403.4731 | 14403.4731 | 14403.4731 | 14403.4731 | 14403.4731 | 14403.4731 | 14403.4731 | 14403.4731 | 14403.4731 | 14403.4731 | 14403.4731 | 14403.4731 | 14403.4731 |  | 12285.6019 | 16666.5563 | 17864.1701 | 12504.9697 | 12621.8628 | 12879.5985 | 13489.106 | 13821.3422 | 14455.2991 | 16383.5076 | 14792.5795 | 14480.992 | 14900.2636 | 15817.872 | 15195.8058 | 15195.8058 | 15195.8058 | 15195.8058 | 15195.8058 | 15195.8058 | 15195.8058 | 15195.8058 | 15195.8058 | 15195.8058 | 15195.8058 | 15195.8058 | 15195.8058 | 15195.8058 | 15195.8058 | 15195.8058
65% | 12096.053 | 16771.7086 | 17986.3189 | 12350.5287 | 12511.2295 | 12788.8663 | 13421.2774 | 13844.1089 | 14380.3012 | 14658.3296 | 14902.5565 | 14450.3149 | 14979.0311 | 15810.5759 | 15178.4989 | 15178.4989 | 15178.4989 | 15178.4989 | 15178.4989 | 15178.4989 | 15178.4989 | 15178.4989 | 15178.4989 | 15178.4989 | 15178.4989 | 15178.4989 | 15178.4989 | 15178.4989 | 15178.4989 | 15178.4989 |  | 12946.6687 | 17563.3547 | 18825.4101 | 13177.8404 | 13301.0233 | 13572.6272 | 14214.9314 | 14565.0446 | 15233.1136 | 17265.0757 | 15588.5424 | 15260.189 | 15702.0209 | 16669.0042 | 16013.4657 | 16013.4657 | 16013.4657 | 16013.4657 | 16013.4657 | 16013.4657 | 16013.4657 | 16013.4657 | 16013.4657 | 16013.4657 | 16013.4657 | 16013.4657 | 16013.4657 | 16013.4657 | 16013.4657 | 16013.4657
60% | 13316.2645 | 18463.5854 | 19800.7217 | 13596.4108 | 13773.3227 | 14078.9666 | 14775.1733 | 15240.6587 | 15830.9404 | 16137.0154 | 16405.8792 | 15908.0169 | 16490.0683 | 17405.4967 | 16709.6578 | 16709.6578 | 16709.6578 | 16709.6578 | 16709.6578 | 16709.6578 | 16709.6578 | 16709.6578 | 16709.6578 | 16709.6578 | 16709.6578 | 16709.6578 | 16709.6578 | 16709.6578 | 16709.6578 | 16709.6578 |  | 14252.6876 | 19335.0902 | 20724.4577 | 14507.1791 | 14642.7883 | 14941.7908 | 15648.8886 | 16034.3201 | 16769.7818 | 19006.7218 | 17161.0652 | 16799.5885 | 17285.991 | 18350.5205 | 17628.8533 | 17628.8533 | 17628.8533 | 17628.8533 | 17628.8533 | 17628.8533 | 17628.8533 | 17628.8533 | 17628.8533 | 17628.8533 | 17628.8533 | 17628.8533 | 17628.8533 | 17628.8533 | 17628.8533 | 17628.8533
55% | 14813.5078 | 20539.579 | 22027.0592 | 15125.153 | 15321.9563 | 15661.966 | 16436.4522 | 16954.2755 | 17610.9268 | 17951.416 | 18250.5101 | 17696.6695 | 18344.1652 | 19362.5217 | 18588.4447 | 18588.4447 | 18588.4447 | 18588.4447 | 18588.4447 | 18588.4447 | 18588.4447 | 18588.4447 | 18588.4447 | 18588.4447 | 18588.4447 | 18588.4447 | 18588.4447 | 18588.4447 | 18588.4447 | 18588.4447 |  | 15855.2197 | 21509.0734 | 23054.6574 | 16138.3255 | 16289.1822 | 16621.8038 | 17408.4056 | 17837.1739 | 18655.3289 | 21143.7841 | 19090.607 | 18688.4869 | 19229.5792 | 20413.8014 | 19610.992 | 19610.992 | 19610.992 | 19610.992 | 19610.992 | 19610.992 | 19610.992 | 19610.992 | 19610.992 | 19610.992 | 19610.992 | 19610.992 | 19610.992 | 19610.992 | 19610.992 | 19610.992
50% | 15014.9247 | 20818.8523 | 22326.5575 | 15330.8072 | 15530.2865 | 15874.9192 | 16659.9359 | 17184.8 | 17850.3797 | 18195.4985 | 18498.6593 | 17937.2882 | 18593.5878 | 19625.7908 | 18841.1887 | 18841.1887 | 18841.1887 | 18841.1887 | 18841.1887 | 18841.1887 | 18841.1887 | 18841.1887 | 18841.1887 | 18841.1887 | 18841.1887 | 18841.1887 | 18841.1887 | 18841.1887 | 18841.1887 | 18841.1887 |  | 16070.8005 | 21801.5288 | 23368.1279 | 16357.7557 | 16510.6636 | 16847.8077 | 17645.1048 | 18079.7031 | 18908.9824 | 21431.2727 | 19350.1789 | 18942.5912 | 19491.0406 | 20691.3645 | 19877.6395 | 19877.6395 | 19877.6395 | 19877.6395 | 19877.6395 | 19877.6395 | 19877.6395 | 19877.6395 | 19877.6395 | 19877.6395 | 19877.6395 | 19877.6395 | 19877.6395 | 19877.6395 | 19877.6395 | 19877.6395
45% | 11588.8305 | 16068.4223 | 17232.1005 | 11832.6352 | 11986.5974 | 12252.5921 | 12858.4843 | 13263.5853 | 13777.2936 | 14043.6634 | 14277.6492 | 13844.3714 | 14350.917 | 15147.5927 | 14542.0205 | 14542.0205 | 14542.0205 | 14542.0205 | 14542.0205 | 14542.0205 | 14542.0205 | 14542.0205 | 14542.0205 | 14542.0205 | 14542.0205 | 14542.0205 | 14542.0205 | 14542.0205 | 14542.0205 | 14542.0205 |  | 12403.7774 | 16826.8724 | 18036.0061 | 12625.2553 | 12743.2728 | 13003.4877 | 13618.8581 | 13954.2901 | 14594.3451 | 16541.1011 | 14934.8697 | 14620.2851 | 15043.5897 | 15970.0246 | 15341.9747 | 15341.9747 | 15341.9747 | 15341.9747 | 15341.9747 | 15341.9747 | 15341.9747 | 15341.9747 | 15341.9747 | 15341.9747 | 15341.9747 | 15341.9747 | 15341.9747 | 15341.9747 | 15341.9747 | 15341.9747
40% | 5693.5395 | 7894.3425 | 8466.0523 | 5813.3197 | 5888.9606 | 6019.6426 | 6317.3147 | 6516.3389 | 6768.7214 | 6899.5877 | 7014.5439 | 6801.6765 | 7050.54 | 7441.9431 | 7144.4283 | 7144.4283 | 7144.4283 | 7144.4283 | 7144.4283 | 7144.4283 | 7144.4283 | 7144.4283 | 7144.4283 | 7144.4283 | 7144.4283 | 7144.4283 | 7144.4283 | 7144.4283 | 7144.4283 | 7144.4283 |  | 6093.9192 | 8266.9656 | 8861.0075 | 6202.7303 | 6260.7118 | 6388.5541 | 6690.8828 | 6855.679 | 7170.1351 | 8126.5674 | 7337.4333 | 7182.8793 | 7390.847 | 7846.0002 | 7537.4421 | 7537.4421 | 7537.4421 | 7537.4421 | 7537.4421 | 7537.4421 | 7537.4421 | 7537.4421 | 7537.4421 | 7537.4421 | 7537.4421 | 7537.4421 | 7537.4421 | 7537.4421 | 7537.4421 | 7537.4421
35% | 2127.9257 | 2950.4624 | 3164.1354 | 2172.6928 | 2200.9631 | 2249.8047 | 2361.0578 | 2435.4419 | 2529.7684 | 2578.6788 | 2621.643 | 2542.0851 | 2635.0963 | 2781.3809 | 2670.1865 | 2670.1865 | 2670.1865 | 2670.1865 | 2670.1865 | 2670.1865 | 2670.1865 | 2670.1865 | 2670.1865 | 2670.1865 | 2670.1865 | 2670.1865 | 2670.1865 | 2670.1865 | 2670.1865 | 2670.1865 |  | 2277.5652 | 3089.728 | 3311.7475 | 2318.2326 | 2339.9029 | 2387.6832 | 2500.6767 | 2562.2682 | 2679.7943 | 3037.255 | 2742.321 | 2684.5574 | 2762.284 | 2932.3947 | 2817.073 | 2817.073 | 2817.073 | 2817.073 | 2817.073 | 2817.073 | 2817.073 | 2817.073 | 2817.073 | 2817.073 | 2817.073 | 2817.073 | 2817.073 | 2817.073 | 2817.073 | 2817.073
30% | 1061.2862 | 1471.5199 | 1578.0877 | 1083.6134 | 1097.7131 | 1122.0724 | 1177.559 | 1214.6575 | 1261.7021 | 1286.0958 | 1307.5238 | 1267.845 | 1314.2336 | 1387.1918 | 1331.7345 | 1331.7345 | 1331.7345 | 1331.7345 | 1331.7345 | 1331.7345 | 1331.7345 | 1331.7345 | 1331.7345 | 1331.7345 | 1331.7345 | 1331.7345 | 1331.7345 | 1331.7345 | 1331.7345 | 1331.7345 |  | 1135.9177 | 1540.9775 | 1651.708 | 1156.2003 | 1167.0082 | 1190.8382 | 1247.1928 | 1277.9111 | 1336.5263 | 1514.8071 | 1367.711 | 1338.9019 | 1377.6674 | 1462.5088 | 1404.993 | 1404.993 | 1404.993 | 1404.993 | 1404.993 | 1404.993 | 1404.993 | 1404.993 | 1404.993 | 1404.993 | 1404.993 | 1404.993 | 1404.993 | 1404.993 | 1404.993 | 1404.993
25% | 625.6637 | 867.5102 | 930.3354 | 638.8263 | 647.1385 | 661.4992 | 694.2104 | 716.0812 | 743.8155 | 758.1965 | 770.829 | 747.437 | 774.7846 | 817.7959 | 785.102 | 785.102 | 785.102 | 785.102 | 785.102 | 785.102 | 785.102 | 785.102 | 785.102 | 785.102 | 785.102 | 785.102 | 785.102 | 785.102 | 785.102 | 785.102 |  | 669.6615 | 908.4578 | 973.7371 | 681.6187 | 687.9903 | 702.0389 | 735.2619 | 753.3713 | 787.9269 | 893.0294 | 806.3114 | 789.3274 | 812.181 | 862.1978 | 828.2903 | 828.2903 | 828.2903 | 828.2903 | 828.2903 | 828.2903 | 828.2903 | 828.2903 | 828.2903 | 828.2903 | 828.2903 | 828.2903 | 828.2903 | 828.2903 | 828.2903 | 828.2903
20% | 316.1776 | 438.3942 | 470.1428 | 322.8294 | 327.0299 | 334.287 | 350.8176 | 361.8699 | 375.8854 | 383.1528 | 389.5366 | 377.7155 | 391.5355 | 413.2712 | 396.7494 | 396.7494 | 396.7494 | 396.7494 | 396.7494 | 396.7494 | 396.7494 | 396.7494 | 396.7494 | 396.7494 | 396.7494 | 396.7494 | 396.7494 | 396.7494 | 396.7494 | 396.7494 |  | 338.4118 | 459.0869 | 492.0757 | 344.4544 | 347.6742 | 354.7737 | 371.5628 | 380.7144 | 398.177 | 451.2903 | 407.4675 | 398.8847 | 410.4337 | 435.7096 | 418.5745 | 418.5745 | 418.5745 | 418.5745 | 418.5745 | 418.5745 | 418.5745 | 418.5745 | 418.5745 | 418.5745 | 418.5745 | 418.5745 | 418.5745 | 418.5745 | 418.5745 | 418.5745
15% | 128.8131 | 178.605 | 191.5396 | 131.5231 | 133.2344 | 136.191 | 142.9257 | 147.4285 | 153.1385 | 156.0993 | 158.7001 | 153.8841 | 159.5145 | 168.3698 | 161.6386 | 161.6386 | 161.6386 | 161.6386 | 161.6386 | 161.6386 | 161.6386 | 161.6386 | 161.6386 | 161.6386 | 161.6386 | 161.6386 | 161.6386 | 161.6386 | 161.6386 | 161.6386 |  | 137.8715 | 187.0354 | 200.4753 | 140.3333 | 141.6451 | 144.5374 | 151.3774 | 155.1059 | 162.2203 | 183.859 | 166.0053 | 162.5086 | 167.2137 | 177.5113 | 170.5304 | 170.5304 | 170.5304 | 170.5304 | 170.5304 | 170.5304 | 170.5304 | 170.5304 | 170.5304 | 170.5304 | 170.5304 | 170.5304 | 170.5304 | 170.5304 | 170.5304 | 170.5304
10% | 51.8598 | 71.9059 | 77.1134 | 52.9508 | 53.6398 | 54.8301 | 57.5415 | 59.3543 | 61.6532 | 62.8452 | 63.8922 | 61.9533 | 64.2201 | 67.7852 | 65.0753 | 65.0753 | 65.0753 | 65.0753 | 65.0753 | 65.0753 | 65.0753 | 65.0753 | 65.0753 | 65.0753 | 65.0753 | 65.0753 | 65.0753 | 65.0753 | 65.0753 | 65.0753 |  | 55.5067 | 75.3 | 80.7108 | 56.4978 | 57.0259 | 58.1904 | 60.9442 | 62.4452 | 65.3095 | 74.0212 | 66.8333 | 65.4255 | 67.3198 | 71.4656 | 68.6551 | 68.6551 | 68.6551 | 68.6551 | 68.6551 | 68.6551 | 68.6551 | 68.6551 | 68.6551 | 68.6551 | 68.6551 | 68.6551 | 68.6551 | 68.6551 | 68.6551 | 68.6551
5% | 44.1645 | 61.236 | 65.6707 | 45.0936 | 45.6804 | 46.6941 | 49.0031 | 50.5469 | 52.5046 | 53.5197 | 54.4115 | 52.7603 | 54.6907 | 57.7268 | 55.419 | 55.419 | 55.419 | 55.419 | 55.419 | 55.419 | 55.419 | 55.419 | 55.419 | 55.419 | 55.419 | 55.419 | 55.419 | 55.419 | 55.419 | 55.419 |  | 47.2702 | 64.1264 | 68.7344 | 48.1143 | 48.564 | 49.5557 | 51.9008 | 53.1792 | 55.6184 | 63.0374 | 56.9161 | 55.7172 | 57.3304 | 60.861 | 58.4676 | 58.4676 | 58.4676 | 58.4676 | 58.4676 | 58.4676 | 58.4676 | 58.4676 | 58.4676 | 58.4676 | 58.4676 | 58.4676 | 58.4676 | 58.4676 | 58.4676 | 58.4676
9.992e-14% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E @ R (MWh) | 118268.4368 | 163984.3799 | 175860.1598 | 120756.5569 | 122327.7998 | 125042.3772 | 131225.7384 | 135359.9486 | 140602.5373 | 143320.943 | 145708.8572 | 141287.0917 | 146456.5832 | 154586.9625 | 148406.8675 | 148406.8675 | 148406.8675 | 148406.8675 | 148406.8675 | 148406.8675 | 148406.8675 | 148406.8675 | 148406.8675 | 148406.8675 | 148406.8675 | 148406.8675 | 148406.8675 | 148406.8675 | 148406.8675 | 148406.8675 | E @ R (MWh) | 126585.2808 | 171724.6525 | 184064.3234 | 128845.5476 | 130049.9613 | 132705.553 | 138985.6433 | 142408.8544 | 148940.8594 | 168808.2471 | 152416.0435 | 149205.5871 | 153525.5724 | 162980.1939 | 156570.7052 | 156570.7052 | 156570.7052 | 156570.7052 | 156570.7052 | 156570.7052 | 156570.7052 | 156570.7052 | 156570.7052 | 156570.7052 | 156570.7052 | 156570.7052 | 156570.7052 | 156570.7052 | 156570.7052 | 156570.7052
Option 5 Winter POE50 W E @ R (MWh) N 2 | 82787.9057 | 114789.066 | 123102.1118 | 84529.5898 | 85629.4599 | 87529.664 | 91858.0169 | 94751.964 | 98421.7761 | 100324.6601 | 101996.2 | 98900.9642 | 102519.6082 | 108210.8737 | 103884.8072 | 103884.8072 | 103884.8072 | 103884.8072 | 103884.8072 | 103884.8072 | 103884.8072 | 103884.8072 | 103884.8072 | 103884.8072 | 103884.8072 | 103884.8072 | 103884.8072 | 103884.8072 | 103884.8072 | 103884.8072 | Option 5 Winter POE10 W E @ R (MWh) N 2 | 37975.5842 | 51517.3957 | 55219.297 | 38653.6643 | 39014.9884 | 39811.6659 | 41695.693 | 42722.6563 | 44682.2578 | 50642.4741 | 45724.813 | 44761.6761 | 46057.6717 | 48894.0582 | 46971.2115 | 46971.2115 | 46971.2115 | 46971.2115 | 46971.2115 | 46971.2115 | 46971.2115 | 46971.2115 | 46971.2115 | 46971.2115 | 46971.2115 | 46971.2115 | 46971.2115 | 46971.2115 | 46971.2115 | 46971.2115
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 85.8327 | 111.1071 | 117.7202 | 84.5875 | 84.6155 | 85.2935 | 87.084 | 88.2816 | 89.4547 | 90.8268 | 92.0975 | 93.3318 | 93.4718 | 94.9125 | 93.8186 | 93.8186 | 93.8186 | 93.8186 | 93.8186 | 93.8186 | 93.8186 | 93.8186 | 93.8186 | 93.8186 | 93.8186 | 93.8186 | 93.8186 | 93.8186 | 93.8186 | 93.8186
98% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 42.4851 | 54.9952 | 58.2686 | 41.8687 | 41.8826 | 42.2182 | 43.1044 | 43.6972 | 44.2778 | 44.957 | 45.586 | 46.1969 | 46.2662 | 46.9793 | 46.4379 | 46.4379 | 46.4379 | 46.4379 | 46.4379 | 46.4379 | 46.4379 | 46.4379 | 46.4379 | 46.4379 | 46.4379 | 46.4379 | 46.4379 | 46.4379 | 46.4379 | 46.4379
97% | 18.864 | 25.0432 | 26.7251 | 18.6567 | 18.6549 | 18.8466 | 19.0569 | 19.4888 | 19.7991 | 19.9674 | 20.1515 | 20.32 | 20.6245 | 21.0025 | 20.9761 | 20.9761 | 20.9761 | 20.9761 | 20.9761 | 20.9761 | 20.9761 | 20.9761 | 20.9761 | 20.9761 | 20.9761 | 20.9761 | 20.9761 | 20.9761 | 20.9761 | 20.9761 |  | 84.1075 | 108.8738 | 115.354 | 82.8872 | 82.9147 | 83.5791 | 85.3335 | 86.5071 | 87.6566 | 89.0011 | 90.2463 | 91.4558 | 91.593 | 93.0048 | 91.9328 | 91.9328 | 91.9328 | 91.9328 | 91.9328 | 91.9328 | 91.9328 | 91.9328 | 91.9328 | 91.9328 | 91.9328 | 91.9328 | 91.9328 | 91.9328 | 91.9328 | 91.9328
95% | 92.8689 | 123.2894 | 131.5698 | 91.8483 | 91.8394 | 92.7831 | 93.8186 | 95.9447 | 97.4725 | 98.3012 | 99.2075 | 100.0371 | 101.5362 | 103.3969 | 103.2668 | 103.2668 | 103.2668 | 103.2668 | 103.2668 | 103.2668 | 103.2668 | 103.2668 | 103.2668 | 103.2668 | 103.2668 | 103.2668 | 103.2668 | 103.2668 | 103.2668 | 103.2668 |  | 124.2203 | 160.7982 | 170.369 | 122.4181 | 122.4586 | 123.4399 | 126.0311 | 127.7644 | 129.4621 | 131.4478 | 133.2869 | 135.0731 | 135.2758 | 137.3609 | 135.7777 | 135.7777 | 135.7777 | 135.7777 | 135.7777 | 135.7777 | 135.7777 | 135.7777 | 135.7777 | 135.7777 | 135.7777 | 135.7777 | 135.7777 | 135.7777 | 135.7777 | 135.7777
90% | 161.0694 | 213.8301 | 228.1913 | 159.2993 | 159.2839 | 160.9207 | 162.7167 | 166.4041 | 169.0538 | 170.4912 | 172.0629 | 173.5018 | 176.1019 | 179.329 | 179.1034 | 179.1034 | 179.1034 | 179.1034 | 179.1034 | 179.1034 | 179.1034 | 179.1034 | 179.1034 | 179.1034 | 179.1034 | 179.1034 | 179.1034 | 179.1034 | 179.1034 | 179.1034 |  | 538.6113 | 697.2109 | 738.7092 | 530.7971 | 530.973 | 535.2276 | 546.4628 | 553.9784 | 561.3394 | 569.9494 | 577.9236 | 585.6687 | 586.5474 | 595.5881 | 588.7236 | 588.7236 | 588.7236 | 588.7236 | 588.7236 | 588.7236 | 588.7236 | 588.7236 | 588.7236 | 588.7236 | 588.7236 | 588.7236 | 588.7236 | 588.7236 | 588.7236 | 588.7236
85% | 457.0889 | 606.8151 | 647.57 | 452.0657 | 452.0219 | 456.6667 | 461.7637 | 472.2278 | 479.7472 | 483.8262 | 488.2867 | 492.37 | 499.7486 | 508.9066 | 508.2665 | 508.2665 | 508.2665 | 508.2665 | 508.2665 | 508.2665 | 508.2665 | 508.2665 | 508.2665 | 508.2665 | 508.2665 | 508.2665 | 508.2665 | 508.2665 | 508.2665 | 508.2665 |  | 509.4971 | 659.5238 | 698.779 | 502.1054 | 502.2718 | 506.2964 | 516.9243 | 524.0336 | 530.9967 | 539.1413 | 546.6845 | 554.0109 | 554.8422 | 563.3942 | 556.9007 | 556.9007 | 556.9007 | 556.9007 | 556.9007 | 556.9007 | 556.9007 | 556.9007 | 556.9007 | 556.9007 | 556.9007 | 556.9007 | 556.9007 | 556.9007 | 556.9007 | 556.9007
80% | 638.4734 | 847.6148 | 904.5422 | 631.4568 | 631.3957 | 637.8837 | 645.0032 | 659.6198 | 670.1231 | 675.8208 | 682.0513 | 687.7549 | 698.0615 | 710.8536 | 709.9595 | 709.9595 | 709.9595 | 709.9595 | 709.9595 | 709.9595 | 709.9595 | 709.9595 | 709.9595 | 709.9595 | 709.9595 | 709.9595 | 709.9595 | 709.9595 | 709.9595 | 709.9595 |  | 355.8393 | 460.6198 | 488.0361 | 350.6768 | 350.793 | 353.6038 | 361.0265 | 365.9917 | 370.8548 | 376.5431 | 381.8114 | 386.9283 | 387.5088 | 393.4817 | 388.9465 | 388.9465 | 388.9465 | 388.9465 | 388.9465 | 388.9465 | 388.9465 | 388.9465 | 388.9465 | 388.9465 | 388.9465 | 388.9465 | 388.9465 | 388.9465 | 388.9465 | 388.9465
75% | 1664.3841 | 2209.5776 | 2357.9769 | 1646.0931 | 1645.9338 | 1662.8467 | 1681.4061 | 1719.509 | 1746.8892 | 1761.7419 | 1777.9836 | 1792.8521 | 1819.7193 | 1853.0662 | 1850.7353 | 1850.7353 | 1850.7353 | 1850.7353 | 1850.7353 | 1850.7353 | 1850.7353 | 1850.7353 | 1850.7353 | 1850.7353 | 1850.7353 | 1850.7353 | 1850.7353 | 1850.7353 | 1850.7353 | 1850.7353 |  | 635.1192 | 822.1366 | 871.0705 | 625.9049 | 626.1123 | 631.1293 | 644.3775 | 653.2398 | 661.9197 | 672.0724 | 681.4755 | 690.6084 | 691.6445 | 702.3051 | 694.2106 | 694.2106 | 694.2106 | 694.2106 | 694.2106 | 694.2106 | 694.2106 | 694.2106 | 694.2106 | 694.2106 | 694.2106 | 694.2106 | 694.2106 | 694.2106 | 694.2106 | 694.2106
70% | 2875.5487 | 3817.4772 | 4073.866 | 2843.9475 | 2843.6723 | 2872.8927 | 2904.9576 | 2970.7879 | 3018.0924 | 3043.7535 | 3071.8142 | 3097.5024 | 3143.9208 | 3201.534 | 3197.507 | 3197.507 | 3197.507 | 3197.507 | 3197.507 | 3197.507 | 3197.507 | 3197.507 | 3197.507 | 3197.507 | 3197.507 | 3197.507 | 3197.507 | 3197.507 | 3197.507 | 3197.507 |  | 1157.0168 | 1497.7123 | 1586.8569 | 1140.2309 | 1140.6087 | 1149.7483 | 1173.883 | 1190.0277 | 1205.8401 | 1224.3357 | 1241.4656 | 1258.1032 | 1259.9908 | 1279.4116 | 1264.6655 | 1264.6655 | 1264.6655 | 1264.6655 | 1264.6655 | 1264.6655 | 1264.6655 | 1264.6655 | 1264.6655 | 1264.6655 | 1264.6655 | 1264.6655 | 1264.6655 | 1264.6655 | 1264.6655 | 1264.6655
65% | 7222.0048 | 9587.679 | 10231.6052 | 7142.6376 | 7141.9464 | 7215.3341 | 7295.8659 | 7461.1999 | 7580.0064 | 7644.4547 | 7714.9299 | 7779.4462 | 7896.0271 | 8040.724 | 8030.61 | 8030.61 | 8030.61 | 8030.61 | 8030.61 | 8030.61 | 8030.61 | 8030.61 | 8030.61 | 8030.61 | 8030.61 | 8030.61 | 8030.61 | 8030.61 | 8030.61 | 8030.61 |  | 1455.7061 | 1884.3537 | 1996.5114 | 1434.5869 | 1435.0622 | 1446.5612 | 1476.9264 | 1497.2389 | 1517.1334 | 1540.4037 | 1561.9558 | 1582.8884 | 1585.2633 | 1609.6977 | 1591.1448 | 1591.1448 | 1591.1448 | 1591.1448 | 1591.1448 | 1591.1448 | 1591.1448 | 1591.1448 | 1591.1448 | 1591.1448 | 1591.1448 | 1591.1448 | 1591.1448 | 1591.1448 | 1591.1448 | 1591.1448
60% | 10556.5772 | 14014.5398 | 14955.7822 | 10440.5643 | 10439.554 | 10546.8265 | 10664.5417 | 10906.2145 | 11079.8767 | 11174.0824 | 11277.0976 | 11371.4027 | 11541.8118 | 11753.3187 | 11738.5348 | 11738.5348 | 11738.5348 | 11738.5348 | 11738.5348 | 11738.5348 | 11738.5348 | 11738.5348 | 11738.5348 | 11738.5348 | 11738.5348 | 11738.5348 | 11738.5348 | 11738.5348 | 11738.5348 | 11738.5348 |  | 2277.9105 | 2948.6646 | 3124.1707 | 2244.8628 | 2245.6066 | 2263.6004 | 2311.1164 | 2342.9016 | 2374.0329 | 2410.4465 | 2444.1715 | 2476.9273 | 2480.6435 | 2518.8788 | 2489.847 | 2489.847 | 2489.847 | 2489.847 | 2489.847 | 2489.847 | 2489.847 | 2489.847 | 2489.847 | 2489.847 | 2489.847 | 2489.847 | 2489.847 | 2489.847 | 2489.847 | 2489.847
55% | 11937.0341 | 15847.1857 | 16911.512 | 11805.8504 | 11804.708 | 11926.0083 | 12059.1169 | 12332.3926 | 12528.7642 | 12635.2889 | 12751.7751 | 12858.4122 | 13051.1053 | 13290.2705 | 13273.5532 | 13273.5532 | 13273.5532 | 13273.5532 | 13273.5532 | 13273.5532 | 13273.5532 | 13273.5532 | 13273.5532 | 13273.5532 | 13273.5532 | 13273.5532 | 13273.5532 | 13273.5532 | 13273.5532 | 13273.5532 |  | 4377.3623 | 5666.3214 | 6003.5838 | 4313.8558 | 4315.2851 | 4349.8631 | 4441.1725 | 4502.2528 | 4562.0764 | 4632.051 | 4696.8588 | 4759.8041 | 4766.9455 | 4840.4206 | 4784.6314 | 4784.6314 | 4784.6314 | 4784.6314 | 4784.6314 | 4784.6314 | 4784.6314 | 4784.6314 | 4784.6314 | 4784.6314 | 4784.6314 | 4784.6314 | 4784.6314 | 4784.6314 | 4784.6314 | 4784.6314
50% | 15327.7148 | 20348.5339 | 21715.179 | 15159.2688 | 15157.8019 | 15313.5572 | 15484.4748 | 15835.3737 | 16087.5241 | 16224.3069 | 16373.8807 | 16510.8077 | 16758.2348 | 17065.3341 | 17043.8684 | 17043.8684 | 17043.8684 | 17043.8684 | 17043.8684 | 17043.8684 | 17043.8684 | 17043.8684 | 17043.8684 | 17043.8684 | 17043.8684 | 17043.8684 | 17043.8684 | 17043.8684 | 17043.8684 | 17043.8684 |  | 9714.4123 | 12574.9205 | 13323.3863 | 9573.4764 | 9576.6483 | 9653.3851 | 9856.0224 | 9991.5742 | 10124.3371 | 10279.6274 | 10423.4514 | 10563.1421 | 10578.9906 | 10742.0492 | 10618.2398 | 10618.2398 | 10618.2398 | 10618.2398 | 10618.2398 | 10618.2398 | 10618.2398 | 10618.2398 | 10618.2398 | 10618.2398 | 10618.2398 | 10618.2398 | 10618.2398 | 10618.2398 | 10618.2398 | 10618.2398
45% | 20411.3174 | 27097.3455 | 28917.2533 | 20187.0044 | 20185.0511 | 20392.4643 | 20620.0686 | 21087.3469 | 21423.1257 | 21605.274 | 21804.4555 | 21986.7959 | 22316.2848 | 22725.237 | 22696.6519 | 22696.6519 | 22696.6519 | 22696.6519 | 22696.6519 | 22696.6519 | 22696.6519 | 22696.6519 | 22696.6519 | 22696.6519 | 22696.6519 | 22696.6519 | 22696.6519 | 22696.6519 | 22696.6519 | 22696.6519 |  | 14720.4239 | 19055.0036 | 20189.1672 | 14506.8612 | 14511.6677 | 14627.9483 | 14935.0083 | 15140.4124 | 15341.5904 | 15576.9046 | 15794.8437 | 16006.5195 | 16030.5351 | 16277.6207 | 16090.01 | 16090.01 | 16090.01 | 16090.01 | 16090.01 | 16090.01 | 16090.01 | 16090.01 | 16090.01 | 16090.01 | 16090.01 | 16090.01 | 16090.01 | 16090.01 | 16090.01 | 16090.01
40% | 14315.8312 | 19005.1929 | 20281.6168 | 14158.5054 | 14157.1354 | 14302.6082 | 14462.2425 | 14789.9762 | 15025.4805 | 15153.2333 | 15292.9328 | 15420.8204 | 15651.9131 | 15938.7388 | 15918.6902 | 15918.6902 | 15918.6902 | 15918.6902 | 15918.6902 | 15918.6902 | 15918.6902 | 15918.6902 | 15918.6902 | 15918.6902 | 15918.6902 | 15918.6902 | 15918.6902 | 15918.6902 | 15918.6902 | 15918.6902 |  | 15242.3215 | 19730.5793 | 20904.9535 | 15021.1871 | 15026.1641 | 15146.5673 | 15464.5138 | 15677.2002 | 15885.5108 | 16129.1679 | 16354.8337 | 16574.0143 | 16598.8813 | 16854.7271 | 16660.4649 | 16660.4649 | 16660.4649 | 16660.4649 | 16660.4649 | 16660.4649 | 16660.4649 | 16660.4649 | 16660.4649 | 16660.4649 | 16660.4649 | 16660.4649 | 16660.4649 | 16660.4649 | 16660.4649 | 16660.4649
35% | 7422.2532 | 9853.5218 | 10515.3025 | 7340.6854 | 7339.9751 | 7415.3976 | 7498.1623 | 7668.0807 | 7790.1814 | 7856.4167 | 7928.8459 | 7995.1512 | 8114.9646 | 8263.6736 | 8253.2791 | 8253.2791 | 8253.2791 | 8253.2791 | 8253.2791 | 8253.2791 | 8253.2791 | 8253.2791 | 8253.2791 | 8253.2791 | 8253.2791 | 8253.2791 | 8253.2791 | 8253.2791 | 8253.2791 | 8253.2791 |  | 20759.9869 | 26872.9779 | 28472.4713 | 20458.8027 | 20465.5813 | 20629.57 | 21062.612 | 21352.2902 | 21636.0084 | 21967.8684 | 22275.2245 | 22573.7477 | 22607.6165 | 22956.0775 | 22691.4931 | 22691.4931 | 22691.4931 | 22691.4931 | 22691.4931 | 22691.4931 | 22691.4931 | 22691.4931 | 22691.4931 | 22691.4931 | 22691.4931 | 22691.4931 | 22691.4931 | 22691.4931 | 22691.4931 | 22691.4931
30% | 3452.1096 | 4582.899 | 4890.695 | 3414.1722 | 3413.8418 | 3448.921 | 3487.4151 | 3566.4446 | 3623.2339 | 3654.0402 | 3687.7272 | 3718.5659 | 3774.2914 | 3843.4564 | 3838.6219 | 3838.6219 | 3838.6219 | 3838.6219 | 3838.6219 | 3838.6219 | 3838.6219 | 3838.6219 | 3838.6219 | 3838.6219 | 3838.6219 | 3838.6219 | 3838.6219 | 3838.6219 | 3838.6219 | 3838.6219 |  | 19183.5111 | 24832.2926 | 26310.3234 | 18905.1983 | 18911.4621 | 19062.9978 | 19463.1554 | 19730.8359 | 19993.0091 | 20299.6683 | 20583.6843 | 20859.5382 | 20890.835 | 21212.8346 | 20968.3422 | 20968.3422 | 20968.3422 | 20968.3422 | 20968.3422 | 20968.3422 | 20968.3422 | 20968.3422 | 20968.3422 | 20968.3422 | 20968.3422 | 20968.3422 | 20968.3422 | 20968.3422 | 20968.3422 | 20968.3422
25% | 2357.031 | 3129.1112 | 3339.2681 | 2331.1281 | 2330.9025 | 2354.8539 | 2381.1369 | 2435.0966 | 2473.8712 | 2494.9051 | 2517.9059 | 2538.962 | 2577.0103 | 2624.2347 | 2620.9338 | 2620.9338 | 2620.9338 | 2620.9338 | 2620.9338 | 2620.9338 | 2620.9338 | 2620.9338 | 2620.9338 | 2620.9338 | 2620.9338 | 2620.9338 | 2620.9338 | 2620.9338 | 2620.9338 | 2620.9338 |  | 5533.3008 | 7162.6379 | 7588.9618 | 5453.0241 | 5454.8308 | 5498.5398 | 5613.9615 | 5691.1714 | 5766.7927 | 5855.2456 | 5937.1674 | 6016.7348 | 6025.7621 | 6118.6398 | 6048.1183 | 6048.1183 | 6048.1183 | 6048.1183 | 6048.1183 | 6048.1183 | 6048.1183 | 6048.1183 | 6048.1183 | 6048.1183 | 6048.1183 | 6048.1183 | 6048.1183 | 6048.1183 | 6048.1183 | 6048.1183
20% | 1427.8587 | 1895.5749 | 2022.8852 | 1412.167 | 1412.0304 | 1426.5398 | 1442.4617 | 1475.1498 | 1498.639 | 1511.381 | 1525.3146 | 1538.0701 | 1561.1193 | 1589.7272 | 1587.7276 | 1587.7276 | 1587.7276 | 1587.7276 | 1587.7276 | 1587.7276 | 1587.7276 | 1587.7276 | 1587.7276 | 1587.7276 | 1587.7276 | 1587.7276 | 1587.7276 | 1587.7276 | 1587.7276 | 1587.7276 |  | 1484.8203 | 1922.0408 | 2036.4417 | 1463.2786 | 1463.7634 | 1475.4924 | 1506.465 | 1527.1837 | 1547.4761 | 1571.2118 | 1593.1949 | 1614.5462 | 1616.9686 | 1641.8916 | 1622.9677 | 1622.9677 | 1622.9677 | 1622.9677 | 1622.9677 | 1622.9677 | 1622.9677 | 1622.9677 | 1622.9677 | 1622.9677 | 1622.9677 | 1622.9677 | 1622.9677 | 1622.9677 | 1622.9677 | 1622.9677
15% | 914.1778 | 1213.6303 | 1295.1399 | 904.1313 | 904.0439 | 913.3334 | 923.5273 | 944.4557 | 959.4945 | 967.6525 | 976.5734 | 984.74 | 999.4971 | 1017.8132 | 1016.5329 | 1016.5329 | 1016.5329 | 1016.5329 | 1016.5329 | 1016.5329 | 1016.5329 | 1016.5329 | 1016.5329 | 1016.5329 | 1016.5329 | 1016.5329 | 1016.5329 | 1016.5329 | 1016.5329 | 1016.5329 |  | 818.9695 | 1060.1234 | 1123.2225 | 807.0879 | 807.3554 | 813.8246 | 830.9079 | 842.3355 | 853.528 | 866.6197 | 878.7447 | 890.5213 | 891.8574 | 905.604 | 895.1663 | 895.1663 | 895.1663 | 895.1663 | 895.1663 | 895.1663 | 895.1663 | 895.1663 | 895.1663 | 895.1663 | 895.1663 | 895.1663 | 895.1663 | 895.1663 | 895.1663 | 895.1663
10% | 611.8703 | 812.2975 | 866.8529 | 605.1461 | 605.0876 | 611.3052 | 618.1281 | 632.1357 | 642.2013 | 647.6616 | 653.6325 | 659.0985 | 668.9756 | 681.2347 | 680.3778 | 680.3778 | 680.3778 | 680.3778 | 680.3778 | 680.3778 | 680.3778 | 680.3778 | 680.3778 | 680.3778 | 680.3778 | 680.3778 | 680.3778 | 680.3778 | 680.3778 | 680.3778 |  | 191.3984 | 247.7576 | 262.5043 | 188.6216 | 188.6841 | 190.196 | 194.1885 | 196.8592 | 199.475 | 202.5346 | 205.3683 | 208.1205 | 208.4328 | 211.6454 | 209.2061 | 209.2061 | 209.2061 | 209.2061 | 209.2061 | 209.2061 | 209.2061 | 209.2061 | 209.2061 | 209.2061 | 209.2061 | 209.2061 | 209.2061 | 209.2061 | 209.2061 | 209.2061
5% | 435.3228 | 577.9192 | 616.7333 | 430.5387 | 430.4971 | 434.9207 | 439.7749 | 449.7408 | 456.9021 | 460.7869 | 465.035 | 468.9238 | 475.951 | 484.6729 | 484.0633 | 484.0633 | 484.0633 | 484.0633 | 484.0633 | 484.0633 | 484.0633 | 484.0633 | 484.0633 | 484.0633 | 484.0633 | 484.0633 | 484.0633 | 484.0633 | 484.0633 | 484.0633 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9.992e-14% | 38.2117 | 50.7285 | 54.1355 | 37.7917 | 37.7881 | 38.1764 | 38.6025 | 39.4772 | 40.1059 | 40.4469 | 40.8197 | 41.1611 | 41.7779 | 42.5435 | 42.49 | 42.49 | 42.49 | 42.49 | 42.49 | 42.49 | 42.49 | 42.49 | 42.49 | 42.49 | 42.49 | 42.49 | 42.49 | 42.49 | 42.49 | 42.49 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E @ R (MWh) | 102337.6118 | 135859.8063 | 144984.402 | 101212.9589 | 101203.165 | 102243.0869 | 103384.242 | 105727.0671 | 107410.5842 | 108323.8334 | 109322.4835 | 110236.696 | 111888.677 | 113939.0683 | 113795.7494 | 113795.7494 | 113795.7494 | 113795.7494 | 113795.7494 | 113795.7494 | 113795.7494 | 113795.7494 | 113795.7494 | 113795.7494 | 113795.7494 | 113795.7494 | 113795.7494 | 113795.7494 | 113795.7494 | 113795.7494 | E @ R (MWh) | 99292.8528 | 128530.651 | 136180.8614 | 97852.32 | 97884.7413 | 98669.0821 | 100740.277 | 102125.7774 | 103482.7723 | 105070.0241 | 106540.0762 | 107967.8816 | 108129.8722 | 109796.5252 | 108531.0452 | 108531.0452 | 108531.0452 | 108531.0452 | 108531.0452 | 108531.0452 | 108531.0452 | 108531.0452 | 108531.0452 | 108531.0452 | 108531.0452 | 108531.0452 | 108531.0452 | 108531.0452 | 108531.0452 | 108531.0452
Option 5 Summer POE50 W E @ R (MWh) N 2 | 71636.3283 | 95101.8644 | 101489.0814 | 70849.0712 | 70842.2155 | 71570.1608 | 72368.9694 | 74008.947 | 75187.4089 | 75826.6834 | 76525.7384 | 77165.6872 | 78322.0739 | 79757.3478 | 79657.0246 | 79657.0246 | 79657.0246 | 79657.0246 | 79657.0246 | 79657.0246 | 79657.0246 | 79657.0246 | 79657.0246 | 79657.0246 | 79657.0246 | 79657.0246 | 79657.0246 | 79657.0246 | 79657.0246 | 79657.0246 | Option 5 Summer POE10 W E @ R (MWh) N 2 | 29787.8558 | 38559.1953 | 40854.2584 | 29355.696 | 29365.4224 | 29600.7246 | 30222.0831 | 30637.7332 | 31044.8317 | 31521.0072 | 31962.0229 | 32390.3645 | 32438.9617 | 32938.9576 | 32559.3136 | 32559.3136 | 32559.3136 | 32559.3136 | 32559.3136 | 32559.3136 | 32559.3136 | 32559.3136 | 32559.3136 | 32559.3136 | 32559.3136 | 32559.3136 | 32559.3136 | 32559.3136 | 32559.3136 | 32559.3136
Option 6 -
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | 66.5813 | 92.3179 | 99.0036 | 100.1408 | 101.0254 | 102.5536 | 106.0346 | 108.362 | 111.3134 | 112.8438 | 114.1881 | 111.6988 | 114.6091 | 119.1862 | 115.707 | 115.707 | 115.707 | 115.707 | 115.707 | 115.707 | 115.707 | 115.707 | 115.707 | 115.707 | 115.707 | 115.707 | 115.707 | 115.707 | 115.707 | 115.707 |  | 71.2634 | 96.6755 | 103.6223 | 104.6946 | 105.3727 | 106.8677 | 110.4032 | 112.3303 | 116.0076 | 127.1923 | 117.9641 | 116.1567 | 118.5887 | 123.9113 | 120.303 | 120.303 | 120.303 | 120.303 | 120.303 | 120.303 | 120.303 | 120.303 | 120.303 | 120.303 | 120.303 | 120.303 | 120.303 | 120.303 | 120.303 | 120.303
98% | 79.0946 | 109.6681 | 117.6103 | 118.9612 | 120.012 | 121.8275 | 125.9627 | 128.7276 | 132.2337 | 134.0516 | 135.6486 | 132.6915 | 136.1487 | 141.586 | 137.453 | 137.453 | 137.453 | 137.453 | 137.453 | 137.453 | 137.453 | 137.453 | 137.453 | 137.453 | 137.453 | 137.453 | 137.453 | 137.453 | 137.453 | 137.453 |  | 84.6567 | 114.8446 | 123.097 | 124.3709 | 125.1764 | 126.9524 | 131.1523 | 133.4417 | 137.8101 | 151.0968 | 140.1342 | 137.9871 | 140.8762 | 147.1992 | 142.9127 | 142.9127 | 142.9127 | 142.9127 | 142.9127 | 142.9127 | 142.9127 | 142.9127 | 142.9127 | 142.9127 | 142.9127 | 142.9127 | 142.9127 | 142.9127 | 142.9127 | 142.9127
97% | 156.5832 | 217.1095 | 232.8326 | 235.507 | 237.5873 | 241.1813 | 249.3678 | 254.8414 | 261.7824 | 265.3814 | 268.543 | 262.6887 | 269.5329 | 280.2972 | 272.115 | 272.115 | 272.115 | 272.115 | 272.115 | 272.115 | 272.115 | 272.115 | 272.115 | 272.115 | 272.115 | 272.115 | 272.115 | 272.115 | 272.115 | 272.115 |  | 167.5944 | 227.3573 | 243.6946 | 246.2165 | 247.8111 | 251.327 | 259.6417 | 264.1739 | 272.822 | 299.1257 | 277.423 | 273.1725 | 278.892 | 291.4096 | 282.9237 | 282.9237 | 282.9237 | 282.9237 | 282.9237 | 282.9237 | 282.9237 | 282.9237 | 282.9237 | 282.9237 | 282.9237 | 282.9237 | 282.9237 | 282.9237 | 282.9237 | 282.9237
95% | 462.5227 | 641.3081 | 687.7517 | 695.6514 | 701.7962 | 712.4124 | 736.5942 | 752.7622 | 773.2648 | 783.8959 | 793.2346 | 775.942 | 796.1588 | 827.9549 | 803.7859 | 803.7859 | 803.7859 | 803.7859 | 803.7859 | 803.7859 | 803.7859 | 803.7859 | 803.7859 | 803.7859 | 803.7859 | 803.7859 | 803.7859 | 803.7859 | 803.7859 | 803.7859 |  | 495.0481 | 671.5786 | 719.8364 | 727.2857 | 731.996 | 742.3814 | 766.9415 | 780.329 | 805.8742 | 883.5714 | 819.4649 | 806.9095 | 823.8041 | 860.7791 | 835.7129 | 835.7129 | 835.7129 | 835.7129 | 835.7129 | 835.7129 | 835.7129 | 835.7129 | 835.7129 | 835.7129 | 835.7129 | 835.7129 | 835.7129 | 835.7129 | 835.7129 | 835.7129
90% | 2550.165 | 3535.9158 | 3791.9875 | 3835.5434 | 3869.4233 | 3927.9564 | 4061.2852 | 4150.4292 | 4263.4726 | 4322.0883 | 4373.5777 | 4278.2333 | 4389.7006 | 4565.012 | 4431.7536 | 4431.7536 | 4431.7536 | 4431.7536 | 4431.7536 | 4431.7536 | 4431.7536 | 4431.7536 | 4431.7536 | 4431.7536 | 4431.7536 | 4431.7536 | 4431.7536 | 4431.7536 | 4431.7536 | 4431.7536 |  | 2729.4971 | 3702.8155 | 3968.8899 | 4009.9623 | 4035.9325 | 4093.1938 | 4228.6083 | 4302.4214 | 4443.2678 | 4871.6587 | 4518.2015 | 4448.976 | 4542.1258 | 4745.9912 | 4607.7865 | 4607.7865 | 4607.7865 | 4607.7865 | 4607.7865 | 4607.7865 | 4607.7865 | 4607.7865 | 4607.7865 | 4607.7865 | 4607.7865 | 4607.7865 | 4607.7865 | 4607.7865 | 4607.7865 | 4607.7865
85% | 6229.8705 | 8637.9889 | 9263.5537 | 9369.9577 | 9452.724 | 9595.7162 | 9921.4289 | 10139.2013 | 10415.3582 | 10558.5521 | 10684.3371 | 10451.4176 | 10723.7241 | 11151.9973 | 10826.4566 | 10826.4566 | 10826.4566 | 10826.4566 | 10826.4566 | 10826.4566 | 10826.4566 | 10826.4566 | 10826.4566 | 10826.4566 | 10826.4566 | 10826.4566 | 10826.4566 | 10826.4566 | 10826.4566 | 10826.4566 |  | 6667.9659 | 9045.7131 | 9695.7136 | 9796.0508 | 9859.4941 | 9999.3792 | 10330.1872 | 10510.5072 | 10854.585 | 11901.1132 | 11037.6427 | 10868.5297 | 11096.0879 | 11594.1165 | 11256.4923 | 11256.4923 | 11256.4923 | 11256.4923 | 11256.4923 | 11256.4923 | 11256.4923 | 11256.4923 | 11256.4923 | 11256.4923 | 11256.4923 | 11256.4923 | 11256.4923 | 11256.4923 | 11256.4923 | 11256.4923
80% | 9683.0656 | 13425.9956 | 14398.3087 | 14563.692 | 14692.3353 | 14914.5876 | 15420.8418 | 15759.3246 | 16188.5543 | 16411.1201 | 16606.6272 | 16244.6013 | 16667.8463 | 17333.5099 | 16827.5231 | 16827.5231 | 16827.5231 | 16827.5231 | 16827.5231 | 16827.5231 | 16827.5231 | 16827.5231 | 16827.5231 | 16827.5231 | 16827.5231 | 16827.5231 | 16827.5231 | 16827.5231 | 16827.5231 | 16827.5231 |  | 10363.9958 | 14059.7198 | 15070.0133 | 15225.967 | 15324.5767 | 15541.9996 | 16056.1734 | 16336.4441 | 16871.243 | 18497.858 | 17155.7689 | 16892.9172 | 17246.6101 | 18020.6942 | 17495.9261 | 17495.9261 | 17495.9261 | 17495.9261 | 17495.9261 | 17495.9261 | 17495.9261 | 17495.9261 | 17495.9261 | 17495.9261 | 17495.9261 | 17495.9261 | 17495.9261 | 17495.9261 | 17495.9261 | 17495.9261
75% | 10683.1238 | 14812.6201 | 15885.3529 | 16067.8168 | 16209.7463 | 16454.9526 | 17013.4923 | 17386.9332 | 17860.4934 | 18106.0455 | 18321.7445 | 17922.3288 | 18389.2862 | 19123.699 | 18565.4543 | 18565.4543 | 18565.4543 | 18565.4543 | 18565.4543 | 18565.4543 | 18565.4543 | 18565.4543 | 18565.4543 | 18565.4543 | 18565.4543 | 18565.4543 | 18565.4543 | 18565.4543 | 18565.4543 | 18565.4543 |  | 11434.3798 | 15511.7948 | 16626.4305 | 16798.4909 | 16907.2849 | 17147.1631 | 17714.4402 | 18023.6571 | 18613.6895 | 20408.2999 | 18927.601 | 18637.6022 | 19027.8242 | 19881.855 | 19302.8894 | 19302.8894 | 19302.8894 | 19302.8894 | 19302.8894 | 19302.8894 | 19302.8894 | 19302.8894 | 19302.8894 | 19302.8894 | 19302.8894 | 19302.8894 | 19302.8894 | 19302.8894 | 19302.8894 | 19302.8894
70% | 11478.4193 | 15915.3323 | 17067.9236 | 17263.9709 | 17416.4662 | 17679.9267 | 18280.0463 | 18681.2877 | 19190.1017 | 19453.9337 | 19685.6902 | 19256.5404 | 19758.26 | 20547.3454 | 19947.5428 | 19947.5428 | 19947.5428 | 19947.5428 | 19947.5428 | 19947.5428 | 19947.5428 | 19947.5428 | 19947.5428 | 19947.5428 | 19947.5428 | 19947.5428 | 19947.5428 | 19947.5428 | 19947.5428 | 19947.5428 |  | 12285.6019 | 16666.5563 | 17864.1701 | 18049.0394 | 18165.9325 | 18423.6682 | 19033.1757 | 19365.4119 | 19999.3688 | 21927.5773 | 20336.6492 | 20025.0617 | 20444.3333 | 21361.9417 | 20739.8755 | 20739.8755 | 20739.8755 | 20739.8755 | 20739.8755 | 20739.8755 | 20739.8755 | 20739.8755 | 20739.8755 | 20739.8755 | 20739.8755 | 20739.8755 | 20739.8755 | 20739.8755 | 20739.8755 | 20739.8755
65% | 12096.053 | 16771.7086 | 17986.3189 | 18192.9151 | 18353.6159 | 18631.2528 | 19263.6638 | 19686.4953 | 20222.6877 | 20500.7161 | 20744.943 | 20292.7014 | 20821.4176 | 21652.9624 | 21020.8854 | 21020.8854 | 21020.8854 | 21020.8854 | 21020.8854 | 21020.8854 | 21020.8854 | 21020.8854 | 21020.8854 | 21020.8854 | 21020.8854 | 21020.8854 | 21020.8854 | 21020.8854 | 21020.8854 | 21020.8854 |  | 12946.6687 | 17563.3547 | 18825.4101 | 19020.2268 | 19143.4097 | 19415.0137 | 20057.3178 | 20407.431 | 21075.5001 | 23107.4621 | 21430.9289 | 21102.5754 | 21544.4074 | 22511.3907 | 21855.8521 | 21855.8521 | 21855.8521 | 21855.8521 | 21855.8521 | 21855.8521 | 21855.8521 | 21855.8521 | 21855.8521 | 21855.8521 | 21855.8521 | 21855.8521 | 21855.8521 | 21855.8521 | 21855.8521 | 21855.8521
60% | 13316.2645 | 18463.5854 | 19800.7217 | 20028.1587 | 20205.0705 | 20510.7145 | 21206.9211 | 21672.4066 | 22262.6883 | 22568.7633 | 22837.627 | 22339.7647 | 22921.8162 | 23837.2445 | 23141.4056 | 23141.4056 | 23141.4056 | 23141.4056 | 23141.4056 | 23141.4056 | 23141.4056 | 23141.4056 | 23141.4056 | 23141.4056 | 23141.4056 | 23141.4056 | 23141.4056 | 23141.4056 | 23141.4056 | 23141.4056 |  | 14252.6876 | 19335.0902 | 20724.4577 | 20938.927 | 21074.5362 | 21373.5387 | 22080.6365 | 22466.068 | 23201.5297 | 25438.4696 | 23592.813 | 23231.3363 | 23717.7389 | 24782.2684 | 24060.6012 | 24060.6012 | 24060.6012 | 24060.6012 | 24060.6012 | 24060.6012 | 24060.6012 | 24060.6012 | 24060.6012 | 24060.6012 | 24060.6012 | 24060.6012 | 24060.6012 | 24060.6012 | 24060.6012 | 24060.6012
55% | 14813.5078 | 20539.579 | 22027.0592 | 22280.0685 | 22476.8718 | 22816.8815 | 23591.3677 | 24109.191 | 24765.8423 | 25106.3315 | 25405.4256 | 24851.585 | 25499.0807 | 26517.4372 | 25743.3602 | 25743.3602 | 25743.3602 | 25743.3602 | 25743.3602 | 25743.3602 | 25743.3602 | 25743.3602 | 25743.3602 | 25743.3602 | 25743.3602 | 25743.3602 | 25743.3602 | 25743.3602 | 25743.3602 | 25743.3602 |  | 15855.2197 | 21509.0734 | 23054.6574 | 23293.241 | 23444.0977 | 23776.7193 | 24563.3211 | 24992.0894 | 25810.2444 | 28298.6996 | 26245.5225 | 25843.4024 | 26384.4947 | 27568.7169 | 26765.9075 | 26765.9075 | 26765.9075 | 26765.9075 | 26765.9075 | 26765.9075 | 26765.9075 | 26765.9075 | 26765.9075 | 26765.9075 | 26765.9075 | 26765.9075 | 26765.9075 | 26765.9075 | 26765.9075 | 26765.9075
50% | 15014.9247 | 20818.8523 | 22326.5575 | 22583.007 | 22782.4862 | 23127.1189 | 23912.1357 | 24436.9997 | 25102.5795 | 25447.6982 | 25750.859 | 25189.488 | 25845.7876 | 26877.9905 | 26093.3885 | 26093.3885 | 26093.3885 | 26093.3885 | 26093.3885 | 26093.3885 | 26093.3885 | 26093.3885 | 26093.3885 | 26093.3885 | 26093.3885 | 26093.3885 | 26093.3885 | 26093.3885 | 26093.3885 | 26093.3885 |  | 16070.8005 | 21801.5288 | 23368.1279 | 23609.9554 | 23762.8633 | 24100.0075 | 24897.3046 | 25331.9028 | 26161.1821 | 28683.4724 | 26602.3787 | 26194.791 | 26743.2404 | 27943.5643 | 27129.8392 | 27129.8392 | 27129.8392 | 27129.8392 | 27129.8392 | 27129.8392 | 27129.8392 | 27129.8392 | 27129.8392 | 27129.8392 | 27129.8392 | 27129.8392 | 27129.8392 | 27129.8392 | 27129.8392 | 27129.8392
45% | 11588.8305 | 16068.4223 | 17232.1005 | 17430.0335 | 17583.9957 | 17849.9904 | 18455.8826 | 18860.9836 | 19374.6918 | 19641.0617 | 19875.0474 | 19441.7696 | 19948.3153 | 20744.9909 | 20139.4188 | 20139.4188 | 20139.4188 | 20139.4188 | 20139.4188 | 20139.4188 | 20139.4188 | 20139.4188 | 20139.4188 | 20139.4188 | 20139.4188 | 20139.4188 | 20139.4188 | 20139.4188 | 20139.4188 | 20139.4188 |  | 12403.7774 | 16826.8724 | 18036.0061 | 18222.6536 | 18340.6711 | 18600.8859 | 19216.2564 | 19551.6884 | 20191.7433 | 22138.4993 | 20532.268 | 20217.6833 | 20640.988 | 21567.4228 | 20939.373 | 20939.373 | 20939.373 | 20939.373 | 20939.373 | 20939.373 | 20939.373 | 20939.373 | 20939.373 | 20939.373 | 20939.373 | 20939.373 | 20939.373 | 20939.373 | 20939.373 | 20939.373
40% | 5693.5395 | 7894.3425 | 8466.0523 | 8563.2959 | 8638.9368 | 8769.6188 | 9067.2909 | 9266.3151 | 9518.6977 | 9649.5639 | 9764.5201 | 9551.6527 | 9800.5162 | 10191.9194 | 9894.4045 | 9894.4045 | 9894.4045 | 9894.4045 | 9894.4045 | 9894.4045 | 9894.4045 | 9894.4045 | 9894.4045 | 9894.4045 | 9894.4045 | 9894.4045 | 9894.4045 | 9894.4045 | 9894.4045 | 9894.4045 |  | 6093.9192 | 8266.9656 | 8861.0075 | 8952.7065 | 9010.688 | 9138.5304 | 9440.8591 | 9605.6552 | 9920.1113 | 10876.5437 | 10087.4095 | 9932.8555 | 10140.8232 | 10595.9764 | 10287.4184 | 10287.4184 | 10287.4184 | 10287.4184 | 10287.4184 | 10287.4184 | 10287.4184 | 10287.4184 | 10287.4184 | 10287.4184 | 10287.4184 | 10287.4184 | 10287.4184 | 10287.4184 | 10287.4184 | 10287.4184
35% | 2127.9257 | 2950.4624 | 3164.1354 | 3200.4796 | 3228.75 | 3277.5916 | 3388.8447 | 3463.2288 | 3557.5552 | 3606.4657 | 3649.4298 | 3569.872 | 3662.8832 | 3809.1677 | 3697.9734 | 3697.9734 | 3697.9734 | 3697.9734 | 3697.9734 | 3697.9734 | 3697.9734 | 3697.9734 | 3697.9734 | 3697.9734 | 3697.9734 | 3697.9734 | 3697.9734 | 3697.9734 | 3697.9734 | 3697.9734 |  | 2277.5652 | 3089.728 | 3311.7475 | 3346.0195 | 3367.6897 | 3415.47 | 3528.4635 | 3590.0551 | 3707.5811 | 4065.0419 | 3770.1078 | 3712.3442 | 3790.0708 | 3960.1816 | 3844.8599 | 3844.8599 | 3844.8599 | 3844.8599 | 3844.8599 | 3844.8599 | 3844.8599 | 3844.8599 | 3844.8599 | 3844.8599 | 3844.8599 | 3844.8599 | 3844.8599 | 3844.8599 | 3844.8599 | 3844.8599
30% | 1061.2862 | 1471.5199 | 1578.0877 | 1596.2141 | 1610.3137 | 1634.673 | 1690.1596 | 1727.2581 | 1774.3027 | 1798.6964 | 1820.1244 | 1780.4456 | 1826.8342 | 1899.7925 | 1844.3351 | 1844.3351 | 1844.3351 | 1844.3351 | 1844.3351 | 1844.3351 | 1844.3351 | 1844.3351 | 1844.3351 | 1844.3351 | 1844.3351 | 1844.3351 | 1844.3351 | 1844.3351 | 1844.3351 | 1844.3351 |  | 1135.9177 | 1540.9775 | 1651.708 | 1668.8009 | 1679.6088 | 1703.4388 | 1759.7934 | 1790.5117 | 1849.1269 | 2027.4077 | 1880.3116 | 1851.5025 | 1890.268 | 1975.1094 | 1917.5936 | 1917.5936 | 1917.5936 | 1917.5936 | 1917.5936 | 1917.5936 | 1917.5936 | 1917.5936 | 1917.5936 | 1917.5936 | 1917.5936 | 1917.5936 | 1917.5936 | 1917.5936 | 1917.5936 | 1917.5936
25% | 625.6637 | 867.5102 | 930.3354 | 941.0215 | 949.3337 | 963.6944 | 996.4056 | 1018.2764 | 1046.0107 | 1060.3916 | 1073.0242 | 1049.6322 | 1076.9798 | 1119.9911 | 1087.2972 | 1087.2972 | 1087.2972 | 1087.2972 | 1087.2972 | 1087.2972 | 1087.2972 | 1087.2972 | 1087.2972 | 1087.2972 | 1087.2972 | 1087.2972 | 1087.2972 | 1087.2972 | 1087.2972 | 1087.2972 |  | 669.6615 | 908.4578 | 973.7371 | 983.8139 | 990.1855 | 1004.2341 | 1037.457 | 1055.5665 | 1090.1221 | 1195.2246 | 1108.5065 | 1091.5226 | 1114.3762 | 1164.393 | 1130.4855 | 1130.4855 | 1130.4855 | 1130.4855 | 1130.4855 | 1130.4855 | 1130.4855 | 1130.4855 | 1130.4855 | 1130.4855 | 1130.4855 | 1130.4855 | 1130.4855 | 1130.4855 | 1130.4855 | 1130.4855
20% | 316.1776 | 438.3942 | 470.1428 | 475.543 | 479.7435 | 487.0006 | 503.5312 | 514.5835 | 528.599 | 535.8664 | 542.2502 | 530.4291 | 544.2492 | 565.9848 | 549.463 | 549.463 | 549.463 | 549.463 | 549.463 | 549.463 | 549.463 | 549.463 | 549.463 | 549.463 | 549.463 | 549.463 | 549.463 | 549.463 | 549.463 | 549.463 |  | 338.4118 | 459.0869 | 492.0757 | 497.168 | 500.3879 | 507.4873 | 524.2764 | 533.428 | 550.8906 | 604.0039 | 560.1811 | 551.5983 | 563.1473 | 588.4232 | 571.2881 | 571.2881 | 571.2881 | 571.2881 | 571.2881 | 571.2881 | 571.2881 | 571.2881 | 571.2881 | 571.2881 | 571.2881 | 571.2881 | 571.2881 | 571.2881 | 571.2881 | 571.2881
15% | 128.8131 | 178.605 | 191.5396 | 193.7397 | 195.4511 | 198.4077 | 205.1423 | 209.6451 | 215.3552 | 218.3159 | 220.9167 | 216.1007 | 221.7311 | 230.5864 | 223.8553 | 223.8553 | 223.8553 | 223.8553 | 223.8553 | 223.8553 | 223.8553 | 223.8553 | 223.8553 | 223.8553 | 223.8553 | 223.8553 | 223.8553 | 223.8553 | 223.8553 | 223.8553 |  | 137.8715 | 187.0354 | 200.4753 | 202.5499 | 203.8617 | 206.7541 | 213.5941 | 217.3225 | 224.4369 | 246.0756 | 228.2219 | 224.7252 | 229.4304 | 239.728 | 232.747 | 232.747 | 232.747 | 232.747 | 232.747 | 232.747 | 232.747 | 232.747 | 232.747 | 232.747 | 232.747 | 232.747 | 232.747 | 232.747 | 232.747 | 232.747
10% | 51.8598 | 71.9059 | 77.1134 | 77.9991 | 78.6881 | 79.8784 | 82.5898 | 84.4026 | 86.7014 | 87.8934 | 88.9405 | 87.0016 | 89.2684 | 92.8335 | 90.1236 | 90.1236 | 90.1236 | 90.1236 | 90.1236 | 90.1236 | 90.1236 | 90.1236 | 90.1236 | 90.1236 | 90.1236 | 90.1236 | 90.1236 | 90.1236 | 90.1236 | 90.1236 |  | 55.5067 | 75.3 | 80.7108 | 81.5461 | 82.0742 | 83.2387 | 85.9924 | 87.4935 | 90.3577 | 99.0694 | 91.8816 | 90.4738 | 92.3681 | 96.5139 | 93.7033 | 93.7033 | 93.7033 | 93.7033 | 93.7033 | 93.7033 | 93.7033 | 93.7033 | 93.7033 | 93.7033 | 93.7033 | 93.7033 | 93.7033 | 93.7033 | 93.7033 | 93.7033
5% | 44.1645 | 61.236 | 65.6707 | 66.425 | 67.0118 | 68.0255 | 70.3345 | 71.8783 | 73.8361 | 74.8512 | 75.7429 | 74.0917 | 76.0221 | 79.0582 | 76.7504 | 76.7504 | 76.7504 | 76.7504 | 76.7504 | 76.7504 | 76.7504 | 76.7504 | 76.7504 | 76.7504 | 76.7504 | 76.7504 | 76.7504 | 76.7504 | 76.7504 | 76.7504 |  | 47.2702 | 64.1264 | 68.7344 | 69.4457 | 69.8954 | 70.8871 | 73.2323 | 74.5106 | 76.9498 | 84.3688 | 78.2475 | 77.0487 | 78.6618 | 82.1924 | 79.799 | 79.799 | 79.799 | 79.799 | 79.799 | 79.799 | 79.799 | 79.799 | 79.799 | 79.799 | 79.799 | 79.799 | 79.799 | 79.799 | 79.799 | 79.799
9.992e-14% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E @ R (MWh) | 118268.4368 | 163984.3799 | 175860.1598 | 177880.1417 | 179451.3847 | 182165.962 | 188349.3233 | 192483.5334 | 197726.1221 | 200444.5279 | 202832.442 | 198410.6765 | 203580.168 | 211710.5473 | 205530.4523 | 205530.4523 | 205530.4523 | 205530.4523 | 205530.4523 | 205530.4523 | 205530.4523 | 205530.4523 | 205530.4523 | 205530.4523 | 205530.4523 | 205530.4523 | 205530.4523 | 205530.4523 | 205530.4523 | 205530.4523 | E @ R (MWh) | 126585.2808 | 171724.6525 | 184064.3234 | 185969.1325 | 187173.5461 | 189829.1378 | 196109.2281 | 199532.4392 | 206064.4443 | 225931.832 | 209539.6283 | 206329.172 | 210649.1573 | 220103.7788 | 213694.29 | 213694.29 | 213694.29 | 213694.29 | 213694.29 | 213694.29 | 213694.29 | 213694.29 | 213694.29 | 213694.29 | 213694.29 | 213694.29 | 213694.29 | 213694.29 | 213694.29 | 213694.29
Option 6 Winter POE50 W E @ R (MWh) N 2 | 82787.9057 | 114789.066 | 123102.1118 | 124516.0992 | 125615.9693 | 127516.1734 | 131844.5263 | 134738.4734 | 138408.2855 | 140311.1695 | 141982.7094 | 138887.4736 | 142506.1176 | 148197.3831 | 143871.3166 | 143871.3166 | 143871.3166 | 143871.3166 | 143871.3166 | 143871.3166 | 143871.3166 | 143871.3166 | 143871.3166 | 143871.3166 | 143871.3166 | 143871.3166 | 143871.3166 | 143871.3166 | 143871.3166 | 143871.3166 | Option 6 Winter POE10 W E @ R (MWh) N 2 | 37975.5842 | 51517.3957 | 55219.297 | 55790.7397 | 56152.0638 | 56948.7413 | 58832.7684 | 59859.7318 | 61819.3333 | 67779.5496 | 62861.8885 | 61898.7516 | 63194.7472 | 66031.1336 | 64108.287 | 64108.287 | 64108.287 | 64108.287 | 64108.287 | 64108.287 | 64108.287 | 64108.287 | 64108.287 | 64108.287 | 64108.287 | 64108.287 | 64108.287 | 64108.287 | 64108.287 | 64108.287
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 85.8327 | 111.1071 | 117.7202 | 117.3233 | 117.3513 | 118.0293 | 119.8198 | 121.0174 | 122.1905 | 123.5626 | 124.8333 | 126.0676 | 126.2076 | 127.6483 | 126.5544 | 126.5544 | 126.5544 | 126.5544 | 126.5544 | 126.5544 | 126.5544 | 126.5544 | 126.5544 | 126.5544 | 126.5544 | 126.5544 | 126.5544 | 126.5544 | 126.5544 | 126.5544
98% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 42.4851 | 54.9952 | 58.2686 | 58.0721 | 58.0859 | 58.4216 | 59.3078 | 59.9006 | 60.4812 | 61.1604 | 61.7894 | 62.4003 | 62.4696 | 63.1827 | 62.6413 | 62.6413 | 62.6413 | 62.6413 | 62.6413 | 62.6413 | 62.6413 | 62.6413 | 62.6413 | 62.6413 | 62.6413 | 62.6413 | 62.6413 | 62.6413 | 62.6413 | 62.6413
97% | 18.864 | 25.0432 | 26.7251 | 26.6761 | 26.6743 | 26.866 | 27.0764 | 27.5082 | 27.8185 | 27.9869 | 28.171 | 28.3395 | 28.644 | 29.0219 | 28.9955 | 28.9955 | 28.9955 | 28.9955 | 28.9955 | 28.9955 | 28.9955 | 28.9955 | 28.9955 | 28.9955 | 28.9955 | 28.9955 | 28.9955 | 28.9955 | 28.9955 | 28.9955 |  | 84.1075 | 108.8738 | 115.354 | 114.965 | 114.9925 | 115.6569 | 117.4113 | 118.5849 | 119.7344 | 121.0789 | 122.3241 | 123.5336 | 123.6708 | 125.0825 | 124.0106 | 124.0106 | 124.0106 | 124.0106 | 124.0106 | 124.0106 | 124.0106 | 124.0106 | 124.0106 | 124.0106 | 124.0106 | 124.0106 | 124.0106 | 124.0106 | 124.0106 | 124.0106
95% | 92.8689 | 123.2894 | 131.5698 | 131.3286 | 131.3197 | 132.2634 | 133.299 | 135.4251 | 136.9528 | 137.7816 | 138.6878 | 139.5174 | 141.0166 | 142.8772 | 142.7472 | 142.7472 | 142.7472 | 142.7472 | 142.7472 | 142.7472 | 142.7472 | 142.7472 | 142.7472 | 142.7472 | 142.7472 | 142.7472 | 142.7472 | 142.7472 | 142.7472 | 142.7472 |  | 124.2203 | 160.7982 | 170.369 | 169.7945 | 169.8351 | 170.8163 | 173.4075 | 175.1408 | 176.8385 | 178.8242 | 180.6633 | 182.4496 | 182.6522 | 184.7373 | 183.1541 | 183.1541 | 183.1541 | 183.1541 | 183.1541 | 183.1541 | 183.1541 | 183.1541 | 183.1541 | 183.1541 | 183.1541 | 183.1541 | 183.1541 | 183.1541 | 183.1541 | 183.1541
90% | 161.0694 | 213.8301 | 228.1913 | 227.7731 | 227.7577 | 229.3944 | 231.1905 | 234.8778 | 237.5275 | 238.9649 | 240.5367 | 241.9755 | 244.5756 | 247.8027 | 247.5772 | 247.5772 | 247.5772 | 247.5772 | 247.5772 | 247.5772 | 247.5772 | 247.5772 | 247.5772 | 247.5772 | 247.5772 | 247.5772 | 247.5772 | 247.5772 | 247.5772 | 247.5772 |  | 538.6113 | 697.2109 | 738.7092 | 736.2183 | 736.3942 | 740.6488 | 751.884 | 759.3996 | 766.7606 | 775.3706 | 783.3448 | 791.0899 | 791.9686 | 801.0093 | 794.1448 | 794.1448 | 794.1448 | 794.1448 | 794.1448 | 794.1448 | 794.1448 | 794.1448 | 794.1448 | 794.1448 | 794.1448 | 794.1448 | 794.1448 | 794.1448 | 794.1448 | 794.1448
85% | 457.0889 | 606.8151 | 647.57 | 646.383 | 646.3393 | 650.9841 | 656.081 | 666.5452 | 674.0646 | 678.1436 | 682.6041 | 686.6874 | 694.0659 | 703.2239 | 702.5838 | 702.5838 | 702.5838 | 702.5838 | 702.5838 | 702.5838 | 702.5838 | 702.5838 | 702.5838 | 702.5838 | 702.5838 | 702.5838 | 702.5838 | 702.5838 | 702.5838 | 702.5838 |  | 509.4971 | 659.5238 | 698.779 | 696.4228 | 696.5891 | 700.6138 | 711.2416 | 718.351 | 725.3141 | 733.4587 | 741.0019 | 748.3283 | 749.1595 | 757.7115 | 751.218 | 751.218 | 751.218 | 751.218 | 751.218 | 751.218 | 751.218 | 751.218 | 751.218 | 751.218 | 751.218 | 751.218 | 751.218 | 751.218 | 751.218 | 751.218
80% | 638.4734 | 847.6148 | 904.5422 | 902.8842 | 902.8231 | 909.3111 | 916.4306 | 931.0473 | 941.5505 | 947.2482 | 953.4787 | 959.1824 | 969.4889 | 982.2811 | 981.3869 | 981.3869 | 981.3869 | 981.3869 | 981.3869 | 981.3869 | 981.3869 | 981.3869 | 981.3869 | 981.3869 | 981.3869 | 981.3869 | 981.3869 | 981.3869 | 981.3869 | 981.3869 |  | 355.8393 | 460.6198 | 488.0361 | 486.3905 | 486.5067 | 489.3176 | 496.7402 | 501.7054 | 506.5685 | 512.2568 | 517.5251 | 522.642 | 523.2225 | 529.1954 | 524.6602 | 524.6602 | 524.6602 | 524.6602 | 524.6602 | 524.6602 | 524.6602 | 524.6602 | 524.6602 | 524.6602 | 524.6602 | 524.6602 | 524.6602 | 524.6602 | 524.6602 | 524.6602
75% | 1664.3841 | 2209.5776 | 2357.9769 | 2353.655 | 2353.4957 | 2370.4087 | 2388.968 | 2427.0709 | 2454.4511 | 2469.3039 | 2485.5456 | 2500.414 | 2527.2813 | 2560.6281 | 2558.2972 | 2558.2972 | 2558.2972 | 2558.2972 | 2558.2972 | 2558.2972 | 2558.2972 | 2558.2972 | 2558.2972 | 2558.2972 | 2558.2972 | 2558.2972 | 2558.2972 | 2558.2972 | 2558.2972 | 2558.2972 |  | 635.1192 | 822.1366 | 871.0705 | 868.1333 | 868.3407 | 873.3577 | 886.6059 | 895.4682 | 904.1481 | 914.3008 | 923.7039 | 932.8368 | 933.8729 | 944.5335 | 936.439 | 936.439 | 936.439 | 936.439 | 936.439 | 936.439 | 936.439 | 936.439 | 936.439 | 936.439 | 936.439 | 936.439 | 936.439 | 936.439 | 936.439 | 936.439
70% | 2875.5487 | 3817.4772 | 4073.866 | 4066.399 | 4066.1238 | 4095.3442 | 4127.4091 | 4193.2394 | 4240.5439 | 4266.205 | 4294.2657 | 4319.9539 | 4366.3723 | 4423.9855 | 4419.9585 | 4419.9585 | 4419.9585 | 4419.9585 | 4419.9585 | 4419.9585 | 4419.9585 | 4419.9585 | 4419.9585 | 4419.9585 | 4419.9585 | 4419.9585 | 4419.9585 | 4419.9585 | 4419.9585 | 4419.9585 |  | 1157.0168 | 1497.7123 | 1586.8569 | 1581.5061 | 1581.8839 | 1591.0234 | 1615.1582 | 1631.3028 | 1647.1153 | 1665.6109 | 1682.7407 | 1699.3783 | 1701.266 | 1720.6867 | 1705.9407 | 1705.9407 | 1705.9407 | 1705.9407 | 1705.9407 | 1705.9407 | 1705.9407 | 1705.9407 | 1705.9407 | 1705.9407 | 1705.9407 | 1705.9407 | 1705.9407 | 1705.9407 | 1705.9407 | 1705.9407
65% | 7222.0048 | 9587.679 | 10231.6052 | 10212.8518 | 10212.1606 | 10285.5483 | 10366.0801 | 10531.4141 | 10650.2206 | 10714.6689 | 10785.1441 | 10849.6604 | 10966.2413 | 11110.9382 | 11100.8242 | 11100.8242 | 11100.8242 | 11100.8242 | 11100.8242 | 11100.8242 | 11100.8242 | 11100.8242 | 11100.8242 | 11100.8242 | 11100.8242 | 11100.8242 | 11100.8242 | 11100.8242 | 11100.8242 | 11100.8242 |  | 1455.7061 | 1884.3537 | 1996.5114 | 1989.7793 | 1990.2546 | 2001.7536 | 2032.1189 | 2052.4313 | 2072.3259 | 2095.5961 | 2117.1482 | 2138.0809 | 2140.4558 | 2164.8901 | 2146.3373 | 2146.3373 | 2146.3373 | 2146.3373 | 2146.3373 | 2146.3373 | 2146.3373 | 2146.3373 | 2146.3373 | 2146.3373 | 2146.3373 | 2146.3373 | 2146.3373 | 2146.3373 | 2146.3373 | 2146.3373
60% | 10556.5772 | 14014.5398 | 14955.7822 | 14928.3698 | 14927.3596 | 15034.6321 | 15152.3473 | 15394.0201 | 15567.6823 | 15661.888 | 15764.9032 | 15859.2082 | 16029.6174 | 16241.1243 | 16226.3403 | 16226.3403 | 16226.3403 | 16226.3403 | 16226.3403 | 16226.3403 | 16226.3403 | 16226.3403 | 16226.3403 | 16226.3403 | 16226.3403 | 16226.3403 | 16226.3403 | 16226.3403 | 16226.3403 | 16226.3403 |  | 2277.9105 | 2948.6646 | 3124.1707 | 3113.6361 | 3114.3799 | 3132.3737 | 3179.8897 | 3211.675 | 3242.8062 | 3279.2199 | 3312.9449 | 3345.7006 | 3349.4169 | 3387.6521 | 3358.6203 | 3358.6203 | 3358.6203 | 3358.6203 | 3358.6203 | 3358.6203 | 3358.6203 | 3358.6203 | 3358.6203 | 3358.6203 | 3358.6203 | 3358.6203 | 3358.6203 | 3358.6203 | 3358.6203 | 3358.6203
55% | 11937.0341 | 15847.1857 | 16911.512 | 16880.515 | 16879.3726 | 17000.6729 | 17133.7814 | 17407.0571 | 17603.4287 | 17709.9534 | 17826.4396 | 17933.0767 | 18125.7699 | 18364.935 | 18348.2178 | 18348.2178 | 18348.2178 | 18348.2178 | 18348.2178 | 18348.2178 | 18348.2178 | 18348.2178 | 18348.2178 | 18348.2178 | 18348.2178 | 18348.2178 | 18348.2178 | 18348.2178 | 18348.2178 | 18348.2178 |  | 4377.3623 | 5666.3214 | 6003.5838 | 5983.3401 | 5984.7694 | 6019.3473 | 6110.6567 | 6171.737 | 6231.5606 | 6301.5352 | 6366.343 | 6429.2884 | 6436.4298 | 6509.9048 | 6454.1156 | 6454.1156 | 6454.1156 | 6454.1156 | 6454.1156 | 6454.1156 | 6454.1156 | 6454.1156 | 6454.1156 | 6454.1156 | 6454.1156 | 6454.1156 | 6454.1156 | 6454.1156 | 6454.1156 | 6454.1156
50% | 15327.7148 | 20348.5339 | 21715.179 | 21675.3774 | 21673.9105 | 21829.6658 | 22000.5834 | 22351.4823 | 22603.6327 | 22740.4155 | 22889.9893 | 23026.9163 | 23274.3434 | 23581.4427 | 23559.977 | 23559.977 | 23559.977 | 23559.977 | 23559.977 | 23559.977 | 23559.977 | 23559.977 | 23559.977 | 23559.977 | 23559.977 | 23559.977 | 23559.977 | 23559.977 | 23559.977 | 23559.977 |  | 9714.4123 | 12574.9205 | 13323.3863 | 13278.4606 | 13281.6325 | 13358.3693 | 13561.0066 | 13696.5584 | 13829.3213 | 13984.6116 | 14128.4356 | 14268.1263 | 14283.9748 | 14447.0334 | 14323.224 | 14323.224 | 14323.224 | 14323.224 | 14323.224 | 14323.224 | 14323.224 | 14323.224 | 14323.224 | 14323.224 | 14323.224 | 14323.224 | 14323.224 | 14323.224 | 14323.224 | 14323.224
45% | 20411.3174 | 27097.3455 | 28917.2533 | 28864.251 | 28862.2976 | 29069.7109 | 29297.3152 | 29764.5935 | 30100.3723 | 30282.5206 | 30481.7021 | 30664.0425 | 30993.5314 | 31402.4836 | 31373.8985 | 31373.8985 | 31373.8985 | 31373.8985 | 31373.8985 | 31373.8985 | 31373.8985 | 31373.8985 | 31373.8985 | 31373.8985 | 31373.8985 | 31373.8985 | 31373.8985 | 31373.8985 | 31373.8985 | 31373.8985 |  | 14720.4239 | 19055.0036 | 20189.1672 | 20121.0905 | 20125.8971 | 20242.1776 | 20549.2377 | 20754.6417 | 20955.8197 | 21191.1339 | 21409.073 | 21620.7489 | 21644.7644 | 21891.85 | 21704.2393 | 21704.2393 | 21704.2393 | 21704.2393 | 21704.2393 | 21704.2393 | 21704.2393 | 21704.2393 | 21704.2393 | 21704.2393 | 21704.2393 | 21704.2393 | 21704.2393 | 21704.2393 | 21704.2393 | 21704.2393
40% | 14315.8312 | 19005.1929 | 20281.6168 | 20244.4427 | 20243.0727 | 20388.5455 | 20548.1797 | 20875.9135 | 21111.4178 | 21239.1706 | 21378.87 | 21506.7576 | 21737.8504 | 22024.6761 | 22004.6275 | 22004.6275 | 22004.6275 | 22004.6275 | 22004.6275 | 22004.6275 | 22004.6275 | 22004.6275 | 22004.6275 | 22004.6275 | 22004.6275 | 22004.6275 | 22004.6275 | 22004.6275 | 22004.6275 | 22004.6275 |  | 15242.3215 | 19730.5793 | 20904.9535 | 20834.4632 | 20839.4402 | 20959.8434 | 21277.7899 | 21490.4763 | 21698.7869 | 21942.444 | 22168.1098 | 22387.2904 | 22412.1574 | 22668.0032 | 22473.741 | 22473.741 | 22473.741 | 22473.741 | 22473.741 | 22473.741 | 22473.741 | 22473.741 | 22473.741 | 22473.741 | 22473.741 | 22473.741 | 22473.741 | 22473.741 | 22473.741 | 22473.741
35% | 7422.2532 | 9853.5218 | 10515.3025 | 10496.0291 | 10495.3188 | 10570.7413 | 10653.506 | 10823.4244 | 10945.5251 | 11011.7604 | 11084.1896 | 11150.4949 | 11270.3083 | 11419.0173 | 11408.6228 | 11408.6228 | 11408.6228 | 11408.6228 | 11408.6228 | 11408.6228 | 11408.6228 | 11408.6228 | 11408.6228 | 11408.6228 | 11408.6228 | 11408.6228 | 11408.6228 | 11408.6228 | 11408.6228 | 11408.6228 |  | 20759.9869 | 26872.9779 | 28472.4713 | 28376.4638 | 28383.2424 | 28547.2311 | 28980.2731 | 29269.9512 | 29553.6695 | 29885.5295 | 30192.8856 | 30491.4088 | 30525.2776 | 30873.7386 | 30609.1541 | 30609.1541 | 30609.1541 | 30609.1541 | 30609.1541 | 30609.1541 | 30609.1541 | 30609.1541 | 30609.1541 | 30609.1541 | 30609.1541 | 30609.1541 | 30609.1541 | 30609.1541 | 30609.1541 | 30609.1541
30% | 3452.1096 | 4582.899 | 4890.695 | 4881.7308 | 4881.4005 | 4916.4797 | 4954.9738 | 5034.0033 | 5090.7926 | 5121.5988 | 5155.2859 | 5186.1246 | 5241.8501 | 5311.0151 | 5306.1806 | 5306.1806 | 5306.1806 | 5306.1806 | 5306.1806 | 5306.1806 | 5306.1806 | 5306.1806 | 5306.1806 | 5306.1806 | 5306.1806 | 5306.1806 | 5306.1806 | 5306.1806 | 5306.1806 | 5306.1806 |  | 19183.5111 | 24832.2926 | 26310.3234 | 26221.6065 | 26227.8703 | 26379.406 | 26779.5636 | 27047.2441 | 27309.4173 | 27616.0765 | 27900.0925 | 28175.9464 | 28207.2432 | 28529.2428 | 28284.7504 | 28284.7504 | 28284.7504 | 28284.7504 | 28284.7504 | 28284.7504 | 28284.7504 | 28284.7504 | 28284.7504 | 28284.7504 | 28284.7504 | 28284.7504 | 28284.7504 | 28284.7504 | 28284.7504 | 28284.7504
25% | 2357.031 | 3129.1112 | 3339.2681 | 3333.1476 | 3332.922 | 3356.8734 | 3383.1564 | 3437.1161 | 3475.8908 | 3496.9246 | 3519.9255 | 3540.9815 | 3579.0298 | 3626.2542 | 3622.9533 | 3622.9533 | 3622.9533 | 3622.9533 | 3622.9533 | 3622.9533 | 3622.9533 | 3622.9533 | 3622.9533 | 3622.9533 | 3622.9533 | 3622.9533 | 3622.9533 | 3622.9533 | 3622.9533 | 3622.9533 |  | 5533.3008 | 7162.6379 | 7588.9618 | 7563.3722 | 7565.179 | 7608.888 | 7724.3096 | 7801.5195 | 7877.1409 | 7965.5938 | 8047.5155 | 8127.0829 | 8136.1102 | 8228.9879 | 8158.4664 | 8158.4664 | 8158.4664 | 8158.4664 | 8158.4664 | 8158.4664 | 8158.4664 | 8158.4664 | 8158.4664 | 8158.4664 | 8158.4664 | 8158.4664 | 8158.4664 | 8158.4664 | 8158.4664 | 8158.4664
20% | 1427.8587 | 1895.5749 | 2022.8852 | 2019.1774 | 2019.0408 | 2033.5502 | 2049.4721 | 2082.1602 | 2105.6494 | 2118.3914 | 2132.325 | 2145.0805 | 2168.1297 | 2196.7376 | 2194.738 | 2194.738 | 2194.738 | 2194.738 | 2194.738 | 2194.738 | 2194.738 | 2194.738 | 2194.738 | 2194.738 | 2194.738 | 2194.738 | 2194.738 | 2194.738 | 2194.738 | 2194.738 |  | 1484.8203 | 1922.0408 | 2036.4417 | 2029.5749 | 2030.0597 | 2041.7887 | 2072.7613 | 2093.48 | 2113.7724 | 2137.5081 | 2159.4912 | 2180.8425 | 2183.2649 | 2208.1879 | 2189.264 | 2189.264 | 2189.264 | 2189.264 | 2189.264 | 2189.264 | 2189.264 | 2189.264 | 2189.264 | 2189.264 | 2189.264 | 2189.264 | 2189.264 | 2189.264 | 2189.264 | 2189.264
15% | 914.1778 | 1213.6303 | 1295.1399 | 1292.766 | 1292.6786 | 1301.9681 | 1312.162 | 1333.0904 | 1348.1292 | 1356.2872 | 1365.2081 | 1373.3747 | 1388.1318 | 1406.4479 | 1405.1676 | 1405.1676 | 1405.1676 | 1405.1676 | 1405.1676 | 1405.1676 | 1405.1676 | 1405.1676 | 1405.1676 | 1405.1676 | 1405.1676 | 1405.1676 | 1405.1676 | 1405.1676 | 1405.1676 | 1405.1676 |  | 818.9695 | 1060.1234 | 1123.2225 | 1119.4351 | 1119.7025 | 1126.1718 | 1143.255 | 1154.6827 | 1165.8752 | 1178.9669 | 1191.0919 | 1202.8685 | 1204.2046 | 1217.9511 | 1207.5134 | 1207.5134 | 1207.5134 | 1207.5134 | 1207.5134 | 1207.5134 | 1207.5134 | 1207.5134 | 1207.5134 | 1207.5134 | 1207.5134 | 1207.5134 | 1207.5134 | 1207.5134 | 1207.5134 | 1207.5134
10% | 611.8703 | 812.2975 | 866.8529 | 865.264 | 865.2055 | 871.4231 | 878.246 | 892.2536 | 902.3193 | 907.7795 | 913.7504 | 919.2164 | 929.0935 | 941.3527 | 940.4958 | 940.4958 | 940.4958 | 940.4958 | 940.4958 | 940.4958 | 940.4958 | 940.4958 | 940.4958 | 940.4958 | 940.4958 | 940.4958 | 940.4958 | 940.4958 | 940.4958 | 940.4958 |  | 191.3984 | 247.7576 | 262.5043 | 261.6191 | 261.6816 | 263.1935 | 267.186 | 269.8567 | 272.4725 | 275.5321 | 278.3658 | 281.118 | 281.4303 | 284.643 | 282.2036 | 282.2036 | 282.2036 | 282.2036 | 282.2036 | 282.2036 | 282.2036 | 282.2036 | 282.2036 | 282.2036 | 282.2036 | 282.2036 | 282.2036 | 282.2036 | 282.2036 | 282.2036
5% | 435.3228 | 577.9192 | 616.7333 | 615.6029 | 615.5612 | 619.9848 | 624.8391 | 634.805 | 641.9663 | 645.8511 | 650.0991 | 653.988 | 661.0151 | 669.7371 | 669.1274 | 669.1274 | 669.1274 | 669.1274 | 669.1274 | 669.1274 | 669.1274 | 669.1274 | 669.1274 | 669.1274 | 669.1274 | 669.1274 | 669.1274 | 669.1274 | 669.1274 | 669.1274 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9.992e-14% | 38.2117 | 50.7285 | 54.1355 | 54.0363 | 54.0326 | 54.4209 | 54.847 | 55.7218 | 56.3504 | 56.6914 | 57.0643 | 57.4056 | 58.0224 | 58.788 | 58.7345 | 58.7345 | 58.7345 | 58.7345 | 58.7345 | 58.7345 | 58.7345 | 58.7345 | 58.7345 | 58.7345 | 58.7345 | 58.7345 | 58.7345 | 58.7345 | 58.7345 | 58.7345 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E @ R (MWh) | 102337.6118 | 135859.8063 | 144984.402 | 144718.661 | 144708.8672 | 145748.789 | 146889.9441 | 149232.7692 | 150916.2863 | 151829.5355 | 152828.1856 | 153742.3981 | 155394.3791 | 157444.7704 | 157301.4516 | 157301.4516 | 157301.4516 | 157301.4516 | 157301.4516 | 157301.4516 | 157301.4516 | 157301.4516 | 157301.4516 | 157301.4516 | 157301.4516 | 157301.4516 | 157301.4516 | 157301.4516 | 157301.4516 | 157301.4516 | E @ R (MWh) | 99292.8528 | 128530.651 | 136180.8614 | 135721.6674 | 135754.0887 | 136538.4294 | 138609.6244 | 139995.1247 | 141352.1196 | 142939.3714 | 144409.4236 | 145837.2289 | 145999.2196 | 147665.8725 | 146400.3925 | 146400.3925 | 146400.3925 | 146400.3925 | 146400.3925 | 146400.3925 | 146400.3925 | 146400.3925 | 146400.3925 | 146400.3925 | 146400.3925 | 146400.3925 | 146400.3925 | 146400.3925 | 146400.3925 | 146400.3925
Option 6 Summer POE50 W E @ R (MWh) N 2 | 71636.3283 | 95101.8644 | 101489.0814 | 101303.0627 | 101296.207 | 102024.1523 | 102822.9609 | 104462.9384 | 105641.4004 | 106280.6749 | 106979.7299 | 107619.6787 | 108776.0654 | 110211.3393 | 110111.0161 | 110111.0161 | 110111.0161 | 110111.0161 | 110111.0161 | 110111.0161 | 110111.0161 | 110111.0161 | 110111.0161 | 110111.0161 | 110111.0161 | 110111.0161 | 110111.0161 | 110111.0161 | 110111.0161 | 110111.0161 | Option 6 Summer POE10 W E @ R (MWh) N 2 | 29787.8558 | 38559.1953 | 40854.2584 | 40716.5002 | 40726.2266 | 40961.5288 | 41582.8873 | 41998.5374 | 42405.6359 | 42881.8114 | 43322.8271 | 43751.1687 | 43799.7659 | 44299.7618 | 43920.1178 | 43920.1178 | 43920.1178 | 43920.1178 | 43920.1178 | 43920.1178 | 43920.1178 | 43920.1178 | 43920.1178 | 43920.1178 | 43920.1178 | 43920.1178 | 43920.1178 | 43920.1178 | 43920.1178 | 43920.1178
Option 7 -
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | 66.5813 | 92.3179 | 99.0036 | 100.1408 | 101.0254 | 102.5536 | 106.0346 | 108.362 | 111.3134 | 112.8438 | 114.1881 | 111.6988 | 114.6091 | 119.1862 | 115.707 | 115.707 | 115.707 | 115.707 | 115.707 | 115.707 | 115.707 | 115.707 | 115.707 | 115.707 | 115.707 | 115.707 | 115.707 | 115.707 | 115.707 | 115.707 |  | 71.2634 | 96.6755 | 103.6223 | 104.6946 | 105.3727 | 106.8677 | 110.4032 | 112.3303 | 116.0076 | 127.1923 | 117.9641 | 116.1567 | 118.5887 | 123.9113 | 120.303 | 120.303 | 120.303 | 120.303 | 120.303 | 120.303 | 120.303 | 120.303 | 120.303 | 120.303 | 120.303 | 120.303 | 120.303 | 120.303 | 120.303 | 120.303
98% | 79.0946 | 109.6681 | 117.6103 | 118.9612 | 120.012 | 121.8275 | 125.9627 | 128.7276 | 132.2337 | 134.0516 | 135.6486 | 132.6915 | 136.1487 | 141.586 | 137.453 | 137.453 | 137.453 | 137.453 | 137.453 | 137.453 | 137.453 | 137.453 | 137.453 | 137.453 | 137.453 | 137.453 | 137.453 | 137.453 | 137.453 | 137.453 |  | 84.6567 | 114.8446 | 123.097 | 124.3709 | 125.1764 | 126.9524 | 131.1523 | 133.4417 | 137.8101 | 151.0968 | 140.1342 | 137.9871 | 140.8762 | 147.1992 | 142.9127 | 142.9127 | 142.9127 | 142.9127 | 142.9127 | 142.9127 | 142.9127 | 142.9127 | 142.9127 | 142.9127 | 142.9127 | 142.9127 | 142.9127 | 142.9127 | 142.9127 | 142.9127
97% | 156.5832 | 217.1095 | 232.8326 | 235.507 | 237.5873 | 241.1813 | 249.3678 | 254.8414 | 261.7824 | 265.3814 | 268.543 | 262.6887 | 269.5329 | 280.2972 | 272.115 | 272.115 | 272.115 | 272.115 | 272.115 | 272.115 | 272.115 | 272.115 | 272.115 | 272.115 | 272.115 | 272.115 | 272.115 | 272.115 | 272.115 | 272.115 |  | 167.5944 | 227.3573 | 243.6946 | 246.2165 | 247.8111 | 251.327 | 259.6417 | 264.1739 | 272.822 | 299.1257 | 277.423 | 273.1725 | 278.892 | 291.4096 | 282.9237 | 282.9237 | 282.9237 | 282.9237 | 282.9237 | 282.9237 | 282.9237 | 282.9237 | 282.9237 | 282.9237 | 282.9237 | 282.9237 | 282.9237 | 282.9237 | 282.9237 | 282.9237
95% | 462.5227 | 641.3081 | 687.7517 | 695.6514 | 701.7962 | 712.4124 | 736.5942 | 752.7622 | 773.2648 | 783.8959 | 793.2346 | 775.942 | 796.1588 | 827.9549 | 803.7859 | 803.7859 | 803.7859 | 803.7859 | 803.7859 | 803.7859 | 803.7859 | 803.7859 | 803.7859 | 803.7859 | 803.7859 | 803.7859 | 803.7859 | 803.7859 | 803.7859 | 803.7859 |  | 495.0481 | 671.5786 | 719.8364 | 727.2857 | 731.996 | 742.3814 | 766.9415 | 780.329 | 805.8742 | 883.5714 | 819.4649 | 806.9095 | 823.8041 | 860.7791 | 835.7129 | 835.7129 | 835.7129 | 835.7129 | 835.7129 | 835.7129 | 835.7129 | 835.7129 | 835.7129 | 835.7129 | 835.7129 | 835.7129 | 835.7129 | 835.7129 | 835.7129 | 835.7129
90% | 2550.165 | 3535.9158 | 3791.9875 | 3835.5434 | 3869.4233 | 3927.9564 | 4061.2852 | 4150.4292 | 4263.4726 | 4322.0883 | 4373.5777 | 4278.2333 | 4389.7006 | 4565.012 | 4431.7536 | 4431.7536 | 4431.7536 | 4431.7536 | 4431.7536 | 4431.7536 | 4431.7536 | 4431.7536 | 4431.7536 | 4431.7536 | 4431.7536 | 4431.7536 | 4431.7536 | 4431.7536 | 4431.7536 | 4431.7536 |  | 2729.4971 | 3702.8155 | 3968.8899 | 4009.9623 | 4035.9325 | 4093.1938 | 4228.6083 | 4302.4214 | 4443.2678 | 4871.6587 | 4518.2015 | 4448.976 | 4542.1258 | 4745.9912 | 4607.7865 | 4607.7865 | 4607.7865 | 4607.7865 | 4607.7865 | 4607.7865 | 4607.7865 | 4607.7865 | 4607.7865 | 4607.7865 | 4607.7865 | 4607.7865 | 4607.7865 | 4607.7865 | 4607.7865 | 4607.7865
85% | 6229.8705 | 8637.9889 | 9263.5537 | 9369.9577 | 9452.724 | 9595.7162 | 9921.4289 | 10139.2013 | 10415.3582 | 10558.5521 | 10684.3371 | 10451.4176 | 10723.7241 | 11151.9973 | 10826.4566 | 10826.4566 | 10826.4566 | 10826.4566 | 10826.4566 | 10826.4566 | 10826.4566 | 10826.4566 | 10826.4566 | 10826.4566 | 10826.4566 | 10826.4566 | 10826.4566 | 10826.4566 | 10826.4566 | 10826.4566 |  | 6667.9659 | 9045.7131 | 9695.7136 | 9796.0508 | 9859.4941 | 9999.3792 | 10330.1872 | 10510.5072 | 10854.585 | 11901.1132 | 11037.6427 | 10868.5297 | 11096.0879 | 11594.1165 | 11256.4923 | 11256.4923 | 11256.4923 | 11256.4923 | 11256.4923 | 11256.4923 | 11256.4923 | 11256.4923 | 11256.4923 | 11256.4923 | 11256.4923 | 11256.4923 | 11256.4923 | 11256.4923 | 11256.4923 | 11256.4923
80% | 9683.0656 | 13425.9956 | 14398.3087 | 14563.692 | 14692.3353 | 14914.5876 | 15420.8418 | 15759.3246 | 16188.5543 | 16411.1201 | 16606.6272 | 16244.6013 | 16667.8463 | 17333.5099 | 16827.5231 | 16827.5231 | 16827.5231 | 16827.5231 | 16827.5231 | 16827.5231 | 16827.5231 | 16827.5231 | 16827.5231 | 16827.5231 | 16827.5231 | 16827.5231 | 16827.5231 | 16827.5231 | 16827.5231 | 16827.5231 |  | 10363.9958 | 14059.7198 | 15070.0133 | 15225.967 | 15324.5767 | 15541.9996 | 16056.1734 | 16336.4441 | 16871.243 | 18497.858 | 17155.7689 | 16892.9172 | 17246.6101 | 18020.6942 | 17495.9261 | 17495.9261 | 17495.9261 | 17495.9261 | 17495.9261 | 17495.9261 | 17495.9261 | 17495.9261 | 17495.9261 | 17495.9261 | 17495.9261 | 17495.9261 | 17495.9261 | 17495.9261 | 17495.9261 | 17495.9261
75% | 10683.1238 | 14812.6201 | 15885.3529 | 16067.8168 | 16209.7463 | 16454.9526 | 17013.4923 | 17386.9332 | 17860.4934 | 18106.0455 | 18321.7445 | 17922.3288 | 18389.2862 | 19123.699 | 18565.4543 | 18565.4543 | 18565.4543 | 18565.4543 | 18565.4543 | 18565.4543 | 18565.4543 | 18565.4543 | 18565.4543 | 18565.4543 | 18565.4543 | 18565.4543 | 18565.4543 | 18565.4543 | 18565.4543 | 18565.4543 |  | 11434.3798 | 15511.7948 | 16626.4305 | 16798.4909 | 16907.2849 | 17147.1631 | 17714.4402 | 18023.6571 | 18613.6895 | 20408.2999 | 18927.601 | 18637.6022 | 19027.8242 | 19881.855 | 19302.8894 | 19302.8894 | 19302.8894 | 19302.8894 | 19302.8894 | 19302.8894 | 19302.8894 | 19302.8894 | 19302.8894 | 19302.8894 | 19302.8894 | 19302.8894 | 19302.8894 | 19302.8894 | 19302.8894 | 19302.8894
70% | 11478.4193 | 15915.3323 | 17067.9236 | 17263.9709 | 17416.4662 | 17679.9267 | 18280.0463 | 18681.2877 | 19190.1017 | 19453.9337 | 19685.6902 | 19256.5404 | 19758.26 | 20547.3454 | 19947.5428 | 19947.5428 | 19947.5428 | 19947.5428 | 19947.5428 | 19947.5428 | 19947.5428 | 19947.5428 | 19947.5428 | 19947.5428 | 19947.5428 | 19947.5428 | 19947.5428 | 19947.5428 | 19947.5428 | 19947.5428 |  | 12285.6019 | 16666.5563 | 17864.1701 | 18049.0394 | 18165.9325 | 18423.6682 | 19033.1757 | 19365.4119 | 19999.3688 | 21927.5773 | 20336.6492 | 20025.0617 | 20444.3333 | 21361.9417 | 20739.8755 | 20739.8755 | 20739.8755 | 20739.8755 | 20739.8755 | 20739.8755 | 20739.8755 | 20739.8755 | 20739.8755 | 20739.8755 | 20739.8755 | 20739.8755 | 20739.8755 | 20739.8755 | 20739.8755 | 20739.8755
65% | 12096.053 | 16771.7086 | 17986.3189 | 18192.9151 | 18353.6159 | 18631.2528 | 19263.6638 | 19686.4953 | 20222.6877 | 20500.7161 | 20744.943 | 20292.7014 | 20821.4176 | 21652.9624 | 21020.8854 | 21020.8854 | 21020.8854 | 21020.8854 | 21020.8854 | 21020.8854 | 21020.8854 | 21020.8854 | 21020.8854 | 21020.8854 | 21020.8854 | 21020.8854 | 21020.8854 | 21020.8854 | 21020.8854 | 21020.8854 |  | 12946.6687 | 17563.3547 | 18825.4101 | 19020.2268 | 19143.4097 | 19415.0137 | 20057.3178 | 20407.431 | 21075.5001 | 23107.4621 | 21430.9289 | 21102.5754 | 21544.4074 | 22511.3907 | 21855.8521 | 21855.8521 | 21855.8521 | 21855.8521 | 21855.8521 | 21855.8521 | 21855.8521 | 21855.8521 | 21855.8521 | 21855.8521 | 21855.8521 | 21855.8521 | 21855.8521 | 21855.8521 | 21855.8521 | 21855.8521
60% | 13316.2645 | 18463.5854 | 19800.7217 | 20028.1587 | 20205.0705 | 20510.7145 | 21206.9211 | 21672.4066 | 22262.6883 | 22568.7633 | 22837.627 | 22339.7647 | 22921.8162 | 23837.2445 | 23141.4056 | 23141.4056 | 23141.4056 | 23141.4056 | 23141.4056 | 23141.4056 | 23141.4056 | 23141.4056 | 23141.4056 | 23141.4056 | 23141.4056 | 23141.4056 | 23141.4056 | 23141.4056 | 23141.4056 | 23141.4056 |  | 14252.6876 | 19335.0902 | 20724.4577 | 20938.927 | 21074.5362 | 21373.5387 | 22080.6365 | 22466.068 | 23201.5297 | 25438.4696 | 23592.813 | 23231.3363 | 23717.7389 | 24782.2684 | 24060.6012 | 24060.6012 | 24060.6012 | 24060.6012 | 24060.6012 | 24060.6012 | 24060.6012 | 24060.6012 | 24060.6012 | 24060.6012 | 24060.6012 | 24060.6012 | 24060.6012 | 24060.6012 | 24060.6012 | 24060.6012
55% | 14813.5078 | 20539.579 | 22027.0592 | 22280.0685 | 22476.8718 | 22816.8815 | 23591.3677 | 24109.191 | 24765.8423 | 25106.3315 | 25405.4256 | 24851.585 | 25499.0807 | 26517.4372 | 25743.3602 | 25743.3602 | 25743.3602 | 25743.3602 | 25743.3602 | 25743.3602 | 25743.3602 | 25743.3602 | 25743.3602 | 25743.3602 | 25743.3602 | 25743.3602 | 25743.3602 | 25743.3602 | 25743.3602 | 25743.3602 |  | 15855.2197 | 21509.0734 | 23054.6574 | 23293.241 | 23444.0977 | 23776.7193 | 24563.3211 | 24992.0894 | 25810.2444 | 28298.6996 | 26245.5225 | 25843.4024 | 26384.4947 | 27568.7169 | 26765.9075 | 26765.9075 | 26765.9075 | 26765.9075 | 26765.9075 | 26765.9075 | 26765.9075 | 26765.9075 | 26765.9075 | 26765.9075 | 26765.9075 | 26765.9075 | 26765.9075 | 26765.9075 | 26765.9075 | 26765.9075
50% | 15014.9247 | 20818.8523 | 22326.5575 | 22583.007 | 22782.4862 | 23127.1189 | 23912.1357 | 24436.9997 | 25102.5795 | 25447.6982 | 25750.859 | 25189.488 | 25845.7876 | 26877.9905 | 26093.3885 | 26093.3885 | 26093.3885 | 26093.3885 | 26093.3885 | 26093.3885 | 26093.3885 | 26093.3885 | 26093.3885 | 26093.3885 | 26093.3885 | 26093.3885 | 26093.3885 | 26093.3885 | 26093.3885 | 26093.3885 |  | 16070.8005 | 21801.5288 | 23368.1279 | 23609.9554 | 23762.8633 | 24100.0075 | 24897.3046 | 25331.9028 | 26161.1821 | 28683.4724 | 26602.3787 | 26194.791 | 26743.2404 | 27943.5643 | 27129.8392 | 27129.8392 | 27129.8392 | 27129.8392 | 27129.8392 | 27129.8392 | 27129.8392 | 27129.8392 | 27129.8392 | 27129.8392 | 27129.8392 | 27129.8392 | 27129.8392 | 27129.8392 | 27129.8392 | 27129.8392
45% | 11588.8305 | 16068.4223 | 17232.1005 | 17430.0335 | 17583.9957 | 17849.9904 | 18455.8826 | 18860.9836 | 19374.6918 | 19641.0617 | 19875.0474 | 19441.7696 | 19948.3153 | 20744.9909 | 20139.4188 | 20139.4188 | 20139.4188 | 20139.4188 | 20139.4188 | 20139.4188 | 20139.4188 | 20139.4188 | 20139.4188 | 20139.4188 | 20139.4188 | 20139.4188 | 20139.4188 | 20139.4188 | 20139.4188 | 20139.4188 |  | 12403.7774 | 16826.8724 | 18036.0061 | 18222.6536 | 18340.6711 | 18600.8859 | 19216.2564 | 19551.6884 | 20191.7433 | 22138.4993 | 20532.268 | 20217.6833 | 20640.988 | 21567.4228 | 20939.373 | 20939.373 | 20939.373 | 20939.373 | 20939.373 | 20939.373 | 20939.373 | 20939.373 | 20939.373 | 20939.373 | 20939.373 | 20939.373 | 20939.373 | 20939.373 | 20939.373 | 20939.373
40% | 5693.5395 | 7894.3425 | 8466.0523 | 8563.2959 | 8638.9368 | 8769.6188 | 9067.2909 | 9266.3151 | 9518.6977 | 9649.5639 | 9764.5201 | 9551.6527 | 9800.5162 | 10191.9194 | 9894.4045 | 9894.4045 | 9894.4045 | 9894.4045 | 9894.4045 | 9894.4045 | 9894.4045 | 9894.4045 | 9894.4045 | 9894.4045 | 9894.4045 | 9894.4045 | 9894.4045 | 9894.4045 | 9894.4045 | 9894.4045 |  | 6093.9192 | 8266.9656 | 8861.0075 | 8952.7065 | 9010.688 | 9138.5304 | 9440.8591 | 9605.6552 | 9920.1113 | 10876.5437 | 10087.4095 | 9932.8555 | 10140.8232 | 10595.9764 | 10287.4184 | 10287.4184 | 10287.4184 | 10287.4184 | 10287.4184 | 10287.4184 | 10287.4184 | 10287.4184 | 10287.4184 | 10287.4184 | 10287.4184 | 10287.4184 | 10287.4184 | 10287.4184 | 10287.4184 | 10287.4184
35% | 2127.9257 | 2950.4624 | 3164.1354 | 3200.4796 | 3228.75 | 3277.5916 | 3388.8447 | 3463.2288 | 3557.5552 | 3606.4657 | 3649.4298 | 3569.872 | 3662.8832 | 3809.1677 | 3697.9734 | 3697.9734 | 3697.9734 | 3697.9734 | 3697.9734 | 3697.9734 | 3697.9734 | 3697.9734 | 3697.9734 | 3697.9734 | 3697.9734 | 3697.9734 | 3697.9734 | 3697.9734 | 3697.9734 | 3697.9734 |  | 2277.5652 | 3089.728 | 3311.7475 | 3346.0195 | 3367.6897 | 3415.47 | 3528.4635 | 3590.0551 | 3707.5811 | 4065.0419 | 3770.1078 | 3712.3442 | 3790.0708 | 3960.1816 | 3844.8599 | 3844.8599 | 3844.8599 | 3844.8599 | 3844.8599 | 3844.8599 | 3844.8599 | 3844.8599 | 3844.8599 | 3844.8599 | 3844.8599 | 3844.8599 | 3844.8599 | 3844.8599 | 3844.8599 | 3844.8599
30% | 1061.2862 | 1471.5199 | 1578.0877 | 1596.2141 | 1610.3137 | 1634.673 | 1690.1596 | 1727.2581 | 1774.3027 | 1798.6964 | 1820.1244 | 1780.4456 | 1826.8342 | 1899.7925 | 1844.3351 | 1844.3351 | 1844.3351 | 1844.3351 | 1844.3351 | 1844.3351 | 1844.3351 | 1844.3351 | 1844.3351 | 1844.3351 | 1844.3351 | 1844.3351 | 1844.3351 | 1844.3351 | 1844.3351 | 1844.3351 |  | 1135.9177 | 1540.9775 | 1651.708 | 1668.8009 | 1679.6088 | 1703.4388 | 1759.7934 | 1790.5117 | 1849.1269 | 2027.4077 | 1880.3116 | 1851.5025 | 1890.268 | 1975.1094 | 1917.5936 | 1917.5936 | 1917.5936 | 1917.5936 | 1917.5936 | 1917.5936 | 1917.5936 | 1917.5936 | 1917.5936 | 1917.5936 | 1917.5936 | 1917.5936 | 1917.5936 | 1917.5936 | 1917.5936 | 1917.5936
25% | 625.6637 | 867.5102 | 930.3354 | 941.0215 | 949.3337 | 963.6944 | 996.4056 | 1018.2764 | 1046.0107 | 1060.3916 | 1073.0242 | 1049.6322 | 1076.9798 | 1119.9911 | 1087.2972 | 1087.2972 | 1087.2972 | 1087.2972 | 1087.2972 | 1087.2972 | 1087.2972 | 1087.2972 | 1087.2972 | 1087.2972 | 1087.2972 | 1087.2972 | 1087.2972 | 1087.2972 | 1087.2972 | 1087.2972 |  | 669.6615 | 908.4578 | 973.7371 | 983.8139 | 990.1855 | 1004.2341 | 1037.457 | 1055.5665 | 1090.1221 | 1195.2246 | 1108.5065 | 1091.5226 | 1114.3762 | 1164.393 | 1130.4855 | 1130.4855 | 1130.4855 | 1130.4855 | 1130.4855 | 1130.4855 | 1130.4855 | 1130.4855 | 1130.4855 | 1130.4855 | 1130.4855 | 1130.4855 | 1130.4855 | 1130.4855 | 1130.4855 | 1130.4855
20% | 316.1776 | 438.3942 | 470.1428 | 475.543 | 479.7435 | 487.0006 | 503.5312 | 514.5835 | 528.599 | 535.8664 | 542.2502 | 530.4291 | 544.2492 | 565.9848 | 549.463 | 549.463 | 549.463 | 549.463 | 549.463 | 549.463 | 549.463 | 549.463 | 549.463 | 549.463 | 549.463 | 549.463 | 549.463 | 549.463 | 549.463 | 549.463 |  | 338.4118 | 459.0869 | 492.0757 | 497.168 | 500.3879 | 507.4873 | 524.2764 | 533.428 | 550.8906 | 604.0039 | 560.1811 | 551.5983 | 563.1473 | 588.4232 | 571.2881 | 571.2881 | 571.2881 | 571.2881 | 571.2881 | 571.2881 | 571.2881 | 571.2881 | 571.2881 | 571.2881 | 571.2881 | 571.2881 | 571.2881 | 571.2881 | 571.2881 | 571.2881
15% | 128.8131 | 178.605 | 191.5396 | 193.7397 | 195.4511 | 198.4077 | 205.1423 | 209.6451 | 215.3552 | 218.3159 | 220.9167 | 216.1007 | 221.7311 | 230.5864 | 223.8553 | 223.8553 | 223.8553 | 223.8553 | 223.8553 | 223.8553 | 223.8553 | 223.8553 | 223.8553 | 223.8553 | 223.8553 | 223.8553 | 223.8553 | 223.8553 | 223.8553 | 223.8553 |  | 137.8715 | 187.0354 | 200.4753 | 202.5499 | 203.8617 | 206.7541 | 213.5941 | 217.3225 | 224.4369 | 246.0756 | 228.2219 | 224.7252 | 229.4304 | 239.728 | 232.747 | 232.747 | 232.747 | 232.747 | 232.747 | 232.747 | 232.747 | 232.747 | 232.747 | 232.747 | 232.747 | 232.747 | 232.747 | 232.747 | 232.747 | 232.747
10% | 51.8598 | 71.9059 | 77.1134 | 77.9991 | 78.6881 | 79.8784 | 82.5898 | 84.4026 | 86.7014 | 87.8934 | 88.9405 | 87.0016 | 89.2684 | 92.8335 | 90.1236 | 90.1236 | 90.1236 | 90.1236 | 90.1236 | 90.1236 | 90.1236 | 90.1236 | 90.1236 | 90.1236 | 90.1236 | 90.1236 | 90.1236 | 90.1236 | 90.1236 | 90.1236 |  | 55.5067 | 75.3 | 80.7108 | 81.5461 | 82.0742 | 83.2387 | 85.9924 | 87.4935 | 90.3577 | 99.0694 | 91.8816 | 90.4738 | 92.3681 | 96.5139 | 93.7033 | 93.7033 | 93.7033 | 93.7033 | 93.7033 | 93.7033 | 93.7033 | 93.7033 | 93.7033 | 93.7033 | 93.7033 | 93.7033 | 93.7033 | 93.7033 | 93.7033 | 93.7033
5% | 44.1645 | 61.236 | 65.6707 | 66.425 | 67.0118 | 68.0255 | 70.3345 | 71.8783 | 73.8361 | 74.8512 | 75.7429 | 74.0917 | 76.0221 | 79.0582 | 76.7504 | 76.7504 | 76.7504 | 76.7504 | 76.7504 | 76.7504 | 76.7504 | 76.7504 | 76.7504 | 76.7504 | 76.7504 | 76.7504 | 76.7504 | 76.7504 | 76.7504 | 76.7504 |  | 47.2702 | 64.1264 | 68.7344 | 69.4457 | 69.8954 | 70.8871 | 73.2323 | 74.5106 | 76.9498 | 84.3688 | 78.2475 | 77.0487 | 78.6618 | 82.1924 | 79.799 | 79.799 | 79.799 | 79.799 | 79.799 | 79.799 | 79.799 | 79.799 | 79.799 | 79.799 | 79.799 | 79.799 | 79.799 | 79.799 | 79.799 | 79.799
9.992e-14% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E @ R (MWh) | 118268.4368 | 163984.3799 | 175860.1598 | 177880.1417 | 179451.3847 | 182165.962 | 188349.3233 | 192483.5334 | 197726.1221 | 200444.5279 | 202832.442 | 198410.6765 | 203580.168 | 211710.5473 | 205530.4523 | 205530.4523 | 205530.4523 | 205530.4523 | 205530.4523 | 205530.4523 | 205530.4523 | 205530.4523 | 205530.4523 | 205530.4523 | 205530.4523 | 205530.4523 | 205530.4523 | 205530.4523 | 205530.4523 | 205530.4523 | E @ R (MWh) | 126585.2808 | 171724.6525 | 184064.3234 | 185969.1325 | 187173.5461 | 189829.1378 | 196109.2281 | 199532.4392 | 206064.4443 | 225931.832 | 209539.6283 | 206329.172 | 210649.1573 | 220103.7788 | 213694.29 | 213694.29 | 213694.29 | 213694.29 | 213694.29 | 213694.29 | 213694.29 | 213694.29 | 213694.29 | 213694.29 | 213694.29 | 213694.29 | 213694.29 | 213694.29 | 213694.29 | 213694.29
Option 7 Winter POE50 W E @ R (MWh) N 2 | 82787.9057 | 114789.066 | 123102.1118 | 124516.0992 | 125615.9693 | 127516.1734 | 131844.5263 | 134738.4734 | 138408.2855 | 140311.1695 | 141982.7094 | 138887.4736 | 142506.1176 | 148197.3831 | 143871.3166 | 143871.3166 | 143871.3166 | 143871.3166 | 143871.3166 | 143871.3166 | 143871.3166 | 143871.3166 | 143871.3166 | 143871.3166 | 143871.3166 | 143871.3166 | 143871.3166 | 143871.3166 | 143871.3166 | 143871.3166 | Option 7 Winter POE10 W E @ R (MWh) N 2 | 37975.5842 | 51517.3957 | 55219.297 | 55790.7397 | 56152.0638 | 56948.7413 | 58832.7684 | 59859.7318 | 61819.3333 | 67779.5496 | 62861.8885 | 61898.7516 | 63194.7472 | 66031.1336 | 64108.287 | 64108.287 | 64108.287 | 64108.287 | 64108.287 | 64108.287 | 64108.287 | 64108.287 | 64108.287 | 64108.287 | 64108.287 | 64108.287 | 64108.287 | 64108.287 | 64108.287 | 64108.287
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 85.8327 | 111.1071 | 117.7202 | 117.3233 | 117.3513 | 118.0293 | 119.8198 | 121.0174 | 122.1905 | 123.5626 | 124.8333 | 126.0676 | 126.2076 | 127.6483 | 126.5544 | 126.5544 | 126.5544 | 126.5544 | 126.5544 | 126.5544 | 126.5544 | 126.5544 | 126.5544 | 126.5544 | 126.5544 | 126.5544 | 126.5544 | 126.5544 | 126.5544 | 126.5544
98% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 42.4851 | 54.9952 | 58.2686 | 58.0721 | 58.0859 | 58.4216 | 59.3078 | 59.9006 | 60.4812 | 61.1604 | 61.7894 | 62.4003 | 62.4696 | 63.1827 | 62.6413 | 62.6413 | 62.6413 | 62.6413 | 62.6413 | 62.6413 | 62.6413 | 62.6413 | 62.6413 | 62.6413 | 62.6413 | 62.6413 | 62.6413 | 62.6413 | 62.6413 | 62.6413
97% | 18.864 | 25.0432 | 26.7251 | 26.6761 | 26.6743 | 26.866 | 27.0764 | 27.5082 | 27.8185 | 27.9869 | 28.171 | 28.3395 | 28.644 | 29.0219 | 28.9955 | 28.9955 | 28.9955 | 28.9955 | 28.9955 | 28.9955 | 28.9955 | 28.9955 | 28.9955 | 28.9955 | 28.9955 | 28.9955 | 28.9955 | 28.9955 | 28.9955 | 28.9955 |  | 84.1075 | 108.8738 | 115.354 | 114.965 | 114.9925 | 115.6569 | 117.4113 | 118.5849 | 119.7344 | 121.0789 | 122.3241 | 123.5336 | 123.6708 | 125.0825 | 124.0106 | 124.0106 | 124.0106 | 124.0106 | 124.0106 | 124.0106 | 124.0106 | 124.0106 | 124.0106 | 124.0106 | 124.0106 | 124.0106 | 124.0106 | 124.0106 | 124.0106 | 124.0106
95% | 92.8689 | 123.2894 | 131.5698 | 131.3286 | 131.3197 | 132.2634 | 133.299 | 135.4251 | 136.9528 | 137.7816 | 138.6878 | 139.5174 | 141.0166 | 142.8772 | 142.7472 | 142.7472 | 142.7472 | 142.7472 | 142.7472 | 142.7472 | 142.7472 | 142.7472 | 142.7472 | 142.7472 | 142.7472 | 142.7472 | 142.7472 | 142.7472 | 142.7472 | 142.7472 |  | 124.2203 | 160.7982 | 170.369 | 169.7945 | 169.8351 | 170.8163 | 173.4075 | 175.1408 | 176.8385 | 178.8242 | 180.6633 | 182.4496 | 182.6522 | 184.7373 | 183.1541 | 183.1541 | 183.1541 | 183.1541 | 183.1541 | 183.1541 | 183.1541 | 183.1541 | 183.1541 | 183.1541 | 183.1541 | 183.1541 | 183.1541 | 183.1541 | 183.1541 | 183.1541
90% | 161.0694 | 213.8301 | 228.1913 | 227.7731 | 227.7577 | 229.3944 | 231.1905 | 234.8778 | 237.5275 | 238.9649 | 240.5367 | 241.9755 | 244.5756 | 247.8027 | 247.5772 | 247.5772 | 247.5772 | 247.5772 | 247.5772 | 247.5772 | 247.5772 | 247.5772 | 247.5772 | 247.5772 | 247.5772 | 247.5772 | 247.5772 | 247.5772 | 247.5772 | 247.5772 |  | 538.6113 | 697.2109 | 738.7092 | 736.2183 | 736.3942 | 740.6488 | 751.884 | 759.3996 | 766.7606 | 775.3706 | 783.3448 | 791.0899 | 791.9686 | 801.0093 | 794.1448 | 794.1448 | 794.1448 | 794.1448 | 794.1448 | 794.1448 | 794.1448 | 794.1448 | 794.1448 | 794.1448 | 794.1448 | 794.1448 | 794.1448 | 794.1448 | 794.1448 | 794.1448
85% | 457.0889 | 606.8151 | 647.57 | 646.383 | 646.3393 | 650.9841 | 656.081 | 666.5452 | 674.0646 | 678.1436 | 682.6041 | 686.6874 | 694.0659 | 703.2239 | 702.5838 | 702.5838 | 702.5838 | 702.5838 | 702.5838 | 702.5838 | 702.5838 | 702.5838 | 702.5838 | 702.5838 | 702.5838 | 702.5838 | 702.5838 | 702.5838 | 702.5838 | 702.5838 |  | 509.4971 | 659.5238 | 698.779 | 696.4228 | 696.5891 | 700.6138 | 711.2416 | 718.351 | 725.3141 | 733.4587 | 741.0019 | 748.3283 | 749.1595 | 757.7115 | 751.218 | 751.218 | 751.218 | 751.218 | 751.218 | 751.218 | 751.218 | 751.218 | 751.218 | 751.218 | 751.218 | 751.218 | 751.218 | 751.218 | 751.218 | 751.218
80% | 638.4734 | 847.6148 | 904.5422 | 902.8842 | 902.8231 | 909.3111 | 916.4306 | 931.0473 | 941.5505 | 947.2482 | 953.4787 | 959.1824 | 969.4889 | 982.2811 | 981.3869 | 981.3869 | 981.3869 | 981.3869 | 981.3869 | 981.3869 | 981.3869 | 981.3869 | 981.3869 | 981.3869 | 981.3869 | 981.3869 | 981.3869 | 981.3869 | 981.3869 | 981.3869 |  | 355.8393 | 460.6198 | 488.0361 | 486.3905 | 486.5067 | 489.3176 | 496.7402 | 501.7054 | 506.5685 | 512.2568 | 517.5251 | 522.642 | 523.2225 | 529.1954 | 524.6602 | 524.6602 | 524.6602 | 524.6602 | 524.6602 | 524.6602 | 524.6602 | 524.6602 | 524.6602 | 524.6602 | 524.6602 | 524.6602 | 524.6602 | 524.6602 | 524.6602 | 524.6602
75% | 1664.3841 | 2209.5776 | 2357.9769 | 2353.655 | 2353.4957 | 2370.4087 | 2388.968 | 2427.0709 | 2454.4511 | 2469.3039 | 2485.5456 | 2500.414 | 2527.2813 | 2560.6281 | 2558.2972 | 2558.2972 | 2558.2972 | 2558.2972 | 2558.2972 | 2558.2972 | 2558.2972 | 2558.2972 | 2558.2972 | 2558.2972 | 2558.2972 | 2558.2972 | 2558.2972 | 2558.2972 | 2558.2972 | 2558.2972 |  | 635.1192 | 822.1366 | 871.0705 | 868.1333 | 868.3407 | 873.3577 | 886.6059 | 895.4682 | 904.1481 | 914.3008 | 923.7039 | 932.8368 | 933.8729 | 944.5335 | 936.439 | 936.439 | 936.439 | 936.439 | 936.439 | 936.439 | 936.439 | 936.439 | 936.439 | 936.439 | 936.439 | 936.439 | 936.439 | 936.439 | 936.439 | 936.439
70% | 2875.5487 | 3817.4772 | 4073.866 | 4066.399 | 4066.1238 | 4095.3442 | 4127.4091 | 4193.2394 | 4240.5439 | 4266.205 | 4294.2657 | 4319.9539 | 4366.3723 | 4423.9855 | 4419.9585 | 4419.9585 | 4419.9585 | 4419.9585 | 4419.9585 | 4419.9585 | 4419.9585 | 4419.9585 | 4419.9585 | 4419.9585 | 4419.9585 | 4419.9585 | 4419.9585 | 4419.9585 | 4419.9585 | 4419.9585 |  | 1157.0168 | 1497.7123 | 1586.8569 | 1581.5061 | 1581.8839 | 1591.0234 | 1615.1582 | 1631.3028 | 1647.1153 | 1665.6109 | 1682.7407 | 1699.3783 | 1701.266 | 1720.6867 | 1705.9407 | 1705.9407 | 1705.9407 | 1705.9407 | 1705.9407 | 1705.9407 | 1705.9407 | 1705.9407 | 1705.9407 | 1705.9407 | 1705.9407 | 1705.9407 | 1705.9407 | 1705.9407 | 1705.9407 | 1705.9407
65% | 7222.0048 | 9587.679 | 10231.6052 | 10212.8518 | 10212.1606 | 10285.5483 | 10366.0801 | 10531.4141 | 10650.2206 | 10714.6689 | 10785.1441 | 10849.6604 | 10966.2413 | 11110.9382 | 11100.8242 | 11100.8242 | 11100.8242 | 11100.8242 | 11100.8242 | 11100.8242 | 11100.8242 | 11100.8242 | 11100.8242 | 11100.8242 | 11100.8242 | 11100.8242 | 11100.8242 | 11100.8242 | 11100.8242 | 11100.8242 |  | 1455.7061 | 1884.3537 | 1996.5114 | 1989.7793 | 1990.2546 | 2001.7536 | 2032.1189 | 2052.4313 | 2072.3259 | 2095.5961 | 2117.1482 | 2138.0809 | 2140.4558 | 2164.8901 | 2146.3373 | 2146.3373 | 2146.3373 | 2146.3373 | 2146.3373 | 2146.3373 | 2146.3373 | 2146.3373 | 2146.3373 | 2146.3373 | 2146.3373 | 2146.3373 | 2146.3373 | 2146.3373 | 2146.3373 | 2146.3373
60% | 10556.5772 | 14014.5398 | 14955.7822 | 14928.3698 | 14927.3596 | 15034.6321 | 15152.3473 | 15394.0201 | 15567.6823 | 15661.888 | 15764.9032 | 15859.2082 | 16029.6174 | 16241.1243 | 16226.3403 | 16226.3403 | 16226.3403 | 16226.3403 | 16226.3403 | 16226.3403 | 16226.3403 | 16226.3403 | 16226.3403 | 16226.3403 | 16226.3403 | 16226.3403 | 16226.3403 | 16226.3403 | 16226.3403 | 16226.3403 |  | 2277.9105 | 2948.6646 | 3124.1707 | 3113.6361 | 3114.3799 | 3132.3737 | 3179.8897 | 3211.675 | 3242.8062 | 3279.2199 | 3312.9449 | 3345.7006 | 3349.4169 | 3387.6521 | 3358.6203 | 3358.6203 | 3358.6203 | 3358.6203 | 3358.6203 | 3358.6203 | 3358.6203 | 3358.6203 | 3358.6203 | 3358.6203 | 3358.6203 | 3358.6203 | 3358.6203 | 3358.6203 | 3358.6203 | 3358.6203
55% | 11937.0341 | 15847.1857 | 16911.512 | 16880.515 | 16879.3726 | 17000.6729 | 17133.7814 | 17407.0571 | 17603.4287 | 17709.9534 | 17826.4396 | 17933.0767 | 18125.7699 | 18364.935 | 18348.2178 | 18348.2178 | 18348.2178 | 18348.2178 | 18348.2178 | 18348.2178 | 18348.2178 | 18348.2178 | 18348.2178 | 18348.2178 | 18348.2178 | 18348.2178 | 18348.2178 | 18348.2178 | 18348.2178 | 18348.2178 |  | 4377.3623 | 5666.3214 | 6003.5838 | 5983.3401 | 5984.7694 | 6019.3473 | 6110.6567 | 6171.737 | 6231.5606 | 6301.5352 | 6366.343 | 6429.2884 | 6436.4298 | 6509.9048 | 6454.1156 | 6454.1156 | 6454.1156 | 6454.1156 | 6454.1156 | 6454.1156 | 6454.1156 | 6454.1156 | 6454.1156 | 6454.1156 | 6454.1156 | 6454.1156 | 6454.1156 | 6454.1156 | 6454.1156 | 6454.1156
50% | 15327.7148 | 20348.5339 | 21715.179 | 21675.3774 | 21673.9105 | 21829.6658 | 22000.5834 | 22351.4823 | 22603.6327 | 22740.4155 | 22889.9893 | 23026.9163 | 23274.3434 | 23581.4427 | 23559.977 | 23559.977 | 23559.977 | 23559.977 | 23559.977 | 23559.977 | 23559.977 | 23559.977 | 23559.977 | 23559.977 | 23559.977 | 23559.977 | 23559.977 | 23559.977 | 23559.977 | 23559.977 |  | 9714.4123 | 12574.9205 | 13323.3863 | 13278.4606 | 13281.6325 | 13358.3693 | 13561.0066 | 13696.5584 | 13829.3213 | 13984.6116 | 14128.4356 | 14268.1263 | 14283.9748 | 14447.0334 | 14323.224 | 14323.224 | 14323.224 | 14323.224 | 14323.224 | 14323.224 | 14323.224 | 14323.224 | 14323.224 | 14323.224 | 14323.224 | 14323.224 | 14323.224 | 14323.224 | 14323.224 | 14323.224
45% | 20411.3174 | 27097.3455 | 28917.2533 | 28864.251 | 28862.2976 | 29069.7109 | 29297.3152 | 29764.5935 | 30100.3723 | 30282.5206 | 30481.7021 | 30664.0425 | 30993.5314 | 31402.4836 | 31373.8985 | 31373.8985 | 31373.8985 | 31373.8985 | 31373.8985 | 31373.8985 | 31373.8985 | 31373.8985 | 31373.8985 | 31373.8985 | 31373.8985 | 31373.8985 | 31373.8985 | 31373.8985 | 31373.8985 | 31373.8985 |  | 14720.4239 | 19055.0036 | 20189.1672 | 20121.0905 | 20125.8971 | 20242.1776 | 20549.2377 | 20754.6417 | 20955.8197 | 21191.1339 | 21409.073 | 21620.7489 | 21644.7644 | 21891.85 | 21704.2393 | 21704.2393 | 21704.2393 | 21704.2393 | 21704.2393 | 21704.2393 | 21704.2393 | 21704.2393 | 21704.2393 | 21704.2393 | 21704.2393 | 21704.2393 | 21704.2393 | 21704.2393 | 21704.2393 | 21704.2393
40% | 14315.8312 | 19005.1929 | 20281.6168 | 20244.4427 | 20243.0727 | 20388.5455 | 20548.1797 | 20875.9135 | 21111.4178 | 21239.1706 | 21378.87 | 21506.7576 | 21737.8504 | 22024.6761 | 22004.6275 | 22004.6275 | 22004.6275 | 22004.6275 | 22004.6275 | 22004.6275 | 22004.6275 | 22004.6275 | 22004.6275 | 22004.6275 | 22004.6275 | 22004.6275 | 22004.6275 | 22004.6275 | 22004.6275 | 22004.6275 |  | 15242.3215 | 19730.5793 | 20904.9535 | 20834.4632 | 20839.4402 | 20959.8434 | 21277.7899 | 21490.4763 | 21698.7869 | 21942.444 | 22168.1098 | 22387.2904 | 22412.1574 | 22668.0032 | 22473.741 | 22473.741 | 22473.741 | 22473.741 | 22473.741 | 22473.741 | 22473.741 | 22473.741 | 22473.741 | 22473.741 | 22473.741 | 22473.741 | 22473.741 | 22473.741 | 22473.741 | 22473.741
35% | 7422.2532 | 9853.5218 | 10515.3025 | 10496.0291 | 10495.3188 | 10570.7413 | 10653.506 | 10823.4244 | 10945.5251 | 11011.7604 | 11084.1896 | 11150.4949 | 11270.3083 | 11419.0173 | 11408.6228 | 11408.6228 | 11408.6228 | 11408.6228 | 11408.6228 | 11408.6228 | 11408.6228 | 11408.6228 | 11408.6228 | 11408.6228 | 11408.6228 | 11408.6228 | 11408.6228 | 11408.6228 | 11408.6228 | 11408.6228 |  | 20759.9869 | 26872.9779 | 28472.4713 | 28376.4638 | 28383.2424 | 28547.2311 | 28980.2731 | 29269.9512 | 29553.6695 | 29885.5295 | 30192.8856 | 30491.4088 | 30525.2776 | 30873.7386 | 30609.1541 | 30609.1541 | 30609.1541 | 30609.1541 | 30609.1541 | 30609.1541 | 30609.1541 | 30609.1541 | 30609.1541 | 30609.1541 | 30609.1541 | 30609.1541 | 30609.1541 | 30609.1541 | 30609.1541 | 30609.1541
30% | 3452.1096 | 4582.899 | 4890.695 | 4881.7308 | 4881.4005 | 4916.4797 | 4954.9738 | 5034.0033 | 5090.7926 | 5121.5988 | 5155.2859 | 5186.1246 | 5241.8501 | 5311.0151 | 5306.1806 | 5306.1806 | 5306.1806 | 5306.1806 | 5306.1806 | 5306.1806 | 5306.1806 | 5306.1806 | 5306.1806 | 5306.1806 | 5306.1806 | 5306.1806 | 5306.1806 | 5306.1806 | 5306.1806 | 5306.1806 |  | 19183.5111 | 24832.2926 | 26310.3234 | 26221.6065 | 26227.8703 | 26379.406 | 26779.5636 | 27047.2441 | 27309.4173 | 27616.0765 | 27900.0925 | 28175.9464 | 28207.2432 | 28529.2428 | 28284.7504 | 28284.7504 | 28284.7504 | 28284.7504 | 28284.7504 | 28284.7504 | 28284.7504 | 28284.7504 | 28284.7504 | 28284.7504 | 28284.7504 | 28284.7504 | 28284.7504 | 28284.7504 | 28284.7504 | 28284.7504
25% | 2357.031 | 3129.1112 | 3339.2681 | 3333.1476 | 3332.922 | 3356.8734 | 3383.1564 | 3437.1161 | 3475.8908 | 3496.9246 | 3519.9255 | 3540.9815 | 3579.0298 | 3626.2542 | 3622.9533 | 3622.9533 | 3622.9533 | 3622.9533 | 3622.9533 | 3622.9533 | 3622.9533 | 3622.9533 | 3622.9533 | 3622.9533 | 3622.9533 | 3622.9533 | 3622.9533 | 3622.9533 | 3622.9533 | 3622.9533 |  | 5533.3008 | 7162.6379 | 7588.9618 | 7563.3722 | 7565.179 | 7608.888 | 7724.3096 | 7801.5195 | 7877.1409 | 7965.5938 | 8047.5155 | 8127.0829 | 8136.1102 | 8228.9879 | 8158.4664 | 8158.4664 | 8158.4664 | 8158.4664 | 8158.4664 | 8158.4664 | 8158.4664 | 8158.4664 | 8158.4664 | 8158.4664 | 8158.4664 | 8158.4664 | 8158.4664 | 8158.4664 | 8158.4664 | 8158.4664
20% | 1427.8587 | 1895.5749 | 2022.8852 | 2019.1774 | 2019.0408 | 2033.5502 | 2049.4721 | 2082.1602 | 2105.6494 | 2118.3914 | 2132.325 | 2145.0805 | 2168.1297 | 2196.7376 | 2194.738 | 2194.738 | 2194.738 | 2194.738 | 2194.738 | 2194.738 | 2194.738 | 2194.738 | 2194.738 | 2194.738 | 2194.738 | 2194.738 | 2194.738 | 2194.738 | 2194.738 | 2194.738 |  | 1484.8203 | 1922.0408 | 2036.4417 | 2029.5749 | 2030.0597 | 2041.7887 | 2072.7613 | 2093.48 | 2113.7724 | 2137.5081 | 2159.4912 | 2180.8425 | 2183.2649 | 2208.1879 | 2189.264 | 2189.264 | 2189.264 | 2189.264 | 2189.264 | 2189.264 | 2189.264 | 2189.264 | 2189.264 | 2189.264 | 2189.264 | 2189.264 | 2189.264 | 2189.264 | 2189.264 | 2189.264
15% | 914.1778 | 1213.6303 | 1295.1399 | 1292.766 | 1292.6786 | 1301.9681 | 1312.162 | 1333.0904 | 1348.1292 | 1356.2872 | 1365.2081 | 1373.3747 | 1388.1318 | 1406.4479 | 1405.1676 | 1405.1676 | 1405.1676 | 1405.1676 | 1405.1676 | 1405.1676 | 1405.1676 | 1405.1676 | 1405.1676 | 1405.1676 | 1405.1676 | 1405.1676 | 1405.1676 | 1405.1676 | 1405.1676 | 1405.1676 |  | 818.9695 | 1060.1234 | 1123.2225 | 1119.4351 | 1119.7025 | 1126.1718 | 1143.255 | 1154.6827 | 1165.8752 | 1178.9669 | 1191.0919 | 1202.8685 | 1204.2046 | 1217.9511 | 1207.5134 | 1207.5134 | 1207.5134 | 1207.5134 | 1207.5134 | 1207.5134 | 1207.5134 | 1207.5134 | 1207.5134 | 1207.5134 | 1207.5134 | 1207.5134 | 1207.5134 | 1207.5134 | 1207.5134 | 1207.5134
10% | 611.8703 | 812.2975 | 866.8529 | 865.264 | 865.2055 | 871.4231 | 878.246 | 892.2536 | 902.3193 | 907.7795 | 913.7504 | 919.2164 | 929.0935 | 941.3527 | 940.4958 | 940.4958 | 940.4958 | 940.4958 | 940.4958 | 940.4958 | 940.4958 | 940.4958 | 940.4958 | 940.4958 | 940.4958 | 940.4958 | 940.4958 | 940.4958 | 940.4958 | 940.4958 |  | 191.3984 | 247.7576 | 262.5043 | 261.6191 | 261.6816 | 263.1935 | 267.186 | 269.8567 | 272.4725 | 275.5321 | 278.3658 | 281.118 | 281.4303 | 284.643 | 282.2036 | 282.2036 | 282.2036 | 282.2036 | 282.2036 | 282.2036 | 282.2036 | 282.2036 | 282.2036 | 282.2036 | 282.2036 | 282.2036 | 282.2036 | 282.2036 | 282.2036 | 282.2036
5% | 435.3228 | 577.9192 | 616.7333 | 615.6029 | 615.5612 | 619.9848 | 624.8391 | 634.805 | 641.9663 | 645.8511 | 650.0991 | 653.988 | 661.0151 | 669.7371 | 669.1274 | 669.1274 | 669.1274 | 669.1274 | 669.1274 | 669.1274 | 669.1274 | 669.1274 | 669.1274 | 669.1274 | 669.1274 | 669.1274 | 669.1274 | 669.1274 | 669.1274 | 669.1274 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9.992e-14% | 38.2117 | 50.7285 | 54.1355 | 54.0363 | 54.0326 | 54.4209 | 54.847 | 55.7218 | 56.3504 | 56.6914 | 57.0643 | 57.4056 | 58.0224 | 58.788 | 58.7345 | 58.7345 | 58.7345 | 58.7345 | 58.7345 | 58.7345 | 58.7345 | 58.7345 | 58.7345 | 58.7345 | 58.7345 | 58.7345 | 58.7345 | 58.7345 | 58.7345 | 58.7345 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E @ R (MWh) | 102337.6118 | 135859.8063 | 144984.402 | 144718.661 | 144708.8672 | 145748.789 | 146889.9441 | 149232.7692 | 150916.2863 | 151829.5355 | 152828.1856 | 153742.3981 | 155394.3791 | 157444.7704 | 157301.4516 | 157301.4516 | 157301.4516 | 157301.4516 | 157301.4516 | 157301.4516 | 157301.4516 | 157301.4516 | 157301.4516 | 157301.4516 | 157301.4516 | 157301.4516 | 157301.4516 | 157301.4516 | 157301.4516 | 157301.4516 | E @ R (MWh) | 99292.8528 | 128530.651 | 136180.8614 | 135721.6674 | 135754.0887 | 136538.4294 | 138609.6244 | 139995.1247 | 141352.1196 | 142939.3714 | 144409.4236 | 145837.2289 | 145999.2196 | 147665.8725 | 146400.3925 | 146400.3925 | 146400.3925 | 146400.3925 | 146400.3925 | 146400.3925 | 146400.3925 | 146400.3925 | 146400.3925 | 146400.3925 | 146400.3925 | 146400.3925 | 146400.3925 | 146400.3925 | 146400.3925 | 146400.3925
Option 7 Summer POE50 W E @ R (MWh) N 2 | 71636.3283 | 95101.8644 | 101489.0814 | 101303.0627 | 101296.207 | 102024.1523 | 102822.9609 | 104462.9384 | 105641.4004 | 106280.6749 | 106979.7299 | 107619.6787 | 108776.0654 | 110211.3393 | 110111.0161 | 110111.0161 | 110111.0161 | 110111.0161 | 110111.0161 | 110111.0161 | 110111.0161 | 110111.0161 | 110111.0161 | 110111.0161 | 110111.0161 | 110111.0161 | 110111.0161 | 110111.0161 | 110111.0161 | 110111.0161 | Option 7 Summer POE10 W E @ R (MWh) N 2 | 29787.8558 | 38559.1953 | 40854.2584 | 40716.5002 | 40726.2266 | 40961.5288 | 41582.8873 | 41998.5374 | 42405.6359 | 42881.8114 | 43322.8271 | 43751.1687 | 43799.7659 | 44299.7618 | 43920.1178 | 43920.1178 | 43920.1178 | 43920.1178 | 43920.1178 | 43920.1178 | 43920.1178 | 43920.1178 | 43920.1178 | 43920.1178 | 43920.1178 | 43920.1178 | 43920.1178 | 43920.1178 | 43920.1178 | 43920.1178
Option 8 -
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | 66.5813 | 92.3179 | 99.0036 | 100.1408 | 101.0254 | 102.5536 | 106.0346 | 108.362 | 111.3134 | 112.8438 | 114.1881 | 111.6988 | 114.6091 | 119.1862 | 115.707 | 115.707 | 115.707 | 115.707 | 115.707 | 115.707 | 115.707 | 115.707 | 115.707 | 115.707 | 115.707 | 115.707 | 115.707 | 115.707 | 115.707 | 115.707 |  | 71.2634 | 96.6755 | 103.6223 | 104.6946 | 105.3727 | 106.8677 | 110.4032 | 112.3303 | 116.0076 | 127.1923 | 117.9641 | 116.1567 | 118.5887 | 123.9113 | 120.303 | 120.303 | 120.303 | 120.303 | 120.303 | 120.303 | 120.303 | 120.303 | 120.303 | 120.303 | 120.303 | 120.303 | 120.303 | 120.303 | 120.303 | 120.303
98% | 79.0946 | 109.6681 | 117.6103 | 118.9612 | 120.012 | 121.8275 | 125.9627 | 128.7276 | 132.2337 | 134.0516 | 135.6486 | 132.6915 | 136.1487 | 141.586 | 137.453 | 137.453 | 137.453 | 137.453 | 137.453 | 137.453 | 137.453 | 137.453 | 137.453 | 137.453 | 137.453 | 137.453 | 137.453 | 137.453 | 137.453 | 137.453 |  | 84.6567 | 114.8446 | 123.097 | 124.3709 | 125.1764 | 126.9524 | 131.1523 | 133.4417 | 137.8101 | 151.0968 | 140.1342 | 137.9871 | 140.8762 | 147.1992 | 142.9127 | 142.9127 | 142.9127 | 142.9127 | 142.9127 | 142.9127 | 142.9127 | 142.9127 | 142.9127 | 142.9127 | 142.9127 | 142.9127 | 142.9127 | 142.9127 | 142.9127 | 142.9127
97% | 156.5832 | 217.1095 | 232.8326 | 235.507 | 237.5873 | 241.1813 | 249.3678 | 254.8414 | 261.7824 | 265.3814 | 268.543 | 262.6887 | 269.5329 | 280.2972 | 272.115 | 272.115 | 272.115 | 272.115 | 272.115 | 272.115 | 272.115 | 272.115 | 272.115 | 272.115 | 272.115 | 272.115 | 272.115 | 272.115 | 272.115 | 272.115 |  | 167.5944 | 227.3573 | 243.6946 | 246.2165 | 247.8111 | 251.327 | 259.6417 | 264.1739 | 272.822 | 299.1257 | 277.423 | 273.1725 | 278.892 | 291.4096 | 282.9237 | 282.9237 | 282.9237 | 282.9237 | 282.9237 | 282.9237 | 282.9237 | 282.9237 | 282.9237 | 282.9237 | 282.9237 | 282.9237 | 282.9237 | 282.9237 | 282.9237 | 282.9237
95% | 462.5227 | 641.3081 | 687.7517 | 695.6514 | 701.7962 | 712.4124 | 736.5942 | 752.7622 | 773.2648 | 783.8959 | 793.2346 | 775.942 | 796.1588 | 827.9549 | 803.7859 | 803.7859 | 803.7859 | 803.7859 | 803.7859 | 803.7859 | 803.7859 | 803.7859 | 803.7859 | 803.7859 | 803.7859 | 803.7859 | 803.7859 | 803.7859 | 803.7859 | 803.7859 |  | 495.0481 | 671.5786 | 719.8364 | 727.2857 | 731.996 | 742.3814 | 766.9415 | 780.329 | 805.8742 | 883.5714 | 819.4649 | 806.9095 | 823.8041 | 860.7791 | 835.7129 | 835.7129 | 835.7129 | 835.7129 | 835.7129 | 835.7129 | 835.7129 | 835.7129 | 835.7129 | 835.7129 | 835.7129 | 835.7129 | 835.7129 | 835.7129 | 835.7129 | 835.7129
90% | 2550.165 | 3535.9158 | 3791.9875 | 3835.5434 | 3869.4233 | 3927.9564 | 4061.2852 | 4150.4292 | 4263.4726 | 4322.0883 | 4373.5777 | 4278.2333 | 4389.7006 | 4565.012 | 4431.7536 | 4431.7536 | 4431.7536 | 4431.7536 | 4431.7536 | 4431.7536 | 4431.7536 | 4431.7536 | 4431.7536 | 4431.7536 | 4431.7536 | 4431.7536 | 4431.7536 | 4431.7536 | 4431.7536 | 4431.7536 |  | 2729.4971 | 3702.8155 | 3968.8899 | 4009.9623 | 4035.9325 | 4093.1938 | 4228.6083 | 4302.4214 | 4443.2678 | 4871.6587 | 4518.2015 | 4448.976 | 4542.1258 | 4745.9912 | 4607.7865 | 4607.7865 | 4607.7865 | 4607.7865 | 4607.7865 | 4607.7865 | 4607.7865 | 4607.7865 | 4607.7865 | 4607.7865 | 4607.7865 | 4607.7865 | 4607.7865 | 4607.7865 | 4607.7865 | 4607.7865
85% | 6229.8705 | 8637.9889 | 9263.5537 | 9369.9577 | 9452.724 | 9595.7162 | 9921.4289 | 10139.2013 | 10415.3582 | 10558.5521 | 10684.3371 | 10451.4176 | 10723.7241 | 11151.9973 | 10826.4566 | 10826.4566 | 10826.4566 | 10826.4566 | 10826.4566 | 10826.4566 | 10826.4566 | 10826.4566 | 10826.4566 | 10826.4566 | 10826.4566 | 10826.4566 | 10826.4566 | 10826.4566 | 10826.4566 | 10826.4566 |  | 6667.9659 | 9045.7131 | 9695.7136 | 9796.0508 | 9859.4941 | 9999.3792 | 10330.1872 | 10510.5072 | 10854.585 | 11901.1132 | 11037.6427 | 10868.5297 | 11096.0879 | 11594.1165 | 11256.4923 | 11256.4923 | 11256.4923 | 11256.4923 | 11256.4923 | 11256.4923 | 11256.4923 | 11256.4923 | 11256.4923 | 11256.4923 | 11256.4923 | 11256.4923 | 11256.4923 | 11256.4923 | 11256.4923 | 11256.4923
80% | 9683.0656 | 13425.9956 | 14398.3087 | 14563.692 | 14692.3353 | 14914.5876 | 15420.8418 | 15759.3246 | 16188.5543 | 16411.1201 | 16606.6272 | 16244.6013 | 16667.8463 | 17333.5099 | 16827.5231 | 16827.5231 | 16827.5231 | 16827.5231 | 16827.5231 | 16827.5231 | 16827.5231 | 16827.5231 | 16827.5231 | 16827.5231 | 16827.5231 | 16827.5231 | 16827.5231 | 16827.5231 | 16827.5231 | 16827.5231 |  | 10363.9958 | 14059.7198 | 15070.0133 | 15225.967 | 15324.5767 | 15541.9996 | 16056.1734 | 16336.4441 | 16871.243 | 18497.858 | 17155.7689 | 16892.9172 | 17246.6101 | 18020.6942 | 17495.9261 | 17495.9261 | 17495.9261 | 17495.9261 | 17495.9261 | 17495.9261 | 17495.9261 | 17495.9261 | 17495.9261 | 17495.9261 | 17495.9261 | 17495.9261 | 17495.9261 | 17495.9261 | 17495.9261 | 17495.9261
75% | 10683.1238 | 14812.6201 | 15885.3529 | 16067.8168 | 16209.7463 | 16454.9526 | 17013.4923 | 17386.9332 | 17860.4934 | 18106.0455 | 18321.7445 | 17922.3288 | 18389.2862 | 19123.699 | 18565.4543 | 18565.4543 | 18565.4543 | 18565.4543 | 18565.4543 | 18565.4543 | 18565.4543 | 18565.4543 | 18565.4543 | 18565.4543 | 18565.4543 | 18565.4543 | 18565.4543 | 18565.4543 | 18565.4543 | 18565.4543 |  | 11434.3798 | 15511.7948 | 16626.4305 | 16798.4909 | 16907.2849 | 17147.1631 | 17714.4402 | 18023.6571 | 18613.6895 | 20408.2999 | 18927.601 | 18637.6022 | 19027.8242 | 19881.855 | 19302.8894 | 19302.8894 | 19302.8894 | 19302.8894 | 19302.8894 | 19302.8894 | 19302.8894 | 19302.8894 | 19302.8894 | 19302.8894 | 19302.8894 | 19302.8894 | 19302.8894 | 19302.8894 | 19302.8894 | 19302.8894
70% | 11478.4193 | 15915.3323 | 17067.9236 | 17263.9709 | 17416.4662 | 17679.9267 | 18280.0463 | 18681.2877 | 19190.1017 | 19453.9337 | 19685.6902 | 19256.5404 | 19758.26 | 20547.3454 | 19947.5428 | 19947.5428 | 19947.5428 | 19947.5428 | 19947.5428 | 19947.5428 | 19947.5428 | 19947.5428 | 19947.5428 | 19947.5428 | 19947.5428 | 19947.5428 | 19947.5428 | 19947.5428 | 19947.5428 | 19947.5428 |  | 12285.6019 | 16666.5563 | 17864.1701 | 18049.0394 | 18165.9325 | 18423.6682 | 19033.1757 | 19365.4119 | 19999.3688 | 21927.5773 | 20336.6492 | 20025.0617 | 20444.3333 | 21361.9417 | 20739.8755 | 20739.8755 | 20739.8755 | 20739.8755 | 20739.8755 | 20739.8755 | 20739.8755 | 20739.8755 | 20739.8755 | 20739.8755 | 20739.8755 | 20739.8755 | 20739.8755 | 20739.8755 | 20739.8755 | 20739.8755
65% | 12096.053 | 16771.7086 | 17986.3189 | 18192.9151 | 18353.6159 | 18631.2528 | 19263.6638 | 19686.4953 | 20222.6877 | 20500.7161 | 20744.943 | 20292.7014 | 20821.4176 | 21652.9624 | 21020.8854 | 21020.8854 | 21020.8854 | 21020.8854 | 21020.8854 | 21020.8854 | 21020.8854 | 21020.8854 | 21020.8854 | 21020.8854 | 21020.8854 | 21020.8854 | 21020.8854 | 21020.8854 | 21020.8854 | 21020.8854 |  | 12946.6687 | 17563.3547 | 18825.4101 | 19020.2268 | 19143.4097 | 19415.0137 | 20057.3178 | 20407.431 | 21075.5001 | 23107.4621 | 21430.9289 | 21102.5754 | 21544.4074 | 22511.3907 | 21855.8521 | 21855.8521 | 21855.8521 | 21855.8521 | 21855.8521 | 21855.8521 | 21855.8521 | 21855.8521 | 21855.8521 | 21855.8521 | 21855.8521 | 21855.8521 | 21855.8521 | 21855.8521 | 21855.8521 | 21855.8521
60% | 13316.2645 | 18463.5854 | 19800.7217 | 20028.1587 | 20205.0705 | 20510.7145 | 21206.9211 | 21672.4066 | 22262.6883 | 22568.7633 | 22837.627 | 22339.7647 | 22921.8162 | 23837.2445 | 23141.4056 | 23141.4056 | 23141.4056 | 23141.4056 | 23141.4056 | 23141.4056 | 23141.4056 | 23141.4056 | 23141.4056 | 23141.4056 | 23141.4056 | 23141.4056 | 23141.4056 | 23141.4056 | 23141.4056 | 23141.4056 |  | 14252.6876 | 19335.0902 | 20724.4577 | 20938.927 | 21074.5362 | 21373.5387 | 22080.6365 | 22466.068 | 23201.5297 | 25438.4696 | 23592.813 | 23231.3363 | 23717.7389 | 24782.2684 | 24060.6012 | 24060.6012 | 24060.6012 | 24060.6012 | 24060.6012 | 24060.6012 | 24060.6012 | 24060.6012 | 24060.6012 | 24060.6012 | 24060.6012 | 24060.6012 | 24060.6012 | 24060.6012 | 24060.6012 | 24060.6012
55% | 14813.5078 | 20539.579 | 22027.0592 | 22280.0685 | 22476.8718 | 22816.8815 | 23591.3677 | 24109.191 | 24765.8423 | 25106.3315 | 25405.4256 | 24851.585 | 25499.0807 | 26517.4372 | 25743.3602 | 25743.3602 | 25743.3602 | 25743.3602 | 25743.3602 | 25743.3602 | 25743.3602 | 25743.3602 | 25743.3602 | 25743.3602 | 25743.3602 | 25743.3602 | 25743.3602 | 25743.3602 | 25743.3602 | 25743.3602 |  | 15855.2197 | 21509.0734 | 23054.6574 | 23293.241 | 23444.0977 | 23776.7193 | 24563.3211 | 24992.0894 | 25810.2444 | 28298.6996 | 26245.5225 | 25843.4024 | 26384.4947 | 27568.7169 | 26765.9075 | 26765.9075 | 26765.9075 | 26765.9075 | 26765.9075 | 26765.9075 | 26765.9075 | 26765.9075 | 26765.9075 | 26765.9075 | 26765.9075 | 26765.9075 | 26765.9075 | 26765.9075 | 26765.9075 | 26765.9075
50% | 15014.9247 | 20818.8523 | 22326.5575 | 22583.007 | 22782.4862 | 23127.1189 | 23912.1357 | 24436.9997 | 25102.5795 | 25447.6982 | 25750.859 | 25189.488 | 25845.7876 | 26877.9905 | 26093.3885 | 26093.3885 | 26093.3885 | 26093.3885 | 26093.3885 | 26093.3885 | 26093.3885 | 26093.3885 | 26093.3885 | 26093.3885 | 26093.3885 | 26093.3885 | 26093.3885 | 26093.3885 | 26093.3885 | 26093.3885 |  | 16070.8005 | 21801.5288 | 23368.1279 | 23609.9554 | 23762.8633 | 24100.0075 | 24897.3046 | 25331.9028 | 26161.1821 | 28683.4724 | 26602.3787 | 26194.791 | 26743.2404 | 27943.5643 | 27129.8392 | 27129.8392 | 27129.8392 | 27129.8392 | 27129.8392 | 27129.8392 | 27129.8392 | 27129.8392 | 27129.8392 | 27129.8392 | 27129.8392 | 27129.8392 | 27129.8392 | 27129.8392 | 27129.8392 | 27129.8392
45% | 11588.8305 | 16068.4223 | 17232.1005 | 17430.0335 | 17583.9957 | 17849.9904 | 18455.8826 | 18860.9836 | 19374.6918 | 19641.0617 | 19875.0474 | 19441.7696 | 19948.3153 | 20744.9909 | 20139.4188 | 20139.4188 | 20139.4188 | 20139.4188 | 20139.4188 | 20139.4188 | 20139.4188 | 20139.4188 | 20139.4188 | 20139.4188 | 20139.4188 | 20139.4188 | 20139.4188 | 20139.4188 | 20139.4188 | 20139.4188 |  | 12403.7774 | 16826.8724 | 18036.0061 | 18222.6536 | 18340.6711 | 18600.8859 | 19216.2564 | 19551.6884 | 20191.7433 | 22138.4993 | 20532.268 | 20217.6833 | 20640.988 | 21567.4228 | 20939.373 | 20939.373 | 20939.373 | 20939.373 | 20939.373 | 20939.373 | 20939.373 | 20939.373 | 20939.373 | 20939.373 | 20939.373 | 20939.373 | 20939.373 | 20939.373 | 20939.373 | 20939.373
40% | 5693.5395 | 7894.3425 | 8466.0523 | 8563.2959 | 8638.9368 | 8769.6188 | 9067.2909 | 9266.3151 | 9518.6977 | 9649.5639 | 9764.5201 | 9551.6527 | 9800.5162 | 10191.9194 | 9894.4045 | 9894.4045 | 9894.4045 | 9894.4045 | 9894.4045 | 9894.4045 | 9894.4045 | 9894.4045 | 9894.4045 | 9894.4045 | 9894.4045 | 9894.4045 | 9894.4045 | 9894.4045 | 9894.4045 | 9894.4045 |  | 6093.9192 | 8266.9656 | 8861.0075 | 8952.7065 | 9010.688 | 9138.5304 | 9440.8591 | 9605.6552 | 9920.1113 | 10876.5437 | 10087.4095 | 9932.8555 | 10140.8232 | 10595.9764 | 10287.4184 | 10287.4184 | 10287.4184 | 10287.4184 | 10287.4184 | 10287.4184 | 10287.4184 | 10287.4184 | 10287.4184 | 10287.4184 | 10287.4184 | 10287.4184 | 10287.4184 | 10287.4184 | 10287.4184 | 10287.4184
35% | 2127.9257 | 2950.4624 | 3164.1354 | 3200.4796 | 3228.75 | 3277.5916 | 3388.8447 | 3463.2288 | 3557.5552 | 3606.4657 | 3649.4298 | 3569.872 | 3662.8832 | 3809.1677 | 3697.9734 | 3697.9734 | 3697.9734 | 3697.9734 | 3697.9734 | 3697.9734 | 3697.9734 | 3697.9734 | 3697.9734 | 3697.9734 | 3697.9734 | 3697.9734 | 3697.9734 | 3697.9734 | 3697.9734 | 3697.9734 |  | 2277.5652 | 3089.728 | 3311.7475 | 3346.0195 | 3367.6897 | 3415.47 | 3528.4635 | 3590.0551 | 3707.5811 | 4065.0419 | 3770.1078 | 3712.3442 | 3790.0708 | 3960.1816 | 3844.8599 | 3844.8599 | 3844.8599 | 3844.8599 | 3844.8599 | 3844.8599 | 3844.8599 | 3844.8599 | 3844.8599 | 3844.8599 | 3844.8599 | 3844.8599 | 3844.8599 | 3844.8599 | 3844.8599 | 3844.8599
30% | 1061.2862 | 1471.5199 | 1578.0877 | 1596.2141 | 1610.3137 | 1634.673 | 1690.1596 | 1727.2581 | 1774.3027 | 1798.6964 | 1820.1244 | 1780.4456 | 1826.8342 | 1899.7925 | 1844.3351 | 1844.3351 | 1844.3351 | 1844.3351 | 1844.3351 | 1844.3351 | 1844.3351 | 1844.3351 | 1844.3351 | 1844.3351 | 1844.3351 | 1844.3351 | 1844.3351 | 1844.3351 | 1844.3351 | 1844.3351 |  | 1135.9177 | 1540.9775 | 1651.708 | 1668.8009 | 1679.6088 | 1703.4388 | 1759.7934 | 1790.5117 | 1849.1269 | 2027.4077 | 1880.3116 | 1851.5025 | 1890.268 | 1975.1094 | 1917.5936 | 1917.5936 | 1917.5936 | 1917.5936 | 1917.5936 | 1917.5936 | 1917.5936 | 1917.5936 | 1917.5936 | 1917.5936 | 1917.5936 | 1917.5936 | 1917.5936 | 1917.5936 | 1917.5936 | 1917.5936
25% | 625.6637 | 867.5102 | 930.3354 | 941.0215 | 949.3337 | 963.6944 | 996.4056 | 1018.2764 | 1046.0107 | 1060.3916 | 1073.0242 | 1049.6322 | 1076.9798 | 1119.9911 | 1087.2972 | 1087.2972 | 1087.2972 | 1087.2972 | 1087.2972 | 1087.2972 | 1087.2972 | 1087.2972 | 1087.2972 | 1087.2972 | 1087.2972 | 1087.2972 | 1087.2972 | 1087.2972 | 1087.2972 | 1087.2972 |  | 669.6615 | 908.4578 | 973.7371 | 983.8139 | 990.1855 | 1004.2341 | 1037.457 | 1055.5665 | 1090.1221 | 1195.2246 | 1108.5065 | 1091.5226 | 1114.3762 | 1164.393 | 1130.4855 | 1130.4855 | 1130.4855 | 1130.4855 | 1130.4855 | 1130.4855 | 1130.4855 | 1130.4855 | 1130.4855 | 1130.4855 | 1130.4855 | 1130.4855 | 1130.4855 | 1130.4855 | 1130.4855 | 1130.4855
20% | 316.1776 | 438.3942 | 470.1428 | 475.543 | 479.7435 | 487.0006 | 503.5312 | 514.5835 | 528.599 | 535.8664 | 542.2502 | 530.4291 | 544.2492 | 565.9848 | 549.463 | 549.463 | 549.463 | 549.463 | 549.463 | 549.463 | 549.463 | 549.463 | 549.463 | 549.463 | 549.463 | 549.463 | 549.463 | 549.463 | 549.463 | 549.463 |  | 338.4118 | 459.0869 | 492.0757 | 497.168 | 500.3879 | 507.4873 | 524.2764 | 533.428 | 550.8906 | 604.0039 | 560.1811 | 551.5983 | 563.1473 | 588.4232 | 571.2881 | 571.2881 | 571.2881 | 571.2881 | 571.2881 | 571.2881 | 571.2881 | 571.2881 | 571.2881 | 571.2881 | 571.2881 | 571.2881 | 571.2881 | 571.2881 | 571.2881 | 571.2881
15% | 128.8131 | 178.605 | 191.5396 | 193.7397 | 195.4511 | 198.4077 | 205.1423 | 209.6451 | 215.3552 | 218.3159 | 220.9167 | 216.1007 | 221.7311 | 230.5864 | 223.8553 | 223.8553 | 223.8553 | 223.8553 | 223.8553 | 223.8553 | 223.8553 | 223.8553 | 223.8553 | 223.8553 | 223.8553 | 223.8553 | 223.8553 | 223.8553 | 223.8553 | 223.8553 |  | 137.8715 | 187.0354 | 200.4753 | 202.5499 | 203.8617 | 206.7541 | 213.5941 | 217.3225 | 224.4369 | 246.0756 | 228.2219 | 224.7252 | 229.4304 | 239.728 | 232.747 | 232.747 | 232.747 | 232.747 | 232.747 | 232.747 | 232.747 | 232.747 | 232.747 | 232.747 | 232.747 | 232.747 | 232.747 | 232.747 | 232.747 | 232.747
10% | 51.8598 | 71.9059 | 77.1134 | 77.9991 | 78.6881 | 79.8784 | 82.5898 | 84.4026 | 86.7014 | 87.8934 | 88.9405 | 87.0016 | 89.2684 | 92.8335 | 90.1236 | 90.1236 | 90.1236 | 90.1236 | 90.1236 | 90.1236 | 90.1236 | 90.1236 | 90.1236 | 90.1236 | 90.1236 | 90.1236 | 90.1236 | 90.1236 | 90.1236 | 90.1236 |  | 55.5067 | 75.3 | 80.7108 | 81.5461 | 82.0742 | 83.2387 | 85.9924 | 87.4935 | 90.3577 | 99.0694 | 91.8816 | 90.4738 | 92.3681 | 96.5139 | 93.7033 | 93.7033 | 93.7033 | 93.7033 | 93.7033 | 93.7033 | 93.7033 | 93.7033 | 93.7033 | 93.7033 | 93.7033 | 93.7033 | 93.7033 | 93.7033 | 93.7033 | 93.7033
5% | 44.1645 | 61.236 | 65.6707 | 66.425 | 67.0118 | 68.0255 | 70.3345 | 71.8783 | 73.8361 | 74.8512 | 75.7429 | 74.0917 | 76.0221 | 79.0582 | 76.7504 | 76.7504 | 76.7504 | 76.7504 | 76.7504 | 76.7504 | 76.7504 | 76.7504 | 76.7504 | 76.7504 | 76.7504 | 76.7504 | 76.7504 | 76.7504 | 76.7504 | 76.7504 |  | 47.2702 | 64.1264 | 68.7344 | 69.4457 | 69.8954 | 70.8871 | 73.2323 | 74.5106 | 76.9498 | 84.3688 | 78.2475 | 77.0487 | 78.6618 | 82.1924 | 79.799 | 79.799 | 79.799 | 79.799 | 79.799 | 79.799 | 79.799 | 79.799 | 79.799 | 79.799 | 79.799 | 79.799 | 79.799 | 79.799 | 79.799 | 79.799
9.992e-14% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E @ R (MWh) | 118268.4368 | 163984.3799 | 175860.1598 | 177880.1417 | 179451.3847 | 182165.962 | 188349.3233 | 192483.5334 | 197726.1221 | 200444.5279 | 202832.442 | 198410.6765 | 203580.168 | 211710.5473 | 205530.4523 | 205530.4523 | 205530.4523 | 205530.4523 | 205530.4523 | 205530.4523 | 205530.4523 | 205530.4523 | 205530.4523 | 205530.4523 | 205530.4523 | 205530.4523 | 205530.4523 | 205530.4523 | 205530.4523 | 205530.4523 | E @ R (MWh) | 126585.2808 | 171724.6525 | 184064.3234 | 185969.1325 | 187173.5461 | 189829.1378 | 196109.2281 | 199532.4392 | 206064.4443 | 225931.832 | 209539.6283 | 206329.172 | 210649.1573 | 220103.7788 | 213694.29 | 213694.29 | 213694.29 | 213694.29 | 213694.29 | 213694.29 | 213694.29 | 213694.29 | 213694.29 | 213694.29 | 213694.29 | 213694.29 | 213694.29 | 213694.29 | 213694.29 | 213694.29
Option 8 Winter POE50 W E @ R (MWh) N 2 | 82787.9057 | 114789.066 | 123102.1118 | 124516.0992 | 125615.9693 | 127516.1734 | 131844.5263 | 134738.4734 | 138408.2855 | 140311.1695 | 141982.7094 | 138887.4736 | 142506.1176 | 148197.3831 | 143871.3166 | 143871.3166 | 143871.3166 | 143871.3166 | 143871.3166 | 143871.3166 | 143871.3166 | 143871.3166 | 143871.3166 | 143871.3166 | 143871.3166 | 143871.3166 | 143871.3166 | 143871.3166 | 143871.3166 | 143871.3166 | Option 8 Winter POE10 W E @ R (MWh) N 2 | 37975.5842 | 51517.3957 | 55219.297 | 55790.7397 | 56152.0638 | 56948.7413 | 58832.7684 | 59859.7318 | 61819.3333 | 67779.5496 | 62861.8885 | 61898.7516 | 63194.7472 | 66031.1336 | 64108.287 | 64108.287 | 64108.287 | 64108.287 | 64108.287 | 64108.287 | 64108.287 | 64108.287 | 64108.287 | 64108.287 | 64108.287 | 64108.287 | 64108.287 | 64108.287 | 64108.287 | 64108.287
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 85.8327 | 111.1071 | 117.7202 | 117.3233 | 117.3513 | 118.0293 | 119.8198 | 121.0174 | 122.1905 | 123.5626 | 124.8333 | 126.0676 | 126.2076 | 127.6483 | 126.5544 | 126.5544 | 126.5544 | 126.5544 | 126.5544 | 126.5544 | 126.5544 | 126.5544 | 126.5544 | 126.5544 | 126.5544 | 126.5544 | 126.5544 | 126.5544 | 126.5544 | 126.5544
98% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 42.4851 | 54.9952 | 58.2686 | 58.0721 | 58.0859 | 58.4216 | 59.3078 | 59.9006 | 60.4812 | 61.1604 | 61.7894 | 62.4003 | 62.4696 | 63.1827 | 62.6413 | 62.6413 | 62.6413 | 62.6413 | 62.6413 | 62.6413 | 62.6413 | 62.6413 | 62.6413 | 62.6413 | 62.6413 | 62.6413 | 62.6413 | 62.6413 | 62.6413 | 62.6413
97% | 18.864 | 25.0432 | 26.7251 | 26.6761 | 26.6743 | 26.866 | 27.0764 | 27.5082 | 27.8185 | 27.9869 | 28.171 | 28.3395 | 28.644 | 29.0219 | 28.9955 | 28.9955 | 28.9955 | 28.9955 | 28.9955 | 28.9955 | 28.9955 | 28.9955 | 28.9955 | 28.9955 | 28.9955 | 28.9955 | 28.9955 | 28.9955 | 28.9955 | 28.9955 |  | 84.1075 | 108.8738 | 115.354 | 114.965 | 114.9925 | 115.6569 | 117.4113 | 118.5849 | 119.7344 | 121.0789 | 122.3241 | 123.5336 | 123.6708 | 125.0825 | 124.0106 | 124.0106 | 124.0106 | 124.0106 | 124.0106 | 124.0106 | 124.0106 | 124.0106 | 124.0106 | 124.0106 | 124.0106 | 124.0106 | 124.0106 | 124.0106 | 124.0106 | 124.0106
95% | 92.8689 | 123.2894 | 131.5698 | 131.3286 | 131.3197 | 132.2634 | 133.299 | 135.4251 | 136.9528 | 137.7816 | 138.6878 | 139.5174 | 141.0166 | 142.8772 | 142.7472 | 142.7472 | 142.7472 | 142.7472 | 142.7472 | 142.7472 | 142.7472 | 142.7472 | 142.7472 | 142.7472 | 142.7472 | 142.7472 | 142.7472 | 142.7472 | 142.7472 | 142.7472 |  | 124.2203 | 160.7982 | 170.369 | 169.7945 | 169.8351 | 170.8163 | 173.4075 | 175.1408 | 176.8385 | 178.8242 | 180.6633 | 182.4496 | 182.6522 | 184.7373 | 183.1541 | 183.1541 | 183.1541 | 183.1541 | 183.1541 | 183.1541 | 183.1541 | 183.1541 | 183.1541 | 183.1541 | 183.1541 | 183.1541 | 183.1541 | 183.1541 | 183.1541 | 183.1541
90% | 161.0694 | 213.8301 | 228.1913 | 227.7731 | 227.7577 | 229.3944 | 231.1905 | 234.8778 | 237.5275 | 238.9649 | 240.5367 | 241.9755 | 244.5756 | 247.8027 | 247.5772 | 247.5772 | 247.5772 | 247.5772 | 247.5772 | 247.5772 | 247.5772 | 247.5772 | 247.5772 | 247.5772 | 247.5772 | 247.5772 | 247.5772 | 247.5772 | 247.5772 | 247.5772 |  | 538.6113 | 697.2109 | 738.7092 | 736.2183 | 736.3942 | 740.6488 | 751.884 | 759.3996 | 766.7606 | 775.3706 | 783.3448 | 791.0899 | 791.9686 | 801.0093 | 794.1448 | 794.1448 | 794.1448 | 794.1448 | 794.1448 | 794.1448 | 794.1448 | 794.1448 | 794.1448 | 794.1448 | 794.1448 | 794.1448 | 794.1448 | 794.1448 | 794.1448 | 794.1448
85% | 457.0889 | 606.8151 | 647.57 | 646.383 | 646.3393 | 650.9841 | 656.081 | 666.5452 | 674.0646 | 678.1436 | 682.6041 | 686.6874 | 694.0659 | 703.2239 | 702.5838 | 702.5838 | 702.5838 | 702.5838 | 702.5838 | 702.5838 | 702.5838 | 702.5838 | 702.5838 | 702.5838 | 702.5838 | 702.5838 | 702.5838 | 702.5838 | 702.5838 | 702.5838 |  | 509.4971 | 659.5238 | 698.779 | 696.4228 | 696.5891 | 700.6138 | 711.2416 | 718.351 | 725.3141 | 733.4587 | 741.0019 | 748.3283 | 749.1595 | 757.7115 | 751.218 | 751.218 | 751.218 | 751.218 | 751.218 | 751.218 | 751.218 | 751.218 | 751.218 | 751.218 | 751.218 | 751.218 | 751.218 | 751.218 | 751.218 | 751.218
80% | 638.4734 | 847.6148 | 904.5422 | 902.8842 | 902.8231 | 909.3111 | 916.4306 | 931.0473 | 941.5505 | 947.2482 | 953.4787 | 959.1824 | 969.4889 | 982.2811 | 981.3869 | 981.3869 | 981.3869 | 981.3869 | 981.3869 | 981.3869 | 981.3869 | 981.3869 | 981.3869 | 981.3869 | 981.3869 | 981.3869 | 981.3869 | 981.3869 | 981.3869 | 981.3869 |  | 355.8393 | 460.6198 | 488.0361 | 486.3905 | 486.5067 | 489.3176 | 496.7402 | 501.7054 | 506.5685 | 512.2568 | 517.5251 | 522.642 | 523.2225 | 529.1954 | 524.6602 | 524.6602 | 524.6602 | 524.6602 | 524.6602 | 524.6602 | 524.6602 | 524.6602 | 524.6602 | 524.6602 | 524.6602 | 524.6602 | 524.6602 | 524.6602 | 524.6602 | 524.6602
75% | 1664.3841 | 2209.5776 | 2357.9769 | 2353.655 | 2353.4957 | 2370.4087 | 2388.968 | 2427.0709 | 2454.4511 | 2469.3039 | 2485.5456 | 2500.414 | 2527.2813 | 2560.6281 | 2558.2972 | 2558.2972 | 2558.2972 | 2558.2972 | 2558.2972 | 2558.2972 | 2558.2972 | 2558.2972 | 2558.2972 | 2558.2972 | 2558.2972 | 2558.2972 | 2558.2972 | 2558.2972 | 2558.2972 | 2558.2972 |  | 635.1192 | 822.1366 | 871.0705 | 868.1333 | 868.3407 | 873.3577 | 886.6059 | 895.4682 | 904.1481 | 914.3008 | 923.7039 | 932.8368 | 933.8729 | 944.5335 | 936.439 | 936.439 | 936.439 | 936.439 | 936.439 | 936.439 | 936.439 | 936.439 | 936.439 | 936.439 | 936.439 | 936.439 | 936.439 | 936.439 | 936.439 | 936.439
70% | 2875.5487 | 3817.4772 | 4073.866 | 4066.399 | 4066.1238 | 4095.3442 | 4127.4091 | 4193.2394 | 4240.5439 | 4266.205 | 4294.2657 | 4319.9539 | 4366.3723 | 4423.9855 | 4419.9585 | 4419.9585 | 4419.9585 | 4419.9585 | 4419.9585 | 4419.9585 | 4419.9585 | 4419.9585 | 4419.9585 | 4419.9585 | 4419.9585 | 4419.9585 | 4419.9585 | 4419.9585 | 4419.9585 | 4419.9585 |  | 1157.0168 | 1497.7123 | 1586.8569 | 1581.5061 | 1581.8839 | 1591.0234 | 1615.1582 | 1631.3028 | 1647.1153 | 1665.6109 | 1682.7407 | 1699.3783 | 1701.266 | 1720.6867 | 1705.9407 | 1705.9407 | 1705.9407 | 1705.9407 | 1705.9407 | 1705.9407 | 1705.9407 | 1705.9407 | 1705.9407 | 1705.9407 | 1705.9407 | 1705.9407 | 1705.9407 | 1705.9407 | 1705.9407 | 1705.9407
65% | 7222.0048 | 9587.679 | 10231.6052 | 10212.8518 | 10212.1606 | 10285.5483 | 10366.0801 | 10531.4141 | 10650.2206 | 10714.6689 | 10785.1441 | 10849.6604 | 10966.2413 | 11110.9382 | 11100.8242 | 11100.8242 | 11100.8242 | 11100.8242 | 11100.8242 | 11100.8242 | 11100.8242 | 11100.8242 | 11100.8242 | 11100.8242 | 11100.8242 | 11100.8242 | 11100.8242 | 11100.8242 | 11100.8242 | 11100.8242 |  | 1455.7061 | 1884.3537 | 1996.5114 | 1989.7793 | 1990.2546 | 2001.7536 | 2032.1189 | 2052.4313 | 2072.3259 | 2095.5961 | 2117.1482 | 2138.0809 | 2140.4558 | 2164.8901 | 2146.3373 | 2146.3373 | 2146.3373 | 2146.3373 | 2146.3373 | 2146.3373 | 2146.3373 | 2146.3373 | 2146.3373 | 2146.3373 | 2146.3373 | 2146.3373 | 2146.3373 | 2146.3373 | 2146.3373 | 2146.3373
60% | 10556.5772 | 14014.5398 | 14955.7822 | 14928.3698 | 14927.3596 | 15034.6321 | 15152.3473 | 15394.0201 | 15567.6823 | 15661.888 | 15764.9032 | 15859.2082 | 16029.6174 | 16241.1243 | 16226.3403 | 16226.3403 | 16226.3403 | 16226.3403 | 16226.3403 | 16226.3403 | 16226.3403 | 16226.3403 | 16226.3403 | 16226.3403 | 16226.3403 | 16226.3403 | 16226.3403 | 16226.3403 | 16226.3403 | 16226.3403 |  | 2277.9105 | 2948.6646 | 3124.1707 | 3113.6361 | 3114.3799 | 3132.3737 | 3179.8897 | 3211.675 | 3242.8062 | 3279.2199 | 3312.9449 | 3345.7006 | 3349.4169 | 3387.6521 | 3358.6203 | 3358.6203 | 3358.6203 | 3358.6203 | 3358.6203 | 3358.6203 | 3358.6203 | 3358.6203 | 3358.6203 | 3358.6203 | 3358.6203 | 3358.6203 | 3358.6203 | 3358.6203 | 3358.6203 | 3358.6203
55% | 11937.0341 | 15847.1857 | 16911.512 | 16880.515 | 16879.3726 | 17000.6729 | 17133.7814 | 17407.0571 | 17603.4287 | 17709.9534 | 17826.4396 | 17933.0767 | 18125.7699 | 18364.935 | 18348.2178 | 18348.2178 | 18348.2178 | 18348.2178 | 18348.2178 | 18348.2178 | 18348.2178 | 18348.2178 | 18348.2178 | 18348.2178 | 18348.2178 | 18348.2178 | 18348.2178 | 18348.2178 | 18348.2178 | 18348.2178 |  | 4377.3623 | 5666.3214 | 6003.5838 | 5983.3401 | 5984.7694 | 6019.3473 | 6110.6567 | 6171.737 | 6231.5606 | 6301.5352 | 6366.343 | 6429.2884 | 6436.4298 | 6509.9048 | 6454.1156 | 6454.1156 | 6454.1156 | 6454.1156 | 6454.1156 | 6454.1156 | 6454.1156 | 6454.1156 | 6454.1156 | 6454.1156 | 6454.1156 | 6454.1156 | 6454.1156 | 6454.1156 | 6454.1156 | 6454.1156
50% | 15327.7148 | 20348.5339 | 21715.179 | 21675.3774 | 21673.9105 | 21829.6658 | 22000.5834 | 22351.4823 | 22603.6327 | 22740.4155 | 22889.9893 | 23026.9163 | 23274.3434 | 23581.4427 | 23559.977 | 23559.977 | 23559.977 | 23559.977 | 23559.977 | 23559.977 | 23559.977 | 23559.977 | 23559.977 | 23559.977 | 23559.977 | 23559.977 | 23559.977 | 23559.977 | 23559.977 | 23559.977 |  | 9714.4123 | 12574.9205 | 13323.3863 | 13278.4606 | 13281.6325 | 13358.3693 | 13561.0066 | 13696.5584 | 13829.3213 | 13984.6116 | 14128.4356 | 14268.1263 | 14283.9748 | 14447.0334 | 14323.224 | 14323.224 | 14323.224 | 14323.224 | 14323.224 | 14323.224 | 14323.224 | 14323.224 | 14323.224 | 14323.224 | 14323.224 | 14323.224 | 14323.224 | 14323.224 | 14323.224 | 14323.224
45% | 20411.3174 | 27097.3455 | 28917.2533 | 28864.251 | 28862.2976 | 29069.7109 | 29297.3152 | 29764.5935 | 30100.3723 | 30282.5206 | 30481.7021 | 30664.0425 | 30993.5314 | 31402.4836 | 31373.8985 | 31373.8985 | 31373.8985 | 31373.8985 | 31373.8985 | 31373.8985 | 31373.8985 | 31373.8985 | 31373.8985 | 31373.8985 | 31373.8985 | 31373.8985 | 31373.8985 | 31373.8985 | 31373.8985 | 31373.8985 |  | 14720.4239 | 19055.0036 | 20189.1672 | 20121.0905 | 20125.8971 | 20242.1776 | 20549.2377 | 20754.6417 | 20955.8197 | 21191.1339 | 21409.073 | 21620.7489 | 21644.7644 | 21891.85 | 21704.2393 | 21704.2393 | 21704.2393 | 21704.2393 | 21704.2393 | 21704.2393 | 21704.2393 | 21704.2393 | 21704.2393 | 21704.2393 | 21704.2393 | 21704.2393 | 21704.2393 | 21704.2393 | 21704.2393 | 21704.2393
40% | 14315.8312 | 19005.1929 | 20281.6168 | 20244.4427 | 20243.0727 | 20388.5455 | 20548.1797 | 20875.9135 | 21111.4178 | 21239.1706 | 21378.87 | 21506.7576 | 21737.8504 | 22024.6761 | 22004.6275 | 22004.6275 | 22004.6275 | 22004.6275 | 22004.6275 | 22004.6275 | 22004.6275 | 22004.6275 | 22004.6275 | 22004.6275 | 22004.6275 | 22004.6275 | 22004.6275 | 22004.6275 | 22004.6275 | 22004.6275 |  | 15242.3215 | 19730.5793 | 20904.9535 | 20834.4632 | 20839.4402 | 20959.8434 | 21277.7899 | 21490.4763 | 21698.7869 | 21942.444 | 22168.1098 | 22387.2904 | 22412.1574 | 22668.0032 | 22473.741 | 22473.741 | 22473.741 | 22473.741 | 22473.741 | 22473.741 | 22473.741 | 22473.741 | 22473.741 | 22473.741 | 22473.741 | 22473.741 | 22473.741 | 22473.741 | 22473.741 | 22473.741
35% | 7422.2532 | 9853.5218 | 10515.3025 | 10496.0291 | 10495.3188 | 10570.7413 | 10653.506 | 10823.4244 | 10945.5251 | 11011.7604 | 11084.1896 | 11150.4949 | 11270.3083 | 11419.0173 | 11408.6228 | 11408.6228 | 11408.6228 | 11408.6228 | 11408.6228 | 11408.6228 | 11408.6228 | 11408.6228 | 11408.6228 | 11408.6228 | 11408.6228 | 11408.6228 | 11408.6228 | 11408.6228 | 11408.6228 | 11408.6228 |  | 20759.9869 | 26872.9779 | 28472.4713 | 28376.4638 | 28383.2424 | 28547.2311 | 28980.2731 | 29269.9512 | 29553.6695 | 29885.5295 | 30192.8856 | 30491.4088 | 30525.2776 | 30873.7386 | 30609.1541 | 30609.1541 | 30609.1541 | 30609.1541 | 30609.1541 | 30609.1541 | 30609.1541 | 30609.1541 | 30609.1541 | 30609.1541 | 30609.1541 | 30609.1541 | 30609.1541 | 30609.1541 | 30609.1541 | 30609.1541
30% | 3452.1096 | 4582.899 | 4890.695 | 4881.7308 | 4881.4005 | 4916.4797 | 4954.9738 | 5034.0033 | 5090.7926 | 5121.5988 | 5155.2859 | 5186.1246 | 5241.8501 | 5311.0151 | 5306.1806 | 5306.1806 | 5306.1806 | 5306.1806 | 5306.1806 | 5306.1806 | 5306.1806 | 5306.1806 | 5306.1806 | 5306.1806 | 5306.1806 | 5306.1806 | 5306.1806 | 5306.1806 | 5306.1806 | 5306.1806 |  | 19183.5111 | 24832.2926 | 26310.3234 | 26221.6065 | 26227.8703 | 26379.406 | 26779.5636 | 27047.2441 | 27309.4173 | 27616.0765 | 27900.0925 | 28175.9464 | 28207.2432 | 28529.2428 | 28284.7504 | 28284.7504 | 28284.7504 | 28284.7504 | 28284.7504 | 28284.7504 | 28284.7504 | 28284.7504 | 28284.7504 | 28284.7504 | 28284.7504 | 28284.7504 | 28284.7504 | 28284.7504 | 28284.7504 | 28284.7504
25% | 2357.031 | 3129.1112 | 3339.2681 | 3333.1476 | 3332.922 | 3356.8734 | 3383.1564 | 3437.1161 | 3475.8908 | 3496.9246 | 3519.9255 | 3540.9815 | 3579.0298 | 3626.2542 | 3622.9533 | 3622.9533 | 3622.9533 | 3622.9533 | 3622.9533 | 3622.9533 | 3622.9533 | 3622.9533 | 3622.9533 | 3622.9533 | 3622.9533 | 3622.9533 | 3622.9533 | 3622.9533 | 3622.9533 | 3622.9533 |  | 5533.3008 | 7162.6379 | 7588.9618 | 7563.3722 | 7565.179 | 7608.888 | 7724.3096 | 7801.5195 | 7877.1409 | 7965.5938 | 8047.5155 | 8127.0829 | 8136.1102 | 8228.9879 | 8158.4664 | 8158.4664 | 8158.4664 | 8158.4664 | 8158.4664 | 8158.4664 | 8158.4664 | 8158.4664 | 8158.4664 | 8158.4664 | 8158.4664 | 8158.4664 | 8158.4664 | 8158.4664 | 8158.4664 | 8158.4664
20% | 1427.8587 | 1895.5749 | 2022.8852 | 2019.1774 | 2019.0408 | 2033.5502 | 2049.4721 | 2082.1602 | 2105.6494 | 2118.3914 | 2132.325 | 2145.0805 | 2168.1297 | 2196.7376 | 2194.738 | 2194.738 | 2194.738 | 2194.738 | 2194.738 | 2194.738 | 2194.738 | 2194.738 | 2194.738 | 2194.738 | 2194.738 | 2194.738 | 2194.738 | 2194.738 | 2194.738 | 2194.738 |  | 1484.8203 | 1922.0408 | 2036.4417 | 2029.5749 | 2030.0597 | 2041.7887 | 2072.7613 | 2093.48 | 2113.7724 | 2137.5081 | 2159.4912 | 2180.8425 | 2183.2649 | 2208.1879 | 2189.264 | 2189.264 | 2189.264 | 2189.264 | 2189.264 | 2189.264 | 2189.264 | 2189.264 | 2189.264 | 2189.264 | 2189.264 | 2189.264 | 2189.264 | 2189.264 | 2189.264 | 2189.264
15% | 914.1778 | 1213.6303 | 1295.1399 | 1292.766 | 1292.6786 | 1301.9681 | 1312.162 | 1333.0904 | 1348.1292 | 1356.2872 | 1365.2081 | 1373.3747 | 1388.1318 | 1406.4479 | 1405.1676 | 1405.1676 | 1405.1676 | 1405.1676 | 1405.1676 | 1405.1676 | 1405.1676 | 1405.1676 | 1405.1676 | 1405.1676 | 1405.1676 | 1405.1676 | 1405.1676 | 1405.1676 | 1405.1676 | 1405.1676 |  | 818.9695 | 1060.1234 | 1123.2225 | 1119.4351 | 1119.7025 | 1126.1718 | 1143.255 | 1154.6827 | 1165.8752 | 1178.9669 | 1191.0919 | 1202.8685 | 1204.2046 | 1217.9511 | 1207.5134 | 1207.5134 | 1207.5134 | 1207.5134 | 1207.5134 | 1207.5134 | 1207.5134 | 1207.5134 | 1207.5134 | 1207.5134 | 1207.5134 | 1207.5134 | 1207.5134 | 1207.5134 | 1207.5134 | 1207.5134
10% | 611.8703 | 812.2975 | 866.8529 | 865.264 | 865.2055 | 871.4231 | 878.246 | 892.2536 | 902.3193 | 907.7795 | 913.7504 | 919.2164 | 929.0935 | 941.3527 | 940.4958 | 940.4958 | 940.4958 | 940.4958 | 940.4958 | 940.4958 | 940.4958 | 940.4958 | 940.4958 | 940.4958 | 940.4958 | 940.4958 | 940.4958 | 940.4958 | 940.4958 | 940.4958 |  | 191.3984 | 247.7576 | 262.5043 | 261.6191 | 261.6816 | 263.1935 | 267.186 | 269.8567 | 272.4725 | 275.5321 | 278.3658 | 281.118 | 281.4303 | 284.643 | 282.2036 | 282.2036 | 282.2036 | 282.2036 | 282.2036 | 282.2036 | 282.2036 | 282.2036 | 282.2036 | 282.2036 | 282.2036 | 282.2036 | 282.2036 | 282.2036 | 282.2036 | 282.2036
5% | 435.3228 | 577.9192 | 616.7333 | 615.6029 | 615.5612 | 619.9848 | 624.8391 | 634.805 | 641.9663 | 645.8511 | 650.0991 | 653.988 | 661.0151 | 669.7371 | 669.1274 | 669.1274 | 669.1274 | 669.1274 | 669.1274 | 669.1274 | 669.1274 | 669.1274 | 669.1274 | 669.1274 | 669.1274 | 669.1274 | 669.1274 | 669.1274 | 669.1274 | 669.1274 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9.992e-14% | 38.2117 | 50.7285 | 54.1355 | 54.0363 | 54.0326 | 54.4209 | 54.847 | 55.7218 | 56.3504 | 56.6914 | 57.0643 | 57.4056 | 58.0224 | 58.788 | 58.7345 | 58.7345 | 58.7345 | 58.7345 | 58.7345 | 58.7345 | 58.7345 | 58.7345 | 58.7345 | 58.7345 | 58.7345 | 58.7345 | 58.7345 | 58.7345 | 58.7345 | 58.7345 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E @ R (MWh) | 102337.6118 | 135859.8063 | 144984.402 | 144718.661 | 144708.8672 | 145748.789 | 146889.9441 | 149232.7692 | 150916.2863 | 151829.5355 | 152828.1856 | 153742.3981 | 155394.3791 | 157444.7704 | 157301.4516 | 157301.4516 | 157301.4516 | 157301.4516 | 157301.4516 | 157301.4516 | 157301.4516 | 157301.4516 | 157301.4516 | 157301.4516 | 157301.4516 | 157301.4516 | 157301.4516 | 157301.4516 | 157301.4516 | 157301.4516 | E @ R (MWh) | 99292.8528 | 128530.651 | 136180.8614 | 135721.6674 | 135754.0887 | 136538.4294 | 138609.6244 | 139995.1247 | 141352.1196 | 142939.3714 | 144409.4236 | 145837.2289 | 145999.2196 | 147665.8725 | 146400.3925 | 146400.3925 | 146400.3925 | 146400.3925 | 146400.3925 | 146400.3925 | 146400.3925 | 146400.3925 | 146400.3925 | 146400.3925 | 146400.3925 | 146400.3925 | 146400.3925 | 146400.3925 | 146400.3925 | 146400.3925
Option 8 Summer POE50 W E @ R (MWh) N 2 | 71636.3283 | 95101.8644 | 101489.0814 | 101303.0627 | 101296.207 | 102024.1523 | 102822.9609 | 104462.9384 | 105641.4004 | 106280.6749 | 106979.7299 | 107619.6787 | 108776.0654 | 110211.3393 | 110111.0161 | 110111.0161 | 110111.0161 | 110111.0161 | 110111.0161 | 110111.0161 | 110111.0161 | 110111.0161 | 110111.0161 | 110111.0161 | 110111.0161 | 110111.0161 | 110111.0161 | 110111.0161 | 110111.0161 | 110111.0161 | Option 8 Summer POE10 W E @ R (MWh) N 2 | 29787.8558 | 38559.1953 | 40854.2584 | 40716.5002 | 40726.2266 | 40961.5288 | 41582.8873 | 41998.5374 | 42405.6359 | 42881.8114 | 43322.8271 | 43751.1687 | 43799.7659 | 44299.7618 | 43920.1178 | 43920.1178 | 43920.1178 | 43920.1178 | 43920.1178 | 43920.1178 | 43920.1178 | 43920.1178 | 43920.1178 | 43920.1178 | 43920.1178 | 43920.1178 | 43920.1178 | 43920.1178 | 43920.1178 | 43920.1178

## POF N,N-1 & N-2 Risk
N-2 Method 1
| Asset name | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Tx 1 Pof | DS-PHM-TRNFMR-9000004393 | 0.02036% | 0.02036% | 0.02687% | 0.0345% | 0.0433% | 0.05332% | 0.06462% | 0.07725% | 0.09126% | 0.1067% | 0.1236% | 0.142% | 0.1619% | 0.1835% | 0.2066% | 0.2066% | 0.2066% | 0.2066% | 0.2066% | 0.2066% | 0.2066% | 0.2066% | 0.2066% | 0.2066% | 0.2066% | 0.2066% | 0.2066% | 0.2066% | 0.2066% | 0.2066%
Tx 2 Pof | DS-PHM-TRNFMR-9000007050 | 0.02036% | 0.02036% | 0.02687% | 0.0345% | 0.0433% | 0.05332% | 0.06462% | 0.07725% | 0.09126% | 0.1067% | 0.1236% | 0.142% | 0.1619% | 0.1835% | 0.2066% | 0.2066% | 0.2066% | 0.2066% | 0.2066% | 0.2066% | 0.2066% | 0.2066% | 0.2066% | 0.2066% | 0.2066% | 0.2066% | 0.2066% | 0.2066% | 0.2066% | 0.2066%
Tx 3 Pof | bar: FY25 to FY54
Tx 4 Pof
Tx 5 Pof
Total Tx Pof |  | 0.04072% | 0.04072% | 0.05374% | 0.069% | 0.0866% | 0.1066% | 0.1292% | 0.1545% | 0.1825% | 0.2134% | 0.2471% | 0.2839% | 0.3238% | 0.3669% | 0.4133% | 0.4133% | 0.4133% | 0.4133% | 0.4133% | 0.4133% | 0.4133% | 0.4133% | 0.4133% | 0.4133% | 0.4133% | 0.4133% | 0.4133% | 0.4133% | 0.4133% | 0.4133%
N-1 Risk |  | 0.01571% | 0.01571% | 0.02073% | 0.02662% | 0.03341% | 0.04114% | 0.04986% | 0.05961% | 0.07041% | 0.08231% | 0.09535% | 0.1095% | 0.1249% | 0.1416% | 0.1594% | 0.1594% | 0.1594% | 0.1594% | 0.1594% | 0.1594% | 0.1594% | 0.1594% | 0.1594% | 0.1594% | 0.1594% | 0.1594% | 0.1594% | 0.1594% | 0.1594% | 0.1594%
N-2 Risk |  | 9.715e-07% | 9.715e-07% | 1.693e-06% | 2.79e-06% | 4.394e-06% | 6.665e-06% | 9.789e-06% | 1.399e-05% | 1.952e-05% | 2.668e-05% | 3.579e-05% | 4.725e-05% | 6.146e-05% | 7.89e-05% | 0.0001001% | 0.0001001% | 0.0001001% | 0.0001001% | 0.0001001% | 0.0001001% | 0.0001001% | 0.0001001% | 0.0001001% | 0.0001001% | 0.0001001% | 0.0001001% | 0.0001001% | 0.0001001% | 0.0001001% | 0.0001001%
N Risk |  | 99.98% | 99.98% | 99.98% | 99.97% | 99.97% | 99.96% | 99.95% | 99.94% | 99.93% | 99.92% | 99.9% | 99.89% | 99.87% | 99.86% | 99.84% | 99.84% | 99.84% | 99.84% | 99.84% | 99.84% | 99.84% | 99.84% | 99.84% | 99.84% | 99.84% | 99.84% | 99.84% | 99.84% | 99.84% | 99.84%

## Summary
Involuntary load shedding (NER 5.17.1(c)(4)(ii))
Option 1 - Do Nothing / Base Case | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Weighted Energy @ Risk (MWh) under N Conditions | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Weighted Energy @ Risk (MWh) under N-1 Conditions | 0.016047 | 0.76653 | 2.0475 | 2.7981 | 3.6899 | 5.0618 | 7.5976 | 10.4828 | 14.6943 | 21.3996 | 22.8419 | 24.1564 | 31.4577 | 43.8687 | 43.1274 | 43.1274 | 43.1274 | 43.1274 | 43.1274 | 43.1274 | 43.1274 | 43.1274 | 43.1274 | 43.1274 | 43.1274 | 43.1274 | 43.1274 | 43.1274 | 43.1274 | 43.1274
Weighted Energy @ Risk (MWh) under N-2 Conditions | 0.0026361 | 0.0035526 | 0.006615 | 0.010954 | 0.017327 | 0.026566 | 0.039893 | 0.058009 | 0.082599 | 0.11565 | 0.1544 | 0.20231 | 0.26757 | 0.35314 | 0.44028 | 0.44028 | 0.44028 | 0.44028 | 0.44028 | 0.44028 | 0.44028 | 0.44028 | 0.44028 | 0.44028 | 0.44028 | 0.44028 | 0.44028 | 0.44028 | 0.44028 | 0.44028
Total EUE (MWh) - Option 1 | 0.018683 | 0.77009 | 2.0541 | 2.809 | 3.7072 | 5.0883 | 7.6375 | 10.5408 | 14.7769 | 21.5152 | 22.9963 | 24.3587 | 31.7253 | 44.2218 | 43.5677 | 43.5677 | 43.5677 | 43.5677 | 43.5677 | 43.5677 | 43.5677 | 43.5677 | 43.5677 | 43.5677 | 43.5677 | 43.5677 | 43.5677 | 43.5677 | 43.5677 | 43.5677
Cost of EUE ($) - Option 1 | 721.2723 | 29730.0409 | 79301.1305 | 108446.461 | 143122.56 | 196441.0945 | 294855.058 | 406939.1331 | 570477.8372 | 830619.5531 | 887800.3865 | 940395.7407 | 1224791.8707 | 1707233.0663 | 1681981.0333 | 1681981.0333 | 1681981.0333 | 1681981.0333 | 1681981.0333 | 1681981.0333 | 1681981.0333 | 1681981.0333 | 1681981.0333 | 1681981.0333 | 1681981.0333 | 1681981.0333 | 1681981.0333 | 1681981.0333 | 1681981.0333 | 1681981.0333
Hours at Risk pA. (Hrs) (N) | 1.486 | 1.486 | 1.486 | 1.486 | 1.486 | 1.486 | 1.486 | 1.486 | 1.486 | 1.486 | 1.486 | 1.486 | 1.486 | 1.486 | 1.486 | 1.486 | 1.486 | 1.486 | 1.486 | 1.486 | 1.486 | 1.486 | 1.486 | 1.486 | 1.486 | 1.486 | 1.486 | 1.486 | 1.486 | 1.486
Option 2 - 1B New PHS ZSS + Three new feeders | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Weighted Energy @ Risk (MWh) under N Conditions | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Weighted Energy @ Risk (MWh) under N-1 Conditions | 0.016047 | 0.76653 | 2.0475 | 0.03982 | 0.050982 | 0.07379 | 0.14464 | 0.26665 | 0.57809 | 1.9032 | 1.2498 | 1.0531 | 1.8593 | 4.2371 | 2.9694 | 2.9694 | 2.9694 | 2.9694 | 2.9694 | 2.9694 | 2.9694 | 2.9694 | 2.9694 | 2.9694 | 2.9694 | 2.9694 | 2.9694 | 2.9694 | 2.9694 | 2.9694
Weighted Energy @ Risk (MWh) under N-2 Conditions | 0.0026361 | 0.0035526 | 0.006615 | 0.0079741 | 0.012633 | 0.019448 | 0.029437 | 0.043068 | 0.06175 | 0.087155 | 0.11617 | 0.15185 | 0.20192 | 0.26886 | 0.33337 | 0.33337 | 0.33337 | 0.33337 | 0.33337 | 0.33337 | 0.33337 | 0.33337 | 0.33337 | 0.33337 | 0.33337 | 0.33337 | 0.33337 | 0.33337 | 0.33337 | 0.33337
Total EUE (MWh) - Option 2 | 0.018683 | 0.77009 | 2.0541 | 0.047795 | 0.063615 | 0.093237 | 0.17408 | 0.30972 | 0.63984 | 1.9904 | 1.366 | 1.2049 | 2.0613 | 4.5059 | 3.3028 | 3.3028 | 3.3028 | 3.3028 | 3.3028 | 3.3028 | 3.3028 | 3.3028 | 3.3028 | 3.3028 | 3.3028 | 3.3028 | 3.3028 | 3.3028 | 3.3028 | 3.3028
Cost of EUE ($) - Option 2 | 721.2723 | 29730.0409 | 79301.1305 | 1845.1643 | 2455.9123 | 3599.5374 | 6720.5222 | 11957.1139 | 24701.6085 | 76840.6577 | 52734.7325 | 46517.8469 | 79577.4036 | 173956.1343 | 127508.6775 | 127508.6775 | 127508.6775 | 127508.6775 | 127508.6775 | 127508.6775 | 127508.6775 | 127508.6775 | 127508.6775 | 127508.6775 | 127508.6775 | 127508.6775 | 127508.6775 | 127508.6775 | 127508.6775 | 127508.6775
Option 3 - 2B PHM 3rd Tx + Switchroom + Two new feeders + OFR12 New Feeder | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Weighted Energy @ Risk (MWh) under N Conditions | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Weighted Energy @ Risk (MWh) under N-1 Conditions | 0.016047 | 0.76653 | 2.0475 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Weighted Energy @ Risk (MWh) under N-2 Conditions | 0.0026361 | 0.0035526 | 0.006615 | 0.0004579 | 0.00075348 | 0.0012511 | 0.0022084 | 0.0035602 | 0.005761 | 0.0095348 | 0.011901 | 0.01454 | 0.021259 | 0.032825 | 0.036817 | 0.036817 | 0.036817 | 0.036817 | 0.036817 | 0.036817 | 0.036817 | 0.036817 | 0.036817 | 0.036817 | 0.036817 | 0.036817 | 0.036817 | 0.036817 | 0.036817 | 0.036817
Total EUE (MWh) - Option 3 | 0.018683 | 0.77009 | 2.0541 | 0.0004579 | 0.00075348 | 0.0012511 | 0.0022084 | 0.0035602 | 0.005761 | 0.0095348 | 0.011901 | 0.01454 | 0.021259 | 0.032825 | 0.036817 | 0.036817 | 0.036817 | 0.036817 | 0.036817 | 0.036817 | 0.036817 | 0.036817 | 0.036817 | 0.036817 | 0.036817 | 0.036817 | 0.036817 | 0.036817 | 0.036817 | 0.036817
Cost of EUE ($) - Option 3 | 721.2723 | 29730.0409 | 79301.1305 | 17.6778 | 29.0888 | 48.2991 | 85.2584 | 137.4461 | 222.4108 | 368.1027 | 459.437 | 561.3151 | 820.7279 | 1267.2603 | 1421.3458 | 1421.3458 | 1421.3458 | 1421.3458 | 1421.3458 | 1421.3458 | 1421.3458 | 1421.3458 | 1421.3458 | 1421.3458 | 1421.3458 | 1421.3458 | 1421.3458 | 1421.3458 | 1421.3458 | 1421.3458
Option 4 - 3B OFR 3rd Tx + Switchroom + Two new feeders + OFR12 New Feeder | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Weighted Energy @ Risk (MWh) under N Conditions | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Weighted Energy @ Risk (MWh) under N-1 Conditions | 0.016047 | 0.76653 | 2.0475 | 1.5595 | 2.089 | 2.9541 | 4.7111 | 6.7241 | 9.8279 | 15.1247 | 15.7349 | 16.2751 | 21.8172 | 31.7237 | 30.3126 | 30.3126 | 30.3126 | 30.3126 | 30.3126 | 30.3126 | 30.3126 | 30.3126 | 30.3126 | 30.3126 | 30.3126 | 30.3126 | 30.3126 | 30.3126 | 30.3126 | 30.3126
Weighted Energy @ Risk (MWh) under N-2 Conditions | 0.0026361 | 0.0035526 | 0.006615 | 0.010338 | 0.016356 | 0.025093 | 0.037729 | 0.054918 | 0.078285 | 0.10975 | 0.14649 | 0.19187 | 0.25398 | 0.3357 | 0.41816 | 0.41816 | 0.41816 | 0.41816 | 0.41816 | 0.41816 | 0.41816 | 0.41816 | 0.41816 | 0.41816 | 0.41816 | 0.41816 | 0.41816 | 0.41816 | 0.41816 | 0.41816
Total EUE (MWh) - Option 4 | 0.018683 | 0.77009 | 2.0541 | 1.5698 | 2.1054 | 2.9792 | 4.7488 | 6.7791 | 9.9062 | 15.2345 | 15.8814 | 16.467 | 22.0712 | 32.0594 | 30.7308 | 30.7308 | 30.7308 | 30.7308 | 30.7308 | 30.7308 | 30.7308 | 30.7308 | 30.7308 | 30.7308 | 30.7308 | 30.7308 | 30.7308 | 30.7308 | 30.7308 | 30.7308
Cost of EUE ($) - Option 4 | 721.2723 | 29730.0409 | 79301.1305 | 60604.9537 | 81281.5245 | 115016.5332 | 183333.3324 | 261713.4258 | 382440.0661 | 588145.3014 | 613117.9283 | 635725.6232 | 852082.6931 | 1237691.3303 | 1186397.9945 | 1186397.9945 | 1186397.9945 | 1186397.9945 | 1186397.9945 | 1186397.9945 | 1186397.9945 | 1186397.9945 | 1186397.9945 | 1186397.9945 | 1186397.9945 | 1186397.9945 | 1186397.9945 | 1186397.9945 | 1186397.9945 | 1186397.9945
Option 5 - 4B LLG 2nd Tx + Switchroom + Two new feeders + OFR12 New Feeder | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Weighted Energy @ Risk (MWh) under N Conditions | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Weighted Energy @ Risk (MWh) under N-1 Conditions | 0.016047 | 0.76653 | 2.0475 | 0.02327 | 0.029298 | 0.040456 | 0.068538 | 0.11771 | 0.26321 | 1.1681 | 0.60142 | 0.50886 | 0.92352 | 2.4286 | 1.5452 | 1.5452 | 1.5452 | 1.5452 | 1.5452 | 1.5452 | 1.5452 | 1.5452 | 1.5452 | 1.5452 | 1.5452 | 1.5452 | 1.5452 | 1.5452 | 1.5452 | 1.5452
Weighted Energy @ Risk (MWh) under N-2 Conditions | 0.0026361 | 0.0035526 | 0.006615 | 0.0076016 | 0.012046 | 0.018558 | 0.02813 | 0.0412 | 0.059144 | 0.083593 | 0.11139 | 0.14554 | 0.19372 | 0.25833 | 0.32001 | 0.32001 | 0.32001 | 0.32001 | 0.32001 | 0.32001 | 0.32001 | 0.32001 | 0.32001 | 0.32001 | 0.32001 | 0.32001 | 0.32001 | 0.32001 | 0.32001 | 0.32001
Total EUE (MWh) - Option 5 | 0.018683 | 0.77009 | 2.0541 | 0.030871 | 0.041345 | 0.059013 | 0.096668 | 0.15891 | 0.32235 | 1.2517 | 0.71281 | 0.6544 | 1.1172 | 2.687 | 1.8652 | 1.8652 | 1.8652 | 1.8652 | 1.8652 | 1.8652 | 1.8652 | 1.8652 | 1.8652 | 1.8652 | 1.8652 | 1.8652 | 1.8652 | 1.8652 | 1.8652 | 1.8652
Cost of EUE ($) - Option 5 | 721.2723 | 29730.0409 | 79301.1305 | 1191.826 | 1596.1579 | 2278.2802 | 3731.9708 | 6134.811 | 12444.7412 | 48321.5356 | 27518.9192 | 25263.8609 | 43132.0129 | 103733.367 | 72008.3378 | 72008.3378 | 72008.3378 | 72008.3378 | 72008.3378 | 72008.3378 | 72008.3378 | 72008.3378 | 72008.3378 | 72008.3378 | 72008.3378 | 72008.3378 | 72008.3378 | 72008.3378 | 72008.3378 | 72008.3378
Option 6 - | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Weighted Energy @ Risk (MWh) under N Conditions | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Weighted Energy @ Risk (MWh) under N-1 Conditions | 0.016047 | 0.76653 | 2.0475 | 2.7981 | 3.6899 | 5.0618 | 7.5976 | 10.4828 | 14.6943 | 21.3996 | 22.8419 | 24.1564 | 31.4577 | 43.8687 | 43.1274 | 43.1274 | 43.1274 | 43.1274 | 43.1274 | 43.1274 | 43.1274 | 43.1274 | 43.1274 | 43.1274 | 43.1274 | 43.1274 | 43.1274 | 43.1274 | 43.1274 | 43.1274
Weighted Energy @ Risk (MWh) under N-2 Conditions | 0.0026361 | 0.0035526 | 0.006615 | 0.010954 | 0.017327 | 0.026566 | 0.039893 | 0.058009 | 0.082599 | 0.11565 | 0.1544 | 0.20231 | 0.26757 | 0.35314 | 0.44028 | 0.44028 | 0.44028 | 0.44028 | 0.44028 | 0.44028 | 0.44028 | 0.44028 | 0.44028 | 0.44028 | 0.44028 | 0.44028 | 0.44028 | 0.44028 | 0.44028 | 0.44028
Total EUE (MWh) - Option 6 | 0.018683 | 0.77009 | 2.0541 | 2.809 | 3.7072 | 5.0883 | 7.6375 | 10.5408 | 14.7769 | 21.5152 | 22.9963 | 24.3587 | 31.7253 | 44.2218 | 43.5677 | 43.5677 | 43.5677 | 43.5677 | 43.5677 | 43.5677 | 43.5677 | 43.5677 | 43.5677 | 43.5677 | 43.5677 | 43.5677 | 43.5677 | 43.5677 | 43.5677 | 43.5677
Cost of EUE ($) - Option 6 | 721.2723 | 29730.0409 | 79301.1305 | 108446.461 | 143122.56 | 196441.0945 | 294855.058 | 406939.1331 | 570477.8372 | 830619.5531 | 887800.3865 | 940395.7407 | 1224791.8707 | 1707233.0663 | 1681981.0333 | 1681981.0333 | 1681981.0333 | 1681981.0333 | 1681981.0333 | 1681981.0333 | 1681981.0333 | 1681981.0333 | 1681981.0333 | 1681981.0333 | 1681981.0333 | 1681981.0333 | 1681981.0333 | 1681981.0333 | 1681981.0333 | 1681981.0333
Option 7 - | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Weighted Energy @ Risk (MWh) under N Conditions | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Weighted Energy @ Risk (MWh) under N-1 Conditions | 0.016047 | 0.76653 | 2.0475 | 2.7981 | 3.6899 | 5.0618 | 7.5976 | 10.4828 | 14.6943 | 21.3996 | 22.8419 | 24.1564 | 31.4577 | 43.8687 | 43.1274 | 43.1274 | 43.1274 | 43.1274 | 43.1274 | 43.1274 | 43.1274 | 43.1274 | 43.1274 | 43.1274 | 43.1274 | 43.1274 | 43.1274 | 43.1274 | 43.1274 | 43.1274
Weighted Energy @ Risk (MWh) under N-2 Conditions | 0.0026361 | 0.0035526 | 0.006615 | 0.010954 | 0.017327 | 0.026566 | 0.039893 | 0.058009 | 0.082599 | 0.11565 | 0.1544 | 0.20231 | 0.26757 | 0.35314 | 0.44028 | 0.44028 | 0.44028 | 0.44028 | 0.44028 | 0.44028 | 0.44028 | 0.44028 | 0.44028 | 0.44028 | 0.44028 | 0.44028 | 0.44028 | 0.44028 | 0.44028 | 0.44028
Total EUE (MWh) - Option 7 | 0.018683 | 0.77009 | 2.0541 | 2.809 | 3.7072 | 5.0883 | 7.6375 | 10.5408 | 14.7769 | 21.5152 | 22.9963 | 24.3587 | 31.7253 | 44.2218 | 43.5677 | 43.5677 | 43.5677 | 43.5677 | 43.5677 | 43.5677 | 43.5677 | 43.5677 | 43.5677 | 43.5677 | 43.5677 | 43.5677 | 43.5677 | 43.5677 | 43.5677 | 43.5677
Cost of EUE ($) - Option 7 | 721.2723 | 29730.0409 | 79301.1305 | 108446.461 | 143122.56 | 196441.0945 | 294855.058 | 406939.1331 | 570477.8372 | 830619.5531 | 887800.3865 | 940395.7407 | 1224791.8707 | 1707233.0663 | 1681981.0333 | 1681981.0333 | 1681981.0333 | 1681981.0333 | 1681981.0333 | 1681981.0333 | 1681981.0333 | 1681981.0333 | 1681981.0333 | 1681981.0333 | 1681981.0333 | 1681981.0333 | 1681981.0333 | 1681981.0333 | 1681981.0333 | 1681981.0333
Option 8 - | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Weighted Energy @ Risk (MWh) under N Conditions | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Weighted Energy @ Risk (MWh) under N-1 Conditions | 0.016047 | 0.76653 | 2.0475 | 2.7981 | 3.6899 | 5.0618 | 7.5976 | 10.4828 | 14.6943 | 21.3996 | 22.8419 | 24.1564 | 31.4577 | 43.8687 | 43.1274 | 43.1274 | 43.1274 | 43.1274 | 43.1274 | 43.1274 | 43.1274 | 43.1274 | 43.1274 | 43.1274 | 43.1274 | 43.1274 | 43.1274 | 43.1274 | 43.1274 | 43.1274
Weighted Energy @ Risk (MWh) under N-2 Conditions | 0.0026361 | 0.0035526 | 0.006615 | 0.010954 | 0.017327 | 0.026566 | 0.039893 | 0.058009 | 0.082599 | 0.11565 | 0.1544 | 0.20231 | 0.26757 | 0.35314 | 0.44028 | 0.44028 | 0.44028 | 0.44028 | 0.44028 | 0.44028 | 0.44028 | 0.44028 | 0.44028 | 0.44028 | 0.44028 | 0.44028 | 0.44028 | 0.44028 | 0.44028 | 0.44028
Total EUE (MWh) - Option 8 | 0.018683 | 0.77009 | 2.0541 | 2.809 | 3.7072 | 5.0883 | 7.6375 | 10.5408 | 14.7769 | 21.5152 | 22.9963 | 24.3587 | 31.7253 | 44.2218 | 43.5677 | 43.5677 | 43.5677 | 43.5677 | 43.5677 | 43.5677 | 43.5677 | 43.5677 | 43.5677 | 43.5677 | 43.5677 | 43.5677 | 43.5677 | 43.5677 | 43.5677 | 43.5677
Cost of EUE ($) - Option 8 | 721.2723 | 29730.0409 | 79301.1305 | 108446.461 | 143122.56 | 196441.0945 | 294855.058 | 406939.1331 | 570477.8372 | 830619.5531 | 887800.3865 | 940395.7407 | 1224791.8707 | 1707233.0663 | 1681981.0333 | 1681981.0333 | 1681981.0333 | 1681981.0333 | 1681981.0333 | 1681981.0333 | 1681981.0333 | 1681981.0333 | 1681981.0333 | 1681981.0333 | 1681981.0333 | 1681981.0333 | 1681981.0333 | 1681981.0333 | 1681981.0333 | 1681981.0333