## Info
Document description
This model Energy at Risk model has been developed to calculated Energy at Risk (EaR) in terms of Expected Unsureved Energy (EUE) and the cost of EUE. The modelling inputs, calculation steps and outputs are described in the 'Modelling Steps' tab. Further detail on EaR/EUE calculations can be found in AusNet's Network Planning Policy and Guidelines.
Tab # | Tab Name | Description | Source/ Inputs
0.1 | Modelling Steps | E@R model process flowchart and underlying equations | N/A
0.2 | Modelling Example & QA | Example E@R model calculations and data flow; also used to validate base case | N/A
0.3 | QA | Quality assurance and data validation | Entire workbook
1.1 | Output for AusNet's NPV Model | Aggregates Supply Risk ($M) and EUE (MWh) for input into AusNet’s NPV model | Summary tab
2.1 | Key Model Assumptions & Inputs | E@R model inputs and asset selection | Augmentation plans from RPs/EPCs, Embedded Generation DB, Demand Management DB
2.2 | Tx PoF | Transformer Probabilities of Failure | Provided by Asset Management Team
2.3 | Customer No. and Volume per Feeder | Customer consumption data | Provided by Finance Team
2.4 | AER VCR Rates (2024) | AER 2024 VCR rates | AER VCR Factsheet
2.5 | Forecast - Summer | Summer Forecast Data | Extract from Forecasting Toolbox
2.6 | Forecast- Winter | Winter Forecast Data | Extract from Forecasting Toolbox
2.7 | Ratings | Station Rating Data | AMS 20-101 / Provided by Asset mangement Team
2.8 | FT (Forecast & Transfers) | Forecast, transfer & PF inputs | Forecast Summer , Forecast Winter , NP Transfer Sheet, PF = avg. max demand PF across stations
2.9 | Load Duration Curves | Load duration curve data | LDC Tool; data sourced from PI SCADA Historian and AEMO
3.1 | Capacity N | Option N capacity calculated | FT Sheet, Ratings & Key Model Assumptions
3.2 | Capacity N-1 | Option N-1 capacity calculated | FT Sheet, Ratings & Key Model Assumptions
3.3 | Capacity N-1 | Option N-2 capacity calculated | FT Sheet, Ratings & Key Model Assumptions
3.4 | Demand | Calculates maximum demand | FT Sheet & Key Model Assumptions
3.5 | MD Weighted LDC | Maps maximum demand forecast to load duration curve | Demand Sheet & Load Duration Curve Sheet
3.6 | Locational VCR | Calculates tailored VCR by location using feeder energy mix and AER rates | AER VCR Rates (2024) & Customer No./Volume per Feeder
3.7 | E@R N | Calculates N EUE using capacity and demand inputs | MD Weighted LDC & Capacity N
3.8 | E@R N-1 | Calculates N-1 EUE using capacity and demand inputs | MD Weighted LDC & Capacity N-1
3.9 | E@R N-2 | Calculates N-2 EUE using capacity and demand inputs | MD Weighted LDC & Capacity N-2
4 | POF N,N-1 & N-2 Risk | Calculates Station N , N-1 & N-2 PoF's from Tx PoF Data & MTTR | TX PoF & Key Model Assumptions
4.1 | Summary | Collates weighted EUE and calculates supply risk | E@R & Locational VCR
Revision table
Date | Editted by | Change
2025-10-14 | HT | Draft Version 2.1
2025-10-20 | HT | Version 2.2
2025-11-10 | HT | Version 2.3 Example Page Update and General Refinements

## Modelling Steps
Eq1. Locational VCR |  | Data Inputs |  |  | Calculations |  |  |  |  | Outputs
|  |  | Customer No. and Vol per Feeder |  | Eq1.
Locational VCR
Eq2. Maximum Demand
AER Latetst VCR Rates
Eq3. Options & Do nothing Capacity
Eq6. & Eq7.
Load Forecast
[9 empty] | Summary Sheet | Output for AusNet's NPV Model
Eq4. Help Sheet | Re Name Forecasted LDC add Forecast MD to eq
Transfer Capacity
Eq2.
Eq5. Energy at Risk ( Option/ Do Nothing Capacity) |  |  |  |  | Options & Do Nothing Max Demand
Embeded Generation
Eq6. Weighted Expected Unserved Energy
[6 empty] | Eq.4 | Eq.5
Demand Mangement Capacity
[6 empty] | Forecasted LDC |  | Energy @ Risk Sheet
Eq7. Supply Risk
Load Duration Curves
|  |  | Asset Ratings |  | Eq3.
Options & Do Nothing Capacity
Planned & Proposed Works

## Modelling Steps Example & QA
End of Sheet
Data Inputs |  |  | Calculations | [12 empty] | Outputs
AER VCR Rates(2024 |  |  | Locational (Tailored VCR)
Category | Rate |  | Base case |  | Energy Usage (CY 2024 kWh) | Energy Usage (CY 2024 %) | Tailored VCR
Dec 24 AER VCR ($/kWh) - Res | 49.23 |  | Dec 24 AER VCR ($/kWh) - Res | 49.23 | 67934749.1441 | 34.06% | 16.7657
Dec 24 AER VCR ($/kWh) - Com | 34.39 |  | Dec 24 AER VCR ($/kWh) - Com | 34.39 | 101368150.4504 | 50.82% | 17.4756
Dec 24 AER VCR ($/kWh) - Ind | 33.49 |  | Dec 24 AER VCR ($/kWh) - Ind | 33.49 | 17726336.2671 | 8.886% | 2.976
Dec 24 AER VCR ($/kWh) - Agr | 22.25 |  | Dec 24 AER VCR ($/kWh) - Agr | 22.25 | 12451243.5083 | 6.242% | 1.3888
[5 empty] | 199480479.3698 |  | 38.6062
Customer No. and Vol per Feeder | [6 empty] | 38606.1513 | [8 empty] | Summary |  | Outputs for NPV model
COMMERCIAL | 101368150.4504 | [14 empty] | Year | 2031 | Year | 2031
[16 empty] | E@R MWh | 1.8981 | E@R MWh | 1.8981
RESIDENTL | 67934749.1441 | [14 empty] | cost of EUE ($) | 73276.699 | cost of EUE ($M) | 0.073277
FARM | 12451243.5083
INDUSTRIAL | 17726336.2671
Forecast (FCT)
Forecast | 2031
Summer POE50 | 67.5138
Summer POE10 | 73.0705
Winter POE50 | 65.9652
Winter POE10 | 68.6243
Transfer Capacity |  |  | Option Max Demand |  |  |  | MD Weighted LDC |  |  | E@R (N) |  | E@R (N-1) |  | E@R (N-2)
Year | 2031 |  | Forecast | 2031 |  |  | % of MD | Summer - AD - Hours | FY31 | % of MD | FY31 | % of MD | FY31 | % of MD | FY31
Capacity | 1.58 |  | Summer POE50 | 65.9338 |  |  | 100% | 0 | 65.9338 | 100% |  | 100% |  | 100%
|  |  | Summer POE10 | 71.4905 |  |  | 99% | 0 | 65.2745 | 99% |  | 99% | 0 | 99% | 0
Embedded Generation |  |  | Winter POE50 | 64.3852 |  |  | 98% | 0 | 64.6151 | 98% |  | 98% | 0 | 98% | 0
|  |  | Winter POE10 | 67.0443 |  |  | 97% | 0.37816 | 63.9558 | 97% |  | 97% | 7.2931 | 97% | 24.3105
Year | 2031 | [5 empty] | 95% | 2.269 | 62.6371 | 95% |  | 95% | 34.5953 | 95% | 119.6823
Capacity | 0 | [5 empty] | 90% | 5.6725 | 59.3404 | 90% |  | 90% | 54.4175 | 90% | 207.574
[7 empty] | 85% | 15.8829 | 56.0437 | 85% |  | 85% | 129.5917 | 85% | 589.0613
Demand Mangement | [6 empty] | 80% | 31.0095 | 52.747 | 80% |  | 80% | 142.1201 | 80% | 822.8158
[7 empty] | 75% | 72.9857 | 49.4504 | 75% |  | 75% | 256.0006 | 75% | 2144.9312
Year | 2031 | [5 empty] | 70% | 150.5094 | 46.1537 | 70% |  | 70% | 217.2224 | 70% | 3705.7879
Capacity | 0 | [5 empty] | 65% | 359.6342 | 42.857 | 65% |  | 65% | 42.2143 | 65% | 9307.1689
[7 empty] | 60% | 689.7717 | 39.5603 | 60% |  | 60% |  | 60% | 13604.5115
LDC | [6 empty] | 55% | 1095.5419 | 36.2636 | 55% |  | 55% |  | 55% | 15383.539
[7 empty] | 50% | 1666.1918 | 32.9669 | 50% |  | 50% |  | 50% | 19753.1897
% of MD | Summer - AD - Duration % | Summer - AD - Hours |  |  |  |  | 45% | 2506.0947 | 29.6702 | 45% |  | 45% |  | 45% | 26304.5489
100% | 0% | 0 |  |  |  |  | 40% | 3164.4787 | 26.3735 | 40% |  | 40% |  | 40% | 18449.1513
99% | 0% | 0 |  |  |  |  | 35% | 3551.3408 | 23.0768 | 35% |  | 35% |  | 35% | 9565.2339
98% | 0% | 0 |  |  |  |  | 30% | 3758.953 | 19.7801 | 30% |  | 30% |  | 30% | 4448.8155
97% | 0.00861% | 0.37816 |  |  |  |  | 25% | 3926.4798 | 16.4835 | 25% |  | 25% |  | 25% | 3037.5617
95% | 0.05166% | 2.269 |  |  |  |  | 20% | 4050.5177 | 13.1868 | 20% |  | 20% |  | 20% | 1840.1154
90% | 0.1292% | 5.6725 |  |  |  |  | 15% | 4152.622 | 9.8901 | 15% |  | 15% |  | 15% | 1178.1226
85% | 0.3616% | 15.8829 |  |  |  |  | 10% | 4248.2976 | 6.5934 | 10% |  | 10% |  | 10% | 788.5318
80% | 0.706% | 31.0095 |  |  |  |  | 5% | 4361.7469 | 3.2967 | 5% |  | 5% |  | 5% | 561.0108
75% | 1.662% | 72.9857 |  |  |  |  | 9.992e-14% | 4391.6218 | 6.5881e-14 | 9.992e-14% |  | 9.992e-14% |  | 9.992e-14% | 49.2443
70% | 3.427% | 150.5094 | [7 empty] | Total E@R | 0 | Total E@R | 883.4549 | Total E@R | 131884.9083
65% | 8.188% | 359.6342 | [7 empty] | Total WE@R | 0 | Total WE@R | 0.27342 | Total WE@R | 0.005342
60% | 15.71% | 689.7717 |  |  |  |  | MD Weighted LDC
55% | 24.94% | 1095.5419
50% | 37.94% | 1666.1918 |  |  |  |  | % of MD | Summer - MD - Hours | FY31
45% | 57.06% | 2506.0947 |  |  |  |  | 100% | 0 | 71.4905 | E@R (N) |  | E@R (N-1) |  | E@R (N-2)
40% | 72.05% | 3164.4787 |  |  |  |  | 99% | 1.5127 | 70.7756
35% | 80.86% | 3551.3408 |  |  |  |  | 98% | 2.269 | 70.0607 | % of MD | FY31 | % of MD | FY31 | % of MD | FY31
30% | 85.59% | 3758.953 |  |  |  |  | 97% | 3.7816 | 69.3458 | 100% |  | 100% |  | 100%
25% | 89.4% | 3926.4798 |  |  |  |  | 95% | 6.0506 | 67.916 | 99% |  | 99% | 39.5304 | 99% | 107.6
20% | 92.22% | 4050.5177 |  |  |  |  | 90% | 16.2611 | 64.3415 | 98% |  | 98% | 19.2245 | 98% | 53.2593
15% | 94.55% | 4152.622 |  |  |  |  | 85% | 26.4715 | 60.767 | 97% |  | 97% | 37.3676 | 97% | 105.4372
10% | 96.73% | 4248.2976 |  |  |  |  | 80% | 34.0348 | 57.1924 | 95% |  | 95% | 53.6182 | 95% | 155.7226
5% | 99.31% | 4361.7469 |  |  |  |  | 75% | 48.405 | 53.6179 | 90% |  | 90% | 215.7337 | 90% | 675.2033
9.992e-14% | 99.99% | 4391.6218 |  |  |  |  | 70% | 76.3892 | 50.0434 | 85% |  | 85% | 179.2362 | 85% | 638.7059
[7 empty] | 65% | 114.2056 | 46.4689 | 80% |  | 80% | 105.7324 | 80% | 446.0803
[7 empty] | 60% | 178.1154 | 42.8943 | 75% |  | 75% | 149.5248 | 75% | 796.1857
[7 empty] | 55% | 311.6074 | 39.3198 | 70% |  | 70% | 191.1497 | 70% | 1450.4368
LDC | [6 empty] | 50% | 636.0723 | 35.7453 | 65% |  | 65% | 123.1346 | 65% | 1824.8739
[7 empty] | 45% | 1179.4944 | 32.1707 | 60% |  | 60% | 19.2874 | 60% | 2855.5897
% of MD | Summer - MD - Duration % | Summer - MD - Hours |  |  |  |  | 40% | 1808.3816 | 28.5962 | 55% |  | 55% |  | 55% | 5487.4633
100% | 0% | 0 |  |  |  |  | 35% | 2779.1293 | 25.0217 | 50% |  | 50% |  | 50% | 12177.9916
99% | 0.03444% | 1.5127 |  |  |  |  | 30% | 3814.165 | 21.4472 | 45% |  | 45% |  | 45% | 18453.5301
98% | 0.05166% | 2.269 |  |  |  |  | 25% | 4166.9923 | 17.8726 | 40% |  | 40% |  | 40% | 19107.7811
97% | 0.0861% | 3.7816 |  |  |  |  | 20% | 4282.7105 | 14.2981 | 35% |  | 35% |  | 35% | 26024.729
95% | 0.1378% | 6.0506 |  |  |  |  | 15% | 4364.7722 | 10.7236 | 30% |  | 30% |  | 30% | 24048.4582
90% | 0.3702% | 16.2611 |  |  |  |  | 10% | 4391.6218 | 7.1491 | 25% |  | 25% |  | 25% | 6936.5483
85% | 0.6027% | 26.4715 |  |  |  |  | 5% | 4391.6218 | 3.5745 | 20% |  | 20% |  | 20% | 1861.3713
80% | 0.7749% | 34.0348 |  |  |  |  | 9.992e-14% | 4391.6218 | 7.1433e-14 | 15% |  | 15% |  | 15% | 1026.6605
75% | 1.102% | 48.405 | [7 empty] | 10% |  | 10% |  | 10% | 239.9371
70% | 1.739% | 76.3892 | [7 empty] | 5% |  | 5% |  | 5% | 0
65% | 2.6% | 114.2056 | [7 empty] | 9.992e-14% |  | 9.992e-14% |  | 9.992e-14% | 0
60% | 4.055% | 178.1154 | [7 empty] | Total E@R | 0 | Total E@R | 1133.5396 | Total E@R | 124473.5651
55% | 7.095% | 311.6074 |  |  |  |  | MD Weighted LDC |  |  | Total WE@R | 0 | Total WE@R | 0.15035 | Total WE@R | 0.0021608
50% | 14.48% | 636.0723
45% | 26.86% | 1179.4944 |  |  |  |  | % of MD | Winter - AD - Hours | FY31
40% | 41.17% | 1808.3816 |  |  |  |  | 100% | 0 | 64.3852
35% | 63.28% | 2779.1293 |  |  |  |  | 99% | 1.486 | 63.7413 | E@R (N) |  | E@R (N-1) |  | E@R (N-2)
30% | 86.84% | 3814.165 |  |  |  |  | 98% | 3.2692 | 63.0975
25% | 94.88% | 4166.9923 |  |  |  |  | 97% | 6.8356 | 62.4536 | % of MD | FY31 | % of MD | FY31 | % of MD | FY31
20% | 97.51% | 4282.7105 |  |  |  |  | 95% | 17.5347 | 61.1659 | 100% |  | 100% |  | 100%
15% | 99.38% | 4364.7722 |  |  |  |  | 90% | 78.7576 | 57.9467 | 99% |  | 99% | 22.2353 | 99% | 95.1975
10% | 99.99% | 4391.6218 |  |  |  |  | 85% | 236.8672 | 54.7274 | 98% |  | 98% | 25.5342 | 98% | 113.0889
5% | 99.99% | 4391.6218 |  |  |  |  | 80% | 497.5104 | 51.5081 | 97% |  | 97% | 48.7723 | 97% | 223.8816
9.992e-14% | 99.99% | 4391.6218 |  |  |  |  | 75% | 803.6248 | 48.2889 | 95% |  | 95% | 135.9838 | 95% | 661.3119
[7 empty] | 70% | 1155.2107 | 45.0696 | 90% |  | 90% | 640.1647 | 90% | 3646.209
[7 empty] | 65% | 1553.1596 | 41.8504 | 85% |  | 85% | 1144.2449 | 85% | 8907.4274
[7 empty] | 60% | 2026.2996 | 38.6311 | 80% |  | 80% | 1047.2057 | 80% | 13844.7828
LDC | [6 empty] | 55% | 2598.4068 | 35.4119 | 75% |  | 75% | 275.7172 | 75% | 15274.6593
[7 empty] | 50% | 3233.5201 | 32.1926 | 70% |  | 70% |  | 70% | 16411.7675
% of MD | Winter - AD (P50) - Duration % | Winter - AD - Hours |  |  |  |  | 45% | 3775.313 | 28.9733 | 65% |  | 65% |  | 65% | 17294.8562
100% | 0% | 0 |  |  |  |  | 40% | 4072.8088 | 25.7541 | 60% |  | 60% |  | 60% | 19039.5064
99% | 0.03383% | 1.486 |  |  |  |  | 35% | 4198.821 | 22.5348 | 55% |  | 55% |  | 55% | 21180.255
98% | 0.07443% | 3.2692 |  |  |  |  | 30% | 4271.3374 | 19.3156 | 50% |  | 50% |  | 50% | 21468.2395
97% | 0.1556% | 6.8356 |  |  |  |  | 25% | 4321.8611 | 16.0963 | 45% |  | 45% |  | 45% | 16569.6328
95% | 0.3992% | 17.5347 |  |  |  |  | 20% | 4353.067 | 12.877 | 40% |  | 40% |  | 40% | 8140.5849
90% | 1.793% | 78.7576 |  |  |  |  | 15% | 4369.4129 | 9.6578 | 35% |  | 35% |  | 35% | 3042.494
85% | 5.393% | 236.8672 |  |  |  |  | 10% | 4378.6261 | 6.4385 | 30% |  | 30% |  | 30% | 1517.42
80% | 11.33% | 497.5104 |  |  |  |  | 5% | 4391.7028 | 3.2193 | 25% |  | 25% |  | 25% | 894.5698
75% | 18.3% | 803.6248 |  |  |  |  | 9.992e-14% | 4391.7028 | 6.4334e-14 | 20% |  | 20% |  | 20% | 452.0687
70% | 26.3% | 1155.2107 | [7 empty] | 15% |  | 15% |  | 15% | 184.1761
65% | 35.36% | 1553.1596 | [7 empty] | 10% |  | 10% |  | 10% | 74.1488
60% | 46.14% | 2026.2996 | [7 empty] | 5% |  | 5% |  | 5% | 63.1461
55% | 59.16% | 2598.4068 | [7 empty] | 9.992e-14% |  | 9.992e-14% |  | 9.992e-14% | 0
50% | 73.62% | 3233.5201 |  |  |  |  | MD Weighted LDC |  |  | Total E@R | 0 | Total E@R | 3339.858 | Total E@R | 169099.4242
45% | 85.96% | 3775.313 | [7 empty] | Total WE@R | 0 | Total WE@R | 0.8782 | Total WE@R | 0.0058193
40% | 92.73% | 4072.8088 |  |  |  |  | % of MD | Winter - MD - Hours | FY31
35% | 95.6% | 4198.821 |  |  |  |  | 100% | 0 | 67.0443 | E@R (N) |  | E@R (N) |  | E@R (N)
30% | 97.25% | 4271.3374 |  |  |  |  | 99% | 1.486 | 66.3739
25% | 98.4% | 4321.8611 |  |  |  |  | 98% | 3.2692 | 65.7034 | % of MD | FY31 | % of MD | FY31 | % of MD | FY31
20% | 99.11% | 4353.067 |  |  |  |  | 97% | 6.8356 | 65.033 | 100% |  | 100% |  | 100%
15% | 99.49% | 4369.4129 |  |  |  |  | 95% | 17.5347 | 63.6921 | 99% |  | 99% | 26.167 | 99% | 99.1293
10% | 99.7% | 4378.6261 |  |  |  |  | 90% | 78.7576 | 60.3399 | 98% |  | 98% | 30.2049 | 98% | 117.7596
5% | 99.99% | 4391.7028 |  |  |  |  | 85% | 236.8672 | 56.9877 | 97% |  | 97% | 58.0187 | 97% | 233.1281
9.992e-14% | 99.99% | 4391.7028 |  |  |  |  | 80% | 497.5104 | 53.6355 | 95% |  | 95% | 163.2964 | 95% | 688.6245
[7 empty] | 75% | 803.6248 | 50.2832 | 90% |  | 90% | 790.7554 | 90% | 3796.7998
[7 empty] | 70% | 1155.2107 | 46.931 | 85% |  | 85% | 1512.1274 | 85% | 9275.3098
[7 empty] | 65% | 1553.1596 | 43.5788 | 80% |  | 80% | 1619.0041 | 80% | 14416.5812
LDC | [6 empty] | 60% | 2026.2996 | 40.2266 | 75% |  | 75% | 875.2908 | 75% | 15905.5125
[7 empty] | 55% | 2598.4068 | 36.8744 | 70% |  | 70% | 73.4213 | 70% | 17089.584
% of MD | Winter - MD (P10) - Duration % | Winter - MD - Hours |  |  |  |  | 50% | 3233.5201 | 33.5222 | 65% |  | 65% |  | 65% | 18009.1448
100% | 0% | 0 |  |  |  |  | 45% | 3775.313 | 30.1699 | 60% |  | 60% |  | 60% | 19825.8502
99% | 0.03383% | 1.486 |  |  |  |  | 40% | 4072.8088 | 26.8177 | 55% |  | 55% |  | 55% | 22055.013
98% | 0.07443% | 3.2692 |  |  |  |  | 35% | 4198.821 | 23.4655 | 50% |  | 50% |  | 50% | 22354.8915
97% | 0.1556% | 6.8356 |  |  |  |  | 30% | 4271.3374 | 20.1133 | 45% |  | 45% |  | 45% | 17253.9692
95% | 0.3992% | 17.5347 |  |  |  |  | 25% | 4321.8611 | 16.7611 | 40% |  | 40% |  | 40% | 8476.7963
90% | 1.793% | 78.7576 |  |  |  |  | 20% | 4353.067 | 13.4089 | 35% |  | 35% |  | 35% | 3168.1509
85% | 5.393% | 236.8672 |  |  |  |  | 15% | 4369.4129 | 10.0566 | 30% |  | 30% |  | 30% | 1580.0904
80% | 11.33% | 497.5104 |  |  |  |  | 10% | 4378.6261 | 6.7044 | 25% |  | 25% |  | 25% | 931.5161
75% | 18.3% | 803.6248 |  |  |  |  | 5% | 4391.7028 | 3.3522 | 20% |  | 20% |  | 20% | 470.7394
70% | 26.3% | 1155.2107 |  |  |  |  | 9.992e-14% | 4391.7028 | 6.6991e-14 | 15% |  | 15% |  | 15% | 191.7827
65% | 35.36% | 1553.1596 | [7 empty] | 10% |  | 10% |  | 10% | 77.2112
60% | 46.14% | 2026.2996 | [7 empty] | 5% |  | 5% |  | 5% | 65.7541
55% | 59.16% | 2598.4068 | [7 empty] | 9.992e-14% |  | 9.992e-14% | 0 | 9.992e-14% | 0
50% | 73.62% | 3233.5201 | [7 empty] | Total E@R | 0 | Total E@R | 5148.2859 | Total E@R | 176083.3386
45% | 85.96% | 3775.313 | [7 empty] | Total WE@R | 0 | Total WE@R | 0.58017 | Total WE@R | 0.002597
40% | 92.73% | 4072.8088
35% | 95.6% | 4198.821
30% | 97.25% | 4271.3374
25% | 98.4% | 4321.8611
20% | 99.11% | 4353.067
15% | 99.49% | 4369.4129
10% | 99.7% | 4378.6261
5% | 99.99% | 4391.7028
9.992e-14% | 99.99% | 4391.7028
Ratings (MVA) |  |  |  | Option Capacity
SCR (N) | 91.9 |  |  | Year | 2031
SCR (N-1) | 45 |  |  | SCR (N) | 91.9
SCR (N-2) | 0 |  |  | SCR (N-1) | 45
WCR (N) | 95.7 |  |  | SCR (N-2) | 0
WCR (N-1) | 49.1 |  |  | WCR (N) | 95.7
WCR (N-2) | 0 |  |  | WCR (N-1) | 49.1
|  |  |  | WCR (N-2) | 0
Planned Works
Year | 2031
Capacity (N) | 0
Capacity (N-1) | 0
Capacity (N-2) | 0
Power Factor
Value | 1
End of Sheet

## QA
Overall Status
Good
Number | Check Name | Status | Info
1 | Forecast | Good | Confirms POE10 forecast is higher than POE50
2 | Option Maximum Demand | Good | Confirms whether transfers, embedded generation, and demand management contribute to demand reduction when present
3 | EUE Base Case | Good | Confirms Do Nothing/Base Case EUE for FY31 is the same as the example / checks model in Modelling Steps Example Sheet
4 | Feeder Consumption | Good | Confirms if aggregated feeder energy consumption by customer category matches with total feeder energy consumption (excluding uncategorised consumption)

## Output for AusNet's NPV model
Involuntary load shedding (NER 5.17.1(c)(4)(ii))
Base Case
Cost
Option 1 - Do Nothing / Base Case | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Cost of EUE ($M) | 0.00013013 | 0.0045354 | 0.015907 | 0.02253 | 0.030537 | 0.04405 | 0.073277 | 0.10689 | 0.16079 | 0.25784 | 0.26283 | 0.26751 | 0.36579 | 0.54793 | 0.51363 | 0.51363 | 0.51363 | 0.51363 | 0.51363 | 0.51363 | 0.51363 | 0.51363 | 0.51363 | 0.51363 | 0.51363 | 0.51363 | 0.51363 | 0.51363 | 0.51363 | 0.51363
Total EUE (MWh) | 0.0033707 | 0.11748 | 0.41204 | 0.58358 | 0.79099 | 1.141 | 1.8981 | 2.7688 | 4.165 | 6.6787 | 6.808 | 6.9292 | 9.4749 | 14.1927 | 13.3044 | 13.3044 | 13.3044 | 13.3044 | 13.3044 | 13.3044 | 13.3044 | 13.3044 | 13.3044 | 13.3044 | 13.3044 | 13.3044 | 13.3044 | 13.3044 | 13.3044 | 13.3044
Residual Values
Option 2 - 1B New PHS ZSS + Three new feeders | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Cost of Avoided EUE ($M) | 0.00013013 | 0.0045354 | 0.015907 | 0.00024453 | 0.00034686 | 0.00051617 | 0.00082746 | 0.001234 | 0.0018393 | 0.0072018 | 0.0036935 | 0.0045711 | 0.0062434 | 0.013102 | 0.010328 | 0.010328 | 0.010328 | 0.010328 | 0.010328 | 0.010328 | 0.010328 | 0.010328 | 0.010328 | 0.010328 | 0.010328 | 0.010328 | 0.010328 | 0.010328 | 0.010328 | 0.010328
Total EUE (MWh) | 0.0033707 | 0.11748 | 0.41204 | 0.0063341 | 0.0089846 | 0.01337 | 0.021433 | 0.031963 | 0.047641 | 0.18655 | 0.095671 | 0.1184 | 0.16172 | 0.33938 | 0.26752 | 0.26752 | 0.26752 | 0.26752 | 0.26752 | 0.26752 | 0.26752 | 0.26752 | 0.26752 | 0.26752 | 0.26752 | 0.26752 | 0.26752 | 0.26752 | 0.26752 | 0.26752
Option 3 - 2B PHM 3rd Tx + Switchroom + Two new feeders + OFR12 New Feeder | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Cost of Avoided EUE ($M) | 0.00013013 | 0.0045354 | 0.015907 | 3.1666e-06 | 5.3194e-06 | 9.1408e-06 | 1.7313e-05 | 2.8909e-05 | 4.9015e-05 | 8.6489e-05 | 0.00010449 | 0.00012388 | 0.00018723 | 0.00030398 | 0.00032875 | 0.00032875 | 0.00032875 | 0.00032875 | 0.00032875 | 0.00032875 | 0.00032875 | 0.00032875 | 0.00032875 | 0.00032875 | 0.00032875 | 0.00032875 | 0.00032875 | 0.00032875 | 0.00032875 | 0.00032875
Total EUE (MWh) | 0.0033707 | 0.11748 | 0.41204 | 8.2023e-05 | 0.00013779 | 0.00023677 | 0.00044845 | 0.00074881 | 0.0012696 | 0.0022403 | 0.0027066 | 0.0032087 | 0.0048497 | 0.0078739 | 0.0085154 | 0.0085154 | 0.0085154 | 0.0085154 | 0.0085154 | 0.0085154 | 0.0085154 | 0.0085154 | 0.0085154 | 0.0085154 | 0.0085154 | 0.0085154 | 0.0085154 | 0.0085154 | 0.0085154 | 0.0085154
Option 4 - 3B OFR 3rd Tx + Switchroom + Two new feeders + OFR12 New Feeder | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Cost of Avoided EUE ($M) | 0.00013013 | 0.0045354 | 0.015907 | 0.0089534 | 0.012376 | 0.018712 | 0.034724 | 0.053964 | 0.087903 | 0.15807 | 0.15169 | 0.14809 | 0.21353 | 0.3459 | 0.30738 | 0.30738 | 0.30738 | 0.30738 | 0.30738 | 0.30738 | 0.30738 | 0.30738 | 0.30738 | 0.30738 | 0.30738 | 0.30738 | 0.30738 | 0.30738 | 0.30738 | 0.30738
Total EUE (MWh) | 0.0033707 | 0.11748 | 0.41204 | 0.23192 | 0.32057 | 0.48468 | 0.89944 | 1.3978 | 2.2769 | 4.0943 | 3.9291 | 3.8359 | 5.5309 | 8.9598 | 7.962 | 7.962 | 7.962 | 7.962 | 7.962 | 7.962 | 7.962 | 7.962 | 7.962 | 7.962 | 7.962 | 7.962 | 7.962 | 7.962 | 7.962 | 7.962
Option 5 - 4B LLG 2nd Tx + Switchroom + Two new feeders + OFR12 New Feeder | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Cost of Avoided EUE ($M) | 0.00013013 | 0.0045354 | 0.015907 | 0.00014933 | 0.00022476 | 0.00034878 | 0.00057544 | 0.00086882 | 0.0012729 | 0.0035813 | 0.0025385 | 0.0033876 | 0.0043851 | 0.0071215 | 0.0070071 | 0.0070071 | 0.0070071 | 0.0070071 | 0.0070071 | 0.0070071 | 0.0070071 | 0.0070071 | 0.0070071 | 0.0070071 | 0.0070071 | 0.0070071 | 0.0070071 | 0.0070071 | 0.0070071 | 0.0070071
Total EUE (MWh) | 0.0033707 | 0.11748 | 0.41204 | 0.0038679 | 0.005822 | 0.0090343 | 0.014905 | 0.022505 | 0.032972 | 0.092766 | 0.065753 | 0.087747 | 0.11358 | 0.18446 | 0.1815 | 0.1815 | 0.1815 | 0.1815 | 0.1815 | 0.1815 | 0.1815 | 0.1815 | 0.1815 | 0.1815 | 0.1815 | 0.1815 | 0.1815 | 0.1815 | 0.1815 | 0.1815
Option 6 - | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Cost of Avoided EUE ($M) | 0.00013013 | 0.0045354 | 0.015907 | 0.02253 | 0.030537 | 0.04405 | 0.073277 | 0.10689 | 0.16079 | 0.25784 | 0.26283 | 0.26751 | 0.36579 | 0.54793 | 0.51363 | 0.51363 | 0.51363 | 0.51363 | 0.51363 | 0.51363 | 0.51363 | 0.51363 | 0.51363 | 0.51363 | 0.51363 | 0.51363 | 0.51363 | 0.51363 | 0.51363 | 0.51363
Total EUE (MWh) | 0.0033707 | 0.11748 | 0.41204 | 0.58358 | 0.79099 | 1.141 | 1.8981 | 2.7688 | 4.165 | 6.6787 | 6.808 | 6.9292 | 9.4749 | 14.1927 | 13.3044 | 13.3044 | 13.3044 | 13.3044 | 13.3044 | 13.3044 | 13.3044 | 13.3044 | 13.3044 | 13.3044 | 13.3044 | 13.3044 | 13.3044 | 13.3044 | 13.3044 | 13.3044
Option 7 - | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Cost of Avoided EUE ($M) | 0.00013013 | 0.0045354 | 0.015907 | 0.02253 | 0.030537 | 0.04405 | 0.073277 | 0.10689 | 0.16079 | 0.25784 | 0.26283 | 0.26751 | 0.36579 | 0.54793 | 0.51363 | 0.51363 | 0.51363 | 0.51363 | 0.51363 | 0.51363 | 0.51363 | 0.51363 | 0.51363 | 0.51363 | 0.51363 | 0.51363 | 0.51363 | 0.51363 | 0.51363 | 0.51363
Total EUE (MWh) | 0.0033707 | 0.11748 | 0.41204 | 0.58358 | 0.79099 | 1.141 | 1.8981 | 2.7688 | 4.165 | 6.6787 | 6.808 | 6.9292 | 9.4749 | 14.1927 | 13.3044 | 13.3044 | 13.3044 | 13.3044 | 13.3044 | 13.3044 | 13.3044 | 13.3044 | 13.3044 | 13.3044 | 13.3044 | 13.3044 | 13.3044 | 13.3044 | 13.3044 | 13.3044
Option 8 - | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Cost of Avoided EUE ($M) | 0.00013013 | 0.0045354 | 0.015907 | 0.02253 | 0.030537 | 0.04405 | 0.073277 | 0.10689 | 0.16079 | 0.25784 | 0.26283 | 0.26751 | 0.36579 | 0.54793 | 0.51363 | 0.51363 | 0.51363 | 0.51363 | 0.51363 | 0.51363 | 0.51363 | 0.51363 | 0.51363 | 0.51363 | 0.51363 | 0.51363 | 0.51363 | 0.51363 | 0.51363 | 0.51363
Total EUE (MWh) | 0.0033707 | 0.11748 | 0.41204 | 0.58358 | 0.79099 | 1.141 | 1.8981 | 2.7688 | 4.165 | 6.6787 | 6.808 | 6.9292 | 9.4749 | 14.1927 | 13.3044 | 13.3044 | 13.3044 | 13.3044 | 13.3044 | 13.3044 | 13.3044 | 13.3044 | 13.3044 | 13.3044 | 13.3044 | 13.3044 | 13.3044 | 13.3044 | 13.3044 | 13.3044

## Key Model Assumption & Inputs
Select ZSS & Region | PHM | Central | MTTR
Probability Weighting for 10% POE MDs | 30% |  |  | Central | North | East | For Analysis
Probability Weighting for 50% POE MDs | 70% |  | N-1 MTTR (years) | 0.3858 | 0.1418 | 0.3858 | 0.3858
First year of analysis | FY25 |  | N-2 MTTR (years) | 0.2344 | 0.049 | 0.2344 | 0.2344
Select Sensitivity Variant | Forecast Sensitivity
Low | 90% |  | PV Factor's |  |  | PoF Sensitvity
Options | Name |  | Summer | 1.33 |  | Varaint
Option 1 - Do Nothing / Base Case | Do Nothing / Base Case |  | Winter | 1.13 |  | Base | 100%
Option 2 - 1B New PHS ZSS + Three new feeders | 1B New PHS ZSS + Three new feeders
Option 3 - 2B PHM 3rd Tx + Switchroom + Two new feeders + OFR12 New Feeder | 2B PHM 3rd Tx + Switchroom + Two new feeders + OFR12 New Feeder |  | Demand Response
Option 4 - 3B OFR 3rd Tx + Switchroom + Two new feeders + OFR12 New Feeder | 3B OFR 3rd Tx + Switchroom + Two new feeders + OFR12 New Feeder |  | Average Rate % | 20%
Option 5 - 4B LLG 2nd Tx + Switchroom + Two new feeders + OFR12 New Feeder | 4B LLG 2nd Tx + Switchroom + Two new feeders + OFR12 New Feeder
Option 6 -
Option 7 -
Option 8 -
Added Capacity (MVA) | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39
Added Capacity (MVA) Option 1 N | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 1 N-1 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 1 N-2 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 2 N | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 2 N-1 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 2 N-2 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 3 N |  |  |  | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45
Added Capacity (MVA) Option 3 N-1 |  |  |  | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45
Added Capacity (MVA) Option 3 N-2 |  |  |  | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45
Added Capacity (MVA) Option 4 N | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 4 N-1 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 4 N-2 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 5 N | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 5 N-1 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 5 N-2 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 6 N | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 6 N-1 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 6 N-2 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 7 N | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 7 N-1 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 7 N-2 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 8 N | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 8 N-1 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 8 N-2 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Embedded Generation (MVA) | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39
Avaliable Embedded Generation (MVA) Option 1 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Embedded Generation (MVA) Option 2 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Embedded Generation (MVA) Option 3 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Embedded Generation (MVA) Option 4 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Embedded Generation (MVA) Option 5 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Embedded Generation (MVA) Option 6 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Embedded Generation (MVA) Option 7 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Embedded Generation (MVA) Option 8 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Demand Management (MVA) | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39
Avaliable Demand Management (MVA) Option 1 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Demand Management (MVA) Option 2 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Demand Management (MVA) Option 3 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Demand Management (MVA) Option 4 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Demand Management (MVA) Option 5 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Demand Management (MVA) Option 6 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Demand Management (MVA) Option 7 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Demand Management (MVA) Option 8 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Transfers (MVA) | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39
Planned Transfers (MVA) Option 1 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Transfers (MVA) Option 2 |  |  |  | 19.3333 | 19.3333 | 19.3333 | 19.3333 | 19.3333 | 19.3333 | 19.3333 | 19.3333 | 19.3333 | 19.3333 | 19.3333 | 19.3333
Added Transfers (MVA) Option 3 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Transfers (MVA) Option 4 |  |  |  | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
Added Transfers (MVA) Option 5 |  |  |  | 21.75 | 21.75 | 21.75 | 21.75 | 21.75 | 21.75 | 21.75 | 21.75 | 21.75 | 21.75 | 21.75 | 21.75
Added Transfers (MVA) Option 6 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Transfers (MVA) Option 7 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Transfers (MVA) Option 8 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Block Loads Not in Forecast (MVA) | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39
Block Loads (MVA) | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Base | FY25: 100%
High | FY25: 110%
Low | FY25: 90%

## Tx PoF
Transformer Failure Rates for individual Transformers
[5 empty] | 10 | 8 | 10 | 6 | 8 | 6 | 6 | 10 | 6
Zone | arm_asset_id | floc | user_status | Age | Major Winding insulation | Accelerated cellulose Aging | Winding insulating liquid | Hot metal fault covered by paper | Chemical contamination, degradation | Physical & chemical contamination, degradation | Physical contamination | Short Circuit Concern | OLTC | WMA Health Score | WMA CS | WMA effective age | WMA Beta | WMA Eta | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WGI | 30192717 | DS-WGI-TRNFMR-9000004493 |  | 59 | 5 | 3 | 1 | 5 | 2 | 1 | 5 | 5 | 5 | 351.4286 | 4 | 60 | 3.5 | 82 | 1.976% | 1.976% | 2.058% | 2.142% | 2.227% | 2.315% | 2.405% | 2.496% | 2.59% | 2.686% | 2.783% | 2.883% | 2.985% | 3.089% | 3.195% | 3.303% | 3.413% | 3.525% | 3.639% | 3.755% | 3.873% | 3.994% | 4.116% | 4.241% | 4.368% | 4.497% | 4.628% | 4.761% | 4.897% | 5.034%
WGI | 30111322 | DS-WGI-TRNFMR-9000003147 |  | 59 | 5 | 5 | 1 | 3 | 2 | 1 | 4 | 5 | 5 | 348.5714 | 3 | 44 | 3.5 | 82 | 0.9218% | 0.9218% | 0.9742% | 1.028% | 1.084% | 1.142% | 1.201% | 1.262% | 1.325% | 1.39% | 1.457% | 1.525% | 1.596% | 1.668% | 1.742% | 1.818% | 1.896% | 1.976% | 2.058% | 2.142% | 2.227% | 2.315% | 2.405% | 2.496% | 2.59% | 2.686% | 2.783% | 2.883% | 2.985% | 3.089%
EPG | 30026486 | DS-EPG-TRNFMR-9000010175 |  | 45 | 5 | 3 | 2 | 1 | 2 | 1 | 4 | 5 | 5 | 322.8571 | 3 | 44 | 3.5 | 84.05 | 0.8458% | 0.8458% | 0.8939% | 0.9436% | 0.9949% | 1.048% | 1.102% | 1.159% | 1.216% | 1.276% | 1.337% | 1.4% | 1.465% | 1.531% | 1.599% | 1.669% | 1.741% | 1.814% | 1.889% | 1.966% | 2.045% | 2.125% | 2.208% | 2.292% | 2.378% | 2.466% | 2.556% | 2.648% | 2.741% | 2.837%
EPG | 30058367 | DS-EPG-TRNFMR-9000010174 |  | 45 | 5 | 3 | 2 | 1 | 2 | 1 | 4 | 5 | 5 | 322.8571 | 3 | 44 | 3.5 | 84.05 | 0.8458% | 0.8458% | 0.8939% | 0.9436% | 0.9949% | 1.048% | 1.102% | 1.159% | 1.216% | 1.276% | 1.337% | 1.4% | 1.465% | 1.531% | 1.599% | 1.669% | 1.741% | 1.814% | 1.889% | 1.966% | 2.045% | 2.125% | 2.208% | 2.292% | 2.378% | 2.466% | 2.556% | 2.648% | 2.741% | 2.837%
WGI | 30475971 | DS-WGI-TRNFMR-9000007146 |  | 49 | 5 | 5 | 1 | 1 | 1 | 1 | 2 | 5 | 1 | 268.5714 | 3 | 44 | 3.5 | 82 | 0.9218% | 0.9218% | 0.9742% | 1.028% | 1.084% | 1.142% | 1.201% | 1.262% | 1.325% | 1.39% | 1.457% | 1.525% | 1.596% | 1.668% | 1.742% | 1.818% | 1.896% | 1.976% | 2.058% | 2.142% | 2.227% | 2.315% | 2.405% | 2.496% | 2.59% | 2.686% | 2.783% | 2.883% | 2.985% | 3.089%
EPG | 30209984 | DS-EPG-TRNFMR-9000007095 |  | 24 | 3 | 3 | 1 | 3 | 2 | 1 | 4 | 3 | 3 | 251.4286 | 3 | 44 | 3.5 | 84.05 | 0.8458% | 0.8458% | 0.8939% | 0.9436% | 0.9949% | 1.048% | 1.102% | 1.159% | 1.216% | 1.276% | 1.337% | 1.4% | 1.465% | 1.531% | 1.599% | 1.669% | 1.741% | 1.814% | 1.889% | 1.966% | 2.045% | 2.125% | 2.208% | 2.292% | 2.378% | 2.466% | 2.556% | 2.648% | 2.741% | 2.837%
CLN | 30338702 | DS-CLN-TRNFMR-9000006730 |  | 21 | 3 | 2 | 2 | 3 | 1 | 1 | 3 | 3 | 2 | 225.7143 | 2 | 24 | 3.5 | 84.05 | 0.1909% | 0.1909% | 0.211% | 0.2322% | 0.2547% | 0.2785% | 0.3035% | 0.3298% | 0.3575% | 0.3865% | 0.4168% | 0.4486% | 0.4817% | 0.5162% | 0.5522% | 0.5897% | 0.6286% | 0.669% | 0.7109% | 0.7543% | 0.7993% | 0.8458% | 0.8939% | 0.9436% | 0.9949% | 1.048% | 1.102% | 1.159% | 1.216% | 1.276%
CRE | 30165029 | DS-CRE-TRNFMR-9000525811 |  | 13 | 3 | 2 | 1 | 3 | 2 | 1 | 4 | 2 | 2 | 217.1429 | 2 | 24 | 3.5 | 84.05 | 0.1909% | 0.1909% | 0.211% | 0.2322% | 0.2547% | 0.2785% | 0.3035% | 0.3298% | 0.3575% | 0.3865% | 0.4168% | 0.4486% | 0.4817% | 0.5162% | 0.5522% | 0.5897% | 0.6286% | 0.669% | 0.7109% | 0.7543% | 0.7993% | 0.8458% | 0.8939% | 0.9436% | 0.9949% | 1.048% | 1.102% | 1.159% | 1.216% | 1.276%
LLG | 30359074 | DS-LLG-TRNFMR-9000007796 |  | 20 | 1 | 2 | 1 | 2 | 1 | 1 | 5 | 3 | 2 | 191.4286 | 2 | 24 | 3.5 | 84.05 | 0.1909% | 0.1909% | 0.211% | 0.2322% | 0.2547% | 0.2785% | 0.3035% | 0.3298% | 0.3575% | 0.3865% | 0.4168% | 0.4486% | 0.4817% | 0.5162% | 0.5522% | 0.5897% | 0.6286% | 0.669% | 0.7109% | 0.7543% | 0.7993% | 0.8458% | 0.8939% | 0.9436% | 0.9949% | 1.048% | 1.102% | 1.159% | 1.216% | 1.276%
CRE | 30380287 | DS-CRE-TRNFMR-9000525810 |  | 13 | 2 | 2 | 1 | 1 | 2 | 1 | 3 | 2 | 2 | 177.1429 | 2 | 24 | 3.5 | 84.05 | 0.1909% | 0.1909% | 0.211% | 0.2322% | 0.2547% | 0.2785% | 0.3035% | 0.3298% | 0.3575% | 0.3865% | 0.4168% | 0.4486% | 0.4817% | 0.5162% | 0.5522% | 0.5897% | 0.6286% | 0.669% | 0.7109% | 0.7543% | 0.7993% | 0.8458% | 0.8939% | 0.9436% | 0.9949% | 1.048% | 1.102% | 1.159% | 1.216% | 1.276%
CLN | 30000439 | DS-CLN-TRNFMR-9000001306 |  | 19 | 2 | 2 | 1 | 1 | 1 | 1 | 3 | 2 | 2 | 165.7143 | 2 | 24 | 3.5 | 84.05 | 0.1909% | 0.1909% | 0.211% | 0.2322% | 0.2547% | 0.2785% | 0.3035% | 0.3298% | 0.3575% | 0.3865% | 0.4168% | 0.4486% | 0.4817% | 0.5162% | 0.5522% | 0.5897% | 0.6286% | 0.669% | 0.7109% | 0.7543% | 0.7993% | 0.8458% | 0.8939% | 0.9436% | 0.9949% | 1.048% | 1.102% | 1.159% | 1.216% | 1.276%
OFR | 30035965 | DS-OFR-TRNFMR-9000014181 |  | 16 | 2 | 2 | 1 | 1 | 1 | 1 | 3 | 2 | 2 | 165.7143 | 2 | 24 | 3.5 | 84.05 | 0.1909% | 0.1909% | 0.211% | 0.2322% | 0.2547% | 0.2785% | 0.3035% | 0.3298% | 0.3575% | 0.3865% | 0.4168% | 0.4486% | 0.4817% | 0.5162% | 0.5522% | 0.5897% | 0.6286% | 0.669% | 0.7109% | 0.7543% | 0.7993% | 0.8458% | 0.8939% | 0.9436% | 0.9949% | 1.048% | 1.102% | 1.159% | 1.216% | 1.276%
KLO | 30002764 | DS-KLO-TRNFMR-9000412348 |  | 15 | 1 | 2 | 1 | 1 | 1 | 1 | 4 | 2 | 2 | 160 | 2 | 24 | 3.5 | 84.05 | 0.1909% | 0.1909% | 0.211% | 0.2322% | 0.2547% | 0.2785% | 0.3035% | 0.3298% | 0.3575% | 0.3865% | 0.4168% | 0.4486% | 0.4817% | 0.5162% | 0.5522% | 0.5897% | 0.6286% | 0.669% | 0.7109% | 0.7543% | 0.7993% | 0.8458% | 0.8939% | 0.9436% | 0.9949% | 1.048% | 1.102% | 1.159% | 1.216% | 1.276%
OFR | 30221642 | DS-OFR-TRNFMR-9000016122 |  | 16 | 1 | 2 | 1 | 1 | 1 | 1 | 3 | 2 | 2 | 151.4286 | 2 | 24 | 3.5 | 84.05 | 0.1909% | 0.1909% | 0.211% | 0.2322% | 0.2547% | 0.2785% | 0.3035% | 0.3298% | 0.3575% | 0.3865% | 0.4168% | 0.4486% | 0.4817% | 0.5162% | 0.5522% | 0.5897% | 0.6286% | 0.669% | 0.7109% | 0.7543% | 0.7993% | 0.8458% | 0.8939% | 0.9436% | 0.9949% | 1.048% | 1.102% | 1.159% | 1.216% | 1.276%
KLO | 30208816 | DS-KLO-TRNFMR-9000412347 |  | 15 | 1 | 2 | 1 | 1 | 1 | 1 | 3 | 2 | 2 | 151.4286 | 2 | 24 | 3.5 | 84.05 | 0.1909% | 0.1909% | 0.211% | 0.2322% | 0.2547% | 0.2785% | 0.3035% | 0.3298% | 0.3575% | 0.3865% | 0.4168% | 0.4486% | 0.4817% | 0.5162% | 0.5522% | 0.5897% | 0.6286% | 0.669% | 0.7109% | 0.7543% | 0.7993% | 0.8458% | 0.8939% | 0.9436% | 0.9949% | 1.048% | 1.102% | 1.159% | 1.216% | 1.276%
PHM | 32944656 | DS-PHM-TRNFMR-9000004393 |  | 8 | 2 | 2 | 1 | 1 | 1 | 1 | 3 | 1 | 1 | 142.8571 | 1 | 8 | 3.5 | 84.05 | 0.01357% | 0.01357% | 0.01791% | 0.023% | 0.02887% | 0.03555% | 0.04308% | 0.0515% | 0.06084% | 0.07112% | 0.08238% | 0.09465% | 0.1079% | 0.1223% | 0.1378% | 0.1543% | 0.172% | 0.1909% | 0.211% | 0.2322% | 0.2547% | 0.2785% | 0.3035% | 0.3298% | 0.3575% | 0.3865% | 0.4168% | 0.4486% | 0.4817% | 0.5162%
PHM | 32944654 | DS-PHM-TRNFMR-9000007050 |  | 8 | 2 | 2 | 1 | 1 | 1 | 1 | 3 | 1 | 1 | 142.8571 | 1 | 8 | 3.5 | 84.05 | 0.01357% | 0.01357% | 0.01791% | 0.023% | 0.02887% | 0.03555% | 0.04308% | 0.0515% | 0.06084% | 0.07112% | 0.08238% | 0.09465% | 0.1079% | 0.1223% | 0.1378% | 0.1543% | 0.172% | 0.1909% | 0.211% | 0.2322% | 0.2547% | 0.2785% | 0.3035% | 0.3298% | 0.3575% | 0.3865% | 0.4168% | 0.4486% | 0.4817% | 0.5162%

## AER VCR Rates(2024)
Category | Rate | Notes
Dec 24 AER VCR ($/kWh) - Res | 49.23 | Vic Av Res
Dec 24 AER VCR ($/kWh) - Com | 34.39 | Vic Av Com
Dec 24 AER VCR ($/kWh) - Ind | 33.49 | Vic Av Ind
Dec 24 AER VCR ($/kWh) - Agr | 22.25 | Vic Av Agr

## Customer No. and Vol per Feeder
CUSTOMER_CLASS | Feeder | VOL | CUST_NO | ZSS | Customer mix received from AusNet Financial Planning & Strategy on 25/7/2025
COMMERCIAL | bra11 | 9860526.7854 | 168 | bra
COMMERCIAL | bge13 | 654988.62 | 45 | bge
COMMERCIAL | phi11 | 1878610.03 | 37 | phi
NCONUML | moe11 | 47447.48 | 18 | moe
NCONUML | drn13 | 27414.73 | 17 | drn
COMMERCIAL | smg34 | 5224461.8 | 1 | smg
FARM | wgl13 | 901266.5312 | 97 | wgl
FARM | msd2 | 2808295.5668 | 471 | msd
NCONUML | elm34 | 86758.8 | 34 | elm
| rwt36 | 703.54 | 2 | rwt
COMMERCIAL | lga41 | 1099100.22 | 2 | lga
| bdl33 | 4298.82 | 8 | bdl
NCONUML | smr14 | 27225.34 | 18 | smr
COMMERCIAL | cln24 | 4484028.8333 | 290 | cln
RESIDENTL | ofr14 | 13024383.6958 | 3554 | ofr
NCONUML | bdl43 | 100361.9983 | 38 | bdl
| ofr22 | 16469.09 | 22 | ofr
NCONUML | rwn33 | 8721.79 | 7 | rwn
LIGHTING | hpk12 | 342838 | 1 | hpk
COMMERCIAL | bra23 | 6262297.01 | 84 | bra
FARM | tt1 | 1865.76 | 1 | tt
LIGHTING | mfa14 | 787800.53 | 1 | mfa
RESIDENTL | brt22 | 9968534.1043 | 1376 | brt
RESIDENTL | mwl25 | 4092575.372 | 493 | mwl
NCONUML | wgi22 | 83961.44 | 23 | wgi
INDUSTRIAL | ldl22 | 4379901.5885 | 45 | ldl
RESIDENTL | phm22 | 3628742.5283 | 796 | phm
FARM | mfa23 | 2691321.6324 | 201 | mfa
NCONUML | rwn32 | 60415.37 | 23 | rwn
FARM | cre22 | 55644.16 | 17 | cre
RESIDENTL | elm24 | 17367685.5307 | 2999 | elm
COMMERCIAL | tt9 | 7181168.3052 | 213 | tt
COMMERCIAL | kms12 | 15257134.8455 | 395 | kms
NCONUML | cyn31 | 24759.23 | 14 | cyn
| llg12 | 26420.7189 | 15 | llg
LIGHTING | ruba22 | 247422.69 | 1 | ruba
RESIDENTL | wt12 | 10803758.701 | 2579 | wt
COMMERCIAL | bwn14 | 6975240.1 | 156 | bwn
NCONUML | bge12 | 37366.03 | 11 | bge
NCONUML | rwn24 | 30489.76 | 21 | rwn
FARM | sfs1 | 113380.09 | 9 | sfs
| bwr13 | 80076.52 | 46 | bwr
FARM | wt13 | 37228.86 | 3 | wt
FARM | cre23 | 226478.55 | 9 | cre
COMMERCIAL | rwn22 | 1886562.0146 | 72 | rwn
| tgn23 | 13898.1302 | 15 | tgn
FARM | ldl22 | 7887.95 | 1 | ldl
RESIDENTL | fgy21 | 7153989.4877 | 1047 | fgy
FARM | mjg11 | 735019.886 | 74 | mjg
| ldl14 | 17432.2687 | 11 | ldl
INDUSTRIAL | ldl24 | 64751.4 | 12 | ldl
| sle13 | 253.3245 | 2 | sle
FARM | moe21 | 6301170.9744 | 504 | moe
FARM | bge23 | 671977.1074 | 66 | bge
RESIDENTL | elm32 | 19949095.4752 | 2463 | elm
COMMERCIAL | ftr12 | 1975462.7263 | 113 | ftr
RESIDENTL | lyd12 | 6657897.88 | 1592 | lyd
RESIDENTL | epg31 | 11862355.3417 | 3027 | epg
NCONUML | ofr11 | 57102.89 | 18 | ofr
FARM | moe11 | 65350.2807 | 7 | moe
FARM | nla32 | 1181128.1259 | 84 | nla
FARM | smr24 | 4141783.4574 | 392 | smr
RESIDENTL | fgy13 | 7970231.1446 | 1518 | fgy
FARM | bdl41 | 1305847.5951 | 258 | bdl
NCONUML | elm23 | 62172.37 | 40 | elm
| elm22 | 20617.5429 | 26 | elm
NCONUML | cre21 | 58240.1 | 18 | cre
FARM | phm32 | 50851.13 | 8 | phm
INDUSTRIAL | lga21 | 208132.02 | 16 | lga
INDUSTRIAL | nrn13 | 39703.59 | 6 | nrn
RESIDENTL | hpk22 | 18949862.0449 | 4569 | hpk
NCONUML | cyn13 | 17637.49 | 6 | cyn
COMMERCIAL | cre31 | 14851829.6913 | 363 | cre
COMMERCIAL | epg32 | 5001490.9226 | 156 | epg
| phm32 | 41386.12 | 47 | phm
NCONUML | wo33 | 6875.31 | 2 | wo
FARM | wgl21 | 5056187.7677 | 366 | wgl
INDUSTRIAL | cre22 | 240829.25 | 4 | cre
RESIDENTL | wgi34 | 3671110.7601 | 570 | wgi
INDUSTRIAL | ldl12 | 10352583.7 | 7 | ldl
INDUSTRIAL | wyk12 | 149433.7 | 6 | wyk
INDUSTRIAL | cyn14 | 23200.151 | 3 | cyn
| wo11 | 4136.2425 | 3 | wo
| msd4 | 20521.76 | 37 | msd
FARM | mby12 | 52034.88 | 19 | mby
COMMERCIAL | rwt22 | 7145877.6761 | 143 | rwt
COMMERCIAL | wo12 | 23719023.8 | 1 | wo
RESIDENTL | wn2 | 17414453.5902 | 3500 | wn
COMMERCIAL | wots25 | 3483725.2811 | 72 | wots
RESIDENTL | bwr33 | 46024.67 | 2 | bwr
RESIDENTL | wn3 | 12349888.6736 | 2099 | wn
RESIDENTL | bn24 | 2992797.8263 | 559 | bn
| bra21 | 41455.7142 | 65 | bra
INDUSTRIAL | hpk14 | 16381.88 | 4 | hpk
RESIDENTL | epg32 | 14811809.1158 | 3829 | epg
COMMERCIAL | cln14 | 10141314.5039 | 129 | cln
FARM | smg31 | 14995.46 | 5 | smg
INDUSTRIAL | drn22 | 2117102.6666 | 12 | drn
NCONUML | drn12 | 43785.8374 | 16 | drn
INDUSTRIAL | fgy34 | 128392.6893 | 5 | fgy
NCONUML | fgy31 | 6707.46 | 4 | fgy
| wt8 | 7059.0655 | 13 | wt
| bwn12 | 6521.57 | 6 | bwn
COMMERCIAL | myt12 | 10774273.2986 | 307 | myt
COMMERCIAL | ldl21 | 5339830.9491 | 117 | ldl
| cln21 | 32425.72 | 66 | cln
INDUSTRIAL | fgy14 | 162921.94 | 7 | fgy
| tgn12 | 22490.11 | 3 | tgn
COMMERCIAL | epg12 | 8214339.5389 | 163 | epg
NCONUML | moe23 | 69334.91 | 17 | moe
FARM | cyn14 | 7715.15 | 1 | cyn
RESIDENTL | lyd14 | 10580841.4317 | 1203 | lyd
COMMERCIAL | smg23 | 21963007.1063 | 434 | smg
INDUSTRIAL | bra33 | 2076536.62 | 34 | bra
INDUSTRIAL | rwt14 | 2271244.55 | 44 | rwt
COMMERCIAL | lga14 | 2174194.9787 | 115 | lga
INDUSTRIAL | myt22 | 3176.32 | 3 | myt
FARM | cyn21 | 10230.57 | 2 | cyn
| klo24 | 65411.35 | 119 | klo
COMMERCIAL | brt21 | 6571769.7252 | 216 | brt
FARM | kms11 | 665243.0597 | 75 | kms
| elm34 | 25999.6869 | 33 | elm
INDUSTRIAL | mwl11 | 366139.79 | 15 | mwl
INDUSTRIAL | lyd14 | 80895.88 | 12 | lyd
LIGHTING | cpk11 | 1086.88 | 1 | cpk
NCONUML | fgy23 | 34402.31 | 12 | fgy
| bra32 | 15753.982 | 22 | bra
RESIDENTL | epg12 | 26391788.5687 | 6905 | epg
COMMERCIAL | cyn24 | 15647575.1097 | 304 | cyn
INDUSTRIAL | phm21 | 511727.73 | 19 | phm
NCONUML | ftr12 | 5424.58 | 5 | ftr
| bwa23 | 5447.575 | 8 | bwa
NCONUML | llg12 | 4182.92 | 3 | llg
COMMERCIAL | drn13 | 5299129.684 | 96 | drn
INDUSTRIAL | hpk21 | 31624.71 | 8 | hpk
INDUSTRIAL | wyk23 | 1500537.4334 | 28 | wyk
RESIDENTL | lga12 | 4152631.2896 | 644 | lga
RESIDENTL | cyn11 | 6009338.551 | 1440 | cyn
NCONUML | fgy24 | 70027.41 | 43 | fgy
| moe23 | 74726.3012 | 22 | moe
COMMERCIAL | elm24 | 3531802.26 | 46 | elm
LIGHTING | elm33 | 1000.47 | 1 | elm
RESIDENTL | smg23 | 6500499.5996 | 1411 | smg
FARM | msd4 | 1851245.0012 | 252 | msd
COMMERCIAL | lga24 | 21693950.3379 | 92 | lga
COMMERCIAL | ldl11 | 7360578.73 | 74 | ldl
NCONUML | rve13 | 29515.6981 | 24 | rve
COMMERCIAL | trc01 | 365242.5067 | 42 | trc
COMMERCIAL | wt15 | 1164715.6471 | 30 | wt
COMMERCIAL | bra14 | 811059.401 | 59 | bra
| ftr21 | 17034.7542 | 20 | ftr
RESIDENTL | bra23 | 7643359.408 | 1736 | bra
INDUSTRIAL | cpk11 | 59065.36 | 14 | cpk
INDUSTRIAL | hpk12 | 531460.54 | 46 | hpk
FARM | fgy23 | 137430.23 | 3 | fgy
INDUSTRIAL | tt4 | 77015.1997 | 16 | tt
FARM | cpk22 | 45399.86 | 6 | cpk
INDUSTRIAL | yn31 | 1004932.7745 | 6 | yn
FARM | myt22 | 1873055.6433 | 191 | myt
| cpk12 | 20188.43 | 32 | cpk
RESIDENTL | bwa22 | 6606654.3694 | 1106 | bwa
| mfa34 | 1434.55 | 6 | mfa
| nla31 | 4780.58 | 5 | nla
FARM | mdg1 | 36782.2 | 6 | mdg
RESIDENTL | mwl21 | 3605605.4081 | 859 | mwl
COMMERCIAL | phm33 | 14452041.4603 | 180 | phm
INDUSTRIAL | ofr23 | 154535.41 | 17 | ofr
INDUSTRIAL | elm21 | 177435.466 | 7 | elm
INDUSTRIAL | wt5 | 89.11 | 1 | wt
FARM | llg13 | 1917532.2118 | 152 | llg
INDUSTRIAL | klk21 | 41156.68 | 10 | klk
NCONUML | wt9 | 48247.64 | 17 | wt
FARM | mdi1 | 153288.2952 | 21 | mdi
INDUSTRIAL | nrn14 | 19245.31 | 5 | nrn
INDUSTRIAL | wgl12 | 500659.11 | 16 | wgl
FARM | fgy13 | 80534.51 | 6 | fgy
INDUSTRIAL | bwr14 | 1597974.48 | 1 | bwr
LIGHTING | bn11 | 103048.5 | 1 | bn
RESIDENTL | klo14 | 40411755.0117 | 10946 | klo
RESIDENTL | fgy33 | 9101921.8028 | 1763 | fgy
LIGHTING | cre31 | 2308168.51 | 1 | cre
RESIDENTL | wn5 | 8555201.9981 | 1156 | wn
COMMERCIAL | mfa22 | 5299491.9938 | 179 | mfa
COMMERCIAL | lyd11 | 3798691.89 | 62 | lyd
LIGHTING | bn24 | 2014.81 | 1 | bn
COMMERCIAL | cf1 | 9360587.4941 | 189 | cf
FARM | lga11 | 4665290.6529 | 555 | lga
RESIDENTL | lyd13 | 10895753.2364 | 2051 | lyd
NCONUML | cre33 | 35388.67 | 19 | cre
| smg32 | 685.05 | 3 | smg
INDUSTRIAL | cyn11 | 1966971.1028 | 55 | cyn
COMMERCIAL | wn2 | 10157994.9798 | 156 | wn
| phm21 | 32464.7212 | 22 | phm
| sfs1 | 13890.635 | 10 | sfs
NCONUML | tt12 | 15011.94 | 8 | tt
FARM | lga21 | 1065599.6961 | 147 | lga
| ldl12 | 52350.63 | 6 | ldl
INDUSTRIAL | smg31 | 231921 | 9 | smg
LIGHTING | myt12 | 813470.88 | 6 | myt
| smr24 | 66801.9 | 34 | smr
NCONUML | cre32 | 49453.4427 | 23 | cre
INDUSTRIAL | bdl44 | 2337630.2078 | 41 | bdl
| rve11 | 302066.1 | 12 | rve
FARM | wo31 | 3245.01 | 1 | wo
LIGHTING | ofr13 | 171706.2 | 2 | ofr
RESIDENTL | tt9 | 13181645.445 | 3553 | tt
COMMERCIAL | wgl11 | 13522117.9742 | 216 | wgl
COMMERCIAL | hpk24 | 15242696.9791 | 271 | hpk
COMMERCIAL | bwr34 | 12222544.1423 | 437 | bwr
NCONUML | nla34 | 19980.17 | 11 | nla
FARM | bwr24 | 9303.26 | 1 | bwr
| wgi23 | 15962.8799 | 36 | wgi
RESIDENTL | cln13 | 18593732.5659 | 6830 | cln
RESIDENTL | lga13 | 1879247.7046 | 295 | lga
RESIDENTL | cnr3 | 108696.4186 | 22 | cnr
| wgl12 | 112644.3661 | 43 | wgl
COMMERCIAL | cln12 | 8203266.5202 | 86 | cln
NCONUML | ofr21 | 100427.35 | 34 | ofr
RESIDENTL | drn24 | 10021102.8231 | 2473 | drn
COMMERCIAL | cyn31 | 1940881.6507 | 53 | cyn
NCONUML | ldl24 | 34534.3 | 19 | ldl
COMMERCIAL | ofr13 | 9302944.2987 | 197 | ofr
| wots13 | 58538.6484 | 32 | wots
| cpk23 | 23360.0808 | 24 | cpk
NCONUML | cln11 | 4587.8606 | 9 | cln
| wt15 | 51811.4 | 11 | wt
COMMERCIAL | epg24 | 26841528 | 1 | epg
FARM | drn22 | 329138.5031 | 52 | drn
| mfa31 | 16838.31 | 22 | mfa
COMMERCIAL | bra32 | 4055727.3404 | 158 | bra
COMMERCIAL | cpk21 | 14974774.5549 | 258 | cpk
INDUSTRIAL | myt21 | 335981.9667 | 19 | myt
FARM | nrn14 | 139044.47 | 14 | nrn
| wt5 | 22324.85 | 13 | wt
INDUSTRIAL | mfa23 | 139940.33 | 14 | mfa
FARM | wyk12 | 2634438.6357 | 233 | wyk
RESIDENTL | epg23 | 3653084.6682 | 932 | epg
COMMERCIAL | tgn11 | 2525258.71 | 85 | tgn
| wt13 | 22551.0062 | 37 | wt
| cyn13 | 10533.28 | 7 | cyn
INDUSTRIAL | fgy13 | 259435.94 | 2 | fgy
RESIDENTL | cln12 | 23908773.0216 | 6775 | cln
COMMERCIAL | brt22 | 9042592.2197 | 210 | brt
COMMERCIAL | rwt25 | 7526054.6961 | 146 | rwt
FARM | mfa31 | 218040.8355 | 21 | mfa
COMMERCIAL | cln22 | 3248277.4443 | 37 | cln
NCONUML | bdl33 | 22970.8 | 8 | bdl
COMMERCIAL | fgy12 | 74427.591 | 4 | fgy
RESIDENTL | mwl16 | 8188909.2298 | 1700 | mwl
INDUSTRIAL | moe25 | 612177.9824 | 16 | moe
COMMERCIAL | tt7 | 24970154.3491 | 341 | tt
INDUSTRIAL | bwr24 | 4118148.7987 | 125 | bwr
RESIDENTL | moe13 | 2791200.4315 | 357 | moe
FARM | wyk24 | 694188.3378 | 94 | wyk
NCONUML | wo14 | 36996.26 | 12 | wo
RESIDENTL | bra13 | 6470560.8911 | 1572 | bra
RESIDENTL | tt7 | 39398.92 | 9 | tt
FARM | epg34 | 15821.91 | 5 | epg
INDUSTRIAL | yn35 | 6582.38 | 2 | yn
NCONUML | bwa23 | 749.23 | 1 | bwa
FARM | sle13 | 1461316.56 | 213 | sle
COMMERCIAL | cpk13 | 4127340.5971 | 198 | cpk
INDUSTRIAL | ldl14 | 1064067.7426 | 16 | ldl
| rwt14 | 62105.3312 | 18 | rwt
LIGHTING | hpk13 | 14513.85 | 1 | hpk
RESIDENTL | klk22 | 940238.19 | 128 | klk
COMMERCIAL | mwl25 | 259300.06 | 16 | mwl
| mjg11 | 96977.3135 | 7 | mjg
RESIDENTL | hpk24 | 4867180.3451 | 1284 | hpk
FARM | ftr21 | 6703423.0704 | 705 | ftr
FARM | smr12 | 441800.25 | 44 | smr
FARM | bwr13 | 73574.54 | 13 | bwr
| ldl22 | 9241.11 | 9 | ldl
FARM | wo22 | 35676.335 | 7 | wo
NCONUML | moe12 | 9318.9 | 3 | moe
INDUSTRIAL | bdl31 | 1561951.6978 | 44 | bdl
COMMERCIAL | ofr14 | 8393968.2568 | 77 | ofr
NCONUML | tgn23 | 48562.71 | 16 | tgn
NCONUML | cyn21 | 25127.29 | 5 | cyn
FARM | phm34 | 22945.58 | 3 | phm
INDUSTRIAL | cyn33 | 36519.92 | 4 | cyn
LIGHTING | bm8b32 | 1070.04 | 1 | bmb
FARM | llg12 | 5311057.9488 | 488 | llg
NCONUML | rwt32 | 94072.85 | 46 | rwt
COMMERCIAL | myt11 | 912988.53 | 42 | myt
INDUSTRIAL | cpk22 | 129954.91 | 11 | cpk
| cre22 | 20388.051 | 33 | cre
RESIDENTL | ldl21 | 5451727.7741 | 1502 | ldl
FARM | bdl44 | 8189534.7866 | 736 | bdl
INDUSTRIAL | bn11 | 1899511.3657 | 45 | bn
INDUSTRIAL | wgi31 | 152399.6 | 19 | wgi
INDUSTRIAL | mdi1 | 16.0426 | 1 | mdi
| ofr11 | 90492.4817 | 79 | ofr
LIGHTING | kms11 | 547479.19 | 1 | kms
RESIDENTL | phi12 | 18738852.0082 | 4967 | phi
COMMERCIAL | bwr12 | 7897915.6022 | 287 | bwr
FARM | msd1 | 2520603.4144 | 354 | msd
COMMERCIAL | tgn44 | 4662112.18 | 89 | tgn
NCONUML | uwy1 | 29815.85 | 15 | uwy
NCONUML | lga22 | 54192.29 | 17 | lga
NCONUML | lga23 | 17186.13 | 6 | lga
INDUSTRIAL | hpk13 | 1952010.47 | 3 | hpk
FARM | drn23 | 391232.6382 | 58 | drn
FARM | ldl23 | 5910515.5529 | 453 | ldl
FARM | bdl31 | 55336.85 | 12 | bdl
RESIDENTL | bwr34 | 11176240.016 | 2984 | bwr
RESIDENTL | ofr13 | 5689359.8131 | 1445 | ofr
NCONUML | bra21 | 145563.002 | 72 | bra
COMMERCIAL | cf2 | 1114027.3697 | 138 | cf
RESIDENTL | bdl32 | 16368580.902 | 3124 | bdl
COMMERCIAL | smr22 | 10240657.5236 | 95 | smr
NCONUML | rve12 | 34563.18 | 21 | rve
COMMERCIAL | cnr3 | 208527.63 | 11 | cnr
| elm25 | 9741.0155 | 15 | elm
INDUSTRIAL | lyd13 | 30651.21 | 5 | lyd
INDUSTRIAL | mby12 | 279353.09 | 7 | mby
INDUSTRIAL | epg21 | 31298.6803 | 2 | epg
FARM | wgl12 | 7817936.5802 | 624 | wgl
COMMERCIAL | moe13 | 1401894.0174 | 82 | moe
RESIDENTL | lga14 | 7239522.4699 | 1158 | lga
RESIDENTL | epg35 | 308209.78 | 22 | epg
FARM | hpk14 | 29274.39 | 5 | hpk
LIGHTING | bn22 | 341591.58 | 1 | bn
NCONUML | bge11 | 85890.46 | 45 | bge
NCONUML | wt7 | 26985.19 | 18 | wt
| wo31 | 27869.149 | 41 | wo
INDUSTRIAL | elm32 | 759094.4258 | 68 | elm
NCONUML | cre23 | 95638.5 | 25 | cre
RESIDENTL | cln23 | 19292170.1488 | 4992 | cln
| lga21 | 17263.28 | 18 | lga
NCONUML | bwn12 | 35975.24 | 12 | bwn
| fgy31 | 1671.76 | 6 | fgy
NCONUML | ftr23 | 39743.6852 | 30 | ftr
NCONUML | smg21 | 9405.11 | 5 | smg
RESIDENTL | epg13 | 24819451.0174 | 7299 | epg
RESIDENTL | ruba22 | 5955886.59 | 1080 | ruba
INDUSTRIAL | bwr23 | 1917390.4058 | 110 | bwr
COMMERCIAL | bn23 | 4585306.9 | 117 | bn
| fgy24 | 60212.15 | 95 | fgy
LIGHTING | brt21 | 27441.26 | 1 | brt
COMMERCIAL | mby14 | 13812.56 | 3 | mby
RESIDENTL | drn21 | 15235611.8074 | 3585 | drn
RESIDENTL | nrn11 | 3368324.1063 | 703 | nrn
NCONUML | cln21 | 97183.1897 | 28 | cln
NCONUML | tgn12 | 26909.78 | 9 | tgn
FARM | moe22 | 48531.59 | 7 | moe
RESIDENTL | bra14 | 17287022.2386 | 4193 | bra
RESIDENTL | brt21 | 8587133.8204 | 1368 | brt
INDUSTRIAL | ldl23 | 2181365.61 | 45 | ldl
NCONUML | klo24 | 121410.57 | 41 | klo
INDUSTRIAL | wt8 | 22231.36 | 5 | wt
| bdl41 | 27628.4721 | 32 | bdl
COMMERCIAL | sle14 | 13227565.7623 | 343 | sle
| smr14 | 17300.3116 | 19 | smr
INDUSTRIAL | llg11 | 439641.21 | 9 | llg
| wgi22 | 13903.1 | 35 | wgi
NCONUML | moe22 | 34069.45 | 10 | moe
| ftr12 | 15921.46 | 17 | ftr
COMMERCIAL | epg11 | 902129.45 | 16 | epg
RESIDENTL | cpk13 | 21255549.7429 | 4974 | cpk
| fgy23 | 9273.25 | 10 | fgy
FARM | cyn12 | 9105.46 | 2 | cyn
INDUSTRIAL | rwn31 | 527467.66 | 22 | rwn
RESIDENTL | bm8b32 | 357081.227 | 62 | bmb
FARM | ruba22 | 1060033.1321 | 158 | ruba
INDUSTRIAL | cnr1 | 88077.93 | 3 | cnr
FARM | cpk12 | 972803.9358 | 91 | cpk
COMMERCIAL | wo14 | 14658340.7796 | 304 | wo
COMMERCIAL | tt5 | 6134357.4395 | 224 | tt
INDUSTRIAL | wo11 | 18559582.74 | 7 | wo
| wgl23 | 17798.7289 | 12 | wgl
NCONUML | cyn12 | 64730.9 | 21 | cyn
COMMERCIAL | bwr33 | 3515549.759 | 83 | bwr
COMMERCIAL | cyn22 | 10287381.4837 | 183 | cyn
COMMERCIAL | rwt32 | 5482054.6843 | 198 | rwt
INDUSTRIAL | nrn12 | 7260.73 | 2 | nrn
RESIDENTL | cln22 | 8137131.1146 | 3340 | cln
| kms12 | 36774.1343 | 44 | kms
| cyn24 | 12784.0842 | 11 | cyn
| smg33 | 11524.64 | 21 | smg
COMMERCIAL | rve11 | 18192998.0721 | 274 | rve
FARM | wt5 | 8146.48 | 2 | wt
INDUSTRIAL | bge23 | 983662.8538 | 7 | bge
| msd2 | 9983.6 | 13 | msd
| bra12 | 98134.87 | 2 | bra
RESIDENTL | hpk23 | 13762355.5073 | 3377 | hpk
COMMERCIAL | smr13 | 15057236.7589 | 394 | smr
INDUSTRIAL | rwt21 | 372221.49 | 45 | rwt
FARM | rve12 | 22362.86 | 5 | rve
NCONUML | fgy32 | 32042.28 | 18 | fgy
INDUSTRIAL | smr12 | 37387308.69 | 3 | smr
NCONUML | mfa34 | 19451.19 | 8 | mfa
FARM | wots13 | 4844280.0942 | 510 | wots
COMMERCIAL | drn21 | 3220798.94 | 52 | drn
INDUSTRIAL | wo31 | 765.77 | 1 | wo
| fgy32 | 8528.5063 | 10 | fgy
INDUSTRIAL | bwr32 | 3058614 | 72 | bwr
| elm23 | 20831.6 | 30 | elm
INDUSTRIAL | mwl12 | 574569.29 | 12 | mwl
RESIDENTL | cpk21 | 7771248.352 | 1679 | cpk
COMMERCIAL | wots11 | 6621581.9604 | 243 | wots
INDUSTRIAL | ftr21 | 313604.8 | 24 | ftr
NCONUML | lyd11 | 43059.75 | 9 | lyd
FARM | phm21 | 25361.56 | 3 | phm
INDUSTRIAL | wyk13 | 453974.55 | 15 | wyk
INDUSTRIAL | mdg1 | 21781.42 | 1 | mdg
INDUSTRIAL | tt1 | 7434378.9861 | 77 | tt
INDUSTRIAL | wgi34 | 1206209.57 | 8 | wgi
LIGHTING | wgi33 | 1050486.0487 | 2 | wgi
COMMERCIAL | wgl15 | 27996457.3831 | 596 | wgl
RESIDENTL | bge23 | 16900476.9279 | 2094 | bge
INDUSTRIAL | bwr13 | 2417661.2776 | 147 | bwr
NCONUML | epg23 | 28250.73 | 7 | epg
INDUSTRIAL | drn14 | 25996.95 | 2 | drn
RESIDENTL | drn14 | 23831050.9741 | 4399 | drn
RESIDENTL | rwt31 | 5842296.4371 | 1436 | rwt
COMMERCIAL | drn24 | 1717660.9 | 35 | drn
FARM | epg14 | 3614.72 | 1 | epg
RESIDENTL | smr13 | 11225814.5464 | 2447 | smr
COMMERCIAL | wots12 | 14359758.4732 | 371 | wots
COMMERCIAL | klk11 | 3080934.4269 | 114 | klk
NCONUML | mwl14 | 31252.61 | 13 | mwl
INDUSTRIAL | sle11 | 266690.1 | 32 | sle
NCONUML | epg31 | 41319.36 | 24 | epg
RESIDENTL | cf1 | 4176161.3871 | 493 | cf
INDUSTRIAL | phm34 | 816155.12 | 6 | phm
FARM | rwn34 | 20402.21 | 4 | rwn
| mby12 | 1524.95 | 3 | mby
RESIDENTL | wgi31 | 14866992.8529 | 3617 | wgi
RESIDENTL | wots25 | 16858284.9544 | 3532 | wots
RESIDENTL | cre33 | 21876811.5892 | 4235 | cre
RESIDENTL | fgy34 | 4606270.9018 | 975 | fgy
RESIDENTL | cyn32 | 15011504.2579 | 3573 | cyn
RESIDENTL | klk11 | 9194980.7775 | 1227 | klk
INDUSTRIAL | fgy33 | 1452360.19 | 13 | fgy
INDUSTRIAL | wgl13 | 6688610.4344 | 14 | wgl
| tgn41 | 12751.16 | 13 | tgn
COMMERCIAL | klk22 | 85830.78 | 8 | klk
| mby11 | 4292.69 | 12 | mby
FARM | drn12 | 9939.61 | 1 | drn
RESIDENTL | rwn24 | 15617115.6722 | 2794 | rwn
RESIDENTL | cre32 | 8053371.5554 | 2218 | cre
COMMERCIAL | bwn11 | 5920812.2037 | 76 | bwn
NCONUML | smg33 | 19709.42 | 12 | smg
INDUSTRIAL | mby11 | 90387.22 | 16 | mby
COMMERCIAL | tgn41 | 8173213.7745 | 338 | tgn
INDUSTRIAL | wn7 | 3582803.57 | 9 | wn
FARM | bwr23 | 29264.76 | 8 | bwr
RESIDENTL | bwn13 | 8026926.4045 | 1629 | bwn
FARM | wgi24 | 1757204.2906 | 142 | wgi
| rve13 | 21148.03 | 29 | rve
RESIDENTL | wgl21 | 23764201.6622 | 4642 | wgl
COMMERCIAL | wn1 | 22168293.2818 | 620 | wn
INDUSTRIAL | cyn32 | 738566.1077 | 85 | cyn
| hpk21 | 27858.58 | 57 | hpk
COMMERCIAL | klo11 | 2030116.61 | 11 | klo
INDUSTRIAL | bn22 | 260832.7234 | 23 | bn
| ofr24 | 25053.77 | 43 | ofr
| drn12 | 30292.1138 | 29 | drn
COMMERCIAL | smg22 | 18806077.0677 | 136 | smg
COMMERCIAL | bwa22 | 4509592.2057 | 144 | bwa
COMMERCIAL | drn12 | 15118769.4919 | 112 | drn
| ldl23 | 80304.9161 | 48 | ldl
| rwn32 | 14306.27 | 22 | rwn
| drn23 | 12868.4314 | 15 | drn
RESIDENTL | mwl22 | 12904194.2639 | 2809 | mwl
COMMERCIAL | tt6 | 3682930.1298 | 115 | tt
COMMERCIAL | bra24 | 3429037.1414 | 127 | bra
NCONUML | hpk11 | 112614.82 | 31 | hpk
RESIDENTL | mfa21 | 12551518.2306 | 1921 | mfa
RESIDENTL | bge22 | 19945240.9452 | 3164 | bge
| tt4 | 9710.0483 | 41 | tt
NCONUML | phm22 | 22255.8232 | 9 | phm
COMMERCIAL | fgy21 | 1241019.6707 | 34 | fgy
INDUSTRIAL | nla31 | 516137.35 | 16 | nla
FARM | wyk13 | 707273.0378 | 84 | wyk
NCONUML | elm25 | 44655.33 | 20 | elm
| ofr23 | 28214.1089 | 26 | ofr
INDUSTRIAL | ruba22 | 167892.49 | 8 | ruba
FARM | hpk21 | 3124.97 | 1 | hpk
FARM | wn4 | 999664.927 | 129 | wn
COMMERCIAL | wn6 | 8795190.5545 | 246 | wn
| cre23 | 50195.43 | 25 | cre
COMMERCIAL | bwr22 | 15914202.1636 | 269 | bwr
INDUSTRIAL | elm22 | 545216.4127 | 27 | elm
NCONUML | bwr32 | 46210.27 | 31 | bwr
COMMERCIAL | moe12 | 4799517.76 | 51 | moe
| drn22 | 43438.5 | 28 | drn
FARM | bn22 | 13032.09 | 3 | bn
FARM | ldl24 | 222231.4641 | 11 | ldl
| bdl31 | 24144.6762 | 16 | bdl
FARM | cpk11 | 227979.0877 | 18 | cpk
FARM | elm33 | 50441.5205 | 4 | elm
INDUSTRIAL | rve13 | 147824.4003 | 10 | rve
COMMERCIAL | uwy1 | 603856.89 | 33 | uwy
FARM | mfa21 | 13347321.3386 | 701 | mfa
RESIDENTL | wo14 | 1446838.665 | 266 | wo
NCONUML | rwt14 | 102266.96 | 37 | rwt
| kms11 | 9612.23 | 20 | kms
RESIDENTL | phi11 | 5828644.3864 | 1391 | phi
COMMERCIAL | tgn12 | 10174331.2835 | 242 | tgn
LIGHTING | drn21 | 522455.53 | 1 | drn
INDUSTRIAL | smr22 | 2060432.23 | 13 | smr
| moe21 | 19173.8011 | 29 | moe
NCONUML | fgy12 | 1668.8419 | 4 | fgy
COMMERCIAL | elm25 | 2590499.6378 | 73 | elm
| epg34 | 11737.1961 | 27 | epg
COMMERCIAL | cpk23 | 2022573.8223 | 44 | cpk
COMMERCIAL | sle31 | 4198591.4215 | 178 | sle
FARM | nrn13 | 23844.37 | 5 | nrn
FARM | elm26 | 83060.0495 | 12 | elm
INDUSTRIAL | rve12 | 67014.5 | 12 | rve
INDUSTRIAL | moe21 | 304282.5341 | 37 | moe
COMMERCIAL | ofr21 | 9424773.56 | 126 | ofr
FARM | wn3 | 4385381.9629 | 585 | wn
FARM | klk21 | 574949.1868 | 82 | klk
NCONUML | wyk13 | 97422.66 | 49 | wyk
FARM | bwn12 | 14573.05 | 3 | bwn
NCONUML | msd2 | 8161.26 | 6 | msd
COMMERCIAL | elm31 | 474386.1613 | 1 | elm
RESIDENTL | rwt35 | 12065.95 | 2 | rwt
RESIDENTL | wt6 | 15702930.1084 | 3397 | wt
RESIDENTL | cln24 | 3991370.9732 | 1090 | cln
COMMERCIAL | smg21 | 2744632.8687 | 43 | smg
| myt21 | 64545.94 | 22 | myt
RESIDENTL | lga22 | 9862202.3617 | 1608 | lga
INDUSTRIAL | cyn13 | 4447831.06 | 67 | cyn
COMMERCIAL | ruba12 | 6703349.3664 | 290 | ruba
| smr23 | 7378.7014 | 9 | smr
FARM | phi13 | 230339.12 | 15 | phi
RESIDENTL | wt11 | 8665012.8839 | 2213 | wt
RESIDENTL | bge13 | 9255563.8982 | 1458 | bge
COMMERCIAL | bge11 | 11367890.3817 | 330 | bge
COMMERCIAL | wgi23 | 2290528.82 | 95 | wgi
COMMERCIAL | epg35 | 29855241.8371 | 304 | epg
NCONUML | mwl23 | 55631.52 | 20 | mwl
RESIDENTL | tgn11 | 18615536.7391 | 4196 | tgn
RESIDENTL | klo24 | 35150523.3753 | 8219 | klo
| wgi32 | 32777.55 | 36 | wgi
| uwy1 | 1895.86 | 6 | uwy
COMMERCIAL | wots24 | 5008654.6646 | 265 | wots
INDUSTRIAL | phi13 | 601326.64 | 38 | phi
LIGHTING | cf1 | 76883.018 | 3 | cf
RESIDENTL | cre21 | 18876617.5647 | 4715 | cre
INDUSTRIAL | wo32 | 73086.25 | 1 | wo
COMMERCIAL | lga13 | 621321.4861 | 47 | lga
FARM | cnr2 | 245915.51 | 48 | cnr
COMMERCIAL | bge22 | 4521687.9575 | 100 | bge
INDUSTRIAL | cyn12 | 101425.5 | 5 | cyn
FARM | drn11 | 51881.33 | 8 | drn
INDUSTRIAL | wo23 | 212041.78 | 1 | wo
RESIDENTL | lga23 | 5064870.5947 | 821 | lga
RESIDENTL | bn12 | 3438265.7182 | 625 | bn
RESIDENTL | bra21 | 23268334.8963 | 5707 | bra
| bdl42 | 11198.42 | 14 | bdl
FARM | cnr1 | 2440.03 | 2 | cnr
| phm34 | 68320.3174 | 32 | phm
FARM | rwt31 | 12148.87 | 1 | rwt
| smg31 | 8879.89 | 17 | smg
LIGHTING | tgn11 | 1064655.8 | 1 | tgn
FARM | llg14 | 4195351.6172 | 347 | llg
FARM | mwl11 | 2401732.236 | 295 | mwl
INDUSTRIAL | brt22 | 103539.39 | 15 | brt
COMMERCIAL | mwl14 | 15268408.4249 | 139 | mwl
RESIDENTL | wn1 | 4757807.4084 | 1039 | wn
COMMERCIAL | wo33 | 4706642.85 | 27 | wo
| nrn14 | 10562.91 | 10 | nrn
RESIDENTL | wgl15 | 10836827.2608 | 2158 | wgl
RESIDENTL | mfa22 | 4069843.249 | 701 | mfa
NCONUML | wyk24 | 96009.71 | 32 | wyk
NCONUML | rwn34 | 17137.95 | 21 | rwn
NCONUML | rve11 | 32578.28 | 16 | rve
INDUSTRIAL | klk11 | 54511.69 | 7 | klk
RESIDENTL | tt2 | 73044.37 | 7 | tt
COMMERCIAL | rwn32 | 3002784.6794 | 97 | rwn
NCONUML | tt1 | 9612.49 | 4 | tt
NCONUML | bwr23 | 79898.93 | 30 | bwr
NCONUML | epg14 | 19866.64 | 14 | epg
| elm26 | 27328.755 | 32 | elm
INDUSTRIAL | bdl32 | 418697.92 | 34 | bdl
FARM | wt11 | 3746.97 | 1 | wt
NCONUML | ofr23 | 50364.93 | 30 | ofr
INDUSTRIAL | smg23 | 412547.84 | 9 | smg
LIGHTING | klo14 | 3058096.87 | 1 | klo
| nrn13 | 13473.67 | 22 | nrn
FARM | bra12 | 12444.91 | 1 | bra
COMMERCIAL | cre21 | 15222170.3645 | 489 | cre
INDUSTRIAL | wgi32 | 984365.53 | 33 | wgi
NCONUML | rwt25 | 118451.05 | 54 | rwt
INDUSTRIAL | mwe236 | 280541.09 | 16 | mwe
RESIDENTL | epg33 | 183201.2006 | 6 | epg
INDUSTRIAL | elm33 | 243571.284 | 12 | elm
RESIDENTL | ldl11 | 13512975.3636 | 2241 | ldl
| mwl12 | 15850.97 | 9 | mwl
INDUSTRIAL | fgy21 | 6595081.67 | 18 | fgy
LIGHTING | smr24 | 109914.08 | 1 | smr
RESIDENTL | rwt25 | 10768082.8154 | 2324 | rwt
INDUSTRIAL | rwt15 | 3409961.2906 | 83 | rwt
INDUSTRIAL | phi12 | 3418741.3516 | 25 | phi
INDUSTRIAL | bwa22 | 1592049.74 | 9 | bwa
NCONUML | wo22 | 90587.46 | 26 | wo
INDUSTRIAL | ldl21 | 599666.7 | 44 | ldl
INDUSTRIAL | wt6 | 1814.16 | 1 | wt
NCONUML | ofr22 | 9198.59 | 2 | ofr
INDUSTRIAL | bra13 | 1860337.5903 | 47 | bra
COMMERCIAL | fgy24 | 2616699.5517 | 109 | fgy
RESIDENTL | epg11 | 6094828.0666 | 1503 | epg
NCONUML | rwt36 | 1279.88 | 1 | rwt
RESIDENTL | bwn14 | 23184606.5946 | 3016 | bwn
COMMERCIAL | bra31 | 7996775.7312 | 141 | bra
| nla32 | 13550.62 | 15 | nla
FARM | brt11 | 223967.42 | 33 | brt
| hpk12 | 10433.13 | 13 | hpk
INDUSTRIAL | llg13 | 899195.7591 | 21 | llg
INDUSTRIAL | wgl21 | 1687828.17 | 29 | wgl
INDUSTRIAL | cnr2 | 615523.18 | 19 | cnr
INDUSTRIAL | mfa14 | 499885.98 | 5 | mfa
RESIDENTL | drn13 | 15714620.5428 | 2698 | drn
FARM | kms12 | 1180373.8068 | 156 | kms
COMMERCIAL | rwn24 | 15303994.2605 | 63 | rwn
NCONUML | wn4 | 65357.11 | 21 | wn
COMMERCIAL | rwn33 | 562037.42 | 22 | rwn
| moe22 | 3614.75 | 12 | moe
| wgl13 | 39374.2 | 44 | wgl
| moe11 | 8193.3901 | 21 | moe
COMMERCIAL | wt7 | 4475658.5866 | 198 | wt
NCONUML | bwr13 | 106489.72 | 46 | bwr
NCONUML | kms12 | 115620.45 | 45 | kms
NCONUML | cyn24 | 41312.6858 | 21 | cyn
COMMERCIAL | mwl13 | 8520395.3383 | 232 | mwl
COMMERCIAL | cyn32 | 10902527.7138 | 351 | cyn
INDUSTRIAL | tgn31 | 3050316.88 | 29 | tgn
| wo13 | 12961.22 | 9 | wo
NCONUML | bra12 | 30121.15 | 6 | bra
| mwl24 | 4141.68 | 3 | mwl
RESIDENTL | ftr22 | 5196242.6186 | 1010 | ftr
| cyn12 | 33132.831 | 28 | cyn
| mwl11 | 4217.9 | 11 | mwl
NCONUML | sle13 | 9744.3474 | 7 | sle
RESIDENTL | sle14 | 16027394.2978 | 4223 | sle
RESIDENTL | wgl23 | 5362246.1099 | 739 | wgl
COMMERCIAL | cre23 | 25513720.5265 | 132 | cre
RESIDENTL | bdl43 | 5886157.096 | 1122 | bdl
RESIDENTL | bge21 | 100743.92 | 11 | bge
RESIDENTL | smg22 | 10427736.14 | 2476 | smg
FARM | rwn31 | 347566.14 | 21 | rwn
INDUSTRIAL | bn12 | 8173831.79 | 6 | bn
| wgi24 | 27543.5394 | 32 | wgi
| mfa23 | 2828.28 | 3 | mfa
NCONUML | elm22 | 93887.89 | 42 | elm
INDUSTRIAL | wots13 | 2426481.9937 | 28 | wots
RESIDENTL | mwl13 | 9372820.2657 | 1896 | mwl
COMMERCIAL | epg31 | 8736205.1691 | 170 | epg
| bdl44 | 43009.9658 | 33 | bdl
COMMERCIAL | wgl24 | 14484234.4559 | 200 | wgl
INDUSTRIAL | wn3 | 1104797.78 | 30 | wn
| wgi33 | 38017.7186 | 28 | wgi
NCONUML | wo31 | 91536.41 | 24 | wo
FARM | ldl14 | 3990495.203 | 142 | ldl
NCONUML | wyk12 | 43139.17 | 24 | wyk
INDUSTRIAL | mwl15 | 15961047.4 | 1 | mwl
LIGHTING | bdl32 | 23514.52 | 1 | bdl
| rve12 | 15159.19 | 33 | rve
NCONUML | phm34 | 55440.25 | 17 | phm
COMMERCIAL | phm22 | 18761180.3018 | 732 | phm
RESIDENTL | cyn22 | 8715945.6121 | 2142 | cyn
FARM | fgy31 | 3345.68 | 2 | fgy
RESIDENTL | smr22 | 8159798.5324 | 1327 | smr
RESIDENTL | cyn23 | 7298806.6664 | 1621 | cyn
FARM | bdl42 | 2407309.4815 | 483 | bdl
| wyk23 | 31976.68 | 33 | wyk
INDUSTRIAL | rwn26 | 257525.5397 | 10 | rwn
NCONUML | bwn11 | 91006.47 | 23 | bwn
COMMERCIAL | cyn23 | 7883296.3431 | 299 | cyn
| moe15 | 19145.0797 | 16 | moe
| drn11 | 44271.4909 | 65 | drn
INDUSTRIAL | moe22 | 88009.47 | 4 | moe
NCONUML | mdg1 | 4146.1 | 9 | mdg
FARM | bra33 | 5568.67 | 1 | bra
LIGHTING | bwa22 | 75542.46 | 1 | bwa
NCONUML | hpk14 | 64164.68 | 20 | hpk
NCONUML |  | 262.3928 | 5 | #REF!
INDUSTRIAL | cln13 | 2016187.9013 | 2 | cln
FARM | ofr11 | 1184021.9516 | 51 | ofr
FARM | phm31 | 2011038.4476 | 90 | phm
NCONUML | elm21 | 62554.36 | 23 | elm
NCONUML | wt8 | 36862.33 | 14 | wt
NCONUML | cnr1 | 1922.85 | 2 | cnr
INDUSTRIAL | cre31 | 212230.18 | 2 | cre
COMMERCIAL | mfa34 | 8313764.4144 | 170 | mfa
INDUSTRIAL | tt5 | 637183.9506 | 23 | tt
INDUSTRIAL | llg14 | 1201432.9268 | 29 | llg
RESIDENTL | wo23 | 1549813.7708 | 361 | wo
| bwr23 | 25383.1703 | 47 | bwr
| sle11 | 3997.21 | 10 | sle
NCONUML | epg22 | 8538.04 | 7 | epg
NCONUML | bwr24 | 20744.02 | 14 | bwr
INDUSTRIAL | myt12 | 952524.23 | 20 | myt
| ftr23 | 53453.1274 | 33 | ftr
RESIDENTL | bra11 | 9331476.9371 | 2277 | bra
FARM | ldl13 | 3504918.0126 | 302 | ldl
| brt11 | 8693.81 | 14 | brt
INDUSTRIAL | phm31 | 91642.7039 | 2 | phm
COMMERCIAL | bdl43 | 22280533.2345 | 523 | bdl
FARM | moe23 | 4928404.5033 | 365 | moe
| klk21 | 7164.56 | 8 | klk
| wt7 | 8483.27 | 17 | wt
FARM | llg11 | 4501914.1562 | 365 | llg
LIGHTING | cf2 | 13221.322 | 1 | cf
| tgn31 | 23134.1673 | 13 | tgn
RESIDENTL | nla31 | 3471883.5329 | 742 | nla
COMMERCIAL | bdl31 | 6479518.62 | 206 | bdl
COMMERCIAL | smr23 | 799486.21 | 26 | smr
INDUSTRIAL | rve11 | 154936.16 | 21 | rve
RESIDENTL | bm8b33 | 130717.0048 | 17 | bmb
FARM | phi12 | 364625.9 | 40 | phi
INDUSTRIAL | klk22 | 5518.6 | 1 | klk
RESIDENTL | llg12 | 7619865.2998 | 1210 | llg
RESIDENTL | cln21 | 24090170.4832 | 5877 | cln
NCONUML | cpk11 | 17830.25 | 17 | cpk
COMMERCIAL | ruba22 | 3463594.5603 | 120 | ruba
NCONUML | brt22 | 9306.55 | 7 | brt
INDUSTRIAL | epg32 | 7635590.16 | 5 | epg
INDUSTRIAL | cln12 | 360384.55 | 1 | cln
COMMERCIAL | bwr13 | 10101102.0366 | 288 | bwr
COMMERCIAL | wo22 | 9017310.64 | 153 | wo
INDUSTRIAL | hpk24 | 9439809.63 | 31 | hpk
COMMERCIAL | cpk12 | 5057421.24 | 115 | cpk
| lyd14 | 55928.8081 | 17 | lyd
INDUSTRIAL | klo11 | 67703.26 | 1 | klo
RESIDENTL | ldl14 | 11349760.1474 | 1905 | ldl
LIGHTING | myt21 | 2294.9 | 1 | myt
RESIDENTL | rwn22 | 13452598.5118 | 2640 | rwn
COMMERCIAL | bm8b32 | 168652.4116 | 16 | bmb
INDUSTRIAL | bdl34 | 328519.77 | 31 | bdl
| tt12 | 16952.1045 | 5 | tt
RESIDENTL | wots24 | 6979604.5034 | 1172 | wots
INDUSTRIAL | wyk24 | 160679.33 | 16 | wyk
COMMERCIAL | klo12 | 12237846.22 | 9 | klo
RESIDENTL | wo33 | 232024.16 | 58 | wo
COMMERCIAL | bn24 | 3468313.5774 | 163 | bn
COMMERCIAL | lga12 | 9341312.33 | 61 | lga
| msd1 | 16071.3636 | 20 | msd
INDUSTRIAL | ofr24 | 300622.14 | 4 | ofr
INDUSTRIAL | bwn13 | 24333.45 | 4 | bwn
| tt1 | 26786.62 | 3 | tt
INDUSTRIAL | rwt31 | 22449174.23 | 3 | rwt
FARM | mfa14 | 28798.91 | 1 | mfa
| bwr32 | 10607.4826 | 52 | bwr
INDUSTRIAL | wn4 | 1120535.2101 | 54 | wn
RESIDENTL | bwr12 | 975012.274 | 199 | bwr
INDUSTRIAL | wgi24 | 1432383.73 | 33 | wgi
| llg13 | 135285.4952 | 24 | llg
| rwn34 | 10950.9 | 10 | rwn
FARM | elm34 | 16399.68 | 6 | elm
RESIDENTL | ruba12 | 12797333.4035 | 1890 | ruba
COMMERCIAL | hpk22 | 5875279.82 | 181 | hpk
| cln11 | 262675.9461 | 229 | cln
RESIDENTL | cf2 | 494427.3912 | 409 | cf
FARM | elm22 | 15544.2323 | 4 | elm
INDUSTRIAL | smg32 | 67645.78 | 1 | smg
FARM | bwa23 | 3495492.525 | 169 | bwa
NCONUML | phm24 | 66511.6 | 15 | phm
NCONUML | wgi23 | 35701.3 | 15 | wgi
NCONUML | epg35 | 18576.68 | 9 | epg
NCONUML | llg13 | 26801.83 | 12 | llg
LIGHTING | phi13 | 74566.47 | 1 | phi
| ldl24 | 28689.7774 | 48 | ldl
| bge11 | 41147.6131 | 30 | bge
RESIDENTL | ofr21 | 18456788.2346 | 4412 | ofr
INDUSTRIAL | ofr11 | 52339.71 | 6 | ofr
COMMERCIAL | nrn11 | 8254682.48 | 13 | nrn
FARM | moe15 | 1053275.4428 | 126 | moe
INDUSTRIAL | lyd12 | 15947.41 | 3 | lyd
INDUSTRIAL | wt10 | 5540.7 | 1 | wt
RESIDENTL | rwt21 | 965731.93 | 282 | rwt
FARM | wo13 | 51683.13 | 6 | wo
INDUSTRIAL | epg34 | 25722.81 | 2 | epg
COMMERCIAL | lys36 | 31611.41 | 1 | lys
RESIDENTL | wn6 | 17451542.0984 | 3750 | wn
NCONUML | hpk12 | 23613.79 | 7 | hpk
INDUSTRIAL | ruba24 | 189283.4035 | 13 | ruba
| nrn12 | 36108.6 | 9 | nrn
NCONUML | nla32 | 30069.03 | 18 | nla
COMMERCIAL | bm8b31 | 174913.9253 | 14 | bmb
| wo22 | 26321.2427 | 38 | wo
INDUSTRIAL | fgy31 | 4952.61 | 1 | fgy
RESIDENTL | cln14 | 25051991.2109 | 8311 | cln
RESIDENTL | lga24 | 3807672.9803 | 653 | lga
RESIDENTL | bra31 | 2624204.8049 | 649 | bra
COMMERCIAL | cln21 | 7282112.3749 | 104 | cln
COMMERCIAL | ftr23 | 8984637.4811 | 336 | ftr
RESIDENTL | klo13 | 97850.5847 | 89 | klo
INDUSTRIAL | ofr14 | 250.62 | 1 | ofr
FARM | mwl24 | 966080.4815 | 75 | mwl
NCONUML | bdl41 | 86032.0652 | 28 | bdl
INDUSTRIAL | epg13 | 201122.3196 | 20 | epg
COMMERCIAL | tgn23 | 6173474.1124 | 95 | tgn
| moe12 | 11374.0239 | 16 | moe
INDUSTRIAL | drn11 | 8297.91 | 2 | drn
| wn4 | 46461.2191 | 29 | wn
NCONUML | wgl13 | 85005.64 | 23 | wgl
INDUSTRIAL | ftr22 | 264831.3749 | 23 | ftr
NCONUML | mjg11 | 5653.43 | 3 | mjg
RESIDENTL | klo12 | 526.2 | 1 | klo
COMMERCIAL | cln11 | 18408618.7138 | 182 | cln
NCONUML | wo13 | 11132.69 | 4 | wo
COMMERCIAL | yn38 | 28127.08 | 5 | yn
NCONUML | mwl24 | 19701.6 | 5 | mwl
RESIDENTL | wots12 | 7880580.6899 | 1786 | wots
COMMERCIAL | tgn43 | 5598797.62 | 126 | tgn
NCONUML | mfa23 | 6277.17 | 3 | mfa
NCONUML | bra32 | 63005.82 | 38 | bra
FARM | bdl34 | 247623.03 | 51 | bdl
INDUSTRIAL | wn5 | 6299826.69 | 33 | wn
| mby13 | 155.9226 | 1 | mby
FARM | ofr23 | 2419763.5413 | 305 | ofr
NCONUML | cre22 | 86458.6773 | 42 | cre
NCONUML | hpk23 | 84001.53 | 23 | hpk
RESIDENTL | bra24 | 8260262.5707 | 1824 | bra
| cyn14 | 12637.7523 | 26 | cyn
LIGHTING | wgl11 | 2443513.25 | 2 | wgl
NCONUML | wgi24 | 69610.83 | 24 | wgi
COMMERCIAL | klo14 | 11961206.944 | 269 | klo
FARM | drn14 | 379625.3327 | 36 | drn
RESIDENTL | bwr22 | 1941843.629 | 510 | bwr
| llg14 | 42684.6726 | 22 | llg
INDUSTRIAL | drn21 | 709809.96 | 3 | drn
INDUSTRIAL | tgn42 | 199383.97 | 5 | tgn
RESIDENTL | sle32 | 6677118.757 | 1350 | sle
RESIDENTL | myt12 | 14552002.0991 | 2380 | myt
FARM | myt21 | 821475.54 | 124 | myt
| bn11 | 39921.12 | 40 | bn
NCONUML | mby12 | 15769.2 | 4 | mby
NCONUML | bdl44 | 1602.59 | 5 | bdl
COMMERCIAL | tt12 | 10810239.5174 | 467 | tt
NCONUML | wn7 | 7884.6 | 2 | wn
| bdl34 | 14430.17 | 36 | bdl
RESIDENTL | lyd11 | 11014119.7855 | 2574 | lyd
FARM | wyk23 | 2329152.6841 | 202 | wyk
| epg23 | 66262.7623 | 20 | epg
RESIDENTL | rwt32 | 15157646.1346 | 3808 | rwt
RESIDENTL | cre31 | 23125994.5084 | 5990 | cre
FARM | bn11 | 9012293.1298 | 1372 | bn
COMMERCIAL |  | 2470964.7554 | 79 | #REF!
INDUSTRIAL | kms11 | 3849512.37 | 9 | kms
RESIDENTL | sle31 | 15232222.0022 | 4728 | sle
RESIDENTL | myt11 | 3230941.4261 | 365 | myt
| wyk12 | 33744.4845 | 17 | wyk
| lga11 | 13750.1489 | 25 | lga
COMMERCIAL | cre33 | 14716025.8299 | 132 | cre
RESIDENTL | trc01 | 404888.8876 | 85 | trc
| moe25 | 10579.3743 | 23 | moe
NCONUML | msd1 | 8725.66 | 9 | msd
RESIDENTL | mwl14 | 1637810.9082 | 178 | mwl
FARM | wn5 | 10157746.9699 | 1090 | wn
INDUSTRIAL | bwr33 | 13101695.07 | 41 | bwr
NCONUML | ofr24 | 72292.73 | 18 | ofr
| mdg1 | 5594.13 | 4 | mdg
FARM | wgi33 | 86057.74 | 7 | wgi
RESIDENTL | rwt22 | 12512450.4989 | 3066 | rwt
RESIDENTL | cnr2 | 3844076.3719 | 1054 | cnr
| hpk14 | 17565.23 | 35 | hpk
NCONUML | drn23 | 37389.78 | 20 | drn
RESIDENTL | tgn44 | 11943542.7304 | 2804 | tgn
| tgn42 | 0 | 1 | tgn
NCONUML | rwt22 | 27503.296 | 22 | rwt
FARM | mwl16 | 172184.54 | 14 | mwl
COMMERCIAL | nla34 | 1413700.5844 | 93 | nla
| epg22 | 2049.9261 | 2 | epg
FARM | tgn41 | 3728231.4432 | 423 | tgn
COMMERCIAL | lga23 | 3382991.9134 | 119 | lga
NCONUML | sle31 | 61055.23 | 20 | sle
NCONUML | tgn44 | 66469.79 | 20 | tgn
| phm24 | 18272.6834 | 34 | phm
RESIDENTL | hpk11 | 16523367.4098 | 4141 | hpk
| hpk13 | 40054.7485 | 22 | hpk
| bwr24 | 10180.34 | 28 | bwr
COMMERCIAL | bdl33 | 34051046.7333 | 257 | bdl
COMMERCIAL | wt9 | 7035668.1433 | 128 | wt
NCONUML | wt15 | 16005.53 | 14 | wt
FARM | ruba24 | 730484.142 | 55 | ruba
NCONUML | cpk23 | 20021.69 | 18 | cpk
INDUSTRIAL | mwl21 | 320021.87 | 5 | mwl
COMMERCIAL | hpk23 | 12064171.7331 | 206 | hpk
INDUSTRIAL | wt11 | 2563605.84 | 2 | wt
RESIDENTL | wt15 | 8580853.2399 | 1947 | wt
| elm21 | 24345.52 | 16 | elm
INDUSTRIAL | mwl16 | 183545.9668 | 9 | mwl
FARM | rve13 | 9637.99 | 1 | rve
NCONUML | drn22 | 69938.3 | 27 | drn
NCONUML | bdl31 | 70697.58 | 29 | bdl
NCONUML | bwa24 | 1320.25 | 1 | bwa
COMMERCIAL | mwl23 | 10773058.8537 | 154 | mwl
COMMERCIAL | elm23 | 5093994.3825 | 95 | elm
FARM | smr23 | 1078615.6398 | 156 | smr
| cpk11 | 37835.6667 | 47 | cpk
INDUSTRIAL | bra14 | 14750.52 | 4 | bra
RESIDENTL | rwn33 | 5693275.4596 | 1153 | rwn
| bn22 | 41634.09 | 21 | bn
INDUSTRIAL | tt2 | 11531135.8238 | 100 | tt
INDUSTRIAL | wt12 | 3871876.0911 | 67 | wt
INDUSTRIAL | mwl22 | 292678.42 | 8 | mwl
RESIDENTL | bn23 | 8695284.412 | 1665 | bn
COMMERCIAL | cyn11 | 9621618.8569 | 233 | cyn
| cyn21 | 22400.14 | 28 | cyn
INDUSTRIAL | mjg11 | 1321804.29 | 13 | mjg
INDUSTRIAL | cf2 | 1970.494 | 2 | cf
RESIDENTL | tt5 | 6560032.4165 | 1633 | tt
COMMERCIAL | smr14 | 6818307.6657 | 239 | smr
COMMERCIAL | smg33 | 1348313.99 | 14 | smg
RESIDENTL | rwt15 | 11066767.0768 | 2454 | rwt
COMMERCIAL | cre32 | 14440881.1645 | 427 | cre
INDUSTRIAL | smr24 | 4639865.5557 | 45 | smr
COMMERCIAL | fgy23 | 10185283.97 | 98 | fgy
COMMERCIAL | hpk11 | 3476478.711 | 53 | hpk
| cre32 | 19011.64 | 13 | cre
NCONUML | wgl23 | 12760.41 | 6 | wgl
COMMERCIAL | nrn15 | 84419.81 | 3 | nrn
NCONUML | moe15 | 22748.39 | 11 | moe
RESIDENTL | tt12 | 86039.86 | 6 | tt
RESIDENTL | cyn31 | 8632445.7043 | 2077 | cyn
RESIDENTL | wgl24 | 16633542.8094 | 2715 | wgl
COMMERCIAL | wgi22 | 6881286.006 | 159 | wgi
INDUSTRIAL | smr13 | 992080.85 | 26 | smr
NCONUML | cpk12 | 17033.61 | 10 | cpk
NCONUML | ftr21 | 16597.26 | 11 | ftr
FARM | mwl12 | 18529.37 | 2 | mwl
INDUSTRIAL | epg33 | 1129768.4897 | 4 | epg
| wyk13 | 9658.4809 | 15 | wyk
LIGHTING | trc01 | 669938.2281 | 2 | trc
FARM | hpk13 | 2305.94 | 1 | hpk
RESIDENTL | tt6 | 19150788.3328 | 4695 | tt
FARM | tgn31 | 5369095.0164 | 562 | tgn
NCONUML | wgl24 | 11028.97 | 10 | wgl
INDUSTRIAL | brt11 | 82545.9018 | 12 | brt
LIGHTING | mby11 | 10728.24 | 1 | mby
NCONUML | myt21 | 24178.1 | 12 | myt
| wt10 | 6115.9374 | 5 | wt
RESIDENTL | bge12 | 9796026.1467 | 1789 | bge
FARM | myt11 | 2640136.7565 | 257 | myt
NCONUML | cyn11 | 21168.08 | 13 | cyn
INDUSTRIAL |  | 942329979.1078 | 12 | #REF!
INDUSTRIAL | elm34 | 168803.0667 | 15 | elm
| brt22 | 30486.3216 | 18 | brt
INDUSTRIAL | epg11 | 6777.42 | 2 | epg
RESIDENTL | elm34 | 19825611.7814 | 4189 | elm
COMMERCIAL | sle13 | 974523.8832 | 109 | sle
INDUSTRIAL | lga13 | 207007.5439 | 9 | lga
RESIDENTL | mwl23 | 3618535.6291 | 812 | mwl
| fgy14 | 28887.99 | 26 | fgy
COMMERCIAL | mby13 | 2521770.2974 | 71 | mby
| lga12 | 14720.56 | 12 | lga
RESIDENTL | cpk12 | 17343162.547 | 2927 | cpk
COMMERCIAL | wt5 | 19785711.5258 | 118 | wt
INDUSTRIAL | drn24 | 4643890.64 | 3 | drn
FARM | drn21 | 13254.24 | 1 | drn
NCONUML | mwl11 | 360.93 | 3 | mwl
RESIDENTL | epg34 | 15669683.4078 | 3862 | epg
NCONUML | wt10 | 27658.61 | 16 | wt
LIGHTING | rwt14 | 962126.36 | 3 | rwt
COMMERCIAL | drn23 | 5472888.3558 | 161 | drn
LIGHTING | bwn11 | 6340546.01 | 1 | bwn
INDUSTRIAL | sfs1 | 80102.39 | 5 | sfs
COMMERCIAL | phm34 | 4610839.9937 | 66 | phm
COMMERCIAL | mfa31 | 3803351.87 | 100 | mfa
INDUSTRIAL | rwt25 | 2203508.65 | 42 | rwt
| bwa22 | 41045.3074 | 24 | bwa
FARM | smr13 | 139441.5096 | 27 | smr
NCONUML | phi12 | 84007.84 | 24 | phi
| fgy21 | 10377.87 | 9 | fgy
NCONUML | rwt15 | 44056.974 | 28 | rwt
LIGHTING | nla34 | 5187.52 | 1 | nla
RESIDENTL | sfs1 | 6449039.4989 | 958 | sfs
RESIDENTL | msd4 | 16354350.3097 | 2395 | msd
INDUSTRIAL | phm33 | 724516.58 | 21 | phm
COMMERCIAL | wgl14 | 59932538.6 | 1 | wgl
COMMERCIAL | rwt31 | 3904134.109 | 54 | rwt
RESIDENTL | wt5 | 5466545.168 | 1335 | wt
FARM | ftr22 | 3872176.8459 | 271 | ftr
| wn5 | 51237.831 | 23 | wn
INDUSTRIAL | kms12 | 880994.04 | 26 | kms
NCONUML | rwt31 | 27889.28 | 18 | rwt
RESIDENTL | elm22 | 20622579.4478 | 3120 | elm
| bn24 | 7126.586 | 9 | bn
FARM | wots11 | 7572710.4051 | 689 | wots
INDUSTRIAL | myt11 | 122662.09 | 11 | myt
NCONUML | bdl32 | 81716.25 | 38 | bdl
NCONUML | cyn33 | 39860.39 | 20 | cyn
| lga13 | 7900.07 | 12 | lga
COMMERCIAL | wn7 | 705796.26 | 31 | wn
RESIDENTL | tgn23 | 12995258.1614 | 2157 | tgn
RESIDENTL | wgl12 | 18309192.1093 | 3011 | wgl
NCONUML | drn14 | 58816.42 | 20 | drn
INDUSTRIAL | tt9 | 1853761.73 | 4 | tt
RESIDENTL | kms12 | 23913269.0041 | 4277 | kms
COMMERCIAL | wgi33 | 13737748.8552 | 364 | wgi
COMMERCIAL | phm21 | 28428865.0993 | 838 | phm
FARM | sle32 | 5441049.7096 | 310 | sle
NCONUML | cyn32 | 58907.16 | 38 | cyn
INDUSTRIAL | msd2 | 165834.72 | 18 | msd
COMMERCIAL | bwr23 | 26845428.111 | 233 | bwr
RESIDENTL | msd2 | 5810770.2828 | 1153 | msd
FARM | klk11 | 2014936.8264 | 177 | klk
| wots12 | 13459.1171 | 22 | wots
INDUSTRIAL | rwn24 | 4339629.96 | 13 | rwn
INDUSTRIAL | tgn41 | 1853911.3546 | 62 | tgn
COMMERCIAL | smg32 | 6595824.87 | 22 | smg
| wgi34 | 86239.94 | 15 | wgi
RESIDENTL | bn22 | 13286130.4589 | 3118 | bn
RESIDENTL | mfa31 | 9237847.4317 | 2206 | mfa
COMMERCIAL | wgi34 | 9571334.08 | 60 | wgi
RESIDENTL | mdi1 | 176577.17 | 31 | mdi
NCONUML | rwn31 | 16738.19 | 15 | rwn
INDUSTRIAL | drn13 | 239296.9 | 11 | drn
INDUSTRIAL | bdl43 | 306419.52 | 21 | bdl
NCONUML | wo23 | 56204.51 | 16 | wo
COMMERCIAL | ftr21 | 2804675.8206 | 100 | ftr
COMMERCIAL | bwa23 | 206762.2501 | 23 | bwa
NCONUML | mfa21 | 28416.84 | 12 | mfa
| cln23 | 52144.7804 | 85 | cln
RESIDENTL | rve11 | 2276471.0008 | 508 | rve
COMMERCIAL | ofr24 | 6649904.8426 | 113 | ofr
NCONUML | phi13 | 105028.33 | 33 | phi
FARM | smg22 | 25054.15 | 4 | smg
FARM | bwn11 | 18419.1 | 1 | bwn
INDUSTRIAL | epg31 | 360181.3871 | 31 | epg
COMMERCIAL | fgy14 | 7872993.2117 | 231 | fgy
| ldl11 | 24480.7 | 22 | ldl
INDUSTRIAL | wgl24 | 939120.3004 | 39 | wgl
| phm22 | 31542.7748 | 10 | phm
COMMERCIAL | moe15 | 2469270.3666 | 172 | moe
| cnr3 | 100.0469 | 1 | cnr
RESIDENTL | bwn12 | 4456239.3509 | 1013 | bwn
COMMERCIAL | mwl24 | 5791496.4979 | 78 | mwl
COMMERCIAL | wo13 | 2493976.37 | 46 | wo
RESIDENTL | elm25 | 10534980.5572 | 2009 | elm
RESIDENTL | phm32 | 14466986.7977 | 3288 | phm
COMMERCIAL | ofr11 | 14130002.2904 | 224 | ofr
INDUSTRIAL | bge13 | 1057475.88 | 11 | bge
RESIDENTL | ofr22 | 7907197.5875 | 2174 | ofr
INDUSTRIAL | lga22 | 745287.81 | 44 | lga
FARM | hpk22 | 33600.65 | 5 | hpk
COMMERCIAL | epg23 | 63543126.9632 | 711 | epg
NCONUML | epg34 | 29379.47 | 21 | epg
| mwl23 | 14018.9088 | 10 | mwl
FARM | lyd14 | 350081.37 | 31 | lyd
| elm33 | 18371.0537 | 30 | elm
RESIDENTL | bwn11 | 14758921.2622 | 2984 | bwn
| cyn33 | 33636.86 | 37 | cyn
INDUSTRIAL | ldl13 | 1566146.5513 | 31 | ldl
NCONUML | smg32 | 19512.15 | 10 | smg
NCONUML | lga21 | 24931.49 | 9 | lga
RESIDENTL | mfa34 | 6438005.323 | 995 | mfa
COMMERCIAL | lga22 | 10229963.6597 | 340 | lga
COMMERCIAL | wgi31 | 4363035.5887 | 128 | wgi
| wt9 | 17175.83 | 21 | wt
INDUSTRIAL | mfa21 | 1292894.4886 | 57 | mfa
FARM | wgi32 | 343056.5273 | 19 | wgi
COMMERCIAL | bge21 | 44944.8 | 1 | bge
INDUSTRIAL | elm26 | 46289.86 | 5 | elm
NCONUML | msd4 | 12187.83 | 6 | msd
COMMERCIAL | bra21 | 14789918.5926 | 289 | bra
| cpk22 | 7305.07 | 12 | cpk
NCONUML | phm32 | 76324.09 | 20 | phm
NCONUML | sfs1 | 44865.78 | 10 | sfs
COMMERCIAL | lyd13 | 6072257.17 | 42 | lyd
FARM | cyn33 | 36456.98 | 4 | cyn
NCONUML | phm21 | 71428.0533 | 24 | phm
COMMERCIAL | sle32 | 5434267.6149 | 190 | sle
NCONUML | smg31 | 21751.86 | 17 | smg
NCONUML | wots11 | 25057.91 | 11 | wots
RESIDENTL | tgn43 | 15724147.9465 | 3608 | tgn
INDUSTRIAL | cyn21 | 9259443.95 | 23 | cyn
INDUSTRIAL | bn23 | 1923467.13 | 19 | bn
NCONUML | nrn14 | 79150.17 | 17 | nrn
NCONUML | cyn22 | 32483.16 | 10 | cyn
NCONUML | wgl12 | 47271.49 | 20 | wgl
COMMERCIAL | phm24 | 600129.57 | 25 | phm
NCONUML | lga11 | 25837.14 | 8 | lga
NCONUML | tgn41 | 7415.11 | 5 | tgn
RESIDENTL | wgl11 | 17118670.1537 | 3818 | wgl
RESIDENTL | wots11 | 15871220.8415 | 2910 | wots
| rwn31 | 40233.5106 | 27 | rwn
COMMERCIAL | elm32 | 8171019.0636 | 263 | elm
FARM | mby11 | 1335559.7721 | 187 | mby
INDUSTRIAL | mwl25 | 33119.15 | 8 | mwl
FARM | rwn26 | 5055.63 | 2 | rwn
| nla34 | 8234.98 | 10 | nla
RESIDENTL |  | 349105.8277 | 492 | #REF!
FARM | epg13 | 82815.8863 | 12 | epg
| wyk24 | 32167.14 | 30 | wyk
FARM | sle11 | 16862.17 | 6 | sle
COMMERCIAL | bm8b33 | 3349.12 | 2 | bmb
RESIDENTL | smg21 | 17914575.4009 | 3718 | smg
INDUSTRIAL | bdl42 | 622534.62 | 24 | bdl
| yn38 | 7519.7419 | 1 | yn
| phi13 | 28221.5917 | 27 | phi
| epg14 | 9258.9052 | 38 | epg
FARM | nla31 | 1791184.5035 | 140 | nla
INDUSTRIAL | wgi33 | 1188063.8119 | 37 | wgi
LIGHTING | phm33 | 4303153.65 | 2 | phm
RESIDENTL | phm33 | 12878778.4238 | 2134 | phm
COMMERCIAL | wgl23 | 3870974.8784 | 252 | wgl
NCONUML | wt5 | 58508.56 | 14 | wt
NCONUML | bwn14 | 81385.02 | 37 | bwn
NCONUML | mfa31 | 49958.93 | 14 | mfa
COMMERCIAL | bra12 | 23355928.37 | 122 | bra
NCONUML | wt13 | 98966.19 | 41 | wt
COMMERCIAL | klo24 | 13267963.2484 | 244 | klo
COMMERCIAL | bge12 | 6262328.83 | 64 | bge
COMMERCIAL | wn4 | 10511680.2174 | 332 | wn
INDUSTRIAL | tt6 | 2940006.87 | 14 | tt
FARM | cln13 | 4519.0334 | 1 | cln
RESIDENTL | bwa23 | 1839261.5711 | 259 | bwa
RESIDENTL | smr12 | 601661.7559 | 102 | smr
NCONUML | bra31 | 17155.48 | 11 | bra
FARM | cln22 | 84599.56 | 6 | cln
RESIDENTL | moe23 | 10757204.18 | 1872 | moe
FARM | bn23 | 4995698.9571 | 709 | bn
INDUSTRIAL | bwr12 | 7576207.2428 | 317 | bwr
COMMERCIAL | elm33 | 8652520.7547 | 229 | elm
RESIDENTL | tgn12 | 769554.192 | 239 | tgn
NCONUML | bn23 | 5729.17 | 9 | bn
| cyn11 | 35169.6447 | 13 | cyn
INDUSTRIAL | wots12 | 5742170.47 | 22 | wots
INDUSTRIAL | llg12 | 8080777.31 | 18 | llg
NCONUML | ofr14 | 11958.45 | 3 | ofr
RESIDENTL | rwn34 | 11161403.5989 | 1490 | rwn
RESIDENTL | fgy12 | 975691.3435 | 398 | fgy
COMMERCIAL | wyk24 | 11852940.7836 | 290 | wyk
COMMERCIAL | smr12 | 1199230.8 | 20 | smr
INDUSTRIAL | wgl11 | 590499.13 | 17 | wgl
INDUSTRIAL | moe13 | 8896507.14 | 13 | moe
INDUSTRIAL | wots11 | 14616083.73 | 22 | wots
NCONUML | epg13 | 4325.18 | 2 | epg
NCONUML | bn22 | 72789.04 | 38 | bn
RESIDENTL | bwr23 | 15381612.1105 | 3589 | bwr
NCONUML | cln13 | 19538.3161 | 10 | cln
COMMERCIAL | bwa24 | 4350900.07 | 4 | bwa
COMMERCIAL | bwr32 | 11258727.4704 | 251 | bwr
RESIDENTL | bra32 | 8710928.5985 | 2041 | bra
FARM | klo14 | 681766.459 | 92 | klo
INDUSTRIAL | tt7 | 9353368.9205 | 125 | tt
RESIDENTL | wo11 | 815896.564 | 156 | wo
LIGHTING | mwl24 | 803944.3 | 2 | mwl
COMMERCIAL | bwr24 | 7860784.794 | 262 | bwr
COMMERCIAL | drn14 | 5284276.4061 | 147 | drn
NCONUML | hpk24 | 27055.52 | 10 | hpk
| cyn32 | 34865.18 | 48 | cyn
| bra23 | 7974.72 | 25 | bra
RESIDENTL | rve13 | 16767421.4281 | 3587 | rve
COMMERCIAL | bwn13 | 11531398.8601 | 263 | bwn
FARM | cln23 | 76487.94 | 5 | cln
NCONUML | ruba24 | 1482.28 | 4 | ruba
COMMERCIAL | msd1 | 4448954.738 | 126 | msd
| phm31 | 2299.25 | 4 | phm
LIGHTING | wn1 | 677520.74 | 1 | wn
COMMERCIAL | wt8 | 2125517.5597 | 71 | wt
RESIDENTL | bdl33 | 5101200.3632 | 906 | bdl
COMMERCIAL | rwt21 | 33203170.5825 | 281 | rwt
FARM |  | 15223.9488 | 53 | #REF!
| fgy13 | 16173.63 | 19 | fgy
| wt11 | 14907.843 | 20 | wt
RESIDENTL | mwl24 | 4259131.5949 | 729 | mwl
INDUSTRIAL | bwn12 | 375603.57 | 33 | bwn
| lyd12 | 10355.6 | 16 | lyd
| lyd13 | 31235.27 | 24 | lyd
| elm32 | 28931.8643 | 22 | elm
RESIDENTL | ldl13 | 20183081.1078 | 3515 | ldl
COMMERCIAL | epg14 | 4722560.1631 | 66 | epg
FARM | epg32 | 616929.8369 | 16 | epg
| smg23 | 6841.4304 | 12 | smg
NCONUML | mwl16 | 31954.29 | 10 | mwl
COMMERCIAL | ofr22 | 3955299.41 | 63 | ofr
FARM | wgl24 | 9990463.449 | 886 | wgl
COMMERCIAL | llg14 | 8402501.0583 | 280 | llg
COMMERCIAL | wgi24 | 3234685.3433 | 136 | wgi
FARM | cnr3 | 47812.597 | 17 | cnr
| epg33 | 55263.0616 | 6 | epg
INDUSTRIAL | bra24 | 1115020.317 | 14 | bra
NCONUML | wgi33 | 84992.31 | 23 | wgi
FARM | rwt15 | 1849.17 | 1 | rwt
RESIDENTL | ldl12 | 620798.3677 | 119 | ldl
INDUSTRIAL | bwr22 | 8606432.4227 | 334 | bwr
FARM | cf2 | 2033.193 | 1 | cf
NCONUML | klo14 | 36515.49 | 28 | klo
INDUSTRIAL | trc01 | 31629.57 | 2 | trc
RESIDENTL | lga21 | 9412760.8279 | 1623 | lga
RESIDENTL | wt13 | 15834142.0313 | 3223 | wt
RESIDENTL | cyn13 | 3260017.5153 | 858 | cyn
INDUSTRIAL | ofr21 | 138382.59 | 9 | ofr
NCONUML | sle32 | 22407.43 | 13 | sle
COMMERCIAL | lyd12 | 210380 | 9 | lyd
NCONUML | wyk23 | 87622.06 | 45 | wyk
| fgy33 | 11652.67 | 18 | fgy
INDUSTRIAL | hpk22 | 98414.21 | 14 | hpk
NCONUML | sle11 | 59204.61 | 19 | sle
RESIDENTL | bwr13 | 20902397.8318 | 4170 | bwr
COMMERCIAL | rwn34 | 3999387.7688 | 144 | rwn
| hpk22 | 19671.58 | 41 | hpk
FARM | klk22 | 332413.14 | 10 | klk
INDUSTRIAL | wn1 | 2988984.92 | 20 | wn
NCONUML | rwn26 | 27156.61 | 25 | rwn
| bwr33 | 13120.641 | 3 | bwr
NCONUML | mby11 | 20114.34 | 7 | mby
RESIDENTL | smg33 | 11198068.0634 | 2626 | smg
FARM | bn12 | 813334.585 | 146 | bn
FARM | bdl32 | 1026406.0127 | 170 | bdl
FARM | drn24 | 15422429 | 2 | drn
LIGHTING | cre21 | 378603.77 | 3 | cre
RESIDENTL | smg32 | 834640.09 | 219 | smg
| wt12 | 39199.7023 | 19 | wt
FARM | bwn14 | 804408.7 | 76 | bwn
NCONUML | bwr33 | 16865.43 | 3 | bwr
INDUSTRIAL | rwn22 | 12871.85 | 4 | rwn
NCONUML | drn11 | 63307.01 | 20 | drn
INDUSTRIAL | mwl13 | 228128.43 | 11 | mwl
COMMERCIAL | elm22 | 6567142.5918 | 154 | elm
FARM | trc01 | 521142.3328 | 100 | trc
COMMERCIAL | rwt14 | 11855990.576 | 301 | rwt
INDUSTRIAL | sle14 | 1780526.4437 | 64 | sle
RESIDENTL | smr24 | 17064871.7804 | 2952 | smr
FARM | bwa22 | 1586063.9755 | 254 | bwa
NCONUML | tt4 | 37478.54 | 17 | tt
| tt9 | 28146.8116 | 74 | tt
COMMERCIAL | epg34 | 4040655.8363 | 65 | epg
FARM | nrn11 | 7816.07 | 2 | nrn
LIGHTING | cpk23 | 1632459.3 | 1 | cpk
RESIDENTL | fgy31 | 4476808.4262 | 913 | fgy
COMMERCIAL | fgy33 | 6399813.6929 | 132 | fgy
| cnr2 | 20535.9245 | 15 | cnr
INDUSTRIAL | sle32 | 10933678.58 | 25 | sle
| bra13 | 120577.89 | 18 | bra
RESIDENTL | wgi23 | 12118480.0079 | 2685 | wgi
INDUSTRIAL | wn6 | 922850.6842 | 19 | wn
LIGHTING | tgn44 | 752.53 | 1 | tgn
RESIDENTL | wt8 | 8250779.9392 | 1851 | wt
COMMERCIAL | moe25 | 5695010.3572 | 176 | moe
FARM | wgi34 | 4315044.5216 | 374 | wgi
INDUSTRIAL | fgy32 | 667572.7217 | 61 | fgy
NCONUML | wo32 | 55386.46 | 14 | wo
INDUSTRIAL | lys36 | 1267258.48 | 1 | lys
| bn12 | 10728.35 | 13 | bn
NCONUML | brt11 | 10828.27 | 7 | brt
| drn21 | 27694.76 | 39 | drn
| drn24 | 16030.7 | 26 | drn
RESIDENTL | cpk23 | 11646034.7633 | 2466 | cpk
RESIDENTL | wots13 | 7948103.7952 | 1344 | wots
FARM | wgl23 | 3908847.1376 | 390 | wgl
COMMERCIAL | wyk13 | 4417313.7071 | 191 | wyk
NCONUML | klk21 | 10664.54 | 6 | klk
INDUSTRIAL | smg22 | 31514.93 | 2 | smg
RESIDENTL | wgi22 | 12719214.8315 | 3088 | wgi
| cpk13 | 49314.0333 | 41 | cpk
COMMERCIAL | bdl41 | 11311068.2286 | 367 | bdl
NCONUML | nrn12 | 43208.48 | 18 | nrn
RESIDENTL | fgy23 | 5177398.3937 | 1023 | fgy
NCONUML | brt21 | 3240.29 | 5 | brt
NCONUML | tgn31 | 2100.01 | 7 | tgn
RESIDENTL | mjg11 | 6256821.3625 | 1064 | mjg
INDUSTRIAL | lga24 | 175905.212 | 21 | lga
COMMERCIAL | moe21 | 6644337.36 | 291 | moe
INDUSTRIAL | bwn14 | 326743.47 | 17 | bwn
INDUSTRIAL | phm22 | 15545673.5732 | 29 | phm
LIGHTING | klo24 | 2201282.63 | 3 | klo
FARM | epg12 | 13782.33 | 2 | epg
INDUSTRIAL | cln14 | 247.5387 | 1 | cln
FARM | bge13 | 383352.554 | 75 | bge
NCONUML | bra14 | 25509.54 | 26 | bra
RESIDENTL | fgy24 | 17189073.2659 | 3574 | fgy
NCONUML | lyd14 | 37348.84 | 18 | lyd
FARM | fgy21 | 91303 | 9 | fgy
INDUSTRIAL | elm24 | 6476.78 | 2 | elm
FARM | bra24 | 985.88 | 1 | bra
COMMERCIAL | ldl24 | 1420329.0926 | 55 | ldl
INDUSTRIAL | wots24 | 329358.8434 | 32 | wots
| moe13 | 6325.43 | 5 | moe
COMMERCIAL | cyn14 | 5422735.5047 | 221 | cyn
LIGHTING | smg21 | 4640189.26 | 4 | smg
COMMERCIAL | tgn42 | 24454733.755 | 420 | tgn
INDUSTRIAL | lga14 | 502652.15 | 16 | lga
INDUSTRIAL | cre33 | 377497.19 | 17 | cre
FARM | ldl11 | 223383.36 | 16 | ldl
INDUSTRIAL | bn24 | 28582582.13 | 34 | bn
COMMERCIAL | tt1 | 14308038.8686 | 155 | tt
| wn3 | 30735.58 | 33 | wn
NCONUML | ldl21 | 10778.31 | 7 | ldl
NCONUML | wt6 | 188781.23 | 35 | wt
RESIDENTL | elm23 | 20356024.4153 | 3325 | elm
COMMERCIAL | drn11 | 4003224.2127 | 79 | drn
COMMERCIAL | bra34 | 7850026.49 | 9 | bra
FARM | cyn32 | 3133.97 | 2 | cyn
FARM | cpk23 | 18946.87 | 2 | cpk
FARM | wt15 | 5251.96 | 1 | wt
NCONUML | wgi32 | 95036.63 | 31 | wgi
COMMERCIAL | phm32 | 13343791.1884 | 221 | phm
COMMERCIAL | epg22 | 38007492.3668 | 89 | epg
INDUSTRIAL | wgl15 | 1553419.6108 | 26 | wgl
FARM | phm33 | 7138587.5126 | 545 | phm
LIGHTING | bra32 | 1301740.84 | 1 | bra
COMMERCIAL | bra22 | 30448240 | 1 | bra
COMMERCIAL | msd4 | 11090376.2999 | 395 | msd
COMMERCIAL | lyd14 | 7038791.6959 | 51 | lyd
| phi12 | 701365.4285 | 34 | phi
| nrn11 | 5120.38 | 9 | nrn
INDUSTRIAL | smg21 | 777155.28 | 5 | smg
NCONUML | nla31 | 5002.08 | 5 | nla
RESIDENTL | wyk13 | 19583843.7522 | 3346 | wyk
RESIDENTL | tgn41 | 6800482.2089 | 1104 | tgn
COMMERCIAL | fgy34 | 7285642.6158 | 201 | fgy
FARM | wgl11 | 5210774.8775 | 355 | wgl
FARM | tgn11 | 616949.6887 | 82 | tgn
NCONUML | wn5 | 5268.61 | 9 | wn
NCONUML | bdl42 | 6088.6 | 9 | bdl
INDUSTRIAL | hpk23 | 515987.93 | 6 | hpk
FARM | tgn44 | 47621.17 | 6 | tgn
| smr13 | 35140.976 | 19 | smr
| wgi31 | 18377.08 | 37 | wgi
NCONUML | bwr34 | 85519.21 | 30 | bwr
| bdl32 | 24365.9844 | 40 | bdl
COMMERCIAL | fgy13 | 5672167.28 | 57 | fgy
INDUSTRIAL | sle31 | 621920.2305 | 85 | sle
NCONUML | cyn23 | 72679.67 | 24 | cyn
NCONUML | hpk22 | 92149.17 | 38 | hpk
RESIDENTL | cre23 | 13902510.3441 | 3180 | cre
COMMERCIAL | lga21 | 4415159.211 | 179 | lga
| cre33 | 51988.0123 | 70 | cre
INDUSTRIAL | bra32 | 800790.5812 | 33 | bra
| rwn26 | 43959.1499 | 36 | rwn
NCONUML | ftr22 | 27457.1971 | 11 | ftr
FARM | cyn23 | 28738.28 | 3 | cyn
FARM | wn2 | 2722540.844 | 262 | wn
FARM | wots25 | 1192605.1156 | 155 | wots
COMMERCIAL | lga11 | 2601951.4442 | 115 | lga
COMMERCIAL | cnr1 | 836269.15 | 40 | cnr
RESIDENTL | cre22 | 15737441.9951 | 3931 | cre
RESIDENTL | cyn24 | 3227627.7482 | 729 | cyn
| drn14 | 42739.5968 | 43 | drn
NCONUML | wgi34 | 240.62 | 2 | wgi
COMMERCIAL | mdi1 | 200221.43 | 4 | mdi
LIGHTING | lga22 | 290997.27 | 1 | lga
RESIDENTL | sle13 | 2426821.6594 | 1643 | sle
RESIDENTL | mby12 | 3267894.3821 | 609 | mby
FARM | wgi31 | 368672.79 | 43 | wgi
INDUSTRIAL | cyn24 | 15644182.2427 | 207 | cyn
| fgy34 | 3433.61 | 11 | fgy
RESIDENTL | bge11 | 15368827.4604 | 2654 | bge
RESIDENTL | ftr12 | 3825364.7454 | 636 | ftr
| mfa21 | 17049.39 | 26 | mfa
COMMERCIAL | wgi21 | 45541.7604 | 2 | wgi
INDUSTRIAL | wo14 | 2975508 | 24 | wo
COMMERCIAL | wgl12 | 5759083.9004 | 210 | wgl
INDUSTRIAL | moe23 | 765740.5661 | 26 | moe
COMMERCIAL | hpk14 | 5487941.7 | 85 | hpk
NCONUML | tt2 | 10017.24 | 3 | tt
INDUSTRIAL | cpk13 | 1507420.269 | 6 | cpk
INDUSTRIAL | lga41 | 52440142.6 | 1 | lga
NCONUML | elm26 | 60173.53 | 25 | elm
FARM | cf1 | 12492.747 | 1 | cf
RESIDENTL | bwr32 | 11435795.4629 | 2903 | bwr
NCONUML | cln23 | 19017.15 | 5 | cln
RESIDENTL | bdl41 | 18711766.0554 | 3582 | bdl
RESIDENTL | tt4 | 9918702.5206 | 2673 | tt
NCONUML | nrn13 | 44749.68 | 14 | nrn
NCONUML | mwl12 | 43601.75 | 11 | mwl
FARM | cln12 | 30466.72 | 1 | cln
INDUSTRIAL | cpk21 | 122110.94 | 5 | cpk
NCONUML | epg11 | 2275 | 2 | epg
FARM | brt22 | 1064314.9433 | 146 | brt
NCONUML | moe21 | 60919.67 | 15 | moe
RESIDENTL | ldl22 | 4948357.507 | 1104 | ldl
INDUSTRIAL | epg22 | 206880.17 | 13 | epg
NCONUML | cln12 | 55224.6632 | 17 | cln
| wo14 | 16653.0726 | 14 | wo
INDUSTRIAL | wo13 | 14774006.15 | 3 | wo
INDUSTRIAL | wgi22 | 729700.7 | 28 | wgi
COMMERCIAL | msd2 | 2629949.014 | 87 | msd
NCONUML | ldl22 | 11421.24 | 5 | ldl
RESIDENTL | wo22 | 17812297.6729 | 4125 | wo
FARM | mwl25 | 2028215.2676 | 224 | mwl
| cln14 | 46492.03 | 68 | cln
INDUSTRIAL | smr14 | 413387.45 | 34 | smr
FARM | rwn33 | 39914.72 | 5 | rwn
NCONUML | tt7 | 28203.83 | 11 | tt
INDUSTRIAL | lga11 | 317451.8284 | 16 | lga
INDUSTRIAL | tt12 | 6074893.6495 | 86 | tt
INDUSTRIAL | rwn32 | 87972.96 | 1 | rwn
RESIDENTL | myt21 | 10899844.0445 | 1487 | myt
RESIDENTL | cyn14 | 9596207.6734 | 2758 | cyn
RESIDENTL | kms11 | 9874885.3712 | 1972 | kms
COMMERCIAL | wo32 | 9961950.2687 | 147 | wo
NCONUML | hpk21 | 96497.83 | 40 | hpk
FARM | mwl13 | 248036.6173 | 7 | mwl
RESIDENTL | smr23 | 3447913.5369 | 523 | smr
INDUSTRIAL | nla32 | 1443086.18 | 25 | nla
| rwt32 | 35174.87 | 36 | rwt
INDUSTRIAL | moe11 | 65970.59 | 6 | moe
INDUSTRIAL | wo33 | 33298223.9508 | 7 | wo
INDUSTRIAL | bra31 | 2919.84 | 1 | bra
RESIDENTL | moe15 | 9740983.6859 | 1552 | moe
RESIDENTL | moe12 | 4538532.291 | 887 | moe
INDUSTRIAL | bdl41 | 1328921.5447 | 34 | bdl
NCONUML | tt6 | 36560.52 | 20 | tt
RESIDENTL | uwy1 | 6496143.3356 | 1032 | uwy
RESIDENTL | wgi32 | 16438958.2366 | 3917 | wgi
COMMERCIAL | rwn31 | 2125446.8547 | 72 | rwn
| ldl13 | 45979.2126 | 34 | ldl
LIGHTING | hpk23 | 2010173.36 | 1 | hpk
RESIDENTL | fgy14 | 9703108.5669 | 2483 | fgy
FARM | rwn24 | 30208.83 | 4 | rwn
COMMERCIAL | wo23 | 11409957.4027 | 304 | wo
| myt12 | 115131.3847 | 34 | myt
| bge13 | 13458.3255 | 19 | bge
| sle32 | 15918.6359 | 20 | sle
FARM | epg11 | 14625.27 | 2 | epg
NCONUML | mwl21 | 34561.25 | 17 | mwl
COMMERCIAL | nrn12 | 21654160.6835 | 271 | nrn
COMMERCIAL | llg13 | 15983000.2277 | 99 | llg
| lga22 | 14116.8478 | 12 | lga
FARM | hpk11 | 14620.89 | 5 | hpk
RESIDENTL | ofr11 | 25072251.243 | 5672 | ofr
FARM | ftr12 | 9732520.1395 | 879 | ftr
RESIDENTL | epg21 | 580054.4394 | 151 | epg
FARM | bge22 | 343097.1961 | 60 | bge
COMMERCIAL | sfs1 | 1879673.1771 | 124 | sfs
| cln24 | 61460.6675 | 37 | cln
NCONUML | smg22 | 48204.28 | 25 | smg
RESIDENTL | phm34 | 11301839.7716 | 2904 | phm
RESIDENTL | phm31 | 2762476.4376 | 550 | phm
NCONUML | smr13 | 69764.68 | 26 | smr
RESIDENTL | wyk12 | 12357178.5976 | 1789 | wyk
INDUSTRIAL | sle13 | 125251.914 | 47 | sle
FARM | phm24 | 689286.43 | 52 | phm
| cre31 | 63798.4484 | 85 | cre
INDUSTRIAL | bge12 | 121322.77 | 7 | bge
FARM | wots12 | 5076.62 | 1 | wots
NCONUML | cf1 | 1922.85 | 2 | cf
RESIDENTL | wo31 | 20016820.444 | 4554 | wo
FARM | smr22 | 1275801.32 | 154 | smr
FARM | lga22 | 1443457.6222 | 105 | lga
COMMERCIAL | mwl22 | 10003347.9587 | 192 | mwl
FARM | bn24 | 2239563.0749 | 370 | bn
NCONUML | wots25 | 45798.68 | 13 | wots
NCONUML | wgi31 | 79233.36 | 21 | wgi
FARM | epg23 | 30049.96 | 2 | epg
NCONUML | klk11 | 24723.1 | 13 | klk
| mwl14 | 3593.32 | 2 | mwl
RESIDENTL | mdg1 | 4384126.608 | 684 | mdg
RESIDENTL | nrn14 | 9562152.1887 | 1877 | nrn
LIGHTING | msd4 | 139319.89 | 1 | msd
LIGHTING | sfs1 | 1558457.9 | 1 | sfs
| klo14 | 120043.1087 | 185 | klo
RESIDENTL | hpk14 | 17025183.7337 | 3944 | hpk
FARM | lga12 | 4046898.7707 | 351 | lga
COMMERCIAL | ldl14 | 12475957.7156 | 266 | ldl
RESIDENTL | bn11 | 14382992.5485 | 2912 | bn
COMMERCIAL | bdl34 | 6213094.4744 | 204 | bdl
FARM | lyd11 | 23799.7 | 3 | lyd
| mwl22 | 10189.434 | 23 | mwl
NCONUML | cf2 | 120.31 | 1 | cf
| epg32 | 18473.04 | 31 | epg
RESIDENTL | bdl34 | 21922135.2151 | 5106 | bdl
COMMERCIAL | rwn26 | 3719056.4225 | 81 | rwn
INDUSTRIAL | mby13 | 219583.33 | 2 | mby
NCONUML | fgy33 | 40029.49 | 14 | fgy
| ftr22 | 13372.1897 | 14 | ftr
NCONUML | mwl13 | 53127.87 | 17 | mwl
INDUSTRIAL | rwt32 | 132361.99 | 4 | rwt
COMMERCIAL | phm23 | 17053480.4 | 2 | phm
COMMERCIAL | bra13 | 19208526.3529 | 181 | bra
FARM | wn1 | 37241.96 | 7 | wn
FARM | bm8b33 | 1540.9 | 2 | bmb
COMMERCIAL | wt10 | 13883699.3972 | 155 | wt
INDUSTRIAL | uwy1 | 90405.23 | 3 | uwy
RESIDENTL | ldl23 | 26005181.5029 | 4084 | ldl
FARM | klo24 | 194259.84 | 22 | klo
| hpk11 | 33718.6052 | 42 | hpk
NCONUML | phm33 | 47915.862 | 19 | phm
FARM | wn6 | 4543418.3442 | 605 | wn
COMMERCIAL | cyn21 | 3633643.5973 | 195 | cyn
INDUSTRIAL | wo22 | 393144.5 | 11 | wo
RESIDENTL | tgn42 | 795534.2193 | 223 | tgn
INDUSTRIAL | mwl23 | 715134.0252 | 54 | mwl
| rwt22 | 26934.55 | 52 | rwt
COMMERCIAL | phm31 | 4117822.4369 | 32 | phm
RESIDENTL | epg22 | 39578.43 | 14 | epg
RESIDENTL | nla32 | 6559402.1513 | 1220 | nla
RESIDENTL | myt22 | 1017937.6841 | 120 | myt
| wgl15 | 30619.4 | 19 | wgl
LIGHTING | mjg11 | 68938.73 | 1 | mjg
COMMERCIAL | phi12 | 2400712.314 | 73 | phi
COMMERCIAL | rwt36 | 2264519.95 | 43 | rwt
INDUSTRIAL | wgi23 | 157973.74 | 15 | wgi
NCONUML | elm24 | 74942.52 | 25 | elm
RESIDENTL | wt10 | 3332972.5881 | 860 | wt
NCONUML | ruba22 | 360.93 | 3 | ruba
FARM | phi11 | 82538.05 | 19 | phi
| bra11 | 11169.2884 | 32 | bra
INDUSTRIAL | moe15 | 1465208.8927 | 46 | moe
| tt5 | 13084.5535 | 33 | tt
LIGHTING | elm34 | 2971413.79 | 6 | elm
FARM | rwt25 | 33966.32 | 4 | rwt
RESIDENTL | moe11 | 9711471.9521 | 1967 | moe
INDUSTRIAL | rwt22 | 12240.297 | 2 | rwt
FARM | tgn23 | 1979366.6929 | 215 | tgn
COMMERCIAL | elm34 | 4840398.0166 | 153 | elm
NCONUML | phi11 | 19831.48 | 5 | phi
NCONUML | bra13 | 31922.03 | 14 | bra
RESIDENTL | mwl11 | 7113484.1589 | 1047 | mwl
| sle14 | 9929.5555 | 28 | sle
COMMERCIAL | cpk11 | 7316179.79 | 51 | cpk
| cyn31 | 5192.9 | 11 | cyn
NCONUML | epg12 | 1563.57 | 9 | epg
| epg11 | 4794.77 | 9 | epg
INDUSTRIAL | bwa23 | 17470876.21 | 8 | bwa
FARM | cln21 | 792.83 | 1 | cln
COMMERCIAL | wn3 | 8489705.5245 | 275 | wn
COMMERCIAL | bwn12 | 29123057.9665 | 274 | bwn
NCONUML | bra23 | 28962.5293 | 21 | bra
| bge12 | 5967.8256 | 14 | bge
INDUSTRIAL | tgn12 | 464065.58 | 15 | tgn
LIGHTING | fgy31 | 1047083.29 | 1 | fgy
NCONUML | moe25 | 63582.44 | 18 | moe
NCONUML | fgy21 | 30728.13 | 12 | fgy
INDUSTRIAL | lyd11 | 151654.68 | 9 | lyd
FARM | bwn13 | 5960.02 | 1 | bwn
RESIDENTL | lga11 | 6965787.8425 | 1044 | lga
NCONUML | bwr22 | 31744.79 | 14 | bwr
COMMERCIAL | llg12 | 3977405.3306 | 115 | llg
COMMERCIAL | mfa21 | 3716072.0048 | 197 | mfa
INDUSTRIAL | phm32 | 1008.48 | 1 | phm
COMMERCIAL | nrn13 | 3605622.38 | 41 | nrn
FARM | cyn22 | 1131.4275 | 1 | cyn
INDUSTRIAL | ftr23 | 1828762.8842 | 76 | ftr
INDUSTRIAL | mfa31 | 463955.39 | 14 | mfa
INDUSTRIAL | bge11 | 395339.98 | 10 | bge
RESIDENTL | wo13 | 2691801.805 | 586 | wo
RESIDENTL | llg11 | 4969161.4408 | 709 | llg
| cpk21 | 8908.612 | 12 | cpk
INDUSTRIAL | cre23 | 238715.04 | 8 | cre
COMMERCIAL | epg33 | 43303826.6612 | 357 | epg
FARM | ofr21 | 60907.55 | 6 | ofr
COMMERCIAL | cpk22 | 8802072.7366 | 32 | cpk
NCONUML | bra24 | 34184.91 | 27 | bra
NCONUML | wn6 | 84222.69 | 35 | wn
FARM | mfa22 | 15017348.1505 | 702 | mfa
FARM | lga24 | 2675198.7919 | 323 | lga
COMMERCIAL | phi13 | 13565764.588 | 480 | phi
FARM | lga13 | 6142984.8245 | 572 | lga
NCONUML | wn2 | 74469.51 | 25 | wn
COMMERCIAL | wyk23 | 9043742.9219 | 306 | wyk
INDUSTRIAL | cyn31 | 110897.03 | 2 | cyn
RESIDENTL | wt7 | 9398293.9689 | 2293 | wt
COMMERCIAL | rwt15 | 2407529.701 | 118 | rwt
| wots11 | 29868.01 | 43 | wots
COMMERCIAL | wt12 | 9788397.4198 | 246 | wt
FARM | wots24 | 5049980.8194 | 706 | wots
COMMERCIAL | ftr22 | 3919173.7529 | 139 | ftr
INDUSTRIAL | ruba12 | 859698.6565 | 35 | ruba
| wots25 | 37134.4365 | 43 | wots
RESIDENTL | ofr24 | 14317680.0438 | 3420 | ofr
COMMERCIAL | bdl32 | 9327480.3168 | 349 | bdl
NCONUML | trc01 | 2600.11 | 1 | trc
RESIDENTL | wgi33 | 15074294.4922 | 2906 | wgi
RESIDENTL | wyk24 | 16651462.561 | 3130 | wyk
NCONUML | wn1 | 109135.95 | 32 | wn
NCONUML | fgy34 | 69468.4 | 26 | fgy
| tgn43 | 23585.3 | 37 | tgn
| bwn11 | 22540.96 | 33 | bwn
COMMERCIAL | bn11 | 11469939.8143 | 448 | bn
RESIDENTL | wn7 | 334597.06 | 81 | wn
FARM | lga23 | 6580772.0568 | 604 | lga
RESIDENTL | mby13 | 1114988.13 | 129 | mby
INDUSTRIAL | moe12 | 309363.05 | 10 | moe
NCONUML | wgl21 | 72341.71 | 26 | wgl
| rwn22 | 13422.17 | 20 | rwn
FARM | ofr13 | 1726.88 | 2 | ofr
INDUSTRIAL | smg33 | 3791.86 | 1 | smg
COMMERCIAL | cnr2 | 2241662.7301 | 123 | cnr
NCONUML | bwn13 | 114734.08 | 27 | bwn
INDUSTRIAL | tgn43 | 8336.37 | 2 | tgn
NCONUML | bra33 | 54640.5039 | 38 | bra
LIGHTING | drn23 | 137376.82 | 1 | drn
COMMERCIAL | wt11 | 6045415.4763 | 137 | wt
| wo23 | 3425.76 | 13 | wo
RESIDENTL | drn11 | 23689909.4015 | 5897 | drn
RESIDENTL | bra33 | 17227071.6094 | 3920 | bra
FARM | cre21 | 1165190.53 | 9 | cre
| wo32 | 20472.5797 | 26 | wo
NCONUML | mfa22 | 12133.93 | 8 | mfa
COMMERCIAL | fgy32 | 10874129.2215 | 316 | fgy
INDUSTRIAL | bdl33 | 6444229.03 | 34 | bdl
NCONUML | cnr3 | 880.96 | 3 | cnr
COMMERCIAL | bwr14 | 64319.73 | 1 | bwr
NCONUML | ldl11 | 15379.88 | 9 | ldl
FARM | bdl33 | 333127.23 | 48 | bdl
INDUSTRIAL | elm23 | 351538.3612 | 12 | elm
NCONUML | lga14 | 16509.29 | 6 | lga
NCONUML | rwt21 | 45520.76 | 13 | rwt
INDUSTRIAL | mwl24 | 3823292.43 | 15 | mwl
RESIDENTL | epg14 | 8906284.5994 | 2218 | epg
NCONUML | drn21 | 11559.57 | 6 | drn
FARM | ldl21 | 4274.77 | 1 | ldl
| lga14 | 13272.15 | 11 | lga
LIGHTING | wo22 | 1145144.2306 | 3 | wo
LIGHTING | bdl33 | 755365.47 | 1 | bdl
INDUSTRIAL | lga12 | 340570.559 | 7 | lga
RESIDENTL | ofr23 | 20573594.8025 | 3065 | ofr
LIGHTING | tgn12 | 393.8997 | 1 | tgn
RESIDENTL | fgy32 | 4718000.0914 | 1180 | fgy
COMMERCIAL | moe11 | 6876107.6583 | 169 | moe
COMMERCIAL | wgl13 | 16726185.3211 | 289 | wgl
COMMERCIAL | cre22 | 19152716.1468 | 212 | cre
RESIDENTL | drn12 | 16081122.8597 | 3986 | drn
COMMERCIAL | mfa23 | 8005013.26 | 78 | mfa
| cln13 | 39224.5517 | 61 | cln
INDUSTRIAL | mfa22 | 1793714.26 | 36 | mfa
LIGHTING | smr23 | 37560.88 | 1 | smr
RESIDENTL | rwn32 | 6727398.7344 | 1603 | rwn
FARM | lga14 | 4550189.1065 | 436 | lga
| cln12 | 24735.6225 | 51 | cln
COMMERCIAL | kms11 | 4936701.5866 | 120 | kms
RESIDENTL | smr14 | 10997106.9114 | 1697 | smr
| epg13 | 194183.3358 | 102 | epg
| brt21 | 9723.1397 | 7 | brt
INDUSTRIAL | drn12 | 10032.09 | 2 | drn
| tt7 | 34871.95 | 3 | tt
INDUSTRIAL | wots25 | 7153785.931 | 7 | wots
FARM | tgn43 | 14451.81 | 2 | tgn
NCONUML | ldl14 | 38917.21 | 26 | ldl
INDUSTRIAL | brt21 | 238786.6 | 10 | brt
| llg11 | 8477.8 | 10 | llg
RESIDENTL | wgi24 | 12721878.952 | 3596 | wgi
RESIDENTL | cyn21 | 10508542.767 | 2257 | cyn
INDUSTRIAL | bra11 | 3982632.29 | 3 | bra
INDUSTRIAL | phi11 | 184139.3994 | 13 | phi
| hpk24 | 8609.4373 | 14 | hpk
NCONUML | ldl13 | 24965.12 | 22 | ldl
RESIDENTL | hpk21 | 20637351.8958 | 5254 | hpk
RESIDENTL | wgl13 | 19626090.0794 | 4751 | wgl
COMMERCIAL | elm21 | 12124007.57 | 258 | elm
COMMERCIAL | wt13 | 23168272.4303 | 498 | wt
| hpk23 | 55023.71 | 41 | hpk
COMMERCIAL | mdg1 | 1157212.0402 | 52 | mdg
NCONUML | wt11 | 64055.27 | 25 | wt
NCONUML | phm31 | 9383.328 | 4 | phm
COMMERCIAL | bge23 | 4904566.2339 | 176 | bge
NCONUML | smg23 | 17942.69 | 11 | smg
| mwl16 | 4764.4783 | 12 | mwl
COMMERCIAL | hpk12 | 20352329.5415 | 361 | hpk
RESIDENTL | ruba24 | 4395729.6843 | 894 | ruba
COMMERCIAL | nla32 | 3390681.6399 | 175 | nla
NCONUML | lyd12 | 44439.84 | 9 | lyd
| cln22 | 289385.5413 | 85 | cln
NCONUML | cpk21 | 53769.1 | 26 | cpk
| ruba22 | 8482.6526 | 15 | ruba
COMMERCIAL | myt22 | 191990.12 | 18 | myt
RESIDENTL | mby11 | 5261006.6685 | 922 | mby
RESIDENTL | rwn26 | 21195116.3973 | 2454 | rwn
| rwt31 | 14608.62 | 19 | rwt
INDUSTRIAL | epg35 | 1615230.05 | 4 | epg
| bge23 | 30837.693 | 28 | bge
NCONUML | bdl34 | 70291.97 | 25 | bdl
NCONUML | ofr13 | 30258.73 | 11 | ofr
| klk11 | 25230.2094 | 21 | klk
NCONUML | bn12 | 1241.66 | 2 | bn
COMMERCIAL | wgi32 | 5461052.6827 | 195 | wgi
NCONUML | ldl12 | 45990.38 | 14 | ldl
INDUSTRIAL | bra23 | 3394433.4433 | 42 | bra
| wo33 | 4138.8 | 1 | wo
NCONUML | myt12 | 33269.22 | 16 | myt
INDUSTRIAL | ldl11 | 1468879.69 | 10 | ldl
RESIDENTL | msd1 | 8481569.4252 | 1750 | msd
NCONUML | bn11 | 57126.91 | 28 | bn
INDUSTRIAL | ftr12 | 2824402.5 | 31 | ftr
INDUSTRIAL | hpk11 | 29483.41 | 8 | hpk
NCONUML | epg33 | 5589.26 | 2 | epg
COMMERCIAL | wo31 | 10532525.1457 | 139 | wo
| wgl21 | 38182.04 | 53 | wgl
| bge22 | 25062.3495 | 31 | bge
RESIDENTL | tt1 | 171030.69 | 8 | tt
INDUSTRIAL | bwr34 | 134229.36 | 26 | bwr
COMMERCIAL | bra33 | 14409139.6368 | 303 | bra
COMMERCIAL | bdl44 | 4495186.894 | 197 | bdl
| bwn13 | 12482.8878 | 14 | bwn
NCONUML | wn3 | 40552.61 | 16 | wn
NCONUML | smr24 | 41055.27 | 16 | smr
INDUSTRIAL | mwl14 | 4499194.0326 | 50 | mwl
| wots24 | 36833.8626 | 36 | wots
NCONUML | wt12 | 74491.29 | 36 | wt
COMMERCIAL | smg31 | 17181337.4 | 81 | smg
FARM | lyd13 | 146611.14 | 18 | lyd
NCONUML | wots12 | 53576.05 | 15 | wots
INDUSTRIAL | fgy12 | 30820.7097 | 2 | fgy
FARM | myt12 | 4025860.4278 | 600 | myt
INDUSTRIAL | cyn22 | 204983.76 | 12 | cyn
COMMERCIAL | cyn33 | 3196035.4476 | 122 | cyn
COMMERCIAL | mby12 | 1853426.4391 | 89 | mby
NCONUML | tgn43 | 111938.06 | 34 | tgn
NCONUML | wo11 | 17571.55 | 5 | wo
INDUSTRIAL | epg12 | 1405424.52 | 3 | epg
| cf2 | 30699.57 | 2 | cf
COMMERCIAL | llg11 | 3213282.749 | 85 | llg
LIGHTING | rwn24 | 1936572.72 | 3 | rwn
INDUSTRIAL | cln24 | 15633.29 | 3 | cln
FARM | sle31 | 4999785.6618 | 315 | sle
INDUSTRIAL | cf1 | 129164.746 | 4 | cf
| ruba12 | 126134.0367 | 24 | ruba
| bwr12 | 18318.3952 | 15 | bwr
FARM | elm32 | 382389.8968 | 32 | elm
| ofr21 | 113717.1 | 52 | ofr
INDUSTRIAL | wn2 | 282430.54 | 13 | wn
NCONUML | bge22 | 82280.88 | 49 | bge
NCONUML | cnr2 | 33661.17 | 17 | cnr
NCONUML | wots13 | 10386.18 | 6 | wots
FARM | elm24 | 39172.3194 | 4 | elm
COMMERCIAL | nrn14 | 6896476.1265 | 116 | nrn
NCONUML | ruba12 | 27603.68 | 16 | ruba
NCONUML | hpk13 | 50290.3 | 16 | hpk
NCONUML | bra11 | 44798.92 | 35 | bra
| rwt21 | 23376.2409 | 6 | rwt
RESIDENTL | drn23 | 20613814.4846 | 2434 | drn
RESIDENTL | rwt36 | 2676215.9999 | 821 | rwt
RESIDENTL | llg13 | 6857833.0372 | 1230 | llg
COMMERCIAL | wyk12 | 4295149.2844 | 131 | wyk
INDUSTRIAL | ofr13 | 1622296.11 | 21 | ofr
| bra14 | 30334.7783 | 42 | bra
INDUSTRIAL | tgn11 | 3321263.75 | 18 | tgn
LIGHTING | mby13 | 9944.78 | 1 | mby
RESIDENTL | cln11 | 39284605.9906 | 12154 | cln
COMMERCIAL | drn22 | 10741065.2473 | 246 | drn
RESIDENTL | wo32 | 11244170.0715 | 2343 | wo
| bra33 | 27895.4569 | 47 | bra
COMMERCIAL | epg21 | 21867278.1603 | 75 | epg
INDUSTRIAL | cre21 | 293542.6 | 2 | cre
RESIDENTL | bwr24 | 1834966.95 | 415 | bwr
RESIDENTL | hpk13 | 8888406.848 | 2283 | hpk
NCONUML | moe13 | 240.62 | 2 | moe
RESIDENTL | mwl12 | 3605926.3697 | 887 | mwl
| elm24 | 29520.3106 | 27 | elm
COMMERCIAL | tgn31 | 5251765.7474 | 163 | tgn
| rwt25 | 17882.0217 | 23 | rwt
RESIDENTL | moe21 | 9438147.1697 | 1978 | moe
COMMERCIAL | mjg11 | 16973320.0649 | 258 | mjg
COMMERCIAL | moe22 | 1619971.835 | 34 | moe
NCONUML | cpk13 | 44472.2623 | 32 | cpk
| phi11 | 13149.9006 | 9 | phi
FARM | cyn11 | 2814.65 | 1 | cyn
FARM | cyn24 | 25049.8 | 2 | cyn
FARM | drn13 | 379220.8035 | 25 | drn
COMMERCIAL | mwe236 | 663523.2 | 21 | mwe
INDUSTRIAL | phm24 | 35612.08 | 4 | phm
INDUSTRIAL | bge22 | 36211.2493 | 9 | bge
RESIDENTL | cnr1 | 478523.9112 | 104 | cnr
| lga24 | 10918.35 | 11 | lga
NCONUML | sle14 | 98131.7526 | 34 | sle
NCONUML | tt5 | 14462.54 | 12 | tt
| epg12 | 53720.6497 | 70 | epg
NCONUML | kms11 | 42647.24 | 13 | kms
FARM | elm23 | 38507.8 | 8 | elm
COMMERCIAL | cyn12 | 12045879.7132 | 241 | cyn
INDUSTRIAL | fgy23 | 1420677.79 | 11 | fgy
COMMERCIAL | mfa14 | 259168.13 | 17 | mfa
| bra31 | 49797.7422 | 13 | bra
COMMERCIAL | mwl12 | 1780079.4127 | 78 | mwl
| bwr22 | 2405.71 | 25 | bwr
INDUSTRIAL | fgy24 | 415478.9 | 15 | fgy
COMMERCIAL | hpk13 | 9763023.5697 | 134 | hpk
| cyn22 | 22272.33 | 22 | cyn
| ldl21 | 13369.5383 | 42 | ldl
| wt6 | 17591.4373 | 23 | wt
RESIDENTL | wn4 | 11276854.4814 | 2349 | wn
FARM | mwl14 | 451834.7532 | 54 | mwl
RESIDENTL | bm8b31 | 357131.6719 | 111 | bmb
NCONUML | cyn14 | 48577.9677 | 22 | cyn
FARM | cre32 | 5136.47 | 1 | cre
FARM | bwr34 | 4550.33 | 1 | bwr
RESIDENTL | llg14 | 14855712.1657 | 2170 | llg
FARM | smg33 | 29400.19 | 7 | smg
RESIDENTL | drn22 | 21996972.8148 | 3999 | drn
NCONUML | elm32 | 42948.38 | 25 | elm
INDUSTRIAL | klo14 | 587332.99 | 17 | klo
| tgn11 | 22256.53 | 32 | tgn
INDUSTRIAL | tgn44 | 4536032.57 | 9 | tgn
COMMERCIAL | ldl23 | 15994398.5627 | 272 | ldl
| wn6 | 146062.0009 | 59 | wn
COMMERCIAL | tt2 | 18806104.6367 | 399 | tt
COMMERCIAL | brt11 | 4047117.81 | 129 | brt
NCONUML | llg14 | 65195.01 | 40 | llg
FARM | fgy24 | 95940.3 | 9 | fgy
NCONUML | fgy14 | 61562.37 | 33 | fgy
COMMERCIAL | rve12 | 3272242.91 | 54 | rve
INDUSTRIAL | cpk23 | 208291.634 | 5 | cpk
| lga23 | 41697.3391 | 21 | lga
INDUSTRIAL | yn38 | 642769.3081 | 6 | yn
COMMERCIAL | bwa21 | 7920817.52 | 6 | bwa
INDUSTRIAL | elm25 | 2097.04 | 1 | elm
COMMERCIAL | wots13 | 3416108.1488 | 213 | wots
FARM | wgi22 | 191494.2501 | 24 | wgi
NCONUML | fgy13 | 27847.71 | 7 | fgy
| bra24 | 9840.15 | 27 | bra
FARM | ofr14 | 100163.6258 | 21 | ofr
NCONUML | nrn11 | 16820.36 | 5 | nrn
RESIDENTL | smg31 | 12434679.8443 | 2879 | smg
COMMERCIAL | smr24 | 15083854.4686 | 348 | smr
| lyd11 | 12152.66 | 25 | lyd
INDUSTRIAL | bra12 | 1282907.1727 | 55 | bra
FARM | wgl15 | 3297105.6723 | 233 | wgl
INDUSTRIAL | msd1 | 544058.7154 | 15 | msd
| epg31 | 13971.3347 | 31 | epg
INDUSTRIAL | wgl23 | 572354.5027 | 44 | wgl
INDUSTRIAL | cpk12 | 343353.79 | 14 | cpk
INDUSTRIAL | mfa34 | 4790944.63 | 37 | mfa
| wn2 | 65478.1843 | 60 | wn
INDUSTRIAL | drn23 | 222019.33 | 21 | drn
| klo11 | 24997.4 | 1 | klo
COMMERCIAL | cyn13 | 11562540.4133 | 213 | cyn
| tgn44 | 15598.29 | 27 | tgn
| wn1 | 5093 | 9 | wn
NCONUML | wots24 | 22958.48 | 11 | wots
RESIDENTL | ftr21 | 5974099.1685 | 1654 | ftr
NCONUML | wgl11 | 116770.29 | 32 | wgl
FARM | phm22 | 2513172.8482 | 159 | phm
| mfa22 | 25912.0235 | 15 | mfa
| tt2 | 5693.01 | 1 | tt
RESIDENTL | cyn12 | 11384819.6049 | 2642 | cyn
COMMERCIAL | mby11 | 1920906.95 | 83 | mby
RESIDENTL | bdl42 | 7579399.6648 | 1528 | bdl
COMMERCIAL | sle11 | 16789466.3124 | 430 | sle
COMMERCIAL | bdl42 | 3935066.2305 | 228 | bdl
NCONUML | rwn22 | 25304.89 | 19 | rwn
INDUSTRIAL | cre32 | 1414910.91 | 33 | cre
INDUSTRIAL | bwn11 | 121807.37 | 8 | bwn
NCONUML | smr22 | 29006.3 | 13 | smr
RESIDENTL | phm24 | 12991887.5254 | 2975 | phm
RESIDENTL | phm21 | 5600884.0097 | 1319 | phm
NCONUML | ldl23 | 93357.12 | 44 | ldl
RESIDENTL | ldl24 | 19255310.9766 | 3964 | ldl
INDUSTRIAL | bra21 | 9682528.358 | 10 | bra
| sle31 | 21276.5675 | 34 | sle
| myt11 | 11671.01 | 10 | myt
RESIDENTL | elm21 | 10927220.6891 | 2208 | elm
COMMERCIAL | epg13 | 13081700.0195 | 121 | epg
COMMERCIAL | hpk21 | 6771211.022 | 80 | hpk
NCONUML | bwr12 | 55323.1848 | 22 | bwr
| trc01 | 7370.1419 | 1 | trc
| epg35 | 12733.43 | 3 | epg
INDUSTRIAL | bge21 | 30163.23 | 3 | bge
RESIDENTL | tgn31 | 10330935.5842 | 1504 | tgn
COMMERCIAL | moe23 | 8180066.6029 | 204 | moe
FARM | bra21 | 5211.11 | 2 | bra
LIGHTING | llg12 | 9573.66 | 1 | llg
RESIDENTL | bdl31 | 18828777.9984 | 3534 | bdl
COMMERCIAL | nla31 | 1365542.8767 | 73 | nla
INDUSTRIAL | klo24 | 421040.3606 | 14 | klo
FARM | bdl43 | 35833.9 | 4 | bdl
FARM | cyn31 | 3324.08 | 1 | cyn
FARM | sle14 | 508528.62 | 59 | sle
FARM | fgy34 | 3609.3 | 1 | fgy
RESIDENTL | elm26 | 19204314.084 | 3128 | elm
COMMERCIAL | ldl13 | 4974121.0157 | 271 | ldl
NCONUML | tgn42 | 32526.3 | 9 | tgn
RESIDENTL | nrn13 | 11128338.9236 | 2708 | nrn
| drn13 | 33230.29 | 35 | drn
RESIDENTL | mfa14 | 15628.16 | 8 | mfa
RESIDENTL | rwt14 | 5266292.5405 | 1232 | rwt
FARM | ftr23 | 7584335.745 | 587 | ftr
FARM | moe12 | 2890738.1544 | 266 | moe
RESIDENTL | klk21 | 6022162.144 | 692 | klk
COMMERCIAL | bn22 | 11917129.8815 | 407 | bn
COMMERCIAL | cln13 | 10498926.3291 | 102 | cln
INDUSTRIAL | cln11 | 955300.36 | 11 | cln
FARM | bge11 | 1450445.3683 | 132 | bge
| mwl25 | 368.2898 | 2 | mwl
| rwn33 | 13688.96 | 19 | rwn
| bdl43 | 33766.9817 | 15 | bdl
NCONUML | cln14 | 95979.5703 | 31 | cln
NCONUML | lga24 | 7306.35 | 4 | lga
| bn23 | 36133.4118 | 23 | bn
| ofr14 | 18460.3638 | 32 | ofr
FARM | wo14 | 29381.84 | 3 | wo
FARM | cln24 | 15169.45 | 1 | cln
FARM | smg21 | 2813.13 | 1 | smg
FARM | uwy1 | 50419.26 | 6 | uwy
RESIDENTL | cpk11 | 18255270.9798 | 3705 | cpk
INDUSTRIAL | rwn34 | 151721.8975 | 12 | rwn
FARM | mfa34 | 8352796.4311 | 398 | mfa
INDUSTRIAL | cyn23 | 283668.3977 | 39 | cyn
COMMERCIAL | cln23 | 7919442.4187 | 94 | cln
| rwn24 | 145239.1574 | 36 | rwn
INDUSTRIAL | cln21 | 91173.7471 | 8 | cln
INDUSTRIAL | wots23 | 9771996.01 | 2 | wots
COMMERCIAL | ofr23 | 7962081.4442 | 137 | ofr
FARM | cln11 | 5358747.3528 | 175 | cln
INDUSTRIAL | epg23 | 1603069.098 | 49 | epg
NCONUML | elm33 | 106570.09 | 33 | elm
| tt6 | 16214.4725 | 50 | tt
NCONUML | lga12 | 120.31 | 1 | lga
RESIDENTL | moe25 | 15202048.016 | 3044 | moe
RESIDENTL | moe22 | 6183768.6959 | 1343 | moe
RESIDENTL | mfa23 | 1535883.9368 | 206 | mfa
FARM | rwn22 | 76017.25 | 13 | rwn
COMMERCIAL | fgy31 | 26687.08 | 5 | fgy
RESIDENTL | elm33 | 17751529.9107 | 3238 | elm
COMMERCIAL | ldl22 | 7642772.3181 | 272 | ldl
NCONUML | llg11 | 13058.17 | 7 | llg
| ruba24 | 72607.09 | 10 | ruba
FARM | rwt32 | 21924.18 | 3 | rwt
FARM | ruba12 | 5735958.293 | 534 | ruba
FARM | brt21 | 526055.8565 | 65 | brt
| rwt15 | 24735.76 | 50 | rwt
NCONUML | bge13 | 40077 | 45 | bge
COMMERCIAL | klk21 | 1344972.0506 | 75 | klk
INDUSTRIAL | msd4 | 532825.24 | 27 | msd
| mwl21 | 2371.576 | 7 | mwl
RESIDENTL | wt9 | 13126762.7947 | 2901 | wt
FARM | wgi23 | 957555.9102 | 143 | wgi
| wgl24 | 12928.4076 | 27 | wgl
NCONUML | tgn11 | 50804.93 | 14 | tgn
LIGHTING | hpk22 | 402155.12 | 2 | hpk
INDUSTRIAL | wt13 | 198794.34 | 24 | wt
LIGHTING | wots24 | 69082.45 | 1 | wots
| ofr13 | 25120.5182 | 29 | ofr
| cre21 | 98632.2224 | 69 | cre
| smg22 | 13378.71 | 23 | smg
COMMERCIAL | tt4 | 4770691.1401 | 169 | tt
COMMERCIAL | elm26 | 2765254.86 | 47 | elm
NCONUML | bwa22 | 120.31 | 1 | bwa
| cyn23 | 386495.78 | 52 | cyn
INDUSTRIAL | nla34 | 227255.6563 | 13 | nla
FARM | mwl22 | 63.01 | 1 | mwl
| cf1 | 5771.13 | 3 | cf
NCONUML | cpk22 | 15413.02 | 10 | cpk
NCONUML | lyd13 | 28195.47 | 10 | lyd
NCONUML | cre31 | 35482.06 | 18 | cre
COMMERCIAL | wo11 | 6006584.4175 | 54 | wo
INDUSTRIAL | wt7 | 2382042.5333 | 25 | wt
| bwr34 | 19530.96 | 64 | bwr
NCONUML | bge23 | 57838.96 | 34 | bge
INDUSTRIAL | tgn23 | 187420.5 | 24 | tgn
RESIDENTL | cyn33 | 17836008.3498 | 3662 | cyn
RESIDENTL | nla34 | 7124747.0562 | 1408 | nla
| wgl11 | 21820.8596 | 38 | wgl
COMMERCIAL | bn12 | 3658135.6563 | 31 | bn
| mwl13 | 7054.2121 | 17 | mwl
COMMERCIAL | rwt26 | 65754589.65 | 1 | rwt
FARM | wt9 | 2789.4 | 1 | wt
RESIDENTL | bdl44 | 10906570.4152 | 1766 | bdl
FARM | cre33 | 2156267.3416 | 81 | cre
COMMERCIAL | wgl21 | 7364849.9167 | 150 | wgl
COMMERCIAL | wn5 | 3727109.367 | 208 | wn
NCONUML | mwl22 | 81020 | 27 | mwl
NCONUML | bn24 | 14677.57 | 9 | bn
| smr22 | 9887.67 | 15 | smr
|  | 8782.36 | 2 | #REF!
RESIDENTL | sle11 | 5311421.2716 | 1344 | sle
RESIDENTL | nw13 | 126364.0108 | 18 | nw
RESIDENTL | ftr23 | 12909653.9148 | 2620 | ftr
COMMERCIAL | mwl11 | 1278518.3133 | 72 | mwl
LIGHTING | llg13 | 66328.6913 | 1 | llg
NCONUML | klk22 | 2600.11 | 1 | klk
RESIDENTL | wyk23 | 22445865.182 | 3391 | wyk
COMMERCIAL | wt6 | 6354339.6482 | 191 | wt
RESIDENTL | brt11 | 6592458.6386 | 1001 | brt
NCONUML | tt9 | 66916.75 | 41 | tt
FARM | smr14 | 4406259.38 | 487 | smr
NCONUML | epg32 | 55568.91 | 13 | epg
RESIDENTL | rwn31 | 17135173.2235 | 2210 | rwn
| phm33 | 20993.1171 | 27 | phm
NCONUML | myt11 | 6079.5 | 6 | myt
RESIDENTL | nrn12 | 2807836.1314 | 591 | nrn
COMMERCIAL | mwl16 | 411566.3345 | 42 | mwl
INDUSTRIAL | lga23 | 1068068.6578 | 23 | lga
COMMERCIAL | ldl12 | 15390056.6509 | 380 | ldl
FARM | nla34 | 624678.3932 | 78 | nla
COMMERCIAL | rve13 | 1685040.429 | 44 | rve
NCONUML | drn24 | 11009.3526 | 4 | drn
COMMERCIAL | myt21 | 6919383.7104 | 251 | myt
FARM | moe13 | 3478506.4958 | 306 | moe
COMMERCIAL | mwl21 | 9182796.6603 | 240 | mwl
NCONUML | wgl15 | 97647.0301 | 36 | wgl
| bwn14 | 31300.22 | 31 | bwn
RESIDENTL | cpk22 | 8203984.593 | 1482 | cpk
RESIDENTL | rve12 | 17634581.2748 | 3656 | rve
RESIDENTL | phi13 | 17016004.0328 | 4317 | phi
RESIDENTL | hpk12 | 5058413.1519 | 1238 | hpk
COMMERCIAL | ruba24 | 4555190.3466 | 105 | ruba
FARM | cln14 | 51639.06 | 13 | cln
INDUSTRIAL | wt9 | 148098.11 | 5 | wt
| smg21 | 44014.37 | 27 | smg
INDUSTRIAL | smr23 | 883845.12 | 6 | smr

## Forecast - Summer
Forecasting Application - 13/10/2025
asset_type | asset | extremum | scenario | demand_year | season | poe | customer_count | pv_capacity | value | forecast_round | unit | region
zone_sub | cln | maximum |  | 2022 | Summer | 50 | 38619 | 72.2578 | 77.9086 | 202503 | MVA | central
zone_sub | cln | maximum |  | 2022 | Summer | 10 | 38619 | 72.2578 | 91.3183 | 202503 | MVA | central
zone_sub | cln | maximum |  | 2023 | Summer | 10 | 41429 | 81.3604 | 97.5884 | 202503 | MVA | central
zone_sub | cln | maximum |  | 2023 | Summer | 50 | 41429 | 81.3604 | 83.3369 | 202503 | MVA | central
zone_sub | cln | maximum |  | 2024 | Summer | 10 | 44846 | 94.6588 | 104.9463 | 202503 | MVA | central
zone_sub | cln | maximum |  | 2024 | Summer | 50 | 44846 | 94.6588 | 89.7351 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2025 | Summer | 10 |  |  | 119.6766 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2025 | Summer | 50 |  |  | 104.3341 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2026 | Summer | 10 |  |  | 124.2514 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2026 | Summer | 50 |  |  | 108.3435 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2027 | Summer | 10 |  |  | 128.0364 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2027 | Summer | 50 |  |  | 111.4611 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2028 | Summer | 10 |  |  | 131.3686 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2028 | Summer | 50 |  |  | 115.2173 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2029 | Summer | 10 |  |  | 136.7682 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2029 | Summer | 50 |  |  | 119.0984 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2030 | Summer | 10 |  |  | 141.634 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2030 | Summer | 50 |  |  | 123.2461 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2031 | Summer | 10 |  |  | 148.4809 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2031 | Summer | 50 |  |  | 128.0275 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2032 | Summer | 10 |  |  | 155.6302 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2032 | Summer | 50 |  |  | 133.6994 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2033 | Summer | 10 |  |  | 161.4365 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2033 | Summer | 50 |  |  | 139.0092 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2034 | Summer | 10 |  |  | 166.8996 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2034 | Summer | 50 |  |  | 144.6013 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2035 | Summer | 10 |  |  | 175.1342 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2035 | Summer | 50 |  |  | 154.2938 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2036 | Summer | 10 |  |  | 181.0486 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2036 | Summer | 50 |  |  | 157.43 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2037 | Summer | 10 |  |  | 187.0195 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2037 | Summer | 50 |  |  | 163.5566 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2038 | Summer | 10 |  |  | 193.3671 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2038 | Summer | 50 |  |  | 168.1999 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2039 | Summer | 10 |  |  | 192.0421 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2039 | Summer | 50 |  |  | 167.0472 | 202503 | MVA | central
zone_sub | cre | maximum |  | 2022 | Summer | 10 | 24937 | 39.5122 | 71.3044 | 202503 | MVA | central
zone_sub | cre | maximum |  | 2022 | Summer | 50 | 24937 | 39.5122 | 64.1683 | 202503 | MVA | central
zone_sub | cre | maximum |  | 2023 | Summer | 10 | 25835 | 43.8704 | 73.6781 | 202503 | MVA | central
zone_sub | cre | maximum |  | 2023 | Summer | 50 | 25835 | 43.8704 | 65.8328 | 202503 | MVA | central
zone_sub | cre | maximum |  | 2024 | Summer | 10 | 26314 | 48.9572 | 74.7994 | 202503 | MVA | central
zone_sub | cre | maximum |  | 2024 | Summer | 50 | 26314 | 48.9572 | 66.0879 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2025 | Summer | 10 |  |  | 89.8342 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2025 | Summer | 50 |  |  | 80.6612 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2026 | Summer | 10 |  |  | 90.653 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2026 | Summer | 50 |  |  | 81.4056 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2027 | Summer | 10 |  |  | 89.7773 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2027 | Summer | 50 |  |  | 80.6131 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2028 | Summer | 10 |  |  | 94.9573 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2028 | Summer | 50 |  |  | 85.9509 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2029 | Summer | 10 |  |  | 94.8385 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2029 | Summer | 50 |  |  | 85.6114 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2030 | Summer | 10 |  |  | 96.1186 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2030 | Summer | 50 |  |  | 85.7941 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2031 | Summer | 10 |  |  | 97.2062 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2031 | Summer | 50 |  |  | 86.4866 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2032 | Summer | 10 |  |  | 98.0786 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2032 | Summer | 50 |  |  | 87.2925 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2033 | Summer | 10 |  |  | 98.8781 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2033 | Summer | 50 |  |  | 88.2343 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2034 | Summer | 10 |  |  | 99.6475 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2034 | Summer | 50 |  |  | 88.9575 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2035 | Summer | 10 |  |  | 99.2707 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2035 | Summer | 50 |  |  | 89.8044 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2036 | Summer | 10 |  |  | 99.9981 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2036 | Summer | 50 |  |  | 89.5675 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2037 | Summer | 10 |  |  | 101.1509 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2037 | Summer | 50 |  |  | 90.5821 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2038 | Summer | 10 |  |  | 101.3208 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2038 | Summer | 50 |  |  | 90.3196 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2039 | Summer | 10 |  |  | 99.6095 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2039 | Summer | 50 |  |  | 88.5146 | 202503 | MVA | central
zone_sub | epg | maximum |  | 2022 | Summer | 10 | 29371 | 40.0067 | 87.2498 | 202503 | MVA | central
zone_sub | epg | maximum |  | 2022 | Summer | 50 | 29371 | 40.0067 | 72.9666 | 202503 | MVA | central
zone_sub | epg | maximum |  | 2023 | Summer | 10 | 30422 | 45.1511 | 90.3071 | 202503 | MVA | central
zone_sub | epg | maximum |  | 2023 | Summer | 50 | 30422 | 45.1511 | 75.7012 | 202503 | MVA | central
zone_sub | epg | maximum |  | 2024 | Summer | 10 | 32118 | 51.557 | 95.8895 | 202503 | MVA | central
zone_sub | epg | maximum |  | 2024 | Summer | 50 | 32118 | 51.557 | 79.9844 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2025 | Summer | 10 |  |  | 109.0669 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2025 | Summer | 50 |  |  | 92.5622 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2026 | Summer | 10 |  |  | 118.5447 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2026 | Summer | 50 |  |  | 101.6723 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2027 | Summer | 10 |  |  | 121.4869 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2027 | Summer | 50 |  |  | 104.4042 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2028 | Summer | 10 |  |  | 119.8786 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2028 | Summer | 50 |  |  | 102.6031 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2029 | Summer | 10 |  |  | 121.9204 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2029 | Summer | 50 |  |  | 105.5757 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2030 | Summer | 10 |  |  | 124.6444 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2030 | Summer | 50 |  |  | 106.371 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2031 | Summer | 10 |  |  | 127.5507 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2031 | Summer | 50 |  |  | 110.1341 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2032 | Summer | 10 |  |  | 131.8742 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2032 | Summer | 50 |  |  | 112.2581 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2033 | Summer | 10 |  |  | 136.3355 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2033 | Summer | 50 |  |  | 113.9316 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2034 | Summer | 10 |  |  | 140.9437 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2034 | Summer | 50 |  |  | 117.5793 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2035 | Summer | 10 |  |  | 144.5914 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2035 | Summer | 50 |  |  | 120.4726 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2036 | Summer | 50 |  |  | 128.0797 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2036 | Summer | 10 |  |  | 149.6115 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2037 | Summer | 10 |  |  | 152.9797 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2037 | Summer | 50 |  |  | 129.922 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2038 | Summer | 10 |  |  | 155.1715 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2038 | Summer | 50 |  |  | 132.5568 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2039 | Summer | 10 |  |  | 152.1644 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2039 | Summer | 50 |  |  | 125.7761 | 202503 | MVA | central
zone_sub | klo | maximum |  | 2022 | Summer | 10 | 14879 | 23.0226 | 53.5677 | 202503 | MVA | central
zone_sub | klo | maximum |  | 2022 | Summer | 50 | 14879 | 23.0226 | 41.9423 | 202503 | MVA | central
zone_sub | klo | maximum |  | 2023 | Summer | 10 | 17175 | 27.7177 | 61.121 | 202503 | MVA | central
zone_sub | klo | maximum |  | 2023 | Summer | 50 | 17175 | 27.7177 | 48.3019 | 202503 | MVA | central
zone_sub | klo | maximum |  | 2024 | Summer | 10 | 19951 | 34.2052 | 70.1897 | 202503 | MVA | central
zone_sub | klo | maximum |  | 2024 | Summer | 50 | 19951 | 34.2052 | 55.7613 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2025 | Summer | 10 |  |  | 83.6879 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2025 | Summer | 50 |  |  | 68.2523 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2026 | Summer | 10 |  |  | 94.1984 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2026 | Summer | 50 |  |  | 77.9353 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2027 | Summer | 10 |  |  | 102.4436 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2027 | Summer | 50 |  |  | 84.7194 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2028 | Summer | 10 |  |  | 118.3247 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2028 | Summer | 50 |  |  | 99.6669 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2029 | Summer | 10 |  |  | 126.3487 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2029 | Summer | 50 |  |  | 106.8624 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2030 | Summer | 10 |  |  | 135.5692 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2030 | Summer | 50 |  |  | 115.5707 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2031 | Summer | 10 |  |  | 148.561 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2031 | Summer | 50 |  |  | 127.0156 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2032 | Summer | 10 |  |  | 164.8827 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2032 | Summer | 50 |  |  | 137.8179 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2033 | Summer | 10 |  |  | 180.5841 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2033 | Summer | 50 |  |  | 151.2391 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2034 | Summer | 10 |  |  | 196.9964 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2034 | Summer | 50 |  |  | 164.8814 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2035 | Summer | 10 |  |  | 212.9758 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2035 | Summer | 50 |  |  | 181.5355 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2036 | Summer | 10 |  |  | 230.0573 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2036 | Summer | 50 |  |  | 195.8954 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2037 | Summer | 10 |  |  | 248.4456 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2037 | Summer | 50 |  |  | 212.2991 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2038 | Summer | 10 |  |  | 266.5409 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2038 | Summer | 50 |  |  | 225.6959 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2039 | Summer | 10 |  |  | 272.6357 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2039 | Summer | 50 |  |  | 228.9049 | 202503 | MVA | central
zone_sub | ofr | maximum |  | 2022 | Summer | 10 | 23246 | 35.5119 | 59.9776 | 202503 | MVA | central
zone_sub | ofr | maximum |  | 2022 | Summer | 50 | 23246 | 35.5119 | 53.856 | 202503 | MVA | central
zone_sub | ofr | maximum |  | 2023 | Summer | 10 | 24109 | 39.5748 | 62.0639 | 202503 | MVA | central
zone_sub | ofr | maximum |  | 2023 | Summer | 50 | 24109 | 39.5748 | 55.451 | 202503 | MVA | central
zone_sub | ofr | maximum |  | 2024 | Summer | 10 | 24997 | 44.4669 | 64.073 | 202503 | MVA | central
zone_sub | ofr | maximum |  | 2024 | Summer | 50 | 24997 | 44.4669 | 56.9594 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2025 | Summer | 10 |  |  | 69.589 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2025 | Summer | 50 |  |  | 61.9907 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2026 | Summer | 10 |  |  | 76.597 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2026 | Summer | 50 |  |  | 68.9791 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2027 | Summer | 10 |  |  | 81.5678 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2027 | Summer | 50 |  |  | 74.0072 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2028 | Summer | 10 |  |  | 84.5283 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2028 | Summer | 50 |  |  | 76.6284 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2029 | Summer | 10 |  |  | 86.8984 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2029 | Summer | 50 |  |  | 78.9811 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2030 | Summer | 10 |  |  | 88.8048 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2030 | Summer | 50 |  |  | 80.4506 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2031 | Summer | 10 |  |  | 90.6365 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2031 | Summer | 50 |  |  | 82.1352 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2032 | Summer | 10 |  |  | 92.2256 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2032 | Summer | 50 |  |  | 83.4813 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2033 | Summer | 10 |  |  | 92.9929 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2033 | Summer | 50 |  |  | 84.3346 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2034 | Summer | 10 |  |  | 94.1573 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2034 | Summer | 50 |  |  | 86.446 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2035 | Summer | 10 |  |  | 95.4952 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2035 | Summer | 50 |  |  | 87.894 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2036 | Summer | 10 |  |  | 96.8516 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2036 | Summer | 50 |  |  | 88.627 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2037 | Summer | 10 |  |  | 98.5806 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2037 | Summer | 50 |  |  | 90.0391 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2038 | Summer | 10 |  |  | 98.8168 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2038 | Summer | 50 |  |  | 89.5765 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2039 | Summer | 10 |  |  | 97.8239 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2039 | Summer | 50 |  |  | 88.3981 | 202503 | MVA | central
zone_sub | phm | maximum |  | 2022 | Summer | 50 | 16270 | 23.521 | 51.4174 | 202503 | MVA | central
zone_sub | phm | maximum |  | 2022 | Summer | 10 | 16270 | 23.521 | 56.9097 | 202503 | MVA | central
zone_sub | phm | maximum |  | 2023 | Summer | 10 | 16562 | 25.5412 | 57.758 | 202503 | MVA | central
zone_sub | phm | maximum |  | 2023 | Summer | 50 | 16562 | 25.5412 | 52.1386 | 202503 | MVA | central
zone_sub | phm | maximum |  | 2024 | Summer | 10 | 16854 | 27.7496 | 58.7282 | 202503 | MVA | central
zone_sub | phm | maximum |  | 2024 | Summer | 50 | 16854 | 27.7496 | 52.8621 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2025 | Summer | 10 |  |  | 75.5207 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2025 | Summer | 50 |  |  | 69.621 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2026 | Summer | 10 |  |  | 79.8845 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2026 | Summer | 50 |  |  | 74.1527 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2027 | Summer | 10 |  |  | 79.6008 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2027 | Summer | 50 |  |  | 73.9998 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2028 | Summer | 10 |  |  | 79.5894 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2028 | Summer | 50 |  |  | 73.965 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2029 | Summer | 10 |  |  | 80.0199 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2029 | Summer | 50 |  |  | 74.4648 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2030 | Summer | 10 |  |  | 81.1895 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2030 | Summer | 50 |  |  | 75.0153 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2031 | Summer | 10 |  |  | 81.9552 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2031 | Summer | 50 |  |  | 76.1566 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2032 | Summer | 10 |  |  | 82.7146 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2032 | Summer | 50 |  |  | 76.9783 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2033 | Summer | 10 |  |  | 83.6062 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2033 | Summer | 50 |  |  | 77.4148 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2034 | Summer | 10 |  |  | 84.4206 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2034 | Summer | 50 |  |  | 77.8841 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2035 | Summer | 10 |  |  | 85.2206 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2035 | Summer | 50 |  |  | 78.3211 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2036 | Summer | 10 |  |  | 85.2937 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2036 | Summer | 50 |  |  | 79.127 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2037 | Summer | 10 |  |  | 86.2309 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2037 | Summer | 50 |  |  | 80.1321 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2038 | Summer | 10 |  |  | 85.4841 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2038 | Summer | 50 |  |  | 80.0404 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2039 | Summer | 10 |  |  | 79.3417 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2039 | Summer | 50 |  |  | 73.3195 | 202503 | MVA | central
zone_sub | llg | maximum |  | 2022 | Summer | 10 | 7174 | 11.5134 | 25.3928 | 202503 | MVA | central
zone_sub | llg | maximum |  | 2022 | Summer | 50 | 7174 | 11.5134 | 23.4346 | 202503 | MVA | central
zone_sub | llg | maximum |  | 2023 | Summer | 10 | 7235 | 12.7349 | 25.4543 | 202503 | MVA | central
zone_sub | llg | maximum |  | 2023 | Summer | 50 | 7235 | 12.7349 | 23.4406 | 202503 | MVA | central
zone_sub | llg | maximum |  | 2024 | Summer | 10 | 7295 | 13.7538 | 25.544 | 202503 | MVA | central
zone_sub | llg | maximum |  | 2024 | Summer | 50 | 7295 | 13.7538 | 23.5081 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2025 | Summer | 10 |  |  | 28.7312 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2025 | Summer | 50 |  |  | 26.0976 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2026 | Summer | 10 |  |  | 33.0834 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2026 | Summer | 50 |  |  | 30.4575 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2027 | Summer | 10 |  |  | 33.0249 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2027 | Summer | 50 |  |  | 30.4247 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2028 | Summer | 10 |  |  | 33.0633 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2028 | Summer | 50 |  |  | 30.3952 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2029 | Summer | 10 |  |  | 33.1822 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2029 | Summer | 50 |  |  | 30.8677 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2030 | Summer | 10 |  |  | 33.5865 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2030 | Summer | 50 |  |  | 31.5616 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2031 | Summer | 10 |  |  | 33.8573 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2031 | Summer | 50 |  |  | 32.037 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2032 | Summer | 10 |  |  | 34.0794 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2032 | Summer | 50 |  |  | 31.4591 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2033 | Summer | 10 |  |  | 34.1121 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2033 | Summer | 50 |  |  | 31.5166 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2034 | Summer | 10 |  |  | 34.3124 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2034 | Summer | 50 |  |  | 31.792 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2035 | Summer | 10 |  |  | 34.3834 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2035 | Summer | 50 |  |  | 32.8827 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2036 | Summer | 10 |  |  | 34.3832 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2036 | Summer | 50 |  |  | 31.8492 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2037 | Summer | 10 |  |  | 34.3374 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2037 | Summer | 50 |  |  | 31.7885 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2038 | Summer | 10 |  |  | 34.3276 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2038 | Summer | 50 |  |  | 31.7234 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2039 | Summer | 10 |  |  | 32.6827 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2039 | Summer | 50 |  |  | 30.3101 | 202503 | MVA | central
zone_sub | wgi | maximum |  | 2022 | Summer | 10 | 21696 | 27.3902 | 50.299 | 202503 | MVA | east
zone_sub | wgi | maximum |  | 2022 | Summer | 50 | 21696 | 27.3902 | 41.2414 | 202503 | MVA | east
zone_sub | wgi | maximum |  | 2023 | Summer | 10 | 22045 | 30.4273 | 50.6919 | 202503 | MVA | east
zone_sub | wgi | maximum |  | 2023 | Summer | 50 | 22045 | 30.4273 | 41.4384 | 202503 | MVA | east
zone_sub | wgi | maximum |  | 2024 | Summer | 10 | 22388 | 33.5461 | 51.0465 | 202503 | MVA | east
zone_sub | wgi | maximum |  | 2024 | Summer | 50 | 22388 | 33.5461 | 41.5121 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2025 | Summer | 10 |  |  | 54.5057 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2025 | Summer | 50 |  |  | 44.6075 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2026 | Summer | 10 |  |  | 54.6012 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2026 | Summer | 50 |  |  | 44.9185 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2027 | Summer | 10 |  |  | 54.4983 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2027 | Summer | 50 |  |  | 44.7661 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2028 | Summer | 10 |  |  | 54.5247 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2028 | Summer | 50 |  |  | 44.911 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2029 | Summer | 10 |  |  | 54.7136 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2029 | Summer | 50 |  |  | 44.9706 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2030 | Summer | 10 |  |  | 55.0965 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2030 | Summer | 50 |  |  | 45.1615 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2031 | Summer | 10 |  |  | 55.7707 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2031 | Summer | 50 |  |  | 45.5541 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2032 | Summer | 50 |  |  | 45.8843 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2032 | Summer | 10 |  |  | 56.122 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2033 | Summer | 10 |  |  | 56.3761 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2033 | Summer | 50 |  |  | 46.0363 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2034 | Summer | 10 |  |  | 56.7608 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2034 | Summer | 50 |  |  | 45.9008 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2035 | Summer | 10 |  |  | 57.2519 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2035 | Summer | 50 |  |  | 46.4689 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2036 | Summer | 10 |  |  | 57.8457 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2036 | Summer | 50 |  |  | 46.559 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2037 | Summer | 10 |  |  | 58.1569 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2037 | Summer | 50 |  |  | 46.4523 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2038 | Summer | 10 |  |  | 58.056 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2038 | Summer | 50 |  |  | 46.6661 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2039 | Summer | 10 |  |  | 56.811 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2039 | Summer | 50 |  |  | 45.5652 | 202503 | MVA | east

## Forecast- Winter
Forecasting Application - 13/10/2025
asset_type | asset | extremum | scenario | demand_year | season | poe | customer_count | pv_capacity | value | forecast_round | unit | region
zone_sub | cln | maximum |  | 2022 | Winter | 10 | 38619 | 72.2578 | 63.0362 | 202503 | MVA | central
zone_sub | cln | maximum |  | 2022 | Winter | 50 | 38619 | 72.2578 | 58.8161 | 202503 | MVA | central
zone_sub | cln | maximum |  | 2023 | Winter | 10 | 41429 | 81.3604 | 67.9918 | 202503 | MVA | central
zone_sub | cln | maximum |  | 2023 | Winter | 50 | 41429 | 81.3604 | 63.4647 | 202503 | MVA | central
zone_sub | cln | maximum |  | 2024 | Winter | 10 | 44846 | 94.6588 | 74.018 | 202503 | MVA | central
zone_sub | cln | maximum |  | 2024 | Winter | 50 | 44846 | 94.6588 | 69.1182 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2025 | Winter | 10 |  |  | 89.4372 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2025 | Winter | 50 |  |  | 84.5179 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2026 | Winter | 10 |  |  | 93.2911 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2026 | Winter | 50 |  |  | 88.1502 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2027 | Winter | 10 |  |  | 98.0701 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2027 | Winter | 50 |  |  | 92.8679 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2028 | Winter | 10 |  |  | 102.5171 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2028 | Winter | 50 |  |  | 97.437 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2029 | Winter | 10 |  |  | 107.2692 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2029 | Winter | 50 |  |  | 101.4753 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2030 | Winter | 10 |  |  | 112.2902 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2030 | Winter | 50 |  |  | 107.1286 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2031 | Winter | 10 |  |  | 119.5588 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2031 | Winter | 50 |  |  | 113.3315 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2032 | Winter | 10 |  |  | 125.8642 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2032 | Winter | 50 |  |  | 119.6901 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2033 | Winter | 10 |  |  | 131.807 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2033 | Winter | 50 |  |  | 125.9989 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2034 | Winter | 10 |  |  | 137.993 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2034 | Winter | 50 |  |  | 131.579 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2035 | Winter | 10 |  |  | 145.465 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2035 | Winter | 50 |  |  | 137.6925 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2036 | Winter | 10 |  |  | 147.8036 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2036 | Winter | 50 |  |  | 139.8743 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2037 | Winter | 10 |  |  | 155.8793 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2037 | Winter | 50 |  |  | 147.8441 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2038 | Winter | 10 |  |  | 163.4009 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2038 | Winter | 50 |  |  | 156.1056 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2039 | Winter | 10 |  |  | 133.5693 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2039 | Winter | 50 |  |  | 127.2077 | 202503 | MVA | central
zone_sub | cre | maximum |  | 2022 | Winter | 10 | 24937 | 39.5122 | 50.635 | 202503 | MVA | central
zone_sub | cre | maximum |  | 2022 | Winter | 50 | 24937 | 39.5122 | 48.3881 | 202503 | MVA | central
zone_sub | cre | maximum |  | 2023 | Winter | 10 | 25835 | 43.8704 | 52.4586 | 202503 | MVA | central
zone_sub | cre | maximum |  | 2023 | Winter | 50 | 25835 | 43.8704 | 50.1308 | 202503 | MVA | central
zone_sub | cre | maximum |  | 2024 | Winter | 10 | 26314 | 48.9572 | 53.4328 | 202503 | MVA | central
zone_sub | cre | maximum |  | 2024 | Winter | 50 | 26314 | 48.9572 | 51.0617 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2025 | Winter | 10 |  |  | 68.4471 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2025 | Winter | 50 |  |  | 65.7336 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2026 | Winter | 10 |  |  | 69.4459 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2026 | Winter | 50 |  |  | 66.605 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2027 | Winter | 10 |  |  | 69.249 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2027 | Winter | 50 |  |  | 66.728 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2028 | Winter | 10 |  |  | 74.3386 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2028 | Winter | 50 |  |  | 72.0847 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2029 | Winter | 10 |  |  | 74.5773 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2029 | Winter | 50 |  |  | 72.2361 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2030 | Winter | 10 |  |  | 76.3193 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2030 | Winter | 50 |  |  | 74.0669 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2031 | Winter | 10 |  |  | 77.7248 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2031 | Winter | 50 |  |  | 75.6012 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2032 | Winter | 10 |  |  | 79.2116 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2032 | Winter | 50 |  |  | 76.7507 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2033 | Winter | 10 |  |  | 79.7367 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2033 | Winter | 50 |  |  | 77.8762 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2034 | Winter | 10 |  |  | 80.3545 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2034 | Winter | 50 |  |  | 78.6625 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2035 | Winter | 10 |  |  | 81.081 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2035 | Winter | 50 |  |  | 79.0014 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2036 | Winter | 10 |  |  | 80.0375 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2036 | Winter | 50 |  |  | 78.1499 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2037 | Winter | 10 |  |  | 83.4116 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2037 | Winter | 50 |  |  | 80.9567 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2038 | Winter | 10 |  |  | 84.3767 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2038 | Winter | 50 |  |  | 81.4995 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2039 | Winter | 10 |  |  | 72.4681 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2039 | Winter | 50 |  |  | 69.0004 | 202503 | MVA | central
zone_sub | epg | maximum |  | 2022 | Winter | 10 | 29371 | 40.0067 | 65.9271 | 202503 | MVA | central
zone_sub | epg | maximum |  | 2022 | Winter | 50 | 29371 | 40.0067 | 59.4269 | 202503 | MVA | central
zone_sub | epg | maximum |  | 2023 | Winter | 10 | 30422 | 45.1511 | 68.3101 | 202503 | MVA | central
zone_sub | epg | maximum |  | 2023 | Winter | 50 | 30422 | 45.1511 | 61.7598 | 202503 | MVA | central
zone_sub | epg | maximum |  | 2024 | Winter | 50 | 32118 | 51.557 | 65.5719 | 202503 | MVA | central
zone_sub | epg | maximum |  | 2024 | Winter | 10 | 32118 | 51.557 | 72.1952 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2025 | Winter | 10 |  |  | 85.9871 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2025 | Winter | 50 |  |  | 79.3939 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2026 | Winter | 10 |  |  | 95.0802 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2026 | Winter | 50 |  |  | 89.3565 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2027 | Winter | 10 |  |  | 100.5082 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2027 | Winter | 50 |  |  | 92.7492 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2028 | Winter | 10 |  |  | 99.8778 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2028 | Winter | 50 |  |  | 93.3308 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2029 | Winter | 10 |  |  | 103.1049 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2029 | Winter | 50 |  |  | 96.5577 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2030 | Winter | 10 |  |  | 109.1359 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2030 | Winter | 50 |  |  | 102.3455 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2031 | Winter | 10 |  |  | 112.51 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2031 | Winter | 50 |  |  | 104.2867 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2032 | Winter | 10 |  |  | 121.7799 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2032 | Winter | 50 |  |  | 114.0182 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2033 | Winter | 10 |  |  | 127.6696 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2033 | Winter | 50 |  |  | 119.7255 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2034 | Winter | 10 |  |  | 133.3287 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2034 | Winter | 50 |  |  | 125.5482 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2035 | Winter | 10 |  |  | 135.1129 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2035 | Winter | 50 |  |  | 126.6853 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2036 | Winter | 10 |  |  | 142.2751 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2036 | Winter | 50 |  |  | 134.3407 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2037 | Winter | 10 |  |  | 149.629 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2037 | Winter | 50 |  |  | 142.1357 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2038 | Winter | 10 |  |  | 150.109 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2038 | Winter | 50 |  |  | 141.9626 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2039 | Winter | 10 |  |  | 116.0207 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2039 | Winter | 50 |  |  | 101.3122 | 202503 | MVA | central
zone_sub | klo | maximum |  | 2022 | Winter | 10 | 14879 | 23.0226 | 48.7862 | 202503 | MVA | central
zone_sub | klo | maximum |  | 2022 | Winter | 50 | 14879 | 23.0226 | 43.3886 | 202503 | MVA | central
zone_sub | klo | maximum |  | 2023 | Winter | 10 | 17175 | 27.7177 | 56.3067 | 202503 | MVA | central
zone_sub | klo | maximum |  | 2023 | Winter | 50 | 17175 | 27.7177 | 50.077 | 202503 | MVA | central
zone_sub | klo | maximum |  | 2024 | Winter | 10 | 19951 | 34.2052 | 65.4015 | 202503 | MVA | central
zone_sub | klo | maximum |  | 2024 | Winter | 50 | 19951 | 34.2052 | 58.1655 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2025 | Winter | 10 |  |  | 79.8942 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2025 | Winter | 50 |  |  | 72.3119 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2026 | Winter | 10 |  |  | 92.3723 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2026 | Winter | 50 |  |  | 83.7626 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2027 | Winter | 10 |  |  | 102.9502 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2027 | Winter | 50 |  |  | 93.3778 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2028 | Winter | 10 |  |  | 120.3965 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2028 | Winter | 50 |  |  | 109.8362 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2029 | Winter | 10 |  |  | 129.7211 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2029 | Winter | 50 |  |  | 118.6301 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2030 | Winter | 10 |  |  | 142.5707 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2030 | Winter | 50 |  |  | 129.8167 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2031 | Winter | 10 |  |  | 159.4027 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2031 | Winter | 50 |  |  | 143.8497 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2032 | Winter | 10 |  |  | 178.8568 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2032 | Winter | 50 |  |  | 161.743 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2033 | Winter | 10 |  |  | 196.8658 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2033 | Winter | 50 |  |  | 178.8635 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2034 | Winter | 10 |  |  | 214.3536 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2034 | Winter | 50 |  |  | 194.8729 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2035 | Winter | 10 |  |  | 235.0946 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2035 | Winter | 50 |  |  | 213.0243 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2036 | Winter | 10 |  |  | 246.5584 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2036 | Winter | 50 |  |  | 225.0657 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2037 | Winter | 10 |  |  | 273.2503 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2037 | Winter | 50 |  |  | 249.8153 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2038 | Winter | 10 |  |  | 298.8878 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2038 | Winter | 50 |  |  | 271.7276 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2039 | Winter | 10 |  |  | 252.4111 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2039 | Winter | 50 |  |  | 227.0702 | 202503 | MVA | central
zone_sub | llg | maximum |  | 2022 | Winter | 10 | 7174 | 11.5134 | 22.426 | 202503 | MVA | central
zone_sub | llg | maximum |  | 2022 | Winter | 50 | 7174 | 11.5134 | 20.2322 | 202503 | MVA | central
zone_sub | llg | maximum |  | 2023 | Winter | 10 | 7235 | 12.7349 | 22.5982 | 202503 | MVA | central
zone_sub | llg | maximum |  | 2023 | Winter | 50 | 7235 | 12.7349 | 20.4035 | 202503 | MVA | central
zone_sub | llg | maximum |  | 2024 | Winter | 10 | 7295 | 13.7538 | 22.7705 | 202503 | MVA | central
zone_sub | llg | maximum |  | 2024 | Winter | 50 | 7295 | 13.7538 | 20.5738 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2025 | Winter | 10 |  |  | 26.1225 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2025 | Winter | 50 |  |  | 23.9159 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2026 | Winter | 10 |  |  | 30.6829 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2026 | Winter | 50 |  |  | 28.4398 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2027 | Winter | 10 |  |  | 31.049 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2027 | Winter | 50 |  |  | 28.8402 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2028 | Winter | 10 |  |  | 31.3064 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2028 | Winter | 50 |  |  | 29.108 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2029 | Winter | 10 |  |  | 31.5714 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2029 | Winter | 50 |  |  | 29.4846 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2030 | Winter | 10 |  |  | 32.5932 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2030 | Winter | 50 |  |  | 30.3426 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2031 | Winter | 10 |  |  | 33.1905 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2031 | Winter | 50 |  |  | 31.0163 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2032 | Winter | 10 |  |  | 33.8014 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2032 | Winter | 50 |  |  | 31.6154 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2033 | Winter | 10 |  |  | 34.0793 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2033 | Winter | 50 |  |  | 31.8255 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2034 | Winter | 10 |  |  | 34.2253 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2034 | Winter | 50 |  |  | 32.0656 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2035 | Winter | 10 |  |  | 33.7185 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2035 | Winter | 50 |  |  | 31.7299 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2036 | Winter | 10 |  |  | 33.9832 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2036 | Winter | 50 |  |  | 31.9069 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2037 | Winter | 10 |  |  | 34.9987 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2037 | Winter | 50 |  |  | 32.7389 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2038 | Winter | 10 |  |  | 34.5209 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2038 | Winter | 50 |  |  | 32.3709 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2039 | Winter | 10 |  |  | 28.3277 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2039 | Winter | 50 |  |  | 26.2847 | 202503 | MVA | central
zone_sub | ofr | maximum |  | 2022 | Winter | 10 | 23246 | 35.5119 | 49.8939 | 202503 | MVA | central
zone_sub | ofr | maximum |  | 2022 | Winter | 50 | 23246 | 35.5119 | 46.8764 | 202503 | MVA | central
zone_sub | ofr | maximum |  | 2023 | Winter | 10 | 24109 | 39.5748 | 51.7437 | 202503 | MVA | central
zone_sub | ofr | maximum |  | 2023 | Winter | 50 | 24109 | 39.5748 | 48.6149 | 202503 | MVA | central
zone_sub | ofr | maximum |  | 2024 | Winter | 10 | 24997 | 44.4669 | 53.6497 | 202503 | MVA | central
zone_sub | ofr | maximum |  | 2024 | Winter | 50 | 24997 | 44.4669 | 50.4065 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2025 | Winter | 10 |  |  | 59.4536 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2025 | Winter | 50 |  |  | 56.1183 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2026 | Winter | 10 |  |  | 66.5595 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2026 | Winter | 50 |  |  | 63.2802 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2027 | Winter | 10 |  |  | 72.8129 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2027 | Winter | 50 |  |  | 69.3039 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2028 | Winter | 10 |  |  | 76.0509 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2028 | Winter | 50 |  |  | 72.5305 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2029 | Winter | 10 |  |  | 78.6773 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2029 | Winter | 50 |  |  | 74.8582 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2030 | Winter | 10 |  |  | 81.1629 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2030 | Winter | 50 |  |  | 77.5373 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2031 | Winter | 10 |  |  | 83.2732 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2031 | Winter | 50 |  |  | 79.5294 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2032 | Winter | 10 |  |  | 85.4834 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2032 | Winter | 50 |  |  | 81.7407 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2033 | Winter | 10 |  |  | 86.4197 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2033 | Winter | 50 |  |  | 82.8706 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2034 | Winter | 10 |  |  | 87.7259 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2034 | Winter | 50 |  |  | 83.8526 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2035 | Winter | 10 |  |  | 90.1815 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2035 | Winter | 50 |  |  | 86.3425 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2036 | Winter | 10 |  |  | 89.3155 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2036 | Winter | 50 |  |  | 84.7668 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2037 | Winter | 10 |  |  | 92.5351 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2037 | Winter | 50 |  |  | 88.8524 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2038 | Winter | 10 |  |  | 94.3753 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2038 | Winter | 50 |  |  | 94.1939 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2039 | Winter | 10 |  |  | 80.6717 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2039 | Winter | 50 |  |  | 77.1549 | 202503 | MVA | central
zone_sub | phm | maximum |  | 2022 | Winter | 10 | 16270 | 23.521 | 48.1658 | 202503 | MVA | central
zone_sub | phm | maximum |  | 2022 | Winter | 50 | 16270 | 23.521 | 45.1092 | 202503 | MVA | central
zone_sub | phm | maximum |  | 2023 | Winter | 10 | 16562 | 25.5412 | 49.0318 | 202503 | MVA | central
zone_sub | phm | maximum |  | 2023 | Winter | 50 | 16562 | 25.5412 | 45.9202 | 202503 | MVA | central
zone_sub | phm | maximum |  | 2024 | Winter | 10 | 16854 | 27.7496 | 49.8978 | 202503 | MVA | central
zone_sub | phm | maximum |  | 2024 | Winter | 50 | 16854 | 27.7496 | 46.7311 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2025 | Winter | 10 |  |  | 67.0847 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2025 | Winter | 50 |  |  | 64.1376 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2026 | Winter | 10 |  |  | 71.7531 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2026 | Winter | 50 |  |  | 68.6294 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2027 | Winter | 10 |  |  | 72.4584 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2027 | Winter | 50 |  |  | 69.3785 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2028 | Winter | 10 |  |  | 72.887 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2028 | Winter | 50 |  |  | 69.9467 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2029 | Winter | 10 |  |  | 73.8781 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2029 | Winter | 50 |  |  | 70.9603 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2030 | Winter | 10 |  |  | 76.2493 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2030 | Winter | 50 |  |  | 73.2946 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2031 | Winter | 10 |  |  | 77.5227 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2031 | Winter | 50 |  |  | 74.8388 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2032 | Winter | 10 |  |  | 79.9897 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2032 | Winter | 50 |  |  | 76.8149 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2033 | Winter | 10 |  |  | 87.5343 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2033 | Winter | 50 |  |  | 77.8299 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2034 | Winter | 10 |  |  | 81.2629 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2034 | Winter | 50 |  |  | 78.7091 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2035 | Winter | 10 |  |  | 80.0205 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2035 | Winter | 50 |  |  | 77.0055 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2036 | Winter | 10 |  |  | 81.6454 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2036 | Winter | 50 |  |  | 78.9538 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2037 | Winter | 10 |  |  | 85.2253 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2037 | Winter | 50 |  |  | 82.0295 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2038 | Winter | 10 |  |  | 82.7648 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2038 | Winter | 50 |  |  | 79.6564 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2039 | Winter | 10 |  |  | 67.0558 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2039 | Winter | 50 |  |  | 63.9852 | 202503 | MVA | central
zone_sub | wgi | maximum |  | 2022 | Winter | 10 | 21696 | 27.3902 | 41.941 | 202503 | MVA | east
zone_sub | wgi | maximum |  | 2022 | Winter | 50 | 21696 | 27.3902 | 38.234 | 202503 | MVA | east
zone_sub | wgi | maximum |  | 2023 | Winter | 10 | 22045 | 30.4273 | 42.6315 | 202503 | MVA | east
zone_sub | wgi | maximum |  | 2023 | Winter | 50 | 22045 | 30.4273 | 38.883 | 202503 | MVA | east
zone_sub | wgi | maximum |  | 2024 | Winter | 10 | 22388 | 33.5461 | 43.3126 | 202503 | MVA | east
zone_sub | wgi | maximum |  | 2024 | Winter | 50 | 22388 | 33.5461 | 39.5207 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2025 | Winter | 10 |  |  | 47.2482 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2025 | Winter | 50 |  |  | 43.6466 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2026 | Winter | 10 |  |  | 47.6557 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2026 | Winter | 50 |  |  | 44.0841 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2027 | Winter | 10 |  |  | 49.0622 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2027 | Winter | 50 |  |  | 44.625 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2028 | Winter | 10 |  |  | 49.028 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2028 | Winter | 50 |  |  | 45.3431 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2029 | Winter | 10 |  |  | 49.3373 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2029 | Winter | 50 |  |  | 46.0239 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2030 | Winter | 10 |  |  | 50.5469 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2030 | Winter | 50 |  |  | 47.2137 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2031 | Winter | 10 |  |  | 54.0224 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2031 | Winter | 50 |  |  | 50.206 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2032 | Winter | 10 |  |  | 55.4565 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2032 | Winter | 50 |  |  | 51.8155 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2033 | Winter | 10 |  |  | 54.099 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2033 | Winter | 50 |  |  | 50.6413 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2034 | Winter | 10 |  |  | 57.8491 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2034 | Winter | 50 |  |  | 54.2764 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2035 | Winter | 10 |  |  | 56.2746 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2035 | Winter | 50 |  |  | 54.9313 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2036 | Winter | 10 |  |  | 57.6913 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2036 | Winter | 50 |  |  | 55.4021 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2037 | Winter | 10 |  |  | 58.7122 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2037 | Winter | 50 |  |  | 57.6212 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2038 | Winter | 10 |  |  | 58.2928 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2038 | Winter | 50 |  |  | 57.9824 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2039 | Winter | 10 |  |  | 49.2493 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2039 | Winter | 50 |  |  | 45.4578 | 202503 | MVA | east

## Ratings
STATION OUTPUT RATING (TRANSFORMER SUMMATION) SUMMARY
|  |  | Station N Rating |  | Station N-1 Rating |  | Station N-2 Rating
|  |  | SCR | WCR | SCR | WCR | SCR | WCR | Remarks | Remarks | Bus Target | Station Cap Bank
S/S Name | No. TX | Name Plate MVA | MVA | MVA | MVA | MVA | MVA | MVA | For N-1 Ratings | N-2 | Voltage kV | MVAr
CLN_Old | 2 | 66 | 87.3 | 95.3 | 44.6 | 48.9 | 0 | 0 | Loss of T1 |  | 22 | 12
CLN | 3 | 99 | 130.95 | 142.95 | 89.2 | 97.8 | 44.6 | 48.9
CRE | 2 | 66 | 84.3 | 93.8 | 41.1 | 46.3 | 0 | 0 | Loss of T2 or T3 |  | 22 | 12
EPG | 3 | 99 | 123.1 | 139.9 | 87.8 | 98.1 | 43.9 | 49.05 | Loss of T3 | Using Highest value | 22
KLO | 2 | 66 | 97.5 | 97.5 | 49.1 | 49.1 | 0 | 0 | Loss of T1 or T2 |  | 22.44 | 6
LLG | 1 | 33 | 47.4 | 48.3 | 0 | 0 | 0 | 0 | N rating only |  | 22 | 4
OFR | 2 | 66 | 93.2 | 93.2 | 45.2 | 48 | 0 | 0 | Loss of T1 or T2 |  | 22 | 6
PHM | 2 | 66 | 91.9 | 95.7 | 45 | 49.1 | 0 | 0 | Loss of T1 or T2 |  | 22 | 12
WGI | 3 | 40.5 | 55.8 | 56.8 | 35.3 | 36.1 | 17.65 | 18.05

## Power Factor
asset_type | asset | PF
zone_sub | cln | 1
zone_sub | cre | 1
zone_sub | cyn | 1
zone_sub | epg | 1
zone_sub | klo | 0.99
zone_sub | llg | 0.99
zone_sub | ofr | 1
zone_sub | phm | 1
zone_sub | wgi | 0.99

## FT
Forecast tool (MVA) |  | Forecast Capacity & Transfers
ZSS |  | PHM
Summer
[5 empty] | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads
DY (Apr 1 to Mar 30) |  | 2022/23 | 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2028/29 | 2029/30 | 2030/31 | 2031/32 | 2032/33 | 2033/34 | 2034/35 | 2035/36 | 2036/37 | 2037/38 | 2038/39
DY (Apr 1 to Mar 30) |  | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038
FY (Jul 1 to Jun 30) |  | 2022/23 | 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2028/29 | 2029/30 | 2030/31 | 2031/32 | 2032/33 | 2033/34 | 2034/35 | 2035/36 | 2036/37 | 2037/38 | 2038/39
FY (Jul 1 to Jun 30) |  |  |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39
Summer POE50 | 50 |  |  | 52.8621 | 69.621 | 74.1527 | 73.9998 | 73.965 | 74.4648 | 75.0153 | 76.1566 | 76.9783 | 77.4148 | 77.8841 | 78.3211 | 79.127 | 80.1321 | 80.0404
Summer POE10 | 10 |  |  | 58.7282 | 75.5207 | 79.8845 | 79.6008 | 79.5894 | 80.0199 | 81.1895 | 81.9552 | 82.7146 | 83.6062 | 84.4206 | 85.2206 | 85.2937 | 86.2309 | 85.4841
Winter
[5 empty] | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads
DM (Apr 1 to Mar 30) |  |  |  | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2028/29 | 2029/30 | 2030/31 | 2031/32 | 2032/33 | 2033/34 | 2034/35 | 2035/36 | 2036/37 | 2037/38 | 2038/39
DY (Apr 1 to Mar 30) |  |  |  | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038
FY (Jul 1 to Jun 30) |  |  |  | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2028/29 | 2029/30 | 2030/31 | 2031/32 | 2032/33 | 2033/34 | 2034/35 | 2035/36 | 2036/37 | 2037/38 | 2038/39
FY (Jul 1 to Jun 30) |  |  |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39
Winter POE50 | 50 |  |  | 46.7311 | 64.1376 | 68.6294 | 69.3785 | 69.9467 | 70.9603 | 73.2946 | 74.8388 | 76.8149 | 77.8299 | 78.7091 | 77.0055 | 78.9538 | 82.0295 | 79.6564
Winter POE10 | 10 |  |  | 49.8978 | 67.0847 | 71.7531 | 72.4584 | 72.887 | 73.8781 | 76.2493 | 77.5227 | 79.9897 | 87.5343 | 81.2629 | 80.0205 | 81.6454 | 85.2253 | 82.7648
Transfers (MVA)
|  | Feeder | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39
|  | PHM | 1.7 | 1.7 | 1.67 | 1.65 | 1.62 | 1.6 | 1.58 | 1.55 | 1.53 | 1.51 | 1.48 | 1.46 | 1.44 | 1.42 | 1.4
|  | PowerFactor | 1

## Load Duration Curves
Station
PHM
POE10
[6 empty] | Stations | KLO |  | EPG |  | CRE |  | CLN |  | PHM |  | OFR |  | LLG |  | WGI
| % of MD | Winter - MD (P10) - Duration % | Winter - MD - Hours | Summer - MD - Duration % | Summer - MD - Hours | %MD | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration %
| 100% | 0% | 0 | 0% | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| 99% | 0.03383% | 1.486 | 0.03444% | 1.5127 | 99% | 0.01722% | 0.02707% | 0% | 0.04737% | 0% | 0% | 0.00861% | 0.01353% | 0.03444% | 0.03383% | 0.01722% | 0.0203% | 0.02583% | 0.006767% | 0% | 0.006767%
| 98% | 0.07443% | 3.2692 | 0.05166% | 2.269 | 98% | 0.01722% | 0.07443% | 0.00861% | 0.08797% | 0.02583% | 0.01353% | 0.02583% | 0.0203% | 0.05166% | 0.07443% | 0.02583% | 0.0812% | 0.04305% | 0.0203% | 0% | 0.006767%
| 97% | 0.1556% | 6.8356 | 0.0861% | 3.7816 | 97% | 0.02583% | 0.09474% | 0.02583% | 0.1421% | 0.04305% | 0.02707% | 0.05166% | 0.03383% | 0.0861% | 0.1556% | 0.04305% | 0.1083% | 0.05166% | 0.04737% | 0.00861% | 0.006767%
| 95% | 0.3992% | 17.5347 | 0.1378% | 6.0506 | 95% | 0.05166% | 0.1895% | 0.09471% | 0.3519% | 0.0861% | 0.08797% | 0.1033% | 0.05413% | 0.1378% | 0.3992% | 0.07749% | 0.1759% | 0.09471% | 0.09474% | 0.00861% | 0.03383%
| 90% | 1.793% | 78.7576 | 0.3702% | 16.2611 | 90% | 0.0861% | 0.9135% | 0.1894% | 1.786% | 0.1894% | 0.7579% | 0.1808% | 0.07443% | 0.3702% | 1.793% | 0.2066% | 0.8932% | 0.353% | 0.2639% | 0.01722% | 0.1962%
| 85% | 5.393% | 236.8672 | 0.6027% | 26.4715 | 85% | 0.1205% | 2.355% | 0.353% | 4.588% | 0.2669% | 2.761% | 0.3272% | 0.318% | 0.6027% | 5.393% | 0.3702% | 2.68% | 0.7147% | 0.7443% | 0.02583% | 0.9135%
| 80% | 11.33% | 497.5104 | 0.7749% | 34.0348 | 80% | 0.31% | 5.616% | 0.6458% | 8.885% | 0.4219% | 6.787% | 0.4477% | 0.9406% | 0.7749% | 11.33% | 0.5683% | 6.11% | 1.317% | 1.915% | 0.06027% | 2.118%
| 75% | 18.3% | 803.6248 | 1.102% | 48.405 | 75% | 0.4822% | 9.995% | 0.9988% | 14.05% | 0.5338% | 11.76% | 0.5855% | 2.876% | 1.102% | 18.3% | 0.7491% | 10.38% | 2.764% | 4.601% | 0.07749% | 4.486%
| 70% | 26.3% | 1155.2107 | 1.739% | 76.3892 | 70% | 0.7491% | 14.12% | 1.498% | 19.88% | 0.8438% | 17.56% | 0.7921% | 7.376% | 1.739% | 26.3% | 0.9557% | 15.73% | 6.225% | 8.837% | 0.1292% | 8.607%
| 65% | 35.36% | 1553.1596 | 2.6% | 114.2056 | 65% | 1.154% | 18.84% | 2.265% | 27.11% | 1.102% | 25.21% | 1.05% | 12.51% | 2.6% | 35.36% | 1.541% | 22.03% | 12.05% | 15.25% | 0.1464% | 14.03%
| 60% | 46.14% | 2026.2996 | 4.055% | 178.1154 | 60% | 1.602% | 25.14% | 3.203% | 35.21% | 1.627% | 33.62% | 1.748% | 18.2% | 4.055% | 46.14% | 2.247% | 29.44% | 20.92% | 25.15% | 0.2583% | 21.29%
| 55% | 59.16% | 2598.4068 | 7.095% | 311.6074 | 55% | 2.411% | 33.56% | 4.357% | 45.33% | 2.48% | 42.68% | 2.419% | 25.42% | 7.095% | 59.16% | 3.496% | 37.5% | 33.11% | 37.15% | 0.8094% | 29.85%
| 50% | 73.62% | 3233.5201 | 14.48% | 636.0723 | 50% | 4.598% | 44.25% | 6.303% | 58.26% | 3.84% | 54.87% | 4.064% | 34.04% | 14.48% | 73.62% | 5.881% | 47.91% | 47.93% | 51.32% | 2.17% | 39.4%
| 45% | 85.96% | 3775.313 | 26.86% | 1179.4944 | 45% | 9.592% | 58.98% | 10.8% | 69.36% | 6.535% | 71.48% | 8.378% | 45.63% | 26.86% | 85.96% | 11.13% | 62.3% | 62.8% | 65.85% | 4.753% | 49.36%
| 40% | 92.73% | 4072.8088 | 41.17% | 1808.3816 | 40% | 19.83% | 71.65% | 21.2% | 75.98% | 14.01% | 84.31% | 16.88% | 65.51% | 41.17% | 92.73% | 21.13% | 79.32% | 76.24% | 79.08% | 8.662% | 59.42%
| 35% | 95.6% | 4198.821 | 63.28% | 2779.1293 | 35% | 37.74% | 78.94% | 37.58% | 85.16% | 27.53% | 88.52% | 26.59% | 78.66% | 63.28% | 95.6% | 34.85% | 87.21% | 86.9% | 88.41% | 15.86% | 68.26%
| 30% | 97.25% | 4271.3374 | 86.84% | 3814.165 | 30% | 66.82% | 83.24% | 57.09% | 93.38% | 49.73% | 90.98% | 45.59% | 83.41% | 86.84% | 97.25% | 59.02% | 90.02% | 92.6% | 93.97% | 28.71% | 75.35%
| 25% | 98.4% | 4321.8611 | 94.88% | 4166.9923 | 25% | 77.33% | 87.43% | 77.75% | 96.1% | 81.07% | 93.44% | 72.26% | 87.95% | 94.88% | 98.4% | 83.32% | 92.46% | 96.47% | 96.66% | 44.75% | 80.55%
| 20% | 99.11% | 4353.067 | 97.51% | 4282.7105 | 20% | 85.59% | 92.06% | 96.84% | 97.65% | 89.22% | 95.65% | 79.18% | 93.87% | 97.51% | 99.11% | 91.2% | 94.84% | 98.65% | 98.41% | 56.7% | 84.95%
| 15% | 99.49% | 4369.4129 | 99.38% | 4364.7722 | 15% | 96.14% | 98.9% | 99.64% | 98.65% | 96.11% | 97.43% | 86.26% | 99.55% | 99.38% | 99.49% | 97.48% | 97.23% | 99.31% | 99.14% | 68.25% | 89.03%
| 10% | 99.7% | 4378.6261 | 99.99% | 4391.6218 | 10% | 99.99% | 99.99% | 99.99% | 99.16% | 99.9% | 98.78% | 98.3% | 99.6% | 99.99% | 99.7% | 99.99% | 99.59% | 99.63% | 99.41% | 79.5% | 92.79%
| 5% | 99.99% | 4391.7028 | 99.99% | 4391.6218 | 5% | 99.99% | 99.99% | 99.99% | 99.49% | 99.99% | 99.76% | 99.99% | 99.61% | 99.99% | 99.99% | 99.99% | 99.99% | 99.68% | 99.6% | 90.07% | 96.81%
| 9.992e-14% | 99.99% | 4391.7028 | 99.99% | 4391.6218 | 0% | 99.99% | 99.99% | 99.99% | 99.99% | 99.99% | 99.99% | 99.99% | 99.63% | 99.99% | 99.99% | 99.99% | 99.99% | 99.71% | 99.63% | 99.99% | 99.99%
POE 50
[6 empty] | Stations | KLO |  | EPG |  | CRE |  | CLN |  | PHM |  | OFR |  | LLG |  | WGI
| % of MD | Winter - AD (P50) - Duration % | Winter - AD - Hours | Summer - AD - Duration % | Summer - AD - Hours | %MD | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration %
| 100% | 0% | 0 | 0% | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| 99% | 0.03383% | 1.486 | 0% | 0 | 99% | 0.03444% | 0.02707% | 0.04305% | 0.04737% | 0% | 0% | 0% | 0.01353% | 0% | 0.03383% | 0% | 0.0203% | 0.00861% | 0.006767% | 0.00861% | 0.006767%
| 98% | 0.07443% | 3.2692 | 0% | 0 | 98% | 0.05166% | 0.07443% | 0.07749% | 0.08797% | 0% | 0.01353% | 0.00861% | 0.0203% | 0% | 0.07443% | 0.00861% | 0.0812% | 0.00861% | 0.0203% | 0.00861% | 0.006767%
| 97% | 0.1556% | 6.8356 | 0.00861% | 0.37816 | 97% | 0.06888% | 0.09474% | 0.07749% | 0.1421% | 0.02583% | 0.02707% | 0.01722% | 0.03383% | 0.00861% | 0.1556% | 0.01722% | 0.1083% | 0.01722% | 0.0406% | 0.00861% | 0.006767%
| 95% | 0.3992% | 17.5347 | 0.05166% | 2.269 | 95% | 0.0861% | 0.1895% | 0.1378% | 0.3519% | 0.04305% | 0.08797% | 0.02583% | 0.05413% | 0.05166% | 0.3992% | 0.04305% | 0.1759% | 0.01722% | 0.1015% | 0.01722% | 0.03383%
| 90% | 1.793% | 78.7576 | 0.1292% | 5.6725 | 90% | 0.1292% | 0.9135% | 0.2583% | 1.786% | 0.1119% | 0.7579% | 0.1033% | 0.07443% | 0.1292% | 1.793% | 0.1033% | 0.8932% | 0.0861% | 0.3451% | 0.2066% | 0.1962%
| 85% | 5.393% | 236.8672 | 0.3616% | 15.8829 | 85% | 0.2497% | 2.355% | 0.465% | 4.588% | 0.2755% | 2.761% | 0.1808% | 0.318% | 0.3616% | 5.393% | 0.2066% | 2.68% | 0.31% | 0.9% | 0.9213% | 0.9135%
| 80% | 11.33% | 497.5104 | 0.706% | 31.0095 | 80% | 0.4133% | 5.616% | 0.7835% | 8.885% | 0.6113% | 6.787% | 0.2669% | 0.9406% | 0.706% | 11.33% | 0.6286% | 6.11% | 0.8008% | 2.517% | 2.153% | 2.118%
| 75% | 18.3% | 803.6248 | 1.662% | 72.9857 | 75% | 0.8352% | 9.995% | 1.257% | 14.05% | 0.9902% | 11.76% | 0.4047% | 2.876% | 1.662% | 18.3% | 1.309% | 10.38% | 1.834% | 5.562% | 4.486% | 4.486%
| 70% | 26.3% | 1155.2107 | 3.427% | 150.5094 | 70% | 1.619% | 14.12% | 2.101% | 19.88% | 1.911% | 17.56% | 0.8008% | 7.376% | 3.427% | 26.3% | 2.419% | 15.73% | 4.374% | 10.11% | 7.672% | 8.607%
| 65% | 35.36% | 1553.1596 | 8.188% | 359.6342 | 65% | 3.057% | 18.84% | 4.288% | 27.11% | 3.504% | 25.21% | 1.352% | 12.51% | 8.188% | 35.36% | 4.598% | 22.03% | 9.179% | 17.54% | 11.87% | 14.03%
| 60% | 46.14% | 2026.2996 | 15.71% | 689.7717 | 60% | 5.528% | 25.14% | 9.342% | 35.21% | 7.758% | 33.62% | 3.573% | 18.2% | 15.71% | 46.14% | 9.17% | 29.44% | 16.83% | 27.53% | 18.5% | 21.29%
| 55% | 59.16% | 2598.4068 | 24.94% | 1095.5419 | 55% | 11.8% | 33.56% | 17.61% | 45.33% | 16.05% | 42.68% | 8.283% | 25.42% | 24.94% | 59.16% | 14.93% | 37.5% | 27.43% | 40.02% | 27.37% | 29.85%
| 50% | 73.62% | 3233.5201 | 37.94% | 1666.1918 | 50% | 21.47% | 44.25% | 28.46% | 58.26% | 24.85% | 54.87% | 17.57% | 34.04% | 37.94% | 73.62% | 22.35% | 47.91% | 40.6% | 54.15% | 38.39% | 39.4%
| 45% | 85.96% | 3775.313 | 57.06% | 2506.0947 | 45% | 35.07% | 58.98% | 42.44% | 69.36% | 37.15% | 71.48% | 28.59% | 45.63% | 57.06% | 85.96% | 36.95% | 62.3% | 53.97% | 68.39% | 48.48% | 49.36%
| 40% | 92.73% | 4072.8088 | 72.05% | 3164.4787 | 40% | 60.78% | 71.65% | 63.35% | 75.98% | 61.17% | 84.31% | 46.88% | 65.51% | 72.05% | 92.73% | 55.62% | 79.32% | 65.21% | 80.79% | 56.57% | 59.42%
| 35% | 95.6% | 4198.821 | 80.86% | 3551.3408 | 35% | 70.59% | 78.94% | 76.04% | 85.16% | 71.05% | 88.52% | 69.68% | 78.66% | 80.86% | 95.6% | 68.46% | 87.21% | 75.09% | 89.43% | 63.94% | 68.26%
| 30% | 97.25% | 4271.3374 | 85.59% | 3758.953 | 30% | 76.73% | 83.24% | 80.97% | 93.38% | 75.06% | 90.98% | 76.64% | 83.41% | 85.59% | 97.25% | 74.6% | 90.02% | 81.51% | 94.17% | 70.48% | 75.35%
| 25% | 98.4% | 4321.8611 | 89.4% | 3926.4798 | 25% | 83.08% | 87.43% | 85.41% | 96.1% | 78.56% | 93.44% | 83.93% | 87.95% | 89.4% | 98.4% | 78.93% | 92.46% | 86.44% | 96.81% | 76.48% | 80.55%
| 20% | 99.11% | 4353.067 | 92.22% | 4050.5177 | 20% | 91.12% | 92.06% | 89.28% | 97.65% | 81.79% | 95.65% | 91.73% | 93.87% | 92.22% | 99.11% | 84.56% | 94.84% | 90.52% | 98.48% | 81.71% | 84.95%
| 15% | 99.49% | 4369.4129 | 94.55% | 4152.622 | 15% | 99.18% | 98.9% | 92.61% | 98.65% | 86.18% | 97.43% | 98.93% | 99.55% | 94.55% | 99.49% | 92.06% | 97.23% | 93.75% | 99.28% | 86.58% | 89.03%
| 10% | 99.7% | 4378.6261 | 96.73% | 4248.2976 | 10% | 99.99% | 99.99% | 95.16% | 99.16% | 91.73% | 98.78% | 99.75% | 99.6% | 96.73% | 99.7% | 99.06% | 99.59% | 96.19% | 99.59% | 91.64% | 92.79%
| 5% | 99.99% | 4391.7028 | 99.31% | 4361.7469 | 5% | 99.99% | 99.99% | 97.15% | 99.49% | 97.84% | 99.76% | 99.99% | 99.61% | 99.31% | 99.99% | 99.99% | 99.99% | 98.14% | 99.77% | 96.54% | 96.81%
| 9.992e-14% | 99.99% | 4391.7028 | 99.99% | 4391.6218 | 0% | 99.99% | 99.99% | 99.99% | 99.99% | 99.99% | 99.99% | 99.99% | 99.63% | 99.99% | 99.99% | 99.99% | 99.99% | 99.78% | 99.99% | 99.99% | 99.99%
POE10
|  | Summer | Winter
| Year | 2019/2020 | 2023
| Start | 2024-10-01 | 2024-04-01
| End | 2025-04-01 | 2024-10-01
| Days | 183 | 183
| Hours | 4392 | 4392
POE50
|  | Summer | Winter
| Year | 2023/2024 | 2023
| Start | 2023-10-01 | 2024-04-01
| End | 2024-04-01 | 2024-10-01
| Days | 183 | 183
| Hours | 4392 | 4392

## Capacity N
Option 1 - Do Nothing / Base Case - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N Rating (MVA) - Option 1 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7
SCR N Rating (MVA) - Option 1 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9
Planned Additional Capacity (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2 - 1B New PHS ZSS + Three new feeders - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N Rating (MVA) - Option 2 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7
SCR N Rating (MVA) - Option 2 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 - 2B PHM 3rd Tx + Switchroom + Two new feeders + OFR12 New Feeder - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N Rating (MVA) - Option 3 | 95.7 | 95.7 | 95.7 | 140.7 | 140.7 | 140.7 | 140.7 | 140.7 | 140.7 | 140.7 | 140.7 | 140.7 | 140.7 | 140.7 | 140.7 | 140.7 | 140.7 | 140.7 | 140.7 | 140.7 | 140.7 | 140.7 | 140.7 | 140.7 | 140.7 | 140.7 | 140.7 | 140.7 | 140.7 | 140.7
SCR N Rating (MVA) - Option 3 | 91.9 | 91.9 | 91.9 | 136.9 | 136.9 | 136.9 | 136.9 | 136.9 | 136.9 | 136.9 | 136.9 | 136.9 | 136.9 | 136.9 | 136.9 | 136.9 | 136.9 | 136.9 | 136.9 | 136.9 | 136.9 | 136.9 | 136.9 | 136.9 | 136.9 | 136.9 | 136.9 | 136.9 | 136.9 | 136.9
Capacity Added (MVA) | 0 | 0 | 0 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45
Option 4 - 3B OFR 3rd Tx + Switchroom + Two new feeders + OFR12 New Feeder - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N Rating (MVA) - Option 4 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7
SCR N Rating (MVA) - Option 4 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 - 4B LLG 2nd Tx + Switchroom + Two new feeders + OFR12 New Feeder - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N Rating (MVA) - Option 5 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7
SCR N Rating (MVA) - Option 5 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 6 - - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N Rating (MVA) - Option 6 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7
SCR N Rating (MVA) - Option 6 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 7 - - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N Rating (MVA) - Option 7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7
SCR N Rating (MVA) - Option 7 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 8 - - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N Rating (MVA) - Option 8 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7
SCR N Rating (MVA) - Option 8 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Capacity N-1
Option 1 - Do Nothing / Base Case - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-1 Rating (MVA) - Option 1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1
SCR N-1 Rating (MVA) - Option 1 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45
Planned Additional Capacity (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2 - 1B New PHS ZSS + Three new feeders - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-1 Rating (MVA) - Option 2 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1
SCR N-1 Rating (MVA) - Option 2 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 - 2B PHM 3rd Tx + Switchroom + Two new feeders + OFR12 New Feeder - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-1 Rating (MVA) - Option 3 | 49.1 | 49.1 | 49.1 | 94.1 | 94.1 | 94.1 | 94.1 | 94.1 | 94.1 | 94.1 | 94.1 | 94.1 | 94.1 | 94.1 | 94.1 | 94.1 | 94.1 | 94.1 | 94.1 | 94.1 | 94.1 | 94.1 | 94.1 | 94.1 | 94.1 | 94.1 | 94.1 | 94.1 | 94.1 | 94.1
SCR N-1 Rating (MVA) - Option 3 | 45 | 45 | 45 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90
Capacity Added (MVA) | 0 | 0 | 0 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45
Option 4 - 3B OFR 3rd Tx + Switchroom + Two new feeders + OFR12 New Feeder - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-1 Rating (MVA) - Option 4 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1
SCR N-1 Rating (MVA) - Option 4 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 - 4B LLG 2nd Tx + Switchroom + Two new feeders + OFR12 New Feeder - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-1 Rating (MVA) - Option 5 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1
SCR N-1 Rating (MVA) - Option 5 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 6 - - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-1 Rating (MVA) - Option 6 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1
SCR N-1 Rating (MVA) - Option 6 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 7 - - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-1 Rating (MVA) - Option 7 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1
SCR N-1 Rating (MVA) - Option 7 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 8 - - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-1 Rating (MVA) - Option 8 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1
SCR N-1 Rating (MVA) - Option 8 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Capacity N-2
Option 1 - Do Nothing / Base Case - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-2 Rating (MVA) - Option 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCR N-2 Rating (MVA) - Option 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Planned Additional Capacity (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2 - 1B New PHS ZSS + Three new feeders - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-2 Rating (MVA) - Option 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCR N-2 Rating (MVA) - Option 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 - 2B PHM 3rd Tx + Switchroom + Two new feeders + OFR12 New Feeder - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-2 Rating (MVA) - Option 3 | 0 | 0 | 0 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45
SCR N-2 Rating (MVA) - Option 3 | 0 | 0 | 0 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45
Capacity Added (MVA) | 0 | 0 | 0 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45
Option 4 - 3B OFR 3rd Tx + Switchroom + Two new feeders + OFR12 New Feeder - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-2 Rating (MVA) - Option 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCR N-2 Rating (MVA) - Option 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 - 4B LLG 2nd Tx + Switchroom + Two new feeders + OFR12 New Feeder - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-2 Rating (MVA) - Option 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCR N-2 Rating (MVA) - Option 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 6 - - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-2 Rating (MVA) - Option 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCR N-2 Rating (MVA) - Option 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 7 - - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-2 Rating (MVA) - Option 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCR N-2 Rating (MVA) - Option 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 8 - - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-2 Rating (MVA) - Option 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCR N-2 Rating (MVA) - Option 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Demand
Option 1 - Do Nothing / Base Case
Winter Season | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Maximum Demand (MVA) - P50 | 42.058 | 57.7239 | 61.7664 | 62.4406 | 62.9521 | 63.8643 | 65.9652 | 67.3549 | 69.1334 | 70.0469 | 70.8382 | 69.305 | 71.0585 | 73.8266 | 71.6908 | 71.6908 | 71.6908 | 71.6908 | 71.6908 | 71.6908 | 71.6908 | 71.6908 | 71.6908 | 71.6908 | 71.6908 | 71.6908 | 71.6908 | 71.6908 | 71.6908 | 71.6908
Maximum Demand (MVA) - P10 | 44.908 | 60.3763 | 64.5778 | 65.2125 | 65.5983 | 66.4903 | 68.6243 | 69.7704 | 71.9908 | 78.7809 | 73.1366 | 72.0185 | 73.4808 | 76.7027 | 74.4883 | 74.4883 | 74.4883 | 74.4883 | 74.4883 | 74.4883 | 74.4883 | 74.4883 | 74.4883 | 74.4883 | 74.4883 | 74.4883 | 74.4883 | 74.4883 | 74.4883 | 74.4883
Block loads (MVA) not in the forecast | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Available Transfers (MVA) | 1.7 | 1.7 | 1.67 | 1.65 | 1.62 | 1.6 | 1.58 | 1.55 | 1.53 | 1.51 | 1.48 | 1.46 | 1.44 | 1.42 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4
Demand management (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Embedded generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Maximum Demand (MVA) - Option 1 Winter POE50 | 40.358 | 56.0239 | 60.0964 | 60.7906 | 61.3321 | 62.2643 | 64.3852 | 65.8049 | 67.6034 | 68.5369 | 69.3582 | 67.845 | 69.6185 | 72.4066 | 70.2908 | 70.2908 | 70.2908 | 70.2908 | 70.2908 | 70.2908 | 70.2908 | 70.2908 | 70.2908 | 70.2908 | 70.2908 | 70.2908 | 70.2908 | 70.2908 | 70.2908 | 70.2908
Total Maximum Demand (MVA) - Option 1 Winter POE10 | 43.208 | 58.6763 | 62.9078 | 63.5625 | 63.9783 | 64.8903 | 67.0443 | 68.2204 | 70.4608 | 77.2709 | 71.6566 | 70.5585 | 72.0408 | 75.2827 | 73.0883 | 73.0883 | 73.0883 | 73.0883 | 73.0883 | 73.0883 | 73.0883 | 73.0883 | 73.0883 | 73.0883 | 73.0883 | 73.0883 | 73.0883 | 73.0883 | 73.0883 | 73.0883
Summer Season | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Maximum Demand (MVA) - P50 | 47.5759 | 62.6589 | 66.7374 | 66.5999 | 66.5685 | 67.0184 | 67.5138 | 68.5409 | 69.2804 | 69.6733 | 70.0957 | 70.489 | 71.2143 | 72.1189 | 72.0364 | 72.0364 | 72.0364 | 72.0364 | 72.0364 | 72.0364 | 72.0364 | 72.0364 | 72.0364 | 72.0364 | 72.0364 | 72.0364 | 72.0364 | 72.0364 | 72.0364 | 72.0364
Maximum Demand (MVA) - P10 | 52.8554 | 67.9686 | 71.8961 | 71.6407 | 71.6305 | 72.0179 | 73.0705 | 73.7597 | 74.4432 | 75.2456 | 75.9785 | 76.6986 | 76.7643 | 77.6078 | 76.9357 | 76.9357 | 76.9357 | 76.9357 | 76.9357 | 76.9357 | 76.9357 | 76.9357 | 76.9357 | 76.9357 | 76.9357 | 76.9357 | 76.9357 | 76.9357 | 76.9357 | 76.9357
Block loads (MVA) not in the forecast | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Available Transfers (MVA) | 1.7 | 1.7 | 1.67 | 1.65 | 1.62 | 1.6 | 1.58 | 1.55 | 1.53 | 1.51 | 1.48 | 1.46 | 1.44 | 1.42 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4
Demand management (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Embedded generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Maximum Demand (MVA) - Option 1 Summer POE50 | 45.8759 | 60.9589 | 65.0674 | 64.9499 | 64.9485 | 65.4184 | 65.9338 | 66.9909 | 67.7504 | 68.1633 | 68.6157 | 69.029 | 69.7743 | 70.6989 | 70.6364 | 70.6364 | 70.6364 | 70.6364 | 70.6364 | 70.6364 | 70.6364 | 70.6364 | 70.6364 | 70.6364 | 70.6364 | 70.6364 | 70.6364 | 70.6364 | 70.6364 | 70.6364
Total Maximum Demand (MVA) - Option 1 Summer POE10 | 51.1554 | 66.2686 | 70.2261 | 69.9907 | 70.0105 | 70.4179 | 71.4905 | 72.2097 | 72.9132 | 73.7356 | 74.4985 | 75.2386 | 75.3243 | 76.1878 | 75.5357 | 75.5357 | 75.5357 | 75.5357 | 75.5357 | 75.5357 | 75.5357 | 75.5357 | 75.5357 | 75.5357 | 75.5357 | 75.5357 | 75.5357 | 75.5357 | 75.5357 | 75.5357
Option 2 - 1B New PHS ZSS + Three new feeders
Year | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Added Transfers (MVA) | 0 | 0 | 0 | 19.3333 | 19.3333 | 19.3333 | 19.3333 | 19.3333 | 19.3333 | 19.3333 | 19.3333 | 19.3333 | 19.3333 | 19.3333 | 19.3333 | 19.3333 | 19.3333 | 19.3333 | 19.3333 | 19.3333 | 19.3333 | 19.3333 | 19.3333 | 19.3333 | 19.3333 | 19.3333 | 19.3333 | 19.3333 | 19.3333 | 19.3333
Added Demand management (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Added Embedded generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Maximum Demand (MVA) - Option 2 Winter POE50 | 40.358 | 56.0239 | 60.0964 | 41.4573 | 41.9987 | 42.9309 | 45.0518 | 46.4716 | 48.2701 | 49.2036 | 50.0249 | 48.5117 | 50.2851 | 53.0732 | 50.9574 | 50.9574 | 50.9574 | 50.9574 | 50.9574 | 50.9574 | 50.9574 | 50.9574 | 50.9574 | 50.9574 | 50.9574 | 50.9574 | 50.9574 | 50.9574 | 50.9574 | 50.9574
Total Maximum Demand (MVA) - Option 2 Winter POE10 | 43.208 | 58.6763 | 62.9078 | 44.2292 | 44.6449 | 45.5569 | 47.711 | 48.8871 | 51.1274 | 57.9376 | 52.3233 | 51.2251 | 52.7075 | 55.9494 | 53.755 | 53.755 | 53.755 | 53.755 | 53.755 | 53.755 | 53.755 | 53.755 | 53.755 | 53.755 | 53.755 | 53.755 | 53.755 | 53.755 | 53.755 | 53.755
Total Maximum Demand (MVA) - Option 2 Summer POE50 | 45.8759 | 60.9589 | 65.0674 | 45.6165 | 45.6151 | 46.085 | 46.6005 | 47.6576 | 48.4171 | 48.83 | 49.2823 | 49.6957 | 50.441 | 51.3655 | 51.303 | 51.303 | 51.303 | 51.303 | 51.303 | 51.303 | 51.303 | 51.303 | 51.303 | 51.303 | 51.303 | 51.303 | 51.303 | 51.303 | 51.303 | 51.303
Total Maximum Demand (MVA) - Option 2 Summer POE10 | 51.1554 | 66.2686 | 70.2261 | 50.6574 | 50.6772 | 51.0846 | 52.1572 | 52.8764 | 53.5798 | 54.4023 | 55.1652 | 55.9052 | 55.991 | 56.8545 | 56.2023 | 56.2023 | 56.2023 | 56.2023 | 56.2023 | 56.2023 | 56.2023 | 56.2023 | 56.2023 | 56.2023 | 56.2023 | 56.2023 | 56.2023 | 56.2023 | 56.2023 | 56.2023
Option 3 - 2B PHM 3rd Tx + Switchroom + Two new feeders + OFR12 New Feeder
Year | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Added Transfers (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Added Demand management (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Added Embedded generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Maximum Demand (MVA) - Option 3 Winter POE50 | 40.358 | 56.0239 | 60.0964 | 60.7906 | 61.3321 | 62.2643 | 64.3852 | 65.8049 | 67.6034 | 68.5369 | 69.3582 | 67.845 | 69.6185 | 72.4066 | 70.2908 | 70.2908 | 70.2908 | 70.2908 | 70.2908 | 70.2908 | 70.2908 | 70.2908 | 70.2908 | 70.2908 | 70.2908 | 70.2908 | 70.2908 | 70.2908 | 70.2908 | 70.2908
Total Maximum Demand (MVA) - Option 3 Winter POE10 | 43.208 | 58.6763 | 62.9078 | 63.5625 | 63.9783 | 64.8903 | 67.0443 | 68.2204 | 70.4608 | 77.2709 | 71.6566 | 70.5585 | 72.0408 | 75.2827 | 73.0883 | 73.0883 | 73.0883 | 73.0883 | 73.0883 | 73.0883 | 73.0883 | 73.0883 | 73.0883 | 73.0883 | 73.0883 | 73.0883 | 73.0883 | 73.0883 | 73.0883 | 73.0883
Total Maximum Demand (MVA) - Option 3 Summer POE50 | 45.8759 | 60.9589 | 65.0674 | 64.9499 | 64.9485 | 65.4184 | 65.9338 | 66.9909 | 67.7504 | 68.1633 | 68.6157 | 69.029 | 69.7743 | 70.6989 | 70.6364 | 70.6364 | 70.6364 | 70.6364 | 70.6364 | 70.6364 | 70.6364 | 70.6364 | 70.6364 | 70.6364 | 70.6364 | 70.6364 | 70.6364 | 70.6364 | 70.6364 | 70.6364
Total Maximum Demand (MVA) - Option 3 Summer POE10 | 51.1554 | 66.2686 | 70.2261 | 69.9907 | 70.0105 | 70.4179 | 71.4905 | 72.2097 | 72.9132 | 73.7356 | 74.4985 | 75.2386 | 75.3243 | 76.1878 | 75.5357 | 75.5357 | 75.5357 | 75.5357 | 75.5357 | 75.5357 | 75.5357 | 75.5357 | 75.5357 | 75.5357 | 75.5357 | 75.5357 | 75.5357 | 75.5357 | 75.5357 | 75.5357
Option 4 - 3B OFR 3rd Tx + Switchroom + Two new feeders + OFR12 New Feeder
Year | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Added Transfers (MVA) | 0 | 0 | 0 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
Added Demand management (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Added Embedded generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Maximum Demand (MVA) - Option 4 Winter POE50 | 40.358 | 56.0239 | 60.0964 | 56.7906 | 57.3321 | 58.2643 | 60.3852 | 61.8049 | 63.6034 | 64.5369 | 65.3582 | 63.845 | 65.6185 | 68.4066 | 66.2908 | 66.2908 | 66.2908 | 66.2908 | 66.2908 | 66.2908 | 66.2908 | 66.2908 | 66.2908 | 66.2908 | 66.2908 | 66.2908 | 66.2908 | 66.2908 | 66.2908 | 66.2908
Total Maximum Demand (MVA) - Option 4 Winter POE10 | 43.208 | 58.6763 | 62.9078 | 59.5625 | 59.9783 | 60.8903 | 63.0443 | 64.2204 | 66.4608 | 73.2709 | 67.6566 | 66.5585 | 68.0408 | 71.2827 | 69.0883 | 69.0883 | 69.0883 | 69.0883 | 69.0883 | 69.0883 | 69.0883 | 69.0883 | 69.0883 | 69.0883 | 69.0883 | 69.0883 | 69.0883 | 69.0883 | 69.0883 | 69.0883
Total Maximum Demand (MVA) - Option 4 Summer POE50 | 45.8759 | 60.9589 | 65.0674 | 60.9499 | 60.9485 | 61.4184 | 61.9338 | 62.9909 | 63.7504 | 64.1633 | 64.6157 | 65.029 | 65.7743 | 66.6989 | 66.6364 | 66.6364 | 66.6364 | 66.6364 | 66.6364 | 66.6364 | 66.6364 | 66.6364 | 66.6364 | 66.6364 | 66.6364 | 66.6364 | 66.6364 | 66.6364 | 66.6364 | 66.6364
Total Maximum Demand (MVA) - Option 4 Summer POE10 | 51.1554 | 66.2686 | 70.2261 | 65.9907 | 66.0105 | 66.4179 | 67.4905 | 68.2097 | 68.9132 | 69.7356 | 70.4985 | 71.2386 | 71.3243 | 72.1878 | 71.5357 | 71.5357 | 71.5357 | 71.5357 | 71.5357 | 71.5357 | 71.5357 | 71.5357 | 71.5357 | 71.5357 | 71.5357 | 71.5357 | 71.5357 | 71.5357 | 71.5357 | 71.5357
Option 5 - 4B LLG 2nd Tx + Switchroom + Two new feeders + OFR12 New Feeder
Year | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Added Transfers (MVA) | 0 | 0 | 0 | 21.75 | 21.75 | 21.75 | 21.75 | 21.75 | 21.75 | 21.75 | 21.75 | 21.75 | 21.75 | 21.75 | 21.75 | 21.75 | 21.75 | 21.75 | 21.75 | 21.75 | 21.75 | 21.75 | 21.75 | 21.75 | 21.75 | 21.75 | 21.75 | 21.75 | 21.75 | 21.75
Added Demand management (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Added Embedded generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Maximum Demand (MVA) - Option 5 Winter POE50 | 40.358 | 56.0239 | 60.0964 | 39.0406 | 39.5821 | 40.5143 | 42.6352 | 44.0549 | 45.8534 | 46.7869 | 47.6082 | 46.095 | 47.8685 | 50.6566 | 48.5408 | 48.5408 | 48.5408 | 48.5408 | 48.5408 | 48.5408 | 48.5408 | 48.5408 | 48.5408 | 48.5408 | 48.5408 | 48.5408 | 48.5408 | 48.5408 | 48.5408 | 48.5408
Total Maximum Demand (MVA) - Option 5 Winter POE10 | 43.208 | 58.6763 | 62.9078 | 41.8125 | 42.2283 | 43.1403 | 45.2943 | 46.4704 | 48.7108 | 55.5209 | 49.9066 | 48.8085 | 50.2908 | 53.5327 | 51.3383 | 51.3383 | 51.3383 | 51.3383 | 51.3383 | 51.3383 | 51.3383 | 51.3383 | 51.3383 | 51.3383 | 51.3383 | 51.3383 | 51.3383 | 51.3383 | 51.3383 | 51.3383
Total Maximum Demand (MVA) - Option 5 Summer POE50 | 45.8759 | 60.9589 | 65.0674 | 43.1999 | 43.1985 | 43.6684 | 44.1838 | 45.2409 | 46.0004 | 46.4133 | 46.8657 | 47.279 | 48.0243 | 48.9489 | 48.8864 | 48.8864 | 48.8864 | 48.8864 | 48.8864 | 48.8864 | 48.8864 | 48.8864 | 48.8864 | 48.8864 | 48.8864 | 48.8864 | 48.8864 | 48.8864 | 48.8864 | 48.8864
Total Maximum Demand (MVA) - Option 5 Summer POE10 | 51.1554 | 66.2686 | 70.2261 | 48.2407 | 48.2605 | 48.6679 | 49.7405 | 50.4597 | 51.1632 | 51.9856 | 52.7485 | 53.4886 | 53.5743 | 54.4378 | 53.7857 | 53.7857 | 53.7857 | 53.7857 | 53.7857 | 53.7857 | 53.7857 | 53.7857 | 53.7857 | 53.7857 | 53.7857 | 53.7857 | 53.7857 | 53.7857 | 53.7857 | 53.7857
Option 6 -
Year | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Added Transfers (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Added Demand management (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Added Embedded generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Maximum Demand (MVA) - Option 6 Winter POE50 | 40.358 | 56.0239 | 60.0964 | 60.7906 | 61.3321 | 62.2643 | 64.3852 | 65.8049 | 67.6034 | 68.5369 | 69.3582 | 67.845 | 69.6185 | 72.4066 | 70.2908 | 70.2908 | 70.2908 | 70.2908 | 70.2908 | 70.2908 | 70.2908 | 70.2908 | 70.2908 | 70.2908 | 70.2908 | 70.2908 | 70.2908 | 70.2908 | 70.2908 | 70.2908
Total Maximum Demand (MVA) - Option 6 Winter POE10 | 43.208 | 58.6763 | 62.9078 | 63.5625 | 63.9783 | 64.8903 | 67.0443 | 68.2204 | 70.4608 | 77.2709 | 71.6566 | 70.5585 | 72.0408 | 75.2827 | 73.0883 | 73.0883 | 73.0883 | 73.0883 | 73.0883 | 73.0883 | 73.0883 | 73.0883 | 73.0883 | 73.0883 | 73.0883 | 73.0883 | 73.0883 | 73.0883 | 73.0883 | 73.0883
Total Maximum Demand (MVA) - Option 6 Summer POE50 | 45.8759 | 60.9589 | 65.0674 | 64.9499 | 64.9485 | 65.4184 | 65.9338 | 66.9909 | 67.7504 | 68.1633 | 68.6157 | 69.029 | 69.7743 | 70.6989 | 70.6364 | 70.6364 | 70.6364 | 70.6364 | 70.6364 | 70.6364 | 70.6364 | 70.6364 | 70.6364 | 70.6364 | 70.6364 | 70.6364 | 70.6364 | 70.6364 | 70.6364 | 70.6364
Total Maximum Demand (MVA) - Option 6 Summer POE10 | 51.1554 | 66.2686 | 70.2261 | 69.9907 | 70.0105 | 70.4179 | 71.4905 | 72.2097 | 72.9132 | 73.7356 | 74.4985 | 75.2386 | 75.3243 | 76.1878 | 75.5357 | 75.5357 | 75.5357 | 75.5357 | 75.5357 | 75.5357 | 75.5357 | 75.5357 | 75.5357 | 75.5357 | 75.5357 | 75.5357 | 75.5357 | 75.5357 | 75.5357 | 75.5357
Option 7 -
Year | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Added Transfers (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Added Demand management (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Added Embedded generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Maximum Demand (MVA) - Option 7 Winter POE50 | 40.358 | 56.0239 | 60.0964 | 60.7906 | 61.3321 | 62.2643 | 64.3852 | 65.8049 | 67.6034 | 68.5369 | 69.3582 | 67.845 | 69.6185 | 72.4066 | 70.2908 | 70.2908 | 70.2908 | 70.2908 | 70.2908 | 70.2908 | 70.2908 | 70.2908 | 70.2908 | 70.2908 | 70.2908 | 70.2908 | 70.2908 | 70.2908 | 70.2908 | 70.2908
Total Maximum Demand (MVA) - Option 7 Winter POE10 | 43.208 | 58.6763 | 62.9078 | 63.5625 | 63.9783 | 64.8903 | 67.0443 | 68.2204 | 70.4608 | 77.2709 | 71.6566 | 70.5585 | 72.0408 | 75.2827 | 73.0883 | 73.0883 | 73.0883 | 73.0883 | 73.0883 | 73.0883 | 73.0883 | 73.0883 | 73.0883 | 73.0883 | 73.0883 | 73.0883 | 73.0883 | 73.0883 | 73.0883 | 73.0883
Total Maximum Demand (MVA) - Option 7 Summer POE50 | 45.8759 | 60.9589 | 65.0674 | 64.9499 | 64.9485 | 65.4184 | 65.9338 | 66.9909 | 67.7504 | 68.1633 | 68.6157 | 69.029 | 69.7743 | 70.6989 | 70.6364 | 70.6364 | 70.6364 | 70.6364 | 70.6364 | 70.6364 | 70.6364 | 70.6364 | 70.6364 | 70.6364 | 70.6364 | 70.6364 | 70.6364 | 70.6364 | 70.6364 | 70.6364
Total Maximum Demand (MVA) - Option 7 Summer POE10 | 51.1554 | 66.2686 | 70.2261 | 69.9907 | 70.0105 | 70.4179 | 71.4905 | 72.2097 | 72.9132 | 73.7356 | 74.4985 | 75.2386 | 75.3243 | 76.1878 | 75.5357 | 75.5357 | 75.5357 | 75.5357 | 75.5357 | 75.5357 | 75.5357 | 75.5357 | 75.5357 | 75.5357 | 75.5357 | 75.5357 | 75.5357 | 75.5357 | 75.5357 | 75.5357
Option 8 -
Year | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Added Transfers (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Added Demand management (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Added Embedded generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Maximum Demand (MVA) - Option 8 Winter POE50 | 40.358 | 56.0239 | 60.0964 | 60.7906 | 61.3321 | 62.2643 | 64.3852 | 65.8049 | 67.6034 | 68.5369 | 69.3582 | 67.845 | 69.6185 | 72.4066 | 70.2908 | 70.2908 | 70.2908 | 70.2908 | 70.2908 | 70.2908 | 70.2908 | 70.2908 | 70.2908 | 70.2908 | 70.2908 | 70.2908 | 70.2908 | 70.2908 | 70.2908 | 70.2908
Total Maximum Demand (MVA) - Option 8 Winter POE10 | 43.208 | 58.6763 | 62.9078 | 63.5625 | 63.9783 | 64.8903 | 67.0443 | 68.2204 | 70.4608 | 77.2709 | 71.6566 | 70.5585 | 72.0408 | 75.2827 | 73.0883 | 73.0883 | 73.0883 | 73.0883 | 73.0883 | 73.0883 | 73.0883 | 73.0883 | 73.0883 | 73.0883 | 73.0883 | 73.0883 | 73.0883 | 73.0883 | 73.0883 | 73.0883
Total Maximum Demand (MVA) - Option 8 Summer POE50 | 45.8759 | 60.9589 | 65.0674 | 64.9499 | 64.9485 | 65.4184 | 65.9338 | 66.9909 | 67.7504 | 68.1633 | 68.6157 | 69.029 | 69.7743 | 70.6989 | 70.6364 | 70.6364 | 70.6364 | 70.6364 | 70.6364 | 70.6364 | 70.6364 | 70.6364 | 70.6364 | 70.6364 | 70.6364 | 70.6364 | 70.6364 | 70.6364 | 70.6364 | 70.6364
Total Maximum Demand (MVA) - Option 8 Summer POE10 | 51.1554 | 66.2686 | 70.2261 | 69.9907 | 70.0105 | 70.4179 | 71.4905 | 72.2097 | 72.9132 | 73.7356 | 74.4985 | 75.2386 | 75.3243 | 76.1878 | 75.5357 | 75.5357 | 75.5357 | 75.5357 | 75.5357 | 75.5357 | 75.5357 | 75.5357 | 75.5357 | 75.5357 | 75.5357 | 75.5357 | 75.5357 | 75.5357 | 75.5357 | 75.5357

## Forecasted LDC
Option 1 - Do Nothing / Base Case
Winter Season | [31 empty] | Winter Season
P50 | [31 empty] | P10
% of MD | Winter - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Winter - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 40.358 | 56.0239 | 60.0964 | 60.7906 | 61.3321 | 62.2643 | 64.3852 | 65.8049 | 67.6034 | 68.5369 | 69.3582 | 67.845 | 69.6185 | 72.4066 | 70.2908 | 70.2908 | 70.2908 | 70.2908 | 70.2908 | 70.2908 | 70.2908 | 70.2908 | 70.2908 | 70.2908 | 70.2908 | 70.2908 | 70.2908 | 70.2908 | 70.2908 | 70.2908 | 100% | 0 | 43.208 | 58.6763 | 62.9078 | 63.5625 | 63.9783 | 64.8903 | 67.0443 | 68.2204 | 70.4608 | 77.2709 | 71.6566 | 70.5585 | 72.0408 | 75.2827 | 73.0883 | 73.0883 | 73.0883 | 73.0883 | 73.0883 | 73.0883 | 73.0883 | 73.0883 | 73.0883 | 73.0883 | 73.0883 | 73.0883 | 73.0883 | 73.0883 | 73.0883 | 73.0883
99% | 1.486 | 39.9544 | 55.4636 | 59.4955 | 60.1827 | 60.7187 | 61.6416 | 63.7413 | 65.1468 | 66.9274 | 67.8516 | 68.6646 | 67.1665 | 68.9223 | 71.6825 | 69.5879 | 69.5879 | 69.5879 | 69.5879 | 69.5879 | 69.5879 | 69.5879 | 69.5879 | 69.5879 | 69.5879 | 69.5879 | 69.5879 | 69.5879 | 69.5879 | 69.5879 | 69.5879 | 99% | 1.486 | 42.7759 | 58.0895 | 62.2787 | 62.9269 | 63.3385 | 64.2414 | 66.3739 | 67.5382 | 69.7562 | 76.4982 | 70.9401 | 69.8529 | 71.3204 | 74.5299 | 72.3575 | 72.3575 | 72.3575 | 72.3575 | 72.3575 | 72.3575 | 72.3575 | 72.3575 | 72.3575 | 72.3575 | 72.3575 | 72.3575 | 72.3575 | 72.3575 | 72.3575 | 72.3575
98% | 3.2692 | 39.5508 | 54.9034 | 58.8945 | 59.5748 | 60.1054 | 61.019 | 63.0975 | 64.4888 | 66.2513 | 67.1662 | 67.9711 | 66.4881 | 68.2261 | 70.9584 | 68.885 | 68.885 | 68.885 | 68.885 | 68.885 | 68.885 | 68.885 | 68.885 | 68.885 | 68.885 | 68.885 | 68.885 | 68.885 | 68.885 | 68.885 | 68.885 | 98% | 3.2692 | 42.3438 | 57.5027 | 61.6497 | 62.2913 | 62.6987 | 63.5925 | 65.7034 | 66.856 | 69.0516 | 75.7255 | 70.2235 | 69.1473 | 70.6 | 73.7771 | 71.6266 | 71.6266 | 71.6266 | 71.6266 | 71.6266 | 71.6266 | 71.6266 | 71.6266 | 71.6266 | 71.6266 | 71.6266 | 71.6266 | 71.6266 | 71.6266 | 71.6266 | 71.6266
97% | 6.8356 | 39.1473 | 54.3431 | 58.2935 | 58.9669 | 59.4921 | 60.3964 | 62.4536 | 63.8307 | 65.5753 | 66.4808 | 67.2775 | 65.8096 | 67.5299 | 70.2344 | 68.1821 | 68.1821 | 68.1821 | 68.1821 | 68.1821 | 68.1821 | 68.1821 | 68.1821 | 68.1821 | 68.1821 | 68.1821 | 68.1821 | 68.1821 | 68.1821 | 68.1821 | 68.1821 | 97% | 6.8356 | 41.9118 | 56.916 | 61.0206 | 61.6557 | 62.0589 | 62.9436 | 65.033 | 66.1738 | 68.3469 | 74.9528 | 69.5069 | 68.4417 | 69.8796 | 73.0243 | 70.8957 | 70.8957 | 70.8957 | 70.8957 | 70.8957 | 70.8957 | 70.8957 | 70.8957 | 70.8957 | 70.8957 | 70.8957 | 70.8957 | 70.8957 | 70.8957 | 70.8957 | 70.8957
95% | 17.5347 | 38.3401 | 53.2227 | 57.0916 | 57.7511 | 58.2655 | 59.1511 | 61.1659 | 62.5146 | 64.2232 | 65.1101 | 65.8903 | 64.4527 | 66.1375 | 68.7862 | 66.7762 | 66.7762 | 66.7762 | 66.7762 | 66.7762 | 66.7762 | 66.7762 | 66.7762 | 66.7762 | 66.7762 | 66.7762 | 66.7762 | 66.7762 | 66.7762 | 66.7762 | 66.7762 | 95% | 17.5347 | 41.0476 | 55.7425 | 59.7624 | 60.3844 | 60.7794 | 61.6458 | 63.6921 | 64.8094 | 66.9377 | 73.4073 | 68.0738 | 67.0306 | 68.4388 | 71.5186 | 69.4339 | 69.4339 | 69.4339 | 69.4339 | 69.4339 | 69.4339 | 69.4339 | 69.4339 | 69.4339 | 69.4339 | 69.4339 | 69.4339 | 69.4339 | 69.4339 | 69.4339 | 69.4339
90% | 78.7576 | 36.3222 | 50.4215 | 54.0868 | 54.7116 | 55.1988 | 56.0379 | 57.9467 | 59.2244 | 60.8431 | 61.6833 | 62.4224 | 61.0605 | 62.6566 | 65.1659 | 63.2617 | 63.2617 | 63.2617 | 63.2617 | 63.2617 | 63.2617 | 63.2617 | 63.2617 | 63.2617 | 63.2617 | 63.2617 | 63.2617 | 63.2617 | 63.2617 | 63.2617 | 63.2617 | 90% | 78.7576 | 38.8872 | 52.8086 | 56.617 | 57.2063 | 57.5804 | 58.4013 | 60.3399 | 61.3984 | 63.4147 | 69.5438 | 64.491 | 63.5026 | 64.8368 | 67.7545 | 65.7795 | 65.7795 | 65.7795 | 65.7795 | 65.7795 | 65.7795 | 65.7795 | 65.7795 | 65.7795 | 65.7795 | 65.7795 | 65.7795 | 65.7795 | 65.7795 | 65.7795 | 65.7795
85% | 236.8672 | 34.3043 | 47.6203 | 51.082 | 51.672 | 52.1322 | 52.9246 | 54.7274 | 55.9342 | 57.4629 | 58.2564 | 58.9545 | 57.6682 | 59.1757 | 61.5456 | 59.7472 | 59.7472 | 59.7472 | 59.7472 | 59.7472 | 59.7472 | 59.7472 | 59.7472 | 59.7472 | 59.7472 | 59.7472 | 59.7472 | 59.7472 | 59.7472 | 59.7472 | 59.7472 | 85% | 236.8672 | 36.7268 | 49.8748 | 53.4716 | 54.0282 | 54.3815 | 55.1567 | 56.9877 | 57.9873 | 59.8917 | 65.6803 | 60.9081 | 59.9747 | 61.2347 | 63.9903 | 62.1251 | 62.1251 | 62.1251 | 62.1251 | 62.1251 | 62.1251 | 62.1251 | 62.1251 | 62.1251 | 62.1251 | 62.1251 | 62.1251 | 62.1251 | 62.1251 | 62.1251 | 62.1251
80% | 497.5104 | 32.2864 | 44.8191 | 48.0771 | 48.6325 | 49.0656 | 49.8114 | 51.5081 | 52.6439 | 54.0827 | 54.8296 | 55.4866 | 54.276 | 55.6948 | 57.9252 | 56.2326 | 56.2326 | 56.2326 | 56.2326 | 56.2326 | 56.2326 | 56.2326 | 56.2326 | 56.2326 | 56.2326 | 56.2326 | 56.2326 | 56.2326 | 56.2326 | 56.2326 | 56.2326 | 80% | 497.5104 | 34.5664 | 46.941 | 50.3262 | 50.85 | 51.1826 | 51.9122 | 53.6355 | 54.5763 | 56.3686 | 61.8167 | 57.3253 | 56.4468 | 57.6327 | 60.2262 | 58.4707 | 58.4707 | 58.4707 | 58.4707 | 58.4707 | 58.4707 | 58.4707 | 58.4707 | 58.4707 | 58.4707 | 58.4707 | 58.4707 | 58.4707 | 58.4707 | 58.4707 | 58.4707
75% | 803.6248 | 30.2685 | 42.0179 | 45.0723 | 45.593 | 45.999 | 46.6982 | 48.2889 | 49.3537 | 50.7026 | 51.4027 | 52.0187 | 50.8837 | 52.2138 | 54.3049 | 52.7181 | 52.7181 | 52.7181 | 52.7181 | 52.7181 | 52.7181 | 52.7181 | 52.7181 | 52.7181 | 52.7181 | 52.7181 | 52.7181 | 52.7181 | 52.7181 | 52.7181 | 52.7181 | 75% | 803.6248 | 32.406 | 44.0072 | 47.1809 | 47.6719 | 47.9837 | 48.6677 | 50.2832 | 51.1653 | 52.8456 | 57.9532 | 53.7425 | 52.9189 | 54.0306 | 56.4621 | 54.8163 | 54.8163 | 54.8163 | 54.8163 | 54.8163 | 54.8163 | 54.8163 | 54.8163 | 54.8163 | 54.8163 | 54.8163 | 54.8163 | 54.8163 | 54.8163 | 54.8163 | 54.8163
70% | 1155.2107 | 28.2506 | 39.2167 | 42.0675 | 42.5534 | 42.9324 | 43.585 | 45.0696 | 46.0634 | 47.3224 | 47.9759 | 48.5508 | 47.4915 | 48.7329 | 50.6846 | 49.2035 | 49.2035 | 49.2035 | 49.2035 | 49.2035 | 49.2035 | 49.2035 | 49.2035 | 49.2035 | 49.2035 | 49.2035 | 49.2035 | 49.2035 | 49.2035 | 49.2035 | 49.2035 | 70% | 1155.2107 | 30.2456 | 41.0734 | 44.0355 | 44.4938 | 44.7848 | 45.4232 | 46.931 | 47.7543 | 49.3225 | 54.0896 | 50.1596 | 49.3909 | 50.4286 | 52.6979 | 51.1618 | 51.1618 | 51.1618 | 51.1618 | 51.1618 | 51.1618 | 51.1618 | 51.1618 | 51.1618 | 51.1618 | 51.1618 | 51.1618 | 51.1618 | 51.1618 | 51.1618 | 51.1618
65% | 1553.1596 | 26.2327 | 36.4155 | 39.0627 | 39.5139 | 39.8658 | 40.4718 | 41.8504 | 42.7732 | 43.9422 | 44.549 | 45.0828 | 44.0992 | 45.252 | 47.0643 | 45.689 | 45.689 | 45.689 | 45.689 | 45.689 | 45.689 | 45.689 | 45.689 | 45.689 | 45.689 | 45.689 | 45.689 | 45.689 | 45.689 | 45.689 | 45.689 | 65% | 1553.1596 | 28.0852 | 38.1396 | 40.8901 | 41.3157 | 41.5859 | 42.1787 | 43.5788 | 44.3433 | 45.7995 | 50.2261 | 46.5768 | 45.863 | 46.8266 | 48.9338 | 47.5074 | 47.5074 | 47.5074 | 47.5074 | 47.5074 | 47.5074 | 47.5074 | 47.5074 | 47.5074 | 47.5074 | 47.5074 | 47.5074 | 47.5074 | 47.5074 | 47.5074 | 47.5074
60% | 2026.2996 | 24.2148 | 33.6143 | 36.0579 | 36.4744 | 36.7992 | 37.3586 | 38.6311 | 39.4829 | 40.562 | 41.1222 | 41.6149 | 40.707 | 41.7711 | 43.4439 | 42.1745 | 42.1745 | 42.1745 | 42.1745 | 42.1745 | 42.1745 | 42.1745 | 42.1745 | 42.1745 | 42.1745 | 42.1745 | 42.1745 | 42.1745 | 42.1745 | 42.1745 | 42.1745 | 60% | 2026.2996 | 25.9248 | 35.2058 | 37.7447 | 38.1375 | 38.387 | 38.9342 | 40.2266 | 40.9322 | 42.2765 | 46.3625 | 42.994 | 42.3351 | 43.2245 | 45.1696 | 43.853 | 43.853 | 43.853 | 43.853 | 43.853 | 43.853 | 43.853 | 43.853 | 43.853 | 43.853 | 43.853 | 43.853 | 43.853 | 43.853 | 43.853 | 43.853
55% | 2598.4068 | 22.1969 | 30.8131 | 33.053 | 33.4348 | 33.7326 | 34.2454 | 35.4119 | 36.1927 | 37.1819 | 37.6953 | 38.147 | 37.3147 | 38.2902 | 39.8236 | 38.6599 | 38.6599 | 38.6599 | 38.6599 | 38.6599 | 38.6599 | 38.6599 | 38.6599 | 38.6599 | 38.6599 | 38.6599 | 38.6599 | 38.6599 | 38.6599 | 38.6599 | 38.6599 | 55% | 2598.4068 | 23.7644 | 32.272 | 34.5993 | 34.9594 | 35.188 | 35.6897 | 36.8744 | 37.5212 | 38.7534 | 42.499 | 39.4111 | 38.8072 | 39.6225 | 41.4055 | 40.1986 | 40.1986 | 40.1986 | 40.1986 | 40.1986 | 40.1986 | 40.1986 | 40.1986 | 40.1986 | 40.1986 | 40.1986 | 40.1986 | 40.1986 | 40.1986 | 40.1986 | 40.1986
50% | 3233.5201 | 20.179 | 28.0119 | 30.0482 | 30.3953 | 30.666 | 31.1321 | 32.1926 | 32.9024 | 33.8017 | 34.2685 | 34.6791 | 33.9225 | 34.8092 | 36.2033 | 35.1454 | 35.1454 | 35.1454 | 35.1454 | 35.1454 | 35.1454 | 35.1454 | 35.1454 | 35.1454 | 35.1454 | 35.1454 | 35.1454 | 35.1454 | 35.1454 | 35.1454 | 35.1454 | 50% | 3233.5201 | 21.604 | 29.3381 | 31.4539 | 31.7813 | 31.9891 | 32.4451 | 33.5222 | 34.1102 | 35.2304 | 38.6354 | 35.8283 | 35.2792 | 36.0204 | 37.6414 | 36.5442 | 36.5442 | 36.5442 | 36.5442 | 36.5442 | 36.5442 | 36.5442 | 36.5442 | 36.5442 | 36.5442 | 36.5442 | 36.5442 | 36.5442 | 36.5442 | 36.5442 | 36.5442
45% | 3775.313 | 18.1611 | 25.2107 | 27.0434 | 27.3558 | 27.5994 | 28.0189 | 28.9733 | 29.6122 | 30.4215 | 30.8416 | 31.2112 | 30.5302 | 31.3283 | 32.583 | 31.6309 | 31.6309 | 31.6309 | 31.6309 | 31.6309 | 31.6309 | 31.6309 | 31.6309 | 31.6309 | 31.6309 | 31.6309 | 31.6309 | 31.6309 | 31.6309 | 31.6309 | 31.6309 | 45% | 3775.313 | 19.4436 | 26.4043 | 28.3085 | 28.6031 | 28.7902 | 29.2006 | 30.1699 | 30.6992 | 31.7073 | 34.7719 | 32.2455 | 31.7513 | 32.4184 | 33.8772 | 32.8898 | 32.8898 | 32.8898 | 32.8898 | 32.8898 | 32.8898 | 32.8898 | 32.8898 | 32.8898 | 32.8898 | 32.8898 | 32.8898 | 32.8898 | 32.8898 | 32.8898 | 32.8898
40% | 4072.8088 | 16.1432 | 22.4095 | 24.0386 | 24.3162 | 24.5328 | 24.9057 | 25.7541 | 26.322 | 27.0414 | 27.4148 | 27.7433 | 27.138 | 27.8474 | 28.9626 | 28.1163 | 28.1163 | 28.1163 | 28.1163 | 28.1163 | 28.1163 | 28.1163 | 28.1163 | 28.1163 | 28.1163 | 28.1163 | 28.1163 | 28.1163 | 28.1163 | 28.1163 | 28.1163 | 40% | 4072.8088 | 17.2832 | 23.4705 | 25.1631 | 25.425 | 25.5913 | 25.9561 | 26.8177 | 27.2882 | 28.1843 | 30.9084 | 28.6627 | 28.2234 | 28.8163 | 30.1131 | 29.2353 | 29.2353 | 29.2353 | 29.2353 | 29.2353 | 29.2353 | 29.2353 | 29.2353 | 29.2353 | 29.2353 | 29.2353 | 29.2353 | 29.2353 | 29.2353 | 29.2353 | 29.2353
35% | 4198.821 | 14.1253 | 19.6083 | 21.0337 | 21.2767 | 21.4662 | 21.7925 | 22.5348 | 23.0317 | 23.6612 | 23.9879 | 24.2754 | 23.7457 | 24.3665 | 25.3423 | 24.6018 | 24.6018 | 24.6018 | 24.6018 | 24.6018 | 24.6018 | 24.6018 | 24.6018 | 24.6018 | 24.6018 | 24.6018 | 24.6018 | 24.6018 | 24.6018 | 24.6018 | 24.6018 | 35% | 4198.821 | 15.1228 | 20.5367 | 22.0177 | 22.2469 | 22.3924 | 22.7116 | 23.4655 | 23.8771 | 24.6613 | 27.0448 | 25.0798 | 24.6955 | 25.2143 | 26.349 | 25.5809 | 25.5809 | 25.5809 | 25.5809 | 25.5809 | 25.5809 | 25.5809 | 25.5809 | 25.5809 | 25.5809 | 25.5809 | 25.5809 | 25.5809 | 25.5809 | 25.5809 | 25.5809
30% | 4271.3374 | 12.1074 | 16.8072 | 18.0289 | 18.2372 | 18.3996 | 18.6793 | 19.3156 | 19.7415 | 20.281 | 20.5611 | 20.8075 | 20.3535 | 20.8855 | 21.722 | 21.0872 | 21.0872 | 21.0872 | 21.0872 | 21.0872 | 21.0872 | 21.0872 | 21.0872 | 21.0872 | 21.0872 | 21.0872 | 21.0872 | 21.0872 | 21.0872 | 21.0872 | 21.0872 | 30% | 4271.3374 | 12.9624 | 17.6029 | 18.8723 | 19.0688 | 19.1935 | 19.4671 | 20.1133 | 20.4661 | 21.1382 | 23.1813 | 21.497 | 21.1675 | 21.6123 | 22.5848 | 21.9265 | 21.9265 | 21.9265 | 21.9265 | 21.9265 | 21.9265 | 21.9265 | 21.9265 | 21.9265 | 21.9265 | 21.9265 | 21.9265 | 21.9265 | 21.9265 | 21.9265 | 21.9265
25% | 4321.8611 | 10.0895 | 14.006 | 15.0241 | 15.1977 | 15.333 | 15.5661 | 16.0963 | 16.4512 | 16.9009 | 17.1342 | 17.3396 | 16.9612 | 17.4046 | 18.1016 | 17.5727 | 17.5727 | 17.5727 | 17.5727 | 17.5727 | 17.5727 | 17.5727 | 17.5727 | 17.5727 | 17.5727 | 17.5727 | 17.5727 | 17.5727 | 17.5727 | 17.5727 | 17.5727 | 25% | 4321.8611 | 10.802 | 14.6691 | 15.727 | 15.8906 | 15.9946 | 16.2226 | 16.7611 | 17.0551 | 17.6152 | 19.3177 | 17.9142 | 17.6396 | 18.0102 | 18.8207 | 18.2721 | 18.2721 | 18.2721 | 18.2721 | 18.2721 | 18.2721 | 18.2721 | 18.2721 | 18.2721 | 18.2721 | 18.2721 | 18.2721 | 18.2721 | 18.2721 | 18.2721 | 18.2721
20% | 4353.067 | 8.0716 | 11.2048 | 12.0193 | 12.1581 | 12.2664 | 12.4529 | 12.877 | 13.161 | 13.5207 | 13.7074 | 13.8716 | 13.569 | 13.9237 | 14.4813 | 14.0582 | 14.0582 | 14.0582 | 14.0582 | 14.0582 | 14.0582 | 14.0582 | 14.0582 | 14.0582 | 14.0582 | 14.0582 | 14.0582 | 14.0582 | 14.0582 | 14.0582 | 14.0582 | 20% | 4353.067 | 8.6416 | 11.7353 | 12.5816 | 12.7125 | 12.7957 | 12.9781 | 13.4089 | 13.6441 | 14.0922 | 15.4542 | 14.3313 | 14.1117 | 14.4082 | 15.0565 | 14.6177 | 14.6177 | 14.6177 | 14.6177 | 14.6177 | 14.6177 | 14.6177 | 14.6177 | 14.6177 | 14.6177 | 14.6177 | 14.6177 | 14.6177 | 14.6177 | 14.6177 | 14.6177
15% | 4369.4129 | 6.0537 | 8.4036 | 9.0145 | 9.1186 | 9.1998 | 9.3396 | 9.6578 | 9.8707 | 10.1405 | 10.2805 | 10.4037 | 10.1767 | 10.4428 | 10.861 | 10.5436 | 10.5436 | 10.5436 | 10.5436 | 10.5436 | 10.5436 | 10.5436 | 10.5436 | 10.5436 | 10.5436 | 10.5436 | 10.5436 | 10.5436 | 10.5436 | 10.5436 | 10.5436 | 15% | 4369.4129 | 6.4812 | 8.8014 | 9.4362 | 9.5344 | 9.5967 | 9.7335 | 10.0566 | 10.2331 | 10.5691 | 11.5906 | 10.7485 | 10.5838 | 10.8061 | 11.2924 | 10.9633 | 10.9633 | 10.9633 | 10.9633 | 10.9633 | 10.9633 | 10.9633 | 10.9633 | 10.9633 | 10.9633 | 10.9633 | 10.9633 | 10.9633 | 10.9633 | 10.9633 | 10.9633
10% | 4378.6261 | 4.0358 | 5.6024 | 6.0096 | 6.0791 | 6.1332 | 6.2264 | 6.4385 | 6.5805 | 6.7603 | 6.8537 | 6.9358 | 6.7845 | 6.9618 | 7.2407 | 7.0291 | 7.0291 | 7.0291 | 7.0291 | 7.0291 | 7.0291 | 7.0291 | 7.0291 | 7.0291 | 7.0291 | 7.0291 | 7.0291 | 7.0291 | 7.0291 | 7.0291 | 7.0291 | 10% | 4378.6261 | 4.3208 | 5.8676 | 6.2908 | 6.3563 | 6.3978 | 6.489 | 6.7044 | 6.822 | 7.0461 | 7.7271 | 7.1657 | 7.0558 | 7.2041 | 7.5283 | 7.3088 | 7.3088 | 7.3088 | 7.3088 | 7.3088 | 7.3088 | 7.3088 | 7.3088 | 7.3088 | 7.3088 | 7.3088 | 7.3088 | 7.3088 | 7.3088 | 7.3088 | 7.3088
5% | 4391.7028 | 2.0179 | 2.8012 | 3.0048 | 3.0395 | 3.0666 | 3.1132 | 3.2193 | 3.2902 | 3.3802 | 3.4268 | 3.4679 | 3.3922 | 3.4809 | 3.6203 | 3.5145 | 3.5145 | 3.5145 | 3.5145 | 3.5145 | 3.5145 | 3.5145 | 3.5145 | 3.5145 | 3.5145 | 3.5145 | 3.5145 | 3.5145 | 3.5145 | 3.5145 | 3.5145 | 5% | 4391.7028 | 2.1604 | 2.9338 | 3.1454 | 3.1781 | 3.1989 | 3.2445 | 3.3522 | 3.411 | 3.523 | 3.8635 | 3.5828 | 3.5279 | 3.602 | 3.7641 | 3.6544 | 3.6544 | 3.6544 | 3.6544 | 3.6544 | 3.6544 | 3.6544 | 3.6544 | 3.6544 | 3.6544 | 3.6544 | 3.6544 | 3.6544 | 3.6544 | 3.6544 | 3.6544
9.992e-14% | 4391.7028 | 4.0326e-14 | 5.5979e-14 | 6.0048e-14 | 6.0742e-14 | 6.1283e-14 | 6.2215e-14 | 6.4334e-14 | 6.5752e-14 | 6.7549e-14 | 6.8482e-14 | 6.9303e-14 | 6.7791e-14 | 6.9563e-14 | 7.2349e-14 | 7.0235e-14 | 7.0235e-14 | 7.0235e-14 | 7.0235e-14 | 7.0235e-14 | 7.0235e-14 | 7.0235e-14 | 7.0235e-14 | 7.0235e-14 | 7.0235e-14 | 7.0235e-14 | 7.0235e-14 | 7.0235e-14 | 7.0235e-14 | 7.0235e-14 | 7.0235e-14 | 9.992e-14% | 4391.7028 | 4.3173e-14 | 5.8629e-14 | 6.2858e-14 | 6.3512e-14 | 6.3927e-14 | 6.4838e-14 | 6.6991e-14 | 6.8166e-14 | 7.0404e-14 | 7.7209e-14 | 7.1599e-14 | 7.0502e-14 | 7.1983e-14 | 7.5223e-14 | 7.303e-14 | 7.303e-14 | 7.303e-14 | 7.303e-14 | 7.303e-14 | 7.303e-14 | 7.303e-14 | 7.303e-14 | 7.303e-14 | 7.303e-14 | 7.303e-14 | 7.303e-14 | 7.303e-14 | 7.303e-14 | 7.303e-14 | 7.303e-14
Summer Season | [31 empty] | Summer Season
P50 | [31 empty] | P10
% of MD | Summer - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Summer - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 45.8759 | 60.9589 | 65.0674 | 64.9499 | 64.9485 | 65.4184 | 65.9338 | 66.9909 | 67.7504 | 68.1633 | 68.6157 | 69.029 | 69.7743 | 70.6989 | 70.6364 | 70.6364 | 70.6364 | 70.6364 | 70.6364 | 70.6364 | 70.6364 | 70.6364 | 70.6364 | 70.6364 | 70.6364 | 70.6364 | 70.6364 | 70.6364 | 70.6364 | 70.6364 | 100% | 0 | 51.1554 | 66.2686 | 70.2261 | 69.9907 | 70.0105 | 70.4179 | 71.4905 | 72.2097 | 72.9132 | 73.7356 | 74.4985 | 75.2386 | 75.3243 | 76.1878 | 75.5357 | 75.5357 | 75.5357 | 75.5357 | 75.5357 | 75.5357 | 75.5357 | 75.5357 | 75.5357 | 75.5357 | 75.5357 | 75.5357 | 75.5357 | 75.5357 | 75.5357 | 75.5357
99% | 0 | 45.4171 | 60.3493 | 64.4168 | 64.3004 | 64.299 | 64.7642 | 65.2745 | 66.321 | 67.0729 | 67.4817 | 67.9295 | 68.3387 | 69.0766 | 69.9919 | 69.93 | 69.93 | 69.93 | 69.93 | 69.93 | 69.93 | 69.93 | 69.93 | 69.93 | 69.93 | 69.93 | 69.93 | 69.93 | 69.93 | 69.93 | 69.93 | 99% | 1.5127 | 50.6438 | 65.6059 | 69.5238 | 69.2908 | 69.3104 | 69.7137 | 70.7756 | 71.4876 | 72.184 | 72.9983 | 73.7535 | 74.4862 | 74.571 | 75.4259 | 74.7803 | 74.7803 | 74.7803 | 74.7803 | 74.7803 | 74.7803 | 74.7803 | 74.7803 | 74.7803 | 74.7803 | 74.7803 | 74.7803 | 74.7803 | 74.7803 | 74.7803 | 74.7803
98% | 0 | 44.9584 | 59.7397 | 63.7661 | 63.6509 | 63.6495 | 64.11 | 64.6151 | 65.6511 | 66.3954 | 66.8001 | 67.2434 | 67.6484 | 68.3788 | 69.2849 | 69.2236 | 69.2236 | 69.2236 | 69.2236 | 69.2236 | 69.2236 | 69.2236 | 69.2236 | 69.2236 | 69.2236 | 69.2236 | 69.2236 | 69.2236 | 69.2236 | 69.2236 | 69.2236 | 98% | 2.269 | 50.1322 | 64.9433 | 68.8216 | 68.5909 | 68.6103 | 69.0096 | 70.0607 | 70.7655 | 71.4549 | 72.2609 | 73.0085 | 73.7338 | 73.8178 | 74.664 | 74.0249 | 74.0249 | 74.0249 | 74.0249 | 74.0249 | 74.0249 | 74.0249 | 74.0249 | 74.0249 | 74.0249 | 74.0249 | 74.0249 | 74.0249 | 74.0249 | 74.0249 | 74.0249
97% | 0.37816 | 44.4996 | 59.1301 | 63.1154 | 63.0014 | 63 | 63.4558 | 63.9558 | 64.9812 | 65.7179 | 66.1184 | 66.5572 | 66.9581 | 67.6811 | 68.5779 | 68.5173 | 68.5173 | 68.5173 | 68.5173 | 68.5173 | 68.5173 | 68.5173 | 68.5173 | 68.5173 | 68.5173 | 68.5173 | 68.5173 | 68.5173 | 68.5173 | 68.5173 | 68.5173 | 97% | 3.7816 | 49.6207 | 64.2806 | 68.1193 | 67.891 | 67.9102 | 68.3054 | 69.3458 | 70.0434 | 70.7258 | 71.5236 | 72.2636 | 72.9814 | 73.0646 | 73.9022 | 73.2696 | 73.2696 | 73.2696 | 73.2696 | 73.2696 | 73.2696 | 73.2696 | 73.2696 | 73.2696 | 73.2696 | 73.2696 | 73.2696 | 73.2696 | 73.2696 | 73.2696 | 73.2696
95% | 2.269 | 43.5821 | 57.911 | 61.8141 | 61.7024 | 61.701 | 62.1474 | 62.6371 | 63.6414 | 64.3629 | 64.7552 | 65.1849 | 65.5776 | 66.2856 | 67.1639 | 67.1046 | 67.1046 | 67.1046 | 67.1046 | 67.1046 | 67.1046 | 67.1046 | 67.1046 | 67.1046 | 67.1046 | 67.1046 | 67.1046 | 67.1046 | 67.1046 | 67.1046 | 67.1046 | 95% | 6.0506 | 48.5976 | 62.9552 | 66.7148 | 66.4912 | 66.51 | 66.897 | 67.916 | 68.5992 | 69.2675 | 70.0488 | 70.7736 | 71.4766 | 71.5581 | 72.3784 | 71.7589 | 71.7589 | 71.7589 | 71.7589 | 71.7589 | 71.7589 | 71.7589 | 71.7589 | 71.7589 | 71.7589 | 71.7589 | 71.7589 | 71.7589 | 71.7589 | 71.7589 | 71.7589
90% | 5.6725 | 41.2883 | 54.863 | 58.5607 | 58.4549 | 58.4536 | 58.8765 | 59.3404 | 60.2918 | 60.9754 | 61.347 | 61.7541 | 62.1261 | 62.7969 | 63.629 | 63.5727 | 63.5727 | 63.5727 | 63.5727 | 63.5727 | 63.5727 | 63.5727 | 63.5727 | 63.5727 | 63.5727 | 63.5727 | 63.5727 | 63.5727 | 63.5727 | 63.5727 | 63.5727 | 90% | 16.2611 | 46.0398 | 59.6418 | 63.2035 | 62.9917 | 63.0094 | 63.3761 | 64.3415 | 64.9887 | 65.6218 | 66.3621 | 67.0487 | 67.7147 | 67.7919 | 68.569 | 67.9821 | 67.9821 | 67.9821 | 67.9821 | 67.9821 | 67.9821 | 67.9821 | 67.9821 | 67.9821 | 67.9821 | 67.9821 | 67.9821 | 67.9821 | 67.9821 | 67.9821 | 67.9821
85% | 15.8829 | 38.9945 | 51.8151 | 55.3073 | 55.2074 | 55.2062 | 55.6056 | 56.0437 | 56.9423 | 57.5879 | 57.9388 | 58.3233 | 58.6747 | 59.3082 | 60.094 | 60.0409 | 60.0409 | 60.0409 | 60.0409 | 60.0409 | 60.0409 | 60.0409 | 60.0409 | 60.0409 | 60.0409 | 60.0409 | 60.0409 | 60.0409 | 60.0409 | 60.0409 | 60.0409 | 85% | 26.4715 | 43.482 | 56.3283 | 59.6922 | 59.4921 | 59.5089 | 59.8552 | 60.767 | 61.3783 | 61.9762 | 62.6753 | 63.3237 | 63.9528 | 64.0256 | 64.7596 | 64.2053 | 64.2053 | 64.2053 | 64.2053 | 64.2053 | 64.2053 | 64.2053 | 64.2053 | 64.2053 | 64.2053 | 64.2053 | 64.2053 | 64.2053 | 64.2053 | 64.2053 | 64.2053
80% | 31.0095 | 36.7007 | 48.7671 | 52.0539 | 51.9599 | 51.9588 | 52.3347 | 52.747 | 53.5928 | 54.2003 | 54.5307 | 54.8925 | 55.2232 | 55.8194 | 56.5591 | 56.5091 | 56.5091 | 56.5091 | 56.5091 | 56.5091 | 56.5091 | 56.5091 | 56.5091 | 56.5091 | 56.5091 | 56.5091 | 56.5091 | 56.5091 | 56.5091 | 56.5091 | 56.5091 | 80% | 34.0348 | 40.9243 | 53.0149 | 56.1809 | 55.9926 | 56.0084 | 56.3343 | 57.1924 | 57.7678 | 58.3305 | 58.9885 | 59.5988 | 60.1908 | 60.2594 | 60.9502 | 60.4285 | 60.4285 | 60.4285 | 60.4285 | 60.4285 | 60.4285 | 60.4285 | 60.4285 | 60.4285 | 60.4285 | 60.4285 | 60.4285 | 60.4285 | 60.4285 | 60.4285 | 60.4285
75% | 72.9857 | 34.4069 | 45.7192 | 48.8006 | 48.7124 | 48.7113 | 49.0638 | 49.4504 | 50.2432 | 50.8128 | 51.1225 | 51.4618 | 51.7718 | 52.3307 | 53.0241 | 52.9773 | 52.9773 | 52.9773 | 52.9773 | 52.9773 | 52.9773 | 52.9773 | 52.9773 | 52.9773 | 52.9773 | 52.9773 | 52.9773 | 52.9773 | 52.9773 | 52.9773 | 52.9773 | 75% | 48.405 | 38.3665 | 49.7015 | 52.6696 | 52.493 | 52.5079 | 52.8134 | 53.6179 | 54.1573 | 54.6849 | 55.3017 | 55.8739 | 56.4289 | 56.4932 | 57.1408 | 56.6517 | 56.6517 | 56.6517 | 56.6517 | 56.6517 | 56.6517 | 56.6517 | 56.6517 | 56.6517 | 56.6517 | 56.6517 | 56.6517 | 56.6517 | 56.6517 | 56.6517 | 56.6517
70% | 150.5094 | 32.1131 | 42.6712 | 45.5472 | 45.4649 | 45.4639 | 45.7929 | 46.1537 | 46.8937 | 47.4253 | 47.7143 | 48.031 | 48.3203 | 48.842 | 49.4892 | 49.4455 | 49.4455 | 49.4455 | 49.4455 | 49.4455 | 49.4455 | 49.4455 | 49.4455 | 49.4455 | 49.4455 | 49.4455 | 49.4455 | 49.4455 | 49.4455 | 49.4455 | 49.4455 | 70% | 76.3892 | 35.8087 | 46.388 | 49.1583 | 48.9935 | 49.0073 | 49.2925 | 50.0434 | 50.5468 | 51.0392 | 51.6149 | 52.149 | 52.667 | 52.727 | 53.3315 | 52.875 | 52.875 | 52.875 | 52.875 | 52.875 | 52.875 | 52.875 | 52.875 | 52.875 | 52.875 | 52.875 | 52.875 | 52.875 | 52.875 | 52.875 | 52.875
65% | 359.6342 | 29.8193 | 39.6233 | 42.2938 | 42.2174 | 42.2165 | 42.5219 | 42.857 | 43.5441 | 44.0378 | 44.3062 | 44.6002 | 44.8689 | 45.3533 | 45.9543 | 45.9136 | 45.9136 | 45.9136 | 45.9136 | 45.9136 | 45.9136 | 45.9136 | 45.9136 | 45.9136 | 45.9136 | 45.9136 | 45.9136 | 45.9136 | 45.9136 | 45.9136 | 45.9136 | 65% | 114.2056 | 33.251 | 43.0746 | 45.647 | 45.494 | 45.5068 | 45.7716 | 46.4689 | 46.9363 | 47.3936 | 47.9282 | 48.424 | 48.9051 | 48.9608 | 49.5221 | 49.0982 | 49.0982 | 49.0982 | 49.0982 | 49.0982 | 49.0982 | 49.0982 | 49.0982 | 49.0982 | 49.0982 | 49.0982 | 49.0982 | 49.0982 | 49.0982 | 49.0982 | 49.0982
60% | 689.7717 | 27.5255 | 36.5753 | 39.0405 | 38.9699 | 38.9691 | 39.251 | 39.5603 | 40.1946 | 40.6503 | 40.898 | 41.1694 | 41.4174 | 41.8646 | 42.4193 | 42.3818 | 42.3818 | 42.3818 | 42.3818 | 42.3818 | 42.3818 | 42.3818 | 42.3818 | 42.3818 | 42.3818 | 42.3818 | 42.3818 | 42.3818 | 42.3818 | 42.3818 | 42.3818 | 60% | 178.1154 | 30.6932 | 39.7612 | 42.1357 | 41.9944 | 42.0063 | 42.2508 | 42.8943 | 43.3258 | 43.7479 | 44.2414 | 44.6991 | 45.1431 | 45.1946 | 45.7127 | 45.3214 | 45.3214 | 45.3214 | 45.3214 | 45.3214 | 45.3214 | 45.3214 | 45.3214 | 45.3214 | 45.3214 | 45.3214 | 45.3214 | 45.3214 | 45.3214 | 45.3214 | 45.3214
55% | 1095.5419 | 25.2317 | 33.5274 | 35.7871 | 35.7224 | 35.7217 | 35.9801 | 36.2636 | 36.845 | 37.2627 | 37.4898 | 37.7386 | 37.966 | 38.3759 | 38.8844 | 38.85 | 38.85 | 38.85 | 38.85 | 38.85 | 38.85 | 38.85 | 38.85 | 38.85 | 38.85 | 38.85 | 38.85 | 38.85 | 38.85 | 38.85 | 38.85 | 55% | 311.6074 | 28.1354 | 36.4477 | 38.6243 | 38.4949 | 38.5058 | 38.7299 | 39.3198 | 39.7153 | 40.1022 | 40.5546 | 40.9742 | 41.3812 | 41.4284 | 41.9033 | 41.5446 | 41.5446 | 41.5446 | 41.5446 | 41.5446 | 41.5446 | 41.5446 | 41.5446 | 41.5446 | 41.5446 | 41.5446 | 41.5446 | 41.5446 | 41.5446 | 41.5446 | 41.5446
50% | 1666.1918 | 22.9379 | 30.4794 | 32.5337 | 32.4749 | 32.4742 | 32.7092 | 32.9669 | 33.4955 | 33.8752 | 34.0817 | 34.3078 | 34.5145 | 34.8872 | 35.3494 | 35.3182 | 35.3182 | 35.3182 | 35.3182 | 35.3182 | 35.3182 | 35.3182 | 35.3182 | 35.3182 | 35.3182 | 35.3182 | 35.3182 | 35.3182 | 35.3182 | 35.3182 | 35.3182 | 50% | 636.0723 | 25.5777 | 33.1343 | 35.113 | 34.9954 | 35.0052 | 35.209 | 35.7453 | 36.1049 | 36.4566 | 36.8678 | 37.2493 | 37.6193 | 37.6621 | 38.0939 | 37.7678 | 37.7678 | 37.7678 | 37.7678 | 37.7678 | 37.7678 | 37.7678 | 37.7678 | 37.7678 | 37.7678 | 37.7678 | 37.7678 | 37.7678 | 37.7678 | 37.7678 | 37.7678
45% | 2506.0947 | 20.6442 | 27.4315 | 29.2803 | 29.2274 | 29.2268 | 29.4383 | 29.6702 | 30.1459 | 30.4877 | 30.6735 | 30.8771 | 31.0631 | 31.3984 | 31.8145 | 31.7864 | 31.7864 | 31.7864 | 31.7864 | 31.7864 | 31.7864 | 31.7864 | 31.7864 | 31.7864 | 31.7864 | 31.7864 | 31.7864 | 31.7864 | 31.7864 | 31.7864 | 31.7864 | 45% | 1179.4944 | 23.0199 | 29.8209 | 31.6017 | 31.4958 | 31.5047 | 31.6881 | 32.1707 | 32.4944 | 32.8109 | 33.181 | 33.5243 | 33.8573 | 33.8959 | 34.2845 | 33.991 | 33.991 | 33.991 | 33.991 | 33.991 | 33.991 | 33.991 | 33.991 | 33.991 | 33.991 | 33.991 | 33.991 | 33.991 | 33.991 | 33.991 | 33.991
40% | 3164.4787 | 18.3504 | 24.3836 | 26.027 | 25.9799 | 25.9794 | 26.1673 | 26.3735 | 26.7964 | 27.1002 | 27.2653 | 27.4463 | 27.6116 | 27.9097 | 28.2795 | 28.2546 | 28.2546 | 28.2546 | 28.2546 | 28.2546 | 28.2546 | 28.2546 | 28.2546 | 28.2546 | 28.2546 | 28.2546 | 28.2546 | 28.2546 | 28.2546 | 28.2546 | 28.2546 | 40% | 1808.3816 | 20.4621 | 26.5075 | 28.0904 | 27.9963 | 28.0042 | 28.1672 | 28.5962 | 28.8839 | 29.1653 | 29.4942 | 29.7994 | 30.0954 | 30.1297 | 30.4751 | 30.2143 | 30.2143 | 30.2143 | 30.2143 | 30.2143 | 30.2143 | 30.2143 | 30.2143 | 30.2143 | 30.2143 | 30.2143 | 30.2143 | 30.2143 | 30.2143 | 30.2143 | 30.2143
35% | 3551.3408 | 16.0566 | 21.3356 | 22.7736 | 22.7325 | 22.732 | 22.8964 | 23.0768 | 23.4468 | 23.7126 | 23.8572 | 24.0155 | 24.1602 | 24.421 | 24.7446 | 24.7227 | 24.7227 | 24.7227 | 24.7227 | 24.7227 | 24.7227 | 24.7227 | 24.7227 | 24.7227 | 24.7227 | 24.7227 | 24.7227 | 24.7227 | 24.7227 | 24.7227 | 24.7227 | 35% | 2779.1293 | 17.9044 | 23.194 | 24.5791 | 24.4968 | 24.5037 | 24.6463 | 25.0217 | 25.2734 | 25.5196 | 25.8075 | 26.0745 | 26.3335 | 26.3635 | 26.6657 | 26.4375 | 26.4375 | 26.4375 | 26.4375 | 26.4375 | 26.4375 | 26.4375 | 26.4375 | 26.4375 | 26.4375 | 26.4375 | 26.4375 | 26.4375 | 26.4375 | 26.4375 | 26.4375
30% | 3758.953 | 13.7628 | 18.2877 | 19.5202 | 19.485 | 19.4845 | 19.6255 | 19.7801 | 20.0973 | 20.3251 | 20.449 | 20.5847 | 20.7087 | 20.9323 | 21.2097 | 21.1909 | 21.1909 | 21.1909 | 21.1909 | 21.1909 | 21.1909 | 21.1909 | 21.1909 | 21.1909 | 21.1909 | 21.1909 | 21.1909 | 21.1909 | 21.1909 | 21.1909 | 21.1909 | 30% | 3814.165 | 15.3466 | 19.8806 | 21.0678 | 20.9972 | 21.0031 | 21.1254 | 21.4472 | 21.6629 | 21.8739 | 22.1207 | 22.3496 | 22.5716 | 22.5973 | 22.8563 | 22.6607 | 22.6607 | 22.6607 | 22.6607 | 22.6607 | 22.6607 | 22.6607 | 22.6607 | 22.6607 | 22.6607 | 22.6607 | 22.6607 | 22.6607 | 22.6607 | 22.6607 | 22.6607
25% | 3926.4798 | 11.469 | 15.2397 | 16.2669 | 16.2375 | 16.2371 | 16.3546 | 16.4835 | 16.7477 | 16.9376 | 17.0408 | 17.1539 | 17.2573 | 17.4436 | 17.6747 | 17.6591 | 17.6591 | 17.6591 | 17.6591 | 17.6591 | 17.6591 | 17.6591 | 17.6591 | 17.6591 | 17.6591 | 17.6591 | 17.6591 | 17.6591 | 17.6591 | 17.6591 | 17.6591 | 25% | 4166.9923 | 12.7888 | 16.5672 | 17.5565 | 17.4977 | 17.5026 | 17.6045 | 17.8726 | 18.0524 | 18.2283 | 18.4339 | 18.6246 | 18.8096 | 18.8311 | 19.0469 | 18.8839 | 18.8839 | 18.8839 | 18.8839 | 18.8839 | 18.8839 | 18.8839 | 18.8839 | 18.8839 | 18.8839 | 18.8839 | 18.8839 | 18.8839 | 18.8839 | 18.8839 | 18.8839
20% | 4050.5177 | 9.1752 | 12.1918 | 13.0135 | 12.99 | 12.9897 | 13.0837 | 13.1868 | 13.3982 | 13.5501 | 13.6327 | 13.7231 | 13.8058 | 13.9549 | 14.1398 | 14.1273 | 14.1273 | 14.1273 | 14.1273 | 14.1273 | 14.1273 | 14.1273 | 14.1273 | 14.1273 | 14.1273 | 14.1273 | 14.1273 | 14.1273 | 14.1273 | 14.1273 | 14.1273 | 20% | 4282.7105 | 10.2311 | 13.2537 | 14.0452 | 13.9981 | 14.0021 | 14.0836 | 14.2981 | 14.4419 | 14.5826 | 14.7471 | 14.8997 | 15.0477 | 15.0649 | 15.2376 | 15.1071 | 15.1071 | 15.1071 | 15.1071 | 15.1071 | 15.1071 | 15.1071 | 15.1071 | 15.1071 | 15.1071 | 15.1071 | 15.1071 | 15.1071 | 15.1071 | 15.1071 | 15.1071
15% | 4152.622 | 6.8814 | 9.1438 | 9.7601 | 9.7425 | 9.7423 | 9.8128 | 9.8901 | 10.0486 | 10.1626 | 10.2245 | 10.2924 | 10.3544 | 10.4661 | 10.6048 | 10.5955 | 10.5955 | 10.5955 | 10.5955 | 10.5955 | 10.5955 | 10.5955 | 10.5955 | 10.5955 | 10.5955 | 10.5955 | 10.5955 | 10.5955 | 10.5955 | 10.5955 | 10.5955 | 15% | 4364.7722 | 7.6733 | 9.9403 | 10.5339 | 10.4986 | 10.5016 | 10.5627 | 10.7236 | 10.8315 | 10.937 | 11.0603 | 11.1748 | 11.2858 | 11.2986 | 11.4282 | 11.3303 | 11.3303 | 11.3303 | 11.3303 | 11.3303 | 11.3303 | 11.3303 | 11.3303 | 11.3303 | 11.3303 | 11.3303 | 11.3303 | 11.3303 | 11.3303 | 11.3303 | 11.3303
10% | 4248.2976 | 4.5876 | 6.0959 | 6.5067 | 6.495 | 6.4948 | 6.5418 | 6.5934 | 6.6991 | 6.775 | 6.8163 | 6.8616 | 6.9029 | 6.9774 | 7.0699 | 7.0636 | 7.0636 | 7.0636 | 7.0636 | 7.0636 | 7.0636 | 7.0636 | 7.0636 | 7.0636 | 7.0636 | 7.0636 | 7.0636 | 7.0636 | 7.0636 | 7.0636 | 7.0636 | 10% | 4391.6218 | 5.1155 | 6.6269 | 7.0226 | 6.9991 | 7.001 | 7.0418 | 7.1491 | 7.221 | 7.2913 | 7.3736 | 7.4499 | 7.5239 | 7.5324 | 7.6188 | 7.5536 | 7.5536 | 7.5536 | 7.5536 | 7.5536 | 7.5536 | 7.5536 | 7.5536 | 7.5536 | 7.5536 | 7.5536 | 7.5536 | 7.5536 | 7.5536 | 7.5536 | 7.5536
5% | 4361.7469 | 2.2938 | 3.0479 | 3.2534 | 3.2475 | 3.2474 | 3.2709 | 3.2967 | 3.3495 | 3.3875 | 3.4082 | 3.4308 | 3.4515 | 3.4887 | 3.5349 | 3.5318 | 3.5318 | 3.5318 | 3.5318 | 3.5318 | 3.5318 | 3.5318 | 3.5318 | 3.5318 | 3.5318 | 3.5318 | 3.5318 | 3.5318 | 3.5318 | 3.5318 | 3.5318 | 5% | 4391.6218 | 2.5578 | 3.3134 | 3.5113 | 3.4995 | 3.5005 | 3.5209 | 3.5745 | 3.6105 | 3.6457 | 3.6868 | 3.7249 | 3.7619 | 3.7662 | 3.8094 | 3.7768 | 3.7768 | 3.7768 | 3.7768 | 3.7768 | 3.7768 | 3.7768 | 3.7768 | 3.7768 | 3.7768 | 3.7768 | 3.7768 | 3.7768 | 3.7768 | 3.7768 | 3.7768
9.992e-14% | 4391.6218 | 4.5839e-14 | 6.091e-14 | 6.5015e-14 | 6.4898e-14 | 6.4897e-14 | 6.5366e-14 | 6.5881e-14 | 6.6937e-14 | 6.7696e-14 | 6.8109e-14 | 6.8561e-14 | 6.8974e-14 | 6.9719e-14 | 7.0642e-14 | 7.058e-14 | 7.058e-14 | 7.058e-14 | 7.058e-14 | 7.058e-14 | 7.058e-14 | 7.058e-14 | 7.058e-14 | 7.058e-14 | 7.058e-14 | 7.058e-14 | 7.058e-14 | 7.058e-14 | 7.058e-14 | 7.058e-14 | 7.058e-14 | 9.992e-14% | 4391.6218 | 5.1114e-14 | 6.6216e-14 | 7.017e-14 | 6.9935e-14 | 6.9955e-14 | 7.0362e-14 | 7.1433e-14 | 7.2152e-14 | 7.2855e-14 | 7.3677e-14 | 7.4439e-14 | 7.5178e-14 | 7.5264e-14 | 7.6127e-14 | 7.5475e-14 | 7.5475e-14 | 7.5475e-14 | 7.5475e-14 | 7.5475e-14 | 7.5475e-14 | 7.5475e-14 | 7.5475e-14 | 7.5475e-14 | 7.5475e-14 | 7.5475e-14 | 7.5475e-14 | 7.5475e-14 | 7.5475e-14 | 7.5475e-14 | 7.5475e-14
Option 2
Winter Season | [31 empty] | Winter Season
P50 | [31 empty] | P10
% of MD | Winter - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Winter - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 40.358 | 56.0239 | 60.0964 | 41.4573 | 41.9987 | 42.9309 | 45.0518 | 46.4716 | 48.2701 | 49.2036 | 50.0249 | 48.5117 | 50.2851 | 53.0732 | 50.9574 | 50.9574 | 50.9574 | 50.9574 | 50.9574 | 50.9574 | 50.9574 | 50.9574 | 50.9574 | 50.9574 | 50.9574 | 50.9574 | 50.9574 | 50.9574 | 50.9574 | 50.9574 | 100% | 0 | 43.208 | 58.6763 | 62.9078 | 44.2292 | 44.6449 | 45.5569 | 47.711 | 48.8871 | 51.1274 | 57.9376 | 52.3233 | 51.2251 | 52.7075 | 55.9494 | 53.755 | 53.755 | 53.755 | 53.755 | 53.755 | 53.755 | 53.755 | 53.755 | 53.755 | 53.755 | 53.755 | 53.755 | 53.755 | 53.755 | 53.755 | 53.755
99% | 1.486 | 39.9544 | 55.4636 | 59.4955 | 41.0427 | 41.5787 | 42.5016 | 44.6013 | 46.0068 | 47.7874 | 48.7116 | 49.5246 | 48.0265 | 49.7823 | 52.5425 | 50.4479 | 50.4479 | 50.4479 | 50.4479 | 50.4479 | 50.4479 | 50.4479 | 50.4479 | 50.4479 | 50.4479 | 50.4479 | 50.4479 | 50.4479 | 50.4479 | 50.4479 | 50.4479 | 99% | 1.486 | 42.7759 | 58.0895 | 62.2787 | 43.7869 | 44.1985 | 45.1014 | 47.2339 | 48.3982 | 50.6162 | 57.3582 | 51.8001 | 50.7129 | 52.1804 | 55.3899 | 53.2175 | 53.2175 | 53.2175 | 53.2175 | 53.2175 | 53.2175 | 53.2175 | 53.2175 | 53.2175 | 53.2175 | 53.2175 | 53.2175 | 53.2175 | 53.2175 | 53.2175 | 53.2175
98% | 3.2692 | 39.5508 | 54.9034 | 58.8945 | 40.6281 | 41.1587 | 42.0723 | 44.1508 | 45.5421 | 47.3047 | 48.2195 | 49.0244 | 47.5414 | 49.2794 | 52.0118 | 49.9383 | 49.9383 | 49.9383 | 49.9383 | 49.9383 | 49.9383 | 49.9383 | 49.9383 | 49.9383 | 49.9383 | 49.9383 | 49.9383 | 49.9383 | 49.9383 | 49.9383 | 49.9383 | 98% | 3.2692 | 42.3438 | 57.5027 | 61.6497 | 43.3446 | 43.752 | 44.6458 | 46.7568 | 47.9093 | 50.1049 | 56.7788 | 51.2768 | 50.2006 | 51.6534 | 54.8304 | 52.6799 | 52.6799 | 52.6799 | 52.6799 | 52.6799 | 52.6799 | 52.6799 | 52.6799 | 52.6799 | 52.6799 | 52.6799 | 52.6799 | 52.6799 | 52.6799 | 52.6799 | 52.6799
97% | 6.8356 | 39.1473 | 54.3431 | 58.2935 | 40.2136 | 40.7388 | 41.643 | 43.7003 | 45.0774 | 46.822 | 47.7275 | 48.5242 | 47.0563 | 48.7766 | 51.481 | 49.4287 | 49.4287 | 49.4287 | 49.4287 | 49.4287 | 49.4287 | 49.4287 | 49.4287 | 49.4287 | 49.4287 | 49.4287 | 49.4287 | 49.4287 | 49.4287 | 49.4287 | 49.4287 | 97% | 6.8356 | 41.9118 | 56.916 | 61.0206 | 42.9023 | 43.3056 | 44.1902 | 46.2797 | 47.4204 | 49.5936 | 56.1994 | 50.7536 | 49.6884 | 51.1263 | 54.2709 | 52.1424 | 52.1424 | 52.1424 | 52.1424 | 52.1424 | 52.1424 | 52.1424 | 52.1424 | 52.1424 | 52.1424 | 52.1424 | 52.1424 | 52.1424 | 52.1424 | 52.1424 | 52.1424
95% | 17.5347 | 38.3401 | 53.2227 | 57.0916 | 39.3844 | 39.8988 | 40.7844 | 42.7993 | 44.148 | 45.8566 | 46.7434 | 47.5237 | 46.0861 | 47.7709 | 50.4196 | 48.4096 | 48.4096 | 48.4096 | 48.4096 | 48.4096 | 48.4096 | 48.4096 | 48.4096 | 48.4096 | 48.4096 | 48.4096 | 48.4096 | 48.4096 | 48.4096 | 48.4096 | 48.4096 | 95% | 17.5347 | 41.0476 | 55.7425 | 59.7624 | 42.0178 | 42.4127 | 43.2791 | 45.3254 | 46.4427 | 48.5711 | 55.0407 | 49.7071 | 48.6639 | 50.0721 | 53.1519 | 51.0673 | 51.0673 | 51.0673 | 51.0673 | 51.0673 | 51.0673 | 51.0673 | 51.0673 | 51.0673 | 51.0673 | 51.0673 | 51.0673 | 51.0673 | 51.0673 | 51.0673 | 51.0673
90% | 78.7576 | 36.3222 | 50.4215 | 54.0868 | 37.3116 | 37.7988 | 38.6379 | 40.5467 | 41.8244 | 43.4431 | 44.2833 | 45.0224 | 43.6605 | 45.2566 | 47.7659 | 45.8617 | 45.8617 | 45.8617 | 45.8617 | 45.8617 | 45.8617 | 45.8617 | 45.8617 | 45.8617 | 45.8617 | 45.8617 | 45.8617 | 45.8617 | 45.8617 | 45.8617 | 45.8617 | 90% | 78.7576 | 38.8872 | 52.8086 | 56.617 | 39.8063 | 40.1804 | 41.0013 | 42.9399 | 43.9984 | 46.0147 | 52.1438 | 47.091 | 46.1026 | 47.4368 | 50.3545 | 48.3795 | 48.3795 | 48.3795 | 48.3795 | 48.3795 | 48.3795 | 48.3795 | 48.3795 | 48.3795 | 48.3795 | 48.3795 | 48.3795 | 48.3795 | 48.3795 | 48.3795 | 48.3795
85% | 236.8672 | 34.3043 | 47.6203 | 51.082 | 35.2387 | 35.6989 | 36.4913 | 38.2941 | 39.5008 | 41.0296 | 41.8231 | 42.5212 | 41.2349 | 42.7424 | 45.1122 | 43.3138 | 43.3138 | 43.3138 | 43.3138 | 43.3138 | 43.3138 | 43.3138 | 43.3138 | 43.3138 | 43.3138 | 43.3138 | 43.3138 | 43.3138 | 43.3138 | 43.3138 | 43.3138 | 85% | 236.8672 | 36.7268 | 49.8748 | 53.4716 | 37.5948 | 37.9482 | 38.7234 | 40.5543 | 41.554 | 43.4583 | 49.2469 | 44.4748 | 43.5414 | 44.8014 | 47.557 | 45.6918 | 45.6918 | 45.6918 | 45.6918 | 45.6918 | 45.6918 | 45.6918 | 45.6918 | 45.6918 | 45.6918 | 45.6918 | 45.6918 | 45.6918 | 45.6918 | 45.6918 | 45.6918
80% | 497.5104 | 32.2864 | 44.8191 | 48.0771 | 33.1658 | 33.599 | 34.3448 | 36.0415 | 37.1772 | 38.6161 | 39.3629 | 40.0199 | 38.8093 | 40.2281 | 42.4586 | 40.766 | 40.766 | 40.766 | 40.766 | 40.766 | 40.766 | 40.766 | 40.766 | 40.766 | 40.766 | 40.766 | 40.766 | 40.766 | 40.766 | 40.766 | 40.766 | 80% | 497.5104 | 34.5664 | 46.941 | 50.3262 | 35.3834 | 35.7159 | 36.4456 | 38.1688 | 39.1096 | 40.9019 | 46.35 | 41.8586 | 40.9801 | 42.166 | 44.7595 | 43.004 | 43.004 | 43.004 | 43.004 | 43.004 | 43.004 | 43.004 | 43.004 | 43.004 | 43.004 | 43.004 | 43.004 | 43.004 | 43.004 | 43.004 | 43.004
75% | 803.6248 | 30.2685 | 42.0179 | 45.0723 | 31.093 | 31.499 | 32.1982 | 33.7889 | 34.8537 | 36.2026 | 36.9027 | 37.5187 | 36.3837 | 37.7138 | 39.8049 | 38.2181 | 38.2181 | 38.2181 | 38.2181 | 38.2181 | 38.2181 | 38.2181 | 38.2181 | 38.2181 | 38.2181 | 38.2181 | 38.2181 | 38.2181 | 38.2181 | 38.2181 | 38.2181 | 75% | 803.6248 | 32.406 | 44.0072 | 47.1809 | 33.1719 | 33.4837 | 34.1677 | 35.7832 | 36.6653 | 38.3456 | 43.4532 | 39.2425 | 38.4189 | 39.5306 | 41.9621 | 40.3163 | 40.3163 | 40.3163 | 40.3163 | 40.3163 | 40.3163 | 40.3163 | 40.3163 | 40.3163 | 40.3163 | 40.3163 | 40.3163 | 40.3163 | 40.3163 | 40.3163 | 40.3163
70% | 1155.2107 | 28.2506 | 39.2167 | 42.0675 | 29.0201 | 29.3991 | 30.0517 | 31.5363 | 32.5301 | 33.7891 | 34.4425 | 35.0174 | 33.9582 | 35.1996 | 37.1513 | 35.6702 | 35.6702 | 35.6702 | 35.6702 | 35.6702 | 35.6702 | 35.6702 | 35.6702 | 35.6702 | 35.6702 | 35.6702 | 35.6702 | 35.6702 | 35.6702 | 35.6702 | 35.6702 | 70% | 1155.2107 | 30.2456 | 41.0734 | 44.0355 | 30.9604 | 31.2515 | 31.8899 | 33.3977 | 34.2209 | 35.7892 | 40.5563 | 36.6263 | 35.8576 | 36.8953 | 39.1646 | 37.6285 | 37.6285 | 37.6285 | 37.6285 | 37.6285 | 37.6285 | 37.6285 | 37.6285 | 37.6285 | 37.6285 | 37.6285 | 37.6285 | 37.6285 | 37.6285 | 37.6285 | 37.6285
65% | 1553.1596 | 26.2327 | 36.4155 | 39.0627 | 26.9472 | 27.2992 | 27.9051 | 29.2837 | 30.2065 | 31.3755 | 31.9823 | 32.5162 | 31.5326 | 32.6853 | 34.4976 | 33.1223 | 33.1223 | 33.1223 | 33.1223 | 33.1223 | 33.1223 | 33.1223 | 33.1223 | 33.1223 | 33.1223 | 33.1223 | 33.1223 | 33.1223 | 33.1223 | 33.1223 | 33.1223 | 65% | 1553.1596 | 28.0852 | 38.1396 | 40.8901 | 28.749 | 29.0192 | 29.612 | 31.0121 | 31.7766 | 33.2328 | 37.6594 | 34.0101 | 33.2963 | 34.2599 | 36.3671 | 34.9408 | 34.9408 | 34.9408 | 34.9408 | 34.9408 | 34.9408 | 34.9408 | 34.9408 | 34.9408 | 34.9408 | 34.9408 | 34.9408 | 34.9408 | 34.9408 | 34.9408 | 34.9408
60% | 2026.2996 | 24.2148 | 33.6143 | 36.0579 | 24.8744 | 25.1992 | 25.7586 | 27.0311 | 27.8829 | 28.962 | 29.5222 | 30.0149 | 29.107 | 30.1711 | 31.8439 | 30.5745 | 30.5745 | 30.5745 | 30.5745 | 30.5745 | 30.5745 | 30.5745 | 30.5745 | 30.5745 | 30.5745 | 30.5745 | 30.5745 | 30.5745 | 30.5745 | 30.5745 | 30.5745 | 60% | 2026.2996 | 25.9248 | 35.2058 | 37.7447 | 26.5375 | 26.787 | 27.3342 | 28.6266 | 29.3322 | 30.6765 | 34.7625 | 31.394 | 30.7351 | 31.6245 | 33.5696 | 32.253 | 32.253 | 32.253 | 32.253 | 32.253 | 32.253 | 32.253 | 32.253 | 32.253 | 32.253 | 32.253 | 32.253 | 32.253 | 32.253 | 32.253 | 32.253
55% | 2598.4068 | 22.1969 | 30.8131 | 33.053 | 22.8015 | 23.0993 | 23.612 | 24.7785 | 25.5594 | 26.5485 | 27.062 | 27.5137 | 26.6814 | 27.6568 | 29.1903 | 28.0266 | 28.0266 | 28.0266 | 28.0266 | 28.0266 | 28.0266 | 28.0266 | 28.0266 | 28.0266 | 28.0266 | 28.0266 | 28.0266 | 28.0266 | 28.0266 | 28.0266 | 28.0266 | 55% | 2598.4068 | 23.7644 | 32.272 | 34.5993 | 24.3261 | 24.5547 | 25.0563 | 26.241 | 26.8879 | 28.1201 | 31.8657 | 28.7778 | 28.1738 | 28.9891 | 30.7722 | 29.5653 | 29.5653 | 29.5653 | 29.5653 | 29.5653 | 29.5653 | 29.5653 | 29.5653 | 29.5653 | 29.5653 | 29.5653 | 29.5653 | 29.5653 | 29.5653 | 29.5653 | 29.5653
50% | 3233.5201 | 20.179 | 28.0119 | 30.0482 | 20.7286 | 20.9994 | 21.4655 | 22.5259 | 23.2358 | 24.135 | 24.6018 | 25.0124 | 24.2558 | 25.1426 | 26.5366 | 25.4787 | 25.4787 | 25.4787 | 25.4787 | 25.4787 | 25.4787 | 25.4787 | 25.4787 | 25.4787 | 25.4787 | 25.4787 | 25.4787 | 25.4787 | 25.4787 | 25.4787 | 25.4787 | 50% | 3233.5201 | 21.604 | 29.3381 | 31.4539 | 22.1146 | 22.3225 | 22.7785 | 23.8555 | 24.4435 | 25.5637 | 28.9688 | 26.1617 | 25.6126 | 26.3538 | 27.9747 | 26.8775 | 26.8775 | 26.8775 | 26.8775 | 26.8775 | 26.8775 | 26.8775 | 26.8775 | 26.8775 | 26.8775 | 26.8775 | 26.8775 | 26.8775 | 26.8775 | 26.8775 | 26.8775
45% | 3775.313 | 18.1611 | 25.2107 | 27.0434 | 18.6558 | 18.8994 | 19.3189 | 20.2733 | 20.9122 | 21.7215 | 22.1416 | 22.5112 | 21.8302 | 22.6283 | 23.883 | 22.9309 | 22.9309 | 22.9309 | 22.9309 | 22.9309 | 22.9309 | 22.9309 | 22.9309 | 22.9309 | 22.9309 | 22.9309 | 22.9309 | 22.9309 | 22.9309 | 22.9309 | 22.9309 | 45% | 3775.313 | 19.4436 | 26.4043 | 28.3085 | 19.9031 | 20.0902 | 20.5006 | 21.4699 | 21.9992 | 23.0073 | 26.0719 | 23.5455 | 23.0513 | 23.7184 | 25.1772 | 24.1898 | 24.1898 | 24.1898 | 24.1898 | 24.1898 | 24.1898 | 24.1898 | 24.1898 | 24.1898 | 24.1898 | 24.1898 | 24.1898 | 24.1898 | 24.1898 | 24.1898 | 24.1898
40% | 4072.8088 | 16.1432 | 22.4095 | 24.0386 | 16.5829 | 16.7995 | 17.1724 | 18.0207 | 18.5886 | 19.308 | 19.6814 | 20.01 | 19.4047 | 20.1141 | 21.2293 | 20.383 | 20.383 | 20.383 | 20.383 | 20.383 | 20.383 | 20.383 | 20.383 | 20.383 | 20.383 | 20.383 | 20.383 | 20.383 | 20.383 | 20.383 | 20.383 | 40% | 4072.8088 | 17.2832 | 23.4705 | 25.1631 | 17.6917 | 17.858 | 18.2228 | 19.0844 | 19.5548 | 20.451 | 23.175 | 20.9293 | 20.4901 | 21.083 | 22.3798 | 21.502 | 21.502 | 21.502 | 21.502 | 21.502 | 21.502 | 21.502 | 21.502 | 21.502 | 21.502 | 21.502 | 21.502 | 21.502 | 21.502 | 21.502 | 21.502
35% | 4198.821 | 14.1253 | 19.6083 | 21.0337 | 14.5101 | 14.6996 | 15.0258 | 15.7681 | 16.265 | 16.8945 | 17.2213 | 17.5087 | 16.9791 | 17.5998 | 18.5756 | 17.8351 | 17.8351 | 17.8351 | 17.8351 | 17.8351 | 17.8351 | 17.8351 | 17.8351 | 17.8351 | 17.8351 | 17.8351 | 17.8351 | 17.8351 | 17.8351 | 17.8351 | 17.8351 | 35% | 4198.821 | 15.1228 | 20.5367 | 22.0177 | 15.4802 | 15.6257 | 15.9449 | 16.6988 | 17.1105 | 17.8946 | 20.2781 | 18.3132 | 17.9288 | 18.4476 | 19.5823 | 18.8143 | 18.8143 | 18.8143 | 18.8143 | 18.8143 | 18.8143 | 18.8143 | 18.8143 | 18.8143 | 18.8143 | 18.8143 | 18.8143 | 18.8143 | 18.8143 | 18.8143 | 18.8143
30% | 4271.3374 | 12.1074 | 16.8072 | 18.0289 | 12.4372 | 12.5996 | 12.8793 | 13.5156 | 13.9415 | 14.481 | 14.7611 | 15.0075 | 14.5535 | 15.0855 | 15.922 | 15.2872 | 15.2872 | 15.2872 | 15.2872 | 15.2872 | 15.2872 | 15.2872 | 15.2872 | 15.2872 | 15.2872 | 15.2872 | 15.2872 | 15.2872 | 15.2872 | 15.2872 | 15.2872 | 30% | 4271.3374 | 12.9624 | 17.6029 | 18.8723 | 13.2688 | 13.3935 | 13.6671 | 14.3133 | 14.6661 | 15.3382 | 17.3813 | 15.697 | 15.3675 | 15.8123 | 16.7848 | 16.1265 | 16.1265 | 16.1265 | 16.1265 | 16.1265 | 16.1265 | 16.1265 | 16.1265 | 16.1265 | 16.1265 | 16.1265 | 16.1265 | 16.1265 | 16.1265 | 16.1265 | 16.1265
25% | 4321.8611 | 10.0895 | 14.006 | 15.0241 | 10.3643 | 10.4997 | 10.7327 | 11.263 | 11.6179 | 12.0675 | 12.3009 | 12.5062 | 12.1279 | 12.5713 | 13.2683 | 12.7394 | 12.7394 | 12.7394 | 12.7394 | 12.7394 | 12.7394 | 12.7394 | 12.7394 | 12.7394 | 12.7394 | 12.7394 | 12.7394 | 12.7394 | 12.7394 | 12.7394 | 12.7394 | 25% | 4321.8611 | 10.802 | 14.6691 | 15.727 | 11.0573 | 11.1612 | 11.3892 | 11.9277 | 12.2218 | 12.7819 | 14.4844 | 13.0808 | 12.8063 | 13.1769 | 13.9874 | 13.4388 | 13.4388 | 13.4388 | 13.4388 | 13.4388 | 13.4388 | 13.4388 | 13.4388 | 13.4388 | 13.4388 | 13.4388 | 13.4388 | 13.4388 | 13.4388 | 13.4388 | 13.4388
20% | 4353.067 | 8.0716 | 11.2048 | 12.0193 | 8.2915 | 8.3997 | 8.5862 | 9.0104 | 9.2943 | 9.654 | 9.8407 | 10.005 | 9.7023 | 10.057 | 10.6146 | 10.1915 | 10.1915 | 10.1915 | 10.1915 | 10.1915 | 10.1915 | 10.1915 | 10.1915 | 10.1915 | 10.1915 | 10.1915 | 10.1915 | 10.1915 | 10.1915 | 10.1915 | 10.1915 | 20% | 4353.067 | 8.6416 | 11.7353 | 12.5816 | 8.8458 | 8.929 | 9.1114 | 9.5422 | 9.7774 | 10.2255 | 11.5875 | 10.4647 | 10.245 | 10.5415 | 11.1899 | 10.751 | 10.751 | 10.751 | 10.751 | 10.751 | 10.751 | 10.751 | 10.751 | 10.751 | 10.751 | 10.751 | 10.751 | 10.751 | 10.751 | 10.751 | 10.751
15% | 4369.4129 | 6.0537 | 8.4036 | 9.0145 | 6.2186 | 6.2998 | 6.4396 | 6.7578 | 6.9707 | 7.2405 | 7.3805 | 7.5037 | 7.2767 | 7.5428 | 7.961 | 7.6436 | 7.6436 | 7.6436 | 7.6436 | 7.6436 | 7.6436 | 7.6436 | 7.6436 | 7.6436 | 7.6436 | 7.6436 | 7.6436 | 7.6436 | 7.6436 | 7.6436 | 7.6436 | 15% | 4369.4129 | 6.4812 | 8.8014 | 9.4362 | 6.6344 | 6.6967 | 6.8335 | 7.1566 | 7.3331 | 7.6691 | 8.6906 | 7.8485 | 7.6838 | 7.9061 | 8.3924 | 8.0633 | 8.0633 | 8.0633 | 8.0633 | 8.0633 | 8.0633 | 8.0633 | 8.0633 | 8.0633 | 8.0633 | 8.0633 | 8.0633 | 8.0633 | 8.0633 | 8.0633 | 8.0633
10% | 4378.6261 | 4.0358 | 5.6024 | 6.0096 | 4.1457 | 4.1999 | 4.2931 | 4.5052 | 4.6472 | 4.827 | 4.9204 | 5.0025 | 4.8512 | 5.0285 | 5.3073 | 5.0957 | 5.0957 | 5.0957 | 5.0957 | 5.0957 | 5.0957 | 5.0957 | 5.0957 | 5.0957 | 5.0957 | 5.0957 | 5.0957 | 5.0957 | 5.0957 | 5.0957 | 5.0957 | 10% | 4378.6261 | 4.3208 | 5.8676 | 6.2908 | 4.4229 | 4.4645 | 4.5557 | 4.7711 | 4.8887 | 5.1127 | 5.7938 | 5.2323 | 5.1225 | 5.2708 | 5.5949 | 5.3755 | 5.3755 | 5.3755 | 5.3755 | 5.3755 | 5.3755 | 5.3755 | 5.3755 | 5.3755 | 5.3755 | 5.3755 | 5.3755 | 5.3755 | 5.3755 | 5.3755 | 5.3755
5% | 4391.7028 | 2.0179 | 2.8012 | 3.0048 | 2.0729 | 2.0999 | 2.1465 | 2.2526 | 2.3236 | 2.4135 | 2.4602 | 2.5012 | 2.4256 | 2.5143 | 2.6537 | 2.5479 | 2.5479 | 2.5479 | 2.5479 | 2.5479 | 2.5479 | 2.5479 | 2.5479 | 2.5479 | 2.5479 | 2.5479 | 2.5479 | 2.5479 | 2.5479 | 2.5479 | 2.5479 | 5% | 4391.7028 | 2.1604 | 2.9338 | 3.1454 | 2.2115 | 2.2322 | 2.2778 | 2.3855 | 2.4444 | 2.5564 | 2.8969 | 2.6162 | 2.5613 | 2.6354 | 2.7975 | 2.6878 | 2.6878 | 2.6878 | 2.6878 | 2.6878 | 2.6878 | 2.6878 | 2.6878 | 2.6878 | 2.6878 | 2.6878 | 2.6878 | 2.6878 | 2.6878 | 2.6878 | 2.6878
9.992e-14% | 4391.7028 | 4.0326e-14 | 5.5979e-14 | 6.0048e-14 | 4.1424e-14 | 4.1965e-14 | 4.2897e-14 | 4.5016e-14 | 4.6434e-14 | 4.8231e-14 | 4.9164e-14 | 4.9985e-14 | 4.8473e-14 | 5.0245e-14 | 5.3031e-14 | 5.0917e-14 | 5.0917e-14 | 5.0917e-14 | 5.0917e-14 | 5.0917e-14 | 5.0917e-14 | 5.0917e-14 | 5.0917e-14 | 5.0917e-14 | 5.0917e-14 | 5.0917e-14 | 5.0917e-14 | 5.0917e-14 | 5.0917e-14 | 5.0917e-14 | 5.0917e-14 | 9.992e-14% | 4391.7028 | 4.3173e-14 | 5.8629e-14 | 6.2858e-14 | 4.4194e-14 | 4.4609e-14 | 4.5521e-14 | 4.7673e-14 | 4.8848e-14 | 5.1087e-14 | 5.7891e-14 | 5.2281e-14 | 5.1184e-14 | 5.2665e-14 | 5.5905e-14 | 5.3712e-14 | 5.3712e-14 | 5.3712e-14 | 5.3712e-14 | 5.3712e-14 | 5.3712e-14 | 5.3712e-14 | 5.3712e-14 | 5.3712e-14 | 5.3712e-14 | 5.3712e-14 | 5.3712e-14 | 5.3712e-14 | 5.3712e-14 | 5.3712e-14 | 5.3712e-14
Summer Season | [31 empty] | Summer Season
P50 | [31 empty] | P10
% of MD | Summer - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Summer - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 45.8759 | 60.9589 | 65.0674 | 45.6165 | 45.6151 | 46.085 | 46.6005 | 47.6576 | 48.4171 | 48.83 | 49.2823 | 49.6957 | 50.441 | 51.3655 | 51.303 | 51.303 | 51.303 | 51.303 | 51.303 | 51.303 | 51.303 | 51.303 | 51.303 | 51.303 | 51.303 | 51.303 | 51.303 | 51.303 | 51.303 | 51.303 | 100% | 0 | 51.1554 | 66.2686 | 70.2261 | 50.6574 | 50.6772 | 51.0846 | 52.1572 | 52.8764 | 53.5798 | 54.4023 | 55.1652 | 55.9052 | 55.991 | 56.8545 | 56.2023 | 56.2023 | 56.2023 | 56.2023 | 56.2023 | 56.2023 | 56.2023 | 56.2023 | 56.2023 | 56.2023 | 56.2023 | 56.2023 | 56.2023 | 56.2023 | 56.2023 | 56.2023
99% | 0 | 45.4171 | 60.3493 | 64.4168 | 45.1604 | 45.159 | 45.6242 | 46.1345 | 47.181 | 47.9329 | 48.3417 | 48.7895 | 49.1987 | 49.9366 | 50.8519 | 50.79 | 50.79 | 50.79 | 50.79 | 50.79 | 50.79 | 50.79 | 50.79 | 50.79 | 50.79 | 50.79 | 50.79 | 50.79 | 50.79 | 50.79 | 50.79 | 99% | 1.5127 | 50.6438 | 65.6059 | 69.5238 | 50.1508 | 50.1704 | 50.5737 | 51.6356 | 52.3476 | 53.044 | 53.8583 | 54.6135 | 55.3462 | 55.431 | 56.2859 | 55.6403 | 55.6403 | 55.6403 | 55.6403 | 55.6403 | 55.6403 | 55.6403 | 55.6403 | 55.6403 | 55.6403 | 55.6403 | 55.6403 | 55.6403 | 55.6403 | 55.6403 | 55.6403
98% | 0 | 44.9584 | 59.7397 | 63.7661 | 44.7042 | 44.7028 | 45.1633 | 45.6685 | 46.7045 | 47.4488 | 47.8534 | 48.2967 | 48.7018 | 49.4322 | 50.3382 | 50.277 | 50.277 | 50.277 | 50.277 | 50.277 | 50.277 | 50.277 | 50.277 | 50.277 | 50.277 | 50.277 | 50.277 | 50.277 | 50.277 | 50.277 | 50.277 | 98% | 2.269 | 50.1322 | 64.9433 | 68.8216 | 49.6442 | 49.6636 | 50.0629 | 51.1141 | 51.8189 | 52.5082 | 53.3142 | 54.0619 | 54.7871 | 54.8711 | 55.7174 | 55.0783 | 55.0783 | 55.0783 | 55.0783 | 55.0783 | 55.0783 | 55.0783 | 55.0783 | 55.0783 | 55.0783 | 55.0783 | 55.0783 | 55.0783 | 55.0783 | 55.0783 | 55.0783
97% | 0.37816 | 44.4996 | 59.1301 | 63.1154 | 44.248 | 44.2467 | 44.7025 | 45.2025 | 46.2279 | 46.9646 | 47.3651 | 47.8039 | 48.2048 | 48.9277 | 49.8246 | 49.764 | 49.764 | 49.764 | 49.764 | 49.764 | 49.764 | 49.764 | 49.764 | 49.764 | 49.764 | 49.764 | 49.764 | 49.764 | 49.764 | 49.764 | 49.764 | 97% | 3.7816 | 49.6207 | 64.2806 | 68.1193 | 49.1377 | 49.1568 | 49.552 | 50.5925 | 51.2901 | 51.9724 | 52.7702 | 53.5102 | 54.2281 | 54.3112 | 55.1488 | 54.5163 | 54.5163 | 54.5163 | 54.5163 | 54.5163 | 54.5163 | 54.5163 | 54.5163 | 54.5163 | 54.5163 | 54.5163 | 54.5163 | 54.5163 | 54.5163 | 54.5163 | 54.5163
95% | 2.269 | 43.5821 | 57.911 | 61.8141 | 43.3357 | 43.3344 | 43.7808 | 44.2705 | 45.2747 | 45.9962 | 46.3885 | 46.8182 | 47.2109 | 47.9189 | 48.7973 | 48.7379 | 48.7379 | 48.7379 | 48.7379 | 48.7379 | 48.7379 | 48.7379 | 48.7379 | 48.7379 | 48.7379 | 48.7379 | 48.7379 | 48.7379 | 48.7379 | 48.7379 | 48.7379 | 95% | 6.0506 | 48.5976 | 62.9552 | 66.7148 | 48.1245 | 48.1433 | 48.5304 | 49.5493 | 50.2326 | 50.9008 | 51.6822 | 52.4069 | 53.11 | 53.1914 | 54.0117 | 53.3922 | 53.3922 | 53.3922 | 53.3922 | 53.3922 | 53.3922 | 53.3922 | 53.3922 | 53.3922 | 53.3922 | 53.3922 | 53.3922 | 53.3922 | 53.3922 | 53.3922 | 53.3922
90% | 5.6725 | 41.2883 | 54.863 | 58.5607 | 41.0549 | 41.0536 | 41.4765 | 41.9404 | 42.8918 | 43.5754 | 43.947 | 44.3541 | 44.7261 | 45.3969 | 46.229 | 46.1727 | 46.1727 | 46.1727 | 46.1727 | 46.1727 | 46.1727 | 46.1727 | 46.1727 | 46.1727 | 46.1727 | 46.1727 | 46.1727 | 46.1727 | 46.1727 | 46.1727 | 46.1727 | 90% | 16.2611 | 46.0398 | 59.6418 | 63.2035 | 45.5917 | 45.6094 | 45.9761 | 46.9415 | 47.5887 | 48.2218 | 48.9621 | 49.6487 | 50.3147 | 50.3919 | 51.169 | 50.5821 | 50.5821 | 50.5821 | 50.5821 | 50.5821 | 50.5821 | 50.5821 | 50.5821 | 50.5821 | 50.5821 | 50.5821 | 50.5821 | 50.5821 | 50.5821 | 50.5821 | 50.5821
85% | 15.8829 | 38.9945 | 51.8151 | 55.3073 | 38.774 | 38.7729 | 39.1723 | 39.6104 | 40.509 | 41.1545 | 41.5055 | 41.89 | 42.2413 | 42.8748 | 43.6607 | 43.6076 | 43.6076 | 43.6076 | 43.6076 | 43.6076 | 43.6076 | 43.6076 | 43.6076 | 43.6076 | 43.6076 | 43.6076 | 43.6076 | 43.6076 | 43.6076 | 43.6076 | 43.6076 | 85% | 26.4715 | 43.482 | 56.3283 | 59.6922 | 43.0588 | 43.0756 | 43.4219 | 44.3336 | 44.9449 | 45.5429 | 46.2419 | 46.8904 | 47.5194 | 47.5923 | 48.3263 | 47.772 | 47.772 | 47.772 | 47.772 | 47.772 | 47.772 | 47.772 | 47.772 | 47.772 | 47.772 | 47.772 | 47.772 | 47.772 | 47.772 | 47.772 | 47.772
80% | 31.0095 | 36.7007 | 48.7671 | 52.0539 | 36.4932 | 36.4921 | 36.868 | 37.2804 | 38.1261 | 38.7337 | 39.064 | 39.4259 | 39.7565 | 40.3528 | 41.0924 | 41.0424 | 41.0424 | 41.0424 | 41.0424 | 41.0424 | 41.0424 | 41.0424 | 41.0424 | 41.0424 | 41.0424 | 41.0424 | 41.0424 | 41.0424 | 41.0424 | 41.0424 | 41.0424 | 80% | 34.0348 | 40.9243 | 53.0149 | 56.1809 | 40.5259 | 40.5417 | 40.8677 | 41.7258 | 42.3011 | 42.8639 | 43.5218 | 44.1321 | 44.7242 | 44.7928 | 45.4836 | 44.9619 | 44.9619 | 44.9619 | 44.9619 | 44.9619 | 44.9619 | 44.9619 | 44.9619 | 44.9619 | 44.9619 | 44.9619 | 44.9619 | 44.9619 | 44.9619 | 44.9619 | 44.9619
75% | 72.9857 | 34.4069 | 45.7192 | 48.8006 | 34.2124 | 34.2113 | 34.5638 | 34.9504 | 35.7432 | 36.3128 | 36.6225 | 36.9618 | 37.2718 | 37.8307 | 38.5241 | 38.4773 | 38.4773 | 38.4773 | 38.4773 | 38.4773 | 38.4773 | 38.4773 | 38.4773 | 38.4773 | 38.4773 | 38.4773 | 38.4773 | 38.4773 | 38.4773 | 38.4773 | 38.4773 | 75% | 48.405 | 38.3665 | 49.7015 | 52.6696 | 37.993 | 38.0079 | 38.3134 | 39.1179 | 39.6573 | 40.1849 | 40.8017 | 41.3739 | 41.9289 | 41.9932 | 42.6408 | 42.1517 | 42.1517 | 42.1517 | 42.1517 | 42.1517 | 42.1517 | 42.1517 | 42.1517 | 42.1517 | 42.1517 | 42.1517 | 42.1517 | 42.1517 | 42.1517 | 42.1517 | 42.1517
70% | 150.5094 | 32.1131 | 42.6712 | 45.5472 | 31.9316 | 31.9306 | 32.2595 | 32.6203 | 33.3603 | 33.892 | 34.181 | 34.4976 | 34.787 | 35.3087 | 35.9559 | 35.9121 | 35.9121 | 35.9121 | 35.9121 | 35.9121 | 35.9121 | 35.9121 | 35.9121 | 35.9121 | 35.9121 | 35.9121 | 35.9121 | 35.9121 | 35.9121 | 35.9121 | 35.9121 | 70% | 76.3892 | 35.8087 | 46.388 | 49.1583 | 35.4602 | 35.474 | 35.7592 | 36.51 | 37.0135 | 37.5059 | 38.0816 | 38.6156 | 39.1337 | 39.1937 | 39.7981 | 39.3416 | 39.3416 | 39.3416 | 39.3416 | 39.3416 | 39.3416 | 39.3416 | 39.3416 | 39.3416 | 39.3416 | 39.3416 | 39.3416 | 39.3416 | 39.3416 | 39.3416 | 39.3416
65% | 359.6342 | 29.8193 | 39.6233 | 42.2938 | 29.6507 | 29.6498 | 29.9553 | 30.2903 | 30.9774 | 31.4711 | 31.7395 | 32.0335 | 32.3022 | 32.7866 | 33.3876 | 33.347 | 33.347 | 33.347 | 33.347 | 33.347 | 33.347 | 33.347 | 33.347 | 33.347 | 33.347 | 33.347 | 33.347 | 33.347 | 33.347 | 33.347 | 33.347 | 65% | 114.2056 | 33.251 | 43.0746 | 45.647 | 32.9273 | 32.9401 | 33.205 | 33.9022 | 34.3696 | 34.8269 | 35.3615 | 35.8574 | 36.3384 | 36.3941 | 36.9554 | 36.5315 | 36.5315 | 36.5315 | 36.5315 | 36.5315 | 36.5315 | 36.5315 | 36.5315 | 36.5315 | 36.5315 | 36.5315 | 36.5315 | 36.5315 | 36.5315 | 36.5315 | 36.5315
60% | 689.7717 | 27.5255 | 36.5753 | 39.0405 | 27.3699 | 27.3691 | 27.651 | 27.9603 | 28.5946 | 29.0503 | 29.298 | 29.5694 | 29.8174 | 30.2646 | 30.8193 | 30.7818 | 30.7818 | 30.7818 | 30.7818 | 30.7818 | 30.7818 | 30.7818 | 30.7818 | 30.7818 | 30.7818 | 30.7818 | 30.7818 | 30.7818 | 30.7818 | 30.7818 | 30.7818 | 60% | 178.1154 | 30.6932 | 39.7612 | 42.1357 | 30.3944 | 30.4063 | 30.6508 | 31.2943 | 31.7258 | 32.1479 | 32.6414 | 33.0991 | 33.5431 | 33.5946 | 34.1127 | 33.7214 | 33.7214 | 33.7214 | 33.7214 | 33.7214 | 33.7214 | 33.7214 | 33.7214 | 33.7214 | 33.7214 | 33.7214 | 33.7214 | 33.7214 | 33.7214 | 33.7214 | 33.7214
55% | 1095.5419 | 25.2317 | 33.5274 | 35.7871 | 25.0891 | 25.0883 | 25.3468 | 25.6303 | 26.2117 | 26.6294 | 26.8565 | 27.1053 | 27.3326 | 27.7425 | 28.251 | 28.2167 | 28.2167 | 28.2167 | 28.2167 | 28.2167 | 28.2167 | 28.2167 | 28.2167 | 28.2167 | 28.2167 | 28.2167 | 28.2167 | 28.2167 | 28.2167 | 28.2167 | 28.2167 | 55% | 311.6074 | 28.1354 | 36.4477 | 38.6243 | 27.8616 | 27.8724 | 28.0965 | 28.6865 | 29.082 | 29.4689 | 29.9213 | 30.3408 | 30.7479 | 30.795 | 31.27 | 30.9113 | 30.9113 | 30.9113 | 30.9113 | 30.9113 | 30.9113 | 30.9113 | 30.9113 | 30.9113 | 30.9113 | 30.9113 | 30.9113 | 30.9113 | 30.9113 | 30.9113 | 30.9113
50% | 1666.1918 | 22.9379 | 30.4794 | 32.5337 | 22.8083 | 22.8076 | 23.0425 | 23.3002 | 23.8288 | 24.2085 | 24.415 | 24.6412 | 24.8478 | 25.2205 | 25.6828 | 25.6515 | 25.6515 | 25.6515 | 25.6515 | 25.6515 | 25.6515 | 25.6515 | 25.6515 | 25.6515 | 25.6515 | 25.6515 | 25.6515 | 25.6515 | 25.6515 | 25.6515 | 25.6515 | 50% | 636.0723 | 25.5777 | 33.1343 | 35.113 | 25.3287 | 25.3386 | 25.5423 | 26.0786 | 26.4382 | 26.7899 | 27.2011 | 27.5826 | 27.9526 | 27.9955 | 28.4272 | 28.1012 | 28.1012 | 28.1012 | 28.1012 | 28.1012 | 28.1012 | 28.1012 | 28.1012 | 28.1012 | 28.1012 | 28.1012 | 28.1012 | 28.1012 | 28.1012 | 28.1012 | 28.1012
45% | 2506.0947 | 20.6442 | 27.4315 | 29.2803 | 20.5274 | 20.5268 | 20.7383 | 20.9702 | 21.4459 | 21.7877 | 21.9735 | 22.1771 | 22.3631 | 22.6984 | 23.1145 | 23.0864 | 23.0864 | 23.0864 | 23.0864 | 23.0864 | 23.0864 | 23.0864 | 23.0864 | 23.0864 | 23.0864 | 23.0864 | 23.0864 | 23.0864 | 23.0864 | 23.0864 | 23.0864 | 45% | 1179.4944 | 23.0199 | 29.8209 | 31.6017 | 22.7958 | 22.8047 | 22.9881 | 23.4707 | 23.7944 | 24.1109 | 24.481 | 24.8243 | 25.1573 | 25.1959 | 25.5845 | 25.291 | 25.291 | 25.291 | 25.291 | 25.291 | 25.291 | 25.291 | 25.291 | 25.291 | 25.291 | 25.291 | 25.291 | 25.291 | 25.291 | 25.291 | 25.291
40% | 3164.4787 | 18.3504 | 24.3836 | 26.027 | 18.2466 | 18.246 | 18.434 | 18.6402 | 19.063 | 19.3668 | 19.532 | 19.7129 | 19.8783 | 20.1764 | 20.5462 | 20.5212 | 20.5212 | 20.5212 | 20.5212 | 20.5212 | 20.5212 | 20.5212 | 20.5212 | 20.5212 | 20.5212 | 20.5212 | 20.5212 | 20.5212 | 20.5212 | 20.5212 | 20.5212 | 40% | 1808.3816 | 20.4621 | 26.5075 | 28.0904 | 20.263 | 20.2709 | 20.4338 | 20.8629 | 21.1506 | 21.4319 | 21.7609 | 22.0661 | 22.3621 | 22.3964 | 22.7418 | 22.4809 | 22.4809 | 22.4809 | 22.4809 | 22.4809 | 22.4809 | 22.4809 | 22.4809 | 22.4809 | 22.4809 | 22.4809 | 22.4809 | 22.4809 | 22.4809 | 22.4809 | 22.4809
35% | 3551.3408 | 16.0566 | 21.3356 | 22.7736 | 15.9658 | 15.9653 | 16.1298 | 16.3102 | 16.6802 | 16.946 | 17.0905 | 17.2488 | 17.3935 | 17.6543 | 17.9779 | 17.9561 | 17.9561 | 17.9561 | 17.9561 | 17.9561 | 17.9561 | 17.9561 | 17.9561 | 17.9561 | 17.9561 | 17.9561 | 17.9561 | 17.9561 | 17.9561 | 17.9561 | 17.9561 | 35% | 2779.1293 | 17.9044 | 23.194 | 24.5791 | 17.7301 | 17.737 | 17.8796 | 18.255 | 18.5067 | 18.7529 | 19.0408 | 19.3078 | 19.5668 | 19.5968 | 19.8991 | 19.6708 | 19.6708 | 19.6708 | 19.6708 | 19.6708 | 19.6708 | 19.6708 | 19.6708 | 19.6708 | 19.6708 | 19.6708 | 19.6708 | 19.6708 | 19.6708 | 19.6708 | 19.6708
30% | 3758.953 | 13.7628 | 18.2877 | 19.5202 | 13.685 | 13.6845 | 13.8255 | 13.9801 | 14.2973 | 14.5251 | 14.649 | 14.7847 | 14.9087 | 15.1323 | 15.4097 | 15.3909 | 15.3909 | 15.3909 | 15.3909 | 15.3909 | 15.3909 | 15.3909 | 15.3909 | 15.3909 | 15.3909 | 15.3909 | 15.3909 | 15.3909 | 15.3909 | 15.3909 | 15.3909 | 30% | 3814.165 | 15.3466 | 19.8806 | 21.0678 | 15.1972 | 15.2031 | 15.3254 | 15.6472 | 15.8629 | 16.0739 | 16.3207 | 16.5496 | 16.7716 | 16.7973 | 17.0563 | 16.8607 | 16.8607 | 16.8607 | 16.8607 | 16.8607 | 16.8607 | 16.8607 | 16.8607 | 16.8607 | 16.8607 | 16.8607 | 16.8607 | 16.8607 | 16.8607 | 16.8607 | 16.8607
25% | 3926.4798 | 11.469 | 15.2397 | 16.2669 | 11.4041 | 11.4038 | 11.5213 | 11.6501 | 11.9144 | 12.1043 | 12.2075 | 12.3206 | 12.4239 | 12.6102 | 12.8414 | 12.8258 | 12.8258 | 12.8258 | 12.8258 | 12.8258 | 12.8258 | 12.8258 | 12.8258 | 12.8258 | 12.8258 | 12.8258 | 12.8258 | 12.8258 | 12.8258 | 12.8258 | 12.8258 | 25% | 4166.9923 | 12.7888 | 16.5672 | 17.5565 | 12.6643 | 12.6693 | 12.7711 | 13.0393 | 13.2191 | 13.395 | 13.6006 | 13.7913 | 13.9763 | 13.9977 | 14.2136 | 14.0506 | 14.0506 | 14.0506 | 14.0506 | 14.0506 | 14.0506 | 14.0506 | 14.0506 | 14.0506 | 14.0506 | 14.0506 | 14.0506 | 14.0506 | 14.0506 | 14.0506 | 14.0506
20% | 4050.5177 | 9.1752 | 12.1918 | 13.0135 | 9.1233 | 9.123 | 9.217 | 9.3201 | 9.5315 | 9.6834 | 9.766 | 9.8565 | 9.9391 | 10.0882 | 10.2731 | 10.2606 | 10.2606 | 10.2606 | 10.2606 | 10.2606 | 10.2606 | 10.2606 | 10.2606 | 10.2606 | 10.2606 | 10.2606 | 10.2606 | 10.2606 | 10.2606 | 10.2606 | 10.2606 | 20% | 4282.7105 | 10.2311 | 13.2537 | 14.0452 | 10.1315 | 10.1354 | 10.2169 | 10.4314 | 10.5753 | 10.716 | 10.8805 | 11.033 | 11.181 | 11.1982 | 11.3709 | 11.2405 | 11.2405 | 11.2405 | 11.2405 | 11.2405 | 11.2405 | 11.2405 | 11.2405 | 11.2405 | 11.2405 | 11.2405 | 11.2405 | 11.2405 | 11.2405 | 11.2405 | 11.2405
15% | 4152.622 | 6.8814 | 9.1438 | 9.7601 | 6.8425 | 6.8423 | 6.9128 | 6.9901 | 7.1486 | 7.2626 | 7.3245 | 7.3924 | 7.4544 | 7.5661 | 7.7048 | 7.6955 | 7.6955 | 7.6955 | 7.6955 | 7.6955 | 7.6955 | 7.6955 | 7.6955 | 7.6955 | 7.6955 | 7.6955 | 7.6955 | 7.6955 | 7.6955 | 7.6955 | 7.6955 | 15% | 4364.7722 | 7.6733 | 9.9403 | 10.5339 | 7.5986 | 7.6016 | 7.6627 | 7.8236 | 7.9315 | 8.037 | 8.1603 | 8.2748 | 8.3858 | 8.3986 | 8.5282 | 8.4303 | 8.4303 | 8.4303 | 8.4303 | 8.4303 | 8.4303 | 8.4303 | 8.4303 | 8.4303 | 8.4303 | 8.4303 | 8.4303 | 8.4303 | 8.4303 | 8.4303 | 8.4303
10% | 4248.2976 | 4.5876 | 6.0959 | 6.5067 | 4.5617 | 4.5615 | 4.6085 | 4.66 | 4.7658 | 4.8417 | 4.883 | 4.9282 | 4.9696 | 5.0441 | 5.1366 | 5.1303 | 5.1303 | 5.1303 | 5.1303 | 5.1303 | 5.1303 | 5.1303 | 5.1303 | 5.1303 | 5.1303 | 5.1303 | 5.1303 | 5.1303 | 5.1303 | 5.1303 | 5.1303 | 10% | 4391.6218 | 5.1155 | 6.6269 | 7.0226 | 5.0657 | 5.0677 | 5.1085 | 5.2157 | 5.2876 | 5.358 | 5.4402 | 5.5165 | 5.5905 | 5.5991 | 5.6854 | 5.6202 | 5.6202 | 5.6202 | 5.6202 | 5.6202 | 5.6202 | 5.6202 | 5.6202 | 5.6202 | 5.6202 | 5.6202 | 5.6202 | 5.6202 | 5.6202 | 5.6202 | 5.6202
5% | 4361.7469 | 2.2938 | 3.0479 | 3.2534 | 2.2808 | 2.2808 | 2.3043 | 2.33 | 2.3829 | 2.4209 | 2.4415 | 2.4641 | 2.4848 | 2.522 | 2.5683 | 2.5652 | 2.5652 | 2.5652 | 2.5652 | 2.5652 | 2.5652 | 2.5652 | 2.5652 | 2.5652 | 2.5652 | 2.5652 | 2.5652 | 2.5652 | 2.5652 | 2.5652 | 2.5652 | 5% | 4391.6218 | 2.5578 | 3.3134 | 3.5113 | 2.5329 | 2.5339 | 2.5542 | 2.6079 | 2.6438 | 2.679 | 2.7201 | 2.7583 | 2.7953 | 2.7995 | 2.8427 | 2.8101 | 2.8101 | 2.8101 | 2.8101 | 2.8101 | 2.8101 | 2.8101 | 2.8101 | 2.8101 | 2.8101 | 2.8101 | 2.8101 | 2.8101 | 2.8101 | 2.8101 | 2.8101
9.992e-14% | 4391.6218 | 4.5839e-14 | 6.091e-14 | 6.5015e-14 | 4.558e-14 | 4.5579e-14 | 4.6048e-14 | 4.6563e-14 | 4.762e-14 | 4.8378e-14 | 4.8791e-14 | 4.9243e-14 | 4.9656e-14 | 5.0401e-14 | 5.1324e-14 | 5.1262e-14 | 5.1262e-14 | 5.1262e-14 | 5.1262e-14 | 5.1262e-14 | 5.1262e-14 | 5.1262e-14 | 5.1262e-14 | 5.1262e-14 | 5.1262e-14 | 5.1262e-14 | 5.1262e-14 | 5.1262e-14 | 5.1262e-14 | 5.1262e-14 | 5.1262e-14 | 9.992e-14% | 4391.6218 | 5.1114e-14 | 6.6216e-14 | 7.017e-14 | 5.0617e-14 | 5.0637e-14 | 5.1044e-14 | 5.2116e-14 | 5.2834e-14 | 5.3537e-14 | 5.4359e-14 | 5.5121e-14 | 5.5861e-14 | 5.5946e-14 | 5.6809e-14 | 5.6157e-14 | 5.6157e-14 | 5.6157e-14 | 5.6157e-14 | 5.6157e-14 | 5.6157e-14 | 5.6157e-14 | 5.6157e-14 | 5.6157e-14 | 5.6157e-14 | 5.6157e-14 | 5.6157e-14 | 5.6157e-14 | 5.6157e-14 | 5.6157e-14 | 5.6157e-14
Option 3
Winter Season | [31 empty] | Winter Season
P50 | [31 empty] | P10
% of MD | Winter - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Winter - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 40.358 | 56.0239 | 60.0964 | 60.7906 | 61.3321 | 62.2643 | 64.3852 | 65.8049 | 67.6034 | 68.5369 | 69.3582 | 67.845 | 69.6185 | 72.4066 | 70.2908 | 70.2908 | 70.2908 | 70.2908 | 70.2908 | 70.2908 | 70.2908 | 70.2908 | 70.2908 | 70.2908 | 70.2908 | 70.2908 | 70.2908 | 70.2908 | 70.2908 | 70.2908 | 100% | 0 | 43.208 | 58.6763 | 62.9078 | 63.5625 | 63.9783 | 64.8903 | 67.0443 | 68.2204 | 70.4608 | 77.2709 | 71.6566 | 70.5585 | 72.0408 | 75.2827 | 73.0883 | 73.0883 | 73.0883 | 73.0883 | 73.0883 | 73.0883 | 73.0883 | 73.0883 | 73.0883 | 73.0883 | 73.0883 | 73.0883 | 73.0883 | 73.0883 | 73.0883 | 73.0883
99% | 1.486 | 39.9544 | 55.4636 | 59.4955 | 60.1827 | 60.7187 | 61.6416 | 63.7413 | 65.1468 | 66.9274 | 67.8516 | 68.6646 | 67.1665 | 68.9223 | 71.6825 | 69.5879 | 69.5879 | 69.5879 | 69.5879 | 69.5879 | 69.5879 | 69.5879 | 69.5879 | 69.5879 | 69.5879 | 69.5879 | 69.5879 | 69.5879 | 69.5879 | 69.5879 | 69.5879 | 99% | 1.486 | 42.7759 | 58.0895 | 62.2787 | 62.9269 | 63.3385 | 64.2414 | 66.3739 | 67.5382 | 69.7562 | 76.4982 | 70.9401 | 69.8529 | 71.3204 | 74.5299 | 72.3575 | 72.3575 | 72.3575 | 72.3575 | 72.3575 | 72.3575 | 72.3575 | 72.3575 | 72.3575 | 72.3575 | 72.3575 | 72.3575 | 72.3575 | 72.3575 | 72.3575 | 72.3575
98% | 3.2692 | 39.5508 | 54.9034 | 58.8945 | 59.5748 | 60.1054 | 61.019 | 63.0975 | 64.4888 | 66.2513 | 67.1662 | 67.9711 | 66.4881 | 68.2261 | 70.9584 | 68.885 | 68.885 | 68.885 | 68.885 | 68.885 | 68.885 | 68.885 | 68.885 | 68.885 | 68.885 | 68.885 | 68.885 | 68.885 | 68.885 | 68.885 | 68.885 | 98% | 3.2692 | 42.3438 | 57.5027 | 61.6497 | 62.2913 | 62.6987 | 63.5925 | 65.7034 | 66.856 | 69.0516 | 75.7255 | 70.2235 | 69.1473 | 70.6 | 73.7771 | 71.6266 | 71.6266 | 71.6266 | 71.6266 | 71.6266 | 71.6266 | 71.6266 | 71.6266 | 71.6266 | 71.6266 | 71.6266 | 71.6266 | 71.6266 | 71.6266 | 71.6266 | 71.6266
97% | 6.8356 | 39.1473 | 54.3431 | 58.2935 | 58.9669 | 59.4921 | 60.3964 | 62.4536 | 63.8307 | 65.5753 | 66.4808 | 67.2775 | 65.8096 | 67.5299 | 70.2344 | 68.1821 | 68.1821 | 68.1821 | 68.1821 | 68.1821 | 68.1821 | 68.1821 | 68.1821 | 68.1821 | 68.1821 | 68.1821 | 68.1821 | 68.1821 | 68.1821 | 68.1821 | 68.1821 | 97% | 6.8356 | 41.9118 | 56.916 | 61.0206 | 61.6557 | 62.0589 | 62.9436 | 65.033 | 66.1738 | 68.3469 | 74.9528 | 69.5069 | 68.4417 | 69.8796 | 73.0243 | 70.8957 | 70.8957 | 70.8957 | 70.8957 | 70.8957 | 70.8957 | 70.8957 | 70.8957 | 70.8957 | 70.8957 | 70.8957 | 70.8957 | 70.8957 | 70.8957 | 70.8957 | 70.8957
95% | 17.5347 | 38.3401 | 53.2227 | 57.0916 | 57.7511 | 58.2655 | 59.1511 | 61.1659 | 62.5146 | 64.2232 | 65.1101 | 65.8903 | 64.4527 | 66.1375 | 68.7862 | 66.7762 | 66.7762 | 66.7762 | 66.7762 | 66.7762 | 66.7762 | 66.7762 | 66.7762 | 66.7762 | 66.7762 | 66.7762 | 66.7762 | 66.7762 | 66.7762 | 66.7762 | 66.7762 | 95% | 17.5347 | 41.0476 | 55.7425 | 59.7624 | 60.3844 | 60.7794 | 61.6458 | 63.6921 | 64.8094 | 66.9377 | 73.4073 | 68.0738 | 67.0306 | 68.4388 | 71.5186 | 69.4339 | 69.4339 | 69.4339 | 69.4339 | 69.4339 | 69.4339 | 69.4339 | 69.4339 | 69.4339 | 69.4339 | 69.4339 | 69.4339 | 69.4339 | 69.4339 | 69.4339 | 69.4339
90% | 78.7576 | 36.3222 | 50.4215 | 54.0868 | 54.7116 | 55.1988 | 56.0379 | 57.9467 | 59.2244 | 60.8431 | 61.6833 | 62.4224 | 61.0605 | 62.6566 | 65.1659 | 63.2617 | 63.2617 | 63.2617 | 63.2617 | 63.2617 | 63.2617 | 63.2617 | 63.2617 | 63.2617 | 63.2617 | 63.2617 | 63.2617 | 63.2617 | 63.2617 | 63.2617 | 63.2617 | 90% | 78.7576 | 38.8872 | 52.8086 | 56.617 | 57.2063 | 57.5804 | 58.4013 | 60.3399 | 61.3984 | 63.4147 | 69.5438 | 64.491 | 63.5026 | 64.8368 | 67.7545 | 65.7795 | 65.7795 | 65.7795 | 65.7795 | 65.7795 | 65.7795 | 65.7795 | 65.7795 | 65.7795 | 65.7795 | 65.7795 | 65.7795 | 65.7795 | 65.7795 | 65.7795 | 65.7795
85% | 236.8672 | 34.3043 | 47.6203 | 51.082 | 51.672 | 52.1322 | 52.9246 | 54.7274 | 55.9342 | 57.4629 | 58.2564 | 58.9545 | 57.6682 | 59.1757 | 61.5456 | 59.7472 | 59.7472 | 59.7472 | 59.7472 | 59.7472 | 59.7472 | 59.7472 | 59.7472 | 59.7472 | 59.7472 | 59.7472 | 59.7472 | 59.7472 | 59.7472 | 59.7472 | 59.7472 | 85% | 236.8672 | 36.7268 | 49.8748 | 53.4716 | 54.0282 | 54.3815 | 55.1567 | 56.9877 | 57.9873 | 59.8917 | 65.6803 | 60.9081 | 59.9747 | 61.2347 | 63.9903 | 62.1251 | 62.1251 | 62.1251 | 62.1251 | 62.1251 | 62.1251 | 62.1251 | 62.1251 | 62.1251 | 62.1251 | 62.1251 | 62.1251 | 62.1251 | 62.1251 | 62.1251 | 62.1251
80% | 497.5104 | 32.2864 | 44.8191 | 48.0771 | 48.6325 | 49.0656 | 49.8114 | 51.5081 | 52.6439 | 54.0827 | 54.8296 | 55.4866 | 54.276 | 55.6948 | 57.9252 | 56.2326 | 56.2326 | 56.2326 | 56.2326 | 56.2326 | 56.2326 | 56.2326 | 56.2326 | 56.2326 | 56.2326 | 56.2326 | 56.2326 | 56.2326 | 56.2326 | 56.2326 | 56.2326 | 80% | 497.5104 | 34.5664 | 46.941 | 50.3262 | 50.85 | 51.1826 | 51.9122 | 53.6355 | 54.5763 | 56.3686 | 61.8167 | 57.3253 | 56.4468 | 57.6327 | 60.2262 | 58.4707 | 58.4707 | 58.4707 | 58.4707 | 58.4707 | 58.4707 | 58.4707 | 58.4707 | 58.4707 | 58.4707 | 58.4707 | 58.4707 | 58.4707 | 58.4707 | 58.4707 | 58.4707
75% | 803.6248 | 30.2685 | 42.0179 | 45.0723 | 45.593 | 45.999 | 46.6982 | 48.2889 | 49.3537 | 50.7026 | 51.4027 | 52.0187 | 50.8837 | 52.2138 | 54.3049 | 52.7181 | 52.7181 | 52.7181 | 52.7181 | 52.7181 | 52.7181 | 52.7181 | 52.7181 | 52.7181 | 52.7181 | 52.7181 | 52.7181 | 52.7181 | 52.7181 | 52.7181 | 52.7181 | 75% | 803.6248 | 32.406 | 44.0072 | 47.1809 | 47.6719 | 47.9837 | 48.6677 | 50.2832 | 51.1653 | 52.8456 | 57.9532 | 53.7425 | 52.9189 | 54.0306 | 56.4621 | 54.8163 | 54.8163 | 54.8163 | 54.8163 | 54.8163 | 54.8163 | 54.8163 | 54.8163 | 54.8163 | 54.8163 | 54.8163 | 54.8163 | 54.8163 | 54.8163 | 54.8163 | 54.8163
70% | 1155.2107 | 28.2506 | 39.2167 | 42.0675 | 42.5534 | 42.9324 | 43.585 | 45.0696 | 46.0634 | 47.3224 | 47.9759 | 48.5508 | 47.4915 | 48.7329 | 50.6846 | 49.2035 | 49.2035 | 49.2035 | 49.2035 | 49.2035 | 49.2035 | 49.2035 | 49.2035 | 49.2035 | 49.2035 | 49.2035 | 49.2035 | 49.2035 | 49.2035 | 49.2035 | 49.2035 | 70% | 1155.2107 | 30.2456 | 41.0734 | 44.0355 | 44.4938 | 44.7848 | 45.4232 | 46.931 | 47.7543 | 49.3225 | 54.0896 | 50.1596 | 49.3909 | 50.4286 | 52.6979 | 51.1618 | 51.1618 | 51.1618 | 51.1618 | 51.1618 | 51.1618 | 51.1618 | 51.1618 | 51.1618 | 51.1618 | 51.1618 | 51.1618 | 51.1618 | 51.1618 | 51.1618 | 51.1618
65% | 1553.1596 | 26.2327 | 36.4155 | 39.0627 | 39.5139 | 39.8658 | 40.4718 | 41.8504 | 42.7732 | 43.9422 | 44.549 | 45.0828 | 44.0992 | 45.252 | 47.0643 | 45.689 | 45.689 | 45.689 | 45.689 | 45.689 | 45.689 | 45.689 | 45.689 | 45.689 | 45.689 | 45.689 | 45.689 | 45.689 | 45.689 | 45.689 | 45.689 | 65% | 1553.1596 | 28.0852 | 38.1396 | 40.8901 | 41.3157 | 41.5859 | 42.1787 | 43.5788 | 44.3433 | 45.7995 | 50.2261 | 46.5768 | 45.863 | 46.8266 | 48.9338 | 47.5074 | 47.5074 | 47.5074 | 47.5074 | 47.5074 | 47.5074 | 47.5074 | 47.5074 | 47.5074 | 47.5074 | 47.5074 | 47.5074 | 47.5074 | 47.5074 | 47.5074 | 47.5074
60% | 2026.2996 | 24.2148 | 33.6143 | 36.0579 | 36.4744 | 36.7992 | 37.3586 | 38.6311 | 39.4829 | 40.562 | 41.1222 | 41.6149 | 40.707 | 41.7711 | 43.4439 | 42.1745 | 42.1745 | 42.1745 | 42.1745 | 42.1745 | 42.1745 | 42.1745 | 42.1745 | 42.1745 | 42.1745 | 42.1745 | 42.1745 | 42.1745 | 42.1745 | 42.1745 | 42.1745 | 60% | 2026.2996 | 25.9248 | 35.2058 | 37.7447 | 38.1375 | 38.387 | 38.9342 | 40.2266 | 40.9322 | 42.2765 | 46.3625 | 42.994 | 42.3351 | 43.2245 | 45.1696 | 43.853 | 43.853 | 43.853 | 43.853 | 43.853 | 43.853 | 43.853 | 43.853 | 43.853 | 43.853 | 43.853 | 43.853 | 43.853 | 43.853 | 43.853 | 43.853
55% | 2598.4068 | 22.1969 | 30.8131 | 33.053 | 33.4348 | 33.7326 | 34.2454 | 35.4119 | 36.1927 | 37.1819 | 37.6953 | 38.147 | 37.3147 | 38.2902 | 39.8236 | 38.6599 | 38.6599 | 38.6599 | 38.6599 | 38.6599 | 38.6599 | 38.6599 | 38.6599 | 38.6599 | 38.6599 | 38.6599 | 38.6599 | 38.6599 | 38.6599 | 38.6599 | 38.6599 | 55% | 2598.4068 | 23.7644 | 32.272 | 34.5993 | 34.9594 | 35.188 | 35.6897 | 36.8744 | 37.5212 | 38.7534 | 42.499 | 39.4111 | 38.8072 | 39.6225 | 41.4055 | 40.1986 | 40.1986 | 40.1986 | 40.1986 | 40.1986 | 40.1986 | 40.1986 | 40.1986 | 40.1986 | 40.1986 | 40.1986 | 40.1986 | 40.1986 | 40.1986 | 40.1986 | 40.1986
50% | 3233.5201 | 20.179 | 28.0119 | 30.0482 | 30.3953 | 30.666 | 31.1321 | 32.1926 | 32.9024 | 33.8017 | 34.2685 | 34.6791 | 33.9225 | 34.8092 | 36.2033 | 35.1454 | 35.1454 | 35.1454 | 35.1454 | 35.1454 | 35.1454 | 35.1454 | 35.1454 | 35.1454 | 35.1454 | 35.1454 | 35.1454 | 35.1454 | 35.1454 | 35.1454 | 35.1454 | 50% | 3233.5201 | 21.604 | 29.3381 | 31.4539 | 31.7813 | 31.9891 | 32.4451 | 33.5222 | 34.1102 | 35.2304 | 38.6354 | 35.8283 | 35.2792 | 36.0204 | 37.6414 | 36.5442 | 36.5442 | 36.5442 | 36.5442 | 36.5442 | 36.5442 | 36.5442 | 36.5442 | 36.5442 | 36.5442 | 36.5442 | 36.5442 | 36.5442 | 36.5442 | 36.5442 | 36.5442
45% | 3775.313 | 18.1611 | 25.2107 | 27.0434 | 27.3558 | 27.5994 | 28.0189 | 28.9733 | 29.6122 | 30.4215 | 30.8416 | 31.2112 | 30.5302 | 31.3283 | 32.583 | 31.6309 | 31.6309 | 31.6309 | 31.6309 | 31.6309 | 31.6309 | 31.6309 | 31.6309 | 31.6309 | 31.6309 | 31.6309 | 31.6309 | 31.6309 | 31.6309 | 31.6309 | 31.6309 | 45% | 3775.313 | 19.4436 | 26.4043 | 28.3085 | 28.6031 | 28.7902 | 29.2006 | 30.1699 | 30.6992 | 31.7073 | 34.7719 | 32.2455 | 31.7513 | 32.4184 | 33.8772 | 32.8898 | 32.8898 | 32.8898 | 32.8898 | 32.8898 | 32.8898 | 32.8898 | 32.8898 | 32.8898 | 32.8898 | 32.8898 | 32.8898 | 32.8898 | 32.8898 | 32.8898 | 32.8898
40% | 4072.8088 | 16.1432 | 22.4095 | 24.0386 | 24.3162 | 24.5328 | 24.9057 | 25.7541 | 26.322 | 27.0414 | 27.4148 | 27.7433 | 27.138 | 27.8474 | 28.9626 | 28.1163 | 28.1163 | 28.1163 | 28.1163 | 28.1163 | 28.1163 | 28.1163 | 28.1163 | 28.1163 | 28.1163 | 28.1163 | 28.1163 | 28.1163 | 28.1163 | 28.1163 | 28.1163 | 40% | 4072.8088 | 17.2832 | 23.4705 | 25.1631 | 25.425 | 25.5913 | 25.9561 | 26.8177 | 27.2882 | 28.1843 | 30.9084 | 28.6627 | 28.2234 | 28.8163 | 30.1131 | 29.2353 | 29.2353 | 29.2353 | 29.2353 | 29.2353 | 29.2353 | 29.2353 | 29.2353 | 29.2353 | 29.2353 | 29.2353 | 29.2353 | 29.2353 | 29.2353 | 29.2353 | 29.2353
35% | 4198.821 | 14.1253 | 19.6083 | 21.0337 | 21.2767 | 21.4662 | 21.7925 | 22.5348 | 23.0317 | 23.6612 | 23.9879 | 24.2754 | 23.7457 | 24.3665 | 25.3423 | 24.6018 | 24.6018 | 24.6018 | 24.6018 | 24.6018 | 24.6018 | 24.6018 | 24.6018 | 24.6018 | 24.6018 | 24.6018 | 24.6018 | 24.6018 | 24.6018 | 24.6018 | 24.6018 | 35% | 4198.821 | 15.1228 | 20.5367 | 22.0177 | 22.2469 | 22.3924 | 22.7116 | 23.4655 | 23.8771 | 24.6613 | 27.0448 | 25.0798 | 24.6955 | 25.2143 | 26.349 | 25.5809 | 25.5809 | 25.5809 | 25.5809 | 25.5809 | 25.5809 | 25.5809 | 25.5809 | 25.5809 | 25.5809 | 25.5809 | 25.5809 | 25.5809 | 25.5809 | 25.5809 | 25.5809
30% | 4271.3374 | 12.1074 | 16.8072 | 18.0289 | 18.2372 | 18.3996 | 18.6793 | 19.3156 | 19.7415 | 20.281 | 20.5611 | 20.8075 | 20.3535 | 20.8855 | 21.722 | 21.0872 | 21.0872 | 21.0872 | 21.0872 | 21.0872 | 21.0872 | 21.0872 | 21.0872 | 21.0872 | 21.0872 | 21.0872 | 21.0872 | 21.0872 | 21.0872 | 21.0872 | 21.0872 | 30% | 4271.3374 | 12.9624 | 17.6029 | 18.8723 | 19.0688 | 19.1935 | 19.4671 | 20.1133 | 20.4661 | 21.1382 | 23.1813 | 21.497 | 21.1675 | 21.6123 | 22.5848 | 21.9265 | 21.9265 | 21.9265 | 21.9265 | 21.9265 | 21.9265 | 21.9265 | 21.9265 | 21.9265 | 21.9265 | 21.9265 | 21.9265 | 21.9265 | 21.9265 | 21.9265 | 21.9265
25% | 4321.8611 | 10.0895 | 14.006 | 15.0241 | 15.1977 | 15.333 | 15.5661 | 16.0963 | 16.4512 | 16.9009 | 17.1342 | 17.3396 | 16.9612 | 17.4046 | 18.1016 | 17.5727 | 17.5727 | 17.5727 | 17.5727 | 17.5727 | 17.5727 | 17.5727 | 17.5727 | 17.5727 | 17.5727 | 17.5727 | 17.5727 | 17.5727 | 17.5727 | 17.5727 | 17.5727 | 25% | 4321.8611 | 10.802 | 14.6691 | 15.727 | 15.8906 | 15.9946 | 16.2226 | 16.7611 | 17.0551 | 17.6152 | 19.3177 | 17.9142 | 17.6396 | 18.0102 | 18.8207 | 18.2721 | 18.2721 | 18.2721 | 18.2721 | 18.2721 | 18.2721 | 18.2721 | 18.2721 | 18.2721 | 18.2721 | 18.2721 | 18.2721 | 18.2721 | 18.2721 | 18.2721 | 18.2721
20% | 4353.067 | 8.0716 | 11.2048 | 12.0193 | 12.1581 | 12.2664 | 12.4529 | 12.877 | 13.161 | 13.5207 | 13.7074 | 13.8716 | 13.569 | 13.9237 | 14.4813 | 14.0582 | 14.0582 | 14.0582 | 14.0582 | 14.0582 | 14.0582 | 14.0582 | 14.0582 | 14.0582 | 14.0582 | 14.0582 | 14.0582 | 14.0582 | 14.0582 | 14.0582 | 14.0582 | 20% | 4353.067 | 8.6416 | 11.7353 | 12.5816 | 12.7125 | 12.7957 | 12.9781 | 13.4089 | 13.6441 | 14.0922 | 15.4542 | 14.3313 | 14.1117 | 14.4082 | 15.0565 | 14.6177 | 14.6177 | 14.6177 | 14.6177 | 14.6177 | 14.6177 | 14.6177 | 14.6177 | 14.6177 | 14.6177 | 14.6177 | 14.6177 | 14.6177 | 14.6177 | 14.6177 | 14.6177
15% | 4369.4129 | 6.0537 | 8.4036 | 9.0145 | 9.1186 | 9.1998 | 9.3396 | 9.6578 | 9.8707 | 10.1405 | 10.2805 | 10.4037 | 10.1767 | 10.4428 | 10.861 | 10.5436 | 10.5436 | 10.5436 | 10.5436 | 10.5436 | 10.5436 | 10.5436 | 10.5436 | 10.5436 | 10.5436 | 10.5436 | 10.5436 | 10.5436 | 10.5436 | 10.5436 | 10.5436 | 15% | 4369.4129 | 6.4812 | 8.8014 | 9.4362 | 9.5344 | 9.5967 | 9.7335 | 10.0566 | 10.2331 | 10.5691 | 11.5906 | 10.7485 | 10.5838 | 10.8061 | 11.2924 | 10.9633 | 10.9633 | 10.9633 | 10.9633 | 10.9633 | 10.9633 | 10.9633 | 10.9633 | 10.9633 | 10.9633 | 10.9633 | 10.9633 | 10.9633 | 10.9633 | 10.9633 | 10.9633
10% | 4378.6261 | 4.0358 | 5.6024 | 6.0096 | 6.0791 | 6.1332 | 6.2264 | 6.4385 | 6.5805 | 6.7603 | 6.8537 | 6.9358 | 6.7845 | 6.9618 | 7.2407 | 7.0291 | 7.0291 | 7.0291 | 7.0291 | 7.0291 | 7.0291 | 7.0291 | 7.0291 | 7.0291 | 7.0291 | 7.0291 | 7.0291 | 7.0291 | 7.0291 | 7.0291 | 7.0291 | 10% | 4378.6261 | 4.3208 | 5.8676 | 6.2908 | 6.3563 | 6.3978 | 6.489 | 6.7044 | 6.822 | 7.0461 | 7.7271 | 7.1657 | 7.0558 | 7.2041 | 7.5283 | 7.3088 | 7.3088 | 7.3088 | 7.3088 | 7.3088 | 7.3088 | 7.3088 | 7.3088 | 7.3088 | 7.3088 | 7.3088 | 7.3088 | 7.3088 | 7.3088 | 7.3088 | 7.3088
5% | 4391.7028 | 2.0179 | 2.8012 | 3.0048 | 3.0395 | 3.0666 | 3.1132 | 3.2193 | 3.2902 | 3.3802 | 3.4268 | 3.4679 | 3.3922 | 3.4809 | 3.6203 | 3.5145 | 3.5145 | 3.5145 | 3.5145 | 3.5145 | 3.5145 | 3.5145 | 3.5145 | 3.5145 | 3.5145 | 3.5145 | 3.5145 | 3.5145 | 3.5145 | 3.5145 | 3.5145 | 5% | 4391.7028 | 2.1604 | 2.9338 | 3.1454 | 3.1781 | 3.1989 | 3.2445 | 3.3522 | 3.411 | 3.523 | 3.8635 | 3.5828 | 3.5279 | 3.602 | 3.7641 | 3.6544 | 3.6544 | 3.6544 | 3.6544 | 3.6544 | 3.6544 | 3.6544 | 3.6544 | 3.6544 | 3.6544 | 3.6544 | 3.6544 | 3.6544 | 3.6544 | 3.6544 | 3.6544
9.992e-14% | 4391.7028 | 4.0326e-14 | 5.5979e-14 | 6.0048e-14 | 6.0742e-14 | 6.1283e-14 | 6.2215e-14 | 6.4334e-14 | 6.5752e-14 | 6.7549e-14 | 6.8482e-14 | 6.9303e-14 | 6.7791e-14 | 6.9563e-14 | 7.2349e-14 | 7.0235e-14 | 7.0235e-14 | 7.0235e-14 | 7.0235e-14 | 7.0235e-14 | 7.0235e-14 | 7.0235e-14 | 7.0235e-14 | 7.0235e-14 | 7.0235e-14 | 7.0235e-14 | 7.0235e-14 | 7.0235e-14 | 7.0235e-14 | 7.0235e-14 | 7.0235e-14 | 9.992e-14% | 4391.7028 | 4.3173e-14 | 5.8629e-14 | 6.2858e-14 | 6.3512e-14 | 6.3927e-14 | 6.4838e-14 | 6.6991e-14 | 6.8166e-14 | 7.0404e-14 | 7.7209e-14 | 7.1599e-14 | 7.0502e-14 | 7.1983e-14 | 7.5223e-14 | 7.303e-14 | 7.303e-14 | 7.303e-14 | 7.303e-14 | 7.303e-14 | 7.303e-14 | 7.303e-14 | 7.303e-14 | 7.303e-14 | 7.303e-14 | 7.303e-14 | 7.303e-14 | 7.303e-14 | 7.303e-14 | 7.303e-14 | 7.303e-14
Summer Season | [31 empty] | Summer Season
P50 | [31 empty] | P10
% of MD | Summer - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Summer - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 45.8759 | 60.9589 | 65.0674 | 64.9499 | 64.9485 | 65.4184 | 65.9338 | 66.9909 | 67.7504 | 68.1633 | 68.6157 | 69.029 | 69.7743 | 70.6989 | 70.6364 | 70.6364 | 70.6364 | 70.6364 | 70.6364 | 70.6364 | 70.6364 | 70.6364 | 70.6364 | 70.6364 | 70.6364 | 70.6364 | 70.6364 | 70.6364 | 70.6364 | 70.6364 | 100% | 0 | 51.1554 | 66.2686 | 70.2261 | 69.9907 | 70.0105 | 70.4179 | 71.4905 | 72.2097 | 72.9132 | 73.7356 | 74.4985 | 75.2386 | 75.3243 | 76.1878 | 75.5357 | 75.5357 | 75.5357 | 75.5357 | 75.5357 | 75.5357 | 75.5357 | 75.5357 | 75.5357 | 75.5357 | 75.5357 | 75.5357 | 75.5357 | 75.5357 | 75.5357 | 75.5357
99% | 0 | 45.4171 | 60.3493 | 64.4168 | 64.3004 | 64.299 | 64.7642 | 65.2745 | 66.321 | 67.0729 | 67.4817 | 67.9295 | 68.3387 | 69.0766 | 69.9919 | 69.93 | 69.93 | 69.93 | 69.93 | 69.93 | 69.93 | 69.93 | 69.93 | 69.93 | 69.93 | 69.93 | 69.93 | 69.93 | 69.93 | 69.93 | 69.93 | 99% | 1.5127 | 50.6438 | 65.6059 | 69.5238 | 69.2908 | 69.3104 | 69.7137 | 70.7756 | 71.4876 | 72.184 | 72.9983 | 73.7535 | 74.4862 | 74.571 | 75.4259 | 74.7803 | 74.7803 | 74.7803 | 74.7803 | 74.7803 | 74.7803 | 74.7803 | 74.7803 | 74.7803 | 74.7803 | 74.7803 | 74.7803 | 74.7803 | 74.7803 | 74.7803 | 74.7803
98% | 0 | 44.9584 | 59.7397 | 63.7661 | 63.6509 | 63.6495 | 64.11 | 64.6151 | 65.6511 | 66.3954 | 66.8001 | 67.2434 | 67.6484 | 68.3788 | 69.2849 | 69.2236 | 69.2236 | 69.2236 | 69.2236 | 69.2236 | 69.2236 | 69.2236 | 69.2236 | 69.2236 | 69.2236 | 69.2236 | 69.2236 | 69.2236 | 69.2236 | 69.2236 | 69.2236 | 98% | 2.269 | 50.1322 | 64.9433 | 68.8216 | 68.5909 | 68.6103 | 69.0096 | 70.0607 | 70.7655 | 71.4549 | 72.2609 | 73.0085 | 73.7338 | 73.8178 | 74.664 | 74.0249 | 74.0249 | 74.0249 | 74.0249 | 74.0249 | 74.0249 | 74.0249 | 74.0249 | 74.0249 | 74.0249 | 74.0249 | 74.0249 | 74.0249 | 74.0249 | 74.0249 | 74.0249
97% | 0.37816 | 44.4996 | 59.1301 | 63.1154 | 63.0014 | 63 | 63.4558 | 63.9558 | 64.9812 | 65.7179 | 66.1184 | 66.5572 | 66.9581 | 67.6811 | 68.5779 | 68.5173 | 68.5173 | 68.5173 | 68.5173 | 68.5173 | 68.5173 | 68.5173 | 68.5173 | 68.5173 | 68.5173 | 68.5173 | 68.5173 | 68.5173 | 68.5173 | 68.5173 | 68.5173 | 97% | 3.7816 | 49.6207 | 64.2806 | 68.1193 | 67.891 | 67.9102 | 68.3054 | 69.3458 | 70.0434 | 70.7258 | 71.5236 | 72.2636 | 72.9814 | 73.0646 | 73.9022 | 73.2696 | 73.2696 | 73.2696 | 73.2696 | 73.2696 | 73.2696 | 73.2696 | 73.2696 | 73.2696 | 73.2696 | 73.2696 | 73.2696 | 73.2696 | 73.2696 | 73.2696 | 73.2696
95% | 2.269 | 43.5821 | 57.911 | 61.8141 | 61.7024 | 61.701 | 62.1474 | 62.6371 | 63.6414 | 64.3629 | 64.7552 | 65.1849 | 65.5776 | 66.2856 | 67.1639 | 67.1046 | 67.1046 | 67.1046 | 67.1046 | 67.1046 | 67.1046 | 67.1046 | 67.1046 | 67.1046 | 67.1046 | 67.1046 | 67.1046 | 67.1046 | 67.1046 | 67.1046 | 67.1046 | 95% | 6.0506 | 48.5976 | 62.9552 | 66.7148 | 66.4912 | 66.51 | 66.897 | 67.916 | 68.5992 | 69.2675 | 70.0488 | 70.7736 | 71.4766 | 71.5581 | 72.3784 | 71.7589 | 71.7589 | 71.7589 | 71.7589 | 71.7589 | 71.7589 | 71.7589 | 71.7589 | 71.7589 | 71.7589 | 71.7589 | 71.7589 | 71.7589 | 71.7589 | 71.7589 | 71.7589
90% | 5.6725 | 41.2883 | 54.863 | 58.5607 | 58.4549 | 58.4536 | 58.8765 | 59.3404 | 60.2918 | 60.9754 | 61.347 | 61.7541 | 62.1261 | 62.7969 | 63.629 | 63.5727 | 63.5727 | 63.5727 | 63.5727 | 63.5727 | 63.5727 | 63.5727 | 63.5727 | 63.5727 | 63.5727 | 63.5727 | 63.5727 | 63.5727 | 63.5727 | 63.5727 | 63.5727 | 90% | 16.2611 | 46.0398 | 59.6418 | 63.2035 | 62.9917 | 63.0094 | 63.3761 | 64.3415 | 64.9887 | 65.6218 | 66.3621 | 67.0487 | 67.7147 | 67.7919 | 68.569 | 67.9821 | 67.9821 | 67.9821 | 67.9821 | 67.9821 | 67.9821 | 67.9821 | 67.9821 | 67.9821 | 67.9821 | 67.9821 | 67.9821 | 67.9821 | 67.9821 | 67.9821 | 67.9821
85% | 15.8829 | 38.9945 | 51.8151 | 55.3073 | 55.2074 | 55.2062 | 55.6056 | 56.0437 | 56.9423 | 57.5879 | 57.9388 | 58.3233 | 58.6747 | 59.3082 | 60.094 | 60.0409 | 60.0409 | 60.0409 | 60.0409 | 60.0409 | 60.0409 | 60.0409 | 60.0409 | 60.0409 | 60.0409 | 60.0409 | 60.0409 | 60.0409 | 60.0409 | 60.0409 | 60.0409 | 85% | 26.4715 | 43.482 | 56.3283 | 59.6922 | 59.4921 | 59.5089 | 59.8552 | 60.767 | 61.3783 | 61.9762 | 62.6753 | 63.3237 | 63.9528 | 64.0256 | 64.7596 | 64.2053 | 64.2053 | 64.2053 | 64.2053 | 64.2053 | 64.2053 | 64.2053 | 64.2053 | 64.2053 | 64.2053 | 64.2053 | 64.2053 | 64.2053 | 64.2053 | 64.2053 | 64.2053
80% | 31.0095 | 36.7007 | 48.7671 | 52.0539 | 51.9599 | 51.9588 | 52.3347 | 52.747 | 53.5928 | 54.2003 | 54.5307 | 54.8925 | 55.2232 | 55.8194 | 56.5591 | 56.5091 | 56.5091 | 56.5091 | 56.5091 | 56.5091 | 56.5091 | 56.5091 | 56.5091 | 56.5091 | 56.5091 | 56.5091 | 56.5091 | 56.5091 | 56.5091 | 56.5091 | 56.5091 | 80% | 34.0348 | 40.9243 | 53.0149 | 56.1809 | 55.9926 | 56.0084 | 56.3343 | 57.1924 | 57.7678 | 58.3305 | 58.9885 | 59.5988 | 60.1908 | 60.2594 | 60.9502 | 60.4285 | 60.4285 | 60.4285 | 60.4285 | 60.4285 | 60.4285 | 60.4285 | 60.4285 | 60.4285 | 60.4285 | 60.4285 | 60.4285 | 60.4285 | 60.4285 | 60.4285 | 60.4285
75% | 72.9857 | 34.4069 | 45.7192 | 48.8006 | 48.7124 | 48.7113 | 49.0638 | 49.4504 | 50.2432 | 50.8128 | 51.1225 | 51.4618 | 51.7718 | 52.3307 | 53.0241 | 52.9773 | 52.9773 | 52.9773 | 52.9773 | 52.9773 | 52.9773 | 52.9773 | 52.9773 | 52.9773 | 52.9773 | 52.9773 | 52.9773 | 52.9773 | 52.9773 | 52.9773 | 52.9773 | 75% | 48.405 | 38.3665 | 49.7015 | 52.6696 | 52.493 | 52.5079 | 52.8134 | 53.6179 | 54.1573 | 54.6849 | 55.3017 | 55.8739 | 56.4289 | 56.4932 | 57.1408 | 56.6517 | 56.6517 | 56.6517 | 56.6517 | 56.6517 | 56.6517 | 56.6517 | 56.6517 | 56.6517 | 56.6517 | 56.6517 | 56.6517 | 56.6517 | 56.6517 | 56.6517 | 56.6517
70% | 150.5094 | 32.1131 | 42.6712 | 45.5472 | 45.4649 | 45.4639 | 45.7929 | 46.1537 | 46.8937 | 47.4253 | 47.7143 | 48.031 | 48.3203 | 48.842 | 49.4892 | 49.4455 | 49.4455 | 49.4455 | 49.4455 | 49.4455 | 49.4455 | 49.4455 | 49.4455 | 49.4455 | 49.4455 | 49.4455 | 49.4455 | 49.4455 | 49.4455 | 49.4455 | 49.4455 | 70% | 76.3892 | 35.8087 | 46.388 | 49.1583 | 48.9935 | 49.0073 | 49.2925 | 50.0434 | 50.5468 | 51.0392 | 51.6149 | 52.149 | 52.667 | 52.727 | 53.3315 | 52.875 | 52.875 | 52.875 | 52.875 | 52.875 | 52.875 | 52.875 | 52.875 | 52.875 | 52.875 | 52.875 | 52.875 | 52.875 | 52.875 | 52.875 | 52.875
65% | 359.6342 | 29.8193 | 39.6233 | 42.2938 | 42.2174 | 42.2165 | 42.5219 | 42.857 | 43.5441 | 44.0378 | 44.3062 | 44.6002 | 44.8689 | 45.3533 | 45.9543 | 45.9136 | 45.9136 | 45.9136 | 45.9136 | 45.9136 | 45.9136 | 45.9136 | 45.9136 | 45.9136 | 45.9136 | 45.9136 | 45.9136 | 45.9136 | 45.9136 | 45.9136 | 45.9136 | 65% | 114.2056 | 33.251 | 43.0746 | 45.647 | 45.494 | 45.5068 | 45.7716 | 46.4689 | 46.9363 | 47.3936 | 47.9282 | 48.424 | 48.9051 | 48.9608 | 49.5221 | 49.0982 | 49.0982 | 49.0982 | 49.0982 | 49.0982 | 49.0982 | 49.0982 | 49.0982 | 49.0982 | 49.0982 | 49.0982 | 49.0982 | 49.0982 | 49.0982 | 49.0982 | 49.0982
60% | 689.7717 | 27.5255 | 36.5753 | 39.0405 | 38.9699 | 38.9691 | 39.251 | 39.5603 | 40.1946 | 40.6503 | 40.898 | 41.1694 | 41.4174 | 41.8646 | 42.4193 | 42.3818 | 42.3818 | 42.3818 | 42.3818 | 42.3818 | 42.3818 | 42.3818 | 42.3818 | 42.3818 | 42.3818 | 42.3818 | 42.3818 | 42.3818 | 42.3818 | 42.3818 | 42.3818 | 60% | 178.1154 | 30.6932 | 39.7612 | 42.1357 | 41.9944 | 42.0063 | 42.2508 | 42.8943 | 43.3258 | 43.7479 | 44.2414 | 44.6991 | 45.1431 | 45.1946 | 45.7127 | 45.3214 | 45.3214 | 45.3214 | 45.3214 | 45.3214 | 45.3214 | 45.3214 | 45.3214 | 45.3214 | 45.3214 | 45.3214 | 45.3214 | 45.3214 | 45.3214 | 45.3214 | 45.3214
55% | 1095.5419 | 25.2317 | 33.5274 | 35.7871 | 35.7224 | 35.7217 | 35.9801 | 36.2636 | 36.845 | 37.2627 | 37.4898 | 37.7386 | 37.966 | 38.3759 | 38.8844 | 38.85 | 38.85 | 38.85 | 38.85 | 38.85 | 38.85 | 38.85 | 38.85 | 38.85 | 38.85 | 38.85 | 38.85 | 38.85 | 38.85 | 38.85 | 38.85 | 55% | 311.6074 | 28.1354 | 36.4477 | 38.6243 | 38.4949 | 38.5058 | 38.7299 | 39.3198 | 39.7153 | 40.1022 | 40.5546 | 40.9742 | 41.3812 | 41.4284 | 41.9033 | 41.5446 | 41.5446 | 41.5446 | 41.5446 | 41.5446 | 41.5446 | 41.5446 | 41.5446 | 41.5446 | 41.5446 | 41.5446 | 41.5446 | 41.5446 | 41.5446 | 41.5446 | 41.5446
50% | 1666.1918 | 22.9379 | 30.4794 | 32.5337 | 32.4749 | 32.4742 | 32.7092 | 32.9669 | 33.4955 | 33.8752 | 34.0817 | 34.3078 | 34.5145 | 34.8872 | 35.3494 | 35.3182 | 35.3182 | 35.3182 | 35.3182 | 35.3182 | 35.3182 | 35.3182 | 35.3182 | 35.3182 | 35.3182 | 35.3182 | 35.3182 | 35.3182 | 35.3182 | 35.3182 | 35.3182 | 50% | 636.0723 | 25.5777 | 33.1343 | 35.113 | 34.9954 | 35.0052 | 35.209 | 35.7453 | 36.1049 | 36.4566 | 36.8678 | 37.2493 | 37.6193 | 37.6621 | 38.0939 | 37.7678 | 37.7678 | 37.7678 | 37.7678 | 37.7678 | 37.7678 | 37.7678 | 37.7678 | 37.7678 | 37.7678 | 37.7678 | 37.7678 | 37.7678 | 37.7678 | 37.7678 | 37.7678
45% | 2506.0947 | 20.6442 | 27.4315 | 29.2803 | 29.2274 | 29.2268 | 29.4383 | 29.6702 | 30.1459 | 30.4877 | 30.6735 | 30.8771 | 31.0631 | 31.3984 | 31.8145 | 31.7864 | 31.7864 | 31.7864 | 31.7864 | 31.7864 | 31.7864 | 31.7864 | 31.7864 | 31.7864 | 31.7864 | 31.7864 | 31.7864 | 31.7864 | 31.7864 | 31.7864 | 31.7864 | 45% | 1179.4944 | 23.0199 | 29.8209 | 31.6017 | 31.4958 | 31.5047 | 31.6881 | 32.1707 | 32.4944 | 32.8109 | 33.181 | 33.5243 | 33.8573 | 33.8959 | 34.2845 | 33.991 | 33.991 | 33.991 | 33.991 | 33.991 | 33.991 | 33.991 | 33.991 | 33.991 | 33.991 | 33.991 | 33.991 | 33.991 | 33.991 | 33.991 | 33.991
40% | 3164.4787 | 18.3504 | 24.3836 | 26.027 | 25.9799 | 25.9794 | 26.1673 | 26.3735 | 26.7964 | 27.1002 | 27.2653 | 27.4463 | 27.6116 | 27.9097 | 28.2795 | 28.2546 | 28.2546 | 28.2546 | 28.2546 | 28.2546 | 28.2546 | 28.2546 | 28.2546 | 28.2546 | 28.2546 | 28.2546 | 28.2546 | 28.2546 | 28.2546 | 28.2546 | 28.2546 | 40% | 1808.3816 | 20.4621 | 26.5075 | 28.0904 | 27.9963 | 28.0042 | 28.1672 | 28.5962 | 28.8839 | 29.1653 | 29.4942 | 29.7994 | 30.0954 | 30.1297 | 30.4751 | 30.2143 | 30.2143 | 30.2143 | 30.2143 | 30.2143 | 30.2143 | 30.2143 | 30.2143 | 30.2143 | 30.2143 | 30.2143 | 30.2143 | 30.2143 | 30.2143 | 30.2143 | 30.2143
35% | 3551.3408 | 16.0566 | 21.3356 | 22.7736 | 22.7325 | 22.732 | 22.8964 | 23.0768 | 23.4468 | 23.7126 | 23.8572 | 24.0155 | 24.1602 | 24.421 | 24.7446 | 24.7227 | 24.7227 | 24.7227 | 24.7227 | 24.7227 | 24.7227 | 24.7227 | 24.7227 | 24.7227 | 24.7227 | 24.7227 | 24.7227 | 24.7227 | 24.7227 | 24.7227 | 24.7227 | 35% | 2779.1293 | 17.9044 | 23.194 | 24.5791 | 24.4968 | 24.5037 | 24.6463 | 25.0217 | 25.2734 | 25.5196 | 25.8075 | 26.0745 | 26.3335 | 26.3635 | 26.6657 | 26.4375 | 26.4375 | 26.4375 | 26.4375 | 26.4375 | 26.4375 | 26.4375 | 26.4375 | 26.4375 | 26.4375 | 26.4375 | 26.4375 | 26.4375 | 26.4375 | 26.4375 | 26.4375
30% | 3758.953 | 13.7628 | 18.2877 | 19.5202 | 19.485 | 19.4845 | 19.6255 | 19.7801 | 20.0973 | 20.3251 | 20.449 | 20.5847 | 20.7087 | 20.9323 | 21.2097 | 21.1909 | 21.1909 | 21.1909 | 21.1909 | 21.1909 | 21.1909 | 21.1909 | 21.1909 | 21.1909 | 21.1909 | 21.1909 | 21.1909 | 21.1909 | 21.1909 | 21.1909 | 21.1909 | 30% | 3814.165 | 15.3466 | 19.8806 | 21.0678 | 20.9972 | 21.0031 | 21.1254 | 21.4472 | 21.6629 | 21.8739 | 22.1207 | 22.3496 | 22.5716 | 22.5973 | 22.8563 | 22.6607 | 22.6607 | 22.6607 | 22.6607 | 22.6607 | 22.6607 | 22.6607 | 22.6607 | 22.6607 | 22.6607 | 22.6607 | 22.6607 | 22.6607 | 22.6607 | 22.6607 | 22.6607
25% | 3926.4798 | 11.469 | 15.2397 | 16.2669 | 16.2375 | 16.2371 | 16.3546 | 16.4835 | 16.7477 | 16.9376 | 17.0408 | 17.1539 | 17.2573 | 17.4436 | 17.6747 | 17.6591 | 17.6591 | 17.6591 | 17.6591 | 17.6591 | 17.6591 | 17.6591 | 17.6591 | 17.6591 | 17.6591 | 17.6591 | 17.6591 | 17.6591 | 17.6591 | 17.6591 | 17.6591 | 25% | 4166.9923 | 12.7888 | 16.5672 | 17.5565 | 17.4977 | 17.5026 | 17.6045 | 17.8726 | 18.0524 | 18.2283 | 18.4339 | 18.6246 | 18.8096 | 18.8311 | 19.0469 | 18.8839 | 18.8839 | 18.8839 | 18.8839 | 18.8839 | 18.8839 | 18.8839 | 18.8839 | 18.8839 | 18.8839 | 18.8839 | 18.8839 | 18.8839 | 18.8839 | 18.8839 | 18.8839
20% | 4050.5177 | 9.1752 | 12.1918 | 13.0135 | 12.99 | 12.9897 | 13.0837 | 13.1868 | 13.3982 | 13.5501 | 13.6327 | 13.7231 | 13.8058 | 13.9549 | 14.1398 | 14.1273 | 14.1273 | 14.1273 | 14.1273 | 14.1273 | 14.1273 | 14.1273 | 14.1273 | 14.1273 | 14.1273 | 14.1273 | 14.1273 | 14.1273 | 14.1273 | 14.1273 | 14.1273 | 20% | 4282.7105 | 10.2311 | 13.2537 | 14.0452 | 13.9981 | 14.0021 | 14.0836 | 14.2981 | 14.4419 | 14.5826 | 14.7471 | 14.8997 | 15.0477 | 15.0649 | 15.2376 | 15.1071 | 15.1071 | 15.1071 | 15.1071 | 15.1071 | 15.1071 | 15.1071 | 15.1071 | 15.1071 | 15.1071 | 15.1071 | 15.1071 | 15.1071 | 15.1071 | 15.1071 | 15.1071
15% | 4152.622 | 6.8814 | 9.1438 | 9.7601 | 9.7425 | 9.7423 | 9.8128 | 9.8901 | 10.0486 | 10.1626 | 10.2245 | 10.2924 | 10.3544 | 10.4661 | 10.6048 | 10.5955 | 10.5955 | 10.5955 | 10.5955 | 10.5955 | 10.5955 | 10.5955 | 10.5955 | 10.5955 | 10.5955 | 10.5955 | 10.5955 | 10.5955 | 10.5955 | 10.5955 | 10.5955 | 15% | 4364.7722 | 7.6733 | 9.9403 | 10.5339 | 10.4986 | 10.5016 | 10.5627 | 10.7236 | 10.8315 | 10.937 | 11.0603 | 11.1748 | 11.2858 | 11.2986 | 11.4282 | 11.3303 | 11.3303 | 11.3303 | 11.3303 | 11.3303 | 11.3303 | 11.3303 | 11.3303 | 11.3303 | 11.3303 | 11.3303 | 11.3303 | 11.3303 | 11.3303 | 11.3303 | 11.3303
10% | 4248.2976 | 4.5876 | 6.0959 | 6.5067 | 6.495 | 6.4948 | 6.5418 | 6.5934 | 6.6991 | 6.775 | 6.8163 | 6.8616 | 6.9029 | 6.9774 | 7.0699 | 7.0636 | 7.0636 | 7.0636 | 7.0636 | 7.0636 | 7.0636 | 7.0636 | 7.0636 | 7.0636 | 7.0636 | 7.0636 | 7.0636 | 7.0636 | 7.0636 | 7.0636 | 7.0636 | 10% | 4391.6218 | 5.1155 | 6.6269 | 7.0226 | 6.9991 | 7.001 | 7.0418 | 7.1491 | 7.221 | 7.2913 | 7.3736 | 7.4499 | 7.5239 | 7.5324 | 7.6188 | 7.5536 | 7.5536 | 7.5536 | 7.5536 | 7.5536 | 7.5536 | 7.5536 | 7.5536 | 7.5536 | 7.5536 | 7.5536 | 7.5536 | 7.5536 | 7.5536 | 7.5536 | 7.5536
5% | 4361.7469 | 2.2938 | 3.0479 | 3.2534 | 3.2475 | 3.2474 | 3.2709 | 3.2967 | 3.3495 | 3.3875 | 3.4082 | 3.4308 | 3.4515 | 3.4887 | 3.5349 | 3.5318 | 3.5318 | 3.5318 | 3.5318 | 3.5318 | 3.5318 | 3.5318 | 3.5318 | 3.5318 | 3.5318 | 3.5318 | 3.5318 | 3.5318 | 3.5318 | 3.5318 | 3.5318 | 5% | 4391.6218 | 2.5578 | 3.3134 | 3.5113 | 3.4995 | 3.5005 | 3.5209 | 3.5745 | 3.6105 | 3.6457 | 3.6868 | 3.7249 | 3.7619 | 3.7662 | 3.8094 | 3.7768 | 3.7768 | 3.7768 | 3.7768 | 3.7768 | 3.7768 | 3.7768 | 3.7768 | 3.7768 | 3.7768 | 3.7768 | 3.7768 | 3.7768 | 3.7768 | 3.7768 | 3.7768
9.992e-14% | 4391.6218 | 4.5839e-14 | 6.091e-14 | 6.5015e-14 | 6.4898e-14 | 6.4897e-14 | 6.5366e-14 | 6.5881e-14 | 6.6937e-14 | 6.7696e-14 | 6.8109e-14 | 6.8561e-14 | 6.8974e-14 | 6.9719e-14 | 7.0642e-14 | 7.058e-14 | 7.058e-14 | 7.058e-14 | 7.058e-14 | 7.058e-14 | 7.058e-14 | 7.058e-14 | 7.058e-14 | 7.058e-14 | 7.058e-14 | 7.058e-14 | 7.058e-14 | 7.058e-14 | 7.058e-14 | 7.058e-14 | 7.058e-14 | 9.992e-14% | 4391.6218 | 5.1114e-14 | 6.6216e-14 | 7.017e-14 | 6.9935e-14 | 6.9955e-14 | 7.0362e-14 | 7.1433e-14 | 7.2152e-14 | 7.2855e-14 | 7.3677e-14 | 7.4439e-14 | 7.5178e-14 | 7.5264e-14 | 7.6127e-14 | 7.5475e-14 | 7.5475e-14 | 7.5475e-14 | 7.5475e-14 | 7.5475e-14 | 7.5475e-14 | 7.5475e-14 | 7.5475e-14 | 7.5475e-14 | 7.5475e-14 | 7.5475e-14 | 7.5475e-14 | 7.5475e-14 | 7.5475e-14 | 7.5475e-14 | 7.5475e-14
Option 4
Winter Season | [31 empty] | Winter Season
P50 | [31 empty] | P10
% of MD | Winter - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Winter - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 40.358 | 56.0239 | 60.0964 | 56.7906 | 57.3321 | 58.2643 | 60.3852 | 61.8049 | 63.6034 | 64.5369 | 65.3582 | 63.845 | 65.6185 | 68.4066 | 66.2908 | 66.2908 | 66.2908 | 66.2908 | 66.2908 | 66.2908 | 66.2908 | 66.2908 | 66.2908 | 66.2908 | 66.2908 | 66.2908 | 66.2908 | 66.2908 | 66.2908 | 66.2908 | 100% | 0 | 43.208 | 58.6763 | 62.9078 | 59.5625 | 59.9783 | 60.8903 | 63.0443 | 64.2204 | 66.4608 | 73.2709 | 67.6566 | 66.5585 | 68.0408 | 71.2827 | 69.0883 | 69.0883 | 69.0883 | 69.0883 | 69.0883 | 69.0883 | 69.0883 | 69.0883 | 69.0883 | 69.0883 | 69.0883 | 69.0883 | 69.0883 | 69.0883 | 69.0883 | 69.0883
99% | 1.486 | 39.9544 | 55.4636 | 59.4955 | 56.2227 | 56.7587 | 57.6816 | 59.7813 | 61.1868 | 62.9674 | 63.8916 | 64.7046 | 63.2065 | 64.9623 | 67.7225 | 65.6279 | 65.6279 | 65.6279 | 65.6279 | 65.6279 | 65.6279 | 65.6279 | 65.6279 | 65.6279 | 65.6279 | 65.6279 | 65.6279 | 65.6279 | 65.6279 | 65.6279 | 65.6279 | 99% | 1.486 | 42.7759 | 58.0895 | 62.2787 | 58.9669 | 59.3785 | 60.2814 | 62.4139 | 63.5782 | 65.7962 | 72.5382 | 66.9801 | 65.8929 | 67.3604 | 70.5699 | 68.3975 | 68.3975 | 68.3975 | 68.3975 | 68.3975 | 68.3975 | 68.3975 | 68.3975 | 68.3975 | 68.3975 | 68.3975 | 68.3975 | 68.3975 | 68.3975 | 68.3975 | 68.3975
98% | 3.2692 | 39.5508 | 54.9034 | 58.8945 | 55.6548 | 56.1854 | 57.099 | 59.1775 | 60.5688 | 62.3313 | 63.2462 | 64.0511 | 62.5681 | 64.3061 | 67.0384 | 64.965 | 64.965 | 64.965 | 64.965 | 64.965 | 64.965 | 64.965 | 64.965 | 64.965 | 64.965 | 64.965 | 64.965 | 64.965 | 64.965 | 64.965 | 64.965 | 98% | 3.2692 | 42.3438 | 57.5027 | 61.6497 | 58.3713 | 58.7787 | 59.6725 | 61.7834 | 62.936 | 65.1316 | 71.8055 | 66.3035 | 65.2273 | 66.68 | 69.8571 | 67.7066 | 67.7066 | 67.7066 | 67.7066 | 67.7066 | 67.7066 | 67.7066 | 67.7066 | 67.7066 | 67.7066 | 67.7066 | 67.7066 | 67.7066 | 67.7066 | 67.7066 | 67.7066
97% | 6.8356 | 39.1473 | 54.3431 | 58.2935 | 55.0869 | 55.6121 | 56.5164 | 58.5736 | 59.9507 | 61.6953 | 62.6008 | 63.3975 | 61.9296 | 63.6499 | 66.3544 | 64.3021 | 64.3021 | 64.3021 | 64.3021 | 64.3021 | 64.3021 | 64.3021 | 64.3021 | 64.3021 | 64.3021 | 64.3021 | 64.3021 | 64.3021 | 64.3021 | 64.3021 | 64.3021 | 97% | 6.8356 | 41.9118 | 56.916 | 61.0206 | 57.7757 | 58.1789 | 59.0636 | 61.153 | 62.2938 | 64.4669 | 71.0728 | 65.6269 | 64.5617 | 65.9996 | 69.1443 | 67.0157 | 67.0157 | 67.0157 | 67.0157 | 67.0157 | 67.0157 | 67.0157 | 67.0157 | 67.0157 | 67.0157 | 67.0157 | 67.0157 | 67.0157 | 67.0157 | 67.0157 | 67.0157
95% | 17.5347 | 38.3401 | 53.2227 | 57.0916 | 53.9511 | 54.4655 | 55.3511 | 57.3659 | 58.7146 | 60.4232 | 61.3101 | 62.0903 | 60.6527 | 62.3375 | 64.9862 | 62.9762 | 62.9762 | 62.9762 | 62.9762 | 62.9762 | 62.9762 | 62.9762 | 62.9762 | 62.9762 | 62.9762 | 62.9762 | 62.9762 | 62.9762 | 62.9762 | 62.9762 | 62.9762 | 95% | 17.5347 | 41.0476 | 55.7425 | 59.7624 | 56.5844 | 56.9794 | 57.8458 | 59.8921 | 61.0094 | 63.1377 | 69.6073 | 64.2738 | 63.2306 | 64.6388 | 67.7186 | 65.6339 | 65.6339 | 65.6339 | 65.6339 | 65.6339 | 65.6339 | 65.6339 | 65.6339 | 65.6339 | 65.6339 | 65.6339 | 65.6339 | 65.6339 | 65.6339 | 65.6339 | 65.6339
90% | 78.7576 | 36.3222 | 50.4215 | 54.0868 | 51.1116 | 51.5988 | 52.4379 | 54.3467 | 55.6244 | 57.2431 | 58.0833 | 58.8224 | 57.4605 | 59.0566 | 61.5659 | 59.6617 | 59.6617 | 59.6617 | 59.6617 | 59.6617 | 59.6617 | 59.6617 | 59.6617 | 59.6617 | 59.6617 | 59.6617 | 59.6617 | 59.6617 | 59.6617 | 59.6617 | 59.6617 | 90% | 78.7576 | 38.8872 | 52.8086 | 56.617 | 53.6063 | 53.9804 | 54.8013 | 56.7399 | 57.7984 | 59.8147 | 65.9438 | 60.891 | 59.9026 | 61.2368 | 64.1545 | 62.1795 | 62.1795 | 62.1795 | 62.1795 | 62.1795 | 62.1795 | 62.1795 | 62.1795 | 62.1795 | 62.1795 | 62.1795 | 62.1795 | 62.1795 | 62.1795 | 62.1795 | 62.1795
85% | 236.8672 | 34.3043 | 47.6203 | 51.082 | 48.272 | 48.7322 | 49.5246 | 51.3274 | 52.5342 | 54.0629 | 54.8564 | 55.5545 | 54.2682 | 55.7757 | 58.1456 | 56.3472 | 56.3472 | 56.3472 | 56.3472 | 56.3472 | 56.3472 | 56.3472 | 56.3472 | 56.3472 | 56.3472 | 56.3472 | 56.3472 | 56.3472 | 56.3472 | 56.3472 | 56.3472 | 85% | 236.8672 | 36.7268 | 49.8748 | 53.4716 | 50.6282 | 50.9815 | 51.7567 | 53.5877 | 54.5873 | 56.4917 | 62.2803 | 57.5081 | 56.5747 | 57.8347 | 60.5903 | 58.7251 | 58.7251 | 58.7251 | 58.7251 | 58.7251 | 58.7251 | 58.7251 | 58.7251 | 58.7251 | 58.7251 | 58.7251 | 58.7251 | 58.7251 | 58.7251 | 58.7251 | 58.7251
80% | 497.5104 | 32.2864 | 44.8191 | 48.0771 | 45.4325 | 45.8656 | 46.6114 | 48.3081 | 49.4439 | 50.8827 | 51.6296 | 52.2866 | 51.076 | 52.4948 | 54.7252 | 53.0326 | 53.0326 | 53.0326 | 53.0326 | 53.0326 | 53.0326 | 53.0326 | 53.0326 | 53.0326 | 53.0326 | 53.0326 | 53.0326 | 53.0326 | 53.0326 | 53.0326 | 53.0326 | 80% | 497.5104 | 34.5664 | 46.941 | 50.3262 | 47.65 | 47.9826 | 48.7122 | 50.4355 | 51.3763 | 53.1686 | 58.6167 | 54.1253 | 53.2468 | 54.4327 | 57.0262 | 55.2707 | 55.2707 | 55.2707 | 55.2707 | 55.2707 | 55.2707 | 55.2707 | 55.2707 | 55.2707 | 55.2707 | 55.2707 | 55.2707 | 55.2707 | 55.2707 | 55.2707 | 55.2707
75% | 803.6248 | 30.2685 | 42.0179 | 45.0723 | 42.593 | 42.999 | 43.6982 | 45.2889 | 46.3537 | 47.7026 | 48.4027 | 49.0187 | 47.8837 | 49.2138 | 51.3049 | 49.7181 | 49.7181 | 49.7181 | 49.7181 | 49.7181 | 49.7181 | 49.7181 | 49.7181 | 49.7181 | 49.7181 | 49.7181 | 49.7181 | 49.7181 | 49.7181 | 49.7181 | 49.7181 | 75% | 803.6248 | 32.406 | 44.0072 | 47.1809 | 44.6719 | 44.9837 | 45.6677 | 47.2832 | 48.1653 | 49.8456 | 54.9532 | 50.7425 | 49.9189 | 51.0306 | 53.4621 | 51.8163 | 51.8163 | 51.8163 | 51.8163 | 51.8163 | 51.8163 | 51.8163 | 51.8163 | 51.8163 | 51.8163 | 51.8163 | 51.8163 | 51.8163 | 51.8163 | 51.8163 | 51.8163
70% | 1155.2107 | 28.2506 | 39.2167 | 42.0675 | 39.7534 | 40.1324 | 40.785 | 42.2696 | 43.2634 | 44.5224 | 45.1759 | 45.7508 | 44.6915 | 45.9329 | 47.8846 | 46.4035 | 46.4035 | 46.4035 | 46.4035 | 46.4035 | 46.4035 | 46.4035 | 46.4035 | 46.4035 | 46.4035 | 46.4035 | 46.4035 | 46.4035 | 46.4035 | 46.4035 | 46.4035 | 70% | 1155.2107 | 30.2456 | 41.0734 | 44.0355 | 41.6938 | 41.9848 | 42.6232 | 44.131 | 44.9543 | 46.5225 | 51.2896 | 47.3596 | 46.5909 | 47.6286 | 49.8979 | 48.3618 | 48.3618 | 48.3618 | 48.3618 | 48.3618 | 48.3618 | 48.3618 | 48.3618 | 48.3618 | 48.3618 | 48.3618 | 48.3618 | 48.3618 | 48.3618 | 48.3618 | 48.3618
65% | 1553.1596 | 26.2327 | 36.4155 | 39.0627 | 36.9139 | 37.2658 | 37.8718 | 39.2504 | 40.1732 | 41.3422 | 41.949 | 42.4828 | 41.4992 | 42.652 | 44.4643 | 43.089 | 43.089 | 43.089 | 43.089 | 43.089 | 43.089 | 43.089 | 43.089 | 43.089 | 43.089 | 43.089 | 43.089 | 43.089 | 43.089 | 43.089 | 43.089 | 65% | 1553.1596 | 28.0852 | 38.1396 | 40.8901 | 38.7157 | 38.9859 | 39.5787 | 40.9788 | 41.7433 | 43.1995 | 47.6261 | 43.9768 | 43.263 | 44.2266 | 46.3338 | 44.9074 | 44.9074 | 44.9074 | 44.9074 | 44.9074 | 44.9074 | 44.9074 | 44.9074 | 44.9074 | 44.9074 | 44.9074 | 44.9074 | 44.9074 | 44.9074 | 44.9074 | 44.9074
60% | 2026.2996 | 24.2148 | 33.6143 | 36.0579 | 34.0744 | 34.3992 | 34.9586 | 36.2311 | 37.0829 | 38.162 | 38.7222 | 39.2149 | 38.307 | 39.3711 | 41.0439 | 39.7745 | 39.7745 | 39.7745 | 39.7745 | 39.7745 | 39.7745 | 39.7745 | 39.7745 | 39.7745 | 39.7745 | 39.7745 | 39.7745 | 39.7745 | 39.7745 | 39.7745 | 39.7745 | 60% | 2026.2996 | 25.9248 | 35.2058 | 37.7447 | 35.7375 | 35.987 | 36.5342 | 37.8266 | 38.5322 | 39.8765 | 43.9625 | 40.594 | 39.9351 | 40.8245 | 42.7696 | 41.453 | 41.453 | 41.453 | 41.453 | 41.453 | 41.453 | 41.453 | 41.453 | 41.453 | 41.453 | 41.453 | 41.453 | 41.453 | 41.453 | 41.453 | 41.453
55% | 2598.4068 | 22.1969 | 30.8131 | 33.053 | 31.2348 | 31.5326 | 32.0454 | 33.2119 | 33.9927 | 34.9819 | 35.4953 | 35.947 | 35.1147 | 36.0902 | 37.6236 | 36.4599 | 36.4599 | 36.4599 | 36.4599 | 36.4599 | 36.4599 | 36.4599 | 36.4599 | 36.4599 | 36.4599 | 36.4599 | 36.4599 | 36.4599 | 36.4599 | 36.4599 | 36.4599 | 55% | 2598.4068 | 23.7644 | 32.272 | 34.5993 | 32.7594 | 32.988 | 33.4897 | 34.6744 | 35.3212 | 36.5534 | 40.299 | 37.2111 | 36.6072 | 37.4225 | 39.2055 | 37.9986 | 37.9986 | 37.9986 | 37.9986 | 37.9986 | 37.9986 | 37.9986 | 37.9986 | 37.9986 | 37.9986 | 37.9986 | 37.9986 | 37.9986 | 37.9986 | 37.9986 | 37.9986
50% | 3233.5201 | 20.179 | 28.0119 | 30.0482 | 28.3953 | 28.666 | 29.1321 | 30.1926 | 30.9024 | 31.8017 | 32.2685 | 32.6791 | 31.9225 | 32.8092 | 34.2033 | 33.1454 | 33.1454 | 33.1454 | 33.1454 | 33.1454 | 33.1454 | 33.1454 | 33.1454 | 33.1454 | 33.1454 | 33.1454 | 33.1454 | 33.1454 | 33.1454 | 33.1454 | 33.1454 | 50% | 3233.5201 | 21.604 | 29.3381 | 31.4539 | 29.7813 | 29.9891 | 30.4451 | 31.5222 | 32.1102 | 33.2304 | 36.6354 | 33.8283 | 33.2792 | 34.0204 | 35.6414 | 34.5442 | 34.5442 | 34.5442 | 34.5442 | 34.5442 | 34.5442 | 34.5442 | 34.5442 | 34.5442 | 34.5442 | 34.5442 | 34.5442 | 34.5442 | 34.5442 | 34.5442 | 34.5442
45% | 3775.313 | 18.1611 | 25.2107 | 27.0434 | 25.5558 | 25.7994 | 26.2189 | 27.1733 | 27.8122 | 28.6215 | 29.0416 | 29.4112 | 28.7302 | 29.5283 | 30.783 | 29.8309 | 29.8309 | 29.8309 | 29.8309 | 29.8309 | 29.8309 | 29.8309 | 29.8309 | 29.8309 | 29.8309 | 29.8309 | 29.8309 | 29.8309 | 29.8309 | 29.8309 | 29.8309 | 45% | 3775.313 | 19.4436 | 26.4043 | 28.3085 | 26.8031 | 26.9902 | 27.4006 | 28.3699 | 28.8992 | 29.9073 | 32.9719 | 30.4455 | 29.9513 | 30.6184 | 32.0772 | 31.0898 | 31.0898 | 31.0898 | 31.0898 | 31.0898 | 31.0898 | 31.0898 | 31.0898 | 31.0898 | 31.0898 | 31.0898 | 31.0898 | 31.0898 | 31.0898 | 31.0898 | 31.0898
40% | 4072.8088 | 16.1432 | 22.4095 | 24.0386 | 22.7162 | 22.9328 | 23.3057 | 24.1541 | 24.722 | 25.4414 | 25.8148 | 26.1433 | 25.538 | 26.2474 | 27.3626 | 26.5163 | 26.5163 | 26.5163 | 26.5163 | 26.5163 | 26.5163 | 26.5163 | 26.5163 | 26.5163 | 26.5163 | 26.5163 | 26.5163 | 26.5163 | 26.5163 | 26.5163 | 26.5163 | 40% | 4072.8088 | 17.2832 | 23.4705 | 25.1631 | 23.825 | 23.9913 | 24.3561 | 25.2177 | 25.6882 | 26.5843 | 29.3084 | 27.0627 | 26.6234 | 27.2163 | 28.5131 | 27.6353 | 27.6353 | 27.6353 | 27.6353 | 27.6353 | 27.6353 | 27.6353 | 27.6353 | 27.6353 | 27.6353 | 27.6353 | 27.6353 | 27.6353 | 27.6353 | 27.6353 | 27.6353
35% | 4198.821 | 14.1253 | 19.6083 | 21.0337 | 19.8767 | 20.0662 | 20.3925 | 21.1348 | 21.6317 | 22.2612 | 22.5879 | 22.8754 | 22.3457 | 22.9665 | 23.9423 | 23.2018 | 23.2018 | 23.2018 | 23.2018 | 23.2018 | 23.2018 | 23.2018 | 23.2018 | 23.2018 | 23.2018 | 23.2018 | 23.2018 | 23.2018 | 23.2018 | 23.2018 | 23.2018 | 35% | 4198.821 | 15.1228 | 20.5367 | 22.0177 | 20.8469 | 20.9924 | 21.3116 | 22.0655 | 22.4771 | 23.2613 | 25.6448 | 23.6798 | 23.2955 | 23.8143 | 24.949 | 24.1809 | 24.1809 | 24.1809 | 24.1809 | 24.1809 | 24.1809 | 24.1809 | 24.1809 | 24.1809 | 24.1809 | 24.1809 | 24.1809 | 24.1809 | 24.1809 | 24.1809 | 24.1809
30% | 4271.3374 | 12.1074 | 16.8072 | 18.0289 | 17.0372 | 17.1996 | 17.4793 | 18.1156 | 18.5415 | 19.081 | 19.3611 | 19.6075 | 19.1535 | 19.6855 | 20.522 | 19.8872 | 19.8872 | 19.8872 | 19.8872 | 19.8872 | 19.8872 | 19.8872 | 19.8872 | 19.8872 | 19.8872 | 19.8872 | 19.8872 | 19.8872 | 19.8872 | 19.8872 | 19.8872 | 30% | 4271.3374 | 12.9624 | 17.6029 | 18.8723 | 17.8688 | 17.9935 | 18.2671 | 18.9133 | 19.2661 | 19.9382 | 21.9813 | 20.297 | 19.9675 | 20.4123 | 21.3848 | 20.7265 | 20.7265 | 20.7265 | 20.7265 | 20.7265 | 20.7265 | 20.7265 | 20.7265 | 20.7265 | 20.7265 | 20.7265 | 20.7265 | 20.7265 | 20.7265 | 20.7265 | 20.7265
25% | 4321.8611 | 10.0895 | 14.006 | 15.0241 | 14.1977 | 14.333 | 14.5661 | 15.0963 | 15.4512 | 15.9009 | 16.1342 | 16.3396 | 15.9612 | 16.4046 | 17.1016 | 16.5727 | 16.5727 | 16.5727 | 16.5727 | 16.5727 | 16.5727 | 16.5727 | 16.5727 | 16.5727 | 16.5727 | 16.5727 | 16.5727 | 16.5727 | 16.5727 | 16.5727 | 16.5727 | 25% | 4321.8611 | 10.802 | 14.6691 | 15.727 | 14.8906 | 14.9946 | 15.2226 | 15.7611 | 16.0551 | 16.6152 | 18.3177 | 16.9142 | 16.6396 | 17.0102 | 17.8207 | 17.2721 | 17.2721 | 17.2721 | 17.2721 | 17.2721 | 17.2721 | 17.2721 | 17.2721 | 17.2721 | 17.2721 | 17.2721 | 17.2721 | 17.2721 | 17.2721 | 17.2721 | 17.2721
20% | 4353.067 | 8.0716 | 11.2048 | 12.0193 | 11.3581 | 11.4664 | 11.6529 | 12.077 | 12.361 | 12.7207 | 12.9074 | 13.0716 | 12.769 | 13.1237 | 13.6813 | 13.2582 | 13.2582 | 13.2582 | 13.2582 | 13.2582 | 13.2582 | 13.2582 | 13.2582 | 13.2582 | 13.2582 | 13.2582 | 13.2582 | 13.2582 | 13.2582 | 13.2582 | 13.2582 | 20% | 4353.067 | 8.6416 | 11.7353 | 12.5816 | 11.9125 | 11.9957 | 12.1781 | 12.6089 | 12.8441 | 13.2922 | 14.6542 | 13.5313 | 13.3117 | 13.6082 | 14.2565 | 13.8177 | 13.8177 | 13.8177 | 13.8177 | 13.8177 | 13.8177 | 13.8177 | 13.8177 | 13.8177 | 13.8177 | 13.8177 | 13.8177 | 13.8177 | 13.8177 | 13.8177 | 13.8177
15% | 4369.4129 | 6.0537 | 8.4036 | 9.0145 | 8.5186 | 8.5998 | 8.7396 | 9.0578 | 9.2707 | 9.5405 | 9.6805 | 9.8037 | 9.5767 | 9.8428 | 10.261 | 9.9436 | 9.9436 | 9.9436 | 9.9436 | 9.9436 | 9.9436 | 9.9436 | 9.9436 | 9.9436 | 9.9436 | 9.9436 | 9.9436 | 9.9436 | 9.9436 | 9.9436 | 9.9436 | 15% | 4369.4129 | 6.4812 | 8.8014 | 9.4362 | 8.9344 | 8.9967 | 9.1335 | 9.4566 | 9.6331 | 9.9691 | 10.9906 | 10.1485 | 9.9838 | 10.2061 | 10.6924 | 10.3633 | 10.3633 | 10.3633 | 10.3633 | 10.3633 | 10.3633 | 10.3633 | 10.3633 | 10.3633 | 10.3633 | 10.3633 | 10.3633 | 10.3633 | 10.3633 | 10.3633 | 10.3633
10% | 4378.6261 | 4.0358 | 5.6024 | 6.0096 | 5.6791 | 5.7332 | 5.8264 | 6.0385 | 6.1805 | 6.3603 | 6.4537 | 6.5358 | 6.3845 | 6.5618 | 6.8407 | 6.6291 | 6.6291 | 6.6291 | 6.6291 | 6.6291 | 6.6291 | 6.6291 | 6.6291 | 6.6291 | 6.6291 | 6.6291 | 6.6291 | 6.6291 | 6.6291 | 6.6291 | 6.6291 | 10% | 4378.6261 | 4.3208 | 5.8676 | 6.2908 | 5.9563 | 5.9978 | 6.089 | 6.3044 | 6.422 | 6.6461 | 7.3271 | 6.7657 | 6.6558 | 6.8041 | 7.1283 | 6.9088 | 6.9088 | 6.9088 | 6.9088 | 6.9088 | 6.9088 | 6.9088 | 6.9088 | 6.9088 | 6.9088 | 6.9088 | 6.9088 | 6.9088 | 6.9088 | 6.9088 | 6.9088
5% | 4391.7028 | 2.0179 | 2.8012 | 3.0048 | 2.8395 | 2.8666 | 2.9132 | 3.0193 | 3.0902 | 3.1802 | 3.2268 | 3.2679 | 3.1922 | 3.2809 | 3.4203 | 3.3145 | 3.3145 | 3.3145 | 3.3145 | 3.3145 | 3.3145 | 3.3145 | 3.3145 | 3.3145 | 3.3145 | 3.3145 | 3.3145 | 3.3145 | 3.3145 | 3.3145 | 3.3145 | 5% | 4391.7028 | 2.1604 | 2.9338 | 3.1454 | 2.9781 | 2.9989 | 3.0445 | 3.1522 | 3.211 | 3.323 | 3.6635 | 3.3828 | 3.3279 | 3.402 | 3.5641 | 3.4544 | 3.4544 | 3.4544 | 3.4544 | 3.4544 | 3.4544 | 3.4544 | 3.4544 | 3.4544 | 3.4544 | 3.4544 | 3.4544 | 3.4544 | 3.4544 | 3.4544 | 3.4544
9.992e-14% | 4391.7028 | 4.0326e-14 | 5.5979e-14 | 6.0048e-14 | 5.6745e-14 | 5.7286e-14 | 5.8218e-14 | 6.0337e-14 | 6.1755e-14 | 6.3553e-14 | 6.4485e-14 | 6.5306e-14 | 6.3794e-14 | 6.5566e-14 | 6.8352e-14 | 6.6238e-14 | 6.6238e-14 | 6.6238e-14 | 6.6238e-14 | 6.6238e-14 | 6.6238e-14 | 6.6238e-14 | 6.6238e-14 | 6.6238e-14 | 6.6238e-14 | 6.6238e-14 | 6.6238e-14 | 6.6238e-14 | 6.6238e-14 | 6.6238e-14 | 6.6238e-14 | 9.992e-14% | 4391.7028 | 4.3173e-14 | 5.8629e-14 | 6.2858e-14 | 5.9515e-14 | 5.993e-14 | 6.0842e-14 | 6.2994e-14 | 6.4169e-14 | 6.6408e-14 | 7.3212e-14 | 6.7603e-14 | 6.6505e-14 | 6.7986e-14 | 7.1226e-14 | 6.9033e-14 | 6.9033e-14 | 6.9033e-14 | 6.9033e-14 | 6.9033e-14 | 6.9033e-14 | 6.9033e-14 | 6.9033e-14 | 6.9033e-14 | 6.9033e-14 | 6.9033e-14 | 6.9033e-14 | 6.9033e-14 | 6.9033e-14 | 6.9033e-14 | 6.9033e-14
Summer Season | [31 empty] | Summer Season
P50 | [31 empty] | P10
% of MD | Summer - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Summer - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 45.8759 | 60.9589 | 65.0674 | 60.9499 | 60.9485 | 61.4184 | 61.9338 | 62.9909 | 63.7504 | 64.1633 | 64.6157 | 65.029 | 65.7743 | 66.6989 | 66.6364 | 66.6364 | 66.6364 | 66.6364 | 66.6364 | 66.6364 | 66.6364 | 66.6364 | 66.6364 | 66.6364 | 66.6364 | 66.6364 | 66.6364 | 66.6364 | 66.6364 | 66.6364 | 100% | 0 | 51.1554 | 66.2686 | 70.2261 | 65.9907 | 66.0105 | 66.4179 | 67.4905 | 68.2097 | 68.9132 | 69.7356 | 70.4985 | 71.2386 | 71.3243 | 72.1878 | 71.5357 | 71.5357 | 71.5357 | 71.5357 | 71.5357 | 71.5357 | 71.5357 | 71.5357 | 71.5357 | 71.5357 | 71.5357 | 71.5357 | 71.5357 | 71.5357 | 71.5357 | 71.5357
99% | 0 | 45.4171 | 60.3493 | 64.4168 | 60.3404 | 60.339 | 60.8042 | 61.3145 | 62.361 | 63.1129 | 63.5217 | 63.9695 | 64.3787 | 65.1166 | 66.0319 | 65.97 | 65.97 | 65.97 | 65.97 | 65.97 | 65.97 | 65.97 | 65.97 | 65.97 | 65.97 | 65.97 | 65.97 | 65.97 | 65.97 | 65.97 | 65.97 | 99% | 1.5127 | 50.6438 | 65.6059 | 69.5238 | 65.3308 | 65.3504 | 65.7537 | 66.8156 | 67.5276 | 68.224 | 69.0383 | 69.7935 | 70.5262 | 70.611 | 71.4659 | 70.8203 | 70.8203 | 70.8203 | 70.8203 | 70.8203 | 70.8203 | 70.8203 | 70.8203 | 70.8203 | 70.8203 | 70.8203 | 70.8203 | 70.8203 | 70.8203 | 70.8203 | 70.8203
98% | 0 | 44.9584 | 59.7397 | 63.7661 | 59.7309 | 59.7295 | 60.19 | 60.6951 | 61.7311 | 62.4754 | 62.8801 | 63.3234 | 63.7284 | 64.4588 | 65.3649 | 65.3036 | 65.3036 | 65.3036 | 65.3036 | 65.3036 | 65.3036 | 65.3036 | 65.3036 | 65.3036 | 65.3036 | 65.3036 | 65.3036 | 65.3036 | 65.3036 | 65.3036 | 65.3036 | 98% | 2.269 | 50.1322 | 64.9433 | 68.8216 | 64.6709 | 64.6903 | 65.0896 | 66.1407 | 66.8455 | 67.5349 | 68.3409 | 69.0885 | 69.8138 | 69.8978 | 70.744 | 70.1049 | 70.1049 | 70.1049 | 70.1049 | 70.1049 | 70.1049 | 70.1049 | 70.1049 | 70.1049 | 70.1049 | 70.1049 | 70.1049 | 70.1049 | 70.1049 | 70.1049 | 70.1049
97% | 0.37816 | 44.4996 | 59.1301 | 63.1154 | 59.1214 | 59.12 | 59.5758 | 60.0758 | 61.1012 | 61.8379 | 62.2384 | 62.6772 | 63.0781 | 63.8011 | 64.6979 | 64.6373 | 64.6373 | 64.6373 | 64.6373 | 64.6373 | 64.6373 | 64.6373 | 64.6373 | 64.6373 | 64.6373 | 64.6373 | 64.6373 | 64.6373 | 64.6373 | 64.6373 | 64.6373 | 97% | 3.7816 | 49.6207 | 64.2806 | 68.1193 | 64.011 | 64.0302 | 64.4254 | 65.4658 | 66.1634 | 66.8458 | 67.6436 | 68.3836 | 69.1014 | 69.1846 | 70.0222 | 69.3896 | 69.3896 | 69.3896 | 69.3896 | 69.3896 | 69.3896 | 69.3896 | 69.3896 | 69.3896 | 69.3896 | 69.3896 | 69.3896 | 69.3896 | 69.3896 | 69.3896 | 69.3896
95% | 2.269 | 43.5821 | 57.911 | 61.8141 | 57.9024 | 57.901 | 58.3474 | 58.8371 | 59.8414 | 60.5629 | 60.9552 | 61.3849 | 61.7776 | 62.4856 | 63.3639 | 63.3046 | 63.3046 | 63.3046 | 63.3046 | 63.3046 | 63.3046 | 63.3046 | 63.3046 | 63.3046 | 63.3046 | 63.3046 | 63.3046 | 63.3046 | 63.3046 | 63.3046 | 63.3046 | 95% | 6.0506 | 48.5976 | 62.9552 | 66.7148 | 62.6912 | 62.71 | 63.097 | 64.116 | 64.7992 | 65.4675 | 66.2488 | 66.9736 | 67.6766 | 67.7581 | 68.5784 | 67.9589 | 67.9589 | 67.9589 | 67.9589 | 67.9589 | 67.9589 | 67.9589 | 67.9589 | 67.9589 | 67.9589 | 67.9589 | 67.9589 | 67.9589 | 67.9589 | 67.9589 | 67.9589
90% | 5.6725 | 41.2883 | 54.863 | 58.5607 | 54.8549 | 54.8536 | 55.2765 | 55.7404 | 56.6918 | 57.3754 | 57.747 | 58.1541 | 58.5261 | 59.1969 | 60.029 | 59.9727 | 59.9727 | 59.9727 | 59.9727 | 59.9727 | 59.9727 | 59.9727 | 59.9727 | 59.9727 | 59.9727 | 59.9727 | 59.9727 | 59.9727 | 59.9727 | 59.9727 | 59.9727 | 90% | 16.2611 | 46.0398 | 59.6418 | 63.2035 | 59.3917 | 59.4094 | 59.7761 | 60.7415 | 61.3887 | 62.0218 | 62.7621 | 63.4487 | 64.1147 | 64.1919 | 64.969 | 64.3821 | 64.3821 | 64.3821 | 64.3821 | 64.3821 | 64.3821 | 64.3821 | 64.3821 | 64.3821 | 64.3821 | 64.3821 | 64.3821 | 64.3821 | 64.3821 | 64.3821 | 64.3821
85% | 15.8829 | 38.9945 | 51.8151 | 55.3073 | 51.8074 | 51.8062 | 52.2056 | 52.6437 | 53.5423 | 54.1879 | 54.5388 | 54.9233 | 55.2747 | 55.9082 | 56.694 | 56.6409 | 56.6409 | 56.6409 | 56.6409 | 56.6409 | 56.6409 | 56.6409 | 56.6409 | 56.6409 | 56.6409 | 56.6409 | 56.6409 | 56.6409 | 56.6409 | 56.6409 | 56.6409 | 85% | 26.4715 | 43.482 | 56.3283 | 59.6922 | 56.0921 | 56.1089 | 56.4552 | 57.367 | 57.9783 | 58.5762 | 59.2753 | 59.9237 | 60.5528 | 60.6256 | 61.3596 | 60.8053 | 60.8053 | 60.8053 | 60.8053 | 60.8053 | 60.8053 | 60.8053 | 60.8053 | 60.8053 | 60.8053 | 60.8053 | 60.8053 | 60.8053 | 60.8053 | 60.8053 | 60.8053
80% | 31.0095 | 36.7007 | 48.7671 | 52.0539 | 48.7599 | 48.7588 | 49.1347 | 49.547 | 50.3928 | 51.0003 | 51.3307 | 51.6925 | 52.0232 | 52.6194 | 53.3591 | 53.3091 | 53.3091 | 53.3091 | 53.3091 | 53.3091 | 53.3091 | 53.3091 | 53.3091 | 53.3091 | 53.3091 | 53.3091 | 53.3091 | 53.3091 | 53.3091 | 53.3091 | 53.3091 | 80% | 34.0348 | 40.9243 | 53.0149 | 56.1809 | 52.7926 | 52.8084 | 53.1343 | 53.9924 | 54.5678 | 55.1305 | 55.7885 | 56.3988 | 56.9908 | 57.0594 | 57.7502 | 57.2285 | 57.2285 | 57.2285 | 57.2285 | 57.2285 | 57.2285 | 57.2285 | 57.2285 | 57.2285 | 57.2285 | 57.2285 | 57.2285 | 57.2285 | 57.2285 | 57.2285 | 57.2285
75% | 72.9857 | 34.4069 | 45.7192 | 48.8006 | 45.7124 | 45.7113 | 46.0638 | 46.4504 | 47.2432 | 47.8128 | 48.1225 | 48.4618 | 48.7718 | 49.3307 | 50.0241 | 49.9773 | 49.9773 | 49.9773 | 49.9773 | 49.9773 | 49.9773 | 49.9773 | 49.9773 | 49.9773 | 49.9773 | 49.9773 | 49.9773 | 49.9773 | 49.9773 | 49.9773 | 49.9773 | 75% | 48.405 | 38.3665 | 49.7015 | 52.6696 | 49.493 | 49.5079 | 49.8134 | 50.6179 | 51.1573 | 51.6849 | 52.3017 | 52.8739 | 53.4289 | 53.4932 | 54.1408 | 53.6517 | 53.6517 | 53.6517 | 53.6517 | 53.6517 | 53.6517 | 53.6517 | 53.6517 | 53.6517 | 53.6517 | 53.6517 | 53.6517 | 53.6517 | 53.6517 | 53.6517 | 53.6517
70% | 150.5094 | 32.1131 | 42.6712 | 45.5472 | 42.6649 | 42.6639 | 42.9929 | 43.3537 | 44.0937 | 44.6253 | 44.9143 | 45.231 | 45.5203 | 46.042 | 46.6892 | 46.6455 | 46.6455 | 46.6455 | 46.6455 | 46.6455 | 46.6455 | 46.6455 | 46.6455 | 46.6455 | 46.6455 | 46.6455 | 46.6455 | 46.6455 | 46.6455 | 46.6455 | 46.6455 | 70% | 76.3892 | 35.8087 | 46.388 | 49.1583 | 46.1935 | 46.2073 | 46.4925 | 47.2434 | 47.7468 | 48.2392 | 48.8149 | 49.349 | 49.867 | 49.927 | 50.5315 | 50.075 | 50.075 | 50.075 | 50.075 | 50.075 | 50.075 | 50.075 | 50.075 | 50.075 | 50.075 | 50.075 | 50.075 | 50.075 | 50.075 | 50.075 | 50.075
65% | 359.6342 | 29.8193 | 39.6233 | 42.2938 | 39.6174 | 39.6165 | 39.9219 | 40.257 | 40.9441 | 41.4378 | 41.7062 | 42.0002 | 42.2689 | 42.7533 | 43.3543 | 43.3136 | 43.3136 | 43.3136 | 43.3136 | 43.3136 | 43.3136 | 43.3136 | 43.3136 | 43.3136 | 43.3136 | 43.3136 | 43.3136 | 43.3136 | 43.3136 | 43.3136 | 43.3136 | 65% | 114.2056 | 33.251 | 43.0746 | 45.647 | 42.894 | 42.9068 | 43.1716 | 43.8689 | 44.3363 | 44.7936 | 45.3282 | 45.824 | 46.3051 | 46.3608 | 46.9221 | 46.4982 | 46.4982 | 46.4982 | 46.4982 | 46.4982 | 46.4982 | 46.4982 | 46.4982 | 46.4982 | 46.4982 | 46.4982 | 46.4982 | 46.4982 | 46.4982 | 46.4982 | 46.4982
60% | 689.7717 | 27.5255 | 36.5753 | 39.0405 | 36.5699 | 36.5691 | 36.851 | 37.1603 | 37.7946 | 38.2503 | 38.498 | 38.7694 | 39.0174 | 39.4646 | 40.0193 | 39.9818 | 39.9818 | 39.9818 | 39.9818 | 39.9818 | 39.9818 | 39.9818 | 39.9818 | 39.9818 | 39.9818 | 39.9818 | 39.9818 | 39.9818 | 39.9818 | 39.9818 | 39.9818 | 60% | 178.1154 | 30.6932 | 39.7612 | 42.1357 | 39.5944 | 39.6063 | 39.8508 | 40.4943 | 40.9258 | 41.3479 | 41.8414 | 42.2991 | 42.7431 | 42.7946 | 43.3127 | 42.9214 | 42.9214 | 42.9214 | 42.9214 | 42.9214 | 42.9214 | 42.9214 | 42.9214 | 42.9214 | 42.9214 | 42.9214 | 42.9214 | 42.9214 | 42.9214 | 42.9214 | 42.9214
55% | 1095.5419 | 25.2317 | 33.5274 | 35.7871 | 33.5224 | 33.5217 | 33.7801 | 34.0636 | 34.645 | 35.0627 | 35.2898 | 35.5386 | 35.766 | 36.1759 | 36.6844 | 36.65 | 36.65 | 36.65 | 36.65 | 36.65 | 36.65 | 36.65 | 36.65 | 36.65 | 36.65 | 36.65 | 36.65 | 36.65 | 36.65 | 36.65 | 36.65 | 55% | 311.6074 | 28.1354 | 36.4477 | 38.6243 | 36.2949 | 36.3058 | 36.5299 | 37.1198 | 37.5153 | 37.9022 | 38.3546 | 38.7742 | 39.1812 | 39.2284 | 39.7033 | 39.3446 | 39.3446 | 39.3446 | 39.3446 | 39.3446 | 39.3446 | 39.3446 | 39.3446 | 39.3446 | 39.3446 | 39.3446 | 39.3446 | 39.3446 | 39.3446 | 39.3446 | 39.3446
50% | 1666.1918 | 22.9379 | 30.4794 | 32.5337 | 30.4749 | 30.4742 | 30.7092 | 30.9669 | 31.4955 | 31.8752 | 32.0817 | 32.3078 | 32.5145 | 32.8872 | 33.3494 | 33.3182 | 33.3182 | 33.3182 | 33.3182 | 33.3182 | 33.3182 | 33.3182 | 33.3182 | 33.3182 | 33.3182 | 33.3182 | 33.3182 | 33.3182 | 33.3182 | 33.3182 | 33.3182 | 50% | 636.0723 | 25.5777 | 33.1343 | 35.113 | 32.9954 | 33.0052 | 33.209 | 33.7453 | 34.1049 | 34.4566 | 34.8678 | 35.2493 | 35.6193 | 35.6621 | 36.0939 | 35.7678 | 35.7678 | 35.7678 | 35.7678 | 35.7678 | 35.7678 | 35.7678 | 35.7678 | 35.7678 | 35.7678 | 35.7678 | 35.7678 | 35.7678 | 35.7678 | 35.7678 | 35.7678
45% | 2506.0947 | 20.6442 | 27.4315 | 29.2803 | 27.4274 | 27.4268 | 27.6383 | 27.8702 | 28.3459 | 28.6877 | 28.8735 | 29.0771 | 29.2631 | 29.5984 | 30.0145 | 29.9864 | 29.9864 | 29.9864 | 29.9864 | 29.9864 | 29.9864 | 29.9864 | 29.9864 | 29.9864 | 29.9864 | 29.9864 | 29.9864 | 29.9864 | 29.9864 | 29.9864 | 29.9864 | 45% | 1179.4944 | 23.0199 | 29.8209 | 31.6017 | 29.6958 | 29.7047 | 29.8881 | 30.3707 | 30.6944 | 31.0109 | 31.381 | 31.7243 | 32.0573 | 32.0959 | 32.4845 | 32.191 | 32.191 | 32.191 | 32.191 | 32.191 | 32.191 | 32.191 | 32.191 | 32.191 | 32.191 | 32.191 | 32.191 | 32.191 | 32.191 | 32.191 | 32.191
40% | 3164.4787 | 18.3504 | 24.3836 | 26.027 | 24.3799 | 24.3794 | 24.5673 | 24.7735 | 25.1964 | 25.5002 | 25.6653 | 25.8463 | 26.0116 | 26.3097 | 26.6795 | 26.6546 | 26.6546 | 26.6546 | 26.6546 | 26.6546 | 26.6546 | 26.6546 | 26.6546 | 26.6546 | 26.6546 | 26.6546 | 26.6546 | 26.6546 | 26.6546 | 26.6546 | 26.6546 | 40% | 1808.3816 | 20.4621 | 26.5075 | 28.0904 | 26.3963 | 26.4042 | 26.5672 | 26.9962 | 27.2839 | 27.5653 | 27.8942 | 28.1994 | 28.4954 | 28.5297 | 28.8751 | 28.6143 | 28.6143 | 28.6143 | 28.6143 | 28.6143 | 28.6143 | 28.6143 | 28.6143 | 28.6143 | 28.6143 | 28.6143 | 28.6143 | 28.6143 | 28.6143 | 28.6143 | 28.6143
35% | 3551.3408 | 16.0566 | 21.3356 | 22.7736 | 21.3325 | 21.332 | 21.4964 | 21.6768 | 22.0468 | 22.3126 | 22.4572 | 22.6155 | 22.7602 | 23.021 | 23.3446 | 23.3227 | 23.3227 | 23.3227 | 23.3227 | 23.3227 | 23.3227 | 23.3227 | 23.3227 | 23.3227 | 23.3227 | 23.3227 | 23.3227 | 23.3227 | 23.3227 | 23.3227 | 23.3227 | 35% | 2779.1293 | 17.9044 | 23.194 | 24.5791 | 23.0968 | 23.1037 | 23.2463 | 23.6217 | 23.8734 | 24.1196 | 24.4075 | 24.6745 | 24.9335 | 24.9635 | 25.2657 | 25.0375 | 25.0375 | 25.0375 | 25.0375 | 25.0375 | 25.0375 | 25.0375 | 25.0375 | 25.0375 | 25.0375 | 25.0375 | 25.0375 | 25.0375 | 25.0375 | 25.0375 | 25.0375
30% | 3758.953 | 13.7628 | 18.2877 | 19.5202 | 18.285 | 18.2845 | 18.4255 | 18.5801 | 18.8973 | 19.1251 | 19.249 | 19.3847 | 19.5087 | 19.7323 | 20.0097 | 19.9909 | 19.9909 | 19.9909 | 19.9909 | 19.9909 | 19.9909 | 19.9909 | 19.9909 | 19.9909 | 19.9909 | 19.9909 | 19.9909 | 19.9909 | 19.9909 | 19.9909 | 19.9909 | 30% | 3814.165 | 15.3466 | 19.8806 | 21.0678 | 19.7972 | 19.8031 | 19.9254 | 20.2472 | 20.4629 | 20.6739 | 20.9207 | 21.1496 | 21.3716 | 21.3973 | 21.6563 | 21.4607 | 21.4607 | 21.4607 | 21.4607 | 21.4607 | 21.4607 | 21.4607 | 21.4607 | 21.4607 | 21.4607 | 21.4607 | 21.4607 | 21.4607 | 21.4607 | 21.4607 | 21.4607
25% | 3926.4798 | 11.469 | 15.2397 | 16.2669 | 15.2375 | 15.2371 | 15.3546 | 15.4835 | 15.7477 | 15.9376 | 16.0408 | 16.1539 | 16.2573 | 16.4436 | 16.6747 | 16.6591 | 16.6591 | 16.6591 | 16.6591 | 16.6591 | 16.6591 | 16.6591 | 16.6591 | 16.6591 | 16.6591 | 16.6591 | 16.6591 | 16.6591 | 16.6591 | 16.6591 | 16.6591 | 25% | 4166.9923 | 12.7888 | 16.5672 | 17.5565 | 16.4977 | 16.5026 | 16.6045 | 16.8726 | 17.0524 | 17.2283 | 17.4339 | 17.6246 | 17.8096 | 17.8311 | 18.0469 | 17.8839 | 17.8839 | 17.8839 | 17.8839 | 17.8839 | 17.8839 | 17.8839 | 17.8839 | 17.8839 | 17.8839 | 17.8839 | 17.8839 | 17.8839 | 17.8839 | 17.8839 | 17.8839
20% | 4050.5177 | 9.1752 | 12.1918 | 13.0135 | 12.19 | 12.1897 | 12.2837 | 12.3868 | 12.5982 | 12.7501 | 12.8327 | 12.9231 | 13.0058 | 13.1549 | 13.3398 | 13.3273 | 13.3273 | 13.3273 | 13.3273 | 13.3273 | 13.3273 | 13.3273 | 13.3273 | 13.3273 | 13.3273 | 13.3273 | 13.3273 | 13.3273 | 13.3273 | 13.3273 | 13.3273 | 20% | 4282.7105 | 10.2311 | 13.2537 | 14.0452 | 13.1981 | 13.2021 | 13.2836 | 13.4981 | 13.6419 | 13.7826 | 13.9471 | 14.0997 | 14.2477 | 14.2649 | 14.4376 | 14.3071 | 14.3071 | 14.3071 | 14.3071 | 14.3071 | 14.3071 | 14.3071 | 14.3071 | 14.3071 | 14.3071 | 14.3071 | 14.3071 | 14.3071 | 14.3071 | 14.3071 | 14.3071
15% | 4152.622 | 6.8814 | 9.1438 | 9.7601 | 9.1425 | 9.1423 | 9.2128 | 9.2901 | 9.4486 | 9.5626 | 9.6245 | 9.6924 | 9.7544 | 9.8661 | 10.0048 | 9.9955 | 9.9955 | 9.9955 | 9.9955 | 9.9955 | 9.9955 | 9.9955 | 9.9955 | 9.9955 | 9.9955 | 9.9955 | 9.9955 | 9.9955 | 9.9955 | 9.9955 | 9.9955 | 15% | 4364.7722 | 7.6733 | 9.9403 | 10.5339 | 9.8986 | 9.9016 | 9.9627 | 10.1236 | 10.2315 | 10.337 | 10.4603 | 10.5748 | 10.6858 | 10.6986 | 10.8282 | 10.7303 | 10.7303 | 10.7303 | 10.7303 | 10.7303 | 10.7303 | 10.7303 | 10.7303 | 10.7303 | 10.7303 | 10.7303 | 10.7303 | 10.7303 | 10.7303 | 10.7303 | 10.7303
10% | 4248.2976 | 4.5876 | 6.0959 | 6.5067 | 6.095 | 6.0948 | 6.1418 | 6.1934 | 6.2991 | 6.375 | 6.4163 | 6.4616 | 6.5029 | 6.5774 | 6.6699 | 6.6636 | 6.6636 | 6.6636 | 6.6636 | 6.6636 | 6.6636 | 6.6636 | 6.6636 | 6.6636 | 6.6636 | 6.6636 | 6.6636 | 6.6636 | 6.6636 | 6.6636 | 6.6636 | 10% | 4391.6218 | 5.1155 | 6.6269 | 7.0226 | 6.5991 | 6.601 | 6.6418 | 6.7491 | 6.821 | 6.8913 | 6.9736 | 7.0499 | 7.1239 | 7.1324 | 7.2188 | 7.1536 | 7.1536 | 7.1536 | 7.1536 | 7.1536 | 7.1536 | 7.1536 | 7.1536 | 7.1536 | 7.1536 | 7.1536 | 7.1536 | 7.1536 | 7.1536 | 7.1536 | 7.1536
5% | 4361.7469 | 2.2938 | 3.0479 | 3.2534 | 3.0475 | 3.0474 | 3.0709 | 3.0967 | 3.1495 | 3.1875 | 3.2082 | 3.2308 | 3.2515 | 3.2887 | 3.3349 | 3.3318 | 3.3318 | 3.3318 | 3.3318 | 3.3318 | 3.3318 | 3.3318 | 3.3318 | 3.3318 | 3.3318 | 3.3318 | 3.3318 | 3.3318 | 3.3318 | 3.3318 | 3.3318 | 5% | 4391.6218 | 2.5578 | 3.3134 | 3.5113 | 3.2995 | 3.3005 | 3.3209 | 3.3745 | 3.4105 | 3.4457 | 3.4868 | 3.5249 | 3.5619 | 3.5662 | 3.6094 | 3.5768 | 3.5768 | 3.5768 | 3.5768 | 3.5768 | 3.5768 | 3.5768 | 3.5768 | 3.5768 | 3.5768 | 3.5768 | 3.5768 | 3.5768 | 3.5768 | 3.5768 | 3.5768
9.992e-14% | 4391.6218 | 4.5839e-14 | 6.091e-14 | 6.5015e-14 | 6.0901e-14 | 6.09e-14 | 6.1369e-14 | 6.1884e-14 | 6.2941e-14 | 6.3699e-14 | 6.4112e-14 | 6.4564e-14 | 6.4977e-14 | 6.5722e-14 | 6.6646e-14 | 6.6583e-14 | 6.6583e-14 | 6.6583e-14 | 6.6583e-14 | 6.6583e-14 | 6.6583e-14 | 6.6583e-14 | 6.6583e-14 | 6.6583e-14 | 6.6583e-14 | 6.6583e-14 | 6.6583e-14 | 6.6583e-14 | 6.6583e-14 | 6.6583e-14 | 6.6583e-14 | 9.992e-14% | 4391.6218 | 5.1114e-14 | 6.6216e-14 | 7.017e-14 | 6.5938e-14 | 6.5958e-14 | 6.6365e-14 | 6.7437e-14 | 6.8155e-14 | 6.8858e-14 | 6.968e-14 | 7.0442e-14 | 7.1182e-14 | 7.1267e-14 | 7.213e-14 | 7.1478e-14 | 7.1478e-14 | 7.1478e-14 | 7.1478e-14 | 7.1478e-14 | 7.1478e-14 | 7.1478e-14 | 7.1478e-14 | 7.1478e-14 | 7.1478e-14 | 7.1478e-14 | 7.1478e-14 | 7.1478e-14 | 7.1478e-14 | 7.1478e-14 | 7.1478e-14
Option 5
Winter Season | [31 empty] | Winter Season
P50 | [31 empty] | P10
% of MD | Winter - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Winter - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 40.358 | 56.0239 | 60.0964 | 39.0406 | 39.5821 | 40.5143 | 42.6352 | 44.0549 | 45.8534 | 46.7869 | 47.6082 | 46.095 | 47.8685 | 50.6566 | 48.5408 | 48.5408 | 48.5408 | 48.5408 | 48.5408 | 48.5408 | 48.5408 | 48.5408 | 48.5408 | 48.5408 | 48.5408 | 48.5408 | 48.5408 | 48.5408 | 48.5408 | 48.5408 | 100% | 0 | 43.208 | 58.6763 | 62.9078 | 41.8125 | 42.2283 | 43.1403 | 45.2943 | 46.4704 | 48.7108 | 55.5209 | 49.9066 | 48.8085 | 50.2908 | 53.5327 | 51.3383 | 51.3383 | 51.3383 | 51.3383 | 51.3383 | 51.3383 | 51.3383 | 51.3383 | 51.3383 | 51.3383 | 51.3383 | 51.3383 | 51.3383 | 51.3383 | 51.3383 | 51.3383
99% | 1.486 | 39.9544 | 55.4636 | 59.4955 | 38.6502 | 39.1862 | 40.1091 | 42.2088 | 43.6143 | 45.3949 | 46.3191 | 47.1321 | 45.634 | 47.3898 | 50.15 | 48.0554 | 48.0554 | 48.0554 | 48.0554 | 48.0554 | 48.0554 | 48.0554 | 48.0554 | 48.0554 | 48.0554 | 48.0554 | 48.0554 | 48.0554 | 48.0554 | 48.0554 | 48.0554 | 99% | 1.486 | 42.7759 | 58.0895 | 62.2787 | 41.3944 | 41.806 | 42.7089 | 44.8414 | 46.0057 | 48.2237 | 54.9657 | 49.4076 | 48.3204 | 49.7879 | 52.9974 | 50.825 | 50.825 | 50.825 | 50.825 | 50.825 | 50.825 | 50.825 | 50.825 | 50.825 | 50.825 | 50.825 | 50.825 | 50.825 | 50.825 | 50.825 | 50.825
98% | 3.2692 | 39.5508 | 54.9034 | 58.8945 | 38.2598 | 38.7904 | 39.704 | 41.7825 | 43.1738 | 44.9363 | 45.8512 | 46.6561 | 45.1731 | 46.9111 | 49.6434 | 47.57 | 47.57 | 47.57 | 47.57 | 47.57 | 47.57 | 47.57 | 47.57 | 47.57 | 47.57 | 47.57 | 47.57 | 47.57 | 47.57 | 47.57 | 47.57 | 98% | 3.2692 | 42.3438 | 57.5027 | 61.6497 | 40.9763 | 41.3837 | 42.2775 | 44.3884 | 45.541 | 47.7366 | 54.4105 | 48.9085 | 47.8323 | 49.285 | 52.4621 | 50.3116 | 50.3116 | 50.3116 | 50.3116 | 50.3116 | 50.3116 | 50.3116 | 50.3116 | 50.3116 | 50.3116 | 50.3116 | 50.3116 | 50.3116 | 50.3116 | 50.3116 | 50.3116
97% | 6.8356 | 39.1473 | 54.3431 | 58.2935 | 37.8694 | 38.3946 | 39.2989 | 41.3561 | 42.7332 | 44.4778 | 45.3833 | 46.18 | 44.7121 | 46.4324 | 49.1369 | 47.0846 | 47.0846 | 47.0846 | 47.0846 | 47.0846 | 47.0846 | 47.0846 | 47.0846 | 47.0846 | 47.0846 | 47.0846 | 47.0846 | 47.0846 | 47.0846 | 47.0846 | 47.0846 | 97% | 6.8356 | 41.9118 | 56.916 | 61.0206 | 40.5582 | 40.9614 | 41.8461 | 43.9355 | 45.0763 | 47.2494 | 53.8553 | 48.4094 | 47.3442 | 48.7821 | 51.9268 | 49.7982 | 49.7982 | 49.7982 | 49.7982 | 49.7982 | 49.7982 | 49.7982 | 49.7982 | 49.7982 | 49.7982 | 49.7982 | 49.7982 | 49.7982 | 49.7982 | 49.7982 | 49.7982
95% | 17.5347 | 38.3401 | 53.2227 | 57.0916 | 37.0886 | 37.603 | 38.4886 | 40.5034 | 41.8521 | 43.5607 | 44.4476 | 45.2278 | 43.7902 | 45.475 | 48.1237 | 46.1137 | 46.1137 | 46.1137 | 46.1137 | 46.1137 | 46.1137 | 46.1137 | 46.1137 | 46.1137 | 46.1137 | 46.1137 | 46.1137 | 46.1137 | 46.1137 | 46.1137 | 46.1137 | 95% | 17.5347 | 41.0476 | 55.7425 | 59.7624 | 39.7219 | 40.1169 | 40.9833 | 43.0296 | 44.1469 | 46.2752 | 52.7448 | 47.4113 | 46.3681 | 47.7763 | 50.8561 | 48.7714 | 48.7714 | 48.7714 | 48.7714 | 48.7714 | 48.7714 | 48.7714 | 48.7714 | 48.7714 | 48.7714 | 48.7714 | 48.7714 | 48.7714 | 48.7714 | 48.7714 | 48.7714
90% | 78.7576 | 36.3222 | 50.4215 | 54.0868 | 35.1366 | 35.6238 | 36.4629 | 38.3717 | 39.6494 | 41.2681 | 42.1083 | 42.8474 | 41.4855 | 43.0816 | 45.5909 | 43.6867 | 43.6867 | 43.6867 | 43.6867 | 43.6867 | 43.6867 | 43.6867 | 43.6867 | 43.6867 | 43.6867 | 43.6867 | 43.6867 | 43.6867 | 43.6867 | 43.6867 | 43.6867 | 90% | 78.7576 | 38.8872 | 52.8086 | 56.617 | 37.6313 | 38.0054 | 38.8263 | 40.7649 | 41.8234 | 43.8397 | 49.9688 | 44.916 | 43.9276 | 45.2618 | 48.1795 | 46.2045 | 46.2045 | 46.2045 | 46.2045 | 46.2045 | 46.2045 | 46.2045 | 46.2045 | 46.2045 | 46.2045 | 46.2045 | 46.2045 | 46.2045 | 46.2045 | 46.2045 | 46.2045
85% | 236.8672 | 34.3043 | 47.6203 | 51.082 | 33.1845 | 33.6447 | 34.4371 | 36.2399 | 37.4467 | 38.9754 | 39.7689 | 40.467 | 39.1807 | 40.6882 | 43.0581 | 41.2597 | 41.2597 | 41.2597 | 41.2597 | 41.2597 | 41.2597 | 41.2597 | 41.2597 | 41.2597 | 41.2597 | 41.2597 | 41.2597 | 41.2597 | 41.2597 | 41.2597 | 41.2597 | 85% | 236.8672 | 36.7268 | 49.8748 | 53.4716 | 35.5407 | 35.894 | 36.6692 | 38.5002 | 39.4998 | 41.4042 | 47.1928 | 42.4206 | 41.4872 | 42.7472 | 45.5028 | 43.6376 | 43.6376 | 43.6376 | 43.6376 | 43.6376 | 43.6376 | 43.6376 | 43.6376 | 43.6376 | 43.6376 | 43.6376 | 43.6376 | 43.6376 | 43.6376 | 43.6376 | 43.6376
80% | 497.5104 | 32.2864 | 44.8191 | 48.0771 | 31.2325 | 31.6656 | 32.4114 | 34.1081 | 35.2439 | 36.6827 | 37.4296 | 38.0866 | 36.876 | 38.2948 | 40.5252 | 38.8326 | 38.8326 | 38.8326 | 38.8326 | 38.8326 | 38.8326 | 38.8326 | 38.8326 | 38.8326 | 38.8326 | 38.8326 | 38.8326 | 38.8326 | 38.8326 | 38.8326 | 38.8326 | 80% | 497.5104 | 34.5664 | 46.941 | 50.3262 | 33.45 | 33.7826 | 34.5122 | 36.2355 | 37.1763 | 38.9686 | 44.4167 | 39.9253 | 39.0468 | 40.2327 | 42.8262 | 41.0707 | 41.0707 | 41.0707 | 41.0707 | 41.0707 | 41.0707 | 41.0707 | 41.0707 | 41.0707 | 41.0707 | 41.0707 | 41.0707 | 41.0707 | 41.0707 | 41.0707 | 41.0707
75% | 803.6248 | 30.2685 | 42.0179 | 45.0723 | 29.2805 | 29.6865 | 30.3857 | 31.9764 | 33.0412 | 34.3901 | 35.0902 | 35.7062 | 34.5712 | 35.9013 | 37.9924 | 36.4056 | 36.4056 | 36.4056 | 36.4056 | 36.4056 | 36.4056 | 36.4056 | 36.4056 | 36.4056 | 36.4056 | 36.4056 | 36.4056 | 36.4056 | 36.4056 | 36.4056 | 36.4056 | 75% | 803.6248 | 32.406 | 44.0072 | 47.1809 | 31.3594 | 31.6712 | 32.3552 | 33.9707 | 34.8528 | 36.5331 | 41.6407 | 37.43 | 36.6064 | 37.7181 | 40.1496 | 38.5038 | 38.5038 | 38.5038 | 38.5038 | 38.5038 | 38.5038 | 38.5038 | 38.5038 | 38.5038 | 38.5038 | 38.5038 | 38.5038 | 38.5038 | 38.5038 | 38.5038 | 38.5038
70% | 1155.2107 | 28.2506 | 39.2167 | 42.0675 | 27.3284 | 27.7074 | 28.36 | 29.8446 | 30.8384 | 32.0974 | 32.7509 | 33.3258 | 32.2665 | 33.5079 | 35.4596 | 33.9785 | 33.9785 | 33.9785 | 33.9785 | 33.9785 | 33.9785 | 33.9785 | 33.9785 | 33.9785 | 33.9785 | 33.9785 | 33.9785 | 33.9785 | 33.9785 | 33.9785 | 33.9785 | 70% | 1155.2107 | 30.2456 | 41.0734 | 44.0355 | 29.2688 | 29.5598 | 30.1982 | 31.706 | 32.5293 | 34.0975 | 38.8646 | 34.9346 | 34.1659 | 35.2036 | 37.4729 | 35.9368 | 35.9368 | 35.9368 | 35.9368 | 35.9368 | 35.9368 | 35.9368 | 35.9368 | 35.9368 | 35.9368 | 35.9368 | 35.9368 | 35.9368 | 35.9368 | 35.9368 | 35.9368
65% | 1553.1596 | 26.2327 | 36.4155 | 39.0627 | 25.3764 | 25.7283 | 26.3343 | 27.7129 | 28.6357 | 29.8047 | 30.4115 | 30.9453 | 29.9617 | 31.1145 | 32.9268 | 31.5515 | 31.5515 | 31.5515 | 31.5515 | 31.5515 | 31.5515 | 31.5515 | 31.5515 | 31.5515 | 31.5515 | 31.5515 | 31.5515 | 31.5515 | 31.5515 | 31.5515 | 31.5515 | 65% | 1553.1596 | 28.0852 | 38.1396 | 40.8901 | 27.1782 | 27.4484 | 28.0412 | 29.4413 | 30.2058 | 31.662 | 36.0886 | 32.4393 | 31.7255 | 32.6891 | 34.7963 | 33.3699 | 33.3699 | 33.3699 | 33.3699 | 33.3699 | 33.3699 | 33.3699 | 33.3699 | 33.3699 | 33.3699 | 33.3699 | 33.3699 | 33.3699 | 33.3699 | 33.3699 | 33.3699
60% | 2026.2996 | 24.2148 | 33.6143 | 36.0579 | 23.4244 | 23.7492 | 24.3086 | 25.5811 | 26.4329 | 27.512 | 28.0722 | 28.5649 | 27.657 | 28.7211 | 30.3939 | 29.1245 | 29.1245 | 29.1245 | 29.1245 | 29.1245 | 29.1245 | 29.1245 | 29.1245 | 29.1245 | 29.1245 | 29.1245 | 29.1245 | 29.1245 | 29.1245 | 29.1245 | 29.1245 | 60% | 2026.2996 | 25.9248 | 35.2058 | 37.7447 | 25.0875 | 25.337 | 25.8842 | 27.1766 | 27.8822 | 29.2265 | 33.3125 | 29.944 | 29.2851 | 30.1745 | 32.1196 | 30.803 | 30.803 | 30.803 | 30.803 | 30.803 | 30.803 | 30.803 | 30.803 | 30.803 | 30.803 | 30.803 | 30.803 | 30.803 | 30.803 | 30.803 | 30.803
55% | 2598.4068 | 22.1969 | 30.8131 | 33.053 | 21.4723 | 21.7701 | 22.2829 | 23.4494 | 24.2302 | 25.2194 | 25.7328 | 26.1845 | 25.3522 | 26.3277 | 27.8611 | 26.6974 | 26.6974 | 26.6974 | 26.6974 | 26.6974 | 26.6974 | 26.6974 | 26.6974 | 26.6974 | 26.6974 | 26.6974 | 26.6974 | 26.6974 | 26.6974 | 26.6974 | 26.6974 | 55% | 2598.4068 | 23.7644 | 32.272 | 34.5993 | 22.9969 | 23.2255 | 23.7272 | 24.9119 | 25.5587 | 26.7909 | 30.5365 | 27.4486 | 26.8447 | 27.66 | 29.443 | 28.2361 | 28.2361 | 28.2361 | 28.2361 | 28.2361 | 28.2361 | 28.2361 | 28.2361 | 28.2361 | 28.2361 | 28.2361 | 28.2361 | 28.2361 | 28.2361 | 28.2361 | 28.2361
50% | 3233.5201 | 20.179 | 28.0119 | 30.0482 | 19.5203 | 19.791 | 20.2571 | 21.3176 | 22.0274 | 22.9267 | 23.3935 | 23.8041 | 23.0475 | 23.9342 | 25.3283 | 24.2704 | 24.2704 | 24.2704 | 24.2704 | 24.2704 | 24.2704 | 24.2704 | 24.2704 | 24.2704 | 24.2704 | 24.2704 | 24.2704 | 24.2704 | 24.2704 | 24.2704 | 24.2704 | 50% | 3233.5201 | 21.604 | 29.3381 | 31.4539 | 20.9063 | 21.1141 | 21.5701 | 22.6472 | 23.2352 | 24.3554 | 27.7604 | 24.9533 | 24.4042 | 25.1454 | 26.7664 | 25.6692 | 25.6692 | 25.6692 | 25.6692 | 25.6692 | 25.6692 | 25.6692 | 25.6692 | 25.6692 | 25.6692 | 25.6692 | 25.6692 | 25.6692 | 25.6692 | 25.6692 | 25.6692
45% | 3775.313 | 18.1611 | 25.2107 | 27.0434 | 17.5683 | 17.8119 | 18.2314 | 19.1858 | 19.8247 | 20.634 | 21.0541 | 21.4237 | 20.7427 | 21.5408 | 22.7955 | 21.8434 | 21.8434 | 21.8434 | 21.8434 | 21.8434 | 21.8434 | 21.8434 | 21.8434 | 21.8434 | 21.8434 | 21.8434 | 21.8434 | 21.8434 | 21.8434 | 21.8434 | 21.8434 | 45% | 3775.313 | 19.4436 | 26.4043 | 28.3085 | 18.8156 | 19.0027 | 19.4131 | 20.3824 | 20.9117 | 21.9198 | 24.9844 | 22.458 | 21.9638 | 22.6309 | 24.0897 | 23.1023 | 23.1023 | 23.1023 | 23.1023 | 23.1023 | 23.1023 | 23.1023 | 23.1023 | 23.1023 | 23.1023 | 23.1023 | 23.1023 | 23.1023 | 23.1023 | 23.1023 | 23.1023
40% | 4072.8088 | 16.1432 | 22.4095 | 24.0386 | 15.6162 | 15.8328 | 16.2057 | 17.0541 | 17.622 | 18.3414 | 18.7148 | 19.0433 | 18.438 | 19.1474 | 20.2626 | 19.4163 | 19.4163 | 19.4163 | 19.4163 | 19.4163 | 19.4163 | 19.4163 | 19.4163 | 19.4163 | 19.4163 | 19.4163 | 19.4163 | 19.4163 | 19.4163 | 19.4163 | 19.4163 | 40% | 4072.8088 | 17.2832 | 23.4705 | 25.1631 | 16.725 | 16.8913 | 17.2561 | 18.1177 | 18.5882 | 19.4843 | 22.2084 | 19.9627 | 19.5234 | 20.1163 | 21.4131 | 20.5353 | 20.5353 | 20.5353 | 20.5353 | 20.5353 | 20.5353 | 20.5353 | 20.5353 | 20.5353 | 20.5353 | 20.5353 | 20.5353 | 20.5353 | 20.5353 | 20.5353 | 20.5353
35% | 4198.821 | 14.1253 | 19.6083 | 21.0337 | 13.6642 | 13.8537 | 14.18 | 14.9223 | 15.4192 | 16.0487 | 16.3754 | 16.6629 | 16.1332 | 16.754 | 17.7298 | 16.9893 | 16.9893 | 16.9893 | 16.9893 | 16.9893 | 16.9893 | 16.9893 | 16.9893 | 16.9893 | 16.9893 | 16.9893 | 16.9893 | 16.9893 | 16.9893 | 16.9893 | 16.9893 | 35% | 4198.821 | 15.1228 | 20.5367 | 22.0177 | 14.6344 | 14.7799 | 15.0991 | 15.853 | 16.2646 | 17.0488 | 19.4323 | 17.4673 | 17.083 | 17.6018 | 18.7365 | 17.9684 | 17.9684 | 17.9684 | 17.9684 | 17.9684 | 17.9684 | 17.9684 | 17.9684 | 17.9684 | 17.9684 | 17.9684 | 17.9684 | 17.9684 | 17.9684 | 17.9684 | 17.9684
30% | 4271.3374 | 12.1074 | 16.8072 | 18.0289 | 11.7122 | 11.8746 | 12.1543 | 12.7906 | 13.2165 | 13.756 | 14.0361 | 14.2825 | 13.8285 | 14.3605 | 15.197 | 14.5622 | 14.5622 | 14.5622 | 14.5622 | 14.5622 | 14.5622 | 14.5622 | 14.5622 | 14.5622 | 14.5622 | 14.5622 | 14.5622 | 14.5622 | 14.5622 | 14.5622 | 14.5622 | 30% | 4271.3374 | 12.9624 | 17.6029 | 18.8723 | 12.5438 | 12.6685 | 12.9421 | 13.5883 | 13.9411 | 14.6132 | 16.6563 | 14.972 | 14.6425 | 15.0873 | 16.0598 | 15.4015 | 15.4015 | 15.4015 | 15.4015 | 15.4015 | 15.4015 | 15.4015 | 15.4015 | 15.4015 | 15.4015 | 15.4015 | 15.4015 | 15.4015 | 15.4015 | 15.4015 | 15.4015
25% | 4321.8611 | 10.0895 | 14.006 | 15.0241 | 9.7602 | 9.8955 | 10.1286 | 10.6588 | 11.0137 | 11.4634 | 11.6967 | 11.9021 | 11.5237 | 11.9671 | 12.6641 | 12.1352 | 12.1352 | 12.1352 | 12.1352 | 12.1352 | 12.1352 | 12.1352 | 12.1352 | 12.1352 | 12.1352 | 12.1352 | 12.1352 | 12.1352 | 12.1352 | 12.1352 | 12.1352 | 25% | 4321.8611 | 10.802 | 14.6691 | 15.727 | 10.4531 | 10.5571 | 10.7851 | 11.3236 | 11.6176 | 12.1777 | 13.8802 | 12.4767 | 12.2021 | 12.5727 | 13.3832 | 12.8346 | 12.8346 | 12.8346 | 12.8346 | 12.8346 | 12.8346 | 12.8346 | 12.8346 | 12.8346 | 12.8346 | 12.8346 | 12.8346 | 12.8346 | 12.8346 | 12.8346 | 12.8346
20% | 4353.067 | 8.0716 | 11.2048 | 12.0193 | 7.8081 | 7.9164 | 8.1029 | 8.527 | 8.811 | 9.1707 | 9.3574 | 9.5216 | 9.219 | 9.5737 | 10.1313 | 9.7082 | 9.7082 | 9.7082 | 9.7082 | 9.7082 | 9.7082 | 9.7082 | 9.7082 | 9.7082 | 9.7082 | 9.7082 | 9.7082 | 9.7082 | 9.7082 | 9.7082 | 9.7082 | 20% | 4353.067 | 8.6416 | 11.7353 | 12.5816 | 8.3625 | 8.4457 | 8.6281 | 9.0589 | 9.2941 | 9.7422 | 11.1042 | 9.9813 | 9.7617 | 10.0582 | 10.7065 | 10.2677 | 10.2677 | 10.2677 | 10.2677 | 10.2677 | 10.2677 | 10.2677 | 10.2677 | 10.2677 | 10.2677 | 10.2677 | 10.2677 | 10.2677 | 10.2677 | 10.2677 | 10.2677
15% | 4369.4129 | 6.0537 | 8.4036 | 9.0145 | 5.8561 | 5.9373 | 6.0771 | 6.3953 | 6.6082 | 6.878 | 7.018 | 7.1412 | 6.9142 | 7.1803 | 7.5985 | 7.2811 | 7.2811 | 7.2811 | 7.2811 | 7.2811 | 7.2811 | 7.2811 | 7.2811 | 7.2811 | 7.2811 | 7.2811 | 7.2811 | 7.2811 | 7.2811 | 7.2811 | 7.2811 | 15% | 4369.4129 | 6.4812 | 8.8014 | 9.4362 | 6.2719 | 6.3342 | 6.471 | 6.7941 | 6.9706 | 7.3066 | 8.3281 | 7.486 | 7.3213 | 7.5436 | 8.0299 | 7.7008 | 7.7008 | 7.7008 | 7.7008 | 7.7008 | 7.7008 | 7.7008 | 7.7008 | 7.7008 | 7.7008 | 7.7008 | 7.7008 | 7.7008 | 7.7008 | 7.7008 | 7.7008
10% | 4378.6261 | 4.0358 | 5.6024 | 6.0096 | 3.9041 | 3.9582 | 4.0514 | 4.2635 | 4.4055 | 4.5853 | 4.6787 | 4.7608 | 4.6095 | 4.7868 | 5.0657 | 4.8541 | 4.8541 | 4.8541 | 4.8541 | 4.8541 | 4.8541 | 4.8541 | 4.8541 | 4.8541 | 4.8541 | 4.8541 | 4.8541 | 4.8541 | 4.8541 | 4.8541 | 4.8541 | 10% | 4378.6261 | 4.3208 | 5.8676 | 6.2908 | 4.1813 | 4.2228 | 4.314 | 4.5294 | 4.647 | 4.8711 | 5.5521 | 4.9907 | 4.8808 | 5.0291 | 5.3533 | 5.1338 | 5.1338 | 5.1338 | 5.1338 | 5.1338 | 5.1338 | 5.1338 | 5.1338 | 5.1338 | 5.1338 | 5.1338 | 5.1338 | 5.1338 | 5.1338 | 5.1338 | 5.1338
5% | 4391.7028 | 2.0179 | 2.8012 | 3.0048 | 1.952 | 1.9791 | 2.0257 | 2.1318 | 2.2027 | 2.2927 | 2.3393 | 2.3804 | 2.3047 | 2.3934 | 2.5328 | 2.427 | 2.427 | 2.427 | 2.427 | 2.427 | 2.427 | 2.427 | 2.427 | 2.427 | 2.427 | 2.427 | 2.427 | 2.427 | 2.427 | 2.427 | 2.427 | 5% | 4391.7028 | 2.1604 | 2.9338 | 3.1454 | 2.0906 | 2.1114 | 2.157 | 2.2647 | 2.3235 | 2.4355 | 2.776 | 2.4953 | 2.4404 | 2.5145 | 2.6766 | 2.5669 | 2.5669 | 2.5669 | 2.5669 | 2.5669 | 2.5669 | 2.5669 | 2.5669 | 2.5669 | 2.5669 | 2.5669 | 2.5669 | 2.5669 | 2.5669 | 2.5669 | 2.5669
9.992e-14% | 4391.7028 | 4.0326e-14 | 5.5979e-14 | 6.0048e-14 | 3.9009e-14 | 3.955e-14 | 4.0482e-14 | 4.2601e-14 | 4.402e-14 | 4.5817e-14 | 4.675e-14 | 4.757e-14 | 4.6058e-14 | 4.783e-14 | 5.0616e-14 | 4.8502e-14 | 4.8502e-14 | 4.8502e-14 | 4.8502e-14 | 4.8502e-14 | 4.8502e-14 | 4.8502e-14 | 4.8502e-14 | 4.8502e-14 | 4.8502e-14 | 4.8502e-14 | 4.8502e-14 | 4.8502e-14 | 4.8502e-14 | 4.8502e-14 | 4.8502e-14 | 9.992e-14% | 4391.7028 | 4.3173e-14 | 5.8629e-14 | 6.2858e-14 | 4.1779e-14 | 4.2195e-14 | 4.3106e-14 | 4.5258e-14 | 4.6433e-14 | 4.8672e-14 | 5.5477e-14 | 4.9867e-14 | 4.8769e-14 | 5.0251e-14 | 5.349e-14 | 5.1297e-14 | 5.1297e-14 | 5.1297e-14 | 5.1297e-14 | 5.1297e-14 | 5.1297e-14 | 5.1297e-14 | 5.1297e-14 | 5.1297e-14 | 5.1297e-14 | 5.1297e-14 | 5.1297e-14 | 5.1297e-14 | 5.1297e-14 | 5.1297e-14 | 5.1297e-14
Summer Season | [31 empty] | Summer Season
P50 | [31 empty] | P10
% of MD | Summer - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Summer - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 45.8759 | 60.9589 | 65.0674 | 43.1999 | 43.1985 | 43.6684 | 44.1838 | 45.2409 | 46.0004 | 46.4133 | 46.8657 | 47.279 | 48.0243 | 48.9489 | 48.8864 | 48.8864 | 48.8864 | 48.8864 | 48.8864 | 48.8864 | 48.8864 | 48.8864 | 48.8864 | 48.8864 | 48.8864 | 48.8864 | 48.8864 | 48.8864 | 48.8864 | 48.8864 | 100% | 0 | 51.1554 | 66.2686 | 70.2261 | 48.2407 | 48.2605 | 48.6679 | 49.7405 | 50.4597 | 51.1632 | 51.9856 | 52.7485 | 53.4886 | 53.5743 | 54.4378 | 53.7857 | 53.7857 | 53.7857 | 53.7857 | 53.7857 | 53.7857 | 53.7857 | 53.7857 | 53.7857 | 53.7857 | 53.7857 | 53.7857 | 53.7857 | 53.7857 | 53.7857 | 53.7857
99% | 0 | 45.4171 | 60.3493 | 64.4168 | 42.7679 | 42.7665 | 43.2317 | 43.742 | 44.7885 | 45.5404 | 45.9492 | 46.397 | 46.8062 | 47.5441 | 48.4594 | 48.3975 | 48.3975 | 48.3975 | 48.3975 | 48.3975 | 48.3975 | 48.3975 | 48.3975 | 48.3975 | 48.3975 | 48.3975 | 48.3975 | 48.3975 | 48.3975 | 48.3975 | 48.3975 | 99% | 1.5127 | 50.6438 | 65.6059 | 69.5238 | 47.7583 | 47.7779 | 48.1812 | 49.2431 | 49.9551 | 50.6515 | 51.4658 | 52.221 | 52.9537 | 53.0385 | 53.8934 | 53.2478 | 53.2478 | 53.2478 | 53.2478 | 53.2478 | 53.2478 | 53.2478 | 53.2478 | 53.2478 | 53.2478 | 53.2478 | 53.2478 | 53.2478 | 53.2478 | 53.2478 | 53.2478
98% | 0 | 44.9584 | 59.7397 | 63.7661 | 42.3359 | 42.3345 | 42.795 | 43.3001 | 44.3361 | 45.0804 | 45.4851 | 45.9284 | 46.3334 | 47.0638 | 47.9699 | 47.9086 | 47.9086 | 47.9086 | 47.9086 | 47.9086 | 47.9086 | 47.9086 | 47.9086 | 47.9086 | 47.9086 | 47.9086 | 47.9086 | 47.9086 | 47.9086 | 47.9086 | 47.9086 | 98% | 2.269 | 50.1322 | 64.9433 | 68.8216 | 47.2759 | 47.2953 | 47.6946 | 48.7457 | 49.4505 | 50.1399 | 50.9459 | 51.6935 | 52.4188 | 52.5028 | 53.349 | 52.7099 | 52.7099 | 52.7099 | 52.7099 | 52.7099 | 52.7099 | 52.7099 | 52.7099 | 52.7099 | 52.7099 | 52.7099 | 52.7099 | 52.7099 | 52.7099 | 52.7099 | 52.7099
97% | 0.37816 | 44.4996 | 59.1301 | 63.1154 | 41.9039 | 41.9025 | 42.3583 | 42.8583 | 43.8837 | 44.6204 | 45.0209 | 45.4597 | 45.8606 | 46.5836 | 47.4804 | 47.4198 | 47.4198 | 47.4198 | 47.4198 | 47.4198 | 47.4198 | 47.4198 | 47.4198 | 47.4198 | 47.4198 | 47.4198 | 47.4198 | 47.4198 | 47.4198 | 47.4198 | 47.4198 | 97% | 3.7816 | 49.6207 | 64.2806 | 68.1193 | 46.7935 | 46.8127 | 47.2079 | 48.2483 | 48.9459 | 49.6283 | 50.4261 | 51.1661 | 51.8839 | 51.9671 | 52.8047 | 52.1721 | 52.1721 | 52.1721 | 52.1721 | 52.1721 | 52.1721 | 52.1721 | 52.1721 | 52.1721 | 52.1721 | 52.1721 | 52.1721 | 52.1721 | 52.1721 | 52.1721 | 52.1721
95% | 2.269 | 43.5821 | 57.911 | 61.8141 | 41.0399 | 41.0385 | 41.4849 | 41.9746 | 42.9789 | 43.7004 | 44.0927 | 44.5224 | 44.9151 | 45.6231 | 46.5014 | 46.4421 | 46.4421 | 46.4421 | 46.4421 | 46.4421 | 46.4421 | 46.4421 | 46.4421 | 46.4421 | 46.4421 | 46.4421 | 46.4421 | 46.4421 | 46.4421 | 46.4421 | 46.4421 | 95% | 6.0506 | 48.5976 | 62.9552 | 66.7148 | 45.8287 | 45.8475 | 46.2345 | 47.2535 | 47.9367 | 48.605 | 49.3863 | 50.1111 | 50.8141 | 50.8956 | 51.7159 | 51.0964 | 51.0964 | 51.0964 | 51.0964 | 51.0964 | 51.0964 | 51.0964 | 51.0964 | 51.0964 | 51.0964 | 51.0964 | 51.0964 | 51.0964 | 51.0964 | 51.0964 | 51.0964
90% | 5.6725 | 41.2883 | 54.863 | 58.5607 | 38.8799 | 38.8786 | 39.3015 | 39.7654 | 40.7168 | 41.4004 | 41.772 | 42.1791 | 42.5511 | 43.2219 | 44.054 | 43.9977 | 43.9977 | 43.9977 | 43.9977 | 43.9977 | 43.9977 | 43.9977 | 43.9977 | 43.9977 | 43.9977 | 43.9977 | 43.9977 | 43.9977 | 43.9977 | 43.9977 | 43.9977 | 90% | 16.2611 | 46.0398 | 59.6418 | 63.2035 | 43.4167 | 43.4344 | 43.8011 | 44.7665 | 45.4137 | 46.0468 | 46.7871 | 47.4737 | 48.1397 | 48.2169 | 48.994 | 48.4071 | 48.4071 | 48.4071 | 48.4071 | 48.4071 | 48.4071 | 48.4071 | 48.4071 | 48.4071 | 48.4071 | 48.4071 | 48.4071 | 48.4071 | 48.4071 | 48.4071 | 48.4071
85% | 15.8829 | 38.9945 | 51.8151 | 55.3073 | 36.7199 | 36.7187 | 37.1181 | 37.5562 | 38.4548 | 39.1004 | 39.4513 | 39.8358 | 40.1872 | 40.8207 | 41.6065 | 41.5534 | 41.5534 | 41.5534 | 41.5534 | 41.5534 | 41.5534 | 41.5534 | 41.5534 | 41.5534 | 41.5534 | 41.5534 | 41.5534 | 41.5534 | 41.5534 | 41.5534 | 41.5534 | 85% | 26.4715 | 43.482 | 56.3283 | 59.6922 | 41.0046 | 41.0214 | 41.3677 | 42.2795 | 42.8908 | 43.4887 | 44.1878 | 44.8362 | 45.4653 | 45.5381 | 46.2721 | 45.7178 | 45.7178 | 45.7178 | 45.7178 | 45.7178 | 45.7178 | 45.7178 | 45.7178 | 45.7178 | 45.7178 | 45.7178 | 45.7178 | 45.7178 | 45.7178 | 45.7178 | 45.7178
80% | 31.0095 | 36.7007 | 48.7671 | 52.0539 | 34.5599 | 34.5588 | 34.9347 | 35.347 | 36.1928 | 36.8003 | 37.1307 | 37.4925 | 37.8232 | 38.4194 | 39.1591 | 39.1091 | 39.1091 | 39.1091 | 39.1091 | 39.1091 | 39.1091 | 39.1091 | 39.1091 | 39.1091 | 39.1091 | 39.1091 | 39.1091 | 39.1091 | 39.1091 | 39.1091 | 39.1091 | 80% | 34.0348 | 40.9243 | 53.0149 | 56.1809 | 38.5926 | 38.6084 | 38.9343 | 39.7924 | 40.3678 | 40.9305 | 41.5885 | 42.1988 | 42.7908 | 42.8594 | 43.5502 | 43.0285 | 43.0285 | 43.0285 | 43.0285 | 43.0285 | 43.0285 | 43.0285 | 43.0285 | 43.0285 | 43.0285 | 43.0285 | 43.0285 | 43.0285 | 43.0285 | 43.0285 | 43.0285
75% | 72.9857 | 34.4069 | 45.7192 | 48.8006 | 32.3999 | 32.3988 | 32.7513 | 33.1379 | 33.9307 | 34.5003 | 34.81 | 35.1493 | 35.4593 | 36.0182 | 36.7116 | 36.6648 | 36.6648 | 36.6648 | 36.6648 | 36.6648 | 36.6648 | 36.6648 | 36.6648 | 36.6648 | 36.6648 | 36.6648 | 36.6648 | 36.6648 | 36.6648 | 36.6648 | 36.6648 | 75% | 48.405 | 38.3665 | 49.7015 | 52.6696 | 36.1805 | 36.1954 | 36.5009 | 37.3054 | 37.8448 | 38.3724 | 38.9892 | 39.5614 | 40.1164 | 40.1807 | 40.8283 | 40.3392 | 40.3392 | 40.3392 | 40.3392 | 40.3392 | 40.3392 | 40.3392 | 40.3392 | 40.3392 | 40.3392 | 40.3392 | 40.3392 | 40.3392 | 40.3392 | 40.3392 | 40.3392
70% | 150.5094 | 32.1131 | 42.6712 | 45.5472 | 30.2399 | 30.2389 | 30.5679 | 30.9287 | 31.6687 | 32.2003 | 32.4893 | 32.806 | 33.0953 | 33.617 | 34.2642 | 34.2205 | 34.2205 | 34.2205 | 34.2205 | 34.2205 | 34.2205 | 34.2205 | 34.2205 | 34.2205 | 34.2205 | 34.2205 | 34.2205 | 34.2205 | 34.2205 | 34.2205 | 34.2205 | 70% | 76.3892 | 35.8087 | 46.388 | 49.1583 | 33.7685 | 33.7823 | 34.0675 | 34.8184 | 35.3218 | 35.8142 | 36.3899 | 36.924 | 37.442 | 37.502 | 38.1065 | 37.65 | 37.65 | 37.65 | 37.65 | 37.65 | 37.65 | 37.65 | 37.65 | 37.65 | 37.65 | 37.65 | 37.65 | 37.65 | 37.65 | 37.65 | 37.65
65% | 359.6342 | 29.8193 | 39.6233 | 42.2938 | 28.0799 | 28.079 | 28.3844 | 28.7195 | 29.4066 | 29.9003 | 30.1687 | 30.4627 | 30.7314 | 31.2158 | 31.8168 | 31.7761 | 31.7761 | 31.7761 | 31.7761 | 31.7761 | 31.7761 | 31.7761 | 31.7761 | 31.7761 | 31.7761 | 31.7761 | 31.7761 | 31.7761 | 31.7761 | 31.7761 | 31.7761 | 65% | 114.2056 | 33.251 | 43.0746 | 45.647 | 31.3565 | 31.3693 | 31.6341 | 32.3314 | 32.7988 | 33.2561 | 33.7907 | 34.2865 | 34.7676 | 34.8233 | 35.3846 | 34.9607 | 34.9607 | 34.9607 | 34.9607 | 34.9607 | 34.9607 | 34.9607 | 34.9607 | 34.9607 | 34.9607 | 34.9607 | 34.9607 | 34.9607 | 34.9607 | 34.9607 | 34.9607
60% | 689.7717 | 27.5255 | 36.5753 | 39.0405 | 25.9199 | 25.9191 | 26.201 | 26.5103 | 27.1446 | 27.6003 | 27.848 | 28.1194 | 28.3674 | 28.8146 | 29.3693 | 29.3318 | 29.3318 | 29.3318 | 29.3318 | 29.3318 | 29.3318 | 29.3318 | 29.3318 | 29.3318 | 29.3318 | 29.3318 | 29.3318 | 29.3318 | 29.3318 | 29.3318 | 29.3318 | 60% | 178.1154 | 30.6932 | 39.7612 | 42.1357 | 28.9444 | 28.9563 | 29.2008 | 29.8443 | 30.2758 | 30.6979 | 31.1914 | 31.6491 | 32.0931 | 32.1446 | 32.6627 | 32.2714 | 32.2714 | 32.2714 | 32.2714 | 32.2714 | 32.2714 | 32.2714 | 32.2714 | 32.2714 | 32.2714 | 32.2714 | 32.2714 | 32.2714 | 32.2714 | 32.2714 | 32.2714
55% | 1095.5419 | 25.2317 | 33.5274 | 35.7871 | 23.7599 | 23.7592 | 24.0176 | 24.3011 | 24.8825 | 25.3002 | 25.5273 | 25.7761 | 26.0035 | 26.4134 | 26.9219 | 26.8875 | 26.8875 | 26.8875 | 26.8875 | 26.8875 | 26.8875 | 26.8875 | 26.8875 | 26.8875 | 26.8875 | 26.8875 | 26.8875 | 26.8875 | 26.8875 | 26.8875 | 26.8875 | 55% | 311.6074 | 28.1354 | 36.4477 | 38.6243 | 26.5324 | 26.5433 | 26.7674 | 27.3573 | 27.7528 | 28.1397 | 28.5921 | 29.0117 | 29.4187 | 29.4659 | 29.9408 | 29.5821 | 29.5821 | 29.5821 | 29.5821 | 29.5821 | 29.5821 | 29.5821 | 29.5821 | 29.5821 | 29.5821 | 29.5821 | 29.5821 | 29.5821 | 29.5821 | 29.5821 | 29.5821
50% | 1666.1918 | 22.9379 | 30.4794 | 32.5337 | 21.5999 | 21.5992 | 21.8342 | 22.0919 | 22.6205 | 23.0002 | 23.2067 | 23.4328 | 23.6395 | 24.0122 | 24.4744 | 24.4432 | 24.4432 | 24.4432 | 24.4432 | 24.4432 | 24.4432 | 24.4432 | 24.4432 | 24.4432 | 24.4432 | 24.4432 | 24.4432 | 24.4432 | 24.4432 | 24.4432 | 24.4432 | 50% | 636.0723 | 25.5777 | 33.1343 | 35.113 | 24.1204 | 24.1302 | 24.334 | 24.8703 | 25.2299 | 25.5816 | 25.9928 | 26.3743 | 26.7443 | 26.7871 | 27.2189 | 26.8928 | 26.8928 | 26.8928 | 26.8928 | 26.8928 | 26.8928 | 26.8928 | 26.8928 | 26.8928 | 26.8928 | 26.8928 | 26.8928 | 26.8928 | 26.8928 | 26.8928 | 26.8928
45% | 2506.0947 | 20.6442 | 27.4315 | 29.2803 | 19.4399 | 19.4393 | 19.6508 | 19.8827 | 20.3584 | 20.7002 | 20.886 | 21.0896 | 21.2756 | 21.6109 | 22.027 | 21.9989 | 21.9989 | 21.9989 | 21.9989 | 21.9989 | 21.9989 | 21.9989 | 21.9989 | 21.9989 | 21.9989 | 21.9989 | 21.9989 | 21.9989 | 21.9989 | 21.9989 | 21.9989 | 45% | 1179.4944 | 23.0199 | 29.8209 | 31.6017 | 21.7083 | 21.7172 | 21.9006 | 22.3832 | 22.7069 | 23.0234 | 23.3935 | 23.7368 | 24.0698 | 24.1084 | 24.497 | 24.2035 | 24.2035 | 24.2035 | 24.2035 | 24.2035 | 24.2035 | 24.2035 | 24.2035 | 24.2035 | 24.2035 | 24.2035 | 24.2035 | 24.2035 | 24.2035 | 24.2035 | 24.2035
40% | 3164.4787 | 18.3504 | 24.3836 | 26.027 | 17.2799 | 17.2794 | 17.4673 | 17.6735 | 18.0964 | 18.4002 | 18.5653 | 18.7463 | 18.9116 | 19.2097 | 19.5795 | 19.5546 | 19.5546 | 19.5546 | 19.5546 | 19.5546 | 19.5546 | 19.5546 | 19.5546 | 19.5546 | 19.5546 | 19.5546 | 19.5546 | 19.5546 | 19.5546 | 19.5546 | 19.5546 | 40% | 1808.3816 | 20.4621 | 26.5075 | 28.0904 | 19.2963 | 19.3042 | 19.4672 | 19.8962 | 20.1839 | 20.4653 | 20.7942 | 21.0994 | 21.3954 | 21.4297 | 21.7751 | 21.5143 | 21.5143 | 21.5143 | 21.5143 | 21.5143 | 21.5143 | 21.5143 | 21.5143 | 21.5143 | 21.5143 | 21.5143 | 21.5143 | 21.5143 | 21.5143 | 21.5143 | 21.5143
35% | 3551.3408 | 16.0566 | 21.3356 | 22.7736 | 15.12 | 15.1195 | 15.2839 | 15.4643 | 15.8343 | 16.1001 | 16.2447 | 16.403 | 16.5477 | 16.8085 | 17.1321 | 17.1102 | 17.1102 | 17.1102 | 17.1102 | 17.1102 | 17.1102 | 17.1102 | 17.1102 | 17.1102 | 17.1102 | 17.1102 | 17.1102 | 17.1102 | 17.1102 | 17.1102 | 17.1102 | 35% | 2779.1293 | 17.9044 | 23.194 | 24.5791 | 16.8843 | 16.8912 | 17.0338 | 17.4092 | 17.6609 | 17.9071 | 18.195 | 18.462 | 18.721 | 18.751 | 19.0532 | 18.825 | 18.825 | 18.825 | 18.825 | 18.825 | 18.825 | 18.825 | 18.825 | 18.825 | 18.825 | 18.825 | 18.825 | 18.825 | 18.825 | 18.825 | 18.825
30% | 3758.953 | 13.7628 | 18.2877 | 19.5202 | 12.96 | 12.9595 | 13.1005 | 13.2551 | 13.5723 | 13.8001 | 13.924 | 14.0597 | 14.1837 | 14.4073 | 14.6847 | 14.6659 | 14.6659 | 14.6659 | 14.6659 | 14.6659 | 14.6659 | 14.6659 | 14.6659 | 14.6659 | 14.6659 | 14.6659 | 14.6659 | 14.6659 | 14.6659 | 14.6659 | 14.6659 | 30% | 3814.165 | 15.3466 | 19.8806 | 21.0678 | 14.4722 | 14.4781 | 14.6004 | 14.9222 | 15.1379 | 15.3489 | 15.5957 | 15.8246 | 16.0466 | 16.0723 | 16.3313 | 16.1357 | 16.1357 | 16.1357 | 16.1357 | 16.1357 | 16.1357 | 16.1357 | 16.1357 | 16.1357 | 16.1357 | 16.1357 | 16.1357 | 16.1357 | 16.1357 | 16.1357 | 16.1357
25% | 3926.4798 | 11.469 | 15.2397 | 16.2669 | 10.8 | 10.7996 | 10.9171 | 11.046 | 11.3102 | 11.5001 | 11.6033 | 11.7164 | 11.8198 | 12.0061 | 12.2372 | 12.2216 | 12.2216 | 12.2216 | 12.2216 | 12.2216 | 12.2216 | 12.2216 | 12.2216 | 12.2216 | 12.2216 | 12.2216 | 12.2216 | 12.2216 | 12.2216 | 12.2216 | 12.2216 | 25% | 4166.9923 | 12.7888 | 16.5672 | 17.5565 | 12.0602 | 12.0651 | 12.167 | 12.4351 | 12.6149 | 12.7908 | 12.9964 | 13.1871 | 13.3721 | 13.3936 | 13.6094 | 13.4464 | 13.4464 | 13.4464 | 13.4464 | 13.4464 | 13.4464 | 13.4464 | 13.4464 | 13.4464 | 13.4464 | 13.4464 | 13.4464 | 13.4464 | 13.4464 | 13.4464 | 13.4464
20% | 4050.5177 | 9.1752 | 12.1918 | 13.0135 | 8.64 | 8.6397 | 8.7337 | 8.8368 | 9.0482 | 9.2001 | 9.2827 | 9.3731 | 9.4558 | 9.6049 | 9.7898 | 9.7773 | 9.7773 | 9.7773 | 9.7773 | 9.7773 | 9.7773 | 9.7773 | 9.7773 | 9.7773 | 9.7773 | 9.7773 | 9.7773 | 9.7773 | 9.7773 | 9.7773 | 9.7773 | 20% | 4282.7105 | 10.2311 | 13.2537 | 14.0452 | 9.6481 | 9.6521 | 9.7336 | 9.9481 | 10.0919 | 10.2326 | 10.3971 | 10.5497 | 10.6977 | 10.7149 | 10.8876 | 10.7571 | 10.7571 | 10.7571 | 10.7571 | 10.7571 | 10.7571 | 10.7571 | 10.7571 | 10.7571 | 10.7571 | 10.7571 | 10.7571 | 10.7571 | 10.7571 | 10.7571 | 10.7571
15% | 4152.622 | 6.8814 | 9.1438 | 9.7601 | 6.48 | 6.4798 | 6.5503 | 6.6276 | 6.7861 | 6.9001 | 6.962 | 7.0299 | 7.0919 | 7.2036 | 7.3423 | 7.333 | 7.333 | 7.333 | 7.333 | 7.333 | 7.333 | 7.333 | 7.333 | 7.333 | 7.333 | 7.333 | 7.333 | 7.333 | 7.333 | 7.333 | 7.333 | 15% | 4364.7722 | 7.6733 | 9.9403 | 10.5339 | 7.2361 | 7.2391 | 7.3002 | 7.4611 | 7.569 | 7.6745 | 7.7978 | 7.9123 | 8.0233 | 8.0361 | 8.1657 | 8.0678 | 8.0678 | 8.0678 | 8.0678 | 8.0678 | 8.0678 | 8.0678 | 8.0678 | 8.0678 | 8.0678 | 8.0678 | 8.0678 | 8.0678 | 8.0678 | 8.0678 | 8.0678
10% | 4248.2976 | 4.5876 | 6.0959 | 6.5067 | 4.32 | 4.3198 | 4.3668 | 4.4184 | 4.5241 | 4.6 | 4.6413 | 4.6866 | 4.7279 | 4.8024 | 4.8949 | 4.8886 | 4.8886 | 4.8886 | 4.8886 | 4.8886 | 4.8886 | 4.8886 | 4.8886 | 4.8886 | 4.8886 | 4.8886 | 4.8886 | 4.8886 | 4.8886 | 4.8886 | 4.8886 | 10% | 4391.6218 | 5.1155 | 6.6269 | 7.0226 | 4.8241 | 4.826 | 4.8668 | 4.9741 | 5.046 | 5.1163 | 5.1986 | 5.2749 | 5.3489 | 5.3574 | 5.4438 | 5.3786 | 5.3786 | 5.3786 | 5.3786 | 5.3786 | 5.3786 | 5.3786 | 5.3786 | 5.3786 | 5.3786 | 5.3786 | 5.3786 | 5.3786 | 5.3786 | 5.3786 | 5.3786
5% | 4361.7469 | 2.2938 | 3.0479 | 3.2534 | 2.16 | 2.1599 | 2.1834 | 2.2092 | 2.262 | 2.3 | 2.3207 | 2.3433 | 2.364 | 2.4012 | 2.4474 | 2.4443 | 2.4443 | 2.4443 | 2.4443 | 2.4443 | 2.4443 | 2.4443 | 2.4443 | 2.4443 | 2.4443 | 2.4443 | 2.4443 | 2.4443 | 2.4443 | 2.4443 | 2.4443 | 5% | 4391.6218 | 2.5578 | 3.3134 | 3.5113 | 2.412 | 2.413 | 2.4334 | 2.487 | 2.523 | 2.5582 | 2.5993 | 2.6374 | 2.6744 | 2.6787 | 2.7219 | 2.6893 | 2.6893 | 2.6893 | 2.6893 | 2.6893 | 2.6893 | 2.6893 | 2.6893 | 2.6893 | 2.6893 | 2.6893 | 2.6893 | 2.6893 | 2.6893 | 2.6893 | 2.6893
9.992e-14% | 4391.6218 | 4.5839e-14 | 6.091e-14 | 6.5015e-14 | 4.3165e-14 | 4.3164e-14 | 4.3633e-14 | 4.4148e-14 | 4.5205e-14 | 4.5964e-14 | 4.6376e-14 | 4.6828e-14 | 4.7241e-14 | 4.7986e-14 | 4.891e-14 | 4.8847e-14 | 4.8847e-14 | 4.8847e-14 | 4.8847e-14 | 4.8847e-14 | 4.8847e-14 | 4.8847e-14 | 4.8847e-14 | 4.8847e-14 | 4.8847e-14 | 4.8847e-14 | 4.8847e-14 | 4.8847e-14 | 4.8847e-14 | 4.8847e-14 | 4.8847e-14 | 9.992e-14% | 4391.6218 | 5.1114e-14 | 6.6216e-14 | 7.017e-14 | 4.8202e-14 | 4.8222e-14 | 4.8629e-14 | 4.9701e-14 | 5.0419e-14 | 5.1122e-14 | 5.1944e-14 | 5.2706e-14 | 5.3446e-14 | 5.3531e-14 | 5.4394e-14 | 5.3743e-14 | 5.3743e-14 | 5.3743e-14 | 5.3743e-14 | 5.3743e-14 | 5.3743e-14 | 5.3743e-14 | 5.3743e-14 | 5.3743e-14 | 5.3743e-14 | 5.3743e-14 | 5.3743e-14 | 5.3743e-14 | 5.3743e-14 | 5.3743e-14 | 5.3743e-14
Option 6
Winter Season | [31 empty] | Winter Season
P50 | [31 empty] | P10
% of MD | Winter - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Winter - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 40.358 | 56.0239 | 60.0964 | 60.7906 | 61.3321 | 62.2643 | 64.3852 | 65.8049 | 67.6034 | 68.5369 | 69.3582 | 67.845 | 69.6185 | 72.4066 | 70.2908 | 70.2908 | 70.2908 | 70.2908 | 70.2908 | 70.2908 | 70.2908 | 70.2908 | 70.2908 | 70.2908 | 70.2908 | 70.2908 | 70.2908 | 70.2908 | 70.2908 | 70.2908 | 100% | 0 | 43.208 | 58.6763 | 62.9078 | 63.5625 | 63.9783 | 64.8903 | 67.0443 | 68.2204 | 70.4608 | 77.2709 | 71.6566 | 70.5585 | 72.0408 | 75.2827 | 73.0883 | 73.0883 | 73.0883 | 73.0883 | 73.0883 | 73.0883 | 73.0883 | 73.0883 | 73.0883 | 73.0883 | 73.0883 | 73.0883 | 73.0883 | 73.0883 | 73.0883 | 73.0883
99% | 1.486 | 39.9544 | 55.4636 | 59.4955 | 60.1827 | 60.7187 | 61.6416 | 63.7413 | 65.1468 | 66.9274 | 67.8516 | 68.6646 | 67.1665 | 68.9223 | 71.6825 | 69.5879 | 69.5879 | 69.5879 | 69.5879 | 69.5879 | 69.5879 | 69.5879 | 69.5879 | 69.5879 | 69.5879 | 69.5879 | 69.5879 | 69.5879 | 69.5879 | 69.5879 | 69.5879 | 99% | 1.486 | 42.7759 | 58.0895 | 62.2787 | 62.9269 | 63.3385 | 64.2414 | 66.3739 | 67.5382 | 69.7562 | 76.4982 | 70.9401 | 69.8529 | 71.3204 | 74.5299 | 72.3575 | 72.3575 | 72.3575 | 72.3575 | 72.3575 | 72.3575 | 72.3575 | 72.3575 | 72.3575 | 72.3575 | 72.3575 | 72.3575 | 72.3575 | 72.3575 | 72.3575 | 72.3575
98% | 3.2692 | 39.5508 | 54.9034 | 58.8945 | 59.5748 | 60.1054 | 61.019 | 63.0975 | 64.4888 | 66.2513 | 67.1662 | 67.9711 | 66.4881 | 68.2261 | 70.9584 | 68.885 | 68.885 | 68.885 | 68.885 | 68.885 | 68.885 | 68.885 | 68.885 | 68.885 | 68.885 | 68.885 | 68.885 | 68.885 | 68.885 | 68.885 | 68.885 | 98% | 3.2692 | 42.3438 | 57.5027 | 61.6497 | 62.2913 | 62.6987 | 63.5925 | 65.7034 | 66.856 | 69.0516 | 75.7255 | 70.2235 | 69.1473 | 70.6 | 73.7771 | 71.6266 | 71.6266 | 71.6266 | 71.6266 | 71.6266 | 71.6266 | 71.6266 | 71.6266 | 71.6266 | 71.6266 | 71.6266 | 71.6266 | 71.6266 | 71.6266 | 71.6266 | 71.6266
97% | 6.8356 | 39.1473 | 54.3431 | 58.2935 | 58.9669 | 59.4921 | 60.3964 | 62.4536 | 63.8307 | 65.5753 | 66.4808 | 67.2775 | 65.8096 | 67.5299 | 70.2344 | 68.1821 | 68.1821 | 68.1821 | 68.1821 | 68.1821 | 68.1821 | 68.1821 | 68.1821 | 68.1821 | 68.1821 | 68.1821 | 68.1821 | 68.1821 | 68.1821 | 68.1821 | 68.1821 | 97% | 6.8356 | 41.9118 | 56.916 | 61.0206 | 61.6557 | 62.0589 | 62.9436 | 65.033 | 66.1738 | 68.3469 | 74.9528 | 69.5069 | 68.4417 | 69.8796 | 73.0243 | 70.8957 | 70.8957 | 70.8957 | 70.8957 | 70.8957 | 70.8957 | 70.8957 | 70.8957 | 70.8957 | 70.8957 | 70.8957 | 70.8957 | 70.8957 | 70.8957 | 70.8957 | 70.8957
95% | 17.5347 | 38.3401 | 53.2227 | 57.0916 | 57.7511 | 58.2655 | 59.1511 | 61.1659 | 62.5146 | 64.2232 | 65.1101 | 65.8903 | 64.4527 | 66.1375 | 68.7862 | 66.7762 | 66.7762 | 66.7762 | 66.7762 | 66.7762 | 66.7762 | 66.7762 | 66.7762 | 66.7762 | 66.7762 | 66.7762 | 66.7762 | 66.7762 | 66.7762 | 66.7762 | 66.7762 | 95% | 17.5347 | 41.0476 | 55.7425 | 59.7624 | 60.3844 | 60.7794 | 61.6458 | 63.6921 | 64.8094 | 66.9377 | 73.4073 | 68.0738 | 67.0306 | 68.4388 | 71.5186 | 69.4339 | 69.4339 | 69.4339 | 69.4339 | 69.4339 | 69.4339 | 69.4339 | 69.4339 | 69.4339 | 69.4339 | 69.4339 | 69.4339 | 69.4339 | 69.4339 | 69.4339 | 69.4339
90% | 78.7576 | 36.3222 | 50.4215 | 54.0868 | 54.7116 | 55.1988 | 56.0379 | 57.9467 | 59.2244 | 60.8431 | 61.6833 | 62.4224 | 61.0605 | 62.6566 | 65.1659 | 63.2617 | 63.2617 | 63.2617 | 63.2617 | 63.2617 | 63.2617 | 63.2617 | 63.2617 | 63.2617 | 63.2617 | 63.2617 | 63.2617 | 63.2617 | 63.2617 | 63.2617 | 63.2617 | 90% | 78.7576 | 38.8872 | 52.8086 | 56.617 | 57.2063 | 57.5804 | 58.4013 | 60.3399 | 61.3984 | 63.4147 | 69.5438 | 64.491 | 63.5026 | 64.8368 | 67.7545 | 65.7795 | 65.7795 | 65.7795 | 65.7795 | 65.7795 | 65.7795 | 65.7795 | 65.7795 | 65.7795 | 65.7795 | 65.7795 | 65.7795 | 65.7795 | 65.7795 | 65.7795 | 65.7795
85% | 236.8672 | 34.3043 | 47.6203 | 51.082 | 51.672 | 52.1322 | 52.9246 | 54.7274 | 55.9342 | 57.4629 | 58.2564 | 58.9545 | 57.6682 | 59.1757 | 61.5456 | 59.7472 | 59.7472 | 59.7472 | 59.7472 | 59.7472 | 59.7472 | 59.7472 | 59.7472 | 59.7472 | 59.7472 | 59.7472 | 59.7472 | 59.7472 | 59.7472 | 59.7472 | 59.7472 | 85% | 236.8672 | 36.7268 | 49.8748 | 53.4716 | 54.0282 | 54.3815 | 55.1567 | 56.9877 | 57.9873 | 59.8917 | 65.6803 | 60.9081 | 59.9747 | 61.2347 | 63.9903 | 62.1251 | 62.1251 | 62.1251 | 62.1251 | 62.1251 | 62.1251 | 62.1251 | 62.1251 | 62.1251 | 62.1251 | 62.1251 | 62.1251 | 62.1251 | 62.1251 | 62.1251 | 62.1251
80% | 497.5104 | 32.2864 | 44.8191 | 48.0771 | 48.6325 | 49.0656 | 49.8114 | 51.5081 | 52.6439 | 54.0827 | 54.8296 | 55.4866 | 54.276 | 55.6948 | 57.9252 | 56.2326 | 56.2326 | 56.2326 | 56.2326 | 56.2326 | 56.2326 | 56.2326 | 56.2326 | 56.2326 | 56.2326 | 56.2326 | 56.2326 | 56.2326 | 56.2326 | 56.2326 | 56.2326 | 80% | 497.5104 | 34.5664 | 46.941 | 50.3262 | 50.85 | 51.1826 | 51.9122 | 53.6355 | 54.5763 | 56.3686 | 61.8167 | 57.3253 | 56.4468 | 57.6327 | 60.2262 | 58.4707 | 58.4707 | 58.4707 | 58.4707 | 58.4707 | 58.4707 | 58.4707 | 58.4707 | 58.4707 | 58.4707 | 58.4707 | 58.4707 | 58.4707 | 58.4707 | 58.4707 | 58.4707
75% | 803.6248 | 30.2685 | 42.0179 | 45.0723 | 45.593 | 45.999 | 46.6982 | 48.2889 | 49.3537 | 50.7026 | 51.4027 | 52.0187 | 50.8837 | 52.2138 | 54.3049 | 52.7181 | 52.7181 | 52.7181 | 52.7181 | 52.7181 | 52.7181 | 52.7181 | 52.7181 | 52.7181 | 52.7181 | 52.7181 | 52.7181 | 52.7181 | 52.7181 | 52.7181 | 52.7181 | 75% | 803.6248 | 32.406 | 44.0072 | 47.1809 | 47.6719 | 47.9837 | 48.6677 | 50.2832 | 51.1653 | 52.8456 | 57.9532 | 53.7425 | 52.9189 | 54.0306 | 56.4621 | 54.8163 | 54.8163 | 54.8163 | 54.8163 | 54.8163 | 54.8163 | 54.8163 | 54.8163 | 54.8163 | 54.8163 | 54.8163 | 54.8163 | 54.8163 | 54.8163 | 54.8163 | 54.8163
70% | 1155.2107 | 28.2506 | 39.2167 | 42.0675 | 42.5534 | 42.9324 | 43.585 | 45.0696 | 46.0634 | 47.3224 | 47.9759 | 48.5508 | 47.4915 | 48.7329 | 50.6846 | 49.2035 | 49.2035 | 49.2035 | 49.2035 | 49.2035 | 49.2035 | 49.2035 | 49.2035 | 49.2035 | 49.2035 | 49.2035 | 49.2035 | 49.2035 | 49.2035 | 49.2035 | 49.2035 | 70% | 1155.2107 | 30.2456 | 41.0734 | 44.0355 | 44.4938 | 44.7848 | 45.4232 | 46.931 | 47.7543 | 49.3225 | 54.0896 | 50.1596 | 49.3909 | 50.4286 | 52.6979 | 51.1618 | 51.1618 | 51.1618 | 51.1618 | 51.1618 | 51.1618 | 51.1618 | 51.1618 | 51.1618 | 51.1618 | 51.1618 | 51.1618 | 51.1618 | 51.1618 | 51.1618 | 51.1618
65% | 1553.1596 | 26.2327 | 36.4155 | 39.0627 | 39.5139 | 39.8658 | 40.4718 | 41.8504 | 42.7732 | 43.9422 | 44.549 | 45.0828 | 44.0992 | 45.252 | 47.0643 | 45.689 | 45.689 | 45.689 | 45.689 | 45.689 | 45.689 | 45.689 | 45.689 | 45.689 | 45.689 | 45.689 | 45.689 | 45.689 | 45.689 | 45.689 | 45.689 | 65% | 1553.1596 | 28.0852 | 38.1396 | 40.8901 | 41.3157 | 41.5859 | 42.1787 | 43.5788 | 44.3433 | 45.7995 | 50.2261 | 46.5768 | 45.863 | 46.8266 | 48.9338 | 47.5074 | 47.5074 | 47.5074 | 47.5074 | 47.5074 | 47.5074 | 47.5074 | 47.5074 | 47.5074 | 47.5074 | 47.5074 | 47.5074 | 47.5074 | 47.5074 | 47.5074 | 47.5074
60% | 2026.2996 | 24.2148 | 33.6143 | 36.0579 | 36.4744 | 36.7992 | 37.3586 | 38.6311 | 39.4829 | 40.562 | 41.1222 | 41.6149 | 40.707 | 41.7711 | 43.4439 | 42.1745 | 42.1745 | 42.1745 | 42.1745 | 42.1745 | 42.1745 | 42.1745 | 42.1745 | 42.1745 | 42.1745 | 42.1745 | 42.1745 | 42.1745 | 42.1745 | 42.1745 | 42.1745 | 60% | 2026.2996 | 25.9248 | 35.2058 | 37.7447 | 38.1375 | 38.387 | 38.9342 | 40.2266 | 40.9322 | 42.2765 | 46.3625 | 42.994 | 42.3351 | 43.2245 | 45.1696 | 43.853 | 43.853 | 43.853 | 43.853 | 43.853 | 43.853 | 43.853 | 43.853 | 43.853 | 43.853 | 43.853 | 43.853 | 43.853 | 43.853 | 43.853 | 43.853
55% | 2598.4068 | 22.1969 | 30.8131 | 33.053 | 33.4348 | 33.7326 | 34.2454 | 35.4119 | 36.1927 | 37.1819 | 37.6953 | 38.147 | 37.3147 | 38.2902 | 39.8236 | 38.6599 | 38.6599 | 38.6599 | 38.6599 | 38.6599 | 38.6599 | 38.6599 | 38.6599 | 38.6599 | 38.6599 | 38.6599 | 38.6599 | 38.6599 | 38.6599 | 38.6599 | 38.6599 | 55% | 2598.4068 | 23.7644 | 32.272 | 34.5993 | 34.9594 | 35.188 | 35.6897 | 36.8744 | 37.5212 | 38.7534 | 42.499 | 39.4111 | 38.8072 | 39.6225 | 41.4055 | 40.1986 | 40.1986 | 40.1986 | 40.1986 | 40.1986 | 40.1986 | 40.1986 | 40.1986 | 40.1986 | 40.1986 | 40.1986 | 40.1986 | 40.1986 | 40.1986 | 40.1986 | 40.1986
50% | 3233.5201 | 20.179 | 28.0119 | 30.0482 | 30.3953 | 30.666 | 31.1321 | 32.1926 | 32.9024 | 33.8017 | 34.2685 | 34.6791 | 33.9225 | 34.8092 | 36.2033 | 35.1454 | 35.1454 | 35.1454 | 35.1454 | 35.1454 | 35.1454 | 35.1454 | 35.1454 | 35.1454 | 35.1454 | 35.1454 | 35.1454 | 35.1454 | 35.1454 | 35.1454 | 35.1454 | 50% | 3233.5201 | 21.604 | 29.3381 | 31.4539 | 31.7813 | 31.9891 | 32.4451 | 33.5222 | 34.1102 | 35.2304 | 38.6354 | 35.8283 | 35.2792 | 36.0204 | 37.6414 | 36.5442 | 36.5442 | 36.5442 | 36.5442 | 36.5442 | 36.5442 | 36.5442 | 36.5442 | 36.5442 | 36.5442 | 36.5442 | 36.5442 | 36.5442 | 36.5442 | 36.5442 | 36.5442
45% | 3775.313 | 18.1611 | 25.2107 | 27.0434 | 27.3558 | 27.5994 | 28.0189 | 28.9733 | 29.6122 | 30.4215 | 30.8416 | 31.2112 | 30.5302 | 31.3283 | 32.583 | 31.6309 | 31.6309 | 31.6309 | 31.6309 | 31.6309 | 31.6309 | 31.6309 | 31.6309 | 31.6309 | 31.6309 | 31.6309 | 31.6309 | 31.6309 | 31.6309 | 31.6309 | 31.6309 | 45% | 3775.313 | 19.4436 | 26.4043 | 28.3085 | 28.6031 | 28.7902 | 29.2006 | 30.1699 | 30.6992 | 31.7073 | 34.7719 | 32.2455 | 31.7513 | 32.4184 | 33.8772 | 32.8898 | 32.8898 | 32.8898 | 32.8898 | 32.8898 | 32.8898 | 32.8898 | 32.8898 | 32.8898 | 32.8898 | 32.8898 | 32.8898 | 32.8898 | 32.8898 | 32.8898 | 32.8898
40% | 4072.8088 | 16.1432 | 22.4095 | 24.0386 | 24.3162 | 24.5328 | 24.9057 | 25.7541 | 26.322 | 27.0414 | 27.4148 | 27.7433 | 27.138 | 27.8474 | 28.9626 | 28.1163 | 28.1163 | 28.1163 | 28.1163 | 28.1163 | 28.1163 | 28.1163 | 28.1163 | 28.1163 | 28.1163 | 28.1163 | 28.1163 | 28.1163 | 28.1163 | 28.1163 | 28.1163 | 40% | 4072.8088 | 17.2832 | 23.4705 | 25.1631 | 25.425 | 25.5913 | 25.9561 | 26.8177 | 27.2882 | 28.1843 | 30.9084 | 28.6627 | 28.2234 | 28.8163 | 30.1131 | 29.2353 | 29.2353 | 29.2353 | 29.2353 | 29.2353 | 29.2353 | 29.2353 | 29.2353 | 29.2353 | 29.2353 | 29.2353 | 29.2353 | 29.2353 | 29.2353 | 29.2353 | 29.2353
35% | 4198.821 | 14.1253 | 19.6083 | 21.0337 | 21.2767 | 21.4662 | 21.7925 | 22.5348 | 23.0317 | 23.6612 | 23.9879 | 24.2754 | 23.7457 | 24.3665 | 25.3423 | 24.6018 | 24.6018 | 24.6018 | 24.6018 | 24.6018 | 24.6018 | 24.6018 | 24.6018 | 24.6018 | 24.6018 | 24.6018 | 24.6018 | 24.6018 | 24.6018 | 24.6018 | 24.6018 | 35% | 4198.821 | 15.1228 | 20.5367 | 22.0177 | 22.2469 | 22.3924 | 22.7116 | 23.4655 | 23.8771 | 24.6613 | 27.0448 | 25.0798 | 24.6955 | 25.2143 | 26.349 | 25.5809 | 25.5809 | 25.5809 | 25.5809 | 25.5809 | 25.5809 | 25.5809 | 25.5809 | 25.5809 | 25.5809 | 25.5809 | 25.5809 | 25.5809 | 25.5809 | 25.5809 | 25.5809
30% | 4271.3374 | 12.1074 | 16.8072 | 18.0289 | 18.2372 | 18.3996 | 18.6793 | 19.3156 | 19.7415 | 20.281 | 20.5611 | 20.8075 | 20.3535 | 20.8855 | 21.722 | 21.0872 | 21.0872 | 21.0872 | 21.0872 | 21.0872 | 21.0872 | 21.0872 | 21.0872 | 21.0872 | 21.0872 | 21.0872 | 21.0872 | 21.0872 | 21.0872 | 21.0872 | 21.0872 | 30% | 4271.3374 | 12.9624 | 17.6029 | 18.8723 | 19.0688 | 19.1935 | 19.4671 | 20.1133 | 20.4661 | 21.1382 | 23.1813 | 21.497 | 21.1675 | 21.6123 | 22.5848 | 21.9265 | 21.9265 | 21.9265 | 21.9265 | 21.9265 | 21.9265 | 21.9265 | 21.9265 | 21.9265 | 21.9265 | 21.9265 | 21.9265 | 21.9265 | 21.9265 | 21.9265 | 21.9265
25% | 4321.8611 | 10.0895 | 14.006 | 15.0241 | 15.1977 | 15.333 | 15.5661 | 16.0963 | 16.4512 | 16.9009 | 17.1342 | 17.3396 | 16.9612 | 17.4046 | 18.1016 | 17.5727 | 17.5727 | 17.5727 | 17.5727 | 17.5727 | 17.5727 | 17.5727 | 17.5727 | 17.5727 | 17.5727 | 17.5727 | 17.5727 | 17.5727 | 17.5727 | 17.5727 | 17.5727 | 25% | 4321.8611 | 10.802 | 14.6691 | 15.727 | 15.8906 | 15.9946 | 16.2226 | 16.7611 | 17.0551 | 17.6152 | 19.3177 | 17.9142 | 17.6396 | 18.0102 | 18.8207 | 18.2721 | 18.2721 | 18.2721 | 18.2721 | 18.2721 | 18.2721 | 18.2721 | 18.2721 | 18.2721 | 18.2721 | 18.2721 | 18.2721 | 18.2721 | 18.2721 | 18.2721 | 18.2721
20% | 4353.067 | 8.0716 | 11.2048 | 12.0193 | 12.1581 | 12.2664 | 12.4529 | 12.877 | 13.161 | 13.5207 | 13.7074 | 13.8716 | 13.569 | 13.9237 | 14.4813 | 14.0582 | 14.0582 | 14.0582 | 14.0582 | 14.0582 | 14.0582 | 14.0582 | 14.0582 | 14.0582 | 14.0582 | 14.0582 | 14.0582 | 14.0582 | 14.0582 | 14.0582 | 14.0582 | 20% | 4353.067 | 8.6416 | 11.7353 | 12.5816 | 12.7125 | 12.7957 | 12.9781 | 13.4089 | 13.6441 | 14.0922 | 15.4542 | 14.3313 | 14.1117 | 14.4082 | 15.0565 | 14.6177 | 14.6177 | 14.6177 | 14.6177 | 14.6177 | 14.6177 | 14.6177 | 14.6177 | 14.6177 | 14.6177 | 14.6177 | 14.6177 | 14.6177 | 14.6177 | 14.6177 | 14.6177
15% | 4369.4129 | 6.0537 | 8.4036 | 9.0145 | 9.1186 | 9.1998 | 9.3396 | 9.6578 | 9.8707 | 10.1405 | 10.2805 | 10.4037 | 10.1767 | 10.4428 | 10.861 | 10.5436 | 10.5436 | 10.5436 | 10.5436 | 10.5436 | 10.5436 | 10.5436 | 10.5436 | 10.5436 | 10.5436 | 10.5436 | 10.5436 | 10.5436 | 10.5436 | 10.5436 | 10.5436 | 15% | 4369.4129 | 6.4812 | 8.8014 | 9.4362 | 9.5344 | 9.5967 | 9.7335 | 10.0566 | 10.2331 | 10.5691 | 11.5906 | 10.7485 | 10.5838 | 10.8061 | 11.2924 | 10.9633 | 10.9633 | 10.9633 | 10.9633 | 10.9633 | 10.9633 | 10.9633 | 10.9633 | 10.9633 | 10.9633 | 10.9633 | 10.9633 | 10.9633 | 10.9633 | 10.9633 | 10.9633
10% | 4378.6261 | 4.0358 | 5.6024 | 6.0096 | 6.0791 | 6.1332 | 6.2264 | 6.4385 | 6.5805 | 6.7603 | 6.8537 | 6.9358 | 6.7845 | 6.9618 | 7.2407 | 7.0291 | 7.0291 | 7.0291 | 7.0291 | 7.0291 | 7.0291 | 7.0291 | 7.0291 | 7.0291 | 7.0291 | 7.0291 | 7.0291 | 7.0291 | 7.0291 | 7.0291 | 7.0291 | 10% | 4378.6261 | 4.3208 | 5.8676 | 6.2908 | 6.3563 | 6.3978 | 6.489 | 6.7044 | 6.822 | 7.0461 | 7.7271 | 7.1657 | 7.0558 | 7.2041 | 7.5283 | 7.3088 | 7.3088 | 7.3088 | 7.3088 | 7.3088 | 7.3088 | 7.3088 | 7.3088 | 7.3088 | 7.3088 | 7.3088 | 7.3088 | 7.3088 | 7.3088 | 7.3088 | 7.3088
5% | 4391.7028 | 2.0179 | 2.8012 | 3.0048 | 3.0395 | 3.0666 | 3.1132 | 3.2193 | 3.2902 | 3.3802 | 3.4268 | 3.4679 | 3.3922 | 3.4809 | 3.6203 | 3.5145 | 3.5145 | 3.5145 | 3.5145 | 3.5145 | 3.5145 | 3.5145 | 3.5145 | 3.5145 | 3.5145 | 3.5145 | 3.5145 | 3.5145 | 3.5145 | 3.5145 | 3.5145 | 5% | 4391.7028 | 2.1604 | 2.9338 | 3.1454 | 3.1781 | 3.1989 | 3.2445 | 3.3522 | 3.411 | 3.523 | 3.8635 | 3.5828 | 3.5279 | 3.602 | 3.7641 | 3.6544 | 3.6544 | 3.6544 | 3.6544 | 3.6544 | 3.6544 | 3.6544 | 3.6544 | 3.6544 | 3.6544 | 3.6544 | 3.6544 | 3.6544 | 3.6544 | 3.6544 | 3.6544
9.992e-14% | 4391.7028 | 4.0326e-14 | 5.5979e-14 | 6.0048e-14 | 6.0742e-14 | 6.1283e-14 | 6.2215e-14 | 6.4334e-14 | 6.5752e-14 | 6.7549e-14 | 6.8482e-14 | 6.9303e-14 | 6.7791e-14 | 6.9563e-14 | 7.2349e-14 | 7.0235e-14 | 7.0235e-14 | 7.0235e-14 | 7.0235e-14 | 7.0235e-14 | 7.0235e-14 | 7.0235e-14 | 7.0235e-14 | 7.0235e-14 | 7.0235e-14 | 7.0235e-14 | 7.0235e-14 | 7.0235e-14 | 7.0235e-14 | 7.0235e-14 | 7.0235e-14 | 9.992e-14% | 4391.7028 | 4.3173e-14 | 5.8629e-14 | 6.2858e-14 | 6.3512e-14 | 6.3927e-14 | 6.4838e-14 | 6.6991e-14 | 6.8166e-14 | 7.0404e-14 | 7.7209e-14 | 7.1599e-14 | 7.0502e-14 | 7.1983e-14 | 7.5223e-14 | 7.303e-14 | 7.303e-14 | 7.303e-14 | 7.303e-14 | 7.303e-14 | 7.303e-14 | 7.303e-14 | 7.303e-14 | 7.303e-14 | 7.303e-14 | 7.303e-14 | 7.303e-14 | 7.303e-14 | 7.303e-14 | 7.303e-14 | 7.303e-14
Summer Season | [31 empty] | Summer Season
P50 | [31 empty] | P10
% of MD | Summer - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Summer - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 45.8759 | 60.9589 | 65.0674 | 64.9499 | 64.9485 | 65.4184 | 65.9338 | 66.9909 | 67.7504 | 68.1633 | 68.6157 | 69.029 | 69.7743 | 70.6989 | 70.6364 | 70.6364 | 70.6364 | 70.6364 | 70.6364 | 70.6364 | 70.6364 | 70.6364 | 70.6364 | 70.6364 | 70.6364 | 70.6364 | 70.6364 | 70.6364 | 70.6364 | 70.6364 | 100% | 0 | 51.1554 | 66.2686 | 70.2261 | 69.9907 | 70.0105 | 70.4179 | 71.4905 | 72.2097 | 72.9132 | 73.7356 | 74.4985 | 75.2386 | 75.3243 | 76.1878 | 75.5357 | 75.5357 | 75.5357 | 75.5357 | 75.5357 | 75.5357 | 75.5357 | 75.5357 | 75.5357 | 75.5357 | 75.5357 | 75.5357 | 75.5357 | 75.5357 | 75.5357 | 75.5357
99% | 0 | 45.4171 | 60.3493 | 64.4168 | 64.3004 | 64.299 | 64.7642 | 65.2745 | 66.321 | 67.0729 | 67.4817 | 67.9295 | 68.3387 | 69.0766 | 69.9919 | 69.93 | 69.93 | 69.93 | 69.93 | 69.93 | 69.93 | 69.93 | 69.93 | 69.93 | 69.93 | 69.93 | 69.93 | 69.93 | 69.93 | 69.93 | 69.93 | 99% | 1.5127 | 50.6438 | 65.6059 | 69.5238 | 69.2908 | 69.3104 | 69.7137 | 70.7756 | 71.4876 | 72.184 | 72.9983 | 73.7535 | 74.4862 | 74.571 | 75.4259 | 74.7803 | 74.7803 | 74.7803 | 74.7803 | 74.7803 | 74.7803 | 74.7803 | 74.7803 | 74.7803 | 74.7803 | 74.7803 | 74.7803 | 74.7803 | 74.7803 | 74.7803 | 74.7803
98% | 0 | 44.9584 | 59.7397 | 63.7661 | 63.6509 | 63.6495 | 64.11 | 64.6151 | 65.6511 | 66.3954 | 66.8001 | 67.2434 | 67.6484 | 68.3788 | 69.2849 | 69.2236 | 69.2236 | 69.2236 | 69.2236 | 69.2236 | 69.2236 | 69.2236 | 69.2236 | 69.2236 | 69.2236 | 69.2236 | 69.2236 | 69.2236 | 69.2236 | 69.2236 | 69.2236 | 98% | 2.269 | 50.1322 | 64.9433 | 68.8216 | 68.5909 | 68.6103 | 69.0096 | 70.0607 | 70.7655 | 71.4549 | 72.2609 | 73.0085 | 73.7338 | 73.8178 | 74.664 | 74.0249 | 74.0249 | 74.0249 | 74.0249 | 74.0249 | 74.0249 | 74.0249 | 74.0249 | 74.0249 | 74.0249 | 74.0249 | 74.0249 | 74.0249 | 74.0249 | 74.0249 | 74.0249
97% | 0.37816 | 44.4996 | 59.1301 | 63.1154 | 63.0014 | 63 | 63.4558 | 63.9558 | 64.9812 | 65.7179 | 66.1184 | 66.5572 | 66.9581 | 67.6811 | 68.5779 | 68.5173 | 68.5173 | 68.5173 | 68.5173 | 68.5173 | 68.5173 | 68.5173 | 68.5173 | 68.5173 | 68.5173 | 68.5173 | 68.5173 | 68.5173 | 68.5173 | 68.5173 | 68.5173 | 97% | 3.7816 | 49.6207 | 64.2806 | 68.1193 | 67.891 | 67.9102 | 68.3054 | 69.3458 | 70.0434 | 70.7258 | 71.5236 | 72.2636 | 72.9814 | 73.0646 | 73.9022 | 73.2696 | 73.2696 | 73.2696 | 73.2696 | 73.2696 | 73.2696 | 73.2696 | 73.2696 | 73.2696 | 73.2696 | 73.2696 | 73.2696 | 73.2696 | 73.2696 | 73.2696 | 73.2696
95% | 2.269 | 43.5821 | 57.911 | 61.8141 | 61.7024 | 61.701 | 62.1474 | 62.6371 | 63.6414 | 64.3629 | 64.7552 | 65.1849 | 65.5776 | 66.2856 | 67.1639 | 67.1046 | 67.1046 | 67.1046 | 67.1046 | 67.1046 | 67.1046 | 67.1046 | 67.1046 | 67.1046 | 67.1046 | 67.1046 | 67.1046 | 67.1046 | 67.1046 | 67.1046 | 67.1046 | 95% | 6.0506 | 48.5976 | 62.9552 | 66.7148 | 66.4912 | 66.51 | 66.897 | 67.916 | 68.5992 | 69.2675 | 70.0488 | 70.7736 | 71.4766 | 71.5581 | 72.3784 | 71.7589 | 71.7589 | 71.7589 | 71.7589 | 71.7589 | 71.7589 | 71.7589 | 71.7589 | 71.7589 | 71.7589 | 71.7589 | 71.7589 | 71.7589 | 71.7589 | 71.7589 | 71.7589
90% | 5.6725 | 41.2883 | 54.863 | 58.5607 | 58.4549 | 58.4536 | 58.8765 | 59.3404 | 60.2918 | 60.9754 | 61.347 | 61.7541 | 62.1261 | 62.7969 | 63.629 | 63.5727 | 63.5727 | 63.5727 | 63.5727 | 63.5727 | 63.5727 | 63.5727 | 63.5727 | 63.5727 | 63.5727 | 63.5727 | 63.5727 | 63.5727 | 63.5727 | 63.5727 | 63.5727 | 90% | 16.2611 | 46.0398 | 59.6418 | 63.2035 | 62.9917 | 63.0094 | 63.3761 | 64.3415 | 64.9887 | 65.6218 | 66.3621 | 67.0487 | 67.7147 | 67.7919 | 68.569 | 67.9821 | 67.9821 | 67.9821 | 67.9821 | 67.9821 | 67.9821 | 67.9821 | 67.9821 | 67.9821 | 67.9821 | 67.9821 | 67.9821 | 67.9821 | 67.9821 | 67.9821 | 67.9821
85% | 15.8829 | 38.9945 | 51.8151 | 55.3073 | 55.2074 | 55.2062 | 55.6056 | 56.0437 | 56.9423 | 57.5879 | 57.9388 | 58.3233 | 58.6747 | 59.3082 | 60.094 | 60.0409 | 60.0409 | 60.0409 | 60.0409 | 60.0409 | 60.0409 | 60.0409 | 60.0409 | 60.0409 | 60.0409 | 60.0409 | 60.0409 | 60.0409 | 60.0409 | 60.0409 | 60.0409 | 85% | 26.4715 | 43.482 | 56.3283 | 59.6922 | 59.4921 | 59.5089 | 59.8552 | 60.767 | 61.3783 | 61.9762 | 62.6753 | 63.3237 | 63.9528 | 64.0256 | 64.7596 | 64.2053 | 64.2053 | 64.2053 | 64.2053 | 64.2053 | 64.2053 | 64.2053 | 64.2053 | 64.2053 | 64.2053 | 64.2053 | 64.2053 | 64.2053 | 64.2053 | 64.2053 | 64.2053
80% | 31.0095 | 36.7007 | 48.7671 | 52.0539 | 51.9599 | 51.9588 | 52.3347 | 52.747 | 53.5928 | 54.2003 | 54.5307 | 54.8925 | 55.2232 | 55.8194 | 56.5591 | 56.5091 | 56.5091 | 56.5091 | 56.5091 | 56.5091 | 56.5091 | 56.5091 | 56.5091 | 56.5091 | 56.5091 | 56.5091 | 56.5091 | 56.5091 | 56.5091 | 56.5091 | 56.5091 | 80% | 34.0348 | 40.9243 | 53.0149 | 56.1809 | 55.9926 | 56.0084 | 56.3343 | 57.1924 | 57.7678 | 58.3305 | 58.9885 | 59.5988 | 60.1908 | 60.2594 | 60.9502 | 60.4285 | 60.4285 | 60.4285 | 60.4285 | 60.4285 | 60.4285 | 60.4285 | 60.4285 | 60.4285 | 60.4285 | 60.4285 | 60.4285 | 60.4285 | 60.4285 | 60.4285 | 60.4285
75% | 72.9857 | 34.4069 | 45.7192 | 48.8006 | 48.7124 | 48.7113 | 49.0638 | 49.4504 | 50.2432 | 50.8128 | 51.1225 | 51.4618 | 51.7718 | 52.3307 | 53.0241 | 52.9773 | 52.9773 | 52.9773 | 52.9773 | 52.9773 | 52.9773 | 52.9773 | 52.9773 | 52.9773 | 52.9773 | 52.9773 | 52.9773 | 52.9773 | 52.9773 | 52.9773 | 52.9773 | 75% | 48.405 | 38.3665 | 49.7015 | 52.6696 | 52.493 | 52.5079 | 52.8134 | 53.6179 | 54.1573 | 54.6849 | 55.3017 | 55.8739 | 56.4289 | 56.4932 | 57.1408 | 56.6517 | 56.6517 | 56.6517 | 56.6517 | 56.6517 | 56.6517 | 56.6517 | 56.6517 | 56.6517 | 56.6517 | 56.6517 | 56.6517 | 56.6517 | 56.6517 | 56.6517 | 56.6517
70% | 150.5094 | 32.1131 | 42.6712 | 45.5472 | 45.4649 | 45.4639 | 45.7929 | 46.1537 | 46.8937 | 47.4253 | 47.7143 | 48.031 | 48.3203 | 48.842 | 49.4892 | 49.4455 | 49.4455 | 49.4455 | 49.4455 | 49.4455 | 49.4455 | 49.4455 | 49.4455 | 49.4455 | 49.4455 | 49.4455 | 49.4455 | 49.4455 | 49.4455 | 49.4455 | 49.4455 | 70% | 76.3892 | 35.8087 | 46.388 | 49.1583 | 48.9935 | 49.0073 | 49.2925 | 50.0434 | 50.5468 | 51.0392 | 51.6149 | 52.149 | 52.667 | 52.727 | 53.3315 | 52.875 | 52.875 | 52.875 | 52.875 | 52.875 | 52.875 | 52.875 | 52.875 | 52.875 | 52.875 | 52.875 | 52.875 | 52.875 | 52.875 | 52.875 | 52.875
65% | 359.6342 | 29.8193 | 39.6233 | 42.2938 | 42.2174 | 42.2165 | 42.5219 | 42.857 | 43.5441 | 44.0378 | 44.3062 | 44.6002 | 44.8689 | 45.3533 | 45.9543 | 45.9136 | 45.9136 | 45.9136 | 45.9136 | 45.9136 | 45.9136 | 45.9136 | 45.9136 | 45.9136 | 45.9136 | 45.9136 | 45.9136 | 45.9136 | 45.9136 | 45.9136 | 45.9136 | 65% | 114.2056 | 33.251 | 43.0746 | 45.647 | 45.494 | 45.5068 | 45.7716 | 46.4689 | 46.9363 | 47.3936 | 47.9282 | 48.424 | 48.9051 | 48.9608 | 49.5221 | 49.0982 | 49.0982 | 49.0982 | 49.0982 | 49.0982 | 49.0982 | 49.0982 | 49.0982 | 49.0982 | 49.0982 | 49.0982 | 49.0982 | 49.0982 | 49.0982 | 49.0982 | 49.0982
60% | 689.7717 | 27.5255 | 36.5753 | 39.0405 | 38.9699 | 38.9691 | 39.251 | 39.5603 | 40.1946 | 40.6503 | 40.898 | 41.1694 | 41.4174 | 41.8646 | 42.4193 | 42.3818 | 42.3818 | 42.3818 | 42.3818 | 42.3818 | 42.3818 | 42.3818 | 42.3818 | 42.3818 | 42.3818 | 42.3818 | 42.3818 | 42.3818 | 42.3818 | 42.3818 | 42.3818 | 60% | 178.1154 | 30.6932 | 39.7612 | 42.1357 | 41.9944 | 42.0063 | 42.2508 | 42.8943 | 43.3258 | 43.7479 | 44.2414 | 44.6991 | 45.1431 | 45.1946 | 45.7127 | 45.3214 | 45.3214 | 45.3214 | 45.3214 | 45.3214 | 45.3214 | 45.3214 | 45.3214 | 45.3214 | 45.3214 | 45.3214 | 45.3214 | 45.3214 | 45.3214 | 45.3214 | 45.3214
55% | 1095.5419 | 25.2317 | 33.5274 | 35.7871 | 35.7224 | 35.7217 | 35.9801 | 36.2636 | 36.845 | 37.2627 | 37.4898 | 37.7386 | 37.966 | 38.3759 | 38.8844 | 38.85 | 38.85 | 38.85 | 38.85 | 38.85 | 38.85 | 38.85 | 38.85 | 38.85 | 38.85 | 38.85 | 38.85 | 38.85 | 38.85 | 38.85 | 38.85 | 55% | 311.6074 | 28.1354 | 36.4477 | 38.6243 | 38.4949 | 38.5058 | 38.7299 | 39.3198 | 39.7153 | 40.1022 | 40.5546 | 40.9742 | 41.3812 | 41.4284 | 41.9033 | 41.5446 | 41.5446 | 41.5446 | 41.5446 | 41.5446 | 41.5446 | 41.5446 | 41.5446 | 41.5446 | 41.5446 | 41.5446 | 41.5446 | 41.5446 | 41.5446 | 41.5446 | 41.5446
50% | 1666.1918 | 22.9379 | 30.4794 | 32.5337 | 32.4749 | 32.4742 | 32.7092 | 32.9669 | 33.4955 | 33.8752 | 34.0817 | 34.3078 | 34.5145 | 34.8872 | 35.3494 | 35.3182 | 35.3182 | 35.3182 | 35.3182 | 35.3182 | 35.3182 | 35.3182 | 35.3182 | 35.3182 | 35.3182 | 35.3182 | 35.3182 | 35.3182 | 35.3182 | 35.3182 | 35.3182 | 50% | 636.0723 | 25.5777 | 33.1343 | 35.113 | 34.9954 | 35.0052 | 35.209 | 35.7453 | 36.1049 | 36.4566 | 36.8678 | 37.2493 | 37.6193 | 37.6621 | 38.0939 | 37.7678 | 37.7678 | 37.7678 | 37.7678 | 37.7678 | 37.7678 | 37.7678 | 37.7678 | 37.7678 | 37.7678 | 37.7678 | 37.7678 | 37.7678 | 37.7678 | 37.7678 | 37.7678
45% | 2506.0947 | 20.6442 | 27.4315 | 29.2803 | 29.2274 | 29.2268 | 29.4383 | 29.6702 | 30.1459 | 30.4877 | 30.6735 | 30.8771 | 31.0631 | 31.3984 | 31.8145 | 31.7864 | 31.7864 | 31.7864 | 31.7864 | 31.7864 | 31.7864 | 31.7864 | 31.7864 | 31.7864 | 31.7864 | 31.7864 | 31.7864 | 31.7864 | 31.7864 | 31.7864 | 31.7864 | 45% | 1179.4944 | 23.0199 | 29.8209 | 31.6017 | 31.4958 | 31.5047 | 31.6881 | 32.1707 | 32.4944 | 32.8109 | 33.181 | 33.5243 | 33.8573 | 33.8959 | 34.2845 | 33.991 | 33.991 | 33.991 | 33.991 | 33.991 | 33.991 | 33.991 | 33.991 | 33.991 | 33.991 | 33.991 | 33.991 | 33.991 | 33.991 | 33.991 | 33.991
40% | 3164.4787 | 18.3504 | 24.3836 | 26.027 | 25.9799 | 25.9794 | 26.1673 | 26.3735 | 26.7964 | 27.1002 | 27.2653 | 27.4463 | 27.6116 | 27.9097 | 28.2795 | 28.2546 | 28.2546 | 28.2546 | 28.2546 | 28.2546 | 28.2546 | 28.2546 | 28.2546 | 28.2546 | 28.2546 | 28.2546 | 28.2546 | 28.2546 | 28.2546 | 28.2546 | 28.2546 | 40% | 1808.3816 | 20.4621 | 26.5075 | 28.0904 | 27.9963 | 28.0042 | 28.1672 | 28.5962 | 28.8839 | 29.1653 | 29.4942 | 29.7994 | 30.0954 | 30.1297 | 30.4751 | 30.2143 | 30.2143 | 30.2143 | 30.2143 | 30.2143 | 30.2143 | 30.2143 | 30.2143 | 30.2143 | 30.2143 | 30.2143 | 30.2143 | 30.2143 | 30.2143 | 30.2143 | 30.2143
35% | 3551.3408 | 16.0566 | 21.3356 | 22.7736 | 22.7325 | 22.732 | 22.8964 | 23.0768 | 23.4468 | 23.7126 | 23.8572 | 24.0155 | 24.1602 | 24.421 | 24.7446 | 24.7227 | 24.7227 | 24.7227 | 24.7227 | 24.7227 | 24.7227 | 24.7227 | 24.7227 | 24.7227 | 24.7227 | 24.7227 | 24.7227 | 24.7227 | 24.7227 | 24.7227 | 24.7227 | 35% | 2779.1293 | 17.9044 | 23.194 | 24.5791 | 24.4968 | 24.5037 | 24.6463 | 25.0217 | 25.2734 | 25.5196 | 25.8075 | 26.0745 | 26.3335 | 26.3635 | 26.6657 | 26.4375 | 26.4375 | 26.4375 | 26.4375 | 26.4375 | 26.4375 | 26.4375 | 26.4375 | 26.4375 | 26.4375 | 26.4375 | 26.4375 | 26.4375 | 26.4375 | 26.4375 | 26.4375
30% | 3758.953 | 13.7628 | 18.2877 | 19.5202 | 19.485 | 19.4845 | 19.6255 | 19.7801 | 20.0973 | 20.3251 | 20.449 | 20.5847 | 20.7087 | 20.9323 | 21.2097 | 21.1909 | 21.1909 | 21.1909 | 21.1909 | 21.1909 | 21.1909 | 21.1909 | 21.1909 | 21.1909 | 21.1909 | 21.1909 | 21.1909 | 21.1909 | 21.1909 | 21.1909 | 21.1909 | 30% | 3814.165 | 15.3466 | 19.8806 | 21.0678 | 20.9972 | 21.0031 | 21.1254 | 21.4472 | 21.6629 | 21.8739 | 22.1207 | 22.3496 | 22.5716 | 22.5973 | 22.8563 | 22.6607 | 22.6607 | 22.6607 | 22.6607 | 22.6607 | 22.6607 | 22.6607 | 22.6607 | 22.6607 | 22.6607 | 22.6607 | 22.6607 | 22.6607 | 22.6607 | 22.6607 | 22.6607
25% | 3926.4798 | 11.469 | 15.2397 | 16.2669 | 16.2375 | 16.2371 | 16.3546 | 16.4835 | 16.7477 | 16.9376 | 17.0408 | 17.1539 | 17.2573 | 17.4436 | 17.6747 | 17.6591 | 17.6591 | 17.6591 | 17.6591 | 17.6591 | 17.6591 | 17.6591 | 17.6591 | 17.6591 | 17.6591 | 17.6591 | 17.6591 | 17.6591 | 17.6591 | 17.6591 | 17.6591 | 25% | 4166.9923 | 12.7888 | 16.5672 | 17.5565 | 17.4977 | 17.5026 | 17.6045 | 17.8726 | 18.0524 | 18.2283 | 18.4339 | 18.6246 | 18.8096 | 18.8311 | 19.0469 | 18.8839 | 18.8839 | 18.8839 | 18.8839 | 18.8839 | 18.8839 | 18.8839 | 18.8839 | 18.8839 | 18.8839 | 18.8839 | 18.8839 | 18.8839 | 18.8839 | 18.8839 | 18.8839
20% | 4050.5177 | 9.1752 | 12.1918 | 13.0135 | 12.99 | 12.9897 | 13.0837 | 13.1868 | 13.3982 | 13.5501 | 13.6327 | 13.7231 | 13.8058 | 13.9549 | 14.1398 | 14.1273 | 14.1273 | 14.1273 | 14.1273 | 14.1273 | 14.1273 | 14.1273 | 14.1273 | 14.1273 | 14.1273 | 14.1273 | 14.1273 | 14.1273 | 14.1273 | 14.1273 | 14.1273 | 20% | 4282.7105 | 10.2311 | 13.2537 | 14.0452 | 13.9981 | 14.0021 | 14.0836 | 14.2981 | 14.4419 | 14.5826 | 14.7471 | 14.8997 | 15.0477 | 15.0649 | 15.2376 | 15.1071 | 15.1071 | 15.1071 | 15.1071 | 15.1071 | 15.1071 | 15.1071 | 15.1071 | 15.1071 | 15.1071 | 15.1071 | 15.1071 | 15.1071 | 15.1071 | 15.1071 | 15.1071
15% | 4152.622 | 6.8814 | 9.1438 | 9.7601 | 9.7425 | 9.7423 | 9.8128 | 9.8901 | 10.0486 | 10.1626 | 10.2245 | 10.2924 | 10.3544 | 10.4661 | 10.6048 | 10.5955 | 10.5955 | 10.5955 | 10.5955 | 10.5955 | 10.5955 | 10.5955 | 10.5955 | 10.5955 | 10.5955 | 10.5955 | 10.5955 | 10.5955 | 10.5955 | 10.5955 | 10.5955 | 15% | 4364.7722 | 7.6733 | 9.9403 | 10.5339 | 10.4986 | 10.5016 | 10.5627 | 10.7236 | 10.8315 | 10.937 | 11.0603 | 11.1748 | 11.2858 | 11.2986 | 11.4282 | 11.3303 | 11.3303 | 11.3303 | 11.3303 | 11.3303 | 11.3303 | 11.3303 | 11.3303 | 11.3303 | 11.3303 | 11.3303 | 11.3303 | 11.3303 | 11.3303 | 11.3303 | 11.3303
10% | 4248.2976 | 4.5876 | 6.0959 | 6.5067 | 6.495 | 6.4948 | 6.5418 | 6.5934 | 6.6991 | 6.775 | 6.8163 | 6.8616 | 6.9029 | 6.9774 | 7.0699 | 7.0636 | 7.0636 | 7.0636 | 7.0636 | 7.0636 | 7.0636 | 7.0636 | 7.0636 | 7.0636 | 7.0636 | 7.0636 | 7.0636 | 7.0636 | 7.0636 | 7.0636 | 7.0636 | 10% | 4391.6218 | 5.1155 | 6.6269 | 7.0226 | 6.9991 | 7.001 | 7.0418 | 7.1491 | 7.221 | 7.2913 | 7.3736 | 7.4499 | 7.5239 | 7.5324 | 7.6188 | 7.5536 | 7.5536 | 7.5536 | 7.5536 | 7.5536 | 7.5536 | 7.5536 | 7.5536 | 7.5536 | 7.5536 | 7.5536 | 7.5536 | 7.5536 | 7.5536 | 7.5536 | 7.5536
5% | 4361.7469 | 2.2938 | 3.0479 | 3.2534 | 3.2475 | 3.2474 | 3.2709 | 3.2967 | 3.3495 | 3.3875 | 3.4082 | 3.4308 | 3.4515 | 3.4887 | 3.5349 | 3.5318 | 3.5318 | 3.5318 | 3.5318 | 3.5318 | 3.5318 | 3.5318 | 3.5318 | 3.5318 | 3.5318 | 3.5318 | 3.5318 | 3.5318 | 3.5318 | 3.5318 | 3.5318 | 5% | 4391.6218 | 2.5578 | 3.3134 | 3.5113 | 3.4995 | 3.5005 | 3.5209 | 3.5745 | 3.6105 | 3.6457 | 3.6868 | 3.7249 | 3.7619 | 3.7662 | 3.8094 | 3.7768 | 3.7768 | 3.7768 | 3.7768 | 3.7768 | 3.7768 | 3.7768 | 3.7768 | 3.7768 | 3.7768 | 3.7768 | 3.7768 | 3.7768 | 3.7768 | 3.7768 | 3.7768
9.992e-14% | 4391.6218 | 4.5839e-14 | 6.091e-14 | 6.5015e-14 | 6.4898e-14 | 6.4897e-14 | 6.5366e-14 | 6.5881e-14 | 6.6937e-14 | 6.7696e-14 | 6.8109e-14 | 6.8561e-14 | 6.8974e-14 | 6.9719e-14 | 7.0642e-14 | 7.058e-14 | 7.058e-14 | 7.058e-14 | 7.058e-14 | 7.058e-14 | 7.058e-14 | 7.058e-14 | 7.058e-14 | 7.058e-14 | 7.058e-14 | 7.058e-14 | 7.058e-14 | 7.058e-14 | 7.058e-14 | 7.058e-14 | 7.058e-14 | 9.992e-14% | 4391.6218 | 5.1114e-14 | 6.6216e-14 | 7.017e-14 | 6.9935e-14 | 6.9955e-14 | 7.0362e-14 | 7.1433e-14 | 7.2152e-14 | 7.2855e-14 | 7.3677e-14 | 7.4439e-14 | 7.5178e-14 | 7.5264e-14 | 7.6127e-14 | 7.5475e-14 | 7.5475e-14 | 7.5475e-14 | 7.5475e-14 | 7.5475e-14 | 7.5475e-14 | 7.5475e-14 | 7.5475e-14 | 7.5475e-14 | 7.5475e-14 | 7.5475e-14 | 7.5475e-14 | 7.5475e-14 | 7.5475e-14 | 7.5475e-14 | 7.5475e-14
Option 7
Winter Season | [31 empty] | Winter Season
P50 | [31 empty] | P10
% of MD | Winter - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Winter - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 40.358 | 56.0239 | 60.0964 | 60.7906 | 61.3321 | 62.2643 | 64.3852 | 65.8049 | 67.6034 | 68.5369 | 69.3582 | 67.845 | 69.6185 | 72.4066 | 70.2908 | 70.2908 | 70.2908 | 70.2908 | 70.2908 | 70.2908 | 70.2908 | 70.2908 | 70.2908 | 70.2908 | 70.2908 | 70.2908 | 70.2908 | 70.2908 | 70.2908 | 70.2908 | 100% | 0 | 43.208 | 58.6763 | 62.9078 | 63.5625 | 63.9783 | 64.8903 | 67.0443 | 68.2204 | 70.4608 | 77.2709 | 71.6566 | 70.5585 | 72.0408 | 75.2827 | 73.0883 | 73.0883 | 73.0883 | 73.0883 | 73.0883 | 73.0883 | 73.0883 | 73.0883 | 73.0883 | 73.0883 | 73.0883 | 73.0883 | 73.0883 | 73.0883 | 73.0883 | 73.0883
99% | 1.486 | 39.9544 | 55.4636 | 59.4955 | 60.1827 | 60.7187 | 61.6416 | 63.7413 | 65.1468 | 66.9274 | 67.8516 | 68.6646 | 67.1665 | 68.9223 | 71.6825 | 69.5879 | 69.5879 | 69.5879 | 69.5879 | 69.5879 | 69.5879 | 69.5879 | 69.5879 | 69.5879 | 69.5879 | 69.5879 | 69.5879 | 69.5879 | 69.5879 | 69.5879 | 69.5879 | 99% | 1.486 | 42.7759 | 58.0895 | 62.2787 | 62.9269 | 63.3385 | 64.2414 | 66.3739 | 67.5382 | 69.7562 | 76.4982 | 70.9401 | 69.8529 | 71.3204 | 74.5299 | 72.3575 | 72.3575 | 72.3575 | 72.3575 | 72.3575 | 72.3575 | 72.3575 | 72.3575 | 72.3575 | 72.3575 | 72.3575 | 72.3575 | 72.3575 | 72.3575 | 72.3575 | 72.3575
98% | 3.2692 | 39.5508 | 54.9034 | 58.8945 | 59.5748 | 60.1054 | 61.019 | 63.0975 | 64.4888 | 66.2513 | 67.1662 | 67.9711 | 66.4881 | 68.2261 | 70.9584 | 68.885 | 68.885 | 68.885 | 68.885 | 68.885 | 68.885 | 68.885 | 68.885 | 68.885 | 68.885 | 68.885 | 68.885 | 68.885 | 68.885 | 68.885 | 68.885 | 98% | 3.2692 | 42.3438 | 57.5027 | 61.6497 | 62.2913 | 62.6987 | 63.5925 | 65.7034 | 66.856 | 69.0516 | 75.7255 | 70.2235 | 69.1473 | 70.6 | 73.7771 | 71.6266 | 71.6266 | 71.6266 | 71.6266 | 71.6266 | 71.6266 | 71.6266 | 71.6266 | 71.6266 | 71.6266 | 71.6266 | 71.6266 | 71.6266 | 71.6266 | 71.6266 | 71.6266
97% | 6.8356 | 39.1473 | 54.3431 | 58.2935 | 58.9669 | 59.4921 | 60.3964 | 62.4536 | 63.8307 | 65.5753 | 66.4808 | 67.2775 | 65.8096 | 67.5299 | 70.2344 | 68.1821 | 68.1821 | 68.1821 | 68.1821 | 68.1821 | 68.1821 | 68.1821 | 68.1821 | 68.1821 | 68.1821 | 68.1821 | 68.1821 | 68.1821 | 68.1821 | 68.1821 | 68.1821 | 97% | 6.8356 | 41.9118 | 56.916 | 61.0206 | 61.6557 | 62.0589 | 62.9436 | 65.033 | 66.1738 | 68.3469 | 74.9528 | 69.5069 | 68.4417 | 69.8796 | 73.0243 | 70.8957 | 70.8957 | 70.8957 | 70.8957 | 70.8957 | 70.8957 | 70.8957 | 70.8957 | 70.8957 | 70.8957 | 70.8957 | 70.8957 | 70.8957 | 70.8957 | 70.8957 | 70.8957
95% | 17.5347 | 38.3401 | 53.2227 | 57.0916 | 57.7511 | 58.2655 | 59.1511 | 61.1659 | 62.5146 | 64.2232 | 65.1101 | 65.8903 | 64.4527 | 66.1375 | 68.7862 | 66.7762 | 66.7762 | 66.7762 | 66.7762 | 66.7762 | 66.7762 | 66.7762 | 66.7762 | 66.7762 | 66.7762 | 66.7762 | 66.7762 | 66.7762 | 66.7762 | 66.7762 | 66.7762 | 95% | 17.5347 | 41.0476 | 55.7425 | 59.7624 | 60.3844 | 60.7794 | 61.6458 | 63.6921 | 64.8094 | 66.9377 | 73.4073 | 68.0738 | 67.0306 | 68.4388 | 71.5186 | 69.4339 | 69.4339 | 69.4339 | 69.4339 | 69.4339 | 69.4339 | 69.4339 | 69.4339 | 69.4339 | 69.4339 | 69.4339 | 69.4339 | 69.4339 | 69.4339 | 69.4339 | 69.4339
90% | 78.7576 | 36.3222 | 50.4215 | 54.0868 | 54.7116 | 55.1988 | 56.0379 | 57.9467 | 59.2244 | 60.8431 | 61.6833 | 62.4224 | 61.0605 | 62.6566 | 65.1659 | 63.2617 | 63.2617 | 63.2617 | 63.2617 | 63.2617 | 63.2617 | 63.2617 | 63.2617 | 63.2617 | 63.2617 | 63.2617 | 63.2617 | 63.2617 | 63.2617 | 63.2617 | 63.2617 | 90% | 78.7576 | 38.8872 | 52.8086 | 56.617 | 57.2063 | 57.5804 | 58.4013 | 60.3399 | 61.3984 | 63.4147 | 69.5438 | 64.491 | 63.5026 | 64.8368 | 67.7545 | 65.7795 | 65.7795 | 65.7795 | 65.7795 | 65.7795 | 65.7795 | 65.7795 | 65.7795 | 65.7795 | 65.7795 | 65.7795 | 65.7795 | 65.7795 | 65.7795 | 65.7795 | 65.7795
85% | 236.8672 | 34.3043 | 47.6203 | 51.082 | 51.672 | 52.1322 | 52.9246 | 54.7274 | 55.9342 | 57.4629 | 58.2564 | 58.9545 | 57.6682 | 59.1757 | 61.5456 | 59.7472 | 59.7472 | 59.7472 | 59.7472 | 59.7472 | 59.7472 | 59.7472 | 59.7472 | 59.7472 | 59.7472 | 59.7472 | 59.7472 | 59.7472 | 59.7472 | 59.7472 | 59.7472 | 85% | 236.8672 | 36.7268 | 49.8748 | 53.4716 | 54.0282 | 54.3815 | 55.1567 | 56.9877 | 57.9873 | 59.8917 | 65.6803 | 60.9081 | 59.9747 | 61.2347 | 63.9903 | 62.1251 | 62.1251 | 62.1251 | 62.1251 | 62.1251 | 62.1251 | 62.1251 | 62.1251 | 62.1251 | 62.1251 | 62.1251 | 62.1251 | 62.1251 | 62.1251 | 62.1251 | 62.1251
80% | 497.5104 | 32.2864 | 44.8191 | 48.0771 | 48.6325 | 49.0656 | 49.8114 | 51.5081 | 52.6439 | 54.0827 | 54.8296 | 55.4866 | 54.276 | 55.6948 | 57.9252 | 56.2326 | 56.2326 | 56.2326 | 56.2326 | 56.2326 | 56.2326 | 56.2326 | 56.2326 | 56.2326 | 56.2326 | 56.2326 | 56.2326 | 56.2326 | 56.2326 | 56.2326 | 56.2326 | 80% | 497.5104 | 34.5664 | 46.941 | 50.3262 | 50.85 | 51.1826 | 51.9122 | 53.6355 | 54.5763 | 56.3686 | 61.8167 | 57.3253 | 56.4468 | 57.6327 | 60.2262 | 58.4707 | 58.4707 | 58.4707 | 58.4707 | 58.4707 | 58.4707 | 58.4707 | 58.4707 | 58.4707 | 58.4707 | 58.4707 | 58.4707 | 58.4707 | 58.4707 | 58.4707 | 58.4707
75% | 803.6248 | 30.2685 | 42.0179 | 45.0723 | 45.593 | 45.999 | 46.6982 | 48.2889 | 49.3537 | 50.7026 | 51.4027 | 52.0187 | 50.8837 | 52.2138 | 54.3049 | 52.7181 | 52.7181 | 52.7181 | 52.7181 | 52.7181 | 52.7181 | 52.7181 | 52.7181 | 52.7181 | 52.7181 | 52.7181 | 52.7181 | 52.7181 | 52.7181 | 52.7181 | 52.7181 | 75% | 803.6248 | 32.406 | 44.0072 | 47.1809 | 47.6719 | 47.9837 | 48.6677 | 50.2832 | 51.1653 | 52.8456 | 57.9532 | 53.7425 | 52.9189 | 54.0306 | 56.4621 | 54.8163 | 54.8163 | 54.8163 | 54.8163 | 54.8163 | 54.8163 | 54.8163 | 54.8163 | 54.8163 | 54.8163 | 54.8163 | 54.8163 | 54.8163 | 54.8163 | 54.8163 | 54.8163
70% | 1155.2107 | 28.2506 | 39.2167 | 42.0675 | 42.5534 | 42.9324 | 43.585 | 45.0696 | 46.0634 | 47.3224 | 47.9759 | 48.5508 | 47.4915 | 48.7329 | 50.6846 | 49.2035 | 49.2035 | 49.2035 | 49.2035 | 49.2035 | 49.2035 | 49.2035 | 49.2035 | 49.2035 | 49.2035 | 49.2035 | 49.2035 | 49.2035 | 49.2035 | 49.2035 | 49.2035 | 70% | 1155.2107 | 30.2456 | 41.0734 | 44.0355 | 44.4938 | 44.7848 | 45.4232 | 46.931 | 47.7543 | 49.3225 | 54.0896 | 50.1596 | 49.3909 | 50.4286 | 52.6979 | 51.1618 | 51.1618 | 51.1618 | 51.1618 | 51.1618 | 51.1618 | 51.1618 | 51.1618 | 51.1618 | 51.1618 | 51.1618 | 51.1618 | 51.1618 | 51.1618 | 51.1618 | 51.1618
65% | 1553.1596 | 26.2327 | 36.4155 | 39.0627 | 39.5139 | 39.8658 | 40.4718 | 41.8504 | 42.7732 | 43.9422 | 44.549 | 45.0828 | 44.0992 | 45.252 | 47.0643 | 45.689 | 45.689 | 45.689 | 45.689 | 45.689 | 45.689 | 45.689 | 45.689 | 45.689 | 45.689 | 45.689 | 45.689 | 45.689 | 45.689 | 45.689 | 45.689 | 65% | 1553.1596 | 28.0852 | 38.1396 | 40.8901 | 41.3157 | 41.5859 | 42.1787 | 43.5788 | 44.3433 | 45.7995 | 50.2261 | 46.5768 | 45.863 | 46.8266 | 48.9338 | 47.5074 | 47.5074 | 47.5074 | 47.5074 | 47.5074 | 47.5074 | 47.5074 | 47.5074 | 47.5074 | 47.5074 | 47.5074 | 47.5074 | 47.5074 | 47.5074 | 47.5074 | 47.5074
60% | 2026.2996 | 24.2148 | 33.6143 | 36.0579 | 36.4744 | 36.7992 | 37.3586 | 38.6311 | 39.4829 | 40.562 | 41.1222 | 41.6149 | 40.707 | 41.7711 | 43.4439 | 42.1745 | 42.1745 | 42.1745 | 42.1745 | 42.1745 | 42.1745 | 42.1745 | 42.1745 | 42.1745 | 42.1745 | 42.1745 | 42.1745 | 42.1745 | 42.1745 | 42.1745 | 42.1745 | 60% | 2026.2996 | 25.9248 | 35.2058 | 37.7447 | 38.1375 | 38.387 | 38.9342 | 40.2266 | 40.9322 | 42.2765 | 46.3625 | 42.994 | 42.3351 | 43.2245 | 45.1696 | 43.853 | 43.853 | 43.853 | 43.853 | 43.853 | 43.853 | 43.853 | 43.853 | 43.853 | 43.853 | 43.853 | 43.853 | 43.853 | 43.853 | 43.853 | 43.853
55% | 2598.4068 | 22.1969 | 30.8131 | 33.053 | 33.4348 | 33.7326 | 34.2454 | 35.4119 | 36.1927 | 37.1819 | 37.6953 | 38.147 | 37.3147 | 38.2902 | 39.8236 | 38.6599 | 38.6599 | 38.6599 | 38.6599 | 38.6599 | 38.6599 | 38.6599 | 38.6599 | 38.6599 | 38.6599 | 38.6599 | 38.6599 | 38.6599 | 38.6599 | 38.6599 | 38.6599 | 55% | 2598.4068 | 23.7644 | 32.272 | 34.5993 | 34.9594 | 35.188 | 35.6897 | 36.8744 | 37.5212 | 38.7534 | 42.499 | 39.4111 | 38.8072 | 39.6225 | 41.4055 | 40.1986 | 40.1986 | 40.1986 | 40.1986 | 40.1986 | 40.1986 | 40.1986 | 40.1986 | 40.1986 | 40.1986 | 40.1986 | 40.1986 | 40.1986 | 40.1986 | 40.1986 | 40.1986
50% | 3233.5201 | 20.179 | 28.0119 | 30.0482 | 30.3953 | 30.666 | 31.1321 | 32.1926 | 32.9024 | 33.8017 | 34.2685 | 34.6791 | 33.9225 | 34.8092 | 36.2033 | 35.1454 | 35.1454 | 35.1454 | 35.1454 | 35.1454 | 35.1454 | 35.1454 | 35.1454 | 35.1454 | 35.1454 | 35.1454 | 35.1454 | 35.1454 | 35.1454 | 35.1454 | 35.1454 | 50% | 3233.5201 | 21.604 | 29.3381 | 31.4539 | 31.7813 | 31.9891 | 32.4451 | 33.5222 | 34.1102 | 35.2304 | 38.6354 | 35.8283 | 35.2792 | 36.0204 | 37.6414 | 36.5442 | 36.5442 | 36.5442 | 36.5442 | 36.5442 | 36.5442 | 36.5442 | 36.5442 | 36.5442 | 36.5442 | 36.5442 | 36.5442 | 36.5442 | 36.5442 | 36.5442 | 36.5442
45% | 3775.313 | 18.1611 | 25.2107 | 27.0434 | 27.3558 | 27.5994 | 28.0189 | 28.9733 | 29.6122 | 30.4215 | 30.8416 | 31.2112 | 30.5302 | 31.3283 | 32.583 | 31.6309 | 31.6309 | 31.6309 | 31.6309 | 31.6309 | 31.6309 | 31.6309 | 31.6309 | 31.6309 | 31.6309 | 31.6309 | 31.6309 | 31.6309 | 31.6309 | 31.6309 | 31.6309 | 45% | 3775.313 | 19.4436 | 26.4043 | 28.3085 | 28.6031 | 28.7902 | 29.2006 | 30.1699 | 30.6992 | 31.7073 | 34.7719 | 32.2455 | 31.7513 | 32.4184 | 33.8772 | 32.8898 | 32.8898 | 32.8898 | 32.8898 | 32.8898 | 32.8898 | 32.8898 | 32.8898 | 32.8898 | 32.8898 | 32.8898 | 32.8898 | 32.8898 | 32.8898 | 32.8898 | 32.8898
40% | 4072.8088 | 16.1432 | 22.4095 | 24.0386 | 24.3162 | 24.5328 | 24.9057 | 25.7541 | 26.322 | 27.0414 | 27.4148 | 27.7433 | 27.138 | 27.8474 | 28.9626 | 28.1163 | 28.1163 | 28.1163 | 28.1163 | 28.1163 | 28.1163 | 28.1163 | 28.1163 | 28.1163 | 28.1163 | 28.1163 | 28.1163 | 28.1163 | 28.1163 | 28.1163 | 28.1163 | 40% | 4072.8088 | 17.2832 | 23.4705 | 25.1631 | 25.425 | 25.5913 | 25.9561 | 26.8177 | 27.2882 | 28.1843 | 30.9084 | 28.6627 | 28.2234 | 28.8163 | 30.1131 | 29.2353 | 29.2353 | 29.2353 | 29.2353 | 29.2353 | 29.2353 | 29.2353 | 29.2353 | 29.2353 | 29.2353 | 29.2353 | 29.2353 | 29.2353 | 29.2353 | 29.2353 | 29.2353
35% | 4198.821 | 14.1253 | 19.6083 | 21.0337 | 21.2767 | 21.4662 | 21.7925 | 22.5348 | 23.0317 | 23.6612 | 23.9879 | 24.2754 | 23.7457 | 24.3665 | 25.3423 | 24.6018 | 24.6018 | 24.6018 | 24.6018 | 24.6018 | 24.6018 | 24.6018 | 24.6018 | 24.6018 | 24.6018 | 24.6018 | 24.6018 | 24.6018 | 24.6018 | 24.6018 | 24.6018 | 35% | 4198.821 | 15.1228 | 20.5367 | 22.0177 | 22.2469 | 22.3924 | 22.7116 | 23.4655 | 23.8771 | 24.6613 | 27.0448 | 25.0798 | 24.6955 | 25.2143 | 26.349 | 25.5809 | 25.5809 | 25.5809 | 25.5809 | 25.5809 | 25.5809 | 25.5809 | 25.5809 | 25.5809 | 25.5809 | 25.5809 | 25.5809 | 25.5809 | 25.5809 | 25.5809 | 25.5809
30% | 4271.3374 | 12.1074 | 16.8072 | 18.0289 | 18.2372 | 18.3996 | 18.6793 | 19.3156 | 19.7415 | 20.281 | 20.5611 | 20.8075 | 20.3535 | 20.8855 | 21.722 | 21.0872 | 21.0872 | 21.0872 | 21.0872 | 21.0872 | 21.0872 | 21.0872 | 21.0872 | 21.0872 | 21.0872 | 21.0872 | 21.0872 | 21.0872 | 21.0872 | 21.0872 | 21.0872 | 30% | 4271.3374 | 12.9624 | 17.6029 | 18.8723 | 19.0688 | 19.1935 | 19.4671 | 20.1133 | 20.4661 | 21.1382 | 23.1813 | 21.497 | 21.1675 | 21.6123 | 22.5848 | 21.9265 | 21.9265 | 21.9265 | 21.9265 | 21.9265 | 21.9265 | 21.9265 | 21.9265 | 21.9265 | 21.9265 | 21.9265 | 21.9265 | 21.9265 | 21.9265 | 21.9265 | 21.9265
25% | 4321.8611 | 10.0895 | 14.006 | 15.0241 | 15.1977 | 15.333 | 15.5661 | 16.0963 | 16.4512 | 16.9009 | 17.1342 | 17.3396 | 16.9612 | 17.4046 | 18.1016 | 17.5727 | 17.5727 | 17.5727 | 17.5727 | 17.5727 | 17.5727 | 17.5727 | 17.5727 | 17.5727 | 17.5727 | 17.5727 | 17.5727 | 17.5727 | 17.5727 | 17.5727 | 17.5727 | 25% | 4321.8611 | 10.802 | 14.6691 | 15.727 | 15.8906 | 15.9946 | 16.2226 | 16.7611 | 17.0551 | 17.6152 | 19.3177 | 17.9142 | 17.6396 | 18.0102 | 18.8207 | 18.2721 | 18.2721 | 18.2721 | 18.2721 | 18.2721 | 18.2721 | 18.2721 | 18.2721 | 18.2721 | 18.2721 | 18.2721 | 18.2721 | 18.2721 | 18.2721 | 18.2721 | 18.2721
20% | 4353.067 | 8.0716 | 11.2048 | 12.0193 | 12.1581 | 12.2664 | 12.4529 | 12.877 | 13.161 | 13.5207 | 13.7074 | 13.8716 | 13.569 | 13.9237 | 14.4813 | 14.0582 | 14.0582 | 14.0582 | 14.0582 | 14.0582 | 14.0582 | 14.0582 | 14.0582 | 14.0582 | 14.0582 | 14.0582 | 14.0582 | 14.0582 | 14.0582 | 14.0582 | 14.0582 | 20% | 4353.067 | 8.6416 | 11.7353 | 12.5816 | 12.7125 | 12.7957 | 12.9781 | 13.4089 | 13.6441 | 14.0922 | 15.4542 | 14.3313 | 14.1117 | 14.4082 | 15.0565 | 14.6177 | 14.6177 | 14.6177 | 14.6177 | 14.6177 | 14.6177 | 14.6177 | 14.6177 | 14.6177 | 14.6177 | 14.6177 | 14.6177 | 14.6177 | 14.6177 | 14.6177 | 14.6177
15% | 4369.4129 | 6.0537 | 8.4036 | 9.0145 | 9.1186 | 9.1998 | 9.3396 | 9.6578 | 9.8707 | 10.1405 | 10.2805 | 10.4037 | 10.1767 | 10.4428 | 10.861 | 10.5436 | 10.5436 | 10.5436 | 10.5436 | 10.5436 | 10.5436 | 10.5436 | 10.5436 | 10.5436 | 10.5436 | 10.5436 | 10.5436 | 10.5436 | 10.5436 | 10.5436 | 10.5436 | 15% | 4369.4129 | 6.4812 | 8.8014 | 9.4362 | 9.5344 | 9.5967 | 9.7335 | 10.0566 | 10.2331 | 10.5691 | 11.5906 | 10.7485 | 10.5838 | 10.8061 | 11.2924 | 10.9633 | 10.9633 | 10.9633 | 10.9633 | 10.9633 | 10.9633 | 10.9633 | 10.9633 | 10.9633 | 10.9633 | 10.9633 | 10.9633 | 10.9633 | 10.9633 | 10.9633 | 10.9633
10% | 4378.6261 | 4.0358 | 5.6024 | 6.0096 | 6.0791 | 6.1332 | 6.2264 | 6.4385 | 6.5805 | 6.7603 | 6.8537 | 6.9358 | 6.7845 | 6.9618 | 7.2407 | 7.0291 | 7.0291 | 7.0291 | 7.0291 | 7.0291 | 7.0291 | 7.0291 | 7.0291 | 7.0291 | 7.0291 | 7.0291 | 7.0291 | 7.0291 | 7.0291 | 7.0291 | 7.0291 | 10% | 4378.6261 | 4.3208 | 5.8676 | 6.2908 | 6.3563 | 6.3978 | 6.489 | 6.7044 | 6.822 | 7.0461 | 7.7271 | 7.1657 | 7.0558 | 7.2041 | 7.5283 | 7.3088 | 7.3088 | 7.3088 | 7.3088 | 7.3088 | 7.3088 | 7.3088 | 7.3088 | 7.3088 | 7.3088 | 7.3088 | 7.3088 | 7.3088 | 7.3088 | 7.3088 | 7.3088
5% | 4391.7028 | 2.0179 | 2.8012 | 3.0048 | 3.0395 | 3.0666 | 3.1132 | 3.2193 | 3.2902 | 3.3802 | 3.4268 | 3.4679 | 3.3922 | 3.4809 | 3.6203 | 3.5145 | 3.5145 | 3.5145 | 3.5145 | 3.5145 | 3.5145 | 3.5145 | 3.5145 | 3.5145 | 3.5145 | 3.5145 | 3.5145 | 3.5145 | 3.5145 | 3.5145 | 3.5145 | 5% | 4391.7028 | 2.1604 | 2.9338 | 3.1454 | 3.1781 | 3.1989 | 3.2445 | 3.3522 | 3.411 | 3.523 | 3.8635 | 3.5828 | 3.5279 | 3.602 | 3.7641 | 3.6544 | 3.6544 | 3.6544 | 3.6544 | 3.6544 | 3.6544 | 3.6544 | 3.6544 | 3.6544 | 3.6544 | 3.6544 | 3.6544 | 3.6544 | 3.6544 | 3.6544 | 3.6544
9.992e-14% | 4391.7028 | 4.0326e-14 | 5.5979e-14 | 6.0048e-14 | 6.0742e-14 | 6.1283e-14 | 6.2215e-14 | 6.4334e-14 | 6.5752e-14 | 6.7549e-14 | 6.8482e-14 | 6.9303e-14 | 6.7791e-14 | 6.9563e-14 | 7.2349e-14 | 7.0235e-14 | 7.0235e-14 | 7.0235e-14 | 7.0235e-14 | 7.0235e-14 | 7.0235e-14 | 7.0235e-14 | 7.0235e-14 | 7.0235e-14 | 7.0235e-14 | 7.0235e-14 | 7.0235e-14 | 7.0235e-14 | 7.0235e-14 | 7.0235e-14 | 7.0235e-14 | 9.992e-14% | 4391.7028 | 4.3173e-14 | 5.8629e-14 | 6.2858e-14 | 6.3512e-14 | 6.3927e-14 | 6.4838e-14 | 6.6991e-14 | 6.8166e-14 | 7.0404e-14 | 7.7209e-14 | 7.1599e-14 | 7.0502e-14 | 7.1983e-14 | 7.5223e-14 | 7.303e-14 | 7.303e-14 | 7.303e-14 | 7.303e-14 | 7.303e-14 | 7.303e-14 | 7.303e-14 | 7.303e-14 | 7.303e-14 | 7.303e-14 | 7.303e-14 | 7.303e-14 | 7.303e-14 | 7.303e-14 | 7.303e-14 | 7.303e-14
Summer Season | [31 empty] | Summer Season
P50 | [31 empty] | P10
% of MD | Summer - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Summer - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 45.8759 | 60.9589 | 65.0674 | 64.9499 | 64.9485 | 65.4184 | 65.9338 | 66.9909 | 67.7504 | 68.1633 | 68.6157 | 69.029 | 69.7743 | 70.6989 | 70.6364 | 70.6364 | 70.6364 | 70.6364 | 70.6364 | 70.6364 | 70.6364 | 70.6364 | 70.6364 | 70.6364 | 70.6364 | 70.6364 | 70.6364 | 70.6364 | 70.6364 | 70.6364 | 100% | 0 | 51.1554 | 66.2686 | 70.2261 | 69.9907 | 70.0105 | 70.4179 | 71.4905 | 72.2097 | 72.9132 | 73.7356 | 74.4985 | 75.2386 | 75.3243 | 76.1878 | 75.5357 | 75.5357 | 75.5357 | 75.5357 | 75.5357 | 75.5357 | 75.5357 | 75.5357 | 75.5357 | 75.5357 | 75.5357 | 75.5357 | 75.5357 | 75.5357 | 75.5357 | 75.5357
99% | 0 | 45.4171 | 60.3493 | 64.4168 | 64.3004 | 64.299 | 64.7642 | 65.2745 | 66.321 | 67.0729 | 67.4817 | 67.9295 | 68.3387 | 69.0766 | 69.9919 | 69.93 | 69.93 | 69.93 | 69.93 | 69.93 | 69.93 | 69.93 | 69.93 | 69.93 | 69.93 | 69.93 | 69.93 | 69.93 | 69.93 | 69.93 | 69.93 | 99% | 1.5127 | 50.6438 | 65.6059 | 69.5238 | 69.2908 | 69.3104 | 69.7137 | 70.7756 | 71.4876 | 72.184 | 72.9983 | 73.7535 | 74.4862 | 74.571 | 75.4259 | 74.7803 | 74.7803 | 74.7803 | 74.7803 | 74.7803 | 74.7803 | 74.7803 | 74.7803 | 74.7803 | 74.7803 | 74.7803 | 74.7803 | 74.7803 | 74.7803 | 74.7803 | 74.7803
98% | 0 | 44.9584 | 59.7397 | 63.7661 | 63.6509 | 63.6495 | 64.11 | 64.6151 | 65.6511 | 66.3954 | 66.8001 | 67.2434 | 67.6484 | 68.3788 | 69.2849 | 69.2236 | 69.2236 | 69.2236 | 69.2236 | 69.2236 | 69.2236 | 69.2236 | 69.2236 | 69.2236 | 69.2236 | 69.2236 | 69.2236 | 69.2236 | 69.2236 | 69.2236 | 69.2236 | 98% | 2.269 | 50.1322 | 64.9433 | 68.8216 | 68.5909 | 68.6103 | 69.0096 | 70.0607 | 70.7655 | 71.4549 | 72.2609 | 73.0085 | 73.7338 | 73.8178 | 74.664 | 74.0249 | 74.0249 | 74.0249 | 74.0249 | 74.0249 | 74.0249 | 74.0249 | 74.0249 | 74.0249 | 74.0249 | 74.0249 | 74.0249 | 74.0249 | 74.0249 | 74.0249 | 74.0249
97% | 0.37816 | 44.4996 | 59.1301 | 63.1154 | 63.0014 | 63 | 63.4558 | 63.9558 | 64.9812 | 65.7179 | 66.1184 | 66.5572 | 66.9581 | 67.6811 | 68.5779 | 68.5173 | 68.5173 | 68.5173 | 68.5173 | 68.5173 | 68.5173 | 68.5173 | 68.5173 | 68.5173 | 68.5173 | 68.5173 | 68.5173 | 68.5173 | 68.5173 | 68.5173 | 68.5173 | 97% | 3.7816 | 49.6207 | 64.2806 | 68.1193 | 67.891 | 67.9102 | 68.3054 | 69.3458 | 70.0434 | 70.7258 | 71.5236 | 72.2636 | 72.9814 | 73.0646 | 73.9022 | 73.2696 | 73.2696 | 73.2696 | 73.2696 | 73.2696 | 73.2696 | 73.2696 | 73.2696 | 73.2696 | 73.2696 | 73.2696 | 73.2696 | 73.2696 | 73.2696 | 73.2696 | 73.2696
95% | 2.269 | 43.5821 | 57.911 | 61.8141 | 61.7024 | 61.701 | 62.1474 | 62.6371 | 63.6414 | 64.3629 | 64.7552 | 65.1849 | 65.5776 | 66.2856 | 67.1639 | 67.1046 | 67.1046 | 67.1046 | 67.1046 | 67.1046 | 67.1046 | 67.1046 | 67.1046 | 67.1046 | 67.1046 | 67.1046 | 67.1046 | 67.1046 | 67.1046 | 67.1046 | 67.1046 | 95% | 6.0506 | 48.5976 | 62.9552 | 66.7148 | 66.4912 | 66.51 | 66.897 | 67.916 | 68.5992 | 69.2675 | 70.0488 | 70.7736 | 71.4766 | 71.5581 | 72.3784 | 71.7589 | 71.7589 | 71.7589 | 71.7589 | 71.7589 | 71.7589 | 71.7589 | 71.7589 | 71.7589 | 71.7589 | 71.7589 | 71.7589 | 71.7589 | 71.7589 | 71.7589 | 71.7589
90% | 5.6725 | 41.2883 | 54.863 | 58.5607 | 58.4549 | 58.4536 | 58.8765 | 59.3404 | 60.2918 | 60.9754 | 61.347 | 61.7541 | 62.1261 | 62.7969 | 63.629 | 63.5727 | 63.5727 | 63.5727 | 63.5727 | 63.5727 | 63.5727 | 63.5727 | 63.5727 | 63.5727 | 63.5727 | 63.5727 | 63.5727 | 63.5727 | 63.5727 | 63.5727 | 63.5727 | 90% | 16.2611 | 46.0398 | 59.6418 | 63.2035 | 62.9917 | 63.0094 | 63.3761 | 64.3415 | 64.9887 | 65.6218 | 66.3621 | 67.0487 | 67.7147 | 67.7919 | 68.569 | 67.9821 | 67.9821 | 67.9821 | 67.9821 | 67.9821 | 67.9821 | 67.9821 | 67.9821 | 67.9821 | 67.9821 | 67.9821 | 67.9821 | 67.9821 | 67.9821 | 67.9821 | 67.9821
85% | 15.8829 | 38.9945 | 51.8151 | 55.3073 | 55.2074 | 55.2062 | 55.6056 | 56.0437 | 56.9423 | 57.5879 | 57.9388 | 58.3233 | 58.6747 | 59.3082 | 60.094 | 60.0409 | 60.0409 | 60.0409 | 60.0409 | 60.0409 | 60.0409 | 60.0409 | 60.0409 | 60.0409 | 60.0409 | 60.0409 | 60.0409 | 60.0409 | 60.0409 | 60.0409 | 60.0409 | 85% | 26.4715 | 43.482 | 56.3283 | 59.6922 | 59.4921 | 59.5089 | 59.8552 | 60.767 | 61.3783 | 61.9762 | 62.6753 | 63.3237 | 63.9528 | 64.0256 | 64.7596 | 64.2053 | 64.2053 | 64.2053 | 64.2053 | 64.2053 | 64.2053 | 64.2053 | 64.2053 | 64.2053 | 64.2053 | 64.2053 | 64.2053 | 64.2053 | 64.2053 | 64.2053 | 64.2053
80% | 31.0095 | 36.7007 | 48.7671 | 52.0539 | 51.9599 | 51.9588 | 52.3347 | 52.747 | 53.5928 | 54.2003 | 54.5307 | 54.8925 | 55.2232 | 55.8194 | 56.5591 | 56.5091 | 56.5091 | 56.5091 | 56.5091 | 56.5091 | 56.5091 | 56.5091 | 56.5091 | 56.5091 | 56.5091 | 56.5091 | 56.5091 | 56.5091 | 56.5091 | 56.5091 | 56.5091 | 80% | 34.0348 | 40.9243 | 53.0149 | 56.1809 | 55.9926 | 56.0084 | 56.3343 | 57.1924 | 57.7678 | 58.3305 | 58.9885 | 59.5988 | 60.1908 | 60.2594 | 60.9502 | 60.4285 | 60.4285 | 60.4285 | 60.4285 | 60.4285 | 60.4285 | 60.4285 | 60.4285 | 60.4285 | 60.4285 | 60.4285 | 60.4285 | 60.4285 | 60.4285 | 60.4285 | 60.4285
75% | 72.9857 | 34.4069 | 45.7192 | 48.8006 | 48.7124 | 48.7113 | 49.0638 | 49.4504 | 50.2432 | 50.8128 | 51.1225 | 51.4618 | 51.7718 | 52.3307 | 53.0241 | 52.9773 | 52.9773 | 52.9773 | 52.9773 | 52.9773 | 52.9773 | 52.9773 | 52.9773 | 52.9773 | 52.9773 | 52.9773 | 52.9773 | 52.9773 | 52.9773 | 52.9773 | 52.9773 | 75% | 48.405 | 38.3665 | 49.7015 | 52.6696 | 52.493 | 52.5079 | 52.8134 | 53.6179 | 54.1573 | 54.6849 | 55.3017 | 55.8739 | 56.4289 | 56.4932 | 57.1408 | 56.6517 | 56.6517 | 56.6517 | 56.6517 | 56.6517 | 56.6517 | 56.6517 | 56.6517 | 56.6517 | 56.6517 | 56.6517 | 56.6517 | 56.6517 | 56.6517 | 56.6517 | 56.6517
70% | 150.5094 | 32.1131 | 42.6712 | 45.5472 | 45.4649 | 45.4639 | 45.7929 | 46.1537 | 46.8937 | 47.4253 | 47.7143 | 48.031 | 48.3203 | 48.842 | 49.4892 | 49.4455 | 49.4455 | 49.4455 | 49.4455 | 49.4455 | 49.4455 | 49.4455 | 49.4455 | 49.4455 | 49.4455 | 49.4455 | 49.4455 | 49.4455 | 49.4455 | 49.4455 | 49.4455 | 70% | 76.3892 | 35.8087 | 46.388 | 49.1583 | 48.9935 | 49.0073 | 49.2925 | 50.0434 | 50.5468 | 51.0392 | 51.6149 | 52.149 | 52.667 | 52.727 | 53.3315 | 52.875 | 52.875 | 52.875 | 52.875 | 52.875 | 52.875 | 52.875 | 52.875 | 52.875 | 52.875 | 52.875 | 52.875 | 52.875 | 52.875 | 52.875 | 52.875
65% | 359.6342 | 29.8193 | 39.6233 | 42.2938 | 42.2174 | 42.2165 | 42.5219 | 42.857 | 43.5441 | 44.0378 | 44.3062 | 44.6002 | 44.8689 | 45.3533 | 45.9543 | 45.9136 | 45.9136 | 45.9136 | 45.9136 | 45.9136 | 45.9136 | 45.9136 | 45.9136 | 45.9136 | 45.9136 | 45.9136 | 45.9136 | 45.9136 | 45.9136 | 45.9136 | 45.9136 | 65% | 114.2056 | 33.251 | 43.0746 | 45.647 | 45.494 | 45.5068 | 45.7716 | 46.4689 | 46.9363 | 47.3936 | 47.9282 | 48.424 | 48.9051 | 48.9608 | 49.5221 | 49.0982 | 49.0982 | 49.0982 | 49.0982 | 49.0982 | 49.0982 | 49.0982 | 49.0982 | 49.0982 | 49.0982 | 49.0982 | 49.0982 | 49.0982 | 49.0982 | 49.0982 | 49.0982
60% | 689.7717 | 27.5255 | 36.5753 | 39.0405 | 38.9699 | 38.9691 | 39.251 | 39.5603 | 40.1946 | 40.6503 | 40.898 | 41.1694 | 41.4174 | 41.8646 | 42.4193 | 42.3818 | 42.3818 | 42.3818 | 42.3818 | 42.3818 | 42.3818 | 42.3818 | 42.3818 | 42.3818 | 42.3818 | 42.3818 | 42.3818 | 42.3818 | 42.3818 | 42.3818 | 42.3818 | 60% | 178.1154 | 30.6932 | 39.7612 | 42.1357 | 41.9944 | 42.0063 | 42.2508 | 42.8943 | 43.3258 | 43.7479 | 44.2414 | 44.6991 | 45.1431 | 45.1946 | 45.7127 | 45.3214 | 45.3214 | 45.3214 | 45.3214 | 45.3214 | 45.3214 | 45.3214 | 45.3214 | 45.3214 | 45.3214 | 45.3214 | 45.3214 | 45.3214 | 45.3214 | 45.3214 | 45.3214
55% | 1095.5419 | 25.2317 | 33.5274 | 35.7871 | 35.7224 | 35.7217 | 35.9801 | 36.2636 | 36.845 | 37.2627 | 37.4898 | 37.7386 | 37.966 | 38.3759 | 38.8844 | 38.85 | 38.85 | 38.85 | 38.85 | 38.85 | 38.85 | 38.85 | 38.85 | 38.85 | 38.85 | 38.85 | 38.85 | 38.85 | 38.85 | 38.85 | 38.85 | 55% | 311.6074 | 28.1354 | 36.4477 | 38.6243 | 38.4949 | 38.5058 | 38.7299 | 39.3198 | 39.7153 | 40.1022 | 40.5546 | 40.9742 | 41.3812 | 41.4284 | 41.9033 | 41.5446 | 41.5446 | 41.5446 | 41.5446 | 41.5446 | 41.5446 | 41.5446 | 41.5446 | 41.5446 | 41.5446 | 41.5446 | 41.5446 | 41.5446 | 41.5446 | 41.5446 | 41.5446
50% | 1666.1918 | 22.9379 | 30.4794 | 32.5337 | 32.4749 | 32.4742 | 32.7092 | 32.9669 | 33.4955 | 33.8752 | 34.0817 | 34.3078 | 34.5145 | 34.8872 | 35.3494 | 35.3182 | 35.3182 | 35.3182 | 35.3182 | 35.3182 | 35.3182 | 35.3182 | 35.3182 | 35.3182 | 35.3182 | 35.3182 | 35.3182 | 35.3182 | 35.3182 | 35.3182 | 35.3182 | 50% | 636.0723 | 25.5777 | 33.1343 | 35.113 | 34.9954 | 35.0052 | 35.209 | 35.7453 | 36.1049 | 36.4566 | 36.8678 | 37.2493 | 37.6193 | 37.6621 | 38.0939 | 37.7678 | 37.7678 | 37.7678 | 37.7678 | 37.7678 | 37.7678 | 37.7678 | 37.7678 | 37.7678 | 37.7678 | 37.7678 | 37.7678 | 37.7678 | 37.7678 | 37.7678 | 37.7678
45% | 2506.0947 | 20.6442 | 27.4315 | 29.2803 | 29.2274 | 29.2268 | 29.4383 | 29.6702 | 30.1459 | 30.4877 | 30.6735 | 30.8771 | 31.0631 | 31.3984 | 31.8145 | 31.7864 | 31.7864 | 31.7864 | 31.7864 | 31.7864 | 31.7864 | 31.7864 | 31.7864 | 31.7864 | 31.7864 | 31.7864 | 31.7864 | 31.7864 | 31.7864 | 31.7864 | 31.7864 | 45% | 1179.4944 | 23.0199 | 29.8209 | 31.6017 | 31.4958 | 31.5047 | 31.6881 | 32.1707 | 32.4944 | 32.8109 | 33.181 | 33.5243 | 33.8573 | 33.8959 | 34.2845 | 33.991 | 33.991 | 33.991 | 33.991 | 33.991 | 33.991 | 33.991 | 33.991 | 33.991 | 33.991 | 33.991 | 33.991 | 33.991 | 33.991 | 33.991 | 33.991
40% | 3164.4787 | 18.3504 | 24.3836 | 26.027 | 25.9799 | 25.9794 | 26.1673 | 26.3735 | 26.7964 | 27.1002 | 27.2653 | 27.4463 | 27.6116 | 27.9097 | 28.2795 | 28.2546 | 28.2546 | 28.2546 | 28.2546 | 28.2546 | 28.2546 | 28.2546 | 28.2546 | 28.2546 | 28.2546 | 28.2546 | 28.2546 | 28.2546 | 28.2546 | 28.2546 | 28.2546 | 40% | 1808.3816 | 20.4621 | 26.5075 | 28.0904 | 27.9963 | 28.0042 | 28.1672 | 28.5962 | 28.8839 | 29.1653 | 29.4942 | 29.7994 | 30.0954 | 30.1297 | 30.4751 | 30.2143 | 30.2143 | 30.2143 | 30.2143 | 30.2143 | 30.2143 | 30.2143 | 30.2143 | 30.2143 | 30.2143 | 30.2143 | 30.2143 | 30.2143 | 30.2143 | 30.2143 | 30.2143
35% | 3551.3408 | 16.0566 | 21.3356 | 22.7736 | 22.7325 | 22.732 | 22.8964 | 23.0768 | 23.4468 | 23.7126 | 23.8572 | 24.0155 | 24.1602 | 24.421 | 24.7446 | 24.7227 | 24.7227 | 24.7227 | 24.7227 | 24.7227 | 24.7227 | 24.7227 | 24.7227 | 24.7227 | 24.7227 | 24.7227 | 24.7227 | 24.7227 | 24.7227 | 24.7227 | 24.7227 | 35% | 2779.1293 | 17.9044 | 23.194 | 24.5791 | 24.4968 | 24.5037 | 24.6463 | 25.0217 | 25.2734 | 25.5196 | 25.8075 | 26.0745 | 26.3335 | 26.3635 | 26.6657 | 26.4375 | 26.4375 | 26.4375 | 26.4375 | 26.4375 | 26.4375 | 26.4375 | 26.4375 | 26.4375 | 26.4375 | 26.4375 | 26.4375 | 26.4375 | 26.4375 | 26.4375 | 26.4375
30% | 3758.953 | 13.7628 | 18.2877 | 19.5202 | 19.485 | 19.4845 | 19.6255 | 19.7801 | 20.0973 | 20.3251 | 20.449 | 20.5847 | 20.7087 | 20.9323 | 21.2097 | 21.1909 | 21.1909 | 21.1909 | 21.1909 | 21.1909 | 21.1909 | 21.1909 | 21.1909 | 21.1909 | 21.1909 | 21.1909 | 21.1909 | 21.1909 | 21.1909 | 21.1909 | 21.1909 | 30% | 3814.165 | 15.3466 | 19.8806 | 21.0678 | 20.9972 | 21.0031 | 21.1254 | 21.4472 | 21.6629 | 21.8739 | 22.1207 | 22.3496 | 22.5716 | 22.5973 | 22.8563 | 22.6607 | 22.6607 | 22.6607 | 22.6607 | 22.6607 | 22.6607 | 22.6607 | 22.6607 | 22.6607 | 22.6607 | 22.6607 | 22.6607 | 22.6607 | 22.6607 | 22.6607 | 22.6607
25% | 3926.4798 | 11.469 | 15.2397 | 16.2669 | 16.2375 | 16.2371 | 16.3546 | 16.4835 | 16.7477 | 16.9376 | 17.0408 | 17.1539 | 17.2573 | 17.4436 | 17.6747 | 17.6591 | 17.6591 | 17.6591 | 17.6591 | 17.6591 | 17.6591 | 17.6591 | 17.6591 | 17.6591 | 17.6591 | 17.6591 | 17.6591 | 17.6591 | 17.6591 | 17.6591 | 17.6591 | 25% | 4166.9923 | 12.7888 | 16.5672 | 17.5565 | 17.4977 | 17.5026 | 17.6045 | 17.8726 | 18.0524 | 18.2283 | 18.4339 | 18.6246 | 18.8096 | 18.8311 | 19.0469 | 18.8839 | 18.8839 | 18.8839 | 18.8839 | 18.8839 | 18.8839 | 18.8839 | 18.8839 | 18.8839 | 18.8839 | 18.8839 | 18.8839 | 18.8839 | 18.8839 | 18.8839 | 18.8839
20% | 4050.5177 | 9.1752 | 12.1918 | 13.0135 | 12.99 | 12.9897 | 13.0837 | 13.1868 | 13.3982 | 13.5501 | 13.6327 | 13.7231 | 13.8058 | 13.9549 | 14.1398 | 14.1273 | 14.1273 | 14.1273 | 14.1273 | 14.1273 | 14.1273 | 14.1273 | 14.1273 | 14.1273 | 14.1273 | 14.1273 | 14.1273 | 14.1273 | 14.1273 | 14.1273 | 14.1273 | 20% | 4282.7105 | 10.2311 | 13.2537 | 14.0452 | 13.9981 | 14.0021 | 14.0836 | 14.2981 | 14.4419 | 14.5826 | 14.7471 | 14.8997 | 15.0477 | 15.0649 | 15.2376 | 15.1071 | 15.1071 | 15.1071 | 15.1071 | 15.1071 | 15.1071 | 15.1071 | 15.1071 | 15.1071 | 15.1071 | 15.1071 | 15.1071 | 15.1071 | 15.1071 | 15.1071 | 15.1071
15% | 4152.622 | 6.8814 | 9.1438 | 9.7601 | 9.7425 | 9.7423 | 9.8128 | 9.8901 | 10.0486 | 10.1626 | 10.2245 | 10.2924 | 10.3544 | 10.4661 | 10.6048 | 10.5955 | 10.5955 | 10.5955 | 10.5955 | 10.5955 | 10.5955 | 10.5955 | 10.5955 | 10.5955 | 10.5955 | 10.5955 | 10.5955 | 10.5955 | 10.5955 | 10.5955 | 10.5955 | 15% | 4364.7722 | 7.6733 | 9.9403 | 10.5339 | 10.4986 | 10.5016 | 10.5627 | 10.7236 | 10.8315 | 10.937 | 11.0603 | 11.1748 | 11.2858 | 11.2986 | 11.4282 | 11.3303 | 11.3303 | 11.3303 | 11.3303 | 11.3303 | 11.3303 | 11.3303 | 11.3303 | 11.3303 | 11.3303 | 11.3303 | 11.3303 | 11.3303 | 11.3303 | 11.3303 | 11.3303
10% | 4248.2976 | 4.5876 | 6.0959 | 6.5067 | 6.495 | 6.4948 | 6.5418 | 6.5934 | 6.6991 | 6.775 | 6.8163 | 6.8616 | 6.9029 | 6.9774 | 7.0699 | 7.0636 | 7.0636 | 7.0636 | 7.0636 | 7.0636 | 7.0636 | 7.0636 | 7.0636 | 7.0636 | 7.0636 | 7.0636 | 7.0636 | 7.0636 | 7.0636 | 7.0636 | 7.0636 | 10% | 4391.6218 | 5.1155 | 6.6269 | 7.0226 | 6.9991 | 7.001 | 7.0418 | 7.1491 | 7.221 | 7.2913 | 7.3736 | 7.4499 | 7.5239 | 7.5324 | 7.6188 | 7.5536 | 7.5536 | 7.5536 | 7.5536 | 7.5536 | 7.5536 | 7.5536 | 7.5536 | 7.5536 | 7.5536 | 7.5536 | 7.5536 | 7.5536 | 7.5536 | 7.5536 | 7.5536
5% | 4361.7469 | 2.2938 | 3.0479 | 3.2534 | 3.2475 | 3.2474 | 3.2709 | 3.2967 | 3.3495 | 3.3875 | 3.4082 | 3.4308 | 3.4515 | 3.4887 | 3.5349 | 3.5318 | 3.5318 | 3.5318 | 3.5318 | 3.5318 | 3.5318 | 3.5318 | 3.5318 | 3.5318 | 3.5318 | 3.5318 | 3.5318 | 3.5318 | 3.5318 | 3.5318 | 3.5318 | 5% | 4391.6218 | 2.5578 | 3.3134 | 3.5113 | 3.4995 | 3.5005 | 3.5209 | 3.5745 | 3.6105 | 3.6457 | 3.6868 | 3.7249 | 3.7619 | 3.7662 | 3.8094 | 3.7768 | 3.7768 | 3.7768 | 3.7768 | 3.7768 | 3.7768 | 3.7768 | 3.7768 | 3.7768 | 3.7768 | 3.7768 | 3.7768 | 3.7768 | 3.7768 | 3.7768 | 3.7768
9.992e-14% | 4391.6218 | 4.5839e-14 | 6.091e-14 | 6.5015e-14 | 6.4898e-14 | 6.4897e-14 | 6.5366e-14 | 6.5881e-14 | 6.6937e-14 | 6.7696e-14 | 6.8109e-14 | 6.8561e-14 | 6.8974e-14 | 6.9719e-14 | 7.0642e-14 | 7.058e-14 | 7.058e-14 | 7.058e-14 | 7.058e-14 | 7.058e-14 | 7.058e-14 | 7.058e-14 | 7.058e-14 | 7.058e-14 | 7.058e-14 | 7.058e-14 | 7.058e-14 | 7.058e-14 | 7.058e-14 | 7.058e-14 | 7.058e-14 | 9.992e-14% | 4391.6218 | 5.1114e-14 | 6.6216e-14 | 7.017e-14 | 6.9935e-14 | 6.9955e-14 | 7.0362e-14 | 7.1433e-14 | 7.2152e-14 | 7.2855e-14 | 7.3677e-14 | 7.4439e-14 | 7.5178e-14 | 7.5264e-14 | 7.6127e-14 | 7.5475e-14 | 7.5475e-14 | 7.5475e-14 | 7.5475e-14 | 7.5475e-14 | 7.5475e-14 | 7.5475e-14 | 7.5475e-14 | 7.5475e-14 | 7.5475e-14 | 7.5475e-14 | 7.5475e-14 | 7.5475e-14 | 7.5475e-14 | 7.5475e-14 | 7.5475e-14
Option 8
Winter Season | [31 empty] | Winter Season
P50 | [31 empty] | P10
% of MD | Winter - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Winter - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 40.358 | 56.0239 | 60.0964 | 60.7906 | 61.3321 | 62.2643 | 64.3852 | 65.8049 | 67.6034 | 68.5369 | 69.3582 | 67.845 | 69.6185 | 72.4066 | 70.2908 | 70.2908 | 70.2908 | 70.2908 | 70.2908 | 70.2908 | 70.2908 | 70.2908 | 70.2908 | 70.2908 | 70.2908 | 70.2908 | 70.2908 | 70.2908 | 70.2908 | 70.2908 | 100% | 0 | 43.208 | 58.6763 | 62.9078 | 63.5625 | 63.9783 | 64.8903 | 67.0443 | 68.2204 | 70.4608 | 77.2709 | 71.6566 | 70.5585 | 72.0408 | 75.2827 | 73.0883 | 73.0883 | 73.0883 | 73.0883 | 73.0883 | 73.0883 | 73.0883 | 73.0883 | 73.0883 | 73.0883 | 73.0883 | 73.0883 | 73.0883 | 73.0883 | 73.0883 | 73.0883
99% | 1.486 | 39.9544 | 55.4636 | 59.4955 | 60.1827 | 60.7187 | 61.6416 | 63.7413 | 65.1468 | 66.9274 | 67.8516 | 68.6646 | 67.1665 | 68.9223 | 71.6825 | 69.5879 | 69.5879 | 69.5879 | 69.5879 | 69.5879 | 69.5879 | 69.5879 | 69.5879 | 69.5879 | 69.5879 | 69.5879 | 69.5879 | 69.5879 | 69.5879 | 69.5879 | 69.5879 | 99% | 1.486 | 42.7759 | 58.0895 | 62.2787 | 62.9269 | 63.3385 | 64.2414 | 66.3739 | 67.5382 | 69.7562 | 76.4982 | 70.9401 | 69.8529 | 71.3204 | 74.5299 | 72.3575 | 72.3575 | 72.3575 | 72.3575 | 72.3575 | 72.3575 | 72.3575 | 72.3575 | 72.3575 | 72.3575 | 72.3575 | 72.3575 | 72.3575 | 72.3575 | 72.3575 | 72.3575
98% | 3.2692 | 39.5508 | 54.9034 | 58.8945 | 59.5748 | 60.1054 | 61.019 | 63.0975 | 64.4888 | 66.2513 | 67.1662 | 67.9711 | 66.4881 | 68.2261 | 70.9584 | 68.885 | 68.885 | 68.885 | 68.885 | 68.885 | 68.885 | 68.885 | 68.885 | 68.885 | 68.885 | 68.885 | 68.885 | 68.885 | 68.885 | 68.885 | 68.885 | 98% | 3.2692 | 42.3438 | 57.5027 | 61.6497 | 62.2913 | 62.6987 | 63.5925 | 65.7034 | 66.856 | 69.0516 | 75.7255 | 70.2235 | 69.1473 | 70.6 | 73.7771 | 71.6266 | 71.6266 | 71.6266 | 71.6266 | 71.6266 | 71.6266 | 71.6266 | 71.6266 | 71.6266 | 71.6266 | 71.6266 | 71.6266 | 71.6266 | 71.6266 | 71.6266 | 71.6266
97% | 6.8356 | 39.1473 | 54.3431 | 58.2935 | 58.9669 | 59.4921 | 60.3964 | 62.4536 | 63.8307 | 65.5753 | 66.4808 | 67.2775 | 65.8096 | 67.5299 | 70.2344 | 68.1821 | 68.1821 | 68.1821 | 68.1821 | 68.1821 | 68.1821 | 68.1821 | 68.1821 | 68.1821 | 68.1821 | 68.1821 | 68.1821 | 68.1821 | 68.1821 | 68.1821 | 68.1821 | 97% | 6.8356 | 41.9118 | 56.916 | 61.0206 | 61.6557 | 62.0589 | 62.9436 | 65.033 | 66.1738 | 68.3469 | 74.9528 | 69.5069 | 68.4417 | 69.8796 | 73.0243 | 70.8957 | 70.8957 | 70.8957 | 70.8957 | 70.8957 | 70.8957 | 70.8957 | 70.8957 | 70.8957 | 70.8957 | 70.8957 | 70.8957 | 70.8957 | 70.8957 | 70.8957 | 70.8957
95% | 17.5347 | 38.3401 | 53.2227 | 57.0916 | 57.7511 | 58.2655 | 59.1511 | 61.1659 | 62.5146 | 64.2232 | 65.1101 | 65.8903 | 64.4527 | 66.1375 | 68.7862 | 66.7762 | 66.7762 | 66.7762 | 66.7762 | 66.7762 | 66.7762 | 66.7762 | 66.7762 | 66.7762 | 66.7762 | 66.7762 | 66.7762 | 66.7762 | 66.7762 | 66.7762 | 66.7762 | 95% | 17.5347 | 41.0476 | 55.7425 | 59.7624 | 60.3844 | 60.7794 | 61.6458 | 63.6921 | 64.8094 | 66.9377 | 73.4073 | 68.0738 | 67.0306 | 68.4388 | 71.5186 | 69.4339 | 69.4339 | 69.4339 | 69.4339 | 69.4339 | 69.4339 | 69.4339 | 69.4339 | 69.4339 | 69.4339 | 69.4339 | 69.4339 | 69.4339 | 69.4339 | 69.4339 | 69.4339
90% | 78.7576 | 36.3222 | 50.4215 | 54.0868 | 54.7116 | 55.1988 | 56.0379 | 57.9467 | 59.2244 | 60.8431 | 61.6833 | 62.4224 | 61.0605 | 62.6566 | 65.1659 | 63.2617 | 63.2617 | 63.2617 | 63.2617 | 63.2617 | 63.2617 | 63.2617 | 63.2617 | 63.2617 | 63.2617 | 63.2617 | 63.2617 | 63.2617 | 63.2617 | 63.2617 | 63.2617 | 90% | 78.7576 | 38.8872 | 52.8086 | 56.617 | 57.2063 | 57.5804 | 58.4013 | 60.3399 | 61.3984 | 63.4147 | 69.5438 | 64.491 | 63.5026 | 64.8368 | 67.7545 | 65.7795 | 65.7795 | 65.7795 | 65.7795 | 65.7795 | 65.7795 | 65.7795 | 65.7795 | 65.7795 | 65.7795 | 65.7795 | 65.7795 | 65.7795 | 65.7795 | 65.7795 | 65.7795
85% | 236.8672 | 34.3043 | 47.6203 | 51.082 | 51.672 | 52.1322 | 52.9246 | 54.7274 | 55.9342 | 57.4629 | 58.2564 | 58.9545 | 57.6682 | 59.1757 | 61.5456 | 59.7472 | 59.7472 | 59.7472 | 59.7472 | 59.7472 | 59.7472 | 59.7472 | 59.7472 | 59.7472 | 59.7472 | 59.7472 | 59.7472 | 59.7472 | 59.7472 | 59.7472 | 59.7472 | 85% | 236.8672 | 36.7268 | 49.8748 | 53.4716 | 54.0282 | 54.3815 | 55.1567 | 56.9877 | 57.9873 | 59.8917 | 65.6803 | 60.9081 | 59.9747 | 61.2347 | 63.9903 | 62.1251 | 62.1251 | 62.1251 | 62.1251 | 62.1251 | 62.1251 | 62.1251 | 62.1251 | 62.1251 | 62.1251 | 62.1251 | 62.1251 | 62.1251 | 62.1251 | 62.1251 | 62.1251
80% | 497.5104 | 32.2864 | 44.8191 | 48.0771 | 48.6325 | 49.0656 | 49.8114 | 51.5081 | 52.6439 | 54.0827 | 54.8296 | 55.4866 | 54.276 | 55.6948 | 57.9252 | 56.2326 | 56.2326 | 56.2326 | 56.2326 | 56.2326 | 56.2326 | 56.2326 | 56.2326 | 56.2326 | 56.2326 | 56.2326 | 56.2326 | 56.2326 | 56.2326 | 56.2326 | 56.2326 | 80% | 497.5104 | 34.5664 | 46.941 | 50.3262 | 50.85 | 51.1826 | 51.9122 | 53.6355 | 54.5763 | 56.3686 | 61.8167 | 57.3253 | 56.4468 | 57.6327 | 60.2262 | 58.4707 | 58.4707 | 58.4707 | 58.4707 | 58.4707 | 58.4707 | 58.4707 | 58.4707 | 58.4707 | 58.4707 | 58.4707 | 58.4707 | 58.4707 | 58.4707 | 58.4707 | 58.4707
75% | 803.6248 | 30.2685 | 42.0179 | 45.0723 | 45.593 | 45.999 | 46.6982 | 48.2889 | 49.3537 | 50.7026 | 51.4027 | 52.0187 | 50.8837 | 52.2138 | 54.3049 | 52.7181 | 52.7181 | 52.7181 | 52.7181 | 52.7181 | 52.7181 | 52.7181 | 52.7181 | 52.7181 | 52.7181 | 52.7181 | 52.7181 | 52.7181 | 52.7181 | 52.7181 | 52.7181 | 75% | 803.6248 | 32.406 | 44.0072 | 47.1809 | 47.6719 | 47.9837 | 48.6677 | 50.2832 | 51.1653 | 52.8456 | 57.9532 | 53.7425 | 52.9189 | 54.0306 | 56.4621 | 54.8163 | 54.8163 | 54.8163 | 54.8163 | 54.8163 | 54.8163 | 54.8163 | 54.8163 | 54.8163 | 54.8163 | 54.8163 | 54.8163 | 54.8163 | 54.8163 | 54.8163 | 54.8163
70% | 1155.2107 | 28.2506 | 39.2167 | 42.0675 | 42.5534 | 42.9324 | 43.585 | 45.0696 | 46.0634 | 47.3224 | 47.9759 | 48.5508 | 47.4915 | 48.7329 | 50.6846 | 49.2035 | 49.2035 | 49.2035 | 49.2035 | 49.2035 | 49.2035 | 49.2035 | 49.2035 | 49.2035 | 49.2035 | 49.2035 | 49.2035 | 49.2035 | 49.2035 | 49.2035 | 49.2035 | 70% | 1155.2107 | 30.2456 | 41.0734 | 44.0355 | 44.4938 | 44.7848 | 45.4232 | 46.931 | 47.7543 | 49.3225 | 54.0896 | 50.1596 | 49.3909 | 50.4286 | 52.6979 | 51.1618 | 51.1618 | 51.1618 | 51.1618 | 51.1618 | 51.1618 | 51.1618 | 51.1618 | 51.1618 | 51.1618 | 51.1618 | 51.1618 | 51.1618 | 51.1618 | 51.1618 | 51.1618
65% | 1553.1596 | 26.2327 | 36.4155 | 39.0627 | 39.5139 | 39.8658 | 40.4718 | 41.8504 | 42.7732 | 43.9422 | 44.549 | 45.0828 | 44.0992 | 45.252 | 47.0643 | 45.689 | 45.689 | 45.689 | 45.689 | 45.689 | 45.689 | 45.689 | 45.689 | 45.689 | 45.689 | 45.689 | 45.689 | 45.689 | 45.689 | 45.689 | 45.689 | 65% | 1553.1596 | 28.0852 | 38.1396 | 40.8901 | 41.3157 | 41.5859 | 42.1787 | 43.5788 | 44.3433 | 45.7995 | 50.2261 | 46.5768 | 45.863 | 46.8266 | 48.9338 | 47.5074 | 47.5074 | 47.5074 | 47.5074 | 47.5074 | 47.5074 | 47.5074 | 47.5074 | 47.5074 | 47.5074 | 47.5074 | 47.5074 | 47.5074 | 47.5074 | 47.5074 | 47.5074
60% | 2026.2996 | 24.2148 | 33.6143 | 36.0579 | 36.4744 | 36.7992 | 37.3586 | 38.6311 | 39.4829 | 40.562 | 41.1222 | 41.6149 | 40.707 | 41.7711 | 43.4439 | 42.1745 | 42.1745 | 42.1745 | 42.1745 | 42.1745 | 42.1745 | 42.1745 | 42.1745 | 42.1745 | 42.1745 | 42.1745 | 42.1745 | 42.1745 | 42.1745 | 42.1745 | 42.1745 | 60% | 2026.2996 | 25.9248 | 35.2058 | 37.7447 | 38.1375 | 38.387 | 38.9342 | 40.2266 | 40.9322 | 42.2765 | 46.3625 | 42.994 | 42.3351 | 43.2245 | 45.1696 | 43.853 | 43.853 | 43.853 | 43.853 | 43.853 | 43.853 | 43.853 | 43.853 | 43.853 | 43.853 | 43.853 | 43.853 | 43.853 | 43.853 | 43.853 | 43.853
55% | 2598.4068 | 22.1969 | 30.8131 | 33.053 | 33.4348 | 33.7326 | 34.2454 | 35.4119 | 36.1927 | 37.1819 | 37.6953 | 38.147 | 37.3147 | 38.2902 | 39.8236 | 38.6599 | 38.6599 | 38.6599 | 38.6599 | 38.6599 | 38.6599 | 38.6599 | 38.6599 | 38.6599 | 38.6599 | 38.6599 | 38.6599 | 38.6599 | 38.6599 | 38.6599 | 38.6599 | 55% | 2598.4068 | 23.7644 | 32.272 | 34.5993 | 34.9594 | 35.188 | 35.6897 | 36.8744 | 37.5212 | 38.7534 | 42.499 | 39.4111 | 38.8072 | 39.6225 | 41.4055 | 40.1986 | 40.1986 | 40.1986 | 40.1986 | 40.1986 | 40.1986 | 40.1986 | 40.1986 | 40.1986 | 40.1986 | 40.1986 | 40.1986 | 40.1986 | 40.1986 | 40.1986 | 40.1986
50% | 3233.5201 | 20.179 | 28.0119 | 30.0482 | 30.3953 | 30.666 | 31.1321 | 32.1926 | 32.9024 | 33.8017 | 34.2685 | 34.6791 | 33.9225 | 34.8092 | 36.2033 | 35.1454 | 35.1454 | 35.1454 | 35.1454 | 35.1454 | 35.1454 | 35.1454 | 35.1454 | 35.1454 | 35.1454 | 35.1454 | 35.1454 | 35.1454 | 35.1454 | 35.1454 | 35.1454 | 50% | 3233.5201 | 21.604 | 29.3381 | 31.4539 | 31.7813 | 31.9891 | 32.4451 | 33.5222 | 34.1102 | 35.2304 | 38.6354 | 35.8283 | 35.2792 | 36.0204 | 37.6414 | 36.5442 | 36.5442 | 36.5442 | 36.5442 | 36.5442 | 36.5442 | 36.5442 | 36.5442 | 36.5442 | 36.5442 | 36.5442 | 36.5442 | 36.5442 | 36.5442 | 36.5442 | 36.5442
45% | 3775.313 | 18.1611 | 25.2107 | 27.0434 | 27.3558 | 27.5994 | 28.0189 | 28.9733 | 29.6122 | 30.4215 | 30.8416 | 31.2112 | 30.5302 | 31.3283 | 32.583 | 31.6309 | 31.6309 | 31.6309 | 31.6309 | 31.6309 | 31.6309 | 31.6309 | 31.6309 | 31.6309 | 31.6309 | 31.6309 | 31.6309 | 31.6309 | 31.6309 | 31.6309 | 31.6309 | 45% | 3775.313 | 19.4436 | 26.4043 | 28.3085 | 28.6031 | 28.7902 | 29.2006 | 30.1699 | 30.6992 | 31.7073 | 34.7719 | 32.2455 | 31.7513 | 32.4184 | 33.8772 | 32.8898 | 32.8898 | 32.8898 | 32.8898 | 32.8898 | 32.8898 | 32.8898 | 32.8898 | 32.8898 | 32.8898 | 32.8898 | 32.8898 | 32.8898 | 32.8898 | 32.8898 | 32.8898
40% | 4072.8088 | 16.1432 | 22.4095 | 24.0386 | 24.3162 | 24.5328 | 24.9057 | 25.7541 | 26.322 | 27.0414 | 27.4148 | 27.7433 | 27.138 | 27.8474 | 28.9626 | 28.1163 | 28.1163 | 28.1163 | 28.1163 | 28.1163 | 28.1163 | 28.1163 | 28.1163 | 28.1163 | 28.1163 | 28.1163 | 28.1163 | 28.1163 | 28.1163 | 28.1163 | 28.1163 | 40% | 4072.8088 | 17.2832 | 23.4705 | 25.1631 | 25.425 | 25.5913 | 25.9561 | 26.8177 | 27.2882 | 28.1843 | 30.9084 | 28.6627 | 28.2234 | 28.8163 | 30.1131 | 29.2353 | 29.2353 | 29.2353 | 29.2353 | 29.2353 | 29.2353 | 29.2353 | 29.2353 | 29.2353 | 29.2353 | 29.2353 | 29.2353 | 29.2353 | 29.2353 | 29.2353 | 29.2353
35% | 4198.821 | 14.1253 | 19.6083 | 21.0337 | 21.2767 | 21.4662 | 21.7925 | 22.5348 | 23.0317 | 23.6612 | 23.9879 | 24.2754 | 23.7457 | 24.3665 | 25.3423 | 24.6018 | 24.6018 | 24.6018 | 24.6018 | 24.6018 | 24.6018 | 24.6018 | 24.6018 | 24.6018 | 24.6018 | 24.6018 | 24.6018 | 24.6018 | 24.6018 | 24.6018 | 24.6018 | 35% | 4198.821 | 15.1228 | 20.5367 | 22.0177 | 22.2469 | 22.3924 | 22.7116 | 23.4655 | 23.8771 | 24.6613 | 27.0448 | 25.0798 | 24.6955 | 25.2143 | 26.349 | 25.5809 | 25.5809 | 25.5809 | 25.5809 | 25.5809 | 25.5809 | 25.5809 | 25.5809 | 25.5809 | 25.5809 | 25.5809 | 25.5809 | 25.5809 | 25.5809 | 25.5809 | 25.5809
30% | 4271.3374 | 12.1074 | 16.8072 | 18.0289 | 18.2372 | 18.3996 | 18.6793 | 19.3156 | 19.7415 | 20.281 | 20.5611 | 20.8075 | 20.3535 | 20.8855 | 21.722 | 21.0872 | 21.0872 | 21.0872 | 21.0872 | 21.0872 | 21.0872 | 21.0872 | 21.0872 | 21.0872 | 21.0872 | 21.0872 | 21.0872 | 21.0872 | 21.0872 | 21.0872 | 21.0872 | 30% | 4271.3374 | 12.9624 | 17.6029 | 18.8723 | 19.0688 | 19.1935 | 19.4671 | 20.1133 | 20.4661 | 21.1382 | 23.1813 | 21.497 | 21.1675 | 21.6123 | 22.5848 | 21.9265 | 21.9265 | 21.9265 | 21.9265 | 21.9265 | 21.9265 | 21.9265 | 21.9265 | 21.9265 | 21.9265 | 21.9265 | 21.9265 | 21.9265 | 21.9265 | 21.9265 | 21.9265
25% | 4321.8611 | 10.0895 | 14.006 | 15.0241 | 15.1977 | 15.333 | 15.5661 | 16.0963 | 16.4512 | 16.9009 | 17.1342 | 17.3396 | 16.9612 | 17.4046 | 18.1016 | 17.5727 | 17.5727 | 17.5727 | 17.5727 | 17.5727 | 17.5727 | 17.5727 | 17.5727 | 17.5727 | 17.5727 | 17.5727 | 17.5727 | 17.5727 | 17.5727 | 17.5727 | 17.5727 | 25% | 4321.8611 | 10.802 | 14.6691 | 15.727 | 15.8906 | 15.9946 | 16.2226 | 16.7611 | 17.0551 | 17.6152 | 19.3177 | 17.9142 | 17.6396 | 18.0102 | 18.8207 | 18.2721 | 18.2721 | 18.2721 | 18.2721 | 18.2721 | 18.2721 | 18.2721 | 18.2721 | 18.2721 | 18.2721 | 18.2721 | 18.2721 | 18.2721 | 18.2721 | 18.2721 | 18.2721
20% | 4353.067 | 8.0716 | 11.2048 | 12.0193 | 12.1581 | 12.2664 | 12.4529 | 12.877 | 13.161 | 13.5207 | 13.7074 | 13.8716 | 13.569 | 13.9237 | 14.4813 | 14.0582 | 14.0582 | 14.0582 | 14.0582 | 14.0582 | 14.0582 | 14.0582 | 14.0582 | 14.0582 | 14.0582 | 14.0582 | 14.0582 | 14.0582 | 14.0582 | 14.0582 | 14.0582 | 20% | 4353.067 | 8.6416 | 11.7353 | 12.5816 | 12.7125 | 12.7957 | 12.9781 | 13.4089 | 13.6441 | 14.0922 | 15.4542 | 14.3313 | 14.1117 | 14.4082 | 15.0565 | 14.6177 | 14.6177 | 14.6177 | 14.6177 | 14.6177 | 14.6177 | 14.6177 | 14.6177 | 14.6177 | 14.6177 | 14.6177 | 14.6177 | 14.6177 | 14.6177 | 14.6177 | 14.6177
15% | 4369.4129 | 6.0537 | 8.4036 | 9.0145 | 9.1186 | 9.1998 | 9.3396 | 9.6578 | 9.8707 | 10.1405 | 10.2805 | 10.4037 | 10.1767 | 10.4428 | 10.861 | 10.5436 | 10.5436 | 10.5436 | 10.5436 | 10.5436 | 10.5436 | 10.5436 | 10.5436 | 10.5436 | 10.5436 | 10.5436 | 10.5436 | 10.5436 | 10.5436 | 10.5436 | 10.5436 | 15% | 4369.4129 | 6.4812 | 8.8014 | 9.4362 | 9.5344 | 9.5967 | 9.7335 | 10.0566 | 10.2331 | 10.5691 | 11.5906 | 10.7485 | 10.5838 | 10.8061 | 11.2924 | 10.9633 | 10.9633 | 10.9633 | 10.9633 | 10.9633 | 10.9633 | 10.9633 | 10.9633 | 10.9633 | 10.9633 | 10.9633 | 10.9633 | 10.9633 | 10.9633 | 10.9633 | 10.9633
10% | 4378.6261 | 4.0358 | 5.6024 | 6.0096 | 6.0791 | 6.1332 | 6.2264 | 6.4385 | 6.5805 | 6.7603 | 6.8537 | 6.9358 | 6.7845 | 6.9618 | 7.2407 | 7.0291 | 7.0291 | 7.0291 | 7.0291 | 7.0291 | 7.0291 | 7.0291 | 7.0291 | 7.0291 | 7.0291 | 7.0291 | 7.0291 | 7.0291 | 7.0291 | 7.0291 | 7.0291 | 10% | 4378.6261 | 4.3208 | 5.8676 | 6.2908 | 6.3563 | 6.3978 | 6.489 | 6.7044 | 6.822 | 7.0461 | 7.7271 | 7.1657 | 7.0558 | 7.2041 | 7.5283 | 7.3088 | 7.3088 | 7.3088 | 7.3088 | 7.3088 | 7.3088 | 7.3088 | 7.3088 | 7.3088 | 7.3088 | 7.3088 | 7.3088 | 7.3088 | 7.3088 | 7.3088 | 7.3088
5% | 4391.7028 | 2.0179 | 2.8012 | 3.0048 | 3.0395 | 3.0666 | 3.1132 | 3.2193 | 3.2902 | 3.3802 | 3.4268 | 3.4679 | 3.3922 | 3.4809 | 3.6203 | 3.5145 | 3.5145 | 3.5145 | 3.5145 | 3.5145 | 3.5145 | 3.5145 | 3.5145 | 3.5145 | 3.5145 | 3.5145 | 3.5145 | 3.5145 | 3.5145 | 3.5145 | 3.5145 | 5% | 4391.7028 | 2.1604 | 2.9338 | 3.1454 | 3.1781 | 3.1989 | 3.2445 | 3.3522 | 3.411 | 3.523 | 3.8635 | 3.5828 | 3.5279 | 3.602 | 3.7641 | 3.6544 | 3.6544 | 3.6544 | 3.6544 | 3.6544 | 3.6544 | 3.6544 | 3.6544 | 3.6544 | 3.6544 | 3.6544 | 3.6544 | 3.6544 | 3.6544 | 3.6544 | 3.6544
9.992e-14% | 4391.7028 | 4.0326e-14 | 5.5979e-14 | 6.0048e-14 | 6.0742e-14 | 6.1283e-14 | 6.2215e-14 | 6.4334e-14 | 6.5752e-14 | 6.7549e-14 | 6.8482e-14 | 6.9303e-14 | 6.7791e-14 | 6.9563e-14 | 7.2349e-14 | 7.0235e-14 | 7.0235e-14 | 7.0235e-14 | 7.0235e-14 | 7.0235e-14 | 7.0235e-14 | 7.0235e-14 | 7.0235e-14 | 7.0235e-14 | 7.0235e-14 | 7.0235e-14 | 7.0235e-14 | 7.0235e-14 | 7.0235e-14 | 7.0235e-14 | 7.0235e-14 | 9.992e-14% | 4391.7028 | 4.3173e-14 | 5.8629e-14 | 6.2858e-14 | 6.3512e-14 | 6.3927e-14 | 6.4838e-14 | 6.6991e-14 | 6.8166e-14 | 7.0404e-14 | 7.7209e-14 | 7.1599e-14 | 7.0502e-14 | 7.1983e-14 | 7.5223e-14 | 7.303e-14 | 7.303e-14 | 7.303e-14 | 7.303e-14 | 7.303e-14 | 7.303e-14 | 7.303e-14 | 7.303e-14 | 7.303e-14 | 7.303e-14 | 7.303e-14 | 7.303e-14 | 7.303e-14 | 7.303e-14 | 7.303e-14 | 7.303e-14
Summer Season | [31 empty] | Summer Season
P50 | [31 empty] | P10
% of MD | Summer - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Summer - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 45.8759 | 60.9589 | 65.0674 | 64.9499 | 64.9485 | 65.4184 | 65.9338 | 66.9909 | 67.7504 | 68.1633 | 68.6157 | 69.029 | 69.7743 | 70.6989 | 70.6364 | 70.6364 | 70.6364 | 70.6364 | 70.6364 | 70.6364 | 70.6364 | 70.6364 | 70.6364 | 70.6364 | 70.6364 | 70.6364 | 70.6364 | 70.6364 | 70.6364 | 70.6364 | 100% | 0 | 51.1554 | 66.2686 | 70.2261 | 69.9907 | 70.0105 | 70.4179 | 71.4905 | 72.2097 | 72.9132 | 73.7356 | 74.4985 | 75.2386 | 75.3243 | 76.1878 | 75.5357 | 75.5357 | 75.5357 | 75.5357 | 75.5357 | 75.5357 | 75.5357 | 75.5357 | 75.5357 | 75.5357 | 75.5357 | 75.5357 | 75.5357 | 75.5357 | 75.5357 | 75.5357
99% | 0 | 45.4171 | 60.3493 | 64.4168 | 64.3004 | 64.299 | 64.7642 | 65.2745 | 66.321 | 67.0729 | 67.4817 | 67.9295 | 68.3387 | 69.0766 | 69.9919 | 69.93 | 69.93 | 69.93 | 69.93 | 69.93 | 69.93 | 69.93 | 69.93 | 69.93 | 69.93 | 69.93 | 69.93 | 69.93 | 69.93 | 69.93 | 69.93 | 99% | 1.5127 | 50.6438 | 65.6059 | 69.5238 | 69.2908 | 69.3104 | 69.7137 | 70.7756 | 71.4876 | 72.184 | 72.9983 | 73.7535 | 74.4862 | 74.571 | 75.4259 | 74.7803 | 74.7803 | 74.7803 | 74.7803 | 74.7803 | 74.7803 | 74.7803 | 74.7803 | 74.7803 | 74.7803 | 74.7803 | 74.7803 | 74.7803 | 74.7803 | 74.7803 | 74.7803
98% | 0 | 44.9584 | 59.7397 | 63.7661 | 63.6509 | 63.6495 | 64.11 | 64.6151 | 65.6511 | 66.3954 | 66.8001 | 67.2434 | 67.6484 | 68.3788 | 69.2849 | 69.2236 | 69.2236 | 69.2236 | 69.2236 | 69.2236 | 69.2236 | 69.2236 | 69.2236 | 69.2236 | 69.2236 | 69.2236 | 69.2236 | 69.2236 | 69.2236 | 69.2236 | 69.2236 | 98% | 2.269 | 50.1322 | 64.9433 | 68.8216 | 68.5909 | 68.6103 | 69.0096 | 70.0607 | 70.7655 | 71.4549 | 72.2609 | 73.0085 | 73.7338 | 73.8178 | 74.664 | 74.0249 | 74.0249 | 74.0249 | 74.0249 | 74.0249 | 74.0249 | 74.0249 | 74.0249 | 74.0249 | 74.0249 | 74.0249 | 74.0249 | 74.0249 | 74.0249 | 74.0249 | 74.0249
97% | 0.37816 | 44.4996 | 59.1301 | 63.1154 | 63.0014 | 63 | 63.4558 | 63.9558 | 64.9812 | 65.7179 | 66.1184 | 66.5572 | 66.9581 | 67.6811 | 68.5779 | 68.5173 | 68.5173 | 68.5173 | 68.5173 | 68.5173 | 68.5173 | 68.5173 | 68.5173 | 68.5173 | 68.5173 | 68.5173 | 68.5173 | 68.5173 | 68.5173 | 68.5173 | 68.5173 | 97% | 3.7816 | 49.6207 | 64.2806 | 68.1193 | 67.891 | 67.9102 | 68.3054 | 69.3458 | 70.0434 | 70.7258 | 71.5236 | 72.2636 | 72.9814 | 73.0646 | 73.9022 | 73.2696 | 73.2696 | 73.2696 | 73.2696 | 73.2696 | 73.2696 | 73.2696 | 73.2696 | 73.2696 | 73.2696 | 73.2696 | 73.2696 | 73.2696 | 73.2696 | 73.2696 | 73.2696
95% | 2.269 | 43.5821 | 57.911 | 61.8141 | 61.7024 | 61.701 | 62.1474 | 62.6371 | 63.6414 | 64.3629 | 64.7552 | 65.1849 | 65.5776 | 66.2856 | 67.1639 | 67.1046 | 67.1046 | 67.1046 | 67.1046 | 67.1046 | 67.1046 | 67.1046 | 67.1046 | 67.1046 | 67.1046 | 67.1046 | 67.1046 | 67.1046 | 67.1046 | 67.1046 | 67.1046 | 95% | 6.0506 | 48.5976 | 62.9552 | 66.7148 | 66.4912 | 66.51 | 66.897 | 67.916 | 68.5992 | 69.2675 | 70.0488 | 70.7736 | 71.4766 | 71.5581 | 72.3784 | 71.7589 | 71.7589 | 71.7589 | 71.7589 | 71.7589 | 71.7589 | 71.7589 | 71.7589 | 71.7589 | 71.7589 | 71.7589 | 71.7589 | 71.7589 | 71.7589 | 71.7589 | 71.7589
90% | 5.6725 | 41.2883 | 54.863 | 58.5607 | 58.4549 | 58.4536 | 58.8765 | 59.3404 | 60.2918 | 60.9754 | 61.347 | 61.7541 | 62.1261 | 62.7969 | 63.629 | 63.5727 | 63.5727 | 63.5727 | 63.5727 | 63.5727 | 63.5727 | 63.5727 | 63.5727 | 63.5727 | 63.5727 | 63.5727 | 63.5727 | 63.5727 | 63.5727 | 63.5727 | 63.5727 | 90% | 16.2611 | 46.0398 | 59.6418 | 63.2035 | 62.9917 | 63.0094 | 63.3761 | 64.3415 | 64.9887 | 65.6218 | 66.3621 | 67.0487 | 67.7147 | 67.7919 | 68.569 | 67.9821 | 67.9821 | 67.9821 | 67.9821 | 67.9821 | 67.9821 | 67.9821 | 67.9821 | 67.9821 | 67.9821 | 67.9821 | 67.9821 | 67.9821 | 67.9821 | 67.9821 | 67.9821
85% | 15.8829 | 38.9945 | 51.8151 | 55.3073 | 55.2074 | 55.2062 | 55.6056 | 56.0437 | 56.9423 | 57.5879 | 57.9388 | 58.3233 | 58.6747 | 59.3082 | 60.094 | 60.0409 | 60.0409 | 60.0409 | 60.0409 | 60.0409 | 60.0409 | 60.0409 | 60.0409 | 60.0409 | 60.0409 | 60.0409 | 60.0409 | 60.0409 | 60.0409 | 60.0409 | 60.0409 | 85% | 26.4715 | 43.482 | 56.3283 | 59.6922 | 59.4921 | 59.5089 | 59.8552 | 60.767 | 61.3783 | 61.9762 | 62.6753 | 63.3237 | 63.9528 | 64.0256 | 64.7596 | 64.2053 | 64.2053 | 64.2053 | 64.2053 | 64.2053 | 64.2053 | 64.2053 | 64.2053 | 64.2053 | 64.2053 | 64.2053 | 64.2053 | 64.2053 | 64.2053 | 64.2053 | 64.2053
80% | 31.0095 | 36.7007 | 48.7671 | 52.0539 | 51.9599 | 51.9588 | 52.3347 | 52.747 | 53.5928 | 54.2003 | 54.5307 | 54.8925 | 55.2232 | 55.8194 | 56.5591 | 56.5091 | 56.5091 | 56.5091 | 56.5091 | 56.5091 | 56.5091 | 56.5091 | 56.5091 | 56.5091 | 56.5091 | 56.5091 | 56.5091 | 56.5091 | 56.5091 | 56.5091 | 56.5091 | 80% | 34.0348 | 40.9243 | 53.0149 | 56.1809 | 55.9926 | 56.0084 | 56.3343 | 57.1924 | 57.7678 | 58.3305 | 58.9885 | 59.5988 | 60.1908 | 60.2594 | 60.9502 | 60.4285 | 60.4285 | 60.4285 | 60.4285 | 60.4285 | 60.4285 | 60.4285 | 60.4285 | 60.4285 | 60.4285 | 60.4285 | 60.4285 | 60.4285 | 60.4285 | 60.4285 | 60.4285
75% | 72.9857 | 34.4069 | 45.7192 | 48.8006 | 48.7124 | 48.7113 | 49.0638 | 49.4504 | 50.2432 | 50.8128 | 51.1225 | 51.4618 | 51.7718 | 52.3307 | 53.0241 | 52.9773 | 52.9773 | 52.9773 | 52.9773 | 52.9773 | 52.9773 | 52.9773 | 52.9773 | 52.9773 | 52.9773 | 52.9773 | 52.9773 | 52.9773 | 52.9773 | 52.9773 | 52.9773 | 75% | 48.405 | 38.3665 | 49.7015 | 52.6696 | 52.493 | 52.5079 | 52.8134 | 53.6179 | 54.1573 | 54.6849 | 55.3017 | 55.8739 | 56.4289 | 56.4932 | 57.1408 | 56.6517 | 56.6517 | 56.6517 | 56.6517 | 56.6517 | 56.6517 | 56.6517 | 56.6517 | 56.6517 | 56.6517 | 56.6517 | 56.6517 | 56.6517 | 56.6517 | 56.6517 | 56.6517
70% | 150.5094 | 32.1131 | 42.6712 | 45.5472 | 45.4649 | 45.4639 | 45.7929 | 46.1537 | 46.8937 | 47.4253 | 47.7143 | 48.031 | 48.3203 | 48.842 | 49.4892 | 49.4455 | 49.4455 | 49.4455 | 49.4455 | 49.4455 | 49.4455 | 49.4455 | 49.4455 | 49.4455 | 49.4455 | 49.4455 | 49.4455 | 49.4455 | 49.4455 | 49.4455 | 49.4455 | 70% | 76.3892 | 35.8087 | 46.388 | 49.1583 | 48.9935 | 49.0073 | 49.2925 | 50.0434 | 50.5468 | 51.0392 | 51.6149 | 52.149 | 52.667 | 52.727 | 53.3315 | 52.875 | 52.875 | 52.875 | 52.875 | 52.875 | 52.875 | 52.875 | 52.875 | 52.875 | 52.875 | 52.875 | 52.875 | 52.875 | 52.875 | 52.875 | 52.875
65% | 359.6342 | 29.8193 | 39.6233 | 42.2938 | 42.2174 | 42.2165 | 42.5219 | 42.857 | 43.5441 | 44.0378 | 44.3062 | 44.6002 | 44.8689 | 45.3533 | 45.9543 | 45.9136 | 45.9136 | 45.9136 | 45.9136 | 45.9136 | 45.9136 | 45.9136 | 45.9136 | 45.9136 | 45.9136 | 45.9136 | 45.9136 | 45.9136 | 45.9136 | 45.9136 | 45.9136 | 65% | 114.2056 | 33.251 | 43.0746 | 45.647 | 45.494 | 45.5068 | 45.7716 | 46.4689 | 46.9363 | 47.3936 | 47.9282 | 48.424 | 48.9051 | 48.9608 | 49.5221 | 49.0982 | 49.0982 | 49.0982 | 49.0982 | 49.0982 | 49.0982 | 49.0982 | 49.0982 | 49.0982 | 49.0982 | 49.0982 | 49.0982 | 49.0982 | 49.0982 | 49.0982 | 49.0982
60% | 689.7717 | 27.5255 | 36.5753 | 39.0405 | 38.9699 | 38.9691 | 39.251 | 39.5603 | 40.1946 | 40.6503 | 40.898 | 41.1694 | 41.4174 | 41.8646 | 42.4193 | 42.3818 | 42.3818 | 42.3818 | 42.3818 | 42.3818 | 42.3818 | 42.3818 | 42.3818 | 42.3818 | 42.3818 | 42.3818 | 42.3818 | 42.3818 | 42.3818 | 42.3818 | 42.3818 | 60% | 178.1154 | 30.6932 | 39.7612 | 42.1357 | 41.9944 | 42.0063 | 42.2508 | 42.8943 | 43.3258 | 43.7479 | 44.2414 | 44.6991 | 45.1431 | 45.1946 | 45.7127 | 45.3214 | 45.3214 | 45.3214 | 45.3214 | 45.3214 | 45.3214 | 45.3214 | 45.3214 | 45.3214 | 45.3214 | 45.3214 | 45.3214 | 45.3214 | 45.3214 | 45.3214 | 45.3214
55% | 1095.5419 | 25.2317 | 33.5274 | 35.7871 | 35.7224 | 35.7217 | 35.9801 | 36.2636 | 36.845 | 37.2627 | 37.4898 | 37.7386 | 37.966 | 38.3759 | 38.8844 | 38.85 | 38.85 | 38.85 | 38.85 | 38.85 | 38.85 | 38.85 | 38.85 | 38.85 | 38.85 | 38.85 | 38.85 | 38.85 | 38.85 | 38.85 | 38.85 | 55% | 311.6074 | 28.1354 | 36.4477 | 38.6243 | 38.4949 | 38.5058 | 38.7299 | 39.3198 | 39.7153 | 40.1022 | 40.5546 | 40.9742 | 41.3812 | 41.4284 | 41.9033 | 41.5446 | 41.5446 | 41.5446 | 41.5446 | 41.5446 | 41.5446 | 41.5446 | 41.5446 | 41.5446 | 41.5446 | 41.5446 | 41.5446 | 41.5446 | 41.5446 | 41.5446 | 41.5446
50% | 1666.1918 | 22.9379 | 30.4794 | 32.5337 | 32.4749 | 32.4742 | 32.7092 | 32.9669 | 33.4955 | 33.8752 | 34.0817 | 34.3078 | 34.5145 | 34.8872 | 35.3494 | 35.3182 | 35.3182 | 35.3182 | 35.3182 | 35.3182 | 35.3182 | 35.3182 | 35.3182 | 35.3182 | 35.3182 | 35.3182 | 35.3182 | 35.3182 | 35.3182 | 35.3182 | 35.3182 | 50% | 636.0723 | 25.5777 | 33.1343 | 35.113 | 34.9954 | 35.0052 | 35.209 | 35.7453 | 36.1049 | 36.4566 | 36.8678 | 37.2493 | 37.6193 | 37.6621 | 38.0939 | 37.7678 | 37.7678 | 37.7678 | 37.7678 | 37.7678 | 37.7678 | 37.7678 | 37.7678 | 37.7678 | 37.7678 | 37.7678 | 37.7678 | 37.7678 | 37.7678 | 37.7678 | 37.7678
45% | 2506.0947 | 20.6442 | 27.4315 | 29.2803 | 29.2274 | 29.2268 | 29.4383 | 29.6702 | 30.1459 | 30.4877 | 30.6735 | 30.8771 | 31.0631 | 31.3984 | 31.8145 | 31.7864 | 31.7864 | 31.7864 | 31.7864 | 31.7864 | 31.7864 | 31.7864 | 31.7864 | 31.7864 | 31.7864 | 31.7864 | 31.7864 | 31.7864 | 31.7864 | 31.7864 | 31.7864 | 45% | 1179.4944 | 23.0199 | 29.8209 | 31.6017 | 31.4958 | 31.5047 | 31.6881 | 32.1707 | 32.4944 | 32.8109 | 33.181 | 33.5243 | 33.8573 | 33.8959 | 34.2845 | 33.991 | 33.991 | 33.991 | 33.991 | 33.991 | 33.991 | 33.991 | 33.991 | 33.991 | 33.991 | 33.991 | 33.991 | 33.991 | 33.991 | 33.991 | 33.991
40% | 3164.4787 | 18.3504 | 24.3836 | 26.027 | 25.9799 | 25.9794 | 26.1673 | 26.3735 | 26.7964 | 27.1002 | 27.2653 | 27.4463 | 27.6116 | 27.9097 | 28.2795 | 28.2546 | 28.2546 | 28.2546 | 28.2546 | 28.2546 | 28.2546 | 28.2546 | 28.2546 | 28.2546 | 28.2546 | 28.2546 | 28.2546 | 28.2546 | 28.2546 | 28.2546 | 28.2546 | 40% | 1808.3816 | 20.4621 | 26.5075 | 28.0904 | 27.9963 | 28.0042 | 28.1672 | 28.5962 | 28.8839 | 29.1653 | 29.4942 | 29.7994 | 30.0954 | 30.1297 | 30.4751 | 30.2143 | 30.2143 | 30.2143 | 30.2143 | 30.2143 | 30.2143 | 30.2143 | 30.2143 | 30.2143 | 30.2143 | 30.2143 | 30.2143 | 30.2143 | 30.2143 | 30.2143 | 30.2143
35% | 3551.3408 | 16.0566 | 21.3356 | 22.7736 | 22.7325 | 22.732 | 22.8964 | 23.0768 | 23.4468 | 23.7126 | 23.8572 | 24.0155 | 24.1602 | 24.421 | 24.7446 | 24.7227 | 24.7227 | 24.7227 | 24.7227 | 24.7227 | 24.7227 | 24.7227 | 24.7227 | 24.7227 | 24.7227 | 24.7227 | 24.7227 | 24.7227 | 24.7227 | 24.7227 | 24.7227 | 35% | 2779.1293 | 17.9044 | 23.194 | 24.5791 | 24.4968 | 24.5037 | 24.6463 | 25.0217 | 25.2734 | 25.5196 | 25.8075 | 26.0745 | 26.3335 | 26.3635 | 26.6657 | 26.4375 | 26.4375 | 26.4375 | 26.4375 | 26.4375 | 26.4375 | 26.4375 | 26.4375 | 26.4375 | 26.4375 | 26.4375 | 26.4375 | 26.4375 | 26.4375 | 26.4375 | 26.4375
30% | 3758.953 | 13.7628 | 18.2877 | 19.5202 | 19.485 | 19.4845 | 19.6255 | 19.7801 | 20.0973 | 20.3251 | 20.449 | 20.5847 | 20.7087 | 20.9323 | 21.2097 | 21.1909 | 21.1909 | 21.1909 | 21.1909 | 21.1909 | 21.1909 | 21.1909 | 21.1909 | 21.1909 | 21.1909 | 21.1909 | 21.1909 | 21.1909 | 21.1909 | 21.1909 | 21.1909 | 30% | 3814.165 | 15.3466 | 19.8806 | 21.0678 | 20.9972 | 21.0031 | 21.1254 | 21.4472 | 21.6629 | 21.8739 | 22.1207 | 22.3496 | 22.5716 | 22.5973 | 22.8563 | 22.6607 | 22.6607 | 22.6607 | 22.6607 | 22.6607 | 22.6607 | 22.6607 | 22.6607 | 22.6607 | 22.6607 | 22.6607 | 22.6607 | 22.6607 | 22.6607 | 22.6607 | 22.6607
25% | 3926.4798 | 11.469 | 15.2397 | 16.2669 | 16.2375 | 16.2371 | 16.3546 | 16.4835 | 16.7477 | 16.9376 | 17.0408 | 17.1539 | 17.2573 | 17.4436 | 17.6747 | 17.6591 | 17.6591 | 17.6591 | 17.6591 | 17.6591 | 17.6591 | 17.6591 | 17.6591 | 17.6591 | 17.6591 | 17.6591 | 17.6591 | 17.6591 | 17.6591 | 17.6591 | 17.6591 | 25% | 4166.9923 | 12.7888 | 16.5672 | 17.5565 | 17.4977 | 17.5026 | 17.6045 | 17.8726 | 18.0524 | 18.2283 | 18.4339 | 18.6246 | 18.8096 | 18.8311 | 19.0469 | 18.8839 | 18.8839 | 18.8839 | 18.8839 | 18.8839 | 18.8839 | 18.8839 | 18.8839 | 18.8839 | 18.8839 | 18.8839 | 18.8839 | 18.8839 | 18.8839 | 18.8839 | 18.8839
20% | 4050.5177 | 9.1752 | 12.1918 | 13.0135 | 12.99 | 12.9897 | 13.0837 | 13.1868 | 13.3982 | 13.5501 | 13.6327 | 13.7231 | 13.8058 | 13.9549 | 14.1398 | 14.1273 | 14.1273 | 14.1273 | 14.1273 | 14.1273 | 14.1273 | 14.1273 | 14.1273 | 14.1273 | 14.1273 | 14.1273 | 14.1273 | 14.1273 | 14.1273 | 14.1273 | 14.1273 | 20% | 4282.7105 | 10.2311 | 13.2537 | 14.0452 | 13.9981 | 14.0021 | 14.0836 | 14.2981 | 14.4419 | 14.5826 | 14.7471 | 14.8997 | 15.0477 | 15.0649 | 15.2376 | 15.1071 | 15.1071 | 15.1071 | 15.1071 | 15.1071 | 15.1071 | 15.1071 | 15.1071 | 15.1071 | 15.1071 | 15.1071 | 15.1071 | 15.1071 | 15.1071 | 15.1071 | 15.1071
15% | 4152.622 | 6.8814 | 9.1438 | 9.7601 | 9.7425 | 9.7423 | 9.8128 | 9.8901 | 10.0486 | 10.1626 | 10.2245 | 10.2924 | 10.3544 | 10.4661 | 10.6048 | 10.5955 | 10.5955 | 10.5955 | 10.5955 | 10.5955 | 10.5955 | 10.5955 | 10.5955 | 10.5955 | 10.5955 | 10.5955 | 10.5955 | 10.5955 | 10.5955 | 10.5955 | 10.5955 | 15% | 4364.7722 | 7.6733 | 9.9403 | 10.5339 | 10.4986 | 10.5016 | 10.5627 | 10.7236 | 10.8315 | 10.937 | 11.0603 | 11.1748 | 11.2858 | 11.2986 | 11.4282 | 11.3303 | 11.3303 | 11.3303 | 11.3303 | 11.3303 | 11.3303 | 11.3303 | 11.3303 | 11.3303 | 11.3303 | 11.3303 | 11.3303 | 11.3303 | 11.3303 | 11.3303 | 11.3303
10% | 4248.2976 | 4.5876 | 6.0959 | 6.5067 | 6.495 | 6.4948 | 6.5418 | 6.5934 | 6.6991 | 6.775 | 6.8163 | 6.8616 | 6.9029 | 6.9774 | 7.0699 | 7.0636 | 7.0636 | 7.0636 | 7.0636 | 7.0636 | 7.0636 | 7.0636 | 7.0636 | 7.0636 | 7.0636 | 7.0636 | 7.0636 | 7.0636 | 7.0636 | 7.0636 | 7.0636 | 10% | 4391.6218 | 5.1155 | 6.6269 | 7.0226 | 6.9991 | 7.001 | 7.0418 | 7.1491 | 7.221 | 7.2913 | 7.3736 | 7.4499 | 7.5239 | 7.5324 | 7.6188 | 7.5536 | 7.5536 | 7.5536 | 7.5536 | 7.5536 | 7.5536 | 7.5536 | 7.5536 | 7.5536 | 7.5536 | 7.5536 | 7.5536 | 7.5536 | 7.5536 | 7.5536 | 7.5536
5% | 4361.7469 | 2.2938 | 3.0479 | 3.2534 | 3.2475 | 3.2474 | 3.2709 | 3.2967 | 3.3495 | 3.3875 | 3.4082 | 3.4308 | 3.4515 | 3.4887 | 3.5349 | 3.5318 | 3.5318 | 3.5318 | 3.5318 | 3.5318 | 3.5318 | 3.5318 | 3.5318 | 3.5318 | 3.5318 | 3.5318 | 3.5318 | 3.5318 | 3.5318 | 3.5318 | 3.5318 | 5% | 4391.6218 | 2.5578 | 3.3134 | 3.5113 | 3.4995 | 3.5005 | 3.5209 | 3.5745 | 3.6105 | 3.6457 | 3.6868 | 3.7249 | 3.7619 | 3.7662 | 3.8094 | 3.7768 | 3.7768 | 3.7768 | 3.7768 | 3.7768 | 3.7768 | 3.7768 | 3.7768 | 3.7768 | 3.7768 | 3.7768 | 3.7768 | 3.7768 | 3.7768 | 3.7768 | 3.7768
9.992e-14% | 4391.6218 | 4.5839e-14 | 6.091e-14 | 6.5015e-14 | 6.4898e-14 | 6.4897e-14 | 6.5366e-14 | 6.5881e-14 | 6.6937e-14 | 6.7696e-14 | 6.8109e-14 | 6.8561e-14 | 6.8974e-14 | 6.9719e-14 | 7.0642e-14 | 7.058e-14 | 7.058e-14 | 7.058e-14 | 7.058e-14 | 7.058e-14 | 7.058e-14 | 7.058e-14 | 7.058e-14 | 7.058e-14 | 7.058e-14 | 7.058e-14 | 7.058e-14 | 7.058e-14 | 7.058e-14 | 7.058e-14 | 7.058e-14 | 9.992e-14% | 4391.6218 | 5.1114e-14 | 6.6216e-14 | 7.017e-14 | 6.9935e-14 | 6.9955e-14 | 7.0362e-14 | 7.1433e-14 | 7.2152e-14 | 7.2855e-14 | 7.3677e-14 | 7.4439e-14 | 7.5178e-14 | 7.5264e-14 | 7.6127e-14 | 7.5475e-14 | 7.5475e-14 | 7.5475e-14 | 7.5475e-14 | 7.5475e-14 | 7.5475e-14 | 7.5475e-14 | 7.5475e-14 | 7.5475e-14 | 7.5475e-14 | 7.5475e-14 | 7.5475e-14 | 7.5475e-14 | 7.5475e-14 | 7.5475e-14 | 7.5475e-14

## Locational VCR
Base case |  | Energy Usage (CY 2024 kWh) | Energy Usage (CY 2024 %) | Tailored VCR
Dec 24 AER VCR ($/kWh) - Res | 49.23 | 67934749.1441 | 34.06% | 16.7657
Dec 24 AER VCR ($/kWh) - Com | 34.39 | 101368150.4504 | 50.82% | 17.4756
Dec 24 AER VCR ($/kWh) - Ind | 33.49 | 17726336.2671 | 8.886% | 2.976
Dec 24 AER VCR ($/kWh) - Agr | 22.25 | 12451243.5083 | 6.242% | 1.3888
|  | 199480479.3698 |  | 38.6062 | KW/h
|  |  |  | 38606.1513 | MW/h

## E@R N
Option 1 - Do Nothing / Base Case
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99%
98%
97%
95%
90%
85%
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1 Winter POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 1 Winter POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99
98%
97%
95%
90%
85%
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1 Summer POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 1 Summer POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2 - 1B New PHS ZSS + Three new feeders
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99%
98%
97%
95%
90%
85%
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2 Winter POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 2 Winter POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99
98%
97%
95%
90%
85%
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2 Summer POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 2 Summer POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 - 2B PHM 3rd Tx + Switchroom + Two new feeders + OFR12 New Feeder
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99%
98%
97%
95%
90%
85%
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 Winter POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 3 Winter POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99
98%
97%
95%
90%
85%
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 Summer POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 3 Summer POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 - 3B OFR 3rd Tx + Switchroom + Two new feeders + OFR12 New Feeder
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99%
98%
97%
95%
90%
85%
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 Winter POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 4 Winter POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99
98%
97%
95%
90%
85%
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 Summer POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 4 Summer POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 - 4B LLG 2nd Tx + Switchroom + Two new feeders + OFR12 New Feeder
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99%
98%
97%
95%
90%
85%
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 Winter POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 5 Winter POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99
98%
97%
95%
90%
85%
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 Summer POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 5 Summer POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 6 -
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99%
98%
97%
95%
90%
85%
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 6 Winter POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 6 Winter POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99
98%
97%
95%
90%
85%
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 6 Summer POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 6 Summer POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 7 -
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99%
98%
97%
95%
90%
85%
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 7 Winter POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 7 Winter POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99
98%
97%
95%
90%
85%
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 7 Summer POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 7 Summer POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 8 -
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99%
98%
97%
95%
90%
85%
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 8 Winter POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 8 Winter POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99
98%
97%
95%
90%
85%
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 8 Summer POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 8 Summer POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## E@R N-1
Option 1 - Do Nothing / Base Case
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% |  | 9.8725 | 15.8941 | 16.9205 | 17.721 | 19.0994 | 22.2353 | 24.3344 | 26.9936 | 28.3739 | 29.5883 | 27.3508 | 29.973 | 34.0954 | 30.9671 | 30.9671 | 30.9671 | 30.9671 | 30.9671 | 30.9671 | 30.9671 | 30.9671 | 30.9671 | 30.9671 | 30.9671 | 30.9671 | 30.9671 | 30.9671 | 30.9671 | 30.9671 |  |  | 13.7943 | 20.0509 | 21.019 | 21.6336 | 22.9821 | 26.167 | 27.9059 | 31.2184 | 41.2876 | 32.9866 | 31.3629 | 33.5547 | 38.348 | 35.1035 | 35.1035 | 35.1035 | 35.1035 | 35.1035 | 35.1035 | 35.1035 | 35.1035 | 35.1035 | 35.1035 | 35.1035 | 35.1035 | 35.1035 | 35.1035 | 35.1035 | 35.1035
98% |  | 10.848 | 18.0013 | 19.2206 | 20.1716 | 21.809 | 25.5342 | 28.0279 | 31.1869 | 32.8266 | 34.2691 | 31.6112 | 34.7262 | 39.6233 | 35.9071 | 35.9071 | 35.9071 | 35.9071 | 35.9071 | 35.9071 | 35.9071 | 35.9071 | 35.9071 | 35.9071 | 35.9071 | 35.9071 | 35.9071 | 35.9071 | 35.9071 | 35.9071 |  |  | 15.5069 | 22.9393 | 24.0893 | 24.8195 | 26.4214 | 30.2049 | 32.2706 | 36.2057 | 48.1672 | 38.3061 | 36.3773 | 38.981 | 44.6752 | 40.8209 | 40.8209 | 40.8209 | 40.8209 | 40.8209 | 40.8209 | 40.8209 | 40.8209 | 40.8209 | 40.8209 | 40.8209 | 40.8209 | 40.8209 | 40.8209 | 40.8209 | 40.8209
97% |  | 19.698 | 33.8593 | 36.2732 | 38.1558 | 41.3974 | 48.7723 | 53.7089 | 59.9627 | 63.2089 | 66.0646 | 60.8028 | 66.9695 | 76.6644 | 69.3073 | 69.3073 | 69.3073 | 69.3073 | 69.3073 | 69.3073 | 69.3073 | 69.3073 | 69.3073 | 69.3073 | 69.3073 | 69.3073 | 69.3073 | 69.3073 | 69.3073 | 69.3073 |  |  | 28.9211 | 43.6351 | 45.9118 | 47.3573 | 50.5286 | 58.0187 | 62.1081 | 69.8984 | 93.5787 | 74.0567 | 70.2382 | 75.3927 | 86.6655 | 79.0351 | 79.0351 | 79.0351 | 79.0351 | 79.0351 | 79.0351 | 79.0351 | 79.0351 | 79.0351 | 79.0351 | 79.0351 | 79.0351 | 79.0351 | 79.0351 | 79.0351 | 79.0351
95% |  | 50.103 | 91.9331 | 99.0634 | 104.6245 | 114.1996 | 135.9838 | 150.5658 | 169.0387 | 178.6273 | 187.0628 | 171.5201 | 189.7357 | 218.3728 | 196.6412 | 196.6412 | 196.6412 | 196.6412 | 196.6412 | 196.6412 | 196.6412 | 196.6412 | 196.6412 | 196.6412 | 196.6412 | 196.6412 | 196.6412 | 196.6412 | 196.6412 | 196.6412 |  |  | 77.3465 | 120.8094 | 127.5343 | 131.8043 | 141.1717 | 163.2964 | 175.3759 | 198.3872 | 268.3351 | 210.6702 | 199.3908 | 214.6165 | 247.9145 | 225.3755 | 225.3755 | 225.3755 | 225.3755 | 225.3755 | 225.3755 | 225.3755 | 225.3755 | 225.3755 | 225.3755 | 225.3755 | 225.3755 | 225.3755 | 225.3755 | 225.3755 | 225.3755
90% |  | 166.6526 | 397.287 | 436.6005 | 467.2624 | 520.0555 | 640.1647 | 720.5641 | 822.4165 | 875.2838 | 921.7942 | 836.0975 | 936.5313 | 1094.4248 | 974.6055 | 974.6055 | 974.6055 | 974.6055 | 974.6055 | 974.6055 | 974.6055 | 974.6055 | 974.6055 | 974.6055 | 974.6055 | 974.6055 | 974.6055 | 974.6055 | 974.6055 | 974.6055 |  |  | 316.8623 | 556.4991 | 593.5776 | 617.1207 | 668.7691 | 790.7554 | 857.3571 | 984.2321 | 1369.8972 | 1051.9556 | 989.7659 | 1073.714 | 1257.3061 | 1133.0351 | 1133.0351 | 1133.0351 | 1133.0351 | 1133.0351 | 1133.0351 | 1133.0351 | 1133.0351 | 1133.0351 | 1133.0351 | 1133.0351 | 1133.0351 | 1133.0351 | 1133.0351 | 1133.0351 | 1133.0351
85% |  | 49.283 | 550.9121 | 646.9524 | 721.8571 | 850.8267 | 1144.2449 | 1340.6551 | 1589.473 | 1718.6242 | 1832.2457 | 1622.8948 | 1868.2474 | 2253.97 | 1961.2601 | 1961.2601 | 1961.2601 | 1961.2601 | 1961.2601 | 1961.2601 | 1961.2601 | 1961.2601 | 1961.2601 | 1961.2601 | 1961.2601 | 1961.2601 | 1961.2601 | 1961.2601 | 1961.2601 | 1961.2601 |  |  | 354.4405 | 939.8561 | 1030.4361 | 1087.9502 | 1214.1234 | 1512.1274 | 1674.8304 | 1984.7771 | 2926.9292 | 2150.2208 | 1998.2958 | 2203.3748 | 2651.8773 | 2348.2922 | 2348.2922 | 2348.2922 | 2348.2922 | 2348.2922 | 2348.2922 | 2348.2922 | 2348.2922 | 2348.2922 | 2348.2922 | 2348.2922 | 2348.2922 | 2348.2922 | 2348.2922 | 2348.2922 | 2348.2922
80% |  |  | 170.3674 | 283.6364 | 390.7399 | 591.1469 | 1047.2057 | 1352.4853 | 1739.2221 | 1939.9613 | 2116.5629 | 1791.1696 | 2172.5202 | 2772.0475 | 2317.0894 | 2317.0894 | 2317.0894 | 2317.0894 | 2317.0894 | 2317.0894 | 2317.0894 | 2317.0894 | 2317.0894 | 2317.0894 | 2317.0894 | 2317.0894 | 2317.0894 | 2317.0894 | 2317.0894 | 2317.0894 |  |  | 26.6685 | 729.5248 | 870.3131 | 959.707 | 1155.8176 | 1619.0041 | 1871.8928 | 2353.6419 | 3818.0255 | 2610.7904 | 2374.6539 | 2693.4076 | 3390.5133 | 2918.6521 | 2918.6521 | 2918.6521 | 2918.6521 | 2918.6521 | 2918.6521 | 2918.6521 | 2918.6521 | 2918.6521 | 2918.6521 | 2918.6521 | 2918.6521 | 2918.6521 | 2918.6521 | 2918.6521 | 2918.6521
75% | [5 empty] | 24.883 | 275.7172 | 581.2462 | 1007.9249 | 1229.3962 | 1424.237 | 1065.2374 | 1485.9735 | 2147.4195 | 1645.4738 | 1645.4738 | 1645.4738 | 1645.4738 | 1645.4738 | 1645.4738 | 1645.4738 | 1645.4738 | 1645.4738 | 1645.4738 | 1645.4738 | 1645.4738 | 1645.4738 | 1645.4738 | 1645.4738 | 1645.4738 |  |  |  | 73.1703 | 147.4946 | 207.5247 | 373.0825 | 875.2908 | 1154.2977 | 1685.8014 | 3301.4252 | 1969.5079 | 1708.9835 | 2060.6577 | 2829.7599 | 2309.1653 | 2309.1653 | 2309.1653 | 2309.1653 | 2309.1653 | 2309.1653 | 2309.1653 | 2309.1653 | 2309.1653 | 2309.1653 | 2309.1653 | 2309.1653 | 2309.1653 | 2309.1653 | 2309.1653 | 2309.1653
70% | [7 empty] | 3.4379 | 133.5638 | 272.0098 | 431.8215 | 164.8836 | 489.6671 | 1193.5489 | 654.2363 | 654.2363 | 654.2363 | 654.2363 | 654.2363 | 654.2363 | 654.2363 | 654.2363 | 654.2363 | 654.2363 | 654.2363 | 654.2363 | 654.2363 | 654.2363 | 654.2363 | 654.2363 | [7 empty] | 73.4213 | 219.8269 | 697.566 | 2433.4635 | 1002.3928 | 722.4739 | 1100.3282 | 1926.6855 | 1367.3357 | 1367.3357 | 1367.3357 | 1367.3357 | 1367.3357 | 1367.3357 | 1367.3357 | 1367.3357 | 1367.3357 | 1367.3357 | 1367.3357 | 1367.3357 | 1367.3357 | 1367.3357 | 1367.3357 | 1367.3357
65% | FY38: 138.0019; FY39: 0.607; FY40: 0.607; FY41: 0.607; FY42: 0.607; FY43: 0.607; FY44: 0.607; FY45: 0.607; FY46: 0.607; FY47: 0.607; FY48: 0.607; FY49: 0.607; FY50: 0.607; FY51: 0.607; FY52: 0.607; FY53: 0.607; FY54: 0.607 | [9 empty] | 2.7969 | 1216.8668 | 62.358 | 4.774 | 97.5063 | 684.2805 | 231.4677 | 231.4677 | 231.4677 | 231.4677 | 231.4677 | 231.4677 | 231.4677 | 231.4677 | 231.4677 | 231.4677 | 231.4677 | 231.4677 | 231.4677 | 231.4677 | 231.4677 | 231.4677
60% | [40 empty] | 77.6441
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 306.4572 | 1278.2542 | 1538.6669 | 1760.5324 | 2183.4175 | 3339.858 | 4255.0255 | 5579.7822 | 6338.312 | 7043.6462 | 5771.5678 | 7274.3439 | 9968.1685 | 7886.0948 | 7886.0948 | 7886.0948 | 7886.0948 | 7886.0948 | 7886.0948 | 7886.0948 | 7886.0948 | 7886.0948 | 7886.0948 | 7886.0948 | 7886.0948 | 7886.0948 | 7886.0948 | 7886.0948 | 7886.0948 | E @ R (MWh) | 0 | 833.5401 | 2506.4849 | 2860.3759 | 3097.9173 | 3652.8965 | 5148.2859 | 6075.8653 | 8044.5252 | 15595.6201 | 9203.2451 | 8136.3162 | 9591.5333 | 13158.0259 | 10688.2832 | 10688.2832 | 10688.2832 | 10688.2832 | 10688.2832 | 10688.2832 | 10688.2832 | 10688.2832 | 10688.2832 | 10688.2832 | 10688.2832 | 10688.2832 | 10688.2832 | 10688.2832 | 10688.2832 | 10688.2832
Option 1 Winter POE50 W E @ R (MWh) N 1 | 0 | 214.5201 | 894.7779 | 1077.0669 | 1232.3727 | 1528.3922 | 2337.9006 | 2978.5179 | 3905.8475 | 4436.8184 | 4930.5523 | 4040.0974 | 5092.0407 | 6977.718 | 5520.2664 | 5520.2664 | 5520.2664 | 5520.2664 | 5520.2664 | 5520.2664 | 5520.2664 | 5520.2664 | 5520.2664 | 5520.2664 | 5520.2664 | 5520.2664 | 5520.2664 | 5520.2664 | 5520.2664 | 5520.2664 | Option 1 Winter POE10 W E @ R (MWh) N 1 | 0 | 250.062 | 751.9455 | 858.1128 | 929.3752 | 1095.8689 | 1544.4858 | 1822.7596 | 2413.3575 | 4678.686 | 2760.9735 | 2440.8949 | 2877.46 | 3947.4078 | 3206.485 | 3206.485 | 3206.485 | 3206.485 | 3206.485 | 3206.485 | 3206.485 | 3206.485 | 3206.485 | 3206.485 | 3206.485 | 3206.485 | 3206.485 | 3206.485 | 3206.485 | 3206.485
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 8.924 | 31.6709 | 37.6273 | 37.273 | 37.3028 | 37.916 | 39.5304 | 40.6128 | 41.6716 | 42.9095 | 44.0577 | 45.1715 | 45.3005 | 46.6002 | 45.6187 | 45.6187 | 45.6187 | 45.6187 | 45.6187 | 45.6187 | 45.6187 | 45.6187 | 45.6187 | 45.6187 | 45.6187 | 45.6187 | 45.6187 | 45.6187 | 45.6187 | 45.6187
98% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4.0751 | 15.3343 | 18.2825 | 18.1072 | 18.1219 | 18.4254 | 19.2245 | 19.7603 | 20.2843 | 20.897 | 21.4654 | 22.0167 | 22.0806 | 22.7239 | 22.238 | 22.238 | 22.238 | 22.238 | 22.238 | 22.238 | 22.238 | 22.238 | 22.238 | 22.238 | 22.238 | 22.238 | 22.238 | 22.238 | 22.238 | 22.238
97% |  | 5.4588 | 6.9736 | 6.9303 | 6.9298 | 7.103 | 7.2931 | 7.6829 | 7.9629 | 8.1151 | 8.2819 | 8.4343 | 8.7091 | 9.05 | 9.027 | 9.027 | 9.027 | 9.027 | 9.027 | 9.027 | 9.027 | 9.027 | 9.027 | 9.027 | 9.027 | 9.027 | 9.027 | 9.027 | 9.027 | 9.027 |  | 7.3764 | 29.6661 | 35.5027 | 35.1556 | 35.1847 | 35.7856 | 37.3676 | 38.4283 | 39.4657 | 40.6787 | 41.8039 | 42.8953 | 43.0218 | 44.2953 | 43.3335 | 43.3335 | 43.3335 | 43.3335 | 43.3335 | 43.3335 | 43.3335 | 43.3335 | 43.3335 | 43.3335 | 43.3335 | 43.3335 | 43.3335 | 43.3335 | 43.3335 | 43.3335
95% |  | 25.5649 | 33.0227 | 32.8093 | 32.8067 | 33.6597 | 34.5953 | 36.5142 | 37.8928 | 38.6423 | 39.4634 | 40.2137 | 41.5666 | 43.2448 | 43.1314 | 43.1314 | 43.1314 | 43.1314 | 43.1314 | 43.1314 | 43.1314 | 43.1314 | 43.1314 | 43.1314 | 43.1314 | 43.1314 | 43.1314 | 43.1314 | 43.1314 | 43.1314 |  | 9.3236 | 42.2437 | 50.864 | 50.3513 | 50.3943 | 51.2818 | 53.6182 | 55.1847 | 56.717 | 58.5085 | 60.1702 | 61.7822 | 61.969 | 63.8499 | 62.4294 | 62.4294 | 62.4294 | 62.4294 | 62.4294 | 62.4294 | 62.4294 | 62.4294 | 62.4294 | 62.4294 | 62.4294 | 62.4294 | 62.4294 | 62.4294 | 62.4294 | 62.4294
90% |  | 38.7554 | 51.6899 | 51.3198 | 51.3153 | 52.7947 | 54.4175 | 57.7455 | 60.1366 | 61.4365 | 62.8605 | 64.1618 | 66.5082 | 69.4189 | 69.2222 | 69.2222 | 69.2222 | 69.2222 | 69.2222 | 69.2222 | 69.2222 | 69.2222 | 69.2222 | 69.2222 | 69.2222 | 69.2222 | 69.2222 | 69.2222 | 69.2222 | 69.2222 |  | 23.6749 | 166.4146 | 203.7914 | 201.5685 | 201.7552 | 205.6032 | 215.7337 | 222.5261 | 229.1699 | 236.9378 | 244.1429 | 251.1324 | 251.9421 | 260.0977 | 253.9385 | 253.9385 | 253.9385 | 253.9385 | 253.9385 | 253.9385 | 253.9385 | 253.9385 | 253.9385 | 253.9385 | 253.9385 | 253.9385 | 253.9385 | 253.9385 | 253.9385 | 253.9385
85% |  | 85.1452 | 121.8514 | 120.801 | 120.7884 | 124.9866 | 129.5917 | 139.0363 | 145.8216 | 149.5106 | 153.5518 | 157.2446 | 163.9032 | 172.1633 | 171.605 | 171.605 | 171.605 | 171.605 | 171.605 | 171.605 | 171.605 | 171.605 | 171.605 | 171.605 | 171.605 | 171.605 | 171.605 | 171.605 | 171.605 | 171.605 |  | 2.1581 | 132.583 | 167.9395 | 165.8367 | 166.0133 | 169.6533 | 179.2362 | 185.6615 | 191.9461 | 199.2941 | 206.1098 | 212.7215 | 213.4874 | 221.2021 | 215.3759 | 215.3759 | 215.3759 | 215.3759 | 215.3759 | 215.3759 | 215.3759 | 215.3759 | 215.3759 | 215.3759 | 215.3759 | 215.3759 | 215.3759 | 215.3759 | 215.3759 | 215.3759
80% |  | 80.0361 | 131.3082 | 129.841 | 129.8234 | 135.6876 | 142.1201 | 155.3125 | 164.7904 | 169.9433 | 175.5881 | 180.7464 | 190.0472 | 201.5852 | 200.8054 | 200.8054 | 200.8054 | 200.8054 | 200.8054 | 200.8054 | 200.8054 | 200.8054 | 200.8054 | 200.8054 | 200.8054 | 200.8054 | 200.8054 | 200.8054 | 200.8054 | 200.8054 |  |  | 73.1492 | 97.8426 | 96.374 | 96.4973 | 99.0396 | 105.7324 | 110.2199 | 114.6092 | 119.7411 | 124.5013 | 129.1189 | 129.6539 | 135.0419 | 130.9728 | 130.9728 | 130.9728 | 130.9728 | 130.9728 | 130.9728 | 130.9728 | 130.9728 | 130.9728 | 130.9728 | 130.9728 | 130.9728 | 130.9728 | 130.9728 | 130.9728 | 130.9728
75% |  | 94.1589 | 227.8159 | 223.9912 | 223.9454 | 239.2321 | 256.0006 | 290.3908 | 315.098 | 328.5306 | 343.2457 | 356.6924 | 380.938 | 411.0152 | 408.9825 | 408.9825 | 408.9825 | 408.9825 | 408.9825 | 408.9825 | 408.9825 | 408.9825 | 408.9825 | 408.9825 | 408.9825 | 408.9825 | 408.9825 | 408.9825 | 408.9825 | 408.9825 |  |  | 91.3687 | 135.4427 | 132.8215 | 133.0415 | 137.5791 | 149.5248 | 157.5342 | 165.3684 | 174.5281 | 183.0243 | 191.2662 | 192.221 | 201.8378 | 194.575 | 194.575 | 194.575 | 194.575 | 194.575 | 194.575 | 194.575 | 194.575 | 194.575 | 194.575 | 194.575 | 194.575 | 194.575 | 194.575 | 194.575 | 194.575
70% |  | 6.5776 | 168.5277 | 161.9198 | 161.8408 | 188.2515 | 217.2224 | 276.6382 | 319.3247 | 342.5321 | 367.9553 | 391.1871 | 433.0761 | 485.0404 | 481.5284 | 481.5284 | 481.5284 | 481.5284 | 481.5284 | 481.5284 | 481.5284 | 481.5284 | 481.5284 | 481.5284 | 481.5284 | 481.5284 | 481.5284 | 481.5284 | 481.5284 | 481.5284 |  |  | 85.2049 | 165.4959 | 160.7208 | 161.1217 | 169.3879 | 191.1497 | 205.7408 | 220.0126 | 236.6991 | 252.1769 | 267.1913 | 268.9307 | 286.45 | 273.2191 | 273.2191 | 273.2191 | 273.2191 | 273.2191 | 273.2191 | 273.2191 | 273.2191 | 273.2191 | 273.2191 | 273.2191 | 273.2191 | 273.2191 | 273.2191 | 273.2191 | 273.2191
65% |  |  | 9.6236 | 6.9591 | 6.9298 | 20.0951 | 42.2143 | 111.9423 | 181.5617 | 226.0382 | 279.9918 | 333.9879 | 438.672 | 569.1816 | 560.3612 | 560.3612 | 560.3612 | 560.3612 | 560.3612 | 560.3612 | 560.3612 | 560.3612 | 560.3612 | 560.3612 | 560.3612 | 560.3612 | 560.3612 | 560.3612 | 560.3612 | 560.3612 |  |  | 10.9945 | 90.8581 | 84.8503 | 85.3547 | 95.7548 | 123.1346 | 141.4924 | 159.4485 | 180.4428 | 199.9162 | 218.8067 | 220.9952 | 243.0371 | 226.3906 | 226.3906 | 226.3906 | 226.3906 | 226.3906 | 226.3906 | 226.3906 | 226.3906 | 226.3906 | 226.3906 | 226.3906 | 226.3906 | 226.3906 | 226.3906 | 226.3906 | 226.3906
60% | [12 empty] | 5.9059 | 42.5222 | 39.014 | 39.014 | 39.014 | 39.014 | 39.014 | 39.014 | 39.014 | 39.014 | 39.014 | 39.014 | 39.014 | 39.014 | 39.014 | 39.014 | 39.014 | 39.014 |  |  |  | 3.8091 | 2.2281 | 2.3448 | 5.4041 | 19.2874 | 33.1836 | 50.2166 | 74.3153 | 100.576 | 129.3594 | 132.7839 | 167.2756 | 141.2268 | 141.2268 | 141.2268 | 141.2268 | 141.2268 | 141.2268 | 141.2268 | 141.2268 | 141.2268 | 141.2268 | 141.2268 | 141.2268 | 141.2268 | 141.2268 | 141.2268 | 141.2268
55% | [42 empty] | 0.36348 | 0.67093 | 8.8993 | 1.8255 | 1.8255 | 1.8255 | 1.8255 | 1.8255 | 1.8255 | 1.8255 | 1.8255 | 1.8255 | 1.8255 | 1.8255 | 1.8255 | 1.8255 | 1.8255 | 1.8255 | 1.8255
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 335.6968 | 750.8128 | 734.5714 | 734.3797 | 801.8103 | 883.4549 | 1075.2627 | 1232.5888 | 1324.7487 | 1430.9386 | 1532.6682 | 1729.3262 | 2003.2214 | 1983.6771 | 1983.6771 | 1983.6771 | 1983.6771 | 1983.6771 | 1983.6771 | 1983.6771 | 1983.6771 | 1983.6771 | 1983.6771 | 1983.6771 | 1983.6771 | 1983.6771 | 1983.6771 | 1983.6771 | 1983.6771 | E @ R (MWh) | 55.5322 | 678.63 | 1007.4559 | 985.2871 | 987.1322 | 1025.8309 | 1133.5396 | 1210.3445 | 1288.9099 | 1384.9521 | 1477.9447 | 1571.8256 | 1583.0571 | 1701.3108 | 1611.1437 | 1611.1437 | 1611.1437 | 1611.1437 | 1611.1437 | 1611.1437 | 1611.1437 | 1611.1437 | 1611.1437 | 1611.1437 | 1611.1437 | 1611.1437 | 1611.1437 | 1611.1437 | 1611.1437 | 1611.1437
Option 1 Summer POE50 W E @ R (MWh) N 1 | 0 | 234.9878 | 525.569 | 514.2 | 514.0658 | 561.2672 | 618.4185 | 752.6839 | 862.8122 | 927.3241 | 1001.657 | 1072.8678 | 1210.5283 | 1402.255 | 1388.5739 | 1388.5739 | 1388.5739 | 1388.5739 | 1388.5739 | 1388.5739 | 1388.5739 | 1388.5739 | 1388.5739 | 1388.5739 | 1388.5739 | 1388.5739 | 1388.5739 | 1388.5739 | 1388.5739 | 1388.5739 | Option 1 Summer POE10 W E @ R (MWh) N 1 | 16.6597 | 203.589 | 302.2368 | 295.5861 | 296.1396 | 307.7493 | 340.0619 | 363.1034 | 386.673 | 415.4856 | 443.3834 | 471.5477 | 474.9171 | 510.3932 | 483.3431 | 483.3431 | 483.3431 | 483.3431 | 483.3431 | 483.3431 | 483.3431 | 483.3431 | 483.3431 | 483.3431 | 483.3431 | 483.3431 | 483.3431 | 483.3431 | 483.3431 | 483.3431
Option 2 - 1B New PHS ZSS + Three new feeders
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% |  | 9.8725 | 15.8941 | [6 empty] | 0.016211 | 1.0027 |  | 1.3875 | 5.5099 | 2.3815 | 2.3815 | 2.3815 | 2.3815 | 2.3815 | 2.3815 | 2.3815 | 2.3815 | 2.3815 | 2.3815 | 2.3815 | 2.3815 | 2.3815 | 2.3815 | 2.3815 | 2.3815 |  |  | 13.7943 | 20.0509 | [5 empty] | 2.6329 | 12.7021 | 4.401 | 2.7774 | 4.9691 | 9.7625 | 6.5179 | 6.5179 | 6.5179 | 6.5179 | 6.5179 | 6.5179 | 6.5179 | 6.5179 | 6.5179 | 6.5179 | 6.5179 | 6.5179 | 6.5179 | 6.5179 | 6.5179 | 6.5179
98% |  | 10.848 | 18.0013 | [7 empty] | 0.3214 |  | 0.76829 | 5.6654 | 1.9492 | 1.9492 | 1.9492 | 1.9492 | 1.9492 | 1.9492 | 1.9492 | 1.9492 | 1.9492 | 1.9492 | 1.9492 | 1.9492 | 1.9492 | 1.9492 | 1.9492 | 1.9492 |  |  | 15.5069 | 22.9393 | [5 empty] | 2.2478 | 14.2093 | 4.3482 | 2.4194 | 5.0231 | 10.7173 | 6.8629 | 6.8629 | 6.8629 | 6.8629 | 6.8629 | 6.8629 | 6.8629 | 6.8629 | 6.8629 | 6.8629 | 6.8629 | 6.8629 | 6.8629 | 6.8629 | 6.8629 | 6.8629
97% |  | 19.698 | 33.8593 | [9 empty] | 0.11416 | 9.4381 | 2.081 | 2.081 | 2.081 | 2.081 | 2.081 | 2.081 | 2.081 | 2.081 | 2.081 | 2.081 | 2.081 | 2.081 | 2.081 | 2.081 | 2.081 | 2.081 |  |  | 28.9211 | 43.6351 | [5 empty] | 2.6721 | 26.3524 | 6.8304 | 3.0119 | 8.1664 | 19.4392 | 11.8088 | 11.8088 | 11.8088 | 11.8088 | 11.8088 | 11.8088 | 11.8088 | 11.8088 | 11.8088 | 11.8088 | 11.8088 | 11.8088 | 11.8088 | 11.8088 | 11.8088 | 11.8088
95% |  | 50.103 | 91.9331 | [10 empty] | 19.7966 | 0.56721 | 0.56721 | 0.56721 | 0.56721 | 0.56721 | 0.56721 | 0.56721 | 0.56721 | 0.56721 | 0.56721 | 0.56721 | 0.56721 | 0.56721 | 0.56721 | 0.56721 | 0.56721 |  |  | 77.3465 | 120.8094 | [5 empty] | 1.2747 | 69.759 | 12.094 | 1.8078 | 16.0403 | 49.3384 | 26.7994 | 26.7994 | 26.7994 | 26.7994 | 26.7994 | 26.7994 | 26.7994 | 26.7994 | 26.7994 | 26.7994 | 26.7994 | 26.7994 | 26.7994 | 26.7994 | 26.7994 | 26.7994
90% | FY26: 166.6526; FY27: 397.287; FY38: 20.0864 |  |  | 316.8623 | 556.4991 | [6 empty] | 275.0277 | 4.3131 |  | 10.9773 | 162.4366 | 44.0778 | 44.0778 | 44.0778 | 44.0778 | 44.0778 | 44.0778 | 44.0778 | 44.0778 | 44.0778 | 44.0778 | 44.0778 | 44.0778 | 44.0778 | 44.0778 | 44.0778 | 44.0778
85% | FY26: 49.283; FY27: 550.9121 |  |  | 354.4405 | 939.8561 | [6 empty] | 252.2414 |  |  |  | 44.4713
80% | FY27: 170.3674 |  |  | 26.6685 | 729.5248 | [6 empty] | 0.97105
75% | [33 empty] | 73.1703
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 306.4572 | 1278.2542 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016211 | 1.3241 | 0 | 2.2699 | 60.4964 | 6.9789 | 6.9789 | 6.9789 | 6.9789 | 6.9789 | 6.9789 | 6.9789 | 6.9789 | 6.9789 | 6.9789 | 6.9789 | 6.9789 | 6.9789 | 6.9789 | 6.9789 | 6.9789 | E @ R (MWh) | 0 | 833.5401 | 2506.4849 | 0 | 0 | 0 | 0 | 0 | 8.8274 | 651.2629 | 31.9868 | 10.0164 | 45.1762 | 296.1652 | 96.0668 | 96.0668 | 96.0668 | 96.0668 | 96.0668 | 96.0668 | 96.0668 | 96.0668 | 96.0668 | 96.0668 | 96.0668 | 96.0668 | 96.0668 | 96.0668 | 96.0668 | 96.0668
Option 2 Winter POE50 W E @ R (MWh) N 1 | 0 | 214.5201 | 894.7779 | 0 | 0 | 0 | 0 | 0 | 0 | 0.011348 | 0.92687 | 0 | 1.5889 | 42.3475 | 4.8853 | 4.8853 | 4.8853 | 4.8853 | 4.8853 | 4.8853 | 4.8853 | 4.8853 | 4.8853 | 4.8853 | 4.8853 | 4.8853 | 4.8853 | 4.8853 | 4.8853 | 4.8853 | Option 2 Winter POE10 W E @ R (MWh) N 1 | 0 | 250.062 | 751.9455 | 0 | 0 | 0 | 0 | 0 | 2.6482 | 195.3789 | 9.596 | 3.0049 | 13.5529 | 88.8496 | 28.8201 | 28.8201 | 28.8201 | 28.8201 | 28.8201 | 28.8201 | 28.8201 | 28.8201 | 28.8201 | 28.8201 | 28.8201 | 28.8201 | 28.8201 | 28.8201 | 28.8201 | 28.8201
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 8.924 | 31.6709 | 37.6273 | 8.1746 | 8.2043 | 8.8175 | 10.4319 | 11.5143 | 12.5731 | 13.811 | 14.9592 | 16.073 | 16.2021 | 17.5017 | 16.5202 | 16.5202 | 16.5202 | 16.5202 | 16.5202 | 16.5202 | 16.5202 | 16.5202 | 16.5202 | 16.5202 | 16.5202 | 16.5202 | 16.5202 | 16.5202 | 16.5202 | 16.5202
98% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4.0751 | 15.3343 | 18.2825 | 3.7041 | 3.7189 | 4.0224 | 4.8215 | 5.3573 | 5.8813 | 6.494 | 7.0624 | 7.6137 | 7.6776 | 8.3209 | 7.835 | 7.835 | 7.835 | 7.835 | 7.835 | 7.835 | 7.835 | 7.835 | 7.835 | 7.835 | 7.835 | 7.835 | 7.835 | 7.835 | 7.835 | 7.835
97% |  | 5.4588 | 6.9736 |  |  | 0.010945 | 0.16468 | 0.55445 | 0.83448 | 0.98673 | 1.1535 | 1.3059 | 1.5807 | 1.9216 | 1.8986 | 1.8986 | 1.8986 | 1.8986 | 1.8986 | 1.8986 | 1.8986 | 1.8986 | 1.8986 | 1.8986 | 1.8986 | 1.8986 | 1.8986 | 1.8986 | 1.8986 | 1.8986 |  | 7.3764 | 29.6661 | 35.5027 | 6.642 | 6.6712 | 7.2721 | 8.854 | 9.9147 | 10.9521 | 12.1651 | 13.2903 | 14.3817 | 14.5082 | 15.7817 | 14.8199 | 14.8199 | 14.8199 | 14.8199 | 14.8199 | 14.8199 | 14.8199 | 14.8199 | 14.8199 | 14.8199 | 14.8199 | 14.8199 | 14.8199 | 14.8199 | 14.8199 | 14.8199
95% |  | 25.5649 | 33.0227 |  |  |  | 0.041581 | 1.4206 | 2.7992 | 3.5487 | 4.3698 | 5.1201 | 6.4729 | 8.1512 | 8.0377 | 8.0377 | 8.0377 | 8.0377 | 8.0377 | 8.0377 | 8.0377 | 8.0377 | 8.0377 | 8.0377 | 8.0377 | 8.0377 | 8.0377 | 8.0377 | 8.0377 | 8.0377 |  | 9.3236 | 42.2437 | 50.864 | 8.2389 | 8.282 | 9.1694 | 11.5058 | 13.0724 | 14.6046 | 16.3961 | 18.0579 | 19.6699 | 19.8566 | 21.7375 | 20.317 | 20.317 | 20.317 | 20.317 | 20.317 | 20.317 | 20.317 | 20.317 | 20.317 | 20.317 | 20.317 | 20.317 | 20.317 | 20.317 | 20.317 | 20.317
90% |  | 38.7554 | 51.6899 |  |  |  |  | 0.053902 | 0.69767 | 1.3438 | 2.2831 | 3.3477 | 5.6426 | 8.5533 | 8.3566 | 8.3566 | 8.3566 | 8.3566 | 8.3566 | 8.3566 | 8.3566 | 8.3566 | 8.3566 | 8.3566 | 8.3566 | 8.3566 | 8.3566 | 8.3566 | 8.3566 | 8.3566 |  | 23.6749 | 166.4146 | 203.7914 | 18.9719 | 19.1585 | 23.0066 | 33.1371 | 39.9295 | 46.5733 | 54.3411 | 61.5463 | 68.5358 | 69.3455 | 77.501 | 71.3418 | 71.3418 | 71.3418 | 71.3418 | 71.3418 | 71.3418 | 71.3418 | 71.3418 | 71.3418 | 71.3418 | 71.3418 | 71.3418 | 71.3418 | 71.3418 | 71.3418 | 71.3418
85% |  | 85.1452 | 121.8514 | [9 empty] | 0.31884 | 3.0023 | 2.7372 | 2.7372 | 2.7372 | 2.7372 | 2.7372 | 2.7372 | 2.7372 | 2.7372 | 2.7372 | 2.7372 | 2.7372 | 2.7372 | 2.7372 | 2.7372 | 2.7372 | 2.7372 |  | 2.1581 | 132.583 | 167.9395 | 0.70557 | 0.74833 | 1.9044 | 7.379 | 12.9408 | 19.2196 | 26.5676 | 33.3833 | 39.9949 | 40.7609 | 48.4756 | 42.6493 | 42.6493 | 42.6493 | 42.6493 | 42.6493 | 42.6493 | 42.6493 | 42.6493 | 42.6493 | 42.6493 | 42.6493 | 42.6493 | 42.6493 | 42.6493 | 42.6493 | 42.6493
80% | FY26: 80.0361; FY27: 131.3082 |  |  | 73.1492 | 97.8426 | [5 empty] | 0.41598 | 2.1444 | 4.8995 | 8.5875 | 9.0775 | 14.4075 | 10.3403 | 10.3403 | 10.3403 | 10.3403 | 10.3403 | 10.3403 | 10.3403 | 10.3403 | 10.3403 | 10.3403 | 10.3403 | 10.3403 | 10.3403 | 10.3403 | 10.3403 | 10.3403
75% | FY26: 94.1589; FY27: 227.8159 |  |  | 91.3687 | 135.4427 | [10 empty] | 0.59104
70% | FY26: 6.5776; FY27: 168.5277 |  |  | 85.2049 | 165.4959
65% | FY27: 9.6236 |  |  | 10.9945 | 90.8581
60% | [33 empty] | 3.8091
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 335.6968 | 750.8128 | 0 | 0 | 0.010945 | 0.20626 | 2.0289 | 4.3313 | 5.8792 | 7.8064 | 9.7736 | 14.0151 | 21.6284 | 21.0301 | 21.0301 | 21.0301 | 21.0301 | 21.0301 | 21.0301 | 21.0301 | 21.0301 | 21.0301 | 21.0301 | 21.0301 | 21.0301 | 21.0301 | 21.0301 | 21.0301 | 21.0301 | E @ R (MWh) | 55.5322 | 678.63 | 1007.4559 | 46.4371 | 46.7831 | 54.1924 | 76.1293 | 92.7289 | 110.22 | 131.9194 | 153.1988 | 174.8565 | 177.4283 | 204.317 | 183.8236 | 183.8236 | 183.8236 | 183.8236 | 183.8236 | 183.8236 | 183.8236 | 183.8236 | 183.8236 | 183.8236 | 183.8236 | 183.8236 | 183.8236 | 183.8236 | 183.8236 | 183.8236
Option 2 Summer POE50 W E @ R (MWh) N 1 | 0 | 234.9878 | 525.569 | 0 | 0 | 0.0076612 | 0.14438 | 1.4203 | 3.0319 | 4.1154 | 5.4645 | 6.8415 | 9.8106 | 15.1399 | 14.7211 | 14.7211 | 14.7211 | 14.7211 | 14.7211 | 14.7211 | 14.7211 | 14.7211 | 14.7211 | 14.7211 | 14.7211 | 14.7211 | 14.7211 | 14.7211 | 14.7211 | 14.7211 | Option 2 Summer POE10 W E @ R (MWh) N 1 | 16.6597 | 203.589 | 302.2368 | 13.9311 | 14.0349 | 16.2577 | 22.8388 | 27.8187 | 33.066 | 39.5758 | 45.9596 | 52.4569 | 53.2285 | 61.2951 | 55.1471 | 55.1471 | 55.1471 | 55.1471 | 55.1471 | 55.1471 | 55.1471 | 55.1471 | 55.1471 | 55.1471 | 55.1471 | 55.1471 | 55.1471 | 55.1471 | 55.1471 | 55.1471
Option 3 - 2B PHM 3rd Tx + Switchroom + Two new feeders + OFR12 New Feeder
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | FY26: 9.8725; FY27: 15.8941 |  |  | 13.7943 | 20.0509
98% | FY26: 10.848; FY27: 18.0013 |  |  | 15.5069 | 22.9393
97% | FY26: 19.698; FY27: 33.8593 |  |  | 28.9211 | 43.6351
95% | FY26: 50.103; FY27: 91.9331 |  |  | 77.3465 | 120.8094
90% | FY26: 166.6526; FY27: 397.287 |  |  | 316.8623 | 556.4991
85% | FY26: 49.283; FY27: 550.9121 |  |  | 354.4405 | 939.8561
80% | FY27: 170.3674 |  |  | 26.6685 | 729.5248
75% | [33 empty] | 73.1703
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 306.4572 | 1278.2542 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 833.5401 | 2506.4849 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 Winter POE50 W E @ R (MWh) N 1 | 0 | 214.5201 | 894.7779 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 3 Winter POE10 W E @ R (MWh) N 1 | 0 | 250.062 | 751.9455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | FY25: 0; FY26: 0; FY27: 0 |  | 8.924 | 31.6709 | 37.6273
98% | FY25: 0; FY26: 0; FY27: 0 |  | 4.0751 | 15.3343 | 18.2825
97% | FY26: 5.4588; FY27: 6.9736 |  | 7.3764 | 29.6661 | 35.5027
95% | FY26: 25.5649; FY27: 33.0227 |  | 9.3236 | 42.2437 | 50.864
90% | FY26: 38.7554; FY27: 51.6899 |  | 23.6749 | 166.4146 | 203.7914
85% | FY26: 85.1452; FY27: 121.8514 |  | 2.1581 | 132.583 | 167.9395
80% | FY26: 80.0361; FY27: 131.3082 |  |  | 73.1492 | 97.8426
75% | FY26: 94.1589; FY27: 227.8159 |  |  | 91.3687 | 135.4427
70% | FY26: 6.5776; FY27: 168.5277 |  |  | 85.2049 | 165.4959
65% | FY27: 9.6236 |  |  | 10.9945 | 90.8581
60% | [33 empty] | 3.8091
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 335.6968 | 750.8128 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 55.5322 | 678.63 | 1007.4559 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 Summer POE50 W E @ R (MWh) N 1 | 0 | 234.9878 | 525.569 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 3 Summer POE10 W E @ R (MWh) N 1 | 16.6597 | 203.589 | 302.2368 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 - 3B OFR 3rd Tx + Switchroom + Two new feeders + OFR12 New Feeder
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% |  | 9.8725 | 15.8941 | 11.0063 | 11.8068 | 13.1852 | 16.321 | 18.4202 | 21.0794 | 22.4597 | 23.674 | 21.4366 | 24.0588 | 28.1812 | 25.0528 | 25.0528 | 25.0528 | 25.0528 | 25.0528 | 25.0528 | 25.0528 | 25.0528 | 25.0528 | 25.0528 | 25.0528 | 25.0528 | 25.0528 | 25.0528 | 25.0528 | 25.0528 |  |  | 13.7943 | 20.0509 | 15.1047 | 15.7194 | 17.0679 | 20.2528 | 21.9916 | 25.3042 | 35.3734 | 27.0723 | 25.4487 | 27.6404 | 32.4338 | 29.1892 | 29.1892 | 29.1892 | 29.1892 | 29.1892 | 29.1892 | 29.1892 | 29.1892 | 29.1892 | 29.1892 | 29.1892 | 29.1892 | 29.1892 | 29.1892 | 29.1892 | 29.1892
98% |  | 10.848 | 18.0013 | 12.1948 | 13.1458 | 14.7832 | 18.5085 | 21.0021 | 24.1611 | 25.8008 | 27.2433 | 24.5854 | 27.7004 | 32.5976 | 28.8813 | 28.8813 | 28.8813 | 28.8813 | 28.8813 | 28.8813 | 28.8813 | 28.8813 | 28.8813 | 28.8813 | 28.8813 | 28.8813 | 28.8813 | 28.8813 | 28.8813 | 28.8813 |  |  | 15.5069 | 22.9393 | 17.0635 | 17.7937 | 19.3956 | 23.1791 | 25.2448 | 29.1799 | 41.1415 | 31.2804 | 29.3515 | 31.9552 | 37.6494 | 33.7951 | 33.7951 | 33.7951 | 33.7951 | 33.7951 | 33.7951 | 33.7951 | 33.7951 | 33.7951 | 33.7951 | 33.7951 | 33.7951 | 33.7951 | 33.7951 | 33.7951 | 33.7951
97% |  | 19.698 | 33.8593 | 22.3643 | 24.247 | 27.4885 | 34.8634 | 39.8 | 46.0538 | 49.3 | 52.1558 | 46.8939 | 53.0606 | 62.7555 | 55.3984 | 55.3984 | 55.3984 | 55.3984 | 55.3984 | 55.3984 | 55.3984 | 55.3984 | 55.3984 | 55.3984 | 55.3984 | 55.3984 | 55.3984 | 55.3984 | 55.3984 | 55.3984 |  |  | 28.9211 | 43.6351 | 32.0029 | 33.4484 | 36.6197 | 44.1098 | 48.1992 | 55.9895 | 79.6698 | 60.1478 | 56.3293 | 61.4838 | 72.7566 | 65.1262 | 65.1262 | 65.1262 | 65.1262 | 65.1262 | 65.1262 | 65.1262 | 65.1262 | 65.1262 | 65.1262 | 65.1262 | 65.1262 | 65.1262 | 65.1262 | 65.1262 | 65.1262
95% |  | 50.103 | 91.9331 | 57.9787 | 63.5398 | 73.1149 | 94.899 | 109.4811 | 127.954 | 137.5425 | 145.9781 | 130.4353 | 148.651 | 177.2881 | 155.5565 | 155.5565 | 155.5565 | 155.5565 | 155.5565 | 155.5565 | 155.5565 | 155.5565 | 155.5565 | 155.5565 | 155.5565 | 155.5565 | 155.5565 | 155.5565 | 155.5565 | 155.5565 |  |  | 77.3465 | 120.8094 | 86.4496 | 90.7196 | 100.087 | 122.2116 | 134.2912 | 157.3025 | 227.2504 | 169.5855 | 158.3061 | 173.5318 | 206.8298 | 184.2908 | 184.2908 | 184.2908 | 184.2908 | 184.2908 | 184.2908 | 184.2908 | 184.2908 | 184.2908 | 184.2908 | 184.2908 | 184.2908 | 184.2908 | 184.2908 | 184.2908 | 184.2908
90% |  | 166.6526 | 397.287 | 210.0758 | 240.7377 | 293.5307 | 413.6399 | 494.0394 | 595.8917 | 648.7591 | 695.2695 | 609.5728 | 710.0066 | 867.9001 | 748.0808 | 748.0808 | 748.0808 | 748.0808 | 748.0808 | 748.0808 | 748.0808 | 748.0808 | 748.0808 | 748.0808 | 748.0808 | 748.0808 | 748.0808 | 748.0808 | 748.0808 | 748.0808 |  |  | 316.8623 | 556.4991 | 367.0529 | 390.596 | 442.2443 | 564.2307 | 630.8323 | 757.7074 | 1143.3724 | 825.4309 | 763.2412 | 847.1892 | 1030.7814 | 906.5104 | 906.5104 | 906.5104 | 906.5104 | 906.5104 | 906.5104 | 906.5104 | 906.5104 | 906.5104 | 906.5104 | 906.5104 | 906.5104 | 906.5104 | 906.5104 | 906.5104 | 906.5104
85% |  | 49.283 | 550.9121 | 112.6545 | 172.2031 | 297.4431 | 590.8612 | 787.2714 | 1036.0893 | 1165.2405 | 1278.862 | 1069.5112 | 1314.8637 | 1700.5863 | 1407.8764 | 1407.8764 | 1407.8764 | 1407.8764 | 1407.8764 | 1407.8764 | 1407.8764 | 1407.8764 | 1407.8764 | 1407.8764 | 1407.8764 | 1407.8764 | 1407.8764 | 1407.8764 | 1407.8764 | 1407.8764 |  |  | 354.4405 | 939.8561 | 477.0525 | 534.5665 | 660.7398 | 958.7437 | 1121.4467 | 1431.3934 | 2373.5455 | 1596.8371 | 1444.9121 | 1649.9911 | 2098.4936 | 1794.9085 | 1794.9085 | 1794.9085 | 1794.9085 | 1794.9085 | 1794.9085 | 1794.9085 | 1794.9085 | 1794.9085 | 1794.9085 | 1794.9085 | 1794.9085 | 1794.9085 | 1794.9085 | 1794.9085 | 1794.9085
80% |  |  | 170.3674 |  |  | 8.0665 | 214.1483 | 492.363 | 879.0998 | 1079.839 | 1256.4406 | 931.0473 | 1312.3979 | 1911.9252 | 1456.9671 | 1456.9671 | 1456.9671 | 1456.9671 | 1456.9671 | 1456.9671 | 1456.9671 | 1456.9671 | 1456.9671 | 1456.9671 | 1456.9671 | 1456.9671 | 1456.9671 | 1456.9671 | 1456.9671 | 1456.9671 |  |  | 26.6685 | 729.5248 | 102.1909 | 153.8418 | 302.1319 | 758.8818 | 1011.7705 | 1493.5196 | 2957.9032 | 1750.6681 | 1514.5316 | 1833.2853 | 2530.391 | 2058.5298 | 2058.5298 | 2058.5298 | 2058.5298 | 2058.5298 | 2058.5298 | 2058.5298 | 2058.5298 | 2058.5298 | 2058.5298 | 2058.5298 | 2058.5298 | 2058.5298 | 2058.5298 | 2058.5298 | 2058.5298
75% | [7 empty] | 5.858 | 152.9581 | 303.5037 | 475.5919 | 187.2091 | 537.0186 | 1198.4645 | 696.5189 | 696.5189 | 696.5189 | 696.5189 | 696.5189 | 696.5189 | 696.5189 | 696.5189 | 696.5189 | 696.5189 | 696.5189 | 696.5189 | 696.5189 | 696.5189 | 696.5189 | 696.5189 |  |  |  | 73.1703 |  |  |  | 86.5971 | 246.9876 | 736.8464 | 2352.4702 | 1020.553 | 760.0285 | 1111.7028 | 1880.805 | 1360.2104 | 1360.2104 | 1360.2104 | 1360.2104 | 1360.2104 | 1360.2104 | 1360.2104 | 1360.2104 | 1360.2104 | 1360.2104 | 1360.2104 | 1360.2104 | 1360.2104 | 1360.2104 | 1360.2104 | 1360.2104
70% | [12 empty] | 0.69444 | 249.8734 | 20.2616 | 20.2616 | 20.2616 | 20.2616 | 20.2616 | 20.2616 | 20.2616 | 20.2616 | 20.2616 | 20.2616 | 20.2616 | 20.2616 | 20.2616 | 20.2616 | 20.2616 | 20.2616 | [9 empty] | 29.4069 | 1413.8644 | 140.1908 | 35.4201 | 192.6027 | 907.0865 | 375.465 | 375.465 | 375.465 | 375.465 | 375.465 | 375.465 | 375.465 | 375.465 | 375.465 | 375.465 | 375.465 | 375.465 | 375.465 | 375.465 | 375.465 | 375.465
65% | [40 empty] | 260.3953 |  |  |  | 35.5434
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 306.4572 | 1278.2542 | 426.2743 | 525.6801 | 727.612 | 1383.2413 | 1968.2351 | 2883.2872 | 3432.4453 | 3955.2152 | 3020.6915 | 4128.4519 | 6229.5719 | 4594.5939 | 4594.5939 | 4594.5939 | 4594.5939 | 4594.5939 | 4594.5939 | 4594.5939 | 4594.5939 | 4594.5939 | 4594.5939 | 4594.5939 | 4594.5939 | 4594.5939 | 4594.5939 | 4594.5939 | 4594.5939 | E @ R (MWh) | 0 | 833.5401 | 2506.4849 | 1096.9169 | 1236.6854 | 1578.2863 | 2578.2066 | 3240.7639 | 4716.6498 | 10884.9862 | 5621.7659 | 4787.5692 | 5929.3823 | 8832.7704 | 6808.0255 | 6808.0255 | 6808.0255 | 6808.0255 | 6808.0255 | 6808.0255 | 6808.0255 | 6808.0255 | 6808.0255 | 6808.0255 | 6808.0255 | 6808.0255 | 6808.0255 | 6808.0255 | 6808.0255 | 6808.0255
Option 4 Winter POE50 W E @ R (MWh) N 1 | 0 | 214.5201 | 894.7779 | 298.392 | 367.9761 | 509.3284 | 968.2689 | 1377.7646 | 2018.3011 | 2402.7117 | 2768.6507 | 2114.4841 | 2889.9164 | 4360.7003 | 3216.2157 | 3216.2157 | 3216.2157 | 3216.2157 | 3216.2157 | 3216.2157 | 3216.2157 | 3216.2157 | 3216.2157 | 3216.2157 | 3216.2157 | 3216.2157 | 3216.2157 | 3216.2157 | 3216.2157 | 3216.2157 | Option 4 Winter POE10 W E @ R (MWh) N 1 | 0 | 250.062 | 751.9455 | 329.0751 | 371.0056 | 473.4859 | 773.462 | 972.2292 | 1414.9949 | 3265.4959 | 1686.5298 | 1436.2708 | 1778.8147 | 2649.8311 | 2042.4077 | 2042.4077 | 2042.4077 | 2042.4077 | 2042.4077 | 2042.4077 | 2042.4077 | 2042.4077 | 2042.4077 | 2042.4077 | 2042.4077 | 2042.4077 | 2042.4077 | 2042.4077 | 2042.4077 | 2042.4077
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 8.924 | 31.6709 | 37.6273 | 31.2527 | 31.2824 | 31.8956 | 33.51 | 34.5925 | 35.6512 | 36.8891 | 38.0373 | 39.1511 | 39.2802 | 40.5798 | 39.5983 | 39.5983 | 39.5983 | 39.5983 | 39.5983 | 39.5983 | 39.5983 | 39.5983 | 39.5983 | 39.5983 | 39.5983 | 39.5983 | 39.5983 | 39.5983 | 39.5983 | 39.5983
98% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4.0751 | 15.3343 | 18.2825 | 15.1272 | 15.1419 | 15.4455 | 16.2446 | 16.7803 | 17.3044 | 17.9171 | 18.4854 | 19.0368 | 19.1006 | 19.7439 | 19.2581 | 19.2581 | 19.2581 | 19.2581 | 19.2581 | 19.2581 | 19.2581 | 19.2581 | 19.2581 | 19.2581 | 19.2581 | 19.2581 | 19.2581 | 19.2581 | 19.2581 | 19.2581
97% |  | 5.4588 | 6.9736 | 5.4554 | 5.4549 | 5.6282 | 5.8182 | 6.208 | 6.488 | 6.6403 | 6.8071 | 6.9595 | 7.2343 | 7.5752 | 7.5521 | 7.5521 | 7.5521 | 7.5521 | 7.5521 | 7.5521 | 7.5521 | 7.5521 | 7.5521 | 7.5521 | 7.5521 | 7.5521 | 7.5521 | 7.5521 | 7.5521 | 7.5521 |  | 7.3764 | 29.6661 | 35.5027 | 29.2562 | 29.2854 | 29.8863 | 31.4682 | 32.5289 | 33.5664 | 34.7794 | 35.9045 | 36.9959 | 37.1224 | 38.3959 | 37.4341 | 37.4341 | 37.4341 | 37.4341 | 37.4341 | 37.4341 | 37.4341 | 37.4341 | 37.4341 | 37.4341 | 37.4341 | 37.4341 | 37.4341 | 37.4341 | 37.4341 | 37.4341
95% |  | 25.5649 | 33.0227 | 25.5485 | 25.546 | 26.3989 | 27.3346 | 29.2535 | 30.6321 | 31.3816 | 32.2027 | 32.953 | 34.3058 | 35.984 | 35.8706 | 35.8706 | 35.8706 | 35.8706 | 35.8706 | 35.8706 | 35.8706 | 35.8706 | 35.8706 | 35.8706 | 35.8706 | 35.8706 | 35.8706 | 35.8706 | 35.8706 | 35.8706 |  | 9.3236 | 42.2437 | 50.864 | 41.6384 | 41.6814 | 42.5689 | 44.9053 | 46.4718 | 48.0041 | 49.7956 | 51.4573 | 53.0693 | 53.2561 | 55.137 | 53.7165 | 53.7165 | 53.7165 | 53.7165 | 53.7165 | 53.7165 | 53.7165 | 53.7165 | 53.7165 | 53.7165 | 53.7165 | 53.7165 | 53.7165 | 53.7165 | 53.7165 | 53.7165
90% |  | 38.7554 | 51.6899 | 38.7269 | 38.7225 | 40.2018 | 41.8246 | 45.1527 | 47.5437 | 48.8436 | 50.2677 | 51.5689 | 53.9153 | 56.826 | 56.6293 | 56.6293 | 56.6293 | 56.6293 | 56.6293 | 56.6293 | 56.6293 | 56.6293 | 56.6293 | 56.6293 | 56.6293 | 56.6293 | 56.6293 | 56.6293 | 56.6293 | 56.6293 |  | 23.6749 | 166.4146 | 203.7914 | 163.7899 | 163.9765 | 167.8246 | 177.9551 | 184.7475 | 191.3913 | 199.1592 | 206.3643 | 213.3538 | 214.1635 | 222.3191 | 216.1598 | 216.1598 | 216.1598 | 216.1598 | 216.1598 | 216.1598 | 216.1598 | 216.1598 | 216.1598 | 216.1598 | 216.1598 | 216.1598 | 216.1598 | 216.1598 | 216.1598 | 216.1598
85% |  | 85.1452 | 121.8514 | 85.0645 | 85.0519 | 89.2501 | 93.8552 | 103.2998 | 110.0851 | 113.7741 | 117.8153 | 121.5081 | 128.1667 | 136.4268 | 135.8685 | 135.8685 | 135.8685 | 135.8685 | 135.8685 | 135.8685 | 135.8685 | 135.8685 | 135.8685 | 135.8685 | 135.8685 | 135.8685 | 135.8685 | 135.8685 | 135.8685 | 135.8685 |  | 2.1581 | 132.583 | 167.9395 | 130.1002 | 130.2767 | 133.9168 | 143.4997 | 149.9249 | 156.2096 | 163.5576 | 170.3733 | 176.985 | 177.7509 | 185.4656 | 179.6393 | 179.6393 | 179.6393 | 179.6393 | 179.6393 | 179.6393 | 179.6393 | 179.6393 | 179.6393 | 179.6393 | 179.6393 | 179.6393 | 179.6393 | 179.6393 | 179.6393 | 179.6393
80% |  | 80.0361 | 131.3082 | 79.9233 | 79.9057 | 85.7699 | 92.2024 | 105.3948 | 114.8727 | 120.0256 | 125.6705 | 130.8287 | 140.1296 | 151.6675 | 150.8877 | 150.8877 | 150.8877 | 150.8877 | 150.8877 | 150.8877 | 150.8877 | 150.8877 | 150.8877 | 150.8877 | 150.8877 | 150.8877 | 150.8877 | 150.8877 | 150.8877 | 150.8877 |  |  | 73.1492 | 97.8426 | 71.4152 | 71.5385 | 74.0807 | 80.7736 | 85.261 | 89.6503 | 94.7823 | 99.5424 | 104.1601 | 104.6951 | 110.0831 | 106.0139 | 106.0139 | 106.0139 | 106.0139 | 106.0139 | 106.0139 | 106.0139 | 106.0139 | 106.0139 | 106.0139 | 106.0139 | 106.0139 | 106.0139 | 106.0139 | 106.0139 | 106.0139
75% |  | 94.1589 | 227.8159 | 93.8649 | 93.8191 | 109.1058 | 125.8743 | 160.2645 | 184.9717 | 198.4043 | 213.1194 | 226.5661 | 250.8116 | 280.8889 | 278.8562 | 278.8562 | 278.8562 | 278.8562 | 278.8562 | 278.8562 | 278.8562 | 278.8562 | 278.8562 | 278.8562 | 278.8562 | 278.8562 | 278.8562 | 278.8562 | 278.8562 | 278.8562 |  |  | 91.3687 | 135.4427 | 88.2737 | 88.4938 | 93.0313 | 104.977 | 112.9865 | 120.8207 | 129.9804 | 138.4766 | 146.7184 | 147.6732 | 157.2901 | 150.0272 | 150.0272 | 150.0272 | 150.0272 | 150.0272 | 150.0272 | 150.0272 | 150.0272 | 150.0272 | 150.0272 | 150.0272 | 150.0272 | 150.0272 | 150.0272 | 150.0272 | 150.0272
70% |  | 6.5776 | 168.5277 | 6.4551 | 6.4362 | 14.2834 | 26.3304 | 61.9292 | 96.2134 | 117.8021 | 143.1367 | 166.3684 | 208.2574 | 260.2217 | 256.7098 | 256.7098 | 256.7098 | 256.7098 | 256.7098 | 256.7098 | 256.7098 | 256.7098 | 256.7098 | 256.7098 | 256.7098 | 256.7098 | 256.7098 | 256.7098 | 256.7098 | 256.7098 |  |  | 85.2049 | 165.4959 | 79.5667 | 79.9676 | 88.2338 | 109.9957 | 124.5867 | 138.8585 | 155.5451 | 171.0229 | 186.0373 | 187.7767 | 205.296 | 192.0651 | 192.0651 | 192.0651 | 192.0651 | 192.0651 | 192.0651 | 192.0651 | 192.0651 | 192.0651 | 192.0651 | 192.0651 | 192.0651 | 192.0651 | 192.0651 | 192.0651 | 192.0651
65% |  |  | 9.6236 | [7 empty] | 1.7265 | 8.706 | 34.522 | 89.4645 | 84.971 | 84.971 | 84.971 | 84.971 | 84.971 | 84.971 | 84.971 | 84.971 | 84.971 | 84.971 | 84.971 | 84.971 | 84.971 | 84.971 | 84.971 | 84.971 |  |  | 10.9945 | 90.8581 | 8.163 | 8.3508 | 12.6838 | 28.1995 | 41.8301 | 57.578 | 78.3385 | 97.8119 | 116.7023 | 118.8908 | 140.9328 | 124.2862 | 124.2862 | 124.2862 | 124.2862 | 124.2862 | 124.2862 | 124.2862 | 124.2862 | 124.2862 | 124.2862 | 124.2862 | 124.2862 | 124.2862 | 124.2862 | 124.2862 | 124.2862
60% | [33 empty] | 3.8091 | [6 empty] | 0.98689 | 6.1556 | 15.2796 | 16.5924 | 32.7069 | 20.0526 | 20.0526 | 20.0526 | 20.0526 | 20.0526 | 20.0526 | 20.0526 | 20.0526 | 20.0526 | 20.0526 | 20.0526 | 20.0526 | 20.0526 | 20.0526 | 20.0526 | 20.0526
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 335.6968 | 750.8128 | 335.0386 | 334.9363 | 370.6381 | 413.2397 | 511.5025 | 590.8067 | 636.8715 | 690.7457 | 745.4587 | 857.3427 | 1019.0545 | 1007.3451 | 1007.3451 | 1007.3451 | 1007.3451 | 1007.3451 | 1007.3451 | 1007.3451 | 1007.3451 | 1007.3451 | 1007.3451 | 1007.3451 | 1007.3451 | 1007.3451 | 1007.3451 | 1007.3451 | 1007.3451 | E @ R (MWh) | 55.5322 | 678.63 | 1007.4559 | 658.5833 | 659.9951 | 689.5674 | 771.5288 | 829.7103 | 889.0344 | 961.731 | 1033.6316 | 1107.4896 | 1116.3019 | 1207.9502 | 1138.2513 | 1138.2513 | 1138.2513 | 1138.2513 | 1138.2513 | 1138.2513 | 1138.2513 | 1138.2513 | 1138.2513 | 1138.2513 | 1138.2513 | 1138.2513 | 1138.2513 | 1138.2513 | 1138.2513 | 1138.2513
Option 4 Summer POE50 W E @ R (MWh) N 1 | 0 | 234.9878 | 525.569 | 234.527 | 234.4554 | 259.4467 | 289.2678 | 358.0517 | 413.5647 | 445.81 | 483.522 | 521.8211 | 600.1399 | 713.3382 | 705.1416 | 705.1416 | 705.1416 | 705.1416 | 705.1416 | 705.1416 | 705.1416 | 705.1416 | 705.1416 | 705.1416 | 705.1416 | 705.1416 | 705.1416 | 705.1416 | 705.1416 | 705.1416 | Option 4 Summer POE10 W E @ R (MWh) N 1 | 16.6597 | 203.589 | 302.2368 | 197.575 | 197.9985 | 206.8702 | 231.4586 | 248.9131 | 266.7103 | 288.5193 | 310.0895 | 332.2469 | 334.8906 | 362.3851 | 341.4754 | 341.4754 | 341.4754 | 341.4754 | 341.4754 | 341.4754 | 341.4754 | 341.4754 | 341.4754 | 341.4754 | 341.4754 | 341.4754 | 341.4754 | 341.4754 | 341.4754 | 341.4754
Option 5 - 4B LLG 2nd Tx + Switchroom + Two new feeders + OFR12 New Feeder
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | FY26: 9.8725; FY27: 15.8941; FY38: 1.9367 |  |  | 13.7943 | 20.0509 | [6 empty] | 9.1289 | 0.82785 |  | 1.3959 | 6.1893 | 2.9447 | 2.9447 | 2.9447 | 2.9447 | 2.9447 | 2.9447 | 2.9447 | 2.9447 | 2.9447 | 2.9447 | 2.9447 | 2.9447 | 2.9447 | 2.9447 | 2.9447 | 2.9447
98% | FY26: 10.848; FY27: 18.0013; FY38: 1.4207 |  |  | 15.5069 | 22.9393 | [6 empty] | 9.9646 | 0.169 |  | 0.77834 | 6.4725 | 2.6182 | 2.6182 | 2.6182 | 2.6182 | 2.6182 | 2.6182 | 2.6182 | 2.6182 | 2.6182 | 2.6182 | 2.6182 | 2.6182 | 2.6182 | 2.6182 | 2.6182 | 2.6182
97% | FY26: 19.698; FY27: 33.8593; FY38: 1.0348 |  |  | 28.9211 | 43.6351 | [6 empty] | 17.9491 |  |  | 0.12139 | 11.0359 | 3.4055 | 3.4055 | 3.4055 | 3.4055 | 3.4055 | 3.4055 | 3.4055 | 3.4055 | 3.4055 | 3.4055 | 3.4055 | 3.4055 | 3.4055 | 3.4055 | 3.4055 | 3.4055
95% | FY26: 50.103; FY27: 91.9331; FY38: 0.0071762 |  |  | 77.3465 | 120.8094 | [6 empty] | 44.9369 |  |  |  | 24.5163 | 2.5398 | 2.5398 | 2.5398 | 2.5398 | 2.5398 | 2.5398 | 2.5398 | 2.5398 | 2.5398 | 2.5398 | 2.5398 | 2.5398 | 2.5398 | 2.5398 | 2.5398 | 2.5398
90% | FY26: 166.6526; FY27: 397.287 |  |  | 316.8623 | 556.4991 | [6 empty] | 138.169 |  |  |  | 35.2691
85% | FY26: 49.283; FY27: 550.9121 |  |  | 354.4405 | 939.8561 | [6 empty] | 21.495
80% | FY27: 170.3674 |  |  | 26.6685 | 729.5248
75% | [33 empty] | 73.1703
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 306.4572 | 1278.2542 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.3993 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 833.5401 | 2506.4849 | 0 | 0 | 0 | 0 | 0 | 0 | 241.6435 | 0.99685 | 0 | 2.2957 | 83.4831 | 11.5083 | 11.5083 | 11.5083 | 11.5083 | 11.5083 | 11.5083 | 11.5083 | 11.5083 | 11.5083 | 11.5083 | 11.5083 | 11.5083 | 11.5083 | 11.5083 | 11.5083 | 11.5083
Option 5 Winter POE50 W E @ R (MWh) N 1 | 0 | 214.5201 | 894.7779 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.0795 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 5 Winter POE10 W E @ R (MWh) N 1 | 0 | 250.062 | 751.9455 | 0 | 0 | 0 | 0 | 0 | 0 | 72.4931 | 0.29906 | 0 | 0.6887 | 25.0449 | 3.4525 | 3.4525 | 3.4525 | 3.4525 | 3.4525 | 3.4525 | 3.4525 | 3.4525 | 3.4525 | 3.4525 | 3.4525 | 3.4525 | 3.4525 | 3.4525 | 3.4525 | 3.4525
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | 0 | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 8.924 | 31.6709 | 37.6273 | 4.5373 | 4.567 | 5.1802 | 6.7946 | 7.877 | 8.9358 | 10.1737 | 11.3219 | 12.4357 | 12.5648 | 13.8644 | 12.8829 | 12.8829 | 12.8829 | 12.8829 | 12.8829 | 12.8829 | 12.8829 | 12.8829 | 12.8829 | 12.8829 | 12.8829 | 12.8829 | 12.8829 | 12.8829 | 12.8829 | 12.8829
98% | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4.0751 | 15.3343 | 18.2825 | 1.9038 | 1.9185 | 2.222 | 3.0211 | 3.5569 | 4.0809 | 4.6937 | 5.262 | 5.8133 | 5.8772 | 6.5205 | 6.0346 | 6.0346 | 6.0346 | 6.0346 | 6.0346 | 6.0346 | 6.0346 | 6.0346 | 6.0346 | 6.0346 | 6.0346 | 6.0346 | 6.0346 | 6.0346 | 6.0346 | 6.0346
97% |  | 5.4588 | 6.9736 | [5 empty] | 0.0026583 | 0.095677 | 0.26246 | 0.41486 | 0.68966 | 1.0306 | 1.0075 | 1.0075 | 1.0075 | 1.0075 | 1.0075 | 1.0075 | 1.0075 | 1.0075 | 1.0075 | 1.0075 | 1.0075 | 1.0075 | 1.0075 | 1.0075 | 1.0075 | 1.0075 |  | 7.3764 | 29.6661 | 35.5027 | 3.0778 | 3.107 | 3.7079 | 5.2898 | 6.3505 | 7.3879 | 8.6009 | 9.7261 | 10.8175 | 10.944 | 12.2175 | 11.2557 | 11.2557 | 11.2557 | 11.2557 | 11.2557 | 11.2557 | 11.2557 | 11.2557 | 11.2557 | 11.2557 | 11.2557 | 11.2557 | 11.2557 | 11.2557 | 11.2557 | 11.2557
95% |  | 25.5649 | 33.0227 | [6 empty] | 0.00044641 | 0.21315 | 0.74057 | 2.0862 | 3.7644 | 3.651 | 3.651 | 3.651 | 3.651 | 3.651 | 3.651 | 3.651 | 3.651 | 3.651 | 3.651 | 3.651 | 3.651 | 3.651 | 3.651 | 3.651 | 3.651 |  | 9.3236 | 42.2437 | 50.864 | 2.9749 | 3.0179 | 3.9054 | 6.2418 | 7.8083 | 9.3406 | 11.1321 | 12.7938 | 14.4058 | 14.5926 | 16.4735 | 15.053 | 15.053 | 15.053 | 15.053 | 15.053 | 15.053 | 15.053 | 15.053 | 15.053 | 15.053 | 15.053 | 15.053 | 15.053 | 15.053 | 15.053 | 15.053
90% |  | 38.7554 | 51.6899 | [9 empty] | 0.27515 | 1.5674 | 1.4478 | 1.4478 | 1.4478 | 1.4478 | 1.4478 | 1.4478 | 1.4478 | 1.4478 | 1.4478 | 1.4478 | 1.4478 | 1.4478 | 1.4478 | 1.4478 | 1.4478 | 1.4478 |  | 23.6749 | 166.4146 | 203.7914 | 1.4535 | 1.5195 | 3.1974 | 10.4245 | 17.1049 | 23.7487 | 31.5166 | 38.7217 | 45.7112 | 46.5209 | 54.6765 | 48.5172 | 48.5172 | 48.5172 | 48.5172 | 48.5172 | 48.5172 | 48.5172 | 48.5172 | 48.5172 | 48.5172 | 48.5172 | 48.5172 | 48.5172 | 48.5172 | 48.5172 | 48.5172
85% | FY26: 85.1452; FY27: 121.8514 |  | 2.1581 | 132.583 | 167.9395 |  |  |  |  | 0.34639 | 2.187 | 6.2725 | 11.8444 | 18.4041 | 19.1701 | 26.8848 | 21.0585 | 21.0585 | 21.0585 | 21.0585 | 21.0585 | 21.0585 | 21.0585 | 21.0585 | 21.0585 | 21.0585 | 21.0585 | 21.0585 | 21.0585 | 21.0585 | 21.0585 | 21.0585
80% | FY26: 80.0361; FY27: 131.3082 |  |  | 73.1492 | 97.8426 | [8 empty] | 0.3061 | 0.40884 | 2.2484 | 0.72454 | 0.72454 | 0.72454 | 0.72454 | 0.72454 | 0.72454 | 0.72454 | 0.72454 | 0.72454 | 0.72454 | 0.72454 | 0.72454 | 0.72454 | 0.72454 | 0.72454 | 0.72454
75% | FY26: 94.1589; FY27: 227.8159 |  |  | 91.3687 | 135.4427
70% | FY26: 6.5776; FY27: 168.5277 |  |  | 85.2049 | 165.4959
65% | FY27: 9.6236 |  |  | 10.9945 | 90.8581
60% | [33 empty] | 3.8091
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 335.6968 | 750.8128 | 0 | 0 | 0 | 0 | 0 | 0.0026583 | 0.096123 | 0.47561 | 1.1554 | 3.051 | 6.3624 | 6.1063 | 6.1063 | 6.1063 | 6.1063 | 6.1063 | 6.1063 | 6.1063 | 6.1063 | 6.1063 | 6.1063 | 6.1063 | 6.1063 | 6.1063 | 6.1063 | 6.1063 | 6.1063 | E @ R (MWh) | 55.5322 | 678.63 | 1007.4559 | 13.9472 | 14.1298 | 18.2129 | 31.7718 | 43.044 | 55.6809 | 72.3894 | 89.6699 | 107.8938 | 110.0783 | 132.8855 | 115.5265 | 115.5265 | 115.5265 | 115.5265 | 115.5265 | 115.5265 | 115.5265 | 115.5265 | 115.5265 | 115.5265 | 115.5265 | 115.5265 | 115.5265 | 115.5265 | 115.5265 | 115.5265
Option 5 Summer POE50 W E @ R (MWh) N 1 | 0 | 234.9878 | 525.569 | 0 | 0 | 0 | 0 | 0 | 0.0018608 | 0.067286 | 0.33292 | 0.8088 | 2.1357 | 4.4537 | 4.2744 | 4.2744 | 4.2744 | 4.2744 | 4.2744 | 4.2744 | 4.2744 | 4.2744 | 4.2744 | 4.2744 | 4.2744 | 4.2744 | 4.2744 | 4.2744 | 4.2744 | 4.2744 | Option 5 Summer POE10 W E @ R (MWh) N 1 | 16.6597 | 203.589 | 302.2368 | 4.1842 | 4.2389 | 5.4639 | 9.5315 | 12.9132 | 16.7043 | 21.7168 | 26.901 | 32.3681 | 33.0235 | 39.8656 | 34.6579 | 34.6579 | 34.6579 | 34.6579 | 34.6579 | 34.6579 | 34.6579 | 34.6579 | 34.6579 | 34.6579 | 34.6579 | 34.6579 | 34.6579 | 34.6579 | 34.6579 | 34.6579
Option 6 -
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% |  | 9.8725 | 15.8941 | 16.9205 | 17.721 | 19.0994 | 22.2353 | 24.3344 | 26.9936 | 28.3739 | 29.5883 | 27.3508 | 29.973 | 34.0954 | 30.9671 | 30.9671 | 30.9671 | 30.9671 | 30.9671 | 30.9671 | 30.9671 | 30.9671 | 30.9671 | 30.9671 | 30.9671 | 30.9671 | 30.9671 | 30.9671 | 30.9671 | 30.9671 |  |  | 13.7943 | 20.0509 | 21.019 | 21.6336 | 22.9821 | 26.167 | 27.9059 | 31.2184 | 41.2876 | 32.9866 | 31.3629 | 33.5547 | 38.348 | 35.1035 | 35.1035 | 35.1035 | 35.1035 | 35.1035 | 35.1035 | 35.1035 | 35.1035 | 35.1035 | 35.1035 | 35.1035 | 35.1035 | 35.1035 | 35.1035 | 35.1035 | 35.1035
98% |  | 10.848 | 18.0013 | 19.2206 | 20.1716 | 21.809 | 25.5342 | 28.0279 | 31.1869 | 32.8266 | 34.2691 | 31.6112 | 34.7262 | 39.6233 | 35.9071 | 35.9071 | 35.9071 | 35.9071 | 35.9071 | 35.9071 | 35.9071 | 35.9071 | 35.9071 | 35.9071 | 35.9071 | 35.9071 | 35.9071 | 35.9071 | 35.9071 | 35.9071 |  |  | 15.5069 | 22.9393 | 24.0893 | 24.8195 | 26.4214 | 30.2049 | 32.2706 | 36.2057 | 48.1672 | 38.3061 | 36.3773 | 38.981 | 44.6752 | 40.8209 | 40.8209 | 40.8209 | 40.8209 | 40.8209 | 40.8209 | 40.8209 | 40.8209 | 40.8209 | 40.8209 | 40.8209 | 40.8209 | 40.8209 | 40.8209 | 40.8209 | 40.8209
97% |  | 19.698 | 33.8593 | 36.2732 | 38.1558 | 41.3974 | 48.7723 | 53.7089 | 59.9627 | 63.2089 | 66.0646 | 60.8028 | 66.9695 | 76.6644 | 69.3073 | 69.3073 | 69.3073 | 69.3073 | 69.3073 | 69.3073 | 69.3073 | 69.3073 | 69.3073 | 69.3073 | 69.3073 | 69.3073 | 69.3073 | 69.3073 | 69.3073 | 69.3073 |  |  | 28.9211 | 43.6351 | 45.9118 | 47.3573 | 50.5286 | 58.0187 | 62.1081 | 69.8984 | 93.5787 | 74.0567 | 70.2382 | 75.3927 | 86.6655 | 79.0351 | 79.0351 | 79.0351 | 79.0351 | 79.0351 | 79.0351 | 79.0351 | 79.0351 | 79.0351 | 79.0351 | 79.0351 | 79.0351 | 79.0351 | 79.0351 | 79.0351 | 79.0351
95% |  | 50.103 | 91.9331 | 99.0634 | 104.6245 | 114.1996 | 135.9838 | 150.5658 | 169.0387 | 178.6273 | 187.0628 | 171.5201 | 189.7357 | 218.3728 | 196.6412 | 196.6412 | 196.6412 | 196.6412 | 196.6412 | 196.6412 | 196.6412 | 196.6412 | 196.6412 | 196.6412 | 196.6412 | 196.6412 | 196.6412 | 196.6412 | 196.6412 | 196.6412 |  |  | 77.3465 | 120.8094 | 127.5343 | 131.8043 | 141.1717 | 163.2964 | 175.3759 | 198.3872 | 268.3351 | 210.6702 | 199.3908 | 214.6165 | 247.9145 | 225.3755 | 225.3755 | 225.3755 | 225.3755 | 225.3755 | 225.3755 | 225.3755 | 225.3755 | 225.3755 | 225.3755 | 225.3755 | 225.3755 | 225.3755 | 225.3755 | 225.3755 | 225.3755
90% |  | 166.6526 | 397.287 | 436.6005 | 467.2624 | 520.0555 | 640.1647 | 720.5641 | 822.4165 | 875.2838 | 921.7942 | 836.0975 | 936.5313 | 1094.4248 | 974.6055 | 974.6055 | 974.6055 | 974.6055 | 974.6055 | 974.6055 | 974.6055 | 974.6055 | 974.6055 | 974.6055 | 974.6055 | 974.6055 | 974.6055 | 974.6055 | 974.6055 | 974.6055 |  |  | 316.8623 | 556.4991 | 593.5776 | 617.1207 | 668.7691 | 790.7554 | 857.3571 | 984.2321 | 1369.8972 | 1051.9556 | 989.7659 | 1073.714 | 1257.3061 | 1133.0351 | 1133.0351 | 1133.0351 | 1133.0351 | 1133.0351 | 1133.0351 | 1133.0351 | 1133.0351 | 1133.0351 | 1133.0351 | 1133.0351 | 1133.0351 | 1133.0351 | 1133.0351 | 1133.0351 | 1133.0351
85% |  | 49.283 | 550.9121 | 646.9524 | 721.8571 | 850.8267 | 1144.2449 | 1340.6551 | 1589.473 | 1718.6242 | 1832.2457 | 1622.8948 | 1868.2474 | 2253.97 | 1961.2601 | 1961.2601 | 1961.2601 | 1961.2601 | 1961.2601 | 1961.2601 | 1961.2601 | 1961.2601 | 1961.2601 | 1961.2601 | 1961.2601 | 1961.2601 | 1961.2601 | 1961.2601 | 1961.2601 | 1961.2601 |  |  | 354.4405 | 939.8561 | 1030.4361 | 1087.9502 | 1214.1234 | 1512.1274 | 1674.8304 | 1984.7771 | 2926.9292 | 2150.2208 | 1998.2958 | 2203.3748 | 2651.8773 | 2348.2922 | 2348.2922 | 2348.2922 | 2348.2922 | 2348.2922 | 2348.2922 | 2348.2922 | 2348.2922 | 2348.2922 | 2348.2922 | 2348.2922 | 2348.2922 | 2348.2922 | 2348.2922 | 2348.2922 | 2348.2922
80% |  |  | 170.3674 | 283.6364 | 390.7399 | 591.1469 | 1047.2057 | 1352.4853 | 1739.2221 | 1939.9613 | 2116.5629 | 1791.1696 | 2172.5202 | 2772.0475 | 2317.0894 | 2317.0894 | 2317.0894 | 2317.0894 | 2317.0894 | 2317.0894 | 2317.0894 | 2317.0894 | 2317.0894 | 2317.0894 | 2317.0894 | 2317.0894 | 2317.0894 | 2317.0894 | 2317.0894 | 2317.0894 |  |  | 26.6685 | 729.5248 | 870.3131 | 959.707 | 1155.8176 | 1619.0041 | 1871.8928 | 2353.6419 | 3818.0255 | 2610.7904 | 2374.6539 | 2693.4076 | 3390.5133 | 2918.6521 | 2918.6521 | 2918.6521 | 2918.6521 | 2918.6521 | 2918.6521 | 2918.6521 | 2918.6521 | 2918.6521 | 2918.6521 | 2918.6521 | 2918.6521 | 2918.6521 | 2918.6521 | 2918.6521 | 2918.6521
75% | [5 empty] | 24.883 | 275.7172 | 581.2462 | 1007.9249 | 1229.3962 | 1424.237 | 1065.2374 | 1485.9735 | 2147.4195 | 1645.4738 | 1645.4738 | 1645.4738 | 1645.4738 | 1645.4738 | 1645.4738 | 1645.4738 | 1645.4738 | 1645.4738 | 1645.4738 | 1645.4738 | 1645.4738 | 1645.4738 | 1645.4738 | 1645.4738 | 1645.4738 |  |  |  | 73.1703 | 147.4946 | 207.5247 | 373.0825 | 875.2908 | 1154.2977 | 1685.8014 | 3301.4252 | 1969.5079 | 1708.9835 | 2060.6577 | 2829.7599 | 2309.1653 | 2309.1653 | 2309.1653 | 2309.1653 | 2309.1653 | 2309.1653 | 2309.1653 | 2309.1653 | 2309.1653 | 2309.1653 | 2309.1653 | 2309.1653 | 2309.1653 | 2309.1653 | 2309.1653 | 2309.1653
70% | [7 empty] | 3.4379 | 133.5638 | 272.0098 | 431.8215 | 164.8836 | 489.6671 | 1193.5489 | 654.2363 | 654.2363 | 654.2363 | 654.2363 | 654.2363 | 654.2363 | 654.2363 | 654.2363 | 654.2363 | 654.2363 | 654.2363 | 654.2363 | 654.2363 | 654.2363 | 654.2363 | 654.2363 | [7 empty] | 73.4213 | 219.8269 | 697.566 | 2433.4635 | 1002.3928 | 722.4739 | 1100.3282 | 1926.6855 | 1367.3357 | 1367.3357 | 1367.3357 | 1367.3357 | 1367.3357 | 1367.3357 | 1367.3357 | 1367.3357 | 1367.3357 | 1367.3357 | 1367.3357 | 1367.3357 | 1367.3357 | 1367.3357 | 1367.3357 | 1367.3357
65% | FY38: 138.0019; FY39: 0.607; FY40: 0.607; FY41: 0.607; FY42: 0.607; FY43: 0.607; FY44: 0.607; FY45: 0.607; FY46: 0.607; FY47: 0.607; FY48: 0.607; FY49: 0.607; FY50: 0.607; FY51: 0.607; FY52: 0.607; FY53: 0.607; FY54: 0.607 | [9 empty] | 2.7969 | 1216.8668 | 62.358 | 4.774 | 97.5063 | 684.2805 | 231.4677 | 231.4677 | 231.4677 | 231.4677 | 231.4677 | 231.4677 | 231.4677 | 231.4677 | 231.4677 | 231.4677 | 231.4677 | 231.4677 | 231.4677 | 231.4677 | 231.4677 | 231.4677
60% | [40 empty] | 77.6441
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 306.4572 | 1278.2542 | 1538.6669 | 1760.5324 | 2183.4175 | 3339.858 | 4255.0255 | 5579.7822 | 6338.312 | 7043.6462 | 5771.5678 | 7274.3439 | 9968.1685 | 7886.0948 | 7886.0948 | 7886.0948 | 7886.0948 | 7886.0948 | 7886.0948 | 7886.0948 | 7886.0948 | 7886.0948 | 7886.0948 | 7886.0948 | 7886.0948 | 7886.0948 | 7886.0948 | 7886.0948 | 7886.0948 | E @ R (MWh) | 0 | 833.5401 | 2506.4849 | 2860.3759 | 3097.9173 | 3652.8965 | 5148.2859 | 6075.8653 | 8044.5252 | 15595.6201 | 9203.2451 | 8136.3162 | 9591.5333 | 13158.0259 | 10688.2832 | 10688.2832 | 10688.2832 | 10688.2832 | 10688.2832 | 10688.2832 | 10688.2832 | 10688.2832 | 10688.2832 | 10688.2832 | 10688.2832 | 10688.2832 | 10688.2832 | 10688.2832 | 10688.2832 | 10688.2832
Option 6 Winter POE50 W E @ R (MWh) N 1 | 0 | 214.5201 | 894.7779 | 1077.0669 | 1232.3727 | 1528.3922 | 2337.9006 | 2978.5179 | 3905.8475 | 4436.8184 | 4930.5523 | 4040.0974 | 5092.0407 | 6977.718 | 5520.2664 | 5520.2664 | 5520.2664 | 5520.2664 | 5520.2664 | 5520.2664 | 5520.2664 | 5520.2664 | 5520.2664 | 5520.2664 | 5520.2664 | 5520.2664 | 5520.2664 | 5520.2664 | 5520.2664 | 5520.2664 | Option 6 Winter POE10 W E @ R (MWh) N 1 | 0 | 250.062 | 751.9455 | 858.1128 | 929.3752 | 1095.8689 | 1544.4858 | 1822.7596 | 2413.3575 | 4678.686 | 2760.9735 | 2440.8949 | 2877.46 | 3947.4078 | 3206.485 | 3206.485 | 3206.485 | 3206.485 | 3206.485 | 3206.485 | 3206.485 | 3206.485 | 3206.485 | 3206.485 | 3206.485 | 3206.485 | 3206.485 | 3206.485 | 3206.485 | 3206.485
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 8.924 | 31.6709 | 37.6273 | 37.273 | 37.3028 | 37.916 | 39.5304 | 40.6128 | 41.6716 | 42.9095 | 44.0577 | 45.1715 | 45.3005 | 46.6002 | 45.6187 | 45.6187 | 45.6187 | 45.6187 | 45.6187 | 45.6187 | 45.6187 | 45.6187 | 45.6187 | 45.6187 | 45.6187 | 45.6187 | 45.6187 | 45.6187 | 45.6187 | 45.6187
98% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4.0751 | 15.3343 | 18.2825 | 18.1072 | 18.1219 | 18.4254 | 19.2245 | 19.7603 | 20.2843 | 20.897 | 21.4654 | 22.0167 | 22.0806 | 22.7239 | 22.238 | 22.238 | 22.238 | 22.238 | 22.238 | 22.238 | 22.238 | 22.238 | 22.238 | 22.238 | 22.238 | 22.238 | 22.238 | 22.238 | 22.238 | 22.238
97% |  | 5.4588 | 6.9736 | 6.9303 | 6.9298 | 7.103 | 7.2931 | 7.6829 | 7.9629 | 8.1151 | 8.2819 | 8.4343 | 8.7091 | 9.05 | 9.027 | 9.027 | 9.027 | 9.027 | 9.027 | 9.027 | 9.027 | 9.027 | 9.027 | 9.027 | 9.027 | 9.027 | 9.027 | 9.027 | 9.027 | 9.027 |  | 7.3764 | 29.6661 | 35.5027 | 35.1556 | 35.1847 | 35.7856 | 37.3676 | 38.4283 | 39.4657 | 40.6787 | 41.8039 | 42.8953 | 43.0218 | 44.2953 | 43.3335 | 43.3335 | 43.3335 | 43.3335 | 43.3335 | 43.3335 | 43.3335 | 43.3335 | 43.3335 | 43.3335 | 43.3335 | 43.3335 | 43.3335 | 43.3335 | 43.3335 | 43.3335
95% |  | 25.5649 | 33.0227 | 32.8093 | 32.8067 | 33.6597 | 34.5953 | 36.5142 | 37.8928 | 38.6423 | 39.4634 | 40.2137 | 41.5666 | 43.2448 | 43.1314 | 43.1314 | 43.1314 | 43.1314 | 43.1314 | 43.1314 | 43.1314 | 43.1314 | 43.1314 | 43.1314 | 43.1314 | 43.1314 | 43.1314 | 43.1314 | 43.1314 | 43.1314 |  | 9.3236 | 42.2437 | 50.864 | 50.3513 | 50.3943 | 51.2818 | 53.6182 | 55.1847 | 56.717 | 58.5085 | 60.1702 | 61.7822 | 61.969 | 63.8499 | 62.4294 | 62.4294 | 62.4294 | 62.4294 | 62.4294 | 62.4294 | 62.4294 | 62.4294 | 62.4294 | 62.4294 | 62.4294 | 62.4294 | 62.4294 | 62.4294 | 62.4294 | 62.4294
90% |  | 38.7554 | 51.6899 | 51.3198 | 51.3153 | 52.7947 | 54.4175 | 57.7455 | 60.1366 | 61.4365 | 62.8605 | 64.1618 | 66.5082 | 69.4189 | 69.2222 | 69.2222 | 69.2222 | 69.2222 | 69.2222 | 69.2222 | 69.2222 | 69.2222 | 69.2222 | 69.2222 | 69.2222 | 69.2222 | 69.2222 | 69.2222 | 69.2222 | 69.2222 |  | 23.6749 | 166.4146 | 203.7914 | 201.5685 | 201.7552 | 205.6032 | 215.7337 | 222.5261 | 229.1699 | 236.9378 | 244.1429 | 251.1324 | 251.9421 | 260.0977 | 253.9385 | 253.9385 | 253.9385 | 253.9385 | 253.9385 | 253.9385 | 253.9385 | 253.9385 | 253.9385 | 253.9385 | 253.9385 | 253.9385 | 253.9385 | 253.9385 | 253.9385 | 253.9385
85% |  | 85.1452 | 121.8514 | 120.801 | 120.7884 | 124.9866 | 129.5917 | 139.0363 | 145.8216 | 149.5106 | 153.5518 | 157.2446 | 163.9032 | 172.1633 | 171.605 | 171.605 | 171.605 | 171.605 | 171.605 | 171.605 | 171.605 | 171.605 | 171.605 | 171.605 | 171.605 | 171.605 | 171.605 | 171.605 | 171.605 | 171.605 |  | 2.1581 | 132.583 | 167.9395 | 165.8367 | 166.0133 | 169.6533 | 179.2362 | 185.6615 | 191.9461 | 199.2941 | 206.1098 | 212.7215 | 213.4874 | 221.2021 | 215.3759 | 215.3759 | 215.3759 | 215.3759 | 215.3759 | 215.3759 | 215.3759 | 215.3759 | 215.3759 | 215.3759 | 215.3759 | 215.3759 | 215.3759 | 215.3759 | 215.3759 | 215.3759
80% |  | 80.0361 | 131.3082 | 129.841 | 129.8234 | 135.6876 | 142.1201 | 155.3125 | 164.7904 | 169.9433 | 175.5881 | 180.7464 | 190.0472 | 201.5852 | 200.8054 | 200.8054 | 200.8054 | 200.8054 | 200.8054 | 200.8054 | 200.8054 | 200.8054 | 200.8054 | 200.8054 | 200.8054 | 200.8054 | 200.8054 | 200.8054 | 200.8054 | 200.8054 |  |  | 73.1492 | 97.8426 | 96.374 | 96.4973 | 99.0396 | 105.7324 | 110.2199 | 114.6092 | 119.7411 | 124.5013 | 129.1189 | 129.6539 | 135.0419 | 130.9728 | 130.9728 | 130.9728 | 130.9728 | 130.9728 | 130.9728 | 130.9728 | 130.9728 | 130.9728 | 130.9728 | 130.9728 | 130.9728 | 130.9728 | 130.9728 | 130.9728 | 130.9728
75% |  | 94.1589 | 227.8159 | 223.9912 | 223.9454 | 239.2321 | 256.0006 | 290.3908 | 315.098 | 328.5306 | 343.2457 | 356.6924 | 380.938 | 411.0152 | 408.9825 | 408.9825 | 408.9825 | 408.9825 | 408.9825 | 408.9825 | 408.9825 | 408.9825 | 408.9825 | 408.9825 | 408.9825 | 408.9825 | 408.9825 | 408.9825 | 408.9825 | 408.9825 |  |  | 91.3687 | 135.4427 | 132.8215 | 133.0415 | 137.5791 | 149.5248 | 157.5342 | 165.3684 | 174.5281 | 183.0243 | 191.2662 | 192.221 | 201.8378 | 194.575 | 194.575 | 194.575 | 194.575 | 194.575 | 194.575 | 194.575 | 194.575 | 194.575 | 194.575 | 194.575 | 194.575 | 194.575 | 194.575 | 194.575 | 194.575
70% |  | 6.5776 | 168.5277 | 161.9198 | 161.8408 | 188.2515 | 217.2224 | 276.6382 | 319.3247 | 342.5321 | 367.9553 | 391.1871 | 433.0761 | 485.0404 | 481.5284 | 481.5284 | 481.5284 | 481.5284 | 481.5284 | 481.5284 | 481.5284 | 481.5284 | 481.5284 | 481.5284 | 481.5284 | 481.5284 | 481.5284 | 481.5284 | 481.5284 | 481.5284 |  |  | 85.2049 | 165.4959 | 160.7208 | 161.1217 | 169.3879 | 191.1497 | 205.7408 | 220.0126 | 236.6991 | 252.1769 | 267.1913 | 268.9307 | 286.45 | 273.2191 | 273.2191 | 273.2191 | 273.2191 | 273.2191 | 273.2191 | 273.2191 | 273.2191 | 273.2191 | 273.2191 | 273.2191 | 273.2191 | 273.2191 | 273.2191 | 273.2191 | 273.2191
65% |  |  | 9.6236 | 6.9591 | 6.9298 | 20.0951 | 42.2143 | 111.9423 | 181.5617 | 226.0382 | 279.9918 | 333.9879 | 438.672 | 569.1816 | 560.3612 | 560.3612 | 560.3612 | 560.3612 | 560.3612 | 560.3612 | 560.3612 | 560.3612 | 560.3612 | 560.3612 | 560.3612 | 560.3612 | 560.3612 | 560.3612 | 560.3612 | 560.3612 |  |  | 10.9945 | 90.8581 | 84.8503 | 85.3547 | 95.7548 | 123.1346 | 141.4924 | 159.4485 | 180.4428 | 199.9162 | 218.8067 | 220.9952 | 243.0371 | 226.3906 | 226.3906 | 226.3906 | 226.3906 | 226.3906 | 226.3906 | 226.3906 | 226.3906 | 226.3906 | 226.3906 | 226.3906 | 226.3906 | 226.3906 | 226.3906 | 226.3906 | 226.3906
60% | [12 empty] | 5.9059 | 42.5222 | 39.014 | 39.014 | 39.014 | 39.014 | 39.014 | 39.014 | 39.014 | 39.014 | 39.014 | 39.014 | 39.014 | 39.014 | 39.014 | 39.014 | 39.014 | 39.014 |  |  |  | 3.8091 | 2.2281 | 2.3448 | 5.4041 | 19.2874 | 33.1836 | 50.2166 | 74.3153 | 100.576 | 129.3594 | 132.7839 | 167.2756 | 141.2268 | 141.2268 | 141.2268 | 141.2268 | 141.2268 | 141.2268 | 141.2268 | 141.2268 | 141.2268 | 141.2268 | 141.2268 | 141.2268 | 141.2268 | 141.2268 | 141.2268 | 141.2268
55% | [42 empty] | 0.36348 | 0.67093 | 8.8993 | 1.8255 | 1.8255 | 1.8255 | 1.8255 | 1.8255 | 1.8255 | 1.8255 | 1.8255 | 1.8255 | 1.8255 | 1.8255 | 1.8255 | 1.8255 | 1.8255 | 1.8255 | 1.8255
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 335.6968 | 750.8128 | 734.5714 | 734.3797 | 801.8103 | 883.4549 | 1075.2627 | 1232.5888 | 1324.7487 | 1430.9386 | 1532.6682 | 1729.3262 | 2003.2214 | 1983.6771 | 1983.6771 | 1983.6771 | 1983.6771 | 1983.6771 | 1983.6771 | 1983.6771 | 1983.6771 | 1983.6771 | 1983.6771 | 1983.6771 | 1983.6771 | 1983.6771 | 1983.6771 | 1983.6771 | 1983.6771 | E @ R (MWh) | 55.5322 | 678.63 | 1007.4559 | 985.2871 | 987.1322 | 1025.8309 | 1133.5396 | 1210.3445 | 1288.9099 | 1384.9521 | 1477.9447 | 1571.8256 | 1583.0571 | 1701.3108 | 1611.1437 | 1611.1437 | 1611.1437 | 1611.1437 | 1611.1437 | 1611.1437 | 1611.1437 | 1611.1437 | 1611.1437 | 1611.1437 | 1611.1437 | 1611.1437 | 1611.1437 | 1611.1437 | 1611.1437 | 1611.1437
Option 6 Summer POE50 W E @ R (MWh) N 1 | 0 | 234.9878 | 525.569 | 514.2 | 514.0658 | 561.2672 | 618.4185 | 752.6839 | 862.8122 | 927.3241 | 1001.657 | 1072.8678 | 1210.5283 | 1402.255 | 1388.5739 | 1388.5739 | 1388.5739 | 1388.5739 | 1388.5739 | 1388.5739 | 1388.5739 | 1388.5739 | 1388.5739 | 1388.5739 | 1388.5739 | 1388.5739 | 1388.5739 | 1388.5739 | 1388.5739 | 1388.5739 | Option 6 Summer POE10 W E @ R (MWh) N 1 | 16.6597 | 203.589 | 302.2368 | 295.5861 | 296.1396 | 307.7493 | 340.0619 | 363.1034 | 386.673 | 415.4856 | 443.3834 | 471.5477 | 474.9171 | 510.3932 | 483.3431 | 483.3431 | 483.3431 | 483.3431 | 483.3431 | 483.3431 | 483.3431 | 483.3431 | 483.3431 | 483.3431 | 483.3431 | 483.3431 | 483.3431 | 483.3431 | 483.3431 | 483.3431
Option 7 -
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% |  | 9.8725 | 15.8941 | 16.9205 | 17.721 | 19.0994 | 22.2353 | 24.3344 | 26.9936 | 28.3739 | 29.5883 | 27.3508 | 29.973 | 34.0954 | 30.9671 | 30.9671 | 30.9671 | 30.9671 | 30.9671 | 30.9671 | 30.9671 | 30.9671 | 30.9671 | 30.9671 | 30.9671 | 30.9671 | 30.9671 | 30.9671 | 30.9671 | 30.9671 |  |  | 13.7943 | 20.0509 | 21.019 | 21.6336 | 22.9821 | 26.167 | 27.9059 | 31.2184 | 41.2876 | 32.9866 | 31.3629 | 33.5547 | 38.348 | 35.1035 | 35.1035 | 35.1035 | 35.1035 | 35.1035 | 35.1035 | 35.1035 | 35.1035 | 35.1035 | 35.1035 | 35.1035 | 35.1035 | 35.1035 | 35.1035 | 35.1035 | 35.1035
98% |  | 10.848 | 18.0013 | 19.2206 | 20.1716 | 21.809 | 25.5342 | 28.0279 | 31.1869 | 32.8266 | 34.2691 | 31.6112 | 34.7262 | 39.6233 | 35.9071 | 35.9071 | 35.9071 | 35.9071 | 35.9071 | 35.9071 | 35.9071 | 35.9071 | 35.9071 | 35.9071 | 35.9071 | 35.9071 | 35.9071 | 35.9071 | 35.9071 | 35.9071 |  |  | 15.5069 | 22.9393 | 24.0893 | 24.8195 | 26.4214 | 30.2049 | 32.2706 | 36.2057 | 48.1672 | 38.3061 | 36.3773 | 38.981 | 44.6752 | 40.8209 | 40.8209 | 40.8209 | 40.8209 | 40.8209 | 40.8209 | 40.8209 | 40.8209 | 40.8209 | 40.8209 | 40.8209 | 40.8209 | 40.8209 | 40.8209 | 40.8209 | 40.8209
97% |  | 19.698 | 33.8593 | 36.2732 | 38.1558 | 41.3974 | 48.7723 | 53.7089 | 59.9627 | 63.2089 | 66.0646 | 60.8028 | 66.9695 | 76.6644 | 69.3073 | 69.3073 | 69.3073 | 69.3073 | 69.3073 | 69.3073 | 69.3073 | 69.3073 | 69.3073 | 69.3073 | 69.3073 | 69.3073 | 69.3073 | 69.3073 | 69.3073 | 69.3073 |  |  | 28.9211 | 43.6351 | 45.9118 | 47.3573 | 50.5286 | 58.0187 | 62.1081 | 69.8984 | 93.5787 | 74.0567 | 70.2382 | 75.3927 | 86.6655 | 79.0351 | 79.0351 | 79.0351 | 79.0351 | 79.0351 | 79.0351 | 79.0351 | 79.0351 | 79.0351 | 79.0351 | 79.0351 | 79.0351 | 79.0351 | 79.0351 | 79.0351 | 79.0351
95% |  | 50.103 | 91.9331 | 99.0634 | 104.6245 | 114.1996 | 135.9838 | 150.5658 | 169.0387 | 178.6273 | 187.0628 | 171.5201 | 189.7357 | 218.3728 | 196.6412 | 196.6412 | 196.6412 | 196.6412 | 196.6412 | 196.6412 | 196.6412 | 196.6412 | 196.6412 | 196.6412 | 196.6412 | 196.6412 | 196.6412 | 196.6412 | 196.6412 | 196.6412 |  |  | 77.3465 | 120.8094 | 127.5343 | 131.8043 | 141.1717 | 163.2964 | 175.3759 | 198.3872 | 268.3351 | 210.6702 | 199.3908 | 214.6165 | 247.9145 | 225.3755 | 225.3755 | 225.3755 | 225.3755 | 225.3755 | 225.3755 | 225.3755 | 225.3755 | 225.3755 | 225.3755 | 225.3755 | 225.3755 | 225.3755 | 225.3755 | 225.3755 | 225.3755
90% |  | 166.6526 | 397.287 | 436.6005 | 467.2624 | 520.0555 | 640.1647 | 720.5641 | 822.4165 | 875.2838 | 921.7942 | 836.0975 | 936.5313 | 1094.4248 | 974.6055 | 974.6055 | 974.6055 | 974.6055 | 974.6055 | 974.6055 | 974.6055 | 974.6055 | 974.6055 | 974.6055 | 974.6055 | 974.6055 | 974.6055 | 974.6055 | 974.6055 | 974.6055 |  |  | 316.8623 | 556.4991 | 593.5776 | 617.1207 | 668.7691 | 790.7554 | 857.3571 | 984.2321 | 1369.8972 | 1051.9556 | 989.7659 | 1073.714 | 1257.3061 | 1133.0351 | 1133.0351 | 1133.0351 | 1133.0351 | 1133.0351 | 1133.0351 | 1133.0351 | 1133.0351 | 1133.0351 | 1133.0351 | 1133.0351 | 1133.0351 | 1133.0351 | 1133.0351 | 1133.0351 | 1133.0351
85% |  | 49.283 | 550.9121 | 646.9524 | 721.8571 | 850.8267 | 1144.2449 | 1340.6551 | 1589.473 | 1718.6242 | 1832.2457 | 1622.8948 | 1868.2474 | 2253.97 | 1961.2601 | 1961.2601 | 1961.2601 | 1961.2601 | 1961.2601 | 1961.2601 | 1961.2601 | 1961.2601 | 1961.2601 | 1961.2601 | 1961.2601 | 1961.2601 | 1961.2601 | 1961.2601 | 1961.2601 | 1961.2601 |  |  | 354.4405 | 939.8561 | 1030.4361 | 1087.9502 | 1214.1234 | 1512.1274 | 1674.8304 | 1984.7771 | 2926.9292 | 2150.2208 | 1998.2958 | 2203.3748 | 2651.8773 | 2348.2922 | 2348.2922 | 2348.2922 | 2348.2922 | 2348.2922 | 2348.2922 | 2348.2922 | 2348.2922 | 2348.2922 | 2348.2922 | 2348.2922 | 2348.2922 | 2348.2922 | 2348.2922 | 2348.2922 | 2348.2922
80% |  |  | 170.3674 | 283.6364 | 390.7399 | 591.1469 | 1047.2057 | 1352.4853 | 1739.2221 | 1939.9613 | 2116.5629 | 1791.1696 | 2172.5202 | 2772.0475 | 2317.0894 | 2317.0894 | 2317.0894 | 2317.0894 | 2317.0894 | 2317.0894 | 2317.0894 | 2317.0894 | 2317.0894 | 2317.0894 | 2317.0894 | 2317.0894 | 2317.0894 | 2317.0894 | 2317.0894 | 2317.0894 |  |  | 26.6685 | 729.5248 | 870.3131 | 959.707 | 1155.8176 | 1619.0041 | 1871.8928 | 2353.6419 | 3818.0255 | 2610.7904 | 2374.6539 | 2693.4076 | 3390.5133 | 2918.6521 | 2918.6521 | 2918.6521 | 2918.6521 | 2918.6521 | 2918.6521 | 2918.6521 | 2918.6521 | 2918.6521 | 2918.6521 | 2918.6521 | 2918.6521 | 2918.6521 | 2918.6521 | 2918.6521 | 2918.6521
75% | [5 empty] | 24.883 | 275.7172 | 581.2462 | 1007.9249 | 1229.3962 | 1424.237 | 1065.2374 | 1485.9735 | 2147.4195 | 1645.4738 | 1645.4738 | 1645.4738 | 1645.4738 | 1645.4738 | 1645.4738 | 1645.4738 | 1645.4738 | 1645.4738 | 1645.4738 | 1645.4738 | 1645.4738 | 1645.4738 | 1645.4738 | 1645.4738 | 1645.4738 |  |  |  | 73.1703 | 147.4946 | 207.5247 | 373.0825 | 875.2908 | 1154.2977 | 1685.8014 | 3301.4252 | 1969.5079 | 1708.9835 | 2060.6577 | 2829.7599 | 2309.1653 | 2309.1653 | 2309.1653 | 2309.1653 | 2309.1653 | 2309.1653 | 2309.1653 | 2309.1653 | 2309.1653 | 2309.1653 | 2309.1653 | 2309.1653 | 2309.1653 | 2309.1653 | 2309.1653 | 2309.1653
70% | [7 empty] | 3.4379 | 133.5638 | 272.0098 | 431.8215 | 164.8836 | 489.6671 | 1193.5489 | 654.2363 | 654.2363 | 654.2363 | 654.2363 | 654.2363 | 654.2363 | 654.2363 | 654.2363 | 654.2363 | 654.2363 | 654.2363 | 654.2363 | 654.2363 | 654.2363 | 654.2363 | 654.2363 | [7 empty] | 73.4213 | 219.8269 | 697.566 | 2433.4635 | 1002.3928 | 722.4739 | 1100.3282 | 1926.6855 | 1367.3357 | 1367.3357 | 1367.3357 | 1367.3357 | 1367.3357 | 1367.3357 | 1367.3357 | 1367.3357 | 1367.3357 | 1367.3357 | 1367.3357 | 1367.3357 | 1367.3357 | 1367.3357 | 1367.3357 | 1367.3357
65% | FY38: 138.0019; FY39: 0.607; FY40: 0.607; FY41: 0.607; FY42: 0.607; FY43: 0.607; FY44: 0.607; FY45: 0.607; FY46: 0.607; FY47: 0.607; FY48: 0.607; FY49: 0.607; FY50: 0.607; FY51: 0.607; FY52: 0.607; FY53: 0.607; FY54: 0.607 | [9 empty] | 2.7969 | 1216.8668 | 62.358 | 4.774 | 97.5063 | 684.2805 | 231.4677 | 231.4677 | 231.4677 | 231.4677 | 231.4677 | 231.4677 | 231.4677 | 231.4677 | 231.4677 | 231.4677 | 231.4677 | 231.4677 | 231.4677 | 231.4677 | 231.4677 | 231.4677
60% | [40 empty] | 77.6441
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 306.4572 | 1278.2542 | 1538.6669 | 1760.5324 | 2183.4175 | 3339.858 | 4255.0255 | 5579.7822 | 6338.312 | 7043.6462 | 5771.5678 | 7274.3439 | 9968.1685 | 7886.0948 | 7886.0948 | 7886.0948 | 7886.0948 | 7886.0948 | 7886.0948 | 7886.0948 | 7886.0948 | 7886.0948 | 7886.0948 | 7886.0948 | 7886.0948 | 7886.0948 | 7886.0948 | 7886.0948 | 7886.0948 | E @ R (MWh) | 0 | 833.5401 | 2506.4849 | 2860.3759 | 3097.9173 | 3652.8965 | 5148.2859 | 6075.8653 | 8044.5252 | 15595.6201 | 9203.2451 | 8136.3162 | 9591.5333 | 13158.0259 | 10688.2832 | 10688.2832 | 10688.2832 | 10688.2832 | 10688.2832 | 10688.2832 | 10688.2832 | 10688.2832 | 10688.2832 | 10688.2832 | 10688.2832 | 10688.2832 | 10688.2832 | 10688.2832 | 10688.2832 | 10688.2832
Option 7 Winter POE50 W E @ R (MWh) N 1 | 0 | 214.5201 | 894.7779 | 1077.0669 | 1232.3727 | 1528.3922 | 2337.9006 | 2978.5179 | 3905.8475 | 4436.8184 | 4930.5523 | 4040.0974 | 5092.0407 | 6977.718 | 5520.2664 | 5520.2664 | 5520.2664 | 5520.2664 | 5520.2664 | 5520.2664 | 5520.2664 | 5520.2664 | 5520.2664 | 5520.2664 | 5520.2664 | 5520.2664 | 5520.2664 | 5520.2664 | 5520.2664 | 5520.2664 | Option 7 Winter POE10 W E @ R (MWh) N 1 | 0 | 250.062 | 751.9455 | 858.1128 | 929.3752 | 1095.8689 | 1544.4858 | 1822.7596 | 2413.3575 | 4678.686 | 2760.9735 | 2440.8949 | 2877.46 | 3947.4078 | 3206.485 | 3206.485 | 3206.485 | 3206.485 | 3206.485 | 3206.485 | 3206.485 | 3206.485 | 3206.485 | 3206.485 | 3206.485 | 3206.485 | 3206.485 | 3206.485 | 3206.485 | 3206.485
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 8.924 | 31.6709 | 37.6273 | 37.273 | 37.3028 | 37.916 | 39.5304 | 40.6128 | 41.6716 | 42.9095 | 44.0577 | 45.1715 | 45.3005 | 46.6002 | 45.6187 | 45.6187 | 45.6187 | 45.6187 | 45.6187 | 45.6187 | 45.6187 | 45.6187 | 45.6187 | 45.6187 | 45.6187 | 45.6187 | 45.6187 | 45.6187 | 45.6187 | 45.6187
98% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4.0751 | 15.3343 | 18.2825 | 18.1072 | 18.1219 | 18.4254 | 19.2245 | 19.7603 | 20.2843 | 20.897 | 21.4654 | 22.0167 | 22.0806 | 22.7239 | 22.238 | 22.238 | 22.238 | 22.238 | 22.238 | 22.238 | 22.238 | 22.238 | 22.238 | 22.238 | 22.238 | 22.238 | 22.238 | 22.238 | 22.238 | 22.238
97% |  | 5.4588 | 6.9736 | 6.9303 | 6.9298 | 7.103 | 7.2931 | 7.6829 | 7.9629 | 8.1151 | 8.2819 | 8.4343 | 8.7091 | 9.05 | 9.027 | 9.027 | 9.027 | 9.027 | 9.027 | 9.027 | 9.027 | 9.027 | 9.027 | 9.027 | 9.027 | 9.027 | 9.027 | 9.027 | 9.027 | 9.027 |  | 7.3764 | 29.6661 | 35.5027 | 35.1556 | 35.1847 | 35.7856 | 37.3676 | 38.4283 | 39.4657 | 40.6787 | 41.8039 | 42.8953 | 43.0218 | 44.2953 | 43.3335 | 43.3335 | 43.3335 | 43.3335 | 43.3335 | 43.3335 | 43.3335 | 43.3335 | 43.3335 | 43.3335 | 43.3335 | 43.3335 | 43.3335 | 43.3335 | 43.3335 | 43.3335
95% |  | 25.5649 | 33.0227 | 32.8093 | 32.8067 | 33.6597 | 34.5953 | 36.5142 | 37.8928 | 38.6423 | 39.4634 | 40.2137 | 41.5666 | 43.2448 | 43.1314 | 43.1314 | 43.1314 | 43.1314 | 43.1314 | 43.1314 | 43.1314 | 43.1314 | 43.1314 | 43.1314 | 43.1314 | 43.1314 | 43.1314 | 43.1314 | 43.1314 | 43.1314 |  | 9.3236 | 42.2437 | 50.864 | 50.3513 | 50.3943 | 51.2818 | 53.6182 | 55.1847 | 56.717 | 58.5085 | 60.1702 | 61.7822 | 61.969 | 63.8499 | 62.4294 | 62.4294 | 62.4294 | 62.4294 | 62.4294 | 62.4294 | 62.4294 | 62.4294 | 62.4294 | 62.4294 | 62.4294 | 62.4294 | 62.4294 | 62.4294 | 62.4294 | 62.4294
90% |  | 38.7554 | 51.6899 | 51.3198 | 51.3153 | 52.7947 | 54.4175 | 57.7455 | 60.1366 | 61.4365 | 62.8605 | 64.1618 | 66.5082 | 69.4189 | 69.2222 | 69.2222 | 69.2222 | 69.2222 | 69.2222 | 69.2222 | 69.2222 | 69.2222 | 69.2222 | 69.2222 | 69.2222 | 69.2222 | 69.2222 | 69.2222 | 69.2222 | 69.2222 |  | 23.6749 | 166.4146 | 203.7914 | 201.5685 | 201.7552 | 205.6032 | 215.7337 | 222.5261 | 229.1699 | 236.9378 | 244.1429 | 251.1324 | 251.9421 | 260.0977 | 253.9385 | 253.9385 | 253.9385 | 253.9385 | 253.9385 | 253.9385 | 253.9385 | 253.9385 | 253.9385 | 253.9385 | 253.9385 | 253.9385 | 253.9385 | 253.9385 | 253.9385 | 253.9385
85% |  | 85.1452 | 121.8514 | 120.801 | 120.7884 | 124.9866 | 129.5917 | 139.0363 | 145.8216 | 149.5106 | 153.5518 | 157.2446 | 163.9032 | 172.1633 | 171.605 | 171.605 | 171.605 | 171.605 | 171.605 | 171.605 | 171.605 | 171.605 | 171.605 | 171.605 | 171.605 | 171.605 | 171.605 | 171.605 | 171.605 | 171.605 |  | 2.1581 | 132.583 | 167.9395 | 165.8367 | 166.0133 | 169.6533 | 179.2362 | 185.6615 | 191.9461 | 199.2941 | 206.1098 | 212.7215 | 213.4874 | 221.2021 | 215.3759 | 215.3759 | 215.3759 | 215.3759 | 215.3759 | 215.3759 | 215.3759 | 215.3759 | 215.3759 | 215.3759 | 215.3759 | 215.3759 | 215.3759 | 215.3759 | 215.3759 | 215.3759
80% |  | 80.0361 | 131.3082 | 129.841 | 129.8234 | 135.6876 | 142.1201 | 155.3125 | 164.7904 | 169.9433 | 175.5881 | 180.7464 | 190.0472 | 201.5852 | 200.8054 | 200.8054 | 200.8054 | 200.8054 | 200.8054 | 200.8054 | 200.8054 | 200.8054 | 200.8054 | 200.8054 | 200.8054 | 200.8054 | 200.8054 | 200.8054 | 200.8054 | 200.8054 |  |  | 73.1492 | 97.8426 | 96.374 | 96.4973 | 99.0396 | 105.7324 | 110.2199 | 114.6092 | 119.7411 | 124.5013 | 129.1189 | 129.6539 | 135.0419 | 130.9728 | 130.9728 | 130.9728 | 130.9728 | 130.9728 | 130.9728 | 130.9728 | 130.9728 | 130.9728 | 130.9728 | 130.9728 | 130.9728 | 130.9728 | 130.9728 | 130.9728 | 130.9728
75% |  | 94.1589 | 227.8159 | 223.9912 | 223.9454 | 239.2321 | 256.0006 | 290.3908 | 315.098 | 328.5306 | 343.2457 | 356.6924 | 380.938 | 411.0152 | 408.9825 | 408.9825 | 408.9825 | 408.9825 | 408.9825 | 408.9825 | 408.9825 | 408.9825 | 408.9825 | 408.9825 | 408.9825 | 408.9825 | 408.9825 | 408.9825 | 408.9825 | 408.9825 |  |  | 91.3687 | 135.4427 | 132.8215 | 133.0415 | 137.5791 | 149.5248 | 157.5342 | 165.3684 | 174.5281 | 183.0243 | 191.2662 | 192.221 | 201.8378 | 194.575 | 194.575 | 194.575 | 194.575 | 194.575 | 194.575 | 194.575 | 194.575 | 194.575 | 194.575 | 194.575 | 194.575 | 194.575 | 194.575 | 194.575 | 194.575
70% |  | 6.5776 | 168.5277 | 161.9198 | 161.8408 | 188.2515 | 217.2224 | 276.6382 | 319.3247 | 342.5321 | 367.9553 | 391.1871 | 433.0761 | 485.0404 | 481.5284 | 481.5284 | 481.5284 | 481.5284 | 481.5284 | 481.5284 | 481.5284 | 481.5284 | 481.5284 | 481.5284 | 481.5284 | 481.5284 | 481.5284 | 481.5284 | 481.5284 | 481.5284 |  |  | 85.2049 | 165.4959 | 160.7208 | 161.1217 | 169.3879 | 191.1497 | 205.7408 | 220.0126 | 236.6991 | 252.1769 | 267.1913 | 268.9307 | 286.45 | 273.2191 | 273.2191 | 273.2191 | 273.2191 | 273.2191 | 273.2191 | 273.2191 | 273.2191 | 273.2191 | 273.2191 | 273.2191 | 273.2191 | 273.2191 | 273.2191 | 273.2191 | 273.2191
65% |  |  | 9.6236 | 6.9591 | 6.9298 | 20.0951 | 42.2143 | 111.9423 | 181.5617 | 226.0382 | 279.9918 | 333.9879 | 438.672 | 569.1816 | 560.3612 | 560.3612 | 560.3612 | 560.3612 | 560.3612 | 560.3612 | 560.3612 | 560.3612 | 560.3612 | 560.3612 | 560.3612 | 560.3612 | 560.3612 | 560.3612 | 560.3612 | 560.3612 |  |  | 10.9945 | 90.8581 | 84.8503 | 85.3547 | 95.7548 | 123.1346 | 141.4924 | 159.4485 | 180.4428 | 199.9162 | 218.8067 | 220.9952 | 243.0371 | 226.3906 | 226.3906 | 226.3906 | 226.3906 | 226.3906 | 226.3906 | 226.3906 | 226.3906 | 226.3906 | 226.3906 | 226.3906 | 226.3906 | 226.3906 | 226.3906 | 226.3906 | 226.3906
60% | [12 empty] | 5.9059 | 42.5222 | 39.014 | 39.014 | 39.014 | 39.014 | 39.014 | 39.014 | 39.014 | 39.014 | 39.014 | 39.014 | 39.014 | 39.014 | 39.014 | 39.014 | 39.014 | 39.014 |  |  |  | 3.8091 | 2.2281 | 2.3448 | 5.4041 | 19.2874 | 33.1836 | 50.2166 | 74.3153 | 100.576 | 129.3594 | 132.7839 | 167.2756 | 141.2268 | 141.2268 | 141.2268 | 141.2268 | 141.2268 | 141.2268 | 141.2268 | 141.2268 | 141.2268 | 141.2268 | 141.2268 | 141.2268 | 141.2268 | 141.2268 | 141.2268 | 141.2268
55% | [42 empty] | 0.36348 | 0.67093 | 8.8993 | 1.8255 | 1.8255 | 1.8255 | 1.8255 | 1.8255 | 1.8255 | 1.8255 | 1.8255 | 1.8255 | 1.8255 | 1.8255 | 1.8255 | 1.8255 | 1.8255 | 1.8255 | 1.8255
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 335.6968 | 750.8128 | 734.5714 | 734.3797 | 801.8103 | 883.4549 | 1075.2627 | 1232.5888 | 1324.7487 | 1430.9386 | 1532.6682 | 1729.3262 | 2003.2214 | 1983.6771 | 1983.6771 | 1983.6771 | 1983.6771 | 1983.6771 | 1983.6771 | 1983.6771 | 1983.6771 | 1983.6771 | 1983.6771 | 1983.6771 | 1983.6771 | 1983.6771 | 1983.6771 | 1983.6771 | 1983.6771 | E @ R (MWh) | 55.5322 | 678.63 | 1007.4559 | 985.2871 | 987.1322 | 1025.8309 | 1133.5396 | 1210.3445 | 1288.9099 | 1384.9521 | 1477.9447 | 1571.8256 | 1583.0571 | 1701.3108 | 1611.1437 | 1611.1437 | 1611.1437 | 1611.1437 | 1611.1437 | 1611.1437 | 1611.1437 | 1611.1437 | 1611.1437 | 1611.1437 | 1611.1437 | 1611.1437 | 1611.1437 | 1611.1437 | 1611.1437 | 1611.1437
Option 7 Summer POE50 W E @ R (MWh) N 1 | 0 | 234.9878 | 525.569 | 514.2 | 514.0658 | 561.2672 | 618.4185 | 752.6839 | 862.8122 | 927.3241 | 1001.657 | 1072.8678 | 1210.5283 | 1402.255 | 1388.5739 | 1388.5739 | 1388.5739 | 1388.5739 | 1388.5739 | 1388.5739 | 1388.5739 | 1388.5739 | 1388.5739 | 1388.5739 | 1388.5739 | 1388.5739 | 1388.5739 | 1388.5739 | 1388.5739 | 1388.5739 | Option 7 Summer POE10 W E @ R (MWh) N 1 | 16.6597 | 203.589 | 302.2368 | 295.5861 | 296.1396 | 307.7493 | 340.0619 | 363.1034 | 386.673 | 415.4856 | 443.3834 | 471.5477 | 474.9171 | 510.3932 | 483.3431 | 483.3431 | 483.3431 | 483.3431 | 483.3431 | 483.3431 | 483.3431 | 483.3431 | 483.3431 | 483.3431 | 483.3431 | 483.3431 | 483.3431 | 483.3431 | 483.3431 | 483.3431
Option 8 -
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% |  | 9.8725 | 15.8941 | 16.9205 | 17.721 | 19.0994 | 22.2353 | 24.3344 | 26.9936 | 28.3739 | 29.5883 | 27.3508 | 29.973 | 34.0954 | 30.9671 | 30.9671 | 30.9671 | 30.9671 | 30.9671 | 30.9671 | 30.9671 | 30.9671 | 30.9671 | 30.9671 | 30.9671 | 30.9671 | 30.9671 | 30.9671 | 30.9671 | 30.9671 |  |  | 13.7943 | 20.0509 | 21.019 | 21.6336 | 22.9821 | 26.167 | 27.9059 | 31.2184 | 41.2876 | 32.9866 | 31.3629 | 33.5547 | 38.348 | 35.1035 | 35.1035 | 35.1035 | 35.1035 | 35.1035 | 35.1035 | 35.1035 | 35.1035 | 35.1035 | 35.1035 | 35.1035 | 35.1035 | 35.1035 | 35.1035 | 35.1035 | 35.1035
98% |  | 10.848 | 18.0013 | 19.2206 | 20.1716 | 21.809 | 25.5342 | 28.0279 | 31.1869 | 32.8266 | 34.2691 | 31.6112 | 34.7262 | 39.6233 | 35.9071 | 35.9071 | 35.9071 | 35.9071 | 35.9071 | 35.9071 | 35.9071 | 35.9071 | 35.9071 | 35.9071 | 35.9071 | 35.9071 | 35.9071 | 35.9071 | 35.9071 | 35.9071 |  |  | 15.5069 | 22.9393 | 24.0893 | 24.8195 | 26.4214 | 30.2049 | 32.2706 | 36.2057 | 48.1672 | 38.3061 | 36.3773 | 38.981 | 44.6752 | 40.8209 | 40.8209 | 40.8209 | 40.8209 | 40.8209 | 40.8209 | 40.8209 | 40.8209 | 40.8209 | 40.8209 | 40.8209 | 40.8209 | 40.8209 | 40.8209 | 40.8209 | 40.8209
97% |  | 19.698 | 33.8593 | 36.2732 | 38.1558 | 41.3974 | 48.7723 | 53.7089 | 59.9627 | 63.2089 | 66.0646 | 60.8028 | 66.9695 | 76.6644 | 69.3073 | 69.3073 | 69.3073 | 69.3073 | 69.3073 | 69.3073 | 69.3073 | 69.3073 | 69.3073 | 69.3073 | 69.3073 | 69.3073 | 69.3073 | 69.3073 | 69.3073 | 69.3073 |  |  | 28.9211 | 43.6351 | 45.9118 | 47.3573 | 50.5286 | 58.0187 | 62.1081 | 69.8984 | 93.5787 | 74.0567 | 70.2382 | 75.3927 | 86.6655 | 79.0351 | 79.0351 | 79.0351 | 79.0351 | 79.0351 | 79.0351 | 79.0351 | 79.0351 | 79.0351 | 79.0351 | 79.0351 | 79.0351 | 79.0351 | 79.0351 | 79.0351 | 79.0351
95% |  | 50.103 | 91.9331 | 99.0634 | 104.6245 | 114.1996 | 135.9838 | 150.5658 | 169.0387 | 178.6273 | 187.0628 | 171.5201 | 189.7357 | 218.3728 | 196.6412 | 196.6412 | 196.6412 | 196.6412 | 196.6412 | 196.6412 | 196.6412 | 196.6412 | 196.6412 | 196.6412 | 196.6412 | 196.6412 | 196.6412 | 196.6412 | 196.6412 | 196.6412 |  |  | 77.3465 | 120.8094 | 127.5343 | 131.8043 | 141.1717 | 163.2964 | 175.3759 | 198.3872 | 268.3351 | 210.6702 | 199.3908 | 214.6165 | 247.9145 | 225.3755 | 225.3755 | 225.3755 | 225.3755 | 225.3755 | 225.3755 | 225.3755 | 225.3755 | 225.3755 | 225.3755 | 225.3755 | 225.3755 | 225.3755 | 225.3755 | 225.3755 | 225.3755
90% |  | 166.6526 | 397.287 | 436.6005 | 467.2624 | 520.0555 | 640.1647 | 720.5641 | 822.4165 | 875.2838 | 921.7942 | 836.0975 | 936.5313 | 1094.4248 | 974.6055 | 974.6055 | 974.6055 | 974.6055 | 974.6055 | 974.6055 | 974.6055 | 974.6055 | 974.6055 | 974.6055 | 974.6055 | 974.6055 | 974.6055 | 974.6055 | 974.6055 | 974.6055 |  |  | 316.8623 | 556.4991 | 593.5776 | 617.1207 | 668.7691 | 790.7554 | 857.3571 | 984.2321 | 1369.8972 | 1051.9556 | 989.7659 | 1073.714 | 1257.3061 | 1133.0351 | 1133.0351 | 1133.0351 | 1133.0351 | 1133.0351 | 1133.0351 | 1133.0351 | 1133.0351 | 1133.0351 | 1133.0351 | 1133.0351 | 1133.0351 | 1133.0351 | 1133.0351 | 1133.0351 | 1133.0351
85% |  | 49.283 | 550.9121 | 646.9524 | 721.8571 | 850.8267 | 1144.2449 | 1340.6551 | 1589.473 | 1718.6242 | 1832.2457 | 1622.8948 | 1868.2474 | 2253.97 | 1961.2601 | 1961.2601 | 1961.2601 | 1961.2601 | 1961.2601 | 1961.2601 | 1961.2601 | 1961.2601 | 1961.2601 | 1961.2601 | 1961.2601 | 1961.2601 | 1961.2601 | 1961.2601 | 1961.2601 | 1961.2601 |  |  | 354.4405 | 939.8561 | 1030.4361 | 1087.9502 | 1214.1234 | 1512.1274 | 1674.8304 | 1984.7771 | 2926.9292 | 2150.2208 | 1998.2958 | 2203.3748 | 2651.8773 | 2348.2922 | 2348.2922 | 2348.2922 | 2348.2922 | 2348.2922 | 2348.2922 | 2348.2922 | 2348.2922 | 2348.2922 | 2348.2922 | 2348.2922 | 2348.2922 | 2348.2922 | 2348.2922 | 2348.2922 | 2348.2922
80% |  |  | 170.3674 | 283.6364 | 390.7399 | 591.1469 | 1047.2057 | 1352.4853 | 1739.2221 | 1939.9613 | 2116.5629 | 1791.1696 | 2172.5202 | 2772.0475 | 2317.0894 | 2317.0894 | 2317.0894 | 2317.0894 | 2317.0894 | 2317.0894 | 2317.0894 | 2317.0894 | 2317.0894 | 2317.0894 | 2317.0894 | 2317.0894 | 2317.0894 | 2317.0894 | 2317.0894 | 2317.0894 |  |  | 26.6685 | 729.5248 | 870.3131 | 959.707 | 1155.8176 | 1619.0041 | 1871.8928 | 2353.6419 | 3818.0255 | 2610.7904 | 2374.6539 | 2693.4076 | 3390.5133 | 2918.6521 | 2918.6521 | 2918.6521 | 2918.6521 | 2918.6521 | 2918.6521 | 2918.6521 | 2918.6521 | 2918.6521 | 2918.6521 | 2918.6521 | 2918.6521 | 2918.6521 | 2918.6521 | 2918.6521 | 2918.6521
75% | [5 empty] | 24.883 | 275.7172 | 581.2462 | 1007.9249 | 1229.3962 | 1424.237 | 1065.2374 | 1485.9735 | 2147.4195 | 1645.4738 | 1645.4738 | 1645.4738 | 1645.4738 | 1645.4738 | 1645.4738 | 1645.4738 | 1645.4738 | 1645.4738 | 1645.4738 | 1645.4738 | 1645.4738 | 1645.4738 | 1645.4738 | 1645.4738 | 1645.4738 |  |  |  | 73.1703 | 147.4946 | 207.5247 | 373.0825 | 875.2908 | 1154.2977 | 1685.8014 | 3301.4252 | 1969.5079 | 1708.9835 | 2060.6577 | 2829.7599 | 2309.1653 | 2309.1653 | 2309.1653 | 2309.1653 | 2309.1653 | 2309.1653 | 2309.1653 | 2309.1653 | 2309.1653 | 2309.1653 | 2309.1653 | 2309.1653 | 2309.1653 | 2309.1653 | 2309.1653 | 2309.1653
70% | [7 empty] | 3.4379 | 133.5638 | 272.0098 | 431.8215 | 164.8836 | 489.6671 | 1193.5489 | 654.2363 | 654.2363 | 654.2363 | 654.2363 | 654.2363 | 654.2363 | 654.2363 | 654.2363 | 654.2363 | 654.2363 | 654.2363 | 654.2363 | 654.2363 | 654.2363 | 654.2363 | 654.2363 | [7 empty] | 73.4213 | 219.8269 | 697.566 | 2433.4635 | 1002.3928 | 722.4739 | 1100.3282 | 1926.6855 | 1367.3357 | 1367.3357 | 1367.3357 | 1367.3357 | 1367.3357 | 1367.3357 | 1367.3357 | 1367.3357 | 1367.3357 | 1367.3357 | 1367.3357 | 1367.3357 | 1367.3357 | 1367.3357 | 1367.3357 | 1367.3357
65% | FY38: 138.0019; FY39: 0.607; FY40: 0.607; FY41: 0.607; FY42: 0.607; FY43: 0.607; FY44: 0.607; FY45: 0.607; FY46: 0.607; FY47: 0.607; FY48: 0.607; FY49: 0.607; FY50: 0.607; FY51: 0.607; FY52: 0.607; FY53: 0.607; FY54: 0.607 | [9 empty] | 2.7969 | 1216.8668 | 62.358 | 4.774 | 97.5063 | 684.2805 | 231.4677 | 231.4677 | 231.4677 | 231.4677 | 231.4677 | 231.4677 | 231.4677 | 231.4677 | 231.4677 | 231.4677 | 231.4677 | 231.4677 | 231.4677 | 231.4677 | 231.4677 | 231.4677
60% | [40 empty] | 77.6441
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 306.4572 | 1278.2542 | 1538.6669 | 1760.5324 | 2183.4175 | 3339.858 | 4255.0255 | 5579.7822 | 6338.312 | 7043.6462 | 5771.5678 | 7274.3439 | 9968.1685 | 7886.0948 | 7886.0948 | 7886.0948 | 7886.0948 | 7886.0948 | 7886.0948 | 7886.0948 | 7886.0948 | 7886.0948 | 7886.0948 | 7886.0948 | 7886.0948 | 7886.0948 | 7886.0948 | 7886.0948 | 7886.0948 | E @ R (MWh) | 0 | 833.5401 | 2506.4849 | 2860.3759 | 3097.9173 | 3652.8965 | 5148.2859 | 6075.8653 | 8044.5252 | 15595.6201 | 9203.2451 | 8136.3162 | 9591.5333 | 13158.0259 | 10688.2832 | 10688.2832 | 10688.2832 | 10688.2832 | 10688.2832 | 10688.2832 | 10688.2832 | 10688.2832 | 10688.2832 | 10688.2832 | 10688.2832 | 10688.2832 | 10688.2832 | 10688.2832 | 10688.2832 | 10688.2832
Option 8 Winter POE50 W E @ R (MWh) N 1 | 0 | 214.5201 | 894.7779 | 1077.0669 | 1232.3727 | 1528.3922 | 2337.9006 | 2978.5179 | 3905.8475 | 4436.8184 | 4930.5523 | 4040.0974 | 5092.0407 | 6977.718 | 5520.2664 | 5520.2664 | 5520.2664 | 5520.2664 | 5520.2664 | 5520.2664 | 5520.2664 | 5520.2664 | 5520.2664 | 5520.2664 | 5520.2664 | 5520.2664 | 5520.2664 | 5520.2664 | 5520.2664 | 5520.2664 | Option 8 Winter POE10 W E @ R (MWh) N 1 | 0 | 250.062 | 751.9455 | 858.1128 | 929.3752 | 1095.8689 | 1544.4858 | 1822.7596 | 2413.3575 | 4678.686 | 2760.9735 | 2440.8949 | 2877.46 | 3947.4078 | 3206.485 | 3206.485 | 3206.485 | 3206.485 | 3206.485 | 3206.485 | 3206.485 | 3206.485 | 3206.485 | 3206.485 | 3206.485 | 3206.485 | 3206.485 | 3206.485 | 3206.485 | 3206.485
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 8.924 | 31.6709 | 37.6273 | 37.273 | 37.3028 | 37.916 | 39.5304 | 40.6128 | 41.6716 | 42.9095 | 44.0577 | 45.1715 | 45.3005 | 46.6002 | 45.6187 | 45.6187 | 45.6187 | 45.6187 | 45.6187 | 45.6187 | 45.6187 | 45.6187 | 45.6187 | 45.6187 | 45.6187 | 45.6187 | 45.6187 | 45.6187 | 45.6187 | 45.6187
98% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4.0751 | 15.3343 | 18.2825 | 18.1072 | 18.1219 | 18.4254 | 19.2245 | 19.7603 | 20.2843 | 20.897 | 21.4654 | 22.0167 | 22.0806 | 22.7239 | 22.238 | 22.238 | 22.238 | 22.238 | 22.238 | 22.238 | 22.238 | 22.238 | 22.238 | 22.238 | 22.238 | 22.238 | 22.238 | 22.238 | 22.238 | 22.238
97% |  | 5.4588 | 6.9736 | 6.9303 | 6.9298 | 7.103 | 7.2931 | 7.6829 | 7.9629 | 8.1151 | 8.2819 | 8.4343 | 8.7091 | 9.05 | 9.027 | 9.027 | 9.027 | 9.027 | 9.027 | 9.027 | 9.027 | 9.027 | 9.027 | 9.027 | 9.027 | 9.027 | 9.027 | 9.027 | 9.027 | 9.027 |  | 7.3764 | 29.6661 | 35.5027 | 35.1556 | 35.1847 | 35.7856 | 37.3676 | 38.4283 | 39.4657 | 40.6787 | 41.8039 | 42.8953 | 43.0218 | 44.2953 | 43.3335 | 43.3335 | 43.3335 | 43.3335 | 43.3335 | 43.3335 | 43.3335 | 43.3335 | 43.3335 | 43.3335 | 43.3335 | 43.3335 | 43.3335 | 43.3335 | 43.3335 | 43.3335
95% |  | 25.5649 | 33.0227 | 32.8093 | 32.8067 | 33.6597 | 34.5953 | 36.5142 | 37.8928 | 38.6423 | 39.4634 | 40.2137 | 41.5666 | 43.2448 | 43.1314 | 43.1314 | 43.1314 | 43.1314 | 43.1314 | 43.1314 | 43.1314 | 43.1314 | 43.1314 | 43.1314 | 43.1314 | 43.1314 | 43.1314 | 43.1314 | 43.1314 | 43.1314 |  | 9.3236 | 42.2437 | 50.864 | 50.3513 | 50.3943 | 51.2818 | 53.6182 | 55.1847 | 56.717 | 58.5085 | 60.1702 | 61.7822 | 61.969 | 63.8499 | 62.4294 | 62.4294 | 62.4294 | 62.4294 | 62.4294 | 62.4294 | 62.4294 | 62.4294 | 62.4294 | 62.4294 | 62.4294 | 62.4294 | 62.4294 | 62.4294 | 62.4294 | 62.4294
90% |  | 38.7554 | 51.6899 | 51.3198 | 51.3153 | 52.7947 | 54.4175 | 57.7455 | 60.1366 | 61.4365 | 62.8605 | 64.1618 | 66.5082 | 69.4189 | 69.2222 | 69.2222 | 69.2222 | 69.2222 | 69.2222 | 69.2222 | 69.2222 | 69.2222 | 69.2222 | 69.2222 | 69.2222 | 69.2222 | 69.2222 | 69.2222 | 69.2222 | 69.2222 |  | 23.6749 | 166.4146 | 203.7914 | 201.5685 | 201.7552 | 205.6032 | 215.7337 | 222.5261 | 229.1699 | 236.9378 | 244.1429 | 251.1324 | 251.9421 | 260.0977 | 253.9385 | 253.9385 | 253.9385 | 253.9385 | 253.9385 | 253.9385 | 253.9385 | 253.9385 | 253.9385 | 253.9385 | 253.9385 | 253.9385 | 253.9385 | 253.9385 | 253.9385 | 253.9385
85% |  | 85.1452 | 121.8514 | 120.801 | 120.7884 | 124.9866 | 129.5917 | 139.0363 | 145.8216 | 149.5106 | 153.5518 | 157.2446 | 163.9032 | 172.1633 | 171.605 | 171.605 | 171.605 | 171.605 | 171.605 | 171.605 | 171.605 | 171.605 | 171.605 | 171.605 | 171.605 | 171.605 | 171.605 | 171.605 | 171.605 | 171.605 |  | 2.1581 | 132.583 | 167.9395 | 165.8367 | 166.0133 | 169.6533 | 179.2362 | 185.6615 | 191.9461 | 199.2941 | 206.1098 | 212.7215 | 213.4874 | 221.2021 | 215.3759 | 215.3759 | 215.3759 | 215.3759 | 215.3759 | 215.3759 | 215.3759 | 215.3759 | 215.3759 | 215.3759 | 215.3759 | 215.3759 | 215.3759 | 215.3759 | 215.3759 | 215.3759
80% |  | 80.0361 | 131.3082 | 129.841 | 129.8234 | 135.6876 | 142.1201 | 155.3125 | 164.7904 | 169.9433 | 175.5881 | 180.7464 | 190.0472 | 201.5852 | 200.8054 | 200.8054 | 200.8054 | 200.8054 | 200.8054 | 200.8054 | 200.8054 | 200.8054 | 200.8054 | 200.8054 | 200.8054 | 200.8054 | 200.8054 | 200.8054 | 200.8054 | 200.8054 |  |  | 73.1492 | 97.8426 | 96.374 | 96.4973 | 99.0396 | 105.7324 | 110.2199 | 114.6092 | 119.7411 | 124.5013 | 129.1189 | 129.6539 | 135.0419 | 130.9728 | 130.9728 | 130.9728 | 130.9728 | 130.9728 | 130.9728 | 130.9728 | 130.9728 | 130.9728 | 130.9728 | 130.9728 | 130.9728 | 130.9728 | 130.9728 | 130.9728 | 130.9728
75% |  | 94.1589 | 227.8159 | 223.9912 | 223.9454 | 239.2321 | 256.0006 | 290.3908 | 315.098 | 328.5306 | 343.2457 | 356.6924 | 380.938 | 411.0152 | 408.9825 | 408.9825 | 408.9825 | 408.9825 | 408.9825 | 408.9825 | 408.9825 | 408.9825 | 408.9825 | 408.9825 | 408.9825 | 408.9825 | 408.9825 | 408.9825 | 408.9825 | 408.9825 |  |  | 91.3687 | 135.4427 | 132.8215 | 133.0415 | 137.5791 | 149.5248 | 157.5342 | 165.3684 | 174.5281 | 183.0243 | 191.2662 | 192.221 | 201.8378 | 194.575 | 194.575 | 194.575 | 194.575 | 194.575 | 194.575 | 194.575 | 194.575 | 194.575 | 194.575 | 194.575 | 194.575 | 194.575 | 194.575 | 194.575 | 194.575
70% |  | 6.5776 | 168.5277 | 161.9198 | 161.8408 | 188.2515 | 217.2224 | 276.6382 | 319.3247 | 342.5321 | 367.9553 | 391.1871 | 433.0761 | 485.0404 | 481.5284 | 481.5284 | 481.5284 | 481.5284 | 481.5284 | 481.5284 | 481.5284 | 481.5284 | 481.5284 | 481.5284 | 481.5284 | 481.5284 | 481.5284 | 481.5284 | 481.5284 | 481.5284 |  |  | 85.2049 | 165.4959 | 160.7208 | 161.1217 | 169.3879 | 191.1497 | 205.7408 | 220.0126 | 236.6991 | 252.1769 | 267.1913 | 268.9307 | 286.45 | 273.2191 | 273.2191 | 273.2191 | 273.2191 | 273.2191 | 273.2191 | 273.2191 | 273.2191 | 273.2191 | 273.2191 | 273.2191 | 273.2191 | 273.2191 | 273.2191 | 273.2191 | 273.2191
65% |  |  | 9.6236 | 6.9591 | 6.9298 | 20.0951 | 42.2143 | 111.9423 | 181.5617 | 226.0382 | 279.9918 | 333.9879 | 438.672 | 569.1816 | 560.3612 | 560.3612 | 560.3612 | 560.3612 | 560.3612 | 560.3612 | 560.3612 | 560.3612 | 560.3612 | 560.3612 | 560.3612 | 560.3612 | 560.3612 | 560.3612 | 560.3612 | 560.3612 |  |  | 10.9945 | 90.8581 | 84.8503 | 85.3547 | 95.7548 | 123.1346 | 141.4924 | 159.4485 | 180.4428 | 199.9162 | 218.8067 | 220.9952 | 243.0371 | 226.3906 | 226.3906 | 226.3906 | 226.3906 | 226.3906 | 226.3906 | 226.3906 | 226.3906 | 226.3906 | 226.3906 | 226.3906 | 226.3906 | 226.3906 | 226.3906 | 226.3906 | 226.3906
60% | [12 empty] | 5.9059 | 42.5222 | 39.014 | 39.014 | 39.014 | 39.014 | 39.014 | 39.014 | 39.014 | 39.014 | 39.014 | 39.014 | 39.014 | 39.014 | 39.014 | 39.014 | 39.014 | 39.014 |  |  |  | 3.8091 | 2.2281 | 2.3448 | 5.4041 | 19.2874 | 33.1836 | 50.2166 | 74.3153 | 100.576 | 129.3594 | 132.7839 | 167.2756 | 141.2268 | 141.2268 | 141.2268 | 141.2268 | 141.2268 | 141.2268 | 141.2268 | 141.2268 | 141.2268 | 141.2268 | 141.2268 | 141.2268 | 141.2268 | 141.2268 | 141.2268 | 141.2268
55% | [42 empty] | 0.36348 | 0.67093 | 8.8993 | 1.8255 | 1.8255 | 1.8255 | 1.8255 | 1.8255 | 1.8255 | 1.8255 | 1.8255 | 1.8255 | 1.8255 | 1.8255 | 1.8255 | 1.8255 | 1.8255 | 1.8255 | 1.8255
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 335.6968 | 750.8128 | 734.5714 | 734.3797 | 801.8103 | 883.4549 | 1075.2627 | 1232.5888 | 1324.7487 | 1430.9386 | 1532.6682 | 1729.3262 | 2003.2214 | 1983.6771 | 1983.6771 | 1983.6771 | 1983.6771 | 1983.6771 | 1983.6771 | 1983.6771 | 1983.6771 | 1983.6771 | 1983.6771 | 1983.6771 | 1983.6771 | 1983.6771 | 1983.6771 | 1983.6771 | 1983.6771 | E @ R (MWh) | 55.5322 | 678.63 | 1007.4559 | 985.2871 | 987.1322 | 1025.8309 | 1133.5396 | 1210.3445 | 1288.9099 | 1384.9521 | 1477.9447 | 1571.8256 | 1583.0571 | 1701.3108 | 1611.1437 | 1611.1437 | 1611.1437 | 1611.1437 | 1611.1437 | 1611.1437 | 1611.1437 | 1611.1437 | 1611.1437 | 1611.1437 | 1611.1437 | 1611.1437 | 1611.1437 | 1611.1437 | 1611.1437 | 1611.1437
Option 8 Summer POE50 W E @ R (MWh) N 1 | 0 | 234.9878 | 525.569 | 514.2 | 514.0658 | 561.2672 | 618.4185 | 752.6839 | 862.8122 | 927.3241 | 1001.657 | 1072.8678 | 1210.5283 | 1402.255 | 1388.5739 | 1388.5739 | 1388.5739 | 1388.5739 | 1388.5739 | 1388.5739 | 1388.5739 | 1388.5739 | 1388.5739 | 1388.5739 | 1388.5739 | 1388.5739 | 1388.5739 | 1388.5739 | 1388.5739 | 1388.5739 | Option 8 Summer POE10 W E @ R (MWh) N 1 | 16.6597 | 203.589 | 302.2368 | 295.5861 | 296.1396 | 307.7493 | 340.0619 | 363.1034 | 386.673 | 415.4856 | 443.3834 | 471.5477 | 474.9171 | 510.3932 | 483.3431 | 483.3431 | 483.3431 | 483.3431 | 483.3431 | 483.3431 | 483.3431 | 483.3431 | 483.3431 | 483.3431 | 483.3431 | 483.3431 | 483.3431 | 483.3431 | 483.3431 | 483.3431

## E@R N-2
Option 1 - Do Nothing / Base Case
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | 59.6718 | 82.8348 | 88.8563 | 89.8828 | 90.6833 | 92.0616 | 95.1975 | 97.2967 | 99.9559 | 101.3362 | 102.5505 | 100.3131 | 102.9353 | 107.0576 | 103.9293 | 103.9293 | 103.9293 | 103.9293 | 103.9293 | 103.9293 | 103.9293 | 103.9293 | 103.9293 | 103.9293 | 103.9293 | 103.9293 | 103.9293 | 103.9293 | 103.9293 | 103.9293 |  | 63.8857 | 86.7566 | 93.0131 | 93.9812 | 94.5959 | 95.9444 | 99.1293 | 100.8681 | 104.1807 | 114.2499 | 105.9488 | 104.3251 | 106.5169 | 111.3103 | 108.0657 | 108.0657 | 108.0657 | 108.0657 | 108.0657 | 108.0657 | 108.0657 | 108.0657 | 108.0657 | 108.0657 | 108.0657 | 108.0657 | 108.0657 | 108.0657 | 108.0657 | 108.0657
98% | 70.8865 | 98.4027 | 105.556 | 106.7753 | 107.7263 | 109.3637 | 113.0889 | 115.5826 | 118.7416 | 120.3813 | 121.8238 | 119.1659 | 122.2809 | 127.178 | 123.4618 | 123.4618 | 123.4618 | 123.4618 | 123.4618 | 123.4618 | 123.4618 | 123.4618 | 123.4618 | 123.4618 | 123.4618 | 123.4618 | 123.4618 | 123.4618 | 123.4618 | 123.4618 |  | 75.8924 | 103.0616 | 110.494 | 111.644 | 112.3742 | 113.9761 | 117.7596 | 119.8253 | 123.7603 | 135.7219 | 125.8608 | 123.932 | 126.5357 | 132.2299 | 128.3755 | 128.3755 | 128.3755 | 128.3755 | 128.3755 | 128.3755 | 128.3755 | 128.3755 | 128.3755 | 128.3755 | 128.3755 | 128.3755 | 128.3755 | 128.3755 | 128.3755 | 128.3755
97% | 140.3338 | 194.8074 | 208.9687 | 211.3826 | 213.2652 | 216.5068 | 223.8816 | 228.8183 | 235.0721 | 238.3182 | 241.174 | 235.9121 | 242.0789 | 251.7738 | 244.4167 | 244.4167 | 244.4167 | 244.4167 | 244.4167 | 244.4167 | 244.4167 | 244.4167 | 244.4167 | 244.4167 | 244.4167 | 244.4167 | 244.4167 | 244.4167 | 244.4167 | 244.4167 |  | 150.2438 | 204.0305 | 218.7445 | 221.0211 | 222.4667 | 225.638 | 233.1281 | 237.2175 | 245.0078 | 268.6881 | 249.1661 | 245.3476 | 250.5021 | 261.7749 | 254.1445 | 254.1445 | 254.1445 | 254.1445 | 254.1445 | 254.1445 | 254.1445 | 254.1445 | 254.1445 | 254.1445 | 254.1445 | 254.1445 | 254.1445 | 254.1445 | 254.1445 | 254.1445
95% | 414.5243 | 575.4311 | 617.2612 | 624.3915 | 629.9527 | 639.5277 | 661.3119 | 675.8939 | 694.3669 | 703.9554 | 712.391 | 696.8482 | 715.0638 | 743.7009 | 721.9694 | 721.9694 | 721.9694 | 721.9694 | 721.9694 | 721.9694 | 721.9694 | 721.9694 | 721.9694 | 721.9694 | 721.9694 | 721.9694 | 721.9694 | 721.9694 | 721.9694 | 721.9694 |  | 443.7972 | 602.6746 | 646.1375 | 652.8624 | 657.1324 | 666.4999 | 688.6245 | 700.704 | 723.7153 | 793.6633 | 735.9983 | 724.719 | 739.9446 | 773.2427 | 750.7037 | 750.7037 | 750.7037 | 750.7037 | 750.7037 | 750.7037 | 750.7037 | 750.7037 | 750.7037 | 750.7037 | 750.7037 | 750.7037 | 750.7037 | 750.7037 | 750.7037 | 750.7037
90% | 2285.5212 | 3172.6969 | 3403.3313 | 3442.6449 | 3473.3067 | 3526.0998 | 3646.209 | 3726.6085 | 3828.4608 | 3881.3281 | 3927.8385 | 3842.1418 | 3942.5756 | 4100.4692 | 3980.6499 | 3980.6499 | 3980.6499 | 3980.6499 | 3980.6499 | 3980.6499 | 3980.6499 | 3980.6499 | 3980.6499 | 3980.6499 | 3980.6499 | 3980.6499 | 3980.6499 | 3980.6499 | 3980.6499 | 3980.6499 |  | 2446.9201 | 3322.9067 | 3562.5435 | 3599.622 | 3623.165 | 3674.8134 | 3796.7998 | 3863.4014 | 3990.2765 | 4375.9415 | 4058 | 3995.8103 | 4079.7583 | 4263.3504 | 4139.0795 | 4139.0795 | 4139.0795 | 4139.0795 | 4139.0795 | 4139.0795 | 4139.0795 | 4139.0795 | 4139.0795 | 4139.0795 | 4139.0795 | 4139.0795 | 4139.0795 | 4139.0795 | 4139.0795 | 4139.0795
85% | 5583.3646 | 7750.6712 | 8314.0946 | 8410.1348 | 8485.0395 | 8614.0092 | 8907.4274 | 9103.8375 | 9352.6555 | 9481.8066 | 9595.4282 | 9386.0773 | 9631.4298 | 10017.1525 | 9724.4425 | 9724.4425 | 9724.4425 | 9724.4425 | 9724.4425 | 9724.4425 | 9724.4425 | 9724.4425 | 9724.4425 | 9724.4425 | 9724.4425 | 9724.4425 | 9724.4425 | 9724.4425 | 9724.4425 | 9724.4425 |  | 5977.6505 | 8117.623 | 8703.0385 | 8793.6186 | 8851.1326 | 8977.3059 | 9275.3098 | 9438.0128 | 9747.9596 | 10690.1116 | 9913.4032 | 9761.4782 | 9966.5573 | 10415.0597 | 10111.4747 | 10111.4747 | 10111.4747 | 10111.4747 | 10111.4747 | 10111.4747 | 10111.4747 | 10111.4747 | 10111.4747 | 10111.4747 | 10111.4747 | 10111.4747 | 10111.4747 | 10111.4747 | 10111.4747 | 10111.4747
80% | 8678.2039 | 12046.8408 | 12922.5678 | 13071.8427 | 13188.2668 | 13388.724 | 13844.7828 | 14150.0624 | 14536.7992 | 14737.5384 | 14914.14 | 14588.7467 | 14970.0973 | 15569.6246 | 15114.6665 | 15114.6665 | 15114.6665 | 15114.6665 | 15114.6665 | 15114.6665 | 15114.6665 | 15114.6665 | 15114.6665 | 15114.6665 | 15114.6665 | 15114.6665 | 15114.6665 | 15114.6665 | 15114.6665 | 15114.6665 |  | 9291.041 | 12617.1926 | 13527.1019 | 13667.8902 | 13757.2841 | 13953.3947 | 14416.5812 | 14669.4699 | 15151.219 | 16615.6026 | 15408.3675 | 15172.231 | 15490.9847 | 16188.0904 | 15716.2292 | 15716.2292 | 15716.2292 | 15716.2292 | 15716.2292 | 15716.2292 | 15716.2292 | 15716.2292 | 15716.2292 | 15716.2292 | 15716.2292 | 15716.2292 | 15716.2292 | 15716.2292 | 15716.2292 | 15716.2292
75% | 9574.4808 | 13291.0275 | 14257.1987 | 14421.8907 | 14550.339 | 14771.4991 | 15274.6593 | 15611.4679 | 16038.1465 | 16259.6179 | 16454.4587 | 16095.4591 | 16516.1952 | 17177.6412 | 16675.6955 | 16675.6955 | 16675.6955 | 16675.6955 | 16675.6955 | 16675.6955 | 16675.6955 | 16675.6955 | 16675.6955 | 16675.6955 | 16675.6955 | 16675.6955 | 16675.6955 | 16675.6955 | 16675.6955 | 16675.6955 |  | 10250.6112 | 13920.2847 | 14924.1686 | 15079.4974 | 15178.1238 | 15394.4886 | 15905.5125 | 16184.5193 | 16716.023 | 18331.6468 | 16999.7296 | 16739.2052 | 17090.8794 | 17859.9816 | 17339.387 | 17339.387 | 17339.387 | 17339.387 | 17339.387 | 17339.387 | 17339.387 | 17339.387 | 17339.387 | 17339.387 | 17339.387 | 17339.387 | 17339.387 | 17339.387 | 17339.387 | 17339.387
70% | 10287.2444 | 14280.4661 | 15318.563 | 15495.5153 | 15633.5258 | 15871.15 | 16411.7675 | 16773.6495 | 17232.0919 | 17470.0505 | 17679.396 | 17293.671 | 17745.7284 | 18456.4151 | 17917.1025 | 17917.1025 | 17917.1025 | 17917.1025 | 17917.1025 | 17917.1025 | 17917.1025 | 17917.1025 | 17917.1025 | 17917.1025 | 17917.1025 | 17917.1025 | 17917.1025 | 17917.1025 | 17917.1025 | 17917.1025 |  | 11013.7087 | 14956.5677 | 16035.1849 | 16202.077 | 16308.0455 | 16540.5174 | 17089.584 | 17389.3613 | 17960.4323 | 19696.3297 | 18265.2591 | 17985.3402 | 18363.1944 | 19189.5518 | 18630.202 | 18630.202 | 18630.202 | 18630.202 | 18630.202 | 18630.202 | 18630.202 | 18630.202 | 18630.202 | 18630.202 | 18630.202 | 18630.202 | 18630.202 | 18630.202 | 18630.202 | 18630.202
65% | 10840.7831 | 15048.8731 | 16142.8282 | 16329.302 | 16474.7386 | 16725.149 | 17294.8562 | 17676.2104 | 18159.3208 | 18410.0835 | 18630.6936 | 18224.2134 | 18700.5952 | 19449.5227 | 18881.1907 | 18881.1907 | 18881.1907 | 18881.1907 | 18881.1907 | 18881.1907 | 18881.1907 | 18881.1907 | 18881.1907 | 18881.1907 | 18881.1907 | 18881.1907 | 18881.1907 | 18881.1907 | 18881.1907 | 18881.1907 |  | 11606.3372 | 15761.3546 | 16898.0103 | 17073.8826 | 17185.553 | 17430.5339 | 18009.1448 | 18325.0525 | 18926.8519 | 20756.155 | 19248.0809 | 18953.1 | 19351.286 | 20222.1082 | 19632.6608 | 19632.6608 | 19632.6608 | 19632.6608 | 19632.6608 | 19632.6608 | 19632.6608 | 19632.6608 | 19632.6608 | 19632.6608 | 19632.6608 | 19632.6608 | 19632.6608 | 19632.6608 | 19632.6608 | 19632.6608
60% | 11934.3669 | 16566.9557 | 17771.2656 | 17976.5503 | 18136.658 | 18412.329 | 19039.5064 | 19459.3305 | 19991.1755 | 20267.2344 | 20510.0989 | 20062.6142 | 20587.052 | 21411.5289 | 20785.8653 | 20785.8653 | 20785.8653 | 20785.8653 | 20785.8653 | 20785.8653 | 20785.8653 | 20785.8653 | 20785.8653 | 20785.8653 | 20785.8653 | 20785.8653 | 20785.8653 | 20785.8653 | 20785.8653 | 20785.8653 |  | 12777.1477 | 17351.3101 | 18602.628 | 18796.2417 | 18919.1771 | 19188.8708 | 19825.8502 | 20173.6257 | 20836.1327 | 22849.9701 | 21189.7663 | 20865.0287 | 21303.3824 | 22262.0503 | 21613.1413 | 21613.1413 | 21613.1413 | 21613.1413 | 21613.1413 | 21613.1413 | 21613.1413 | 21613.1413 | 21613.1413 | 21613.1413 | 21613.1413 | 21613.1413 | 21613.1413 | 21613.1413 | 21613.1413 | 21613.1413
55% | 13276.2336 | 18429.6976 | 19769.4166 | 19997.783 | 20175.8928 | 20482.5595 | 21180.255 | 21647.2828 | 22238.927 | 22546.0252 | 22816.1967 | 22318.3981 | 22901.8021 | 23818.981 | 23122.9695 | 23122.9695 | 23122.9695 | 23122.9695 | 23122.9695 | 23122.9695 | 23122.9695 | 23122.9695 | 23122.9695 | 23122.9695 | 23122.9695 | 23122.9695 | 23122.9695 | 23122.9695 | 23122.9695 | 23122.9695 |  | 14213.7742 | 19302.2426 | 20694.2551 | 20909.6382 | 21046.3962 | 21346.4135 | 22055.013 | 22441.8914 | 23178.8888 | 25419.1564 | 23572.284 | 23211.0338 | 23698.6747 | 24765.1326 | 24043.2621 | 24043.2621 | 24043.2621 | 24043.2621 | 24043.2621 | 24043.2621 | 24043.2621 | 24043.2621 | 24043.2621 | 24043.2621 | 24043.2621 | 24043.2621 | 24043.2621 | 24043.2621 | 24043.2621 | 24043.2621
50% | 13456.7484 | 18680.2832 | 20038.2182 | 20269.6896 | 20450.2212 | 20761.0575 | 21468.2395 | 21941.6174 | 22541.3061 | 22852.5798 | 23126.4248 | 22621.8577 | 23213.1942 | 24142.8438 | 23437.3688 | 23437.3688 | 23437.3688 | 23437.3688 | 23437.3688 | 23437.3688 | 23437.3688 | 23437.3688 | 23437.3688 | 23437.3688 | 23437.3688 | 23437.3688 | 23437.3688 | 23437.3688 | 23437.3688 | 23437.3688 |  | 14407.0366 | 19564.692 | 20975.6315 | 21193.9432 | 21332.5606 | 21636.6572 | 22354.8915 | 22747.0302 | 23494.0484 | 25764.7766 | 23892.7925 | 23526.6304 | 24020.9018 | 25101.8601 | 24370.1745 | 24370.1745 | 24370.1745 | 24370.1745 | 24370.1745 | 24370.1745 | 24370.1745 | 24370.1745 | 24370.1745 | 24370.1745 | 24370.1745 | 24370.1745 | 24370.1745 | 24370.1745 | 24370.1745 | 24370.1745
45% | 10386.1977 | 14417.8303 | 15465.9127 | 15644.5671 | 15783.9051 | 16023.8151 | 16569.6328 | 16934.9957 | 17397.8478 | 17638.0954 | 17849.4547 | 17460.0193 | 17916.4251 | 18633.9479 | 18089.4477 | 18089.4477 | 18089.4477 | 18089.4477 | 18089.4477 | 18089.4477 | 18089.4477 | 18089.4477 | 18089.4477 | 18089.4477 | 18089.4477 | 18089.4477 | 18089.4477 | 18089.4477 | 18089.4477 | 18089.4477 |  | 11119.6499 | 15100.4354 | 16189.4278 | 16357.9252 | 16464.913 | 16699.6211 | 17253.9692 | 17556.63 | 18133.1942 | 19885.7893 | 18440.9531 | 18158.3417 | 18539.8305 | 19374.1366 | 18809.4064 | 18809.4064 | 18809.4064 | 18809.4064 | 18809.4064 | 18809.4064 | 18809.4064 | 18809.4064 | 18809.4064 | 18809.4064 | 18809.4064 | 18809.4064 | 18809.4064 | 18809.4064 | 18809.4064 | 18809.4064
40% | 5102.6915 | 7083.4142 | 7598.3323 | 7686.1044 | 7754.5606 | 7872.4272 | 8140.5849 | 8320.0861 | 8547.4832 | 8665.5158 | 8769.3556 | 8578.0278 | 8802.2579 | 9154.7736 | 8887.2631 | 8887.2631 | 8887.2631 | 8887.2631 | 8887.2631 | 8887.2631 | 8887.2631 | 8887.2631 | 8887.2631 | 8887.2631 | 8887.2631 | 8887.2631 | 8887.2631 | 8887.2631 | 8887.2631 | 8887.2631 |  | 5463.0332 | 7418.775 | 7953.792 | 8036.574 | 8089.1366 | 8204.4476 | 8476.7963 | 8625.4922 | 8908.7555 | 9769.7975 | 9059.9561 | 8921.1104 | 9108.5341 | 9518.4249 | 9240.9755 | 9240.9755 | 9240.9755 | 9240.9755 | 9240.9755 | 9240.9755 | 9240.9755 | 9240.9755 | 9240.9755 | 9240.9755 | 9240.9755 | 9240.9755 | 9240.9755 | 9240.9755 | 9240.9755 | 9240.9755
35% | 1907.0998 | 2647.3829 | 2839.8304 | 2872.6347 | 2898.2197 | 2942.2717 | 3042.494 | 3109.5815 | 3194.5697 | 3238.6837 | 3277.4932 | 3205.9856 | 3289.7902 | 3421.5408 | 3321.5604 | 3321.5604 | 3321.5604 | 3321.5604 | 3321.5604 | 3321.5604 | 3321.5604 | 3321.5604 | 3321.5604 | 3321.5604 | 3321.5604 | 3321.5604 | 3321.5604 | 3321.5604 | 3321.5604 | 3321.5604 |  | 2041.7754 | 2772.7219 | 2972.6813 | 3003.6205 | 3023.2655 | 3066.3623 | 3168.1509 | 3223.7251 | 3329.5931 | 3651.4023 | 3386.1034 | 3334.2106 | 3404.2591 | 3557.4533 | 3453.7583 | 3453.7583 | 3453.7583 | 3453.7583 | 3453.7583 | 3453.7583 | 3453.7583 | 3453.7583 | 3453.7583 | 3453.7583 | 3453.7583 | 3453.7583 | 3453.7583 | 3453.7583 | 3453.7583 | 3453.7583
30% | 951.1511 | 1320.3614 | 1416.3431 | 1432.704 | 1445.4643 | 1467.4349 | 1517.42 | 1550.8793 | 1593.2665 | 1615.268 | 1634.624 | 1598.9601 | 1640.757 | 1706.4666 | 1656.6021 | 1656.6021 | 1656.6021 | 1656.6021 | 1656.6021 | 1656.6021 | 1656.6021 | 1656.6021 | 1656.6021 | 1656.6021 | 1656.6021 | 1656.6021 | 1656.6021 | 1656.6021 | 1656.6021 | 1656.6021 |  | 1018.3194 | 1382.8733 | 1482.6014 | 1498.0321 | 1507.8299 | 1529.3241 | 1580.0904 | 1607.8076 | 1660.6084 | 1821.1082 | 1688.7924 | 1662.9113 | 1697.8475 | 1774.2519 | 1722.5348 | 1722.5348 | 1722.5348 | 1722.5348 | 1722.5348 | 1722.5348 | 1722.5348 | 1722.5348 | 1722.5348 | 1722.5348 | 1722.5348 | 1722.5348 | 1722.5348 | 1722.5348 | 1722.5348 | 1722.5348
25% | 560.7353 | 778.3972 | 834.9816 | 844.6269 | 852.1495 | 865.1019 | 894.5698 | 914.2952 | 939.2839 | 952.2545 | 963.6655 | 942.6404 | 967.2811 | 1006.0191 | 976.6223 | 976.6223 | 976.6223 | 976.6223 | 976.6223 | 976.6223 | 976.6223 | 976.6223 | 976.6223 | 976.6223 | 976.6223 | 976.6223 | 976.6223 | 976.6223 | 976.6223 | 976.6223 |  | 600.3333 | 815.25 | 874.0431 | 883.14 | 888.9161 | 901.5876 | 931.5161 | 947.8563 | 978.9841 | 1073.6041 | 995.5996 | 980.3418 | 1000.9378 | 1045.9808 | 1015.4918 | 1015.4918 | 1015.4918 | 1015.4918 | 1015.4918 | 1015.4918 | 1015.4918 | 1015.4918 | 1015.4918 | 1015.4918 | 1015.4918 | 1015.4918 | 1015.4918 | 1015.4918 | 1015.4918 | 1015.4918
20% | 283.3663 | 393.3611 | 421.9559 | 426.8302 | 430.6317 | 437.1772 | 452.0687 | 462.0369 | 474.6648 | 481.2195 | 486.986 | 476.3611 | 488.8132 | 508.3893 | 493.5337 | 493.5337 | 493.5337 | 493.5337 | 493.5337 | 493.5337 | 493.5337 | 493.5337 | 493.5337 | 493.5337 | 493.5337 | 493.5337 | 493.5337 | 493.5337 | 493.5337 | 493.5337 |  | 303.377 | 411.9846 | 441.6956 | 446.2927 | 449.2116 | 455.6151 | 470.7394 | 478.9969 | 494.7273 | 542.5433 | 503.1238 | 495.4134 | 505.8215 | 528.5839 | 513.1763 | 513.1763 | 513.1763 | 513.1763 | 513.1763 | 513.1763 | 513.1763 | 513.1763 | 513.1763 | 513.1763 | 513.1763 | 513.1763 | 513.1763 | 513.1763 | 513.1763 | 513.1763
15% | 115.4455 | 160.2582 | 171.908 | 173.8938 | 175.4425 | 178.1092 | 184.1761 | 188.2372 | 193.382 | 196.0524 | 198.4017 | 194.073 | 199.1461 | 207.1216 | 201.0693 | 201.0693 | 201.0693 | 201.0693 | 201.0693 | 201.0693 | 201.0693 | 201.0693 | 201.0693 | 201.0693 | 201.0693 | 201.0693 | 201.0693 | 201.0693 | 201.0693 | 201.0693 |  | 123.598 | 167.8456 | 179.95 | 181.8229 | 183.0121 | 185.621 | 191.7827 | 195.1469 | 201.5556 | 221.0361 | 204.9764 | 201.8351 | 206.0754 | 215.349 | 209.0718 | 209.0718 | 209.0718 | 209.0718 | 209.0718 | 209.0718 | 209.0718 | 209.0718 | 209.0718 | 209.0718 | 209.0718 | 209.0718 | 209.0718 | 209.0718 | 209.0718 | 209.0718
10% | 46.4781 | 64.5196 | 69.2097 | 70.0092 | 70.6327 | 71.7063 | 74.1488 | 75.7838 | 77.8551 | 78.9302 | 79.876 | 78.1333 | 80.1757 | 83.3866 | 80.95 | 80.95 | 80.95 | 80.95 | 80.95 | 80.95 | 80.95 | 80.95 | 80.95 | 80.95 | 80.95 | 80.95 | 80.95 | 80.95 | 80.95 | 80.95 |  | 49.7602 | 67.5742 | 72.4474 | 73.2014 | 73.6802 | 74.7305 | 77.2112 | 78.5656 | 81.1457 | 88.9886 | 82.523 | 81.2583 | 82.9654 | 86.6989 | 84.1718 | 84.1718 | 84.1718 | 84.1718 | 84.1718 | 84.1718 | 84.1718 | 84.1718 | 84.1718 | 84.1718 | 84.1718 | 84.1718 | 84.1718 | 84.1718 | 84.1718 | 84.1718
5% | 39.5813 | 54.9457 | 58.9399 | 59.6207 | 60.1517 | 61.066 | 63.1461 | 64.5385 | 66.3024 | 67.218 | 68.0234 | 66.5393 | 68.2787 | 71.0131 | 68.938 | 68.938 | 68.938 | 68.938 | 68.938 | 68.938 | 68.938 | 68.938 | 68.938 | 68.938 | 68.938 | 68.938 | 68.938 | 68.938 | 68.938 | 68.938 |  | 42.3765 | 57.5471 | 61.6972 | 62.3393 | 62.747 | 63.6415 | 65.7541 | 66.9075 | 69.1048 | 75.7838 | 70.2776 | 69.2006 | 70.6544 | 73.8339 | 71.6818 | 71.6818 | 71.6818 | 71.6818 | 71.6818 | 71.6818 | 71.6818 | 71.6818 | 71.6818 | 71.6818 | 71.6818 | 71.6818 | 71.6818 | 71.6818 | 71.6818 | 71.6818
9.992e-14% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E @ R (MWh) | 105995.1099 | 147139.4588 | 157835.5397 | 159658.7762 | 161080.774 | 163529.1464 | 169099.4242 | 172828.0925 | 177551.675 | 180003.4929 | 182160.4948 | 178186.1586 | 182843.9537 | 190166.5478 | 184609.7151 | 184609.7151 | 184609.7151 | 184609.7151 | 184609.7151 | 184609.7151 | 184609.7151 | 184609.7151 | 184609.7151 | 184609.7151 | 184609.7151 | 184609.7151 | 184609.7151 | 184609.7151 | 184609.7151 | 184609.7151 | E @ R (MWh) | 113480.2695 | 154105.704 | 165219.287 | 166938.8679 | 168030.7193 | 170426.0046 | 176083.3386 | 179172.1077 | 185056.165 | 202942.0666 | 188196.9625 | 185312.8045 | 189206.044 | 197720.4561 | 191957.169 | 191957.169 | 191957.169 | 191957.169 | 191957.169 | 191957.169 | 191957.169 | 191957.169 | 191957.169 | 191957.169 | 191957.169 | 191957.169 | 191957.169 | 191957.169 | 191957.169 | 191957.169
Option 1 Winter POE50 W E @ R (MWh) N 2 | 74196.5769 | 102997.6211 | 110484.8778 | 111761.1434 | 112756.5418 | 114470.4025 | 118369.597 | 120979.6647 | 124286.1725 | 126002.4451 | 127512.3464 | 124730.311 | 127990.7676 | 133116.5835 | 129226.8005 | 129226.8005 | 129226.8005 | 129226.8005 | 129226.8005 | 129226.8005 | 129226.8005 | 129226.8005 | 129226.8005 | 129226.8005 | 129226.8005 | 129226.8005 | 129226.8005 | 129226.8005 | 129226.8005 | 129226.8005 | Option 1 Winter POE10 W E @ R (MWh) N 2 | 34044.0809 | 46231.7112 | 49565.7861 | 50081.6604 | 50409.2158 | 51127.8014 | 52825.0016 | 53751.6323 | 55516.8495 | 60882.62 | 56459.0887 | 55593.8414 | 56761.8132 | 59316.1368 | 57587.1507 | 57587.1507 | 57587.1507 | 57587.1507 | 57587.1507 | 57587.1507 | 57587.1507 | 57587.1507 | 57587.1507 | 57587.1507 | 57587.1507 | 57587.1507 | 57587.1507 | 57587.1507 | 57587.1507 | 57587.1507
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 76.9936 | 99.7405 | 105.6969 | 105.3426 | 105.3724 | 105.9856 | 107.6 | 108.6824 | 109.7411 | 110.979 | 112.1272 | 113.2411 | 113.3701 | 114.6698 | 113.6883 | 113.6883 | 113.6883 | 113.6883 | 113.6883 | 113.6883 | 113.6883 | 113.6883 | 113.6883 | 113.6883 | 113.6883 | 113.6883 | 113.6883 | 113.6883 | 113.6883 | 113.6883
98% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 38.1099 | 49.369 | 52.3173 | 52.1419 | 52.1567 | 52.4602 | 53.2593 | 53.7951 | 54.3191 | 54.9318 | 55.5002 | 56.0515 | 56.1154 | 56.7587 | 56.2728 | 56.2728 | 56.2728 | 56.2728 | 56.2728 | 56.2728 | 56.2728 | 56.2728 | 56.2728 | 56.2728 | 56.2728 | 56.2728 | 56.2728 | 56.2728 | 56.2728 | 56.2728
97% | 16.9149 | 22.4762 | 23.991 | 23.9477 | 23.9472 | 24.1204 | 24.3105 | 24.7002 | 24.9803 | 25.1325 | 25.2993 | 25.4517 | 25.7265 | 26.0674 | 26.0444 | 26.0444 | 26.0444 | 26.0444 | 26.0444 | 26.0444 | 26.0444 | 26.0444 | 26.0444 | 26.0444 | 26.0444 | 26.0444 | 26.0444 | 26.0444 | 26.0444 | 26.0444 |  | 75.446 | 97.7357 | 103.5723 | 103.2252 | 103.2543 | 103.8552 | 105.4372 | 106.4978 | 107.5353 | 108.7483 | 109.8734 | 110.9649 | 111.0913 | 112.3649 | 111.4031 | 111.4031 | 111.4031 | 111.4031 | 111.4031 | 111.4031 | 111.4031 | 111.4031 | 111.4031 | 111.4031 | 111.4031 | 111.4031 | 111.4031 | 111.4031 | 111.4031 | 111.4031
95% | 83.2734 | 110.6519 | 118.1097 | 117.8962 | 117.8937 | 118.7467 | 119.6823 | 121.6012 | 122.9798 | 123.7293 | 124.5504 | 125.3007 | 126.6535 | 128.3318 | 128.2183 | 128.2183 | 128.2183 | 128.2183 | 128.2183 | 128.2183 | 128.2183 | 128.2183 | 128.2183 | 128.2183 | 128.2183 | 128.2183 | 128.2183 | 128.2183 | 128.2183 | 128.2183 |  | 111.4279 | 144.3481 | 152.9683 | 152.4556 | 152.4987 | 153.3862 | 155.7226 | 157.2891 | 158.8214 | 160.6129 | 162.2746 | 163.8866 | 164.0733 | 165.9543 | 164.5337 | 164.5337 | 164.5337 | 164.5337 | 164.5337 | 164.5337 | 164.5337 | 164.5337 | 164.5337 | 164.5337 | 164.5337 | 164.5337 | 164.5337 | 164.5337 | 164.5337 | 164.5337
90% | 144.4273 | 191.9119 | 204.8464 | 204.4763 | 204.4719 | 205.9512 | 207.574 | 210.9021 | 213.2931 | 214.593 | 216.0171 | 217.3184 | 219.6647 | 222.5754 | 222.3787 | 222.3787 | 222.3787 | 222.3787 | 222.3787 | 222.3787 | 222.3787 | 222.3787 | 222.3787 | 222.3787 | 222.3787 | 222.3787 | 222.3787 | 222.3787 | 222.3787 | 222.3787 |  | 483.1446 | 625.8842 | 663.261 | 661.0381 | 661.2248 | 665.0728 | 675.2033 | 681.9957 | 688.6395 | 696.4074 | 703.6125 | 710.602 | 711.4117 | 719.5673 | 713.4081 | 713.4081 | 713.4081 | 713.4081 | 713.4081 | 713.4081 | 713.4081 | 713.4081 | 713.4081 | 713.4081 | 713.4081 | 713.4081 | 713.4081 | 713.4081 | 713.4081 | 713.4081
85% | 409.8612 | 544.6148 | 581.321 | 580.2706 | 580.258 | 584.4562 | 589.0613 | 598.5059 | 605.2912 | 608.9802 | 613.0214 | 616.7142 | 623.3728 | 631.6329 | 631.0746 | 631.0746 | 631.0746 | 631.0746 | 631.0746 | 631.0746 | 631.0746 | 631.0746 | 631.0746 | 631.0746 | 631.0746 | 631.0746 | 631.0746 | 631.0746 | 631.0746 | 631.0746 |  | 457.0286 | 592.0526 | 627.4091 | 625.3063 | 625.4829 | 629.1229 | 638.7059 | 645.1311 | 651.4157 | 658.7637 | 665.5794 | 672.1911 | 672.9571 | 680.6717 | 674.8455 | 674.8455 | 674.8455 | 674.8455 | 674.8455 | 674.8455 | 674.8455 | 674.8455 | 674.8455 | 674.8455 | 674.8455 | 674.8455 | 674.8455 | 674.8455 | 674.8455 | 674.8455
80% | 572.5046 | 760.7318 | 812.0039 | 810.5367 | 810.5191 | 816.3833 | 822.8158 | 836.0082 | 845.4861 | 850.639 | 856.2839 | 861.4421 | 870.743 | 882.2809 | 881.5011 | 881.5011 | 881.5011 | 881.5011 | 881.5011 | 881.5011 | 881.5011 | 881.5011 | 881.5011 | 881.5011 | 881.5011 | 881.5011 | 881.5011 | 881.5011 | 881.5011 | 881.5011 |  | 319.1946 | 413.4971 | 438.1905 | 436.7219 | 436.8452 | 439.3874 | 446.0803 | 450.5677 | 454.957 | 460.089 | 464.8491 | 469.4668 | 470.0018 | 475.3898 | 471.3206 | 471.3206 | 471.3206 | 471.3206 | 471.3206 | 471.3206 | 471.3206 | 471.3206 | 471.3206 | 471.3206 | 471.3206 | 471.3206 | 471.3206 | 471.3206 | 471.3206 | 471.3206
75% | 1492.4153 | 1983.0895 | 2116.7465 | 2112.9218 | 2112.876 | 2128.1627 | 2144.9312 | 2179.3214 | 2204.0286 | 2217.4612 | 2232.1763 | 2245.623 | 2269.8686 | 2299.9458 | 2297.9131 | 2297.9131 | 2297.9131 | 2297.9131 | 2297.9131 | 2297.9131 | 2297.9131 | 2297.9131 | 2297.9131 | 2297.9131 | 2297.9131 | 2297.9131 | 2297.9131 | 2297.9131 | 2297.9131 | 2297.9131 |  | 569.714 | 738.0296 | 782.1036 | 779.4824 | 779.7025 | 784.24 | 796.1857 | 804.1951 | 812.0293 | 821.1891 | 829.6853 | 837.9271 | 838.8819 | 848.4987 | 841.2359 | 841.2359 | 841.2359 | 841.2359 | 841.2359 | 841.2359 | 841.2359 | 841.2359 | 841.2359 | 841.2359 | 841.2359 | 841.2359 | 841.2359 | 841.2359 | 841.2359 | 841.2359
70% | 2578.4391 | 3426.1747 | 3657.0932 | 3650.4854 | 3650.4063 | 3676.8171 | 3705.7879 | 3765.2037 | 3807.8902 | 3831.0976 | 3856.5209 | 3879.7526 | 3921.6416 | 3973.6059 | 3970.094 | 3970.094 | 3970.094 | 3970.094 | 3970.094 | 3970.094 | 3970.094 | 3970.094 | 3970.094 | 3970.094 | 3970.094 | 3970.094 | 3970.094 | 3970.094 | 3970.094 | 3970.094 |  | 1037.8661 | 1344.492 | 1424.783 | 1420.0079 | 1420.4087 | 1428.6749 | 1450.4368 | 1465.0278 | 1479.2996 | 1495.9862 | 1511.464 | 1526.4784 | 1528.2178 | 1545.7371 | 1532.5062 | 1532.5062 | 1532.5062 | 1532.5062 | 1532.5062 | 1532.5062 | 1532.5062 | 1532.5062 | 1532.5062 | 1532.5062 | 1532.5062 | 1532.5062 | 1532.5062 | 1532.5062 | 1532.5062 | 1532.5062
65% | 6475.8072 | 8604.914 | 9184.8711 | 9168.2753 | 9168.0768 | 9234.408 | 9307.1689 | 9456.393 | 9563.6012 | 9621.887 | 9685.7381 | 9744.0851 | 9849.2903 | 9979.7998 | 9970.9794 | 9970.9794 | 9970.9794 | 9970.9794 | 9970.9794 | 9970.9794 | 9970.9794 | 9970.9794 | 9970.9794 | 9970.9794 | 9970.9794 | 9970.9794 | 9970.9794 | 9970.9794 | 9970.9794 | 9970.9794 |  | 1305.7961 | 1691.5789 | 1792.5974 | 1786.5896 | 1787.0939 | 1797.4941 | 1824.8739 | 1843.2317 | 1861.1878 | 1882.1821 | 1901.6555 | 1920.546 | 1922.7344 | 1944.7764 | 1928.1299 | 1928.1299 | 1928.1299 | 1928.1299 | 1928.1299 | 1928.1299 | 1928.1299 | 1928.1299 | 1928.1299 | 1928.1299 | 1928.1299 | 1928.1299 | 1928.1299 | 1928.1299 | 1928.1299 | 1928.1299
60% | 9465.8424 | 12578.0087 | 13425.7459 | 13401.4874 | 13401.1972 | 13498.1551 | 13604.5115 | 13822.636 | 13979.3447 | 14064.5425 | 14157.8751 | 14243.1624 | 14396.9433 | 14587.7122 | 14574.8193 | 14574.8193 | 14574.8193 | 14574.8193 | 14574.8193 | 14574.8193 | 14574.8193 | 14574.8193 | 14574.8193 | 14574.8193 | 14574.8193 | 14574.8193 | 14574.8193 | 14574.8193 | 14574.8193 | 14574.8193 |  | 2043.3291 | 2647.0078 | 2805.083 | 2795.6818 | 2796.4711 | 2812.7454 | 2855.5897 | 2884.3162 | 2912.4142 | 2945.2664 | 2975.7387 | 3005.2988 | 3008.7233 | 3043.2149 | 3017.1662 | 3017.1662 | 3017.1662 | 3017.1662 | 3017.1662 | 3017.1662 | 3017.1662 | 3017.1662 | 3017.1662 | 3017.1662 | 3017.1662 | 3017.1662 | 3017.1662 | 3017.1662 | 3017.1662 | 3017.1662
55% | 10703.6666 | 14222.8031 | 15181.3967 | 15153.966 | 15153.6378 | 15263.2747 | 15383.539 | 15630.1871 | 15807.3882 | 15903.7271 | 16009.2646 | 16105.7046 | 16279.5951 | 16495.3104 | 16480.7315 | 16480.7315 | 16480.7315 | 16480.7315 | 16480.7315 | 16480.7315 | 16480.7315 | 16480.7315 | 16480.7315 | 16480.7315 | 16480.7315 | 16480.7315 | 16480.7315 | 16480.7315 | 16480.7315 | 16480.7315 |  | 3926.5772 | 5086.6405 | 5390.4069 | 5372.341 | 5373.8577 | 5405.1313 | 5487.4633 | 5542.6658 | 5596.6606 | 5659.7913 | 5718.3486 | 5775.1529 | 5781.7337 | 5848.0147 | 5797.958 | 5797.958 | 5797.958 | 5797.958 | 5797.958 | 5797.958 | 5797.958 | 5797.958 | 5797.958 | 5797.958 | 5797.958 | 5797.958 | 5797.958 | 5797.958 | 5797.958 | 5797.958
50% | 13744.0128 | 18262.75 | 19493.6294 | 19458.4071 | 19457.9857 | 19598.7646 | 19753.1897 | 20069.8975 | 20297.432 | 20421.1357 | 20556.6509 | 20680.4844 | 20903.7679 | 21180.7565 | 21162.0366 | 21162.0366 | 21162.0366 | 21162.0366 | 21162.0366 | 21162.0366 | 21162.0366 | 21162.0366 | 21162.0366 | 21162.0366 | 21162.0366 | 21162.0366 | 21162.0366 | 21162.0366 | 21162.0366 | 21162.0366 |  | 8714.0125 | 11288.47 | 11962.6002 | 11922.5077 | 11925.8735 | 11995.2773 | 12177.9916 | 12300.4992 | 12420.3265 | 12560.4285 | 12690.3811 | 12816.4434 | 12831.0478 | 12978.1412 | 12867.0534 | 12867.0534 | 12867.0534 | 12867.0534 | 12867.0534 | 12867.0534 | 12867.0534 | 12867.0534 | 12867.0534 | 12867.0534 | 12867.0534 | 12867.0534 | 12867.0534 | 12867.0534 | 12867.0534 | 12867.0534
45% | 18302.3635 | 24319.7888 | 25958.9027 | 25911.9985 | 25911.4373 | 26098.9072 | 26304.5489 | 26726.2963 | 27029.2951 | 27194.0265 | 27374.4867 | 27539.391 | 27836.7289 | 28205.5838 | 28180.6551 | 28180.6551 | 28180.6551 | 28180.6551 | 28180.6551 | 28180.6551 | 28180.6551 | 28180.6551 | 28180.6551 | 28180.6551 | 28180.6551 | 28180.6551 | 28180.6551 | 28180.6551 | 28180.6551 | 28180.6551 |  | 13204.5002 | 17105.6219 | 18127.1435 | 18066.3908 | 18071.491 | 18176.6598 | 18453.5301 | 18639.1681 | 18820.7445 | 19033.0436 | 19229.9631 | 19420.9876 | 19443.1179 | 19666.0112 | 19497.6778 | 19497.6778 | 19497.6778 | 19497.6778 | 19497.6778 | 19497.6778 | 19497.6778 | 19497.6778 | 19497.6778 | 19497.6778 | 19497.6778 | 19497.6778 | 19497.6778 | 19497.6778 | 19497.6778 | 19497.6778
40% | 12836.6798 | 17057.1053 | 18206.7263 | 18173.8293 | 18173.4357 | 18304.9209 | 18449.1513 | 18744.9511 | 18957.4646 | 19073.0018 | 19199.5707 | 19315.2292 | 19523.7723 | 19782.475 | 19764.9909 | 19764.9909 | 19764.9909 | 19764.9909 | 19764.9909 | 19764.9909 | 19764.9909 | 19764.9909 | 19764.9909 | 19764.9909 | 19764.9909 | 19764.9909 | 19764.9909 | 19764.9909 | 19764.9909 | 19764.9909 |  | 13672.6523 | 17712.0843 | 18769.8229 | 18706.9162 | 18712.1973 | 18821.0947 | 19107.7811 | 19300.0008 | 19488.0148 | 19707.8407 | 19911.7418 | 20109.5389 | 20132.4538 | 20363.2496 | 20188.9481 | 20188.9481 | 20188.9481 | 20188.9481 | 20188.9481 | 20188.9481 | 20188.9481 | 20188.9481 | 20188.9481 | 20188.9481 | 20188.9481 | 20188.9481 | 20188.9481 | 20188.9481 | 20188.9481 | 20188.9481
35% | 6655.3655 | 8843.5072 | 9439.545 | 9422.4891 | 9422.285 | 9490.4555 | 9565.2339 | 9718.5956 | 9828.7764 | 9888.6783 | 9954.2998 | 10014.2647 | 10122.3869 | 10256.5152 | 10247.4502 | 10247.4502 | 10247.4502 | 10247.4502 | 10247.4502 | 10247.4502 | 10247.4502 | 10247.4502 | 10247.4502 | 10247.4502 | 10247.4502 | 10247.4502 | 10247.4502 | 10247.4502 | 10247.4502 | 10247.4502 |  | 18622.1031 | 24123.7949 | 25564.4311 | 25478.7524 | 25485.9452 | 25634.2631 | 26024.729 | 26286.5314 | 26542.6059 | 26842.008 | 27119.7205 | 27389.1195 | 27420.3294 | 27734.6724 | 27497.2745 | 27497.2745 | 27497.2745 | 27497.2745 | 27497.2745 | 27497.2745 | 27497.2745 | 27497.2745 | 27497.2745 | 27497.2745 | 27497.2745 | 27497.2745 | 27497.2745 | 27497.2745 | 27497.2745 | 27497.2745
30% | 3095.428 | 4113.1385 | 4390.3573 | 4382.4246 | 4382.3296 | 4414.0359 | 4448.8155 | 4520.1445 | 4571.3898 | 4599.2504 | 4629.7711 | 4657.6609 | 4707.9489 | 4770.3323 | 4766.1162 | 4766.1162 | 4766.1162 | 4766.1162 | 4766.1162 | 4766.1162 | 4766.1162 | 4766.1162 | 4766.1162 | 4766.1162 | 4766.1162 | 4766.1162 | 4766.1162 | 4766.1162 | 4766.1162 | 4766.1162 |  | 17207.9743 | 22291.8776 | 23623.1145 | 23543.942 | 23550.5887 | 23687.6435 | 24048.4582 | 24290.3798 | 24527.0085 | 24803.6745 | 25060.2981 | 25309.2393 | 25338.0792 | 25628.5516 | 25409.1812 | 25409.1812 | 25409.1812 | 25409.1812 | 25409.1812 | 25409.1812 | 25409.1812 | 25409.1812 | 25409.1812 | 25409.1812 | 25409.1812 | 25409.1812 | 25409.1812 | 25409.1812 | 25409.1812 | 25409.1812
25% | 2113.496 | 2808.3682 | 2997.6476 | 2992.2313 | 2992.1665 | 3013.8149 | 3037.5617 | 3086.2637 | 3121.253 | 3140.2756 | 3161.1146 | 3180.1572 | 3214.4928 | 3257.0869 | 3254.2082 | 3254.2082 | 3254.2082 | 3254.2082 | 3254.2082 | 3254.2082 | 3254.2082 | 3254.2082 | 3254.2082 | 3254.2082 | 3254.2082 | 3254.2082 | 3254.2082 | 3254.2082 | 3254.2082 | 3254.2082 |  | 4963.476 | 6429.8794 | 6813.862 | 6791.0255 | 6792.9426 | 6832.4748 | 6936.5483 | 7006.3283 | 7074.5816 | 7154.3833 | 7228.4039 | 7300.2086 | 7308.5272 | 7392.3112 | 7329.0359 | 7329.0359 | 7329.0359 | 7329.0359 | 7329.0359 | 7329.0359 | 7329.0359 | 7329.0359 | 7329.0359 | 7329.0359 | 7329.0359 | 7329.0359 | 7329.0359 | 7329.0359 | 7329.0359 | 7329.0359
20% | 1280.3284 | 1701.2729 | 1815.9359 | 1812.6548 | 1812.6155 | 1825.7299 | 1840.1154 | 1869.6184 | 1890.8145 | 1902.3381 | 1914.9621 | 1926.4978 | 1947.2979 | 1973.1009 | 1971.357 | 1971.357 | 1971.357 | 1971.357 | 1971.357 | 1971.357 | 1971.357 | 1971.357 | 1971.357 | 1971.357 | 1971.357 | 1971.357 | 1971.357 | 1971.357 | 1971.357 | 1971.357 |  | 1331.912 | 1725.4105 | 1828.4494 | 1822.3214 | 1822.8358 | 1833.444 | 1861.3713 | 1880.0963 | 1898.4115 | 1919.8257 | 1939.6886 | 1958.9569 | 1961.1891 | 1983.6719 | 1966.6925 | 1966.6925 | 1966.6925 | 1966.6925 | 1966.6925 | 1966.6925 | 1966.6925 | 1966.6925 | 1966.6925 | 1966.6925 | 1966.6925 | 1966.6925 | 1966.6925 | 1966.6925 | 1966.6925 | 1966.6925
15% | 819.7224 | 1089.2296 | 1162.6419 | 1160.5412 | 1160.516 | 1168.9124 | 1178.1226 | 1197.0118 | 1210.5824 | 1217.9604 | 1226.0428 | 1233.4285 | 1246.7456 | 1263.2658 | 1262.1493 | 1262.1493 | 1262.1493 | 1262.1493 | 1262.1493 | 1262.1493 | 1262.1493 | 1262.1493 | 1262.1493 | 1262.1493 | 1262.1493 | 1262.1493 | 1262.1493 | 1262.1493 | 1262.1493 | 1262.1493 |  | 734.6312 | 951.6698 | 1008.502 | 1005.1221 | 1005.4058 | 1011.2569 | 1026.6605 | 1036.9885 | 1047.0905 | 1058.9017 | 1069.8573 | 1080.4849 | 1081.7162 | 1094.1168 | 1084.7516 | 1084.7516 | 1084.7516 | 1084.7516 | 1084.7516 | 1084.7516 | 1084.7516 | 1084.7516 | 1084.7516 | 1084.7516 | 1084.7516 | 1084.7516 | 1084.7516 | 1084.7516 | 1084.7516 | 1084.7516
10% | 548.6502 | 729.0346 | 778.1704 | 776.7643 | 776.7475 | 782.3673 | 788.5318 | 801.1745 | 810.2575 | 815.1957 | 820.6054 | 825.5487 | 834.462 | 845.5192 | 844.7719 | 844.7719 | 844.7719 | 844.7719 | 844.7719 | 844.7719 | 844.7719 | 844.7719 | 844.7719 | 844.7719 | 844.7719 | 844.7719 | 844.7719 | 844.7719 | 844.7719 | 844.7719 |  | 171.688 | 222.4113 | 235.6934 | 234.9034 | 234.9698 | 236.3372 | 239.9371 | 242.3508 | 244.7117 | 247.4721 | 250.0325 | 252.5162 | 252.804 | 255.7021 | 253.5134 | 253.5134 | 253.5134 | 253.5134 | 253.5134 | 253.5134 | 253.5134 | 253.5134 | 253.5134 | 253.5134 | 253.5134 | 253.5134 | 253.5134 | 253.5134 | 253.5134 | 253.5134
5% | 390.344 | 518.6808 | 553.639 | 552.6387 | 552.6267 | 556.625 | 561.0108 | 570.0056 | 576.4678 | 579.9811 | 583.8299 | 587.3469 | 593.6884 | 601.5551 | 601.0235 | 601.0235 | 601.0235 | 601.0235 | 601.0235 | 601.0235 | 601.0235 | 601.0235 | 601.0235 | 601.0235 | 601.0235 | 601.0235 | 601.0235 | 601.0235 | 601.0235 | 601.0235 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9.992e-14% | 34.2635 | 45.5286 | 48.5972 | 48.5094 | 48.5083 | 48.8593 | 49.2443 | 50.0338 | 50.6011 | 50.9095 | 51.2473 | 51.556 | 52.1126 | 52.8032 | 52.7565 | 52.7565 | 52.7565 | 52.7565 | 52.7565 | 52.7565 | 52.7565 | 52.7565 | 52.7565 | 52.7565 | 52.7565 | 52.7565 | 52.7565 | 52.7565 | 52.7565 | 52.7565 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E @ R (MWh) | 91763.8061 | 121933.7811 | 130151.918 | 129916.7517 | 129913.938 | 130853.8682 | 131884.9083 | 133999.4516 | 135518.6175 | 136344.5424 | 137249.3282 | 138076.12 | 139566.9035 | 141416.2562 | 141291.2697 | 141291.2697 | 141291.2697 | 141291.2697 | 141291.2697 | 141291.2697 | 141291.2697 | 141291.2697 | 141291.2697 | 141291.2697 | 141291.2697 | 141291.2697 | 141291.2697 | 141291.2697 | 141291.2697 | 141291.2697 | E @ R (MWh) | 89067.5772 | 115381.5956 | 122272.0083 | 121862.2159 | 121896.6185 | 122606.0074 | 124473.5651 | 125725.7387 | 126950.5164 | 128382.5252 | 129710.7955 | 130999.3026 | 131148.5764 | 132652.0463 | 131516.5966 | 131516.5966 | 131516.5966 | 131516.5966 | 131516.5966 | 131516.5966 | 131516.5966 | 131516.5966 | 131516.5966 | 131516.5966 | 131516.5966 | 131516.5966 | 131516.5966 | 131516.5966 | 131516.5966 | 131516.5966
Option 1 Summer POE50 W E @ R (MWh) N 2 | 64234.6643 | 85353.6468 | 91106.3426 | 90941.7262 | 90939.7566 | 91597.7077 | 92319.4358 | 93799.6161 | 94863.0323 | 95441.1797 | 96074.5298 | 96653.284 | 97696.8324 | 98991.3793 | 98903.8888 | 98903.8888 | 98903.8888 | 98903.8888 | 98903.8888 | 98903.8888 | 98903.8888 | 98903.8888 | 98903.8888 | 98903.8888 | 98903.8888 | 98903.8888 | 98903.8888 | 98903.8888 | 98903.8888 | 98903.8888 | Option 1 Summer POE10 W E @ R (MWh) N 2 | 26720.2732 | 34614.4787 | 36681.6025 | 36558.6648 | 36568.9855 | 36781.8022 | 37342.0695 | 37717.7216 | 38085.1549 | 38514.7576 | 38913.2387 | 39299.7908 | 39344.5729 | 39795.6139 | 39454.979 | 39454.979 | 39454.979 | 39454.979 | 39454.979 | 39454.979 | 39454.979 | 39454.979 | 39454.979 | 39454.979 | 39454.979 | 39454.979 | 39454.979 | 39454.979 | 39454.979 | 39454.979
Option 2 - 1B New PHS ZSS + Three new feeders
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | 59.6718 | 82.8348 | 88.8563 | 61.2972 | 62.0977 | 63.4761 | 66.612 | 68.7111 | 71.3703 | 72.7506 | 73.9649 | 71.7275 | 74.3497 | 78.4721 | 75.3438 | 75.3438 | 75.3438 | 75.3438 | 75.3438 | 75.3438 | 75.3438 | 75.3438 | 75.3438 | 75.3438 | 75.3438 | 75.3438 | 75.3438 | 75.3438 | 75.3438 | 75.3438 |  | 63.8857 | 86.7566 | 93.0131 | 65.3957 | 66.0103 | 67.3588 | 70.5437 | 72.2826 | 75.5951 | 85.6643 | 77.3633 | 75.7396 | 77.9314 | 82.7247 | 79.4802 | 79.4802 | 79.4802 | 79.4802 | 79.4802 | 79.4802 | 79.4802 | 79.4802 | 79.4802 | 79.4802 | 79.4802 | 79.4802 | 79.4802 | 79.4802 | 79.4802 | 79.4802
98% | 70.8865 | 98.4027 | 105.556 | 72.8174 | 73.7684 | 75.4058 | 79.131 | 81.6247 | 84.7836 | 86.4234 | 87.8659 | 85.208 | 88.323 | 93.2201 | 89.5039 | 89.5039 | 89.5039 | 89.5039 | 89.5039 | 89.5039 | 89.5039 | 89.5039 | 89.5039 | 89.5039 | 89.5039 | 89.5039 | 89.5039 | 89.5039 | 89.5039 | 89.5039 |  | 75.8924 | 103.0616 | 110.494 | 77.6861 | 78.4163 | 80.0182 | 83.8017 | 85.8673 | 89.8024 | 101.764 | 91.9029 | 89.9741 | 92.5778 | 98.272 | 94.4176 | 94.4176 | 94.4176 | 94.4176 | 94.4176 | 94.4176 | 94.4176 | 94.4176 | 94.4176 | 94.4176 | 94.4176 | 94.4176 | 94.4176 | 94.4176 | 94.4176 | 94.4176
97% | 140.3338 | 194.8074 | 208.9687 | 144.1562 | 146.0389 | 149.2805 | 156.6553 | 161.5919 | 167.8458 | 171.0919 | 173.9477 | 168.6858 | 174.8526 | 184.5474 | 177.1904 | 177.1904 | 177.1904 | 177.1904 | 177.1904 | 177.1904 | 177.1904 | 177.1904 | 177.1904 | 177.1904 | 177.1904 | 177.1904 | 177.1904 | 177.1904 | 177.1904 | 177.1904 |  | 150.2438 | 204.0305 | 218.7445 | 153.7948 | 155.2404 | 158.4117 | 165.9018 | 169.9912 | 177.7815 | 201.4618 | 181.9398 | 178.1213 | 183.2758 | 194.5486 | 186.9182 | 186.9182 | 186.9182 | 186.9182 | 186.9182 | 186.9182 | 186.9182 | 186.9182 | 186.9182 | 186.9182 | 186.9182 | 186.9182 | 186.9182 | 186.9182 | 186.9182 | 186.9182
95% | 414.5243 | 575.4311 | 617.2612 | 425.8154 | 431.3765 | 440.9516 | 462.7357 | 477.3178 | 495.7907 | 505.3792 | 513.8148 | 498.272 | 516.4877 | 545.1248 | 523.3932 | 523.3932 | 523.3932 | 523.3932 | 523.3932 | 523.3932 | 523.3932 | 523.3932 | 523.3932 | 523.3932 | 523.3932 | 523.3932 | 523.3932 | 523.3932 | 523.3932 | 523.3932 |  | 443.7972 | 602.6746 | 646.1375 | 454.2863 | 458.5562 | 467.9237 | 490.0483 | 502.1279 | 525.1391 | 595.0871 | 537.4221 | 526.1428 | 541.3684 | 574.6665 | 552.1275 | 552.1275 | 552.1275 | 552.1275 | 552.1275 | 552.1275 | 552.1275 | 552.1275 | 552.1275 | 552.1275 | 552.1275 | 552.1275 | 552.1275 | 552.1275 | 552.1275 | 552.1275
90% | 2285.5212 | 3172.6969 | 3403.3313 | 2347.7754 | 2378.4372 | 2431.2303 | 2551.3395 | 2631.739 | 2733.5913 | 2786.4586 | 2832.969 | 2747.2723 | 2847.7061 | 3005.5997 | 2885.7804 | 2885.7804 | 2885.7804 | 2885.7804 | 2885.7804 | 2885.7804 | 2885.7804 | 2885.7804 | 2885.7804 | 2885.7804 | 2885.7804 | 2885.7804 | 2885.7804 | 2885.7804 | 2885.7804 | 2885.7804 |  | 2446.9201 | 3322.9067 | 3562.5435 | 2504.7525 | 2528.2955 | 2579.9439 | 2701.9303 | 2768.5319 | 2895.407 | 3281.072 | 2963.1305 | 2900.9408 | 2984.8888 | 3168.4809 | 3044.21 | 3044.21 | 3044.21 | 3044.21 | 3044.21 | 3044.21 | 3044.21 | 3044.21 | 3044.21 | 3044.21 | 3044.21 | 3044.21 | 3044.21 | 3044.21 | 3044.21 | 3044.21
85% | 5583.3646 | 7750.6712 | 8314.0946 | 5735.447 | 5810.3517 | 5939.3214 | 6232.7396 | 6429.1497 | 6677.9677 | 6807.1189 | 6920.7404 | 6711.3895 | 6956.7421 | 7342.4647 | 7049.7547 | 7049.7547 | 7049.7547 | 7049.7547 | 7049.7547 | 7049.7547 | 7049.7547 | 7049.7547 | 7049.7547 | 7049.7547 | 7049.7547 | 7049.7547 | 7049.7547 | 7049.7547 | 7049.7547 | 7049.7547 |  | 5977.6505 | 8117.623 | 8703.0385 | 6118.9308 | 6176.4448 | 6302.6181 | 6600.622 | 6763.3251 | 7073.2718 | 8015.4239 | 7238.7154 | 7086.7905 | 7291.8695 | 7740.372 | 7436.7869 | 7436.7869 | 7436.7869 | 7436.7869 | 7436.7869 | 7436.7869 | 7436.7869 | 7436.7869 | 7436.7869 | 7436.7869 | 7436.7869 | 7436.7869 | 7436.7869 | 7436.7869 | 7436.7869 | 7436.7869
80% | 8678.2039 | 12046.8408 | 12922.5678 | 8914.585 | 9031.0091 | 9231.4662 | 9687.5251 | 9992.8047 | 10379.5415 | 10580.2807 | 10756.8823 | 10431.489 | 10812.8395 | 11412.3668 | 10957.4088 | 10957.4088 | 10957.4088 | 10957.4088 | 10957.4088 | 10957.4088 | 10957.4088 | 10957.4088 | 10957.4088 | 10957.4088 | 10957.4088 | 10957.4088 | 10957.4088 | 10957.4088 | 10957.4088 | 10957.4088 |  | 9291.041 | 12617.1926 | 13527.1019 | 9510.6325 | 9600.0263 | 9796.137 | 10259.3235 | 10512.2122 | 10993.9613 | 12458.3449 | 11251.1098 | 11014.9733 | 11333.7269 | 12030.8327 | 11558.9715 | 11558.9715 | 11558.9715 | 11558.9715 | 11558.9715 | 11558.9715 | 11558.9715 | 11558.9715 | 11558.9715 | 11558.9715 | 11558.9715 | 11558.9715 | 11558.9715 | 11558.9715 | 11558.9715 | 11558.9715
75% | 9574.4808 | 13291.0275 | 14257.1987 | 9835.2752 | 9963.7235 | 10184.8836 | 10688.0438 | 11024.8524 | 11451.531 | 11673.0024 | 11867.8432 | 11508.8436 | 11929.5797 | 12591.0256 | 12089.08 | 12089.08 | 12089.08 | 12089.08 | 12089.08 | 12089.08 | 12089.08 | 12089.08 | 12089.08 | 12089.08 | 12089.08 | 12089.08 | 12089.08 | 12089.08 | 12089.08 | 12089.08 |  | 10250.6112 | 13920.2847 | 14924.1686 | 10492.8819 | 10591.5083 | 10807.8731 | 11318.897 | 11597.9038 | 12129.4075 | 13745.0313 | 12413.1141 | 12152.5896 | 12504.2639 | 13273.3661 | 12752.7715 | 12752.7715 | 12752.7715 | 12752.7715 | 12752.7715 | 12752.7715 | 12752.7715 | 12752.7715 | 12752.7715 | 12752.7715 | 12752.7715 | 12752.7715 | 12752.7715 | 12752.7715 | 12752.7715 | 12752.7715
70% | 10287.2444 | 14280.4661 | 15318.563 | 10567.4534 | 10705.4639 | 10943.0881 | 11483.7056 | 11845.5876 | 12304.0299 | 12541.9885 | 12751.3341 | 12365.609 | 12817.6665 | 13528.3532 | 12989.0406 | 12989.0406 | 12989.0406 | 12989.0406 | 12989.0406 | 12989.0406 | 12989.0406 | 12989.0406 | 12989.0406 | 12989.0406 | 12989.0406 | 12989.0406 | 12989.0406 | 12989.0406 | 12989.0406 | 12989.0406 |  | 11013.7087 | 14956.5677 | 16035.1849 | 11274.015 | 11379.9835 | 11612.4554 | 12161.5221 | 12461.2993 | 13032.3703 | 14768.2678 | 13337.1971 | 13057.2782 | 13435.1325 | 14261.4898 | 13702.14 | 13702.14 | 13702.14 | 13702.14 | 13702.14 | 13702.14 | 13702.14 | 13702.14 | 13702.14 | 13702.14 | 13702.14 | 13702.14 | 13702.14 | 13702.14 | 13702.14 | 13702.14
65% | 10840.7831 | 15048.8731 | 16142.8282 | 11136.0696 | 11281.5062 | 11531.9166 | 12101.6238 | 12482.978 | 12966.0884 | 13216.8511 | 13437.4612 | 13030.981 | 13507.3628 | 14256.2903 | 13687.9583 | 13687.9583 | 13687.9583 | 13687.9583 | 13687.9583 | 13687.9583 | 13687.9583 | 13687.9583 | 13687.9583 | 13687.9583 | 13687.9583 | 13687.9583 | 13687.9583 | 13687.9583 | 13687.9583 | 13687.9583 |  | 11606.3372 | 15761.3546 | 16898.0103 | 11880.6502 | 11992.3206 | 12237.3015 | 12815.9124 | 13131.8201 | 13733.6195 | 15562.9226 | 14054.8485 | 13759.8676 | 14158.0536 | 15028.8758 | 14439.4284 | 14439.4284 | 14439.4284 | 14439.4284 | 14439.4284 | 14439.4284 | 14439.4284 | 14439.4284 | 14439.4284 | 14439.4284 | 14439.4284 | 14439.4284 | 14439.4284 | 14439.4284 | 14439.4284 | 14439.4284
60% | 11934.3669 | 16566.9557 | 17771.2656 | 12259.441 | 12419.5488 | 12695.2198 | 13322.3972 | 13742.2213 | 14274.0662 | 14550.1252 | 14792.9897 | 14345.505 | 14869.9427 | 15694.4197 | 15068.7561 | 15068.7561 | 15068.7561 | 15068.7561 | 15068.7561 | 15068.7561 | 15068.7561 | 15068.7561 | 15068.7561 | 15068.7561 | 15068.7561 | 15068.7561 | 15068.7561 | 15068.7561 | 15068.7561 | 15068.7561 |  | 12777.1477 | 17351.3101 | 18602.628 | 13079.1325 | 13202.0679 | 13471.7616 | 14108.741 | 14456.5165 | 15119.0235 | 17132.8609 | 15472.6571 | 15147.9195 | 15586.2732 | 16544.9411 | 15896.0321 | 15896.0321 | 15896.0321 | 15896.0321 | 15896.0321 | 15896.0321 | 15896.0321 | 15896.0321 | 15896.0321 | 15896.0321 | 15896.0321 | 15896.0321 | 15896.0321 | 15896.0321 | 15896.0321 | 15896.0321
55% | 13276.2336 | 18429.6976 | 19769.4166 | 13637.8581 | 13815.9679 | 14122.6346 | 14820.3301 | 15287.3579 | 15879.0021 | 16186.1003 | 16456.2718 | 15958.4732 | 16541.8773 | 17459.0561 | 16763.0446 | 16763.0446 | 16763.0446 | 16763.0446 | 16763.0446 | 16763.0446 | 16763.0446 | 16763.0446 | 16763.0446 | 16763.0446 | 16763.0446 | 16763.0446 | 16763.0446 | 16763.0446 | 16763.0446 | 16763.0446 |  | 14213.7742 | 19302.2426 | 20694.2551 | 14549.7133 | 14686.4713 | 14986.4886 | 15695.0881 | 16081.9666 | 16818.9639 | 19059.2315 | 17212.3591 | 16851.1089 | 17338.7498 | 18405.2078 | 17683.3372 | 17683.3372 | 17683.3372 | 17683.3372 | 17683.3372 | 17683.3372 | 17683.3372 | 17683.3372 | 17683.3372 | 17683.3372 | 17683.3372 | 17683.3372 | 17683.3372 | 17683.3372 | 17683.3372 | 17683.3372
50% | 13456.7484 | 18680.2832 | 20038.2182 | 13823.2898 | 14003.8214 | 14314.6578 | 15021.8397 | 15495.2177 | 16094.9063 | 16406.1801 | 16680.0251 | 16175.458 | 16766.7945 | 17696.444 | 16990.969 | 16990.969 | 16990.969 | 16990.969 | 16990.969 | 16990.969 | 16990.969 | 16990.969 | 16990.969 | 16990.969 | 16990.969 | 16990.969 | 16990.969 | 16990.969 | 16990.969 | 16990.969 |  | 14407.0366 | 19564.692 | 20975.6315 | 14747.5434 | 14886.1609 | 15190.2574 | 15908.4917 | 16300.6305 | 17047.6487 | 19318.3768 | 17446.3927 | 17080.2307 | 17574.502 | 18655.4604 | 17923.7747 | 17923.7747 | 17923.7747 | 17923.7747 | 17923.7747 | 17923.7747 | 17923.7747 | 17923.7747 | 17923.7747 | 17923.7747 | 17923.7747 | 17923.7747 | 17923.7747 | 17923.7747 | 17923.7747 | 17923.7747
45% | 10386.1977 | 14417.8303 | 15465.9127 | 10669.102 | 10808.44 | 11048.35 | 11594.1676 | 11959.5306 | 12422.3827 | 12662.6303 | 12873.9895 | 12484.5542 | 12940.96 | 13658.4828 | 13113.9825 | 13113.9825 | 13113.9825 | 13113.9825 | 13113.9825 | 13113.9825 | 13113.9825 | 13113.9825 | 13113.9825 | 13113.9825 | 13113.9825 | 13113.9825 | 13113.9825 | 13113.9825 | 13113.9825 | 13113.9825 |  | 11119.6499 | 15100.4354 | 16189.4278 | 11382.4601 | 11489.4479 | 11724.156 | 12278.5041 | 12581.1649 | 13157.7291 | 14910.3242 | 13465.488 | 13182.8765 | 13564.3654 | 14398.6715 | 13833.9413 | 13833.9413 | 13833.9413 | 13833.9413 | 13833.9413 | 13833.9413 | 13833.9413 | 13833.9413 | 13833.9413 | 13833.9413 | 13833.9413 | 13833.9413 | 13833.9413 | 13833.9413 | 13833.9413 | 13833.9413
40% | 5102.6915 | 7083.4142 | 7598.3323 | 5241.6811 | 5310.1372 | 5428.0039 | 5696.1616 | 5875.6628 | 6103.0599 | 6221.0925 | 6324.9323 | 6133.6045 | 6357.8346 | 6710.3502 | 6442.8398 | 6442.8398 | 6442.8398 | 6442.8398 | 6442.8398 | 6442.8398 | 6442.8398 | 6442.8398 | 6442.8398 | 6442.8398 | 6442.8398 | 6442.8398 | 6442.8398 | 6442.8398 | 6442.8398 | 6442.8398 |  | 5463.0332 | 7418.775 | 7953.792 | 5592.1507 | 5644.7133 | 5760.0243 | 6032.373 | 6181.0689 | 6464.3322 | 7325.3742 | 6615.5328 | 6476.6871 | 6664.1108 | 7074.0016 | 6796.5522 | 6796.5522 | 6796.5522 | 6796.5522 | 6796.5522 | 6796.5522 | 6796.5522 | 6796.5522 | 6796.5522 | 6796.5522 | 6796.5522 | 6796.5522 | 6796.5522 | 6796.5522 | 6796.5522 | 6796.5522
35% | 1907.0998 | 2647.3829 | 2839.8304 | 1959.0464 | 1984.6314 | 2028.6834 | 2128.9057 | 2195.9931 | 2280.9814 | 2325.0954 | 2363.9049 | 2292.3973 | 2376.2019 | 2507.9525 | 2407.9721 | 2407.9721 | 2407.9721 | 2407.9721 | 2407.9721 | 2407.9721 | 2407.9721 | 2407.9721 | 2407.9721 | 2407.9721 | 2407.9721 | 2407.9721 | 2407.9721 | 2407.9721 | 2407.9721 | 2407.9721 |  | 2041.7754 | 2772.7219 | 2972.6813 | 2090.0322 | 2109.6772 | 2152.774 | 2254.5626 | 2310.1368 | 2416.0048 | 2737.8139 | 2472.515 | 2420.6223 | 2490.6708 | 2643.865 | 2540.17 | 2540.17 | 2540.17 | 2540.17 | 2540.17 | 2540.17 | 2540.17 | 2540.17 | 2540.17 | 2540.17 | 2540.17 | 2540.17 | 2540.17 | 2540.17 | 2540.17 | 2540.17
30% | 951.1511 | 1320.3614 | 1416.3431 | 977.059 | 989.8193 | 1011.7899 | 1061.775 | 1095.2343 | 1137.6216 | 1159.623 | 1178.979 | 1143.3151 | 1185.112 | 1250.8216 | 1200.9571 | 1200.9571 | 1200.9571 | 1200.9571 | 1200.9571 | 1200.9571 | 1200.9571 | 1200.9571 | 1200.9571 | 1200.9571 | 1200.9571 | 1200.9571 | 1200.9571 | 1200.9571 | 1200.9571 | 1200.9571 |  | 1018.3194 | 1382.8733 | 1482.6014 | 1042.3871 | 1052.1849 | 1073.6791 | 1124.4454 | 1152.1626 | 1204.9634 | 1365.4632 | 1233.1474 | 1207.2663 | 1242.2025 | 1318.6069 | 1266.8898 | 1266.8898 | 1266.8898 | 1266.8898 | 1266.8898 | 1266.8898 | 1266.8898 | 1266.8898 | 1266.8898 | 1266.8898 | 1266.8898 | 1266.8898 | 1266.8898 | 1266.8898 | 1266.8898 | 1266.8898
25% | 560.7353 | 778.3972 | 834.9816 | 576.0089 | 583.5316 | 596.4839 | 625.9518 | 645.6772 | 670.6659 | 683.6365 | 695.0475 | 674.0225 | 698.6631 | 737.4011 | 708.0044 | 708.0044 | 708.0044 | 708.0044 | 708.0044 | 708.0044 | 708.0044 | 708.0044 | 708.0044 | 708.0044 | 708.0044 | 708.0044 | 708.0044 | 708.0044 | 708.0044 | 708.0044 |  | 600.3333 | 815.25 | 874.0431 | 614.5221 | 620.2982 | 632.9697 | 662.8981 | 679.2383 | 710.3662 | 804.9862 | 726.9816 | 711.7239 | 732.3199 | 777.3628 | 746.8739 | 746.8739 | 746.8739 | 746.8739 | 746.8739 | 746.8739 | 746.8739 | 746.8739 | 746.8739 | 746.8739 | 746.8739 | 746.8739 | 746.8739 | 746.8739 | 746.8739 | 746.8739
20% | 283.3663 | 393.3611 | 421.9559 | 291.0847 | 294.8863 | 301.4317 | 316.3233 | 326.2914 | 338.9194 | 345.4741 | 351.2406 | 340.6156 | 353.0677 | 372.6439 | 357.7883 | 357.7883 | 357.7883 | 357.7883 | 357.7883 | 357.7883 | 357.7883 | 357.7883 | 357.7883 | 357.7883 | 357.7883 | 357.7883 | 357.7883 | 357.7883 | 357.7883 | 357.7883 |  | 303.377 | 411.9846 | 441.6956 | 310.5472 | 313.4662 | 319.8697 | 334.994 | 343.2515 | 358.9818 | 406.7978 | 367.3784 | 359.6679 | 370.0761 | 392.8384 | 377.4309 | 377.4309 | 377.4309 | 377.4309 | 377.4309 | 377.4309 | 377.4309 | 377.4309 | 377.4309 | 377.4309 | 377.4309 | 377.4309 | 377.4309 | 377.4309 | 377.4309 | 377.4309
15% | 115.4455 | 160.2582 | 171.908 | 118.5901 | 120.1389 | 122.8055 | 128.8724 | 132.9335 | 138.0783 | 140.7487 | 143.098 | 138.7693 | 143.8424 | 151.8179 | 145.7656 | 145.7656 | 145.7656 | 145.7656 | 145.7656 | 145.7656 | 145.7656 | 145.7656 | 145.7656 | 145.7656 | 145.7656 | 145.7656 | 145.7656 | 145.7656 | 145.7656 | 145.7656 |  | 123.598 | 167.8456 | 179.95 | 126.5192 | 127.7084 | 130.3173 | 136.479 | 139.8432 | 146.2519 | 165.7324 | 149.6727 | 146.5314 | 150.7717 | 160.0453 | 153.7681 | 153.7681 | 153.7681 | 153.7681 | 153.7681 | 153.7681 | 153.7681 | 153.7681 | 153.7681 | 153.7681 | 153.7681 | 153.7681 | 153.7681 | 153.7681 | 153.7681 | 153.7681
10% | 46.4781 | 64.5196 | 69.2097 | 47.7441 | 48.3676 | 49.4412 | 51.8837 | 53.5187 | 55.59 | 56.6651 | 57.6109 | 55.8682 | 57.9106 | 61.1215 | 58.6849 | 58.6849 | 58.6849 | 58.6849 | 58.6849 | 58.6849 | 58.6849 | 58.6849 | 58.6849 | 58.6849 | 58.6849 | 58.6849 | 58.6849 | 58.6849 | 58.6849 | 58.6849 |  | 49.7602 | 67.5742 | 72.4474 | 50.9363 | 51.4151 | 52.4654 | 54.9461 | 56.3005 | 58.8806 | 66.7235 | 60.2578 | 58.9932 | 60.7003 | 64.4338 | 61.9067 | 61.9067 | 61.9067 | 61.9067 | 61.9067 | 61.9067 | 61.9067 | 61.9067 | 61.9067 | 61.9067 | 61.9067 | 61.9067 | 61.9067 | 61.9067 | 61.9067 | 61.9067
5% | 39.5813 | 54.9457 | 58.9399 | 40.6595 | 41.1905 | 42.1047 | 44.1848 | 45.5772 | 47.3411 | 48.2567 | 49.0622 | 47.5781 | 49.3174 | 52.0518 | 49.9768 | 49.9768 | 49.9768 | 49.9768 | 49.9768 | 49.9768 | 49.9768 | 49.9768 | 49.9768 | 49.9768 | 49.9768 | 49.9768 | 49.9768 | 49.9768 | 49.9768 | 49.9768 |  | 42.3765 | 57.5471 | 61.6972 | 43.378 | 43.7858 | 44.6802 | 46.7928 | 47.9462 | 50.1435 | 56.8226 | 51.3164 | 50.2393 | 51.6932 | 54.8727 | 52.7205 | 52.7205 | 52.7205 | 52.7205 | 52.7205 | 52.7205 | 52.7205 | 52.7205 | 52.7205 | 52.7205 | 52.7205 | 52.7205 | 52.7205 | 52.7205 | 52.7205 | 52.7205
9.992e-14% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E @ R (MWh) | 105995.1099 | 147139.4588 | 157835.5397 | 108882.2564 | 110304.2541 | 112752.6265 | 118322.9044 | 122051.5726 | 126775.1552 | 129226.9731 | 131383.9749 | 127409.6387 | 132067.4338 | 139390.028 | 133833.1952 | 133833.1952 | 133833.1952 | 133833.1952 | 133833.1952 | 133833.1952 | 133833.1952 | 133833.1952 | 133833.1952 | 133833.1952 | 133833.1952 | 133833.1952 | 133833.1952 | 133833.1952 | 133833.1952 | 133833.1952 | E @ R (MWh) | 113480.2695 | 154105.704 | 165219.287 | 116162.3481 | 117254.1994 | 119649.4847 | 125306.8187 | 128395.5878 | 134279.6451 | 152165.5468 | 137420.4426 | 134536.2847 | 138429.5242 | 146943.9362 | 141180.6491 | 141180.6491 | 141180.6491 | 141180.6491 | 141180.6491 | 141180.6491 | 141180.6491 | 141180.6491 | 141180.6491 | 141180.6491 | 141180.6491 | 141180.6491 | 141180.6491 | 141180.6491 | 141180.6491 | 141180.6491
Option 2 Winter POE50 W E @ R (MWh) N 2 | 74196.5769 | 102997.6211 | 110484.8778 | 76217.5795 | 77212.9779 | 78926.8385 | 82826.033 | 85436.1008 | 88742.6086 | 90458.8812 | 91968.7825 | 89186.7471 | 92447.2037 | 97573.0196 | 93683.2366 | 93683.2366 | 93683.2366 | 93683.2366 | 93683.2366 | 93683.2366 | 93683.2366 | 93683.2366 | 93683.2366 | 93683.2366 | 93683.2366 | 93683.2366 | 93683.2366 | 93683.2366 | 93683.2366 | 93683.2366 | Option 2 Winter POE10 W E @ R (MWh) N 2 | 34044.0809 | 46231.7112 | 49565.7861 | 34848.7044 | 35176.2598 | 35894.8454 | 37592.0456 | 38518.6763 | 40283.8935 | 45649.664 | 41226.1328 | 40360.8854 | 41528.8573 | 44083.1809 | 42354.1947 | 42354.1947 | 42354.1947 | 42354.1947 | 42354.1947 | 42354.1947 | 42354.1947 | 42354.1947 | 42354.1947 | 42354.1947 | 42354.1947 | 42354.1947 | 42354.1947 | 42354.1947 | 42354.1947 | 42354.1947
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 76.9936 | 99.7405 | 105.6969 | 76.2441 | 76.2739 | 76.8871 | 78.5015 | 79.5839 | 80.6427 | 81.8806 | 83.0288 | 84.1426 | 84.2716 | 85.5713 | 84.5898 | 84.5898 | 84.5898 | 84.5898 | 84.5898 | 84.5898 | 84.5898 | 84.5898 | 84.5898 | 84.5898 | 84.5898 | 84.5898 | 84.5898 | 84.5898 | 84.5898 | 84.5898
98% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 38.1099 | 49.369 | 52.3173 | 37.7389 | 37.7537 | 38.0572 | 38.8563 | 39.392 | 39.9161 | 40.5288 | 41.0972 | 41.6485 | 41.7123 | 42.3556 | 41.8698 | 41.8698 | 41.8698 | 41.8698 | 41.8698 | 41.8698 | 41.8698 | 41.8698 | 41.8698 | 41.8698 | 41.8698 | 41.8698 | 41.8698 | 41.8698 | 41.8698 | 41.8698
97% | 16.9149 | 22.4762 | 23.991 | 16.8193 | 16.8188 | 16.992 | 17.1821 | 17.5718 | 17.8519 | 18.0041 | 18.1709 | 18.3233 | 18.5981 | 18.939 | 18.916 | 18.916 | 18.916 | 18.916 | 18.916 | 18.916 | 18.916 | 18.916 | 18.916 | 18.916 | 18.916 | 18.916 | 18.916 | 18.916 | 18.916 | 18.916 |  | 75.446 | 97.7357 | 103.5723 | 74.7116 | 74.7407 | 75.3416 | 76.9236 | 77.9842 | 79.0217 | 80.2347 | 81.3598 | 82.4513 | 82.5777 | 83.8513 | 82.8895 | 82.8895 | 82.8895 | 82.8895 | 82.8895 | 82.8895 | 82.8895 | 82.8895 | 82.8895 | 82.8895 | 82.8895 | 82.8895 | 82.8895 | 82.8895 | 82.8895 | 82.8895
95% | 83.2734 | 110.6519 | 118.1097 | 82.8026 | 82.8 | 83.653 | 84.5887 | 86.5076 | 87.8862 | 88.6357 | 89.4567 | 90.207 | 91.5599 | 93.2381 | 93.1247 | 93.1247 | 93.1247 | 93.1247 | 93.1247 | 93.1247 | 93.1247 | 93.1247 | 93.1247 | 93.1247 | 93.1247 | 93.1247 | 93.1247 | 93.1247 | 93.1247 | 93.1247 |  | 111.4279 | 144.3481 | 152.9683 | 110.3433 | 110.3863 | 111.2738 | 113.6102 | 115.1767 | 116.709 | 118.5005 | 120.1622 | 121.7742 | 121.961 | 123.8419 | 122.4214 | 122.4214 | 122.4214 | 122.4214 | 122.4214 | 122.4214 | 122.4214 | 122.4214 | 122.4214 | 122.4214 | 122.4214 | 122.4214 | 122.4214 | 122.4214 | 122.4214 | 122.4214
90% | 144.4273 | 191.9119 | 204.8464 | 143.6108 | 143.6063 | 145.0857 | 146.7084 | 150.0365 | 152.4276 | 153.7275 | 155.1515 | 156.4528 | 158.7992 | 161.7099 | 161.5131 | 161.5131 | 161.5131 | 161.5131 | 161.5131 | 161.5131 | 161.5131 | 161.5131 | 161.5131 | 161.5131 | 161.5131 | 161.5131 | 161.5131 | 161.5131 | 161.5131 | 161.5131 |  | 483.1446 | 625.8842 | 663.261 | 478.4415 | 478.6281 | 482.4762 | 492.6067 | 499.3991 | 506.0429 | 513.8107 | 521.0159 | 528.0054 | 528.8151 | 536.9706 | 530.8114 | 530.8114 | 530.8114 | 530.8114 | 530.8114 | 530.8114 | 530.8114 | 530.8114 | 530.8114 | 530.8114 | 530.8114 | 530.8114 | 530.8114 | 530.8114 | 530.8114 | 530.8114
85% | 409.8612 | 544.6148 | 581.321 | 407.5441 | 407.5315 | 411.7297 | 416.3348 | 425.7794 | 432.5647 | 436.2537 | 440.2949 | 443.9877 | 450.6463 | 458.9064 | 458.3481 | 458.3481 | 458.3481 | 458.3481 | 458.3481 | 458.3481 | 458.3481 | 458.3481 | 458.3481 | 458.3481 | 458.3481 | 458.3481 | 458.3481 | 458.3481 | 458.3481 | 458.3481 |  | 457.0286 | 592.0526 | 627.4091 | 452.5798 | 452.7563 | 456.3964 | 465.9793 | 472.4045 | 478.6892 | 486.0372 | 492.8529 | 499.4646 | 500.2305 | 507.9452 | 502.1189 | 502.1189 | 502.1189 | 502.1189 | 502.1189 | 502.1189 | 502.1189 | 502.1189 | 502.1189 | 502.1189 | 502.1189 | 502.1189 | 502.1189 | 502.1189 | 502.1189 | 502.1189
80% | 572.5046 | 760.7318 | 812.0039 | 569.2679 | 569.2503 | 575.1145 | 581.547 | 594.7394 | 604.2173 | 609.3702 | 615.015 | 620.1733 | 629.4741 | 641.0121 | 640.2323 | 640.2323 | 640.2323 | 640.2323 | 640.2323 | 640.2323 | 640.2323 | 640.2323 | 640.2323 | 640.2323 | 640.2323 | 640.2323 | 640.2323 | 640.2323 | 640.2323 | 640.2323 |  | 319.1946 | 413.4971 | 438.1905 | 316.0875 | 316.2108 | 318.753 | 325.4459 | 329.9333 | 334.3226 | 339.4545 | 344.2147 | 348.8324 | 349.3673 | 354.7554 | 350.6862 | 350.6862 | 350.6862 | 350.6862 | 350.6862 | 350.6862 | 350.6862 | 350.6862 | 350.6862 | 350.6862 | 350.6862 | 350.6862 | 350.6862 | 350.6862 | 350.6862 | 350.6862
75% | 1492.4153 | 1983.0895 | 2116.7465 | 1483.9779 | 1483.9321 | 1499.2188 | 1515.9873 | 1550.3775 | 1575.0847 | 1588.5173 | 1603.2324 | 1616.6791 | 1640.9247 | 1671.0019 | 1668.9692 | 1668.9692 | 1668.9692 | 1668.9692 | 1668.9692 | 1668.9692 | 1668.9692 | 1668.9692 | 1668.9692 | 1668.9692 | 1668.9692 | 1668.9692 | 1668.9692 | 1668.9692 | 1668.9692 | 1668.9692 |  | 569.714 | 738.0296 | 782.1036 | 564.1683 | 564.3883 | 568.9259 | 580.8716 | 588.881 | 596.7152 | 605.8749 | 614.3711 | 622.613 | 623.5678 | 633.1846 | 625.9218 | 625.9218 | 625.9218 | 625.9218 | 625.9218 | 625.9218 | 625.9218 | 625.9218 | 625.9218 | 625.9218 | 625.9218 | 625.9218 | 625.9218 | 625.9218 | 625.9218 | 625.9218
70% | 2578.4391 | 3426.1747 | 3657.0932 | 2563.8618 | 2563.7827 | 2590.1935 | 2619.1643 | 2678.5802 | 2721.2667 | 2744.474 | 2769.8973 | 2793.129 | 2835.018 | 2886.9823 | 2883.4704 | 2883.4704 | 2883.4704 | 2883.4704 | 2883.4704 | 2883.4704 | 2883.4704 | 2883.4704 | 2883.4704 | 2883.4704 | 2883.4704 | 2883.4704 | 2883.4704 | 2883.4704 | 2883.4704 | 2883.4704 |  | 1037.8661 | 1344.492 | 1424.783 | 1027.7633 | 1028.1641 | 1036.4303 | 1058.1922 | 1072.7832 | 1087.055 | 1103.7416 | 1119.2194 | 1134.2338 | 1135.9732 | 1153.4925 | 1140.2616 | 1140.2616 | 1140.2616 | 1140.2616 | 1140.2616 | 1140.2616 | 1140.2616 | 1140.2616 | 1140.2616 | 1140.2616 | 1140.2616 | 1140.2616 | 1140.2616 | 1140.2616 | 1140.2616 | 1140.2616
65% | 6475.8072 | 8604.914 | 9184.8711 | 6439.196 | 6438.9975 | 6505.3287 | 6578.0896 | 6727.3138 | 6834.5219 | 6892.8077 | 6956.6588 | 7015.0058 | 7120.211 | 7250.7205 | 7241.9002 | 7241.9002 | 7241.9002 | 7241.9002 | 7241.9002 | 7241.9002 | 7241.9002 | 7241.9002 | 7241.9002 | 7241.9002 | 7241.9002 | 7241.9002 | 7241.9002 | 7241.9002 | 7241.9002 | 7241.9002 |  | 1305.7961 | 1691.5789 | 1792.5974 | 1293.0852 | 1293.5895 | 1303.9897 | 1331.3695 | 1349.7273 | 1367.6834 | 1388.6777 | 1408.1511 | 1427.0416 | 1429.23 | 1451.272 | 1434.6255 | 1434.6255 | 1434.6255 | 1434.6255 | 1434.6255 | 1434.6255 | 1434.6255 | 1434.6255 | 1434.6255 | 1434.6255 | 1434.6255 | 1434.6255 | 1434.6255 | 1434.6255 | 1434.6255 | 1434.6255
60% | 9465.8424 | 12578.0087 | 13425.7459 | 9412.3269 | 9412.0367 | 9508.9946 | 9615.351 | 9833.4755 | 9990.1842 | 10075.382 | 10168.7146 | 10254.0019 | 10407.7828 | 10598.5517 | 10585.6588 | 10585.6588 | 10585.6588 | 10585.6588 | 10585.6588 | 10585.6588 | 10585.6588 | 10585.6588 | 10585.6588 | 10585.6588 | 10585.6588 | 10585.6588 | 10585.6588 | 10585.6588 | 10585.6588 | 10585.6588 |  | 2043.3291 | 2647.0078 | 2805.083 | 2023.4388 | 2024.2281 | 2040.5024 | 2083.3467 | 2112.0732 | 2140.1712 | 2173.0234 | 2203.4957 | 2233.0558 | 2236.4803 | 2270.972 | 2244.9232 | 2244.9232 | 2244.9232 | 2244.9232 | 2244.9232 | 2244.9232 | 2244.9232 | 2244.9232 | 2244.9232 | 2244.9232 | 2244.9232 | 2244.9232 | 2244.9232 | 2244.9232 | 2244.9232 | 2244.9232
55% | 10703.6666 | 14222.8031 | 15181.3967 | 10643.1531 | 10642.8249 | 10752.4618 | 10872.7261 | 11119.3742 | 11296.5753 | 11392.9142 | 11498.4517 | 11594.8917 | 11768.7822 | 11984.4975 | 11969.9186 | 11969.9186 | 11969.9186 | 11969.9186 | 11969.9186 | 11969.9186 | 11969.9186 | 11969.9186 | 11969.9186 | 11969.9186 | 11969.9186 | 11969.9186 | 11969.9186 | 11969.9186 | 11969.9186 | 11969.9186 |  | 3926.5772 | 5086.6405 | 5390.4069 | 3888.355 | 3889.8717 | 3921.1454 | 4003.4773 | 4058.6799 | 4112.6746 | 4175.8053 | 4234.3626 | 4291.1669 | 4297.7477 | 4364.0287 | 4313.972 | 4313.972 | 4313.972 | 4313.972 | 4313.972 | 4313.972 | 4313.972 | 4313.972 | 4313.972 | 4313.972 | 4313.972 | 4313.972 | 4313.972 | 4313.972 | 4313.972 | 4313.972
50% | 13744.0128 | 18262.75 | 19493.6294 | 13666.3106 | 13665.8892 | 13806.6681 | 13961.0931 | 14277.8009 | 14505.3355 | 14629.0391 | 14764.5543 | 14888.3879 | 15111.6714 | 15388.66 | 15369.94 | 15369.94 | 15369.94 | 15369.94 | 15369.94 | 15369.94 | 15369.94 | 15369.94 | 15369.94 | 15369.94 | 15369.94 | 15369.94 | 15369.94 | 15369.94 | 15369.94 | 15369.94 |  | 8714.0125 | 11288.47 | 11962.6002 | 8629.1884 | 8632.5542 | 8701.958 | 8884.6723 | 9007.1799 | 9127.0072 | 9267.1092 | 9397.0618 | 9523.1241 | 9537.7285 | 9684.8219 | 9573.7341 | 9573.7341 | 9573.7341 | 9573.7341 | 9573.7341 | 9573.7341 | 9573.7341 | 9573.7341 | 9573.7341 | 9573.7341 | 9573.7341 | 9573.7341 | 9573.7341 | 9573.7341 | 9573.7341 | 9573.7341
45% | 18302.3635 | 24319.7888 | 25958.9027 | 18198.8905 | 18198.3293 | 18385.7991 | 18591.4409 | 19013.1882 | 19316.187 | 19480.9184 | 19661.3786 | 19826.2829 | 20123.6208 | 20492.4757 | 20467.5471 | 20467.5471 | 20467.5471 | 20467.5471 | 20467.5471 | 20467.5471 | 20467.5471 | 20467.5471 | 20467.5471 | 20467.5471 | 20467.5471 | 20467.5471 | 20467.5471 | 20467.5471 | 20467.5471 | 20467.5471 |  | 13204.5002 | 17105.6219 | 18127.1435 | 13075.9647 | 13081.065 | 13186.2337 | 13463.104 | 13648.742 | 13830.3185 | 14042.6175 | 14239.5371 | 14430.5616 | 14452.6918 | 14675.5851 | 14507.2518 | 14507.2518 | 14507.2518 | 14507.2518 | 14507.2518 | 14507.2518 | 14507.2518 | 14507.2518 | 14507.2518 | 14507.2518 | 14507.2518 | 14507.2518 | 14507.2518 | 14507.2518 | 14507.2518 | 14507.2518
40% | 12836.6798 | 17057.1053 | 18206.7263 | 12764.1072 | 12763.7136 | 12895.1988 | 13039.4293 | 13335.2291 | 13547.7425 | 13663.2797 | 13789.8487 | 13905.5071 | 14114.0502 | 14372.753 | 14355.2689 | 14355.2689 | 14355.2689 | 14355.2689 | 14355.2689 | 14355.2689 | 14355.2689 | 14355.2689 | 14355.2689 | 14355.2689 | 14355.2689 | 14355.2689 | 14355.2689 | 14355.2689 | 14355.2689 | 14355.2689 |  | 13672.6523 | 17712.0843 | 18769.8229 | 13539.5597 | 13544.8408 | 13653.7382 | 13940.4246 | 14132.6442 | 14320.6583 | 14540.4842 | 14744.3853 | 14942.1824 | 14965.0973 | 15195.893 | 15021.5916 | 15021.5916 | 15021.5916 | 15021.5916 | 15021.5916 | 15021.5916 | 15021.5916 | 15021.5916 | 15021.5916 | 15021.5916 | 15021.5916 | 15021.5916 | 15021.5916 | 15021.5916 | 15021.5916 | 15021.5916
35% | 6655.3655 | 8843.5072 | 9439.545 | 6617.7391 | 6617.5351 | 6685.7055 | 6760.4839 | 6913.8457 | 7024.0264 | 7083.9284 | 7149.5499 | 7209.5147 | 7317.637 | 7451.7652 | 7442.7003 | 7442.7003 | 7442.7003 | 7442.7003 | 7442.7003 | 7442.7003 | 7442.7003 | 7442.7003 | 7442.7003 | 7442.7003 | 7442.7003 | 7442.7003 | 7442.7003 | 7442.7003 | 7442.7003 | 7442.7003 |  | 18622.1031 | 24123.7949 | 25564.4311 | 18440.8314 | 18448.0243 | 18596.3421 | 18986.808 | 19248.6104 | 19504.6849 | 19804.087 | 20081.7996 | 20351.1985 | 20382.4085 | 20696.7515 | 20459.3535 | 20459.3535 | 20459.3535 | 20459.3535 | 20459.3535 | 20459.3535 | 20459.3535 | 20459.3535 | 20459.3535 | 20459.3535 | 20459.3535 | 20459.3535 | 20459.3535 | 20459.3535 | 20459.3535 | 20459.3535
30% | 3095.428 | 4113.1385 | 4390.3573 | 3077.9279 | 3077.833 | 3109.5393 | 3144.3189 | 3215.6479 | 3266.8932 | 3294.7538 | 3325.2745 | 3353.1643 | 3403.4523 | 3465.8357 | 3461.6195 | 3461.6195 | 3461.6195 | 3461.6195 | 3461.6195 | 3461.6195 | 3461.6195 | 3461.6195 | 3461.6195 | 3461.6195 | 3461.6195 | 3461.6195 | 3461.6195 | 3461.6195 | 3461.6195 | 3461.6195 |  | 17207.9743 | 22291.8776 | 23623.1145 | 17040.4681 | 17047.1147 | 17184.1696 | 17544.9842 | 17786.9058 | 18023.5345 | 18300.2005 | 18556.8241 | 18805.7654 | 18834.6053 | 19125.0776 | 18905.7072 | 18905.7072 | 18905.7072 | 18905.7072 | 18905.7072 | 18905.7072 | 18905.7072 | 18905.7072 | 18905.7072 | 18905.7072 | 18905.7072 | 18905.7072 | 18905.7072 | 18905.7072 | 18905.7072 | 18905.7072
25% | 2113.496 | 2808.3682 | 2997.6476 | 2101.5473 | 2101.4825 | 2123.1309 | 2146.8777 | 2195.5797 | 2230.569 | 2249.5916 | 2270.4305 | 2289.4731 | 2323.8087 | 2366.4029 | 2363.5242 | 2363.5242 | 2363.5242 | 2363.5242 | 2363.5242 | 2363.5242 | 2363.5242 | 2363.5242 | 2363.5242 | 2363.5242 | 2363.5242 | 2363.5242 | 2363.5242 | 2363.5242 | 2363.5242 | 2363.5242 |  | 4963.476 | 6429.8794 | 6813.862 | 4915.1604 | 4917.0776 | 4956.6098 | 5060.6833 | 5130.4633 | 5198.7166 | 5278.5182 | 5352.5389 | 5424.3436 | 5432.6622 | 5516.4462 | 5453.1709 | 5453.1709 | 5453.1709 | 5453.1709 | 5453.1709 | 5453.1709 | 5453.1709 | 5453.1709 | 5453.1709 | 5453.1709 | 5453.1709 | 5453.1709 | 5453.1709 | 5453.1709 | 5453.1709 | 5453.1709
20% | 1280.3284 | 1701.2729 | 1815.9359 | 1273.09 | 1273.0507 | 1286.165 | 1300.5506 | 1330.0536 | 1351.2497 | 1362.7733 | 1375.3973 | 1386.933 | 1407.7331 | 1433.5361 | 1431.7922 | 1431.7922 | 1431.7922 | 1431.7922 | 1431.7922 | 1431.7922 | 1431.7922 | 1431.7922 | 1431.7922 | 1431.7922 | 1431.7922 | 1431.7922 | 1431.7922 | 1431.7922 | 1431.7922 | 1431.7922 |  | 1331.912 | 1725.4105 | 1828.4494 | 1318.9469 | 1319.4613 | 1330.0695 | 1357.9969 | 1376.7218 | 1395.0371 | 1416.4513 | 1436.3141 | 1455.5824 | 1457.8146 | 1480.2975 | 1463.318 | 1463.318 | 1463.318 | 1463.318 | 1463.318 | 1463.318 | 1463.318 | 1463.318 | 1463.318 | 1463.318 | 1463.318 | 1463.318 | 1463.318 | 1463.318 | 1463.318 | 1463.318
15% | 819.7224 | 1089.2296 | 1162.6419 | 815.0881 | 815.063 | 823.4593 | 832.6696 | 851.5587 | 865.1294 | 872.5073 | 880.5897 | 887.9754 | 901.2925 | 917.8127 | 916.6962 | 916.6962 | 916.6962 | 916.6962 | 916.6962 | 916.6962 | 916.6962 | 916.6962 | 916.6962 | 916.6962 | 916.6962 | 916.6962 | 916.6962 | 916.6962 | 916.6962 | 916.6962 |  | 734.6312 | 951.6698 | 1008.502 | 727.4801 | 727.7639 | 733.615 | 749.0186 | 759.3466 | 769.4486 | 781.2598 | 792.2154 | 802.843 | 804.0742 | 816.4749 | 807.1097 | 807.1097 | 807.1097 | 807.1097 | 807.1097 | 807.1097 | 807.1097 | 807.1097 | 807.1097 | 807.1097 | 807.1097 | 807.1097 | 807.1097 | 807.1097 | 807.1097 | 807.1097
10% | 548.6502 | 729.0346 | 778.1704 | 545.5484 | 545.5316 | 551.1514 | 557.3159 | 569.9586 | 579.0416 | 583.9798 | 589.3894 | 594.3328 | 603.2461 | 614.3032 | 613.5559 | 613.5559 | 613.5559 | 613.5559 | 613.5559 | 613.5559 | 613.5559 | 613.5559 | 613.5559 | 613.5559 | 613.5559 | 613.5559 | 613.5559 | 613.5559 | 613.5559 | 613.5559 |  | 171.688 | 222.4113 | 235.6934 | 170.0168 | 170.0831 | 171.4505 | 175.0504 | 177.4641 | 179.825 | 182.5854 | 185.1458 | 187.6295 | 187.9173 | 190.8154 | 188.6267 | 188.6267 | 188.6267 | 188.6267 | 188.6267 | 188.6267 | 188.6267 | 188.6267 | 188.6267 | 188.6267 | 188.6267 | 188.6267 | 188.6267 | 188.6267 | 188.6267 | 188.6267
5% | 390.344 | 518.6808 | 553.639 | 388.1372 | 388.1252 | 392.1235 | 396.5093 | 405.5041 | 411.9664 | 415.4797 | 419.3284 | 422.8454 | 429.1869 | 437.0537 | 436.522 | 436.522 | 436.522 | 436.522 | 436.522 | 436.522 | 436.522 | 436.522 | 436.522 | 436.522 | 436.522 | 436.522 | 436.522 | 436.522 | 436.522 | 436.522 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9.992e-14% | 34.2635 | 45.5286 | 48.5972 | 34.0698 | 34.0688 | 34.4197 | 34.8047 | 35.5943 | 36.1615 | 36.4699 | 36.8077 | 37.1164 | 37.6731 | 38.3636 | 38.3169 | 38.3169 | 38.3169 | 38.3169 | 38.3169 | 38.3169 | 38.3169 | 38.3169 | 38.3169 | 38.3169 | 38.3169 | 38.3169 | 38.3169 | 38.3169 | 38.3169 | 38.3169 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E @ R (MWh) | 91763.8061 | 121933.7811 | 130151.918 | 91245.0165 | 91242.2028 | 92182.133 | 93213.1731 | 95327.7164 | 96846.8823 | 97672.8072 | 98577.593 | 99404.3848 | 100895.1682 | 102744.521 | 102619.5345 | 102619.5345 | 102619.5345 | 102619.5345 | 102619.5345 | 102619.5345 | 102619.5345 | 102619.5345 | 102619.5345 | 102619.5345 | 102619.5345 | 102619.5345 | 102619.5345 | 102619.5345 | 102619.5345 | 102619.5345 | E @ R (MWh) | 89067.5772 | 115381.5956 | 122272.0083 | 88200.5739 | 88234.9764 | 88944.3653 | 90811.923 | 92064.0967 | 93288.8743 | 94720.8832 | 96049.1535 | 97337.6605 | 97486.9344 | 98990.4043 | 97854.9545 | 97854.9545 | 97854.9545 | 97854.9545 | 97854.9545 | 97854.9545 | 97854.9545 | 97854.9545 | 97854.9545 | 97854.9545 | 97854.9545 | 97854.9545 | 97854.9545 | 97854.9545 | 97854.9545 | 97854.9545
Option 2 Summer POE50 W E @ R (MWh) N 2 | 64234.6643 | 85353.6468 | 91106.3426 | 63871.5115 | 63869.5419 | 64527.4931 | 65249.2212 | 66729.4015 | 67792.8176 | 68370.965 | 69004.3151 | 69583.0694 | 70626.6178 | 71921.1647 | 71833.6741 | 71833.6741 | 71833.6741 | 71833.6741 | 71833.6741 | 71833.6741 | 71833.6741 | 71833.6741 | 71833.6741 | 71833.6741 | 71833.6741 | 71833.6741 | 71833.6741 | 71833.6741 | 71833.6741 | 71833.6741 | Option 2 Summer POE10 W E @ R (MWh) N 2 | 26720.2732 | 34614.4787 | 36681.6025 | 26460.1722 | 26470.4929 | 26683.3096 | 27243.5769 | 27619.229 | 27986.6623 | 28416.2649 | 28814.746 | 29201.2982 | 29246.0803 | 29697.1213 | 29356.4864 | 29356.4864 | 29356.4864 | 29356.4864 | 29356.4864 | 29356.4864 | 29356.4864 | 29356.4864 | 29356.4864 | 29356.4864 | 29356.4864 | 29356.4864 | 29356.4864 | 29356.4864 | 29356.4864 | 29356.4864
Option 3 - 2B PHM 3rd Tx + Switchroom + Two new feeders + OFR12 New Feeder
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | 59.6718 | 82.8348 | 88.8563 | 23.0131 | 23.8136 | 25.192 | 28.3279 | 30.427 | 33.0862 | 34.4665 | 35.6808 | 33.4434 | 36.0656 | 40.188 | 37.0597 | 37.0597 | 37.0597 | 37.0597 | 37.0597 | 37.0597 | 37.0597 | 37.0597 | 37.0597 | 37.0597 | 37.0597 | 37.0597 | 37.0597 | 37.0597 | 37.0597 | 37.0597 |  | 63.8857 | 86.7566 | 93.0131 | 27.1115 | 27.7262 | 29.0747 | 32.2596 | 33.9985 | 37.311 | 47.3802 | 39.0792 | 37.4555 | 39.6472 | 44.4406 | 41.196 | 41.196 | 41.196 | 41.196 | 41.196 | 41.196 | 41.196 | 41.196 | 41.196 | 41.196 | 41.196 | 41.196 | 41.196 | 41.196 | 41.196 | 41.196
98% | 70.8865 | 98.4027 | 105.556 | 26.5317 | 27.4827 | 29.1201 | 32.8453 | 35.339 | 38.4979 | 40.1377 | 41.5802 | 38.9223 | 42.0373 | 46.9344 | 43.2182 | 43.2182 | 43.2182 | 43.2182 | 43.2182 | 43.2182 | 43.2182 | 43.2182 | 43.2182 | 43.2182 | 43.2182 | 43.2182 | 43.2182 | 43.2182 | 43.2182 | 43.2182 |  | 75.8924 | 103.0616 | 110.494 | 31.4004 | 32.1306 | 33.7325 | 37.516 | 39.5816 | 43.5167 | 55.4783 | 45.6172 | 43.6884 | 46.2921 | 51.9863 | 48.1319 | 48.1319 | 48.1319 | 48.1319 | 48.1319 | 48.1319 | 48.1319 | 48.1319 | 48.1319 | 48.1319 | 48.1319 | 48.1319 | 48.1319 | 48.1319 | 48.1319 | 48.1319
97% | 140.3338 | 194.8074 | 208.9687 | 50.8953 | 52.778 | 56.0196 | 63.3944 | 68.331 | 74.5849 | 77.831 | 80.6868 | 75.4249 | 81.5917 | 91.2865 | 83.9295 | 83.9295 | 83.9295 | 83.9295 | 83.9295 | 83.9295 | 83.9295 | 83.9295 | 83.9295 | 83.9295 | 83.9295 | 83.9295 | 83.9295 | 83.9295 | 83.9295 | 83.9295 |  | 150.2438 | 204.0305 | 218.7445 | 60.5339 | 61.9795 | 65.1508 | 72.6409 | 76.7303 | 84.5206 | 108.2009 | 88.6789 | 84.8604 | 90.0149 | 101.2877 | 93.6573 | 93.6573 | 93.6573 | 93.6573 | 93.6573 | 93.6573 | 93.6573 | 93.6573 | 93.6573 | 93.6573 | 93.6573 | 93.6573 | 93.6573 | 93.6573 | 93.6573 | 93.6573
95% | 414.5243 | 575.4311 | 617.2612 | 142.9299 | 148.491 | 158.0661 | 179.8503 | 194.4323 | 212.9052 | 222.4938 | 230.9293 | 215.3866 | 233.6022 | 262.2393 | 240.5077 | 240.5077 | 240.5077 | 240.5077 | 240.5077 | 240.5077 | 240.5077 | 240.5077 | 240.5077 | 240.5077 | 240.5077 | 240.5077 | 240.5077 | 240.5077 | 240.5077 | 240.5077 |  | 443.7972 | 602.6746 | 646.1375 | 171.4008 | 175.6708 | 185.0382 | 207.1629 | 219.2424 | 242.2537 | 312.2017 | 254.5367 | 243.2574 | 258.483 | 291.781 | 269.2421 | 269.2421 | 269.2421 | 269.2421 | 269.2421 | 269.2421 | 269.2421 | 269.2421 | 269.2421 | 269.2421 | 269.2421 | 269.2421 | 269.2421 | 269.2421 | 269.2421 | 269.2421
90% | 2285.5212 | 3172.6969 | 3403.3313 | 687.6144 | 718.2763 | 771.0693 | 891.1785 | 971.578 | 1073.4303 | 1126.2977 | 1172.8081 | 1087.1114 | 1187.5452 | 1345.4387 | 1225.6194 | 1225.6194 | 1225.6194 | 1225.6194 | 1225.6194 | 1225.6194 | 1225.6194 | 1225.6194 | 1225.6194 | 1225.6194 | 1225.6194 | 1225.6194 | 1225.6194 | 1225.6194 | 1225.6194 | 1225.6194 |  | 2446.9201 | 3322.9067 | 3562.5435 | 844.5915 | 868.1346 | 919.783 | 1041.7693 | 1108.3709 | 1235.246 | 1620.9111 | 1302.9695 | 1240.7798 | 1324.7279 | 1508.32 | 1384.049 | 1384.049 | 1384.049 | 1384.049 | 1384.049 | 1384.049 | 1384.049 | 1384.049 | 1384.049 | 1384.049 | 1384.049 | 1384.049 | 1384.049 | 1384.049 | 1384.049 | 1384.049
85% | 5583.3646 | 7750.6712 | 8314.0946 | 1295.2018 | 1370.1065 | 1499.0762 | 1792.4944 | 1988.9045 | 2237.7224 | 2366.8736 | 2480.4952 | 2271.1443 | 2516.4968 | 2902.2195 | 2609.5095 | 2609.5095 | 2609.5095 | 2609.5095 | 2609.5095 | 2609.5095 | 2609.5095 | 2609.5095 | 2609.5095 | 2609.5095 | 2609.5095 | 2609.5095 | 2609.5095 | 2609.5095 | 2609.5095 | 2609.5095 |  | 5977.6505 | 8117.623 | 8703.0385 | 1678.6856 | 1736.1996 | 1862.3729 | 2160.3768 | 2323.0798 | 2633.0266 | 3575.1786 | 2798.4702 | 2646.5452 | 2851.6243 | 3300.1267 | 2996.5417 | 2996.5417 | 2996.5417 | 2996.5417 | 2996.5417 | 2996.5417 | 2996.5417 | 2996.5417 | 2996.5417 | 2996.5417 | 2996.5417 | 2996.5417 | 2996.5417 | 2996.5417 | 2996.5417 | 2996.5417
80% | 8678.2039 | 12046.8408 | 12922.5678 | 1342.9024 | 1459.3265 | 1659.7836 | 2115.8425 | 2421.1221 | 2807.8589 | 3008.5981 | 3185.1997 | 2859.8064 | 3241.1569 | 3840.6843 | 3385.7262 | 3385.7262 | 3385.7262 | 3385.7262 | 3385.7262 | 3385.7262 | 3385.7262 | 3385.7262 | 3385.7262 | 3385.7262 | 3385.7262 | 3385.7262 | 3385.7262 | 3385.7262 | 3385.7262 | 3385.7262 |  | 9291.041 | 12617.1926 | 13527.1019 | 1938.9499 | 2028.3437 | 2224.4544 | 2687.6409 | 2940.5296 | 3422.2787 | 4886.6623 | 3679.4272 | 3443.2907 | 3762.0443 | 4459.1501 | 3987.2889 | 3987.2889 | 3987.2889 | 3987.2889 | 3987.2889 | 3987.2889 | 3987.2889 | 3987.2889 | 3987.2889 | 3987.2889 | 3987.2889 | 3987.2889 | 3987.2889 | 3987.2889 | 3987.2889 | 3987.2889
75% | 9574.4808 | 13291.0275 | 14257.1987 | 646.7384 | 775.1867 | 996.3469 | 1499.5071 | 1836.3156 | 2262.9943 | 2484.4657 | 2679.3065 | 2320.3068 | 2741.0429 | 3402.4889 | 2900.5432 | 2900.5432 | 2900.5432 | 2900.5432 | 2900.5432 | 2900.5432 | 2900.5432 | 2900.5432 | 2900.5432 | 2900.5432 | 2900.5432 | 2900.5432 | 2900.5432 | 2900.5432 | 2900.5432 | 2900.5432 |  | 10250.6112 | 13920.2847 | 14924.1686 | 1304.3452 | 1402.9715 | 1619.3363 | 2130.3603 | 2409.3671 | 2940.8708 | 4556.4946 | 3224.5773 | 2964.0529 | 3315.7271 | 4084.8293 | 3564.2347 | 3564.2347 | 3564.2347 | 3564.2347 | 3564.2347 | 3564.2347 | 3564.2347 | 3564.2347 | 3564.2347 | 3564.2347 | 3564.2347 | 3564.2347 | 3564.2347 | 3564.2347 | 3564.2347 | 3564.2347
70% | 10287.2444 | 14280.4661 | 15318.563 | 20.3356 | 57.2151 | 162.8454 | 590.4033 | 952.2853 | 1410.7277 | 1648.6863 | 1858.0319 | 1472.3068 | 1924.3642 | 2635.0509 | 2095.7384 | 2095.7384 | 2095.7384 | 2095.7384 | 2095.7384 | 2095.7384 | 2095.7384 | 2095.7384 | 2095.7384 | 2095.7384 | 2095.7384 | 2095.7384 | 2095.7384 | 2095.7384 | 2095.7384 | 2095.7384 |  | 11013.7087 | 14956.5677 | 16035.1849 | 394.8873 | 489.2265 | 719.1532 | 1268.2198 | 1567.9971 | 2139.0681 | 3874.9655 | 2443.8949 | 2163.976 | 2541.8303 | 3368.1876 | 2808.8378 | 2808.8378 | 2808.8378 | 2808.8378 | 2808.8378 | 2808.8378 | 2808.8378 | 2808.8378 | 2808.8378 | 2808.8378 | 2808.8378 | 2808.8378 | 2808.8378 | 2808.8378 | 2808.8378 | 2808.8378
65% | 10840.7831 | 15048.8731 | 16142.8282 |  |  |  | 0.29965 | 68.3879 | 317.4877 | 514.195 | 722.9957 | 364.1065 | 792.8973 | 1541.8248 | 973.4927 | 973.4927 | 973.4927 | 973.4927 | 973.4927 | 973.4927 | 973.4927 | 973.4927 | 973.4927 | 973.4927 | 973.4927 | 973.4927 | 973.4927 | 973.4927 | 973.4927 | 973.4927 |  | 11606.3372 | 15761.3546 | 16898.0103 |  |  | 10.9834 | 221.3321 | 442.5144 | 1019.154 | 2848.457 | 1340.383 | 1045.4021 | 1443.5881 | 2314.4103 | 1724.9628 | 1724.9628 | 1724.9628 | 1724.9628 | 1724.9628 | 1724.9628 | 1724.9628 | 1724.9628 | 1724.9628 | 1724.9628 | 1724.9628 | 1724.9628 | 1724.9628 | 1724.9628 | 1724.9628 | 1724.9628
60% | 11934.3669 | 16566.9557 | 17771.2656 | [7 empty] | 0.46825 |  | 4.3158 | 278.4473 | 31.955 | 31.955 | 31.955 | 31.955 | 31.955 | 31.955 | 31.955 | 31.955 | 31.955 | 31.955 | 31.955 | 31.955 | 31.955 | 31.955 | 31.955 | 31.955 |  | 12777.1477 | 17351.3101 | 18602.628 | [5 empty] | 42.9218 | 1558.6668 | 164.1701 | 49.9432 | 219.1162 | 970.7471 | 407.0032 | 407.0032 | 407.0032 | 407.0032 | 407.0032 | 407.0032 | 407.0032 | 407.0032 | 407.0032 | 407.0032 | 407.0032 | 407.0032 | 407.0032 | 407.0032 | 407.0032 | 407.0032
55% | FY25: 13276.2336; FY26: 18429.6976; FY27: 19769.4166 |  | 14213.7742 | 19302.2426 | 20694.2551 | [6 empty] | 137.453 |  |  |  | 2.187
50% | FY25: 13456.7484; FY26: 18680.2832; FY27: 20038.2182 |  | 14407.0366 | 19564.692 | 20975.6315
45% | FY25: 10386.1977; FY26: 14417.8303; FY27: 15465.9127 |  | 11119.6499 | 15100.4354 | 16189.4278
40% | FY25: 5102.6915; FY26: 7083.4142; FY27: 7598.3323 |  | 5463.0332 | 7418.775 | 7953.792
35% | FY25: 1907.0998; FY26: 2647.3829; FY27: 2839.8304 |  | 2041.7754 | 2772.7219 | 2972.6813
30% | FY25: 951.1511; FY26: 1320.3614; FY27: 1416.3431 |  | 1018.3194 | 1382.8733 | 1482.6014
25% | FY25: 560.7353; FY26: 778.3972; FY27: 834.9816 |  | 600.3333 | 815.25 | 874.0431
20% | FY25: 283.3663; FY26: 393.3611; FY27: 421.9559 |  | 303.377 | 411.9846 | 441.6956
15% | FY25: 115.4455; FY26: 160.2582; FY27: 171.908 |  | 123.598 | 167.8456 | 179.95
10% | FY25: 46.4781; FY26: 64.5196; FY27: 69.2097 |  | 49.7602 | 67.5742 | 72.4474
5% | FY25: 39.5813; FY26: 54.9457; FY27: 58.9399 |  | 42.3765 | 57.5471 | 61.6972
9.992e-14% | FY25: 0; FY26: 0; FY27: 0 |  | 0 | 0 | 0
E @ R (MWh) | 105995.1099 | 147139.4588 | 157835.5397 | 4236.1627 | 4632.6765 | 5357.5192 | 7194.1433 | 8567.1227 | 10469.2957 | 11524.0454 | 12488.1823 | 10737.9594 | 12801.116 | 16386.8026 | 13627.2995 | 13627.2995 | 13627.2995 | 13627.2995 | 13627.2995 | 13627.2995 | 13627.2995 | 13627.2995 | 13627.2995 | 13627.2995 | 13627.2995 | 13627.2995 | 13627.2995 | 13627.2995 | 13627.2995 | 13627.2995 | E @ R (MWh) | 113480.2695 | 154105.704 | 165219.287 | 6451.9061 | 6822.3831 | 7669.0794 | 9859.2785 | 11161.4117 | 13840.1679 | 23582.05 | 15381.8041 | 13963.2515 | 15893.0952 | 20497.4537 | 17325.1454 | 17325.1454 | 17325.1454 | 17325.1454 | 17325.1454 | 17325.1454 | 17325.1454 | 17325.1454 | 17325.1454 | 17325.1454 | 17325.1454 | 17325.1454 | 17325.1454 | 17325.1454 | 17325.1454 | 17325.1454
Option 3 Winter POE50 W E @ R (MWh) N 2 | 74196.5769 | 102997.6211 | 110484.8778 | 2965.3139 | 3242.8735 | 3750.2634 | 5035.9003 | 5996.9859 | 7328.507 | 8066.8318 | 8741.7276 | 7516.5716 | 8960.7812 | 11470.7618 | 9539.1096 | 9539.1096 | 9539.1096 | 9539.1096 | 9539.1096 | 9539.1096 | 9539.1096 | 9539.1096 | 9539.1096 | 9539.1096 | 9539.1096 | 9539.1096 | 9539.1096 | 9539.1096 | 9539.1096 | 9539.1096 | Option 3 Winter POE10 W E @ R (MWh) N 2 | 34044.0809 | 46231.7112 | 49565.7861 | 1935.5718 | 2046.7149 | 2300.7238 | 2957.7835 | 3348.4235 | 4152.0504 | 7074.615 | 4614.5412 | 4188.9754 | 4767.9286 | 6149.2361 | 5197.5436 | 5197.5436 | 5197.5436 | 5197.5436 | 5197.5436 | 5197.5436 | 5197.5436 | 5197.5436 | 5197.5436 | 5197.5436 | 5197.5436 | 5197.5436 | 5197.5436 | 5197.5436 | 5197.5436 | 5197.5436
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 76.9936 | 99.7405 | 105.6969 | 37.273 | 37.3028 | 37.916 | 39.5304 | 40.6128 | 41.6716 | 42.9095 | 44.0577 | 45.1715 | 45.3005 | 46.6002 | 45.6187 | 45.6187 | 45.6187 | 45.6187 | 45.6187 | 45.6187 | 45.6187 | 45.6187 | 45.6187 | 45.6187 | 45.6187 | 45.6187 | 45.6187 | 45.6187 | 45.6187 | 45.6187
98% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 38.1099 | 49.369 | 52.3173 | 18.1072 | 18.1219 | 18.4254 | 19.2245 | 19.7603 | 20.2843 | 20.897 | 21.4654 | 22.0167 | 22.0806 | 22.7239 | 22.238 | 22.238 | 22.238 | 22.238 | 22.238 | 22.238 | 22.238 | 22.238 | 22.238 | 22.238 | 22.238 | 22.238 | 22.238 | 22.238 | 22.238 | 22.238
97% | 16.9149 | 22.4762 | 23.991 | 6.9303 | 6.9298 | 7.103 | 7.2931 | 7.6829 | 7.9629 | 8.1151 | 8.2819 | 8.4343 | 8.7091 | 9.05 | 9.027 | 9.027 | 9.027 | 9.027 | 9.027 | 9.027 | 9.027 | 9.027 | 9.027 | 9.027 | 9.027 | 9.027 | 9.027 | 9.027 | 9.027 | 9.027 |  | 75.446 | 97.7357 | 103.5723 | 35.1556 | 35.1847 | 35.7856 | 37.3676 | 38.4283 | 39.4657 | 40.6787 | 41.8039 | 42.8953 | 43.0218 | 44.2953 | 43.3335 | 43.3335 | 43.3335 | 43.3335 | 43.3335 | 43.3335 | 43.3335 | 43.3335 | 43.3335 | 43.3335 | 43.3335 | 43.3335 | 43.3335 | 43.3335 | 43.3335 | 43.3335
95% | 83.2734 | 110.6519 | 118.1097 | 32.8093 | 32.8067 | 33.6597 | 34.5953 | 36.5142 | 37.8928 | 38.6423 | 39.4634 | 40.2137 | 41.5666 | 43.2448 | 43.1314 | 43.1314 | 43.1314 | 43.1314 | 43.1314 | 43.1314 | 43.1314 | 43.1314 | 43.1314 | 43.1314 | 43.1314 | 43.1314 | 43.1314 | 43.1314 | 43.1314 | 43.1314 |  | 111.4279 | 144.3481 | 152.9683 | 50.3513 | 50.3943 | 51.2818 | 53.6182 | 55.1847 | 56.717 | 58.5085 | 60.1702 | 61.7822 | 61.969 | 63.8499 | 62.4294 | 62.4294 | 62.4294 | 62.4294 | 62.4294 | 62.4294 | 62.4294 | 62.4294 | 62.4294 | 62.4294 | 62.4294 | 62.4294 | 62.4294 | 62.4294 | 62.4294 | 62.4294
90% | 144.4273 | 191.9119 | 204.8464 | 51.3198 | 51.3153 | 52.7947 | 54.4175 | 57.7455 | 60.1366 | 61.4365 | 62.8605 | 64.1618 | 66.5082 | 69.4189 | 69.2222 | 69.2222 | 69.2222 | 69.2222 | 69.2222 | 69.2222 | 69.2222 | 69.2222 | 69.2222 | 69.2222 | 69.2222 | 69.2222 | 69.2222 | 69.2222 | 69.2222 | 69.2222 |  | 483.1446 | 625.8842 | 663.261 | 201.5685 | 201.7552 | 205.6032 | 215.7337 | 222.5261 | 229.1699 | 236.9378 | 244.1429 | 251.1324 | 251.9421 | 260.0977 | 253.9385 | 253.9385 | 253.9385 | 253.9385 | 253.9385 | 253.9385 | 253.9385 | 253.9385 | 253.9385 | 253.9385 | 253.9385 | 253.9385 | 253.9385 | 253.9385 | 253.9385 | 253.9385
85% | 409.8612 | 544.6148 | 581.321 | 120.801 | 120.7884 | 124.9866 | 129.5917 | 139.0363 | 145.8216 | 149.5106 | 153.5518 | 157.2446 | 163.9032 | 172.1633 | 171.605 | 171.605 | 171.605 | 171.605 | 171.605 | 171.605 | 171.605 | 171.605 | 171.605 | 171.605 | 171.605 | 171.605 | 171.605 | 171.605 | 171.605 | 171.605 |  | 457.0286 | 592.0526 | 627.4091 | 165.8367 | 166.0133 | 169.6533 | 179.2362 | 185.6615 | 191.9461 | 199.2941 | 206.1098 | 212.7215 | 213.4874 | 221.2021 | 215.3759 | 215.3759 | 215.3759 | 215.3759 | 215.3759 | 215.3759 | 215.3759 | 215.3759 | 215.3759 | 215.3759 | 215.3759 | 215.3759 | 215.3759 | 215.3759 | 215.3759 | 215.3759
80% | 572.5046 | 760.7318 | 812.0039 | 129.841 | 129.8234 | 135.6876 | 142.1201 | 155.3125 | 164.7904 | 169.9433 | 175.5881 | 180.7464 | 190.0472 | 201.5852 | 200.8054 | 200.8054 | 200.8054 | 200.8054 | 200.8054 | 200.8054 | 200.8054 | 200.8054 | 200.8054 | 200.8054 | 200.8054 | 200.8054 | 200.8054 | 200.8054 | 200.8054 | 200.8054 |  | 319.1946 | 413.4971 | 438.1905 | 96.374 | 96.4973 | 99.0396 | 105.7324 | 110.2199 | 114.6092 | 119.7411 | 124.5013 | 129.1189 | 129.6539 | 135.0419 | 130.9728 | 130.9728 | 130.9728 | 130.9728 | 130.9728 | 130.9728 | 130.9728 | 130.9728 | 130.9728 | 130.9728 | 130.9728 | 130.9728 | 130.9728 | 130.9728 | 130.9728 | 130.9728
75% | 1492.4153 | 1983.0895 | 2116.7465 | 223.9912 | 223.9454 | 239.2321 | 256.0006 | 290.3908 | 315.098 | 328.5306 | 343.2457 | 356.6924 | 380.938 | 411.0152 | 408.9825 | 408.9825 | 408.9825 | 408.9825 | 408.9825 | 408.9825 | 408.9825 | 408.9825 | 408.9825 | 408.9825 | 408.9825 | 408.9825 | 408.9825 | 408.9825 | 408.9825 | 408.9825 |  | 569.714 | 738.0296 | 782.1036 | 132.8215 | 133.0415 | 137.5791 | 149.5248 | 157.5342 | 165.3684 | 174.5281 | 183.0243 | 191.2662 | 192.221 | 201.8378 | 194.575 | 194.575 | 194.575 | 194.575 | 194.575 | 194.575 | 194.575 | 194.575 | 194.575 | 194.575 | 194.575 | 194.575 | 194.575 | 194.575 | 194.575 | 194.575
70% | 2578.4391 | 3426.1747 | 3657.0932 | 161.9198 | 161.8408 | 188.2515 | 217.2224 | 276.6382 | 319.3247 | 342.5321 | 367.9553 | 391.1871 | 433.0761 | 485.0404 | 481.5284 | 481.5284 | 481.5284 | 481.5284 | 481.5284 | 481.5284 | 481.5284 | 481.5284 | 481.5284 | 481.5284 | 481.5284 | 481.5284 | 481.5284 | 481.5284 | 481.5284 | 481.5284 |  | 1037.8661 | 1344.492 | 1424.783 | 160.7208 | 161.1217 | 169.3879 | 191.1497 | 205.7408 | 220.0126 | 236.6991 | 252.1769 | 267.1913 | 268.9307 | 286.45 | 273.2191 | 273.2191 | 273.2191 | 273.2191 | 273.2191 | 273.2191 | 273.2191 | 273.2191 | 273.2191 | 273.2191 | 273.2191 | 273.2191 | 273.2191 | 273.2191 | 273.2191 | 273.2191
65% | 6475.8072 | 8604.914 | 9184.8711 | 6.9591 | 6.9298 | 20.0951 | 42.2143 | 111.9423 | 181.5617 | 226.0382 | 279.9918 | 333.9879 | 438.672 | 569.1816 | 560.3612 | 560.3612 | 560.3612 | 560.3612 | 560.3612 | 560.3612 | 560.3612 | 560.3612 | 560.3612 | 560.3612 | 560.3612 | 560.3612 | 560.3612 | 560.3612 | 560.3612 | 560.3612 |  | 1305.7961 | 1691.5789 | 1792.5974 | 84.8503 | 85.3547 | 95.7548 | 123.1346 | 141.4924 | 159.4485 | 180.4428 | 199.9162 | 218.8067 | 220.9952 | 243.0371 | 226.3906 | 226.3906 | 226.3906 | 226.3906 | 226.3906 | 226.3906 | 226.3906 | 226.3906 | 226.3906 | 226.3906 | 226.3906 | 226.3906 | 226.3906 | 226.3906 | 226.3906 | 226.3906
60% | 9465.8424 | 12578.0087 | 13425.7459 | [9 empty] | 5.9059 | 42.5222 | 39.014 | 39.014 | 39.014 | 39.014 | 39.014 | 39.014 | 39.014 | 39.014 | 39.014 | 39.014 | 39.014 | 39.014 | 39.014 | 39.014 | 39.014 | 39.014 |  | 2043.3291 | 2647.0078 | 2805.083 | 2.2281 | 2.3448 | 5.4041 | 19.2874 | 33.1836 | 50.2166 | 74.3153 | 100.576 | 129.3594 | 132.7839 | 167.2756 | 141.2268 | 141.2268 | 141.2268 | 141.2268 | 141.2268 | 141.2268 | 141.2268 | 141.2268 | 141.2268 | 141.2268 | 141.2268 | 141.2268 | 141.2268 | 141.2268 | 141.2268 | 141.2268
55% | FY25: 10703.6666; FY26: 14222.8031; FY27: 15181.3967 |  | 3926.5772 | 5086.6405 | 5390.4069 | [8 empty] | 0.36348 | 0.67093 | 8.8993 | 1.8255 | 1.8255 | 1.8255 | 1.8255 | 1.8255 | 1.8255 | 1.8255 | 1.8255 | 1.8255 | 1.8255 | 1.8255 | 1.8255 | 1.8255 | 1.8255 | 1.8255 | 1.8255
50% | FY25: 13744.0128; FY26: 18262.75; FY27: 19493.6294 |  | 8714.0125 | 11288.47 | 11962.6002
45% | FY25: 18302.3635; FY26: 24319.7888; FY27: 25958.9027 |  | 13204.5002 | 17105.6219 | 18127.1435
40% | FY25: 12836.6798; FY26: 17057.1053; FY27: 18206.7263 |  | 13672.6523 | 17712.0843 | 18769.8229
35% | FY25: 6655.3655; FY26: 8843.5072; FY27: 9439.545 |  | 18622.1031 | 24123.7949 | 25564.4311
30% | FY25: 3095.428; FY26: 4113.1385; FY27: 4390.3573 |  | 17207.9743 | 22291.8776 | 23623.1145
25% | FY25: 2113.496; FY26: 2808.3682; FY27: 2997.6476 |  | 4963.476 | 6429.8794 | 6813.862
20% | FY25: 1280.3284; FY26: 1701.2729; FY27: 1815.9359 |  | 1331.912 | 1725.4105 | 1828.4494
15% | FY25: 819.7224; FY26: 1089.2296; FY27: 1162.6419 |  | 734.6312 | 951.6698 | 1008.502
10% | FY25: 548.6502; FY26: 729.0346; FY27: 778.1704 |  | 171.688 | 222.4113 | 235.6934
5% | FY25: 390.344; FY26: 518.6808; FY27: 553.639 |  | 0 | 0 | 0
9.992e-14% | FY25: 34.2635; FY26: 45.5286; FY27: 48.5972 |  | 0 | 0 | 0
E @ R (MWh) | 91763.8061 | 121933.7811 | 130151.918 | 734.5714 | 734.3797 | 801.8103 | 883.4549 | 1075.2627 | 1232.5888 | 1324.7487 | 1430.9386 | 1532.6682 | 1729.3262 | 2003.2214 | 1983.6771 | 1983.6771 | 1983.6771 | 1983.6771 | 1983.6771 | 1983.6771 | 1983.6771 | 1983.6771 | 1983.6771 | 1983.6771 | 1983.6771 | 1983.6771 | 1983.6771 | 1983.6771 | 1983.6771 | 1983.6771 | E @ R (MWh) | 89067.5772 | 115381.5956 | 122272.0083 | 985.2871 | 987.1322 | 1025.8309 | 1133.5396 | 1210.3445 | 1288.9099 | 1384.9521 | 1477.9447 | 1571.8256 | 1583.0571 | 1701.3108 | 1611.1437 | 1611.1437 | 1611.1437 | 1611.1437 | 1611.1437 | 1611.1437 | 1611.1437 | 1611.1437 | 1611.1437 | 1611.1437 | 1611.1437 | 1611.1437 | 1611.1437 | 1611.1437 | 1611.1437 | 1611.1437
Option 3 Summer POE50 W E @ R (MWh) N 2 | 64234.6643 | 85353.6468 | 91106.3426 | 514.2 | 514.0658 | 561.2672 | 618.4185 | 752.6839 | 862.8122 | 927.3241 | 1001.657 | 1072.8678 | 1210.5283 | 1402.255 | 1388.5739 | 1388.5739 | 1388.5739 | 1388.5739 | 1388.5739 | 1388.5739 | 1388.5739 | 1388.5739 | 1388.5739 | 1388.5739 | 1388.5739 | 1388.5739 | 1388.5739 | 1388.5739 | 1388.5739 | 1388.5739 | Option 3 Summer POE10 W E @ R (MWh) N 2 | 26720.2732 | 34614.4787 | 36681.6025 | 295.5861 | 296.1396 | 307.7493 | 340.0619 | 363.1034 | 386.673 | 415.4856 | 443.3834 | 471.5477 | 474.9171 | 510.3932 | 483.3431 | 483.3431 | 483.3431 | 483.3431 | 483.3431 | 483.3431 | 483.3431 | 483.3431 | 483.3431 | 483.3431 | 483.3431 | 483.3431 | 483.3431 | 483.3431 | 483.3431 | 483.3431
Option 4 - 3B OFR 3rd Tx + Switchroom + Two new feeders + OFR12 New Feeder
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | 59.6718 | 82.8348 | 88.8563 | 83.9685 | 84.769 | 86.1474 | 89.2833 | 91.3824 | 94.0416 | 95.4219 | 96.6362 | 94.3988 | 97.021 | 101.1434 | 98.0151 | 98.0151 | 98.0151 | 98.0151 | 98.0151 | 98.0151 | 98.0151 | 98.0151 | 98.0151 | 98.0151 | 98.0151 | 98.0151 | 98.0151 | 98.0151 | 98.0151 | 98.0151 |  | 63.8857 | 86.7566 | 93.0131 | 88.067 | 88.6816 | 90.0301 | 93.215 | 94.9539 | 98.2664 | 108.3356 | 100.0346 | 98.4109 | 100.6027 | 105.396 | 102.1515 | 102.1515 | 102.1515 | 102.1515 | 102.1515 | 102.1515 | 102.1515 | 102.1515 | 102.1515 | 102.1515 | 102.1515 | 102.1515 | 102.1515 | 102.1515 | 102.1515 | 102.1515
98% | 70.8865 | 98.4027 | 105.556 | 99.7495 | 100.7005 | 102.3379 | 106.0632 | 108.5568 | 111.7158 | 113.3555 | 114.798 | 112.1401 | 115.2551 | 120.1523 | 116.436 | 116.436 | 116.436 | 116.436 | 116.436 | 116.436 | 116.436 | 116.436 | 116.436 | 116.436 | 116.436 | 116.436 | 116.436 | 116.436 | 116.436 | 116.436 |  | 75.8924 | 103.0616 | 110.494 | 104.6182 | 105.3484 | 106.9503 | 110.7338 | 112.7995 | 116.7346 | 128.6962 | 118.835 | 116.9062 | 119.5099 | 125.2041 | 121.3498 | 121.3498 | 121.3498 | 121.3498 | 121.3498 | 121.3498 | 121.3498 | 121.3498 | 121.3498 | 121.3498 | 121.3498 | 121.3498 | 121.3498 | 121.3498 | 121.3498 | 121.3498
97% | 140.3338 | 194.8074 | 208.9687 | 197.4737 | 199.3563 | 202.5979 | 209.9727 | 214.9094 | 221.1632 | 224.4093 | 227.2651 | 222.0033 | 228.17 | 237.8649 | 230.5078 | 230.5078 | 230.5078 | 230.5078 | 230.5078 | 230.5078 | 230.5078 | 230.5078 | 230.5078 | 230.5078 | 230.5078 | 230.5078 | 230.5078 | 230.5078 | 230.5078 | 230.5078 |  | 150.2438 | 204.0305 | 218.7445 | 207.1122 | 208.5578 | 211.7291 | 219.2192 | 223.3086 | 231.0989 | 254.7792 | 235.2572 | 231.4387 | 236.5932 | 247.866 | 240.2356 | 240.2356 | 240.2356 | 240.2356 | 240.2356 | 240.2356 | 240.2356 | 240.2356 | 240.2356 | 240.2356 | 240.2356 | 240.2356 | 240.2356 | 240.2356 | 240.2356 | 240.2356
95% | 414.5243 | 575.4311 | 617.2612 | 583.3068 | 588.8679 | 598.443 | 620.2272 | 634.8092 | 653.2821 | 662.8707 | 671.3062 | 655.7635 | 673.9791 | 702.6162 | 680.8846 | 680.8846 | 680.8846 | 680.8846 | 680.8846 | 680.8846 | 680.8846 | 680.8846 | 680.8846 | 680.8846 | 680.8846 | 680.8846 | 680.8846 | 680.8846 | 680.8846 | 680.8846 |  | 443.7972 | 602.6746 | 646.1375 | 611.7777 | 616.0477 | 625.4151 | 647.5398 | 659.6193 | 682.6306 | 752.5786 | 694.9136 | 683.6343 | 698.8599 | 732.1579 | 709.619 | 709.619 | 709.619 | 709.619 | 709.619 | 709.619 | 709.619 | 709.619 | 709.619 | 709.619 | 709.619 | 709.619 | 709.619 | 709.619 | 709.619 | 709.619
90% | 2285.5212 | 3172.6969 | 3403.3313 | 3216.1201 | 3246.782 | 3299.5751 | 3419.6843 | 3500.0837 | 3601.9361 | 3654.8034 | 3701.3138 | 3615.6171 | 3716.0509 | 3873.9445 | 3754.1252 | 3754.1252 | 3754.1252 | 3754.1252 | 3754.1252 | 3754.1252 | 3754.1252 | 3754.1252 | 3754.1252 | 3754.1252 | 3754.1252 | 3754.1252 | 3754.1252 | 3754.1252 | 3754.1252 | 3754.1252 |  | 2446.9201 | 3322.9067 | 3562.5435 | 3373.0972 | 3396.6403 | 3448.2887 | 3570.275 | 3636.8767 | 3763.7517 | 4149.4168 | 3831.4752 | 3769.2855 | 3853.2336 | 4036.8257 | 3912.5548 | 3912.5548 | 3912.5548 | 3912.5548 | 3912.5548 | 3912.5548 | 3912.5548 | 3912.5548 | 3912.5548 | 3912.5548 | 3912.5548 | 3912.5548 | 3912.5548 | 3912.5548 | 3912.5548 | 3912.5548
85% | 5583.3646 | 7750.6712 | 8314.0946 | 7856.7511 | 7931.6558 | 8060.6255 | 8354.0437 | 8550.4538 | 8799.2718 | 8928.423 | 9042.0445 | 8832.6936 | 9078.0462 | 9463.7688 | 9171.0588 | 9171.0588 | 9171.0588 | 9171.0588 | 9171.0588 | 9171.0588 | 9171.0588 | 9171.0588 | 9171.0588 | 9171.0588 | 9171.0588 | 9171.0588 | 9171.0588 | 9171.0588 | 9171.0588 | 9171.0588 |  | 5977.6505 | 8117.623 | 8703.0385 | 8240.2349 | 8297.7489 | 8423.9222 | 8721.9262 | 8884.6292 | 9194.5759 | 10136.728 | 9360.0195 | 9208.0946 | 9413.1736 | 9861.6761 | 9558.091 | 9558.091 | 9558.091 | 9558.091 | 9558.091 | 9558.091 | 9558.091 | 9558.091 | 9558.091 | 9558.091 | 9558.091 | 9558.091 | 9558.091 | 9558.091 | 9558.091 | 9558.091
80% | 8678.2039 | 12046.8408 | 12922.5678 | 12211.7204 | 12328.1446 | 12528.6017 | 12984.6605 | 13289.9401 | 13676.6769 | 13877.4161 | 14054.0177 | 13728.6244 | 14109.975 | 14709.5023 | 14254.5442 | 14254.5442 | 14254.5442 | 14254.5442 | 14254.5442 | 14254.5442 | 14254.5442 | 14254.5442 | 14254.5442 | 14254.5442 | 14254.5442 | 14254.5442 | 14254.5442 | 14254.5442 | 14254.5442 | 14254.5442 |  | 9291.041 | 12617.1926 | 13527.1019 | 12807.7679 | 12897.1618 | 13093.2725 | 13556.4589 | 13809.3476 | 14291.0967 | 15755.4803 | 14548.2452 | 14312.1087 | 14630.8624 | 15327.9681 | 14856.1069 | 14856.1069 | 14856.1069 | 14856.1069 | 14856.1069 | 14856.1069 | 14856.1069 | 14856.1069 | 14856.1069 | 14856.1069 | 14856.1069 | 14856.1069 | 14856.1069 | 14856.1069 | 14856.1069 | 14856.1069
75% | 9574.4808 | 13291.0275 | 14257.1987 | 13472.9358 | 13601.384 | 13822.5442 | 14325.7044 | 14662.513 | 15089.1916 | 15310.663 | 15505.5038 | 15146.5042 | 15567.2403 | 16228.6862 | 15726.7405 | 15726.7405 | 15726.7405 | 15726.7405 | 15726.7405 | 15726.7405 | 15726.7405 | 15726.7405 | 15726.7405 | 15726.7405 | 15726.7405 | 15726.7405 | 15726.7405 | 15726.7405 | 15726.7405 | 15726.7405 |  | 10250.6112 | 13920.2847 | 14924.1686 | 14130.5425 | 14229.1688 | 14445.5337 | 14956.5576 | 15235.5644 | 15767.0681 | 17382.6919 | 16050.7746 | 15790.2502 | 16141.9244 | 16911.0267 | 16390.4321 | 16390.4321 | 16390.4321 | 16390.4321 | 16390.4321 | 16390.4321 | 16390.4321 | 16390.4321 | 16390.4321 | 16390.4321 | 16390.4321 | 16390.4321 | 16390.4321 | 16390.4321 | 16390.4321 | 16390.4321
70% | 10287.2444 | 14280.4661 | 15318.563 | 14475.9163 | 14613.9268 | 14851.551 | 15392.1685 | 15754.0505 | 16212.4928 | 16450.4515 | 16659.797 | 16274.072 | 16726.1294 | 17436.8161 | 16897.5035 | 16897.5035 | 16897.5035 | 16897.5035 | 16897.5035 | 16897.5035 | 16897.5035 | 16897.5035 | 16897.5035 | 16897.5035 | 16897.5035 | 16897.5035 | 16897.5035 | 16897.5035 | 16897.5035 | 16897.5035 |  | 11013.7087 | 14956.5677 | 16035.1849 | 15182.478 | 15288.4465 | 15520.9184 | 16069.985 | 16369.7622 | 16940.8333 | 18676.7307 | 17245.6601 | 16965.7411 | 17343.5954 | 18169.9528 | 17610.603 | 17610.603 | 17610.603 | 17610.603 | 17610.603 | 17610.603 | 17610.603 | 17610.603 | 17610.603 | 17610.603 | 17610.603 | 17610.603 | 17610.603 | 17610.603 | 17610.603 | 17610.603
65% | 10840.7831 | 15048.8731 | 16142.8282 | 15254.8402 | 15400.2768 | 15650.6871 | 16220.3943 | 16601.7485 | 17084.8589 | 17335.6216 | 17556.2317 | 17149.7515 | 17626.1333 | 18375.0609 | 17806.7288 | 17806.7288 | 17806.7288 | 17806.7288 | 17806.7288 | 17806.7288 | 17806.7288 | 17806.7288 | 17806.7288 | 17806.7288 | 17806.7288 | 17806.7288 | 17806.7288 | 17806.7288 | 17806.7288 | 17806.7288 |  | 11606.3372 | 15761.3546 | 16898.0103 | 15999.4207 | 16111.0912 | 16356.072 | 16934.6829 | 17250.5907 | 17852.39 | 19681.6931 | 18173.619 | 17878.6382 | 18276.8241 | 19147.6463 | 18558.1989 | 18558.1989 | 18558.1989 | 18558.1989 | 18558.1989 | 18558.1989 | 18558.1989 | 18558.1989 | 18558.1989 | 18558.1989 | 18558.1989 | 18558.1989 | 18558.1989 | 18558.1989 | 18558.1989 | 18558.1989
60% | 11934.3669 | 16566.9557 | 17771.2656 | 16793.7001 | 16953.8079 | 17229.4788 | 17856.6562 | 18276.4803 | 18808.3253 | 19084.3842 | 19327.2487 | 18879.764 | 19404.2018 | 20228.6787 | 19603.0151 | 19603.0151 | 19603.0151 | 19603.0151 | 19603.0151 | 19603.0151 | 19603.0151 | 19603.0151 | 19603.0151 | 19603.0151 | 19603.0151 | 19603.0151 | 19603.0151 | 19603.0151 | 19603.0151 | 19603.0151 |  | 12777.1477 | 17351.3101 | 18602.628 | 17613.3915 | 17736.327 | 18006.0207 | 18643 | 18990.7756 | 19653.2825 | 21667.1199 | 20006.9161 | 19682.1785 | 20120.5322 | 21079.2002 | 20430.2911 | 20430.2911 | 20430.2911 | 20430.2911 | 20430.2911 | 20430.2911 | 20430.2911 | 20430.2911 | 20430.2911 | 20430.2911 | 20430.2911 | 20430.2911 | 20430.2911 | 20430.2911 | 20430.2911 | 20430.2911
55% | 13276.2336 | 18429.6976 | 19769.4166 | 18681.9364 | 18860.0463 | 19166.7129 | 19864.4084 | 20331.4363 | 20923.0804 | 21230.1786 | 21500.3502 | 21002.5516 | 21585.9556 | 22503.1344 | 21807.123 | 21807.123 | 21807.123 | 21807.123 | 21807.123 | 21807.123 | 21807.123 | 21807.123 | 21807.123 | 21807.123 | 21807.123 | 21807.123 | 21807.123 | 21807.123 | 21807.123 | 21807.123 |  | 14213.7742 | 19302.2426 | 20694.2551 | 19593.7917 | 19730.5496 | 20030.5669 | 20739.1665 | 21126.0449 | 21863.0423 | 24103.3099 | 22256.4374 | 21895.1872 | 22382.8282 | 23449.2861 | 22727.4156 | 22727.4156 | 22727.4156 | 22727.4156 | 22727.4156 | 22727.4156 | 22727.4156 | 22727.4156 | 22727.4156 | 22727.4156 | 22727.4156 | 22727.4156 | 22727.4156 | 22727.4156 | 22727.4156 | 22727.4156
50% | 13456.7484 | 18680.2832 | 20038.2182 | 18935.9517 | 19116.4833 | 19427.3196 | 20134.5016 | 20607.8795 | 21207.5682 | 21518.8419 | 21792.6869 | 21288.1199 | 21879.4564 | 22809.1059 | 22103.6309 | 22103.6309 | 22103.6309 | 22103.6309 | 22103.6309 | 22103.6309 | 22103.6309 | 22103.6309 | 22103.6309 | 22103.6309 | 22103.6309 | 22103.6309 | 22103.6309 | 22103.6309 | 22103.6309 | 22103.6309 |  | 14407.0366 | 19564.692 | 20975.6315 | 19860.2053 | 19998.8227 | 20302.9193 | 21021.1536 | 21413.2923 | 22160.3105 | 24431.0387 | 22559.0546 | 22192.8926 | 22687.1639 | 23768.1223 | 23036.4366 | 23036.4366 | 23036.4366 | 23036.4366 | 23036.4366 | 23036.4366 | 23036.4366 | 23036.4366 | 23036.4366 | 23036.4366 | 23036.4366 | 23036.4366 | 23036.4366 | 23036.4366 | 23036.4366 | 23036.4366
45% | 10386.1977 | 14417.8303 | 15465.9127 | 14615.1605 | 14754.4986 | 14994.4085 | 15540.2262 | 15905.5891 | 16368.4413 | 16608.6888 | 16820.0481 | 16430.6127 | 16887.0185 | 17604.5413 | 17060.0411 | 17060.0411 | 17060.0411 | 17060.0411 | 17060.0411 | 17060.0411 | 17060.0411 | 17060.0411 | 17060.0411 | 17060.0411 | 17060.0411 | 17060.0411 | 17060.0411 | 17060.0411 | 17060.0411 | 17060.0411 |  | 11119.6499 | 15100.4354 | 16189.4278 | 15328.5186 | 15435.5065 | 15670.2145 | 16224.5626 | 16527.2234 | 17103.7876 | 18856.3827 | 17411.5466 | 17128.9351 | 17510.424 | 18344.7301 | 17779.9999 | 17779.9999 | 17779.9999 | 17779.9999 | 17779.9999 | 17779.9999 | 17779.9999 | 17779.9999 | 17779.9999 | 17779.9999 | 17779.9999 | 17779.9999 | 17779.9999 | 17779.9999 | 17779.9999 | 17779.9999
40% | 5102.6915 | 7083.4142 | 7598.3323 | 7180.3617 | 7248.8178 | 7366.6845 | 7634.8422 | 7814.3433 | 8041.7405 | 8159.773 | 8263.6128 | 8072.285 | 8296.5151 | 8649.0308 | 8381.5203 | 8381.5203 | 8381.5203 | 8381.5203 | 8381.5203 | 8381.5203 | 8381.5203 | 8381.5203 | 8381.5203 | 8381.5203 | 8381.5203 | 8381.5203 | 8381.5203 | 8381.5203 | 8381.5203 | 8381.5203 |  | 5463.0332 | 7418.775 | 7953.792 | 7530.8312 | 7583.3939 | 7698.7049 | 7971.0536 | 8119.7494 | 8403.0128 | 9264.0548 | 8554.2133 | 8415.3676 | 8602.7914 | 9012.6821 | 8735.2328 | 8735.2328 | 8735.2328 | 8735.2328 | 8735.2328 | 8735.2328 | 8735.2328 | 8735.2328 | 8735.2328 | 8735.2328 | 8735.2328 | 8735.2328 | 8735.2328 | 8735.2328 | 8735.2328 | 8735.2328
35% | 1907.0998 | 2647.3829 | 2839.8304 | 2683.6164 | 2709.2015 | 2753.2534 | 2853.4757 | 2920.5632 | 3005.5515 | 3049.6654 | 3088.4749 | 3016.9673 | 3100.7719 | 3232.5225 | 3132.5421 | 3132.5421 | 3132.5421 | 3132.5421 | 3132.5421 | 3132.5421 | 3132.5421 | 3132.5421 | 3132.5421 | 3132.5421 | 3132.5421 | 3132.5421 | 3132.5421 | 3132.5421 | 3132.5421 | 3132.5421 |  | 2041.7754 | 2772.7219 | 2972.6813 | 2814.6023 | 2834.2472 | 2877.344 | 2979.1327 | 3034.7068 | 3140.5748 | 3462.384 | 3197.0851 | 3145.1923 | 3215.2408 | 3368.435 | 3264.74 | 3264.74 | 3264.74 | 3264.74 | 3264.74 | 3264.74 | 3264.74 | 3264.74 | 3264.74 | 3264.74 | 3264.74 | 3264.74 | 3264.74 | 3264.74 | 3264.74 | 3264.74
30% | 951.1511 | 1320.3614 | 1416.3431 | 1338.4326 | 1351.1929 | 1373.1635 | 1423.1486 | 1456.6079 | 1498.9952 | 1520.9966 | 1540.3526 | 1504.6887 | 1546.4856 | 1612.1952 | 1562.3308 | 1562.3308 | 1562.3308 | 1562.3308 | 1562.3308 | 1562.3308 | 1562.3308 | 1562.3308 | 1562.3308 | 1562.3308 | 1562.3308 | 1562.3308 | 1562.3308 | 1562.3308 | 1562.3308 | 1562.3308 |  | 1018.3194 | 1382.8733 | 1482.6014 | 1403.7608 | 1413.5585 | 1435.0527 | 1485.819 | 1513.5362 | 1566.337 | 1726.8368 | 1594.5211 | 1568.64 | 1603.5761 | 1679.9805 | 1628.2634 | 1628.2634 | 1628.2634 | 1628.2634 | 1628.2634 | 1628.2634 | 1628.2634 | 1628.2634 | 1628.2634 | 1628.2634 | 1628.2634 | 1628.2634 | 1628.2634 | 1628.2634 | 1628.2634 | 1628.2634
25% | 560.7353 | 778.3972 | 834.9816 | 789.0507 | 796.5734 | 809.5258 | 838.9936 | 858.719 | 883.7077 | 896.6784 | 908.0893 | 887.0643 | 911.705 | 950.4429 | 921.0462 | 921.0462 | 921.0462 | 921.0462 | 921.0462 | 921.0462 | 921.0462 | 921.0462 | 921.0462 | 921.0462 | 921.0462 | 921.0462 | 921.0462 | 921.0462 | 921.0462 | 921.0462 |  | 600.3333 | 815.25 | 874.0431 | 827.5639 | 833.34 | 846.0115 | 875.94 | 892.2802 | 923.408 | 1018.028 | 940.0234 | 924.7657 | 945.3617 | 990.4046 | 959.9157 | 959.9157 | 959.9157 | 959.9157 | 959.9157 | 959.9157 | 959.9157 | 959.9157 | 959.9157 | 959.9157 | 959.9157 | 959.9157 | 959.9157 | 959.9157 | 959.9157 | 959.9157
20% | 283.3663 | 393.3611 | 421.9559 | 398.7449 | 402.5464 | 409.0919 | 423.9834 | 433.9516 | 446.5796 | 453.1342 | 458.9008 | 448.2758 | 460.7279 | 480.3041 | 465.4485 | 465.4485 | 465.4485 | 465.4485 | 465.4485 | 465.4485 | 465.4485 | 465.4485 | 465.4485 | 465.4485 | 465.4485 | 465.4485 | 465.4485 | 465.4485 | 465.4485 | 465.4485 |  | 303.377 | 411.9846 | 441.6956 | 418.2074 | 421.1264 | 427.5299 | 442.6541 | 450.9116 | 466.642 | 514.458 | 475.0386 | 467.3281 | 477.7363 | 500.4986 | 485.0911 | 485.0911 | 485.0911 | 485.0911 | 485.0911 | 485.0911 | 485.0911 | 485.0911 | 485.0911 | 485.0911 | 485.0911 | 485.0911 | 485.0911 | 485.0911 | 485.0911 | 485.0911
15% | 115.4455 | 160.2582 | 171.908 | 162.4516 | 164.0004 | 166.6671 | 172.734 | 176.7951 | 181.9398 | 184.6102 | 186.9596 | 182.6309 | 187.704 | 195.6794 | 189.6272 | 189.6272 | 189.6272 | 189.6272 | 189.6272 | 189.6272 | 189.6272 | 189.6272 | 189.6272 | 189.6272 | 189.6272 | 189.6272 | 189.6272 | 189.6272 | 189.6272 | 189.6272 |  | 123.598 | 167.8456 | 179.95 | 170.3808 | 171.57 | 174.1788 | 180.3406 | 183.7047 | 190.1134 | 209.594 | 193.5342 | 190.3929 | 194.6333 | 203.9068 | 197.6297 | 197.6297 | 197.6297 | 197.6297 | 197.6297 | 197.6297 | 197.6297 | 197.6297 | 197.6297 | 197.6297 | 197.6297 | 197.6297 | 197.6297 | 197.6297 | 197.6297 | 197.6297
10% | 46.4781 | 64.5196 | 69.2097 | 65.4026 | 66.0261 | 67.0997 | 69.5423 | 71.1772 | 73.2485 | 74.3236 | 75.2694 | 73.5267 | 75.5691 | 78.78 | 76.3434 | 76.3434 | 76.3434 | 76.3434 | 76.3434 | 76.3434 | 76.3434 | 76.3434 | 76.3434 | 76.3434 | 76.3434 | 76.3434 | 76.3434 | 76.3434 | 76.3434 | 76.3434 |  | 49.7602 | 67.5742 | 72.4474 | 68.5949 | 69.0736 | 70.1239 | 72.6046 | 73.9591 | 76.5392 | 84.382 | 77.9164 | 76.6517 | 78.3589 | 82.0924 | 79.5652 | 79.5652 | 79.5652 | 79.5652 | 79.5652 | 79.5652 | 79.5652 | 79.5652 | 79.5652 | 79.5652 | 79.5652 | 79.5652 | 79.5652 | 79.5652 | 79.5652 | 79.5652
5% | 39.5813 | 54.9457 | 58.9399 | 55.6977 | 56.2287 | 57.143 | 59.2231 | 60.6155 | 62.3794 | 63.2949 | 64.1004 | 62.6163 | 64.3556 | 67.0901 | 65.015 | 65.015 | 65.015 | 65.015 | 65.015 | 65.015 | 65.015 | 65.015 | 65.015 | 65.015 | 65.015 | 65.015 | 65.015 | 65.015 | 65.015 | 65.015 |  | 42.3765 | 57.5471 | 61.6972 | 58.4163 | 58.824 | 59.7185 | 61.8311 | 62.9845 | 65.1817 | 71.8608 | 66.3546 | 65.2776 | 66.7314 | 69.9109 | 67.7588 | 67.7588 | 67.7588 | 67.7588 | 67.7588 | 67.7588 | 67.7588 | 67.7588 | 67.7588 | 67.7588 | 67.7588 | 67.7588 | 67.7588 | 67.7588 | 67.7588 | 67.7588
9.992e-14% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E @ R (MWh) | 105995.1099 | 147139.4588 | 157835.5397 | 149153.2894 | 150575.2871 | 153023.6595 | 158593.9373 | 162322.6056 | 167046.1882 | 169498.0061 | 171655.0079 | 167680.6717 | 172338.4668 | 179661.0609 | 174104.2282 | 174104.2282 | 174104.2282 | 174104.2282 | 174104.2282 | 174104.2282 | 174104.2282 | 174104.2282 | 174104.2282 | 174104.2282 | 174104.2282 | 174104.2282 | 174104.2282 | 174104.2282 | 174104.2282 | 174104.2282 | E @ R (MWh) | 113480.2695 | 154105.704 | 165219.287 | 156433.381 | 157525.2324 | 159920.5177 | 165577.8517 | 168666.6208 | 174550.6781 | 192436.5798 | 177691.4756 | 174807.3176 | 178700.5572 | 187214.9692 | 181451.6821 | 181451.6821 | 181451.6821 | 181451.6821 | 181451.6821 | 181451.6821 | 181451.6821 | 181451.6821 | 181451.6821 | 181451.6821 | 181451.6821 | 181451.6821 | 181451.6821 | 181451.6821 | 181451.6821 | 181451.6821
Option 4 Winter POE50 W E @ R (MWh) N 2 | 74196.5769 | 102997.6211 | 110484.8778 | 104407.3025 | 105402.701 | 107116.5616 | 111015.7561 | 113625.8239 | 116932.3317 | 118648.6043 | 120158.5055 | 117376.4702 | 120636.9268 | 125762.7427 | 121872.9597 | 121872.9597 | 121872.9597 | 121872.9597 | 121872.9597 | 121872.9597 | 121872.9597 | 121872.9597 | 121872.9597 | 121872.9597 | 121872.9597 | 121872.9597 | 121872.9597 | 121872.9597 | 121872.9597 | 121872.9597 | Option 4 Winter POE10 W E @ R (MWh) N 2 | 34044.0809 | 46231.7112 | 49565.7861 | 46930.0143 | 47257.5697 | 47976.1553 | 49673.3555 | 50599.9862 | 52365.2034 | 57730.9739 | 53307.4427 | 52442.1953 | 53610.1671 | 56164.4908 | 54435.5046 | 54435.5046 | 54435.5046 | 54435.5046 | 54435.5046 | 54435.5046 | 54435.5046 | 54435.5046 | 54435.5046 | 54435.5046 | 54435.5046 | 54435.5046 | 54435.5046 | 54435.5046 | 54435.5046 | 54435.5046
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 76.9936 | 99.7405 | 105.6969 | 99.3222 | 99.352 | 99.9652 | 101.5796 | 102.662 | 103.7208 | 104.9587 | 106.1069 | 107.2207 | 107.3497 | 108.6494 | 107.6679 | 107.6679 | 107.6679 | 107.6679 | 107.6679 | 107.6679 | 107.6679 | 107.6679 | 107.6679 | 107.6679 | 107.6679 | 107.6679 | 107.6679 | 107.6679 | 107.6679 | 107.6679
98% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 38.1099 | 49.369 | 52.3173 | 49.162 | 49.1767 | 49.4803 | 50.2793 | 50.8151 | 51.3392 | 51.9519 | 52.5202 | 53.0716 | 53.1354 | 53.7787 | 53.2929 | 53.2929 | 53.2929 | 53.2929 | 53.2929 | 53.2929 | 53.2929 | 53.2929 | 53.2929 | 53.2929 | 53.2929 | 53.2929 | 53.2929 | 53.2929 | 53.2929 | 53.2929
97% | 16.9149 | 22.4762 | 23.991 | 22.4728 | 22.4723 | 22.6456 | 22.8356 | 23.2254 | 23.5054 | 23.6577 | 23.8245 | 23.9769 | 24.2517 | 24.5925 | 24.5695 | 24.5695 | 24.5695 | 24.5695 | 24.5695 | 24.5695 | 24.5695 | 24.5695 | 24.5695 | 24.5695 | 24.5695 | 24.5695 | 24.5695 | 24.5695 | 24.5695 | 24.5695 |  | 75.446 | 97.7357 | 103.5723 | 97.3258 | 97.355 | 97.9559 | 99.5378 | 100.5985 | 101.6359 | 102.8489 | 103.9741 | 105.0655 | 105.192 | 106.4655 | 105.5037 | 105.5037 | 105.5037 | 105.5037 | 105.5037 | 105.5037 | 105.5037 | 105.5037 | 105.5037 | 105.5037 | 105.5037 | 105.5037 | 105.5037 | 105.5037 | 105.5037 | 105.5037
95% | 83.2734 | 110.6519 | 118.1097 | 110.6355 | 110.6329 | 111.4859 | 112.4215 | 114.3404 | 115.719 | 116.4686 | 117.2896 | 118.0399 | 119.3928 | 121.071 | 120.9576 | 120.9576 | 120.9576 | 120.9576 | 120.9576 | 120.9576 | 120.9576 | 120.9576 | 120.9576 | 120.9576 | 120.9576 | 120.9576 | 120.9576 | 120.9576 | 120.9576 | 120.9576 |  | 111.4279 | 144.3481 | 152.9683 | 143.7427 | 143.7858 | 144.6733 | 147.0097 | 148.5762 | 150.1085 | 151.9 | 153.5617 | 155.1737 | 155.3604 | 157.2413 | 155.8208 | 155.8208 | 155.8208 | 155.8208 | 155.8208 | 155.8208 | 155.8208 | 155.8208 | 155.8208 | 155.8208 | 155.8208 | 155.8208 | 155.8208 | 155.8208 | 155.8208 | 155.8208
90% | 144.4273 | 191.9119 | 204.8464 | 191.8834 | 191.879 | 193.3584 | 194.9811 | 198.3092 | 200.7002 | 202.0001 | 203.4242 | 204.7255 | 207.0718 | 209.9825 | 209.7858 | 209.7858 | 209.7858 | 209.7858 | 209.7858 | 209.7858 | 209.7858 | 209.7858 | 209.7858 | 209.7858 | 209.7858 | 209.7858 | 209.7858 | 209.7858 | 209.7858 | 209.7858 |  | 483.1446 | 625.8842 | 663.261 | 623.2595 | 623.4461 | 627.2942 | 637.4247 | 644.2171 | 650.8609 | 658.6288 | 665.8339 | 672.8234 | 673.6331 | 681.7887 | 675.6294 | 675.6294 | 675.6294 | 675.6294 | 675.6294 | 675.6294 | 675.6294 | 675.6294 | 675.6294 | 675.6294 | 675.6294 | 675.6294 | 675.6294 | 675.6294 | 675.6294 | 675.6294
85% | 409.8612 | 544.6148 | 581.321 | 544.5341 | 544.5215 | 548.7197 | 553.3248 | 562.7694 | 569.5547 | 573.2437 | 577.2849 | 580.9777 | 587.6363 | 595.8964 | 595.3381 | 595.3381 | 595.3381 | 595.3381 | 595.3381 | 595.3381 | 595.3381 | 595.3381 | 595.3381 | 595.3381 | 595.3381 | 595.3381 | 595.3381 | 595.3381 | 595.3381 | 595.3381 |  | 457.0286 | 592.0526 | 627.4091 | 589.5698 | 589.7464 | 593.3864 | 602.9693 | 609.3946 | 615.6792 | 623.0272 | 629.8429 | 636.4546 | 637.2205 | 644.9352 | 639.1089 | 639.1089 | 639.1089 | 639.1089 | 639.1089 | 639.1089 | 639.1089 | 639.1089 | 639.1089 | 639.1089 | 639.1089 | 639.1089 | 639.1089 | 639.1089 | 639.1089 | 639.1089
80% | 572.5046 | 760.7318 | 812.0039 | 760.619 | 760.6015 | 766.4656 | 772.8981 | 786.0905 | 795.5685 | 800.7213 | 806.3662 | 811.5244 | 820.8253 | 832.3632 | 831.5834 | 831.5834 | 831.5834 | 831.5834 | 831.5834 | 831.5834 | 831.5834 | 831.5834 | 831.5834 | 831.5834 | 831.5834 | 831.5834 | 831.5834 | 831.5834 | 831.5834 | 831.5834 |  | 319.1946 | 413.4971 | 438.1905 | 411.7631 | 411.8863 | 414.4286 | 421.1214 | 425.6089 | 429.9982 | 435.1301 | 439.8903 | 444.508 | 445.0429 | 450.4309 | 446.3618 | 446.3618 | 446.3618 | 446.3618 | 446.3618 | 446.3618 | 446.3618 | 446.3618 | 446.3618 | 446.3618 | 446.3618 | 446.3618 | 446.3618 | 446.3618 | 446.3618 | 446.3618
75% | 1492.4153 | 1983.0895 | 2116.7465 | 1982.7955 | 1982.7497 | 1998.0364 | 2014.8049 | 2049.1951 | 2073.9023 | 2087.3349 | 2102.05 | 2115.4967 | 2139.7423 | 2169.8195 | 2167.7868 | 2167.7868 | 2167.7868 | 2167.7868 | 2167.7868 | 2167.7868 | 2167.7868 | 2167.7868 | 2167.7868 | 2167.7868 | 2167.7868 | 2167.7868 | 2167.7868 | 2167.7868 | 2167.7868 | 2167.7868 |  | 569.714 | 738.0296 | 782.1036 | 734.9347 | 735.1547 | 739.6923 | 751.638 | 759.6474 | 767.4816 | 776.6413 | 785.1375 | 793.3793 | 794.3342 | 803.951 | 796.6882 | 796.6882 | 796.6882 | 796.6882 | 796.6882 | 796.6882 | 796.6882 | 796.6882 | 796.6882 | 796.6882 | 796.6882 | 796.6882 | 796.6882 | 796.6882 | 796.6882 | 796.6882
70% | 2578.4391 | 3426.1747 | 3657.0932 | 3425.6667 | 3425.5876 | 3451.9984 | 3480.9692 | 3540.385 | 3583.0716 | 3606.2789 | 3631.7022 | 3654.9339 | 3696.8229 | 3748.7872 | 3745.2753 | 3745.2753 | 3745.2753 | 3745.2753 | 3745.2753 | 3745.2753 | 3745.2753 | 3745.2753 | 3745.2753 | 3745.2753 | 3745.2753 | 3745.2753 | 3745.2753 | 3745.2753 | 3745.2753 | 3745.2753 |  | 1037.8661 | 1344.492 | 1424.783 | 1338.8538 | 1339.2547 | 1347.5209 | 1369.2827 | 1383.8738 | 1398.1456 | 1414.8322 | 1430.3099 | 1445.3243 | 1447.0638 | 1464.583 | 1451.3521 | 1451.3521 | 1451.3521 | 1451.3521 | 1451.3521 | 1451.3521 | 1451.3521 | 1451.3521 | 1451.3521 | 1451.3521 | 1451.3521 | 1451.3521 | 1451.3521 | 1451.3521 | 1451.3521 | 1451.3521
65% | 6475.8072 | 8604.914 | 9184.8711 | 8603.6382 | 8603.4397 | 8669.7709 | 8742.5318 | 8891.7559 | 8998.9641 | 9057.2499 | 9121.101 | 9179.448 | 9284.6532 | 9415.1627 | 9406.3424 | 9406.3424 | 9406.3424 | 9406.3424 | 9406.3424 | 9406.3424 | 9406.3424 | 9406.3424 | 9406.3424 | 9406.3424 | 9406.3424 | 9406.3424 | 9406.3424 | 9406.3424 | 9406.3424 | 9406.3424 |  | 1305.7961 | 1691.5789 | 1792.5974 | 1684.4852 | 1684.9896 | 1695.3897 | 1722.7695 | 1741.1273 | 1759.0834 | 1780.0777 | 1799.5512 | 1818.4416 | 1820.6301 | 1842.6721 | 1826.0255 | 1826.0255 | 1826.0255 | 1826.0255 | 1826.0255 | 1826.0255 | 1826.0255 | 1826.0255 | 1826.0255 | 1826.0255 | 1826.0255 | 1826.0255 | 1826.0255 | 1826.0255 | 1826.0255 | 1826.0255
60% | 9465.8424 | 12578.0087 | 13425.7459 | 12576.1439 | 12575.8536 | 12672.8116 | 12779.1679 | 12997.2924 | 13154.0011 | 13239.1989 | 13332.5316 | 13417.8188 | 13571.5997 | 13762.3686 | 13749.4757 | 13749.4757 | 13749.4757 | 13749.4757 | 13749.4757 | 13749.4757 | 13749.4757 | 13749.4757 | 13749.4757 | 13749.4757 | 13749.4757 | 13749.4757 | 13749.4757 | 13749.4757 | 13749.4757 | 13749.4757 |  | 2043.3291 | 2647.0078 | 2805.083 | 2635.9074 | 2636.6967 | 2652.971 | 2695.8153 | 2724.5418 | 2752.6398 | 2785.492 | 2815.9643 | 2845.5244 | 2848.9489 | 2883.4405 | 2857.3918 | 2857.3918 | 2857.3918 | 2857.3918 | 2857.3918 | 2857.3918 | 2857.3918 | 2857.3918 | 2857.3918 | 2857.3918 | 2857.3918 | 2857.3918 | 2857.3918 | 2857.3918 | 2857.3918 | 2857.3918
55% | 10703.6666 | 14222.8031 | 15181.3967 | 14220.6944 | 14220.3662 | 14330.0031 | 14450.2674 | 14696.9155 | 14874.1165 | 14970.4554 | 15075.993 | 15172.433 | 15346.3235 | 15562.0387 | 15547.4598 | 15547.4598 | 15547.4598 | 15547.4598 | 15547.4598 | 15547.4598 | 15547.4598 | 15547.4598 | 15547.4598 | 15547.4598 | 15547.4598 | 15547.4598 | 15547.4598 | 15547.4598 | 15547.4598 | 15547.4598 |  | 3926.5772 | 5086.6405 | 5390.4069 | 5065.3094 | 5066.8261 | 5098.0998 | 5180.4317 | 5235.6343 | 5289.629 | 5352.7597 | 5411.317 | 5468.1213 | 5474.7021 | 5540.9831 | 5490.9264 | 5490.9264 | 5490.9264 | 5490.9264 | 5490.9264 | 5490.9264 | 5490.9264 | 5490.9264 | 5490.9264 | 5490.9264 | 5490.9264 | 5490.9264 | 5490.9264 | 5490.9264 | 5490.9264 | 5490.9264
50% | 13744.0128 | 18262.75 | 19493.6294 | 18260.0423 | 18259.6209 | 18400.3998 | 18554.8249 | 18871.5326 | 19099.0672 | 19222.7709 | 19358.2861 | 19482.1196 | 19705.4031 | 19982.3917 | 19963.6718 | 19963.6718 | 19963.6718 | 19963.6718 | 19963.6718 | 19963.6718 | 19963.6718 | 19963.6718 | 19963.6718 | 19963.6718 | 19963.6718 | 19963.6718 | 19963.6718 | 19963.6718 | 19963.6718 | 19963.6718 |  | 8714.0125 | 11288.47 | 11962.6002 | 11241.1313 | 11244.4971 | 11313.9009 | 11496.6152 | 11619.1228 | 11738.9501 | 11879.0521 | 12009.0047 | 12135.067 | 12149.6714 | 12296.7648 | 12185.677 | 12185.677 | 12185.677 | 12185.677 | 12185.677 | 12185.677 | 12185.677 | 12185.677 | 12185.677 | 12185.677 | 12185.677 | 12185.677 | 12185.677 | 12185.677 | 12185.677 | 12185.677
45% | 18302.3635 | 24319.7888 | 25958.9027 | 24316.1831 | 24315.6219 | 24503.0917 | 24708.7335 | 25130.4808 | 25433.4796 | 25598.211 | 25778.6713 | 25943.5755 | 26240.9135 | 26609.7683 | 26584.8397 | 26584.8397 | 26584.8397 | 26584.8397 | 26584.8397 | 26584.8397 | 26584.8397 | 26584.8397 | 26584.8397 | 26584.8397 | 26584.8397 | 26584.8397 | 26584.8397 | 26584.8397 | 26584.8397 | 26584.8397 |  | 13204.5002 | 17105.6219 | 18127.1435 | 17033.8888 | 17038.9891 | 17144.1578 | 17421.0281 | 17606.6661 | 17788.2426 | 18000.5416 | 18197.4612 | 18388.4857 | 18410.6159 | 18633.5093 | 18465.1759 | 18465.1759 | 18465.1759 | 18465.1759 | 18465.1759 | 18465.1759 | 18465.1759 | 18465.1759 | 18465.1759 | 18465.1759 | 18465.1759 | 18465.1759 | 18465.1759 | 18465.1759 | 18465.1759 | 18465.1759
40% | 12836.6798 | 17057.1053 | 18206.7263 | 17054.5764 | 17054.1828 | 17185.668 | 17329.8984 | 17625.6982 | 17838.2117 | 17953.7489 | 18080.3179 | 18195.9763 | 18404.5194 | 18663.2222 | 18645.738 | 18645.738 | 18645.738 | 18645.738 | 18645.738 | 18645.738 | 18645.738 | 18645.738 | 18645.738 | 18645.738 | 18645.738 | 18645.738 | 18645.738 | 18645.738 | 18645.738 | 18645.738 |  | 13672.6523 | 17712.0843 | 18769.8229 | 17637.808 | 17643.0891 | 17751.9865 | 18038.6729 | 18230.8925 | 18418.9066 | 18638.7325 | 18842.6336 | 19040.4307 | 19063.3455 | 19294.1413 | 19119.8398 | 19119.8398 | 19119.8398 | 19119.8398 | 19119.8398 | 19119.8398 | 19119.8398 | 19119.8398 | 19119.8398 | 19119.8398 | 19119.8398 | 19119.8398 | 19119.8398 | 19119.8398 | 19119.8398 | 19119.8398
35% | 6655.3655 | 8843.5072 | 9439.545 | 8842.196 | 8841.9919 | 8910.1624 | 8984.9408 | 9138.3025 | 9248.4833 | 9308.3852 | 9374.0067 | 9433.9716 | 9542.0938 | 9676.2221 | 9667.1572 | 9667.1572 | 9667.1572 | 9667.1572 | 9667.1572 | 9667.1572 | 9667.1572 | 9667.1572 | 9667.1572 | 9667.1572 | 9667.1572 | 9667.1572 | 9667.1572 | 9667.1572 | 9667.1572 | 9667.1572 |  | 18622.1031 | 24123.7949 | 25564.4311 | 24022.6308 | 24029.8236 | 24178.1415 | 24568.6074 | 24830.4098 | 25086.4843 | 25385.8864 | 25663.599 | 25932.9979 | 25964.2078 | 26278.5509 | 26041.1529 | 26041.1529 | 26041.1529 | 26041.1529 | 26041.1529 | 26041.1529 | 26041.1529 | 26041.1529 | 26041.1529 | 26041.1529 | 26041.1529 | 26041.1529 | 26041.1529 | 26041.1529 | 26041.1529 | 26041.1529
30% | 3095.428 | 4113.1385 | 4390.3573 | 4112.5287 | 4112.4338 | 4144.14 | 4178.9197 | 4250.2486 | 4301.494 | 4329.3545 | 4359.8753 | 4387.7651 | 4438.053 | 4500.4364 | 4496.2203 | 4496.2203 | 4496.2203 | 4496.2203 | 4496.2203 | 4496.2203 | 4496.2203 | 4496.2203 | 4496.2203 | 4496.2203 | 4496.2203 | 4496.2203 | 4496.2203 | 4496.2203 | 4496.2203 | 4496.2203 |  | 17207.9743 | 22291.8776 | 23623.1145 | 22198.3957 | 22205.0423 | 22342.0972 | 22702.9118 | 22944.8334 | 23181.4621 | 23458.1281 | 23714.7517 | 23963.693 | 23992.5329 | 24283.0053 | 24063.6349 | 24063.6349 | 24063.6349 | 24063.6349 | 24063.6349 | 24063.6349 | 24063.6349 | 24063.6349 | 24063.6349 | 24063.6349 | 24063.6349 | 24063.6349 | 24063.6349 | 24063.6349 | 24063.6349 | 24063.6349
25% | 2113.496 | 2808.3682 | 2997.6476 | 2807.9519 | 2807.887 | 2829.5354 | 2853.2823 | 2901.9842 | 2936.9735 | 2955.9962 | 2976.8351 | 2995.8777 | 3030.2133 | 3072.8074 | 3069.9288 | 3069.9288 | 3069.9288 | 3069.9288 | 3069.9288 | 3069.9288 | 3069.9288 | 3069.9288 | 3069.9288 | 3069.9288 | 3069.9288 | 3069.9288 | 3069.9288 | 3069.9288 | 3069.9288 | 3069.9288 |  | 4963.476 | 6429.8794 | 6813.862 | 6402.9155 | 6404.8326 | 6444.3648 | 6548.4383 | 6618.2183 | 6686.4716 | 6766.2733 | 6840.2939 | 6912.0986 | 6920.4172 | 7004.2012 | 6940.9259 | 6940.9259 | 6940.9259 | 6940.9259 | 6940.9259 | 6940.9259 | 6940.9259 | 6940.9259 | 6940.9259 | 6940.9259 | 6940.9259 | 6940.9259 | 6940.9259 | 6940.9259 | 6940.9259 | 6940.9259
20% | 1280.3284 | 1701.2729 | 1815.9359 | 1701.0207 | 1700.9814 | 1714.0958 | 1728.4813 | 1757.9843 | 1779.1804 | 1790.704 | 1803.328 | 1814.8637 | 1835.6638 | 1861.4668 | 1859.7229 | 1859.7229 | 1859.7229 | 1859.7229 | 1859.7229 | 1859.7229 | 1859.7229 | 1859.7229 | 1859.7229 | 1859.7229 | 1859.7229 | 1859.7229 | 1859.7229 | 1859.7229 | 1859.7229 | 1859.7229 |  | 1331.912 | 1725.4105 | 1828.4494 | 1718.1749 | 1718.6894 | 1729.2975 | 1757.2249 | 1775.9498 | 1794.2651 | 1815.6793 | 1835.5422 | 1854.8104 | 1857.0427 | 1879.5255 | 1862.546 | 1862.546 | 1862.546 | 1862.546 | 1862.546 | 1862.546 | 1862.546 | 1862.546 | 1862.546 | 1862.546 | 1862.546 | 1862.546 | 1862.546 | 1862.546 | 1862.546 | 1862.546
15% | 819.7224 | 1089.2296 | 1162.6419 | 1089.0681 | 1089.043 | 1097.4394 | 1106.6496 | 1125.5387 | 1139.1094 | 1146.4873 | 1154.5697 | 1161.9554 | 1175.2726 | 1191.7927 | 1190.6762 | 1190.6762 | 1190.6762 | 1190.6762 | 1190.6762 | 1190.6762 | 1190.6762 | 1190.6762 | 1190.6762 | 1190.6762 | 1190.6762 | 1190.6762 | 1190.6762 | 1190.6762 | 1190.6762 | 1190.6762 |  | 734.6312 | 951.6698 | 1008.502 | 947.6789 | 947.9627 | 953.8137 | 969.2174 | 979.5453 | 989.6473 | 1001.4585 | 1012.4141 | 1023.0418 | 1024.273 | 1036.6736 | 1027.3084 | 1027.3084 | 1027.3084 | 1027.3084 | 1027.3084 | 1027.3084 | 1027.3084 | 1027.3084 | 1027.3084 | 1027.3084 | 1027.3084 | 1027.3084 | 1027.3084 | 1027.3084 | 1027.3084 | 1027.3084
10% | 548.6502 | 729.0346 | 778.1704 | 728.9266 | 728.9097 | 734.5295 | 740.694 | 753.3368 | 762.4198 | 767.3579 | 772.7676 | 777.7109 | 786.6242 | 797.6814 | 796.9341 | 796.9341 | 796.9341 | 796.9341 | 796.9341 | 796.9341 | 796.9341 | 796.9341 | 796.9341 | 796.9341 | 796.9341 | 796.9341 | 796.9341 | 796.9341 | 796.9341 | 796.9341 |  | 171.688 | 222.4113 | 235.6934 | 221.4786 | 221.5449 | 222.9124 | 226.5123 | 228.926 | 231.2869 | 234.0473 | 236.6077 | 239.0914 | 239.3791 | 242.2773 | 240.0885 | 240.0885 | 240.0885 | 240.0885 | 240.0885 | 240.0885 | 240.0885 | 240.0885 | 240.0885 | 240.0885 | 240.0885 | 240.0885 | 240.0885 | 240.0885 | 240.0885 | 240.0885
5% | 390.344 | 518.6808 | 553.639 | 518.6039 | 518.5919 | 522.5902 | 526.976 | 535.9708 | 542.433 | 545.9463 | 549.7951 | 553.3121 | 559.6536 | 567.5204 | 566.9887 | 566.9887 | 566.9887 | 566.9887 | 566.9887 | 566.9887 | 566.9887 | 566.9887 | 566.9887 | 566.9887 | 566.9887 | 566.9887 | 566.9887 | 566.9887 | 566.9887 | 566.9887 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9.992e-14% | 34.2635 | 45.5286 | 48.5972 | 45.5219 | 45.5208 | 45.8718 | 46.2568 | 47.0463 | 47.6136 | 47.922 | 48.2598 | 48.5685 | 49.1251 | 49.8157 | 49.769 | 49.769 | 49.769 | 49.769 | 49.769 | 49.769 | 49.769 | 49.769 | 49.769 | 49.769 | 49.769 | 49.769 | 49.769 | 49.769 | 49.769 | 49.769 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E @ R (MWh) | 91763.8061 | 121933.7811 | 130151.918 | 121915.703 | 121912.8893 | 122852.8195 | 123883.8596 | 125998.403 | 127517.5689 | 128343.4937 | 129248.2796 | 130075.0713 | 131565.8548 | 133415.2075 | 133290.221 | 133290.221 | 133290.221 | 133290.221 | 133290.221 | 133290.221 | 133290.221 | 133290.221 | 133290.221 | 133290.221 | 133290.221 | 133290.221 | 133290.221 | 133290.221 | 133290.221 | 133290.221 | E @ R (MWh) | 89067.5772 | 115381.5956 | 122272.0083 | 114897.7383 | 114932.1408 | 115641.5297 | 117509.0874 | 118761.2611 | 119986.0387 | 121418.0476 | 122746.3179 | 124034.8249 | 124184.0988 | 125687.5687 | 124552.1189 | 124552.1189 | 124552.1189 | 124552.1189 | 124552.1189 | 124552.1189 | 124552.1189 | 124552.1189 | 124552.1189 | 124552.1189 | 124552.1189 | 124552.1189 | 124552.1189 | 124552.1189 | 124552.1189 | 124552.1189
Option 4 Summer POE50 W E @ R (MWh) N 2 | 64234.6643 | 85353.6468 | 91106.3426 | 85340.9921 | 85339.0225 | 85996.9736 | 86718.7017 | 88198.8821 | 89262.2982 | 89840.4456 | 90473.7957 | 91052.5499 | 92096.0984 | 93390.6452 | 93303.1547 | 93303.1547 | 93303.1547 | 93303.1547 | 93303.1547 | 93303.1547 | 93303.1547 | 93303.1547 | 93303.1547 | 93303.1547 | 93303.1547 | 93303.1547 | 93303.1547 | 93303.1547 | 93303.1547 | 93303.1547 | Option 4 Summer POE10 W E @ R (MWh) N 2 | 26720.2732 | 34614.4787 | 36681.6025 | 34469.3215 | 34479.6422 | 34692.4589 | 35252.7262 | 35628.3783 | 35995.8116 | 36425.4143 | 36823.8954 | 37210.4475 | 37255.2296 | 37706.2706 | 37365.6357 | 37365.6357 | 37365.6357 | 37365.6357 | 37365.6357 | 37365.6357 | 37365.6357 | 37365.6357 | 37365.6357 | 37365.6357 | 37365.6357 | 37365.6357 | 37365.6357 | 37365.6357 | 37365.6357 | 37365.6357
Option 5 - 4B LLG 2nd Tx + Switchroom + Two new feeders + OFR12 New Feeder
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | 59.6718 | 82.8348 | 88.8563 | 57.724 | 58.5246 | 59.9029 | 63.0388 | 65.1379 | 67.7971 | 69.1774 | 70.3918 | 68.1543 | 70.7765 | 74.8989 | 71.7706 | 71.7706 | 71.7706 | 71.7706 | 71.7706 | 71.7706 | 71.7706 | 71.7706 | 71.7706 | 71.7706 | 71.7706 | 71.7706 | 71.7706 | 71.7706 | 71.7706 | 71.7706 |  | 63.8857 | 86.7566 | 93.0131 | 61.8225 | 62.4371 | 63.7856 | 66.9705 | 68.7094 | 72.0219 | 82.0911 | 73.7901 | 72.1664 | 74.3582 | 79.1515 | 75.907 | 75.907 | 75.907 | 75.907 | 75.907 | 75.907 | 75.907 | 75.907 | 75.907 | 75.907 | 75.907 | 75.907 | 75.907 | 75.907 | 75.907 | 75.907
98% | 70.8865 | 98.4027 | 105.556 | 68.5726 | 69.5236 | 71.161 | 74.8863 | 77.3799 | 80.5389 | 82.1786 | 83.6212 | 80.9632 | 84.0782 | 88.9754 | 85.2591 | 85.2591 | 85.2591 | 85.2591 | 85.2591 | 85.2591 | 85.2591 | 85.2591 | 85.2591 | 85.2591 | 85.2591 | 85.2591 | 85.2591 | 85.2591 | 85.2591 | 85.2591 |  | 75.8924 | 103.0616 | 110.494 | 73.4414 | 74.1716 | 75.7735 | 79.5569 | 81.6226 | 85.5577 | 97.5193 | 87.6582 | 85.7293 | 88.333 | 94.0272 | 90.1729 | 90.1729 | 90.1729 | 90.1729 | 90.1729 | 90.1729 | 90.1729 | 90.1729 | 90.1729 | 90.1729 | 90.1729 | 90.1729 | 90.1729 | 90.1729 | 90.1729 | 90.1729
97% | 140.3338 | 194.8074 | 208.9687 | 135.753 | 137.6356 | 140.8772 | 148.252 | 153.1887 | 159.4425 | 162.6886 | 165.5444 | 160.2825 | 166.4493 | 176.1442 | 168.7871 | 168.7871 | 168.7871 | 168.7871 | 168.7871 | 168.7871 | 168.7871 | 168.7871 | 168.7871 | 168.7871 | 168.7871 | 168.7871 | 168.7871 | 168.7871 | 168.7871 | 168.7871 |  | 150.2438 | 204.0305 | 218.7445 | 145.3915 | 146.8371 | 150.0084 | 157.4985 | 161.5879 | 169.3782 | 193.0585 | 173.5365 | 169.718 | 174.8725 | 186.1453 | 178.5149 | 178.5149 | 178.5149 | 178.5149 | 178.5149 | 178.5149 | 178.5149 | 178.5149 | 178.5149 | 178.5149 | 178.5149 | 178.5149 | 178.5149 | 178.5149 | 178.5149 | 178.5149
95% | 414.5243 | 575.4311 | 617.2612 | 400.9933 | 406.5545 | 416.1295 | 437.9137 | 452.4957 | 470.9687 | 480.5572 | 488.9928 | 473.45 | 491.6656 | 520.3027 | 498.5712 | 498.5712 | 498.5712 | 498.5712 | 498.5712 | 498.5712 | 498.5712 | 498.5712 | 498.5712 | 498.5712 | 498.5712 | 498.5712 | 498.5712 | 498.5712 | 498.5712 | 498.5712 |  | 443.7972 | 602.6746 | 646.1375 | 429.4642 | 433.7342 | 443.1017 | 465.2263 | 477.3058 | 500.3171 | 570.2651 | 512.6001 | 501.3208 | 516.5464 | 549.8445 | 527.3055 | 527.3055 | 527.3055 | 527.3055 | 527.3055 | 527.3055 | 527.3055 | 527.3055 | 527.3055 | 527.3055 | 527.3055 | 527.3055 | 527.3055 | 527.3055 | 527.3055 | 527.3055
90% | 2285.5212 | 3172.6969 | 3403.3313 | 2210.9167 | 2241.5785 | 2294.3716 | 2414.4808 | 2494.8803 | 2596.7326 | 2649.6 | 2696.1103 | 2610.4137 | 2710.8474 | 2868.741 | 2748.9217 | 2748.9217 | 2748.9217 | 2748.9217 | 2748.9217 | 2748.9217 | 2748.9217 | 2748.9217 | 2748.9217 | 2748.9217 | 2748.9217 | 2748.9217 | 2748.9217 | 2748.9217 | 2748.9217 | 2748.9217 |  | 2446.9201 | 3322.9067 | 3562.5435 | 2367.8938 | 2391.4368 | 2443.0852 | 2565.0716 | 2631.6732 | 2758.5483 | 3144.2133 | 2826.2718 | 2764.0821 | 2848.0301 | 3031.6222 | 2907.3513 | 2907.3513 | 2907.3513 | 2907.3513 | 2907.3513 | 2907.3513 | 2907.3513 | 2907.3513 | 2907.3513 | 2907.3513 | 2907.3513 | 2907.3513 | 2907.3513 | 2907.3513 | 2907.3513 | 2907.3513
85% | 5583.3646 | 7750.6712 | 8314.0946 | 5401.1111 | 5476.0158 | 5604.9854 | 5898.4036 | 6094.8138 | 6343.6317 | 6472.7829 | 6586.4044 | 6377.0536 | 6622.4061 | 7008.1287 | 6715.4188 | 6715.4188 | 6715.4188 | 6715.4188 | 6715.4188 | 6715.4188 | 6715.4188 | 6715.4188 | 6715.4188 | 6715.4188 | 6715.4188 | 6715.4188 | 6715.4188 | 6715.4188 | 6715.4188 | 6715.4188 |  | 5977.6505 | 8117.623 | 8703.0385 | 5784.5949 | 5842.1089 | 5968.2822 | 6266.2861 | 6428.9891 | 6738.9358 | 7681.0879 | 6904.3795 | 6752.4545 | 6957.5335 | 7406.036 | 7102.4509 | 7102.4509 | 7102.4509 | 7102.4509 | 7102.4509 | 7102.4509 | 7102.4509 | 7102.4509 | 7102.4509 | 7102.4509 | 7102.4509 | 7102.4509 | 7102.4509 | 7102.4509 | 7102.4509 | 7102.4509
80% | 8678.2039 | 12046.8408 | 12922.5678 | 8394.9278 | 8511.3519 | 8711.809 | 9167.8679 | 9473.1474 | 9859.8843 | 10060.6235 | 10237.225 | 9911.8317 | 10293.1823 | 10892.7096 | 10437.7516 | 10437.7516 | 10437.7516 | 10437.7516 | 10437.7516 | 10437.7516 | 10437.7516 | 10437.7516 | 10437.7516 | 10437.7516 | 10437.7516 | 10437.7516 | 10437.7516 | 10437.7516 | 10437.7516 | 10437.7516 |  | 9291.041 | 12617.1926 | 13527.1019 | 8990.9753 | 9080.3691 | 9276.4798 | 9739.6662 | 9992.555 | 10474.3041 | 11938.6877 | 10731.4525 | 10495.3161 | 10814.0697 | 11511.1755 | 11039.3143 | 11039.3143 | 11039.3143 | 11039.3143 | 11039.3143 | 11039.3143 | 11039.3143 | 11039.3143 | 11039.3143 | 11039.3143 | 11039.3143 | 11039.3143 | 11039.3143 | 11039.3143 | 11039.3143 | 11039.3143
75% | 9574.4808 | 13291.0275 | 14257.1987 | 9261.9482 | 9390.3965 | 9611.5567 | 10114.7169 | 10451.5254 | 10878.2041 | 11099.6755 | 11294.5163 | 10935.5166 | 11356.2528 | 12017.6987 | 11515.753 | 11515.753 | 11515.753 | 11515.753 | 11515.753 | 11515.753 | 11515.753 | 11515.753 | 11515.753 | 11515.753 | 11515.753 | 11515.753 | 11515.753 | 11515.753 | 11515.753 | 11515.753 |  | 10250.6112 | 13920.2847 | 14924.1686 | 9919.555 | 10018.1813 | 10234.5461 | 10745.5701 | 11024.5769 | 11556.0806 | 13171.7044 | 11839.7871 | 11579.2627 | 11930.9369 | 12700.0392 | 12179.4445 | 12179.4445 | 12179.4445 | 12179.4445 | 12179.4445 | 12179.4445 | 12179.4445 | 12179.4445 | 12179.4445 | 12179.4445 | 12179.4445 | 12179.4445 | 12179.4445 | 12179.4445 | 12179.4445 | 12179.4445
70% | 10287.2444 | 14280.4661 | 15318.563 | 9951.4456 | 10089.4561 | 10327.0803 | 10867.6978 | 11229.5798 | 11688.0222 | 11925.9808 | 12135.3263 | 11749.6013 | 12201.6587 | 12912.3454 | 12373.0328 | 12373.0328 | 12373.0328 | 12373.0328 | 12373.0328 | 12373.0328 | 12373.0328 | 12373.0328 | 12373.0328 | 12373.0328 | 12373.0328 | 12373.0328 | 12373.0328 | 12373.0328 | 12373.0328 | 12373.0328 |  | 11013.7087 | 14956.5677 | 16035.1849 | 10658.0073 | 10763.9758 | 10996.4477 | 11545.5143 | 11845.2916 | 12416.3626 | 14152.26 | 12721.1894 | 12441.2705 | 12819.1247 | 13645.4821 | 13086.1323 | 13086.1323 | 13086.1323 | 13086.1323 | 13086.1323 | 13086.1323 | 13086.1323 | 13086.1323 | 13086.1323 | 13086.1323 | 13086.1323 | 13086.1323 | 13086.1323 | 13086.1323 | 13086.1323 | 13086.1323
65% | 10840.7831 | 15048.8731 | 16142.8282 | 10486.9156 | 10632.3522 | 10882.7626 | 11452.4697 | 11833.824 | 12316.9343 | 12567.6971 | 12788.3071 | 12381.8269 | 12858.2088 | 13607.1363 | 13038.8042 | 13038.8042 | 13038.8042 | 13038.8042 | 13038.8042 | 13038.8042 | 13038.8042 | 13038.8042 | 13038.8042 | 13038.8042 | 13038.8042 | 13038.8042 | 13038.8042 | 13038.8042 | 13038.8042 | 13038.8042 |  | 11606.3372 | 15761.3546 | 16898.0103 | 11231.4961 | 11343.1666 | 11588.1474 | 12166.7584 | 12482.6661 | 13084.4655 | 14913.7685 | 13405.6945 | 13110.7136 | 13508.8995 | 14379.7217 | 13790.2743 | 13790.2743 | 13790.2743 | 13790.2743 | 13790.2743 | 13790.2743 | 13790.2743 | 13790.2743 | 13790.2743 | 13790.2743 | 13790.2743 | 13790.2743 | 13790.2743 | 13790.2743 | 13790.2743 | 13790.2743
60% | 11934.3669 | 16566.9557 | 17771.2656 | 11544.8024 | 11704.9102 | 11980.5811 | 12607.7586 | 13027.5826 | 13559.4276 | 13835.4865 | 14078.351 | 13630.8663 | 14155.3041 | 14979.781 | 14354.1175 | 14354.1175 | 14354.1175 | 14354.1175 | 14354.1175 | 14354.1175 | 14354.1175 | 14354.1175 | 14354.1175 | 14354.1175 | 14354.1175 | 14354.1175 | 14354.1175 | 14354.1175 | 14354.1175 | 14354.1175 |  | 12777.1477 | 17351.3101 | 18602.628 | 12364.4938 | 12487.4293 | 12757.123 | 13394.1024 | 13741.8779 | 14404.3848 | 16418.2222 | 14758.0184 | 14433.2808 | 14871.6345 | 15830.3025 | 15181.3935 | 15181.3935 | 15181.3935 | 15181.3935 | 15181.3935 | 15181.3935 | 15181.3935 | 15181.3935 | 15181.3935 | 15181.3935 | 15181.3935 | 15181.3935 | 15181.3935 | 15181.3935 | 15181.3935 | 15181.3935
55% | 13276.2336 | 18429.6976 | 19769.4166 | 12842.8675 | 13020.9773 | 13327.644 | 14025.3395 | 14492.3673 | 15084.0115 | 15391.1097 | 15661.2812 | 15163.4826 | 15746.8866 | 16664.0655 | 15968.054 | 15968.054 | 15968.054 | 15968.054 | 15968.054 | 15968.054 | 15968.054 | 15968.054 | 15968.054 | 15968.054 | 15968.054 | 15968.054 | 15968.054 | 15968.054 | 15968.054 | 15968.054 |  | 14213.7742 | 19302.2426 | 20694.2551 | 13754.7227 | 13891.4807 | 14191.498 | 14900.0975 | 15286.9759 | 16023.9733 | 18264.2409 | 16417.3685 | 16056.1183 | 16543.7592 | 17610.2171 | 16888.3466 | 16888.3466 | 16888.3466 | 16888.3466 | 16888.3466 | 16888.3466 | 16888.3466 | 16888.3466 | 16888.3466 | 16888.3466 | 16888.3466 | 16888.3466 | 16888.3466 | 16888.3466 | 16888.3466 | 16888.3466
50% | 13456.7484 | 18680.2832 | 20038.2182 | 13017.4899 | 13198.0215 | 13508.8578 | 14216.0397 | 14689.4177 | 15289.1063 | 15600.3801 | 15874.2251 | 15369.658 | 15960.9945 | 16890.6441 | 16185.1691 | 16185.1691 | 16185.1691 | 16185.1691 | 16185.1691 | 16185.1691 | 16185.1691 | 16185.1691 | 16185.1691 | 16185.1691 | 16185.1691 | 16185.1691 | 16185.1691 | 16185.1691 | 16185.1691 | 16185.1691 |  | 14407.0366 | 19564.692 | 20975.6315 | 13941.7435 | 14080.3609 | 14384.4575 | 15102.6917 | 15494.8305 | 16241.8487 | 18512.5768 | 16640.5928 | 16274.4307 | 16768.702 | 17849.6604 | 17117.9747 | 17117.9747 | 17117.9747 | 17117.9747 | 17117.9747 | 17117.9747 | 17117.9747 | 17117.9747 | 17117.9747 | 17117.9747 | 17117.9747 | 17117.9747 | 17117.9747 | 17117.9747 | 17117.9747 | 17117.9747
45% | 10386.1977 | 14417.8303 | 15465.9127 | 10047.1688 | 10186.5069 | 10426.4168 | 10972.2345 | 11337.5975 | 11800.4496 | 12040.6971 | 12252.0564 | 11862.621 | 12319.0268 | 13036.5496 | 12492.0494 | 12492.0494 | 12492.0494 | 12492.0494 | 12492.0494 | 12492.0494 | 12492.0494 | 12492.0494 | 12492.0494 | 12492.0494 | 12492.0494 | 12492.0494 | 12492.0494 | 12492.0494 | 12492.0494 | 12492.0494 |  | 11119.6499 | 15100.4354 | 16189.4278 | 10760.527 | 10867.5148 | 11102.2228 | 11656.5709 | 11959.2318 | 12535.7959 | 14288.391 | 12843.5549 | 12560.9434 | 12942.4323 | 13776.7384 | 13212.0082 | 13212.0082 | 13212.0082 | 13212.0082 | 13212.0082 | 13212.0082 | 13212.0082 | 13212.0082 | 13212.0082 | 13212.0082 | 13212.0082 | 13212.0082 | 13212.0082 | 13212.0082 | 13212.0082 | 13212.0082
40% | 5102.6915 | 7083.4142 | 7598.3323 | 4936.1282 | 5004.5843 | 5122.451 | 5390.6087 | 5570.1099 | 5797.507 | 5915.5395 | 6019.3794 | 5828.0516 | 6052.2817 | 6404.7973 | 6137.2869 | 6137.2869 | 6137.2869 | 6137.2869 | 6137.2869 | 6137.2869 | 6137.2869 | 6137.2869 | 6137.2869 | 6137.2869 | 6137.2869 | 6137.2869 | 6137.2869 | 6137.2869 | 6137.2869 | 6137.2869 |  | 5463.0332 | 7418.775 | 7953.792 | 5286.5978 | 5339.1604 | 5454.4714 | 5726.8201 | 5875.516 | 6158.7793 | 7019.8213 | 6309.9799 | 6171.1342 | 6358.5579 | 6768.4487 | 6490.9993 | 6490.9993 | 6490.9993 | 6490.9993 | 6490.9993 | 6490.9993 | 6490.9993 | 6490.9993 | 6490.9993 | 6490.9993 | 6490.9993 | 6490.9993 | 6490.9993 | 6490.9993 | 6490.9993 | 6490.9993
35% | 1907.0998 | 2647.3829 | 2839.8304 | 1844.8478 | 1870.4329 | 1914.4848 | 2014.7071 | 2081.7946 | 2166.7829 | 2210.8968 | 2249.7063 | 2178.1987 | 2262.0034 | 2393.754 | 2293.7735 | 2293.7735 | 2293.7735 | 2293.7735 | 2293.7735 | 2293.7735 | 2293.7735 | 2293.7735 | 2293.7735 | 2293.7735 | 2293.7735 | 2293.7735 | 2293.7735 | 2293.7735 | 2293.7735 | 2293.7735 |  | 2041.7754 | 2772.7219 | 2972.6813 | 1975.8337 | 1995.4786 | 2038.5754 | 2140.3641 | 2195.9383 | 2301.8062 | 2623.6154 | 2358.3165 | 2306.4238 | 2376.4722 | 2529.6664 | 2425.9714 | 2425.9714 | 2425.9714 | 2425.9714 | 2425.9714 | 2425.9714 | 2425.9714 | 2425.9714 | 2425.9714 | 2425.9714 | 2425.9714 | 2425.9714 | 2425.9714 | 2425.9714 | 2425.9714 | 2425.9714
30% | 951.1511 | 1320.3614 | 1416.3431 | 920.1033 | 932.8637 | 954.8343 | 1004.8194 | 1038.2787 | 1080.6659 | 1102.6674 | 1122.0234 | 1086.3595 | 1128.1564 | 1193.866 | 1144.0015 | 1144.0015 | 1144.0015 | 1144.0015 | 1144.0015 | 1144.0015 | 1144.0015 | 1144.0015 | 1144.0015 | 1144.0015 | 1144.0015 | 1144.0015 | 1144.0015 | 1144.0015 | 1144.0015 | 1144.0015 |  | 1018.3194 | 1382.8733 | 1482.6014 | 985.4315 | 995.2293 | 1016.7235 | 1067.4898 | 1095.2069 | 1148.0078 | 1308.5076 | 1176.1918 | 1150.3107 | 1185.2469 | 1261.6512 | 1209.9342 | 1209.9342 | 1209.9342 | 1209.9342 | 1209.9342 | 1209.9342 | 1209.9342 | 1209.9342 | 1209.9342 | 1209.9342 | 1209.9342 | 1209.9342 | 1209.9342 | 1209.9342 | 1209.9342 | 1209.9342
25% | 560.7353 | 778.3972 | 834.9816 | 542.4317 | 549.9543 | 562.9067 | 592.3746 | 612.1 | 637.0887 | 650.0593 | 661.4703 | 640.4452 | 665.0859 | 703.8239 | 674.4271 | 674.4271 | 674.4271 | 674.4271 | 674.4271 | 674.4271 | 674.4271 | 674.4271 | 674.4271 | 674.4271 | 674.4271 | 674.4271 | 674.4271 | 674.4271 | 674.4271 | 674.4271 |  | 600.3333 | 815.25 | 874.0431 | 580.9448 | 586.7209 | 599.3925 | 629.3209 | 645.6611 | 676.7889 | 771.4089 | 693.4044 | 678.1466 | 698.7426 | 743.7856 | 713.2966 | 713.2966 | 713.2966 | 713.2966 | 713.2966 | 713.2966 | 713.2966 | 713.2966 | 713.2966 | 713.2966 | 713.2966 | 713.2966 | 713.2966 | 713.2966 | 713.2966 | 713.2966
20% | 283.3663 | 393.3611 | 421.9559 | 274.1165 | 277.9181 | 284.4635 | 299.3551 | 309.3233 | 321.9512 | 328.5059 | 334.2724 | 323.6475 | 336.0996 | 355.6757 | 340.8201 | 340.8201 | 340.8201 | 340.8201 | 340.8201 | 340.8201 | 340.8201 | 340.8201 | 340.8201 | 340.8201 | 340.8201 | 340.8201 | 340.8201 | 340.8201 | 340.8201 | 340.8201 |  | 303.377 | 411.9846 | 441.6956 | 293.5791 | 296.498 | 302.9015 | 318.0258 | 326.2833 | 342.0137 | 389.8296 | 350.4102 | 342.6998 | 353.1079 | 375.8702 | 360.4627 | 360.4627 | 360.4627 | 360.4627 | 360.4627 | 360.4627 | 360.4627 | 360.4627 | 360.4627 | 360.4627 | 360.4627 | 360.4627 | 360.4627 | 360.4627 | 360.4627 | 360.4627
15% | 115.4455 | 160.2582 | 171.908 | 111.6771 | 113.2259 | 115.8926 | 121.9595 | 126.0206 | 131.1653 | 133.8357 | 136.1851 | 131.8564 | 136.9294 | 144.9049 | 138.8526 | 138.8526 | 138.8526 | 138.8526 | 138.8526 | 138.8526 | 138.8526 | 138.8526 | 138.8526 | 138.8526 | 138.8526 | 138.8526 | 138.8526 | 138.8526 | 138.8526 | 138.8526 |  | 123.598 | 167.8456 | 179.95 | 119.6063 | 120.7955 | 123.4043 | 129.5661 | 132.9302 | 139.3389 | 158.8195 | 142.7597 | 139.6184 | 143.8588 | 153.1323 | 146.8552 | 146.8552 | 146.8552 | 146.8552 | 146.8552 | 146.8552 | 146.8552 | 146.8552 | 146.8552 | 146.8552 | 146.8552 | 146.8552 | 146.8552 | 146.8552 | 146.8552 | 146.8552
10% | 46.4781 | 64.5196 | 69.2097 | 44.9609 | 45.5844 | 46.658 | 49.1006 | 50.7356 | 52.8068 | 53.8819 | 54.8277 | 53.085 | 55.1274 | 58.3383 | 55.9017 | 55.9017 | 55.9017 | 55.9017 | 55.9017 | 55.9017 | 55.9017 | 55.9017 | 55.9017 | 55.9017 | 55.9017 | 55.9017 | 55.9017 | 55.9017 | 55.9017 | 55.9017 |  | 49.7602 | 67.5742 | 72.4474 | 48.1532 | 48.6319 | 49.6823 | 52.163 | 53.5174 | 56.0975 | 63.9403 | 57.4747 | 56.21 | 57.9172 | 61.6507 | 59.1235 | 59.1235 | 59.1235 | 59.1235 | 59.1235 | 59.1235 | 59.1235 | 59.1235 | 59.1235 | 59.1235 | 59.1235 | 59.1235 | 59.1235 | 59.1235 | 59.1235 | 59.1235
5% | 39.5813 | 54.9457 | 58.9399 | 38.2893 | 38.8203 | 39.7346 | 41.8147 | 43.2071 | 44.971 | 45.8865 | 46.692 | 45.2079 | 46.9472 | 49.6817 | 47.6066 | 47.6066 | 47.6066 | 47.6066 | 47.6066 | 47.6066 | 47.6066 | 47.6066 | 47.6066 | 47.6066 | 47.6066 | 47.6066 | 47.6066 | 47.6066 | 47.6066 | 47.6066 |  | 42.3765 | 57.5471 | 61.6972 | 41.0079 | 41.4156 | 42.3101 | 44.4227 | 45.5761 | 47.7733 | 54.4524 | 48.9462 | 47.8692 | 49.323 | 52.5025 | 50.3504 | 50.3504 | 50.3504 | 50.3504 | 50.3504 | 50.3504 | 50.3504 | 50.3504 | 50.3504 | 50.3504 | 50.3504 | 50.3504 | 50.3504 | 50.3504 | 50.3504 | 50.3504
9.992e-14% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E @ R (MWh) | 105995.1099 | 147139.4588 | 157835.5397 | 102535.1914 | 103957.1891 | 106405.5615 | 111975.8394 | 115704.5076 | 120428.0902 | 122879.9081 | 125036.9099 | 121062.5737 | 125720.3688 | 133042.963 | 127486.1302 | 127486.1302 | 127486.1302 | 127486.1302 | 127486.1302 | 127486.1302 | 127486.1302 | 127486.1302 | 127486.1302 | 127486.1302 | 127486.1302 | 127486.1302 | 127486.1302 | 127486.1302 | 127486.1302 | 127486.1302 | E @ R (MWh) | 113480.2695 | 154105.704 | 165219.287 | 109815.2831 | 110907.1344 | 113302.4197 | 118959.7537 | 122048.5228 | 127932.5801 | 145818.4818 | 131073.3776 | 128189.2197 | 132082.4592 | 140596.8712 | 134833.5841 | 134833.5841 | 134833.5841 | 134833.5841 | 134833.5841 | 134833.5841 | 134833.5841 | 134833.5841 | 134833.5841 | 134833.5841 | 134833.5841 | 134833.5841 | 134833.5841 | 134833.5841 | 134833.5841 | 134833.5841
Option 5 Winter POE50 W E @ R (MWh) N 2 | 74196.5769 | 102997.6211 | 110484.8778 | 71774.634 | 72770.0324 | 74483.8931 | 78383.0876 | 80993.1553 | 84299.6631 | 86015.9357 | 87525.837 | 84743.8016 | 88004.2582 | 93130.0741 | 89240.2911 | 89240.2911 | 89240.2911 | 89240.2911 | 89240.2911 | 89240.2911 | 89240.2911 | 89240.2911 | 89240.2911 | 89240.2911 | 89240.2911 | 89240.2911 | 89240.2911 | 89240.2911 | 89240.2911 | 89240.2911 | Option 5 Winter POE10 W E @ R (MWh) N 2 | 34044.0809 | 46231.7112 | 49565.7861 | 32944.5849 | 33272.1403 | 33990.7259 | 35687.9261 | 36614.5568 | 38379.774 | 43745.5445 | 39322.0133 | 38456.7659 | 39624.7378 | 42179.0614 | 40450.0752 | 40450.0752 | 40450.0752 | 40450.0752 | 40450.0752 | 40450.0752 | 40450.0752 | 40450.0752 | 40450.0752 | 40450.0752 | 40450.0752 | 40450.0752 | 40450.0752 | 40450.0752 | 40450.0752 | 40450.0752
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 76.9936 | 99.7405 | 105.6969 | 72.6068 | 72.6366 | 73.2498 | 74.8642 | 75.9466 | 77.0054 | 78.2432 | 79.3915 | 80.5053 | 80.6343 | 81.934 | 80.9525 | 80.9525 | 80.9525 | 80.9525 | 80.9525 | 80.9525 | 80.9525 | 80.9525 | 80.9525 | 80.9525 | 80.9525 | 80.9525 | 80.9525 | 80.9525 | 80.9525 | 80.9525
98% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 38.1099 | 49.369 | 52.3173 | 35.9386 | 35.9533 | 36.2568 | 37.0559 | 37.5917 | 38.1157 | 38.7284 | 39.2968 | 39.8481 | 39.912 | 40.5553 | 40.0694 | 40.0694 | 40.0694 | 40.0694 | 40.0694 | 40.0694 | 40.0694 | 40.0694 | 40.0694 | 40.0694 | 40.0694 | 40.0694 | 40.0694 | 40.0694 | 40.0694 | 40.0694
97% | 16.9149 | 22.4762 | 23.991 | 15.9282 | 15.9277 | 16.101 | 16.291 | 16.6808 | 16.9608 | 17.1131 | 17.2798 | 17.4323 | 17.7071 | 18.0479 | 18.0249 | 18.0249 | 18.0249 | 18.0249 | 18.0249 | 18.0249 | 18.0249 | 18.0249 | 18.0249 | 18.0249 | 18.0249 | 18.0249 | 18.0249 | 18.0249 | 18.0249 | 18.0249 |  | 75.446 | 97.7357 | 103.5723 | 71.1474 | 71.1765 | 71.7774 | 73.3594 | 74.42 | 75.4575 | 76.6705 | 77.7956 | 78.8871 | 79.0135 | 80.2871 | 79.3253 | 79.3253 | 79.3253 | 79.3253 | 79.3253 | 79.3253 | 79.3253 | 79.3253 | 79.3253 | 79.3253 | 79.3253 | 79.3253 | 79.3253 | 79.3253 | 79.3253 | 79.3253
95% | 83.2734 | 110.6519 | 118.1097 | 78.4159 | 78.4133 | 79.2663 | 80.2019 | 82.1208 | 83.4995 | 84.249 | 85.07 | 85.8203 | 87.1732 | 88.8514 | 88.738 | 88.738 | 88.738 | 88.738 | 88.738 | 88.738 | 88.738 | 88.738 | 88.738 | 88.738 | 88.738 | 88.738 | 88.738 | 88.738 | 88.738 | 88.738 |  | 111.4279 | 144.3481 | 152.9683 | 105.0792 | 105.1223 | 106.0097 | 108.3461 | 109.9127 | 111.4449 | 113.2365 | 114.8982 | 116.5102 | 116.6969 | 118.5778 | 117.1573 | 117.1573 | 117.1573 | 117.1573 | 117.1573 | 117.1573 | 117.1573 | 117.1573 | 117.1573 | 117.1573 | 117.1573 | 117.1573 | 117.1573 | 117.1573 | 117.1573 | 117.1573
90% | 144.4273 | 191.9119 | 204.8464 | 136.0026 | 135.9981 | 137.4775 | 139.1003 | 142.4283 | 144.8194 | 146.1193 | 147.5433 | 148.8446 | 151.191 | 154.1017 | 153.905 | 153.905 | 153.905 | 153.905 | 153.905 | 153.905 | 153.905 | 153.905 | 153.905 | 153.905 | 153.905 | 153.905 | 153.905 | 153.905 | 153.905 | 153.905 |  | 483.1446 | 625.8842 | 663.261 | 455.6169 | 455.8036 | 459.6516 | 469.7821 | 476.5745 | 483.2183 | 490.9862 | 498.1913 | 505.1808 | 505.9905 | 514.1461 | 507.9869 | 507.9869 | 507.9869 | 507.9869 | 507.9869 | 507.9869 | 507.9869 | 507.9869 | 507.9869 | 507.9869 | 507.9869 | 507.9869 | 507.9869 | 507.9869 | 507.9869 | 507.9869
85% | 409.8612 | 544.6148 | 581.321 | 385.9532 | 385.9407 | 390.1388 | 394.744 | 404.1885 | 410.9739 | 414.6628 | 418.704 | 422.3969 | 429.0554 | 437.3155 | 436.7573 | 436.7573 | 436.7573 | 436.7573 | 436.7573 | 436.7573 | 436.7573 | 436.7573 | 436.7573 | 436.7573 | 436.7573 | 436.7573 | 436.7573 | 436.7573 | 436.7573 | 436.7573 |  | 457.0286 | 592.0526 | 627.4091 | 430.989 | 431.1655 | 434.8056 | 444.3885 | 450.8137 | 457.0984 | 464.4464 | 471.2621 | 477.8737 | 478.6397 | 486.3544 | 480.5281 | 480.5281 | 480.5281 | 480.5281 | 480.5281 | 480.5281 | 480.5281 | 480.5281 | 480.5281 | 480.5281 | 480.5281 | 480.5281 | 480.5281 | 480.5281 | 480.5281 | 480.5281
80% | 572.5046 | 760.7318 | 812.0039 | 539.1093 | 539.0917 | 544.9559 | 551.3884 | 564.5808 | 574.0587 | 579.2116 | 584.8564 | 590.0147 | 599.3155 | 610.8535 | 610.0737 | 610.0737 | 610.0737 | 610.0737 | 610.0737 | 610.0737 | 610.0737 | 610.0737 | 610.0737 | 610.0737 | 610.0737 | 610.0737 | 610.0737 | 610.0737 | 610.0737 | 610.0737 |  | 319.1946 | 413.4971 | 438.1905 | 301.0082 | 301.1315 | 303.6737 | 310.3666 | 314.854 | 319.2433 | 324.3752 | 329.1354 | 333.7531 | 334.288 | 339.6761 | 335.6069 | 335.6069 | 335.6069 | 335.6069 | 335.6069 | 335.6069 | 335.6069 | 335.6069 | 335.6069 | 335.6069 | 335.6069 | 335.6069 | 335.6069 | 335.6069 | 335.6069 | 335.6069
75% | 1492.4153 | 1983.0895 | 2116.7465 | 1405.3599 | 1405.3141 | 1420.6008 | 1437.3693 | 1471.7595 | 1496.4667 | 1509.8993 | 1524.6144 | 1538.0611 | 1562.3067 | 1592.3839 | 1590.3512 | 1590.3512 | 1590.3512 | 1590.3512 | 1590.3512 | 1590.3512 | 1590.3512 | 1590.3512 | 1590.3512 | 1590.3512 | 1590.3512 | 1590.3512 | 1590.3512 | 1590.3512 | 1590.3512 | 1590.3512 |  | 569.714 | 738.0296 | 782.1036 | 537.254 | 537.4741 | 542.0116 | 553.9573 | 561.9667 | 569.8009 | 578.9607 | 587.4569 | 595.6987 | 596.6535 | 606.2703 | 599.0075 | 599.0075 | 599.0075 | 599.0075 | 599.0075 | 599.0075 | 599.0075 | 599.0075 | 599.0075 | 599.0075 | 599.0075 | 599.0075 | 599.0075 | 599.0075 | 599.0075 | 599.0075
70% | 2578.4391 | 3426.1747 | 3657.0932 | 2428.0338 | 2427.9548 | 2454.3656 | 2483.3364 | 2542.7522 | 2585.4387 | 2608.6461 | 2634.0694 | 2657.3011 | 2699.1901 | 2751.1544 | 2747.6425 | 2747.6425 | 2747.6425 | 2747.6425 | 2747.6425 | 2747.6425 | 2747.6425 | 2747.6425 | 2747.6425 | 2747.6425 | 2747.6425 | 2747.6425 | 2747.6425 | 2747.6425 | 2747.6425 | 2747.6425 |  | 1037.8661 | 1344.492 | 1424.783 | 978.7327 | 979.1336 | 987.3998 | 1009.1616 | 1023.7526 | 1038.0245 | 1054.711 | 1070.1888 | 1085.2032 | 1086.9426 | 1104.4619 | 1091.231 | 1091.231 | 1091.231 | 1091.231 | 1091.231 | 1091.231 | 1091.231 | 1091.231 | 1091.231 | 1091.231 | 1091.231 | 1091.231 | 1091.231 | 1091.231 | 1091.231 | 1091.231
65% | 6475.8072 | 8604.914 | 9184.8711 | 6098.0611 | 6097.8626 | 6164.1938 | 6236.9547 | 6386.1788 | 6493.387 | 6551.6728 | 6615.5239 | 6673.8709 | 6779.0761 | 6909.5856 | 6900.7653 | 6900.7653 | 6900.7653 | 6900.7653 | 6900.7653 | 6900.7653 | 6900.7653 | 6900.7653 | 6900.7653 | 6900.7653 | 6900.7653 | 6900.7653 | 6900.7653 | 6900.7653 | 6900.7653 | 6900.7653 |  | 1305.7961 | 1691.5789 | 1792.5974 | 1231.3971 | 1231.9015 | 1242.3017 | 1269.6814 | 1288.0392 | 1305.9954 | 1326.9897 | 1346.4631 | 1365.3535 | 1367.542 | 1389.584 | 1372.9374 | 1372.9374 | 1372.9374 | 1372.9374 | 1372.9374 | 1372.9374 | 1372.9374 | 1372.9374 | 1372.9374 | 1372.9374 | 1372.9374 | 1372.9374 | 1372.9374 | 1372.9374 | 1372.9374 | 1372.9374
60% | 9465.8424 | 12578.0087 | 13425.7459 | 8913.6819 | 8913.3916 | 9010.3496 | 9116.7059 | 9334.8304 | 9491.5391 | 9576.7369 | 9670.0696 | 9755.3568 | 9909.1377 | 10099.9066 | 10087.0137 | 10087.0137 | 10087.0137 | 10087.0137 | 10087.0137 | 10087.0137 | 10087.0137 | 10087.0137 | 10087.0137 | 10087.0137 | 10087.0137 | 10087.0137 | 10087.0137 | 10087.0137 | 10087.0137 | 10087.0137 |  | 2043.3291 | 2647.0078 | 2805.083 | 1926.9085 | 1927.6977 | 1943.972 | 1986.8163 | 2015.5428 | 2043.6409 | 2076.4931 | 2106.9654 | 2136.5254 | 2139.95 | 2174.4416 | 2148.3928 | 2148.3928 | 2148.3928 | 2148.3928 | 2148.3928 | 2148.3928 | 2148.3928 | 2148.3928 | 2148.3928 | 2148.3928 | 2148.3928 | 2148.3928 | 2148.3928 | 2148.3928 | 2148.3928 | 2148.3928
55% | 10703.6666 | 14222.8031 | 15181.3967 | 10079.3015 | 10078.9733 | 10188.6102 | 10308.8745 | 10555.5226 | 10732.7237 | 10829.0626 | 10934.6001 | 11031.0401 | 11204.9306 | 11420.6458 | 11406.067 | 11406.067 | 11406.067 | 11406.067 | 11406.067 | 11406.067 | 11406.067 | 11406.067 | 11406.067 | 11406.067 | 11406.067 | 11406.067 | 11406.067 | 11406.067 | 11406.067 | 11406.067 |  | 3926.5772 | 5086.6405 | 5390.4069 | 3702.8568 | 3704.3734 | 3735.6471 | 3817.9791 | 3873.1816 | 3927.1764 | 3990.307 | 4048.8643 | 4105.6686 | 4112.2494 | 4178.5305 | 4128.4737 | 4128.4737 | 4128.4737 | 4128.4737 | 4128.4737 | 4128.4737 | 4128.4737 | 4128.4737 | 4128.4737 | 4128.4737 | 4128.4737 | 4128.4737 | 4128.4737 | 4128.4737 | 4128.4737 | 4128.4737
50% | 13744.0128 | 18262.75 | 19493.6294 | 12942.2985 | 12941.8771 | 13082.656 | 13237.0811 | 13553.7888 | 13781.3234 | 13905.0271 | 14040.5423 | 14164.3758 | 14387.6593 | 14664.6479 | 14645.9279 | 14645.9279 | 14645.9279 | 14645.9279 | 14645.9279 | 14645.9279 | 14645.9279 | 14645.9279 | 14645.9279 | 14645.9279 | 14645.9279 | 14645.9279 | 14645.9279 | 14645.9279 | 14645.9279 | 14645.9279 |  | 8714.0125 | 11288.47 | 11962.6002 | 8217.5235 | 8220.8893 | 8290.2931 | 8473.0074 | 8595.515 | 8715.3423 | 8855.4443 | 8985.3969 | 9111.4592 | 9126.0636 | 9273.157 | 9162.0692 | 9162.0692 | 9162.0692 | 9162.0692 | 9162.0692 | 9162.0692 | 9162.0692 | 9162.0692 | 9162.0692 | 9162.0692 | 9162.0692 | 9162.0692 | 9162.0692 | 9162.0692 | 9162.0692 | 9162.0692
45% | 18302.3635 | 24319.7888 | 25958.9027 | 17234.752 | 17234.1908 | 17421.6606 | 17627.3023 | 18049.0497 | 18352.0485 | 18516.7799 | 18697.2401 | 18862.1444 | 19159.4823 | 19528.3372 | 19503.4085 | 19503.4085 | 19503.4085 | 19503.4085 | 19503.4085 | 19503.4085 | 19503.4085 | 19503.4085 | 19503.4085 | 19503.4085 | 19503.4085 | 19503.4085 | 19503.4085 | 19503.4085 | 19503.4085 | 19503.4085 |  | 13204.5002 | 17105.6219 | 18127.1435 | 12452.1614 | 12457.2617 | 12562.4305 | 12839.3007 | 13024.9387 | 13206.5152 | 13418.8143 | 13615.7338 | 13806.7583 | 13828.8886 | 14051.7819 | 13883.4485 | 13883.4485 | 13883.4485 | 13883.4485 | 13883.4485 | 13883.4485 | 13883.4485 | 13883.4485 | 13883.4485 | 13883.4485 | 13883.4485 | 13883.4485 | 13883.4485 | 13883.4485 | 13883.4485 | 13883.4485
40% | 12836.6798 | 17057.1053 | 18206.7263 | 12087.892 | 12087.4984 | 12218.9836 | 12363.214 | 12659.0138 | 12871.5273 | 12987.0645 | 13113.6334 | 13229.2919 | 13437.835 | 13696.5377 | 13679.0536 | 13679.0536 | 13679.0536 | 13679.0536 | 13679.0536 | 13679.0536 | 13679.0536 | 13679.0536 | 13679.0536 | 13679.0536 | 13679.0536 | 13679.0536 | 13679.0536 | 13679.0536 | 13679.0536 | 13679.0536 |  | 13672.6523 | 17712.0843 | 18769.8229 | 12893.6401 | 12898.9212 | 13007.8186 | 13294.505 | 13486.7247 | 13674.7387 | 13894.5646 | 14098.4657 | 14296.2628 | 14319.1777 | 14549.9735 | 14375.672 | 14375.672 | 14375.672 | 14375.672 | 14375.672 | 14375.672 | 14375.672 | 14375.672 | 14375.672 | 14375.672 | 14375.672 | 14375.672 | 14375.672 | 14375.672 | 14375.672 | 14375.672
35% | 6655.3655 | 8843.5072 | 9439.545 | 6267.1454 | 6266.9413 | 6335.1118 | 6409.8902 | 6563.2519 | 6673.4327 | 6733.3346 | 6798.9561 | 6858.921 | 6967.0432 | 7101.1715 | 7092.1065 | 7092.1065 | 7092.1065 | 7092.1065 | 7092.1065 | 7092.1065 | 7092.1065 | 7092.1065 | 7092.1065 | 7092.1065 | 7092.1065 | 7092.1065 | 7092.1065 | 7092.1065 | 7092.1065 | 7092.1065 |  | 18622.1031 | 24123.7949 | 25564.4311 | 17561.0913 | 17568.2841 | 17716.602 | 18107.0679 | 18368.8703 | 18624.9448 | 18924.3469 | 19202.0595 | 19471.4584 | 19502.6683 | 19817.0114 | 19579.6134 | 19579.6134 | 19579.6134 | 19579.6134 | 19579.6134 | 19579.6134 | 19579.6134 | 19579.6134 | 19579.6134 | 19579.6134 | 19579.6134 | 19579.6134 | 19579.6134 | 19579.6134 | 19579.6134 | 19579.6134
30% | 3095.428 | 4113.1385 | 4390.3573 | 2914.8659 | 2914.771 | 2946.4772 | 2981.2568 | 3052.5858 | 3103.8311 | 3131.6917 | 3162.2124 | 3190.1022 | 3240.3902 | 3302.7736 | 3298.5575 | 3298.5575 | 3298.5575 | 3298.5575 | 3298.5575 | 3298.5575 | 3298.5575 | 3298.5575 | 3298.5575 | 3298.5575 | 3298.5575 | 3298.5575 | 3298.5575 | 3298.5575 | 3298.5575 | 3298.5575 |  | 17207.9743 | 22291.8776 | 23623.1145 | 16227.5338 | 16234.1804 | 16371.2353 | 16732.0499 | 16973.9716 | 17210.6002 | 17487.2662 | 17743.8898 | 17992.8311 | 18021.671 | 18312.1434 | 18092.773 | 18092.773 | 18092.773 | 18092.773 | 18092.773 | 18092.773 | 18092.773 | 18092.773 | 18092.773 | 18092.773 | 18092.773 | 18092.773 | 18092.773 | 18092.773 | 18092.773 | 18092.773
25% | 2113.496 | 2808.3682 | 2997.6476 | 1990.2118 | 1990.147 | 2011.7954 | 2035.5422 | 2084.2442 | 2119.2335 | 2138.2561 | 2159.095 | 2178.1376 | 2212.4732 | 2255.0674 | 2252.1887 | 2252.1887 | 2252.1887 | 2252.1887 | 2252.1887 | 2252.1887 | 2252.1887 | 2252.1887 | 2252.1887 | 2252.1887 | 2252.1887 | 2252.1887 | 2252.1887 | 2252.1887 | 2252.1887 | 2252.1887 |  | 4963.476 | 6429.8794 | 6813.862 | 4680.6773 | 4682.5945 | 4722.1266 | 4826.2002 | 4895.9802 | 4964.2334 | 5044.0351 | 5118.0557 | 5189.8605 | 5198.1791 | 5281.9631 | 5218.6878 | 5218.6878 | 5218.6878 | 5218.6878 | 5218.6878 | 5218.6878 | 5218.6878 | 5218.6878 | 5218.6878 | 5218.6878 | 5218.6878 | 5218.6878 | 5218.6878 | 5218.6878 | 5218.6878 | 5218.6878
20% | 1280.3284 | 1701.2729 | 1815.9359 | 1205.6444 | 1205.6051 | 1218.7194 | 1233.105 | 1262.608 | 1283.8041 | 1295.3277 | 1307.9517 | 1319.4874 | 1340.2875 | 1366.0905 | 1364.3466 | 1364.3466 | 1364.3466 | 1364.3466 | 1364.3466 | 1364.3466 | 1364.3466 | 1364.3466 | 1364.3466 | 1364.3466 | 1364.3466 | 1364.3466 | 1364.3466 | 1364.3466 | 1364.3466 | 1364.3466 |  | 1331.912 | 1725.4105 | 1828.4494 | 1256.0251 | 1256.5395 | 1267.1477 | 1295.0751 | 1313.8 | 1332.1153 | 1353.5294 | 1373.3923 | 1392.6606 | 1394.8928 | 1417.3756 | 1400.3962 | 1400.3962 | 1400.3962 | 1400.3962 | 1400.3962 | 1400.3962 | 1400.3962 | 1400.3962 | 1400.3962 | 1400.3962 | 1400.3962 | 1400.3962 | 1400.3962 | 1400.3962 | 1400.3962 | 1400.3962
15% | 819.7224 | 1089.2296 | 1162.6419 | 771.9065 | 771.8813 | 780.2777 | 789.4879 | 808.3771 | 821.9477 | 829.3257 | 837.4081 | 844.7938 | 858.1109 | 874.6311 | 873.5146 | 873.5146 | 873.5146 | 873.5146 | 873.5146 | 873.5146 | 873.5146 | 873.5146 | 873.5146 | 873.5146 | 873.5146 | 873.5146 | 873.5146 | 873.5146 | 873.5146 | 873.5146 |  | 734.6312 | 951.6698 | 1008.502 | 692.7749 | 693.0587 | 698.9097 | 714.3134 | 724.6413 | 734.7433 | 746.5545 | 757.5102 | 768.1378 | 769.369 | 781.7696 | 772.4044 | 772.4044 | 772.4044 | 772.4044 | 772.4044 | 772.4044 | 772.4044 | 772.4044 | 772.4044 | 772.4044 | 772.4044 | 772.4044 | 772.4044 | 772.4044 | 772.4044 | 772.4044
10% | 548.6502 | 729.0346 | 778.1704 | 516.6464 | 516.6296 | 522.2494 | 528.4139 | 541.0566 | 550.1396 | 555.0778 | 560.4874 | 565.4308 | 574.3441 | 585.4012 | 584.6539 | 584.6539 | 584.6539 | 584.6539 | 584.6539 | 584.6539 | 584.6539 | 584.6539 | 584.6539 | 584.6539 | 584.6539 | 584.6539 | 584.6539 | 584.6539 | 584.6539 | 584.6539 |  | 171.688 | 222.4113 | 235.6934 | 161.9059 | 161.9722 | 163.3397 | 166.9396 | 169.3533 | 171.7142 | 174.4746 | 177.035 | 179.5187 | 179.8064 | 182.7046 | 180.5158 | 180.5158 | 180.5158 | 180.5158 | 180.5158 | 180.5158 | 180.5158 | 180.5158 | 180.5158 | 180.5158 | 180.5158 | 180.5158 | 180.5158 | 180.5158 | 180.5158 | 180.5158
5% | 390.344 | 518.6808 | 553.639 | 367.5745 | 367.5625 | 371.5608 | 375.9466 | 384.9415 | 391.4037 | 394.917 | 398.7658 | 402.2828 | 408.6242 | 416.491 | 415.9593 | 415.9593 | 415.9593 | 415.9593 | 415.9593 | 415.9593 | 415.9593 | 415.9593 | 415.9593 | 415.9593 | 415.9593 | 415.9593 | 415.9593 | 415.9593 | 415.9593 | 415.9593 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9.992e-14% | 34.2635 | 45.5286 | 48.5972 | 32.2649 | 32.2638 | 32.6148 | 32.9998 | 33.7893 | 34.3565 | 34.6649 | 35.0028 | 35.3115 | 35.8681 | 36.5587 | 36.512 | 36.512 | 36.512 | 36.512 | 36.512 | 36.512 | 36.512 | 36.512 | 36.512 | 36.512 | 36.512 | 36.512 | 36.512 | 36.512 | 36.512 | 36.512 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E @ R (MWh) | 91763.8061 | 121933.7811 | 130151.918 | 86411.0496 | 86408.2359 | 87348.166 | 88379.2062 | 90493.7495 | 92012.9154 | 92838.8403 | 93743.6261 | 94570.4179 | 96061.2013 | 97910.554 | 97785.5676 | 97785.5676 | 97785.5676 | 97785.5676 | 97785.5676 | 97785.5676 | 97785.5676 | 97785.5676 | 97785.5676 | 97785.5676 | 97785.5676 | 97785.5676 | 97785.5676 | 97785.5676 | 97785.5676 | 97785.5676 | E @ R (MWh) | 89067.5772 | 115381.5956 | 122272.0083 | 83992.8686 | 84027.2711 | 84736.6601 | 86604.2177 | 87856.3914 | 89081.169 | 90513.1779 | 91841.4482 | 93129.9553 | 93279.2291 | 94782.699 | 93647.2492 | 93647.2492 | 93647.2492 | 93647.2492 | 93647.2492 | 93647.2492 | 93647.2492 | 93647.2492 | 93647.2492 | 93647.2492 | 93647.2492 | 93647.2492 | 93647.2492 | 93647.2492 | 93647.2492 | 93647.2492
Option 5 Summer POE50 W E @ R (MWh) N 2 | 64234.6643 | 85353.6468 | 91106.3426 | 60487.7347 | 60485.7651 | 61143.7162 | 61865.4443 | 63345.6247 | 64409.0408 | 64987.1882 | 65620.5383 | 66199.2925 | 67242.8409 | 68537.3878 | 68449.8973 | 68449.8973 | 68449.8973 | 68449.8973 | 68449.8973 | 68449.8973 | 68449.8973 | 68449.8973 | 68449.8973 | 68449.8973 | 68449.8973 | 68449.8973 | 68449.8973 | 68449.8973 | 68449.8973 | 68449.8973 | Option 5 Summer POE10 W E @ R (MWh) N 2 | 26720.2732 | 34614.4787 | 36681.6025 | 25197.8606 | 25208.1813 | 25420.998 | 25981.2653 | 26356.9174 | 26724.3507 | 27153.9534 | 27552.4345 | 27938.9866 | 27983.7687 | 28434.8097 | 28094.1748 | 28094.1748 | 28094.1748 | 28094.1748 | 28094.1748 | 28094.1748 | 28094.1748 | 28094.1748 | 28094.1748 | 28094.1748 | 28094.1748 | 28094.1748 | 28094.1748 | 28094.1748 | 28094.1748 | 28094.1748
Option 6 -
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | 59.6718 | 82.8348 | 88.8563 | 89.8828 | 90.6833 | 92.0616 | 95.1975 | 97.2967 | 99.9559 | 101.3362 | 102.5505 | 100.3131 | 102.9353 | 107.0576 | 103.9293 | 103.9293 | 103.9293 | 103.9293 | 103.9293 | 103.9293 | 103.9293 | 103.9293 | 103.9293 | 103.9293 | 103.9293 | 103.9293 | 103.9293 | 103.9293 | 103.9293 | 103.9293 |  | 63.8857 | 86.7566 | 93.0131 | 93.9812 | 94.5959 | 95.9444 | 99.1293 | 100.8681 | 104.1807 | 114.2499 | 105.9488 | 104.3251 | 106.5169 | 111.3103 | 108.0657 | 108.0657 | 108.0657 | 108.0657 | 108.0657 | 108.0657 | 108.0657 | 108.0657 | 108.0657 | 108.0657 | 108.0657 | 108.0657 | 108.0657 | 108.0657 | 108.0657 | 108.0657
98% | 70.8865 | 98.4027 | 105.556 | 106.7753 | 107.7263 | 109.3637 | 113.0889 | 115.5826 | 118.7416 | 120.3813 | 121.8238 | 119.1659 | 122.2809 | 127.178 | 123.4618 | 123.4618 | 123.4618 | 123.4618 | 123.4618 | 123.4618 | 123.4618 | 123.4618 | 123.4618 | 123.4618 | 123.4618 | 123.4618 | 123.4618 | 123.4618 | 123.4618 | 123.4618 |  | 75.8924 | 103.0616 | 110.494 | 111.644 | 112.3742 | 113.9761 | 117.7596 | 119.8253 | 123.7603 | 135.7219 | 125.8608 | 123.932 | 126.5357 | 132.2299 | 128.3755 | 128.3755 | 128.3755 | 128.3755 | 128.3755 | 128.3755 | 128.3755 | 128.3755 | 128.3755 | 128.3755 | 128.3755 | 128.3755 | 128.3755 | 128.3755 | 128.3755 | 128.3755
97% | 140.3338 | 194.8074 | 208.9687 | 211.3826 | 213.2652 | 216.5068 | 223.8816 | 228.8183 | 235.0721 | 238.3182 | 241.174 | 235.9121 | 242.0789 | 251.7738 | 244.4167 | 244.4167 | 244.4167 | 244.4167 | 244.4167 | 244.4167 | 244.4167 | 244.4167 | 244.4167 | 244.4167 | 244.4167 | 244.4167 | 244.4167 | 244.4167 | 244.4167 | 244.4167 |  | 150.2438 | 204.0305 | 218.7445 | 221.0211 | 222.4667 | 225.638 | 233.1281 | 237.2175 | 245.0078 | 268.6881 | 249.1661 | 245.3476 | 250.5021 | 261.7749 | 254.1445 | 254.1445 | 254.1445 | 254.1445 | 254.1445 | 254.1445 | 254.1445 | 254.1445 | 254.1445 | 254.1445 | 254.1445 | 254.1445 | 254.1445 | 254.1445 | 254.1445 | 254.1445
95% | 414.5243 | 575.4311 | 617.2612 | 624.3915 | 629.9527 | 639.5277 | 661.3119 | 675.8939 | 694.3669 | 703.9554 | 712.391 | 696.8482 | 715.0638 | 743.7009 | 721.9694 | 721.9694 | 721.9694 | 721.9694 | 721.9694 | 721.9694 | 721.9694 | 721.9694 | 721.9694 | 721.9694 | 721.9694 | 721.9694 | 721.9694 | 721.9694 | 721.9694 | 721.9694 |  | 443.7972 | 602.6746 | 646.1375 | 652.8624 | 657.1324 | 666.4999 | 688.6245 | 700.704 | 723.7153 | 793.6633 | 735.9983 | 724.719 | 739.9446 | 773.2427 | 750.7037 | 750.7037 | 750.7037 | 750.7037 | 750.7037 | 750.7037 | 750.7037 | 750.7037 | 750.7037 | 750.7037 | 750.7037 | 750.7037 | 750.7037 | 750.7037 | 750.7037 | 750.7037
90% | 2285.5212 | 3172.6969 | 3403.3313 | 3442.6449 | 3473.3067 | 3526.0998 | 3646.209 | 3726.6085 | 3828.4608 | 3881.3281 | 3927.8385 | 3842.1418 | 3942.5756 | 4100.4692 | 3980.6499 | 3980.6499 | 3980.6499 | 3980.6499 | 3980.6499 | 3980.6499 | 3980.6499 | 3980.6499 | 3980.6499 | 3980.6499 | 3980.6499 | 3980.6499 | 3980.6499 | 3980.6499 | 3980.6499 | 3980.6499 |  | 2446.9201 | 3322.9067 | 3562.5435 | 3599.622 | 3623.165 | 3674.8134 | 3796.7998 | 3863.4014 | 3990.2765 | 4375.9415 | 4058 | 3995.8103 | 4079.7583 | 4263.3504 | 4139.0795 | 4139.0795 | 4139.0795 | 4139.0795 | 4139.0795 | 4139.0795 | 4139.0795 | 4139.0795 | 4139.0795 | 4139.0795 | 4139.0795 | 4139.0795 | 4139.0795 | 4139.0795 | 4139.0795 | 4139.0795
85% | 5583.3646 | 7750.6712 | 8314.0946 | 8410.1348 | 8485.0395 | 8614.0092 | 8907.4274 | 9103.8375 | 9352.6555 | 9481.8066 | 9595.4282 | 9386.0773 | 9631.4298 | 10017.1525 | 9724.4425 | 9724.4425 | 9724.4425 | 9724.4425 | 9724.4425 | 9724.4425 | 9724.4425 | 9724.4425 | 9724.4425 | 9724.4425 | 9724.4425 | 9724.4425 | 9724.4425 | 9724.4425 | 9724.4425 | 9724.4425 |  | 5977.6505 | 8117.623 | 8703.0385 | 8793.6186 | 8851.1326 | 8977.3059 | 9275.3098 | 9438.0128 | 9747.9596 | 10690.1116 | 9913.4032 | 9761.4782 | 9966.5573 | 10415.0597 | 10111.4747 | 10111.4747 | 10111.4747 | 10111.4747 | 10111.4747 | 10111.4747 | 10111.4747 | 10111.4747 | 10111.4747 | 10111.4747 | 10111.4747 | 10111.4747 | 10111.4747 | 10111.4747 | 10111.4747 | 10111.4747
80% | 8678.2039 | 12046.8408 | 12922.5678 | 13071.8427 | 13188.2668 | 13388.724 | 13844.7828 | 14150.0624 | 14536.7992 | 14737.5384 | 14914.14 | 14588.7467 | 14970.0973 | 15569.6246 | 15114.6665 | 15114.6665 | 15114.6665 | 15114.6665 | 15114.6665 | 15114.6665 | 15114.6665 | 15114.6665 | 15114.6665 | 15114.6665 | 15114.6665 | 15114.6665 | 15114.6665 | 15114.6665 | 15114.6665 | 15114.6665 |  | 9291.041 | 12617.1926 | 13527.1019 | 13667.8902 | 13757.2841 | 13953.3947 | 14416.5812 | 14669.4699 | 15151.219 | 16615.6026 | 15408.3675 | 15172.231 | 15490.9847 | 16188.0904 | 15716.2292 | 15716.2292 | 15716.2292 | 15716.2292 | 15716.2292 | 15716.2292 | 15716.2292 | 15716.2292 | 15716.2292 | 15716.2292 | 15716.2292 | 15716.2292 | 15716.2292 | 15716.2292 | 15716.2292 | 15716.2292
75% | 9574.4808 | 13291.0275 | 14257.1987 | 14421.8907 | 14550.339 | 14771.4991 | 15274.6593 | 15611.4679 | 16038.1465 | 16259.6179 | 16454.4587 | 16095.4591 | 16516.1952 | 17177.6412 | 16675.6955 | 16675.6955 | 16675.6955 | 16675.6955 | 16675.6955 | 16675.6955 | 16675.6955 | 16675.6955 | 16675.6955 | 16675.6955 | 16675.6955 | 16675.6955 | 16675.6955 | 16675.6955 | 16675.6955 | 16675.6955 |  | 10250.6112 | 13920.2847 | 14924.1686 | 15079.4974 | 15178.1238 | 15394.4886 | 15905.5125 | 16184.5193 | 16716.023 | 18331.6468 | 16999.7296 | 16739.2052 | 17090.8794 | 17859.9816 | 17339.387 | 17339.387 | 17339.387 | 17339.387 | 17339.387 | 17339.387 | 17339.387 | 17339.387 | 17339.387 | 17339.387 | 17339.387 | 17339.387 | 17339.387 | 17339.387 | 17339.387 | 17339.387
70% | 10287.2444 | 14280.4661 | 15318.563 | 15495.5153 | 15633.5258 | 15871.15 | 16411.7675 | 16773.6495 | 17232.0919 | 17470.0505 | 17679.396 | 17293.671 | 17745.7284 | 18456.4151 | 17917.1025 | 17917.1025 | 17917.1025 | 17917.1025 | 17917.1025 | 17917.1025 | 17917.1025 | 17917.1025 | 17917.1025 | 17917.1025 | 17917.1025 | 17917.1025 | 17917.1025 | 17917.1025 | 17917.1025 | 17917.1025 |  | 11013.7087 | 14956.5677 | 16035.1849 | 16202.077 | 16308.0455 | 16540.5174 | 17089.584 | 17389.3613 | 17960.4323 | 19696.3297 | 18265.2591 | 17985.3402 | 18363.1944 | 19189.5518 | 18630.202 | 18630.202 | 18630.202 | 18630.202 | 18630.202 | 18630.202 | 18630.202 | 18630.202 | 18630.202 | 18630.202 | 18630.202 | 18630.202 | 18630.202 | 18630.202 | 18630.202 | 18630.202
65% | 10840.7831 | 15048.8731 | 16142.8282 | 16329.302 | 16474.7386 | 16725.149 | 17294.8562 | 17676.2104 | 18159.3208 | 18410.0835 | 18630.6936 | 18224.2134 | 18700.5952 | 19449.5227 | 18881.1907 | 18881.1907 | 18881.1907 | 18881.1907 | 18881.1907 | 18881.1907 | 18881.1907 | 18881.1907 | 18881.1907 | 18881.1907 | 18881.1907 | 18881.1907 | 18881.1907 | 18881.1907 | 18881.1907 | 18881.1907 |  | 11606.3372 | 15761.3546 | 16898.0103 | 17073.8826 | 17185.553 | 17430.5339 | 18009.1448 | 18325.0525 | 18926.8519 | 20756.155 | 19248.0809 | 18953.1 | 19351.286 | 20222.1082 | 19632.6608 | 19632.6608 | 19632.6608 | 19632.6608 | 19632.6608 | 19632.6608 | 19632.6608 | 19632.6608 | 19632.6608 | 19632.6608 | 19632.6608 | 19632.6608 | 19632.6608 | 19632.6608 | 19632.6608 | 19632.6608
60% | 11934.3669 | 16566.9557 | 17771.2656 | 17976.5503 | 18136.658 | 18412.329 | 19039.5064 | 19459.3305 | 19991.1755 | 20267.2344 | 20510.0989 | 20062.6142 | 20587.052 | 21411.5289 | 20785.8653 | 20785.8653 | 20785.8653 | 20785.8653 | 20785.8653 | 20785.8653 | 20785.8653 | 20785.8653 | 20785.8653 | 20785.8653 | 20785.8653 | 20785.8653 | 20785.8653 | 20785.8653 | 20785.8653 | 20785.8653 |  | 12777.1477 | 17351.3101 | 18602.628 | 18796.2417 | 18919.1771 | 19188.8708 | 19825.8502 | 20173.6257 | 20836.1327 | 22849.9701 | 21189.7663 | 20865.0287 | 21303.3824 | 22262.0503 | 21613.1413 | 21613.1413 | 21613.1413 | 21613.1413 | 21613.1413 | 21613.1413 | 21613.1413 | 21613.1413 | 21613.1413 | 21613.1413 | 21613.1413 | 21613.1413 | 21613.1413 | 21613.1413 | 21613.1413 | 21613.1413
55% | 13276.2336 | 18429.6976 | 19769.4166 | 19997.783 | 20175.8928 | 20482.5595 | 21180.255 | 21647.2828 | 22238.927 | 22546.0252 | 22816.1967 | 22318.3981 | 22901.8021 | 23818.981 | 23122.9695 | 23122.9695 | 23122.9695 | 23122.9695 | 23122.9695 | 23122.9695 | 23122.9695 | 23122.9695 | 23122.9695 | 23122.9695 | 23122.9695 | 23122.9695 | 23122.9695 | 23122.9695 | 23122.9695 | 23122.9695 |  | 14213.7742 | 19302.2426 | 20694.2551 | 20909.6382 | 21046.3962 | 21346.4135 | 22055.013 | 22441.8914 | 23178.8888 | 25419.1564 | 23572.284 | 23211.0338 | 23698.6747 | 24765.1326 | 24043.2621 | 24043.2621 | 24043.2621 | 24043.2621 | 24043.2621 | 24043.2621 | 24043.2621 | 24043.2621 | 24043.2621 | 24043.2621 | 24043.2621 | 24043.2621 | 24043.2621 | 24043.2621 | 24043.2621 | 24043.2621
50% | 13456.7484 | 18680.2832 | 20038.2182 | 20269.6896 | 20450.2212 | 20761.0575 | 21468.2395 | 21941.6174 | 22541.3061 | 22852.5798 | 23126.4248 | 22621.8577 | 23213.1942 | 24142.8438 | 23437.3688 | 23437.3688 | 23437.3688 | 23437.3688 | 23437.3688 | 23437.3688 | 23437.3688 | 23437.3688 | 23437.3688 | 23437.3688 | 23437.3688 | 23437.3688 | 23437.3688 | 23437.3688 | 23437.3688 | 23437.3688 |  | 14407.0366 | 19564.692 | 20975.6315 | 21193.9432 | 21332.5606 | 21636.6572 | 22354.8915 | 22747.0302 | 23494.0484 | 25764.7766 | 23892.7925 | 23526.6304 | 24020.9018 | 25101.8601 | 24370.1745 | 24370.1745 | 24370.1745 | 24370.1745 | 24370.1745 | 24370.1745 | 24370.1745 | 24370.1745 | 24370.1745 | 24370.1745 | 24370.1745 | 24370.1745 | 24370.1745 | 24370.1745 | 24370.1745 | 24370.1745
45% | 10386.1977 | 14417.8303 | 15465.9127 | 15644.5671 | 15783.9051 | 16023.8151 | 16569.6328 | 16934.9957 | 17397.8478 | 17638.0954 | 17849.4547 | 17460.0193 | 17916.4251 | 18633.9479 | 18089.4477 | 18089.4477 | 18089.4477 | 18089.4477 | 18089.4477 | 18089.4477 | 18089.4477 | 18089.4477 | 18089.4477 | 18089.4477 | 18089.4477 | 18089.4477 | 18089.4477 | 18089.4477 | 18089.4477 | 18089.4477 |  | 11119.6499 | 15100.4354 | 16189.4278 | 16357.9252 | 16464.913 | 16699.6211 | 17253.9692 | 17556.63 | 18133.1942 | 19885.7893 | 18440.9531 | 18158.3417 | 18539.8305 | 19374.1366 | 18809.4064 | 18809.4064 | 18809.4064 | 18809.4064 | 18809.4064 | 18809.4064 | 18809.4064 | 18809.4064 | 18809.4064 | 18809.4064 | 18809.4064 | 18809.4064 | 18809.4064 | 18809.4064 | 18809.4064 | 18809.4064
40% | 5102.6915 | 7083.4142 | 7598.3323 | 7686.1044 | 7754.5606 | 7872.4272 | 8140.5849 | 8320.0861 | 8547.4832 | 8665.5158 | 8769.3556 | 8578.0278 | 8802.2579 | 9154.7736 | 8887.2631 | 8887.2631 | 8887.2631 | 8887.2631 | 8887.2631 | 8887.2631 | 8887.2631 | 8887.2631 | 8887.2631 | 8887.2631 | 8887.2631 | 8887.2631 | 8887.2631 | 8887.2631 | 8887.2631 | 8887.2631 |  | 5463.0332 | 7418.775 | 7953.792 | 8036.574 | 8089.1366 | 8204.4476 | 8476.7963 | 8625.4922 | 8908.7555 | 9769.7975 | 9059.9561 | 8921.1104 | 9108.5341 | 9518.4249 | 9240.9755 | 9240.9755 | 9240.9755 | 9240.9755 | 9240.9755 | 9240.9755 | 9240.9755 | 9240.9755 | 9240.9755 | 9240.9755 | 9240.9755 | 9240.9755 | 9240.9755 | 9240.9755 | 9240.9755 | 9240.9755
35% | 1907.0998 | 2647.3829 | 2839.8304 | 2872.6347 | 2898.2197 | 2942.2717 | 3042.494 | 3109.5815 | 3194.5697 | 3238.6837 | 3277.4932 | 3205.9856 | 3289.7902 | 3421.5408 | 3321.5604 | 3321.5604 | 3321.5604 | 3321.5604 | 3321.5604 | 3321.5604 | 3321.5604 | 3321.5604 | 3321.5604 | 3321.5604 | 3321.5604 | 3321.5604 | 3321.5604 | 3321.5604 | 3321.5604 | 3321.5604 |  | 2041.7754 | 2772.7219 | 2972.6813 | 3003.6205 | 3023.2655 | 3066.3623 | 3168.1509 | 3223.7251 | 3329.5931 | 3651.4023 | 3386.1034 | 3334.2106 | 3404.2591 | 3557.4533 | 3453.7583 | 3453.7583 | 3453.7583 | 3453.7583 | 3453.7583 | 3453.7583 | 3453.7583 | 3453.7583 | 3453.7583 | 3453.7583 | 3453.7583 | 3453.7583 | 3453.7583 | 3453.7583 | 3453.7583 | 3453.7583
30% | 951.1511 | 1320.3614 | 1416.3431 | 1432.704 | 1445.4643 | 1467.4349 | 1517.42 | 1550.8793 | 1593.2665 | 1615.268 | 1634.624 | 1598.9601 | 1640.757 | 1706.4666 | 1656.6021 | 1656.6021 | 1656.6021 | 1656.6021 | 1656.6021 | 1656.6021 | 1656.6021 | 1656.6021 | 1656.6021 | 1656.6021 | 1656.6021 | 1656.6021 | 1656.6021 | 1656.6021 | 1656.6021 | 1656.6021 |  | 1018.3194 | 1382.8733 | 1482.6014 | 1498.0321 | 1507.8299 | 1529.3241 | 1580.0904 | 1607.8076 | 1660.6084 | 1821.1082 | 1688.7924 | 1662.9113 | 1697.8475 | 1774.2519 | 1722.5348 | 1722.5348 | 1722.5348 | 1722.5348 | 1722.5348 | 1722.5348 | 1722.5348 | 1722.5348 | 1722.5348 | 1722.5348 | 1722.5348 | 1722.5348 | 1722.5348 | 1722.5348 | 1722.5348 | 1722.5348
25% | 560.7353 | 778.3972 | 834.9816 | 844.6269 | 852.1495 | 865.1019 | 894.5698 | 914.2952 | 939.2839 | 952.2545 | 963.6655 | 942.6404 | 967.2811 | 1006.0191 | 976.6223 | 976.6223 | 976.6223 | 976.6223 | 976.6223 | 976.6223 | 976.6223 | 976.6223 | 976.6223 | 976.6223 | 976.6223 | 976.6223 | 976.6223 | 976.6223 | 976.6223 | 976.6223 |  | 600.3333 | 815.25 | 874.0431 | 883.14 | 888.9161 | 901.5876 | 931.5161 | 947.8563 | 978.9841 | 1073.6041 | 995.5996 | 980.3418 | 1000.9378 | 1045.9808 | 1015.4918 | 1015.4918 | 1015.4918 | 1015.4918 | 1015.4918 | 1015.4918 | 1015.4918 | 1015.4918 | 1015.4918 | 1015.4918 | 1015.4918 | 1015.4918 | 1015.4918 | 1015.4918 | 1015.4918 | 1015.4918
20% | 283.3663 | 393.3611 | 421.9559 | 426.8302 | 430.6317 | 437.1772 | 452.0687 | 462.0369 | 474.6648 | 481.2195 | 486.986 | 476.3611 | 488.8132 | 508.3893 | 493.5337 | 493.5337 | 493.5337 | 493.5337 | 493.5337 | 493.5337 | 493.5337 | 493.5337 | 493.5337 | 493.5337 | 493.5337 | 493.5337 | 493.5337 | 493.5337 | 493.5337 | 493.5337 |  | 303.377 | 411.9846 | 441.6956 | 446.2927 | 449.2116 | 455.6151 | 470.7394 | 478.9969 | 494.7273 | 542.5433 | 503.1238 | 495.4134 | 505.8215 | 528.5839 | 513.1763 | 513.1763 | 513.1763 | 513.1763 | 513.1763 | 513.1763 | 513.1763 | 513.1763 | 513.1763 | 513.1763 | 513.1763 | 513.1763 | 513.1763 | 513.1763 | 513.1763 | 513.1763
15% | 115.4455 | 160.2582 | 171.908 | 173.8938 | 175.4425 | 178.1092 | 184.1761 | 188.2372 | 193.382 | 196.0524 | 198.4017 | 194.073 | 199.1461 | 207.1216 | 201.0693 | 201.0693 | 201.0693 | 201.0693 | 201.0693 | 201.0693 | 201.0693 | 201.0693 | 201.0693 | 201.0693 | 201.0693 | 201.0693 | 201.0693 | 201.0693 | 201.0693 | 201.0693 |  | 123.598 | 167.8456 | 179.95 | 181.8229 | 183.0121 | 185.621 | 191.7827 | 195.1469 | 201.5556 | 221.0361 | 204.9764 | 201.8351 | 206.0754 | 215.349 | 209.0718 | 209.0718 | 209.0718 | 209.0718 | 209.0718 | 209.0718 | 209.0718 | 209.0718 | 209.0718 | 209.0718 | 209.0718 | 209.0718 | 209.0718 | 209.0718 | 209.0718 | 209.0718
10% | 46.4781 | 64.5196 | 69.2097 | 70.0092 | 70.6327 | 71.7063 | 74.1488 | 75.7838 | 77.8551 | 78.9302 | 79.876 | 78.1333 | 80.1757 | 83.3866 | 80.95 | 80.95 | 80.95 | 80.95 | 80.95 | 80.95 | 80.95 | 80.95 | 80.95 | 80.95 | 80.95 | 80.95 | 80.95 | 80.95 | 80.95 | 80.95 |  | 49.7602 | 67.5742 | 72.4474 | 73.2014 | 73.6802 | 74.7305 | 77.2112 | 78.5656 | 81.1457 | 88.9886 | 82.523 | 81.2583 | 82.9654 | 86.6989 | 84.1718 | 84.1718 | 84.1718 | 84.1718 | 84.1718 | 84.1718 | 84.1718 | 84.1718 | 84.1718 | 84.1718 | 84.1718 | 84.1718 | 84.1718 | 84.1718 | 84.1718 | 84.1718
5% | 39.5813 | 54.9457 | 58.9399 | 59.6207 | 60.1517 | 61.066 | 63.1461 | 64.5385 | 66.3024 | 67.218 | 68.0234 | 66.5393 | 68.2787 | 71.0131 | 68.938 | 68.938 | 68.938 | 68.938 | 68.938 | 68.938 | 68.938 | 68.938 | 68.938 | 68.938 | 68.938 | 68.938 | 68.938 | 68.938 | 68.938 | 68.938 |  | 42.3765 | 57.5471 | 61.6972 | 62.3393 | 62.747 | 63.6415 | 65.7541 | 66.9075 | 69.1048 | 75.7838 | 70.2776 | 69.2006 | 70.6544 | 73.8339 | 71.6818 | 71.6818 | 71.6818 | 71.6818 | 71.6818 | 71.6818 | 71.6818 | 71.6818 | 71.6818 | 71.6818 | 71.6818 | 71.6818 | 71.6818 | 71.6818 | 71.6818 | 71.6818
9.992e-14% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E @ R (MWh) | 105995.1099 | 147139.4588 | 157835.5397 | 159658.7762 | 161080.774 | 163529.1464 | 169099.4242 | 172828.0925 | 177551.675 | 180003.4929 | 182160.4948 | 178186.1586 | 182843.9537 | 190166.5478 | 184609.7151 | 184609.7151 | 184609.7151 | 184609.7151 | 184609.7151 | 184609.7151 | 184609.7151 | 184609.7151 | 184609.7151 | 184609.7151 | 184609.7151 | 184609.7151 | 184609.7151 | 184609.7151 | 184609.7151 | 184609.7151 | E @ R (MWh) | 113480.2695 | 154105.704 | 165219.287 | 166938.8679 | 168030.7193 | 170426.0046 | 176083.3386 | 179172.1077 | 185056.165 | 202942.0666 | 188196.9625 | 185312.8045 | 189206.044 | 197720.4561 | 191957.169 | 191957.169 | 191957.169 | 191957.169 | 191957.169 | 191957.169 | 191957.169 | 191957.169 | 191957.169 | 191957.169 | 191957.169 | 191957.169 | 191957.169 | 191957.169 | 191957.169 | 191957.169
Option 6 Winter POE50 W E @ R (MWh) N 2 | 74196.5769 | 102997.6211 | 110484.8778 | 111761.1434 | 112756.5418 | 114470.4025 | 118369.597 | 120979.6647 | 124286.1725 | 126002.4451 | 127512.3464 | 124730.311 | 127990.7676 | 133116.5835 | 129226.8005 | 129226.8005 | 129226.8005 | 129226.8005 | 129226.8005 | 129226.8005 | 129226.8005 | 129226.8005 | 129226.8005 | 129226.8005 | 129226.8005 | 129226.8005 | 129226.8005 | 129226.8005 | 129226.8005 | 129226.8005 | Option 6 Winter POE10 W E @ R (MWh) N 2 | 34044.0809 | 46231.7112 | 49565.7861 | 50081.6604 | 50409.2158 | 51127.8014 | 52825.0016 | 53751.6323 | 55516.8495 | 60882.62 | 56459.0887 | 55593.8414 | 56761.8132 | 59316.1368 | 57587.1507 | 57587.1507 | 57587.1507 | 57587.1507 | 57587.1507 | 57587.1507 | 57587.1507 | 57587.1507 | 57587.1507 | 57587.1507 | 57587.1507 | 57587.1507 | 57587.1507 | 57587.1507 | 57587.1507 | 57587.1507
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 76.9936 | 99.7405 | 105.6969 | 105.3426 | 105.3724 | 105.9856 | 107.6 | 108.6824 | 109.7411 | 110.979 | 112.1272 | 113.2411 | 113.3701 | 114.6698 | 113.6883 | 113.6883 | 113.6883 | 113.6883 | 113.6883 | 113.6883 | 113.6883 | 113.6883 | 113.6883 | 113.6883 | 113.6883 | 113.6883 | 113.6883 | 113.6883 | 113.6883 | 113.6883
98% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 38.1099 | 49.369 | 52.3173 | 52.1419 | 52.1567 | 52.4602 | 53.2593 | 53.7951 | 54.3191 | 54.9318 | 55.5002 | 56.0515 | 56.1154 | 56.7587 | 56.2728 | 56.2728 | 56.2728 | 56.2728 | 56.2728 | 56.2728 | 56.2728 | 56.2728 | 56.2728 | 56.2728 | 56.2728 | 56.2728 | 56.2728 | 56.2728 | 56.2728 | 56.2728
97% | 16.9149 | 22.4762 | 23.991 | 23.9477 | 23.9472 | 24.1204 | 24.3105 | 24.7002 | 24.9803 | 25.1325 | 25.2993 | 25.4517 | 25.7265 | 26.0674 | 26.0444 | 26.0444 | 26.0444 | 26.0444 | 26.0444 | 26.0444 | 26.0444 | 26.0444 | 26.0444 | 26.0444 | 26.0444 | 26.0444 | 26.0444 | 26.0444 | 26.0444 | 26.0444 |  | 75.446 | 97.7357 | 103.5723 | 103.2252 | 103.2543 | 103.8552 | 105.4372 | 106.4978 | 107.5353 | 108.7483 | 109.8734 | 110.9649 | 111.0913 | 112.3649 | 111.4031 | 111.4031 | 111.4031 | 111.4031 | 111.4031 | 111.4031 | 111.4031 | 111.4031 | 111.4031 | 111.4031 | 111.4031 | 111.4031 | 111.4031 | 111.4031 | 111.4031 | 111.4031
95% | 83.2734 | 110.6519 | 118.1097 | 117.8962 | 117.8937 | 118.7467 | 119.6823 | 121.6012 | 122.9798 | 123.7293 | 124.5504 | 125.3007 | 126.6535 | 128.3318 | 128.2183 | 128.2183 | 128.2183 | 128.2183 | 128.2183 | 128.2183 | 128.2183 | 128.2183 | 128.2183 | 128.2183 | 128.2183 | 128.2183 | 128.2183 | 128.2183 | 128.2183 | 128.2183 |  | 111.4279 | 144.3481 | 152.9683 | 152.4556 | 152.4987 | 153.3862 | 155.7226 | 157.2891 | 158.8214 | 160.6129 | 162.2746 | 163.8866 | 164.0733 | 165.9543 | 164.5337 | 164.5337 | 164.5337 | 164.5337 | 164.5337 | 164.5337 | 164.5337 | 164.5337 | 164.5337 | 164.5337 | 164.5337 | 164.5337 | 164.5337 | 164.5337 | 164.5337 | 164.5337
90% | 144.4273 | 191.9119 | 204.8464 | 204.4763 | 204.4719 | 205.9512 | 207.574 | 210.9021 | 213.2931 | 214.593 | 216.0171 | 217.3184 | 219.6647 | 222.5754 | 222.3787 | 222.3787 | 222.3787 | 222.3787 | 222.3787 | 222.3787 | 222.3787 | 222.3787 | 222.3787 | 222.3787 | 222.3787 | 222.3787 | 222.3787 | 222.3787 | 222.3787 | 222.3787 |  | 483.1446 | 625.8842 | 663.261 | 661.0381 | 661.2248 | 665.0728 | 675.2033 | 681.9957 | 688.6395 | 696.4074 | 703.6125 | 710.602 | 711.4117 | 719.5673 | 713.4081 | 713.4081 | 713.4081 | 713.4081 | 713.4081 | 713.4081 | 713.4081 | 713.4081 | 713.4081 | 713.4081 | 713.4081 | 713.4081 | 713.4081 | 713.4081 | 713.4081 | 713.4081
85% | 409.8612 | 544.6148 | 581.321 | 580.2706 | 580.258 | 584.4562 | 589.0613 | 598.5059 | 605.2912 | 608.9802 | 613.0214 | 616.7142 | 623.3728 | 631.6329 | 631.0746 | 631.0746 | 631.0746 | 631.0746 | 631.0746 | 631.0746 | 631.0746 | 631.0746 | 631.0746 | 631.0746 | 631.0746 | 631.0746 | 631.0746 | 631.0746 | 631.0746 | 631.0746 |  | 457.0286 | 592.0526 | 627.4091 | 625.3063 | 625.4829 | 629.1229 | 638.7059 | 645.1311 | 651.4157 | 658.7637 | 665.5794 | 672.1911 | 672.9571 | 680.6717 | 674.8455 | 674.8455 | 674.8455 | 674.8455 | 674.8455 | 674.8455 | 674.8455 | 674.8455 | 674.8455 | 674.8455 | 674.8455 | 674.8455 | 674.8455 | 674.8455 | 674.8455 | 674.8455
80% | 572.5046 | 760.7318 | 812.0039 | 810.5367 | 810.5191 | 816.3833 | 822.8158 | 836.0082 | 845.4861 | 850.639 | 856.2839 | 861.4421 | 870.743 | 882.2809 | 881.5011 | 881.5011 | 881.5011 | 881.5011 | 881.5011 | 881.5011 | 881.5011 | 881.5011 | 881.5011 | 881.5011 | 881.5011 | 881.5011 | 881.5011 | 881.5011 | 881.5011 | 881.5011 |  | 319.1946 | 413.4971 | 438.1905 | 436.7219 | 436.8452 | 439.3874 | 446.0803 | 450.5677 | 454.957 | 460.089 | 464.8491 | 469.4668 | 470.0018 | 475.3898 | 471.3206 | 471.3206 | 471.3206 | 471.3206 | 471.3206 | 471.3206 | 471.3206 | 471.3206 | 471.3206 | 471.3206 | 471.3206 | 471.3206 | 471.3206 | 471.3206 | 471.3206 | 471.3206
75% | 1492.4153 | 1983.0895 | 2116.7465 | 2112.9218 | 2112.876 | 2128.1627 | 2144.9312 | 2179.3214 | 2204.0286 | 2217.4612 | 2232.1763 | 2245.623 | 2269.8686 | 2299.9458 | 2297.9131 | 2297.9131 | 2297.9131 | 2297.9131 | 2297.9131 | 2297.9131 | 2297.9131 | 2297.9131 | 2297.9131 | 2297.9131 | 2297.9131 | 2297.9131 | 2297.9131 | 2297.9131 | 2297.9131 | 2297.9131 |  | 569.714 | 738.0296 | 782.1036 | 779.4824 | 779.7025 | 784.24 | 796.1857 | 804.1951 | 812.0293 | 821.1891 | 829.6853 | 837.9271 | 838.8819 | 848.4987 | 841.2359 | 841.2359 | 841.2359 | 841.2359 | 841.2359 | 841.2359 | 841.2359 | 841.2359 | 841.2359 | 841.2359 | 841.2359 | 841.2359 | 841.2359 | 841.2359 | 841.2359 | 841.2359
70% | 2578.4391 | 3426.1747 | 3657.0932 | 3650.4854 | 3650.4063 | 3676.8171 | 3705.7879 | 3765.2037 | 3807.8902 | 3831.0976 | 3856.5209 | 3879.7526 | 3921.6416 | 3973.6059 | 3970.094 | 3970.094 | 3970.094 | 3970.094 | 3970.094 | 3970.094 | 3970.094 | 3970.094 | 3970.094 | 3970.094 | 3970.094 | 3970.094 | 3970.094 | 3970.094 | 3970.094 | 3970.094 |  | 1037.8661 | 1344.492 | 1424.783 | 1420.0079 | 1420.4087 | 1428.6749 | 1450.4368 | 1465.0278 | 1479.2996 | 1495.9862 | 1511.464 | 1526.4784 | 1528.2178 | 1545.7371 | 1532.5062 | 1532.5062 | 1532.5062 | 1532.5062 | 1532.5062 | 1532.5062 | 1532.5062 | 1532.5062 | 1532.5062 | 1532.5062 | 1532.5062 | 1532.5062 | 1532.5062 | 1532.5062 | 1532.5062 | 1532.5062
65% | 6475.8072 | 8604.914 | 9184.8711 | 9168.2753 | 9168.0768 | 9234.408 | 9307.1689 | 9456.393 | 9563.6012 | 9621.887 | 9685.7381 | 9744.0851 | 9849.2903 | 9979.7998 | 9970.9794 | 9970.9794 | 9970.9794 | 9970.9794 | 9970.9794 | 9970.9794 | 9970.9794 | 9970.9794 | 9970.9794 | 9970.9794 | 9970.9794 | 9970.9794 | 9970.9794 | 9970.9794 | 9970.9794 | 9970.9794 |  | 1305.7961 | 1691.5789 | 1792.5974 | 1786.5896 | 1787.0939 | 1797.4941 | 1824.8739 | 1843.2317 | 1861.1878 | 1882.1821 | 1901.6555 | 1920.546 | 1922.7344 | 1944.7764 | 1928.1299 | 1928.1299 | 1928.1299 | 1928.1299 | 1928.1299 | 1928.1299 | 1928.1299 | 1928.1299 | 1928.1299 | 1928.1299 | 1928.1299 | 1928.1299 | 1928.1299 | 1928.1299 | 1928.1299 | 1928.1299
60% | 9465.8424 | 12578.0087 | 13425.7459 | 13401.4874 | 13401.1972 | 13498.1551 | 13604.5115 | 13822.636 | 13979.3447 | 14064.5425 | 14157.8751 | 14243.1624 | 14396.9433 | 14587.7122 | 14574.8193 | 14574.8193 | 14574.8193 | 14574.8193 | 14574.8193 | 14574.8193 | 14574.8193 | 14574.8193 | 14574.8193 | 14574.8193 | 14574.8193 | 14574.8193 | 14574.8193 | 14574.8193 | 14574.8193 | 14574.8193 |  | 2043.3291 | 2647.0078 | 2805.083 | 2795.6818 | 2796.4711 | 2812.7454 | 2855.5897 | 2884.3162 | 2912.4142 | 2945.2664 | 2975.7387 | 3005.2988 | 3008.7233 | 3043.2149 | 3017.1662 | 3017.1662 | 3017.1662 | 3017.1662 | 3017.1662 | 3017.1662 | 3017.1662 | 3017.1662 | 3017.1662 | 3017.1662 | 3017.1662 | 3017.1662 | 3017.1662 | 3017.1662 | 3017.1662 | 3017.1662
55% | 10703.6666 | 14222.8031 | 15181.3967 | 15153.966 | 15153.6378 | 15263.2747 | 15383.539 | 15630.1871 | 15807.3882 | 15903.7271 | 16009.2646 | 16105.7046 | 16279.5951 | 16495.3104 | 16480.7315 | 16480.7315 | 16480.7315 | 16480.7315 | 16480.7315 | 16480.7315 | 16480.7315 | 16480.7315 | 16480.7315 | 16480.7315 | 16480.7315 | 16480.7315 | 16480.7315 | 16480.7315 | 16480.7315 | 16480.7315 |  | 3926.5772 | 5086.6405 | 5390.4069 | 5372.341 | 5373.8577 | 5405.1313 | 5487.4633 | 5542.6658 | 5596.6606 | 5659.7913 | 5718.3486 | 5775.1529 | 5781.7337 | 5848.0147 | 5797.958 | 5797.958 | 5797.958 | 5797.958 | 5797.958 | 5797.958 | 5797.958 | 5797.958 | 5797.958 | 5797.958 | 5797.958 | 5797.958 | 5797.958 | 5797.958 | 5797.958 | 5797.958
50% | 13744.0128 | 18262.75 | 19493.6294 | 19458.4071 | 19457.9857 | 19598.7646 | 19753.1897 | 20069.8975 | 20297.432 | 20421.1357 | 20556.6509 | 20680.4844 | 20903.7679 | 21180.7565 | 21162.0366 | 21162.0366 | 21162.0366 | 21162.0366 | 21162.0366 | 21162.0366 | 21162.0366 | 21162.0366 | 21162.0366 | 21162.0366 | 21162.0366 | 21162.0366 | 21162.0366 | 21162.0366 | 21162.0366 | 21162.0366 |  | 8714.0125 | 11288.47 | 11962.6002 | 11922.5077 | 11925.8735 | 11995.2773 | 12177.9916 | 12300.4992 | 12420.3265 | 12560.4285 | 12690.3811 | 12816.4434 | 12831.0478 | 12978.1412 | 12867.0534 | 12867.0534 | 12867.0534 | 12867.0534 | 12867.0534 | 12867.0534 | 12867.0534 | 12867.0534 | 12867.0534 | 12867.0534 | 12867.0534 | 12867.0534 | 12867.0534 | 12867.0534 | 12867.0534 | 12867.0534
45% | 18302.3635 | 24319.7888 | 25958.9027 | 25911.9985 | 25911.4373 | 26098.9072 | 26304.5489 | 26726.2963 | 27029.2951 | 27194.0265 | 27374.4867 | 27539.391 | 27836.7289 | 28205.5838 | 28180.6551 | 28180.6551 | 28180.6551 | 28180.6551 | 28180.6551 | 28180.6551 | 28180.6551 | 28180.6551 | 28180.6551 | 28180.6551 | 28180.6551 | 28180.6551 | 28180.6551 | 28180.6551 | 28180.6551 | 28180.6551 |  | 13204.5002 | 17105.6219 | 18127.1435 | 18066.3908 | 18071.491 | 18176.6598 | 18453.5301 | 18639.1681 | 18820.7445 | 19033.0436 | 19229.9631 | 19420.9876 | 19443.1179 | 19666.0112 | 19497.6778 | 19497.6778 | 19497.6778 | 19497.6778 | 19497.6778 | 19497.6778 | 19497.6778 | 19497.6778 | 19497.6778 | 19497.6778 | 19497.6778 | 19497.6778 | 19497.6778 | 19497.6778 | 19497.6778 | 19497.6778
40% | 12836.6798 | 17057.1053 | 18206.7263 | 18173.8293 | 18173.4357 | 18304.9209 | 18449.1513 | 18744.9511 | 18957.4646 | 19073.0018 | 19199.5707 | 19315.2292 | 19523.7723 | 19782.475 | 19764.9909 | 19764.9909 | 19764.9909 | 19764.9909 | 19764.9909 | 19764.9909 | 19764.9909 | 19764.9909 | 19764.9909 | 19764.9909 | 19764.9909 | 19764.9909 | 19764.9909 | 19764.9909 | 19764.9909 | 19764.9909 |  | 13672.6523 | 17712.0843 | 18769.8229 | 18706.9162 | 18712.1973 | 18821.0947 | 19107.7811 | 19300.0008 | 19488.0148 | 19707.8407 | 19911.7418 | 20109.5389 | 20132.4538 | 20363.2496 | 20188.9481 | 20188.9481 | 20188.9481 | 20188.9481 | 20188.9481 | 20188.9481 | 20188.9481 | 20188.9481 | 20188.9481 | 20188.9481 | 20188.9481 | 20188.9481 | 20188.9481 | 20188.9481 | 20188.9481 | 20188.9481
35% | 6655.3655 | 8843.5072 | 9439.545 | 9422.4891 | 9422.285 | 9490.4555 | 9565.2339 | 9718.5956 | 9828.7764 | 9888.6783 | 9954.2998 | 10014.2647 | 10122.3869 | 10256.5152 | 10247.4502 | 10247.4502 | 10247.4502 | 10247.4502 | 10247.4502 | 10247.4502 | 10247.4502 | 10247.4502 | 10247.4502 | 10247.4502 | 10247.4502 | 10247.4502 | 10247.4502 | 10247.4502 | 10247.4502 | 10247.4502 |  | 18622.1031 | 24123.7949 | 25564.4311 | 25478.7524 | 25485.9452 | 25634.2631 | 26024.729 | 26286.5314 | 26542.6059 | 26842.008 | 27119.7205 | 27389.1195 | 27420.3294 | 27734.6724 | 27497.2745 | 27497.2745 | 27497.2745 | 27497.2745 | 27497.2745 | 27497.2745 | 27497.2745 | 27497.2745 | 27497.2745 | 27497.2745 | 27497.2745 | 27497.2745 | 27497.2745 | 27497.2745 | 27497.2745 | 27497.2745
30% | 3095.428 | 4113.1385 | 4390.3573 | 4382.4246 | 4382.3296 | 4414.0359 | 4448.8155 | 4520.1445 | 4571.3898 | 4599.2504 | 4629.7711 | 4657.6609 | 4707.9489 | 4770.3323 | 4766.1162 | 4766.1162 | 4766.1162 | 4766.1162 | 4766.1162 | 4766.1162 | 4766.1162 | 4766.1162 | 4766.1162 | 4766.1162 | 4766.1162 | 4766.1162 | 4766.1162 | 4766.1162 | 4766.1162 | 4766.1162 |  | 17207.9743 | 22291.8776 | 23623.1145 | 23543.942 | 23550.5887 | 23687.6435 | 24048.4582 | 24290.3798 | 24527.0085 | 24803.6745 | 25060.2981 | 25309.2393 | 25338.0792 | 25628.5516 | 25409.1812 | 25409.1812 | 25409.1812 | 25409.1812 | 25409.1812 | 25409.1812 | 25409.1812 | 25409.1812 | 25409.1812 | 25409.1812 | 25409.1812 | 25409.1812 | 25409.1812 | 25409.1812 | 25409.1812 | 25409.1812
25% | 2113.496 | 2808.3682 | 2997.6476 | 2992.2313 | 2992.1665 | 3013.8149 | 3037.5617 | 3086.2637 | 3121.253 | 3140.2756 | 3161.1146 | 3180.1572 | 3214.4928 | 3257.0869 | 3254.2082 | 3254.2082 | 3254.2082 | 3254.2082 | 3254.2082 | 3254.2082 | 3254.2082 | 3254.2082 | 3254.2082 | 3254.2082 | 3254.2082 | 3254.2082 | 3254.2082 | 3254.2082 | 3254.2082 | 3254.2082 |  | 4963.476 | 6429.8794 | 6813.862 | 6791.0255 | 6792.9426 | 6832.4748 | 6936.5483 | 7006.3283 | 7074.5816 | 7154.3833 | 7228.4039 | 7300.2086 | 7308.5272 | 7392.3112 | 7329.0359 | 7329.0359 | 7329.0359 | 7329.0359 | 7329.0359 | 7329.0359 | 7329.0359 | 7329.0359 | 7329.0359 | 7329.0359 | 7329.0359 | 7329.0359 | 7329.0359 | 7329.0359 | 7329.0359 | 7329.0359
20% | 1280.3284 | 1701.2729 | 1815.9359 | 1812.6548 | 1812.6155 | 1825.7299 | 1840.1154 | 1869.6184 | 1890.8145 | 1902.3381 | 1914.9621 | 1926.4978 | 1947.2979 | 1973.1009 | 1971.357 | 1971.357 | 1971.357 | 1971.357 | 1971.357 | 1971.357 | 1971.357 | 1971.357 | 1971.357 | 1971.357 | 1971.357 | 1971.357 | 1971.357 | 1971.357 | 1971.357 | 1971.357 |  | 1331.912 | 1725.4105 | 1828.4494 | 1822.3214 | 1822.8358 | 1833.444 | 1861.3713 | 1880.0963 | 1898.4115 | 1919.8257 | 1939.6886 | 1958.9569 | 1961.1891 | 1983.6719 | 1966.6925 | 1966.6925 | 1966.6925 | 1966.6925 | 1966.6925 | 1966.6925 | 1966.6925 | 1966.6925 | 1966.6925 | 1966.6925 | 1966.6925 | 1966.6925 | 1966.6925 | 1966.6925 | 1966.6925 | 1966.6925
15% | 819.7224 | 1089.2296 | 1162.6419 | 1160.5412 | 1160.516 | 1168.9124 | 1178.1226 | 1197.0118 | 1210.5824 | 1217.9604 | 1226.0428 | 1233.4285 | 1246.7456 | 1263.2658 | 1262.1493 | 1262.1493 | 1262.1493 | 1262.1493 | 1262.1493 | 1262.1493 | 1262.1493 | 1262.1493 | 1262.1493 | 1262.1493 | 1262.1493 | 1262.1493 | 1262.1493 | 1262.1493 | 1262.1493 | 1262.1493 |  | 734.6312 | 951.6698 | 1008.502 | 1005.1221 | 1005.4058 | 1011.2569 | 1026.6605 | 1036.9885 | 1047.0905 | 1058.9017 | 1069.8573 | 1080.4849 | 1081.7162 | 1094.1168 | 1084.7516 | 1084.7516 | 1084.7516 | 1084.7516 | 1084.7516 | 1084.7516 | 1084.7516 | 1084.7516 | 1084.7516 | 1084.7516 | 1084.7516 | 1084.7516 | 1084.7516 | 1084.7516 | 1084.7516 | 1084.7516
10% | 548.6502 | 729.0346 | 778.1704 | 776.7643 | 776.7475 | 782.3673 | 788.5318 | 801.1745 | 810.2575 | 815.1957 | 820.6054 | 825.5487 | 834.462 | 845.5192 | 844.7719 | 844.7719 | 844.7719 | 844.7719 | 844.7719 | 844.7719 | 844.7719 | 844.7719 | 844.7719 | 844.7719 | 844.7719 | 844.7719 | 844.7719 | 844.7719 | 844.7719 | 844.7719 |  | 171.688 | 222.4113 | 235.6934 | 234.9034 | 234.9698 | 236.3372 | 239.9371 | 242.3508 | 244.7117 | 247.4721 | 250.0325 | 252.5162 | 252.804 | 255.7021 | 253.5134 | 253.5134 | 253.5134 | 253.5134 | 253.5134 | 253.5134 | 253.5134 | 253.5134 | 253.5134 | 253.5134 | 253.5134 | 253.5134 | 253.5134 | 253.5134 | 253.5134 | 253.5134
5% | 390.344 | 518.6808 | 553.639 | 552.6387 | 552.6267 | 556.625 | 561.0108 | 570.0056 | 576.4678 | 579.9811 | 583.8299 | 587.3469 | 593.6884 | 601.5551 | 601.0235 | 601.0235 | 601.0235 | 601.0235 | 601.0235 | 601.0235 | 601.0235 | 601.0235 | 601.0235 | 601.0235 | 601.0235 | 601.0235 | 601.0235 | 601.0235 | 601.0235 | 601.0235 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9.992e-14% | 34.2635 | 45.5286 | 48.5972 | 48.5094 | 48.5083 | 48.8593 | 49.2443 | 50.0338 | 50.6011 | 50.9095 | 51.2473 | 51.556 | 52.1126 | 52.8032 | 52.7565 | 52.7565 | 52.7565 | 52.7565 | 52.7565 | 52.7565 | 52.7565 | 52.7565 | 52.7565 | 52.7565 | 52.7565 | 52.7565 | 52.7565 | 52.7565 | 52.7565 | 52.7565 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E @ R (MWh) | 91763.8061 | 121933.7811 | 130151.918 | 129916.7517 | 129913.938 | 130853.8682 | 131884.9083 | 133999.4516 | 135518.6175 | 136344.5424 | 137249.3282 | 138076.12 | 139566.9035 | 141416.2562 | 141291.2697 | 141291.2697 | 141291.2697 | 141291.2697 | 141291.2697 | 141291.2697 | 141291.2697 | 141291.2697 | 141291.2697 | 141291.2697 | 141291.2697 | 141291.2697 | 141291.2697 | 141291.2697 | 141291.2697 | 141291.2697 | E @ R (MWh) | 89067.5772 | 115381.5956 | 122272.0083 | 121862.2159 | 121896.6185 | 122606.0074 | 124473.5651 | 125725.7387 | 126950.5164 | 128382.5252 | 129710.7955 | 130999.3026 | 131148.5764 | 132652.0463 | 131516.5966 | 131516.5966 | 131516.5966 | 131516.5966 | 131516.5966 | 131516.5966 | 131516.5966 | 131516.5966 | 131516.5966 | 131516.5966 | 131516.5966 | 131516.5966 | 131516.5966 | 131516.5966 | 131516.5966 | 131516.5966
Option 6 Summer POE50 W E @ R (MWh) N 2 | 64234.6643 | 85353.6468 | 91106.3426 | 90941.7262 | 90939.7566 | 91597.7077 | 92319.4358 | 93799.6161 | 94863.0323 | 95441.1797 | 96074.5298 | 96653.284 | 97696.8324 | 98991.3793 | 98903.8888 | 98903.8888 | 98903.8888 | 98903.8888 | 98903.8888 | 98903.8888 | 98903.8888 | 98903.8888 | 98903.8888 | 98903.8888 | 98903.8888 | 98903.8888 | 98903.8888 | 98903.8888 | 98903.8888 | 98903.8888 | Option 6 Summer POE10 W E @ R (MWh) N 2 | 26720.2732 | 34614.4787 | 36681.6025 | 36558.6648 | 36568.9855 | 36781.8022 | 37342.0695 | 37717.7216 | 38085.1549 | 38514.7576 | 38913.2387 | 39299.7908 | 39344.5729 | 39795.6139 | 39454.979 | 39454.979 | 39454.979 | 39454.979 | 39454.979 | 39454.979 | 39454.979 | 39454.979 | 39454.979 | 39454.979 | 39454.979 | 39454.979 | 39454.979 | 39454.979 | 39454.979 | 39454.979
Option 7 -
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | 59.6718 | 82.8348 | 88.8563 | 89.8828 | 90.6833 | 92.0616 | 95.1975 | 97.2967 | 99.9559 | 101.3362 | 102.5505 | 100.3131 | 102.9353 | 107.0576 | 103.9293 | 103.9293 | 103.9293 | 103.9293 | 103.9293 | 103.9293 | 103.9293 | 103.9293 | 103.9293 | 103.9293 | 103.9293 | 103.9293 | 103.9293 | 103.9293 | 103.9293 | 103.9293 |  | 63.8857 | 86.7566 | 93.0131 | 93.9812 | 94.5959 | 95.9444 | 99.1293 | 100.8681 | 104.1807 | 114.2499 | 105.9488 | 104.3251 | 106.5169 | 111.3103 | 108.0657 | 108.0657 | 108.0657 | 108.0657 | 108.0657 | 108.0657 | 108.0657 | 108.0657 | 108.0657 | 108.0657 | 108.0657 | 108.0657 | 108.0657 | 108.0657 | 108.0657 | 108.0657
98% | 70.8865 | 98.4027 | 105.556 | 106.7753 | 107.7263 | 109.3637 | 113.0889 | 115.5826 | 118.7416 | 120.3813 | 121.8238 | 119.1659 | 122.2809 | 127.178 | 123.4618 | 123.4618 | 123.4618 | 123.4618 | 123.4618 | 123.4618 | 123.4618 | 123.4618 | 123.4618 | 123.4618 | 123.4618 | 123.4618 | 123.4618 | 123.4618 | 123.4618 | 123.4618 |  | 75.8924 | 103.0616 | 110.494 | 111.644 | 112.3742 | 113.9761 | 117.7596 | 119.8253 | 123.7603 | 135.7219 | 125.8608 | 123.932 | 126.5357 | 132.2299 | 128.3755 | 128.3755 | 128.3755 | 128.3755 | 128.3755 | 128.3755 | 128.3755 | 128.3755 | 128.3755 | 128.3755 | 128.3755 | 128.3755 | 128.3755 | 128.3755 | 128.3755 | 128.3755
97% | 140.3338 | 194.8074 | 208.9687 | 211.3826 | 213.2652 | 216.5068 | 223.8816 | 228.8183 | 235.0721 | 238.3182 | 241.174 | 235.9121 | 242.0789 | 251.7738 | 244.4167 | 244.4167 | 244.4167 | 244.4167 | 244.4167 | 244.4167 | 244.4167 | 244.4167 | 244.4167 | 244.4167 | 244.4167 | 244.4167 | 244.4167 | 244.4167 | 244.4167 | 244.4167 |  | 150.2438 | 204.0305 | 218.7445 | 221.0211 | 222.4667 | 225.638 | 233.1281 | 237.2175 | 245.0078 | 268.6881 | 249.1661 | 245.3476 | 250.5021 | 261.7749 | 254.1445 | 254.1445 | 254.1445 | 254.1445 | 254.1445 | 254.1445 | 254.1445 | 254.1445 | 254.1445 | 254.1445 | 254.1445 | 254.1445 | 254.1445 | 254.1445 | 254.1445 | 254.1445
95% | 414.5243 | 575.4311 | 617.2612 | 624.3915 | 629.9527 | 639.5277 | 661.3119 | 675.8939 | 694.3669 | 703.9554 | 712.391 | 696.8482 | 715.0638 | 743.7009 | 721.9694 | 721.9694 | 721.9694 | 721.9694 | 721.9694 | 721.9694 | 721.9694 | 721.9694 | 721.9694 | 721.9694 | 721.9694 | 721.9694 | 721.9694 | 721.9694 | 721.9694 | 721.9694 |  | 443.7972 | 602.6746 | 646.1375 | 652.8624 | 657.1324 | 666.4999 | 688.6245 | 700.704 | 723.7153 | 793.6633 | 735.9983 | 724.719 | 739.9446 | 773.2427 | 750.7037 | 750.7037 | 750.7037 | 750.7037 | 750.7037 | 750.7037 | 750.7037 | 750.7037 | 750.7037 | 750.7037 | 750.7037 | 750.7037 | 750.7037 | 750.7037 | 750.7037 | 750.7037
90% | 2285.5212 | 3172.6969 | 3403.3313 | 3442.6449 | 3473.3067 | 3526.0998 | 3646.209 | 3726.6085 | 3828.4608 | 3881.3281 | 3927.8385 | 3842.1418 | 3942.5756 | 4100.4692 | 3980.6499 | 3980.6499 | 3980.6499 | 3980.6499 | 3980.6499 | 3980.6499 | 3980.6499 | 3980.6499 | 3980.6499 | 3980.6499 | 3980.6499 | 3980.6499 | 3980.6499 | 3980.6499 | 3980.6499 | 3980.6499 |  | 2446.9201 | 3322.9067 | 3562.5435 | 3599.622 | 3623.165 | 3674.8134 | 3796.7998 | 3863.4014 | 3990.2765 | 4375.9415 | 4058 | 3995.8103 | 4079.7583 | 4263.3504 | 4139.0795 | 4139.0795 | 4139.0795 | 4139.0795 | 4139.0795 | 4139.0795 | 4139.0795 | 4139.0795 | 4139.0795 | 4139.0795 | 4139.0795 | 4139.0795 | 4139.0795 | 4139.0795 | 4139.0795 | 4139.0795
85% | 5583.3646 | 7750.6712 | 8314.0946 | 8410.1348 | 8485.0395 | 8614.0092 | 8907.4274 | 9103.8375 | 9352.6555 | 9481.8066 | 9595.4282 | 9386.0773 | 9631.4298 | 10017.1525 | 9724.4425 | 9724.4425 | 9724.4425 | 9724.4425 | 9724.4425 | 9724.4425 | 9724.4425 | 9724.4425 | 9724.4425 | 9724.4425 | 9724.4425 | 9724.4425 | 9724.4425 | 9724.4425 | 9724.4425 | 9724.4425 |  | 5977.6505 | 8117.623 | 8703.0385 | 8793.6186 | 8851.1326 | 8977.3059 | 9275.3098 | 9438.0128 | 9747.9596 | 10690.1116 | 9913.4032 | 9761.4782 | 9966.5573 | 10415.0597 | 10111.4747 | 10111.4747 | 10111.4747 | 10111.4747 | 10111.4747 | 10111.4747 | 10111.4747 | 10111.4747 | 10111.4747 | 10111.4747 | 10111.4747 | 10111.4747 | 10111.4747 | 10111.4747 | 10111.4747 | 10111.4747
80% | 8678.2039 | 12046.8408 | 12922.5678 | 13071.8427 | 13188.2668 | 13388.724 | 13844.7828 | 14150.0624 | 14536.7992 | 14737.5384 | 14914.14 | 14588.7467 | 14970.0973 | 15569.6246 | 15114.6665 | 15114.6665 | 15114.6665 | 15114.6665 | 15114.6665 | 15114.6665 | 15114.6665 | 15114.6665 | 15114.6665 | 15114.6665 | 15114.6665 | 15114.6665 | 15114.6665 | 15114.6665 | 15114.6665 | 15114.6665 |  | 9291.041 | 12617.1926 | 13527.1019 | 13667.8902 | 13757.2841 | 13953.3947 | 14416.5812 | 14669.4699 | 15151.219 | 16615.6026 | 15408.3675 | 15172.231 | 15490.9847 | 16188.0904 | 15716.2292 | 15716.2292 | 15716.2292 | 15716.2292 | 15716.2292 | 15716.2292 | 15716.2292 | 15716.2292 | 15716.2292 | 15716.2292 | 15716.2292 | 15716.2292 | 15716.2292 | 15716.2292 | 15716.2292 | 15716.2292
75% | 9574.4808 | 13291.0275 | 14257.1987 | 14421.8907 | 14550.339 | 14771.4991 | 15274.6593 | 15611.4679 | 16038.1465 | 16259.6179 | 16454.4587 | 16095.4591 | 16516.1952 | 17177.6412 | 16675.6955 | 16675.6955 | 16675.6955 | 16675.6955 | 16675.6955 | 16675.6955 | 16675.6955 | 16675.6955 | 16675.6955 | 16675.6955 | 16675.6955 | 16675.6955 | 16675.6955 | 16675.6955 | 16675.6955 | 16675.6955 |  | 10250.6112 | 13920.2847 | 14924.1686 | 15079.4974 | 15178.1238 | 15394.4886 | 15905.5125 | 16184.5193 | 16716.023 | 18331.6468 | 16999.7296 | 16739.2052 | 17090.8794 | 17859.9816 | 17339.387 | 17339.387 | 17339.387 | 17339.387 | 17339.387 | 17339.387 | 17339.387 | 17339.387 | 17339.387 | 17339.387 | 17339.387 | 17339.387 | 17339.387 | 17339.387 | 17339.387 | 17339.387
70% | 10287.2444 | 14280.4661 | 15318.563 | 15495.5153 | 15633.5258 | 15871.15 | 16411.7675 | 16773.6495 | 17232.0919 | 17470.0505 | 17679.396 | 17293.671 | 17745.7284 | 18456.4151 | 17917.1025 | 17917.1025 | 17917.1025 | 17917.1025 | 17917.1025 | 17917.1025 | 17917.1025 | 17917.1025 | 17917.1025 | 17917.1025 | 17917.1025 | 17917.1025 | 17917.1025 | 17917.1025 | 17917.1025 | 17917.1025 |  | 11013.7087 | 14956.5677 | 16035.1849 | 16202.077 | 16308.0455 | 16540.5174 | 17089.584 | 17389.3613 | 17960.4323 | 19696.3297 | 18265.2591 | 17985.3402 | 18363.1944 | 19189.5518 | 18630.202 | 18630.202 | 18630.202 | 18630.202 | 18630.202 | 18630.202 | 18630.202 | 18630.202 | 18630.202 | 18630.202 | 18630.202 | 18630.202 | 18630.202 | 18630.202 | 18630.202 | 18630.202
65% | 10840.7831 | 15048.8731 | 16142.8282 | 16329.302 | 16474.7386 | 16725.149 | 17294.8562 | 17676.2104 | 18159.3208 | 18410.0835 | 18630.6936 | 18224.2134 | 18700.5952 | 19449.5227 | 18881.1907 | 18881.1907 | 18881.1907 | 18881.1907 | 18881.1907 | 18881.1907 | 18881.1907 | 18881.1907 | 18881.1907 | 18881.1907 | 18881.1907 | 18881.1907 | 18881.1907 | 18881.1907 | 18881.1907 | 18881.1907 |  | 11606.3372 | 15761.3546 | 16898.0103 | 17073.8826 | 17185.553 | 17430.5339 | 18009.1448 | 18325.0525 | 18926.8519 | 20756.155 | 19248.0809 | 18953.1 | 19351.286 | 20222.1082 | 19632.6608 | 19632.6608 | 19632.6608 | 19632.6608 | 19632.6608 | 19632.6608 | 19632.6608 | 19632.6608 | 19632.6608 | 19632.6608 | 19632.6608 | 19632.6608 | 19632.6608 | 19632.6608 | 19632.6608 | 19632.6608
60% | 11934.3669 | 16566.9557 | 17771.2656 | 17976.5503 | 18136.658 | 18412.329 | 19039.5064 | 19459.3305 | 19991.1755 | 20267.2344 | 20510.0989 | 20062.6142 | 20587.052 | 21411.5289 | 20785.8653 | 20785.8653 | 20785.8653 | 20785.8653 | 20785.8653 | 20785.8653 | 20785.8653 | 20785.8653 | 20785.8653 | 20785.8653 | 20785.8653 | 20785.8653 | 20785.8653 | 20785.8653 | 20785.8653 | 20785.8653 |  | 12777.1477 | 17351.3101 | 18602.628 | 18796.2417 | 18919.1771 | 19188.8708 | 19825.8502 | 20173.6257 | 20836.1327 | 22849.9701 | 21189.7663 | 20865.0287 | 21303.3824 | 22262.0503 | 21613.1413 | 21613.1413 | 21613.1413 | 21613.1413 | 21613.1413 | 21613.1413 | 21613.1413 | 21613.1413 | 21613.1413 | 21613.1413 | 21613.1413 | 21613.1413 | 21613.1413 | 21613.1413 | 21613.1413 | 21613.1413
55% | 13276.2336 | 18429.6976 | 19769.4166 | 19997.783 | 20175.8928 | 20482.5595 | 21180.255 | 21647.2828 | 22238.927 | 22546.0252 | 22816.1967 | 22318.3981 | 22901.8021 | 23818.981 | 23122.9695 | 23122.9695 | 23122.9695 | 23122.9695 | 23122.9695 | 23122.9695 | 23122.9695 | 23122.9695 | 23122.9695 | 23122.9695 | 23122.9695 | 23122.9695 | 23122.9695 | 23122.9695 | 23122.9695 | 23122.9695 |  | 14213.7742 | 19302.2426 | 20694.2551 | 20909.6382 | 21046.3962 | 21346.4135 | 22055.013 | 22441.8914 | 23178.8888 | 25419.1564 | 23572.284 | 23211.0338 | 23698.6747 | 24765.1326 | 24043.2621 | 24043.2621 | 24043.2621 | 24043.2621 | 24043.2621 | 24043.2621 | 24043.2621 | 24043.2621 | 24043.2621 | 24043.2621 | 24043.2621 | 24043.2621 | 24043.2621 | 24043.2621 | 24043.2621 | 24043.2621
50% | 13456.7484 | 18680.2832 | 20038.2182 | 20269.6896 | 20450.2212 | 20761.0575 | 21468.2395 | 21941.6174 | 22541.3061 | 22852.5798 | 23126.4248 | 22621.8577 | 23213.1942 | 24142.8438 | 23437.3688 | 23437.3688 | 23437.3688 | 23437.3688 | 23437.3688 | 23437.3688 | 23437.3688 | 23437.3688 | 23437.3688 | 23437.3688 | 23437.3688 | 23437.3688 | 23437.3688 | 23437.3688 | 23437.3688 | 23437.3688 |  | 14407.0366 | 19564.692 | 20975.6315 | 21193.9432 | 21332.5606 | 21636.6572 | 22354.8915 | 22747.0302 | 23494.0484 | 25764.7766 | 23892.7925 | 23526.6304 | 24020.9018 | 25101.8601 | 24370.1745 | 24370.1745 | 24370.1745 | 24370.1745 | 24370.1745 | 24370.1745 | 24370.1745 | 24370.1745 | 24370.1745 | 24370.1745 | 24370.1745 | 24370.1745 | 24370.1745 | 24370.1745 | 24370.1745 | 24370.1745
45% | 10386.1977 | 14417.8303 | 15465.9127 | 15644.5671 | 15783.9051 | 16023.8151 | 16569.6328 | 16934.9957 | 17397.8478 | 17638.0954 | 17849.4547 | 17460.0193 | 17916.4251 | 18633.9479 | 18089.4477 | 18089.4477 | 18089.4477 | 18089.4477 | 18089.4477 | 18089.4477 | 18089.4477 | 18089.4477 | 18089.4477 | 18089.4477 | 18089.4477 | 18089.4477 | 18089.4477 | 18089.4477 | 18089.4477 | 18089.4477 |  | 11119.6499 | 15100.4354 | 16189.4278 | 16357.9252 | 16464.913 | 16699.6211 | 17253.9692 | 17556.63 | 18133.1942 | 19885.7893 | 18440.9531 | 18158.3417 | 18539.8305 | 19374.1366 | 18809.4064 | 18809.4064 | 18809.4064 | 18809.4064 | 18809.4064 | 18809.4064 | 18809.4064 | 18809.4064 | 18809.4064 | 18809.4064 | 18809.4064 | 18809.4064 | 18809.4064 | 18809.4064 | 18809.4064 | 18809.4064
40% | 5102.6915 | 7083.4142 | 7598.3323 | 7686.1044 | 7754.5606 | 7872.4272 | 8140.5849 | 8320.0861 | 8547.4832 | 8665.5158 | 8769.3556 | 8578.0278 | 8802.2579 | 9154.7736 | 8887.2631 | 8887.2631 | 8887.2631 | 8887.2631 | 8887.2631 | 8887.2631 | 8887.2631 | 8887.2631 | 8887.2631 | 8887.2631 | 8887.2631 | 8887.2631 | 8887.2631 | 8887.2631 | 8887.2631 | 8887.2631 |  | 5463.0332 | 7418.775 | 7953.792 | 8036.574 | 8089.1366 | 8204.4476 | 8476.7963 | 8625.4922 | 8908.7555 | 9769.7975 | 9059.9561 | 8921.1104 | 9108.5341 | 9518.4249 | 9240.9755 | 9240.9755 | 9240.9755 | 9240.9755 | 9240.9755 | 9240.9755 | 9240.9755 | 9240.9755 | 9240.9755 | 9240.9755 | 9240.9755 | 9240.9755 | 9240.9755 | 9240.9755 | 9240.9755 | 9240.9755
35% | 1907.0998 | 2647.3829 | 2839.8304 | 2872.6347 | 2898.2197 | 2942.2717 | 3042.494 | 3109.5815 | 3194.5697 | 3238.6837 | 3277.4932 | 3205.9856 | 3289.7902 | 3421.5408 | 3321.5604 | 3321.5604 | 3321.5604 | 3321.5604 | 3321.5604 | 3321.5604 | 3321.5604 | 3321.5604 | 3321.5604 | 3321.5604 | 3321.5604 | 3321.5604 | 3321.5604 | 3321.5604 | 3321.5604 | 3321.5604 |  | 2041.7754 | 2772.7219 | 2972.6813 | 3003.6205 | 3023.2655 | 3066.3623 | 3168.1509 | 3223.7251 | 3329.5931 | 3651.4023 | 3386.1034 | 3334.2106 | 3404.2591 | 3557.4533 | 3453.7583 | 3453.7583 | 3453.7583 | 3453.7583 | 3453.7583 | 3453.7583 | 3453.7583 | 3453.7583 | 3453.7583 | 3453.7583 | 3453.7583 | 3453.7583 | 3453.7583 | 3453.7583 | 3453.7583 | 3453.7583
30% | 951.1511 | 1320.3614 | 1416.3431 | 1432.704 | 1445.4643 | 1467.4349 | 1517.42 | 1550.8793 | 1593.2665 | 1615.268 | 1634.624 | 1598.9601 | 1640.757 | 1706.4666 | 1656.6021 | 1656.6021 | 1656.6021 | 1656.6021 | 1656.6021 | 1656.6021 | 1656.6021 | 1656.6021 | 1656.6021 | 1656.6021 | 1656.6021 | 1656.6021 | 1656.6021 | 1656.6021 | 1656.6021 | 1656.6021 |  | 1018.3194 | 1382.8733 | 1482.6014 | 1498.0321 | 1507.8299 | 1529.3241 | 1580.0904 | 1607.8076 | 1660.6084 | 1821.1082 | 1688.7924 | 1662.9113 | 1697.8475 | 1774.2519 | 1722.5348 | 1722.5348 | 1722.5348 | 1722.5348 | 1722.5348 | 1722.5348 | 1722.5348 | 1722.5348 | 1722.5348 | 1722.5348 | 1722.5348 | 1722.5348 | 1722.5348 | 1722.5348 | 1722.5348 | 1722.5348
25% | 560.7353 | 778.3972 | 834.9816 | 844.6269 | 852.1495 | 865.1019 | 894.5698 | 914.2952 | 939.2839 | 952.2545 | 963.6655 | 942.6404 | 967.2811 | 1006.0191 | 976.6223 | 976.6223 | 976.6223 | 976.6223 | 976.6223 | 976.6223 | 976.6223 | 976.6223 | 976.6223 | 976.6223 | 976.6223 | 976.6223 | 976.6223 | 976.6223 | 976.6223 | 976.6223 |  | 600.3333 | 815.25 | 874.0431 | 883.14 | 888.9161 | 901.5876 | 931.5161 | 947.8563 | 978.9841 | 1073.6041 | 995.5996 | 980.3418 | 1000.9378 | 1045.9808 | 1015.4918 | 1015.4918 | 1015.4918 | 1015.4918 | 1015.4918 | 1015.4918 | 1015.4918 | 1015.4918 | 1015.4918 | 1015.4918 | 1015.4918 | 1015.4918 | 1015.4918 | 1015.4918 | 1015.4918 | 1015.4918
20% | 283.3663 | 393.3611 | 421.9559 | 426.8302 | 430.6317 | 437.1772 | 452.0687 | 462.0369 | 474.6648 | 481.2195 | 486.986 | 476.3611 | 488.8132 | 508.3893 | 493.5337 | 493.5337 | 493.5337 | 493.5337 | 493.5337 | 493.5337 | 493.5337 | 493.5337 | 493.5337 | 493.5337 | 493.5337 | 493.5337 | 493.5337 | 493.5337 | 493.5337 | 493.5337 |  | 303.377 | 411.9846 | 441.6956 | 446.2927 | 449.2116 | 455.6151 | 470.7394 | 478.9969 | 494.7273 | 542.5433 | 503.1238 | 495.4134 | 505.8215 | 528.5839 | 513.1763 | 513.1763 | 513.1763 | 513.1763 | 513.1763 | 513.1763 | 513.1763 | 513.1763 | 513.1763 | 513.1763 | 513.1763 | 513.1763 | 513.1763 | 513.1763 | 513.1763 | 513.1763
15% | 115.4455 | 160.2582 | 171.908 | 173.8938 | 175.4425 | 178.1092 | 184.1761 | 188.2372 | 193.382 | 196.0524 | 198.4017 | 194.073 | 199.1461 | 207.1216 | 201.0693 | 201.0693 | 201.0693 | 201.0693 | 201.0693 | 201.0693 | 201.0693 | 201.0693 | 201.0693 | 201.0693 | 201.0693 | 201.0693 | 201.0693 | 201.0693 | 201.0693 | 201.0693 |  | 123.598 | 167.8456 | 179.95 | 181.8229 | 183.0121 | 185.621 | 191.7827 | 195.1469 | 201.5556 | 221.0361 | 204.9764 | 201.8351 | 206.0754 | 215.349 | 209.0718 | 209.0718 | 209.0718 | 209.0718 | 209.0718 | 209.0718 | 209.0718 | 209.0718 | 209.0718 | 209.0718 | 209.0718 | 209.0718 | 209.0718 | 209.0718 | 209.0718 | 209.0718
10% | 46.4781 | 64.5196 | 69.2097 | 70.0092 | 70.6327 | 71.7063 | 74.1488 | 75.7838 | 77.8551 | 78.9302 | 79.876 | 78.1333 | 80.1757 | 83.3866 | 80.95 | 80.95 | 80.95 | 80.95 | 80.95 | 80.95 | 80.95 | 80.95 | 80.95 | 80.95 | 80.95 | 80.95 | 80.95 | 80.95 | 80.95 | 80.95 |  | 49.7602 | 67.5742 | 72.4474 | 73.2014 | 73.6802 | 74.7305 | 77.2112 | 78.5656 | 81.1457 | 88.9886 | 82.523 | 81.2583 | 82.9654 | 86.6989 | 84.1718 | 84.1718 | 84.1718 | 84.1718 | 84.1718 | 84.1718 | 84.1718 | 84.1718 | 84.1718 | 84.1718 | 84.1718 | 84.1718 | 84.1718 | 84.1718 | 84.1718 | 84.1718
5% | 39.5813 | 54.9457 | 58.9399 | 59.6207 | 60.1517 | 61.066 | 63.1461 | 64.5385 | 66.3024 | 67.218 | 68.0234 | 66.5393 | 68.2787 | 71.0131 | 68.938 | 68.938 | 68.938 | 68.938 | 68.938 | 68.938 | 68.938 | 68.938 | 68.938 | 68.938 | 68.938 | 68.938 | 68.938 | 68.938 | 68.938 | 68.938 |  | 42.3765 | 57.5471 | 61.6972 | 62.3393 | 62.747 | 63.6415 | 65.7541 | 66.9075 | 69.1048 | 75.7838 | 70.2776 | 69.2006 | 70.6544 | 73.8339 | 71.6818 | 71.6818 | 71.6818 | 71.6818 | 71.6818 | 71.6818 | 71.6818 | 71.6818 | 71.6818 | 71.6818 | 71.6818 | 71.6818 | 71.6818 | 71.6818 | 71.6818 | 71.6818
9.992e-14% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E @ R (MWh) | 105995.1099 | 147139.4588 | 157835.5397 | 159658.7762 | 161080.774 | 163529.1464 | 169099.4242 | 172828.0925 | 177551.675 | 180003.4929 | 182160.4948 | 178186.1586 | 182843.9537 | 190166.5478 | 184609.7151 | 184609.7151 | 184609.7151 | 184609.7151 | 184609.7151 | 184609.7151 | 184609.7151 | 184609.7151 | 184609.7151 | 184609.7151 | 184609.7151 | 184609.7151 | 184609.7151 | 184609.7151 | 184609.7151 | 184609.7151 | E @ R (MWh) | 113480.2695 | 154105.704 | 165219.287 | 166938.8679 | 168030.7193 | 170426.0046 | 176083.3386 | 179172.1077 | 185056.165 | 202942.0666 | 188196.9625 | 185312.8045 | 189206.044 | 197720.4561 | 191957.169 | 191957.169 | 191957.169 | 191957.169 | 191957.169 | 191957.169 | 191957.169 | 191957.169 | 191957.169 | 191957.169 | 191957.169 | 191957.169 | 191957.169 | 191957.169 | 191957.169 | 191957.169
Option 7 Winter POE50 W E @ R (MWh) N 2 | 74196.5769 | 102997.6211 | 110484.8778 | 111761.1434 | 112756.5418 | 114470.4025 | 118369.597 | 120979.6647 | 124286.1725 | 126002.4451 | 127512.3464 | 124730.311 | 127990.7676 | 133116.5835 | 129226.8005 | 129226.8005 | 129226.8005 | 129226.8005 | 129226.8005 | 129226.8005 | 129226.8005 | 129226.8005 | 129226.8005 | 129226.8005 | 129226.8005 | 129226.8005 | 129226.8005 | 129226.8005 | 129226.8005 | 129226.8005 | Option 7 Winter POE10 W E @ R (MWh) N 2 | 34044.0809 | 46231.7112 | 49565.7861 | 50081.6604 | 50409.2158 | 51127.8014 | 52825.0016 | 53751.6323 | 55516.8495 | 60882.62 | 56459.0887 | 55593.8414 | 56761.8132 | 59316.1368 | 57587.1507 | 57587.1507 | 57587.1507 | 57587.1507 | 57587.1507 | 57587.1507 | 57587.1507 | 57587.1507 | 57587.1507 | 57587.1507 | 57587.1507 | 57587.1507 | 57587.1507 | 57587.1507 | 57587.1507 | 57587.1507
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 76.9936 | 99.7405 | 105.6969 | 105.3426 | 105.3724 | 105.9856 | 107.6 | 108.6824 | 109.7411 | 110.979 | 112.1272 | 113.2411 | 113.3701 | 114.6698 | 113.6883 | 113.6883 | 113.6883 | 113.6883 | 113.6883 | 113.6883 | 113.6883 | 113.6883 | 113.6883 | 113.6883 | 113.6883 | 113.6883 | 113.6883 | 113.6883 | 113.6883 | 113.6883
98% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 38.1099 | 49.369 | 52.3173 | 52.1419 | 52.1567 | 52.4602 | 53.2593 | 53.7951 | 54.3191 | 54.9318 | 55.5002 | 56.0515 | 56.1154 | 56.7587 | 56.2728 | 56.2728 | 56.2728 | 56.2728 | 56.2728 | 56.2728 | 56.2728 | 56.2728 | 56.2728 | 56.2728 | 56.2728 | 56.2728 | 56.2728 | 56.2728 | 56.2728 | 56.2728
97% | 16.9149 | 22.4762 | 23.991 | 23.9477 | 23.9472 | 24.1204 | 24.3105 | 24.7002 | 24.9803 | 25.1325 | 25.2993 | 25.4517 | 25.7265 | 26.0674 | 26.0444 | 26.0444 | 26.0444 | 26.0444 | 26.0444 | 26.0444 | 26.0444 | 26.0444 | 26.0444 | 26.0444 | 26.0444 | 26.0444 | 26.0444 | 26.0444 | 26.0444 | 26.0444 |  | 75.446 | 97.7357 | 103.5723 | 103.2252 | 103.2543 | 103.8552 | 105.4372 | 106.4978 | 107.5353 | 108.7483 | 109.8734 | 110.9649 | 111.0913 | 112.3649 | 111.4031 | 111.4031 | 111.4031 | 111.4031 | 111.4031 | 111.4031 | 111.4031 | 111.4031 | 111.4031 | 111.4031 | 111.4031 | 111.4031 | 111.4031 | 111.4031 | 111.4031 | 111.4031
95% | 83.2734 | 110.6519 | 118.1097 | 117.8962 | 117.8937 | 118.7467 | 119.6823 | 121.6012 | 122.9798 | 123.7293 | 124.5504 | 125.3007 | 126.6535 | 128.3318 | 128.2183 | 128.2183 | 128.2183 | 128.2183 | 128.2183 | 128.2183 | 128.2183 | 128.2183 | 128.2183 | 128.2183 | 128.2183 | 128.2183 | 128.2183 | 128.2183 | 128.2183 | 128.2183 |  | 111.4279 | 144.3481 | 152.9683 | 152.4556 | 152.4987 | 153.3862 | 155.7226 | 157.2891 | 158.8214 | 160.6129 | 162.2746 | 163.8866 | 164.0733 | 165.9543 | 164.5337 | 164.5337 | 164.5337 | 164.5337 | 164.5337 | 164.5337 | 164.5337 | 164.5337 | 164.5337 | 164.5337 | 164.5337 | 164.5337 | 164.5337 | 164.5337 | 164.5337 | 164.5337
90% | 144.4273 | 191.9119 | 204.8464 | 204.4763 | 204.4719 | 205.9512 | 207.574 | 210.9021 | 213.2931 | 214.593 | 216.0171 | 217.3184 | 219.6647 | 222.5754 | 222.3787 | 222.3787 | 222.3787 | 222.3787 | 222.3787 | 222.3787 | 222.3787 | 222.3787 | 222.3787 | 222.3787 | 222.3787 | 222.3787 | 222.3787 | 222.3787 | 222.3787 | 222.3787 |  | 483.1446 | 625.8842 | 663.261 | 661.0381 | 661.2248 | 665.0728 | 675.2033 | 681.9957 | 688.6395 | 696.4074 | 703.6125 | 710.602 | 711.4117 | 719.5673 | 713.4081 | 713.4081 | 713.4081 | 713.4081 | 713.4081 | 713.4081 | 713.4081 | 713.4081 | 713.4081 | 713.4081 | 713.4081 | 713.4081 | 713.4081 | 713.4081 | 713.4081 | 713.4081
85% | 409.8612 | 544.6148 | 581.321 | 580.2706 | 580.258 | 584.4562 | 589.0613 | 598.5059 | 605.2912 | 608.9802 | 613.0214 | 616.7142 | 623.3728 | 631.6329 | 631.0746 | 631.0746 | 631.0746 | 631.0746 | 631.0746 | 631.0746 | 631.0746 | 631.0746 | 631.0746 | 631.0746 | 631.0746 | 631.0746 | 631.0746 | 631.0746 | 631.0746 | 631.0746 |  | 457.0286 | 592.0526 | 627.4091 | 625.3063 | 625.4829 | 629.1229 | 638.7059 | 645.1311 | 651.4157 | 658.7637 | 665.5794 | 672.1911 | 672.9571 | 680.6717 | 674.8455 | 674.8455 | 674.8455 | 674.8455 | 674.8455 | 674.8455 | 674.8455 | 674.8455 | 674.8455 | 674.8455 | 674.8455 | 674.8455 | 674.8455 | 674.8455 | 674.8455 | 674.8455
80% | 572.5046 | 760.7318 | 812.0039 | 810.5367 | 810.5191 | 816.3833 | 822.8158 | 836.0082 | 845.4861 | 850.639 | 856.2839 | 861.4421 | 870.743 | 882.2809 | 881.5011 | 881.5011 | 881.5011 | 881.5011 | 881.5011 | 881.5011 | 881.5011 | 881.5011 | 881.5011 | 881.5011 | 881.5011 | 881.5011 | 881.5011 | 881.5011 | 881.5011 | 881.5011 |  | 319.1946 | 413.4971 | 438.1905 | 436.7219 | 436.8452 | 439.3874 | 446.0803 | 450.5677 | 454.957 | 460.089 | 464.8491 | 469.4668 | 470.0018 | 475.3898 | 471.3206 | 471.3206 | 471.3206 | 471.3206 | 471.3206 | 471.3206 | 471.3206 | 471.3206 | 471.3206 | 471.3206 | 471.3206 | 471.3206 | 471.3206 | 471.3206 | 471.3206 | 471.3206
75% | 1492.4153 | 1983.0895 | 2116.7465 | 2112.9218 | 2112.876 | 2128.1627 | 2144.9312 | 2179.3214 | 2204.0286 | 2217.4612 | 2232.1763 | 2245.623 | 2269.8686 | 2299.9458 | 2297.9131 | 2297.9131 | 2297.9131 | 2297.9131 | 2297.9131 | 2297.9131 | 2297.9131 | 2297.9131 | 2297.9131 | 2297.9131 | 2297.9131 | 2297.9131 | 2297.9131 | 2297.9131 | 2297.9131 | 2297.9131 |  | 569.714 | 738.0296 | 782.1036 | 779.4824 | 779.7025 | 784.24 | 796.1857 | 804.1951 | 812.0293 | 821.1891 | 829.6853 | 837.9271 | 838.8819 | 848.4987 | 841.2359 | 841.2359 | 841.2359 | 841.2359 | 841.2359 | 841.2359 | 841.2359 | 841.2359 | 841.2359 | 841.2359 | 841.2359 | 841.2359 | 841.2359 | 841.2359 | 841.2359 | 841.2359
70% | 2578.4391 | 3426.1747 | 3657.0932 | 3650.4854 | 3650.4063 | 3676.8171 | 3705.7879 | 3765.2037 | 3807.8902 | 3831.0976 | 3856.5209 | 3879.7526 | 3921.6416 | 3973.6059 | 3970.094 | 3970.094 | 3970.094 | 3970.094 | 3970.094 | 3970.094 | 3970.094 | 3970.094 | 3970.094 | 3970.094 | 3970.094 | 3970.094 | 3970.094 | 3970.094 | 3970.094 | 3970.094 |  | 1037.8661 | 1344.492 | 1424.783 | 1420.0079 | 1420.4087 | 1428.6749 | 1450.4368 | 1465.0278 | 1479.2996 | 1495.9862 | 1511.464 | 1526.4784 | 1528.2178 | 1545.7371 | 1532.5062 | 1532.5062 | 1532.5062 | 1532.5062 | 1532.5062 | 1532.5062 | 1532.5062 | 1532.5062 | 1532.5062 | 1532.5062 | 1532.5062 | 1532.5062 | 1532.5062 | 1532.5062 | 1532.5062 | 1532.5062
65% | 6475.8072 | 8604.914 | 9184.8711 | 9168.2753 | 9168.0768 | 9234.408 | 9307.1689 | 9456.393 | 9563.6012 | 9621.887 | 9685.7381 | 9744.0851 | 9849.2903 | 9979.7998 | 9970.9794 | 9970.9794 | 9970.9794 | 9970.9794 | 9970.9794 | 9970.9794 | 9970.9794 | 9970.9794 | 9970.9794 | 9970.9794 | 9970.9794 | 9970.9794 | 9970.9794 | 9970.9794 | 9970.9794 | 9970.9794 |  | 1305.7961 | 1691.5789 | 1792.5974 | 1786.5896 | 1787.0939 | 1797.4941 | 1824.8739 | 1843.2317 | 1861.1878 | 1882.1821 | 1901.6555 | 1920.546 | 1922.7344 | 1944.7764 | 1928.1299 | 1928.1299 | 1928.1299 | 1928.1299 | 1928.1299 | 1928.1299 | 1928.1299 | 1928.1299 | 1928.1299 | 1928.1299 | 1928.1299 | 1928.1299 | 1928.1299 | 1928.1299 | 1928.1299 | 1928.1299
60% | 9465.8424 | 12578.0087 | 13425.7459 | 13401.4874 | 13401.1972 | 13498.1551 | 13604.5115 | 13822.636 | 13979.3447 | 14064.5425 | 14157.8751 | 14243.1624 | 14396.9433 | 14587.7122 | 14574.8193 | 14574.8193 | 14574.8193 | 14574.8193 | 14574.8193 | 14574.8193 | 14574.8193 | 14574.8193 | 14574.8193 | 14574.8193 | 14574.8193 | 14574.8193 | 14574.8193 | 14574.8193 | 14574.8193 | 14574.8193 |  | 2043.3291 | 2647.0078 | 2805.083 | 2795.6818 | 2796.4711 | 2812.7454 | 2855.5897 | 2884.3162 | 2912.4142 | 2945.2664 | 2975.7387 | 3005.2988 | 3008.7233 | 3043.2149 | 3017.1662 | 3017.1662 | 3017.1662 | 3017.1662 | 3017.1662 | 3017.1662 | 3017.1662 | 3017.1662 | 3017.1662 | 3017.1662 | 3017.1662 | 3017.1662 | 3017.1662 | 3017.1662 | 3017.1662 | 3017.1662
55% | 10703.6666 | 14222.8031 | 15181.3967 | 15153.966 | 15153.6378 | 15263.2747 | 15383.539 | 15630.1871 | 15807.3882 | 15903.7271 | 16009.2646 | 16105.7046 | 16279.5951 | 16495.3104 | 16480.7315 | 16480.7315 | 16480.7315 | 16480.7315 | 16480.7315 | 16480.7315 | 16480.7315 | 16480.7315 | 16480.7315 | 16480.7315 | 16480.7315 | 16480.7315 | 16480.7315 | 16480.7315 | 16480.7315 | 16480.7315 |  | 3926.5772 | 5086.6405 | 5390.4069 | 5372.341 | 5373.8577 | 5405.1313 | 5487.4633 | 5542.6658 | 5596.6606 | 5659.7913 | 5718.3486 | 5775.1529 | 5781.7337 | 5848.0147 | 5797.958 | 5797.958 | 5797.958 | 5797.958 | 5797.958 | 5797.958 | 5797.958 | 5797.958 | 5797.958 | 5797.958 | 5797.958 | 5797.958 | 5797.958 | 5797.958 | 5797.958 | 5797.958
50% | 13744.0128 | 18262.75 | 19493.6294 | 19458.4071 | 19457.9857 | 19598.7646 | 19753.1897 | 20069.8975 | 20297.432 | 20421.1357 | 20556.6509 | 20680.4844 | 20903.7679 | 21180.7565 | 21162.0366 | 21162.0366 | 21162.0366 | 21162.0366 | 21162.0366 | 21162.0366 | 21162.0366 | 21162.0366 | 21162.0366 | 21162.0366 | 21162.0366 | 21162.0366 | 21162.0366 | 21162.0366 | 21162.0366 | 21162.0366 |  | 8714.0125 | 11288.47 | 11962.6002 | 11922.5077 | 11925.8735 | 11995.2773 | 12177.9916 | 12300.4992 | 12420.3265 | 12560.4285 | 12690.3811 | 12816.4434 | 12831.0478 | 12978.1412 | 12867.0534 | 12867.0534 | 12867.0534 | 12867.0534 | 12867.0534 | 12867.0534 | 12867.0534 | 12867.0534 | 12867.0534 | 12867.0534 | 12867.0534 | 12867.0534 | 12867.0534 | 12867.0534 | 12867.0534 | 12867.0534
45% | 18302.3635 | 24319.7888 | 25958.9027 | 25911.9985 | 25911.4373 | 26098.9072 | 26304.5489 | 26726.2963 | 27029.2951 | 27194.0265 | 27374.4867 | 27539.391 | 27836.7289 | 28205.5838 | 28180.6551 | 28180.6551 | 28180.6551 | 28180.6551 | 28180.6551 | 28180.6551 | 28180.6551 | 28180.6551 | 28180.6551 | 28180.6551 | 28180.6551 | 28180.6551 | 28180.6551 | 28180.6551 | 28180.6551 | 28180.6551 |  | 13204.5002 | 17105.6219 | 18127.1435 | 18066.3908 | 18071.491 | 18176.6598 | 18453.5301 | 18639.1681 | 18820.7445 | 19033.0436 | 19229.9631 | 19420.9876 | 19443.1179 | 19666.0112 | 19497.6778 | 19497.6778 | 19497.6778 | 19497.6778 | 19497.6778 | 19497.6778 | 19497.6778 | 19497.6778 | 19497.6778 | 19497.6778 | 19497.6778 | 19497.6778 | 19497.6778 | 19497.6778 | 19497.6778 | 19497.6778
40% | 12836.6798 | 17057.1053 | 18206.7263 | 18173.8293 | 18173.4357 | 18304.9209 | 18449.1513 | 18744.9511 | 18957.4646 | 19073.0018 | 19199.5707 | 19315.2292 | 19523.7723 | 19782.475 | 19764.9909 | 19764.9909 | 19764.9909 | 19764.9909 | 19764.9909 | 19764.9909 | 19764.9909 | 19764.9909 | 19764.9909 | 19764.9909 | 19764.9909 | 19764.9909 | 19764.9909 | 19764.9909 | 19764.9909 | 19764.9909 |  | 13672.6523 | 17712.0843 | 18769.8229 | 18706.9162 | 18712.1973 | 18821.0947 | 19107.7811 | 19300.0008 | 19488.0148 | 19707.8407 | 19911.7418 | 20109.5389 | 20132.4538 | 20363.2496 | 20188.9481 | 20188.9481 | 20188.9481 | 20188.9481 | 20188.9481 | 20188.9481 | 20188.9481 | 20188.9481 | 20188.9481 | 20188.9481 | 20188.9481 | 20188.9481 | 20188.9481 | 20188.9481 | 20188.9481 | 20188.9481
35% | 6655.3655 | 8843.5072 | 9439.545 | 9422.4891 | 9422.285 | 9490.4555 | 9565.2339 | 9718.5956 | 9828.7764 | 9888.6783 | 9954.2998 | 10014.2647 | 10122.3869 | 10256.5152 | 10247.4502 | 10247.4502 | 10247.4502 | 10247.4502 | 10247.4502 | 10247.4502 | 10247.4502 | 10247.4502 | 10247.4502 | 10247.4502 | 10247.4502 | 10247.4502 | 10247.4502 | 10247.4502 | 10247.4502 | 10247.4502 |  | 18622.1031 | 24123.7949 | 25564.4311 | 25478.7524 | 25485.9452 | 25634.2631 | 26024.729 | 26286.5314 | 26542.6059 | 26842.008 | 27119.7205 | 27389.1195 | 27420.3294 | 27734.6724 | 27497.2745 | 27497.2745 | 27497.2745 | 27497.2745 | 27497.2745 | 27497.2745 | 27497.2745 | 27497.2745 | 27497.2745 | 27497.2745 | 27497.2745 | 27497.2745 | 27497.2745 | 27497.2745 | 27497.2745 | 27497.2745
30% | 3095.428 | 4113.1385 | 4390.3573 | 4382.4246 | 4382.3296 | 4414.0359 | 4448.8155 | 4520.1445 | 4571.3898 | 4599.2504 | 4629.7711 | 4657.6609 | 4707.9489 | 4770.3323 | 4766.1162 | 4766.1162 | 4766.1162 | 4766.1162 | 4766.1162 | 4766.1162 | 4766.1162 | 4766.1162 | 4766.1162 | 4766.1162 | 4766.1162 | 4766.1162 | 4766.1162 | 4766.1162 | 4766.1162 | 4766.1162 |  | 17207.9743 | 22291.8776 | 23623.1145 | 23543.942 | 23550.5887 | 23687.6435 | 24048.4582 | 24290.3798 | 24527.0085 | 24803.6745 | 25060.2981 | 25309.2393 | 25338.0792 | 25628.5516 | 25409.1812 | 25409.1812 | 25409.1812 | 25409.1812 | 25409.1812 | 25409.1812 | 25409.1812 | 25409.1812 | 25409.1812 | 25409.1812 | 25409.1812 | 25409.1812 | 25409.1812 | 25409.1812 | 25409.1812 | 25409.1812
25% | 2113.496 | 2808.3682 | 2997.6476 | 2992.2313 | 2992.1665 | 3013.8149 | 3037.5617 | 3086.2637 | 3121.253 | 3140.2756 | 3161.1146 | 3180.1572 | 3214.4928 | 3257.0869 | 3254.2082 | 3254.2082 | 3254.2082 | 3254.2082 | 3254.2082 | 3254.2082 | 3254.2082 | 3254.2082 | 3254.2082 | 3254.2082 | 3254.2082 | 3254.2082 | 3254.2082 | 3254.2082 | 3254.2082 | 3254.2082 |  | 4963.476 | 6429.8794 | 6813.862 | 6791.0255 | 6792.9426 | 6832.4748 | 6936.5483 | 7006.3283 | 7074.5816 | 7154.3833 | 7228.4039 | 7300.2086 | 7308.5272 | 7392.3112 | 7329.0359 | 7329.0359 | 7329.0359 | 7329.0359 | 7329.0359 | 7329.0359 | 7329.0359 | 7329.0359 | 7329.0359 | 7329.0359 | 7329.0359 | 7329.0359 | 7329.0359 | 7329.0359 | 7329.0359 | 7329.0359
20% | 1280.3284 | 1701.2729 | 1815.9359 | 1812.6548 | 1812.6155 | 1825.7299 | 1840.1154 | 1869.6184 | 1890.8145 | 1902.3381 | 1914.9621 | 1926.4978 | 1947.2979 | 1973.1009 | 1971.357 | 1971.357 | 1971.357 | 1971.357 | 1971.357 | 1971.357 | 1971.357 | 1971.357 | 1971.357 | 1971.357 | 1971.357 | 1971.357 | 1971.357 | 1971.357 | 1971.357 | 1971.357 |  | 1331.912 | 1725.4105 | 1828.4494 | 1822.3214 | 1822.8358 | 1833.444 | 1861.3713 | 1880.0963 | 1898.4115 | 1919.8257 | 1939.6886 | 1958.9569 | 1961.1891 | 1983.6719 | 1966.6925 | 1966.6925 | 1966.6925 | 1966.6925 | 1966.6925 | 1966.6925 | 1966.6925 | 1966.6925 | 1966.6925 | 1966.6925 | 1966.6925 | 1966.6925 | 1966.6925 | 1966.6925 | 1966.6925 | 1966.6925
15% | 819.7224 | 1089.2296 | 1162.6419 | 1160.5412 | 1160.516 | 1168.9124 | 1178.1226 | 1197.0118 | 1210.5824 | 1217.9604 | 1226.0428 | 1233.4285 | 1246.7456 | 1263.2658 | 1262.1493 | 1262.1493 | 1262.1493 | 1262.1493 | 1262.1493 | 1262.1493 | 1262.1493 | 1262.1493 | 1262.1493 | 1262.1493 | 1262.1493 | 1262.1493 | 1262.1493 | 1262.1493 | 1262.1493 | 1262.1493 |  | 734.6312 | 951.6698 | 1008.502 | 1005.1221 | 1005.4058 | 1011.2569 | 1026.6605 | 1036.9885 | 1047.0905 | 1058.9017 | 1069.8573 | 1080.4849 | 1081.7162 | 1094.1168 | 1084.7516 | 1084.7516 | 1084.7516 | 1084.7516 | 1084.7516 | 1084.7516 | 1084.7516 | 1084.7516 | 1084.7516 | 1084.7516 | 1084.7516 | 1084.7516 | 1084.7516 | 1084.7516 | 1084.7516 | 1084.7516
10% | 548.6502 | 729.0346 | 778.1704 | 776.7643 | 776.7475 | 782.3673 | 788.5318 | 801.1745 | 810.2575 | 815.1957 | 820.6054 | 825.5487 | 834.462 | 845.5192 | 844.7719 | 844.7719 | 844.7719 | 844.7719 | 844.7719 | 844.7719 | 844.7719 | 844.7719 | 844.7719 | 844.7719 | 844.7719 | 844.7719 | 844.7719 | 844.7719 | 844.7719 | 844.7719 |  | 171.688 | 222.4113 | 235.6934 | 234.9034 | 234.9698 | 236.3372 | 239.9371 | 242.3508 | 244.7117 | 247.4721 | 250.0325 | 252.5162 | 252.804 | 255.7021 | 253.5134 | 253.5134 | 253.5134 | 253.5134 | 253.5134 | 253.5134 | 253.5134 | 253.5134 | 253.5134 | 253.5134 | 253.5134 | 253.5134 | 253.5134 | 253.5134 | 253.5134 | 253.5134
5% | 390.344 | 518.6808 | 553.639 | 552.6387 | 552.6267 | 556.625 | 561.0108 | 570.0056 | 576.4678 | 579.9811 | 583.8299 | 587.3469 | 593.6884 | 601.5551 | 601.0235 | 601.0235 | 601.0235 | 601.0235 | 601.0235 | 601.0235 | 601.0235 | 601.0235 | 601.0235 | 601.0235 | 601.0235 | 601.0235 | 601.0235 | 601.0235 | 601.0235 | 601.0235 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9.992e-14% | 34.2635 | 45.5286 | 48.5972 | 48.5094 | 48.5083 | 48.8593 | 49.2443 | 50.0338 | 50.6011 | 50.9095 | 51.2473 | 51.556 | 52.1126 | 52.8032 | 52.7565 | 52.7565 | 52.7565 | 52.7565 | 52.7565 | 52.7565 | 52.7565 | 52.7565 | 52.7565 | 52.7565 | 52.7565 | 52.7565 | 52.7565 | 52.7565 | 52.7565 | 52.7565 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E @ R (MWh) | 91763.8061 | 121933.7811 | 130151.918 | 129916.7517 | 129913.938 | 130853.8682 | 131884.9083 | 133999.4516 | 135518.6175 | 136344.5424 | 137249.3282 | 138076.12 | 139566.9035 | 141416.2562 | 141291.2697 | 141291.2697 | 141291.2697 | 141291.2697 | 141291.2697 | 141291.2697 | 141291.2697 | 141291.2697 | 141291.2697 | 141291.2697 | 141291.2697 | 141291.2697 | 141291.2697 | 141291.2697 | 141291.2697 | 141291.2697 | E @ R (MWh) | 89067.5772 | 115381.5956 | 122272.0083 | 121862.2159 | 121896.6185 | 122606.0074 | 124473.5651 | 125725.7387 | 126950.5164 | 128382.5252 | 129710.7955 | 130999.3026 | 131148.5764 | 132652.0463 | 131516.5966 | 131516.5966 | 131516.5966 | 131516.5966 | 131516.5966 | 131516.5966 | 131516.5966 | 131516.5966 | 131516.5966 | 131516.5966 | 131516.5966 | 131516.5966 | 131516.5966 | 131516.5966 | 131516.5966 | 131516.5966
Option 7 Summer POE50 W E @ R (MWh) N 2 | 64234.6643 | 85353.6468 | 91106.3426 | 90941.7262 | 90939.7566 | 91597.7077 | 92319.4358 | 93799.6161 | 94863.0323 | 95441.1797 | 96074.5298 | 96653.284 | 97696.8324 | 98991.3793 | 98903.8888 | 98903.8888 | 98903.8888 | 98903.8888 | 98903.8888 | 98903.8888 | 98903.8888 | 98903.8888 | 98903.8888 | 98903.8888 | 98903.8888 | 98903.8888 | 98903.8888 | 98903.8888 | 98903.8888 | 98903.8888 | Option 7 Summer POE10 W E @ R (MWh) N 2 | 26720.2732 | 34614.4787 | 36681.6025 | 36558.6648 | 36568.9855 | 36781.8022 | 37342.0695 | 37717.7216 | 38085.1549 | 38514.7576 | 38913.2387 | 39299.7908 | 39344.5729 | 39795.6139 | 39454.979 | 39454.979 | 39454.979 | 39454.979 | 39454.979 | 39454.979 | 39454.979 | 39454.979 | 39454.979 | 39454.979 | 39454.979 | 39454.979 | 39454.979 | 39454.979 | 39454.979 | 39454.979
Option 8 -
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | 59.6718 | 82.8348 | 88.8563 | 89.8828 | 90.6833 | 92.0616 | 95.1975 | 97.2967 | 99.9559 | 101.3362 | 102.5505 | 100.3131 | 102.9353 | 107.0576 | 103.9293 | 103.9293 | 103.9293 | 103.9293 | 103.9293 | 103.9293 | 103.9293 | 103.9293 | 103.9293 | 103.9293 | 103.9293 | 103.9293 | 103.9293 | 103.9293 | 103.9293 | 103.9293 |  | 63.8857 | 86.7566 | 93.0131 | 93.9812 | 94.5959 | 95.9444 | 99.1293 | 100.8681 | 104.1807 | 114.2499 | 105.9488 | 104.3251 | 106.5169 | 111.3103 | 108.0657 | 108.0657 | 108.0657 | 108.0657 | 108.0657 | 108.0657 | 108.0657 | 108.0657 | 108.0657 | 108.0657 | 108.0657 | 108.0657 | 108.0657 | 108.0657 | 108.0657 | 108.0657
98% | 70.8865 | 98.4027 | 105.556 | 106.7753 | 107.7263 | 109.3637 | 113.0889 | 115.5826 | 118.7416 | 120.3813 | 121.8238 | 119.1659 | 122.2809 | 127.178 | 123.4618 | 123.4618 | 123.4618 | 123.4618 | 123.4618 | 123.4618 | 123.4618 | 123.4618 | 123.4618 | 123.4618 | 123.4618 | 123.4618 | 123.4618 | 123.4618 | 123.4618 | 123.4618 |  | 75.8924 | 103.0616 | 110.494 | 111.644 | 112.3742 | 113.9761 | 117.7596 | 119.8253 | 123.7603 | 135.7219 | 125.8608 | 123.932 | 126.5357 | 132.2299 | 128.3755 | 128.3755 | 128.3755 | 128.3755 | 128.3755 | 128.3755 | 128.3755 | 128.3755 | 128.3755 | 128.3755 | 128.3755 | 128.3755 | 128.3755 | 128.3755 | 128.3755 | 128.3755
97% | 140.3338 | 194.8074 | 208.9687 | 211.3826 | 213.2652 | 216.5068 | 223.8816 | 228.8183 | 235.0721 | 238.3182 | 241.174 | 235.9121 | 242.0789 | 251.7738 | 244.4167 | 244.4167 | 244.4167 | 244.4167 | 244.4167 | 244.4167 | 244.4167 | 244.4167 | 244.4167 | 244.4167 | 244.4167 | 244.4167 | 244.4167 | 244.4167 | 244.4167 | 244.4167 |  | 150.2438 | 204.0305 | 218.7445 | 221.0211 | 222.4667 | 225.638 | 233.1281 | 237.2175 | 245.0078 | 268.6881 | 249.1661 | 245.3476 | 250.5021 | 261.7749 | 254.1445 | 254.1445 | 254.1445 | 254.1445 | 254.1445 | 254.1445 | 254.1445 | 254.1445 | 254.1445 | 254.1445 | 254.1445 | 254.1445 | 254.1445 | 254.1445 | 254.1445 | 254.1445
95% | 414.5243 | 575.4311 | 617.2612 | 624.3915 | 629.9527 | 639.5277 | 661.3119 | 675.8939 | 694.3669 | 703.9554 | 712.391 | 696.8482 | 715.0638 | 743.7009 | 721.9694 | 721.9694 | 721.9694 | 721.9694 | 721.9694 | 721.9694 | 721.9694 | 721.9694 | 721.9694 | 721.9694 | 721.9694 | 721.9694 | 721.9694 | 721.9694 | 721.9694 | 721.9694 |  | 443.7972 | 602.6746 | 646.1375 | 652.8624 | 657.1324 | 666.4999 | 688.6245 | 700.704 | 723.7153 | 793.6633 | 735.9983 | 724.719 | 739.9446 | 773.2427 | 750.7037 | 750.7037 | 750.7037 | 750.7037 | 750.7037 | 750.7037 | 750.7037 | 750.7037 | 750.7037 | 750.7037 | 750.7037 | 750.7037 | 750.7037 | 750.7037 | 750.7037 | 750.7037
90% | 2285.5212 | 3172.6969 | 3403.3313 | 3442.6449 | 3473.3067 | 3526.0998 | 3646.209 | 3726.6085 | 3828.4608 | 3881.3281 | 3927.8385 | 3842.1418 | 3942.5756 | 4100.4692 | 3980.6499 | 3980.6499 | 3980.6499 | 3980.6499 | 3980.6499 | 3980.6499 | 3980.6499 | 3980.6499 | 3980.6499 | 3980.6499 | 3980.6499 | 3980.6499 | 3980.6499 | 3980.6499 | 3980.6499 | 3980.6499 |  | 2446.9201 | 3322.9067 | 3562.5435 | 3599.622 | 3623.165 | 3674.8134 | 3796.7998 | 3863.4014 | 3990.2765 | 4375.9415 | 4058 | 3995.8103 | 4079.7583 | 4263.3504 | 4139.0795 | 4139.0795 | 4139.0795 | 4139.0795 | 4139.0795 | 4139.0795 | 4139.0795 | 4139.0795 | 4139.0795 | 4139.0795 | 4139.0795 | 4139.0795 | 4139.0795 | 4139.0795 | 4139.0795 | 4139.0795
85% | 5583.3646 | 7750.6712 | 8314.0946 | 8410.1348 | 8485.0395 | 8614.0092 | 8907.4274 | 9103.8375 | 9352.6555 | 9481.8066 | 9595.4282 | 9386.0773 | 9631.4298 | 10017.1525 | 9724.4425 | 9724.4425 | 9724.4425 | 9724.4425 | 9724.4425 | 9724.4425 | 9724.4425 | 9724.4425 | 9724.4425 | 9724.4425 | 9724.4425 | 9724.4425 | 9724.4425 | 9724.4425 | 9724.4425 | 9724.4425 |  | 5977.6505 | 8117.623 | 8703.0385 | 8793.6186 | 8851.1326 | 8977.3059 | 9275.3098 | 9438.0128 | 9747.9596 | 10690.1116 | 9913.4032 | 9761.4782 | 9966.5573 | 10415.0597 | 10111.4747 | 10111.4747 | 10111.4747 | 10111.4747 | 10111.4747 | 10111.4747 | 10111.4747 | 10111.4747 | 10111.4747 | 10111.4747 | 10111.4747 | 10111.4747 | 10111.4747 | 10111.4747 | 10111.4747 | 10111.4747
80% | 8678.2039 | 12046.8408 | 12922.5678 | 13071.8427 | 13188.2668 | 13388.724 | 13844.7828 | 14150.0624 | 14536.7992 | 14737.5384 | 14914.14 | 14588.7467 | 14970.0973 | 15569.6246 | 15114.6665 | 15114.6665 | 15114.6665 | 15114.6665 | 15114.6665 | 15114.6665 | 15114.6665 | 15114.6665 | 15114.6665 | 15114.6665 | 15114.6665 | 15114.6665 | 15114.6665 | 15114.6665 | 15114.6665 | 15114.6665 |  | 9291.041 | 12617.1926 | 13527.1019 | 13667.8902 | 13757.2841 | 13953.3947 | 14416.5812 | 14669.4699 | 15151.219 | 16615.6026 | 15408.3675 | 15172.231 | 15490.9847 | 16188.0904 | 15716.2292 | 15716.2292 | 15716.2292 | 15716.2292 | 15716.2292 | 15716.2292 | 15716.2292 | 15716.2292 | 15716.2292 | 15716.2292 | 15716.2292 | 15716.2292 | 15716.2292 | 15716.2292 | 15716.2292 | 15716.2292
75% | 9574.4808 | 13291.0275 | 14257.1987 | 14421.8907 | 14550.339 | 14771.4991 | 15274.6593 | 15611.4679 | 16038.1465 | 16259.6179 | 16454.4587 | 16095.4591 | 16516.1952 | 17177.6412 | 16675.6955 | 16675.6955 | 16675.6955 | 16675.6955 | 16675.6955 | 16675.6955 | 16675.6955 | 16675.6955 | 16675.6955 | 16675.6955 | 16675.6955 | 16675.6955 | 16675.6955 | 16675.6955 | 16675.6955 | 16675.6955 |  | 10250.6112 | 13920.2847 | 14924.1686 | 15079.4974 | 15178.1238 | 15394.4886 | 15905.5125 | 16184.5193 | 16716.023 | 18331.6468 | 16999.7296 | 16739.2052 | 17090.8794 | 17859.9816 | 17339.387 | 17339.387 | 17339.387 | 17339.387 | 17339.387 | 17339.387 | 17339.387 | 17339.387 | 17339.387 | 17339.387 | 17339.387 | 17339.387 | 17339.387 | 17339.387 | 17339.387 | 17339.387
70% | 10287.2444 | 14280.4661 | 15318.563 | 15495.5153 | 15633.5258 | 15871.15 | 16411.7675 | 16773.6495 | 17232.0919 | 17470.0505 | 17679.396 | 17293.671 | 17745.7284 | 18456.4151 | 17917.1025 | 17917.1025 | 17917.1025 | 17917.1025 | 17917.1025 | 17917.1025 | 17917.1025 | 17917.1025 | 17917.1025 | 17917.1025 | 17917.1025 | 17917.1025 | 17917.1025 | 17917.1025 | 17917.1025 | 17917.1025 |  | 11013.7087 | 14956.5677 | 16035.1849 | 16202.077 | 16308.0455 | 16540.5174 | 17089.584 | 17389.3613 | 17960.4323 | 19696.3297 | 18265.2591 | 17985.3402 | 18363.1944 | 19189.5518 | 18630.202 | 18630.202 | 18630.202 | 18630.202 | 18630.202 | 18630.202 | 18630.202 | 18630.202 | 18630.202 | 18630.202 | 18630.202 | 18630.202 | 18630.202 | 18630.202 | 18630.202 | 18630.202
65% | 10840.7831 | 15048.8731 | 16142.8282 | 16329.302 | 16474.7386 | 16725.149 | 17294.8562 | 17676.2104 | 18159.3208 | 18410.0835 | 18630.6936 | 18224.2134 | 18700.5952 | 19449.5227 | 18881.1907 | 18881.1907 | 18881.1907 | 18881.1907 | 18881.1907 | 18881.1907 | 18881.1907 | 18881.1907 | 18881.1907 | 18881.1907 | 18881.1907 | 18881.1907 | 18881.1907 | 18881.1907 | 18881.1907 | 18881.1907 |  | 11606.3372 | 15761.3546 | 16898.0103 | 17073.8826 | 17185.553 | 17430.5339 | 18009.1448 | 18325.0525 | 18926.8519 | 20756.155 | 19248.0809 | 18953.1 | 19351.286 | 20222.1082 | 19632.6608 | 19632.6608 | 19632.6608 | 19632.6608 | 19632.6608 | 19632.6608 | 19632.6608 | 19632.6608 | 19632.6608 | 19632.6608 | 19632.6608 | 19632.6608 | 19632.6608 | 19632.6608 | 19632.6608 | 19632.6608
60% | 11934.3669 | 16566.9557 | 17771.2656 | 17976.5503 | 18136.658 | 18412.329 | 19039.5064 | 19459.3305 | 19991.1755 | 20267.2344 | 20510.0989 | 20062.6142 | 20587.052 | 21411.5289 | 20785.8653 | 20785.8653 | 20785.8653 | 20785.8653 | 20785.8653 | 20785.8653 | 20785.8653 | 20785.8653 | 20785.8653 | 20785.8653 | 20785.8653 | 20785.8653 | 20785.8653 | 20785.8653 | 20785.8653 | 20785.8653 |  | 12777.1477 | 17351.3101 | 18602.628 | 18796.2417 | 18919.1771 | 19188.8708 | 19825.8502 | 20173.6257 | 20836.1327 | 22849.9701 | 21189.7663 | 20865.0287 | 21303.3824 | 22262.0503 | 21613.1413 | 21613.1413 | 21613.1413 | 21613.1413 | 21613.1413 | 21613.1413 | 21613.1413 | 21613.1413 | 21613.1413 | 21613.1413 | 21613.1413 | 21613.1413 | 21613.1413 | 21613.1413 | 21613.1413 | 21613.1413
55% | 13276.2336 | 18429.6976 | 19769.4166 | 19997.783 | 20175.8928 | 20482.5595 | 21180.255 | 21647.2828 | 22238.927 | 22546.0252 | 22816.1967 | 22318.3981 | 22901.8021 | 23818.981 | 23122.9695 | 23122.9695 | 23122.9695 | 23122.9695 | 23122.9695 | 23122.9695 | 23122.9695 | 23122.9695 | 23122.9695 | 23122.9695 | 23122.9695 | 23122.9695 | 23122.9695 | 23122.9695 | 23122.9695 | 23122.9695 |  | 14213.7742 | 19302.2426 | 20694.2551 | 20909.6382 | 21046.3962 | 21346.4135 | 22055.013 | 22441.8914 | 23178.8888 | 25419.1564 | 23572.284 | 23211.0338 | 23698.6747 | 24765.1326 | 24043.2621 | 24043.2621 | 24043.2621 | 24043.2621 | 24043.2621 | 24043.2621 | 24043.2621 | 24043.2621 | 24043.2621 | 24043.2621 | 24043.2621 | 24043.2621 | 24043.2621 | 24043.2621 | 24043.2621 | 24043.2621
50% | 13456.7484 | 18680.2832 | 20038.2182 | 20269.6896 | 20450.2212 | 20761.0575 | 21468.2395 | 21941.6174 | 22541.3061 | 22852.5798 | 23126.4248 | 22621.8577 | 23213.1942 | 24142.8438 | 23437.3688 | 23437.3688 | 23437.3688 | 23437.3688 | 23437.3688 | 23437.3688 | 23437.3688 | 23437.3688 | 23437.3688 | 23437.3688 | 23437.3688 | 23437.3688 | 23437.3688 | 23437.3688 | 23437.3688 | 23437.3688 |  | 14407.0366 | 19564.692 | 20975.6315 | 21193.9432 | 21332.5606 | 21636.6572 | 22354.8915 | 22747.0302 | 23494.0484 | 25764.7766 | 23892.7925 | 23526.6304 | 24020.9018 | 25101.8601 | 24370.1745 | 24370.1745 | 24370.1745 | 24370.1745 | 24370.1745 | 24370.1745 | 24370.1745 | 24370.1745 | 24370.1745 | 24370.1745 | 24370.1745 | 24370.1745 | 24370.1745 | 24370.1745 | 24370.1745 | 24370.1745
45% | 10386.1977 | 14417.8303 | 15465.9127 | 15644.5671 | 15783.9051 | 16023.8151 | 16569.6328 | 16934.9957 | 17397.8478 | 17638.0954 | 17849.4547 | 17460.0193 | 17916.4251 | 18633.9479 | 18089.4477 | 18089.4477 | 18089.4477 | 18089.4477 | 18089.4477 | 18089.4477 | 18089.4477 | 18089.4477 | 18089.4477 | 18089.4477 | 18089.4477 | 18089.4477 | 18089.4477 | 18089.4477 | 18089.4477 | 18089.4477 |  | 11119.6499 | 15100.4354 | 16189.4278 | 16357.9252 | 16464.913 | 16699.6211 | 17253.9692 | 17556.63 | 18133.1942 | 19885.7893 | 18440.9531 | 18158.3417 | 18539.8305 | 19374.1366 | 18809.4064 | 18809.4064 | 18809.4064 | 18809.4064 | 18809.4064 | 18809.4064 | 18809.4064 | 18809.4064 | 18809.4064 | 18809.4064 | 18809.4064 | 18809.4064 | 18809.4064 | 18809.4064 | 18809.4064 | 18809.4064
40% | 5102.6915 | 7083.4142 | 7598.3323 | 7686.1044 | 7754.5606 | 7872.4272 | 8140.5849 | 8320.0861 | 8547.4832 | 8665.5158 | 8769.3556 | 8578.0278 | 8802.2579 | 9154.7736 | 8887.2631 | 8887.2631 | 8887.2631 | 8887.2631 | 8887.2631 | 8887.2631 | 8887.2631 | 8887.2631 | 8887.2631 | 8887.2631 | 8887.2631 | 8887.2631 | 8887.2631 | 8887.2631 | 8887.2631 | 8887.2631 |  | 5463.0332 | 7418.775 | 7953.792 | 8036.574 | 8089.1366 | 8204.4476 | 8476.7963 | 8625.4922 | 8908.7555 | 9769.7975 | 9059.9561 | 8921.1104 | 9108.5341 | 9518.4249 | 9240.9755 | 9240.9755 | 9240.9755 | 9240.9755 | 9240.9755 | 9240.9755 | 9240.9755 | 9240.9755 | 9240.9755 | 9240.9755 | 9240.9755 | 9240.9755 | 9240.9755 | 9240.9755 | 9240.9755 | 9240.9755
35% | 1907.0998 | 2647.3829 | 2839.8304 | 2872.6347 | 2898.2197 | 2942.2717 | 3042.494 | 3109.5815 | 3194.5697 | 3238.6837 | 3277.4932 | 3205.9856 | 3289.7902 | 3421.5408 | 3321.5604 | 3321.5604 | 3321.5604 | 3321.5604 | 3321.5604 | 3321.5604 | 3321.5604 | 3321.5604 | 3321.5604 | 3321.5604 | 3321.5604 | 3321.5604 | 3321.5604 | 3321.5604 | 3321.5604 | 3321.5604 |  | 2041.7754 | 2772.7219 | 2972.6813 | 3003.6205 | 3023.2655 | 3066.3623 | 3168.1509 | 3223.7251 | 3329.5931 | 3651.4023 | 3386.1034 | 3334.2106 | 3404.2591 | 3557.4533 | 3453.7583 | 3453.7583 | 3453.7583 | 3453.7583 | 3453.7583 | 3453.7583 | 3453.7583 | 3453.7583 | 3453.7583 | 3453.7583 | 3453.7583 | 3453.7583 | 3453.7583 | 3453.7583 | 3453.7583 | 3453.7583
30% | 951.1511 | 1320.3614 | 1416.3431 | 1432.704 | 1445.4643 | 1467.4349 | 1517.42 | 1550.8793 | 1593.2665 | 1615.268 | 1634.624 | 1598.9601 | 1640.757 | 1706.4666 | 1656.6021 | 1656.6021 | 1656.6021 | 1656.6021 | 1656.6021 | 1656.6021 | 1656.6021 | 1656.6021 | 1656.6021 | 1656.6021 | 1656.6021 | 1656.6021 | 1656.6021 | 1656.6021 | 1656.6021 | 1656.6021 |  | 1018.3194 | 1382.8733 | 1482.6014 | 1498.0321 | 1507.8299 | 1529.3241 | 1580.0904 | 1607.8076 | 1660.6084 | 1821.1082 | 1688.7924 | 1662.9113 | 1697.8475 | 1774.2519 | 1722.5348 | 1722.5348 | 1722.5348 | 1722.5348 | 1722.5348 | 1722.5348 | 1722.5348 | 1722.5348 | 1722.5348 | 1722.5348 | 1722.5348 | 1722.5348 | 1722.5348 | 1722.5348 | 1722.5348 | 1722.5348
25% | 560.7353 | 778.3972 | 834.9816 | 844.6269 | 852.1495 | 865.1019 | 894.5698 | 914.2952 | 939.2839 | 952.2545 | 963.6655 | 942.6404 | 967.2811 | 1006.0191 | 976.6223 | 976.6223 | 976.6223 | 976.6223 | 976.6223 | 976.6223 | 976.6223 | 976.6223 | 976.6223 | 976.6223 | 976.6223 | 976.6223 | 976.6223 | 976.6223 | 976.6223 | 976.6223 |  | 600.3333 | 815.25 | 874.0431 | 883.14 | 888.9161 | 901.5876 | 931.5161 | 947.8563 | 978.9841 | 1073.6041 | 995.5996 | 980.3418 | 1000.9378 | 1045.9808 | 1015.4918 | 1015.4918 | 1015.4918 | 1015.4918 | 1015.4918 | 1015.4918 | 1015.4918 | 1015.4918 | 1015.4918 | 1015.4918 | 1015.4918 | 1015.4918 | 1015.4918 | 1015.4918 | 1015.4918 | 1015.4918
20% | 283.3663 | 393.3611 | 421.9559 | 426.8302 | 430.6317 | 437.1772 | 452.0687 | 462.0369 | 474.6648 | 481.2195 | 486.986 | 476.3611 | 488.8132 | 508.3893 | 493.5337 | 493.5337 | 493.5337 | 493.5337 | 493.5337 | 493.5337 | 493.5337 | 493.5337 | 493.5337 | 493.5337 | 493.5337 | 493.5337 | 493.5337 | 493.5337 | 493.5337 | 493.5337 |  | 303.377 | 411.9846 | 441.6956 | 446.2927 | 449.2116 | 455.6151 | 470.7394 | 478.9969 | 494.7273 | 542.5433 | 503.1238 | 495.4134 | 505.8215 | 528.5839 | 513.1763 | 513.1763 | 513.1763 | 513.1763 | 513.1763 | 513.1763 | 513.1763 | 513.1763 | 513.1763 | 513.1763 | 513.1763 | 513.1763 | 513.1763 | 513.1763 | 513.1763 | 513.1763
15% | 115.4455 | 160.2582 | 171.908 | 173.8938 | 175.4425 | 178.1092 | 184.1761 | 188.2372 | 193.382 | 196.0524 | 198.4017 | 194.073 | 199.1461 | 207.1216 | 201.0693 | 201.0693 | 201.0693 | 201.0693 | 201.0693 | 201.0693 | 201.0693 | 201.0693 | 201.0693 | 201.0693 | 201.0693 | 201.0693 | 201.0693 | 201.0693 | 201.0693 | 201.0693 |  | 123.598 | 167.8456 | 179.95 | 181.8229 | 183.0121 | 185.621 | 191.7827 | 195.1469 | 201.5556 | 221.0361 | 204.9764 | 201.8351 | 206.0754 | 215.349 | 209.0718 | 209.0718 | 209.0718 | 209.0718 | 209.0718 | 209.0718 | 209.0718 | 209.0718 | 209.0718 | 209.0718 | 209.0718 | 209.0718 | 209.0718 | 209.0718 | 209.0718 | 209.0718
10% | 46.4781 | 64.5196 | 69.2097 | 70.0092 | 70.6327 | 71.7063 | 74.1488 | 75.7838 | 77.8551 | 78.9302 | 79.876 | 78.1333 | 80.1757 | 83.3866 | 80.95 | 80.95 | 80.95 | 80.95 | 80.95 | 80.95 | 80.95 | 80.95 | 80.95 | 80.95 | 80.95 | 80.95 | 80.95 | 80.95 | 80.95 | 80.95 |  | 49.7602 | 67.5742 | 72.4474 | 73.2014 | 73.6802 | 74.7305 | 77.2112 | 78.5656 | 81.1457 | 88.9886 | 82.523 | 81.2583 | 82.9654 | 86.6989 | 84.1718 | 84.1718 | 84.1718 | 84.1718 | 84.1718 | 84.1718 | 84.1718 | 84.1718 | 84.1718 | 84.1718 | 84.1718 | 84.1718 | 84.1718 | 84.1718 | 84.1718 | 84.1718
5% | 39.5813 | 54.9457 | 58.9399 | 59.6207 | 60.1517 | 61.066 | 63.1461 | 64.5385 | 66.3024 | 67.218 | 68.0234 | 66.5393 | 68.2787 | 71.0131 | 68.938 | 68.938 | 68.938 | 68.938 | 68.938 | 68.938 | 68.938 | 68.938 | 68.938 | 68.938 | 68.938 | 68.938 | 68.938 | 68.938 | 68.938 | 68.938 |  | 42.3765 | 57.5471 | 61.6972 | 62.3393 | 62.747 | 63.6415 | 65.7541 | 66.9075 | 69.1048 | 75.7838 | 70.2776 | 69.2006 | 70.6544 | 73.8339 | 71.6818 | 71.6818 | 71.6818 | 71.6818 | 71.6818 | 71.6818 | 71.6818 | 71.6818 | 71.6818 | 71.6818 | 71.6818 | 71.6818 | 71.6818 | 71.6818 | 71.6818 | 71.6818
9.992e-14% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E @ R (MWh) | 105995.1099 | 147139.4588 | 157835.5397 | 159658.7762 | 161080.774 | 163529.1464 | 169099.4242 | 172828.0925 | 177551.675 | 180003.4929 | 182160.4948 | 178186.1586 | 182843.9537 | 190166.5478 | 184609.7151 | 184609.7151 | 184609.7151 | 184609.7151 | 184609.7151 | 184609.7151 | 184609.7151 | 184609.7151 | 184609.7151 | 184609.7151 | 184609.7151 | 184609.7151 | 184609.7151 | 184609.7151 | 184609.7151 | 184609.7151 | E @ R (MWh) | 113480.2695 | 154105.704 | 165219.287 | 166938.8679 | 168030.7193 | 170426.0046 | 176083.3386 | 179172.1077 | 185056.165 | 202942.0666 | 188196.9625 | 185312.8045 | 189206.044 | 197720.4561 | 191957.169 | 191957.169 | 191957.169 | 191957.169 | 191957.169 | 191957.169 | 191957.169 | 191957.169 | 191957.169 | 191957.169 | 191957.169 | 191957.169 | 191957.169 | 191957.169 | 191957.169 | 191957.169
Option 8 Winter POE50 W E @ R (MWh) N 2 | 74196.5769 | 102997.6211 | 110484.8778 | 111761.1434 | 112756.5418 | 114470.4025 | 118369.597 | 120979.6647 | 124286.1725 | 126002.4451 | 127512.3464 | 124730.311 | 127990.7676 | 133116.5835 | 129226.8005 | 129226.8005 | 129226.8005 | 129226.8005 | 129226.8005 | 129226.8005 | 129226.8005 | 129226.8005 | 129226.8005 | 129226.8005 | 129226.8005 | 129226.8005 | 129226.8005 | 129226.8005 | 129226.8005 | 129226.8005 | Option 8 Winter POE10 W E @ R (MWh) N 2 | 34044.0809 | 46231.7112 | 49565.7861 | 50081.6604 | 50409.2158 | 51127.8014 | 52825.0016 | 53751.6323 | 55516.8495 | 60882.62 | 56459.0887 | 55593.8414 | 56761.8132 | 59316.1368 | 57587.1507 | 57587.1507 | 57587.1507 | 57587.1507 | 57587.1507 | 57587.1507 | 57587.1507 | 57587.1507 | 57587.1507 | 57587.1507 | 57587.1507 | 57587.1507 | 57587.1507 | 57587.1507 | 57587.1507 | 57587.1507
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 76.9936 | 99.7405 | 105.6969 | 105.3426 | 105.3724 | 105.9856 | 107.6 | 108.6824 | 109.7411 | 110.979 | 112.1272 | 113.2411 | 113.3701 | 114.6698 | 113.6883 | 113.6883 | 113.6883 | 113.6883 | 113.6883 | 113.6883 | 113.6883 | 113.6883 | 113.6883 | 113.6883 | 113.6883 | 113.6883 | 113.6883 | 113.6883 | 113.6883 | 113.6883
98% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 38.1099 | 49.369 | 52.3173 | 52.1419 | 52.1567 | 52.4602 | 53.2593 | 53.7951 | 54.3191 | 54.9318 | 55.5002 | 56.0515 | 56.1154 | 56.7587 | 56.2728 | 56.2728 | 56.2728 | 56.2728 | 56.2728 | 56.2728 | 56.2728 | 56.2728 | 56.2728 | 56.2728 | 56.2728 | 56.2728 | 56.2728 | 56.2728 | 56.2728 | 56.2728
97% | 16.9149 | 22.4762 | 23.991 | 23.9477 | 23.9472 | 24.1204 | 24.3105 | 24.7002 | 24.9803 | 25.1325 | 25.2993 | 25.4517 | 25.7265 | 26.0674 | 26.0444 | 26.0444 | 26.0444 | 26.0444 | 26.0444 | 26.0444 | 26.0444 | 26.0444 | 26.0444 | 26.0444 | 26.0444 | 26.0444 | 26.0444 | 26.0444 | 26.0444 | 26.0444 |  | 75.446 | 97.7357 | 103.5723 | 103.2252 | 103.2543 | 103.8552 | 105.4372 | 106.4978 | 107.5353 | 108.7483 | 109.8734 | 110.9649 | 111.0913 | 112.3649 | 111.4031 | 111.4031 | 111.4031 | 111.4031 | 111.4031 | 111.4031 | 111.4031 | 111.4031 | 111.4031 | 111.4031 | 111.4031 | 111.4031 | 111.4031 | 111.4031 | 111.4031 | 111.4031
95% | 83.2734 | 110.6519 | 118.1097 | 117.8962 | 117.8937 | 118.7467 | 119.6823 | 121.6012 | 122.9798 | 123.7293 | 124.5504 | 125.3007 | 126.6535 | 128.3318 | 128.2183 | 128.2183 | 128.2183 | 128.2183 | 128.2183 | 128.2183 | 128.2183 | 128.2183 | 128.2183 | 128.2183 | 128.2183 | 128.2183 | 128.2183 | 128.2183 | 128.2183 | 128.2183 |  | 111.4279 | 144.3481 | 152.9683 | 152.4556 | 152.4987 | 153.3862 | 155.7226 | 157.2891 | 158.8214 | 160.6129 | 162.2746 | 163.8866 | 164.0733 | 165.9543 | 164.5337 | 164.5337 | 164.5337 | 164.5337 | 164.5337 | 164.5337 | 164.5337 | 164.5337 | 164.5337 | 164.5337 | 164.5337 | 164.5337 | 164.5337 | 164.5337 | 164.5337 | 164.5337
90% | 144.4273 | 191.9119 | 204.8464 | 204.4763 | 204.4719 | 205.9512 | 207.574 | 210.9021 | 213.2931 | 214.593 | 216.0171 | 217.3184 | 219.6647 | 222.5754 | 222.3787 | 222.3787 | 222.3787 | 222.3787 | 222.3787 | 222.3787 | 222.3787 | 222.3787 | 222.3787 | 222.3787 | 222.3787 | 222.3787 | 222.3787 | 222.3787 | 222.3787 | 222.3787 |  | 483.1446 | 625.8842 | 663.261 | 661.0381 | 661.2248 | 665.0728 | 675.2033 | 681.9957 | 688.6395 | 696.4074 | 703.6125 | 710.602 | 711.4117 | 719.5673 | 713.4081 | 713.4081 | 713.4081 | 713.4081 | 713.4081 | 713.4081 | 713.4081 | 713.4081 | 713.4081 | 713.4081 | 713.4081 | 713.4081 | 713.4081 | 713.4081 | 713.4081 | 713.4081
85% | 409.8612 | 544.6148 | 581.321 | 580.2706 | 580.258 | 584.4562 | 589.0613 | 598.5059 | 605.2912 | 608.9802 | 613.0214 | 616.7142 | 623.3728 | 631.6329 | 631.0746 | 631.0746 | 631.0746 | 631.0746 | 631.0746 | 631.0746 | 631.0746 | 631.0746 | 631.0746 | 631.0746 | 631.0746 | 631.0746 | 631.0746 | 631.0746 | 631.0746 | 631.0746 |  | 457.0286 | 592.0526 | 627.4091 | 625.3063 | 625.4829 | 629.1229 | 638.7059 | 645.1311 | 651.4157 | 658.7637 | 665.5794 | 672.1911 | 672.9571 | 680.6717 | 674.8455 | 674.8455 | 674.8455 | 674.8455 | 674.8455 | 674.8455 | 674.8455 | 674.8455 | 674.8455 | 674.8455 | 674.8455 | 674.8455 | 674.8455 | 674.8455 | 674.8455 | 674.8455
80% | 572.5046 | 760.7318 | 812.0039 | 810.5367 | 810.5191 | 816.3833 | 822.8158 | 836.0082 | 845.4861 | 850.639 | 856.2839 | 861.4421 | 870.743 | 882.2809 | 881.5011 | 881.5011 | 881.5011 | 881.5011 | 881.5011 | 881.5011 | 881.5011 | 881.5011 | 881.5011 | 881.5011 | 881.5011 | 881.5011 | 881.5011 | 881.5011 | 881.5011 | 881.5011 |  | 319.1946 | 413.4971 | 438.1905 | 436.7219 | 436.8452 | 439.3874 | 446.0803 | 450.5677 | 454.957 | 460.089 | 464.8491 | 469.4668 | 470.0018 | 475.3898 | 471.3206 | 471.3206 | 471.3206 | 471.3206 | 471.3206 | 471.3206 | 471.3206 | 471.3206 | 471.3206 | 471.3206 | 471.3206 | 471.3206 | 471.3206 | 471.3206 | 471.3206 | 471.3206
75% | 1492.4153 | 1983.0895 | 2116.7465 | 2112.9218 | 2112.876 | 2128.1627 | 2144.9312 | 2179.3214 | 2204.0286 | 2217.4612 | 2232.1763 | 2245.623 | 2269.8686 | 2299.9458 | 2297.9131 | 2297.9131 | 2297.9131 | 2297.9131 | 2297.9131 | 2297.9131 | 2297.9131 | 2297.9131 | 2297.9131 | 2297.9131 | 2297.9131 | 2297.9131 | 2297.9131 | 2297.9131 | 2297.9131 | 2297.9131 |  | 569.714 | 738.0296 | 782.1036 | 779.4824 | 779.7025 | 784.24 | 796.1857 | 804.1951 | 812.0293 | 821.1891 | 829.6853 | 837.9271 | 838.8819 | 848.4987 | 841.2359 | 841.2359 | 841.2359 | 841.2359 | 841.2359 | 841.2359 | 841.2359 | 841.2359 | 841.2359 | 841.2359 | 841.2359 | 841.2359 | 841.2359 | 841.2359 | 841.2359 | 841.2359
70% | 2578.4391 | 3426.1747 | 3657.0932 | 3650.4854 | 3650.4063 | 3676.8171 | 3705.7879 | 3765.2037 | 3807.8902 | 3831.0976 | 3856.5209 | 3879.7526 | 3921.6416 | 3973.6059 | 3970.094 | 3970.094 | 3970.094 | 3970.094 | 3970.094 | 3970.094 | 3970.094 | 3970.094 | 3970.094 | 3970.094 | 3970.094 | 3970.094 | 3970.094 | 3970.094 | 3970.094 | 3970.094 |  | 1037.8661 | 1344.492 | 1424.783 | 1420.0079 | 1420.4087 | 1428.6749 | 1450.4368 | 1465.0278 | 1479.2996 | 1495.9862 | 1511.464 | 1526.4784 | 1528.2178 | 1545.7371 | 1532.5062 | 1532.5062 | 1532.5062 | 1532.5062 | 1532.5062 | 1532.5062 | 1532.5062 | 1532.5062 | 1532.5062 | 1532.5062 | 1532.5062 | 1532.5062 | 1532.5062 | 1532.5062 | 1532.5062 | 1532.5062
65% | 6475.8072 | 8604.914 | 9184.8711 | 9168.2753 | 9168.0768 | 9234.408 | 9307.1689 | 9456.393 | 9563.6012 | 9621.887 | 9685.7381 | 9744.0851 | 9849.2903 | 9979.7998 | 9970.9794 | 9970.9794 | 9970.9794 | 9970.9794 | 9970.9794 | 9970.9794 | 9970.9794 | 9970.9794 | 9970.9794 | 9970.9794 | 9970.9794 | 9970.9794 | 9970.9794 | 9970.9794 | 9970.9794 | 9970.9794 |  | 1305.7961 | 1691.5789 | 1792.5974 | 1786.5896 | 1787.0939 | 1797.4941 | 1824.8739 | 1843.2317 | 1861.1878 | 1882.1821 | 1901.6555 | 1920.546 | 1922.7344 | 1944.7764 | 1928.1299 | 1928.1299 | 1928.1299 | 1928.1299 | 1928.1299 | 1928.1299 | 1928.1299 | 1928.1299 | 1928.1299 | 1928.1299 | 1928.1299 | 1928.1299 | 1928.1299 | 1928.1299 | 1928.1299 | 1928.1299
60% | 9465.8424 | 12578.0087 | 13425.7459 | 13401.4874 | 13401.1972 | 13498.1551 | 13604.5115 | 13822.636 | 13979.3447 | 14064.5425 | 14157.8751 | 14243.1624 | 14396.9433 | 14587.7122 | 14574.8193 | 14574.8193 | 14574.8193 | 14574.8193 | 14574.8193 | 14574.8193 | 14574.8193 | 14574.8193 | 14574.8193 | 14574.8193 | 14574.8193 | 14574.8193 | 14574.8193 | 14574.8193 | 14574.8193 | 14574.8193 |  | 2043.3291 | 2647.0078 | 2805.083 | 2795.6818 | 2796.4711 | 2812.7454 | 2855.5897 | 2884.3162 | 2912.4142 | 2945.2664 | 2975.7387 | 3005.2988 | 3008.7233 | 3043.2149 | 3017.1662 | 3017.1662 | 3017.1662 | 3017.1662 | 3017.1662 | 3017.1662 | 3017.1662 | 3017.1662 | 3017.1662 | 3017.1662 | 3017.1662 | 3017.1662 | 3017.1662 | 3017.1662 | 3017.1662 | 3017.1662
55% | 10703.6666 | 14222.8031 | 15181.3967 | 15153.966 | 15153.6378 | 15263.2747 | 15383.539 | 15630.1871 | 15807.3882 | 15903.7271 | 16009.2646 | 16105.7046 | 16279.5951 | 16495.3104 | 16480.7315 | 16480.7315 | 16480.7315 | 16480.7315 | 16480.7315 | 16480.7315 | 16480.7315 | 16480.7315 | 16480.7315 | 16480.7315 | 16480.7315 | 16480.7315 | 16480.7315 | 16480.7315 | 16480.7315 | 16480.7315 |  | 3926.5772 | 5086.6405 | 5390.4069 | 5372.341 | 5373.8577 | 5405.1313 | 5487.4633 | 5542.6658 | 5596.6606 | 5659.7913 | 5718.3486 | 5775.1529 | 5781.7337 | 5848.0147 | 5797.958 | 5797.958 | 5797.958 | 5797.958 | 5797.958 | 5797.958 | 5797.958 | 5797.958 | 5797.958 | 5797.958 | 5797.958 | 5797.958 | 5797.958 | 5797.958 | 5797.958 | 5797.958
50% | 13744.0128 | 18262.75 | 19493.6294 | 19458.4071 | 19457.9857 | 19598.7646 | 19753.1897 | 20069.8975 | 20297.432 | 20421.1357 | 20556.6509 | 20680.4844 | 20903.7679 | 21180.7565 | 21162.0366 | 21162.0366 | 21162.0366 | 21162.0366 | 21162.0366 | 21162.0366 | 21162.0366 | 21162.0366 | 21162.0366 | 21162.0366 | 21162.0366 | 21162.0366 | 21162.0366 | 21162.0366 | 21162.0366 | 21162.0366 |  | 8714.0125 | 11288.47 | 11962.6002 | 11922.5077 | 11925.8735 | 11995.2773 | 12177.9916 | 12300.4992 | 12420.3265 | 12560.4285 | 12690.3811 | 12816.4434 | 12831.0478 | 12978.1412 | 12867.0534 | 12867.0534 | 12867.0534 | 12867.0534 | 12867.0534 | 12867.0534 | 12867.0534 | 12867.0534 | 12867.0534 | 12867.0534 | 12867.0534 | 12867.0534 | 12867.0534 | 12867.0534 | 12867.0534 | 12867.0534
45% | 18302.3635 | 24319.7888 | 25958.9027 | 25911.9985 | 25911.4373 | 26098.9072 | 26304.5489 | 26726.2963 | 27029.2951 | 27194.0265 | 27374.4867 | 27539.391 | 27836.7289 | 28205.5838 | 28180.6551 | 28180.6551 | 28180.6551 | 28180.6551 | 28180.6551 | 28180.6551 | 28180.6551 | 28180.6551 | 28180.6551 | 28180.6551 | 28180.6551 | 28180.6551 | 28180.6551 | 28180.6551 | 28180.6551 | 28180.6551 |  | 13204.5002 | 17105.6219 | 18127.1435 | 18066.3908 | 18071.491 | 18176.6598 | 18453.5301 | 18639.1681 | 18820.7445 | 19033.0436 | 19229.9631 | 19420.9876 | 19443.1179 | 19666.0112 | 19497.6778 | 19497.6778 | 19497.6778 | 19497.6778 | 19497.6778 | 19497.6778 | 19497.6778 | 19497.6778 | 19497.6778 | 19497.6778 | 19497.6778 | 19497.6778 | 19497.6778 | 19497.6778 | 19497.6778 | 19497.6778
40% | 12836.6798 | 17057.1053 | 18206.7263 | 18173.8293 | 18173.4357 | 18304.9209 | 18449.1513 | 18744.9511 | 18957.4646 | 19073.0018 | 19199.5707 | 19315.2292 | 19523.7723 | 19782.475 | 19764.9909 | 19764.9909 | 19764.9909 | 19764.9909 | 19764.9909 | 19764.9909 | 19764.9909 | 19764.9909 | 19764.9909 | 19764.9909 | 19764.9909 | 19764.9909 | 19764.9909 | 19764.9909 | 19764.9909 | 19764.9909 |  | 13672.6523 | 17712.0843 | 18769.8229 | 18706.9162 | 18712.1973 | 18821.0947 | 19107.7811 | 19300.0008 | 19488.0148 | 19707.8407 | 19911.7418 | 20109.5389 | 20132.4538 | 20363.2496 | 20188.9481 | 20188.9481 | 20188.9481 | 20188.9481 | 20188.9481 | 20188.9481 | 20188.9481 | 20188.9481 | 20188.9481 | 20188.9481 | 20188.9481 | 20188.9481 | 20188.9481 | 20188.9481 | 20188.9481 | 20188.9481
35% | 6655.3655 | 8843.5072 | 9439.545 | 9422.4891 | 9422.285 | 9490.4555 | 9565.2339 | 9718.5956 | 9828.7764 | 9888.6783 | 9954.2998 | 10014.2647 | 10122.3869 | 10256.5152 | 10247.4502 | 10247.4502 | 10247.4502 | 10247.4502 | 10247.4502 | 10247.4502 | 10247.4502 | 10247.4502 | 10247.4502 | 10247.4502 | 10247.4502 | 10247.4502 | 10247.4502 | 10247.4502 | 10247.4502 | 10247.4502 |  | 18622.1031 | 24123.7949 | 25564.4311 | 25478.7524 | 25485.9452 | 25634.2631 | 26024.729 | 26286.5314 | 26542.6059 | 26842.008 | 27119.7205 | 27389.1195 | 27420.3294 | 27734.6724 | 27497.2745 | 27497.2745 | 27497.2745 | 27497.2745 | 27497.2745 | 27497.2745 | 27497.2745 | 27497.2745 | 27497.2745 | 27497.2745 | 27497.2745 | 27497.2745 | 27497.2745 | 27497.2745 | 27497.2745 | 27497.2745
30% | 3095.428 | 4113.1385 | 4390.3573 | 4382.4246 | 4382.3296 | 4414.0359 | 4448.8155 | 4520.1445 | 4571.3898 | 4599.2504 | 4629.7711 | 4657.6609 | 4707.9489 | 4770.3323 | 4766.1162 | 4766.1162 | 4766.1162 | 4766.1162 | 4766.1162 | 4766.1162 | 4766.1162 | 4766.1162 | 4766.1162 | 4766.1162 | 4766.1162 | 4766.1162 | 4766.1162 | 4766.1162 | 4766.1162 | 4766.1162 |  | 17207.9743 | 22291.8776 | 23623.1145 | 23543.942 | 23550.5887 | 23687.6435 | 24048.4582 | 24290.3798 | 24527.0085 | 24803.6745 | 25060.2981 | 25309.2393 | 25338.0792 | 25628.5516 | 25409.1812 | 25409.1812 | 25409.1812 | 25409.1812 | 25409.1812 | 25409.1812 | 25409.1812 | 25409.1812 | 25409.1812 | 25409.1812 | 25409.1812 | 25409.1812 | 25409.1812 | 25409.1812 | 25409.1812 | 25409.1812
25% | 2113.496 | 2808.3682 | 2997.6476 | 2992.2313 | 2992.1665 | 3013.8149 | 3037.5617 | 3086.2637 | 3121.253 | 3140.2756 | 3161.1146 | 3180.1572 | 3214.4928 | 3257.0869 | 3254.2082 | 3254.2082 | 3254.2082 | 3254.2082 | 3254.2082 | 3254.2082 | 3254.2082 | 3254.2082 | 3254.2082 | 3254.2082 | 3254.2082 | 3254.2082 | 3254.2082 | 3254.2082 | 3254.2082 | 3254.2082 |  | 4963.476 | 6429.8794 | 6813.862 | 6791.0255 | 6792.9426 | 6832.4748 | 6936.5483 | 7006.3283 | 7074.5816 | 7154.3833 | 7228.4039 | 7300.2086 | 7308.5272 | 7392.3112 | 7329.0359 | 7329.0359 | 7329.0359 | 7329.0359 | 7329.0359 | 7329.0359 | 7329.0359 | 7329.0359 | 7329.0359 | 7329.0359 | 7329.0359 | 7329.0359 | 7329.0359 | 7329.0359 | 7329.0359 | 7329.0359
20% | 1280.3284 | 1701.2729 | 1815.9359 | 1812.6548 | 1812.6155 | 1825.7299 | 1840.1154 | 1869.6184 | 1890.8145 | 1902.3381 | 1914.9621 | 1926.4978 | 1947.2979 | 1973.1009 | 1971.357 | 1971.357 | 1971.357 | 1971.357 | 1971.357 | 1971.357 | 1971.357 | 1971.357 | 1971.357 | 1971.357 | 1971.357 | 1971.357 | 1971.357 | 1971.357 | 1971.357 | 1971.357 |  | 1331.912 | 1725.4105 | 1828.4494 | 1822.3214 | 1822.8358 | 1833.444 | 1861.3713 | 1880.0963 | 1898.4115 | 1919.8257 | 1939.6886 | 1958.9569 | 1961.1891 | 1983.6719 | 1966.6925 | 1966.6925 | 1966.6925 | 1966.6925 | 1966.6925 | 1966.6925 | 1966.6925 | 1966.6925 | 1966.6925 | 1966.6925 | 1966.6925 | 1966.6925 | 1966.6925 | 1966.6925 | 1966.6925 | 1966.6925
15% | 819.7224 | 1089.2296 | 1162.6419 | 1160.5412 | 1160.516 | 1168.9124 | 1178.1226 | 1197.0118 | 1210.5824 | 1217.9604 | 1226.0428 | 1233.4285 | 1246.7456 | 1263.2658 | 1262.1493 | 1262.1493 | 1262.1493 | 1262.1493 | 1262.1493 | 1262.1493 | 1262.1493 | 1262.1493 | 1262.1493 | 1262.1493 | 1262.1493 | 1262.1493 | 1262.1493 | 1262.1493 | 1262.1493 | 1262.1493 |  | 734.6312 | 951.6698 | 1008.502 | 1005.1221 | 1005.4058 | 1011.2569 | 1026.6605 | 1036.9885 | 1047.0905 | 1058.9017 | 1069.8573 | 1080.4849 | 1081.7162 | 1094.1168 | 1084.7516 | 1084.7516 | 1084.7516 | 1084.7516 | 1084.7516 | 1084.7516 | 1084.7516 | 1084.7516 | 1084.7516 | 1084.7516 | 1084.7516 | 1084.7516 | 1084.7516 | 1084.7516 | 1084.7516 | 1084.7516
10% | 548.6502 | 729.0346 | 778.1704 | 776.7643 | 776.7475 | 782.3673 | 788.5318 | 801.1745 | 810.2575 | 815.1957 | 820.6054 | 825.5487 | 834.462 | 845.5192 | 844.7719 | 844.7719 | 844.7719 | 844.7719 | 844.7719 | 844.7719 | 844.7719 | 844.7719 | 844.7719 | 844.7719 | 844.7719 | 844.7719 | 844.7719 | 844.7719 | 844.7719 | 844.7719 |  | 171.688 | 222.4113 | 235.6934 | 234.9034 | 234.9698 | 236.3372 | 239.9371 | 242.3508 | 244.7117 | 247.4721 | 250.0325 | 252.5162 | 252.804 | 255.7021 | 253.5134 | 253.5134 | 253.5134 | 253.5134 | 253.5134 | 253.5134 | 253.5134 | 253.5134 | 253.5134 | 253.5134 | 253.5134 | 253.5134 | 253.5134 | 253.5134 | 253.5134 | 253.5134
5% | 390.344 | 518.6808 | 553.639 | 552.6387 | 552.6267 | 556.625 | 561.0108 | 570.0056 | 576.4678 | 579.9811 | 583.8299 | 587.3469 | 593.6884 | 601.5551 | 601.0235 | 601.0235 | 601.0235 | 601.0235 | 601.0235 | 601.0235 | 601.0235 | 601.0235 | 601.0235 | 601.0235 | 601.0235 | 601.0235 | 601.0235 | 601.0235 | 601.0235 | 601.0235 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9.992e-14% | 34.2635 | 45.5286 | 48.5972 | 48.5094 | 48.5083 | 48.8593 | 49.2443 | 50.0338 | 50.6011 | 50.9095 | 51.2473 | 51.556 | 52.1126 | 52.8032 | 52.7565 | 52.7565 | 52.7565 | 52.7565 | 52.7565 | 52.7565 | 52.7565 | 52.7565 | 52.7565 | 52.7565 | 52.7565 | 52.7565 | 52.7565 | 52.7565 | 52.7565 | 52.7565 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E @ R (MWh) | 91763.8061 | 121933.7811 | 130151.918 | 129916.7517 | 129913.938 | 130853.8682 | 131884.9083 | 133999.4516 | 135518.6175 | 136344.5424 | 137249.3282 | 138076.12 | 139566.9035 | 141416.2562 | 141291.2697 | 141291.2697 | 141291.2697 | 141291.2697 | 141291.2697 | 141291.2697 | 141291.2697 | 141291.2697 | 141291.2697 | 141291.2697 | 141291.2697 | 141291.2697 | 141291.2697 | 141291.2697 | 141291.2697 | 141291.2697 | E @ R (MWh) | 89067.5772 | 115381.5956 | 122272.0083 | 121862.2159 | 121896.6185 | 122606.0074 | 124473.5651 | 125725.7387 | 126950.5164 | 128382.5252 | 129710.7955 | 130999.3026 | 131148.5764 | 132652.0463 | 131516.5966 | 131516.5966 | 131516.5966 | 131516.5966 | 131516.5966 | 131516.5966 | 131516.5966 | 131516.5966 | 131516.5966 | 131516.5966 | 131516.5966 | 131516.5966 | 131516.5966 | 131516.5966 | 131516.5966 | 131516.5966
Option 8 Summer POE50 W E @ R (MWh) N 2 | 64234.6643 | 85353.6468 | 91106.3426 | 90941.7262 | 90939.7566 | 91597.7077 | 92319.4358 | 93799.6161 | 94863.0323 | 95441.1797 | 96074.5298 | 96653.284 | 97696.8324 | 98991.3793 | 98903.8888 | 98903.8888 | 98903.8888 | 98903.8888 | 98903.8888 | 98903.8888 | 98903.8888 | 98903.8888 | 98903.8888 | 98903.8888 | 98903.8888 | 98903.8888 | 98903.8888 | 98903.8888 | 98903.8888 | 98903.8888 | Option 8 Summer POE10 W E @ R (MWh) N 2 | 26720.2732 | 34614.4787 | 36681.6025 | 36558.6648 | 36568.9855 | 36781.8022 | 37342.0695 | 37717.7216 | 38085.1549 | 38514.7576 | 38913.2387 | 39299.7908 | 39344.5729 | 39795.6139 | 39454.979 | 39454.979 | 39454.979 | 39454.979 | 39454.979 | 39454.979 | 39454.979 | 39454.979 | 39454.979 | 39454.979 | 39454.979 | 39454.979 | 39454.979 | 39454.979 | 39454.979 | 39454.979

## POF N,N-1 & N-2 Risk
N-2 Method 1
| Asset name | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Tx 1 Pof | DS-PHM-TRNFMR-9000004393 | 0.01357% | 0.01357% | 0.01791% | 0.023% | 0.02887% | 0.03555% | 0.04308% | 0.0515% | 0.06084% | 0.07112% | 0.08238% | 0.09465% | 0.1079% | 0.1223% | 0.1378% | 0.1378% | 0.1378% | 0.1378% | 0.1378% | 0.1378% | 0.1378% | 0.1378% | 0.1378% | 0.1378% | 0.1378% | 0.1378% | 0.1378% | 0.1378% | 0.1378% | 0.1378%
Tx 2 Pof | DS-PHM-TRNFMR-9000007050 | 0.01357% | 0.01357% | 0.01791% | 0.023% | 0.02887% | 0.03555% | 0.04308% | 0.0515% | 0.06084% | 0.07112% | 0.08238% | 0.09465% | 0.1079% | 0.1223% | 0.1378% | 0.1378% | 0.1378% | 0.1378% | 0.1378% | 0.1378% | 0.1378% | 0.1378% | 0.1378% | 0.1378% | 0.1378% | 0.1378% | 0.1378% | 0.1378% | 0.1378% | 0.1378%
Tx 3 Pof | bar: FY25 to FY54
Tx 4 Pof
Tx 5 Pof
Total Tx Pof |  | 0.02714% | 0.02714% | 0.03583% | 0.046% | 0.05773% | 0.0711% | 0.08616% | 0.103% | 0.1217% | 0.1422% | 0.1648% | 0.1893% | 0.2159% | 0.2446% | 0.2755% | 0.2755% | 0.2755% | 0.2755% | 0.2755% | 0.2755% | 0.2755% | 0.2755% | 0.2755% | 0.2755% | 0.2755% | 0.2755% | 0.2755% | 0.2755% | 0.2755% | 0.2755%
N-1 Risk |  | 0.01047% | 0.01047% | 0.01382% | 0.01775% | 0.02227% | 0.02743% | 0.03324% | 0.03974% | 0.04694% | 0.05488% | 0.06356% | 0.07303% | 0.08329% | 0.09438% | 0.1063% | 0.1063% | 0.1063% | 0.1063% | 0.1063% | 0.1063% | 0.1063% | 0.1063% | 0.1063% | 0.1063% | 0.1063% | 0.1063% | 0.1063% | 0.1063% | 0.1063% | 0.1063%
N-2 Risk |  | 4.318e-07% | 4.318e-07% | 7.523e-07% | 1.24e-06% | 1.953e-06% | 2.962e-06% | 4.351e-06% | 6.217e-06% | 8.675e-06% | 1.186e-05% | 1.591e-05% | 2.1e-05% | 2.731e-05% | 3.507e-05% | 4.449e-05% | 4.449e-05% | 4.449e-05% | 4.449e-05% | 4.449e-05% | 4.449e-05% | 4.449e-05% | 4.449e-05% | 4.449e-05% | 4.449e-05% | 4.449e-05% | 4.449e-05% | 4.449e-05% | 4.449e-05% | 4.449e-05% | 4.449e-05%
N Risk |  | 99.99% | 99.99% | 99.99% | 99.98% | 99.98% | 99.97% | 99.97% | 99.96% | 99.95% | 99.95% | 99.94% | 99.93% | 99.92% | 99.91% | 99.89% | 99.89% | 99.89% | 99.89% | 99.89% | 99.89% | 99.89% | 99.89% | 99.89% | 99.89% | 99.89% | 99.89% | 99.89% | 99.89% | 99.89% | 99.89%

## Summary
Involuntary load shedding (NER 5.17.1(c)(4)(ii))
Option 1 - Do Nothing / Base Case | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Weighted Energy @ Risk (MWh) under N Conditions | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Weighted Energy @ Risk (MWh) under N-1 Conditions | 0.0023203 | 0.11606 | 0.4094 | 0.57921 | 0.78408 | 1.1304 | 1.8821 | 2.7457 | 4.132 | 6.6326 | 6.7463 | 6.8484 | 9.3681 | 14.0517 | 13.1286 | 13.1286 | 13.1286 | 13.1286 | 13.1286 | 13.1286 | 13.1286 | 13.1286 | 13.1286 | 13.1286 | 13.1286 | 13.1286 | 13.1286 | 13.1286 | 13.1286 | 13.1286
Weighted Energy @ Risk (MWh) under N-2 Conditions | 0.0010504 | 0.001417 | 0.0026391 | 0.0043703 | 0.0069132 | 0.0106 | 0.015919 | 0.02315 | 0.032966 | 0.04616 | 0.06163 | 0.080754 | 0.10681 | 0.14098 | 0.17577 | 0.17577 | 0.17577 | 0.17577 | 0.17577 | 0.17577 | 0.17577 | 0.17577 | 0.17577 | 0.17577 | 0.17577 | 0.17577 | 0.17577 | 0.17577 | 0.17577 | 0.17577
Total EUE (MWh) - Option 1 | 0.0033707 | 0.11748 | 0.41204 | 0.58358 | 0.79099 | 1.141 | 1.8981 | 2.7688 | 4.165 | 6.6787 | 6.808 | 6.9292 | 9.4749 | 14.1927 | 13.3044 | 13.3044 | 13.3044 | 13.3044 | 13.3044 | 13.3044 | 13.3044 | 13.3044 | 13.3044 | 13.3044 | 13.3044 | 13.3044 | 13.3044 | 13.3044 | 13.3044 | 13.3044
Cost of EUE ($) - Option 1 | 130.1311 | 4535.3658 | 15907.403 | 22529.7846 | 30537.0779 | 44049.876 | 73276.699 | 106894.3736 | 160794.8873 | 257840.0603 | 262829.0846 | 267509.4891 | 365790.3822 | 547926.623 | 513632.0021 | 513632.0021 | 513632.0021 | 513632.0021 | 513632.0021 | 513632.0021 | 513632.0021 | 513632.0021 | 513632.0021 | 513632.0021 | 513632.0021 | 513632.0021 | 513632.0021 | 513632.0021 | 513632.0021 | 513632.0021
Hours at Risk pA. (Hrs) (N) | 1.486 | 1.486 | 1.486 | 1.486 | 1.486 | 1.486 | 1.486 | 1.486 | 1.486 | 1.486 | 1.486 | 1.486 | 1.486 | 1.486 | 1.486 | 1.486 | 1.486 | 1.486 | 1.486 | 1.486 | 1.486 | 1.486 | 1.486 | 1.486 | 1.486 | 1.486 | 1.486 | 1.486 | 1.486 | 1.486
Option 2 - 1B New PHS ZSS + Three new feeders | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Weighted Energy @ Risk (MWh) under N Conditions | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Weighted Energy @ Risk (MWh) under N-1 Conditions | 0.0023203 | 0.11606 | 0.4094 | 0.0032882 | 0.0041575 | 0.0059337 | 0.010161 | 0.015453 | 0.023941 | 0.15305 | 0.051033 | 0.060076 | 0.084086 | 0.23585 | 0.13926 | 0.13926 | 0.13926 | 0.13926 | 0.13926 | 0.13926 | 0.13926 | 0.13926 | 0.13926 | 0.13926 | 0.13926 | 0.13926 | 0.13926 | 0.13926 | 0.13926 | 0.13926
Weighted Energy @ Risk (MWh) under N-2 Conditions | 0.0010504 | 0.001417 | 0.0026391 | 0.0030459 | 0.0048271 | 0.0074365 | 0.011272 | 0.01651 | 0.0237 | 0.033497 | 0.044638 | 0.058326 | 0.077634 | 0.10352 | 0.12825 | 0.12825 | 0.12825 | 0.12825 | 0.12825 | 0.12825 | 0.12825 | 0.12825 | 0.12825 | 0.12825 | 0.12825 | 0.12825 | 0.12825 | 0.12825 | 0.12825 | 0.12825
Total EUE (MWh) - Option 2 | 0.0033707 | 0.11748 | 0.41204 | 0.0063341 | 0.0089846 | 0.01337 | 0.021433 | 0.031963 | 0.047641 | 0.18655 | 0.095671 | 0.1184 | 0.16172 | 0.33938 | 0.26752 | 0.26752 | 0.26752 | 0.26752 | 0.26752 | 0.26752 | 0.26752 | 0.26752 | 0.26752 | 0.26752 | 0.26752 | 0.26752 | 0.26752 | 0.26752 | 0.26752 | 0.26752
Cost of EUE ($) - Option 2 | 130.1311 | 4535.3658 | 15907.403 | 244.5343 | 346.8606 | 516.1727 | 827.4625 | 1233.9735 | 1839.2543 | 7201.832 | 3693.4958 | 4571.0518 | 6243.384 | 13102.1068 | 10327.7342 | 10327.7342 | 10327.7342 | 10327.7342 | 10327.7342 | 10327.7342 | 10327.7342 | 10327.7342 | 10327.7342 | 10327.7342 | 10327.7342 | 10327.7342 | 10327.7342 | 10327.7342 | 10327.7342 | 10327.7342
Option 3 - 2B PHM 3rd Tx + Switchroom + Two new feeders + OFR12 New Feeder | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Weighted Energy @ Risk (MWh) under N Conditions | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Weighted Energy @ Risk (MWh) under N-1 Conditions | 0.0023203 | 0.11606 | 0.4094 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Weighted Energy @ Risk (MWh) under N-2 Conditions | 0.0010504 | 0.001417 | 0.0026391 | 8.2023e-05 | 0.00013779 | 0.00023677 | 0.00044845 | 0.00074881 | 0.0012696 | 0.0022403 | 0.0027066 | 0.0032087 | 0.0048497 | 0.0078739 | 0.0085154 | 0.0085154 | 0.0085154 | 0.0085154 | 0.0085154 | 0.0085154 | 0.0085154 | 0.0085154 | 0.0085154 | 0.0085154 | 0.0085154 | 0.0085154 | 0.0085154 | 0.0085154 | 0.0085154 | 0.0085154
Total EUE (MWh) - Option 3 | 0.0033707 | 0.11748 | 0.41204 | 8.2023e-05 | 0.00013779 | 0.00023677 | 0.00044845 | 0.00074881 | 0.0012696 | 0.0022403 | 0.0027066 | 0.0032087 | 0.0048497 | 0.0078739 | 0.0085154 | 0.0085154 | 0.0085154 | 0.0085154 | 0.0085154 | 0.0085154 | 0.0085154 | 0.0085154 | 0.0085154 | 0.0085154 | 0.0085154 | 0.0085154 | 0.0085154 | 0.0085154 | 0.0085154 | 0.0085154
Cost of EUE ($) - Option 3 | 130.1311 | 4535.3658 | 15907.403 | 3.1666 | 5.3194 | 9.1408 | 17.313 | 28.9088 | 49.0155 | 86.4888 | 104.4914 | 123.8772 | 187.2276 | 303.9826 | 328.7473 | 328.7473 | 328.7473 | 328.7473 | 328.7473 | 328.7473 | 328.7473 | 328.7473 | 328.7473 | 328.7473 | 328.7473 | 328.7473 | 328.7473 | 328.7473 | 328.7473 | 328.7473
Option 4 - 3B OFR 3rd Tx + Switchroom + Two new feeders + OFR12 New Feeder | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Weighted Energy @ Risk (MWh) under N Conditions | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Weighted Energy @ Risk (MWh) under N-1 Conditions | 0.0023203 | 0.11606 | 0.4094 | 0.22782 | 0.31409 | 0.47474 | 0.88449 | 1.376 | 2.2459 | 4.0508 | 3.871 | 3.7598 | 5.4301 | 8.8266 | 7.7961 | 7.7961 | 7.7961 | 7.7961 | 7.7961 | 7.7961 | 7.7961 | 7.7961 | 7.7961 | 7.7961 | 7.7961 | 7.7961 | 7.7961 | 7.7961 | 7.7961 | 7.7961
Weighted Energy @ Risk (MWh) under N-2 Conditions | 0.0010504 | 0.001417 | 0.0026391 | 0.0040963 | 0.0064816 | 0.0099458 | 0.014958 | 0.021777 | 0.031049 | 0.04354 | 0.058114 | 0.076114 | 0.10077 | 0.13323 | 0.16594 | 0.16594 | 0.16594 | 0.16594 | 0.16594 | 0.16594 | 0.16594 | 0.16594 | 0.16594 | 0.16594 | 0.16594 | 0.16594 | 0.16594 | 0.16594 | 0.16594 | 0.16594
Total EUE (MWh) - Option 4 | 0.0033707 | 0.11748 | 0.41204 | 0.23192 | 0.32057 | 0.48468 | 0.89944 | 1.3978 | 2.2769 | 4.0943 | 3.9291 | 3.8359 | 5.5309 | 8.9598 | 7.962 | 7.962 | 7.962 | 7.962 | 7.962 | 7.962 | 7.962 | 7.962 | 7.962 | 7.962 | 7.962 | 7.962 | 7.962 | 7.962 | 7.962 | 7.962
Cost of EUE ($) - Option 4 | 130.1311 | 4535.3658 | 15907.403 | 8953.3885 | 12376.1346 | 18711.7074 | 34724.0428 | 53964.3002 | 87903.0245 | 158066.8351 | 151687.9301 | 148088.5988 | 213525.1856 | 345903.0605 | 307383.5649 | 307383.5649 | 307383.5649 | 307383.5649 | 307383.5649 | 307383.5649 | 307383.5649 | 307383.5649 | 307383.5649 | 307383.5649 | 307383.5649 | 307383.5649 | 307383.5649 | 307383.5649 | 307383.5649 | 307383.5649
Option 5 - 4B LLG 2nd Tx + Switchroom + Two new feeders + OFR12 New Feeder | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Weighted Energy @ Risk (MWh) under N Conditions | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Weighted Energy @ Risk (MWh) under N-1 Conditions | 0.0023203 | 0.11606 | 0.4094 | 0.00098759 | 0.0012557 | 0.0019933 | 0.0042141 | 0.0068249 | 0.01043 | 0.060852 | 0.023239 | 0.032225 | 0.039597 | 0.085622 | 0.059188 | 0.059188 | 0.059188 | 0.059188 | 0.059188 | 0.059188 | 0.059188 | 0.059188 | 0.059188 | 0.059188 | 0.059188 | 0.059188 | 0.059188 | 0.059188 | 0.059188 | 0.059188
Weighted Energy @ Risk (MWh) under N-2 Conditions | 0.0010504 | 0.001417 | 0.0026391 | 0.0028804 | 0.0045663 | 0.007041 | 0.010691 | 0.01568 | 0.022542 | 0.031914 | 0.042514 | 0.055522 | 0.073987 | 0.098842 | 0.12231 | 0.12231 | 0.12231 | 0.12231 | 0.12231 | 0.12231 | 0.12231 | 0.12231 | 0.12231 | 0.12231 | 0.12231 | 0.12231 | 0.12231 | 0.12231 | 0.12231 | 0.12231
Total EUE (MWh) - Option 5 | 0.0033707 | 0.11748 | 0.41204 | 0.0038679 | 0.005822 | 0.0090343 | 0.014905 | 0.022505 | 0.032972 | 0.092766 | 0.065753 | 0.087747 | 0.11358 | 0.18446 | 0.1815 | 0.1815 | 0.1815 | 0.1815 | 0.1815 | 0.1815 | 0.1815 | 0.1815 | 0.1815 | 0.1815 | 0.1815 | 0.1815 | 0.1815 | 0.1815 | 0.1815 | 0.1815
Cost of EUE ($) - Option 5 | 130.1311 | 4535.3658 | 15907.403 | 149.3263 | 224.7647 | 348.7788 | 575.4353 | 868.8156 | 1272.9111 | 3581.3332 | 2538.4707 | 3387.5783 | 4385.0564 | 7121.4711 | 7007.0862 | 7007.0862 | 7007.0862 | 7007.0862 | 7007.0862 | 7007.0862 | 7007.0862 | 7007.0862 | 7007.0862 | 7007.0862 | 7007.0862 | 7007.0862 | 7007.0862 | 7007.0862 | 7007.0862 | 7007.0862
Option 6 - | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Weighted Energy @ Risk (MWh) under N Conditions | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Weighted Energy @ Risk (MWh) under N-1 Conditions | 0.0023203 | 0.11606 | 0.4094 | 0.57921 | 0.78408 | 1.1304 | 1.8821 | 2.7457 | 4.132 | 6.6326 | 6.7463 | 6.8484 | 9.3681 | 14.0517 | 13.1286 | 13.1286 | 13.1286 | 13.1286 | 13.1286 | 13.1286 | 13.1286 | 13.1286 | 13.1286 | 13.1286 | 13.1286 | 13.1286 | 13.1286 | 13.1286 | 13.1286 | 13.1286
Weighted Energy @ Risk (MWh) under N-2 Conditions | 0.0010504 | 0.001417 | 0.0026391 | 0.0043703 | 0.0069132 | 0.0106 | 0.015919 | 0.02315 | 0.032966 | 0.04616 | 0.06163 | 0.080754 | 0.10681 | 0.14098 | 0.17577 | 0.17577 | 0.17577 | 0.17577 | 0.17577 | 0.17577 | 0.17577 | 0.17577 | 0.17577 | 0.17577 | 0.17577 | 0.17577 | 0.17577 | 0.17577 | 0.17577 | 0.17577
Total EUE (MWh) - Option 6 | 0.0033707 | 0.11748 | 0.41204 | 0.58358 | 0.79099 | 1.141 | 1.8981 | 2.7688 | 4.165 | 6.6787 | 6.808 | 6.9292 | 9.4749 | 14.1927 | 13.3044 | 13.3044 | 13.3044 | 13.3044 | 13.3044 | 13.3044 | 13.3044 | 13.3044 | 13.3044 | 13.3044 | 13.3044 | 13.3044 | 13.3044 | 13.3044 | 13.3044 | 13.3044
Cost of EUE ($) - Option 6 | 130.1311 | 4535.3658 | 15907.403 | 22529.7846 | 30537.0779 | 44049.876 | 73276.699 | 106894.3736 | 160794.8873 | 257840.0603 | 262829.0846 | 267509.4891 | 365790.3822 | 547926.623 | 513632.0021 | 513632.0021 | 513632.0021 | 513632.0021 | 513632.0021 | 513632.0021 | 513632.0021 | 513632.0021 | 513632.0021 | 513632.0021 | 513632.0021 | 513632.0021 | 513632.0021 | 513632.0021 | 513632.0021 | 513632.0021
Option 7 - | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Weighted Energy @ Risk (MWh) under N Conditions | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Weighted Energy @ Risk (MWh) under N-1 Conditions | 0.0023203 | 0.11606 | 0.4094 | 0.57921 | 0.78408 | 1.1304 | 1.8821 | 2.7457 | 4.132 | 6.6326 | 6.7463 | 6.8484 | 9.3681 | 14.0517 | 13.1286 | 13.1286 | 13.1286 | 13.1286 | 13.1286 | 13.1286 | 13.1286 | 13.1286 | 13.1286 | 13.1286 | 13.1286 | 13.1286 | 13.1286 | 13.1286 | 13.1286 | 13.1286
Weighted Energy @ Risk (MWh) under N-2 Conditions | 0.0010504 | 0.001417 | 0.0026391 | 0.0043703 | 0.0069132 | 0.0106 | 0.015919 | 0.02315 | 0.032966 | 0.04616 | 0.06163 | 0.080754 | 0.10681 | 0.14098 | 0.17577 | 0.17577 | 0.17577 | 0.17577 | 0.17577 | 0.17577 | 0.17577 | 0.17577 | 0.17577 | 0.17577 | 0.17577 | 0.17577 | 0.17577 | 0.17577 | 0.17577 | 0.17577
Total EUE (MWh) - Option 7 | 0.0033707 | 0.11748 | 0.41204 | 0.58358 | 0.79099 | 1.141 | 1.8981 | 2.7688 | 4.165 | 6.6787 | 6.808 | 6.9292 | 9.4749 | 14.1927 | 13.3044 | 13.3044 | 13.3044 | 13.3044 | 13.3044 | 13.3044 | 13.3044 | 13.3044 | 13.3044 | 13.3044 | 13.3044 | 13.3044 | 13.3044 | 13.3044 | 13.3044 | 13.3044
Cost of EUE ($) - Option 7 | 130.1311 | 4535.3658 | 15907.403 | 22529.7846 | 30537.0779 | 44049.876 | 73276.699 | 106894.3736 | 160794.8873 | 257840.0603 | 262829.0846 | 267509.4891 | 365790.3822 | 547926.623 | 513632.0021 | 513632.0021 | 513632.0021 | 513632.0021 | 513632.0021 | 513632.0021 | 513632.0021 | 513632.0021 | 513632.0021 | 513632.0021 | 513632.0021 | 513632.0021 | 513632.0021 | 513632.0021 | 513632.0021 | 513632.0021
Option 8 - | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Weighted Energy @ Risk (MWh) under N Conditions | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Weighted Energy @ Risk (MWh) under N-1 Conditions | 0.0023203 | 0.11606 | 0.4094 | 0.57921 | 0.78408 | 1.1304 | 1.8821 | 2.7457 | 4.132 | 6.6326 | 6.7463 | 6.8484 | 9.3681 | 14.0517 | 13.1286 | 13.1286 | 13.1286 | 13.1286 | 13.1286 | 13.1286 | 13.1286 | 13.1286 | 13.1286 | 13.1286 | 13.1286 | 13.1286 | 13.1286 | 13.1286 | 13.1286 | 13.1286
Weighted Energy @ Risk (MWh) under N-2 Conditions | 0.0010504 | 0.001417 | 0.0026391 | 0.0043703 | 0.0069132 | 0.0106 | 0.015919 | 0.02315 | 0.032966 | 0.04616 | 0.06163 | 0.080754 | 0.10681 | 0.14098 | 0.17577 | 0.17577 | 0.17577 | 0.17577 | 0.17577 | 0.17577 | 0.17577 | 0.17577 | 0.17577 | 0.17577 | 0.17577 | 0.17577 | 0.17577 | 0.17577 | 0.17577 | 0.17577
Total EUE (MWh) - Option 8 | 0.0033707 | 0.11748 | 0.41204 | 0.58358 | 0.79099 | 1.141 | 1.8981 | 2.7688 | 4.165 | 6.6787 | 6.808 | 6.9292 | 9.4749 | 14.1927 | 13.3044 | 13.3044 | 13.3044 | 13.3044 | 13.3044 | 13.3044 | 13.3044 | 13.3044 | 13.3044 | 13.3044 | 13.3044 | 13.3044 | 13.3044 | 13.3044 | 13.3044 | 13.3044
Cost of EUE ($) - Option 8 | 130.1311 | 4535.3658 | 15907.403 | 22529.7846 | 30537.0779 | 44049.876 | 73276.699 | 106894.3736 | 160794.8873 | 257840.0603 | 262829.0846 | 267509.4891 | 365790.3822 | 547926.623 | 513632.0021 | 513632.0021 | 513632.0021 | 513632.0021 | 513632.0021 | 513632.0021 | 513632.0021 | 513632.0021 | 513632.0021 | 513632.0021 | 513632.0021 | 513632.0021 | 513632.0021 | 513632.0021 | 513632.0021 | 513632.0021