## Info
Document description
This model Energy at Risk model has been developed to calculated Energy at Risk (EaR) in terms of Expected Unsureved Energy (EUE) and the cost of EUE. The modelling inputs, calculation steps and outputs are described in the 'Modelling Steps' tab. Further detail on EaR/EUE calculations can be found in AusNet's Network Planning Policy and Guidelines.
Tab # | Tab Name | Description | Source/ Inputs
0.1 | Modelling Steps | E@R model process flowchart and underlying equations | N/A
0.2 | Modelling Example & QA | Example E@R model calculations and data flow; also used to validate base case | N/A
0.3 | QA | Quality assurance and data validation | Entire workbook
1.1 | Output for AusNet's NPV Model | Aggregates Supply Risk ($M) and EUE (MWh) for input into AusNet’s NPV model | Summary tab
2.1 | Key Model Assumptions & Inputs | E@R model inputs and asset selection | Augmentation plans from RPs/EPCs, Embedded Generation DB, Demand Management DB
2.2 | Tx PoF | Transformer Probabilities of Failure | Provided by Asset Management Team
2.3 | Customer No. and Volume per Feeder | Customer consumption data | Provided by Finance Team
2.4 | AER VCR Rates (2024) | AER 2024 VCR rates | AER VCR Factsheet
2.5 | Forecast - Summer | Summer Forecast Data | Extract from Forecasting Toolbox
2.6 | Forecast- Winter | Winter Forecast Data | Extract from Forecasting Toolbox
2.7 | Ratings | Station Rating Data | AMS 20-101 / Provided by Asset mangement Team
2.8 | FT (Forecast & Transfers) | Forecast, transfer & PF inputs | Forecast Summer , Forecast Winter , NP Transfer Sheet, PF = avg. max demand PF across stations
2.9 | Load Duration Curves | Load duration curve data | LDC Tool; data sourced from PI SCADA Historian and AEMO
3.1 | Capacity N | Option N capacity calculated | FT Sheet, Ratings & Key Model Assumptions
3.2 | Capacity N-1 | Option N-1 capacity calculated | FT Sheet, Ratings & Key Model Assumptions
3.3 | Capacity N-1 | Option N-2 capacity calculated | FT Sheet, Ratings & Key Model Assumptions
3.4 | Demand | Calculates maximum demand | FT Sheet & Key Model Assumptions
3.5 | MD Weighted LDC | Maps maximum demand forecast to load duration curve | Demand Sheet & Load Duration Curve Sheet
3.6 | Locational VCR | Calculates tailored VCR by location using feeder energy mix and AER rates | AER VCR Rates (2024) & Customer No./Volume per Feeder
3.7 | E@R N | Calculates N EUE using capacity and demand inputs | MD Weighted LDC & Capacity N
3.8 | E@R N-1 | Calculates N-1 EUE using capacity and demand inputs | MD Weighted LDC & Capacity N-1
3.9 | E@R N-2 | Calculates N-2 EUE using capacity and demand inputs | MD Weighted LDC & Capacity N-2
4 | POF N,N-1 & N-2 Risk | Calculates Station N , N-1 & N-2 PoF's from Tx PoF Data & MTTR | TX PoF & Key Model Assumptions
4.1 | Summary | Collates weighted EUE and calculates supply risk | E@R & Locational VCR
Revision table
Date | Editted by | Change
2025-10-14 | HT | Draft Version 2.1
2025-10-20 | HT | Version 2.2
2025-11-10 | HT | Version 2.3 Example Page Update and General Refinements

## Modelling Steps
Eq1. Locational VCR |  | Data Inputs |  |  | Calculations |  |  |  |  | Outputs
|  |  | Customer No. and Vol per Feeder |  | Eq1.
Locational VCR
Eq2. Maximum Demand
AER Latetst VCR Rates
Eq3. Options & Do nothing Capacity
Eq6. & Eq7.
Load Forecast
[9 empty] | Summary Sheet | Output for AusNet's NPV Model
Eq4. Help Sheet | Re Name Forecasted LDC add Forecast MD to eq
Transfer Capacity
Eq2.
Eq5. Energy at Risk ( Option/ Do Nothing Capacity) |  |  |  |  | Options & Do Nothing Max Demand
Embeded Generation
Eq6. Weighted Expected Unserved Energy
[6 empty] | Eq.4 | Eq.5
Demand Mangement Capacity
[6 empty] | Forecasted LDC |  | Energy @ Risk Sheet
Eq7. Supply Risk
Load Duration Curves
|  |  | Asset Ratings |  | Eq3.
Options & Do Nothing Capacity
Planned & Proposed Works

## Modelling Steps Example & QA
End of Sheet
Data Inputs |  |  | Calculations | [12 empty] | Outputs
AER VCR Rates(2024 |  |  | Locational (Tailored VCR)
Category | Rate |  | Base case |  | Energy Usage (CY 2024 kWh) | Energy Usage (CY 2024 %) | Tailored VCR
Dec 24 AER VCR ($/kWh) - Res | 49.23 |  | Dec 24 AER VCR ($/kWh) - Res | 49.23 | 88661416.1819 | 59.86% | 29.4686
Dec 24 AER VCR ($/kWh) - Com | 34.39 |  | Dec 24 AER VCR ($/kWh) - Com | 34.39 | 45585213.1364 | 30.78% | 10.584
Dec 24 AER VCR ($/kWh) - Ind | 33.49 |  | Dec 24 AER VCR ($/kWh) - Ind | 33.49 | 5851096.6819 | 3.95% | 1.323
Dec 24 AER VCR ($/kWh) - Agr | 22.25 |  | Dec 24 AER VCR ($/kWh) - Agr | 22.25 | 8019086.0298 | 5.414% | 1.2046
[5 empty] | 148116812.03 |  | 42.5803
Customer No. and Vol per Feeder | [6 empty] | 42580.277 | [8 empty] | Summary |  | Outputs for NPV model
COMMERCIAL | 45585213.1364 | [14 empty] | Year | 2031 | Year | 2031
[16 empty] | E@R MWh | 68.6979 | E@R MWh | 68.6979
RESIDENTL | 88661416.1819 | [14 empty] | cost of EUE ($) | 2925174.5028 | cost of EUE ($M) | 2.9252
FARM | 8019086.0298
INDUSTRIAL | 5851096.6819
Forecast (FCT)
Forecast | 2031
Summer POE50 | 49.6777
Summer POE10 | 60.6061
Winter POE50 | 51.935
Winter POE10 | 55.6016
Transfer Capacity |  |  | Option Max Demand |  |  |  | MD Weighted LDC |  |  | E@R (N) |  | E@R (N-1) |  | E@R (N-2)
Year | 2031 |  | Forecast | 2031 |  |  | % of MD | Summer - AD - Hours | FY31 | % of MD | FY31 | % of MD | FY31 | % of MD | FY31
Capacity | 0 |  | Summer POE50 | 49.5677 |  |  | 100% | 0 | 49.5677 | 100% |  | 100% |  | 100%
|  |  | Summer POE10 | 60.4961 |  |  | 99% | 0.37816 | 49.072 | 99% |  | 99% | 5.3018 | 99% | 11.9764
Embedded Generation |  |  | Winter POE50 | 51.825 |  |  | 98% | 0.37816 | 48.5763 | 98% |  | 98% | 0 | 98% | 0
|  |  | Winter POE10 | 55.4916 |  |  | 97% | 0.37816 | 48.0806 | 97% |  | 97% | 0 | 97% | 0
Year | 2031 | [5 empty] | 95% | 0.75633 | 47.0893 | 95% |  | 95% | 4.6457 | 95% | 11.3203
Capacity | 0.11 | [5 empty] | 90% | 9.0759 | 44.6109 | 90% |  | 90% | 87.7726 | 90% | 234.6138
[7 empty] | 85% | 40.4636 | 42.1325 | 85% |  | 85% | 253.3514 | 85% | 807.3432
Demand Mangement | [6 empty] | 80% | 94.5411 | 39.6541 | 80% |  | 80% | 302.4723 | 80% | 1256.9401
[7 empty] | 75% | 197.0236 | 37.1757 | 75% |  | 75% | 319.2259 | 75% | 2128.0424
Year | 2031 | [5 empty] | 70% | 336.9444 | 34.6974 | 70% |  | 70% | 99.3182 | 70% | 2558.6681
Capacity | 0 | [5 empty] | 65% | 521.4885 | 32.219 | 65% |  | 65% |  | 65% | 2917.3047
[7 empty] | 60% | 812.675 | 29.7406 | 60% |  | 60% |  | 60% | 3881.4527
LDC | [6 empty] | 55% | 1202.1843 | 27.2622 | 55% |  | 55% |  | 55% | 4226.7202
[7 empty] | 50% | 1686.2345 | 24.7838 | 50% |  | 50% |  | 50% | 4052.9614
% of MD | Summer - AD - Duration % | Summer - AD - Hours |  |  |  |  | 45% | 2129.0649 | 22.3054 | 45% |  | 45% |  | 45% | 2610.3233
100% | 0% | 0 |  |  |  |  | 40% | 2484.5393 | 19.8271 | 40% |  | 40% |  | 40% | 1214.3902
99% | 0.00861% | 0.37816 |  |  |  |  | 35% | 2808.248 | 17.3487 | 35% |  | 35% |  | 35% | 309.5259
98% | 0.00861% | 0.37816 |  |  |  |  | 30% | 3095.6528 | 14.8703 | 30% |  | 30% |  | 30%
97% | 0.00861% | 0.37816 |  |  |  |  | 25% | 3358.8552 | 12.3919 | 25% |  | 25% |  | 25%
95% | 0.01722% | 0.75633 |  |  |  |  | 20% | 3588.7791 | 9.9135 | 20% |  | 20% |  | 20%
90% | 0.2066% | 9.0759 |  |  |  |  | 15% | 3802.4419 | 7.4351 | 15% |  | 15% |  | 15%
85% | 0.9213% | 40.4636 |  |  |  |  | 10% | 4024.8025 | 4.9568 | 10% |  | 10% |  | 10%
80% | 2.153% | 94.5411 |  |  |  |  | 5% | 4239.978 | 2.4784 | 5% |  | 5% |  | 5%
75% | 4.486% | 197.0236 |  |  |  |  | 9.992e-14% | 4391.6218 | 4.9528e-14 | 9.992e-14% |  | 9.992e-14% |  | 9.992e-14%
70% | 7.672% | 336.9444 | [7 empty] | Total E@R | 0 | Total E@R | 1061.367 | Total E@R | 25959.3667
65% | 11.87% | 521.4885 | [7 empty] | Total WE@R | 0 | Total WE@R | 18.3263 | Total WE@R | 4.0904
60% | 18.5% | 812.675 |  |  |  |  | MD Weighted LDC
55% | 27.37% | 1202.1843
50% | 38.39% | 1686.2345 |  |  |  |  | % of MD | Summer - MD - Hours | FY31
45% | 48.48% | 2129.0649 |  |  |  |  | 100% | 0 | 60.4961 | E@R (N) |  | E@R (N) |  | E@R (N-2)
40% | 56.57% | 2484.5393 |  |  |  |  | 99% | 0 | 59.8911
35% | 63.94% | 2808.248 |  |  |  |  | 98% | 0 | 59.2862 | % of MD | FY31 | % of MD | FY31 | % of MD | FY31
30% | 70.48% | 3095.6528 |  |  |  |  | 97% | 0.37816 | 58.6812 | 100% |  | 100% |  | 100%
25% | 76.48% | 3358.8552 |  |  |  |  | 95% | 0.37816 | 57.4713 | 99% | 0 | 99% | 0 | 99% | 0
20% | 81.71% | 3588.7791 |  |  |  |  | 90% | 0.75633 | 54.4465 | 98% | 0 | 98% | 0 | 98% | 0
15% | 86.58% | 3802.4419 |  |  |  |  | 85% | 1.1345 | 51.4217 | 97% | 1.204 | 97% | 8.9563 | 97% | 15.6309
10% | 91.64% | 4024.8025 |  |  |  |  | 80% | 2.6471 | 48.3969 | 95% | 0 | 95% | 0 | 95% | 0
5% | 96.54% | 4239.978 |  |  |  |  | 75% | 3.4035 | 45.3721 | 90% | 0.17461 | 90% | 7.8125 | 90% | 14.4871
9.992e-14% | 99.99% | 4391.6218 |  |  |  |  | 70% | 5.6725 | 42.3473 | 85% |  | 85% | 6.6686 | 85% | 13.3432
[7 empty] | 65% | 6.4288 | 39.3225 | 80% |  | 80% | 22.0988 | 80% | 48.7972
[7 empty] | 60% | 11.3449 | 36.2977 | 75% |  | 75% | 8.7617 | 75% | 22.1109
[7 empty] | 55% | 35.5474 | 33.2729 | 70% |  | 70% | 19.4218 | 70% | 59.4694
LDC | [6 empty] | 50% | 95.2974 | 30.2481 | 65% |  | 65% | 4.1862 | 65% | 17.5354
[7 empty] | 45% | 208.7467 | 27.2232 | 60% |  | 60% | 12.3398 | 60% | 99.1096
% of MD | Summer - MD - Duration % | Summer - MD - Hours |  |  |  |  | 40% | 380.4333 | 24.1984 | 55% |  | 55% | 3.982 | 55% | 414.7164
100% | 0% | 0 |  |  |  |  | 35% | 696.5786 | 21.1736 | 50% |  | 50% |  | 50% | 843.0992
99% | 0% | 0 |  |  |  |  | 30% | 1260.7997 | 18.1488 | 45% |  | 45% |  | 45% | 1257.6592
98% | 0% | 0 |  |  |  |  | 25% | 1965.3198 | 15.124 | 40% |  | 40% |  | 40% | 1383.9391
97% | 0.00861% | 0.37816 |  |  |  |  | 20% | 2490.2118 | 12.0992 | 35% |  | 35% |  | 35% | 1592.1207
95% | 0.00861% | 0.37816 |  |  |  |  | 15% | 2997.7083 | 9.0744 | 30% |  | 30% |  | 30% | 1134.7813
90% | 0.01722% | 0.75633 |  |  |  |  | 10% | 3491.5908 | 6.0496 | 25% |  | 25% |  | 25% | 28.9785
85% | 0.02583% | 1.1345 |  |  |  |  | 5% | 3955.9766 | 3.0248 | 20% |  | 20% |  | 20%
80% | 0.06027% | 2.6471 |  |  |  |  | 9.992e-14% | 4391.6218 | 6.0448e-14 | 15% |  | 15% |  | 15%
75% | 0.07749% | 3.4035 | [7 empty] | 10% |  | 10% |  | 10%
70% | 0.1292% | 5.6725 | [7 empty] | 5% |  | 5% |  | 5%
65% | 0.1464% | 6.4288 | [7 empty] | 9.992e-14% |  | 9.992e-14% |  | 9.992e-14%
60% | 0.2583% | 11.3449 | [7 empty] | Total E@R | 1.3648 | Total E@R | 93.2854 | Total E@R | 6876.3204
55% | 0.8094% | 35.5474 |  |  |  |  | MD Weighted LDC |  |  | Total WE@R | 0.53436 | Total WE@R | 0.69031 | Total WE@R | 0.46435
50% | 2.17% | 95.2974
45% | 4.753% | 208.7467 |  |  |  |  | % of MD | Winter - AD - Hours | FY31
40% | 8.662% | 380.4333 |  |  |  |  | 100% | 0 | 51.825
35% | 15.86% | 696.5786 |  |  |  |  | 99% | 0.2972 | 51.3068 | E@R (N) |  | E@R (N-1) |  | E@R (N-2)
30% | 28.71% | 1260.7997 |  |  |  |  | 98% | 0.2972 | 50.7885
25% | 44.75% | 1965.3198 |  |  |  |  | 97% | 0.2972 | 50.2703 | % of MD | FY31 | % of MD | FY31 | % of MD | FY31
20% | 56.7% | 2490.2118 |  |  |  |  | 95% | 1.486 | 49.2338 | 100% |  | 100% |  | 100%
15% | 68.25% | 2997.7083 |  |  |  |  | 90% | 8.6188 | 46.6425 | 99% |  | 99% | 4.5964 | 99% | 9.9609
10% | 79.5% | 3491.5908 |  |  |  |  | 85% | 40.1218 | 44.0513 | 98% |  | 98% | 0 | 98% | 0
5% | 90.07% | 3955.9766 |  |  |  |  | 80% | 93.0231 | 41.46 | 97% |  | 97% | 0 | 97% | 0
9.992e-14% | 99.99% | 4391.6218 |  |  |  |  | 75% | 197.0426 | 38.8688 | 95% |  | 95% | 16.2295 | 95% | 37.6872
[7 empty] | 70% | 378.0365 | 36.2775 | 90% |  | 90% | 84.4388 | 90% | 213.1852
[7 empty] | 65% | 616.0926 | 33.6863 | 85% |  | 85% | 291.3058 | 85% | 859.9357
[7 empty] | 60% | 934.9866 | 31.095 | 80% |  | 80% | 352.0931 | 80% | 1306.9623
LDC | [6 empty] | 55% | 1310.9428 | 28.5038 | 75% |  | 75% | 422.7773 | 75% | 2300.329
[7 empty] | 50% | 1730.2899 | 25.9125 | 70% |  | 70% | 266.6317 | 70% | 3533.5717
% of MD | Winter - AD (P50) - Duration % | Winter - AD - Hours |  |  |  |  | 45% | 2168.0633 | 23.3213 | 65% |  | 65% | 1.4477 | 65% | 4030.7411
100% | 0% | 0 |  |  |  |  | 40% | 2609.7004 | 20.73 | 60% |  | 60% |  | 60% | 4573.1473
99% | 0.006767% | 0.2972 |  |  |  |  | 35% | 2998.1389 | 18.1388 | 55% |  | 55% |  | 55% | 4417.258
98% | 0.006767% | 0.2972 |  |  |  |  | 30% | 3309.3057 | 15.5475 | 50% |  | 50% |  | 50% | 3840.4419
97% | 0.006767% | 0.2972 |  |  |  |  | 25% | 3537.8514 | 12.9563 | 45% |  | 45% |  | 45% | 2874.8114
95% | 0.03383% | 1.486 |  |  |  |  | 20% | 3731.0305 | 10.365 | 40% |  | 40% |  | 40% | 1755.7904
90% | 0.1962% | 8.6188 |  |  |  |  | 15% | 3910.2412 | 7.7738 | 35% |  | 35% |  | 35% | 537.7501
85% | 0.9135% | 40.1218 |  |  |  |  | 10% | 4075.1864 | 5.1825 | 30% |  | 30% |  | 30% | 0.47307
80% | 2.118% | 93.0231 |  |  |  |  | 5% | 4251.7223 | 2.5913 | 25% |  | 25% |  | 25%
75% | 4.486% | 197.0426 |  |  |  |  | 9.992e-14% | 4391.7028 | 5.1784e-14 | 20% |  | 20% |  | 20%
70% | 8.607% | 378.0365 | [7 empty] | 15% |  | 15% |  | 15%
65% | 14.03% | 616.0926 | [7 empty] | 10% |  | 10% |  | 10%
60% | 21.29% | 934.9866 | [7 empty] | 5% |  | 5% |  | 5%
55% | 29.85% | 1310.9428 | [7 empty] | 9.992e-14% |  | 9.992e-14% |  | 9.992e-14%
50% | 39.4% | 1730.2899 |  |  |  |  | MD Weighted LDC |  |  | Total E@R | 0 | Total E@R | 1425.125 | Total E@R | 29989.1249
45% | 49.36% | 2168.0633 | [7 empty] | Total WE@R | 0 | Total WE@R | 20.9068 | Total WE@R | 4.0148
40% | 59.42% | 2609.7004 |  |  |  |  | % of MD | Winter - MD - Hours | FY31
35% | 68.26% | 2998.1389 |  |  |  |  | 100% | 0 | 55.4916 | E@R (N) |  | E@R (N-1) |  | E@R (N-2)
30% | 75.35% | 3309.3057 |  |  |  |  | 99% | 0.2972 | 54.9367
25% | 80.55% | 3537.8514 |  |  |  |  | 98% | 0.2972 | 54.3818 | % of MD | FY31 | % of MD | FY31 | % of MD | FY31
20% | 84.95% | 3731.0305 |  |  |  |  | 97% | 0.2972 | 53.8269 | 100% |  | 100% |  | 100%
15% | 89.03% | 3910.2412 |  |  |  |  | 95% | 1.486 | 52.717 | 99% |  | 99% | 5.6807 | 99% | 11.0451
10% | 92.79% | 4075.1864 |  |  |  |  | 90% | 8.6188 | 49.9425 | 98% |  | 98% | 0 | 98% | 0
5% | 96.81% | 4251.7223 |  |  |  |  | 85% | 40.1218 | 47.1679 | 97% |  | 97% | 0 | 97% | 0
9.992e-14% | 99.99% | 4391.7028 |  |  |  |  | 80% | 93.0231 | 44.3933 | 95% |  | 95% | 20.4139 | 95% | 41.8717
[7 empty] | 75% | 197.0426 | 41.6187 | 90% |  | 90% | 108.6302 | 90% | 237.3766
[7 empty] | 70% | 378.0365 | 38.8441 | 85% |  | 85% | 392.3758 | 85% | 961.0057
[7 empty] | 65% | 616.0926 | 36.0696 | 80% |  | 80% | 512.1161 | 80% | 1466.9853
LDC | [6 empty] | 60% | 934.9866 | 33.295 | 75% |  | 75% | 718.3593 | 75% | 2595.9111
[7 empty] | 55% | 1310.9428 | 30.5204 | 70% |  | 70% | 747.7629 | 70% | 4014.703
% of MD | Winter - MD (P10) - Duration % | Winter - MD - Hours |  |  |  |  | 50% | 1730.2899 | 27.7458 | 65% |  | 65% | 323.0448 | 65% | 4619.9164
100% | 0% | 0 |  |  |  |  | 45% | 2168.0633 | 24.9712 | 60% |  | 60% |  | 60% | 5303.9296
99% | 0.006767% | 0.2972 |  |  |  |  | 40% | 2609.7004 | 22.1966 | 55% |  | 55% |  | 55% | 5209.881
98% | 0.006767% | 0.2972 |  |  |  |  | 35% | 2998.1389 | 19.4221 | 50% |  | 50% |  | 50% | 4647.6668
97% | 0.006767% | 0.2972 |  |  |  |  | 30% | 3309.3057 | 16.6475 | 45% |  | 45% |  | 45% | 3637.2496
95% | 0.03383% | 1.486 |  |  |  |  | 25% | 3537.8514 | 13.8729 | 40% |  | 40% |  | 40% | 2443.9925
90% | 0.1962% | 8.6188 |  |  |  |  | 20% | 3731.0305 | 11.0983 | 35% |  | 35% |  | 35% | 1071.8409
85% | 0.9135% | 40.1218 |  |  |  |  | 15% | 3910.2412 | 8.3237 | 30% |  | 30% |  | 30% | 105.5643
80% | 2.118% | 93.0231 |  |  |  |  | 10% | 4075.1864 | 5.5492 | 25% |  | 25% |  | 25%
75% | 4.486% | 197.0426 |  |  |  |  | 5% | 4251.7223 | 2.7746 | 20% |  | 20% |  | 20%
70% | 8.607% | 378.0365 |  |  |  |  | 9.992e-14% | 4391.7028 | 5.5447e-14 | 15% |  | 15% |  | 15%
65% | 14.03% | 616.0926 | [7 empty] | 10% |  | 10% |  | 10%
60% | 21.29% | 934.9866 | [7 empty] | 5% |  | 5% |  | 5%
55% | 29.85% | 1310.9428 | [7 empty] | 9.992e-14% |  | 9.992e-14% |  | 9.992e-14%
50% | 39.4% | 1730.2899 | [7 empty] | Total E@R | 0 | Total E@R | 2800.0998 | Total E@R | 36005.2501
45% | 49.36% | 2168.0633 | [7 empty] | Total WE@R | 0 | Total WE@R | 17.6048 | Total WE@R | 2.0658
40% | 59.42% | 2609.7004
35% | 68.26% | 2998.1389
30% | 75.35% | 3309.3057
25% | 80.55% | 3537.8514
20% | 84.95% | 3731.0305
15% | 89.03% | 3910.2412
10% | 92.79% | 4075.1864
5% | 96.81% | 4251.7223
9.992e-14% | 99.99% | 4391.7028
Ratings (MVA) |  |  |  | Option Capacity
SCR (N) | 55.8 |  |  | Year | 2031
SCR (N-1) | 35.3 |  |  | SCR (N) | 55.8
SCR (N-2) | 17.65 |  |  | SCR (N-1) | 35.3
WCR (N) | 56.8 |  |  | SCR (N-2) | 17.65
WCR (N-1) | 36.1 |  |  | WCR (N) | 56.8
WCR (N-2) | 18.05 |  |  | WCR (N-1) | 36.1
|  |  |  | WCR (N-2) | 18.05
Planned Works
Year | 2031
Capacity (N) | 0
Capacity (N-1) | 0
Capacity (N-2) | 0
Power Factor
Value | 0.99
End of Sheet

## QA
Overall Status
Good
Number | Check Name | Status | Info
1 | Forecast | Good | Confirms POE10 forecast is higher than POE50
2 | Option Maximum Demand | Good | Confirms whether transfers, embedded generation, and demand management contribute to demand reduction when present
3 | EUE Base Case | Good | Confirms Do Nothing/Base Case EUE for FY31 is the same as the example / checks model in Modelling Steps Example Sheet
4 | Feeder Consumption | Good | Confirms if aggregated feeder energy consumption by customer category matches with total feeder energy consumption (excluding uncategorised consumption)

## Output for AusNet's NPV model
Involuntary load shedding (NER 5.17.1(c)(4)(ii))
Base Case
Cost
Option 1 - Do Nothing | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Cost of EUE ($M) | 0.56397 | 1.3977 | 1.6041 | 1.8631 | 2.0883 | 2.3634 | 2.9252 | 4.5947 | 5.8437 | 5.3597 | 8.5062 | 8.8402 | 10.176 | 13.1375 | 13.8934 | 13.931 | 13.931 | 13.931 | 13.931 | 13.931 | 13.931 | 13.931 | 13.931 | 13.931 | 13.931 | 13.931 | 13.931 | 13.931 | 13.931 | 13.931
Total EUE (MWh) | 13.2448 | 32.8256 | 37.6731 | 43.7557 | 49.0447 | 55.5048 | 68.6979 | 107.9068 | 137.2388 | 125.8725 | 199.7693 | 207.6126 | 238.9842 | 308.5341 | 326.2872 | 327.1692 | 327.1692 | 327.1692 | 327.1692 | 327.1692 | 327.1692 | 327.1692 | 327.1692 | 327.1692 | 327.1692 | 327.1692 | 327.1692 | 327.1692 | 327.1692 | 327.1692
Residual Values
Option 2 - Replace 3 x 10/13.5 MVA Tx with 3 x 20/33 MVA Tx | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Cost of Avoided EUE ($M) | 0.56382 | 1.3977 | 1.6041 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.2754e-06 | 1.0018e-06 | 4.1678e-06 | 1.5165e-05 | 1.6032e-05 | 1.6259e-05 | 1.6259e-05 | 1.6259e-05 | 1.6259e-05 | 1.6259e-05 | 1.6259e-05 | 1.6259e-05 | 1.6259e-05 | 1.6259e-05 | 1.6259e-05 | 1.6259e-05 | 1.6259e-05 | 1.6259e-05 | 1.6259e-05 | 1.6259e-05
Total EUE (MWh) | 13.2414 | 32.8256 | 37.6731 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3439e-05 | 2.3528e-05 | 9.7881e-05 | 0.00035616 | 0.00037652 | 0.00038184 | 0.00038184 | 0.00038184 | 0.00038184 | 0.00038184 | 0.00038184 | 0.00038184 | 0.00038184 | 0.00038184 | 0.00038184 | 0.00038184 | 0.00038184 | 0.00038184 | 0.00038184 | 0.00038184
Option 3 - Replace 1 x 10/13.5 MVA Tx with 1 x 20/33 MVA Tx | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Cost of Avoided EUE ($M) | 0.56382 | 1.3977 | 1.6041 | 0.025289 | 0.029334 | 0.034415 | 0.044621 | 0.084439 | 0.12589 | 0.10527 | 0.25132 | 0.25216 | 0.32674 | 0.51333 | 0.55609 | 0.55686 | 0.55686 | 0.55686 | 0.55686 | 0.55686 | 0.55686 | 0.55686 | 0.55686 | 0.55686 | 0.55686 | 0.55686 | 0.55686 | 0.55686 | 0.55686 | 0.55686
Total EUE (MWh) | 13.2414 | 32.8256 | 37.6731 | 0.59392 | 0.68891 | 0.80824 | 1.0479 | 1.9831 | 2.9566 | 2.4722 | 5.9023 | 5.9219 | 7.6736 | 12.0556 | 13.0597 | 13.0778 | 13.0778 | 13.0778 | 13.0778 | 13.0778 | 13.0778 | 13.0778 | 13.0778 | 13.0778 | 13.0778 | 13.0778 | 13.0778 | 13.0778 | 13.0778 | 13.0778
Option 4 - Construct 2x 20/33MVA zone substation in Inverloch | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Cost of Avoided EUE ($M) | 0.56382 | 1.3977 | 1.6041 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total EUE (MWh) | 13.2414 | 32.8256 | 37.6731 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 - Contract network support services to defer network investment | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Cost of Avoided EUE ($M) | 0.20178 | 0.49986 | 0.58916 | 0.71288 | 0.80867 | 0.93148 | 1.2066 | 2.1415 | 2.8673 | 2.5256 | 4.4157 | 4.6075 | 5.3312 | 6.9525 | 7.4096 | 7.4297 | 7.4297 | 7.4297 | 7.4297 | 7.4297 | 7.4297 | 7.4297 | 7.4297 | 7.4297 | 7.4297 | 7.4297 | 7.4297 | 7.4297 | 7.4297 | 7.4297
Total EUE (MWh) | 4.7389 | 11.7393 | 13.8364 | 16.742 | 18.9916 | 21.876 | 28.3364 | 50.2933 | 67.3376 | 59.3142 | 103.7018 | 108.2072 | 125.2027 | 163.2788 | 174.0151 | 174.4877 | 174.4877 | 174.4877 | 174.4877 | 174.4877 | 174.4877 | 174.4877 | 174.4877 | 174.4877 | 174.4877 | 174.4877 | 174.4877 | 174.4877 | 174.4877 | 174.4877
Option 6 - | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Cost of Avoided EUE ($M) | 0.56382 | 1.3977 | 1.6041 | 1.8631 | 2.0883 | 2.3634 | 2.9252 | 4.5947 | 5.8437 | 5.3597 | 8.5062 | 8.8402 | 10.176 | 13.1375 | 13.8934 | 13.931 | 13.931 | 13.931 | 13.931 | 13.931 | 13.931 | 13.931 | 13.931 | 13.931 | 13.931 | 13.931 | 13.931 | 13.931 | 13.931 | 13.931
Total EUE (MWh) | 13.2414 | 32.8256 | 37.6731 | 43.7557 | 49.0447 | 55.5048 | 68.6979 | 107.9068 | 137.2388 | 125.8725 | 199.7693 | 207.6126 | 238.9842 | 308.5341 | 326.2872 | 327.1692 | 327.1692 | 327.1692 | 327.1692 | 327.1692 | 327.1692 | 327.1692 | 327.1692 | 327.1692 | 327.1692 | 327.1692 | 327.1692 | 327.1692 | 327.1692 | 327.1692
Option 7 - | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Cost of Avoided EUE ($M) | 0.56382 | 1.3977 | 1.6041 | 1.8631 | 2.0883 | 2.3634 | 2.9252 | 4.5947 | 5.8437 | 5.3597 | 8.5062 | 8.8402 | 10.176 | 13.1375 | 13.8934 | 13.931 | 13.931 | 13.931 | 13.931 | 13.931 | 13.931 | 13.931 | 13.931 | 13.931 | 13.931 | 13.931 | 13.931 | 13.931 | 13.931 | 13.931
Total EUE (MWh) | 13.2414 | 32.8256 | 37.6731 | 43.7557 | 49.0447 | 55.5048 | 68.6979 | 107.9068 | 137.2388 | 125.8725 | 199.7693 | 207.6126 | 238.9842 | 308.5341 | 326.2872 | 327.1692 | 327.1692 | 327.1692 | 327.1692 | 327.1692 | 327.1692 | 327.1692 | 327.1692 | 327.1692 | 327.1692 | 327.1692 | 327.1692 | 327.1692 | 327.1692 | 327.1692
Option 8 - | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Cost of Avoided EUE ($M) | 0.56382 | 1.3977 | 1.6041 | 1.8631 | 2.0883 | 2.3634 | 2.9252 | 4.5947 | 5.8437 | 5.3597 | 8.5062 | 8.8402 | 10.176 | 13.1375 | 13.8934 | 13.931 | 13.931 | 13.931 | 13.931 | 13.931 | 13.931 | 13.931 | 13.931 | 13.931 | 13.931 | 13.931 | 13.931 | 13.931 | 13.931 | 13.931
Total EUE (MWh) | 13.2414 | 32.8256 | 37.6731 | 43.7557 | 49.0447 | 55.5048 | 68.6979 | 107.9068 | 137.2388 | 125.8725 | 199.7693 | 207.6126 | 238.9842 | 308.5341 | 326.2872 | 327.1692 | 327.1692 | 327.1692 | 327.1692 | 327.1692 | 327.1692 | 327.1692 | 327.1692 | 327.1692 | 327.1692 | 327.1692 | 327.1692 | 327.1692 | 327.1692 | 327.1692

## Key Model Assumption & Inputs
Select ZSS & Region | WGI | East | MTTR
Probability Weighting for 10% POE MDs | 30% |  |  | Central | North | East | For Analysis
Probability Weighting for 50% POE MDs | 70% |  | N-1 MTTR (years) | 0.3858 | 0.1418 | 0.3858 | 0.3858
First year of analysis | FY25 |  | N-2 MTTR (years) | 0.2344 | 0.049 | 0.2344 | 0.2344
Select Sensitivity Variant | Forecast Sensitivity
High | 110% |  | PV Factor's |  |  | PoF Sensitvity
Options | Name |  | Summer | 1.33 |  | Varaint
Option 1 - Do Nothing | Do Nothing |  | Winter | 1.13 |  | Base | 100%
Option 2 - Replace 3 x 10/13.5 MVA Tx with 3 x 20/33 MVA Tx | Replace 3 x 10/13.5 MVA Tx with 3 x 20/33 MVA Tx
Option 3 - Replace 1 x 10/13.5 MVA Tx with 1 x 20/33 MVA Tx | Replace 1 x 10/13.5 MVA Tx with 1 x 20/33 MVA Tx |  | Demand Response
Option 4 - Construct 2x 20/33MVA zone substation in Inverloch | Construct 2x 20/33MVA zone substation in Inverloch |  | Average Rate % | 20%
Option 5 - Contract network support services to defer network investment | Contract network support services to defer network investment
Option 6 -
Option 7 -
Option 8 -
Added Capacity (MVA) | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39
Added Capacity (MVA) Option 1 N | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 1 N-1 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 1 N-2 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 2 N |  |  |  | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2
Added Capacity (MVA) Option 2 N-1 |  |  |  | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2
Added Capacity (MVA) Option 2 N-2 |  |  |  | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2
Added Capacity (MVA) Option 3 N |  |  |  | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35
Added Capacity (MVA) Option 3 N-1 |  |  |  | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35
Added Capacity (MVA) Option 3 N-2 |  |  |  | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35
Added Capacity (MVA) Option 4 N | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 4 N-1 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 4 N-2 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 5 N | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 5 N-1 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 5 N-2 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 6 N | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 6 N-1 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 6 N-2 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 7 N | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 7 N-1 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 7 N-2 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 8 N | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 8 N-1 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 8 N-2 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Embedded Generation (MVA) | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39
Avaliable Embedded Generation (MVA) Option 1 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11
Added Embedded Generation (MVA) Option 2 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Embedded Generation (MVA) Option 3 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Embedded Generation (MVA) Option 4 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Embedded Generation (MVA) Option 5 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Embedded Generation (MVA) Option 6 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Embedded Generation (MVA) Option 7 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Embedded Generation (MVA) Option 8 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Demand Management (MVA) | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39
Avaliable Demand Management (MVA) Option 1 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Demand Management (MVA) Option 2 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Demand Management (MVA) Option 3 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Demand Management (MVA) Option 4 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Demand Management (MVA) Option 5 | 4.0981 | 4.3758 | 4.3835 | 4.3752 | 4.3773 | 4.3925 | 4.4232 | 4.4774 | 4.5056 | 4.526 | 4.5569 | 4.5963 | 4.644 | 4.6689 | 4.6608
Added Demand Management (MVA) Option 6 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Demand Management (MVA) Option 7 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Demand Management (MVA) Option 8 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Transfers (MVA) | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39
Planned Transfers (MVA) Option 1 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Transfers (MVA) Option 2 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Transfers (MVA) Option 3 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Transfers (MVA) Option 4 |  |  |  | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66
Added Transfers (MVA) Option 5 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Transfers (MVA) Option 6 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Transfers (MVA) Option 7 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Transfers (MVA) Option 8 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Block Loads Not in Forecast (MVA) | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39
Block Loads (MVA) | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Base | FY25: 100%
High | FY25: 110%
Low | FY25: 90%

## Tx PoF
Transformer Failure Rates for individual Transformers
[5 empty] | 10 | 8 | 10 | 6 | 8 | 6 | 6 | 10 | 6
Zone | arm_asset_id | floc | user_status | Age | Major Winding insulation | Accelerated cellulose Aging | Winding insulating liquid | Hot metal fault covered by paper | Chemical contamination, degradation | Physical & chemical contamination, degradation | Physical contamination | Short Circuit Concern | OLTC | WMA Health Score | WMA CS | WMA effective age | WMA Beta | WMA Eta | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WGI | 30192717 | DS-WGI-TRNFMR-9000004493 |  | 59 | 5 | 3 | 1 | 5 | 2 | 1 | 5 | 5 | 5 | 351.4286 | 4 | 60 | 3.5 | 82 | 1.976% | 1.976% | 2.058% | 2.142% | 2.227% | 2.315% | 2.405% | 2.496% | 2.59% | 2.686% | 2.783% | 2.883% | 2.985% | 3.089% | 3.195% | 3.303% | 3.413% | 3.525% | 3.639% | 3.755% | 3.873% | 3.994% | 4.116% | 4.241% | 4.368% | 4.497% | 4.628% | 4.761% | 4.897% | 5.034%
WGI | 30111322 | DS-WGI-TRNFMR-9000003147 |  | 59 | 5 | 5 | 1 | 3 | 2 | 1 | 4 | 5 | 5 | 348.5714 | 3 | 44 | 3.5 | 82 | 0.9218% | 0.9218% | 0.9742% | 1.028% | 1.084% | 1.142% | 1.201% | 1.262% | 1.325% | 1.39% | 1.457% | 1.525% | 1.596% | 1.668% | 1.742% | 1.818% | 1.896% | 1.976% | 2.058% | 2.142% | 2.227% | 2.315% | 2.405% | 2.496% | 2.59% | 2.686% | 2.783% | 2.883% | 2.985% | 3.089%
EPG | 30026486 | DS-EPG-TRNFMR-9000010175 |  | 45 | 5 | 3 | 2 | 1 | 2 | 1 | 4 | 5 | 5 | 322.8571 | 3 | 44 | 3.5 | 84.05 | 0.8458% | 0.8458% | 0.8939% | 0.9436% | 0.9949% | 1.048% | 1.102% | 1.159% | 1.216% | 1.276% | 1.337% | 1.4% | 1.465% | 1.531% | 1.599% | 1.669% | 1.741% | 1.814% | 1.889% | 1.966% | 2.045% | 2.125% | 2.208% | 2.292% | 2.378% | 2.466% | 2.556% | 2.648% | 2.741% | 2.837%
EPG | 30058367 | DS-EPG-TRNFMR-9000010174 |  | 45 | 5 | 3 | 2 | 1 | 2 | 1 | 4 | 5 | 5 | 322.8571 | 3 | 44 | 3.5 | 84.05 | 0.8458% | 0.8458% | 0.8939% | 0.9436% | 0.9949% | 1.048% | 1.102% | 1.159% | 1.216% | 1.276% | 1.337% | 1.4% | 1.465% | 1.531% | 1.599% | 1.669% | 1.741% | 1.814% | 1.889% | 1.966% | 2.045% | 2.125% | 2.208% | 2.292% | 2.378% | 2.466% | 2.556% | 2.648% | 2.741% | 2.837%
WGI | 30475971 | DS-WGI-TRNFMR-9000007146 |  | 49 | 5 | 5 | 1 | 1 | 1 | 1 | 2 | 5 | 1 | 268.5714 | 3 | 44 | 3.5 | 82 | 0.9218% | 0.9218% | 0.9742% | 1.028% | 1.084% | 1.142% | 1.201% | 1.262% | 1.325% | 1.39% | 1.457% | 1.525% | 1.596% | 1.668% | 1.742% | 1.818% | 1.896% | 1.976% | 2.058% | 2.142% | 2.227% | 2.315% | 2.405% | 2.496% | 2.59% | 2.686% | 2.783% | 2.883% | 2.985% | 3.089%
EPG | 30209984 | DS-EPG-TRNFMR-9000007095 |  | 24 | 3 | 3 | 1 | 3 | 2 | 1 | 4 | 3 | 3 | 251.4286 | 3 | 44 | 3.5 | 84.05 | 0.8458% | 0.8458% | 0.8939% | 0.9436% | 0.9949% | 1.048% | 1.102% | 1.159% | 1.216% | 1.276% | 1.337% | 1.4% | 1.465% | 1.531% | 1.599% | 1.669% | 1.741% | 1.814% | 1.889% | 1.966% | 2.045% | 2.125% | 2.208% | 2.292% | 2.378% | 2.466% | 2.556% | 2.648% | 2.741% | 2.837%
CLN | 30338702 | DS-CLN-TRNFMR-9000006730 |  | 21 | 3 | 2 | 2 | 3 | 1 | 1 | 3 | 3 | 2 | 225.7143 | 2 | 24 | 3.5 | 84.05 | 0.1909% | 0.1909% | 0.211% | 0.2322% | 0.2547% | 0.2785% | 0.3035% | 0.3298% | 0.3575% | 0.3865% | 0.4168% | 0.4486% | 0.4817% | 0.5162% | 0.5522% | 0.5897% | 0.6286% | 0.669% | 0.7109% | 0.7543% | 0.7993% | 0.8458% | 0.8939% | 0.9436% | 0.9949% | 1.048% | 1.102% | 1.159% | 1.216% | 1.276%
CRE | 30165029 | DS-CRE-TRNFMR-9000525811 |  | 13 | 3 | 2 | 1 | 3 | 2 | 1 | 4 | 2 | 2 | 217.1429 | 2 | 24 | 3.5 | 84.05 | 0.1909% | 0.1909% | 0.211% | 0.2322% | 0.2547% | 0.2785% | 0.3035% | 0.3298% | 0.3575% | 0.3865% | 0.4168% | 0.4486% | 0.4817% | 0.5162% | 0.5522% | 0.5897% | 0.6286% | 0.669% | 0.7109% | 0.7543% | 0.7993% | 0.8458% | 0.8939% | 0.9436% | 0.9949% | 1.048% | 1.102% | 1.159% | 1.216% | 1.276%
LLG | 30359074 | DS-LLG-TRNFMR-9000007796 |  | 20 | 1 | 2 | 1 | 2 | 1 | 1 | 5 | 3 | 2 | 191.4286 | 2 | 24 | 3.5 | 84.05 | 0.1909% | 0.1909% | 0.211% | 0.2322% | 0.2547% | 0.2785% | 0.3035% | 0.3298% | 0.3575% | 0.3865% | 0.4168% | 0.4486% | 0.4817% | 0.5162% | 0.5522% | 0.5897% | 0.6286% | 0.669% | 0.7109% | 0.7543% | 0.7993% | 0.8458% | 0.8939% | 0.9436% | 0.9949% | 1.048% | 1.102% | 1.159% | 1.216% | 1.276%
CRE | 30380287 | DS-CRE-TRNFMR-9000525810 |  | 13 | 2 | 2 | 1 | 1 | 2 | 1 | 3 | 2 | 2 | 177.1429 | 2 | 24 | 3.5 | 84.05 | 0.1909% | 0.1909% | 0.211% | 0.2322% | 0.2547% | 0.2785% | 0.3035% | 0.3298% | 0.3575% | 0.3865% | 0.4168% | 0.4486% | 0.4817% | 0.5162% | 0.5522% | 0.5897% | 0.6286% | 0.669% | 0.7109% | 0.7543% | 0.7993% | 0.8458% | 0.8939% | 0.9436% | 0.9949% | 1.048% | 1.102% | 1.159% | 1.216% | 1.276%
CLN | 30000439 | DS-CLN-TRNFMR-9000001306 |  | 19 | 2 | 2 | 1 | 1 | 1 | 1 | 3 | 2 | 2 | 165.7143 | 2 | 24 | 3.5 | 84.05 | 0.1909% | 0.1909% | 0.211% | 0.2322% | 0.2547% | 0.2785% | 0.3035% | 0.3298% | 0.3575% | 0.3865% | 0.4168% | 0.4486% | 0.4817% | 0.5162% | 0.5522% | 0.5897% | 0.6286% | 0.669% | 0.7109% | 0.7543% | 0.7993% | 0.8458% | 0.8939% | 0.9436% | 0.9949% | 1.048% | 1.102% | 1.159% | 1.216% | 1.276%
OFR | 30035965 | DS-OFR-TRNFMR-9000014181 |  | 16 | 2 | 2 | 1 | 1 | 1 | 1 | 3 | 2 | 2 | 165.7143 | 2 | 24 | 3.5 | 84.05 | 0.1909% | 0.1909% | 0.211% | 0.2322% | 0.2547% | 0.2785% | 0.3035% | 0.3298% | 0.3575% | 0.3865% | 0.4168% | 0.4486% | 0.4817% | 0.5162% | 0.5522% | 0.5897% | 0.6286% | 0.669% | 0.7109% | 0.7543% | 0.7993% | 0.8458% | 0.8939% | 0.9436% | 0.9949% | 1.048% | 1.102% | 1.159% | 1.216% | 1.276%
KLO | 30002764 | DS-KLO-TRNFMR-9000412348 |  | 15 | 1 | 2 | 1 | 1 | 1 | 1 | 4 | 2 | 2 | 160 | 2 | 24 | 3.5 | 84.05 | 0.1909% | 0.1909% | 0.211% | 0.2322% | 0.2547% | 0.2785% | 0.3035% | 0.3298% | 0.3575% | 0.3865% | 0.4168% | 0.4486% | 0.4817% | 0.5162% | 0.5522% | 0.5897% | 0.6286% | 0.669% | 0.7109% | 0.7543% | 0.7993% | 0.8458% | 0.8939% | 0.9436% | 0.9949% | 1.048% | 1.102% | 1.159% | 1.216% | 1.276%
OFR | 30221642 | DS-OFR-TRNFMR-9000016122 |  | 16 | 1 | 2 | 1 | 1 | 1 | 1 | 3 | 2 | 2 | 151.4286 | 2 | 24 | 3.5 | 84.05 | 0.1909% | 0.1909% | 0.211% | 0.2322% | 0.2547% | 0.2785% | 0.3035% | 0.3298% | 0.3575% | 0.3865% | 0.4168% | 0.4486% | 0.4817% | 0.5162% | 0.5522% | 0.5897% | 0.6286% | 0.669% | 0.7109% | 0.7543% | 0.7993% | 0.8458% | 0.8939% | 0.9436% | 0.9949% | 1.048% | 1.102% | 1.159% | 1.216% | 1.276%
KLO | 30208816 | DS-KLO-TRNFMR-9000412347 |  | 15 | 1 | 2 | 1 | 1 | 1 | 1 | 3 | 2 | 2 | 151.4286 | 2 | 24 | 3.5 | 84.05 | 0.1909% | 0.1909% | 0.211% | 0.2322% | 0.2547% | 0.2785% | 0.3035% | 0.3298% | 0.3575% | 0.3865% | 0.4168% | 0.4486% | 0.4817% | 0.5162% | 0.5522% | 0.5897% | 0.6286% | 0.669% | 0.7109% | 0.7543% | 0.7993% | 0.8458% | 0.8939% | 0.9436% | 0.9949% | 1.048% | 1.102% | 1.159% | 1.216% | 1.276%
PHM | 32944656 | DS-PHM-TRNFMR-9000004393 |  | 8 | 2 | 2 | 1 | 1 | 1 | 1 | 3 | 1 | 1 | 142.8571 | 1 | 8 | 3.5 | 84.05 | 0.01357% | 0.01357% | 0.01791% | 0.023% | 0.02887% | 0.03555% | 0.04308% | 0.0515% | 0.06084% | 0.07112% | 0.08238% | 0.09465% | 0.1079% | 0.1223% | 0.1378% | 0.1543% | 0.172% | 0.1909% | 0.211% | 0.2322% | 0.2547% | 0.2785% | 0.3035% | 0.3298% | 0.3575% | 0.3865% | 0.4168% | 0.4486% | 0.4817% | 0.5162%
PHM | 32944654 | DS-PHM-TRNFMR-9000007050 |  | 8 | 2 | 2 | 1 | 1 | 1 | 1 | 3 | 1 | 1 | 142.8571 | 1 | 8 | 3.5 | 84.05 | 0.01357% | 0.01357% | 0.01791% | 0.023% | 0.02887% | 0.03555% | 0.04308% | 0.0515% | 0.06084% | 0.07112% | 0.08238% | 0.09465% | 0.1079% | 0.1223% | 0.1378% | 0.1543% | 0.172% | 0.1909% | 0.211% | 0.2322% | 0.2547% | 0.2785% | 0.3035% | 0.3298% | 0.3575% | 0.3865% | 0.4168% | 0.4486% | 0.4817% | 0.5162%

## AER VCR Rates(2024)
Category | Rate | Notes
Dec 24 AER VCR ($/kWh) - Res | 49.23 | Vic Av Res
Dec 24 AER VCR ($/kWh) - Com | 34.39 | Vic Av Com
Dec 24 AER VCR ($/kWh) - Ind | 33.49 | Vic Av Ind
Dec 24 AER VCR ($/kWh) - Agr | 22.25 | Vic Av Agr

## Customer No. and Vol per Feeder
CUSTOMER_CLASS | Feeder | VOL | CUST_NO | ZSS | Customer mix received from AusNet Financial Planning & Strategy on 25/7/2025
COMMERCIAL | bra11 | 9860526.7854 | 168 | bra
COMMERCIAL | bge13 | 654988.62 | 45 | bge
COMMERCIAL | phi11 | 1878610.03 | 37 | phi
NCONUML | moe11 | 47447.48 | 18 | moe
NCONUML | drn13 | 27414.73 | 17 | drn
COMMERCIAL | smg34 | 5224461.8 | 1 | smg
FARM | wgl13 | 901266.5312 | 97 | wgl
FARM | msd2 | 2808295.5668 | 471 | msd
NCONUML | elm34 | 86758.8 | 34 | elm
| rwt36 | 703.54 | 2 | rwt
COMMERCIAL | lga41 | 1099100.22 | 2 | lga
| bdl33 | 4298.82 | 8 | bdl
NCONUML | smr14 | 27225.34 | 18 | smr
COMMERCIAL | cln24 | 4484028.8333 | 290 | cln
RESIDENTL | ofr14 | 13024383.6958 | 3554 | ofr
NCONUML | bdl43 | 100361.9983 | 38 | bdl
| ofr22 | 16469.09 | 22 | ofr
NCONUML | rwn33 | 8721.79 | 7 | rwn
LIGHTING | hpk12 | 342838 | 1 | hpk
COMMERCIAL | bra23 | 6262297.01 | 84 | bra
FARM | tt1 | 1865.76 | 1 | tt
LIGHTING | mfa14 | 787800.53 | 1 | mfa
RESIDENTL | brt22 | 9968534.1043 | 1376 | brt
RESIDENTL | mwl25 | 4092575.372 | 493 | mwl
NCONUML | wgi22 | 83961.44 | 23 | wgi
INDUSTRIAL | ldl22 | 4379901.5885 | 45 | ldl
RESIDENTL | phm22 | 3628742.5283 | 796 | phm
FARM | mfa23 | 2691321.6324 | 201 | mfa
NCONUML | rwn32 | 60415.37 | 23 | rwn
FARM | cre22 | 55644.16 | 17 | cre
RESIDENTL | elm24 | 17367685.5307 | 2999 | elm
COMMERCIAL | tt9 | 7181168.3052 | 213 | tt
COMMERCIAL | kms12 | 15257134.8455 | 395 | kms
NCONUML | cyn31 | 24759.23 | 14 | cyn
| llg12 | 26420.7189 | 15 | llg
LIGHTING | ruba22 | 247422.69 | 1 | ruba
RESIDENTL | wt12 | 10803758.701 | 2579 | wt
COMMERCIAL | bwn14 | 6975240.1 | 156 | bwn
NCONUML | bge12 | 37366.03 | 11 | bge
NCONUML | rwn24 | 30489.76 | 21 | rwn
FARM | sfs1 | 113380.09 | 9 | sfs
| bwr13 | 80076.52 | 46 | bwr
FARM | wt13 | 37228.86 | 3 | wt
FARM | cre23 | 226478.55 | 9 | cre
COMMERCIAL | rwn22 | 1886562.0146 | 72 | rwn
| tgn23 | 13898.1302 | 15 | tgn
FARM | ldl22 | 7887.95 | 1 | ldl
RESIDENTL | fgy21 | 7153989.4877 | 1047 | fgy
FARM | mjg11 | 735019.886 | 74 | mjg
| ldl14 | 17432.2687 | 11 | ldl
INDUSTRIAL | ldl24 | 64751.4 | 12 | ldl
| sle13 | 253.3245 | 2 | sle
FARM | moe21 | 6301170.9744 | 504 | moe
FARM | bge23 | 671977.1074 | 66 | bge
RESIDENTL | elm32 | 19949095.4752 | 2463 | elm
COMMERCIAL | ftr12 | 1975462.7263 | 113 | ftr
RESIDENTL | lyd12 | 6657897.88 | 1592 | lyd
RESIDENTL | epg31 | 11862355.3417 | 3027 | epg
NCONUML | ofr11 | 57102.89 | 18 | ofr
FARM | moe11 | 65350.2807 | 7 | moe
FARM | nla32 | 1181128.1259 | 84 | nla
FARM | smr24 | 4141783.4574 | 392 | smr
RESIDENTL | fgy13 | 7970231.1446 | 1518 | fgy
FARM | bdl41 | 1305847.5951 | 258 | bdl
NCONUML | elm23 | 62172.37 | 40 | elm
| elm22 | 20617.5429 | 26 | elm
NCONUML | cre21 | 58240.1 | 18 | cre
FARM | phm32 | 50851.13 | 8 | phm
INDUSTRIAL | lga21 | 208132.02 | 16 | lga
INDUSTRIAL | nrn13 | 39703.59 | 6 | nrn
RESIDENTL | hpk22 | 18949862.0449 | 4569 | hpk
NCONUML | cyn13 | 17637.49 | 6 | cyn
COMMERCIAL | cre31 | 14851829.6913 | 363 | cre
COMMERCIAL | epg32 | 5001490.9226 | 156 | epg
| phm32 | 41386.12 | 47 | phm
NCONUML | wo33 | 6875.31 | 2 | wo
FARM | wgl21 | 5056187.7677 | 366 | wgl
INDUSTRIAL | cre22 | 240829.25 | 4 | cre
RESIDENTL | wgi34 | 3671110.7601 | 570 | wgi
INDUSTRIAL | ldl12 | 10352583.7 | 7 | ldl
INDUSTRIAL | wyk12 | 149433.7 | 6 | wyk
INDUSTRIAL | cyn14 | 23200.151 | 3 | cyn
| wo11 | 4136.2425 | 3 | wo
| msd4 | 20521.76 | 37 | msd
FARM | mby12 | 52034.88 | 19 | mby
COMMERCIAL | rwt22 | 7145877.6761 | 143 | rwt
COMMERCIAL | wo12 | 23719023.8 | 1 | wo
RESIDENTL | wn2 | 17414453.5902 | 3500 | wn
COMMERCIAL | wots25 | 3483725.2811 | 72 | wots
RESIDENTL | bwr33 | 46024.67 | 2 | bwr
RESIDENTL | wn3 | 12349888.6736 | 2099 | wn
RESIDENTL | bn24 | 2992797.8263 | 559 | bn
| bra21 | 41455.7142 | 65 | bra
INDUSTRIAL | hpk14 | 16381.88 | 4 | hpk
RESIDENTL | epg32 | 14811809.1158 | 3829 | epg
COMMERCIAL | cln14 | 10141314.5039 | 129 | cln
FARM | smg31 | 14995.46 | 5 | smg
INDUSTRIAL | drn22 | 2117102.6666 | 12 | drn
NCONUML | drn12 | 43785.8374 | 16 | drn
INDUSTRIAL | fgy34 | 128392.6893 | 5 | fgy
NCONUML | fgy31 | 6707.46 | 4 | fgy
| wt8 | 7059.0655 | 13 | wt
| bwn12 | 6521.57 | 6 | bwn
COMMERCIAL | myt12 | 10774273.2986 | 307 | myt
COMMERCIAL | ldl21 | 5339830.9491 | 117 | ldl
| cln21 | 32425.72 | 66 | cln
INDUSTRIAL | fgy14 | 162921.94 | 7 | fgy
| tgn12 | 22490.11 | 3 | tgn
COMMERCIAL | epg12 | 8214339.5389 | 163 | epg
NCONUML | moe23 | 69334.91 | 17 | moe
FARM | cyn14 | 7715.15 | 1 | cyn
RESIDENTL | lyd14 | 10580841.4317 | 1203 | lyd
COMMERCIAL | smg23 | 21963007.1063 | 434 | smg
INDUSTRIAL | bra33 | 2076536.62 | 34 | bra
INDUSTRIAL | rwt14 | 2271244.55 | 44 | rwt
COMMERCIAL | lga14 | 2174194.9787 | 115 | lga
INDUSTRIAL | myt22 | 3176.32 | 3 | myt
FARM | cyn21 | 10230.57 | 2 | cyn
| klo24 | 65411.35 | 119 | klo
COMMERCIAL | brt21 | 6571769.7252 | 216 | brt
FARM | kms11 | 665243.0597 | 75 | kms
| elm34 | 25999.6869 | 33 | elm
INDUSTRIAL | mwl11 | 366139.79 | 15 | mwl
INDUSTRIAL | lyd14 | 80895.88 | 12 | lyd
LIGHTING | cpk11 | 1086.88 | 1 | cpk
NCONUML | fgy23 | 34402.31 | 12 | fgy
| bra32 | 15753.982 | 22 | bra
RESIDENTL | epg12 | 26391788.5687 | 6905 | epg
COMMERCIAL | cyn24 | 15647575.1097 | 304 | cyn
INDUSTRIAL | phm21 | 511727.73 | 19 | phm
NCONUML | ftr12 | 5424.58 | 5 | ftr
| bwa23 | 5447.575 | 8 | bwa
NCONUML | llg12 | 4182.92 | 3 | llg
COMMERCIAL | drn13 | 5299129.684 | 96 | drn
INDUSTRIAL | hpk21 | 31624.71 | 8 | hpk
INDUSTRIAL | wyk23 | 1500537.4334 | 28 | wyk
RESIDENTL | lga12 | 4152631.2896 | 644 | lga
RESIDENTL | cyn11 | 6009338.551 | 1440 | cyn
NCONUML | fgy24 | 70027.41 | 43 | fgy
| moe23 | 74726.3012 | 22 | moe
COMMERCIAL | elm24 | 3531802.26 | 46 | elm
LIGHTING | elm33 | 1000.47 | 1 | elm
RESIDENTL | smg23 | 6500499.5996 | 1411 | smg
FARM | msd4 | 1851245.0012 | 252 | msd
COMMERCIAL | lga24 | 21693950.3379 | 92 | lga
COMMERCIAL | ldl11 | 7360578.73 | 74 | ldl
NCONUML | rve13 | 29515.6981 | 24 | rve
COMMERCIAL | trc01 | 365242.5067 | 42 | trc
COMMERCIAL | wt15 | 1164715.6471 | 30 | wt
COMMERCIAL | bra14 | 811059.401 | 59 | bra
| ftr21 | 17034.7542 | 20 | ftr
RESIDENTL | bra23 | 7643359.408 | 1736 | bra
INDUSTRIAL | cpk11 | 59065.36 | 14 | cpk
INDUSTRIAL | hpk12 | 531460.54 | 46 | hpk
FARM | fgy23 | 137430.23 | 3 | fgy
INDUSTRIAL | tt4 | 77015.1997 | 16 | tt
FARM | cpk22 | 45399.86 | 6 | cpk
INDUSTRIAL | yn31 | 1004932.7745 | 6 | yn
FARM | myt22 | 1873055.6433 | 191 | myt
| cpk12 | 20188.43 | 32 | cpk
RESIDENTL | bwa22 | 6606654.3694 | 1106 | bwa
| mfa34 | 1434.55 | 6 | mfa
| nla31 | 4780.58 | 5 | nla
FARM | mdg1 | 36782.2 | 6 | mdg
RESIDENTL | mwl21 | 3605605.4081 | 859 | mwl
COMMERCIAL | phm33 | 14452041.4603 | 180 | phm
INDUSTRIAL | ofr23 | 154535.41 | 17 | ofr
INDUSTRIAL | elm21 | 177435.466 | 7 | elm
INDUSTRIAL | wt5 | 89.11 | 1 | wt
FARM | llg13 | 1917532.2118 | 152 | llg
INDUSTRIAL | klk21 | 41156.68 | 10 | klk
NCONUML | wt9 | 48247.64 | 17 | wt
FARM | mdi1 | 153288.2952 | 21 | mdi
INDUSTRIAL | nrn14 | 19245.31 | 5 | nrn
INDUSTRIAL | wgl12 | 500659.11 | 16 | wgl
FARM | fgy13 | 80534.51 | 6 | fgy
INDUSTRIAL | bwr14 | 1597974.48 | 1 | bwr
LIGHTING | bn11 | 103048.5 | 1 | bn
RESIDENTL | klo14 | 40411755.0117 | 10946 | klo
RESIDENTL | fgy33 | 9101921.8028 | 1763 | fgy
LIGHTING | cre31 | 2308168.51 | 1 | cre
RESIDENTL | wn5 | 8555201.9981 | 1156 | wn
COMMERCIAL | mfa22 | 5299491.9938 | 179 | mfa
COMMERCIAL | lyd11 | 3798691.89 | 62 | lyd
LIGHTING | bn24 | 2014.81 | 1 | bn
COMMERCIAL | cf1 | 9360587.4941 | 189 | cf
FARM | lga11 | 4665290.6529 | 555 | lga
RESIDENTL | lyd13 | 10895753.2364 | 2051 | lyd
NCONUML | cre33 | 35388.67 | 19 | cre
| smg32 | 685.05 | 3 | smg
INDUSTRIAL | cyn11 | 1966971.1028 | 55 | cyn
COMMERCIAL | wn2 | 10157994.9798 | 156 | wn
| phm21 | 32464.7212 | 22 | phm
| sfs1 | 13890.635 | 10 | sfs
NCONUML | tt12 | 15011.94 | 8 | tt
FARM | lga21 | 1065599.6961 | 147 | lga
| ldl12 | 52350.63 | 6 | ldl
INDUSTRIAL | smg31 | 231921 | 9 | smg
LIGHTING | myt12 | 813470.88 | 6 | myt
| smr24 | 66801.9 | 34 | smr
NCONUML | cre32 | 49453.4427 | 23 | cre
INDUSTRIAL | bdl44 | 2337630.2078 | 41 | bdl
| rve11 | 302066.1 | 12 | rve
FARM | wo31 | 3245.01 | 1 | wo
LIGHTING | ofr13 | 171706.2 | 2 | ofr
RESIDENTL | tt9 | 13181645.445 | 3553 | tt
COMMERCIAL | wgl11 | 13522117.9742 | 216 | wgl
COMMERCIAL | hpk24 | 15242696.9791 | 271 | hpk
COMMERCIAL | bwr34 | 12222544.1423 | 437 | bwr
NCONUML | nla34 | 19980.17 | 11 | nla
FARM | bwr24 | 9303.26 | 1 | bwr
| wgi23 | 15962.8799 | 36 | wgi
RESIDENTL | cln13 | 18593732.5659 | 6830 | cln
RESIDENTL | lga13 | 1879247.7046 | 295 | lga
RESIDENTL | cnr3 | 108696.4186 | 22 | cnr
| wgl12 | 112644.3661 | 43 | wgl
COMMERCIAL | cln12 | 8203266.5202 | 86 | cln
NCONUML | ofr21 | 100427.35 | 34 | ofr
RESIDENTL | drn24 | 10021102.8231 | 2473 | drn
COMMERCIAL | cyn31 | 1940881.6507 | 53 | cyn
NCONUML | ldl24 | 34534.3 | 19 | ldl
COMMERCIAL | ofr13 | 9302944.2987 | 197 | ofr
| wots13 | 58538.6484 | 32 | wots
| cpk23 | 23360.0808 | 24 | cpk
NCONUML | cln11 | 4587.8606 | 9 | cln
| wt15 | 51811.4 | 11 | wt
COMMERCIAL | epg24 | 26841528 | 1 | epg
FARM | drn22 | 329138.5031 | 52 | drn
| mfa31 | 16838.31 | 22 | mfa
COMMERCIAL | bra32 | 4055727.3404 | 158 | bra
COMMERCIAL | cpk21 | 14974774.5549 | 258 | cpk
INDUSTRIAL | myt21 | 335981.9667 | 19 | myt
FARM | nrn14 | 139044.47 | 14 | nrn
| wt5 | 22324.85 | 13 | wt
INDUSTRIAL | mfa23 | 139940.33 | 14 | mfa
FARM | wyk12 | 2634438.6357 | 233 | wyk
RESIDENTL | epg23 | 3653084.6682 | 932 | epg
COMMERCIAL | tgn11 | 2525258.71 | 85 | tgn
| wt13 | 22551.0062 | 37 | wt
| cyn13 | 10533.28 | 7 | cyn
INDUSTRIAL | fgy13 | 259435.94 | 2 | fgy
RESIDENTL | cln12 | 23908773.0216 | 6775 | cln
COMMERCIAL | brt22 | 9042592.2197 | 210 | brt
COMMERCIAL | rwt25 | 7526054.6961 | 146 | rwt
FARM | mfa31 | 218040.8355 | 21 | mfa
COMMERCIAL | cln22 | 3248277.4443 | 37 | cln
NCONUML | bdl33 | 22970.8 | 8 | bdl
COMMERCIAL | fgy12 | 74427.591 | 4 | fgy
RESIDENTL | mwl16 | 8188909.2298 | 1700 | mwl
INDUSTRIAL | moe25 | 612177.9824 | 16 | moe
COMMERCIAL | tt7 | 24970154.3491 | 341 | tt
INDUSTRIAL | bwr24 | 4118148.7987 | 125 | bwr
RESIDENTL | moe13 | 2791200.4315 | 357 | moe
FARM | wyk24 | 694188.3378 | 94 | wyk
NCONUML | wo14 | 36996.26 | 12 | wo
RESIDENTL | bra13 | 6470560.8911 | 1572 | bra
RESIDENTL | tt7 | 39398.92 | 9 | tt
FARM | epg34 | 15821.91 | 5 | epg
INDUSTRIAL | yn35 | 6582.38 | 2 | yn
NCONUML | bwa23 | 749.23 | 1 | bwa
FARM | sle13 | 1461316.56 | 213 | sle
COMMERCIAL | cpk13 | 4127340.5971 | 198 | cpk
INDUSTRIAL | ldl14 | 1064067.7426 | 16 | ldl
| rwt14 | 62105.3312 | 18 | rwt
LIGHTING | hpk13 | 14513.85 | 1 | hpk
RESIDENTL | klk22 | 940238.19 | 128 | klk
COMMERCIAL | mwl25 | 259300.06 | 16 | mwl
| mjg11 | 96977.3135 | 7 | mjg
RESIDENTL | hpk24 | 4867180.3451 | 1284 | hpk
FARM | ftr21 | 6703423.0704 | 705 | ftr
FARM | smr12 | 441800.25 | 44 | smr
FARM | bwr13 | 73574.54 | 13 | bwr
| ldl22 | 9241.11 | 9 | ldl
FARM | wo22 | 35676.335 | 7 | wo
NCONUML | moe12 | 9318.9 | 3 | moe
INDUSTRIAL | bdl31 | 1561951.6978 | 44 | bdl
COMMERCIAL | ofr14 | 8393968.2568 | 77 | ofr
NCONUML | tgn23 | 48562.71 | 16 | tgn
NCONUML | cyn21 | 25127.29 | 5 | cyn
FARM | phm34 | 22945.58 | 3 | phm
INDUSTRIAL | cyn33 | 36519.92 | 4 | cyn
LIGHTING | bm8b32 | 1070.04 | 1 | bmb
FARM | llg12 | 5311057.9488 | 488 | llg
NCONUML | rwt32 | 94072.85 | 46 | rwt
COMMERCIAL | myt11 | 912988.53 | 42 | myt
INDUSTRIAL | cpk22 | 129954.91 | 11 | cpk
| cre22 | 20388.051 | 33 | cre
RESIDENTL | ldl21 | 5451727.7741 | 1502 | ldl
FARM | bdl44 | 8189534.7866 | 736 | bdl
INDUSTRIAL | bn11 | 1899511.3657 | 45 | bn
INDUSTRIAL | wgi31 | 152399.6 | 19 | wgi
INDUSTRIAL | mdi1 | 16.0426 | 1 | mdi
| ofr11 | 90492.4817 | 79 | ofr
LIGHTING | kms11 | 547479.19 | 1 | kms
RESIDENTL | phi12 | 18738852.0082 | 4967 | phi
COMMERCIAL | bwr12 | 7897915.6022 | 287 | bwr
FARM | msd1 | 2520603.4144 | 354 | msd
COMMERCIAL | tgn44 | 4662112.18 | 89 | tgn
NCONUML | uwy1 | 29815.85 | 15 | uwy
NCONUML | lga22 | 54192.29 | 17 | lga
NCONUML | lga23 | 17186.13 | 6 | lga
INDUSTRIAL | hpk13 | 1952010.47 | 3 | hpk
FARM | drn23 | 391232.6382 | 58 | drn
FARM | ldl23 | 5910515.5529 | 453 | ldl
FARM | bdl31 | 55336.85 | 12 | bdl
RESIDENTL | bwr34 | 11176240.016 | 2984 | bwr
RESIDENTL | ofr13 | 5689359.8131 | 1445 | ofr
NCONUML | bra21 | 145563.002 | 72 | bra
COMMERCIAL | cf2 | 1114027.3697 | 138 | cf
RESIDENTL | bdl32 | 16368580.902 | 3124 | bdl
COMMERCIAL | smr22 | 10240657.5236 | 95 | smr
NCONUML | rve12 | 34563.18 | 21 | rve
COMMERCIAL | cnr3 | 208527.63 | 11 | cnr
| elm25 | 9741.0155 | 15 | elm
INDUSTRIAL | lyd13 | 30651.21 | 5 | lyd
INDUSTRIAL | mby12 | 279353.09 | 7 | mby
INDUSTRIAL | epg21 | 31298.6803 | 2 | epg
FARM | wgl12 | 7817936.5802 | 624 | wgl
COMMERCIAL | moe13 | 1401894.0174 | 82 | moe
RESIDENTL | lga14 | 7239522.4699 | 1158 | lga
RESIDENTL | epg35 | 308209.78 | 22 | epg
FARM | hpk14 | 29274.39 | 5 | hpk
LIGHTING | bn22 | 341591.58 | 1 | bn
NCONUML | bge11 | 85890.46 | 45 | bge
NCONUML | wt7 | 26985.19 | 18 | wt
| wo31 | 27869.149 | 41 | wo
INDUSTRIAL | elm32 | 759094.4258 | 68 | elm
NCONUML | cre23 | 95638.5 | 25 | cre
RESIDENTL | cln23 | 19292170.1488 | 4992 | cln
| lga21 | 17263.28 | 18 | lga
NCONUML | bwn12 | 35975.24 | 12 | bwn
| fgy31 | 1671.76 | 6 | fgy
NCONUML | ftr23 | 39743.6852 | 30 | ftr
NCONUML | smg21 | 9405.11 | 5 | smg
RESIDENTL | epg13 | 24819451.0174 | 7299 | epg
RESIDENTL | ruba22 | 5955886.59 | 1080 | ruba
INDUSTRIAL | bwr23 | 1917390.4058 | 110 | bwr
COMMERCIAL | bn23 | 4585306.9 | 117 | bn
| fgy24 | 60212.15 | 95 | fgy
LIGHTING | brt21 | 27441.26 | 1 | brt
COMMERCIAL | mby14 | 13812.56 | 3 | mby
RESIDENTL | drn21 | 15235611.8074 | 3585 | drn
RESIDENTL | nrn11 | 3368324.1063 | 703 | nrn
NCONUML | cln21 | 97183.1897 | 28 | cln
NCONUML | tgn12 | 26909.78 | 9 | tgn
FARM | moe22 | 48531.59 | 7 | moe
RESIDENTL | bra14 | 17287022.2386 | 4193 | bra
RESIDENTL | brt21 | 8587133.8204 | 1368 | brt
INDUSTRIAL | ldl23 | 2181365.61 | 45 | ldl
NCONUML | klo24 | 121410.57 | 41 | klo
INDUSTRIAL | wt8 | 22231.36 | 5 | wt
| bdl41 | 27628.4721 | 32 | bdl
COMMERCIAL | sle14 | 13227565.7623 | 343 | sle
| smr14 | 17300.3116 | 19 | smr
INDUSTRIAL | llg11 | 439641.21 | 9 | llg
| wgi22 | 13903.1 | 35 | wgi
NCONUML | moe22 | 34069.45 | 10 | moe
| ftr12 | 15921.46 | 17 | ftr
COMMERCIAL | epg11 | 902129.45 | 16 | epg
RESIDENTL | cpk13 | 21255549.7429 | 4974 | cpk
| fgy23 | 9273.25 | 10 | fgy
FARM | cyn12 | 9105.46 | 2 | cyn
INDUSTRIAL | rwn31 | 527467.66 | 22 | rwn
RESIDENTL | bm8b32 | 357081.227 | 62 | bmb
FARM | ruba22 | 1060033.1321 | 158 | ruba
INDUSTRIAL | cnr1 | 88077.93 | 3 | cnr
FARM | cpk12 | 972803.9358 | 91 | cpk
COMMERCIAL | wo14 | 14658340.7796 | 304 | wo
COMMERCIAL | tt5 | 6134357.4395 | 224 | tt
INDUSTRIAL | wo11 | 18559582.74 | 7 | wo
| wgl23 | 17798.7289 | 12 | wgl
NCONUML | cyn12 | 64730.9 | 21 | cyn
COMMERCIAL | bwr33 | 3515549.759 | 83 | bwr
COMMERCIAL | cyn22 | 10287381.4837 | 183 | cyn
COMMERCIAL | rwt32 | 5482054.6843 | 198 | rwt
INDUSTRIAL | nrn12 | 7260.73 | 2 | nrn
RESIDENTL | cln22 | 8137131.1146 | 3340 | cln
| kms12 | 36774.1343 | 44 | kms
| cyn24 | 12784.0842 | 11 | cyn
| smg33 | 11524.64 | 21 | smg
COMMERCIAL | rve11 | 18192998.0721 | 274 | rve
FARM | wt5 | 8146.48 | 2 | wt
INDUSTRIAL | bge23 | 983662.8538 | 7 | bge
| msd2 | 9983.6 | 13 | msd
| bra12 | 98134.87 | 2 | bra
RESIDENTL | hpk23 | 13762355.5073 | 3377 | hpk
COMMERCIAL | smr13 | 15057236.7589 | 394 | smr
INDUSTRIAL | rwt21 | 372221.49 | 45 | rwt
FARM | rve12 | 22362.86 | 5 | rve
NCONUML | fgy32 | 32042.28 | 18 | fgy
INDUSTRIAL | smr12 | 37387308.69 | 3 | smr
NCONUML | mfa34 | 19451.19 | 8 | mfa
FARM | wots13 | 4844280.0942 | 510 | wots
COMMERCIAL | drn21 | 3220798.94 | 52 | drn
INDUSTRIAL | wo31 | 765.77 | 1 | wo
| fgy32 | 8528.5063 | 10 | fgy
INDUSTRIAL | bwr32 | 3058614 | 72 | bwr
| elm23 | 20831.6 | 30 | elm
INDUSTRIAL | mwl12 | 574569.29 | 12 | mwl
RESIDENTL | cpk21 | 7771248.352 | 1679 | cpk
COMMERCIAL | wots11 | 6621581.9604 | 243 | wots
INDUSTRIAL | ftr21 | 313604.8 | 24 | ftr
NCONUML | lyd11 | 43059.75 | 9 | lyd
FARM | phm21 | 25361.56 | 3 | phm
INDUSTRIAL | wyk13 | 453974.55 | 15 | wyk
INDUSTRIAL | mdg1 | 21781.42 | 1 | mdg
INDUSTRIAL | tt1 | 7434378.9861 | 77 | tt
INDUSTRIAL | wgi34 | 1206209.57 | 8 | wgi
LIGHTING | wgi33 | 1050486.0487 | 2 | wgi
COMMERCIAL | wgl15 | 27996457.3831 | 596 | wgl
RESIDENTL | bge23 | 16900476.9279 | 2094 | bge
INDUSTRIAL | bwr13 | 2417661.2776 | 147 | bwr
NCONUML | epg23 | 28250.73 | 7 | epg
INDUSTRIAL | drn14 | 25996.95 | 2 | drn
RESIDENTL | drn14 | 23831050.9741 | 4399 | drn
RESIDENTL | rwt31 | 5842296.4371 | 1436 | rwt
COMMERCIAL | drn24 | 1717660.9 | 35 | drn
FARM | epg14 | 3614.72 | 1 | epg
RESIDENTL | smr13 | 11225814.5464 | 2447 | smr
COMMERCIAL | wots12 | 14359758.4732 | 371 | wots
COMMERCIAL | klk11 | 3080934.4269 | 114 | klk
NCONUML | mwl14 | 31252.61 | 13 | mwl
INDUSTRIAL | sle11 | 266690.1 | 32 | sle
NCONUML | epg31 | 41319.36 | 24 | epg
RESIDENTL | cf1 | 4176161.3871 | 493 | cf
INDUSTRIAL | phm34 | 816155.12 | 6 | phm
FARM | rwn34 | 20402.21 | 4 | rwn
| mby12 | 1524.95 | 3 | mby
RESIDENTL | wgi31 | 14866992.8529 | 3617 | wgi
RESIDENTL | wots25 | 16858284.9544 | 3532 | wots
RESIDENTL | cre33 | 21876811.5892 | 4235 | cre
RESIDENTL | fgy34 | 4606270.9018 | 975 | fgy
RESIDENTL | cyn32 | 15011504.2579 | 3573 | cyn
RESIDENTL | klk11 | 9194980.7775 | 1227 | klk
INDUSTRIAL | fgy33 | 1452360.19 | 13 | fgy
INDUSTRIAL | wgl13 | 6688610.4344 | 14 | wgl
| tgn41 | 12751.16 | 13 | tgn
COMMERCIAL | klk22 | 85830.78 | 8 | klk
| mby11 | 4292.69 | 12 | mby
FARM | drn12 | 9939.61 | 1 | drn
RESIDENTL | rwn24 | 15617115.6722 | 2794 | rwn
RESIDENTL | cre32 | 8053371.5554 | 2218 | cre
COMMERCIAL | bwn11 | 5920812.2037 | 76 | bwn
NCONUML | smg33 | 19709.42 | 12 | smg
INDUSTRIAL | mby11 | 90387.22 | 16 | mby
COMMERCIAL | tgn41 | 8173213.7745 | 338 | tgn
INDUSTRIAL | wn7 | 3582803.57 | 9 | wn
FARM | bwr23 | 29264.76 | 8 | bwr
RESIDENTL | bwn13 | 8026926.4045 | 1629 | bwn
FARM | wgi24 | 1757204.2906 | 142 | wgi
| rve13 | 21148.03 | 29 | rve
RESIDENTL | wgl21 | 23764201.6622 | 4642 | wgl
COMMERCIAL | wn1 | 22168293.2818 | 620 | wn
INDUSTRIAL | cyn32 | 738566.1077 | 85 | cyn
| hpk21 | 27858.58 | 57 | hpk
COMMERCIAL | klo11 | 2030116.61 | 11 | klo
INDUSTRIAL | bn22 | 260832.7234 | 23 | bn
| ofr24 | 25053.77 | 43 | ofr
| drn12 | 30292.1138 | 29 | drn
COMMERCIAL | smg22 | 18806077.0677 | 136 | smg
COMMERCIAL | bwa22 | 4509592.2057 | 144 | bwa
COMMERCIAL | drn12 | 15118769.4919 | 112 | drn
| ldl23 | 80304.9161 | 48 | ldl
| rwn32 | 14306.27 | 22 | rwn
| drn23 | 12868.4314 | 15 | drn
RESIDENTL | mwl22 | 12904194.2639 | 2809 | mwl
COMMERCIAL | tt6 | 3682930.1298 | 115 | tt
COMMERCIAL | bra24 | 3429037.1414 | 127 | bra
NCONUML | hpk11 | 112614.82 | 31 | hpk
RESIDENTL | mfa21 | 12551518.2306 | 1921 | mfa
RESIDENTL | bge22 | 19945240.9452 | 3164 | bge
| tt4 | 9710.0483 | 41 | tt
NCONUML | phm22 | 22255.8232 | 9 | phm
COMMERCIAL | fgy21 | 1241019.6707 | 34 | fgy
INDUSTRIAL | nla31 | 516137.35 | 16 | nla
FARM | wyk13 | 707273.0378 | 84 | wyk
NCONUML | elm25 | 44655.33 | 20 | elm
| ofr23 | 28214.1089 | 26 | ofr
INDUSTRIAL | ruba22 | 167892.49 | 8 | ruba
FARM | hpk21 | 3124.97 | 1 | hpk
FARM | wn4 | 999664.927 | 129 | wn
COMMERCIAL | wn6 | 8795190.5545 | 246 | wn
| cre23 | 50195.43 | 25 | cre
COMMERCIAL | bwr22 | 15914202.1636 | 269 | bwr
INDUSTRIAL | elm22 | 545216.4127 | 27 | elm
NCONUML | bwr32 | 46210.27 | 31 | bwr
COMMERCIAL | moe12 | 4799517.76 | 51 | moe
| drn22 | 43438.5 | 28 | drn
FARM | bn22 | 13032.09 | 3 | bn
FARM | ldl24 | 222231.4641 | 11 | ldl
| bdl31 | 24144.6762 | 16 | bdl
FARM | cpk11 | 227979.0877 | 18 | cpk
FARM | elm33 | 50441.5205 | 4 | elm
INDUSTRIAL | rve13 | 147824.4003 | 10 | rve
COMMERCIAL | uwy1 | 603856.89 | 33 | uwy
FARM | mfa21 | 13347321.3386 | 701 | mfa
RESIDENTL | wo14 | 1446838.665 | 266 | wo
NCONUML | rwt14 | 102266.96 | 37 | rwt
| kms11 | 9612.23 | 20 | kms
RESIDENTL | phi11 | 5828644.3864 | 1391 | phi
COMMERCIAL | tgn12 | 10174331.2835 | 242 | tgn
LIGHTING | drn21 | 522455.53 | 1 | drn
INDUSTRIAL | smr22 | 2060432.23 | 13 | smr
| moe21 | 19173.8011 | 29 | moe
NCONUML | fgy12 | 1668.8419 | 4 | fgy
COMMERCIAL | elm25 | 2590499.6378 | 73 | elm
| epg34 | 11737.1961 | 27 | epg
COMMERCIAL | cpk23 | 2022573.8223 | 44 | cpk
COMMERCIAL | sle31 | 4198591.4215 | 178 | sle
FARM | nrn13 | 23844.37 | 5 | nrn
FARM | elm26 | 83060.0495 | 12 | elm
INDUSTRIAL | rve12 | 67014.5 | 12 | rve
INDUSTRIAL | moe21 | 304282.5341 | 37 | moe
COMMERCIAL | ofr21 | 9424773.56 | 126 | ofr
FARM | wn3 | 4385381.9629 | 585 | wn
FARM | klk21 | 574949.1868 | 82 | klk
NCONUML | wyk13 | 97422.66 | 49 | wyk
FARM | bwn12 | 14573.05 | 3 | bwn
NCONUML | msd2 | 8161.26 | 6 | msd
COMMERCIAL | elm31 | 474386.1613 | 1 | elm
RESIDENTL | rwt35 | 12065.95 | 2 | rwt
RESIDENTL | wt6 | 15702930.1084 | 3397 | wt
RESIDENTL | cln24 | 3991370.9732 | 1090 | cln
COMMERCIAL | smg21 | 2744632.8687 | 43 | smg
| myt21 | 64545.94 | 22 | myt
RESIDENTL | lga22 | 9862202.3617 | 1608 | lga
INDUSTRIAL | cyn13 | 4447831.06 | 67 | cyn
COMMERCIAL | ruba12 | 6703349.3664 | 290 | ruba
| smr23 | 7378.7014 | 9 | smr
FARM | phi13 | 230339.12 | 15 | phi
RESIDENTL | wt11 | 8665012.8839 | 2213 | wt
RESIDENTL | bge13 | 9255563.8982 | 1458 | bge
COMMERCIAL | bge11 | 11367890.3817 | 330 | bge
COMMERCIAL | wgi23 | 2290528.82 | 95 | wgi
COMMERCIAL | epg35 | 29855241.8371 | 304 | epg
NCONUML | mwl23 | 55631.52 | 20 | mwl
RESIDENTL | tgn11 | 18615536.7391 | 4196 | tgn
RESIDENTL | klo24 | 35150523.3753 | 8219 | klo
| wgi32 | 32777.55 | 36 | wgi
| uwy1 | 1895.86 | 6 | uwy
COMMERCIAL | wots24 | 5008654.6646 | 265 | wots
INDUSTRIAL | phi13 | 601326.64 | 38 | phi
LIGHTING | cf1 | 76883.018 | 3 | cf
RESIDENTL | cre21 | 18876617.5647 | 4715 | cre
INDUSTRIAL | wo32 | 73086.25 | 1 | wo
COMMERCIAL | lga13 | 621321.4861 | 47 | lga
FARM | cnr2 | 245915.51 | 48 | cnr
COMMERCIAL | bge22 | 4521687.9575 | 100 | bge
INDUSTRIAL | cyn12 | 101425.5 | 5 | cyn
FARM | drn11 | 51881.33 | 8 | drn
INDUSTRIAL | wo23 | 212041.78 | 1 | wo
RESIDENTL | lga23 | 5064870.5947 | 821 | lga
RESIDENTL | bn12 | 3438265.7182 | 625 | bn
RESIDENTL | bra21 | 23268334.8963 | 5707 | bra
| bdl42 | 11198.42 | 14 | bdl
FARM | cnr1 | 2440.03 | 2 | cnr
| phm34 | 68320.3174 | 32 | phm
FARM | rwt31 | 12148.87 | 1 | rwt
| smg31 | 8879.89 | 17 | smg
LIGHTING | tgn11 | 1064655.8 | 1 | tgn
FARM | llg14 | 4195351.6172 | 347 | llg
FARM | mwl11 | 2401732.236 | 295 | mwl
INDUSTRIAL | brt22 | 103539.39 | 15 | brt
COMMERCIAL | mwl14 | 15268408.4249 | 139 | mwl
RESIDENTL | wn1 | 4757807.4084 | 1039 | wn
COMMERCIAL | wo33 | 4706642.85 | 27 | wo
| nrn14 | 10562.91 | 10 | nrn
RESIDENTL | wgl15 | 10836827.2608 | 2158 | wgl
RESIDENTL | mfa22 | 4069843.249 | 701 | mfa
NCONUML | wyk24 | 96009.71 | 32 | wyk
NCONUML | rwn34 | 17137.95 | 21 | rwn
NCONUML | rve11 | 32578.28 | 16 | rve
INDUSTRIAL | klk11 | 54511.69 | 7 | klk
RESIDENTL | tt2 | 73044.37 | 7 | tt
COMMERCIAL | rwn32 | 3002784.6794 | 97 | rwn
NCONUML | tt1 | 9612.49 | 4 | tt
NCONUML | bwr23 | 79898.93 | 30 | bwr
NCONUML | epg14 | 19866.64 | 14 | epg
| elm26 | 27328.755 | 32 | elm
INDUSTRIAL | bdl32 | 418697.92 | 34 | bdl
FARM | wt11 | 3746.97 | 1 | wt
NCONUML | ofr23 | 50364.93 | 30 | ofr
INDUSTRIAL | smg23 | 412547.84 | 9 | smg
LIGHTING | klo14 | 3058096.87 | 1 | klo
| nrn13 | 13473.67 | 22 | nrn
FARM | bra12 | 12444.91 | 1 | bra
COMMERCIAL | cre21 | 15222170.3645 | 489 | cre
INDUSTRIAL | wgi32 | 984365.53 | 33 | wgi
NCONUML | rwt25 | 118451.05 | 54 | rwt
INDUSTRIAL | mwe236 | 280541.09 | 16 | mwe
RESIDENTL | epg33 | 183201.2006 | 6 | epg
INDUSTRIAL | elm33 | 243571.284 | 12 | elm
RESIDENTL | ldl11 | 13512975.3636 | 2241 | ldl
| mwl12 | 15850.97 | 9 | mwl
INDUSTRIAL | fgy21 | 6595081.67 | 18 | fgy
LIGHTING | smr24 | 109914.08 | 1 | smr
RESIDENTL | rwt25 | 10768082.8154 | 2324 | rwt
INDUSTRIAL | rwt15 | 3409961.2906 | 83 | rwt
INDUSTRIAL | phi12 | 3418741.3516 | 25 | phi
INDUSTRIAL | bwa22 | 1592049.74 | 9 | bwa
NCONUML | wo22 | 90587.46 | 26 | wo
INDUSTRIAL | ldl21 | 599666.7 | 44 | ldl
INDUSTRIAL | wt6 | 1814.16 | 1 | wt
NCONUML | ofr22 | 9198.59 | 2 | ofr
INDUSTRIAL | bra13 | 1860337.5903 | 47 | bra
COMMERCIAL | fgy24 | 2616699.5517 | 109 | fgy
RESIDENTL | epg11 | 6094828.0666 | 1503 | epg
NCONUML | rwt36 | 1279.88 | 1 | rwt
RESIDENTL | bwn14 | 23184606.5946 | 3016 | bwn
COMMERCIAL | bra31 | 7996775.7312 | 141 | bra
| nla32 | 13550.62 | 15 | nla
FARM | brt11 | 223967.42 | 33 | brt
| hpk12 | 10433.13 | 13 | hpk
INDUSTRIAL | llg13 | 899195.7591 | 21 | llg
INDUSTRIAL | wgl21 | 1687828.17 | 29 | wgl
INDUSTRIAL | cnr2 | 615523.18 | 19 | cnr
INDUSTRIAL | mfa14 | 499885.98 | 5 | mfa
RESIDENTL | drn13 | 15714620.5428 | 2698 | drn
FARM | kms12 | 1180373.8068 | 156 | kms
COMMERCIAL | rwn24 | 15303994.2605 | 63 | rwn
NCONUML | wn4 | 65357.11 | 21 | wn
COMMERCIAL | rwn33 | 562037.42 | 22 | rwn
| moe22 | 3614.75 | 12 | moe
| wgl13 | 39374.2 | 44 | wgl
| moe11 | 8193.3901 | 21 | moe
COMMERCIAL | wt7 | 4475658.5866 | 198 | wt
NCONUML | bwr13 | 106489.72 | 46 | bwr
NCONUML | kms12 | 115620.45 | 45 | kms
NCONUML | cyn24 | 41312.6858 | 21 | cyn
COMMERCIAL | mwl13 | 8520395.3383 | 232 | mwl
COMMERCIAL | cyn32 | 10902527.7138 | 351 | cyn
INDUSTRIAL | tgn31 | 3050316.88 | 29 | tgn
| wo13 | 12961.22 | 9 | wo
NCONUML | bra12 | 30121.15 | 6 | bra
| mwl24 | 4141.68 | 3 | mwl
RESIDENTL | ftr22 | 5196242.6186 | 1010 | ftr
| cyn12 | 33132.831 | 28 | cyn
| mwl11 | 4217.9 | 11 | mwl
NCONUML | sle13 | 9744.3474 | 7 | sle
RESIDENTL | sle14 | 16027394.2978 | 4223 | sle
RESIDENTL | wgl23 | 5362246.1099 | 739 | wgl
COMMERCIAL | cre23 | 25513720.5265 | 132 | cre
RESIDENTL | bdl43 | 5886157.096 | 1122 | bdl
RESIDENTL | bge21 | 100743.92 | 11 | bge
RESIDENTL | smg22 | 10427736.14 | 2476 | smg
FARM | rwn31 | 347566.14 | 21 | rwn
INDUSTRIAL | bn12 | 8173831.79 | 6 | bn
| wgi24 | 27543.5394 | 32 | wgi
| mfa23 | 2828.28 | 3 | mfa
NCONUML | elm22 | 93887.89 | 42 | elm
INDUSTRIAL | wots13 | 2426481.9937 | 28 | wots
RESIDENTL | mwl13 | 9372820.2657 | 1896 | mwl
COMMERCIAL | epg31 | 8736205.1691 | 170 | epg
| bdl44 | 43009.9658 | 33 | bdl
COMMERCIAL | wgl24 | 14484234.4559 | 200 | wgl
INDUSTRIAL | wn3 | 1104797.78 | 30 | wn
| wgi33 | 38017.7186 | 28 | wgi
NCONUML | wo31 | 91536.41 | 24 | wo
FARM | ldl14 | 3990495.203 | 142 | ldl
NCONUML | wyk12 | 43139.17 | 24 | wyk
INDUSTRIAL | mwl15 | 15961047.4 | 1 | mwl
LIGHTING | bdl32 | 23514.52 | 1 | bdl
| rve12 | 15159.19 | 33 | rve
NCONUML | phm34 | 55440.25 | 17 | phm
COMMERCIAL | phm22 | 18761180.3018 | 732 | phm
RESIDENTL | cyn22 | 8715945.6121 | 2142 | cyn
FARM | fgy31 | 3345.68 | 2 | fgy
RESIDENTL | smr22 | 8159798.5324 | 1327 | smr
RESIDENTL | cyn23 | 7298806.6664 | 1621 | cyn
FARM | bdl42 | 2407309.4815 | 483 | bdl
| wyk23 | 31976.68 | 33 | wyk
INDUSTRIAL | rwn26 | 257525.5397 | 10 | rwn
NCONUML | bwn11 | 91006.47 | 23 | bwn
COMMERCIAL | cyn23 | 7883296.3431 | 299 | cyn
| moe15 | 19145.0797 | 16 | moe
| drn11 | 44271.4909 | 65 | drn
INDUSTRIAL | moe22 | 88009.47 | 4 | moe
NCONUML | mdg1 | 4146.1 | 9 | mdg
FARM | bra33 | 5568.67 | 1 | bra
LIGHTING | bwa22 | 75542.46 | 1 | bwa
NCONUML | hpk14 | 64164.68 | 20 | hpk
NCONUML |  | 262.3928 | 5 | #REF!
INDUSTRIAL | cln13 | 2016187.9013 | 2 | cln
FARM | ofr11 | 1184021.9516 | 51 | ofr
FARM | phm31 | 2011038.4476 | 90 | phm
NCONUML | elm21 | 62554.36 | 23 | elm
NCONUML | wt8 | 36862.33 | 14 | wt
NCONUML | cnr1 | 1922.85 | 2 | cnr
INDUSTRIAL | cre31 | 212230.18 | 2 | cre
COMMERCIAL | mfa34 | 8313764.4144 | 170 | mfa
INDUSTRIAL | tt5 | 637183.9506 | 23 | tt
INDUSTRIAL | llg14 | 1201432.9268 | 29 | llg
RESIDENTL | wo23 | 1549813.7708 | 361 | wo
| bwr23 | 25383.1703 | 47 | bwr
| sle11 | 3997.21 | 10 | sle
NCONUML | epg22 | 8538.04 | 7 | epg
NCONUML | bwr24 | 20744.02 | 14 | bwr
INDUSTRIAL | myt12 | 952524.23 | 20 | myt
| ftr23 | 53453.1274 | 33 | ftr
RESIDENTL | bra11 | 9331476.9371 | 2277 | bra
FARM | ldl13 | 3504918.0126 | 302 | ldl
| brt11 | 8693.81 | 14 | brt
INDUSTRIAL | phm31 | 91642.7039 | 2 | phm
COMMERCIAL | bdl43 | 22280533.2345 | 523 | bdl
FARM | moe23 | 4928404.5033 | 365 | moe
| klk21 | 7164.56 | 8 | klk
| wt7 | 8483.27 | 17 | wt
FARM | llg11 | 4501914.1562 | 365 | llg
LIGHTING | cf2 | 13221.322 | 1 | cf
| tgn31 | 23134.1673 | 13 | tgn
RESIDENTL | nla31 | 3471883.5329 | 742 | nla
COMMERCIAL | bdl31 | 6479518.62 | 206 | bdl
COMMERCIAL | smr23 | 799486.21 | 26 | smr
INDUSTRIAL | rve11 | 154936.16 | 21 | rve
RESIDENTL | bm8b33 | 130717.0048 | 17 | bmb
FARM | phi12 | 364625.9 | 40 | phi
INDUSTRIAL | klk22 | 5518.6 | 1 | klk
RESIDENTL | llg12 | 7619865.2998 | 1210 | llg
RESIDENTL | cln21 | 24090170.4832 | 5877 | cln
NCONUML | cpk11 | 17830.25 | 17 | cpk
COMMERCIAL | ruba22 | 3463594.5603 | 120 | ruba
NCONUML | brt22 | 9306.55 | 7 | brt
INDUSTRIAL | epg32 | 7635590.16 | 5 | epg
INDUSTRIAL | cln12 | 360384.55 | 1 | cln
COMMERCIAL | bwr13 | 10101102.0366 | 288 | bwr
COMMERCIAL | wo22 | 9017310.64 | 153 | wo
INDUSTRIAL | hpk24 | 9439809.63 | 31 | hpk
COMMERCIAL | cpk12 | 5057421.24 | 115 | cpk
| lyd14 | 55928.8081 | 17 | lyd
INDUSTRIAL | klo11 | 67703.26 | 1 | klo
RESIDENTL | ldl14 | 11349760.1474 | 1905 | ldl
LIGHTING | myt21 | 2294.9 | 1 | myt
RESIDENTL | rwn22 | 13452598.5118 | 2640 | rwn
COMMERCIAL | bm8b32 | 168652.4116 | 16 | bmb
INDUSTRIAL | bdl34 | 328519.77 | 31 | bdl
| tt12 | 16952.1045 | 5 | tt
RESIDENTL | wots24 | 6979604.5034 | 1172 | wots
INDUSTRIAL | wyk24 | 160679.33 | 16 | wyk
COMMERCIAL | klo12 | 12237846.22 | 9 | klo
RESIDENTL | wo33 | 232024.16 | 58 | wo
COMMERCIAL | bn24 | 3468313.5774 | 163 | bn
COMMERCIAL | lga12 | 9341312.33 | 61 | lga
| msd1 | 16071.3636 | 20 | msd
INDUSTRIAL | ofr24 | 300622.14 | 4 | ofr
INDUSTRIAL | bwn13 | 24333.45 | 4 | bwn
| tt1 | 26786.62 | 3 | tt
INDUSTRIAL | rwt31 | 22449174.23 | 3 | rwt
FARM | mfa14 | 28798.91 | 1 | mfa
| bwr32 | 10607.4826 | 52 | bwr
INDUSTRIAL | wn4 | 1120535.2101 | 54 | wn
RESIDENTL | bwr12 | 975012.274 | 199 | bwr
INDUSTRIAL | wgi24 | 1432383.73 | 33 | wgi
| llg13 | 135285.4952 | 24 | llg
| rwn34 | 10950.9 | 10 | rwn
FARM | elm34 | 16399.68 | 6 | elm
RESIDENTL | ruba12 | 12797333.4035 | 1890 | ruba
COMMERCIAL | hpk22 | 5875279.82 | 181 | hpk
| cln11 | 262675.9461 | 229 | cln
RESIDENTL | cf2 | 494427.3912 | 409 | cf
FARM | elm22 | 15544.2323 | 4 | elm
INDUSTRIAL | smg32 | 67645.78 | 1 | smg
FARM | bwa23 | 3495492.525 | 169 | bwa
NCONUML | phm24 | 66511.6 | 15 | phm
NCONUML | wgi23 | 35701.3 | 15 | wgi
NCONUML | epg35 | 18576.68 | 9 | epg
NCONUML | llg13 | 26801.83 | 12 | llg
LIGHTING | phi13 | 74566.47 | 1 | phi
| ldl24 | 28689.7774 | 48 | ldl
| bge11 | 41147.6131 | 30 | bge
RESIDENTL | ofr21 | 18456788.2346 | 4412 | ofr
INDUSTRIAL | ofr11 | 52339.71 | 6 | ofr
COMMERCIAL | nrn11 | 8254682.48 | 13 | nrn
FARM | moe15 | 1053275.4428 | 126 | moe
INDUSTRIAL | lyd12 | 15947.41 | 3 | lyd
INDUSTRIAL | wt10 | 5540.7 | 1 | wt
RESIDENTL | rwt21 | 965731.93 | 282 | rwt
FARM | wo13 | 51683.13 | 6 | wo
INDUSTRIAL | epg34 | 25722.81 | 2 | epg
COMMERCIAL | lys36 | 31611.41 | 1 | lys
RESIDENTL | wn6 | 17451542.0984 | 3750 | wn
NCONUML | hpk12 | 23613.79 | 7 | hpk
INDUSTRIAL | ruba24 | 189283.4035 | 13 | ruba
| nrn12 | 36108.6 | 9 | nrn
NCONUML | nla32 | 30069.03 | 18 | nla
COMMERCIAL | bm8b31 | 174913.9253 | 14 | bmb
| wo22 | 26321.2427 | 38 | wo
INDUSTRIAL | fgy31 | 4952.61 | 1 | fgy
RESIDENTL | cln14 | 25051991.2109 | 8311 | cln
RESIDENTL | lga24 | 3807672.9803 | 653 | lga
RESIDENTL | bra31 | 2624204.8049 | 649 | bra
COMMERCIAL | cln21 | 7282112.3749 | 104 | cln
COMMERCIAL | ftr23 | 8984637.4811 | 336 | ftr
RESIDENTL | klo13 | 97850.5847 | 89 | klo
INDUSTRIAL | ofr14 | 250.62 | 1 | ofr
FARM | mwl24 | 966080.4815 | 75 | mwl
NCONUML | bdl41 | 86032.0652 | 28 | bdl
INDUSTRIAL | epg13 | 201122.3196 | 20 | epg
COMMERCIAL | tgn23 | 6173474.1124 | 95 | tgn
| moe12 | 11374.0239 | 16 | moe
INDUSTRIAL | drn11 | 8297.91 | 2 | drn
| wn4 | 46461.2191 | 29 | wn
NCONUML | wgl13 | 85005.64 | 23 | wgl
INDUSTRIAL | ftr22 | 264831.3749 | 23 | ftr
NCONUML | mjg11 | 5653.43 | 3 | mjg
RESIDENTL | klo12 | 526.2 | 1 | klo
COMMERCIAL | cln11 | 18408618.7138 | 182 | cln
NCONUML | wo13 | 11132.69 | 4 | wo
COMMERCIAL | yn38 | 28127.08 | 5 | yn
NCONUML | mwl24 | 19701.6 | 5 | mwl
RESIDENTL | wots12 | 7880580.6899 | 1786 | wots
COMMERCIAL | tgn43 | 5598797.62 | 126 | tgn
NCONUML | mfa23 | 6277.17 | 3 | mfa
NCONUML | bra32 | 63005.82 | 38 | bra
FARM | bdl34 | 247623.03 | 51 | bdl
INDUSTRIAL | wn5 | 6299826.69 | 33 | wn
| mby13 | 155.9226 | 1 | mby
FARM | ofr23 | 2419763.5413 | 305 | ofr
NCONUML | cre22 | 86458.6773 | 42 | cre
NCONUML | hpk23 | 84001.53 | 23 | hpk
RESIDENTL | bra24 | 8260262.5707 | 1824 | bra
| cyn14 | 12637.7523 | 26 | cyn
LIGHTING | wgl11 | 2443513.25 | 2 | wgl
NCONUML | wgi24 | 69610.83 | 24 | wgi
COMMERCIAL | klo14 | 11961206.944 | 269 | klo
FARM | drn14 | 379625.3327 | 36 | drn
RESIDENTL | bwr22 | 1941843.629 | 510 | bwr
| llg14 | 42684.6726 | 22 | llg
INDUSTRIAL | drn21 | 709809.96 | 3 | drn
INDUSTRIAL | tgn42 | 199383.97 | 5 | tgn
RESIDENTL | sle32 | 6677118.757 | 1350 | sle
RESIDENTL | myt12 | 14552002.0991 | 2380 | myt
FARM | myt21 | 821475.54 | 124 | myt
| bn11 | 39921.12 | 40 | bn
NCONUML | mby12 | 15769.2 | 4 | mby
NCONUML | bdl44 | 1602.59 | 5 | bdl
COMMERCIAL | tt12 | 10810239.5174 | 467 | tt
NCONUML | wn7 | 7884.6 | 2 | wn
| bdl34 | 14430.17 | 36 | bdl
RESIDENTL | lyd11 | 11014119.7855 | 2574 | lyd
FARM | wyk23 | 2329152.6841 | 202 | wyk
| epg23 | 66262.7623 | 20 | epg
RESIDENTL | rwt32 | 15157646.1346 | 3808 | rwt
RESIDENTL | cre31 | 23125994.5084 | 5990 | cre
FARM | bn11 | 9012293.1298 | 1372 | bn
COMMERCIAL |  | 2470964.7554 | 79 | #REF!
INDUSTRIAL | kms11 | 3849512.37 | 9 | kms
RESIDENTL | sle31 | 15232222.0022 | 4728 | sle
RESIDENTL | myt11 | 3230941.4261 | 365 | myt
| wyk12 | 33744.4845 | 17 | wyk
| lga11 | 13750.1489 | 25 | lga
COMMERCIAL | cre33 | 14716025.8299 | 132 | cre
RESIDENTL | trc01 | 404888.8876 | 85 | trc
| moe25 | 10579.3743 | 23 | moe
NCONUML | msd1 | 8725.66 | 9 | msd
RESIDENTL | mwl14 | 1637810.9082 | 178 | mwl
FARM | wn5 | 10157746.9699 | 1090 | wn
INDUSTRIAL | bwr33 | 13101695.07 | 41 | bwr
NCONUML | ofr24 | 72292.73 | 18 | ofr
| mdg1 | 5594.13 | 4 | mdg
FARM | wgi33 | 86057.74 | 7 | wgi
RESIDENTL | rwt22 | 12512450.4989 | 3066 | rwt
RESIDENTL | cnr2 | 3844076.3719 | 1054 | cnr
| hpk14 | 17565.23 | 35 | hpk
NCONUML | drn23 | 37389.78 | 20 | drn
RESIDENTL | tgn44 | 11943542.7304 | 2804 | tgn
| tgn42 | 0 | 1 | tgn
NCONUML | rwt22 | 27503.296 | 22 | rwt
FARM | mwl16 | 172184.54 | 14 | mwl
COMMERCIAL | nla34 | 1413700.5844 | 93 | nla
| epg22 | 2049.9261 | 2 | epg
FARM | tgn41 | 3728231.4432 | 423 | tgn
COMMERCIAL | lga23 | 3382991.9134 | 119 | lga
NCONUML | sle31 | 61055.23 | 20 | sle
NCONUML | tgn44 | 66469.79 | 20 | tgn
| phm24 | 18272.6834 | 34 | phm
RESIDENTL | hpk11 | 16523367.4098 | 4141 | hpk
| hpk13 | 40054.7485 | 22 | hpk
| bwr24 | 10180.34 | 28 | bwr
COMMERCIAL | bdl33 | 34051046.7333 | 257 | bdl
COMMERCIAL | wt9 | 7035668.1433 | 128 | wt
NCONUML | wt15 | 16005.53 | 14 | wt
FARM | ruba24 | 730484.142 | 55 | ruba
NCONUML | cpk23 | 20021.69 | 18 | cpk
INDUSTRIAL | mwl21 | 320021.87 | 5 | mwl
COMMERCIAL | hpk23 | 12064171.7331 | 206 | hpk
INDUSTRIAL | wt11 | 2563605.84 | 2 | wt
RESIDENTL | wt15 | 8580853.2399 | 1947 | wt
| elm21 | 24345.52 | 16 | elm
INDUSTRIAL | mwl16 | 183545.9668 | 9 | mwl
FARM | rve13 | 9637.99 | 1 | rve
NCONUML | drn22 | 69938.3 | 27 | drn
NCONUML | bdl31 | 70697.58 | 29 | bdl
NCONUML | bwa24 | 1320.25 | 1 | bwa
COMMERCIAL | mwl23 | 10773058.8537 | 154 | mwl
COMMERCIAL | elm23 | 5093994.3825 | 95 | elm
FARM | smr23 | 1078615.6398 | 156 | smr
| cpk11 | 37835.6667 | 47 | cpk
INDUSTRIAL | bra14 | 14750.52 | 4 | bra
RESIDENTL | rwn33 | 5693275.4596 | 1153 | rwn
| bn22 | 41634.09 | 21 | bn
INDUSTRIAL | tt2 | 11531135.8238 | 100 | tt
INDUSTRIAL | wt12 | 3871876.0911 | 67 | wt
INDUSTRIAL | mwl22 | 292678.42 | 8 | mwl
RESIDENTL | bn23 | 8695284.412 | 1665 | bn
COMMERCIAL | cyn11 | 9621618.8569 | 233 | cyn
| cyn21 | 22400.14 | 28 | cyn
INDUSTRIAL | mjg11 | 1321804.29 | 13 | mjg
INDUSTRIAL | cf2 | 1970.494 | 2 | cf
RESIDENTL | tt5 | 6560032.4165 | 1633 | tt
COMMERCIAL | smr14 | 6818307.6657 | 239 | smr
COMMERCIAL | smg33 | 1348313.99 | 14 | smg
RESIDENTL | rwt15 | 11066767.0768 | 2454 | rwt
COMMERCIAL | cre32 | 14440881.1645 | 427 | cre
INDUSTRIAL | smr24 | 4639865.5557 | 45 | smr
COMMERCIAL | fgy23 | 10185283.97 | 98 | fgy
COMMERCIAL | hpk11 | 3476478.711 | 53 | hpk
| cre32 | 19011.64 | 13 | cre
NCONUML | wgl23 | 12760.41 | 6 | wgl
COMMERCIAL | nrn15 | 84419.81 | 3 | nrn
NCONUML | moe15 | 22748.39 | 11 | moe
RESIDENTL | tt12 | 86039.86 | 6 | tt
RESIDENTL | cyn31 | 8632445.7043 | 2077 | cyn
RESIDENTL | wgl24 | 16633542.8094 | 2715 | wgl
COMMERCIAL | wgi22 | 6881286.006 | 159 | wgi
INDUSTRIAL | smr13 | 992080.85 | 26 | smr
NCONUML | cpk12 | 17033.61 | 10 | cpk
NCONUML | ftr21 | 16597.26 | 11 | ftr
FARM | mwl12 | 18529.37 | 2 | mwl
INDUSTRIAL | epg33 | 1129768.4897 | 4 | epg
| wyk13 | 9658.4809 | 15 | wyk
LIGHTING | trc01 | 669938.2281 | 2 | trc
FARM | hpk13 | 2305.94 | 1 | hpk
RESIDENTL | tt6 | 19150788.3328 | 4695 | tt
FARM | tgn31 | 5369095.0164 | 562 | tgn
NCONUML | wgl24 | 11028.97 | 10 | wgl
INDUSTRIAL | brt11 | 82545.9018 | 12 | brt
LIGHTING | mby11 | 10728.24 | 1 | mby
NCONUML | myt21 | 24178.1 | 12 | myt
| wt10 | 6115.9374 | 5 | wt
RESIDENTL | bge12 | 9796026.1467 | 1789 | bge
FARM | myt11 | 2640136.7565 | 257 | myt
NCONUML | cyn11 | 21168.08 | 13 | cyn
INDUSTRIAL |  | 942329979.1078 | 12 | #REF!
INDUSTRIAL | elm34 | 168803.0667 | 15 | elm
| brt22 | 30486.3216 | 18 | brt
INDUSTRIAL | epg11 | 6777.42 | 2 | epg
RESIDENTL | elm34 | 19825611.7814 | 4189 | elm
COMMERCIAL | sle13 | 974523.8832 | 109 | sle
INDUSTRIAL | lga13 | 207007.5439 | 9 | lga
RESIDENTL | mwl23 | 3618535.6291 | 812 | mwl
| fgy14 | 28887.99 | 26 | fgy
COMMERCIAL | mby13 | 2521770.2974 | 71 | mby
| lga12 | 14720.56 | 12 | lga
RESIDENTL | cpk12 | 17343162.547 | 2927 | cpk
COMMERCIAL | wt5 | 19785711.5258 | 118 | wt
INDUSTRIAL | drn24 | 4643890.64 | 3 | drn
FARM | drn21 | 13254.24 | 1 | drn
NCONUML | mwl11 | 360.93 | 3 | mwl
RESIDENTL | epg34 | 15669683.4078 | 3862 | epg
NCONUML | wt10 | 27658.61 | 16 | wt
LIGHTING | rwt14 | 962126.36 | 3 | rwt
COMMERCIAL | drn23 | 5472888.3558 | 161 | drn
LIGHTING | bwn11 | 6340546.01 | 1 | bwn
INDUSTRIAL | sfs1 | 80102.39 | 5 | sfs
COMMERCIAL | phm34 | 4610839.9937 | 66 | phm
COMMERCIAL | mfa31 | 3803351.87 | 100 | mfa
INDUSTRIAL | rwt25 | 2203508.65 | 42 | rwt
| bwa22 | 41045.3074 | 24 | bwa
FARM | smr13 | 139441.5096 | 27 | smr
NCONUML | phi12 | 84007.84 | 24 | phi
| fgy21 | 10377.87 | 9 | fgy
NCONUML | rwt15 | 44056.974 | 28 | rwt
LIGHTING | nla34 | 5187.52 | 1 | nla
RESIDENTL | sfs1 | 6449039.4989 | 958 | sfs
RESIDENTL | msd4 | 16354350.3097 | 2395 | msd
INDUSTRIAL | phm33 | 724516.58 | 21 | phm
COMMERCIAL | wgl14 | 59932538.6 | 1 | wgl
COMMERCIAL | rwt31 | 3904134.109 | 54 | rwt
RESIDENTL | wt5 | 5466545.168 | 1335 | wt
FARM | ftr22 | 3872176.8459 | 271 | ftr
| wn5 | 51237.831 | 23 | wn
INDUSTRIAL | kms12 | 880994.04 | 26 | kms
NCONUML | rwt31 | 27889.28 | 18 | rwt
RESIDENTL | elm22 | 20622579.4478 | 3120 | elm
| bn24 | 7126.586 | 9 | bn
FARM | wots11 | 7572710.4051 | 689 | wots
INDUSTRIAL | myt11 | 122662.09 | 11 | myt
NCONUML | bdl32 | 81716.25 | 38 | bdl
NCONUML | cyn33 | 39860.39 | 20 | cyn
| lga13 | 7900.07 | 12 | lga
COMMERCIAL | wn7 | 705796.26 | 31 | wn
RESIDENTL | tgn23 | 12995258.1614 | 2157 | tgn
RESIDENTL | wgl12 | 18309192.1093 | 3011 | wgl
NCONUML | drn14 | 58816.42 | 20 | drn
INDUSTRIAL | tt9 | 1853761.73 | 4 | tt
RESIDENTL | kms12 | 23913269.0041 | 4277 | kms
COMMERCIAL | wgi33 | 13737748.8552 | 364 | wgi
COMMERCIAL | phm21 | 28428865.0993 | 838 | phm
FARM | sle32 | 5441049.7096 | 310 | sle
NCONUML | cyn32 | 58907.16 | 38 | cyn
INDUSTRIAL | msd2 | 165834.72 | 18 | msd
COMMERCIAL | bwr23 | 26845428.111 | 233 | bwr
RESIDENTL | msd2 | 5810770.2828 | 1153 | msd
FARM | klk11 | 2014936.8264 | 177 | klk
| wots12 | 13459.1171 | 22 | wots
INDUSTRIAL | rwn24 | 4339629.96 | 13 | rwn
INDUSTRIAL | tgn41 | 1853911.3546 | 62 | tgn
COMMERCIAL | smg32 | 6595824.87 | 22 | smg
| wgi34 | 86239.94 | 15 | wgi
RESIDENTL | bn22 | 13286130.4589 | 3118 | bn
RESIDENTL | mfa31 | 9237847.4317 | 2206 | mfa
COMMERCIAL | wgi34 | 9571334.08 | 60 | wgi
RESIDENTL | mdi1 | 176577.17 | 31 | mdi
NCONUML | rwn31 | 16738.19 | 15 | rwn
INDUSTRIAL | drn13 | 239296.9 | 11 | drn
INDUSTRIAL | bdl43 | 306419.52 | 21 | bdl
NCONUML | wo23 | 56204.51 | 16 | wo
COMMERCIAL | ftr21 | 2804675.8206 | 100 | ftr
COMMERCIAL | bwa23 | 206762.2501 | 23 | bwa
NCONUML | mfa21 | 28416.84 | 12 | mfa
| cln23 | 52144.7804 | 85 | cln
RESIDENTL | rve11 | 2276471.0008 | 508 | rve
COMMERCIAL | ofr24 | 6649904.8426 | 113 | ofr
NCONUML | phi13 | 105028.33 | 33 | phi
FARM | smg22 | 25054.15 | 4 | smg
FARM | bwn11 | 18419.1 | 1 | bwn
INDUSTRIAL | epg31 | 360181.3871 | 31 | epg
COMMERCIAL | fgy14 | 7872993.2117 | 231 | fgy
| ldl11 | 24480.7 | 22 | ldl
INDUSTRIAL | wgl24 | 939120.3004 | 39 | wgl
| phm22 | 31542.7748 | 10 | phm
COMMERCIAL | moe15 | 2469270.3666 | 172 | moe
| cnr3 | 100.0469 | 1 | cnr
RESIDENTL | bwn12 | 4456239.3509 | 1013 | bwn
COMMERCIAL | mwl24 | 5791496.4979 | 78 | mwl
COMMERCIAL | wo13 | 2493976.37 | 46 | wo
RESIDENTL | elm25 | 10534980.5572 | 2009 | elm
RESIDENTL | phm32 | 14466986.7977 | 3288 | phm
COMMERCIAL | ofr11 | 14130002.2904 | 224 | ofr
INDUSTRIAL | bge13 | 1057475.88 | 11 | bge
RESIDENTL | ofr22 | 7907197.5875 | 2174 | ofr
INDUSTRIAL | lga22 | 745287.81 | 44 | lga
FARM | hpk22 | 33600.65 | 5 | hpk
COMMERCIAL | epg23 | 63543126.9632 | 711 | epg
NCONUML | epg34 | 29379.47 | 21 | epg
| mwl23 | 14018.9088 | 10 | mwl
FARM | lyd14 | 350081.37 | 31 | lyd
| elm33 | 18371.0537 | 30 | elm
RESIDENTL | bwn11 | 14758921.2622 | 2984 | bwn
| cyn33 | 33636.86 | 37 | cyn
INDUSTRIAL | ldl13 | 1566146.5513 | 31 | ldl
NCONUML | smg32 | 19512.15 | 10 | smg
NCONUML | lga21 | 24931.49 | 9 | lga
RESIDENTL | mfa34 | 6438005.323 | 995 | mfa
COMMERCIAL | lga22 | 10229963.6597 | 340 | lga
COMMERCIAL | wgi31 | 4363035.5887 | 128 | wgi
| wt9 | 17175.83 | 21 | wt
INDUSTRIAL | mfa21 | 1292894.4886 | 57 | mfa
FARM | wgi32 | 343056.5273 | 19 | wgi
COMMERCIAL | bge21 | 44944.8 | 1 | bge
INDUSTRIAL | elm26 | 46289.86 | 5 | elm
NCONUML | msd4 | 12187.83 | 6 | msd
COMMERCIAL | bra21 | 14789918.5926 | 289 | bra
| cpk22 | 7305.07 | 12 | cpk
NCONUML | phm32 | 76324.09 | 20 | phm
NCONUML | sfs1 | 44865.78 | 10 | sfs
COMMERCIAL | lyd13 | 6072257.17 | 42 | lyd
FARM | cyn33 | 36456.98 | 4 | cyn
NCONUML | phm21 | 71428.0533 | 24 | phm
COMMERCIAL | sle32 | 5434267.6149 | 190 | sle
NCONUML | smg31 | 21751.86 | 17 | smg
NCONUML | wots11 | 25057.91 | 11 | wots
RESIDENTL | tgn43 | 15724147.9465 | 3608 | tgn
INDUSTRIAL | cyn21 | 9259443.95 | 23 | cyn
INDUSTRIAL | bn23 | 1923467.13 | 19 | bn
NCONUML | nrn14 | 79150.17 | 17 | nrn
NCONUML | cyn22 | 32483.16 | 10 | cyn
NCONUML | wgl12 | 47271.49 | 20 | wgl
COMMERCIAL | phm24 | 600129.57 | 25 | phm
NCONUML | lga11 | 25837.14 | 8 | lga
NCONUML | tgn41 | 7415.11 | 5 | tgn
RESIDENTL | wgl11 | 17118670.1537 | 3818 | wgl
RESIDENTL | wots11 | 15871220.8415 | 2910 | wots
| rwn31 | 40233.5106 | 27 | rwn
COMMERCIAL | elm32 | 8171019.0636 | 263 | elm
FARM | mby11 | 1335559.7721 | 187 | mby
INDUSTRIAL | mwl25 | 33119.15 | 8 | mwl
FARM | rwn26 | 5055.63 | 2 | rwn
| nla34 | 8234.98 | 10 | nla
RESIDENTL |  | 349105.8277 | 492 | #REF!
FARM | epg13 | 82815.8863 | 12 | epg
| wyk24 | 32167.14 | 30 | wyk
FARM | sle11 | 16862.17 | 6 | sle
COMMERCIAL | bm8b33 | 3349.12 | 2 | bmb
RESIDENTL | smg21 | 17914575.4009 | 3718 | smg
INDUSTRIAL | bdl42 | 622534.62 | 24 | bdl
| yn38 | 7519.7419 | 1 | yn
| phi13 | 28221.5917 | 27 | phi
| epg14 | 9258.9052 | 38 | epg
FARM | nla31 | 1791184.5035 | 140 | nla
INDUSTRIAL | wgi33 | 1188063.8119 | 37 | wgi
LIGHTING | phm33 | 4303153.65 | 2 | phm
RESIDENTL | phm33 | 12878778.4238 | 2134 | phm
COMMERCIAL | wgl23 | 3870974.8784 | 252 | wgl
NCONUML | wt5 | 58508.56 | 14 | wt
NCONUML | bwn14 | 81385.02 | 37 | bwn
NCONUML | mfa31 | 49958.93 | 14 | mfa
COMMERCIAL | bra12 | 23355928.37 | 122 | bra
NCONUML | wt13 | 98966.19 | 41 | wt
COMMERCIAL | klo24 | 13267963.2484 | 244 | klo
COMMERCIAL | bge12 | 6262328.83 | 64 | bge
COMMERCIAL | wn4 | 10511680.2174 | 332 | wn
INDUSTRIAL | tt6 | 2940006.87 | 14 | tt
FARM | cln13 | 4519.0334 | 1 | cln
RESIDENTL | bwa23 | 1839261.5711 | 259 | bwa
RESIDENTL | smr12 | 601661.7559 | 102 | smr
NCONUML | bra31 | 17155.48 | 11 | bra
FARM | cln22 | 84599.56 | 6 | cln
RESIDENTL | moe23 | 10757204.18 | 1872 | moe
FARM | bn23 | 4995698.9571 | 709 | bn
INDUSTRIAL | bwr12 | 7576207.2428 | 317 | bwr
COMMERCIAL | elm33 | 8652520.7547 | 229 | elm
RESIDENTL | tgn12 | 769554.192 | 239 | tgn
NCONUML | bn23 | 5729.17 | 9 | bn
| cyn11 | 35169.6447 | 13 | cyn
INDUSTRIAL | wots12 | 5742170.47 | 22 | wots
INDUSTRIAL | llg12 | 8080777.31 | 18 | llg
NCONUML | ofr14 | 11958.45 | 3 | ofr
RESIDENTL | rwn34 | 11161403.5989 | 1490 | rwn
RESIDENTL | fgy12 | 975691.3435 | 398 | fgy
COMMERCIAL | wyk24 | 11852940.7836 | 290 | wyk
COMMERCIAL | smr12 | 1199230.8 | 20 | smr
INDUSTRIAL | wgl11 | 590499.13 | 17 | wgl
INDUSTRIAL | moe13 | 8896507.14 | 13 | moe
INDUSTRIAL | wots11 | 14616083.73 | 22 | wots
NCONUML | epg13 | 4325.18 | 2 | epg
NCONUML | bn22 | 72789.04 | 38 | bn
RESIDENTL | bwr23 | 15381612.1105 | 3589 | bwr
NCONUML | cln13 | 19538.3161 | 10 | cln
COMMERCIAL | bwa24 | 4350900.07 | 4 | bwa
COMMERCIAL | bwr32 | 11258727.4704 | 251 | bwr
RESIDENTL | bra32 | 8710928.5985 | 2041 | bra
FARM | klo14 | 681766.459 | 92 | klo
INDUSTRIAL | tt7 | 9353368.9205 | 125 | tt
RESIDENTL | wo11 | 815896.564 | 156 | wo
LIGHTING | mwl24 | 803944.3 | 2 | mwl
COMMERCIAL | bwr24 | 7860784.794 | 262 | bwr
COMMERCIAL | drn14 | 5284276.4061 | 147 | drn
NCONUML | hpk24 | 27055.52 | 10 | hpk
| cyn32 | 34865.18 | 48 | cyn
| bra23 | 7974.72 | 25 | bra
RESIDENTL | rve13 | 16767421.4281 | 3587 | rve
COMMERCIAL | bwn13 | 11531398.8601 | 263 | bwn
FARM | cln23 | 76487.94 | 5 | cln
NCONUML | ruba24 | 1482.28 | 4 | ruba
COMMERCIAL | msd1 | 4448954.738 | 126 | msd
| phm31 | 2299.25 | 4 | phm
LIGHTING | wn1 | 677520.74 | 1 | wn
COMMERCIAL | wt8 | 2125517.5597 | 71 | wt
RESIDENTL | bdl33 | 5101200.3632 | 906 | bdl
COMMERCIAL | rwt21 | 33203170.5825 | 281 | rwt
FARM |  | 15223.9488 | 53 | #REF!
| fgy13 | 16173.63 | 19 | fgy
| wt11 | 14907.843 | 20 | wt
RESIDENTL | mwl24 | 4259131.5949 | 729 | mwl
INDUSTRIAL | bwn12 | 375603.57 | 33 | bwn
| lyd12 | 10355.6 | 16 | lyd
| lyd13 | 31235.27 | 24 | lyd
| elm32 | 28931.8643 | 22 | elm
RESIDENTL | ldl13 | 20183081.1078 | 3515 | ldl
COMMERCIAL | epg14 | 4722560.1631 | 66 | epg
FARM | epg32 | 616929.8369 | 16 | epg
| smg23 | 6841.4304 | 12 | smg
NCONUML | mwl16 | 31954.29 | 10 | mwl
COMMERCIAL | ofr22 | 3955299.41 | 63 | ofr
FARM | wgl24 | 9990463.449 | 886 | wgl
COMMERCIAL | llg14 | 8402501.0583 | 280 | llg
COMMERCIAL | wgi24 | 3234685.3433 | 136 | wgi
FARM | cnr3 | 47812.597 | 17 | cnr
| epg33 | 55263.0616 | 6 | epg
INDUSTRIAL | bra24 | 1115020.317 | 14 | bra
NCONUML | wgi33 | 84992.31 | 23 | wgi
FARM | rwt15 | 1849.17 | 1 | rwt
RESIDENTL | ldl12 | 620798.3677 | 119 | ldl
INDUSTRIAL | bwr22 | 8606432.4227 | 334 | bwr
FARM | cf2 | 2033.193 | 1 | cf
NCONUML | klo14 | 36515.49 | 28 | klo
INDUSTRIAL | trc01 | 31629.57 | 2 | trc
RESIDENTL | lga21 | 9412760.8279 | 1623 | lga
RESIDENTL | wt13 | 15834142.0313 | 3223 | wt
RESIDENTL | cyn13 | 3260017.5153 | 858 | cyn
INDUSTRIAL | ofr21 | 138382.59 | 9 | ofr
NCONUML | sle32 | 22407.43 | 13 | sle
COMMERCIAL | lyd12 | 210380 | 9 | lyd
NCONUML | wyk23 | 87622.06 | 45 | wyk
| fgy33 | 11652.67 | 18 | fgy
INDUSTRIAL | hpk22 | 98414.21 | 14 | hpk
NCONUML | sle11 | 59204.61 | 19 | sle
RESIDENTL | bwr13 | 20902397.8318 | 4170 | bwr
COMMERCIAL | rwn34 | 3999387.7688 | 144 | rwn
| hpk22 | 19671.58 | 41 | hpk
FARM | klk22 | 332413.14 | 10 | klk
INDUSTRIAL | wn1 | 2988984.92 | 20 | wn
NCONUML | rwn26 | 27156.61 | 25 | rwn
| bwr33 | 13120.641 | 3 | bwr
NCONUML | mby11 | 20114.34 | 7 | mby
RESIDENTL | smg33 | 11198068.0634 | 2626 | smg
FARM | bn12 | 813334.585 | 146 | bn
FARM | bdl32 | 1026406.0127 | 170 | bdl
FARM | drn24 | 15422429 | 2 | drn
LIGHTING | cre21 | 378603.77 | 3 | cre
RESIDENTL | smg32 | 834640.09 | 219 | smg
| wt12 | 39199.7023 | 19 | wt
FARM | bwn14 | 804408.7 | 76 | bwn
NCONUML | bwr33 | 16865.43 | 3 | bwr
INDUSTRIAL | rwn22 | 12871.85 | 4 | rwn
NCONUML | drn11 | 63307.01 | 20 | drn
INDUSTRIAL | mwl13 | 228128.43 | 11 | mwl
COMMERCIAL | elm22 | 6567142.5918 | 154 | elm
FARM | trc01 | 521142.3328 | 100 | trc
COMMERCIAL | rwt14 | 11855990.576 | 301 | rwt
INDUSTRIAL | sle14 | 1780526.4437 | 64 | sle
RESIDENTL | smr24 | 17064871.7804 | 2952 | smr
FARM | bwa22 | 1586063.9755 | 254 | bwa
NCONUML | tt4 | 37478.54 | 17 | tt
| tt9 | 28146.8116 | 74 | tt
COMMERCIAL | epg34 | 4040655.8363 | 65 | epg
FARM | nrn11 | 7816.07 | 2 | nrn
LIGHTING | cpk23 | 1632459.3 | 1 | cpk
RESIDENTL | fgy31 | 4476808.4262 | 913 | fgy
COMMERCIAL | fgy33 | 6399813.6929 | 132 | fgy
| cnr2 | 20535.9245 | 15 | cnr
INDUSTRIAL | sle32 | 10933678.58 | 25 | sle
| bra13 | 120577.89 | 18 | bra
RESIDENTL | wgi23 | 12118480.0079 | 2685 | wgi
INDUSTRIAL | wn6 | 922850.6842 | 19 | wn
LIGHTING | tgn44 | 752.53 | 1 | tgn
RESIDENTL | wt8 | 8250779.9392 | 1851 | wt
COMMERCIAL | moe25 | 5695010.3572 | 176 | moe
FARM | wgi34 | 4315044.5216 | 374 | wgi
INDUSTRIAL | fgy32 | 667572.7217 | 61 | fgy
NCONUML | wo32 | 55386.46 | 14 | wo
INDUSTRIAL | lys36 | 1267258.48 | 1 | lys
| bn12 | 10728.35 | 13 | bn
NCONUML | brt11 | 10828.27 | 7 | brt
| drn21 | 27694.76 | 39 | drn
| drn24 | 16030.7 | 26 | drn
RESIDENTL | cpk23 | 11646034.7633 | 2466 | cpk
RESIDENTL | wots13 | 7948103.7952 | 1344 | wots
FARM | wgl23 | 3908847.1376 | 390 | wgl
COMMERCIAL | wyk13 | 4417313.7071 | 191 | wyk
NCONUML | klk21 | 10664.54 | 6 | klk
INDUSTRIAL | smg22 | 31514.93 | 2 | smg
RESIDENTL | wgi22 | 12719214.8315 | 3088 | wgi
| cpk13 | 49314.0333 | 41 | cpk
COMMERCIAL | bdl41 | 11311068.2286 | 367 | bdl
NCONUML | nrn12 | 43208.48 | 18 | nrn
RESIDENTL | fgy23 | 5177398.3937 | 1023 | fgy
NCONUML | brt21 | 3240.29 | 5 | brt
NCONUML | tgn31 | 2100.01 | 7 | tgn
RESIDENTL | mjg11 | 6256821.3625 | 1064 | mjg
INDUSTRIAL | lga24 | 175905.212 | 21 | lga
COMMERCIAL | moe21 | 6644337.36 | 291 | moe
INDUSTRIAL | bwn14 | 326743.47 | 17 | bwn
INDUSTRIAL | phm22 | 15545673.5732 | 29 | phm
LIGHTING | klo24 | 2201282.63 | 3 | klo
FARM | epg12 | 13782.33 | 2 | epg
INDUSTRIAL | cln14 | 247.5387 | 1 | cln
FARM | bge13 | 383352.554 | 75 | bge
NCONUML | bra14 | 25509.54 | 26 | bra
RESIDENTL | fgy24 | 17189073.2659 | 3574 | fgy
NCONUML | lyd14 | 37348.84 | 18 | lyd
FARM | fgy21 | 91303 | 9 | fgy
INDUSTRIAL | elm24 | 6476.78 | 2 | elm
FARM | bra24 | 985.88 | 1 | bra
COMMERCIAL | ldl24 | 1420329.0926 | 55 | ldl
INDUSTRIAL | wots24 | 329358.8434 | 32 | wots
| moe13 | 6325.43 | 5 | moe
COMMERCIAL | cyn14 | 5422735.5047 | 221 | cyn
LIGHTING | smg21 | 4640189.26 | 4 | smg
COMMERCIAL | tgn42 | 24454733.755 | 420 | tgn
INDUSTRIAL | lga14 | 502652.15 | 16 | lga
INDUSTRIAL | cre33 | 377497.19 | 17 | cre
FARM | ldl11 | 223383.36 | 16 | ldl
INDUSTRIAL | bn24 | 28582582.13 | 34 | bn
COMMERCIAL | tt1 | 14308038.8686 | 155 | tt
| wn3 | 30735.58 | 33 | wn
NCONUML | ldl21 | 10778.31 | 7 | ldl
NCONUML | wt6 | 188781.23 | 35 | wt
RESIDENTL | elm23 | 20356024.4153 | 3325 | elm
COMMERCIAL | drn11 | 4003224.2127 | 79 | drn
COMMERCIAL | bra34 | 7850026.49 | 9 | bra
FARM | cyn32 | 3133.97 | 2 | cyn
FARM | cpk23 | 18946.87 | 2 | cpk
FARM | wt15 | 5251.96 | 1 | wt
NCONUML | wgi32 | 95036.63 | 31 | wgi
COMMERCIAL | phm32 | 13343791.1884 | 221 | phm
COMMERCIAL | epg22 | 38007492.3668 | 89 | epg
INDUSTRIAL | wgl15 | 1553419.6108 | 26 | wgl
FARM | phm33 | 7138587.5126 | 545 | phm
LIGHTING | bra32 | 1301740.84 | 1 | bra
COMMERCIAL | bra22 | 30448240 | 1 | bra
COMMERCIAL | msd4 | 11090376.2999 | 395 | msd
COMMERCIAL | lyd14 | 7038791.6959 | 51 | lyd
| phi12 | 701365.4285 | 34 | phi
| nrn11 | 5120.38 | 9 | nrn
INDUSTRIAL | smg21 | 777155.28 | 5 | smg
NCONUML | nla31 | 5002.08 | 5 | nla
RESIDENTL | wyk13 | 19583843.7522 | 3346 | wyk
RESIDENTL | tgn41 | 6800482.2089 | 1104 | tgn
COMMERCIAL | fgy34 | 7285642.6158 | 201 | fgy
FARM | wgl11 | 5210774.8775 | 355 | wgl
FARM | tgn11 | 616949.6887 | 82 | tgn
NCONUML | wn5 | 5268.61 | 9 | wn
NCONUML | bdl42 | 6088.6 | 9 | bdl
INDUSTRIAL | hpk23 | 515987.93 | 6 | hpk
FARM | tgn44 | 47621.17 | 6 | tgn
| smr13 | 35140.976 | 19 | smr
| wgi31 | 18377.08 | 37 | wgi
NCONUML | bwr34 | 85519.21 | 30 | bwr
| bdl32 | 24365.9844 | 40 | bdl
COMMERCIAL | fgy13 | 5672167.28 | 57 | fgy
INDUSTRIAL | sle31 | 621920.2305 | 85 | sle
NCONUML | cyn23 | 72679.67 | 24 | cyn
NCONUML | hpk22 | 92149.17 | 38 | hpk
RESIDENTL | cre23 | 13902510.3441 | 3180 | cre
COMMERCIAL | lga21 | 4415159.211 | 179 | lga
| cre33 | 51988.0123 | 70 | cre
INDUSTRIAL | bra32 | 800790.5812 | 33 | bra
| rwn26 | 43959.1499 | 36 | rwn
NCONUML | ftr22 | 27457.1971 | 11 | ftr
FARM | cyn23 | 28738.28 | 3 | cyn
FARM | wn2 | 2722540.844 | 262 | wn
FARM | wots25 | 1192605.1156 | 155 | wots
COMMERCIAL | lga11 | 2601951.4442 | 115 | lga
COMMERCIAL | cnr1 | 836269.15 | 40 | cnr
RESIDENTL | cre22 | 15737441.9951 | 3931 | cre
RESIDENTL | cyn24 | 3227627.7482 | 729 | cyn
| drn14 | 42739.5968 | 43 | drn
NCONUML | wgi34 | 240.62 | 2 | wgi
COMMERCIAL | mdi1 | 200221.43 | 4 | mdi
LIGHTING | lga22 | 290997.27 | 1 | lga
RESIDENTL | sle13 | 2426821.6594 | 1643 | sle
RESIDENTL | mby12 | 3267894.3821 | 609 | mby
FARM | wgi31 | 368672.79 | 43 | wgi
INDUSTRIAL | cyn24 | 15644182.2427 | 207 | cyn
| fgy34 | 3433.61 | 11 | fgy
RESIDENTL | bge11 | 15368827.4604 | 2654 | bge
RESIDENTL | ftr12 | 3825364.7454 | 636 | ftr
| mfa21 | 17049.39 | 26 | mfa
COMMERCIAL | wgi21 | 45541.7604 | 2 | wgi
INDUSTRIAL | wo14 | 2975508 | 24 | wo
COMMERCIAL | wgl12 | 5759083.9004 | 210 | wgl
INDUSTRIAL | moe23 | 765740.5661 | 26 | moe
COMMERCIAL | hpk14 | 5487941.7 | 85 | hpk
NCONUML | tt2 | 10017.24 | 3 | tt
INDUSTRIAL | cpk13 | 1507420.269 | 6 | cpk
INDUSTRIAL | lga41 | 52440142.6 | 1 | lga
NCONUML | elm26 | 60173.53 | 25 | elm
FARM | cf1 | 12492.747 | 1 | cf
RESIDENTL | bwr32 | 11435795.4629 | 2903 | bwr
NCONUML | cln23 | 19017.15 | 5 | cln
RESIDENTL | bdl41 | 18711766.0554 | 3582 | bdl
RESIDENTL | tt4 | 9918702.5206 | 2673 | tt
NCONUML | nrn13 | 44749.68 | 14 | nrn
NCONUML | mwl12 | 43601.75 | 11 | mwl
FARM | cln12 | 30466.72 | 1 | cln
INDUSTRIAL | cpk21 | 122110.94 | 5 | cpk
NCONUML | epg11 | 2275 | 2 | epg
FARM | brt22 | 1064314.9433 | 146 | brt
NCONUML | moe21 | 60919.67 | 15 | moe
RESIDENTL | ldl22 | 4948357.507 | 1104 | ldl
INDUSTRIAL | epg22 | 206880.17 | 13 | epg
NCONUML | cln12 | 55224.6632 | 17 | cln
| wo14 | 16653.0726 | 14 | wo
INDUSTRIAL | wo13 | 14774006.15 | 3 | wo
INDUSTRIAL | wgi22 | 729700.7 | 28 | wgi
COMMERCIAL | msd2 | 2629949.014 | 87 | msd
NCONUML | ldl22 | 11421.24 | 5 | ldl
RESIDENTL | wo22 | 17812297.6729 | 4125 | wo
FARM | mwl25 | 2028215.2676 | 224 | mwl
| cln14 | 46492.03 | 68 | cln
INDUSTRIAL | smr14 | 413387.45 | 34 | smr
FARM | rwn33 | 39914.72 | 5 | rwn
NCONUML | tt7 | 28203.83 | 11 | tt
INDUSTRIAL | lga11 | 317451.8284 | 16 | lga
INDUSTRIAL | tt12 | 6074893.6495 | 86 | tt
INDUSTRIAL | rwn32 | 87972.96 | 1 | rwn
RESIDENTL | myt21 | 10899844.0445 | 1487 | myt
RESIDENTL | cyn14 | 9596207.6734 | 2758 | cyn
RESIDENTL | kms11 | 9874885.3712 | 1972 | kms
COMMERCIAL | wo32 | 9961950.2687 | 147 | wo
NCONUML | hpk21 | 96497.83 | 40 | hpk
FARM | mwl13 | 248036.6173 | 7 | mwl
RESIDENTL | smr23 | 3447913.5369 | 523 | smr
INDUSTRIAL | nla32 | 1443086.18 | 25 | nla
| rwt32 | 35174.87 | 36 | rwt
INDUSTRIAL | moe11 | 65970.59 | 6 | moe
INDUSTRIAL | wo33 | 33298223.9508 | 7 | wo
INDUSTRIAL | bra31 | 2919.84 | 1 | bra
RESIDENTL | moe15 | 9740983.6859 | 1552 | moe
RESIDENTL | moe12 | 4538532.291 | 887 | moe
INDUSTRIAL | bdl41 | 1328921.5447 | 34 | bdl
NCONUML | tt6 | 36560.52 | 20 | tt
RESIDENTL | uwy1 | 6496143.3356 | 1032 | uwy
RESIDENTL | wgi32 | 16438958.2366 | 3917 | wgi
COMMERCIAL | rwn31 | 2125446.8547 | 72 | rwn
| ldl13 | 45979.2126 | 34 | ldl
LIGHTING | hpk23 | 2010173.36 | 1 | hpk
RESIDENTL | fgy14 | 9703108.5669 | 2483 | fgy
FARM | rwn24 | 30208.83 | 4 | rwn
COMMERCIAL | wo23 | 11409957.4027 | 304 | wo
| myt12 | 115131.3847 | 34 | myt
| bge13 | 13458.3255 | 19 | bge
| sle32 | 15918.6359 | 20 | sle
FARM | epg11 | 14625.27 | 2 | epg
NCONUML | mwl21 | 34561.25 | 17 | mwl
COMMERCIAL | nrn12 | 21654160.6835 | 271 | nrn
COMMERCIAL | llg13 | 15983000.2277 | 99 | llg
| lga22 | 14116.8478 | 12 | lga
FARM | hpk11 | 14620.89 | 5 | hpk
RESIDENTL | ofr11 | 25072251.243 | 5672 | ofr
FARM | ftr12 | 9732520.1395 | 879 | ftr
RESIDENTL | epg21 | 580054.4394 | 151 | epg
FARM | bge22 | 343097.1961 | 60 | bge
COMMERCIAL | sfs1 | 1879673.1771 | 124 | sfs
| cln24 | 61460.6675 | 37 | cln
NCONUML | smg22 | 48204.28 | 25 | smg
RESIDENTL | phm34 | 11301839.7716 | 2904 | phm
RESIDENTL | phm31 | 2762476.4376 | 550 | phm
NCONUML | smr13 | 69764.68 | 26 | smr
RESIDENTL | wyk12 | 12357178.5976 | 1789 | wyk
INDUSTRIAL | sle13 | 125251.914 | 47 | sle
FARM | phm24 | 689286.43 | 52 | phm
| cre31 | 63798.4484 | 85 | cre
INDUSTRIAL | bge12 | 121322.77 | 7 | bge
FARM | wots12 | 5076.62 | 1 | wots
NCONUML | cf1 | 1922.85 | 2 | cf
RESIDENTL | wo31 | 20016820.444 | 4554 | wo
FARM | smr22 | 1275801.32 | 154 | smr
FARM | lga22 | 1443457.6222 | 105 | lga
COMMERCIAL | mwl22 | 10003347.9587 | 192 | mwl
FARM | bn24 | 2239563.0749 | 370 | bn
NCONUML | wots25 | 45798.68 | 13 | wots
NCONUML | wgi31 | 79233.36 | 21 | wgi
FARM | epg23 | 30049.96 | 2 | epg
NCONUML | klk11 | 24723.1 | 13 | klk
| mwl14 | 3593.32 | 2 | mwl
RESIDENTL | mdg1 | 4384126.608 | 684 | mdg
RESIDENTL | nrn14 | 9562152.1887 | 1877 | nrn
LIGHTING | msd4 | 139319.89 | 1 | msd
LIGHTING | sfs1 | 1558457.9 | 1 | sfs
| klo14 | 120043.1087 | 185 | klo
RESIDENTL | hpk14 | 17025183.7337 | 3944 | hpk
FARM | lga12 | 4046898.7707 | 351 | lga
COMMERCIAL | ldl14 | 12475957.7156 | 266 | ldl
RESIDENTL | bn11 | 14382992.5485 | 2912 | bn
COMMERCIAL | bdl34 | 6213094.4744 | 204 | bdl
FARM | lyd11 | 23799.7 | 3 | lyd
| mwl22 | 10189.434 | 23 | mwl
NCONUML | cf2 | 120.31 | 1 | cf
| epg32 | 18473.04 | 31 | epg
RESIDENTL | bdl34 | 21922135.2151 | 5106 | bdl
COMMERCIAL | rwn26 | 3719056.4225 | 81 | rwn
INDUSTRIAL | mby13 | 219583.33 | 2 | mby
NCONUML | fgy33 | 40029.49 | 14 | fgy
| ftr22 | 13372.1897 | 14 | ftr
NCONUML | mwl13 | 53127.87 | 17 | mwl
INDUSTRIAL | rwt32 | 132361.99 | 4 | rwt
COMMERCIAL | phm23 | 17053480.4 | 2 | phm
COMMERCIAL | bra13 | 19208526.3529 | 181 | bra
FARM | wn1 | 37241.96 | 7 | wn
FARM | bm8b33 | 1540.9 | 2 | bmb
COMMERCIAL | wt10 | 13883699.3972 | 155 | wt
INDUSTRIAL | uwy1 | 90405.23 | 3 | uwy
RESIDENTL | ldl23 | 26005181.5029 | 4084 | ldl
FARM | klo24 | 194259.84 | 22 | klo
| hpk11 | 33718.6052 | 42 | hpk
NCONUML | phm33 | 47915.862 | 19 | phm
FARM | wn6 | 4543418.3442 | 605 | wn
COMMERCIAL | cyn21 | 3633643.5973 | 195 | cyn
INDUSTRIAL | wo22 | 393144.5 | 11 | wo
RESIDENTL | tgn42 | 795534.2193 | 223 | tgn
INDUSTRIAL | mwl23 | 715134.0252 | 54 | mwl
| rwt22 | 26934.55 | 52 | rwt
COMMERCIAL | phm31 | 4117822.4369 | 32 | phm
RESIDENTL | epg22 | 39578.43 | 14 | epg
RESIDENTL | nla32 | 6559402.1513 | 1220 | nla
RESIDENTL | myt22 | 1017937.6841 | 120 | myt
| wgl15 | 30619.4 | 19 | wgl
LIGHTING | mjg11 | 68938.73 | 1 | mjg
COMMERCIAL | phi12 | 2400712.314 | 73 | phi
COMMERCIAL | rwt36 | 2264519.95 | 43 | rwt
INDUSTRIAL | wgi23 | 157973.74 | 15 | wgi
NCONUML | elm24 | 74942.52 | 25 | elm
RESIDENTL | wt10 | 3332972.5881 | 860 | wt
NCONUML | ruba22 | 360.93 | 3 | ruba
FARM | phi11 | 82538.05 | 19 | phi
| bra11 | 11169.2884 | 32 | bra
INDUSTRIAL | moe15 | 1465208.8927 | 46 | moe
| tt5 | 13084.5535 | 33 | tt
LIGHTING | elm34 | 2971413.79 | 6 | elm
FARM | rwt25 | 33966.32 | 4 | rwt
RESIDENTL | moe11 | 9711471.9521 | 1967 | moe
INDUSTRIAL | rwt22 | 12240.297 | 2 | rwt
FARM | tgn23 | 1979366.6929 | 215 | tgn
COMMERCIAL | elm34 | 4840398.0166 | 153 | elm
NCONUML | phi11 | 19831.48 | 5 | phi
NCONUML | bra13 | 31922.03 | 14 | bra
RESIDENTL | mwl11 | 7113484.1589 | 1047 | mwl
| sle14 | 9929.5555 | 28 | sle
COMMERCIAL | cpk11 | 7316179.79 | 51 | cpk
| cyn31 | 5192.9 | 11 | cyn
NCONUML | epg12 | 1563.57 | 9 | epg
| epg11 | 4794.77 | 9 | epg
INDUSTRIAL | bwa23 | 17470876.21 | 8 | bwa
FARM | cln21 | 792.83 | 1 | cln
COMMERCIAL | wn3 | 8489705.5245 | 275 | wn
COMMERCIAL | bwn12 | 29123057.9665 | 274 | bwn
NCONUML | bra23 | 28962.5293 | 21 | bra
| bge12 | 5967.8256 | 14 | bge
INDUSTRIAL | tgn12 | 464065.58 | 15 | tgn
LIGHTING | fgy31 | 1047083.29 | 1 | fgy
NCONUML | moe25 | 63582.44 | 18 | moe
NCONUML | fgy21 | 30728.13 | 12 | fgy
INDUSTRIAL | lyd11 | 151654.68 | 9 | lyd
FARM | bwn13 | 5960.02 | 1 | bwn
RESIDENTL | lga11 | 6965787.8425 | 1044 | lga
NCONUML | bwr22 | 31744.79 | 14 | bwr
COMMERCIAL | llg12 | 3977405.3306 | 115 | llg
COMMERCIAL | mfa21 | 3716072.0048 | 197 | mfa
INDUSTRIAL | phm32 | 1008.48 | 1 | phm
COMMERCIAL | nrn13 | 3605622.38 | 41 | nrn
FARM | cyn22 | 1131.4275 | 1 | cyn
INDUSTRIAL | ftr23 | 1828762.8842 | 76 | ftr
INDUSTRIAL | mfa31 | 463955.39 | 14 | mfa
INDUSTRIAL | bge11 | 395339.98 | 10 | bge
RESIDENTL | wo13 | 2691801.805 | 586 | wo
RESIDENTL | llg11 | 4969161.4408 | 709 | llg
| cpk21 | 8908.612 | 12 | cpk
INDUSTRIAL | cre23 | 238715.04 | 8 | cre
COMMERCIAL | epg33 | 43303826.6612 | 357 | epg
FARM | ofr21 | 60907.55 | 6 | ofr
COMMERCIAL | cpk22 | 8802072.7366 | 32 | cpk
NCONUML | bra24 | 34184.91 | 27 | bra
NCONUML | wn6 | 84222.69 | 35 | wn
FARM | mfa22 | 15017348.1505 | 702 | mfa
FARM | lga24 | 2675198.7919 | 323 | lga
COMMERCIAL | phi13 | 13565764.588 | 480 | phi
FARM | lga13 | 6142984.8245 | 572 | lga
NCONUML | wn2 | 74469.51 | 25 | wn
COMMERCIAL | wyk23 | 9043742.9219 | 306 | wyk
INDUSTRIAL | cyn31 | 110897.03 | 2 | cyn
RESIDENTL | wt7 | 9398293.9689 | 2293 | wt
COMMERCIAL | rwt15 | 2407529.701 | 118 | rwt
| wots11 | 29868.01 | 43 | wots
COMMERCIAL | wt12 | 9788397.4198 | 246 | wt
FARM | wots24 | 5049980.8194 | 706 | wots
COMMERCIAL | ftr22 | 3919173.7529 | 139 | ftr
INDUSTRIAL | ruba12 | 859698.6565 | 35 | ruba
| wots25 | 37134.4365 | 43 | wots
RESIDENTL | ofr24 | 14317680.0438 | 3420 | ofr
COMMERCIAL | bdl32 | 9327480.3168 | 349 | bdl
NCONUML | trc01 | 2600.11 | 1 | trc
RESIDENTL | wgi33 | 15074294.4922 | 2906 | wgi
RESIDENTL | wyk24 | 16651462.561 | 3130 | wyk
NCONUML | wn1 | 109135.95 | 32 | wn
NCONUML | fgy34 | 69468.4 | 26 | fgy
| tgn43 | 23585.3 | 37 | tgn
| bwn11 | 22540.96 | 33 | bwn
COMMERCIAL | bn11 | 11469939.8143 | 448 | bn
RESIDENTL | wn7 | 334597.06 | 81 | wn
FARM | lga23 | 6580772.0568 | 604 | lga
RESIDENTL | mby13 | 1114988.13 | 129 | mby
INDUSTRIAL | moe12 | 309363.05 | 10 | moe
NCONUML | wgl21 | 72341.71 | 26 | wgl
| rwn22 | 13422.17 | 20 | rwn
FARM | ofr13 | 1726.88 | 2 | ofr
INDUSTRIAL | smg33 | 3791.86 | 1 | smg
COMMERCIAL | cnr2 | 2241662.7301 | 123 | cnr
NCONUML | bwn13 | 114734.08 | 27 | bwn
INDUSTRIAL | tgn43 | 8336.37 | 2 | tgn
NCONUML | bra33 | 54640.5039 | 38 | bra
LIGHTING | drn23 | 137376.82 | 1 | drn
COMMERCIAL | wt11 | 6045415.4763 | 137 | wt
| wo23 | 3425.76 | 13 | wo
RESIDENTL | drn11 | 23689909.4015 | 5897 | drn
RESIDENTL | bra33 | 17227071.6094 | 3920 | bra
FARM | cre21 | 1165190.53 | 9 | cre
| wo32 | 20472.5797 | 26 | wo
NCONUML | mfa22 | 12133.93 | 8 | mfa
COMMERCIAL | fgy32 | 10874129.2215 | 316 | fgy
INDUSTRIAL | bdl33 | 6444229.03 | 34 | bdl
NCONUML | cnr3 | 880.96 | 3 | cnr
COMMERCIAL | bwr14 | 64319.73 | 1 | bwr
NCONUML | ldl11 | 15379.88 | 9 | ldl
FARM | bdl33 | 333127.23 | 48 | bdl
INDUSTRIAL | elm23 | 351538.3612 | 12 | elm
NCONUML | lga14 | 16509.29 | 6 | lga
NCONUML | rwt21 | 45520.76 | 13 | rwt
INDUSTRIAL | mwl24 | 3823292.43 | 15 | mwl
RESIDENTL | epg14 | 8906284.5994 | 2218 | epg
NCONUML | drn21 | 11559.57 | 6 | drn
FARM | ldl21 | 4274.77 | 1 | ldl
| lga14 | 13272.15 | 11 | lga
LIGHTING | wo22 | 1145144.2306 | 3 | wo
LIGHTING | bdl33 | 755365.47 | 1 | bdl
INDUSTRIAL | lga12 | 340570.559 | 7 | lga
RESIDENTL | ofr23 | 20573594.8025 | 3065 | ofr
LIGHTING | tgn12 | 393.8997 | 1 | tgn
RESIDENTL | fgy32 | 4718000.0914 | 1180 | fgy
COMMERCIAL | moe11 | 6876107.6583 | 169 | moe
COMMERCIAL | wgl13 | 16726185.3211 | 289 | wgl
COMMERCIAL | cre22 | 19152716.1468 | 212 | cre
RESIDENTL | drn12 | 16081122.8597 | 3986 | drn
COMMERCIAL | mfa23 | 8005013.26 | 78 | mfa
| cln13 | 39224.5517 | 61 | cln
INDUSTRIAL | mfa22 | 1793714.26 | 36 | mfa
LIGHTING | smr23 | 37560.88 | 1 | smr
RESIDENTL | rwn32 | 6727398.7344 | 1603 | rwn
FARM | lga14 | 4550189.1065 | 436 | lga
| cln12 | 24735.6225 | 51 | cln
COMMERCIAL | kms11 | 4936701.5866 | 120 | kms
RESIDENTL | smr14 | 10997106.9114 | 1697 | smr
| epg13 | 194183.3358 | 102 | epg
| brt21 | 9723.1397 | 7 | brt
INDUSTRIAL | drn12 | 10032.09 | 2 | drn
| tt7 | 34871.95 | 3 | tt
INDUSTRIAL | wots25 | 7153785.931 | 7 | wots
FARM | tgn43 | 14451.81 | 2 | tgn
NCONUML | ldl14 | 38917.21 | 26 | ldl
INDUSTRIAL | brt21 | 238786.6 | 10 | brt
| llg11 | 8477.8 | 10 | llg
RESIDENTL | wgi24 | 12721878.952 | 3596 | wgi
RESIDENTL | cyn21 | 10508542.767 | 2257 | cyn
INDUSTRIAL | bra11 | 3982632.29 | 3 | bra
INDUSTRIAL | phi11 | 184139.3994 | 13 | phi
| hpk24 | 8609.4373 | 14 | hpk
NCONUML | ldl13 | 24965.12 | 22 | ldl
RESIDENTL | hpk21 | 20637351.8958 | 5254 | hpk
RESIDENTL | wgl13 | 19626090.0794 | 4751 | wgl
COMMERCIAL | elm21 | 12124007.57 | 258 | elm
COMMERCIAL | wt13 | 23168272.4303 | 498 | wt
| hpk23 | 55023.71 | 41 | hpk
COMMERCIAL | mdg1 | 1157212.0402 | 52 | mdg
NCONUML | wt11 | 64055.27 | 25 | wt
NCONUML | phm31 | 9383.328 | 4 | phm
COMMERCIAL | bge23 | 4904566.2339 | 176 | bge
NCONUML | smg23 | 17942.69 | 11 | smg
| mwl16 | 4764.4783 | 12 | mwl
COMMERCIAL | hpk12 | 20352329.5415 | 361 | hpk
RESIDENTL | ruba24 | 4395729.6843 | 894 | ruba
COMMERCIAL | nla32 | 3390681.6399 | 175 | nla
NCONUML | lyd12 | 44439.84 | 9 | lyd
| cln22 | 289385.5413 | 85 | cln
NCONUML | cpk21 | 53769.1 | 26 | cpk
| ruba22 | 8482.6526 | 15 | ruba
COMMERCIAL | myt22 | 191990.12 | 18 | myt
RESIDENTL | mby11 | 5261006.6685 | 922 | mby
RESIDENTL | rwn26 | 21195116.3973 | 2454 | rwn
| rwt31 | 14608.62 | 19 | rwt
INDUSTRIAL | epg35 | 1615230.05 | 4 | epg
| bge23 | 30837.693 | 28 | bge
NCONUML | bdl34 | 70291.97 | 25 | bdl
NCONUML | ofr13 | 30258.73 | 11 | ofr
| klk11 | 25230.2094 | 21 | klk
NCONUML | bn12 | 1241.66 | 2 | bn
COMMERCIAL | wgi32 | 5461052.6827 | 195 | wgi
NCONUML | ldl12 | 45990.38 | 14 | ldl
INDUSTRIAL | bra23 | 3394433.4433 | 42 | bra
| wo33 | 4138.8 | 1 | wo
NCONUML | myt12 | 33269.22 | 16 | myt
INDUSTRIAL | ldl11 | 1468879.69 | 10 | ldl
RESIDENTL | msd1 | 8481569.4252 | 1750 | msd
NCONUML | bn11 | 57126.91 | 28 | bn
INDUSTRIAL | ftr12 | 2824402.5 | 31 | ftr
INDUSTRIAL | hpk11 | 29483.41 | 8 | hpk
NCONUML | epg33 | 5589.26 | 2 | epg
COMMERCIAL | wo31 | 10532525.1457 | 139 | wo
| wgl21 | 38182.04 | 53 | wgl
| bge22 | 25062.3495 | 31 | bge
RESIDENTL | tt1 | 171030.69 | 8 | tt
INDUSTRIAL | bwr34 | 134229.36 | 26 | bwr
COMMERCIAL | bra33 | 14409139.6368 | 303 | bra
COMMERCIAL | bdl44 | 4495186.894 | 197 | bdl
| bwn13 | 12482.8878 | 14 | bwn
NCONUML | wn3 | 40552.61 | 16 | wn
NCONUML | smr24 | 41055.27 | 16 | smr
INDUSTRIAL | mwl14 | 4499194.0326 | 50 | mwl
| wots24 | 36833.8626 | 36 | wots
NCONUML | wt12 | 74491.29 | 36 | wt
COMMERCIAL | smg31 | 17181337.4 | 81 | smg
FARM | lyd13 | 146611.14 | 18 | lyd
NCONUML | wots12 | 53576.05 | 15 | wots
INDUSTRIAL | fgy12 | 30820.7097 | 2 | fgy
FARM | myt12 | 4025860.4278 | 600 | myt
INDUSTRIAL | cyn22 | 204983.76 | 12 | cyn
COMMERCIAL | cyn33 | 3196035.4476 | 122 | cyn
COMMERCIAL | mby12 | 1853426.4391 | 89 | mby
NCONUML | tgn43 | 111938.06 | 34 | tgn
NCONUML | wo11 | 17571.55 | 5 | wo
INDUSTRIAL | epg12 | 1405424.52 | 3 | epg
| cf2 | 30699.57 | 2 | cf
COMMERCIAL | llg11 | 3213282.749 | 85 | llg
LIGHTING | rwn24 | 1936572.72 | 3 | rwn
INDUSTRIAL | cln24 | 15633.29 | 3 | cln
FARM | sle31 | 4999785.6618 | 315 | sle
INDUSTRIAL | cf1 | 129164.746 | 4 | cf
| ruba12 | 126134.0367 | 24 | ruba
| bwr12 | 18318.3952 | 15 | bwr
FARM | elm32 | 382389.8968 | 32 | elm
| ofr21 | 113717.1 | 52 | ofr
INDUSTRIAL | wn2 | 282430.54 | 13 | wn
NCONUML | bge22 | 82280.88 | 49 | bge
NCONUML | cnr2 | 33661.17 | 17 | cnr
NCONUML | wots13 | 10386.18 | 6 | wots
FARM | elm24 | 39172.3194 | 4 | elm
COMMERCIAL | nrn14 | 6896476.1265 | 116 | nrn
NCONUML | ruba12 | 27603.68 | 16 | ruba
NCONUML | hpk13 | 50290.3 | 16 | hpk
NCONUML | bra11 | 44798.92 | 35 | bra
| rwt21 | 23376.2409 | 6 | rwt
RESIDENTL | drn23 | 20613814.4846 | 2434 | drn
RESIDENTL | rwt36 | 2676215.9999 | 821 | rwt
RESIDENTL | llg13 | 6857833.0372 | 1230 | llg
COMMERCIAL | wyk12 | 4295149.2844 | 131 | wyk
INDUSTRIAL | ofr13 | 1622296.11 | 21 | ofr
| bra14 | 30334.7783 | 42 | bra
INDUSTRIAL | tgn11 | 3321263.75 | 18 | tgn
LIGHTING | mby13 | 9944.78 | 1 | mby
RESIDENTL | cln11 | 39284605.9906 | 12154 | cln
COMMERCIAL | drn22 | 10741065.2473 | 246 | drn
RESIDENTL | wo32 | 11244170.0715 | 2343 | wo
| bra33 | 27895.4569 | 47 | bra
COMMERCIAL | epg21 | 21867278.1603 | 75 | epg
INDUSTRIAL | cre21 | 293542.6 | 2 | cre
RESIDENTL | bwr24 | 1834966.95 | 415 | bwr
RESIDENTL | hpk13 | 8888406.848 | 2283 | hpk
NCONUML | moe13 | 240.62 | 2 | moe
RESIDENTL | mwl12 | 3605926.3697 | 887 | mwl
| elm24 | 29520.3106 | 27 | elm
COMMERCIAL | tgn31 | 5251765.7474 | 163 | tgn
| rwt25 | 17882.0217 | 23 | rwt
RESIDENTL | moe21 | 9438147.1697 | 1978 | moe
COMMERCIAL | mjg11 | 16973320.0649 | 258 | mjg
COMMERCIAL | moe22 | 1619971.835 | 34 | moe
NCONUML | cpk13 | 44472.2623 | 32 | cpk
| phi11 | 13149.9006 | 9 | phi
FARM | cyn11 | 2814.65 | 1 | cyn
FARM | cyn24 | 25049.8 | 2 | cyn
FARM | drn13 | 379220.8035 | 25 | drn
COMMERCIAL | mwe236 | 663523.2 | 21 | mwe
INDUSTRIAL | phm24 | 35612.08 | 4 | phm
INDUSTRIAL | bge22 | 36211.2493 | 9 | bge
RESIDENTL | cnr1 | 478523.9112 | 104 | cnr
| lga24 | 10918.35 | 11 | lga
NCONUML | sle14 | 98131.7526 | 34 | sle
NCONUML | tt5 | 14462.54 | 12 | tt
| epg12 | 53720.6497 | 70 | epg
NCONUML | kms11 | 42647.24 | 13 | kms
FARM | elm23 | 38507.8 | 8 | elm
COMMERCIAL | cyn12 | 12045879.7132 | 241 | cyn
INDUSTRIAL | fgy23 | 1420677.79 | 11 | fgy
COMMERCIAL | mfa14 | 259168.13 | 17 | mfa
| bra31 | 49797.7422 | 13 | bra
COMMERCIAL | mwl12 | 1780079.4127 | 78 | mwl
| bwr22 | 2405.71 | 25 | bwr
INDUSTRIAL | fgy24 | 415478.9 | 15 | fgy
COMMERCIAL | hpk13 | 9763023.5697 | 134 | hpk
| cyn22 | 22272.33 | 22 | cyn
| ldl21 | 13369.5383 | 42 | ldl
| wt6 | 17591.4373 | 23 | wt
RESIDENTL | wn4 | 11276854.4814 | 2349 | wn
FARM | mwl14 | 451834.7532 | 54 | mwl
RESIDENTL | bm8b31 | 357131.6719 | 111 | bmb
NCONUML | cyn14 | 48577.9677 | 22 | cyn
FARM | cre32 | 5136.47 | 1 | cre
FARM | bwr34 | 4550.33 | 1 | bwr
RESIDENTL | llg14 | 14855712.1657 | 2170 | llg
FARM | smg33 | 29400.19 | 7 | smg
RESIDENTL | drn22 | 21996972.8148 | 3999 | drn
NCONUML | elm32 | 42948.38 | 25 | elm
INDUSTRIAL | klo14 | 587332.99 | 17 | klo
| tgn11 | 22256.53 | 32 | tgn
INDUSTRIAL | tgn44 | 4536032.57 | 9 | tgn
COMMERCIAL | ldl23 | 15994398.5627 | 272 | ldl
| wn6 | 146062.0009 | 59 | wn
COMMERCIAL | tt2 | 18806104.6367 | 399 | tt
COMMERCIAL | brt11 | 4047117.81 | 129 | brt
NCONUML | llg14 | 65195.01 | 40 | llg
FARM | fgy24 | 95940.3 | 9 | fgy
NCONUML | fgy14 | 61562.37 | 33 | fgy
COMMERCIAL | rve12 | 3272242.91 | 54 | rve
INDUSTRIAL | cpk23 | 208291.634 | 5 | cpk
| lga23 | 41697.3391 | 21 | lga
INDUSTRIAL | yn38 | 642769.3081 | 6 | yn
COMMERCIAL | bwa21 | 7920817.52 | 6 | bwa
INDUSTRIAL | elm25 | 2097.04 | 1 | elm
COMMERCIAL | wots13 | 3416108.1488 | 213 | wots
FARM | wgi22 | 191494.2501 | 24 | wgi
NCONUML | fgy13 | 27847.71 | 7 | fgy
| bra24 | 9840.15 | 27 | bra
FARM | ofr14 | 100163.6258 | 21 | ofr
NCONUML | nrn11 | 16820.36 | 5 | nrn
RESIDENTL | smg31 | 12434679.8443 | 2879 | smg
COMMERCIAL | smr24 | 15083854.4686 | 348 | smr
| lyd11 | 12152.66 | 25 | lyd
INDUSTRIAL | bra12 | 1282907.1727 | 55 | bra
FARM | wgl15 | 3297105.6723 | 233 | wgl
INDUSTRIAL | msd1 | 544058.7154 | 15 | msd
| epg31 | 13971.3347 | 31 | epg
INDUSTRIAL | wgl23 | 572354.5027 | 44 | wgl
INDUSTRIAL | cpk12 | 343353.79 | 14 | cpk
INDUSTRIAL | mfa34 | 4790944.63 | 37 | mfa
| wn2 | 65478.1843 | 60 | wn
INDUSTRIAL | drn23 | 222019.33 | 21 | drn
| klo11 | 24997.4 | 1 | klo
COMMERCIAL | cyn13 | 11562540.4133 | 213 | cyn
| tgn44 | 15598.29 | 27 | tgn
| wn1 | 5093 | 9 | wn
NCONUML | wots24 | 22958.48 | 11 | wots
RESIDENTL | ftr21 | 5974099.1685 | 1654 | ftr
NCONUML | wgl11 | 116770.29 | 32 | wgl
FARM | phm22 | 2513172.8482 | 159 | phm
| mfa22 | 25912.0235 | 15 | mfa
| tt2 | 5693.01 | 1 | tt
RESIDENTL | cyn12 | 11384819.6049 | 2642 | cyn
COMMERCIAL | mby11 | 1920906.95 | 83 | mby
RESIDENTL | bdl42 | 7579399.6648 | 1528 | bdl
COMMERCIAL | sle11 | 16789466.3124 | 430 | sle
COMMERCIAL | bdl42 | 3935066.2305 | 228 | bdl
NCONUML | rwn22 | 25304.89 | 19 | rwn
INDUSTRIAL | cre32 | 1414910.91 | 33 | cre
INDUSTRIAL | bwn11 | 121807.37 | 8 | bwn
NCONUML | smr22 | 29006.3 | 13 | smr
RESIDENTL | phm24 | 12991887.5254 | 2975 | phm
RESIDENTL | phm21 | 5600884.0097 | 1319 | phm
NCONUML | ldl23 | 93357.12 | 44 | ldl
RESIDENTL | ldl24 | 19255310.9766 | 3964 | ldl
INDUSTRIAL | bra21 | 9682528.358 | 10 | bra
| sle31 | 21276.5675 | 34 | sle
| myt11 | 11671.01 | 10 | myt
RESIDENTL | elm21 | 10927220.6891 | 2208 | elm
COMMERCIAL | epg13 | 13081700.0195 | 121 | epg
COMMERCIAL | hpk21 | 6771211.022 | 80 | hpk
NCONUML | bwr12 | 55323.1848 | 22 | bwr
| trc01 | 7370.1419 | 1 | trc
| epg35 | 12733.43 | 3 | epg
INDUSTRIAL | bge21 | 30163.23 | 3 | bge
RESIDENTL | tgn31 | 10330935.5842 | 1504 | tgn
COMMERCIAL | moe23 | 8180066.6029 | 204 | moe
FARM | bra21 | 5211.11 | 2 | bra
LIGHTING | llg12 | 9573.66 | 1 | llg
RESIDENTL | bdl31 | 18828777.9984 | 3534 | bdl
COMMERCIAL | nla31 | 1365542.8767 | 73 | nla
INDUSTRIAL | klo24 | 421040.3606 | 14 | klo
FARM | bdl43 | 35833.9 | 4 | bdl
FARM | cyn31 | 3324.08 | 1 | cyn
FARM | sle14 | 508528.62 | 59 | sle
FARM | fgy34 | 3609.3 | 1 | fgy
RESIDENTL | elm26 | 19204314.084 | 3128 | elm
COMMERCIAL | ldl13 | 4974121.0157 | 271 | ldl
NCONUML | tgn42 | 32526.3 | 9 | tgn
RESIDENTL | nrn13 | 11128338.9236 | 2708 | nrn
| drn13 | 33230.29 | 35 | drn
RESIDENTL | mfa14 | 15628.16 | 8 | mfa
RESIDENTL | rwt14 | 5266292.5405 | 1232 | rwt
FARM | ftr23 | 7584335.745 | 587 | ftr
FARM | moe12 | 2890738.1544 | 266 | moe
RESIDENTL | klk21 | 6022162.144 | 692 | klk
COMMERCIAL | bn22 | 11917129.8815 | 407 | bn
COMMERCIAL | cln13 | 10498926.3291 | 102 | cln
INDUSTRIAL | cln11 | 955300.36 | 11 | cln
FARM | bge11 | 1450445.3683 | 132 | bge
| mwl25 | 368.2898 | 2 | mwl
| rwn33 | 13688.96 | 19 | rwn
| bdl43 | 33766.9817 | 15 | bdl
NCONUML | cln14 | 95979.5703 | 31 | cln
NCONUML | lga24 | 7306.35 | 4 | lga
| bn23 | 36133.4118 | 23 | bn
| ofr14 | 18460.3638 | 32 | ofr
FARM | wo14 | 29381.84 | 3 | wo
FARM | cln24 | 15169.45 | 1 | cln
FARM | smg21 | 2813.13 | 1 | smg
FARM | uwy1 | 50419.26 | 6 | uwy
RESIDENTL | cpk11 | 18255270.9798 | 3705 | cpk
INDUSTRIAL | rwn34 | 151721.8975 | 12 | rwn
FARM | mfa34 | 8352796.4311 | 398 | mfa
INDUSTRIAL | cyn23 | 283668.3977 | 39 | cyn
COMMERCIAL | cln23 | 7919442.4187 | 94 | cln
| rwn24 | 145239.1574 | 36 | rwn
INDUSTRIAL | cln21 | 91173.7471 | 8 | cln
INDUSTRIAL | wots23 | 9771996.01 | 2 | wots
COMMERCIAL | ofr23 | 7962081.4442 | 137 | ofr
FARM | cln11 | 5358747.3528 | 175 | cln
INDUSTRIAL | epg23 | 1603069.098 | 49 | epg
NCONUML | elm33 | 106570.09 | 33 | elm
| tt6 | 16214.4725 | 50 | tt
NCONUML | lga12 | 120.31 | 1 | lga
RESIDENTL | moe25 | 15202048.016 | 3044 | moe
RESIDENTL | moe22 | 6183768.6959 | 1343 | moe
RESIDENTL | mfa23 | 1535883.9368 | 206 | mfa
FARM | rwn22 | 76017.25 | 13 | rwn
COMMERCIAL | fgy31 | 26687.08 | 5 | fgy
RESIDENTL | elm33 | 17751529.9107 | 3238 | elm
COMMERCIAL | ldl22 | 7642772.3181 | 272 | ldl
NCONUML | llg11 | 13058.17 | 7 | llg
| ruba24 | 72607.09 | 10 | ruba
FARM | rwt32 | 21924.18 | 3 | rwt
FARM | ruba12 | 5735958.293 | 534 | ruba
FARM | brt21 | 526055.8565 | 65 | brt
| rwt15 | 24735.76 | 50 | rwt
NCONUML | bge13 | 40077 | 45 | bge
COMMERCIAL | klk21 | 1344972.0506 | 75 | klk
INDUSTRIAL | msd4 | 532825.24 | 27 | msd
| mwl21 | 2371.576 | 7 | mwl
RESIDENTL | wt9 | 13126762.7947 | 2901 | wt
FARM | wgi23 | 957555.9102 | 143 | wgi
| wgl24 | 12928.4076 | 27 | wgl
NCONUML | tgn11 | 50804.93 | 14 | tgn
LIGHTING | hpk22 | 402155.12 | 2 | hpk
INDUSTRIAL | wt13 | 198794.34 | 24 | wt
LIGHTING | wots24 | 69082.45 | 1 | wots
| ofr13 | 25120.5182 | 29 | ofr
| cre21 | 98632.2224 | 69 | cre
| smg22 | 13378.71 | 23 | smg
COMMERCIAL | tt4 | 4770691.1401 | 169 | tt
COMMERCIAL | elm26 | 2765254.86 | 47 | elm
NCONUML | bwa22 | 120.31 | 1 | bwa
| cyn23 | 386495.78 | 52 | cyn
INDUSTRIAL | nla34 | 227255.6563 | 13 | nla
FARM | mwl22 | 63.01 | 1 | mwl
| cf1 | 5771.13 | 3 | cf
NCONUML | cpk22 | 15413.02 | 10 | cpk
NCONUML | lyd13 | 28195.47 | 10 | lyd
NCONUML | cre31 | 35482.06 | 18 | cre
COMMERCIAL | wo11 | 6006584.4175 | 54 | wo
INDUSTRIAL | wt7 | 2382042.5333 | 25 | wt
| bwr34 | 19530.96 | 64 | bwr
NCONUML | bge23 | 57838.96 | 34 | bge
INDUSTRIAL | tgn23 | 187420.5 | 24 | tgn
RESIDENTL | cyn33 | 17836008.3498 | 3662 | cyn
RESIDENTL | nla34 | 7124747.0562 | 1408 | nla
| wgl11 | 21820.8596 | 38 | wgl
COMMERCIAL | bn12 | 3658135.6563 | 31 | bn
| mwl13 | 7054.2121 | 17 | mwl
COMMERCIAL | rwt26 | 65754589.65 | 1 | rwt
FARM | wt9 | 2789.4 | 1 | wt
RESIDENTL | bdl44 | 10906570.4152 | 1766 | bdl
FARM | cre33 | 2156267.3416 | 81 | cre
COMMERCIAL | wgl21 | 7364849.9167 | 150 | wgl
COMMERCIAL | wn5 | 3727109.367 | 208 | wn
NCONUML | mwl22 | 81020 | 27 | mwl
NCONUML | bn24 | 14677.57 | 9 | bn
| smr22 | 9887.67 | 15 | smr
|  | 8782.36 | 2 | #REF!
RESIDENTL | sle11 | 5311421.2716 | 1344 | sle
RESIDENTL | nw13 | 126364.0108 | 18 | nw
RESIDENTL | ftr23 | 12909653.9148 | 2620 | ftr
COMMERCIAL | mwl11 | 1278518.3133 | 72 | mwl
LIGHTING | llg13 | 66328.6913 | 1 | llg
NCONUML | klk22 | 2600.11 | 1 | klk
RESIDENTL | wyk23 | 22445865.182 | 3391 | wyk
COMMERCIAL | wt6 | 6354339.6482 | 191 | wt
RESIDENTL | brt11 | 6592458.6386 | 1001 | brt
NCONUML | tt9 | 66916.75 | 41 | tt
FARM | smr14 | 4406259.38 | 487 | smr
NCONUML | epg32 | 55568.91 | 13 | epg
RESIDENTL | rwn31 | 17135173.2235 | 2210 | rwn
| phm33 | 20993.1171 | 27 | phm
NCONUML | myt11 | 6079.5 | 6 | myt
RESIDENTL | nrn12 | 2807836.1314 | 591 | nrn
COMMERCIAL | mwl16 | 411566.3345 | 42 | mwl
INDUSTRIAL | lga23 | 1068068.6578 | 23 | lga
COMMERCIAL | ldl12 | 15390056.6509 | 380 | ldl
FARM | nla34 | 624678.3932 | 78 | nla
COMMERCIAL | rve13 | 1685040.429 | 44 | rve
NCONUML | drn24 | 11009.3526 | 4 | drn
COMMERCIAL | myt21 | 6919383.7104 | 251 | myt
FARM | moe13 | 3478506.4958 | 306 | moe
COMMERCIAL | mwl21 | 9182796.6603 | 240 | mwl
NCONUML | wgl15 | 97647.0301 | 36 | wgl
| bwn14 | 31300.22 | 31 | bwn
RESIDENTL | cpk22 | 8203984.593 | 1482 | cpk
RESIDENTL | rve12 | 17634581.2748 | 3656 | rve
RESIDENTL | phi13 | 17016004.0328 | 4317 | phi
RESIDENTL | hpk12 | 5058413.1519 | 1238 | hpk
COMMERCIAL | ruba24 | 4555190.3466 | 105 | ruba
FARM | cln14 | 51639.06 | 13 | cln
INDUSTRIAL | wt9 | 148098.11 | 5 | wt
| smg21 | 44014.37 | 27 | smg
INDUSTRIAL | smr23 | 883845.12 | 6 | smr

## Forecast - Summer
Forecasting Application - 13/10/2025
asset_type | asset | extremum | scenario | demand_year | season | poe | customer_count | pv_capacity | value | forecast_round | unit | region
zone_sub | cln | maximum |  | 2022 | Summer | 50 | 38619 | 72.2578 | 77.9086 | 202503 | MVA | central
zone_sub | cln | maximum |  | 2022 | Summer | 10 | 38619 | 72.2578 | 91.3183 | 202503 | MVA | central
zone_sub | cln | maximum |  | 2023 | Summer | 10 | 41429 | 81.3604 | 97.5884 | 202503 | MVA | central
zone_sub | cln | maximum |  | 2023 | Summer | 50 | 41429 | 81.3604 | 83.3369 | 202503 | MVA | central
zone_sub | cln | maximum |  | 2024 | Summer | 10 | 44846 | 94.6588 | 104.9463 | 202503 | MVA | central
zone_sub | cln | maximum |  | 2024 | Summer | 50 | 44846 | 94.6588 | 89.7351 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2025 | Summer | 10 |  |  | 119.6766 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2025 | Summer | 50 |  |  | 104.3341 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2026 | Summer | 10 |  |  | 124.2514 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2026 | Summer | 50 |  |  | 108.3435 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2027 | Summer | 10 |  |  | 128.0364 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2027 | Summer | 50 |  |  | 111.4611 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2028 | Summer | 10 |  |  | 131.3686 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2028 | Summer | 50 |  |  | 115.2173 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2029 | Summer | 10 |  |  | 136.7682 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2029 | Summer | 50 |  |  | 119.0984 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2030 | Summer | 10 |  |  | 141.634 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2030 | Summer | 50 |  |  | 123.2461 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2031 | Summer | 10 |  |  | 148.4809 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2031 | Summer | 50 |  |  | 128.0275 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2032 | Summer | 10 |  |  | 155.6302 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2032 | Summer | 50 |  |  | 133.6994 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2033 | Summer | 10 |  |  | 161.4365 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2033 | Summer | 50 |  |  | 139.0092 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2034 | Summer | 10 |  |  | 166.8996 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2034 | Summer | 50 |  |  | 144.6013 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2035 | Summer | 10 |  |  | 175.1342 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2035 | Summer | 50 |  |  | 154.2938 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2036 | Summer | 10 |  |  | 181.0486 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2036 | Summer | 50 |  |  | 157.43 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2037 | Summer | 10 |  |  | 187.0195 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2037 | Summer | 50 |  |  | 163.5566 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2038 | Summer | 10 |  |  | 193.3671 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2038 | Summer | 50 |  |  | 168.1999 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2039 | Summer | 10 |  |  | 192.0421 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2039 | Summer | 50 |  |  | 167.0472 | 202503 | MVA | central
zone_sub | cre | maximum |  | 2022 | Summer | 10 | 24937 | 39.5122 | 71.3044 | 202503 | MVA | central
zone_sub | cre | maximum |  | 2022 | Summer | 50 | 24937 | 39.5122 | 64.1683 | 202503 | MVA | central
zone_sub | cre | maximum |  | 2023 | Summer | 10 | 25835 | 43.8704 | 73.6781 | 202503 | MVA | central
zone_sub | cre | maximum |  | 2023 | Summer | 50 | 25835 | 43.8704 | 65.8328 | 202503 | MVA | central
zone_sub | cre | maximum |  | 2024 | Summer | 10 | 26314 | 48.9572 | 74.7994 | 202503 | MVA | central
zone_sub | cre | maximum |  | 2024 | Summer | 50 | 26314 | 48.9572 | 66.0879 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2025 | Summer | 10 |  |  | 89.8342 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2025 | Summer | 50 |  |  | 80.6612 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2026 | Summer | 10 |  |  | 90.653 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2026 | Summer | 50 |  |  | 81.4056 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2027 | Summer | 10 |  |  | 89.7773 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2027 | Summer | 50 |  |  | 80.6131 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2028 | Summer | 10 |  |  | 94.9573 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2028 | Summer | 50 |  |  | 85.9509 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2029 | Summer | 10 |  |  | 94.8385 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2029 | Summer | 50 |  |  | 85.6114 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2030 | Summer | 10 |  |  | 96.1186 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2030 | Summer | 50 |  |  | 85.7941 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2031 | Summer | 10 |  |  | 97.2062 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2031 | Summer | 50 |  |  | 86.4866 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2032 | Summer | 10 |  |  | 98.0786 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2032 | Summer | 50 |  |  | 87.2925 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2033 | Summer | 10 |  |  | 98.8781 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2033 | Summer | 50 |  |  | 88.2343 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2034 | Summer | 10 |  |  | 99.6475 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2034 | Summer | 50 |  |  | 88.9575 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2035 | Summer | 10 |  |  | 99.2707 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2035 | Summer | 50 |  |  | 89.8044 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2036 | Summer | 10 |  |  | 99.9981 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2036 | Summer | 50 |  |  | 89.5675 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2037 | Summer | 10 |  |  | 101.1509 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2037 | Summer | 50 |  |  | 90.5821 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2038 | Summer | 10 |  |  | 101.3208 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2038 | Summer | 50 |  |  | 90.3196 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2039 | Summer | 10 |  |  | 99.6095 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2039 | Summer | 50 |  |  | 88.5146 | 202503 | MVA | central
zone_sub | epg | maximum |  | 2022 | Summer | 10 | 29371 | 40.0067 | 87.2498 | 202503 | MVA | central
zone_sub | epg | maximum |  | 2022 | Summer | 50 | 29371 | 40.0067 | 72.9666 | 202503 | MVA | central
zone_sub | epg | maximum |  | 2023 | Summer | 10 | 30422 | 45.1511 | 90.3071 | 202503 | MVA | central
zone_sub | epg | maximum |  | 2023 | Summer | 50 | 30422 | 45.1511 | 75.7012 | 202503 | MVA | central
zone_sub | epg | maximum |  | 2024 | Summer | 10 | 32118 | 51.557 | 95.8895 | 202503 | MVA | central
zone_sub | epg | maximum |  | 2024 | Summer | 50 | 32118 | 51.557 | 79.9844 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2025 | Summer | 10 |  |  | 109.0669 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2025 | Summer | 50 |  |  | 92.5622 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2026 | Summer | 10 |  |  | 118.5447 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2026 | Summer | 50 |  |  | 101.6723 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2027 | Summer | 10 |  |  | 121.4869 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2027 | Summer | 50 |  |  | 104.4042 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2028 | Summer | 10 |  |  | 119.8786 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2028 | Summer | 50 |  |  | 102.6031 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2029 | Summer | 10 |  |  | 121.9204 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2029 | Summer | 50 |  |  | 105.5757 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2030 | Summer | 10 |  |  | 124.6444 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2030 | Summer | 50 |  |  | 106.371 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2031 | Summer | 10 |  |  | 127.5507 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2031 | Summer | 50 |  |  | 110.1341 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2032 | Summer | 10 |  |  | 131.8742 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2032 | Summer | 50 |  |  | 112.2581 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2033 | Summer | 10 |  |  | 136.3355 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2033 | Summer | 50 |  |  | 113.9316 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2034 | Summer | 10 |  |  | 140.9437 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2034 | Summer | 50 |  |  | 117.5793 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2035 | Summer | 10 |  |  | 144.5914 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2035 | Summer | 50 |  |  | 120.4726 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2036 | Summer | 50 |  |  | 128.0797 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2036 | Summer | 10 |  |  | 149.6115 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2037 | Summer | 10 |  |  | 152.9797 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2037 | Summer | 50 |  |  | 129.922 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2038 | Summer | 10 |  |  | 155.1715 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2038 | Summer | 50 |  |  | 132.5568 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2039 | Summer | 10 |  |  | 152.1644 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2039 | Summer | 50 |  |  | 125.7761 | 202503 | MVA | central
zone_sub | klo | maximum |  | 2022 | Summer | 10 | 14879 | 23.0226 | 53.5677 | 202503 | MVA | central
zone_sub | klo | maximum |  | 2022 | Summer | 50 | 14879 | 23.0226 | 41.9423 | 202503 | MVA | central
zone_sub | klo | maximum |  | 2023 | Summer | 10 | 17175 | 27.7177 | 61.121 | 202503 | MVA | central
zone_sub | klo | maximum |  | 2023 | Summer | 50 | 17175 | 27.7177 | 48.3019 | 202503 | MVA | central
zone_sub | klo | maximum |  | 2024 | Summer | 10 | 19951 | 34.2052 | 70.1897 | 202503 | MVA | central
zone_sub | klo | maximum |  | 2024 | Summer | 50 | 19951 | 34.2052 | 55.7613 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2025 | Summer | 10 |  |  | 83.6879 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2025 | Summer | 50 |  |  | 68.2523 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2026 | Summer | 10 |  |  | 94.1984 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2026 | Summer | 50 |  |  | 77.9353 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2027 | Summer | 10 |  |  | 102.4436 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2027 | Summer | 50 |  |  | 84.7194 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2028 | Summer | 10 |  |  | 118.3247 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2028 | Summer | 50 |  |  | 99.6669 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2029 | Summer | 10 |  |  | 126.3487 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2029 | Summer | 50 |  |  | 106.8624 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2030 | Summer | 10 |  |  | 135.5692 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2030 | Summer | 50 |  |  | 115.5707 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2031 | Summer | 10 |  |  | 148.561 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2031 | Summer | 50 |  |  | 127.0156 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2032 | Summer | 10 |  |  | 164.8827 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2032 | Summer | 50 |  |  | 137.8179 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2033 | Summer | 10 |  |  | 180.5841 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2033 | Summer | 50 |  |  | 151.2391 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2034 | Summer | 10 |  |  | 196.9964 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2034 | Summer | 50 |  |  | 164.8814 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2035 | Summer | 10 |  |  | 212.9758 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2035 | Summer | 50 |  |  | 181.5355 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2036 | Summer | 10 |  |  | 230.0573 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2036 | Summer | 50 |  |  | 195.8954 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2037 | Summer | 10 |  |  | 248.4456 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2037 | Summer | 50 |  |  | 212.2991 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2038 | Summer | 10 |  |  | 266.5409 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2038 | Summer | 50 |  |  | 225.6959 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2039 | Summer | 10 |  |  | 272.6357 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2039 | Summer | 50 |  |  | 228.9049 | 202503 | MVA | central
zone_sub | ofr | maximum |  | 2022 | Summer | 10 | 23246 | 35.5119 | 59.9776 | 202503 | MVA | central
zone_sub | ofr | maximum |  | 2022 | Summer | 50 | 23246 | 35.5119 | 53.856 | 202503 | MVA | central
zone_sub | ofr | maximum |  | 2023 | Summer | 10 | 24109 | 39.5748 | 62.0639 | 202503 | MVA | central
zone_sub | ofr | maximum |  | 2023 | Summer | 50 | 24109 | 39.5748 | 55.451 | 202503 | MVA | central
zone_sub | ofr | maximum |  | 2024 | Summer | 10 | 24997 | 44.4669 | 64.073 | 202503 | MVA | central
zone_sub | ofr | maximum |  | 2024 | Summer | 50 | 24997 | 44.4669 | 56.9594 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2025 | Summer | 10 |  |  | 69.589 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2025 | Summer | 50 |  |  | 61.9907 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2026 | Summer | 10 |  |  | 76.597 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2026 | Summer | 50 |  |  | 68.9791 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2027 | Summer | 10 |  |  | 81.5678 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2027 | Summer | 50 |  |  | 74.0072 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2028 | Summer | 10 |  |  | 84.5283 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2028 | Summer | 50 |  |  | 76.6284 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2029 | Summer | 10 |  |  | 86.8984 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2029 | Summer | 50 |  |  | 78.9811 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2030 | Summer | 10 |  |  | 88.8048 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2030 | Summer | 50 |  |  | 80.4506 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2031 | Summer | 10 |  |  | 90.6365 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2031 | Summer | 50 |  |  | 82.1352 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2032 | Summer | 10 |  |  | 92.2256 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2032 | Summer | 50 |  |  | 83.4813 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2033 | Summer | 10 |  |  | 92.9929 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2033 | Summer | 50 |  |  | 84.3346 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2034 | Summer | 10 |  |  | 94.1573 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2034 | Summer | 50 |  |  | 86.446 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2035 | Summer | 10 |  |  | 95.4952 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2035 | Summer | 50 |  |  | 87.894 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2036 | Summer | 10 |  |  | 96.8516 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2036 | Summer | 50 |  |  | 88.627 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2037 | Summer | 10 |  |  | 98.5806 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2037 | Summer | 50 |  |  | 90.0391 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2038 | Summer | 10 |  |  | 98.8168 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2038 | Summer | 50 |  |  | 89.5765 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2039 | Summer | 10 |  |  | 97.8239 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2039 | Summer | 50 |  |  | 88.3981 | 202503 | MVA | central
zone_sub | phm | maximum |  | 2022 | Summer | 50 | 16270 | 23.521 | 51.4174 | 202503 | MVA | central
zone_sub | phm | maximum |  | 2022 | Summer | 10 | 16270 | 23.521 | 56.9097 | 202503 | MVA | central
zone_sub | phm | maximum |  | 2023 | Summer | 10 | 16562 | 25.5412 | 57.758 | 202503 | MVA | central
zone_sub | phm | maximum |  | 2023 | Summer | 50 | 16562 | 25.5412 | 52.1386 | 202503 | MVA | central
zone_sub | phm | maximum |  | 2024 | Summer | 10 | 16854 | 27.7496 | 58.7282 | 202503 | MVA | central
zone_sub | phm | maximum |  | 2024 | Summer | 50 | 16854 | 27.7496 | 52.8621 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2025 | Summer | 10 |  |  | 75.5207 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2025 | Summer | 50 |  |  | 69.621 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2026 | Summer | 10 |  |  | 79.8845 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2026 | Summer | 50 |  |  | 74.1527 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2027 | Summer | 10 |  |  | 79.6008 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2027 | Summer | 50 |  |  | 73.9998 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2028 | Summer | 10 |  |  | 79.5894 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2028 | Summer | 50 |  |  | 73.965 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2029 | Summer | 10 |  |  | 80.0199 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2029 | Summer | 50 |  |  | 74.4648 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2030 | Summer | 10 |  |  | 81.1895 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2030 | Summer | 50 |  |  | 75.0153 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2031 | Summer | 10 |  |  | 81.9552 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2031 | Summer | 50 |  |  | 76.1566 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2032 | Summer | 10 |  |  | 82.7146 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2032 | Summer | 50 |  |  | 76.9783 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2033 | Summer | 10 |  |  | 83.6062 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2033 | Summer | 50 |  |  | 77.4148 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2034 | Summer | 10 |  |  | 84.4206 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2034 | Summer | 50 |  |  | 77.8841 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2035 | Summer | 10 |  |  | 85.2206 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2035 | Summer | 50 |  |  | 78.3211 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2036 | Summer | 10 |  |  | 85.2937 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2036 | Summer | 50 |  |  | 79.127 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2037 | Summer | 10 |  |  | 86.2309 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2037 | Summer | 50 |  |  | 80.1321 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2038 | Summer | 10 |  |  | 85.4841 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2038 | Summer | 50 |  |  | 80.0404 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2039 | Summer | 10 |  |  | 79.3417 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2039 | Summer | 50 |  |  | 73.3195 | 202503 | MVA | central
zone_sub | llg | maximum |  | 2022 | Summer | 10 | 7174 | 11.5134 | 25.3928 | 202503 | MVA | central
zone_sub | llg | maximum |  | 2022 | Summer | 50 | 7174 | 11.5134 | 23.4346 | 202503 | MVA | central
zone_sub | llg | maximum |  | 2023 | Summer | 10 | 7235 | 12.7349 | 25.4543 | 202503 | MVA | central
zone_sub | llg | maximum |  | 2023 | Summer | 50 | 7235 | 12.7349 | 23.4406 | 202503 | MVA | central
zone_sub | llg | maximum |  | 2024 | Summer | 10 | 7295 | 13.7538 | 25.544 | 202503 | MVA | central
zone_sub | llg | maximum |  | 2024 | Summer | 50 | 7295 | 13.7538 | 23.5081 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2025 | Summer | 10 |  |  | 28.7312 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2025 | Summer | 50 |  |  | 26.0976 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2026 | Summer | 10 |  |  | 33.0834 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2026 | Summer | 50 |  |  | 30.4575 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2027 | Summer | 10 |  |  | 33.0249 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2027 | Summer | 50 |  |  | 30.4247 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2028 | Summer | 10 |  |  | 33.0633 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2028 | Summer | 50 |  |  | 30.3952 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2029 | Summer | 10 |  |  | 33.1822 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2029 | Summer | 50 |  |  | 30.8677 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2030 | Summer | 10 |  |  | 33.5865 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2030 | Summer | 50 |  |  | 31.5616 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2031 | Summer | 10 |  |  | 33.8573 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2031 | Summer | 50 |  |  | 32.037 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2032 | Summer | 10 |  |  | 34.0794 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2032 | Summer | 50 |  |  | 31.4591 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2033 | Summer | 10 |  |  | 34.1121 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2033 | Summer | 50 |  |  | 31.5166 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2034 | Summer | 10 |  |  | 34.3124 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2034 | Summer | 50 |  |  | 31.792 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2035 | Summer | 10 |  |  | 34.3834 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2035 | Summer | 50 |  |  | 32.8827 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2036 | Summer | 10 |  |  | 34.3832 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2036 | Summer | 50 |  |  | 31.8492 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2037 | Summer | 10 |  |  | 34.3374 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2037 | Summer | 50 |  |  | 31.7885 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2038 | Summer | 10 |  |  | 34.3276 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2038 | Summer | 50 |  |  | 31.7234 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2039 | Summer | 10 |  |  | 32.6827 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2039 | Summer | 50 |  |  | 30.3101 | 202503 | MVA | central
zone_sub | wgi | maximum |  | 2022 | Summer | 10 | 21696 | 27.3902 | 50.299 | 202503 | MVA | east
zone_sub | wgi | maximum |  | 2022 | Summer | 50 | 21696 | 27.3902 | 41.2414 | 202503 | MVA | east
zone_sub | wgi | maximum |  | 2023 | Summer | 10 | 22045 | 30.4273 | 50.6919 | 202503 | MVA | east
zone_sub | wgi | maximum |  | 2023 | Summer | 50 | 22045 | 30.4273 | 41.4384 | 202503 | MVA | east
zone_sub | wgi | maximum |  | 2024 | Summer | 10 | 22388 | 33.5461 | 51.0465 | 202503 | MVA | east
zone_sub | wgi | maximum |  | 2024 | Summer | 50 | 22388 | 33.5461 | 41.5121 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2025 | Summer | 10 |  |  | 54.5057 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2025 | Summer | 50 |  |  | 44.6075 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2026 | Summer | 10 |  |  | 54.6012 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2026 | Summer | 50 |  |  | 44.9185 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2027 | Summer | 10 |  |  | 54.4983 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2027 | Summer | 50 |  |  | 44.7661 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2028 | Summer | 10 |  |  | 54.5247 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2028 | Summer | 50 |  |  | 44.911 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2029 | Summer | 10 |  |  | 54.7136 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2029 | Summer | 50 |  |  | 44.9706 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2030 | Summer | 10 |  |  | 55.0965 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2030 | Summer | 50 |  |  | 45.1615 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2031 | Summer | 10 |  |  | 55.7707 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2031 | Summer | 50 |  |  | 45.5541 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2032 | Summer | 50 |  |  | 45.8843 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2032 | Summer | 10 |  |  | 56.122 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2033 | Summer | 10 |  |  | 56.3761 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2033 | Summer | 50 |  |  | 46.0363 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2034 | Summer | 10 |  |  | 56.7608 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2034 | Summer | 50 |  |  | 45.9008 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2035 | Summer | 10 |  |  | 57.2519 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2035 | Summer | 50 |  |  | 46.4689 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2036 | Summer | 10 |  |  | 57.8457 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2036 | Summer | 50 |  |  | 46.559 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2037 | Summer | 10 |  |  | 58.1569 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2037 | Summer | 50 |  |  | 46.4523 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2038 | Summer | 10 |  |  | 58.056 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2038 | Summer | 50 |  |  | 46.6661 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2039 | Summer | 10 |  |  | 56.811 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2039 | Summer | 50 |  |  | 45.5652 | 202503 | MVA | east

## Forecast- Winter
Forecasting Application - 13/10/2025
asset_type | asset | extremum | scenario | demand_year | season | poe | customer_count | pv_capacity | value | forecast_round | unit | region
zone_sub | cln | maximum |  | 2022 | Winter | 10 | 38619 | 72.2578 | 63.0362 | 202503 | MVA | central
zone_sub | cln | maximum |  | 2022 | Winter | 50 | 38619 | 72.2578 | 58.8161 | 202503 | MVA | central
zone_sub | cln | maximum |  | 2023 | Winter | 10 | 41429 | 81.3604 | 67.9918 | 202503 | MVA | central
zone_sub | cln | maximum |  | 2023 | Winter | 50 | 41429 | 81.3604 | 63.4647 | 202503 | MVA | central
zone_sub | cln | maximum |  | 2024 | Winter | 10 | 44846 | 94.6588 | 74.018 | 202503 | MVA | central
zone_sub | cln | maximum |  | 2024 | Winter | 50 | 44846 | 94.6588 | 69.1182 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2025 | Winter | 10 |  |  | 89.4372 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2025 | Winter | 50 |  |  | 84.5179 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2026 | Winter | 10 |  |  | 93.2911 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2026 | Winter | 50 |  |  | 88.1502 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2027 | Winter | 10 |  |  | 98.0701 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2027 | Winter | 50 |  |  | 92.8679 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2028 | Winter | 10 |  |  | 102.5171 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2028 | Winter | 50 |  |  | 97.437 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2029 | Winter | 10 |  |  | 107.2692 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2029 | Winter | 50 |  |  | 101.4753 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2030 | Winter | 10 |  |  | 112.2902 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2030 | Winter | 50 |  |  | 107.1286 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2031 | Winter | 10 |  |  | 119.5588 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2031 | Winter | 50 |  |  | 113.3315 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2032 | Winter | 10 |  |  | 125.8642 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2032 | Winter | 50 |  |  | 119.6901 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2033 | Winter | 10 |  |  | 131.807 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2033 | Winter | 50 |  |  | 125.9989 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2034 | Winter | 10 |  |  | 137.993 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2034 | Winter | 50 |  |  | 131.579 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2035 | Winter | 10 |  |  | 145.465 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2035 | Winter | 50 |  |  | 137.6925 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2036 | Winter | 10 |  |  | 147.8036 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2036 | Winter | 50 |  |  | 139.8743 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2037 | Winter | 10 |  |  | 155.8793 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2037 | Winter | 50 |  |  | 147.8441 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2038 | Winter | 10 |  |  | 163.4009 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2038 | Winter | 50 |  |  | 156.1056 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2039 | Winter | 10 |  |  | 133.5693 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2039 | Winter | 50 |  |  | 127.2077 | 202503 | MVA | central
zone_sub | cre | maximum |  | 2022 | Winter | 10 | 24937 | 39.5122 | 50.635 | 202503 | MVA | central
zone_sub | cre | maximum |  | 2022 | Winter | 50 | 24937 | 39.5122 | 48.3881 | 202503 | MVA | central
zone_sub | cre | maximum |  | 2023 | Winter | 10 | 25835 | 43.8704 | 52.4586 | 202503 | MVA | central
zone_sub | cre | maximum |  | 2023 | Winter | 50 | 25835 | 43.8704 | 50.1308 | 202503 | MVA | central
zone_sub | cre | maximum |  | 2024 | Winter | 10 | 26314 | 48.9572 | 53.4328 | 202503 | MVA | central
zone_sub | cre | maximum |  | 2024 | Winter | 50 | 26314 | 48.9572 | 51.0617 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2025 | Winter | 10 |  |  | 68.4471 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2025 | Winter | 50 |  |  | 65.7336 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2026 | Winter | 10 |  |  | 69.4459 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2026 | Winter | 50 |  |  | 66.605 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2027 | Winter | 10 |  |  | 69.249 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2027 | Winter | 50 |  |  | 66.728 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2028 | Winter | 10 |  |  | 74.3386 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2028 | Winter | 50 |  |  | 72.0847 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2029 | Winter | 10 |  |  | 74.5773 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2029 | Winter | 50 |  |  | 72.2361 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2030 | Winter | 10 |  |  | 76.3193 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2030 | Winter | 50 |  |  | 74.0669 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2031 | Winter | 10 |  |  | 77.7248 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2031 | Winter | 50 |  |  | 75.6012 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2032 | Winter | 10 |  |  | 79.2116 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2032 | Winter | 50 |  |  | 76.7507 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2033 | Winter | 10 |  |  | 79.7367 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2033 | Winter | 50 |  |  | 77.8762 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2034 | Winter | 10 |  |  | 80.3545 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2034 | Winter | 50 |  |  | 78.6625 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2035 | Winter | 10 |  |  | 81.081 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2035 | Winter | 50 |  |  | 79.0014 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2036 | Winter | 10 |  |  | 80.0375 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2036 | Winter | 50 |  |  | 78.1499 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2037 | Winter | 10 |  |  | 83.4116 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2037 | Winter | 50 |  |  | 80.9567 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2038 | Winter | 10 |  |  | 84.3767 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2038 | Winter | 50 |  |  | 81.4995 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2039 | Winter | 10 |  |  | 72.4681 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2039 | Winter | 50 |  |  | 69.0004 | 202503 | MVA | central
zone_sub | epg | maximum |  | 2022 | Winter | 10 | 29371 | 40.0067 | 65.9271 | 202503 | MVA | central
zone_sub | epg | maximum |  | 2022 | Winter | 50 | 29371 | 40.0067 | 59.4269 | 202503 | MVA | central
zone_sub | epg | maximum |  | 2023 | Winter | 10 | 30422 | 45.1511 | 68.3101 | 202503 | MVA | central
zone_sub | epg | maximum |  | 2023 | Winter | 50 | 30422 | 45.1511 | 61.7598 | 202503 | MVA | central
zone_sub | epg | maximum |  | 2024 | Winter | 50 | 32118 | 51.557 | 65.5719 | 202503 | MVA | central
zone_sub | epg | maximum |  | 2024 | Winter | 10 | 32118 | 51.557 | 72.1952 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2025 | Winter | 10 |  |  | 85.9871 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2025 | Winter | 50 |  |  | 79.3939 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2026 | Winter | 10 |  |  | 95.0802 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2026 | Winter | 50 |  |  | 89.3565 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2027 | Winter | 10 |  |  | 100.5082 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2027 | Winter | 50 |  |  | 92.7492 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2028 | Winter | 10 |  |  | 99.8778 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2028 | Winter | 50 |  |  | 93.3308 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2029 | Winter | 10 |  |  | 103.1049 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2029 | Winter | 50 |  |  | 96.5577 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2030 | Winter | 10 |  |  | 109.1359 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2030 | Winter | 50 |  |  | 102.3455 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2031 | Winter | 10 |  |  | 112.51 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2031 | Winter | 50 |  |  | 104.2867 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2032 | Winter | 10 |  |  | 121.7799 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2032 | Winter | 50 |  |  | 114.0182 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2033 | Winter | 10 |  |  | 127.6696 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2033 | Winter | 50 |  |  | 119.7255 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2034 | Winter | 10 |  |  | 133.3287 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2034 | Winter | 50 |  |  | 125.5482 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2035 | Winter | 10 |  |  | 135.1129 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2035 | Winter | 50 |  |  | 126.6853 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2036 | Winter | 10 |  |  | 142.2751 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2036 | Winter | 50 |  |  | 134.3407 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2037 | Winter | 10 |  |  | 149.629 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2037 | Winter | 50 |  |  | 142.1357 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2038 | Winter | 10 |  |  | 150.109 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2038 | Winter | 50 |  |  | 141.9626 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2039 | Winter | 10 |  |  | 116.0207 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2039 | Winter | 50 |  |  | 101.3122 | 202503 | MVA | central
zone_sub | klo | maximum |  | 2022 | Winter | 10 | 14879 | 23.0226 | 48.7862 | 202503 | MVA | central
zone_sub | klo | maximum |  | 2022 | Winter | 50 | 14879 | 23.0226 | 43.3886 | 202503 | MVA | central
zone_sub | klo | maximum |  | 2023 | Winter | 10 | 17175 | 27.7177 | 56.3067 | 202503 | MVA | central
zone_sub | klo | maximum |  | 2023 | Winter | 50 | 17175 | 27.7177 | 50.077 | 202503 | MVA | central
zone_sub | klo | maximum |  | 2024 | Winter | 10 | 19951 | 34.2052 | 65.4015 | 202503 | MVA | central
zone_sub | klo | maximum |  | 2024 | Winter | 50 | 19951 | 34.2052 | 58.1655 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2025 | Winter | 10 |  |  | 79.8942 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2025 | Winter | 50 |  |  | 72.3119 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2026 | Winter | 10 |  |  | 92.3723 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2026 | Winter | 50 |  |  | 83.7626 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2027 | Winter | 10 |  |  | 102.9502 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2027 | Winter | 50 |  |  | 93.3778 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2028 | Winter | 10 |  |  | 120.3965 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2028 | Winter | 50 |  |  | 109.8362 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2029 | Winter | 10 |  |  | 129.7211 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2029 | Winter | 50 |  |  | 118.6301 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2030 | Winter | 10 |  |  | 142.5707 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2030 | Winter | 50 |  |  | 129.8167 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2031 | Winter | 10 |  |  | 159.4027 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2031 | Winter | 50 |  |  | 143.8497 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2032 | Winter | 10 |  |  | 178.8568 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2032 | Winter | 50 |  |  | 161.743 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2033 | Winter | 10 |  |  | 196.8658 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2033 | Winter | 50 |  |  | 178.8635 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2034 | Winter | 10 |  |  | 214.3536 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2034 | Winter | 50 |  |  | 194.8729 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2035 | Winter | 10 |  |  | 235.0946 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2035 | Winter | 50 |  |  | 213.0243 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2036 | Winter | 10 |  |  | 246.5584 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2036 | Winter | 50 |  |  | 225.0657 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2037 | Winter | 10 |  |  | 273.2503 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2037 | Winter | 50 |  |  | 249.8153 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2038 | Winter | 10 |  |  | 298.8878 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2038 | Winter | 50 |  |  | 271.7276 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2039 | Winter | 10 |  |  | 252.4111 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2039 | Winter | 50 |  |  | 227.0702 | 202503 | MVA | central
zone_sub | llg | maximum |  | 2022 | Winter | 10 | 7174 | 11.5134 | 22.426 | 202503 | MVA | central
zone_sub | llg | maximum |  | 2022 | Winter | 50 | 7174 | 11.5134 | 20.2322 | 202503 | MVA | central
zone_sub | llg | maximum |  | 2023 | Winter | 10 | 7235 | 12.7349 | 22.5982 | 202503 | MVA | central
zone_sub | llg | maximum |  | 2023 | Winter | 50 | 7235 | 12.7349 | 20.4035 | 202503 | MVA | central
zone_sub | llg | maximum |  | 2024 | Winter | 10 | 7295 | 13.7538 | 22.7705 | 202503 | MVA | central
zone_sub | llg | maximum |  | 2024 | Winter | 50 | 7295 | 13.7538 | 20.5738 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2025 | Winter | 10 |  |  | 26.1225 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2025 | Winter | 50 |  |  | 23.9159 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2026 | Winter | 10 |  |  | 30.6829 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2026 | Winter | 50 |  |  | 28.4398 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2027 | Winter | 10 |  |  | 31.049 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2027 | Winter | 50 |  |  | 28.8402 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2028 | Winter | 10 |  |  | 31.3064 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2028 | Winter | 50 |  |  | 29.108 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2029 | Winter | 10 |  |  | 31.5714 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2029 | Winter | 50 |  |  | 29.4846 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2030 | Winter | 10 |  |  | 32.5932 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2030 | Winter | 50 |  |  | 30.3426 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2031 | Winter | 10 |  |  | 33.1905 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2031 | Winter | 50 |  |  | 31.0163 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2032 | Winter | 10 |  |  | 33.8014 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2032 | Winter | 50 |  |  | 31.6154 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2033 | Winter | 10 |  |  | 34.0793 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2033 | Winter | 50 |  |  | 31.8255 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2034 | Winter | 10 |  |  | 34.2253 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2034 | Winter | 50 |  |  | 32.0656 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2035 | Winter | 10 |  |  | 33.7185 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2035 | Winter | 50 |  |  | 31.7299 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2036 | Winter | 10 |  |  | 33.9832 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2036 | Winter | 50 |  |  | 31.9069 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2037 | Winter | 10 |  |  | 34.9987 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2037 | Winter | 50 |  |  | 32.7389 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2038 | Winter | 10 |  |  | 34.5209 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2038 | Winter | 50 |  |  | 32.3709 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2039 | Winter | 10 |  |  | 28.3277 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2039 | Winter | 50 |  |  | 26.2847 | 202503 | MVA | central
zone_sub | ofr | maximum |  | 2022 | Winter | 10 | 23246 | 35.5119 | 49.8939 | 202503 | MVA | central
zone_sub | ofr | maximum |  | 2022 | Winter | 50 | 23246 | 35.5119 | 46.8764 | 202503 | MVA | central
zone_sub | ofr | maximum |  | 2023 | Winter | 10 | 24109 | 39.5748 | 51.7437 | 202503 | MVA | central
zone_sub | ofr | maximum |  | 2023 | Winter | 50 | 24109 | 39.5748 | 48.6149 | 202503 | MVA | central
zone_sub | ofr | maximum |  | 2024 | Winter | 10 | 24997 | 44.4669 | 53.6497 | 202503 | MVA | central
zone_sub | ofr | maximum |  | 2024 | Winter | 50 | 24997 | 44.4669 | 50.4065 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2025 | Winter | 10 |  |  | 59.4536 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2025 | Winter | 50 |  |  | 56.1183 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2026 | Winter | 10 |  |  | 66.5595 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2026 | Winter | 50 |  |  | 63.2802 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2027 | Winter | 10 |  |  | 72.8129 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2027 | Winter | 50 |  |  | 69.3039 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2028 | Winter | 10 |  |  | 76.0509 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2028 | Winter | 50 |  |  | 72.5305 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2029 | Winter | 10 |  |  | 78.6773 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2029 | Winter | 50 |  |  | 74.8582 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2030 | Winter | 10 |  |  | 81.1629 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2030 | Winter | 50 |  |  | 77.5373 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2031 | Winter | 10 |  |  | 83.2732 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2031 | Winter | 50 |  |  | 79.5294 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2032 | Winter | 10 |  |  | 85.4834 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2032 | Winter | 50 |  |  | 81.7407 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2033 | Winter | 10 |  |  | 86.4197 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2033 | Winter | 50 |  |  | 82.8706 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2034 | Winter | 10 |  |  | 87.7259 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2034 | Winter | 50 |  |  | 83.8526 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2035 | Winter | 10 |  |  | 90.1815 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2035 | Winter | 50 |  |  | 86.3425 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2036 | Winter | 10 |  |  | 89.3155 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2036 | Winter | 50 |  |  | 84.7668 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2037 | Winter | 10 |  |  | 92.5351 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2037 | Winter | 50 |  |  | 88.8524 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2038 | Winter | 10 |  |  | 94.3753 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2038 | Winter | 50 |  |  | 94.1939 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2039 | Winter | 10 |  |  | 80.6717 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2039 | Winter | 50 |  |  | 77.1549 | 202503 | MVA | central
zone_sub | phm | maximum |  | 2022 | Winter | 10 | 16270 | 23.521 | 48.1658 | 202503 | MVA | central
zone_sub | phm | maximum |  | 2022 | Winter | 50 | 16270 | 23.521 | 45.1092 | 202503 | MVA | central
zone_sub | phm | maximum |  | 2023 | Winter | 10 | 16562 | 25.5412 | 49.0318 | 202503 | MVA | central
zone_sub | phm | maximum |  | 2023 | Winter | 50 | 16562 | 25.5412 | 45.9202 | 202503 | MVA | central
zone_sub | phm | maximum |  | 2024 | Winter | 10 | 16854 | 27.7496 | 49.8978 | 202503 | MVA | central
zone_sub | phm | maximum |  | 2024 | Winter | 50 | 16854 | 27.7496 | 46.7311 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2025 | Winter | 10 |  |  | 67.0847 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2025 | Winter | 50 |  |  | 64.1376 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2026 | Winter | 10 |  |  | 71.7531 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2026 | Winter | 50 |  |  | 68.6294 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2027 | Winter | 10 |  |  | 72.4584 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2027 | Winter | 50 |  |  | 69.3785 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2028 | Winter | 10 |  |  | 72.887 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2028 | Winter | 50 |  |  | 69.9467 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2029 | Winter | 10 |  |  | 73.8781 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2029 | Winter | 50 |  |  | 70.9603 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2030 | Winter | 10 |  |  | 76.2493 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2030 | Winter | 50 |  |  | 73.2946 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2031 | Winter | 10 |  |  | 77.5227 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2031 | Winter | 50 |  |  | 74.8388 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2032 | Winter | 10 |  |  | 79.9897 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2032 | Winter | 50 |  |  | 76.8149 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2033 | Winter | 10 |  |  | 87.5343 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2033 | Winter | 50 |  |  | 77.8299 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2034 | Winter | 10 |  |  | 81.2629 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2034 | Winter | 50 |  |  | 78.7091 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2035 | Winter | 10 |  |  | 80.0205 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2035 | Winter | 50 |  |  | 77.0055 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2036 | Winter | 10 |  |  | 81.6454 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2036 | Winter | 50 |  |  | 78.9538 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2037 | Winter | 10 |  |  | 85.2253 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2037 | Winter | 50 |  |  | 82.0295 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2038 | Winter | 10 |  |  | 82.7648 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2038 | Winter | 50 |  |  | 79.6564 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2039 | Winter | 10 |  |  | 67.0558 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2039 | Winter | 50 |  |  | 63.9852 | 202503 | MVA | central
zone_sub | wgi | maximum |  | 2022 | Winter | 10 | 21696 | 27.3902 | 41.941 | 202503 | MVA | east
zone_sub | wgi | maximum |  | 2022 | Winter | 50 | 21696 | 27.3902 | 38.234 | 202503 | MVA | east
zone_sub | wgi | maximum |  | 2023 | Winter | 10 | 22045 | 30.4273 | 42.6315 | 202503 | MVA | east
zone_sub | wgi | maximum |  | 2023 | Winter | 50 | 22045 | 30.4273 | 38.883 | 202503 | MVA | east
zone_sub | wgi | maximum |  | 2024 | Winter | 10 | 22388 | 33.5461 | 43.3126 | 202503 | MVA | east
zone_sub | wgi | maximum |  | 2024 | Winter | 50 | 22388 | 33.5461 | 39.5207 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2025 | Winter | 10 |  |  | 47.2482 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2025 | Winter | 50 |  |  | 43.6466 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2026 | Winter | 10 |  |  | 47.6557 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2026 | Winter | 50 |  |  | 44.0841 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2027 | Winter | 10 |  |  | 49.0622 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2027 | Winter | 50 |  |  | 44.625 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2028 | Winter | 10 |  |  | 49.028 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2028 | Winter | 50 |  |  | 45.3431 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2029 | Winter | 10 |  |  | 49.3373 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2029 | Winter | 50 |  |  | 46.0239 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2030 | Winter | 10 |  |  | 50.5469 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2030 | Winter | 50 |  |  | 47.2137 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2031 | Winter | 10 |  |  | 54.0224 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2031 | Winter | 50 |  |  | 50.206 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2032 | Winter | 10 |  |  | 55.4565 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2032 | Winter | 50 |  |  | 51.8155 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2033 | Winter | 10 |  |  | 54.099 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2033 | Winter | 50 |  |  | 50.6413 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2034 | Winter | 10 |  |  | 57.8491 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2034 | Winter | 50 |  |  | 54.2764 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2035 | Winter | 10 |  |  | 56.2746 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2035 | Winter | 50 |  |  | 54.9313 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2036 | Winter | 10 |  |  | 57.6913 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2036 | Winter | 50 |  |  | 55.4021 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2037 | Winter | 10 |  |  | 58.7122 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2037 | Winter | 50 |  |  | 57.6212 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2038 | Winter | 10 |  |  | 58.2928 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2038 | Winter | 50 |  |  | 57.9824 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2039 | Winter | 10 |  |  | 49.2493 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2039 | Winter | 50 |  |  | 45.4578 | 202503 | MVA | east

## Ratings
STATION OUTPUT RATING (TRANSFORMER SUMMATION) SUMMARY
|  |  | Station N Rating |  | Station N-1 Rating |  | Station N-2 Rating
|  |  | SCR | WCR | SCR | WCR | SCR | WCR | Remarks | Remarks | Bus Target | Station Cap Bank
S/S Name | No. TX | Name Plate MVA | MVA | MVA | MVA | MVA | MVA | MVA | For N-1 Ratings | N-2 | Voltage kV | MVAr
CLN_Old | 2 | 66 | 87.3 | 95.3 | 44.6 | 48.9 | 0 | 0 | Loss of T1 |  | 22 | 12
CLN | 3 | 99 | 130.95 | 142.95 | 89.2 | 97.8 | 44.6 | 48.9
CRE | 2 | 66 | 84.3 | 93.8 | 41.1 | 46.3 | 0 | 0 | Loss of T2 or T3 |  | 22 | 12
EPG | 3 | 99 | 123.1 | 139.9 | 87.8 | 98.1 | 43.9 | 49.05 | Loss of T3 | Using Highest value | 22
KLO | 2 | 66 | 97.5 | 97.5 | 49.1 | 49.1 | 0 | 0 | Loss of T1 or T2 |  | 22.44 | 6
LLG | 1 | 33 | 47.4 | 48.3 | 0 | 0 | 0 | 0 | N rating only |  | 22 | 4
OFR | 2 | 66 | 93.2 | 93.2 | 45.2 | 48 | 0 | 0 | Loss of T1 or T2 |  | 22 | 6
PHM | 2 | 66 | 91.9 | 95.7 | 45 | 49.1 | 0 | 0 | Loss of T1 or T2 |  | 22 | 12
WGI | 3 | 40.5 | 55.8 | 56.8 | 35.3 | 36.1 | 17.65 | 18.05

## Power Factor
asset_type | asset | PF
zone_sub | cln | 1
zone_sub | cre | 1
zone_sub | cyn | 1
zone_sub | epg | 1
zone_sub | klo | 0.99
zone_sub | llg | 0.99
zone_sub | ofr | 1
zone_sub | phm | 1
zone_sub | wgi | 0.99

## FT
Forecast tool (MVA) |  | Forecast Capacity & Transfers
ZSS |  | WGI
Summer
[5 empty] | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads
DY (Apr 1 to Mar 30) |  | 2022/23 | 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2028/29 | 2029/30 | 2030/31 | 2031/32 | 2032/33 | 2033/34 | 2034/35 | 2035/36 | 2036/37 | 2037/38 | 2038/39
DY (Apr 1 to Mar 30) |  | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038
FY (Jul 1 to Jun 30) |  | 2022/23 | 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2028/29 | 2029/30 | 2030/31 | 2031/32 | 2032/33 | 2033/34 | 2034/35 | 2035/36 | 2036/37 | 2037/38 | 2038/39
FY (Jul 1 to Jun 30) |  |  |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39
Summer POE50 | 50 |  |  | 41.5121 | 44.6075 | 44.9185 | 44.7661 | 44.911 | 44.9706 | 45.1615 | 45.5541 | 45.8843 | 46.0363 | 45.9008 | 46.4689 | 46.559 | 46.4523 | 46.6661
Summer POE10 | 10 |  |  | 51.0465 | 54.5057 | 54.6012 | 54.4983 | 54.5247 | 54.7136 | 55.0965 | 55.7707 | 56.122 | 56.3761 | 56.7608 | 57.2519 | 57.8457 | 58.1569 | 58.056
Winter
[5 empty] | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads
DM (Apr 1 to Mar 30) |  |  |  | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2028/29 | 2029/30 | 2030/31 | 2031/32 | 2032/33 | 2033/34 | 2034/35 | 2035/36 | 2036/37 | 2037/38 | 2038/39
DY (Apr 1 to Mar 30) |  |  |  | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038
FY (Jul 1 to Jun 30) |  |  |  | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2028/29 | 2029/30 | 2030/31 | 2031/32 | 2032/33 | 2033/34 | 2034/35 | 2035/36 | 2036/37 | 2037/38 | 2038/39
FY (Jul 1 to Jun 30) |  |  |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39
Winter POE50 | 50 |  |  | 39.5207 | 43.6466 | 44.0841 | 44.625 | 45.3431 | 46.0239 | 47.2137 | 50.206 | 51.8155 | 50.6413 | 54.2764 | 54.9313 | 55.4021 | 57.6212 | 57.9824
Winter POE10 | 10 |  |  | 43.3126 | 47.2482 | 47.6557 | 49.0622 | 49.028 | 49.3373 | 50.5469 | 54.0224 | 55.4565 | 54.099 | 57.8491 | 56.2746 | 57.6913 | 58.7122 | 58.2928
Transfers (MVA)
|  | Feeder | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39
|  | WGI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | PowerFactor | 0.99

## Load Duration Curves
Station
WGI
POE10
[6 empty] | Stations | KLO |  | EPG |  | CRE |  | CLN |  | PHM |  | OFR |  | LLG |  | WGI
| % of MD | Winter - MD (P10) - Duration % | Winter - MD - Hours | Summer - MD - Duration % | Summer - MD - Hours | %MD | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration %
| 100% | 0% | 0 | 0% | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| 99% | 0.006767% | 0.2972 | 0% | 0 | 99% | 0.01722% | 0.02707% | 0% | 0.04737% | 0% | 0% | 0.00861% | 0.01353% | 0.03444% | 0.03383% | 0.01722% | 0.0203% | 0.02583% | 0.006767% | 0% | 0.006767%
| 98% | 0.006767% | 0.2972 | 0% | 0 | 98% | 0.01722% | 0.07443% | 0.00861% | 0.08797% | 0.02583% | 0.01353% | 0.02583% | 0.0203% | 0.05166% | 0.07443% | 0.02583% | 0.0812% | 0.04305% | 0.0203% | 0% | 0.006767%
| 97% | 0.006767% | 0.2972 | 0.00861% | 0.37816 | 97% | 0.02583% | 0.09474% | 0.02583% | 0.1421% | 0.04305% | 0.02707% | 0.05166% | 0.03383% | 0.0861% | 0.1556% | 0.04305% | 0.1083% | 0.05166% | 0.04737% | 0.00861% | 0.006767%
| 95% | 0.03383% | 1.486 | 0.00861% | 0.37816 | 95% | 0.05166% | 0.1895% | 0.09471% | 0.3519% | 0.0861% | 0.08797% | 0.1033% | 0.05413% | 0.1378% | 0.3992% | 0.07749% | 0.1759% | 0.09471% | 0.09474% | 0.00861% | 0.03383%
| 90% | 0.1962% | 8.6188 | 0.01722% | 0.75633 | 90% | 0.0861% | 0.9135% | 0.1894% | 1.786% | 0.1894% | 0.7579% | 0.1808% | 0.07443% | 0.3702% | 1.793% | 0.2066% | 0.8932% | 0.353% | 0.2639% | 0.01722% | 0.1962%
| 85% | 0.9135% | 40.1218 | 0.02583% | 1.1345 | 85% | 0.1205% | 2.355% | 0.353% | 4.588% | 0.2669% | 2.761% | 0.3272% | 0.318% | 0.6027% | 5.393% | 0.3702% | 2.68% | 0.7147% | 0.7443% | 0.02583% | 0.9135%
| 80% | 2.118% | 93.0231 | 0.06027% | 2.6471 | 80% | 0.31% | 5.616% | 0.6458% | 8.885% | 0.4219% | 6.787% | 0.4477% | 0.9406% | 0.7749% | 11.33% | 0.5683% | 6.11% | 1.317% | 1.915% | 0.06027% | 2.118%
| 75% | 4.486% | 197.0426 | 0.07749% | 3.4035 | 75% | 0.4822% | 9.995% | 0.9988% | 14.05% | 0.5338% | 11.76% | 0.5855% | 2.876% | 1.102% | 18.3% | 0.7491% | 10.38% | 2.764% | 4.601% | 0.07749% | 4.486%
| 70% | 8.607% | 378.0365 | 0.1292% | 5.6725 | 70% | 0.7491% | 14.12% | 1.498% | 19.88% | 0.8438% | 17.56% | 0.7921% | 7.376% | 1.739% | 26.3% | 0.9557% | 15.73% | 6.225% | 8.837% | 0.1292% | 8.607%
| 65% | 14.03% | 616.0926 | 0.1464% | 6.4288 | 65% | 1.154% | 18.84% | 2.265% | 27.11% | 1.102% | 25.21% | 1.05% | 12.51% | 2.6% | 35.36% | 1.541% | 22.03% | 12.05% | 15.25% | 0.1464% | 14.03%
| 60% | 21.29% | 934.9866 | 0.2583% | 11.3449 | 60% | 1.602% | 25.14% | 3.203% | 35.21% | 1.627% | 33.62% | 1.748% | 18.2% | 4.055% | 46.14% | 2.247% | 29.44% | 20.92% | 25.15% | 0.2583% | 21.29%
| 55% | 29.85% | 1310.9428 | 0.8094% | 35.5474 | 55% | 2.411% | 33.56% | 4.357% | 45.33% | 2.48% | 42.68% | 2.419% | 25.42% | 7.095% | 59.16% | 3.496% | 37.5% | 33.11% | 37.15% | 0.8094% | 29.85%
| 50% | 39.4% | 1730.2899 | 2.17% | 95.2974 | 50% | 4.598% | 44.25% | 6.303% | 58.26% | 3.84% | 54.87% | 4.064% | 34.04% | 14.48% | 73.62% | 5.881% | 47.91% | 47.93% | 51.32% | 2.17% | 39.4%
| 45% | 49.36% | 2168.0633 | 4.753% | 208.7467 | 45% | 9.592% | 58.98% | 10.8% | 69.36% | 6.535% | 71.48% | 8.378% | 45.63% | 26.86% | 85.96% | 11.13% | 62.3% | 62.8% | 65.85% | 4.753% | 49.36%
| 40% | 59.42% | 2609.7004 | 8.662% | 380.4333 | 40% | 19.83% | 71.65% | 21.2% | 75.98% | 14.01% | 84.31% | 16.88% | 65.51% | 41.17% | 92.73% | 21.13% | 79.32% | 76.24% | 79.08% | 8.662% | 59.42%
| 35% | 68.26% | 2998.1389 | 15.86% | 696.5786 | 35% | 37.74% | 78.94% | 37.58% | 85.16% | 27.53% | 88.52% | 26.59% | 78.66% | 63.28% | 95.6% | 34.85% | 87.21% | 86.9% | 88.41% | 15.86% | 68.26%
| 30% | 75.35% | 3309.3057 | 28.71% | 1260.7997 | 30% | 66.82% | 83.24% | 57.09% | 93.38% | 49.73% | 90.98% | 45.59% | 83.41% | 86.84% | 97.25% | 59.02% | 90.02% | 92.6% | 93.97% | 28.71% | 75.35%
| 25% | 80.55% | 3537.8514 | 44.75% | 1965.3198 | 25% | 77.33% | 87.43% | 77.75% | 96.1% | 81.07% | 93.44% | 72.26% | 87.95% | 94.88% | 98.4% | 83.32% | 92.46% | 96.47% | 96.66% | 44.75% | 80.55%
| 20% | 84.95% | 3731.0305 | 56.7% | 2490.2118 | 20% | 85.59% | 92.06% | 96.84% | 97.65% | 89.22% | 95.65% | 79.18% | 93.87% | 97.51% | 99.11% | 91.2% | 94.84% | 98.65% | 98.41% | 56.7% | 84.95%
| 15% | 89.03% | 3910.2412 | 68.25% | 2997.7083 | 15% | 96.14% | 98.9% | 99.64% | 98.65% | 96.11% | 97.43% | 86.26% | 99.55% | 99.38% | 99.49% | 97.48% | 97.23% | 99.31% | 99.14% | 68.25% | 89.03%
| 10% | 92.79% | 4075.1864 | 79.5% | 3491.5908 | 10% | 99.99% | 99.99% | 99.99% | 99.16% | 99.9% | 98.78% | 98.3% | 99.6% | 99.99% | 99.7% | 99.99% | 99.59% | 99.63% | 99.41% | 79.5% | 92.79%
| 5% | 96.81% | 4251.7223 | 90.07% | 3955.9766 | 5% | 99.99% | 99.99% | 99.99% | 99.49% | 99.99% | 99.76% | 99.99% | 99.61% | 99.99% | 99.99% | 99.99% | 99.99% | 99.68% | 99.6% | 90.07% | 96.81%
| 9.992e-14% | 99.99% | 4391.7028 | 99.99% | 4391.6218 | 0% | 99.99% | 99.99% | 99.99% | 99.99% | 99.99% | 99.99% | 99.99% | 99.63% | 99.99% | 99.99% | 99.99% | 99.99% | 99.71% | 99.63% | 99.99% | 99.99%
POE 50
[6 empty] | Stations | KLO |  | EPG |  | CRE |  | CLN |  | PHM |  | OFR |  | LLG |  | WGI
| % of MD | Winter - AD (P50) - Duration % | Winter - AD - Hours | Summer - AD - Duration % | Summer - AD - Hours | %MD | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration %
| 100% | 0% | 0 | 0% | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| 99% | 0.006767% | 0.2972 | 0.00861% | 0.37816 | 99% | 0.03444% | 0.02707% | 0.04305% | 0.04737% | 0% | 0% | 0% | 0.01353% | 0% | 0.03383% | 0% | 0.0203% | 0.00861% | 0.006767% | 0.00861% | 0.006767%
| 98% | 0.006767% | 0.2972 | 0.00861% | 0.37816 | 98% | 0.05166% | 0.07443% | 0.07749% | 0.08797% | 0% | 0.01353% | 0.00861% | 0.0203% | 0% | 0.07443% | 0.00861% | 0.0812% | 0.00861% | 0.0203% | 0.00861% | 0.006767%
| 97% | 0.006767% | 0.2972 | 0.00861% | 0.37816 | 97% | 0.06888% | 0.09474% | 0.07749% | 0.1421% | 0.02583% | 0.02707% | 0.01722% | 0.03383% | 0.00861% | 0.1556% | 0.01722% | 0.1083% | 0.01722% | 0.0406% | 0.00861% | 0.006767%
| 95% | 0.03383% | 1.486 | 0.01722% | 0.75633 | 95% | 0.0861% | 0.1895% | 0.1378% | 0.3519% | 0.04305% | 0.08797% | 0.02583% | 0.05413% | 0.05166% | 0.3992% | 0.04305% | 0.1759% | 0.01722% | 0.1015% | 0.01722% | 0.03383%
| 90% | 0.1962% | 8.6188 | 0.2066% | 9.0759 | 90% | 0.1292% | 0.9135% | 0.2583% | 1.786% | 0.1119% | 0.7579% | 0.1033% | 0.07443% | 0.1292% | 1.793% | 0.1033% | 0.8932% | 0.0861% | 0.3451% | 0.2066% | 0.1962%
| 85% | 0.9135% | 40.1218 | 0.9213% | 40.4636 | 85% | 0.2497% | 2.355% | 0.465% | 4.588% | 0.2755% | 2.761% | 0.1808% | 0.318% | 0.3616% | 5.393% | 0.2066% | 2.68% | 0.31% | 0.9% | 0.9213% | 0.9135%
| 80% | 2.118% | 93.0231 | 2.153% | 94.5411 | 80% | 0.4133% | 5.616% | 0.7835% | 8.885% | 0.6113% | 6.787% | 0.2669% | 0.9406% | 0.706% | 11.33% | 0.6286% | 6.11% | 0.8008% | 2.517% | 2.153% | 2.118%
| 75% | 4.486% | 197.0426 | 4.486% | 197.0236 | 75% | 0.8352% | 9.995% | 1.257% | 14.05% | 0.9902% | 11.76% | 0.4047% | 2.876% | 1.662% | 18.3% | 1.309% | 10.38% | 1.834% | 5.562% | 4.486% | 4.486%
| 70% | 8.607% | 378.0365 | 7.672% | 336.9444 | 70% | 1.619% | 14.12% | 2.101% | 19.88% | 1.911% | 17.56% | 0.8008% | 7.376% | 3.427% | 26.3% | 2.419% | 15.73% | 4.374% | 10.11% | 7.672% | 8.607%
| 65% | 14.03% | 616.0926 | 11.87% | 521.4885 | 65% | 3.057% | 18.84% | 4.288% | 27.11% | 3.504% | 25.21% | 1.352% | 12.51% | 8.188% | 35.36% | 4.598% | 22.03% | 9.179% | 17.54% | 11.87% | 14.03%
| 60% | 21.29% | 934.9866 | 18.5% | 812.675 | 60% | 5.528% | 25.14% | 9.342% | 35.21% | 7.758% | 33.62% | 3.573% | 18.2% | 15.71% | 46.14% | 9.17% | 29.44% | 16.83% | 27.53% | 18.5% | 21.29%
| 55% | 29.85% | 1310.9428 | 27.37% | 1202.1843 | 55% | 11.8% | 33.56% | 17.61% | 45.33% | 16.05% | 42.68% | 8.283% | 25.42% | 24.94% | 59.16% | 14.93% | 37.5% | 27.43% | 40.02% | 27.37% | 29.85%
| 50% | 39.4% | 1730.2899 | 38.39% | 1686.2345 | 50% | 21.47% | 44.25% | 28.46% | 58.26% | 24.85% | 54.87% | 17.57% | 34.04% | 37.94% | 73.62% | 22.35% | 47.91% | 40.6% | 54.15% | 38.39% | 39.4%
| 45% | 49.36% | 2168.0633 | 48.48% | 2129.0649 | 45% | 35.07% | 58.98% | 42.44% | 69.36% | 37.15% | 71.48% | 28.59% | 45.63% | 57.06% | 85.96% | 36.95% | 62.3% | 53.97% | 68.39% | 48.48% | 49.36%
| 40% | 59.42% | 2609.7004 | 56.57% | 2484.5393 | 40% | 60.78% | 71.65% | 63.35% | 75.98% | 61.17% | 84.31% | 46.88% | 65.51% | 72.05% | 92.73% | 55.62% | 79.32% | 65.21% | 80.79% | 56.57% | 59.42%
| 35% | 68.26% | 2998.1389 | 63.94% | 2808.248 | 35% | 70.59% | 78.94% | 76.04% | 85.16% | 71.05% | 88.52% | 69.68% | 78.66% | 80.86% | 95.6% | 68.46% | 87.21% | 75.09% | 89.43% | 63.94% | 68.26%
| 30% | 75.35% | 3309.3057 | 70.48% | 3095.6528 | 30% | 76.73% | 83.24% | 80.97% | 93.38% | 75.06% | 90.98% | 76.64% | 83.41% | 85.59% | 97.25% | 74.6% | 90.02% | 81.51% | 94.17% | 70.48% | 75.35%
| 25% | 80.55% | 3537.8514 | 76.48% | 3358.8552 | 25% | 83.08% | 87.43% | 85.41% | 96.1% | 78.56% | 93.44% | 83.93% | 87.95% | 89.4% | 98.4% | 78.93% | 92.46% | 86.44% | 96.81% | 76.48% | 80.55%
| 20% | 84.95% | 3731.0305 | 81.71% | 3588.7791 | 20% | 91.12% | 92.06% | 89.28% | 97.65% | 81.79% | 95.65% | 91.73% | 93.87% | 92.22% | 99.11% | 84.56% | 94.84% | 90.52% | 98.48% | 81.71% | 84.95%
| 15% | 89.03% | 3910.2412 | 86.58% | 3802.4419 | 15% | 99.18% | 98.9% | 92.61% | 98.65% | 86.18% | 97.43% | 98.93% | 99.55% | 94.55% | 99.49% | 92.06% | 97.23% | 93.75% | 99.28% | 86.58% | 89.03%
| 10% | 92.79% | 4075.1864 | 91.64% | 4024.8025 | 10% | 99.99% | 99.99% | 95.16% | 99.16% | 91.73% | 98.78% | 99.75% | 99.6% | 96.73% | 99.7% | 99.06% | 99.59% | 96.19% | 99.59% | 91.64% | 92.79%
| 5% | 96.81% | 4251.7223 | 96.54% | 4239.978 | 5% | 99.99% | 99.99% | 97.15% | 99.49% | 97.84% | 99.76% | 99.99% | 99.61% | 99.31% | 99.99% | 99.99% | 99.99% | 98.14% | 99.77% | 96.54% | 96.81%
| 9.992e-14% | 99.99% | 4391.7028 | 99.99% | 4391.6218 | 0% | 99.99% | 99.99% | 99.99% | 99.99% | 99.99% | 99.99% | 99.99% | 99.63% | 99.99% | 99.99% | 99.99% | 99.99% | 99.78% | 99.99% | 99.99% | 99.99%
POE10
|  | Summer | Winter
| Year | 2019/2020 | 2023
| Start | 2024-10-01 | 2024-04-01
| End | 2025-04-01 | 2024-10-01
| Days | 183 | 183
| Hours | 4392 | 4392
POE50
|  | Summer | Winter
| Year | 2023/2024 | 2023
| Start | 2023-10-01 | 2024-04-01
| End | 2024-04-01 | 2024-10-01
| Days | 183 | 183
| Hours | 4392 | 4392

## Capacity N
Option 1 - Do Nothing - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N Rating (MVA) - Option 1 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8
SCR N Rating (MVA) - Option 1 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8
Planned Additional Capacity (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2 - Replace 3 x 10/13.5 MVA Tx with 3 x 20/33 MVA Tx - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N Rating (MVA) - Option 2 | 56.8 | 56.8 | 56.8 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
SCR N Rating (MVA) - Option 2 | 55.8 | 55.8 | 55.8 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99
Capacity Added (MVA) | 0 | 0 | 0 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2
Option 3 - Replace 1 x 10/13.5 MVA Tx with 1 x 20/33 MVA Tx - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N Rating (MVA) - Option 3 | 56.8 | 56.8 | 56.8 | 72.15 | 72.15 | 72.15 | 72.15 | 72.15 | 72.15 | 72.15 | 72.15 | 72.15 | 72.15 | 72.15 | 72.15 | 72.15 | 72.15 | 72.15 | 72.15 | 72.15 | 72.15 | 72.15 | 72.15 | 72.15 | 72.15 | 72.15 | 72.15 | 72.15 | 72.15 | 72.15
SCR N Rating (MVA) - Option 3 | 55.8 | 55.8 | 55.8 | 71.15 | 71.15 | 71.15 | 71.15 | 71.15 | 71.15 | 71.15 | 71.15 | 71.15 | 71.15 | 71.15 | 71.15 | 71.15 | 71.15 | 71.15 | 71.15 | 71.15 | 71.15 | 71.15 | 71.15 | 71.15 | 71.15 | 71.15 | 71.15 | 71.15 | 71.15 | 71.15
Capacity Added (MVA) | 0 | 0 | 0 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35
Option 4 - Construct 2x 20/33MVA zone substation in Inverloch - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N Rating (MVA) - Option 4 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8
SCR N Rating (MVA) - Option 4 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 - Contract network support services to defer network investment - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N Rating (MVA) - Option 5 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8
SCR N Rating (MVA) - Option 5 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 6 - - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N Rating (MVA) - Option 6 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8
SCR N Rating (MVA) - Option 6 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 7 - - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N Rating (MVA) - Option 7 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8
SCR N Rating (MVA) - Option 7 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 8 - - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N Rating (MVA) - Option 8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8
SCR N Rating (MVA) - Option 8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Capacity N-1
Option 1 - Do Nothing - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-1 Rating (MVA) - Option 1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1
SCR N-1 Rating (MVA) - Option 1 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3
Planned Additional Capacity (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2 - Replace 3 x 10/13.5 MVA Tx with 3 x 20/33 MVA Tx - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-1 Rating (MVA) - Option 2 | 36.1 | 36.1 | 36.1 | 79.3 | 79.3 | 79.3 | 79.3 | 79.3 | 79.3 | 79.3 | 79.3 | 79.3 | 79.3 | 79.3 | 79.3 | 79.3 | 79.3 | 79.3 | 79.3 | 79.3 | 79.3 | 79.3 | 79.3 | 79.3 | 79.3 | 79.3 | 79.3 | 79.3 | 79.3 | 79.3
SCR N-1 Rating (MVA) - Option 2 | 35.3 | 35.3 | 35.3 | 78.5 | 78.5 | 78.5 | 78.5 | 78.5 | 78.5 | 78.5 | 78.5 | 78.5 | 78.5 | 78.5 | 78.5 | 78.5 | 78.5 | 78.5 | 78.5 | 78.5 | 78.5 | 78.5 | 78.5 | 78.5 | 78.5 | 78.5 | 78.5 | 78.5 | 78.5 | 78.5
Capacity Added (MVA) | 0 | 0 | 0 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2
Option 3 - Replace 1 x 10/13.5 MVA Tx with 1 x 20/33 MVA Tx - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-1 Rating (MVA) - Option 3 | 36.1 | 36.1 | 36.1 | 51.45 | 51.45 | 51.45 | 51.45 | 51.45 | 51.45 | 51.45 | 51.45 | 51.45 | 51.45 | 51.45 | 51.45 | 51.45 | 51.45 | 51.45 | 51.45 | 51.45 | 51.45 | 51.45 | 51.45 | 51.45 | 51.45 | 51.45 | 51.45 | 51.45 | 51.45 | 51.45
SCR N-1 Rating (MVA) - Option 3 | 35.3 | 35.3 | 35.3 | 50.65 | 50.65 | 50.65 | 50.65 | 50.65 | 50.65 | 50.65 | 50.65 | 50.65 | 50.65 | 50.65 | 50.65 | 50.65 | 50.65 | 50.65 | 50.65 | 50.65 | 50.65 | 50.65 | 50.65 | 50.65 | 50.65 | 50.65 | 50.65 | 50.65 | 50.65 | 50.65
Capacity Added (MVA) | 0 | 0 | 0 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35
Option 4 - Construct 2x 20/33MVA zone substation in Inverloch - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-1 Rating (MVA) - Option 4 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1
SCR N-1 Rating (MVA) - Option 4 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 - Contract network support services to defer network investment - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-1 Rating (MVA) - Option 5 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1
SCR N-1 Rating (MVA) - Option 5 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 6 - - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-1 Rating (MVA) - Option 6 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1
SCR N-1 Rating (MVA) - Option 6 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 7 - - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-1 Rating (MVA) - Option 7 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1
SCR N-1 Rating (MVA) - Option 7 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 8 - - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-1 Rating (MVA) - Option 8 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1
SCR N-1 Rating (MVA) - Option 8 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Capacity N-2
Option 1 - Do Nothing - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-2 Rating (MVA) - Option 1 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05
SCR N-2 Rating (MVA) - Option 1 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65
Planned Additional Capacity (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2 - Replace 3 x 10/13.5 MVA Tx with 3 x 20/33 MVA Tx - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-2 Rating (MVA) - Option 2 | 18.05 | 18.05 | 18.05 | 61.25 | 61.25 | 61.25 | 61.25 | 61.25 | 61.25 | 61.25 | 61.25 | 61.25 | 61.25 | 61.25 | 61.25 | 61.25 | 61.25 | 61.25 | 61.25 | 61.25 | 61.25 | 61.25 | 61.25 | 61.25 | 61.25 | 61.25 | 61.25 | 61.25 | 61.25 | 61.25
SCR N-2 Rating (MVA) - Option 2 | 17.65 | 17.65 | 17.65 | 60.85 | 60.85 | 60.85 | 60.85 | 60.85 | 60.85 | 60.85 | 60.85 | 60.85 | 60.85 | 60.85 | 60.85 | 60.85 | 60.85 | 60.85 | 60.85 | 60.85 | 60.85 | 60.85 | 60.85 | 60.85 | 60.85 | 60.85 | 60.85 | 60.85 | 60.85 | 60.85
Capacity Added (MVA) | 0 | 0 | 0 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2
Option 3 - Replace 1 x 10/13.5 MVA Tx with 1 x 20/33 MVA Tx - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-2 Rating (MVA) - Option 3 | 18.05 | 18.05 | 18.05 | 33.4 | 33.4 | 33.4 | 33.4 | 33.4 | 33.4 | 33.4 | 33.4 | 33.4 | 33.4 | 33.4 | 33.4 | 33.4 | 33.4 | 33.4 | 33.4 | 33.4 | 33.4 | 33.4 | 33.4 | 33.4 | 33.4 | 33.4 | 33.4 | 33.4 | 33.4 | 33.4
SCR N-2 Rating (MVA) - Option 3 | 17.65 | 17.65 | 17.65 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33
Capacity Added (MVA) | 0 | 0 | 0 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35
Option 4 - Construct 2x 20/33MVA zone substation in Inverloch - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-2 Rating (MVA) - Option 4 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05
SCR N-2 Rating (MVA) - Option 4 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 - Contract network support services to defer network investment - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-2 Rating (MVA) - Option 5 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05
SCR N-2 Rating (MVA) - Option 5 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 6 - - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-2 Rating (MVA) - Option 6 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05
SCR N-2 Rating (MVA) - Option 6 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 7 - - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-2 Rating (MVA) - Option 7 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05
SCR N-2 Rating (MVA) - Option 7 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 8 - - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-2 Rating (MVA) - Option 8 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05
SCR N-2 Rating (MVA) - Option 8 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Demand
Option 1 - Do Nothing
Winter Season | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Maximum Demand (MVA) - P50 | 43.4728 | 48.0113 | 48.4925 | 49.0875 | 49.8774 | 50.6263 | 51.935 | 55.2266 | 56.997 | 55.7054 | 59.704 | 60.4244 | 60.9423 | 63.3834 | 63.7807 | 63.7807 | 63.7807 | 63.7807 | 63.7807 | 63.7807 | 63.7807 | 63.7807 | 63.7807 | 63.7807 | 63.7807 | 63.7807 | 63.7807 | 63.7807 | 63.7807 | 63.7807
Maximum Demand (MVA) - P10 | 47.6439 | 51.973 | 52.4213 | 53.9685 | 53.9308 | 54.271 | 55.6016 | 59.4246 | 61.0022 | 59.5089 | 63.634 | 61.902 | 63.4604 | 64.5834 | 64.122 | 64.122 | 64.122 | 64.122 | 64.122 | 64.122 | 64.122 | 64.122 | 64.122 | 64.122 | 64.122 | 64.122 | 64.122 | 64.122 | 64.122 | 64.122
Block loads (MVA) not in the forecast | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Available Transfers (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Demand management (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Embedded generation (MVA) | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11
Total Maximum Demand (MVA) - Option 1 Winter POE50 | 43.3628 | 47.9013 | 48.3825 | 48.9775 | 49.7674 | 50.5163 | 51.825 | 55.1166 | 56.887 | 55.5954 | 59.594 | 60.3144 | 60.8323 | 63.2734 | 63.6707 | 63.6707 | 63.6707 | 63.6707 | 63.6707 | 63.6707 | 63.6707 | 63.6707 | 63.6707 | 63.6707 | 63.6707 | 63.6707 | 63.6707 | 63.6707 | 63.6707 | 63.6707
Total Maximum Demand (MVA) - Option 1 Winter POE10 | 47.5339 | 51.863 | 52.3113 | 53.8585 | 53.8208 | 54.161 | 55.4916 | 59.3146 | 60.8922 | 59.3989 | 63.524 | 61.792 | 63.3504 | 64.4734 | 64.012 | 64.012 | 64.012 | 64.012 | 64.012 | 64.012 | 64.012 | 64.012 | 64.012 | 64.012 | 64.012 | 64.012 | 64.012 | 64.012 | 64.012 | 64.012
Summer Season | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Maximum Demand (MVA) - P50 | 45.6633 | 49.0682 | 49.4104 | 49.2427 | 49.4021 | 49.4677 | 49.6777 | 50.1095 | 50.4727 | 50.6399 | 50.4909 | 51.1158 | 51.2149 | 51.0976 | 51.3328 | 51.3328 | 51.3328 | 51.3328 | 51.3328 | 51.3328 | 51.3328 | 51.3328 | 51.3328 | 51.3328 | 51.3328 | 51.3328 | 51.3328 | 51.3328 | 51.3328 | 51.3328
Maximum Demand (MVA) - P10 | 56.1511 | 59.9563 | 60.0613 | 59.9481 | 59.9772 | 60.185 | 60.6061 | 61.3477 | 61.7342 | 62.0137 | 62.4369 | 62.977 | 63.6303 | 63.9726 | 63.8616 | 63.8616 | 63.8616 | 63.8616 | 63.8616 | 63.8616 | 63.8616 | 63.8616 | 63.8616 | 63.8616 | 63.8616 | 63.8616 | 63.8616 | 63.8616 | 63.8616 | 63.8616
Block loads (MVA) not in the forecast | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Available Transfers (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Demand management (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Embedded generation (MVA) | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Maximum Demand (MVA) - Option 1 Summer POE50 | 45.5533 | 48.9582 | 49.3004 | 49.1327 | 49.2921 | 49.3577 | 49.5677 | 49.9995 | 50.3627 | 50.5299 | 50.3809 | 51.0058 | 51.1049 | 50.9876 | 51.2228 | 51.3328 | 51.3328 | 51.3328 | 51.3328 | 51.3328 | 51.3328 | 51.3328 | 51.3328 | 51.3328 | 51.3328 | 51.3328 | 51.3328 | 51.3328 | 51.3328 | 51.3328
Total Maximum Demand (MVA) - Option 1 Summer POE10 | 56.0411 | 59.8463 | 59.9513 | 59.8381 | 59.8672 | 60.075 | 60.4961 | 61.2377 | 61.6242 | 61.9037 | 62.3269 | 62.867 | 63.5203 | 63.8626 | 63.7516 | 63.8616 | 63.8616 | 63.8616 | 63.8616 | 63.8616 | 63.8616 | 63.8616 | 63.8616 | 63.8616 | 63.8616 | 63.8616 | 63.8616 | 63.8616 | 63.8616 | 63.8616
Option 2 - Replace 3 x 10/13.5 MVA Tx with 3 x 20/33 MVA Tx
Year | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Added Transfers (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Added Demand management (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Added Embedded generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Maximum Demand (MVA) - Option 2 Winter POE50 | 43.3628 | 47.9013 | 48.3825 | 48.9775 | 49.7674 | 50.5163 | 51.825 | 55.1166 | 56.887 | 55.5954 | 59.594 | 60.3144 | 60.8323 | 63.2734 | 63.6707 | 63.6707 | 63.6707 | 63.6707 | 63.6707 | 63.6707 | 63.6707 | 63.6707 | 63.6707 | 63.6707 | 63.6707 | 63.6707 | 63.6707 | 63.6707 | 63.6707 | 63.6707
Total Maximum Demand (MVA) - Option 2 Winter POE10 | 47.5339 | 51.863 | 52.3113 | 53.8585 | 53.8208 | 54.161 | 55.4916 | 59.3146 | 60.8922 | 59.3989 | 63.524 | 61.792 | 63.3504 | 64.4734 | 64.012 | 64.012 | 64.012 | 64.012 | 64.012 | 64.012 | 64.012 | 64.012 | 64.012 | 64.012 | 64.012 | 64.012 | 64.012 | 64.012 | 64.012 | 64.012
Total Maximum Demand (MVA) - Option 2 Summer POE50 | 45.5533 | 48.9582 | 49.3004 | 49.1327 | 49.2921 | 49.3577 | 49.5677 | 49.9995 | 50.3627 | 50.5299 | 50.3809 | 51.0058 | 51.1049 | 50.9876 | 51.2228 | 51.3328 | 51.3328 | 51.3328 | 51.3328 | 51.3328 | 51.3328 | 51.3328 | 51.3328 | 51.3328 | 51.3328 | 51.3328 | 51.3328 | 51.3328 | 51.3328 | 51.3328
Total Maximum Demand (MVA) - Option 2 Summer POE10 | 56.0411 | 59.8463 | 59.9513 | 59.8381 | 59.8672 | 60.075 | 60.4961 | 61.2377 | 61.6242 | 61.9037 | 62.3269 | 62.867 | 63.5203 | 63.8626 | 63.7516 | 63.8616 | 63.8616 | 63.8616 | 63.8616 | 63.8616 | 63.8616 | 63.8616 | 63.8616 | 63.8616 | 63.8616 | 63.8616 | 63.8616 | 63.8616 | 63.8616 | 63.8616
Option 3 - Replace 1 x 10/13.5 MVA Tx with 1 x 20/33 MVA Tx
Year | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Added Transfers (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Added Demand management (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Added Embedded generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Maximum Demand (MVA) - Option 3 Winter POE50 | 43.3628 | 47.9013 | 48.3825 | 48.9775 | 49.7674 | 50.5163 | 51.825 | 55.1166 | 56.887 | 55.5954 | 59.594 | 60.3144 | 60.8323 | 63.2734 | 63.6707 | 63.6707 | 63.6707 | 63.6707 | 63.6707 | 63.6707 | 63.6707 | 63.6707 | 63.6707 | 63.6707 | 63.6707 | 63.6707 | 63.6707 | 63.6707 | 63.6707 | 63.6707
Total Maximum Demand (MVA) - Option 3 Winter POE10 | 47.5339 | 51.863 | 52.3113 | 53.8585 | 53.8208 | 54.161 | 55.4916 | 59.3146 | 60.8922 | 59.3989 | 63.524 | 61.792 | 63.3504 | 64.4734 | 64.012 | 64.012 | 64.012 | 64.012 | 64.012 | 64.012 | 64.012 | 64.012 | 64.012 | 64.012 | 64.012 | 64.012 | 64.012 | 64.012 | 64.012 | 64.012
Total Maximum Demand (MVA) - Option 3 Summer POE50 | 45.5533 | 48.9582 | 49.3004 | 49.1327 | 49.2921 | 49.3577 | 49.5677 | 49.9995 | 50.3627 | 50.5299 | 50.3809 | 51.0058 | 51.1049 | 50.9876 | 51.2228 | 51.3328 | 51.3328 | 51.3328 | 51.3328 | 51.3328 | 51.3328 | 51.3328 | 51.3328 | 51.3328 | 51.3328 | 51.3328 | 51.3328 | 51.3328 | 51.3328 | 51.3328
Total Maximum Demand (MVA) - Option 3 Summer POE10 | 56.0411 | 59.8463 | 59.9513 | 59.8381 | 59.8672 | 60.075 | 60.4961 | 61.2377 | 61.6242 | 61.9037 | 62.3269 | 62.867 | 63.5203 | 63.8626 | 63.7516 | 63.8616 | 63.8616 | 63.8616 | 63.8616 | 63.8616 | 63.8616 | 63.8616 | 63.8616 | 63.8616 | 63.8616 | 63.8616 | 63.8616 | 63.8616 | 63.8616 | 63.8616
Option 4 - Construct 2x 20/33MVA zone substation in Inverloch
Year | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Added Transfers (MVA) | 0 | 0 | 0 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66
Added Demand management (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Added Embedded generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Maximum Demand (MVA) - Option 4 Winter POE50 | 43.3628 | 47.9013 | 48.3825 | -17.0225 | -16.2326 | -15.4837 | -14.175 | -10.8834 | -9.113 | -10.4046 | -6.406 | -5.6856 | -5.1677 | -2.7266 | -2.3293 | -2.3293 | -2.3293 | -2.3293 | -2.3293 | -2.3293 | -2.3293 | -2.3293 | -2.3293 | -2.3293 | -2.3293 | -2.3293 | -2.3293 | -2.3293 | -2.3293 | -2.3293
Total Maximum Demand (MVA) - Option 4 Winter POE10 | 47.5339 | 51.863 | 52.3113 | -12.1415 | -12.1792 | -11.839 | -10.5084 | -6.6854 | -5.1078 | -6.6011 | -2.476 | -4.208 | -2.6496 | -1.5266 | -1.988 | -1.988 | -1.988 | -1.988 | -1.988 | -1.988 | -1.988 | -1.988 | -1.988 | -1.988 | -1.988 | -1.988 | -1.988 | -1.988 | -1.988 | -1.988
Total Maximum Demand (MVA) - Option 4 Summer POE50 | 45.5533 | 48.9582 | 49.3004 | -16.8673 | -16.7079 | -16.6423 | -16.4323 | -16.0005 | -15.6373 | -15.4701 | -15.6191 | -14.9942 | -14.8951 | -15.0124 | -14.7772 | -14.6672 | -14.6672 | -14.6672 | -14.6672 | -14.6672 | -14.6672 | -14.6672 | -14.6672 | -14.6672 | -14.6672 | -14.6672 | -14.6672 | -14.6672 | -14.6672 | -14.6672
Total Maximum Demand (MVA) - Option 4 Summer POE10 | 56.0411 | 59.8463 | 59.9513 | -6.1619 | -6.1328 | -5.925 | -5.5039 | -4.7623 | -4.3758 | -4.0963 | -3.6731 | -3.133 | -2.4797 | -2.1374 | -2.2484 | -2.1384 | -2.1384 | -2.1384 | -2.1384 | -2.1384 | -2.1384 | -2.1384 | -2.1384 | -2.1384 | -2.1384 | -2.1384 | -2.1384 | -2.1384 | -2.1384 | -2.1384
Option 5 - Contract network support services to defer network investment
Year | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Added Transfers (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Added Demand management (MVA) | 4.0981 | 4.3758 | 4.3835 | 4.3752 | 4.3773 | 4.3925 | 4.4232 | 4.4774 | 4.5056 | 4.526 | 4.5569 | 4.5963 | 4.644 | 4.6689 | 4.6608 | 4.6608 | 4.6608 | 4.6608 | 4.6608 | 4.6608 | 4.6608 | 4.6608 | 4.6608 | 4.6608 | 4.6608 | 4.6608 | 4.6608 | 4.6608 | 4.6608 | 4.6608
Added Embedded generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Maximum Demand (MVA) - Option 5 Winter POE50 | 39.2647 | 43.5255 | 43.999 | 44.6023 | 45.3901 | 46.1238 | 47.4018 | 50.6392 | 52.3815 | 51.0695 | 55.0372 | 55.7181 | 56.1883 | 58.6044 | 59.0098 | 59.0098 | 59.0098 | 59.0098 | 59.0098 | 59.0098 | 59.0098 | 59.0098 | 59.0098 | 59.0098 | 59.0098 | 59.0098 | 59.0098 | 59.0098 | 59.0098 | 59.0098
Total Maximum Demand (MVA) - Option 5 Winter POE10 | 43.4358 | 47.4872 | 47.9278 | 49.4833 | 49.4434 | 49.7685 | 51.0684 | 54.8372 | 56.3866 | 54.8729 | 58.9671 | 57.1958 | 58.7065 | 59.8045 | 59.3512 | 59.3512 | 59.3512 | 59.3512 | 59.3512 | 59.3512 | 59.3512 | 59.3512 | 59.3512 | 59.3512 | 59.3512 | 59.3512 | 59.3512 | 59.3512 | 59.3512 | 59.3512
Total Maximum Demand (MVA) - Option 5 Summer POE50 | 41.4552 | 44.5824 | 44.9169 | 44.7574 | 44.9148 | 44.9651 | 45.1444 | 45.5221 | 45.8571 | 46.004 | 45.824 | 46.4095 | 46.4609 | 46.3186 | 46.5619 | 46.6719 | 46.6719 | 46.6719 | 46.6719 | 46.6719 | 46.6719 | 46.6719 | 46.6719 | 46.6719 | 46.6719 | 46.6719 | 46.6719 | 46.6719 | 46.6719 | 46.6719
Total Maximum Demand (MVA) - Option 5 Summer POE10 | 51.943 | 55.4705 | 55.5678 | 55.4629 | 55.4899 | 55.6825 | 56.0729 | 56.7604 | 57.1186 | 57.3778 | 57.77 | 58.2708 | 58.8763 | 59.1936 | 59.0908 | 59.2008 | 59.2008 | 59.2008 | 59.2008 | 59.2008 | 59.2008 | 59.2008 | 59.2008 | 59.2008 | 59.2008 | 59.2008 | 59.2008 | 59.2008 | 59.2008 | 59.2008
Option 6 -
Year | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Added Transfers (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Added Demand management (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Added Embedded generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Maximum Demand (MVA) - Option 6 Winter POE50 | 43.3628 | 47.9013 | 48.3825 | 48.9775 | 49.7674 | 50.5163 | 51.825 | 55.1166 | 56.887 | 55.5954 | 59.594 | 60.3144 | 60.8323 | 63.2734 | 63.6707 | 63.6707 | 63.6707 | 63.6707 | 63.6707 | 63.6707 | 63.6707 | 63.6707 | 63.6707 | 63.6707 | 63.6707 | 63.6707 | 63.6707 | 63.6707 | 63.6707 | 63.6707
Total Maximum Demand (MVA) - Option 6 Winter POE10 | 47.5339 | 51.863 | 52.3113 | 53.8585 | 53.8208 | 54.161 | 55.4916 | 59.3146 | 60.8922 | 59.3989 | 63.524 | 61.792 | 63.3504 | 64.4734 | 64.012 | 64.012 | 64.012 | 64.012 | 64.012 | 64.012 | 64.012 | 64.012 | 64.012 | 64.012 | 64.012 | 64.012 | 64.012 | 64.012 | 64.012 | 64.012
Total Maximum Demand (MVA) - Option 6 Summer POE50 | 45.5533 | 48.9582 | 49.3004 | 49.1327 | 49.2921 | 49.3577 | 49.5677 | 49.9995 | 50.3627 | 50.5299 | 50.3809 | 51.0058 | 51.1049 | 50.9876 | 51.2228 | 51.3328 | 51.3328 | 51.3328 | 51.3328 | 51.3328 | 51.3328 | 51.3328 | 51.3328 | 51.3328 | 51.3328 | 51.3328 | 51.3328 | 51.3328 | 51.3328 | 51.3328
Total Maximum Demand (MVA) - Option 6 Summer POE10 | 56.0411 | 59.8463 | 59.9513 | 59.8381 | 59.8672 | 60.075 | 60.4961 | 61.2377 | 61.6242 | 61.9037 | 62.3269 | 62.867 | 63.5203 | 63.8626 | 63.7516 | 63.8616 | 63.8616 | 63.8616 | 63.8616 | 63.8616 | 63.8616 | 63.8616 | 63.8616 | 63.8616 | 63.8616 | 63.8616 | 63.8616 | 63.8616 | 63.8616 | 63.8616
Option 7 -
Year | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Added Transfers (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Added Demand management (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Added Embedded generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Maximum Demand (MVA) - Option 7 Winter POE50 | 43.3628 | 47.9013 | 48.3825 | 48.9775 | 49.7674 | 50.5163 | 51.825 | 55.1166 | 56.887 | 55.5954 | 59.594 | 60.3144 | 60.8323 | 63.2734 | 63.6707 | 63.6707 | 63.6707 | 63.6707 | 63.6707 | 63.6707 | 63.6707 | 63.6707 | 63.6707 | 63.6707 | 63.6707 | 63.6707 | 63.6707 | 63.6707 | 63.6707 | 63.6707
Total Maximum Demand (MVA) - Option 7 Winter POE10 | 47.5339 | 51.863 | 52.3113 | 53.8585 | 53.8208 | 54.161 | 55.4916 | 59.3146 | 60.8922 | 59.3989 | 63.524 | 61.792 | 63.3504 | 64.4734 | 64.012 | 64.012 | 64.012 | 64.012 | 64.012 | 64.012 | 64.012 | 64.012 | 64.012 | 64.012 | 64.012 | 64.012 | 64.012 | 64.012 | 64.012 | 64.012
Total Maximum Demand (MVA) - Option 7 Summer POE50 | 45.5533 | 48.9582 | 49.3004 | 49.1327 | 49.2921 | 49.3577 | 49.5677 | 49.9995 | 50.3627 | 50.5299 | 50.3809 | 51.0058 | 51.1049 | 50.9876 | 51.2228 | 51.3328 | 51.3328 | 51.3328 | 51.3328 | 51.3328 | 51.3328 | 51.3328 | 51.3328 | 51.3328 | 51.3328 | 51.3328 | 51.3328 | 51.3328 | 51.3328 | 51.3328
Total Maximum Demand (MVA) - Option 7 Summer POE10 | 56.0411 | 59.8463 | 59.9513 | 59.8381 | 59.8672 | 60.075 | 60.4961 | 61.2377 | 61.6242 | 61.9037 | 62.3269 | 62.867 | 63.5203 | 63.8626 | 63.7516 | 63.8616 | 63.8616 | 63.8616 | 63.8616 | 63.8616 | 63.8616 | 63.8616 | 63.8616 | 63.8616 | 63.8616 | 63.8616 | 63.8616 | 63.8616 | 63.8616 | 63.8616
Option 8 -
Year | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Added Transfers (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Added Demand management (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Added Embedded generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Maximum Demand (MVA) - Option 8 Winter POE50 | 43.3628 | 47.9013 | 48.3825 | 48.9775 | 49.7674 | 50.5163 | 51.825 | 55.1166 | 56.887 | 55.5954 | 59.594 | 60.3144 | 60.8323 | 63.2734 | 63.6707 | 63.6707 | 63.6707 | 63.6707 | 63.6707 | 63.6707 | 63.6707 | 63.6707 | 63.6707 | 63.6707 | 63.6707 | 63.6707 | 63.6707 | 63.6707 | 63.6707 | 63.6707
Total Maximum Demand (MVA) - Option 8 Winter POE10 | 47.5339 | 51.863 | 52.3113 | 53.8585 | 53.8208 | 54.161 | 55.4916 | 59.3146 | 60.8922 | 59.3989 | 63.524 | 61.792 | 63.3504 | 64.4734 | 64.012 | 64.012 | 64.012 | 64.012 | 64.012 | 64.012 | 64.012 | 64.012 | 64.012 | 64.012 | 64.012 | 64.012 | 64.012 | 64.012 | 64.012 | 64.012
Total Maximum Demand (MVA) - Option 8 Summer POE50 | 45.5533 | 48.9582 | 49.3004 | 49.1327 | 49.2921 | 49.3577 | 49.5677 | 49.9995 | 50.3627 | 50.5299 | 50.3809 | 51.0058 | 51.1049 | 50.9876 | 51.2228 | 51.3328 | 51.3328 | 51.3328 | 51.3328 | 51.3328 | 51.3328 | 51.3328 | 51.3328 | 51.3328 | 51.3328 | 51.3328 | 51.3328 | 51.3328 | 51.3328 | 51.3328
Total Maximum Demand (MVA) - Option 8 Summer POE10 | 56.0411 | 59.8463 | 59.9513 | 59.8381 | 59.8672 | 60.075 | 60.4961 | 61.2377 | 61.6242 | 61.9037 | 62.3269 | 62.867 | 63.5203 | 63.8626 | 63.7516 | 63.8616 | 63.8616 | 63.8616 | 63.8616 | 63.8616 | 63.8616 | 63.8616 | 63.8616 | 63.8616 | 63.8616 | 63.8616 | 63.8616 | 63.8616 | 63.8616 | 63.8616

## Forecasted LDC
Option 1 - Do Nothing
Winter Season | [31 empty] | Winter Season
P50 | [31 empty] | P10
% of MD | Winter - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Winter - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 43.3628 | 47.9013 | 48.3825 | 48.9775 | 49.7674 | 50.5163 | 51.825 | 55.1166 | 56.887 | 55.5954 | 59.594 | 60.3144 | 60.8323 | 63.2734 | 63.6707 | 63.6707 | 63.6707 | 63.6707 | 63.6707 | 63.6707 | 63.6707 | 63.6707 | 63.6707 | 63.6707 | 63.6707 | 63.6707 | 63.6707 | 63.6707 | 63.6707 | 63.6707 | 100% | 0 | 47.5339 | 51.863 | 52.3113 | 53.8585 | 53.8208 | 54.161 | 55.4916 | 59.3146 | 60.8922 | 59.3989 | 63.524 | 61.792 | 63.3504 | 64.4734 | 64.012 | 64.012 | 64.012 | 64.012 | 64.012 | 64.012 | 64.012 | 64.012 | 64.012 | 64.012 | 64.012 | 64.012 | 64.012 | 64.012 | 64.012 | 64.012
99% | 0.2972 | 42.9291 | 47.4223 | 47.8987 | 48.4877 | 49.2697 | 50.0111 | 51.3068 | 54.5654 | 56.3182 | 55.0395 | 58.9981 | 59.7113 | 60.224 | 62.6406 | 63.034 | 63.034 | 63.034 | 63.034 | 63.034 | 63.034 | 63.034 | 63.034 | 63.034 | 63.034 | 63.034 | 63.034 | 63.034 | 63.034 | 63.034 | 63.034 | 99% | 0.2972 | 47.0586 | 51.3443 | 51.7882 | 53.3199 | 53.2826 | 53.6194 | 54.9367 | 58.7214 | 60.2833 | 58.8049 | 62.8887 | 61.1741 | 62.7169 | 63.8287 | 63.3719 | 63.3719 | 63.3719 | 63.3719 | 63.3719 | 63.3719 | 63.3719 | 63.3719 | 63.3719 | 63.3719 | 63.3719 | 63.3719 | 63.3719 | 63.3719 | 63.3719 | 63.3719
98% | 0.2972 | 42.4955 | 46.9432 | 47.4149 | 47.9979 | 48.7721 | 49.506 | 50.7885 | 54.0143 | 55.7493 | 54.4835 | 58.4021 | 59.1081 | 59.6156 | 62.0079 | 62.3973 | 62.3973 | 62.3973 | 62.3973 | 62.3973 | 62.3973 | 62.3973 | 62.3973 | 62.3973 | 62.3973 | 62.3973 | 62.3973 | 62.3973 | 62.3973 | 62.3973 | 62.3973 | 98% | 0.2972 | 46.5832 | 50.8257 | 51.2651 | 52.7813 | 52.7443 | 53.0778 | 54.3818 | 58.1283 | 59.6743 | 58.2109 | 62.2535 | 60.5562 | 62.0834 | 63.184 | 62.7318 | 62.7318 | 62.7318 | 62.7318 | 62.7318 | 62.7318 | 62.7318 | 62.7318 | 62.7318 | 62.7318 | 62.7318 | 62.7318 | 62.7318 | 62.7318 | 62.7318 | 62.7318
97% | 0.2972 | 42.0619 | 46.4642 | 46.931 | 47.5082 | 48.2744 | 49.0008 | 50.2703 | 53.4631 | 55.1804 | 53.9276 | 57.8062 | 58.505 | 59.0073 | 61.3752 | 61.7606 | 61.7606 | 61.7606 | 61.7606 | 61.7606 | 61.7606 | 61.7606 | 61.7606 | 61.7606 | 61.7606 | 61.7606 | 61.7606 | 61.7606 | 61.7606 | 61.7606 | 61.7606 | 97% | 0.2972 | 46.1079 | 50.3071 | 50.7419 | 52.2427 | 52.2061 | 52.5362 | 53.8269 | 57.5352 | 59.0654 | 57.6169 | 61.6183 | 59.9383 | 61.4499 | 62.5392 | 62.0917 | 62.0917 | 62.0917 | 62.0917 | 62.0917 | 62.0917 | 62.0917 | 62.0917 | 62.0917 | 62.0917 | 62.0917 | 62.0917 | 62.0917 | 62.0917 | 62.0917 | 62.0917
95% | 1.486 | 41.1946 | 45.5062 | 45.9634 | 46.5286 | 47.2791 | 47.9905 | 49.2338 | 52.3608 | 54.0427 | 52.8157 | 56.6143 | 57.2987 | 57.7907 | 60.1097 | 60.4871 | 60.4871 | 60.4871 | 60.4871 | 60.4871 | 60.4871 | 60.4871 | 60.4871 | 60.4871 | 60.4871 | 60.4871 | 60.4871 | 60.4871 | 60.4871 | 60.4871 | 60.4871 | 95% | 1.486 | 45.1572 | 49.2698 | 49.6957 | 51.1655 | 51.1297 | 51.4529 | 52.717 | 56.3489 | 57.8476 | 56.4289 | 60.3478 | 58.7024 | 60.1829 | 61.2498 | 60.8114 | 60.8114 | 60.8114 | 60.8114 | 60.8114 | 60.8114 | 60.8114 | 60.8114 | 60.8114 | 60.8114 | 60.8114 | 60.8114 | 60.8114 | 60.8114 | 60.8114 | 60.8114
90% | 8.6188 | 39.0265 | 43.1111 | 43.5443 | 44.0797 | 44.7907 | 45.4647 | 46.6425 | 49.6049 | 51.1983 | 50.0359 | 53.6346 | 54.283 | 54.7491 | 56.946 | 57.3036 | 57.3036 | 57.3036 | 57.3036 | 57.3036 | 57.3036 | 57.3036 | 57.3036 | 57.3036 | 57.3036 | 57.3036 | 57.3036 | 57.3036 | 57.3036 | 57.3036 | 57.3036 | 90% | 8.6188 | 42.7805 | 46.6767 | 47.0802 | 48.4726 | 48.4387 | 48.7449 | 49.9425 | 53.3831 | 54.803 | 53.459 | 57.1716 | 55.6128 | 57.0154 | 58.0261 | 57.6108 | 57.6108 | 57.6108 | 57.6108 | 57.6108 | 57.6108 | 57.6108 | 57.6108 | 57.6108 | 57.6108 | 57.6108 | 57.6108 | 57.6108 | 57.6108 | 57.6108 | 57.6108
85% | 40.1218 | 36.8584 | 40.7161 | 41.1251 | 41.6309 | 42.3023 | 42.9389 | 44.0513 | 46.8491 | 48.354 | 47.2561 | 50.6549 | 51.2673 | 51.7074 | 53.7823 | 54.1201 | 54.1201 | 54.1201 | 54.1201 | 54.1201 | 54.1201 | 54.1201 | 54.1201 | 54.1201 | 54.1201 | 54.1201 | 54.1201 | 54.1201 | 54.1201 | 54.1201 | 54.1201 | 85% | 40.1218 | 40.4038 | 44.0835 | 44.4646 | 45.7797 | 45.7477 | 46.0368 | 47.1679 | 50.4174 | 51.7583 | 50.489 | 53.9954 | 52.5232 | 53.8479 | 54.8024 | 54.4102 | 54.4102 | 54.4102 | 54.4102 | 54.4102 | 54.4102 | 54.4102 | 54.4102 | 54.4102 | 54.4102 | 54.4102 | 54.4102 | 54.4102 | 54.4102 | 54.4102 | 54.4102
80% | 93.0231 | 34.6902 | 38.321 | 38.706 | 39.182 | 39.8139 | 40.413 | 41.46 | 44.0933 | 45.5096 | 44.4764 | 47.6752 | 48.2515 | 48.6658 | 50.6187 | 50.9365 | 50.9365 | 50.9365 | 50.9365 | 50.9365 | 50.9365 | 50.9365 | 50.9365 | 50.9365 | 50.9365 | 50.9365 | 50.9365 | 50.9365 | 50.9365 | 50.9365 | 50.9365 | 80% | 93.0231 | 38.0271 | 41.4904 | 41.849 | 43.0868 | 43.0566 | 43.3288 | 44.3933 | 47.4517 | 48.7137 | 47.5191 | 50.8192 | 49.4336 | 50.6803 | 51.5787 | 51.2096 | 51.2096 | 51.2096 | 51.2096 | 51.2096 | 51.2096 | 51.2096 | 51.2096 | 51.2096 | 51.2096 | 51.2096 | 51.2096 | 51.2096 | 51.2096 | 51.2096 | 51.2096
75% | 197.0426 | 32.5221 | 35.926 | 36.2869 | 36.7331 | 37.3256 | 37.8872 | 38.8688 | 41.3374 | 42.6653 | 41.6966 | 44.6955 | 45.2358 | 45.6242 | 47.455 | 47.753 | 47.753 | 47.753 | 47.753 | 47.753 | 47.753 | 47.753 | 47.753 | 47.753 | 47.753 | 47.753 | 47.753 | 47.753 | 47.753 | 47.753 | 47.753 | 75% | 197.0426 | 35.6504 | 38.8972 | 39.2335 | 40.3939 | 40.3656 | 40.6207 | 41.6187 | 44.4859 | 45.6691 | 44.5491 | 47.643 | 46.344 | 47.5128 | 48.3551 | 48.009 | 48.009 | 48.009 | 48.009 | 48.009 | 48.009 | 48.009 | 48.009 | 48.009 | 48.009 | 48.009 | 48.009 | 48.009 | 48.009 | 48.009 | 48.009
70% | 378.0365 | 30.3539 | 33.5309 | 33.8678 | 34.2842 | 34.8372 | 35.3614 | 36.2775 | 38.5816 | 39.8209 | 38.9168 | 41.7158 | 42.2201 | 42.5826 | 44.2913 | 44.5695 | 44.5695 | 44.5695 | 44.5695 | 44.5695 | 44.5695 | 44.5695 | 44.5695 | 44.5695 | 44.5695 | 44.5695 | 44.5695 | 44.5695 | 44.5695 | 44.5695 | 44.5695 | 70% | 378.0365 | 33.2737 | 36.3041 | 36.6179 | 37.7009 | 37.6745 | 37.9127 | 38.8441 | 41.5202 | 42.6245 | 41.5792 | 44.4668 | 43.2544 | 44.3453 | 45.1314 | 44.8084 | 44.8084 | 44.8084 | 44.8084 | 44.8084 | 44.8084 | 44.8084 | 44.8084 | 44.8084 | 44.8084 | 44.8084 | 44.8084 | 44.8084 | 44.8084 | 44.8084 | 44.8084
65% | 616.0926 | 28.1858 | 31.1358 | 31.4486 | 31.8354 | 32.3488 | 32.8356 | 33.6863 | 35.8258 | 36.9766 | 36.137 | 38.7361 | 39.2044 | 39.541 | 41.1277 | 41.3859 | 41.3859 | 41.3859 | 41.3859 | 41.3859 | 41.3859 | 41.3859 | 41.3859 | 41.3859 | 41.3859 | 41.3859 | 41.3859 | 41.3859 | 41.3859 | 41.3859 | 41.3859 | 65% | 616.0926 | 30.897 | 33.7109 | 34.0023 | 35.008 | 34.9835 | 35.2046 | 36.0696 | 38.5545 | 39.5799 | 38.6093 | 41.2906 | 40.1648 | 41.1778 | 41.9077 | 41.6078 | 41.6078 | 41.6078 | 41.6078 | 41.6078 | 41.6078 | 41.6078 | 41.6078 | 41.6078 | 41.6078 | 41.6078 | 41.6078 | 41.6078 | 41.6078 | 41.6078 | 41.6078
60% | 934.9866 | 26.0177 | 28.7408 | 29.0295 | 29.3865 | 29.8605 | 30.3098 | 31.095 | 33.07 | 34.1322 | 33.3573 | 35.7564 | 36.1887 | 36.4994 | 37.964 | 38.2024 | 38.2024 | 38.2024 | 38.2024 | 38.2024 | 38.2024 | 38.2024 | 38.2024 | 38.2024 | 38.2024 | 38.2024 | 38.2024 | 38.2024 | 38.2024 | 38.2024 | 38.2024 | 60% | 934.9866 | 28.5203 | 31.1178 | 31.3868 | 32.3151 | 32.2925 | 32.4966 | 33.295 | 35.5888 | 36.5353 | 35.6393 | 38.1144 | 37.0752 | 38.0103 | 38.6841 | 38.4072 | 38.4072 | 38.4072 | 38.4072 | 38.4072 | 38.4072 | 38.4072 | 38.4072 | 38.4072 | 38.4072 | 38.4072 | 38.4072 | 38.4072 | 38.4072 | 38.4072 | 38.4072
55% | 1310.9428 | 23.8495 | 26.3457 | 26.6104 | 26.9376 | 27.3721 | 27.784 | 28.5038 | 30.3141 | 31.2879 | 30.5775 | 32.7767 | 33.1729 | 33.4578 | 34.8003 | 35.0189 | 35.0189 | 35.0189 | 35.0189 | 35.0189 | 35.0189 | 35.0189 | 35.0189 | 35.0189 | 35.0189 | 35.0189 | 35.0189 | 35.0189 | 35.0189 | 35.0189 | 35.0189 | 55% | 1310.9428 | 26.1436 | 28.5246 | 28.7712 | 29.6222 | 29.6014 | 29.7885 | 30.5204 | 32.623 | 33.4907 | 32.6694 | 34.9382 | 33.9856 | 34.8427 | 35.4604 | 35.2066 | 35.2066 | 35.2066 | 35.2066 | 35.2066 | 35.2066 | 35.2066 | 35.2066 | 35.2066 | 35.2066 | 35.2066 | 35.2066 | 35.2066 | 35.2066 | 35.2066 | 35.2066
50% | 1730.2899 | 21.6814 | 23.9506 | 24.1913 | 24.4887 | 24.8837 | 25.2582 | 25.9125 | 27.5583 | 28.4435 | 27.7977 | 29.797 | 30.1572 | 30.4161 | 31.6367 | 31.8353 | 31.8353 | 31.8353 | 31.8353 | 31.8353 | 31.8353 | 31.8353 | 31.8353 | 31.8353 | 31.8353 | 31.8353 | 31.8353 | 31.8353 | 31.8353 | 31.8353 | 31.8353 | 50% | 1730.2899 | 23.7669 | 25.9315 | 26.1556 | 26.9292 | 26.9104 | 27.0805 | 27.7458 | 29.6573 | 30.4461 | 29.6994 | 31.762 | 30.896 | 31.6752 | 32.2367 | 32.006 | 32.006 | 32.006 | 32.006 | 32.006 | 32.006 | 32.006 | 32.006 | 32.006 | 32.006 | 32.006 | 32.006 | 32.006 | 32.006 | 32.006 | 32.006
45% | 2168.0633 | 19.5132 | 21.5556 | 21.7721 | 22.0399 | 22.3953 | 22.7323 | 23.3213 | 24.8025 | 25.5992 | 25.0179 | 26.8173 | 27.1415 | 27.3745 | 28.473 | 28.6518 | 28.6518 | 28.6518 | 28.6518 | 28.6518 | 28.6518 | 28.6518 | 28.6518 | 28.6518 | 28.6518 | 28.6518 | 28.6518 | 28.6518 | 28.6518 | 28.6518 | 28.6518 | 45% | 2168.0633 | 21.3903 | 23.3383 | 23.5401 | 24.2363 | 24.2193 | 24.3724 | 24.9712 | 26.6916 | 27.4015 | 26.7295 | 28.5858 | 27.8064 | 28.5077 | 29.013 | 28.8054 | 28.8054 | 28.8054 | 28.8054 | 28.8054 | 28.8054 | 28.8054 | 28.8054 | 28.8054 | 28.8054 | 28.8054 | 28.8054 | 28.8054 | 28.8054 | 28.8054 | 28.8054
40% | 2609.7004 | 17.3451 | 19.1605 | 19.353 | 19.591 | 19.907 | 20.2065 | 20.73 | 22.0466 | 22.7548 | 22.2382 | 23.8376 | 24.1258 | 24.3329 | 25.3093 | 25.4683 | 25.4683 | 25.4683 | 25.4683 | 25.4683 | 25.4683 | 25.4683 | 25.4683 | 25.4683 | 25.4683 | 25.4683 | 25.4683 | 25.4683 | 25.4683 | 25.4683 | 25.4683 | 40% | 2609.7004 | 19.0136 | 20.7452 | 20.9245 | 21.5434 | 21.5283 | 21.6644 | 22.1966 | 23.7258 | 24.3569 | 23.7595 | 25.4096 | 24.7168 | 25.3402 | 25.7894 | 25.6048 | 25.6048 | 25.6048 | 25.6048 | 25.6048 | 25.6048 | 25.6048 | 25.6048 | 25.6048 | 25.6048 | 25.6048 | 25.6048 | 25.6048 | 25.6048 | 25.6048 | 25.6048
35% | 2998.1389 | 15.177 | 16.7654 | 16.9339 | 17.1421 | 17.4186 | 17.6807 | 18.1388 | 19.2908 | 19.9105 | 19.4584 | 20.8579 | 21.1101 | 21.2913 | 22.1457 | 22.2847 | 22.2847 | 22.2847 | 22.2847 | 22.2847 | 22.2847 | 22.2847 | 22.2847 | 22.2847 | 22.2847 | 22.2847 | 22.2847 | 22.2847 | 22.2847 | 22.2847 | 22.2847 | 35% | 2998.1389 | 16.6369 | 18.152 | 18.3089 | 18.8505 | 18.8373 | 18.9563 | 19.4221 | 20.7601 | 21.3123 | 20.7896 | 22.2334 | 21.6272 | 22.1726 | 22.5657 | 22.4042 | 22.4042 | 22.4042 | 22.4042 | 22.4042 | 22.4042 | 22.4042 | 22.4042 | 22.4042 | 22.4042 | 22.4042 | 22.4042 | 22.4042 | 22.4042 | 22.4042 | 22.4042
30% | 3309.3057 | 13.0088 | 14.3704 | 14.5148 | 14.6932 | 14.9302 | 15.1549 | 15.5475 | 16.535 | 17.0661 | 16.6786 | 17.8782 | 18.0943 | 18.2497 | 18.982 | 19.1012 | 19.1012 | 19.1012 | 19.1012 | 19.1012 | 19.1012 | 19.1012 | 19.1012 | 19.1012 | 19.1012 | 19.1012 | 19.1012 | 19.1012 | 19.1012 | 19.1012 | 19.1012 | 30% | 3309.3057 | 14.2602 | 15.5589 | 15.6934 | 16.1575 | 16.1462 | 16.2483 | 16.6475 | 17.7944 | 18.2677 | 17.8197 | 19.0572 | 18.5376 | 19.0051 | 19.342 | 19.2036 | 19.2036 | 19.2036 | 19.2036 | 19.2036 | 19.2036 | 19.2036 | 19.2036 | 19.2036 | 19.2036 | 19.2036 | 19.2036 | 19.2036 | 19.2036 | 19.2036 | 19.2036
25% | 3537.8514 | 10.8407 | 11.9753 | 12.0956 | 12.2444 | 12.4419 | 12.6291 | 12.9563 | 13.7791 | 14.2218 | 13.8989 | 14.8985 | 15.0786 | 15.2081 | 15.8183 | 15.9177 | 15.9177 | 15.9177 | 15.9177 | 15.9177 | 15.9177 | 15.9177 | 15.9177 | 15.9177 | 15.9177 | 15.9177 | 15.9177 | 15.9177 | 15.9177 | 15.9177 | 15.9177 | 25% | 3537.8514 | 11.8835 | 12.9657 | 13.0778 | 13.4646 | 13.4552 | 13.5402 | 13.8729 | 14.8286 | 15.223 | 14.8497 | 15.881 | 15.448 | 15.8376 | 16.1184 | 16.003 | 16.003 | 16.003 | 16.003 | 16.003 | 16.003 | 16.003 | 16.003 | 16.003 | 16.003 | 16.003 | 16.003 | 16.003 | 16.003 | 16.003 | 16.003
20% | 3731.0305 | 8.6726 | 9.5803 | 9.6765 | 9.7955 | 9.9535 | 10.1033 | 10.365 | 11.0233 | 11.3774 | 11.1191 | 11.9188 | 12.0629 | 12.1665 | 12.6547 | 12.7341 | 12.7341 | 12.7341 | 12.7341 | 12.7341 | 12.7341 | 12.7341 | 12.7341 | 12.7341 | 12.7341 | 12.7341 | 12.7341 | 12.7341 | 12.7341 | 12.7341 | 12.7341 | 20% | 3731.0305 | 9.5068 | 10.3726 | 10.4623 | 10.7717 | 10.7642 | 10.8322 | 11.0983 | 11.8629 | 12.1784 | 11.8798 | 12.7048 | 12.3584 | 12.6701 | 12.8947 | 12.8024 | 12.8024 | 12.8024 | 12.8024 | 12.8024 | 12.8024 | 12.8024 | 12.8024 | 12.8024 | 12.8024 | 12.8024 | 12.8024 | 12.8024 | 12.8024 | 12.8024 | 12.8024
15% | 3910.2412 | 6.5044 | 7.1852 | 7.2574 | 7.3466 | 7.4651 | 7.5774 | 7.7738 | 8.2675 | 8.5331 | 8.3393 | 8.9391 | 9.0472 | 9.1248 | 9.491 | 9.5506 | 9.5506 | 9.5506 | 9.5506 | 9.5506 | 9.5506 | 9.5506 | 9.5506 | 9.5506 | 9.5506 | 9.5506 | 9.5506 | 9.5506 | 9.5506 | 9.5506 | 9.5506 | 15% | 3910.2412 | 7.1301 | 7.7794 | 7.8467 | 8.0788 | 8.0731 | 8.1241 | 8.3237 | 8.8972 | 9.1338 | 8.9098 | 9.5286 | 9.2688 | 9.5026 | 9.671 | 9.6018 | 9.6018 | 9.6018 | 9.6018 | 9.6018 | 9.6018 | 9.6018 | 9.6018 | 9.6018 | 9.6018 | 9.6018 | 9.6018 | 9.6018 | 9.6018 | 9.6018 | 9.6018
10% | 4075.1864 | 4.3363 | 4.7901 | 4.8383 | 4.8977 | 4.9767 | 5.0516 | 5.1825 | 5.5117 | 5.6887 | 5.5595 | 5.9594 | 6.0314 | 6.0832 | 6.3273 | 6.3671 | 6.3671 | 6.3671 | 6.3671 | 6.3671 | 6.3671 | 6.3671 | 6.3671 | 6.3671 | 6.3671 | 6.3671 | 6.3671 | 6.3671 | 6.3671 | 6.3671 | 6.3671 | 10% | 4075.1864 | 4.7534 | 5.1863 | 5.2311 | 5.3858 | 5.3821 | 5.4161 | 5.5492 | 5.9315 | 6.0892 | 5.9399 | 6.3524 | 6.1792 | 6.335 | 6.4473 | 6.4012 | 6.4012 | 6.4012 | 6.4012 | 6.4012 | 6.4012 | 6.4012 | 6.4012 | 6.4012 | 6.4012 | 6.4012 | 6.4012 | 6.4012 | 6.4012 | 6.4012 | 6.4012
5% | 4251.7223 | 2.1681 | 2.3951 | 2.4191 | 2.4489 | 2.4884 | 2.5258 | 2.5913 | 2.7558 | 2.8444 | 2.7798 | 2.9797 | 3.0157 | 3.0416 | 3.1637 | 3.1835 | 3.1835 | 3.1835 | 3.1835 | 3.1835 | 3.1835 | 3.1835 | 3.1835 | 3.1835 | 3.1835 | 3.1835 | 3.1835 | 3.1835 | 3.1835 | 3.1835 | 3.1835 | 5% | 4251.7223 | 2.3767 | 2.5931 | 2.6156 | 2.6929 | 2.691 | 2.708 | 2.7746 | 2.9657 | 3.0446 | 2.9699 | 3.1762 | 3.0896 | 3.1675 | 3.2237 | 3.2006 | 3.2006 | 3.2006 | 3.2006 | 3.2006 | 3.2006 | 3.2006 | 3.2006 | 3.2006 | 3.2006 | 3.2006 | 3.2006 | 3.2006 | 3.2006 | 3.2006 | 3.2006
9.992e-14% | 4391.7028 | 4.3328e-14 | 4.7863e-14 | 4.8344e-14 | 4.8938e-14 | 4.9728e-14 | 5.0476e-14 | 5.1784e-14 | 5.5073e-14 | 5.6842e-14 | 5.5551e-14 | 5.9546e-14 | 6.0266e-14 | 6.0784e-14 | 6.3223e-14 | 6.362e-14 | 6.362e-14 | 6.362e-14 | 6.362e-14 | 6.362e-14 | 6.362e-14 | 6.362e-14 | 6.362e-14 | 6.362e-14 | 6.362e-14 | 6.362e-14 | 6.362e-14 | 6.362e-14 | 6.362e-14 | 6.362e-14 | 6.362e-14 | 9.992e-14% | 4391.7028 | 4.7496e-14 | 5.1822e-14 | 5.2269e-14 | 5.3815e-14 | 5.3778e-14 | 5.4118e-14 | 5.5447e-14 | 5.9267e-14 | 6.0844e-14 | 5.9351e-14 | 6.3473e-14 | 6.1743e-14 | 6.33e-14 | 6.4422e-14 | 6.3961e-14 | 6.3961e-14 | 6.3961e-14 | 6.3961e-14 | 6.3961e-14 | 6.3961e-14 | 6.3961e-14 | 6.3961e-14 | 6.3961e-14 | 6.3961e-14 | 6.3961e-14 | 6.3961e-14 | 6.3961e-14 | 6.3961e-14 | 6.3961e-14 | 6.3961e-14
Summer Season | [31 empty] | Summer Season
P50 | [31 empty] | P10
% of MD | Summer - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Summer - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 45.5533 | 48.9582 | 49.3004 | 49.1327 | 49.2921 | 49.3577 | 49.5677 | 49.9995 | 50.3627 | 50.5299 | 50.3809 | 51.0058 | 51.1049 | 50.9876 | 51.2228 | 51.3328 | 51.3328 | 51.3328 | 51.3328 | 51.3328 | 51.3328 | 51.3328 | 51.3328 | 51.3328 | 51.3328 | 51.3328 | 51.3328 | 51.3328 | 51.3328 | 51.3328 | 100% | 0 | 56.0411 | 59.8463 | 59.9513 | 59.8381 | 59.8672 | 60.075 | 60.4961 | 61.2377 | 61.6242 | 61.9037 | 62.3269 | 62.867 | 63.5203 | 63.8626 | 63.7516 | 63.8616 | 63.8616 | 63.8616 | 63.8616 | 63.8616 | 63.8616 | 63.8616 | 63.8616 | 63.8616 | 63.8616 | 63.8616 | 63.8616 | 63.8616 | 63.8616 | 63.8616
99% | 0.37816 | 45.0978 | 48.4686 | 48.8074 | 48.6413 | 48.7992 | 48.8641 | 49.072 | 49.4995 | 49.8591 | 50.0246 | 49.8771 | 50.4957 | 50.5938 | 50.4777 | 50.7105 | 50.8194 | 50.8194 | 50.8194 | 50.8194 | 50.8194 | 50.8194 | 50.8194 | 50.8194 | 50.8194 | 50.8194 | 50.8194 | 50.8194 | 50.8194 | 50.8194 | 50.8194 | 99% | 0 | 55.4807 | 59.2478 | 59.3518 | 59.2397 | 59.2685 | 59.4742 | 59.8911 | 60.6254 | 61.0079 | 61.2847 | 61.7036 | 62.2384 | 62.8851 | 63.224 | 63.1141 | 63.223 | 63.223 | 63.223 | 63.223 | 63.223 | 63.223 | 63.223 | 63.223 | 63.223 | 63.223 | 63.223 | 63.223 | 63.223 | 63.223 | 63.223
98% | 0.37816 | 44.6423 | 47.9791 | 48.3144 | 48.15 | 48.3063 | 48.3705 | 48.5763 | 48.9995 | 49.3555 | 49.5193 | 49.3733 | 49.9856 | 50.0828 | 49.9678 | 50.1983 | 50.3061 | 50.3061 | 50.3061 | 50.3061 | 50.3061 | 50.3061 | 50.3061 | 50.3061 | 50.3061 | 50.3061 | 50.3061 | 50.3061 | 50.3061 | 50.3061 | 50.3061 | 98% | 0 | 54.9203 | 58.6494 | 58.7523 | 58.6413 | 58.6699 | 58.8735 | 59.2862 | 60.013 | 60.3917 | 60.6657 | 61.0803 | 61.6097 | 62.2499 | 62.5853 | 62.4766 | 62.5844 | 62.5844 | 62.5844 | 62.5844 | 62.5844 | 62.5844 | 62.5844 | 62.5844 | 62.5844 | 62.5844 | 62.5844 | 62.5844 | 62.5844 | 62.5844 | 62.5844
97% | 0.37816 | 44.1867 | 47.4895 | 47.8214 | 47.6587 | 47.8134 | 47.8769 | 48.0806 | 48.4995 | 48.8518 | 49.014 | 48.8695 | 49.4756 | 49.5717 | 49.458 | 49.6861 | 49.7928 | 49.7928 | 49.7928 | 49.7928 | 49.7928 | 49.7928 | 49.7928 | 49.7928 | 49.7928 | 49.7928 | 49.7928 | 49.7928 | 49.7928 | 49.7928 | 49.7928 | 97% | 0.37816 | 54.3599 | 58.0509 | 58.1528 | 58.0429 | 58.0712 | 58.2727 | 58.6812 | 59.4006 | 59.7754 | 60.0466 | 60.457 | 60.981 | 61.6146 | 61.9467 | 61.8391 | 61.9458 | 61.9458 | 61.9458 | 61.9458 | 61.9458 | 61.9458 | 61.9458 | 61.9458 | 61.9458 | 61.9458 | 61.9458 | 61.9458 | 61.9458 | 61.9458 | 61.9458
95% | 0.75633 | 43.2757 | 46.5103 | 46.8354 | 46.676 | 46.8275 | 46.8898 | 47.0893 | 47.4995 | 47.8446 | 48.0034 | 47.8618 | 48.4555 | 48.5496 | 48.4382 | 48.6616 | 48.7661 | 48.7661 | 48.7661 | 48.7661 | 48.7661 | 48.7661 | 48.7661 | 48.7661 | 48.7661 | 48.7661 | 48.7661 | 48.7661 | 48.7661 | 48.7661 | 48.7661 | 95% | 0.37816 | 53.2391 | 56.854 | 56.9537 | 56.8462 | 56.8738 | 57.0712 | 57.4713 | 58.1758 | 58.543 | 58.8086 | 59.2105 | 59.7237 | 60.3442 | 60.6695 | 60.564 | 60.6685 | 60.6685 | 60.6685 | 60.6685 | 60.6685 | 60.6685 | 60.6685 | 60.6685 | 60.6685 | 60.6685 | 60.6685 | 60.6685 | 60.6685 | 60.6685 | 60.6685
90% | 9.0759 | 40.998 | 44.0624 | 44.3703 | 44.2194 | 44.3629 | 44.4219 | 44.6109 | 44.9995 | 45.3264 | 45.4769 | 45.3428 | 45.9052 | 45.9944 | 45.8888 | 46.1005 | 46.1995 | 46.1995 | 46.1995 | 46.1995 | 46.1995 | 46.1995 | 46.1995 | 46.1995 | 46.1995 | 46.1995 | 46.1995 | 46.1995 | 46.1995 | 46.1995 | 46.1995 | 90% | 0.75633 | 50.437 | 53.8617 | 53.9562 | 53.8543 | 53.8805 | 54.0675 | 54.4465 | 55.114 | 55.4618 | 55.7134 | 56.0942 | 56.5803 | 57.1682 | 57.4763 | 57.3764 | 57.4754 | 57.4754 | 57.4754 | 57.4754 | 57.4754 | 57.4754 | 57.4754 | 57.4754 | 57.4754 | 57.4754 | 57.4754 | 57.4754 | 57.4754 | 57.4754 | 57.4754
85% | 40.4636 | 38.7203 | 41.6145 | 41.9053 | 41.7628 | 41.8983 | 41.954 | 42.1325 | 42.4995 | 42.8083 | 42.9504 | 42.8238 | 43.3549 | 43.4391 | 43.3394 | 43.5393 | 43.6328 | 43.6328 | 43.6328 | 43.6328 | 43.6328 | 43.6328 | 43.6328 | 43.6328 | 43.6328 | 43.6328 | 43.6328 | 43.6328 | 43.6328 | 43.6328 | 43.6328 | 85% | 1.1345 | 47.6349 | 50.8694 | 50.9586 | 50.8624 | 50.8871 | 51.0637 | 51.4217 | 52.0521 | 52.3805 | 52.6182 | 52.9778 | 53.437 | 53.9922 | 54.2832 | 54.1889 | 54.2824 | 54.2824 | 54.2824 | 54.2824 | 54.2824 | 54.2824 | 54.2824 | 54.2824 | 54.2824 | 54.2824 | 54.2824 | 54.2824 | 54.2824 | 54.2824 | 54.2824
80% | 94.5411 | 36.4427 | 39.1666 | 39.4403 | 39.3061 | 39.4337 | 39.4861 | 39.6541 | 39.9996 | 40.2902 | 40.4239 | 40.3047 | 40.8046 | 40.8839 | 40.7901 | 40.9782 | 41.0662 | 41.0662 | 41.0662 | 41.0662 | 41.0662 | 41.0662 | 41.0662 | 41.0662 | 41.0662 | 41.0662 | 41.0662 | 41.0662 | 41.0662 | 41.0662 | 41.0662 | 80% | 2.6471 | 44.8329 | 47.877 | 47.961 | 47.8705 | 47.8938 | 48.06 | 48.3969 | 48.9902 | 49.2993 | 49.523 | 49.8615 | 50.2936 | 50.8162 | 51.0901 | 51.0013 | 51.0893 | 51.0893 | 51.0893 | 51.0893 | 51.0893 | 51.0893 | 51.0893 | 51.0893 | 51.0893 | 51.0893 | 51.0893 | 51.0893 | 51.0893 | 51.0893 | 51.0893
75% | 197.0236 | 34.165 | 36.7187 | 36.9753 | 36.8495 | 36.9691 | 37.0182 | 37.1757 | 37.4996 | 37.772 | 37.8974 | 37.7857 | 38.2543 | 38.3286 | 38.2407 | 38.4171 | 38.4996 | 38.4996 | 38.4996 | 38.4996 | 38.4996 | 38.4996 | 38.4996 | 38.4996 | 38.4996 | 38.4996 | 38.4996 | 38.4996 | 38.4996 | 38.4996 | 38.4996 | 75% | 3.4035 | 42.0308 | 44.8847 | 44.9635 | 44.8786 | 44.9004 | 45.0562 | 45.3721 | 45.9283 | 46.2181 | 46.4278 | 46.7451 | 47.1503 | 47.6402 | 47.8969 | 47.8137 | 47.8962 | 47.8962 | 47.8962 | 47.8962 | 47.8962 | 47.8962 | 47.8962 | 47.8962 | 47.8962 | 47.8962 | 47.8962 | 47.8962 | 47.8962 | 47.8962 | 47.8962
70% | 336.9444 | 31.8873 | 34.2708 | 34.5103 | 34.3929 | 34.5045 | 34.5504 | 34.6974 | 34.9996 | 35.2539 | 35.371 | 35.2666 | 35.704 | 35.7734 | 35.6913 | 35.8559 | 35.9329 | 35.9329 | 35.9329 | 35.9329 | 35.9329 | 35.9329 | 35.9329 | 35.9329 | 35.9329 | 35.9329 | 35.9329 | 35.9329 | 35.9329 | 35.9329 | 35.9329 | 70% | 5.6725 | 39.2288 | 41.8924 | 41.9659 | 41.8867 | 41.907 | 42.0525 | 42.3473 | 42.8664 | 43.1369 | 43.3326 | 43.6288 | 44.0069 | 44.4642 | 44.7038 | 44.6261 | 44.7031 | 44.7031 | 44.7031 | 44.7031 | 44.7031 | 44.7031 | 44.7031 | 44.7031 | 44.7031 | 44.7031 | 44.7031 | 44.7031 | 44.7031 | 44.7031 | 44.7031
65% | 521.4885 | 29.6097 | 31.8228 | 32.0452 | 31.9362 | 32.0399 | 32.0825 | 32.219 | 32.4996 | 32.7358 | 32.8445 | 32.7476 | 33.1537 | 33.2182 | 33.1419 | 33.2948 | 33.3663 | 33.3663 | 33.3663 | 33.3663 | 33.3663 | 33.3663 | 33.3663 | 33.3663 | 33.3663 | 33.3663 | 33.3663 | 33.3663 | 33.3663 | 33.3663 | 33.3663 | 65% | 6.4288 | 36.4267 | 38.9001 | 38.9683 | 38.8948 | 38.9137 | 39.0487 | 39.3225 | 39.8045 | 40.0557 | 40.2374 | 40.5125 | 40.8636 | 41.2882 | 41.5107 | 41.4385 | 41.51 | 41.51 | 41.51 | 41.51 | 41.51 | 41.51 | 41.51 | 41.51 | 41.51 | 41.51 | 41.51 | 41.51 | 41.51 | 41.51 | 41.51
60% | 812.675 | 27.332 | 29.3749 | 29.5802 | 29.4796 | 29.5753 | 29.6146 | 29.7406 | 29.9997 | 30.2176 | 30.318 | 30.2285 | 30.6035 | 30.6629 | 30.5925 | 30.7337 | 30.7997 | 30.7997 | 30.7997 | 30.7997 | 30.7997 | 30.7997 | 30.7997 | 30.7997 | 30.7997 | 30.7997 | 30.7997 | 30.7997 | 30.7997 | 30.7997 | 30.7997 | 60% | 11.3449 | 33.6247 | 35.9078 | 35.9708 | 35.9029 | 35.9203 | 36.045 | 36.2977 | 36.7426 | 36.9745 | 37.1422 | 37.3961 | 37.7202 | 38.1122 | 38.3176 | 38.251 | 38.317 | 38.317 | 38.317 | 38.317 | 38.317 | 38.317 | 38.317 | 38.317 | 38.317 | 38.317 | 38.317 | 38.317 | 38.317 | 38.317 | 38.317
55% | 1202.1843 | 25.0543 | 26.927 | 27.1152 | 27.023 | 27.1107 | 27.1467 | 27.2622 | 27.4997 | 27.6995 | 27.7915 | 27.7095 | 28.0532 | 28.1077 | 28.0432 | 28.1725 | 28.233 | 28.233 | 28.233 | 28.233 | 28.233 | 28.233 | 28.233 | 28.233 | 28.233 | 28.233 | 28.233 | 28.233 | 28.233 | 28.233 | 28.233 | 55% | 35.5474 | 30.8226 | 32.9155 | 32.9732 | 32.911 | 32.927 | 33.0412 | 33.2729 | 33.6808 | 33.8933 | 34.0471 | 34.2798 | 34.5769 | 34.9361 | 35.1244 | 35.0634 | 35.1239 | 35.1239 | 35.1239 | 35.1239 | 35.1239 | 35.1239 | 35.1239 | 35.1239 | 35.1239 | 35.1239 | 35.1239 | 35.1239 | 35.1239 | 35.1239 | 35.1239
50% | 1686.2345 | 22.7767 | 24.4791 | 24.6502 | 24.5663 | 24.6461 | 24.6788 | 24.7838 | 24.9997 | 25.1814 | 25.265 | 25.1904 | 25.5029 | 25.5524 | 25.4938 | 25.6114 | 25.6664 | 25.6664 | 25.6664 | 25.6664 | 25.6664 | 25.6664 | 25.6664 | 25.6664 | 25.6664 | 25.6664 | 25.6664 | 25.6664 | 25.6664 | 25.6664 | 25.6664 | 50% | 95.2974 | 28.0206 | 29.9231 | 29.9756 | 29.919 | 29.9336 | 30.0375 | 30.2481 | 30.6189 | 30.8121 | 30.9519 | 31.1634 | 31.4335 | 31.7601 | 31.9313 | 31.8758 | 31.9308 | 31.9308 | 31.9308 | 31.9308 | 31.9308 | 31.9308 | 31.9308 | 31.9308 | 31.9308 | 31.9308 | 31.9308 | 31.9308 | 31.9308 | 31.9308 | 31.9308
45% | 2129.0649 | 20.499 | 22.0312 | 22.1852 | 22.1097 | 22.1815 | 22.2109 | 22.3054 | 22.4998 | 22.6632 | 22.7385 | 22.6714 | 22.9526 | 22.9972 | 22.9444 | 23.0502 | 23.0997 | 23.0997 | 23.0997 | 23.0997 | 23.0997 | 23.0997 | 23.0997 | 23.0997 | 23.0997 | 23.0997 | 23.0997 | 23.0997 | 23.0997 | 23.0997 | 23.0997 | 45% | 208.7467 | 25.2185 | 26.9308 | 26.9781 | 26.9271 | 26.9402 | 27.0337 | 27.2232 | 27.557 | 27.7309 | 27.8567 | 28.0471 | 28.2902 | 28.5841 | 28.7382 | 28.6882 | 28.7377 | 28.7377 | 28.7377 | 28.7377 | 28.7377 | 28.7377 | 28.7377 | 28.7377 | 28.7377 | 28.7377 | 28.7377 | 28.7377 | 28.7377 | 28.7377 | 28.7377
40% | 2484.5393 | 18.2213 | 19.5833 | 19.7201 | 19.6531 | 19.7169 | 19.7431 | 19.8271 | 19.9998 | 20.1451 | 20.212 | 20.1524 | 20.4023 | 20.4419 | 20.395 | 20.4891 | 20.5331 | 20.5331 | 20.5331 | 20.5331 | 20.5331 | 20.5331 | 20.5331 | 20.5331 | 20.5331 | 20.5331 | 20.5331 | 20.5331 | 20.5331 | 20.5331 | 20.5331 | 40% | 380.4333 | 22.4164 | 23.9385 | 23.9805 | 23.9352 | 23.9469 | 24.03 | 24.1984 | 24.4951 | 24.6497 | 24.7615 | 24.9307 | 25.1468 | 25.4081 | 25.545 | 25.5006 | 25.5446 | 25.5446 | 25.5446 | 25.5446 | 25.5446 | 25.5446 | 25.5446 | 25.5446 | 25.5446 | 25.5446 | 25.5446 | 25.5446 | 25.5446 | 25.5446 | 25.5446
35% | 2808.248 | 15.9437 | 17.1354 | 17.2551 | 17.1964 | 17.2522 | 17.2752 | 17.3487 | 17.4998 | 17.6269 | 17.6855 | 17.6333 | 17.852 | 17.8867 | 17.8457 | 17.928 | 17.9665 | 17.9665 | 17.9665 | 17.9665 | 17.9665 | 17.9665 | 17.9665 | 17.9665 | 17.9665 | 17.9665 | 17.9665 | 17.9665 | 17.9665 | 17.9665 | 17.9665 | 35% | 696.5786 | 19.6144 | 20.9462 | 20.983 | 20.9433 | 20.9535 | 21.0262 | 21.1736 | 21.4332 | 21.5685 | 21.6663 | 21.8144 | 22.0035 | 22.2321 | 22.3519 | 22.3131 | 22.3516 | 22.3516 | 22.3516 | 22.3516 | 22.3516 | 22.3516 | 22.3516 | 22.3516 | 22.3516 | 22.3516 | 22.3516 | 22.3516 | 22.3516 | 22.3516 | 22.3516
30% | 3095.6528 | 13.666 | 14.6875 | 14.7901 | 14.7398 | 14.7876 | 14.8073 | 14.8703 | 14.9998 | 15.1088 | 15.159 | 15.1143 | 15.3017 | 15.3315 | 15.2963 | 15.3668 | 15.3998 | 15.3998 | 15.3998 | 15.3998 | 15.3998 | 15.3998 | 15.3998 | 15.3998 | 15.3998 | 15.3998 | 15.3998 | 15.3998 | 15.3998 | 15.3998 | 15.3998 | 30% | 1260.7997 | 16.8123 | 17.9539 | 17.9854 | 17.9514 | 17.9602 | 18.0225 | 18.1488 | 18.3713 | 18.4873 | 18.5711 | 18.6981 | 18.8601 | 19.0561 | 19.1588 | 19.1255 | 19.1585 | 19.1585 | 19.1585 | 19.1585 | 19.1585 | 19.1585 | 19.1585 | 19.1585 | 19.1585 | 19.1585 | 19.1585 | 19.1585 | 19.1585 | 19.1585 | 19.1585
25% | 3358.8552 | 11.3883 | 12.2396 | 12.3251 | 12.2832 | 12.323 | 12.3394 | 12.3919 | 12.4999 | 12.5907 | 12.6325 | 12.5952 | 12.7514 | 12.7762 | 12.7469 | 12.8057 | 12.8332 | 12.8332 | 12.8332 | 12.8332 | 12.8332 | 12.8332 | 12.8332 | 12.8332 | 12.8332 | 12.8332 | 12.8332 | 12.8332 | 12.8332 | 12.8332 | 12.8332 | 25% | 1965.3198 | 14.0103 | 14.9616 | 14.9878 | 14.9595 | 14.9668 | 15.0187 | 15.124 | 15.3094 | 15.406 | 15.4759 | 15.5817 | 15.7168 | 15.8801 | 15.9656 | 15.9379 | 15.9654 | 15.9654 | 15.9654 | 15.9654 | 15.9654 | 15.9654 | 15.9654 | 15.9654 | 15.9654 | 15.9654 | 15.9654 | 15.9654 | 15.9654 | 15.9654 | 15.9654
20% | 3588.7791 | 9.1107 | 9.7916 | 9.8601 | 9.8265 | 9.8584 | 9.8715 | 9.9135 | 9.9999 | 10.0725 | 10.106 | 10.0762 | 10.2012 | 10.221 | 10.1975 | 10.2446 | 10.2666 | 10.2666 | 10.2666 | 10.2666 | 10.2666 | 10.2666 | 10.2666 | 10.2666 | 10.2666 | 10.2666 | 10.2666 | 10.2666 | 10.2666 | 10.2666 | 10.2666 | 20% | 2490.2118 | 11.2082 | 11.9693 | 11.9903 | 11.9676 | 11.9734 | 12.015 | 12.0992 | 12.2475 | 12.3248 | 12.3807 | 12.4654 | 12.5734 | 12.7041 | 12.7725 | 12.7503 | 12.7723 | 12.7723 | 12.7723 | 12.7723 | 12.7723 | 12.7723 | 12.7723 | 12.7723 | 12.7723 | 12.7723 | 12.7723 | 12.7723 | 12.7723 | 12.7723 | 12.7723
15% | 3802.4419 | 6.833 | 7.3437 | 7.3951 | 7.3699 | 7.3938 | 7.4036 | 7.4351 | 7.4999 | 7.5544 | 7.5795 | 7.5571 | 7.6509 | 7.6657 | 7.6481 | 7.6834 | 7.6999 | 7.6999 | 7.6999 | 7.6999 | 7.6999 | 7.6999 | 7.6999 | 7.6999 | 7.6999 | 7.6999 | 7.6999 | 7.6999 | 7.6999 | 7.6999 | 7.6999 | 15% | 2997.7083 | 8.4062 | 8.9769 | 8.9927 | 8.9757 | 8.9801 | 9.0112 | 9.0744 | 9.1857 | 9.2436 | 9.2856 | 9.349 | 9.4301 | 9.528 | 9.5794 | 9.5627 | 9.5792 | 9.5792 | 9.5792 | 9.5792 | 9.5792 | 9.5792 | 9.5792 | 9.5792 | 9.5792 | 9.5792 | 9.5792 | 9.5792 | 9.5792 | 9.5792 | 9.5792
10% | 4024.8025 | 4.5553 | 4.8958 | 4.93 | 4.9133 | 4.9292 | 4.9358 | 4.9568 | 4.9999 | 5.0363 | 5.053 | 5.0381 | 5.1006 | 5.1105 | 5.0988 | 5.1223 | 5.1333 | 5.1333 | 5.1333 | 5.1333 | 5.1333 | 5.1333 | 5.1333 | 5.1333 | 5.1333 | 5.1333 | 5.1333 | 5.1333 | 5.1333 | 5.1333 | 5.1333 | 10% | 3491.5908 | 5.6041 | 5.9846 | 5.9951 | 5.9838 | 5.9867 | 6.0075 | 6.0496 | 6.1238 | 6.1624 | 6.1904 | 6.2327 | 6.2867 | 6.352 | 6.3863 | 6.3752 | 6.3862 | 6.3862 | 6.3862 | 6.3862 | 6.3862 | 6.3862 | 6.3862 | 6.3862 | 6.3862 | 6.3862 | 6.3862 | 6.3862 | 6.3862 | 6.3862 | 6.3862
5% | 4239.978 | 2.2777 | 2.4479 | 2.465 | 2.4566 | 2.4646 | 2.4679 | 2.4784 | 2.5 | 2.5181 | 2.5265 | 2.519 | 2.5503 | 2.5552 | 2.5494 | 2.5611 | 2.5666 | 2.5666 | 2.5666 | 2.5666 | 2.5666 | 2.5666 | 2.5666 | 2.5666 | 2.5666 | 2.5666 | 2.5666 | 2.5666 | 2.5666 | 2.5666 | 2.5666 | 5% | 3955.9766 | 2.8021 | 2.9923 | 2.9976 | 2.9919 | 2.9934 | 3.0037 | 3.0248 | 3.0619 | 3.0812 | 3.0952 | 3.1163 | 3.1434 | 3.176 | 3.1931 | 3.1876 | 3.1931 | 3.1931 | 3.1931 | 3.1931 | 3.1931 | 3.1931 | 3.1931 | 3.1931 | 3.1931 | 3.1931 | 3.1931 | 3.1931 | 3.1931 | 3.1931 | 3.1931
9.992e-14% | 4391.6218 | 4.5517e-14 | 4.8919e-14 | 4.9261e-14 | 4.9093e-14 | 4.9253e-14 | 4.9318e-14 | 4.9528e-14 | 4.9959e-14 | 5.0322e-14 | 5.049e-14 | 5.0341e-14 | 5.0965e-14 | 5.1064e-14 | 5.0947e-14 | 5.1182e-14 | 5.1292e-14 | 5.1292e-14 | 5.1292e-14 | 5.1292e-14 | 5.1292e-14 | 5.1292e-14 | 5.1292e-14 | 5.1292e-14 | 5.1292e-14 | 5.1292e-14 | 5.1292e-14 | 5.1292e-14 | 5.1292e-14 | 5.1292e-14 | 5.1292e-14 | 9.992e-14% | 4391.6218 | 5.5996e-14 | 5.9798e-14 | 5.9903e-14 | 5.979e-14 | 5.9819e-14 | 6.0027e-14 | 6.0448e-14 | 6.1189e-14 | 6.1575e-14 | 6.1854e-14 | 6.2277e-14 | 6.2817e-14 | 6.3469e-14 | 6.3812e-14 | 6.3701e-14 | 6.3811e-14 | 6.3811e-14 | 6.3811e-14 | 6.3811e-14 | 6.3811e-14 | 6.3811e-14 | 6.3811e-14 | 6.3811e-14 | 6.3811e-14 | 6.3811e-14 | 6.3811e-14 | 6.3811e-14 | 6.3811e-14 | 6.3811e-14 | 6.3811e-14
Option 2
Winter Season | [31 empty] | Winter Season
P50 | [31 empty] | P10
% of MD | Winter - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Winter - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 43.3628 | 47.9013 | 48.3825 | 48.9775 | 49.7674 | 50.5163 | 51.825 | 55.1166 | 56.887 | 55.5954 | 59.594 | 60.3144 | 60.8323 | 63.2734 | 63.6707 | 63.6707 | 63.6707 | 63.6707 | 63.6707 | 63.6707 | 63.6707 | 63.6707 | 63.6707 | 63.6707 | 63.6707 | 63.6707 | 63.6707 | 63.6707 | 63.6707 | 63.6707 | 100% | 0 | 47.5339 | 51.863 | 52.3113 | 53.8585 | 53.8208 | 54.161 | 55.4916 | 59.3146 | 60.8922 | 59.3989 | 63.524 | 61.792 | 63.3504 | 64.4734 | 64.012 | 64.012 | 64.012 | 64.012 | 64.012 | 64.012 | 64.012 | 64.012 | 64.012 | 64.012 | 64.012 | 64.012 | 64.012 | 64.012 | 64.012 | 64.012
99% | 0.2972 | 42.9291 | 47.4223 | 47.8987 | 48.4877 | 49.2697 | 50.0111 | 51.3068 | 54.5654 | 56.3182 | 55.0395 | 58.9981 | 59.7113 | 60.224 | 62.6406 | 63.034 | 63.034 | 63.034 | 63.034 | 63.034 | 63.034 | 63.034 | 63.034 | 63.034 | 63.034 | 63.034 | 63.034 | 63.034 | 63.034 | 63.034 | 63.034 | 99% | 0.2972 | 47.0586 | 51.3443 | 51.7882 | 53.3199 | 53.2826 | 53.6194 | 54.9367 | 58.7214 | 60.2833 | 58.8049 | 62.8887 | 61.1741 | 62.7169 | 63.8287 | 63.3719 | 63.3719 | 63.3719 | 63.3719 | 63.3719 | 63.3719 | 63.3719 | 63.3719 | 63.3719 | 63.3719 | 63.3719 | 63.3719 | 63.3719 | 63.3719 | 63.3719 | 63.3719
98% | 0.2972 | 42.4955 | 46.9432 | 47.4149 | 47.9979 | 48.7721 | 49.506 | 50.7885 | 54.0143 | 55.7493 | 54.4835 | 58.4021 | 59.1081 | 59.6156 | 62.0079 | 62.3973 | 62.3973 | 62.3973 | 62.3973 | 62.3973 | 62.3973 | 62.3973 | 62.3973 | 62.3973 | 62.3973 | 62.3973 | 62.3973 | 62.3973 | 62.3973 | 62.3973 | 62.3973 | 98% | 0.2972 | 46.5832 | 50.8257 | 51.2651 | 52.7813 | 52.7443 | 53.0778 | 54.3818 | 58.1283 | 59.6743 | 58.2109 | 62.2535 | 60.5562 | 62.0834 | 63.184 | 62.7318 | 62.7318 | 62.7318 | 62.7318 | 62.7318 | 62.7318 | 62.7318 | 62.7318 | 62.7318 | 62.7318 | 62.7318 | 62.7318 | 62.7318 | 62.7318 | 62.7318 | 62.7318
97% | 0.2972 | 42.0619 | 46.4642 | 46.931 | 47.5082 | 48.2744 | 49.0008 | 50.2703 | 53.4631 | 55.1804 | 53.9276 | 57.8062 | 58.505 | 59.0073 | 61.3752 | 61.7606 | 61.7606 | 61.7606 | 61.7606 | 61.7606 | 61.7606 | 61.7606 | 61.7606 | 61.7606 | 61.7606 | 61.7606 | 61.7606 | 61.7606 | 61.7606 | 61.7606 | 61.7606 | 97% | 0.2972 | 46.1079 | 50.3071 | 50.7419 | 52.2427 | 52.2061 | 52.5362 | 53.8269 | 57.5352 | 59.0654 | 57.6169 | 61.6183 | 59.9383 | 61.4499 | 62.5392 | 62.0917 | 62.0917 | 62.0917 | 62.0917 | 62.0917 | 62.0917 | 62.0917 | 62.0917 | 62.0917 | 62.0917 | 62.0917 | 62.0917 | 62.0917 | 62.0917 | 62.0917 | 62.0917
95% | 1.486 | 41.1946 | 45.5062 | 45.9634 | 46.5286 | 47.2791 | 47.9905 | 49.2338 | 52.3608 | 54.0427 | 52.8157 | 56.6143 | 57.2987 | 57.7907 | 60.1097 | 60.4871 | 60.4871 | 60.4871 | 60.4871 | 60.4871 | 60.4871 | 60.4871 | 60.4871 | 60.4871 | 60.4871 | 60.4871 | 60.4871 | 60.4871 | 60.4871 | 60.4871 | 60.4871 | 95% | 1.486 | 45.1572 | 49.2698 | 49.6957 | 51.1655 | 51.1297 | 51.4529 | 52.717 | 56.3489 | 57.8476 | 56.4289 | 60.3478 | 58.7024 | 60.1829 | 61.2498 | 60.8114 | 60.8114 | 60.8114 | 60.8114 | 60.8114 | 60.8114 | 60.8114 | 60.8114 | 60.8114 | 60.8114 | 60.8114 | 60.8114 | 60.8114 | 60.8114 | 60.8114 | 60.8114
90% | 8.6188 | 39.0265 | 43.1111 | 43.5443 | 44.0797 | 44.7907 | 45.4647 | 46.6425 | 49.6049 | 51.1983 | 50.0359 | 53.6346 | 54.283 | 54.7491 | 56.946 | 57.3036 | 57.3036 | 57.3036 | 57.3036 | 57.3036 | 57.3036 | 57.3036 | 57.3036 | 57.3036 | 57.3036 | 57.3036 | 57.3036 | 57.3036 | 57.3036 | 57.3036 | 57.3036 | 90% | 8.6188 | 42.7805 | 46.6767 | 47.0802 | 48.4726 | 48.4387 | 48.7449 | 49.9425 | 53.3831 | 54.803 | 53.459 | 57.1716 | 55.6128 | 57.0154 | 58.0261 | 57.6108 | 57.6108 | 57.6108 | 57.6108 | 57.6108 | 57.6108 | 57.6108 | 57.6108 | 57.6108 | 57.6108 | 57.6108 | 57.6108 | 57.6108 | 57.6108 | 57.6108 | 57.6108
85% | 40.1218 | 36.8584 | 40.7161 | 41.1251 | 41.6309 | 42.3023 | 42.9389 | 44.0513 | 46.8491 | 48.354 | 47.2561 | 50.6549 | 51.2673 | 51.7074 | 53.7823 | 54.1201 | 54.1201 | 54.1201 | 54.1201 | 54.1201 | 54.1201 | 54.1201 | 54.1201 | 54.1201 | 54.1201 | 54.1201 | 54.1201 | 54.1201 | 54.1201 | 54.1201 | 54.1201 | 85% | 40.1218 | 40.4038 | 44.0835 | 44.4646 | 45.7797 | 45.7477 | 46.0368 | 47.1679 | 50.4174 | 51.7583 | 50.489 | 53.9954 | 52.5232 | 53.8479 | 54.8024 | 54.4102 | 54.4102 | 54.4102 | 54.4102 | 54.4102 | 54.4102 | 54.4102 | 54.4102 | 54.4102 | 54.4102 | 54.4102 | 54.4102 | 54.4102 | 54.4102 | 54.4102 | 54.4102
80% | 93.0231 | 34.6902 | 38.321 | 38.706 | 39.182 | 39.8139 | 40.413 | 41.46 | 44.0933 | 45.5096 | 44.4764 | 47.6752 | 48.2515 | 48.6658 | 50.6187 | 50.9365 | 50.9365 | 50.9365 | 50.9365 | 50.9365 | 50.9365 | 50.9365 | 50.9365 | 50.9365 | 50.9365 | 50.9365 | 50.9365 | 50.9365 | 50.9365 | 50.9365 | 50.9365 | 80% | 93.0231 | 38.0271 | 41.4904 | 41.849 | 43.0868 | 43.0566 | 43.3288 | 44.3933 | 47.4517 | 48.7137 | 47.5191 | 50.8192 | 49.4336 | 50.6803 | 51.5787 | 51.2096 | 51.2096 | 51.2096 | 51.2096 | 51.2096 | 51.2096 | 51.2096 | 51.2096 | 51.2096 | 51.2096 | 51.2096 | 51.2096 | 51.2096 | 51.2096 | 51.2096 | 51.2096
75% | 197.0426 | 32.5221 | 35.926 | 36.2869 | 36.7331 | 37.3256 | 37.8872 | 38.8688 | 41.3374 | 42.6653 | 41.6966 | 44.6955 | 45.2358 | 45.6242 | 47.455 | 47.753 | 47.753 | 47.753 | 47.753 | 47.753 | 47.753 | 47.753 | 47.753 | 47.753 | 47.753 | 47.753 | 47.753 | 47.753 | 47.753 | 47.753 | 47.753 | 75% | 197.0426 | 35.6504 | 38.8972 | 39.2335 | 40.3939 | 40.3656 | 40.6207 | 41.6187 | 44.4859 | 45.6691 | 44.5491 | 47.643 | 46.344 | 47.5128 | 48.3551 | 48.009 | 48.009 | 48.009 | 48.009 | 48.009 | 48.009 | 48.009 | 48.009 | 48.009 | 48.009 | 48.009 | 48.009 | 48.009 | 48.009 | 48.009 | 48.009
70% | 378.0365 | 30.3539 | 33.5309 | 33.8678 | 34.2842 | 34.8372 | 35.3614 | 36.2775 | 38.5816 | 39.8209 | 38.9168 | 41.7158 | 42.2201 | 42.5826 | 44.2913 | 44.5695 | 44.5695 | 44.5695 | 44.5695 | 44.5695 | 44.5695 | 44.5695 | 44.5695 | 44.5695 | 44.5695 | 44.5695 | 44.5695 | 44.5695 | 44.5695 | 44.5695 | 44.5695 | 70% | 378.0365 | 33.2737 | 36.3041 | 36.6179 | 37.7009 | 37.6745 | 37.9127 | 38.8441 | 41.5202 | 42.6245 | 41.5792 | 44.4668 | 43.2544 | 44.3453 | 45.1314 | 44.8084 | 44.8084 | 44.8084 | 44.8084 | 44.8084 | 44.8084 | 44.8084 | 44.8084 | 44.8084 | 44.8084 | 44.8084 | 44.8084 | 44.8084 | 44.8084 | 44.8084 | 44.8084
65% | 616.0926 | 28.1858 | 31.1358 | 31.4486 | 31.8354 | 32.3488 | 32.8356 | 33.6863 | 35.8258 | 36.9766 | 36.137 | 38.7361 | 39.2044 | 39.541 | 41.1277 | 41.3859 | 41.3859 | 41.3859 | 41.3859 | 41.3859 | 41.3859 | 41.3859 | 41.3859 | 41.3859 | 41.3859 | 41.3859 | 41.3859 | 41.3859 | 41.3859 | 41.3859 | 41.3859 | 65% | 616.0926 | 30.897 | 33.7109 | 34.0023 | 35.008 | 34.9835 | 35.2046 | 36.0696 | 38.5545 | 39.5799 | 38.6093 | 41.2906 | 40.1648 | 41.1778 | 41.9077 | 41.6078 | 41.6078 | 41.6078 | 41.6078 | 41.6078 | 41.6078 | 41.6078 | 41.6078 | 41.6078 | 41.6078 | 41.6078 | 41.6078 | 41.6078 | 41.6078 | 41.6078 | 41.6078
60% | 934.9866 | 26.0177 | 28.7408 | 29.0295 | 29.3865 | 29.8605 | 30.3098 | 31.095 | 33.07 | 34.1322 | 33.3573 | 35.7564 | 36.1887 | 36.4994 | 37.964 | 38.2024 | 38.2024 | 38.2024 | 38.2024 | 38.2024 | 38.2024 | 38.2024 | 38.2024 | 38.2024 | 38.2024 | 38.2024 | 38.2024 | 38.2024 | 38.2024 | 38.2024 | 38.2024 | 60% | 934.9866 | 28.5203 | 31.1178 | 31.3868 | 32.3151 | 32.2925 | 32.4966 | 33.295 | 35.5888 | 36.5353 | 35.6393 | 38.1144 | 37.0752 | 38.0103 | 38.6841 | 38.4072 | 38.4072 | 38.4072 | 38.4072 | 38.4072 | 38.4072 | 38.4072 | 38.4072 | 38.4072 | 38.4072 | 38.4072 | 38.4072 | 38.4072 | 38.4072 | 38.4072 | 38.4072
55% | 1310.9428 | 23.8495 | 26.3457 | 26.6104 | 26.9376 | 27.3721 | 27.784 | 28.5038 | 30.3141 | 31.2879 | 30.5775 | 32.7767 | 33.1729 | 33.4578 | 34.8003 | 35.0189 | 35.0189 | 35.0189 | 35.0189 | 35.0189 | 35.0189 | 35.0189 | 35.0189 | 35.0189 | 35.0189 | 35.0189 | 35.0189 | 35.0189 | 35.0189 | 35.0189 | 35.0189 | 55% | 1310.9428 | 26.1436 | 28.5246 | 28.7712 | 29.6222 | 29.6014 | 29.7885 | 30.5204 | 32.623 | 33.4907 | 32.6694 | 34.9382 | 33.9856 | 34.8427 | 35.4604 | 35.2066 | 35.2066 | 35.2066 | 35.2066 | 35.2066 | 35.2066 | 35.2066 | 35.2066 | 35.2066 | 35.2066 | 35.2066 | 35.2066 | 35.2066 | 35.2066 | 35.2066 | 35.2066
50% | 1730.2899 | 21.6814 | 23.9506 | 24.1913 | 24.4887 | 24.8837 | 25.2582 | 25.9125 | 27.5583 | 28.4435 | 27.7977 | 29.797 | 30.1572 | 30.4161 | 31.6367 | 31.8353 | 31.8353 | 31.8353 | 31.8353 | 31.8353 | 31.8353 | 31.8353 | 31.8353 | 31.8353 | 31.8353 | 31.8353 | 31.8353 | 31.8353 | 31.8353 | 31.8353 | 31.8353 | 50% | 1730.2899 | 23.7669 | 25.9315 | 26.1556 | 26.9292 | 26.9104 | 27.0805 | 27.7458 | 29.6573 | 30.4461 | 29.6994 | 31.762 | 30.896 | 31.6752 | 32.2367 | 32.006 | 32.006 | 32.006 | 32.006 | 32.006 | 32.006 | 32.006 | 32.006 | 32.006 | 32.006 | 32.006 | 32.006 | 32.006 | 32.006 | 32.006 | 32.006
45% | 2168.0633 | 19.5132 | 21.5556 | 21.7721 | 22.0399 | 22.3953 | 22.7323 | 23.3213 | 24.8025 | 25.5992 | 25.0179 | 26.8173 | 27.1415 | 27.3745 | 28.473 | 28.6518 | 28.6518 | 28.6518 | 28.6518 | 28.6518 | 28.6518 | 28.6518 | 28.6518 | 28.6518 | 28.6518 | 28.6518 | 28.6518 | 28.6518 | 28.6518 | 28.6518 | 28.6518 | 45% | 2168.0633 | 21.3903 | 23.3383 | 23.5401 | 24.2363 | 24.2193 | 24.3724 | 24.9712 | 26.6916 | 27.4015 | 26.7295 | 28.5858 | 27.8064 | 28.5077 | 29.013 | 28.8054 | 28.8054 | 28.8054 | 28.8054 | 28.8054 | 28.8054 | 28.8054 | 28.8054 | 28.8054 | 28.8054 | 28.8054 | 28.8054 | 28.8054 | 28.8054 | 28.8054 | 28.8054
40% | 2609.7004 | 17.3451 | 19.1605 | 19.353 | 19.591 | 19.907 | 20.2065 | 20.73 | 22.0466 | 22.7548 | 22.2382 | 23.8376 | 24.1258 | 24.3329 | 25.3093 | 25.4683 | 25.4683 | 25.4683 | 25.4683 | 25.4683 | 25.4683 | 25.4683 | 25.4683 | 25.4683 | 25.4683 | 25.4683 | 25.4683 | 25.4683 | 25.4683 | 25.4683 | 25.4683 | 40% | 2609.7004 | 19.0136 | 20.7452 | 20.9245 | 21.5434 | 21.5283 | 21.6644 | 22.1966 | 23.7258 | 24.3569 | 23.7595 | 25.4096 | 24.7168 | 25.3402 | 25.7894 | 25.6048 | 25.6048 | 25.6048 | 25.6048 | 25.6048 | 25.6048 | 25.6048 | 25.6048 | 25.6048 | 25.6048 | 25.6048 | 25.6048 | 25.6048 | 25.6048 | 25.6048 | 25.6048
35% | 2998.1389 | 15.177 | 16.7654 | 16.9339 | 17.1421 | 17.4186 | 17.6807 | 18.1388 | 19.2908 | 19.9105 | 19.4584 | 20.8579 | 21.1101 | 21.2913 | 22.1457 | 22.2847 | 22.2847 | 22.2847 | 22.2847 | 22.2847 | 22.2847 | 22.2847 | 22.2847 | 22.2847 | 22.2847 | 22.2847 | 22.2847 | 22.2847 | 22.2847 | 22.2847 | 22.2847 | 35% | 2998.1389 | 16.6369 | 18.152 | 18.3089 | 18.8505 | 18.8373 | 18.9563 | 19.4221 | 20.7601 | 21.3123 | 20.7896 | 22.2334 | 21.6272 | 22.1726 | 22.5657 | 22.4042 | 22.4042 | 22.4042 | 22.4042 | 22.4042 | 22.4042 | 22.4042 | 22.4042 | 22.4042 | 22.4042 | 22.4042 | 22.4042 | 22.4042 | 22.4042 | 22.4042 | 22.4042
30% | 3309.3057 | 13.0088 | 14.3704 | 14.5148 | 14.6932 | 14.9302 | 15.1549 | 15.5475 | 16.535 | 17.0661 | 16.6786 | 17.8782 | 18.0943 | 18.2497 | 18.982 | 19.1012 | 19.1012 | 19.1012 | 19.1012 | 19.1012 | 19.1012 | 19.1012 | 19.1012 | 19.1012 | 19.1012 | 19.1012 | 19.1012 | 19.1012 | 19.1012 | 19.1012 | 19.1012 | 30% | 3309.3057 | 14.2602 | 15.5589 | 15.6934 | 16.1575 | 16.1462 | 16.2483 | 16.6475 | 17.7944 | 18.2677 | 17.8197 | 19.0572 | 18.5376 | 19.0051 | 19.342 | 19.2036 | 19.2036 | 19.2036 | 19.2036 | 19.2036 | 19.2036 | 19.2036 | 19.2036 | 19.2036 | 19.2036 | 19.2036 | 19.2036 | 19.2036 | 19.2036 | 19.2036 | 19.2036
25% | 3537.8514 | 10.8407 | 11.9753 | 12.0956 | 12.2444 | 12.4419 | 12.6291 | 12.9563 | 13.7791 | 14.2218 | 13.8989 | 14.8985 | 15.0786 | 15.2081 | 15.8183 | 15.9177 | 15.9177 | 15.9177 | 15.9177 | 15.9177 | 15.9177 | 15.9177 | 15.9177 | 15.9177 | 15.9177 | 15.9177 | 15.9177 | 15.9177 | 15.9177 | 15.9177 | 15.9177 | 25% | 3537.8514 | 11.8835 | 12.9657 | 13.0778 | 13.4646 | 13.4552 | 13.5402 | 13.8729 | 14.8286 | 15.223 | 14.8497 | 15.881 | 15.448 | 15.8376 | 16.1184 | 16.003 | 16.003 | 16.003 | 16.003 | 16.003 | 16.003 | 16.003 | 16.003 | 16.003 | 16.003 | 16.003 | 16.003 | 16.003 | 16.003 | 16.003 | 16.003
20% | 3731.0305 | 8.6726 | 9.5803 | 9.6765 | 9.7955 | 9.9535 | 10.1033 | 10.365 | 11.0233 | 11.3774 | 11.1191 | 11.9188 | 12.0629 | 12.1665 | 12.6547 | 12.7341 | 12.7341 | 12.7341 | 12.7341 | 12.7341 | 12.7341 | 12.7341 | 12.7341 | 12.7341 | 12.7341 | 12.7341 | 12.7341 | 12.7341 | 12.7341 | 12.7341 | 12.7341 | 20% | 3731.0305 | 9.5068 | 10.3726 | 10.4623 | 10.7717 | 10.7642 | 10.8322 | 11.0983 | 11.8629 | 12.1784 | 11.8798 | 12.7048 | 12.3584 | 12.6701 | 12.8947 | 12.8024 | 12.8024 | 12.8024 | 12.8024 | 12.8024 | 12.8024 | 12.8024 | 12.8024 | 12.8024 | 12.8024 | 12.8024 | 12.8024 | 12.8024 | 12.8024 | 12.8024 | 12.8024
15% | 3910.2412 | 6.5044 | 7.1852 | 7.2574 | 7.3466 | 7.4651 | 7.5774 | 7.7738 | 8.2675 | 8.5331 | 8.3393 | 8.9391 | 9.0472 | 9.1248 | 9.491 | 9.5506 | 9.5506 | 9.5506 | 9.5506 | 9.5506 | 9.5506 | 9.5506 | 9.5506 | 9.5506 | 9.5506 | 9.5506 | 9.5506 | 9.5506 | 9.5506 | 9.5506 | 9.5506 | 15% | 3910.2412 | 7.1301 | 7.7794 | 7.8467 | 8.0788 | 8.0731 | 8.1241 | 8.3237 | 8.8972 | 9.1338 | 8.9098 | 9.5286 | 9.2688 | 9.5026 | 9.671 | 9.6018 | 9.6018 | 9.6018 | 9.6018 | 9.6018 | 9.6018 | 9.6018 | 9.6018 | 9.6018 | 9.6018 | 9.6018 | 9.6018 | 9.6018 | 9.6018 | 9.6018 | 9.6018
10% | 4075.1864 | 4.3363 | 4.7901 | 4.8383 | 4.8977 | 4.9767 | 5.0516 | 5.1825 | 5.5117 | 5.6887 | 5.5595 | 5.9594 | 6.0314 | 6.0832 | 6.3273 | 6.3671 | 6.3671 | 6.3671 | 6.3671 | 6.3671 | 6.3671 | 6.3671 | 6.3671 | 6.3671 | 6.3671 | 6.3671 | 6.3671 | 6.3671 | 6.3671 | 6.3671 | 6.3671 | 10% | 4075.1864 | 4.7534 | 5.1863 | 5.2311 | 5.3858 | 5.3821 | 5.4161 | 5.5492 | 5.9315 | 6.0892 | 5.9399 | 6.3524 | 6.1792 | 6.335 | 6.4473 | 6.4012 | 6.4012 | 6.4012 | 6.4012 | 6.4012 | 6.4012 | 6.4012 | 6.4012 | 6.4012 | 6.4012 | 6.4012 | 6.4012 | 6.4012 | 6.4012 | 6.4012 | 6.4012
5% | 4251.7223 | 2.1681 | 2.3951 | 2.4191 | 2.4489 | 2.4884 | 2.5258 | 2.5913 | 2.7558 | 2.8444 | 2.7798 | 2.9797 | 3.0157 | 3.0416 | 3.1637 | 3.1835 | 3.1835 | 3.1835 | 3.1835 | 3.1835 | 3.1835 | 3.1835 | 3.1835 | 3.1835 | 3.1835 | 3.1835 | 3.1835 | 3.1835 | 3.1835 | 3.1835 | 3.1835 | 5% | 4251.7223 | 2.3767 | 2.5931 | 2.6156 | 2.6929 | 2.691 | 2.708 | 2.7746 | 2.9657 | 3.0446 | 2.9699 | 3.1762 | 3.0896 | 3.1675 | 3.2237 | 3.2006 | 3.2006 | 3.2006 | 3.2006 | 3.2006 | 3.2006 | 3.2006 | 3.2006 | 3.2006 | 3.2006 | 3.2006 | 3.2006 | 3.2006 | 3.2006 | 3.2006 | 3.2006
9.992e-14% | 4391.7028 | 4.3328e-14 | 4.7863e-14 | 4.8344e-14 | 4.8938e-14 | 4.9728e-14 | 5.0476e-14 | 5.1784e-14 | 5.5073e-14 | 5.6842e-14 | 5.5551e-14 | 5.9546e-14 | 6.0266e-14 | 6.0784e-14 | 6.3223e-14 | 6.362e-14 | 6.362e-14 | 6.362e-14 | 6.362e-14 | 6.362e-14 | 6.362e-14 | 6.362e-14 | 6.362e-14 | 6.362e-14 | 6.362e-14 | 6.362e-14 | 6.362e-14 | 6.362e-14 | 6.362e-14 | 6.362e-14 | 6.362e-14 | 9.992e-14% | 4391.7028 | 4.7496e-14 | 5.1822e-14 | 5.2269e-14 | 5.3815e-14 | 5.3778e-14 | 5.4118e-14 | 5.5447e-14 | 5.9267e-14 | 6.0844e-14 | 5.9351e-14 | 6.3473e-14 | 6.1743e-14 | 6.33e-14 | 6.4422e-14 | 6.3961e-14 | 6.3961e-14 | 6.3961e-14 | 6.3961e-14 | 6.3961e-14 | 6.3961e-14 | 6.3961e-14 | 6.3961e-14 | 6.3961e-14 | 6.3961e-14 | 6.3961e-14 | 6.3961e-14 | 6.3961e-14 | 6.3961e-14 | 6.3961e-14 | 6.3961e-14
Summer Season | [31 empty] | Summer Season
P50 | [31 empty] | P10
% of MD | Summer - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Summer - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 45.5533 | 48.9582 | 49.3004 | 49.1327 | 49.2921 | 49.3577 | 49.5677 | 49.9995 | 50.3627 | 50.5299 | 50.3809 | 51.0058 | 51.1049 | 50.9876 | 51.2228 | 51.3328 | 51.3328 | 51.3328 | 51.3328 | 51.3328 | 51.3328 | 51.3328 | 51.3328 | 51.3328 | 51.3328 | 51.3328 | 51.3328 | 51.3328 | 51.3328 | 51.3328 | 100% | 0 | 56.0411 | 59.8463 | 59.9513 | 59.8381 | 59.8672 | 60.075 | 60.4961 | 61.2377 | 61.6242 | 61.9037 | 62.3269 | 62.867 | 63.5203 | 63.8626 | 63.7516 | 63.8616 | 63.8616 | 63.8616 | 63.8616 | 63.8616 | 63.8616 | 63.8616 | 63.8616 | 63.8616 | 63.8616 | 63.8616 | 63.8616 | 63.8616 | 63.8616 | 63.8616
99% | 0.37816 | 45.0978 | 48.4686 | 48.8074 | 48.6413 | 48.7992 | 48.8641 | 49.072 | 49.4995 | 49.8591 | 50.0246 | 49.8771 | 50.4957 | 50.5938 | 50.4777 | 50.7105 | 50.8194 | 50.8194 | 50.8194 | 50.8194 | 50.8194 | 50.8194 | 50.8194 | 50.8194 | 50.8194 | 50.8194 | 50.8194 | 50.8194 | 50.8194 | 50.8194 | 50.8194 | 99% | 0 | 55.4807 | 59.2478 | 59.3518 | 59.2397 | 59.2685 | 59.4742 | 59.8911 | 60.6254 | 61.0079 | 61.2847 | 61.7036 | 62.2384 | 62.8851 | 63.224 | 63.1141 | 63.223 | 63.223 | 63.223 | 63.223 | 63.223 | 63.223 | 63.223 | 63.223 | 63.223 | 63.223 | 63.223 | 63.223 | 63.223 | 63.223 | 63.223
98% | 0.37816 | 44.6423 | 47.9791 | 48.3144 | 48.15 | 48.3063 | 48.3705 | 48.5763 | 48.9995 | 49.3555 | 49.5193 | 49.3733 | 49.9856 | 50.0828 | 49.9678 | 50.1983 | 50.3061 | 50.3061 | 50.3061 | 50.3061 | 50.3061 | 50.3061 | 50.3061 | 50.3061 | 50.3061 | 50.3061 | 50.3061 | 50.3061 | 50.3061 | 50.3061 | 50.3061 | 98% | 0 | 54.9203 | 58.6494 | 58.7523 | 58.6413 | 58.6699 | 58.8735 | 59.2862 | 60.013 | 60.3917 | 60.6657 | 61.0803 | 61.6097 | 62.2499 | 62.5853 | 62.4766 | 62.5844 | 62.5844 | 62.5844 | 62.5844 | 62.5844 | 62.5844 | 62.5844 | 62.5844 | 62.5844 | 62.5844 | 62.5844 | 62.5844 | 62.5844 | 62.5844 | 62.5844
97% | 0.37816 | 44.1867 | 47.4895 | 47.8214 | 47.6587 | 47.8134 | 47.8769 | 48.0806 | 48.4995 | 48.8518 | 49.014 | 48.8695 | 49.4756 | 49.5717 | 49.458 | 49.6861 | 49.7928 | 49.7928 | 49.7928 | 49.7928 | 49.7928 | 49.7928 | 49.7928 | 49.7928 | 49.7928 | 49.7928 | 49.7928 | 49.7928 | 49.7928 | 49.7928 | 49.7928 | 97% | 0.37816 | 54.3599 | 58.0509 | 58.1528 | 58.0429 | 58.0712 | 58.2727 | 58.6812 | 59.4006 | 59.7754 | 60.0466 | 60.457 | 60.981 | 61.6146 | 61.9467 | 61.8391 | 61.9458 | 61.9458 | 61.9458 | 61.9458 | 61.9458 | 61.9458 | 61.9458 | 61.9458 | 61.9458 | 61.9458 | 61.9458 | 61.9458 | 61.9458 | 61.9458 | 61.9458
95% | 0.75633 | 43.2757 | 46.5103 | 46.8354 | 46.676 | 46.8275 | 46.8898 | 47.0893 | 47.4995 | 47.8446 | 48.0034 | 47.8618 | 48.4555 | 48.5496 | 48.4382 | 48.6616 | 48.7661 | 48.7661 | 48.7661 | 48.7661 | 48.7661 | 48.7661 | 48.7661 | 48.7661 | 48.7661 | 48.7661 | 48.7661 | 48.7661 | 48.7661 | 48.7661 | 48.7661 | 95% | 0.37816 | 53.2391 | 56.854 | 56.9537 | 56.8462 | 56.8738 | 57.0712 | 57.4713 | 58.1758 | 58.543 | 58.8086 | 59.2105 | 59.7237 | 60.3442 | 60.6695 | 60.564 | 60.6685 | 60.6685 | 60.6685 | 60.6685 | 60.6685 | 60.6685 | 60.6685 | 60.6685 | 60.6685 | 60.6685 | 60.6685 | 60.6685 | 60.6685 | 60.6685 | 60.6685
90% | 9.0759 | 40.998 | 44.0624 | 44.3703 | 44.2194 | 44.3629 | 44.4219 | 44.6109 | 44.9995 | 45.3264 | 45.4769 | 45.3428 | 45.9052 | 45.9944 | 45.8888 | 46.1005 | 46.1995 | 46.1995 | 46.1995 | 46.1995 | 46.1995 | 46.1995 | 46.1995 | 46.1995 | 46.1995 | 46.1995 | 46.1995 | 46.1995 | 46.1995 | 46.1995 | 46.1995 | 90% | 0.75633 | 50.437 | 53.8617 | 53.9562 | 53.8543 | 53.8805 | 54.0675 | 54.4465 | 55.114 | 55.4618 | 55.7134 | 56.0942 | 56.5803 | 57.1682 | 57.4763 | 57.3764 | 57.4754 | 57.4754 | 57.4754 | 57.4754 | 57.4754 | 57.4754 | 57.4754 | 57.4754 | 57.4754 | 57.4754 | 57.4754 | 57.4754 | 57.4754 | 57.4754 | 57.4754
85% | 40.4636 | 38.7203 | 41.6145 | 41.9053 | 41.7628 | 41.8983 | 41.954 | 42.1325 | 42.4995 | 42.8083 | 42.9504 | 42.8238 | 43.3549 | 43.4391 | 43.3394 | 43.5393 | 43.6328 | 43.6328 | 43.6328 | 43.6328 | 43.6328 | 43.6328 | 43.6328 | 43.6328 | 43.6328 | 43.6328 | 43.6328 | 43.6328 | 43.6328 | 43.6328 | 43.6328 | 85% | 1.1345 | 47.6349 | 50.8694 | 50.9586 | 50.8624 | 50.8871 | 51.0637 | 51.4217 | 52.0521 | 52.3805 | 52.6182 | 52.9778 | 53.437 | 53.9922 | 54.2832 | 54.1889 | 54.2824 | 54.2824 | 54.2824 | 54.2824 | 54.2824 | 54.2824 | 54.2824 | 54.2824 | 54.2824 | 54.2824 | 54.2824 | 54.2824 | 54.2824 | 54.2824 | 54.2824
80% | 94.5411 | 36.4427 | 39.1666 | 39.4403 | 39.3061 | 39.4337 | 39.4861 | 39.6541 | 39.9996 | 40.2902 | 40.4239 | 40.3047 | 40.8046 | 40.8839 | 40.7901 | 40.9782 | 41.0662 | 41.0662 | 41.0662 | 41.0662 | 41.0662 | 41.0662 | 41.0662 | 41.0662 | 41.0662 | 41.0662 | 41.0662 | 41.0662 | 41.0662 | 41.0662 | 41.0662 | 80% | 2.6471 | 44.8329 | 47.877 | 47.961 | 47.8705 | 47.8938 | 48.06 | 48.3969 | 48.9902 | 49.2993 | 49.523 | 49.8615 | 50.2936 | 50.8162 | 51.0901 | 51.0013 | 51.0893 | 51.0893 | 51.0893 | 51.0893 | 51.0893 | 51.0893 | 51.0893 | 51.0893 | 51.0893 | 51.0893 | 51.0893 | 51.0893 | 51.0893 | 51.0893 | 51.0893
75% | 197.0236 | 34.165 | 36.7187 | 36.9753 | 36.8495 | 36.9691 | 37.0182 | 37.1757 | 37.4996 | 37.772 | 37.8974 | 37.7857 | 38.2543 | 38.3286 | 38.2407 | 38.4171 | 38.4996 | 38.4996 | 38.4996 | 38.4996 | 38.4996 | 38.4996 | 38.4996 | 38.4996 | 38.4996 | 38.4996 | 38.4996 | 38.4996 | 38.4996 | 38.4996 | 38.4996 | 75% | 3.4035 | 42.0308 | 44.8847 | 44.9635 | 44.8786 | 44.9004 | 45.0562 | 45.3721 | 45.9283 | 46.2181 | 46.4278 | 46.7451 | 47.1503 | 47.6402 | 47.8969 | 47.8137 | 47.8962 | 47.8962 | 47.8962 | 47.8962 | 47.8962 | 47.8962 | 47.8962 | 47.8962 | 47.8962 | 47.8962 | 47.8962 | 47.8962 | 47.8962 | 47.8962 | 47.8962
70% | 336.9444 | 31.8873 | 34.2708 | 34.5103 | 34.3929 | 34.5045 | 34.5504 | 34.6974 | 34.9996 | 35.2539 | 35.371 | 35.2666 | 35.704 | 35.7734 | 35.6913 | 35.8559 | 35.9329 | 35.9329 | 35.9329 | 35.9329 | 35.9329 | 35.9329 | 35.9329 | 35.9329 | 35.9329 | 35.9329 | 35.9329 | 35.9329 | 35.9329 | 35.9329 | 35.9329 | 70% | 5.6725 | 39.2288 | 41.8924 | 41.9659 | 41.8867 | 41.907 | 42.0525 | 42.3473 | 42.8664 | 43.1369 | 43.3326 | 43.6288 | 44.0069 | 44.4642 | 44.7038 | 44.6261 | 44.7031 | 44.7031 | 44.7031 | 44.7031 | 44.7031 | 44.7031 | 44.7031 | 44.7031 | 44.7031 | 44.7031 | 44.7031 | 44.7031 | 44.7031 | 44.7031 | 44.7031
65% | 521.4885 | 29.6097 | 31.8228 | 32.0452 | 31.9362 | 32.0399 | 32.0825 | 32.219 | 32.4996 | 32.7358 | 32.8445 | 32.7476 | 33.1537 | 33.2182 | 33.1419 | 33.2948 | 33.3663 | 33.3663 | 33.3663 | 33.3663 | 33.3663 | 33.3663 | 33.3663 | 33.3663 | 33.3663 | 33.3663 | 33.3663 | 33.3663 | 33.3663 | 33.3663 | 33.3663 | 65% | 6.4288 | 36.4267 | 38.9001 | 38.9683 | 38.8948 | 38.9137 | 39.0487 | 39.3225 | 39.8045 | 40.0557 | 40.2374 | 40.5125 | 40.8636 | 41.2882 | 41.5107 | 41.4385 | 41.51 | 41.51 | 41.51 | 41.51 | 41.51 | 41.51 | 41.51 | 41.51 | 41.51 | 41.51 | 41.51 | 41.51 | 41.51 | 41.51 | 41.51
60% | 812.675 | 27.332 | 29.3749 | 29.5802 | 29.4796 | 29.5753 | 29.6146 | 29.7406 | 29.9997 | 30.2176 | 30.318 | 30.2285 | 30.6035 | 30.6629 | 30.5925 | 30.7337 | 30.7997 | 30.7997 | 30.7997 | 30.7997 | 30.7997 | 30.7997 | 30.7997 | 30.7997 | 30.7997 | 30.7997 | 30.7997 | 30.7997 | 30.7997 | 30.7997 | 30.7997 | 60% | 11.3449 | 33.6247 | 35.9078 | 35.9708 | 35.9029 | 35.9203 | 36.045 | 36.2977 | 36.7426 | 36.9745 | 37.1422 | 37.3961 | 37.7202 | 38.1122 | 38.3176 | 38.251 | 38.317 | 38.317 | 38.317 | 38.317 | 38.317 | 38.317 | 38.317 | 38.317 | 38.317 | 38.317 | 38.317 | 38.317 | 38.317 | 38.317 | 38.317
55% | 1202.1843 | 25.0543 | 26.927 | 27.1152 | 27.023 | 27.1107 | 27.1467 | 27.2622 | 27.4997 | 27.6995 | 27.7915 | 27.7095 | 28.0532 | 28.1077 | 28.0432 | 28.1725 | 28.233 | 28.233 | 28.233 | 28.233 | 28.233 | 28.233 | 28.233 | 28.233 | 28.233 | 28.233 | 28.233 | 28.233 | 28.233 | 28.233 | 28.233 | 55% | 35.5474 | 30.8226 | 32.9155 | 32.9732 | 32.911 | 32.927 | 33.0412 | 33.2729 | 33.6808 | 33.8933 | 34.0471 | 34.2798 | 34.5769 | 34.9361 | 35.1244 | 35.0634 | 35.1239 | 35.1239 | 35.1239 | 35.1239 | 35.1239 | 35.1239 | 35.1239 | 35.1239 | 35.1239 | 35.1239 | 35.1239 | 35.1239 | 35.1239 | 35.1239 | 35.1239
50% | 1686.2345 | 22.7767 | 24.4791 | 24.6502 | 24.5663 | 24.6461 | 24.6788 | 24.7838 | 24.9997 | 25.1814 | 25.265 | 25.1904 | 25.5029 | 25.5524 | 25.4938 | 25.6114 | 25.6664 | 25.6664 | 25.6664 | 25.6664 | 25.6664 | 25.6664 | 25.6664 | 25.6664 | 25.6664 | 25.6664 | 25.6664 | 25.6664 | 25.6664 | 25.6664 | 25.6664 | 50% | 95.2974 | 28.0206 | 29.9231 | 29.9756 | 29.919 | 29.9336 | 30.0375 | 30.2481 | 30.6189 | 30.8121 | 30.9519 | 31.1634 | 31.4335 | 31.7601 | 31.9313 | 31.8758 | 31.9308 | 31.9308 | 31.9308 | 31.9308 | 31.9308 | 31.9308 | 31.9308 | 31.9308 | 31.9308 | 31.9308 | 31.9308 | 31.9308 | 31.9308 | 31.9308 | 31.9308
45% | 2129.0649 | 20.499 | 22.0312 | 22.1852 | 22.1097 | 22.1815 | 22.2109 | 22.3054 | 22.4998 | 22.6632 | 22.7385 | 22.6714 | 22.9526 | 22.9972 | 22.9444 | 23.0502 | 23.0997 | 23.0997 | 23.0997 | 23.0997 | 23.0997 | 23.0997 | 23.0997 | 23.0997 | 23.0997 | 23.0997 | 23.0997 | 23.0997 | 23.0997 | 23.0997 | 23.0997 | 45% | 208.7467 | 25.2185 | 26.9308 | 26.9781 | 26.9271 | 26.9402 | 27.0337 | 27.2232 | 27.557 | 27.7309 | 27.8567 | 28.0471 | 28.2902 | 28.5841 | 28.7382 | 28.6882 | 28.7377 | 28.7377 | 28.7377 | 28.7377 | 28.7377 | 28.7377 | 28.7377 | 28.7377 | 28.7377 | 28.7377 | 28.7377 | 28.7377 | 28.7377 | 28.7377 | 28.7377
40% | 2484.5393 | 18.2213 | 19.5833 | 19.7201 | 19.6531 | 19.7169 | 19.7431 | 19.8271 | 19.9998 | 20.1451 | 20.212 | 20.1524 | 20.4023 | 20.4419 | 20.395 | 20.4891 | 20.5331 | 20.5331 | 20.5331 | 20.5331 | 20.5331 | 20.5331 | 20.5331 | 20.5331 | 20.5331 | 20.5331 | 20.5331 | 20.5331 | 20.5331 | 20.5331 | 20.5331 | 40% | 380.4333 | 22.4164 | 23.9385 | 23.9805 | 23.9352 | 23.9469 | 24.03 | 24.1984 | 24.4951 | 24.6497 | 24.7615 | 24.9307 | 25.1468 | 25.4081 | 25.545 | 25.5006 | 25.5446 | 25.5446 | 25.5446 | 25.5446 | 25.5446 | 25.5446 | 25.5446 | 25.5446 | 25.5446 | 25.5446 | 25.5446 | 25.5446 | 25.5446 | 25.5446 | 25.5446
35% | 2808.248 | 15.9437 | 17.1354 | 17.2551 | 17.1964 | 17.2522 | 17.2752 | 17.3487 | 17.4998 | 17.6269 | 17.6855 | 17.6333 | 17.852 | 17.8867 | 17.8457 | 17.928 | 17.9665 | 17.9665 | 17.9665 | 17.9665 | 17.9665 | 17.9665 | 17.9665 | 17.9665 | 17.9665 | 17.9665 | 17.9665 | 17.9665 | 17.9665 | 17.9665 | 17.9665 | 35% | 696.5786 | 19.6144 | 20.9462 | 20.983 | 20.9433 | 20.9535 | 21.0262 | 21.1736 | 21.4332 | 21.5685 | 21.6663 | 21.8144 | 22.0035 | 22.2321 | 22.3519 | 22.3131 | 22.3516 | 22.3516 | 22.3516 | 22.3516 | 22.3516 | 22.3516 | 22.3516 | 22.3516 | 22.3516 | 22.3516 | 22.3516 | 22.3516 | 22.3516 | 22.3516 | 22.3516
30% | 3095.6528 | 13.666 | 14.6875 | 14.7901 | 14.7398 | 14.7876 | 14.8073 | 14.8703 | 14.9998 | 15.1088 | 15.159 | 15.1143 | 15.3017 | 15.3315 | 15.2963 | 15.3668 | 15.3998 | 15.3998 | 15.3998 | 15.3998 | 15.3998 | 15.3998 | 15.3998 | 15.3998 | 15.3998 | 15.3998 | 15.3998 | 15.3998 | 15.3998 | 15.3998 | 15.3998 | 30% | 1260.7997 | 16.8123 | 17.9539 | 17.9854 | 17.9514 | 17.9602 | 18.0225 | 18.1488 | 18.3713 | 18.4873 | 18.5711 | 18.6981 | 18.8601 | 19.0561 | 19.1588 | 19.1255 | 19.1585 | 19.1585 | 19.1585 | 19.1585 | 19.1585 | 19.1585 | 19.1585 | 19.1585 | 19.1585 | 19.1585 | 19.1585 | 19.1585 | 19.1585 | 19.1585 | 19.1585
25% | 3358.8552 | 11.3883 | 12.2396 | 12.3251 | 12.2832 | 12.323 | 12.3394 | 12.3919 | 12.4999 | 12.5907 | 12.6325 | 12.5952 | 12.7514 | 12.7762 | 12.7469 | 12.8057 | 12.8332 | 12.8332 | 12.8332 | 12.8332 | 12.8332 | 12.8332 | 12.8332 | 12.8332 | 12.8332 | 12.8332 | 12.8332 | 12.8332 | 12.8332 | 12.8332 | 12.8332 | 25% | 1965.3198 | 14.0103 | 14.9616 | 14.9878 | 14.9595 | 14.9668 | 15.0187 | 15.124 | 15.3094 | 15.406 | 15.4759 | 15.5817 | 15.7168 | 15.8801 | 15.9656 | 15.9379 | 15.9654 | 15.9654 | 15.9654 | 15.9654 | 15.9654 | 15.9654 | 15.9654 | 15.9654 | 15.9654 | 15.9654 | 15.9654 | 15.9654 | 15.9654 | 15.9654 | 15.9654
20% | 3588.7791 | 9.1107 | 9.7916 | 9.8601 | 9.8265 | 9.8584 | 9.8715 | 9.9135 | 9.9999 | 10.0725 | 10.106 | 10.0762 | 10.2012 | 10.221 | 10.1975 | 10.2446 | 10.2666 | 10.2666 | 10.2666 | 10.2666 | 10.2666 | 10.2666 | 10.2666 | 10.2666 | 10.2666 | 10.2666 | 10.2666 | 10.2666 | 10.2666 | 10.2666 | 10.2666 | 20% | 2490.2118 | 11.2082 | 11.9693 | 11.9903 | 11.9676 | 11.9734 | 12.015 | 12.0992 | 12.2475 | 12.3248 | 12.3807 | 12.4654 | 12.5734 | 12.7041 | 12.7725 | 12.7503 | 12.7723 | 12.7723 | 12.7723 | 12.7723 | 12.7723 | 12.7723 | 12.7723 | 12.7723 | 12.7723 | 12.7723 | 12.7723 | 12.7723 | 12.7723 | 12.7723 | 12.7723
15% | 3802.4419 | 6.833 | 7.3437 | 7.3951 | 7.3699 | 7.3938 | 7.4036 | 7.4351 | 7.4999 | 7.5544 | 7.5795 | 7.5571 | 7.6509 | 7.6657 | 7.6481 | 7.6834 | 7.6999 | 7.6999 | 7.6999 | 7.6999 | 7.6999 | 7.6999 | 7.6999 | 7.6999 | 7.6999 | 7.6999 | 7.6999 | 7.6999 | 7.6999 | 7.6999 | 7.6999 | 15% | 2997.7083 | 8.4062 | 8.9769 | 8.9927 | 8.9757 | 8.9801 | 9.0112 | 9.0744 | 9.1857 | 9.2436 | 9.2856 | 9.349 | 9.4301 | 9.528 | 9.5794 | 9.5627 | 9.5792 | 9.5792 | 9.5792 | 9.5792 | 9.5792 | 9.5792 | 9.5792 | 9.5792 | 9.5792 | 9.5792 | 9.5792 | 9.5792 | 9.5792 | 9.5792 | 9.5792
10% | 4024.8025 | 4.5553 | 4.8958 | 4.93 | 4.9133 | 4.9292 | 4.9358 | 4.9568 | 4.9999 | 5.0363 | 5.053 | 5.0381 | 5.1006 | 5.1105 | 5.0988 | 5.1223 | 5.1333 | 5.1333 | 5.1333 | 5.1333 | 5.1333 | 5.1333 | 5.1333 | 5.1333 | 5.1333 | 5.1333 | 5.1333 | 5.1333 | 5.1333 | 5.1333 | 5.1333 | 10% | 3491.5908 | 5.6041 | 5.9846 | 5.9951 | 5.9838 | 5.9867 | 6.0075 | 6.0496 | 6.1238 | 6.1624 | 6.1904 | 6.2327 | 6.2867 | 6.352 | 6.3863 | 6.3752 | 6.3862 | 6.3862 | 6.3862 | 6.3862 | 6.3862 | 6.3862 | 6.3862 | 6.3862 | 6.3862 | 6.3862 | 6.3862 | 6.3862 | 6.3862 | 6.3862 | 6.3862
5% | 4239.978 | 2.2777 | 2.4479 | 2.465 | 2.4566 | 2.4646 | 2.4679 | 2.4784 | 2.5 | 2.5181 | 2.5265 | 2.519 | 2.5503 | 2.5552 | 2.5494 | 2.5611 | 2.5666 | 2.5666 | 2.5666 | 2.5666 | 2.5666 | 2.5666 | 2.5666 | 2.5666 | 2.5666 | 2.5666 | 2.5666 | 2.5666 | 2.5666 | 2.5666 | 2.5666 | 5% | 3955.9766 | 2.8021 | 2.9923 | 2.9976 | 2.9919 | 2.9934 | 3.0037 | 3.0248 | 3.0619 | 3.0812 | 3.0952 | 3.1163 | 3.1434 | 3.176 | 3.1931 | 3.1876 | 3.1931 | 3.1931 | 3.1931 | 3.1931 | 3.1931 | 3.1931 | 3.1931 | 3.1931 | 3.1931 | 3.1931 | 3.1931 | 3.1931 | 3.1931 | 3.1931 | 3.1931
9.992e-14% | 4391.6218 | 4.5517e-14 | 4.8919e-14 | 4.9261e-14 | 4.9093e-14 | 4.9253e-14 | 4.9318e-14 | 4.9528e-14 | 4.9959e-14 | 5.0322e-14 | 5.049e-14 | 5.0341e-14 | 5.0965e-14 | 5.1064e-14 | 5.0947e-14 | 5.1182e-14 | 5.1292e-14 | 5.1292e-14 | 5.1292e-14 | 5.1292e-14 | 5.1292e-14 | 5.1292e-14 | 5.1292e-14 | 5.1292e-14 | 5.1292e-14 | 5.1292e-14 | 5.1292e-14 | 5.1292e-14 | 5.1292e-14 | 5.1292e-14 | 5.1292e-14 | 9.992e-14% | 4391.6218 | 5.5996e-14 | 5.9798e-14 | 5.9903e-14 | 5.979e-14 | 5.9819e-14 | 6.0027e-14 | 6.0448e-14 | 6.1189e-14 | 6.1575e-14 | 6.1854e-14 | 6.2277e-14 | 6.2817e-14 | 6.3469e-14 | 6.3812e-14 | 6.3701e-14 | 6.3811e-14 | 6.3811e-14 | 6.3811e-14 | 6.3811e-14 | 6.3811e-14 | 6.3811e-14 | 6.3811e-14 | 6.3811e-14 | 6.3811e-14 | 6.3811e-14 | 6.3811e-14 | 6.3811e-14 | 6.3811e-14 | 6.3811e-14 | 6.3811e-14
Option 3
Winter Season | [31 empty] | Winter Season
P50 | [31 empty] | P10
% of MD | Winter - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Winter - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 43.3628 | 47.9013 | 48.3825 | 48.9775 | 49.7674 | 50.5163 | 51.825 | 55.1166 | 56.887 | 55.5954 | 59.594 | 60.3144 | 60.8323 | 63.2734 | 63.6707 | 63.6707 | 63.6707 | 63.6707 | 63.6707 | 63.6707 | 63.6707 | 63.6707 | 63.6707 | 63.6707 | 63.6707 | 63.6707 | 63.6707 | 63.6707 | 63.6707 | 63.6707 | 100% | 0 | 47.5339 | 51.863 | 52.3113 | 53.8585 | 53.8208 | 54.161 | 55.4916 | 59.3146 | 60.8922 | 59.3989 | 63.524 | 61.792 | 63.3504 | 64.4734 | 64.012 | 64.012 | 64.012 | 64.012 | 64.012 | 64.012 | 64.012 | 64.012 | 64.012 | 64.012 | 64.012 | 64.012 | 64.012 | 64.012 | 64.012 | 64.012
99% | 0.2972 | 42.9291 | 47.4223 | 47.8987 | 48.4877 | 49.2697 | 50.0111 | 51.3068 | 54.5654 | 56.3182 | 55.0395 | 58.9981 | 59.7113 | 60.224 | 62.6406 | 63.034 | 63.034 | 63.034 | 63.034 | 63.034 | 63.034 | 63.034 | 63.034 | 63.034 | 63.034 | 63.034 | 63.034 | 63.034 | 63.034 | 63.034 | 63.034 | 99% | 0.2972 | 47.0586 | 51.3443 | 51.7882 | 53.3199 | 53.2826 | 53.6194 | 54.9367 | 58.7214 | 60.2833 | 58.8049 | 62.8887 | 61.1741 | 62.7169 | 63.8287 | 63.3719 | 63.3719 | 63.3719 | 63.3719 | 63.3719 | 63.3719 | 63.3719 | 63.3719 | 63.3719 | 63.3719 | 63.3719 | 63.3719 | 63.3719 | 63.3719 | 63.3719 | 63.3719
98% | 0.2972 | 42.4955 | 46.9432 | 47.4149 | 47.9979 | 48.7721 | 49.506 | 50.7885 | 54.0143 | 55.7493 | 54.4835 | 58.4021 | 59.1081 | 59.6156 | 62.0079 | 62.3973 | 62.3973 | 62.3973 | 62.3973 | 62.3973 | 62.3973 | 62.3973 | 62.3973 | 62.3973 | 62.3973 | 62.3973 | 62.3973 | 62.3973 | 62.3973 | 62.3973 | 62.3973 | 98% | 0.2972 | 46.5832 | 50.8257 | 51.2651 | 52.7813 | 52.7443 | 53.0778 | 54.3818 | 58.1283 | 59.6743 | 58.2109 | 62.2535 | 60.5562 | 62.0834 | 63.184 | 62.7318 | 62.7318 | 62.7318 | 62.7318 | 62.7318 | 62.7318 | 62.7318 | 62.7318 | 62.7318 | 62.7318 | 62.7318 | 62.7318 | 62.7318 | 62.7318 | 62.7318 | 62.7318
97% | 0.2972 | 42.0619 | 46.4642 | 46.931 | 47.5082 | 48.2744 | 49.0008 | 50.2703 | 53.4631 | 55.1804 | 53.9276 | 57.8062 | 58.505 | 59.0073 | 61.3752 | 61.7606 | 61.7606 | 61.7606 | 61.7606 | 61.7606 | 61.7606 | 61.7606 | 61.7606 | 61.7606 | 61.7606 | 61.7606 | 61.7606 | 61.7606 | 61.7606 | 61.7606 | 61.7606 | 97% | 0.2972 | 46.1079 | 50.3071 | 50.7419 | 52.2427 | 52.2061 | 52.5362 | 53.8269 | 57.5352 | 59.0654 | 57.6169 | 61.6183 | 59.9383 | 61.4499 | 62.5392 | 62.0917 | 62.0917 | 62.0917 | 62.0917 | 62.0917 | 62.0917 | 62.0917 | 62.0917 | 62.0917 | 62.0917 | 62.0917 | 62.0917 | 62.0917 | 62.0917 | 62.0917 | 62.0917
95% | 1.486 | 41.1946 | 45.5062 | 45.9634 | 46.5286 | 47.2791 | 47.9905 | 49.2338 | 52.3608 | 54.0427 | 52.8157 | 56.6143 | 57.2987 | 57.7907 | 60.1097 | 60.4871 | 60.4871 | 60.4871 | 60.4871 | 60.4871 | 60.4871 | 60.4871 | 60.4871 | 60.4871 | 60.4871 | 60.4871 | 60.4871 | 60.4871 | 60.4871 | 60.4871 | 60.4871 | 95% | 1.486 | 45.1572 | 49.2698 | 49.6957 | 51.1655 | 51.1297 | 51.4529 | 52.717 | 56.3489 | 57.8476 | 56.4289 | 60.3478 | 58.7024 | 60.1829 | 61.2498 | 60.8114 | 60.8114 | 60.8114 | 60.8114 | 60.8114 | 60.8114 | 60.8114 | 60.8114 | 60.8114 | 60.8114 | 60.8114 | 60.8114 | 60.8114 | 60.8114 | 60.8114 | 60.8114
90% | 8.6188 | 39.0265 | 43.1111 | 43.5443 | 44.0797 | 44.7907 | 45.4647 | 46.6425 | 49.6049 | 51.1983 | 50.0359 | 53.6346 | 54.283 | 54.7491 | 56.946 | 57.3036 | 57.3036 | 57.3036 | 57.3036 | 57.3036 | 57.3036 | 57.3036 | 57.3036 | 57.3036 | 57.3036 | 57.3036 | 57.3036 | 57.3036 | 57.3036 | 57.3036 | 57.3036 | 90% | 8.6188 | 42.7805 | 46.6767 | 47.0802 | 48.4726 | 48.4387 | 48.7449 | 49.9425 | 53.3831 | 54.803 | 53.459 | 57.1716 | 55.6128 | 57.0154 | 58.0261 | 57.6108 | 57.6108 | 57.6108 | 57.6108 | 57.6108 | 57.6108 | 57.6108 | 57.6108 | 57.6108 | 57.6108 | 57.6108 | 57.6108 | 57.6108 | 57.6108 | 57.6108 | 57.6108
85% | 40.1218 | 36.8584 | 40.7161 | 41.1251 | 41.6309 | 42.3023 | 42.9389 | 44.0513 | 46.8491 | 48.354 | 47.2561 | 50.6549 | 51.2673 | 51.7074 | 53.7823 | 54.1201 | 54.1201 | 54.1201 | 54.1201 | 54.1201 | 54.1201 | 54.1201 | 54.1201 | 54.1201 | 54.1201 | 54.1201 | 54.1201 | 54.1201 | 54.1201 | 54.1201 | 54.1201 | 85% | 40.1218 | 40.4038 | 44.0835 | 44.4646 | 45.7797 | 45.7477 | 46.0368 | 47.1679 | 50.4174 | 51.7583 | 50.489 | 53.9954 | 52.5232 | 53.8479 | 54.8024 | 54.4102 | 54.4102 | 54.4102 | 54.4102 | 54.4102 | 54.4102 | 54.4102 | 54.4102 | 54.4102 | 54.4102 | 54.4102 | 54.4102 | 54.4102 | 54.4102 | 54.4102 | 54.4102
80% | 93.0231 | 34.6902 | 38.321 | 38.706 | 39.182 | 39.8139 | 40.413 | 41.46 | 44.0933 | 45.5096 | 44.4764 | 47.6752 | 48.2515 | 48.6658 | 50.6187 | 50.9365 | 50.9365 | 50.9365 | 50.9365 | 50.9365 | 50.9365 | 50.9365 | 50.9365 | 50.9365 | 50.9365 | 50.9365 | 50.9365 | 50.9365 | 50.9365 | 50.9365 | 50.9365 | 80% | 93.0231 | 38.0271 | 41.4904 | 41.849 | 43.0868 | 43.0566 | 43.3288 | 44.3933 | 47.4517 | 48.7137 | 47.5191 | 50.8192 | 49.4336 | 50.6803 | 51.5787 | 51.2096 | 51.2096 | 51.2096 | 51.2096 | 51.2096 | 51.2096 | 51.2096 | 51.2096 | 51.2096 | 51.2096 | 51.2096 | 51.2096 | 51.2096 | 51.2096 | 51.2096 | 51.2096
75% | 197.0426 | 32.5221 | 35.926 | 36.2869 | 36.7331 | 37.3256 | 37.8872 | 38.8688 | 41.3374 | 42.6653 | 41.6966 | 44.6955 | 45.2358 | 45.6242 | 47.455 | 47.753 | 47.753 | 47.753 | 47.753 | 47.753 | 47.753 | 47.753 | 47.753 | 47.753 | 47.753 | 47.753 | 47.753 | 47.753 | 47.753 | 47.753 | 47.753 | 75% | 197.0426 | 35.6504 | 38.8972 | 39.2335 | 40.3939 | 40.3656 | 40.6207 | 41.6187 | 44.4859 | 45.6691 | 44.5491 | 47.643 | 46.344 | 47.5128 | 48.3551 | 48.009 | 48.009 | 48.009 | 48.009 | 48.009 | 48.009 | 48.009 | 48.009 | 48.009 | 48.009 | 48.009 | 48.009 | 48.009 | 48.009 | 48.009 | 48.009
70% | 378.0365 | 30.3539 | 33.5309 | 33.8678 | 34.2842 | 34.8372 | 35.3614 | 36.2775 | 38.5816 | 39.8209 | 38.9168 | 41.7158 | 42.2201 | 42.5826 | 44.2913 | 44.5695 | 44.5695 | 44.5695 | 44.5695 | 44.5695 | 44.5695 | 44.5695 | 44.5695 | 44.5695 | 44.5695 | 44.5695 | 44.5695 | 44.5695 | 44.5695 | 44.5695 | 44.5695 | 70% | 378.0365 | 33.2737 | 36.3041 | 36.6179 | 37.7009 | 37.6745 | 37.9127 | 38.8441 | 41.5202 | 42.6245 | 41.5792 | 44.4668 | 43.2544 | 44.3453 | 45.1314 | 44.8084 | 44.8084 | 44.8084 | 44.8084 | 44.8084 | 44.8084 | 44.8084 | 44.8084 | 44.8084 | 44.8084 | 44.8084 | 44.8084 | 44.8084 | 44.8084 | 44.8084 | 44.8084
65% | 616.0926 | 28.1858 | 31.1358 | 31.4486 | 31.8354 | 32.3488 | 32.8356 | 33.6863 | 35.8258 | 36.9766 | 36.137 | 38.7361 | 39.2044 | 39.541 | 41.1277 | 41.3859 | 41.3859 | 41.3859 | 41.3859 | 41.3859 | 41.3859 | 41.3859 | 41.3859 | 41.3859 | 41.3859 | 41.3859 | 41.3859 | 41.3859 | 41.3859 | 41.3859 | 41.3859 | 65% | 616.0926 | 30.897 | 33.7109 | 34.0023 | 35.008 | 34.9835 | 35.2046 | 36.0696 | 38.5545 | 39.5799 | 38.6093 | 41.2906 | 40.1648 | 41.1778 | 41.9077 | 41.6078 | 41.6078 | 41.6078 | 41.6078 | 41.6078 | 41.6078 | 41.6078 | 41.6078 | 41.6078 | 41.6078 | 41.6078 | 41.6078 | 41.6078 | 41.6078 | 41.6078 | 41.6078
60% | 934.9866 | 26.0177 | 28.7408 | 29.0295 | 29.3865 | 29.8605 | 30.3098 | 31.095 | 33.07 | 34.1322 | 33.3573 | 35.7564 | 36.1887 | 36.4994 | 37.964 | 38.2024 | 38.2024 | 38.2024 | 38.2024 | 38.2024 | 38.2024 | 38.2024 | 38.2024 | 38.2024 | 38.2024 | 38.2024 | 38.2024 | 38.2024 | 38.2024 | 38.2024 | 38.2024 | 60% | 934.9866 | 28.5203 | 31.1178 | 31.3868 | 32.3151 | 32.2925 | 32.4966 | 33.295 | 35.5888 | 36.5353 | 35.6393 | 38.1144 | 37.0752 | 38.0103 | 38.6841 | 38.4072 | 38.4072 | 38.4072 | 38.4072 | 38.4072 | 38.4072 | 38.4072 | 38.4072 | 38.4072 | 38.4072 | 38.4072 | 38.4072 | 38.4072 | 38.4072 | 38.4072 | 38.4072
55% | 1310.9428 | 23.8495 | 26.3457 | 26.6104 | 26.9376 | 27.3721 | 27.784 | 28.5038 | 30.3141 | 31.2879 | 30.5775 | 32.7767 | 33.1729 | 33.4578 | 34.8003 | 35.0189 | 35.0189 | 35.0189 | 35.0189 | 35.0189 | 35.0189 | 35.0189 | 35.0189 | 35.0189 | 35.0189 | 35.0189 | 35.0189 | 35.0189 | 35.0189 | 35.0189 | 35.0189 | 55% | 1310.9428 | 26.1436 | 28.5246 | 28.7712 | 29.6222 | 29.6014 | 29.7885 | 30.5204 | 32.623 | 33.4907 | 32.6694 | 34.9382 | 33.9856 | 34.8427 | 35.4604 | 35.2066 | 35.2066 | 35.2066 | 35.2066 | 35.2066 | 35.2066 | 35.2066 | 35.2066 | 35.2066 | 35.2066 | 35.2066 | 35.2066 | 35.2066 | 35.2066 | 35.2066 | 35.2066
50% | 1730.2899 | 21.6814 | 23.9506 | 24.1913 | 24.4887 | 24.8837 | 25.2582 | 25.9125 | 27.5583 | 28.4435 | 27.7977 | 29.797 | 30.1572 | 30.4161 | 31.6367 | 31.8353 | 31.8353 | 31.8353 | 31.8353 | 31.8353 | 31.8353 | 31.8353 | 31.8353 | 31.8353 | 31.8353 | 31.8353 | 31.8353 | 31.8353 | 31.8353 | 31.8353 | 31.8353 | 50% | 1730.2899 | 23.7669 | 25.9315 | 26.1556 | 26.9292 | 26.9104 | 27.0805 | 27.7458 | 29.6573 | 30.4461 | 29.6994 | 31.762 | 30.896 | 31.6752 | 32.2367 | 32.006 | 32.006 | 32.006 | 32.006 | 32.006 | 32.006 | 32.006 | 32.006 | 32.006 | 32.006 | 32.006 | 32.006 | 32.006 | 32.006 | 32.006 | 32.006
45% | 2168.0633 | 19.5132 | 21.5556 | 21.7721 | 22.0399 | 22.3953 | 22.7323 | 23.3213 | 24.8025 | 25.5992 | 25.0179 | 26.8173 | 27.1415 | 27.3745 | 28.473 | 28.6518 | 28.6518 | 28.6518 | 28.6518 | 28.6518 | 28.6518 | 28.6518 | 28.6518 | 28.6518 | 28.6518 | 28.6518 | 28.6518 | 28.6518 | 28.6518 | 28.6518 | 28.6518 | 45% | 2168.0633 | 21.3903 | 23.3383 | 23.5401 | 24.2363 | 24.2193 | 24.3724 | 24.9712 | 26.6916 | 27.4015 | 26.7295 | 28.5858 | 27.8064 | 28.5077 | 29.013 | 28.8054 | 28.8054 | 28.8054 | 28.8054 | 28.8054 | 28.8054 | 28.8054 | 28.8054 | 28.8054 | 28.8054 | 28.8054 | 28.8054 | 28.8054 | 28.8054 | 28.8054 | 28.8054
40% | 2609.7004 | 17.3451 | 19.1605 | 19.353 | 19.591 | 19.907 | 20.2065 | 20.73 | 22.0466 | 22.7548 | 22.2382 | 23.8376 | 24.1258 | 24.3329 | 25.3093 | 25.4683 | 25.4683 | 25.4683 | 25.4683 | 25.4683 | 25.4683 | 25.4683 | 25.4683 | 25.4683 | 25.4683 | 25.4683 | 25.4683 | 25.4683 | 25.4683 | 25.4683 | 25.4683 | 40% | 2609.7004 | 19.0136 | 20.7452 | 20.9245 | 21.5434 | 21.5283 | 21.6644 | 22.1966 | 23.7258 | 24.3569 | 23.7595 | 25.4096 | 24.7168 | 25.3402 | 25.7894 | 25.6048 | 25.6048 | 25.6048 | 25.6048 | 25.6048 | 25.6048 | 25.6048 | 25.6048 | 25.6048 | 25.6048 | 25.6048 | 25.6048 | 25.6048 | 25.6048 | 25.6048 | 25.6048
35% | 2998.1389 | 15.177 | 16.7654 | 16.9339 | 17.1421 | 17.4186 | 17.6807 | 18.1388 | 19.2908 | 19.9105 | 19.4584 | 20.8579 | 21.1101 | 21.2913 | 22.1457 | 22.2847 | 22.2847 | 22.2847 | 22.2847 | 22.2847 | 22.2847 | 22.2847 | 22.2847 | 22.2847 | 22.2847 | 22.2847 | 22.2847 | 22.2847 | 22.2847 | 22.2847 | 22.2847 | 35% | 2998.1389 | 16.6369 | 18.152 | 18.3089 | 18.8505 | 18.8373 | 18.9563 | 19.4221 | 20.7601 | 21.3123 | 20.7896 | 22.2334 | 21.6272 | 22.1726 | 22.5657 | 22.4042 | 22.4042 | 22.4042 | 22.4042 | 22.4042 | 22.4042 | 22.4042 | 22.4042 | 22.4042 | 22.4042 | 22.4042 | 22.4042 | 22.4042 | 22.4042 | 22.4042 | 22.4042
30% | 3309.3057 | 13.0088 | 14.3704 | 14.5148 | 14.6932 | 14.9302 | 15.1549 | 15.5475 | 16.535 | 17.0661 | 16.6786 | 17.8782 | 18.0943 | 18.2497 | 18.982 | 19.1012 | 19.1012 | 19.1012 | 19.1012 | 19.1012 | 19.1012 | 19.1012 | 19.1012 | 19.1012 | 19.1012 | 19.1012 | 19.1012 | 19.1012 | 19.1012 | 19.1012 | 19.1012 | 30% | 3309.3057 | 14.2602 | 15.5589 | 15.6934 | 16.1575 | 16.1462 | 16.2483 | 16.6475 | 17.7944 | 18.2677 | 17.8197 | 19.0572 | 18.5376 | 19.0051 | 19.342 | 19.2036 | 19.2036 | 19.2036 | 19.2036 | 19.2036 | 19.2036 | 19.2036 | 19.2036 | 19.2036 | 19.2036 | 19.2036 | 19.2036 | 19.2036 | 19.2036 | 19.2036 | 19.2036
25% | 3537.8514 | 10.8407 | 11.9753 | 12.0956 | 12.2444 | 12.4419 | 12.6291 | 12.9563 | 13.7791 | 14.2218 | 13.8989 | 14.8985 | 15.0786 | 15.2081 | 15.8183 | 15.9177 | 15.9177 | 15.9177 | 15.9177 | 15.9177 | 15.9177 | 15.9177 | 15.9177 | 15.9177 | 15.9177 | 15.9177 | 15.9177 | 15.9177 | 15.9177 | 15.9177 | 15.9177 | 25% | 3537.8514 | 11.8835 | 12.9657 | 13.0778 | 13.4646 | 13.4552 | 13.5402 | 13.8729 | 14.8286 | 15.223 | 14.8497 | 15.881 | 15.448 | 15.8376 | 16.1184 | 16.003 | 16.003 | 16.003 | 16.003 | 16.003 | 16.003 | 16.003 | 16.003 | 16.003 | 16.003 | 16.003 | 16.003 | 16.003 | 16.003 | 16.003 | 16.003
20% | 3731.0305 | 8.6726 | 9.5803 | 9.6765 | 9.7955 | 9.9535 | 10.1033 | 10.365 | 11.0233 | 11.3774 | 11.1191 | 11.9188 | 12.0629 | 12.1665 | 12.6547 | 12.7341 | 12.7341 | 12.7341 | 12.7341 | 12.7341 | 12.7341 | 12.7341 | 12.7341 | 12.7341 | 12.7341 | 12.7341 | 12.7341 | 12.7341 | 12.7341 | 12.7341 | 12.7341 | 20% | 3731.0305 | 9.5068 | 10.3726 | 10.4623 | 10.7717 | 10.7642 | 10.8322 | 11.0983 | 11.8629 | 12.1784 | 11.8798 | 12.7048 | 12.3584 | 12.6701 | 12.8947 | 12.8024 | 12.8024 | 12.8024 | 12.8024 | 12.8024 | 12.8024 | 12.8024 | 12.8024 | 12.8024 | 12.8024 | 12.8024 | 12.8024 | 12.8024 | 12.8024 | 12.8024 | 12.8024
15% | 3910.2412 | 6.5044 | 7.1852 | 7.2574 | 7.3466 | 7.4651 | 7.5774 | 7.7738 | 8.2675 | 8.5331 | 8.3393 | 8.9391 | 9.0472 | 9.1248 | 9.491 | 9.5506 | 9.5506 | 9.5506 | 9.5506 | 9.5506 | 9.5506 | 9.5506 | 9.5506 | 9.5506 | 9.5506 | 9.5506 | 9.5506 | 9.5506 | 9.5506 | 9.5506 | 9.5506 | 15% | 3910.2412 | 7.1301 | 7.7794 | 7.8467 | 8.0788 | 8.0731 | 8.1241 | 8.3237 | 8.8972 | 9.1338 | 8.9098 | 9.5286 | 9.2688 | 9.5026 | 9.671 | 9.6018 | 9.6018 | 9.6018 | 9.6018 | 9.6018 | 9.6018 | 9.6018 | 9.6018 | 9.6018 | 9.6018 | 9.6018 | 9.6018 | 9.6018 | 9.6018 | 9.6018 | 9.6018
10% | 4075.1864 | 4.3363 | 4.7901 | 4.8383 | 4.8977 | 4.9767 | 5.0516 | 5.1825 | 5.5117 | 5.6887 | 5.5595 | 5.9594 | 6.0314 | 6.0832 | 6.3273 | 6.3671 | 6.3671 | 6.3671 | 6.3671 | 6.3671 | 6.3671 | 6.3671 | 6.3671 | 6.3671 | 6.3671 | 6.3671 | 6.3671 | 6.3671 | 6.3671 | 6.3671 | 6.3671 | 10% | 4075.1864 | 4.7534 | 5.1863 | 5.2311 | 5.3858 | 5.3821 | 5.4161 | 5.5492 | 5.9315 | 6.0892 | 5.9399 | 6.3524 | 6.1792 | 6.335 | 6.4473 | 6.4012 | 6.4012 | 6.4012 | 6.4012 | 6.4012 | 6.4012 | 6.4012 | 6.4012 | 6.4012 | 6.4012 | 6.4012 | 6.4012 | 6.4012 | 6.4012 | 6.4012 | 6.4012
5% | 4251.7223 | 2.1681 | 2.3951 | 2.4191 | 2.4489 | 2.4884 | 2.5258 | 2.5913 | 2.7558 | 2.8444 | 2.7798 | 2.9797 | 3.0157 | 3.0416 | 3.1637 | 3.1835 | 3.1835 | 3.1835 | 3.1835 | 3.1835 | 3.1835 | 3.1835 | 3.1835 | 3.1835 | 3.1835 | 3.1835 | 3.1835 | 3.1835 | 3.1835 | 3.1835 | 3.1835 | 5% | 4251.7223 | 2.3767 | 2.5931 | 2.6156 | 2.6929 | 2.691 | 2.708 | 2.7746 | 2.9657 | 3.0446 | 2.9699 | 3.1762 | 3.0896 | 3.1675 | 3.2237 | 3.2006 | 3.2006 | 3.2006 | 3.2006 | 3.2006 | 3.2006 | 3.2006 | 3.2006 | 3.2006 | 3.2006 | 3.2006 | 3.2006 | 3.2006 | 3.2006 | 3.2006 | 3.2006
9.992e-14% | 4391.7028 | 4.3328e-14 | 4.7863e-14 | 4.8344e-14 | 4.8938e-14 | 4.9728e-14 | 5.0476e-14 | 5.1784e-14 | 5.5073e-14 | 5.6842e-14 | 5.5551e-14 | 5.9546e-14 | 6.0266e-14 | 6.0784e-14 | 6.3223e-14 | 6.362e-14 | 6.362e-14 | 6.362e-14 | 6.362e-14 | 6.362e-14 | 6.362e-14 | 6.362e-14 | 6.362e-14 | 6.362e-14 | 6.362e-14 | 6.362e-14 | 6.362e-14 | 6.362e-14 | 6.362e-14 | 6.362e-14 | 6.362e-14 | 9.992e-14% | 4391.7028 | 4.7496e-14 | 5.1822e-14 | 5.2269e-14 | 5.3815e-14 | 5.3778e-14 | 5.4118e-14 | 5.5447e-14 | 5.9267e-14 | 6.0844e-14 | 5.9351e-14 | 6.3473e-14 | 6.1743e-14 | 6.33e-14 | 6.4422e-14 | 6.3961e-14 | 6.3961e-14 | 6.3961e-14 | 6.3961e-14 | 6.3961e-14 | 6.3961e-14 | 6.3961e-14 | 6.3961e-14 | 6.3961e-14 | 6.3961e-14 | 6.3961e-14 | 6.3961e-14 | 6.3961e-14 | 6.3961e-14 | 6.3961e-14 | 6.3961e-14
Summer Season | [31 empty] | Summer Season
P50 | [31 empty] | P10
% of MD | Summer - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Summer - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 45.5533 | 48.9582 | 49.3004 | 49.1327 | 49.2921 | 49.3577 | 49.5677 | 49.9995 | 50.3627 | 50.5299 | 50.3809 | 51.0058 | 51.1049 | 50.9876 | 51.2228 | 51.3328 | 51.3328 | 51.3328 | 51.3328 | 51.3328 | 51.3328 | 51.3328 | 51.3328 | 51.3328 | 51.3328 | 51.3328 | 51.3328 | 51.3328 | 51.3328 | 51.3328 | 100% | 0 | 56.0411 | 59.8463 | 59.9513 | 59.8381 | 59.8672 | 60.075 | 60.4961 | 61.2377 | 61.6242 | 61.9037 | 62.3269 | 62.867 | 63.5203 | 63.8626 | 63.7516 | 63.8616 | 63.8616 | 63.8616 | 63.8616 | 63.8616 | 63.8616 | 63.8616 | 63.8616 | 63.8616 | 63.8616 | 63.8616 | 63.8616 | 63.8616 | 63.8616 | 63.8616
99% | 0.37816 | 45.0978 | 48.4686 | 48.8074 | 48.6413 | 48.7992 | 48.8641 | 49.072 | 49.4995 | 49.8591 | 50.0246 | 49.8771 | 50.4957 | 50.5938 | 50.4777 | 50.7105 | 50.8194 | 50.8194 | 50.8194 | 50.8194 | 50.8194 | 50.8194 | 50.8194 | 50.8194 | 50.8194 | 50.8194 | 50.8194 | 50.8194 | 50.8194 | 50.8194 | 50.8194 | 99% | 0 | 55.4807 | 59.2478 | 59.3518 | 59.2397 | 59.2685 | 59.4742 | 59.8911 | 60.6254 | 61.0079 | 61.2847 | 61.7036 | 62.2384 | 62.8851 | 63.224 | 63.1141 | 63.223 | 63.223 | 63.223 | 63.223 | 63.223 | 63.223 | 63.223 | 63.223 | 63.223 | 63.223 | 63.223 | 63.223 | 63.223 | 63.223 | 63.223
98% | 0.37816 | 44.6423 | 47.9791 | 48.3144 | 48.15 | 48.3063 | 48.3705 | 48.5763 | 48.9995 | 49.3555 | 49.5193 | 49.3733 | 49.9856 | 50.0828 | 49.9678 | 50.1983 | 50.3061 | 50.3061 | 50.3061 | 50.3061 | 50.3061 | 50.3061 | 50.3061 | 50.3061 | 50.3061 | 50.3061 | 50.3061 | 50.3061 | 50.3061 | 50.3061 | 50.3061 | 98% | 0 | 54.9203 | 58.6494 | 58.7523 | 58.6413 | 58.6699 | 58.8735 | 59.2862 | 60.013 | 60.3917 | 60.6657 | 61.0803 | 61.6097 | 62.2499 | 62.5853 | 62.4766 | 62.5844 | 62.5844 | 62.5844 | 62.5844 | 62.5844 | 62.5844 | 62.5844 | 62.5844 | 62.5844 | 62.5844 | 62.5844 | 62.5844 | 62.5844 | 62.5844 | 62.5844
97% | 0.37816 | 44.1867 | 47.4895 | 47.8214 | 47.6587 | 47.8134 | 47.8769 | 48.0806 | 48.4995 | 48.8518 | 49.014 | 48.8695 | 49.4756 | 49.5717 | 49.458 | 49.6861 | 49.7928 | 49.7928 | 49.7928 | 49.7928 | 49.7928 | 49.7928 | 49.7928 | 49.7928 | 49.7928 | 49.7928 | 49.7928 | 49.7928 | 49.7928 | 49.7928 | 49.7928 | 97% | 0.37816 | 54.3599 | 58.0509 | 58.1528 | 58.0429 | 58.0712 | 58.2727 | 58.6812 | 59.4006 | 59.7754 | 60.0466 | 60.457 | 60.981 | 61.6146 | 61.9467 | 61.8391 | 61.9458 | 61.9458 | 61.9458 | 61.9458 | 61.9458 | 61.9458 | 61.9458 | 61.9458 | 61.9458 | 61.9458 | 61.9458 | 61.9458 | 61.9458 | 61.9458 | 61.9458
95% | 0.75633 | 43.2757 | 46.5103 | 46.8354 | 46.676 | 46.8275 | 46.8898 | 47.0893 | 47.4995 | 47.8446 | 48.0034 | 47.8618 | 48.4555 | 48.5496 | 48.4382 | 48.6616 | 48.7661 | 48.7661 | 48.7661 | 48.7661 | 48.7661 | 48.7661 | 48.7661 | 48.7661 | 48.7661 | 48.7661 | 48.7661 | 48.7661 | 48.7661 | 48.7661 | 48.7661 | 95% | 0.37816 | 53.2391 | 56.854 | 56.9537 | 56.8462 | 56.8738 | 57.0712 | 57.4713 | 58.1758 | 58.543 | 58.8086 | 59.2105 | 59.7237 | 60.3442 | 60.6695 | 60.564 | 60.6685 | 60.6685 | 60.6685 | 60.6685 | 60.6685 | 60.6685 | 60.6685 | 60.6685 | 60.6685 | 60.6685 | 60.6685 | 60.6685 | 60.6685 | 60.6685 | 60.6685
90% | 9.0759 | 40.998 | 44.0624 | 44.3703 | 44.2194 | 44.3629 | 44.4219 | 44.6109 | 44.9995 | 45.3264 | 45.4769 | 45.3428 | 45.9052 | 45.9944 | 45.8888 | 46.1005 | 46.1995 | 46.1995 | 46.1995 | 46.1995 | 46.1995 | 46.1995 | 46.1995 | 46.1995 | 46.1995 | 46.1995 | 46.1995 | 46.1995 | 46.1995 | 46.1995 | 46.1995 | 90% | 0.75633 | 50.437 | 53.8617 | 53.9562 | 53.8543 | 53.8805 | 54.0675 | 54.4465 | 55.114 | 55.4618 | 55.7134 | 56.0942 | 56.5803 | 57.1682 | 57.4763 | 57.3764 | 57.4754 | 57.4754 | 57.4754 | 57.4754 | 57.4754 | 57.4754 | 57.4754 | 57.4754 | 57.4754 | 57.4754 | 57.4754 | 57.4754 | 57.4754 | 57.4754 | 57.4754
85% | 40.4636 | 38.7203 | 41.6145 | 41.9053 | 41.7628 | 41.8983 | 41.954 | 42.1325 | 42.4995 | 42.8083 | 42.9504 | 42.8238 | 43.3549 | 43.4391 | 43.3394 | 43.5393 | 43.6328 | 43.6328 | 43.6328 | 43.6328 | 43.6328 | 43.6328 | 43.6328 | 43.6328 | 43.6328 | 43.6328 | 43.6328 | 43.6328 | 43.6328 | 43.6328 | 43.6328 | 85% | 1.1345 | 47.6349 | 50.8694 | 50.9586 | 50.8624 | 50.8871 | 51.0637 | 51.4217 | 52.0521 | 52.3805 | 52.6182 | 52.9778 | 53.437 | 53.9922 | 54.2832 | 54.1889 | 54.2824 | 54.2824 | 54.2824 | 54.2824 | 54.2824 | 54.2824 | 54.2824 | 54.2824 | 54.2824 | 54.2824 | 54.2824 | 54.2824 | 54.2824 | 54.2824 | 54.2824
80% | 94.5411 | 36.4427 | 39.1666 | 39.4403 | 39.3061 | 39.4337 | 39.4861 | 39.6541 | 39.9996 | 40.2902 | 40.4239 | 40.3047 | 40.8046 | 40.8839 | 40.7901 | 40.9782 | 41.0662 | 41.0662 | 41.0662 | 41.0662 | 41.0662 | 41.0662 | 41.0662 | 41.0662 | 41.0662 | 41.0662 | 41.0662 | 41.0662 | 41.0662 | 41.0662 | 41.0662 | 80% | 2.6471 | 44.8329 | 47.877 | 47.961 | 47.8705 | 47.8938 | 48.06 | 48.3969 | 48.9902 | 49.2993 | 49.523 | 49.8615 | 50.2936 | 50.8162 | 51.0901 | 51.0013 | 51.0893 | 51.0893 | 51.0893 | 51.0893 | 51.0893 | 51.0893 | 51.0893 | 51.0893 | 51.0893 | 51.0893 | 51.0893 | 51.0893 | 51.0893 | 51.0893 | 51.0893
75% | 197.0236 | 34.165 | 36.7187 | 36.9753 | 36.8495 | 36.9691 | 37.0182 | 37.1757 | 37.4996 | 37.772 | 37.8974 | 37.7857 | 38.2543 | 38.3286 | 38.2407 | 38.4171 | 38.4996 | 38.4996 | 38.4996 | 38.4996 | 38.4996 | 38.4996 | 38.4996 | 38.4996 | 38.4996 | 38.4996 | 38.4996 | 38.4996 | 38.4996 | 38.4996 | 38.4996 | 75% | 3.4035 | 42.0308 | 44.8847 | 44.9635 | 44.8786 | 44.9004 | 45.0562 | 45.3721 | 45.9283 | 46.2181 | 46.4278 | 46.7451 | 47.1503 | 47.6402 | 47.8969 | 47.8137 | 47.8962 | 47.8962 | 47.8962 | 47.8962 | 47.8962 | 47.8962 | 47.8962 | 47.8962 | 47.8962 | 47.8962 | 47.8962 | 47.8962 | 47.8962 | 47.8962 | 47.8962
70% | 336.9444 | 31.8873 | 34.2708 | 34.5103 | 34.3929 | 34.5045 | 34.5504 | 34.6974 | 34.9996 | 35.2539 | 35.371 | 35.2666 | 35.704 | 35.7734 | 35.6913 | 35.8559 | 35.9329 | 35.9329 | 35.9329 | 35.9329 | 35.9329 | 35.9329 | 35.9329 | 35.9329 | 35.9329 | 35.9329 | 35.9329 | 35.9329 | 35.9329 | 35.9329 | 35.9329 | 70% | 5.6725 | 39.2288 | 41.8924 | 41.9659 | 41.8867 | 41.907 | 42.0525 | 42.3473 | 42.8664 | 43.1369 | 43.3326 | 43.6288 | 44.0069 | 44.4642 | 44.7038 | 44.6261 | 44.7031 | 44.7031 | 44.7031 | 44.7031 | 44.7031 | 44.7031 | 44.7031 | 44.7031 | 44.7031 | 44.7031 | 44.7031 | 44.7031 | 44.7031 | 44.7031 | 44.7031
65% | 521.4885 | 29.6097 | 31.8228 | 32.0452 | 31.9362 | 32.0399 | 32.0825 | 32.219 | 32.4996 | 32.7358 | 32.8445 | 32.7476 | 33.1537 | 33.2182 | 33.1419 | 33.2948 | 33.3663 | 33.3663 | 33.3663 | 33.3663 | 33.3663 | 33.3663 | 33.3663 | 33.3663 | 33.3663 | 33.3663 | 33.3663 | 33.3663 | 33.3663 | 33.3663 | 33.3663 | 65% | 6.4288 | 36.4267 | 38.9001 | 38.9683 | 38.8948 | 38.9137 | 39.0487 | 39.3225 | 39.8045 | 40.0557 | 40.2374 | 40.5125 | 40.8636 | 41.2882 | 41.5107 | 41.4385 | 41.51 | 41.51 | 41.51 | 41.51 | 41.51 | 41.51 | 41.51 | 41.51 | 41.51 | 41.51 | 41.51 | 41.51 | 41.51 | 41.51 | 41.51
60% | 812.675 | 27.332 | 29.3749 | 29.5802 | 29.4796 | 29.5753 | 29.6146 | 29.7406 | 29.9997 | 30.2176 | 30.318 | 30.2285 | 30.6035 | 30.6629 | 30.5925 | 30.7337 | 30.7997 | 30.7997 | 30.7997 | 30.7997 | 30.7997 | 30.7997 | 30.7997 | 30.7997 | 30.7997 | 30.7997 | 30.7997 | 30.7997 | 30.7997 | 30.7997 | 30.7997 | 60% | 11.3449 | 33.6247 | 35.9078 | 35.9708 | 35.9029 | 35.9203 | 36.045 | 36.2977 | 36.7426 | 36.9745 | 37.1422 | 37.3961 | 37.7202 | 38.1122 | 38.3176 | 38.251 | 38.317 | 38.317 | 38.317 | 38.317 | 38.317 | 38.317 | 38.317 | 38.317 | 38.317 | 38.317 | 38.317 | 38.317 | 38.317 | 38.317 | 38.317
55% | 1202.1843 | 25.0543 | 26.927 | 27.1152 | 27.023 | 27.1107 | 27.1467 | 27.2622 | 27.4997 | 27.6995 | 27.7915 | 27.7095 | 28.0532 | 28.1077 | 28.0432 | 28.1725 | 28.233 | 28.233 | 28.233 | 28.233 | 28.233 | 28.233 | 28.233 | 28.233 | 28.233 | 28.233 | 28.233 | 28.233 | 28.233 | 28.233 | 28.233 | 55% | 35.5474 | 30.8226 | 32.9155 | 32.9732 | 32.911 | 32.927 | 33.0412 | 33.2729 | 33.6808 | 33.8933 | 34.0471 | 34.2798 | 34.5769 | 34.9361 | 35.1244 | 35.0634 | 35.1239 | 35.1239 | 35.1239 | 35.1239 | 35.1239 | 35.1239 | 35.1239 | 35.1239 | 35.1239 | 35.1239 | 35.1239 | 35.1239 | 35.1239 | 35.1239 | 35.1239
50% | 1686.2345 | 22.7767 | 24.4791 | 24.6502 | 24.5663 | 24.6461 | 24.6788 | 24.7838 | 24.9997 | 25.1814 | 25.265 | 25.1904 | 25.5029 | 25.5524 | 25.4938 | 25.6114 | 25.6664 | 25.6664 | 25.6664 | 25.6664 | 25.6664 | 25.6664 | 25.6664 | 25.6664 | 25.6664 | 25.6664 | 25.6664 | 25.6664 | 25.6664 | 25.6664 | 25.6664 | 50% | 95.2974 | 28.0206 | 29.9231 | 29.9756 | 29.919 | 29.9336 | 30.0375 | 30.2481 | 30.6189 | 30.8121 | 30.9519 | 31.1634 | 31.4335 | 31.7601 | 31.9313 | 31.8758 | 31.9308 | 31.9308 | 31.9308 | 31.9308 | 31.9308 | 31.9308 | 31.9308 | 31.9308 | 31.9308 | 31.9308 | 31.9308 | 31.9308 | 31.9308 | 31.9308 | 31.9308
45% | 2129.0649 | 20.499 | 22.0312 | 22.1852 | 22.1097 | 22.1815 | 22.2109 | 22.3054 | 22.4998 | 22.6632 | 22.7385 | 22.6714 | 22.9526 | 22.9972 | 22.9444 | 23.0502 | 23.0997 | 23.0997 | 23.0997 | 23.0997 | 23.0997 | 23.0997 | 23.0997 | 23.0997 | 23.0997 | 23.0997 | 23.0997 | 23.0997 | 23.0997 | 23.0997 | 23.0997 | 45% | 208.7467 | 25.2185 | 26.9308 | 26.9781 | 26.9271 | 26.9402 | 27.0337 | 27.2232 | 27.557 | 27.7309 | 27.8567 | 28.0471 | 28.2902 | 28.5841 | 28.7382 | 28.6882 | 28.7377 | 28.7377 | 28.7377 | 28.7377 | 28.7377 | 28.7377 | 28.7377 | 28.7377 | 28.7377 | 28.7377 | 28.7377 | 28.7377 | 28.7377 | 28.7377 | 28.7377
40% | 2484.5393 | 18.2213 | 19.5833 | 19.7201 | 19.6531 | 19.7169 | 19.7431 | 19.8271 | 19.9998 | 20.1451 | 20.212 | 20.1524 | 20.4023 | 20.4419 | 20.395 | 20.4891 | 20.5331 | 20.5331 | 20.5331 | 20.5331 | 20.5331 | 20.5331 | 20.5331 | 20.5331 | 20.5331 | 20.5331 | 20.5331 | 20.5331 | 20.5331 | 20.5331 | 20.5331 | 40% | 380.4333 | 22.4164 | 23.9385 | 23.9805 | 23.9352 | 23.9469 | 24.03 | 24.1984 | 24.4951 | 24.6497 | 24.7615 | 24.9307 | 25.1468 | 25.4081 | 25.545 | 25.5006 | 25.5446 | 25.5446 | 25.5446 | 25.5446 | 25.5446 | 25.5446 | 25.5446 | 25.5446 | 25.5446 | 25.5446 | 25.5446 | 25.5446 | 25.5446 | 25.5446 | 25.5446
35% | 2808.248 | 15.9437 | 17.1354 | 17.2551 | 17.1964 | 17.2522 | 17.2752 | 17.3487 | 17.4998 | 17.6269 | 17.6855 | 17.6333 | 17.852 | 17.8867 | 17.8457 | 17.928 | 17.9665 | 17.9665 | 17.9665 | 17.9665 | 17.9665 | 17.9665 | 17.9665 | 17.9665 | 17.9665 | 17.9665 | 17.9665 | 17.9665 | 17.9665 | 17.9665 | 17.9665 | 35% | 696.5786 | 19.6144 | 20.9462 | 20.983 | 20.9433 | 20.9535 | 21.0262 | 21.1736 | 21.4332 | 21.5685 | 21.6663 | 21.8144 | 22.0035 | 22.2321 | 22.3519 | 22.3131 | 22.3516 | 22.3516 | 22.3516 | 22.3516 | 22.3516 | 22.3516 | 22.3516 | 22.3516 | 22.3516 | 22.3516 | 22.3516 | 22.3516 | 22.3516 | 22.3516 | 22.3516
30% | 3095.6528 | 13.666 | 14.6875 | 14.7901 | 14.7398 | 14.7876 | 14.8073 | 14.8703 | 14.9998 | 15.1088 | 15.159 | 15.1143 | 15.3017 | 15.3315 | 15.2963 | 15.3668 | 15.3998 | 15.3998 | 15.3998 | 15.3998 | 15.3998 | 15.3998 | 15.3998 | 15.3998 | 15.3998 | 15.3998 | 15.3998 | 15.3998 | 15.3998 | 15.3998 | 15.3998 | 30% | 1260.7997 | 16.8123 | 17.9539 | 17.9854 | 17.9514 | 17.9602 | 18.0225 | 18.1488 | 18.3713 | 18.4873 | 18.5711 | 18.6981 | 18.8601 | 19.0561 | 19.1588 | 19.1255 | 19.1585 | 19.1585 | 19.1585 | 19.1585 | 19.1585 | 19.1585 | 19.1585 | 19.1585 | 19.1585 | 19.1585 | 19.1585 | 19.1585 | 19.1585 | 19.1585 | 19.1585
25% | 3358.8552 | 11.3883 | 12.2396 | 12.3251 | 12.2832 | 12.323 | 12.3394 | 12.3919 | 12.4999 | 12.5907 | 12.6325 | 12.5952 | 12.7514 | 12.7762 | 12.7469 | 12.8057 | 12.8332 | 12.8332 | 12.8332 | 12.8332 | 12.8332 | 12.8332 | 12.8332 | 12.8332 | 12.8332 | 12.8332 | 12.8332 | 12.8332 | 12.8332 | 12.8332 | 12.8332 | 25% | 1965.3198 | 14.0103 | 14.9616 | 14.9878 | 14.9595 | 14.9668 | 15.0187 | 15.124 | 15.3094 | 15.406 | 15.4759 | 15.5817 | 15.7168 | 15.8801 | 15.9656 | 15.9379 | 15.9654 | 15.9654 | 15.9654 | 15.9654 | 15.9654 | 15.9654 | 15.9654 | 15.9654 | 15.9654 | 15.9654 | 15.9654 | 15.9654 | 15.9654 | 15.9654 | 15.9654
20% | 3588.7791 | 9.1107 | 9.7916 | 9.8601 | 9.8265 | 9.8584 | 9.8715 | 9.9135 | 9.9999 | 10.0725 | 10.106 | 10.0762 | 10.2012 | 10.221 | 10.1975 | 10.2446 | 10.2666 | 10.2666 | 10.2666 | 10.2666 | 10.2666 | 10.2666 | 10.2666 | 10.2666 | 10.2666 | 10.2666 | 10.2666 | 10.2666 | 10.2666 | 10.2666 | 10.2666 | 20% | 2490.2118 | 11.2082 | 11.9693 | 11.9903 | 11.9676 | 11.9734 | 12.015 | 12.0992 | 12.2475 | 12.3248 | 12.3807 | 12.4654 | 12.5734 | 12.7041 | 12.7725 | 12.7503 | 12.7723 | 12.7723 | 12.7723 | 12.7723 | 12.7723 | 12.7723 | 12.7723 | 12.7723 | 12.7723 | 12.7723 | 12.7723 | 12.7723 | 12.7723 | 12.7723 | 12.7723
15% | 3802.4419 | 6.833 | 7.3437 | 7.3951 | 7.3699 | 7.3938 | 7.4036 | 7.4351 | 7.4999 | 7.5544 | 7.5795 | 7.5571 | 7.6509 | 7.6657 | 7.6481 | 7.6834 | 7.6999 | 7.6999 | 7.6999 | 7.6999 | 7.6999 | 7.6999 | 7.6999 | 7.6999 | 7.6999 | 7.6999 | 7.6999 | 7.6999 | 7.6999 | 7.6999 | 7.6999 | 15% | 2997.7083 | 8.4062 | 8.9769 | 8.9927 | 8.9757 | 8.9801 | 9.0112 | 9.0744 | 9.1857 | 9.2436 | 9.2856 | 9.349 | 9.4301 | 9.528 | 9.5794 | 9.5627 | 9.5792 | 9.5792 | 9.5792 | 9.5792 | 9.5792 | 9.5792 | 9.5792 | 9.5792 | 9.5792 | 9.5792 | 9.5792 | 9.5792 | 9.5792 | 9.5792 | 9.5792
10% | 4024.8025 | 4.5553 | 4.8958 | 4.93 | 4.9133 | 4.9292 | 4.9358 | 4.9568 | 4.9999 | 5.0363 | 5.053 | 5.0381 | 5.1006 | 5.1105 | 5.0988 | 5.1223 | 5.1333 | 5.1333 | 5.1333 | 5.1333 | 5.1333 | 5.1333 | 5.1333 | 5.1333 | 5.1333 | 5.1333 | 5.1333 | 5.1333 | 5.1333 | 5.1333 | 5.1333 | 10% | 3491.5908 | 5.6041 | 5.9846 | 5.9951 | 5.9838 | 5.9867 | 6.0075 | 6.0496 | 6.1238 | 6.1624 | 6.1904 | 6.2327 | 6.2867 | 6.352 | 6.3863 | 6.3752 | 6.3862 | 6.3862 | 6.3862 | 6.3862 | 6.3862 | 6.3862 | 6.3862 | 6.3862 | 6.3862 | 6.3862 | 6.3862 | 6.3862 | 6.3862 | 6.3862 | 6.3862
5% | 4239.978 | 2.2777 | 2.4479 | 2.465 | 2.4566 | 2.4646 | 2.4679 | 2.4784 | 2.5 | 2.5181 | 2.5265 | 2.519 | 2.5503 | 2.5552 | 2.5494 | 2.5611 | 2.5666 | 2.5666 | 2.5666 | 2.5666 | 2.5666 | 2.5666 | 2.5666 | 2.5666 | 2.5666 | 2.5666 | 2.5666 | 2.5666 | 2.5666 | 2.5666 | 2.5666 | 5% | 3955.9766 | 2.8021 | 2.9923 | 2.9976 | 2.9919 | 2.9934 | 3.0037 | 3.0248 | 3.0619 | 3.0812 | 3.0952 | 3.1163 | 3.1434 | 3.176 | 3.1931 | 3.1876 | 3.1931 | 3.1931 | 3.1931 | 3.1931 | 3.1931 | 3.1931 | 3.1931 | 3.1931 | 3.1931 | 3.1931 | 3.1931 | 3.1931 | 3.1931 | 3.1931 | 3.1931
9.992e-14% | 4391.6218 | 4.5517e-14 | 4.8919e-14 | 4.9261e-14 | 4.9093e-14 | 4.9253e-14 | 4.9318e-14 | 4.9528e-14 | 4.9959e-14 | 5.0322e-14 | 5.049e-14 | 5.0341e-14 | 5.0965e-14 | 5.1064e-14 | 5.0947e-14 | 5.1182e-14 | 5.1292e-14 | 5.1292e-14 | 5.1292e-14 | 5.1292e-14 | 5.1292e-14 | 5.1292e-14 | 5.1292e-14 | 5.1292e-14 | 5.1292e-14 | 5.1292e-14 | 5.1292e-14 | 5.1292e-14 | 5.1292e-14 | 5.1292e-14 | 5.1292e-14 | 9.992e-14% | 4391.6218 | 5.5996e-14 | 5.9798e-14 | 5.9903e-14 | 5.979e-14 | 5.9819e-14 | 6.0027e-14 | 6.0448e-14 | 6.1189e-14 | 6.1575e-14 | 6.1854e-14 | 6.2277e-14 | 6.2817e-14 | 6.3469e-14 | 6.3812e-14 | 6.3701e-14 | 6.3811e-14 | 6.3811e-14 | 6.3811e-14 | 6.3811e-14 | 6.3811e-14 | 6.3811e-14 | 6.3811e-14 | 6.3811e-14 | 6.3811e-14 | 6.3811e-14 | 6.3811e-14 | 6.3811e-14 | 6.3811e-14 | 6.3811e-14 | 6.3811e-14
Option 4
Winter Season | [31 empty] | Winter Season
P50 | [31 empty] | P10
% of MD | Winter - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Winter - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 43.3628 | 47.9013 | 48.3825 | -17.0225 | -16.2326 | -15.4837 | -14.175 | -10.8834 | -9.113 | -10.4046 | -6.406 | -5.6856 | -5.1677 | -2.7266 | -2.3293 | -2.3293 | -2.3293 | -2.3293 | -2.3293 | -2.3293 | -2.3293 | -2.3293 | -2.3293 | -2.3293 | -2.3293 | -2.3293 | -2.3293 | -2.3293 | -2.3293 | -2.3293 | 100% | 0 | 47.5339 | 51.863 | 52.3113 | -12.1415 | -12.1792 | -11.839 | -10.5084 | -6.6854 | -5.1078 | -6.6011 | -2.476 | -4.208 | -2.6496 | -1.5266 | -1.988 | -1.988 | -1.988 | -1.988 | -1.988 | -1.988 | -1.988 | -1.988 | -1.988 | -1.988 | -1.988 | -1.988 | -1.988 | -1.988 | -1.988 | -1.988
99% | 0.2972 | 42.9291 | 47.4223 | 47.8987 | -16.8523 | -16.0703 | -15.3289 | -14.0332 | -10.7746 | -9.0218 | -10.3005 | -6.3419 | -5.6287 | -5.116 | -2.6994 | -2.306 | -2.306 | -2.306 | -2.306 | -2.306 | -2.306 | -2.306 | -2.306 | -2.306 | -2.306 | -2.306 | -2.306 | -2.306 | -2.306 | -2.306 | -2.306 | 99% | 0.2972 | 47.0586 | 51.3443 | 51.7882 | -12.0201 | -12.0574 | -11.7206 | -10.4033 | -6.6186 | -5.0567 | -6.5351 | -2.4513 | -4.1659 | -2.6231 | -1.5113 | -1.9681 | -1.9681 | -1.9681 | -1.9681 | -1.9681 | -1.9681 | -1.9681 | -1.9681 | -1.9681 | -1.9681 | -1.9681 | -1.9681 | -1.9681 | -1.9681 | -1.9681 | -1.9681
98% | 0.2972 | 42.4955 | 46.9432 | 47.4149 | -16.6821 | -15.9079 | -15.174 | -13.8915 | -10.6657 | -8.9307 | -10.1965 | -6.2779 | -5.5719 | -5.0644 | -2.6721 | -2.2827 | -2.2827 | -2.2827 | -2.2827 | -2.2827 | -2.2827 | -2.2827 | -2.2827 | -2.2827 | -2.2827 | -2.2827 | -2.2827 | -2.2827 | -2.2827 | -2.2827 | -2.2827 | 98% | 0.2972 | 46.5832 | 50.8257 | 51.2651 | -11.8987 | -11.9357 | -11.6022 | -10.2982 | -6.5517 | -5.0057 | -6.4691 | -2.4265 | -4.1238 | -2.5966 | -1.496 | -1.9482 | -1.9482 | -1.9482 | -1.9482 | -1.9482 | -1.9482 | -1.9482 | -1.9482 | -1.9482 | -1.9482 | -1.9482 | -1.9482 | -1.9482 | -1.9482 | -1.9482 | -1.9482
97% | 0.2972 | 42.0619 | 46.4642 | 46.931 | -16.5118 | -15.7456 | -15.0192 | -13.7497 | -10.5569 | -8.8396 | -10.0924 | -6.2138 | -5.515 | -5.0127 | -2.6448 | -2.2594 | -2.2594 | -2.2594 | -2.2594 | -2.2594 | -2.2594 | -2.2594 | -2.2594 | -2.2594 | -2.2594 | -2.2594 | -2.2594 | -2.2594 | -2.2594 | -2.2594 | -2.2594 | 97% | 0.2972 | 46.1079 | 50.3071 | 50.7419 | -11.7773 | -11.8139 | -11.4838 | -10.1931 | -6.4848 | -4.9546 | -6.4031 | -2.4017 | -4.0817 | -2.5701 | -1.4808 | -1.9283 | -1.9283 | -1.9283 | -1.9283 | -1.9283 | -1.9283 | -1.9283 | -1.9283 | -1.9283 | -1.9283 | -1.9283 | -1.9283 | -1.9283 | -1.9283 | -1.9283 | -1.9283
95% | 1.486 | 41.1946 | 45.5062 | 45.9634 | -16.1714 | -15.4209 | -14.7095 | -13.4662 | -10.3392 | -8.6573 | -9.8843 | -6.0857 | -5.4013 | -4.9093 | -2.5903 | -2.2129 | -2.2129 | -2.2129 | -2.2129 | -2.2129 | -2.2129 | -2.2129 | -2.2129 | -2.2129 | -2.2129 | -2.2129 | -2.2129 | -2.2129 | -2.2129 | -2.2129 | -2.2129 | 95% | 1.486 | 45.1572 | 49.2698 | 49.6957 | -11.5345 | -11.5703 | -11.2471 | -9.983 | -6.3511 | -4.8524 | -6.2711 | -2.3522 | -3.9976 | -2.5171 | -1.4502 | -1.8886 | -1.8886 | -1.8886 | -1.8886 | -1.8886 | -1.8886 | -1.8886 | -1.8886 | -1.8886 | -1.8886 | -1.8886 | -1.8886 | -1.8886 | -1.8886 | -1.8886 | -1.8886
90% | 8.6188 | 39.0265 | 43.1111 | 43.5443 | -15.3203 | -14.6093 | -13.9353 | -12.7575 | -9.7951 | -8.2017 | -9.3641 | -5.7654 | -5.117 | -4.6509 | -2.454 | -2.0964 | -2.0964 | -2.0964 | -2.0964 | -2.0964 | -2.0964 | -2.0964 | -2.0964 | -2.0964 | -2.0964 | -2.0964 | -2.0964 | -2.0964 | -2.0964 | -2.0964 | -2.0964 | 90% | 8.6188 | 42.7805 | 46.6767 | 47.0802 | -10.9274 | -10.9613 | -10.6551 | -9.4575 | -6.0169 | -4.597 | -5.941 | -2.2284 | -3.7872 | -2.3846 | -1.3739 | -1.7892 | -1.7892 | -1.7892 | -1.7892 | -1.7892 | -1.7892 | -1.7892 | -1.7892 | -1.7892 | -1.7892 | -1.7892 | -1.7892 | -1.7892 | -1.7892 | -1.7892 | -1.7892
85% | 40.1218 | 36.8584 | 40.7161 | 41.1251 | -14.4691 | -13.7977 | -13.1611 | -12.0487 | -9.2509 | -7.746 | -8.8439 | -5.4451 | -4.8327 | -4.3926 | -2.3177 | -1.9799 | -1.9799 | -1.9799 | -1.9799 | -1.9799 | -1.9799 | -1.9799 | -1.9799 | -1.9799 | -1.9799 | -1.9799 | -1.9799 | -1.9799 | -1.9799 | -1.9799 | -1.9799 | 85% | 40.1218 | 40.4038 | 44.0835 | 44.4646 | -10.3203 | -10.3523 | -10.0632 | -8.9321 | -5.6826 | -4.3417 | -5.611 | -2.1046 | -3.5768 | -2.2521 | -1.2976 | -1.6898 | -1.6898 | -1.6898 | -1.6898 | -1.6898 | -1.6898 | -1.6898 | -1.6898 | -1.6898 | -1.6898 | -1.6898 | -1.6898 | -1.6898 | -1.6898 | -1.6898 | -1.6898
80% | 93.0231 | 34.6902 | 38.321 | 38.706 | -13.618 | -12.9861 | -12.387 | -11.34 | -8.7067 | -7.2904 | -8.3236 | -5.1248 | -4.5485 | -4.1342 | -2.1813 | -1.8635 | -1.8635 | -1.8635 | -1.8635 | -1.8635 | -1.8635 | -1.8635 | -1.8635 | -1.8635 | -1.8635 | -1.8635 | -1.8635 | -1.8635 | -1.8635 | -1.8635 | -1.8635 | 80% | 93.0231 | 38.0271 | 41.4904 | 41.849 | -9.7132 | -9.7434 | -9.4712 | -8.4067 | -5.3483 | -4.0863 | -5.2809 | -1.9808 | -3.3664 | -2.1197 | -1.2213 | -1.5904 | -1.5904 | -1.5904 | -1.5904 | -1.5904 | -1.5904 | -1.5904 | -1.5904 | -1.5904 | -1.5904 | -1.5904 | -1.5904 | -1.5904 | -1.5904 | -1.5904 | -1.5904
75% | 197.0426 | 32.5221 | 35.926 | 36.2869 | -12.7669 | -12.1744 | -11.6128 | -10.6312 | -8.1626 | -6.8347 | -7.8034 | -4.8045 | -4.2642 | -3.8758 | -2.045 | -1.747 | -1.747 | -1.747 | -1.747 | -1.747 | -1.747 | -1.747 | -1.747 | -1.747 | -1.747 | -1.747 | -1.747 | -1.747 | -1.747 | -1.747 | -1.747 | 75% | 197.0426 | 35.6504 | 38.8972 | 39.2335 | -9.1061 | -9.1344 | -8.8793 | -7.8813 | -5.0141 | -3.8309 | -4.9509 | -1.857 | -3.156 | -1.9872 | -1.1449 | -1.491 | -1.491 | -1.491 | -1.491 | -1.491 | -1.491 | -1.491 | -1.491 | -1.491 | -1.491 | -1.491 | -1.491 | -1.491 | -1.491 | -1.491 | -1.491
70% | 378.0365 | 30.3539 | 33.5309 | 33.8678 | -11.9158 | -11.3628 | -10.8386 | -9.9225 | -7.6184 | -6.3791 | -7.2832 | -4.4842 | -3.9799 | -3.6174 | -1.9087 | -1.6305 | -1.6305 | -1.6305 | -1.6305 | -1.6305 | -1.6305 | -1.6305 | -1.6305 | -1.6305 | -1.6305 | -1.6305 | -1.6305 | -1.6305 | -1.6305 | -1.6305 | -1.6305 | 70% | 378.0365 | 33.2737 | 36.3041 | 36.6179 | -8.4991 | -8.5255 | -8.2873 | -7.3559 | -4.6798 | -3.5755 | -4.6208 | -1.7332 | -2.9456 | -1.8547 | -1.0686 | -1.3916 | -1.3916 | -1.3916 | -1.3916 | -1.3916 | -1.3916 | -1.3916 | -1.3916 | -1.3916 | -1.3916 | -1.3916 | -1.3916 | -1.3916 | -1.3916 | -1.3916 | -1.3916
65% | 616.0926 | 28.1858 | 31.1358 | 31.4486 | -11.0646 | -10.5512 | -10.0644 | -9.2137 | -7.0742 | -5.9234 | -6.763 | -4.1639 | -3.6956 | -3.359 | -1.7723 | -1.5141 | -1.5141 | -1.5141 | -1.5141 | -1.5141 | -1.5141 | -1.5141 | -1.5141 | -1.5141 | -1.5141 | -1.5141 | -1.5141 | -1.5141 | -1.5141 | -1.5141 | -1.5141 | 65% | 616.0926 | 30.897 | 33.7109 | 34.0023 | -7.892 | -7.9165 | -7.6954 | -6.8304 | -4.3455 | -3.3201 | -4.2907 | -1.6094 | -2.7352 | -1.7222 | -0.99227 | -1.2922 | -1.2922 | -1.2922 | -1.2922 | -1.2922 | -1.2922 | -1.2922 | -1.2922 | -1.2922 | -1.2922 | -1.2922 | -1.2922 | -1.2922 | -1.2922 | -1.2922 | -1.2922
60% | 934.9866 | 26.0177 | 28.7408 | 29.0295 | -10.2135 | -9.7395 | -9.2902 | -8.505 | -6.53 | -5.4678 | -6.2427 | -3.8436 | -3.4113 | -3.1006 | -1.636 | -1.3976 | -1.3976 | -1.3976 | -1.3976 | -1.3976 | -1.3976 | -1.3976 | -1.3976 | -1.3976 | -1.3976 | -1.3976 | -1.3976 | -1.3976 | -1.3976 | -1.3976 | -1.3976 | 60% | 934.9866 | 28.5203 | 31.1178 | 31.3868 | -7.2849 | -7.3075 | -7.1034 | -6.305 | -4.0112 | -3.0647 | -3.9607 | -1.4856 | -2.5248 | -1.5897 | -0.91594 | -1.1928 | -1.1928 | -1.1928 | -1.1928 | -1.1928 | -1.1928 | -1.1928 | -1.1928 | -1.1928 | -1.1928 | -1.1928 | -1.1928 | -1.1928 | -1.1928 | -1.1928 | -1.1928
55% | 1310.9428 | 23.8495 | 26.3457 | 26.6104 | -9.3624 | -8.9279 | -8.516 | -7.7962 | -5.9859 | -5.0121 | -5.7225 | -3.5233 | -3.1271 | -2.8422 | -1.4997 | -1.2811 | -1.2811 | -1.2811 | -1.2811 | -1.2811 | -1.2811 | -1.2811 | -1.2811 | -1.2811 | -1.2811 | -1.2811 | -1.2811 | -1.2811 | -1.2811 | -1.2811 | -1.2811 | 55% | 1310.9428 | 26.1436 | 28.5246 | 28.7712 | -6.6778 | -6.6986 | -6.5115 | -5.7796 | -3.677 | -2.8093 | -3.6306 | -1.3618 | -2.3144 | -1.4573 | -0.83962 | -1.0934 | -1.0934 | -1.0934 | -1.0934 | -1.0934 | -1.0934 | -1.0934 | -1.0934 | -1.0934 | -1.0934 | -1.0934 | -1.0934 | -1.0934 | -1.0934 | -1.0934 | -1.0934
50% | 1730.2899 | 21.6814 | 23.9506 | 24.1913 | -8.5113 | -8.1163 | -7.7418 | -7.0875 | -5.4417 | -4.5565 | -5.2023 | -3.203 | -2.8428 | -2.5839 | -1.3633 | -1.1647 | -1.1647 | -1.1647 | -1.1647 | -1.1647 | -1.1647 | -1.1647 | -1.1647 | -1.1647 | -1.1647 | -1.1647 | -1.1647 | -1.1647 | -1.1647 | -1.1647 | -1.1647 | 50% | 1730.2899 | 23.7669 | 25.9315 | 26.1556 | -6.0708 | -6.0896 | -5.9195 | -5.2542 | -3.3427 | -2.5539 | -3.3006 | -1.238 | -2.104 | -1.3248 | -0.76329 | -0.99398 | -0.99398 | -0.99398 | -0.99398 | -0.99398 | -0.99398 | -0.99398 | -0.99398 | -0.99398 | -0.99398 | -0.99398 | -0.99398 | -0.99398 | -0.99398 | -0.99398 | -0.99398
45% | 2168.0633 | 19.5132 | 21.5556 | 21.7721 | -7.6601 | -7.3047 | -6.9677 | -6.3787 | -4.8975 | -4.1008 | -4.6821 | -2.8827 | -2.5585 | -2.3255 | -1.227 | -1.0482 | -1.0482 | -1.0482 | -1.0482 | -1.0482 | -1.0482 | -1.0482 | -1.0482 | -1.0482 | -1.0482 | -1.0482 | -1.0482 | -1.0482 | -1.0482 | -1.0482 | -1.0482 | 45% | 2168.0633 | 21.3903 | 23.3383 | 23.5401 | -5.4637 | -5.4807 | -5.3276 | -4.7288 | -3.0084 | -2.2985 | -2.9705 | -1.1142 | -1.8936 | -1.1923 | -0.68696 | -0.89458 | -0.89458 | -0.89458 | -0.89458 | -0.89458 | -0.89458 | -0.89458 | -0.89458 | -0.89458 | -0.89458 | -0.89458 | -0.89458 | -0.89458 | -0.89458 | -0.89458 | -0.89458
40% | 2609.7004 | 17.3451 | 19.1605 | 19.353 | -6.809 | -6.493 | -6.1935 | -5.67 | -4.3534 | -3.6452 | -4.1618 | -2.5624 | -2.2742 | -2.0671 | -1.0907 | -0.93173 | -0.93173 | -0.93173 | -0.93173 | -0.93173 | -0.93173 | -0.93173 | -0.93173 | -0.93173 | -0.93173 | -0.93173 | -0.93173 | -0.93173 | -0.93173 | -0.93173 | -0.93173 | 40% | 2609.7004 | 19.0136 | 20.7452 | 20.9245 | -4.8566 | -4.8717 | -4.7356 | -4.2034 | -2.6742 | -2.0431 | -2.6405 | -0.99041 | -1.6832 | -1.0598 | -0.61063 | -0.79518 | -0.79518 | -0.79518 | -0.79518 | -0.79518 | -0.79518 | -0.79518 | -0.79518 | -0.79518 | -0.79518 | -0.79518 | -0.79518 | -0.79518 | -0.79518 | -0.79518 | -0.79518
35% | 2998.1389 | 15.177 | 16.7654 | 16.9339 | -5.9579 | -5.6814 | -5.4193 | -4.9612 | -3.8092 | -3.1895 | -3.6416 | -2.2421 | -1.9899 | -1.8087 | -0.95433 | -0.81526 | -0.81526 | -0.81526 | -0.81526 | -0.81526 | -0.81526 | -0.81526 | -0.81526 | -0.81526 | -0.81526 | -0.81526 | -0.81526 | -0.81526 | -0.81526 | -0.81526 | -0.81526 | 35% | 2998.1389 | 16.6369 | 18.152 | 18.3089 | -4.2495 | -4.2627 | -4.1437 | -3.6779 | -2.3399 | -1.7877 | -2.3104 | -0.86661 | -1.4728 | -0.92735 | -0.5343 | -0.69579 | -0.69579 | -0.69579 | -0.69579 | -0.69579 | -0.69579 | -0.69579 | -0.69579 | -0.69579 | -0.69579 | -0.69579 | -0.69579 | -0.69579 | -0.69579 | -0.69579 | -0.69579
30% | 3309.3057 | 13.0088 | 14.3704 | 14.5148 | -5.1068 | -4.8698 | -4.6451 | -4.2525 | -3.265 | -2.7339 | -3.1214 | -1.9218 | -1.7057 | -1.5503 | -0.81799 | -0.6988 | -0.6988 | -0.6988 | -0.6988 | -0.6988 | -0.6988 | -0.6988 | -0.6988 | -0.6988 | -0.6988 | -0.6988 | -0.6988 | -0.6988 | -0.6988 | -0.6988 | -0.6988 | 30% | 3309.3057 | 14.2602 | 15.5589 | 15.6934 | -3.6425 | -3.6538 | -3.5517 | -3.1525 | -2.0056 | -1.5323 | -1.9803 | -0.74281 | -1.2624 | -0.79487 | -0.45797 | -0.59639 | -0.59639 | -0.59639 | -0.59639 | -0.59639 | -0.59639 | -0.59639 | -0.59639 | -0.59639 | -0.59639 | -0.59639 | -0.59639 | -0.59639 | -0.59639 | -0.59639 | -0.59639
25% | 3537.8514 | 10.8407 | 11.9753 | 12.0956 | -4.2556 | -4.0581 | -3.8709 | -3.5437 | -2.7209 | -2.2782 | -2.6011 | -1.6015 | -1.4214 | -1.2919 | -0.68166 | -0.58233 | -0.58233 | -0.58233 | -0.58233 | -0.58233 | -0.58233 | -0.58233 | -0.58233 | -0.58233 | -0.58233 | -0.58233 | -0.58233 | -0.58233 | -0.58233 | -0.58233 | -0.58233 | 25% | 3537.8514 | 11.8835 | 12.9657 | 13.0778 | -3.0354 | -3.0448 | -2.9598 | -2.6271 | -1.6714 | -1.277 | -1.6503 | -0.61901 | -1.052 | -0.6624 | -0.38164 | -0.49699 | -0.49699 | -0.49699 | -0.49699 | -0.49699 | -0.49699 | -0.49699 | -0.49699 | -0.49699 | -0.49699 | -0.49699 | -0.49699 | -0.49699 | -0.49699 | -0.49699 | -0.49699
20% | 3731.0305 | 8.6726 | 9.5803 | 9.6765 | -3.4045 | -3.2465 | -3.0967 | -2.835 | -2.1767 | -1.8226 | -2.0809 | -1.2812 | -1.1371 | -1.0335 | -0.54533 | -0.46586 | -0.46586 | -0.46586 | -0.46586 | -0.46586 | -0.46586 | -0.46586 | -0.46586 | -0.46586 | -0.46586 | -0.46586 | -0.46586 | -0.46586 | -0.46586 | -0.46586 | -0.46586 | 20% | 3731.0305 | 9.5068 | 10.3726 | 10.4623 | -2.4283 | -2.4358 | -2.3678 | -2.1017 | -1.3371 | -1.0216 | -1.3202 | -0.49521 | -0.84159 | -0.52992 | -0.30531 | -0.39759 | -0.39759 | -0.39759 | -0.39759 | -0.39759 | -0.39759 | -0.39759 | -0.39759 | -0.39759 | -0.39759 | -0.39759 | -0.39759 | -0.39759 | -0.39759 | -0.39759 | -0.39759
15% | 3910.2412 | 6.5044 | 7.1852 | 7.2574 | -2.5534 | -2.4349 | -2.3226 | -2.1262 | -1.6325 | -1.3669 | -1.5607 | -0.9609 | -0.85284 | -0.77516 | -0.409 | -0.3494 | -0.3494 | -0.3494 | -0.3494 | -0.3494 | -0.3494 | -0.3494 | -0.3494 | -0.3494 | -0.3494 | -0.3494 | -0.3494 | -0.3494 | -0.3494 | -0.3494 | -0.3494 | 15% | 3910.2412 | 7.1301 | 7.7794 | 7.8467 | -1.8212 | -1.8269 | -1.7759 | -1.5763 | -1.0028 | -0.76617 | -0.99017 | -0.3714 | -0.6312 | -0.39744 | -0.22899 | -0.29819 | -0.29819 | -0.29819 | -0.29819 | -0.29819 | -0.29819 | -0.29819 | -0.29819 | -0.29819 | -0.29819 | -0.29819 | -0.29819 | -0.29819 | -0.29819 | -0.29819 | -0.29819
10% | 4075.1864 | 4.3363 | 4.7901 | 4.8383 | -1.7023 | -1.6233 | -1.5484 | -1.4175 | -1.0883 | -0.9113 | -1.0405 | -0.6406 | -0.56856 | -0.51677 | -0.27266 | -0.23293 | -0.23293 | -0.23293 | -0.23293 | -0.23293 | -0.23293 | -0.23293 | -0.23293 | -0.23293 | -0.23293 | -0.23293 | -0.23293 | -0.23293 | -0.23293 | -0.23293 | -0.23293 | 10% | 4075.1864 | 4.7534 | 5.1863 | 5.2311 | -1.2142 | -1.2179 | -1.1839 | -1.0508 | -0.66854 | -0.51078 | -0.66011 | -0.2476 | -0.4208 | -0.26496 | -0.15266 | -0.1988 | -0.1988 | -0.1988 | -0.1988 | -0.1988 | -0.1988 | -0.1988 | -0.1988 | -0.1988 | -0.1988 | -0.1988 | -0.1988 | -0.1988 | -0.1988 | -0.1988 | -0.1988
5% | 4251.7223 | 2.1681 | 2.3951 | 2.4191 | -0.85113 | -0.81163 | -0.77418 | -0.70875 | -0.54417 | -0.45565 | -0.52023 | -0.3203 | -0.28428 | -0.25839 | -0.13633 | -0.11647 | -0.11647 | -0.11647 | -0.11647 | -0.11647 | -0.11647 | -0.11647 | -0.11647 | -0.11647 | -0.11647 | -0.11647 | -0.11647 | -0.11647 | -0.11647 | -0.11647 | -0.11647 | 5% | 4251.7223 | 2.3767 | 2.5931 | 2.6156 | -0.60708 | -0.60896 | -0.59195 | -0.52542 | -0.33427 | -0.25539 | -0.33006 | -0.1238 | -0.2104 | -0.13248 | -0.076329 | -0.099398 | -0.099398 | -0.099398 | -0.099398 | -0.099398 | -0.099398 | -0.099398 | -0.099398 | -0.099398 | -0.099398 | -0.099398 | -0.099398 | -0.099398 | -0.099398 | -0.099398 | -0.099398
9.992e-14% | 4391.7028 | 4.3328e-14 | 4.7863e-14 | 4.8344e-14 | -1.7009e-14 | -1.622e-14 | -1.5471e-14 | -1.4164e-14 | -1.0875e-14 | -9.1057e-15 | -1.0396e-14 | -6.4009e-15 | -5.681e-15 | -5.1636e-15 | -2.7245e-15 | -2.3275e-15 | -2.3275e-15 | -2.3275e-15 | -2.3275e-15 | -2.3275e-15 | -2.3275e-15 | -2.3275e-15 | -2.3275e-15 | -2.3275e-15 | -2.3275e-15 | -2.3275e-15 | -2.3275e-15 | -2.3275e-15 | -2.3275e-15 | -2.3275e-15 | -2.3275e-15 | 9.992e-14% | 4391.7028 | 4.7496e-14 | 5.1822e-14 | 5.2269e-14 | -1.2132e-14 | -1.217e-14 | -1.183e-14 | -1.05e-14 | -6.6801e-15 | -5.1037e-15 | -6.5959e-15 | -2.474e-15 | -4.2046e-15 | -2.6475e-15 | -1.5254e-15 | -1.9864e-15 | -1.9864e-15 | -1.9864e-15 | -1.9864e-15 | -1.9864e-15 | -1.9864e-15 | -1.9864e-15 | -1.9864e-15 | -1.9864e-15 | -1.9864e-15 | -1.9864e-15 | -1.9864e-15 | -1.9864e-15 | -1.9864e-15 | -1.9864e-15 | -1.9864e-15
Summer Season | [31 empty] | Summer Season
P50 | [31 empty] | P10
% of MD | Summer - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Summer - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 45.5533 | 48.9582 | 49.3004 | -16.8673 | -16.7079 | -16.6423 | -16.4323 | -16.0005 | -15.6373 | -15.4701 | -15.6191 | -14.9942 | -14.8951 | -15.0124 | -14.7772 | -14.6672 | -14.6672 | -14.6672 | -14.6672 | -14.6672 | -14.6672 | -14.6672 | -14.6672 | -14.6672 | -14.6672 | -14.6672 | -14.6672 | -14.6672 | -14.6672 | -14.6672 | 100% | 0 | 56.0411 | 59.8463 | 59.9513 | -6.1619 | -6.1328 | -5.925 | -5.5039 | -4.7623 | -4.3758 | -4.0963 | -3.6731 | -3.133 | -2.4797 | -2.1374 | -2.2484 | -2.1384 | -2.1384 | -2.1384 | -2.1384 | -2.1384 | -2.1384 | -2.1384 | -2.1384 | -2.1384 | -2.1384 | -2.1384 | -2.1384 | -2.1384 | -2.1384 | -2.1384
99% | 0.37816 | 45.0978 | 48.4686 | 48.8074 | -16.6987 | -16.5408 | -16.4759 | -16.268 | -15.8405 | -15.4809 | -15.3154 | -15.4629 | -14.8443 | -14.7462 | -14.8623 | -14.6295 | -14.5206 | -14.5206 | -14.5206 | -14.5206 | -14.5206 | -14.5206 | -14.5206 | -14.5206 | -14.5206 | -14.5206 | -14.5206 | -14.5206 | -14.5206 | -14.5206 | -14.5206 | 99% | 0 | 55.4807 | 59.2478 | 59.3518 | -6.1003 | -6.0715 | -5.8658 | -5.4489 | -4.7146 | -4.3321 | -4.0553 | -3.6364 | -3.1016 | -2.4549 | -2.116 | -2.2259 | -2.117 | -2.117 | -2.117 | -2.117 | -2.117 | -2.117 | -2.117 | -2.117 | -2.117 | -2.117 | -2.117 | -2.117 | -2.117 | -2.117 | -2.117
98% | 0.37816 | 44.6423 | 47.9791 | 48.3144 | -16.53 | -16.3737 | -16.3095 | -16.1037 | -15.6805 | -15.3245 | -15.1607 | -15.3067 | -14.6944 | -14.5972 | -14.7122 | -14.4817 | -14.3739 | -14.3739 | -14.3739 | -14.3739 | -14.3739 | -14.3739 | -14.3739 | -14.3739 | -14.3739 | -14.3739 | -14.3739 | -14.3739 | -14.3739 | -14.3739 | -14.3739 | 98% | 0 | 54.9203 | 58.6494 | 58.7523 | -6.0387 | -6.0101 | -5.8065 | -5.3938 | -4.667 | -4.2883 | -4.0143 | -3.5997 | -3.0703 | -2.4301 | -2.0947 | -2.2034 | -2.0956 | -2.0956 | -2.0956 | -2.0956 | -2.0956 | -2.0956 | -2.0956 | -2.0956 | -2.0956 | -2.0956 | -2.0956 | -2.0956 | -2.0956 | -2.0956 | -2.0956
97% | 0.37816 | 44.1867 | 47.4895 | 47.8214 | -16.3613 | -16.2066 | -16.1431 | -15.9394 | -15.5205 | -15.1682 | -15.006 | -15.1505 | -14.5444 | -14.4483 | -14.562 | -14.3339 | -14.2272 | -14.2272 | -14.2272 | -14.2272 | -14.2272 | -14.2272 | -14.2272 | -14.2272 | -14.2272 | -14.2272 | -14.2272 | -14.2272 | -14.2272 | -14.2272 | -14.2272 | 97% | 0.37816 | 54.3599 | 58.0509 | 58.1528 | -5.9771 | -5.9488 | -5.7473 | -5.3388 | -4.6194 | -4.2446 | -3.9734 | -3.563 | -3.039 | -2.4054 | -2.0733 | -2.1809 | -2.0742 | -2.0742 | -2.0742 | -2.0742 | -2.0742 | -2.0742 | -2.0742 | -2.0742 | -2.0742 | -2.0742 | -2.0742 | -2.0742 | -2.0742 | -2.0742 | -2.0742
95% | 0.75633 | 43.2757 | 46.5103 | 46.8354 | -16.024 | -15.8725 | -15.8102 | -15.6107 | -15.2005 | -14.8554 | -14.6966 | -14.8382 | -14.2445 | -14.1504 | -14.2618 | -14.0384 | -13.9339 | -13.9339 | -13.9339 | -13.9339 | -13.9339 | -13.9339 | -13.9339 | -13.9339 | -13.9339 | -13.9339 | -13.9339 | -13.9339 | -13.9339 | -13.9339 | -13.9339 | 95% | 0.37816 | 53.2391 | 56.854 | 56.9537 | -5.8538 | -5.8262 | -5.6288 | -5.2287 | -4.5242 | -4.157 | -3.8914 | -3.4895 | -2.9763 | -2.3558 | -2.0305 | -2.136 | -2.0315 | -2.0315 | -2.0315 | -2.0315 | -2.0315 | -2.0315 | -2.0315 | -2.0315 | -2.0315 | -2.0315 | -2.0315 | -2.0315 | -2.0315 | -2.0315 | -2.0315
90% | 9.0759 | 40.998 | 44.0624 | 44.3703 | -15.1806 | -15.0371 | -14.9781 | -14.7891 | -14.4005 | -14.0736 | -13.9231 | -14.0572 | -13.4948 | -13.4056 | -13.5112 | -13.2995 | -13.2005 | -13.2005 | -13.2005 | -13.2005 | -13.2005 | -13.2005 | -13.2005 | -13.2005 | -13.2005 | -13.2005 | -13.2005 | -13.2005 | -13.2005 | -13.2005 | -13.2005 | 90% | 0.75633 | 50.437 | 53.8617 | 53.9562 | -5.5457 | -5.5195 | -5.3325 | -4.9535 | -4.286 | -3.9382 | -3.6866 | -3.3058 | -2.8197 | -2.2318 | -1.9237 | -2.0236 | -1.9246 | -1.9246 | -1.9246 | -1.9246 | -1.9246 | -1.9246 | -1.9246 | -1.9246 | -1.9246 | -1.9246 | -1.9246 | -1.9246 | -1.9246 | -1.9246 | -1.9246
85% | 40.4636 | 38.7203 | 41.6145 | 41.9053 | -14.3372 | -14.2017 | -14.146 | -13.9675 | -13.6005 | -13.2917 | -13.1496 | -13.2762 | -12.7451 | -12.6609 | -12.7606 | -12.5607 | -12.4672 | -12.4672 | -12.4672 | -12.4672 | -12.4672 | -12.4672 | -12.4672 | -12.4672 | -12.4672 | -12.4672 | -12.4672 | -12.4672 | -12.4672 | -12.4672 | -12.4672 | 85% | 1.1345 | 47.6349 | 50.8694 | 50.9586 | -5.2376 | -5.2129 | -5.0363 | -4.6783 | -4.0479 | -3.7195 | -3.4818 | -3.1222 | -2.663 | -2.1078 | -1.8168 | -1.9111 | -1.8176 | -1.8176 | -1.8176 | -1.8176 | -1.8176 | -1.8176 | -1.8176 | -1.8176 | -1.8176 | -1.8176 | -1.8176 | -1.8176 | -1.8176 | -1.8176 | -1.8176
80% | 94.5411 | 36.4427 | 39.1666 | 39.4403 | -13.4939 | -13.3663 | -13.3139 | -13.1459 | -12.8004 | -12.5098 | -12.3761 | -12.4953 | -11.9954 | -11.9161 | -12.0099 | -11.8218 | -11.7338 | -11.7338 | -11.7338 | -11.7338 | -11.7338 | -11.7338 | -11.7338 | -11.7338 | -11.7338 | -11.7338 | -11.7338 | -11.7338 | -11.7338 | -11.7338 | -11.7338 | 80% | 2.6471 | 44.8329 | 47.877 | 47.961 | -4.9295 | -4.9062 | -4.74 | -4.4031 | -3.8098 | -3.5007 | -3.277 | -2.9385 | -2.5064 | -1.9838 | -1.7099 | -1.7987 | -1.7107 | -1.7107 | -1.7107 | -1.7107 | -1.7107 | -1.7107 | -1.7107 | -1.7107 | -1.7107 | -1.7107 | -1.7107 | -1.7107 | -1.7107 | -1.7107 | -1.7107
75% | 197.0236 | 34.165 | 36.7187 | 36.9753 | -12.6505 | -12.5309 | -12.4818 | -12.3243 | -12.0004 | -11.728 | -11.6026 | -11.7143 | -11.2457 | -11.1714 | -11.2593 | -11.0829 | -11.0004 | -11.0004 | -11.0004 | -11.0004 | -11.0004 | -11.0004 | -11.0004 | -11.0004 | -11.0004 | -11.0004 | -11.0004 | -11.0004 | -11.0004 | -11.0004 | -11.0004 | 75% | 3.4035 | 42.0308 | 44.8847 | 44.9635 | -4.6214 | -4.5996 | -4.4438 | -4.1279 | -3.5717 | -3.2819 | -3.0722 | -2.7549 | -2.3497 | -1.8598 | -1.6031 | -1.6863 | -1.6038 | -1.6038 | -1.6038 | -1.6038 | -1.6038 | -1.6038 | -1.6038 | -1.6038 | -1.6038 | -1.6038 | -1.6038 | -1.6038 | -1.6038 | -1.6038 | -1.6038
70% | 336.9444 | 31.8873 | 34.2708 | 34.5103 | -11.8071 | -11.6955 | -11.6496 | -11.5026 | -11.2004 | -10.9461 | -10.829 | -10.9334 | -10.496 | -10.4266 | -10.5087 | -10.3441 | -10.2671 | -10.2671 | -10.2671 | -10.2671 | -10.2671 | -10.2671 | -10.2671 | -10.2671 | -10.2671 | -10.2671 | -10.2671 | -10.2671 | -10.2671 | -10.2671 | -10.2671 | 70% | 5.6725 | 39.2288 | 41.8924 | 41.9659 | -4.3133 | -4.293 | -4.1475 | -3.8527 | -3.3336 | -3.0631 | -2.8674 | -2.5712 | -2.1931 | -1.7358 | -1.4962 | -1.5739 | -1.4969 | -1.4969 | -1.4969 | -1.4969 | -1.4969 | -1.4969 | -1.4969 | -1.4969 | -1.4969 | -1.4969 | -1.4969 | -1.4969 | -1.4969 | -1.4969 | -1.4969
65% | 521.4885 | 29.6097 | 31.8228 | 32.0452 | -10.9638 | -10.8601 | -10.8175 | -10.681 | -10.4004 | -10.1642 | -10.0555 | -10.1524 | -9.7463 | -9.6818 | -9.7581 | -9.6052 | -9.5337 | -9.5337 | -9.5337 | -9.5337 | -9.5337 | -9.5337 | -9.5337 | -9.5337 | -9.5337 | -9.5337 | -9.5337 | -9.5337 | -9.5337 | -9.5337 | -9.5337 | 65% | 6.4288 | 36.4267 | 38.9001 | 38.9683 | -4.0052 | -3.9863 | -3.8513 | -3.5775 | -3.0955 | -2.8443 | -2.6626 | -2.3875 | -2.0364 | -1.6118 | -1.3893 | -1.4615 | -1.39 | -1.39 | -1.39 | -1.39 | -1.39 | -1.39 | -1.39 | -1.39 | -1.39 | -1.39 | -1.39 | -1.39 | -1.39 | -1.39 | -1.39
60% | 812.675 | 27.332 | 29.3749 | 29.5802 | -10.1204 | -10.0247 | -9.9854 | -9.8594 | -9.6003 | -9.3824 | -9.282 | -9.3715 | -8.9965 | -8.9371 | -9.0075 | -8.8663 | -8.8003 | -8.8003 | -8.8003 | -8.8003 | -8.8003 | -8.8003 | -8.8003 | -8.8003 | -8.8003 | -8.8003 | -8.8003 | -8.8003 | -8.8003 | -8.8003 | -8.8003 | 60% | 11.3449 | 33.6247 | 35.9078 | 35.9708 | -3.6971 | -3.6797 | -3.555 | -3.3023 | -2.8574 | -2.6255 | -2.4578 | -2.2039 | -1.8798 | -1.4878 | -1.2824 | -1.349 | -1.283 | -1.283 | -1.283 | -1.283 | -1.283 | -1.283 | -1.283 | -1.283 | -1.283 | -1.283 | -1.283 | -1.283 | -1.283 | -1.283 | -1.283
55% | 1202.1843 | 25.0543 | 26.927 | 27.1152 | -9.277 | -9.1893 | -9.1533 | -9.0378 | -8.8003 | -8.6005 | -8.5085 | -8.5905 | -8.2468 | -8.1923 | -8.2568 | -8.1275 | -8.067 | -8.067 | -8.067 | -8.067 | -8.067 | -8.067 | -8.067 | -8.067 | -8.067 | -8.067 | -8.067 | -8.067 | -8.067 | -8.067 | -8.067 | 55% | 35.5474 | 30.8226 | 32.9155 | 32.9732 | -3.389 | -3.373 | -3.2588 | -3.0271 | -2.6192 | -2.4067 | -2.2529 | -2.0202 | -1.7231 | -1.3639 | -1.1756 | -1.2366 | -1.1761 | -1.1761 | -1.1761 | -1.1761 | -1.1761 | -1.1761 | -1.1761 | -1.1761 | -1.1761 | -1.1761 | -1.1761 | -1.1761 | -1.1761 | -1.1761 | -1.1761
50% | 1686.2345 | 22.7767 | 24.4791 | 24.6502 | -8.4337 | -8.3539 | -8.3212 | -8.2162 | -8.0003 | -7.8186 | -7.735 | -7.8096 | -7.4971 | -7.4476 | -7.5062 | -7.3886 | -7.3336 | -7.3336 | -7.3336 | -7.3336 | -7.3336 | -7.3336 | -7.3336 | -7.3336 | -7.3336 | -7.3336 | -7.3336 | -7.3336 | -7.3336 | -7.3336 | -7.3336 | 50% | 95.2974 | 28.0206 | 29.9231 | 29.9756 | -3.081 | -3.0664 | -2.9625 | -2.7519 | -2.3811 | -2.1879 | -2.0481 | -1.8366 | -1.5665 | -1.2399 | -1.0687 | -1.1242 | -1.0692 | -1.0692 | -1.0692 | -1.0692 | -1.0692 | -1.0692 | -1.0692 | -1.0692 | -1.0692 | -1.0692 | -1.0692 | -1.0692 | -1.0692 | -1.0692 | -1.0692
45% | 2129.0649 | 20.499 | 22.0312 | 22.1852 | -7.5903 | -7.5185 | -7.4891 | -7.3946 | -7.2002 | -7.0368 | -6.9615 | -7.0286 | -6.7474 | -6.7028 | -6.7556 | -6.6498 | -6.6003 | -6.6003 | -6.6003 | -6.6003 | -6.6003 | -6.6003 | -6.6003 | -6.6003 | -6.6003 | -6.6003 | -6.6003 | -6.6003 | -6.6003 | -6.6003 | -6.6003 | 45% | 208.7467 | 25.2185 | 26.9308 | 26.9781 | -2.7729 | -2.7598 | -2.6663 | -2.4768 | -2.143 | -1.9691 | -1.8433 | -1.6529 | -1.4098 | -1.1159 | -0.96184 | -1.0118 | -0.96228 | -0.96228 | -0.96228 | -0.96228 | -0.96228 | -0.96228 | -0.96228 | -0.96228 | -0.96228 | -0.96228 | -0.96228 | -0.96228 | -0.96228 | -0.96228 | -0.96228
40% | 2484.5393 | 18.2213 | 19.5833 | 19.7201 | -6.7469 | -6.6831 | -6.6569 | -6.5729 | -6.4002 | -6.2549 | -6.188 | -6.2476 | -5.9977 | -5.9581 | -6.005 | -5.9109 | -5.8669 | -5.8669 | -5.8669 | -5.8669 | -5.8669 | -5.8669 | -5.8669 | -5.8669 | -5.8669 | -5.8669 | -5.8669 | -5.8669 | -5.8669 | -5.8669 | -5.8669 | 40% | 380.4333 | 22.4164 | 23.9385 | 23.9805 | -2.4648 | -2.4531 | -2.37 | -2.2016 | -1.9049 | -1.7503 | -1.6385 | -1.4693 | -1.2532 | -0.9919 | -0.85496 | -0.89936 | -0.85536 | -0.85536 | -0.85536 | -0.85536 | -0.85536 | -0.85536 | -0.85536 | -0.85536 | -0.85536 | -0.85536 | -0.85536 | -0.85536 | -0.85536 | -0.85536 | -0.85536
35% | 2808.248 | 15.9437 | 17.1354 | 17.2551 | -5.9036 | -5.8478 | -5.8248 | -5.7513 | -5.6002 | -5.4731 | -5.4145 | -5.4667 | -5.248 | -5.2133 | -5.2543 | -5.172 | -5.1335 | -5.1335 | -5.1335 | -5.1335 | -5.1335 | -5.1335 | -5.1335 | -5.1335 | -5.1335 | -5.1335 | -5.1335 | -5.1335 | -5.1335 | -5.1335 | -5.1335 | 35% | 696.5786 | 19.6144 | 20.9462 | 20.983 | -2.1567 | -2.1465 | -2.0738 | -1.9264 | -1.6668 | -1.5315 | -1.4337 | -1.2856 | -1.0965 | -0.86791 | -0.74809 | -0.78694 | -0.74844 | -0.74844 | -0.74844 | -0.74844 | -0.74844 | -0.74844 | -0.74844 | -0.74844 | -0.74844 | -0.74844 | -0.74844 | -0.74844 | -0.74844 | -0.74844 | -0.74844
30% | 3095.6528 | 13.666 | 14.6875 | 14.7901 | -5.0602 | -5.0124 | -4.9927 | -4.9297 | -4.8002 | -4.6912 | -4.641 | -4.6857 | -4.4983 | -4.4685 | -4.5037 | -4.4332 | -4.4002 | -4.4002 | -4.4002 | -4.4002 | -4.4002 | -4.4002 | -4.4002 | -4.4002 | -4.4002 | -4.4002 | -4.4002 | -4.4002 | -4.4002 | -4.4002 | -4.4002 | 30% | 1260.7997 | 16.8123 | 17.9539 | 17.9854 | -1.8486 | -1.8398 | -1.7775 | -1.6512 | -1.4287 | -1.3127 | -1.2289 | -1.1019 | -0.93989 | -0.74392 | -0.64122 | -0.67452 | -0.64152 | -0.64152 | -0.64152 | -0.64152 | -0.64152 | -0.64152 | -0.64152 | -0.64152 | -0.64152 | -0.64152 | -0.64152 | -0.64152 | -0.64152 | -0.64152 | -0.64152
25% | 3358.8552 | 11.3883 | 12.2396 | 12.3251 | -4.2168 | -4.177 | -4.1606 | -4.1081 | -4.0001 | -3.9093 | -3.8675 | -3.9048 | -3.7486 | -3.7238 | -3.7531 | -3.6943 | -3.6668 | -3.6668 | -3.6668 | -3.6668 | -3.6668 | -3.6668 | -3.6668 | -3.6668 | -3.6668 | -3.6668 | -3.6668 | -3.6668 | -3.6668 | -3.6668 | -3.6668 | 25% | 1965.3198 | 14.0103 | 14.9616 | 14.9878 | -1.5405 | -1.5332 | -1.4813 | -1.376 | -1.1906 | -1.094 | -1.0241 | -0.91829 | -0.78324 | -0.61994 | -0.53435 | -0.5621 | -0.5346 | -0.5346 | -0.5346 | -0.5346 | -0.5346 | -0.5346 | -0.5346 | -0.5346 | -0.5346 | -0.5346 | -0.5346 | -0.5346 | -0.5346 | -0.5346 | -0.5346
20% | 3588.7791 | 9.1107 | 9.7916 | 9.8601 | -3.3735 | -3.3416 | -3.3285 | -3.2865 | -3.2001 | -3.1275 | -3.094 | -3.1238 | -2.9988 | -2.979 | -3.0025 | -2.9554 | -2.9334 | -2.9334 | -2.9334 | -2.9334 | -2.9334 | -2.9334 | -2.9334 | -2.9334 | -2.9334 | -2.9334 | -2.9334 | -2.9334 | -2.9334 | -2.9334 | -2.9334 | 20% | 2490.2118 | 11.2082 | 11.9693 | 11.9903 | -1.2324 | -1.2266 | -1.185 | -1.1008 | -0.95245 | -0.87517 | -0.81925 | -0.73463 | -0.62659 | -0.49595 | -0.42748 | -0.44968 | -0.42768 | -0.42768 | -0.42768 | -0.42768 | -0.42768 | -0.42768 | -0.42768 | -0.42768 | -0.42768 | -0.42768 | -0.42768 | -0.42768 | -0.42768 | -0.42768 | -0.42768
15% | 3802.4419 | 6.833 | 7.3437 | 7.3951 | -2.5301 | -2.5062 | -2.4964 | -2.4649 | -2.4001 | -2.3456 | -2.3205 | -2.3429 | -2.2491 | -2.2343 | -2.2519 | -2.2166 | -2.2001 | -2.2001 | -2.2001 | -2.2001 | -2.2001 | -2.2001 | -2.2001 | -2.2001 | -2.2001 | -2.2001 | -2.2001 | -2.2001 | -2.2001 | -2.2001 | -2.2001 | 15% | 2997.7083 | 8.4062 | 8.9769 | 8.9927 | -0.92429 | -0.91992 | -0.88875 | -0.82558 | -0.71434 | -0.65637 | -0.61444 | -0.55097 | -0.46994 | -0.37196 | -0.32061 | -0.33726 | -0.32076 | -0.32076 | -0.32076 | -0.32076 | -0.32076 | -0.32076 | -0.32076 | -0.32076 | -0.32076 | -0.32076 | -0.32076 | -0.32076 | -0.32076 | -0.32076 | -0.32076
10% | 4024.8025 | 4.5553 | 4.8958 | 4.93 | -1.6867 | -1.6708 | -1.6642 | -1.6432 | -1.6001 | -1.5637 | -1.547 | -1.5619 | -1.4994 | -1.4895 | -1.5012 | -1.4777 | -1.4667 | -1.4667 | -1.4667 | -1.4667 | -1.4667 | -1.4667 | -1.4667 | -1.4667 | -1.4667 | -1.4667 | -1.4667 | -1.4667 | -1.4667 | -1.4667 | -1.4667 | 10% | 3491.5908 | 5.6041 | 5.9846 | 5.9951 | -0.61619 | -0.61328 | -0.5925 | -0.55039 | -0.47623 | -0.43758 | -0.40963 | -0.36731 | -0.3133 | -0.24797 | -0.21374 | -0.22484 | -0.21384 | -0.21384 | -0.21384 | -0.21384 | -0.21384 | -0.21384 | -0.21384 | -0.21384 | -0.21384 | -0.21384 | -0.21384 | -0.21384 | -0.21384 | -0.21384 | -0.21384
5% | 4239.978 | 2.2777 | 2.4479 | 2.465 | -0.84337 | -0.83539 | -0.83212 | -0.82162 | -0.80003 | -0.78186 | -0.7735 | -0.78096 | -0.74971 | -0.74476 | -0.75062 | -0.73886 | -0.73336 | -0.73336 | -0.73336 | -0.73336 | -0.73336 | -0.73336 | -0.73336 | -0.73336 | -0.73336 | -0.73336 | -0.73336 | -0.73336 | -0.73336 | -0.73336 | -0.73336 | 5% | 3955.9766 | 2.8021 | 2.9923 | 2.9976 | -0.3081 | -0.30664 | -0.29625 | -0.27519 | -0.23811 | -0.21879 | -0.20481 | -0.18366 | -0.15665 | -0.12399 | -0.10687 | -0.11242 | -0.10692 | -0.10692 | -0.10692 | -0.10692 | -0.10692 | -0.10692 | -0.10692 | -0.10692 | -0.10692 | -0.10692 | -0.10692 | -0.10692 | -0.10692 | -0.10692 | -0.10692
9.992e-14% | 4391.6218 | 4.5517e-14 | 4.8919e-14 | 4.9261e-14 | -1.6854e-14 | -1.6695e-14 | -1.6629e-14 | -1.6419e-14 | -1.5988e-14 | -1.5625e-14 | -1.5458e-14 | -1.5607e-14 | -1.4982e-14 | -1.4883e-14 | -1.5e-14 | -1.4765e-14 | -1.4656e-14 | -1.4656e-14 | -1.4656e-14 | -1.4656e-14 | -1.4656e-14 | -1.4656e-14 | -1.4656e-14 | -1.4656e-14 | -1.4656e-14 | -1.4656e-14 | -1.4656e-14 | -1.4656e-14 | -1.4656e-14 | -1.4656e-14 | -1.4656e-14 | 9.992e-14% | 4391.6218 | 5.5996e-14 | 5.9798e-14 | 5.9903e-14 | -6.157e-15 | -6.1279e-15 | -5.9203e-15 | -5.4995e-15 | -4.7585e-15 | -4.3723e-15 | -4.093e-15 | -3.6702e-15 | -3.1305e-15 | -2.4778e-15 | -2.1357e-15 | -2.2466e-15 | -2.1367e-15 | -2.1367e-15 | -2.1367e-15 | -2.1367e-15 | -2.1367e-15 | -2.1367e-15 | -2.1367e-15 | -2.1367e-15 | -2.1367e-15 | -2.1367e-15 | -2.1367e-15 | -2.1367e-15 | -2.1367e-15 | -2.1367e-15 | -2.1367e-15
Option 5
Winter Season | [31 empty] | Winter Season
P50 | [31 empty] | P10
% of MD | Winter - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Winter - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 39.2647 | 43.5255 | 43.999 | 44.6023 | 45.3901 | 46.1238 | 47.4018 | 50.6392 | 52.3815 | 51.0695 | 55.0372 | 55.7181 | 56.1883 | 58.6044 | 59.0098 | 59.0098 | 59.0098 | 59.0098 | 59.0098 | 59.0098 | 59.0098 | 59.0098 | 59.0098 | 59.0098 | 59.0098 | 59.0098 | 59.0098 | 59.0098 | 59.0098 | 59.0098 | 100% | 0 | 43.4358 | 47.4872 | 47.9278 | 49.4833 | 49.4434 | 49.7685 | 51.0684 | 54.8372 | 56.3866 | 54.8729 | 58.9671 | 57.1958 | 58.7065 | 59.8045 | 59.3512 | 59.3512 | 59.3512 | 59.3512 | 59.3512 | 59.3512 | 59.3512 | 59.3512 | 59.3512 | 59.3512 | 59.3512 | 59.3512 | 59.3512 | 59.3512 | 59.3512 | 59.3512
99% | 0.2972 | 38.872 | 43.0902 | 43.5591 | 44.1562 | 44.9362 | 45.6626 | 46.9278 | 50.1328 | 51.8576 | 50.5588 | 54.4868 | 55.161 | 55.6265 | 58.0184 | 58.4197 | 58.4197 | 58.4197 | 58.4197 | 58.4197 | 58.4197 | 58.4197 | 58.4197 | 58.4197 | 58.4197 | 58.4197 | 58.4197 | 58.4197 | 58.4197 | 58.4197 | 58.4197 | 99% | 0.2972 | 43.0014 | 47.0123 | 47.4485 | 48.9884 | 48.949 | 49.2708 | 50.5577 | 54.2888 | 55.8227 | 54.3242 | 58.3774 | 56.6238 | 58.1194 | 59.2064 | 58.7577 | 58.7577 | 58.7577 | 58.7577 | 58.7577 | 58.7577 | 58.7577 | 58.7577 | 58.7577 | 58.7577 | 58.7577 | 58.7577 | 58.7577 | 58.7577 | 58.7577 | 58.7577
98% | 0.2972 | 38.4794 | 42.6549 | 43.1191 | 43.7102 | 44.4823 | 45.2013 | 46.4538 | 49.6264 | 51.3338 | 50.0481 | 53.9364 | 54.6038 | 55.0646 | 57.4323 | 57.8296 | 57.8296 | 57.8296 | 57.8296 | 57.8296 | 57.8296 | 57.8296 | 57.8296 | 57.8296 | 57.8296 | 57.8296 | 57.8296 | 57.8296 | 57.8296 | 57.8296 | 57.8296 | 98% | 0.2972 | 42.5671 | 46.5374 | 46.9692 | 48.4936 | 48.4546 | 48.7731 | 50.047 | 53.7405 | 55.2589 | 53.7754 | 57.7878 | 56.0518 | 57.5323 | 58.6084 | 58.1642 | 58.1642 | 58.1642 | 58.1642 | 58.1642 | 58.1642 | 58.1642 | 58.1642 | 58.1642 | 58.1642 | 58.1642 | 58.1642 | 58.1642 | 58.1642 | 58.1642 | 58.1642
97% | 0.2972 | 38.0867 | 42.2197 | 42.6791 | 43.2642 | 44.0284 | 44.7401 | 45.9797 | 49.12 | 50.81 | 49.5374 | 53.386 | 54.0466 | 54.5027 | 56.8463 | 57.2395 | 57.2395 | 57.2395 | 57.2395 | 57.2395 | 57.2395 | 57.2395 | 57.2395 | 57.2395 | 57.2395 | 57.2395 | 57.2395 | 57.2395 | 57.2395 | 57.2395 | 57.2395 | 97% | 0.2972 | 42.1327 | 46.0625 | 46.49 | 47.9988 | 47.9601 | 48.2754 | 49.5363 | 53.1921 | 54.695 | 53.2267 | 57.1981 | 55.4799 | 56.9453 | 58.0104 | 57.5707 | 57.5707 | 57.5707 | 57.5707 | 57.5707 | 57.5707 | 57.5707 | 57.5707 | 57.5707 | 57.5707 | 57.5707 | 57.5707 | 57.5707 | 57.5707 | 57.5707 | 57.5707
95% | 1.486 | 37.3014 | 41.3492 | 41.7991 | 42.3722 | 43.1206 | 43.8176 | 45.0317 | 48.1073 | 49.7624 | 48.516 | 52.2853 | 52.9322 | 53.3789 | 55.6742 | 56.0593 | 56.0593 | 56.0593 | 56.0593 | 56.0593 | 56.0593 | 56.0593 | 56.0593 | 56.0593 | 56.0593 | 56.0593 | 56.0593 | 56.0593 | 56.0593 | 56.0593 | 56.0593 | 95% | 1.486 | 41.264 | 45.1128 | 45.5314 | 47.0091 | 46.9713 | 47.2801 | 48.515 | 52.0954 | 53.5673 | 52.1292 | 56.0188 | 54.336 | 55.7711 | 56.8143 | 56.3836 | 56.3836 | 56.3836 | 56.3836 | 56.3836 | 56.3836 | 56.3836 | 56.3836 | 56.3836 | 56.3836 | 56.3836 | 56.3836 | 56.3836 | 56.3836 | 56.3836 | 56.3836
90% | 8.6188 | 35.3382 | 39.1729 | 39.5991 | 40.142 | 40.8511 | 41.5114 | 42.6616 | 45.5753 | 47.1433 | 45.9625 | 49.5334 | 50.1463 | 50.5695 | 52.744 | 53.1089 | 53.1089 | 53.1089 | 53.1089 | 53.1089 | 53.1089 | 53.1089 | 53.1089 | 53.1089 | 53.1089 | 53.1089 | 53.1089 | 53.1089 | 53.1089 | 53.1089 | 53.1089 | 90% | 8.6188 | 39.0922 | 42.7384 | 43.135 | 44.5349 | 44.4991 | 44.7916 | 45.9615 | 49.3535 | 50.7479 | 49.3856 | 53.0704 | 51.4762 | 52.8358 | 53.824 | 53.4161 | 53.4161 | 53.4161 | 53.4161 | 53.4161 | 53.4161 | 53.4161 | 53.4161 | 53.4161 | 53.4161 | 53.4161 | 53.4161 | 53.4161 | 53.4161 | 53.4161 | 53.4161
85% | 40.1218 | 33.375 | 36.9966 | 37.3992 | 37.9119 | 38.5816 | 39.2052 | 40.2915 | 43.0433 | 44.5242 | 43.409 | 46.7816 | 47.3604 | 47.7601 | 49.8138 | 50.1584 | 50.1584 | 50.1584 | 50.1584 | 50.1584 | 50.1584 | 50.1584 | 50.1584 | 50.1584 | 50.1584 | 50.1584 | 50.1584 | 50.1584 | 50.1584 | 50.1584 | 50.1584 | 85% | 40.1218 | 36.9204 | 40.3641 | 40.7386 | 42.0608 | 42.0269 | 42.3032 | 43.4081 | 46.6116 | 47.9286 | 46.642 | 50.1221 | 48.6164 | 49.9005 | 50.8338 | 50.4485 | 50.4485 | 50.4485 | 50.4485 | 50.4485 | 50.4485 | 50.4485 | 50.4485 | 50.4485 | 50.4485 | 50.4485 | 50.4485 | 50.4485 | 50.4485 | 50.4485 | 50.4485
80% | 93.0231 | 31.4117 | 34.8204 | 35.1992 | 35.6818 | 36.3121 | 36.899 | 37.9214 | 40.5114 | 41.9052 | 40.8556 | 44.0297 | 44.5745 | 44.9507 | 46.8835 | 47.2079 | 47.2079 | 47.2079 | 47.2079 | 47.2079 | 47.2079 | 47.2079 | 47.2079 | 47.2079 | 47.2079 | 47.2079 | 47.2079 | 47.2079 | 47.2079 | 47.2079 | 47.2079 | 80% | 93.0231 | 34.7486 | 37.9897 | 38.3422 | 39.5866 | 39.5547 | 39.8148 | 40.8547 | 43.8698 | 45.1093 | 43.8983 | 47.1737 | 45.7566 | 46.9652 | 47.8436 | 47.481 | 47.481 | 47.481 | 47.481 | 47.481 | 47.481 | 47.481 | 47.481 | 47.481 | 47.481 | 47.481 | 47.481 | 47.481 | 47.481 | 47.481 | 47.481
75% | 197.0426 | 29.4485 | 32.6441 | 32.9993 | 33.4517 | 34.0426 | 34.5928 | 35.5513 | 37.9794 | 39.2861 | 38.3021 | 41.2779 | 41.7886 | 42.1413 | 43.9533 | 44.2574 | 44.2574 | 44.2574 | 44.2574 | 44.2574 | 44.2574 | 44.2574 | 44.2574 | 44.2574 | 44.2574 | 44.2574 | 44.2574 | 44.2574 | 44.2574 | 44.2574 | 44.2574 | 75% | 197.0426 | 32.5768 | 35.6154 | 35.9459 | 37.1124 | 37.0826 | 37.3264 | 38.3013 | 41.1279 | 42.29 | 41.1547 | 44.2253 | 42.8968 | 44.0298 | 44.8534 | 44.5134 | 44.5134 | 44.5134 | 44.5134 | 44.5134 | 44.5134 | 44.5134 | 44.5134 | 44.5134 | 44.5134 | 44.5134 | 44.5134 | 44.5134 | 44.5134 | 44.5134 | 44.5134
70% | 378.0365 | 27.4853 | 30.4678 | 30.7993 | 31.2216 | 31.7731 | 32.2867 | 33.1813 | 35.4475 | 36.667 | 35.7486 | 38.526 | 39.0027 | 39.3318 | 41.0231 | 41.3069 | 41.3069 | 41.3069 | 41.3069 | 41.3069 | 41.3069 | 41.3069 | 41.3069 | 41.3069 | 41.3069 | 41.3069 | 41.3069 | 41.3069 | 41.3069 | 41.3069 | 41.3069 | 70% | 378.0365 | 30.4051 | 33.241 | 33.5495 | 34.6383 | 34.6104 | 34.8379 | 35.7479 | 38.3861 | 39.4706 | 38.411 | 41.277 | 40.037 | 41.0945 | 41.8631 | 41.5458 | 41.5458 | 41.5458 | 41.5458 | 41.5458 | 41.5458 | 41.5458 | 41.5458 | 41.5458 | 41.5458 | 41.5458 | 41.5458 | 41.5458 | 41.5458 | 41.5458 | 41.5458
65% | 616.0926 | 25.522 | 28.2915 | 28.5994 | 28.9915 | 29.5036 | 29.9805 | 30.8112 | 32.9155 | 34.0479 | 33.1952 | 35.7741 | 36.2168 | 36.5224 | 38.0929 | 38.3564 | 38.3564 | 38.3564 | 38.3564 | 38.3564 | 38.3564 | 38.3564 | 38.3564 | 38.3564 | 38.3564 | 38.3564 | 38.3564 | 38.3564 | 38.3564 | 38.3564 | 38.3564 | 65% | 616.0926 | 28.2333 | 30.8666 | 31.1531 | 32.1641 | 32.1382 | 32.3495 | 33.1944 | 35.6442 | 36.6513 | 35.6674 | 38.3286 | 37.1772 | 38.1592 | 38.8729 | 38.5783 | 38.5783 | 38.5783 | 38.5783 | 38.5783 | 38.5783 | 38.5783 | 38.5783 | 38.5783 | 38.5783 | 38.5783 | 38.5783 | 38.5783 | 38.5783 | 38.5783 | 38.5783
60% | 934.9866 | 23.5588 | 26.1153 | 26.3994 | 26.7614 | 27.234 | 27.6743 | 28.4411 | 30.3835 | 31.4289 | 30.6417 | 33.0223 | 33.4309 | 33.713 | 35.1626 | 35.4059 | 35.4059 | 35.4059 | 35.4059 | 35.4059 | 35.4059 | 35.4059 | 35.4059 | 35.4059 | 35.4059 | 35.4059 | 35.4059 | 35.4059 | 35.4059 | 35.4059 | 35.4059 | 60% | 934.9866 | 26.0615 | 28.4923 | 28.7567 | 29.69 | 29.6661 | 29.8611 | 30.641 | 32.9023 | 33.832 | 32.9237 | 35.3803 | 34.3175 | 35.2239 | 35.8827 | 35.6107 | 35.6107 | 35.6107 | 35.6107 | 35.6107 | 35.6107 | 35.6107 | 35.6107 | 35.6107 | 35.6107 | 35.6107 | 35.6107 | 35.6107 | 35.6107 | 35.6107 | 35.6107
55% | 1310.9428 | 21.5956 | 23.939 | 24.1995 | 24.5312 | 24.9645 | 25.3681 | 26.071 | 27.8516 | 28.8098 | 28.0882 | 30.2704 | 30.645 | 30.9036 | 32.2324 | 32.4554 | 32.4554 | 32.4554 | 32.4554 | 32.4554 | 32.4554 | 32.4554 | 32.4554 | 32.4554 | 32.4554 | 32.4554 | 32.4554 | 32.4554 | 32.4554 | 32.4554 | 32.4554 | 55% | 1310.9428 | 23.8897 | 26.1179 | 26.3603 | 27.2158 | 27.1939 | 27.3727 | 28.0876 | 30.1605 | 31.0126 | 30.1801 | 32.4319 | 31.4577 | 32.2886 | 32.8925 | 32.6432 | 32.6432 | 32.6432 | 32.6432 | 32.6432 | 32.6432 | 32.6432 | 32.6432 | 32.6432 | 32.6432 | 32.6432 | 32.6432 | 32.6432 | 32.6432 | 32.6432 | 32.6432
50% | 1730.2899 | 19.6323 | 21.7627 | 21.9995 | 22.3011 | 22.695 | 23.0619 | 23.7009 | 25.3196 | 26.1907 | 25.5347 | 27.5186 | 27.8591 | 28.0942 | 29.3022 | 29.5049 | 29.5049 | 29.5049 | 29.5049 | 29.5049 | 29.5049 | 29.5049 | 29.5049 | 29.5049 | 29.5049 | 29.5049 | 29.5049 | 29.5049 | 29.5049 | 29.5049 | 29.5049 | 50% | 1730.2899 | 21.7179 | 23.7436 | 23.9639 | 24.7416 | 24.7217 | 24.8842 | 25.5342 | 27.4186 | 28.1933 | 27.4364 | 29.4836 | 28.5979 | 29.3532 | 29.9022 | 29.6756 | 29.6756 | 29.6756 | 29.6756 | 29.6756 | 29.6756 | 29.6756 | 29.6756 | 29.6756 | 29.6756 | 29.6756 | 29.6756 | 29.6756 | 29.6756 | 29.6756 | 29.6756
45% | 2168.0633 | 17.6691 | 19.5865 | 19.7996 | 20.071 | 20.4255 | 20.7557 | 21.3308 | 22.7877 | 23.5717 | 22.9813 | 24.7667 | 25.0732 | 25.2848 | 26.372 | 26.5544 | 26.5544 | 26.5544 | 26.5544 | 26.5544 | 26.5544 | 26.5544 | 26.5544 | 26.5544 | 26.5544 | 26.5544 | 26.5544 | 26.5544 | 26.5544 | 26.5544 | 26.5544 | 45% | 2168.0633 | 19.5461 | 21.3692 | 21.5675 | 22.2675 | 22.2495 | 22.3958 | 22.9808 | 24.6767 | 25.374 | 24.6928 | 26.5352 | 25.7381 | 26.4179 | 26.912 | 26.708 | 26.708 | 26.708 | 26.708 | 26.708 | 26.708 | 26.708 | 26.708 | 26.708 | 26.708 | 26.708 | 26.708 | 26.708 | 26.708 | 26.708 | 26.708
40% | 2609.7004 | 15.7059 | 17.4102 | 17.5996 | 17.8409 | 18.156 | 18.4495 | 18.9607 | 20.2557 | 20.9526 | 20.4278 | 22.0149 | 22.2873 | 22.4753 | 23.4418 | 23.6039 | 23.6039 | 23.6039 | 23.6039 | 23.6039 | 23.6039 | 23.6039 | 23.6039 | 23.6039 | 23.6039 | 23.6039 | 23.6039 | 23.6039 | 23.6039 | 23.6039 | 23.6039 | 40% | 2609.7004 | 17.3743 | 18.9949 | 19.1711 | 19.7933 | 19.7774 | 19.9074 | 20.4274 | 21.9349 | 22.5546 | 21.9492 | 23.5868 | 22.8783 | 23.4826 | 23.9218 | 23.7405 | 23.7405 | 23.7405 | 23.7405 | 23.7405 | 23.7405 | 23.7405 | 23.7405 | 23.7405 | 23.7405 | 23.7405 | 23.7405 | 23.7405 | 23.7405 | 23.7405 | 23.7405
35% | 2998.1389 | 13.7426 | 15.2339 | 15.3997 | 15.6108 | 15.8865 | 16.1433 | 16.5906 | 17.7237 | 18.3335 | 17.8743 | 19.263 | 19.5014 | 19.6659 | 20.5115 | 20.6534 | 20.6534 | 20.6534 | 20.6534 | 20.6534 | 20.6534 | 20.6534 | 20.6534 | 20.6534 | 20.6534 | 20.6534 | 20.6534 | 20.6534 | 20.6534 | 20.6534 | 20.6534 | 35% | 2998.1389 | 15.2025 | 16.6205 | 16.7747 | 17.3191 | 17.3052 | 17.419 | 17.8739 | 19.193 | 19.7353 | 19.2055 | 20.6385 | 20.0185 | 20.5473 | 20.9316 | 20.7729 | 20.7729 | 20.7729 | 20.7729 | 20.7729 | 20.7729 | 20.7729 | 20.7729 | 20.7729 | 20.7729 | 20.7729 | 20.7729 | 20.7729 | 20.7729 | 20.7729 | 20.7729
30% | 3309.3057 | 11.7794 | 13.0576 | 13.1997 | 13.3807 | 13.617 | 13.8371 | 14.2205 | 15.1918 | 15.7144 | 15.3208 | 16.5111 | 16.7154 | 16.8565 | 17.5813 | 17.703 | 17.703 | 17.703 | 17.703 | 17.703 | 17.703 | 17.703 | 17.703 | 17.703 | 17.703 | 17.703 | 17.703 | 17.703 | 17.703 | 17.703 | 17.703 | 30% | 3309.3057 | 13.0307 | 14.2461 | 14.3783 | 14.845 | 14.833 | 14.9305 | 15.3205 | 16.4512 | 16.916 | 16.4619 | 17.6901 | 17.1587 | 17.6119 | 17.9413 | 17.8054 | 17.8054 | 17.8054 | 17.8054 | 17.8054 | 17.8054 | 17.8054 | 17.8054 | 17.8054 | 17.8054 | 17.8054 | 17.8054 | 17.8054 | 17.8054 | 17.8054 | 17.8054
25% | 3537.8514 | 9.8162 | 10.8814 | 10.9998 | 11.1506 | 11.3475 | 11.5309 | 11.8504 | 12.6598 | 13.0954 | 12.7674 | 13.7593 | 13.9295 | 14.0471 | 14.6511 | 14.7525 | 14.7525 | 14.7525 | 14.7525 | 14.7525 | 14.7525 | 14.7525 | 14.7525 | 14.7525 | 14.7525 | 14.7525 | 14.7525 | 14.7525 | 14.7525 | 14.7525 | 14.7525 | 25% | 3537.8514 | 10.8589 | 11.8718 | 11.982 | 12.3708 | 12.3609 | 12.4421 | 12.7671 | 13.7093 | 14.0967 | 13.7182 | 14.7418 | 14.2989 | 14.6766 | 14.9511 | 14.8378 | 14.8378 | 14.8378 | 14.8378 | 14.8378 | 14.8378 | 14.8378 | 14.8378 | 14.8378 | 14.8378 | 14.8378 | 14.8378 | 14.8378 | 14.8378 | 14.8378 | 14.8378
20% | 3731.0305 | 7.8529 | 8.7051 | 8.7998 | 8.9205 | 9.078 | 9.2248 | 9.4804 | 10.1278 | 10.4763 | 10.2139 | 11.0074 | 11.1436 | 11.2377 | 11.7209 | 11.802 | 11.802 | 11.802 | 11.802 | 11.802 | 11.802 | 11.802 | 11.802 | 11.802 | 11.802 | 11.802 | 11.802 | 11.802 | 11.802 | 11.802 | 11.802 | 20% | 3731.0305 | 8.6872 | 9.4974 | 9.5856 | 9.8967 | 9.8887 | 9.9537 | 10.2137 | 10.9674 | 11.2773 | 10.9746 | 11.7934 | 11.4392 | 11.7413 | 11.9609 | 11.8702 | 11.8702 | 11.8702 | 11.8702 | 11.8702 | 11.8702 | 11.8702 | 11.8702 | 11.8702 | 11.8702 | 11.8702 | 11.8702 | 11.8702 | 11.8702 | 11.8702 | 11.8702
15% | 3910.2412 | 5.8897 | 6.5288 | 6.5999 | 6.6903 | 6.8085 | 6.9186 | 7.1103 | 7.5959 | 7.8572 | 7.6604 | 8.2556 | 8.3577 | 8.4283 | 8.7907 | 8.8515 | 8.8515 | 8.8515 | 8.8515 | 8.8515 | 8.8515 | 8.8515 | 8.8515 | 8.8515 | 8.8515 | 8.8515 | 8.8515 | 8.8515 | 8.8515 | 8.8515 | 8.8515 | 15% | 3910.2412 | 6.5154 | 7.1231 | 7.1892 | 7.4225 | 7.4165 | 7.4653 | 7.6603 | 8.2256 | 8.458 | 8.2309 | 8.8451 | 8.5794 | 8.806 | 8.9707 | 8.9027 | 8.9027 | 8.9027 | 8.9027 | 8.9027 | 8.9027 | 8.9027 | 8.9027 | 8.9027 | 8.9027 | 8.9027 | 8.9027 | 8.9027 | 8.9027 | 8.9027 | 8.9027
10% | 4075.1864 | 3.9265 | 4.3525 | 4.3999 | 4.4602 | 4.539 | 4.6124 | 4.7402 | 5.0639 | 5.2381 | 5.1069 | 5.5037 | 5.5718 | 5.6188 | 5.8604 | 5.901 | 5.901 | 5.901 | 5.901 | 5.901 | 5.901 | 5.901 | 5.901 | 5.901 | 5.901 | 5.901 | 5.901 | 5.901 | 5.901 | 5.901 | 5.901 | 10% | 4075.1864 | 4.3436 | 4.7487 | 4.7928 | 4.9483 | 4.9443 | 4.9768 | 5.1068 | 5.4837 | 5.6387 | 5.4873 | 5.8967 | 5.7196 | 5.8706 | 5.9804 | 5.9351 | 5.9351 | 5.9351 | 5.9351 | 5.9351 | 5.9351 | 5.9351 | 5.9351 | 5.9351 | 5.9351 | 5.9351 | 5.9351 | 5.9351 | 5.9351 | 5.9351 | 5.9351
5% | 4251.7223 | 1.9632 | 2.1763 | 2.2 | 2.2301 | 2.2695 | 2.3062 | 2.3701 | 2.532 | 2.6191 | 2.5535 | 2.7519 | 2.7859 | 2.8094 | 2.9302 | 2.9505 | 2.9505 | 2.9505 | 2.9505 | 2.9505 | 2.9505 | 2.9505 | 2.9505 | 2.9505 | 2.9505 | 2.9505 | 2.9505 | 2.9505 | 2.9505 | 2.9505 | 2.9505 | 5% | 4251.7223 | 2.1718 | 2.3744 | 2.3964 | 2.4742 | 2.4722 | 2.4884 | 2.5534 | 2.7419 | 2.8193 | 2.7436 | 2.9484 | 2.8598 | 2.9353 | 2.9902 | 2.9676 | 2.9676 | 2.9676 | 2.9676 | 2.9676 | 2.9676 | 2.9676 | 2.9676 | 2.9676 | 2.9676 | 2.9676 | 2.9676 | 2.9676 | 2.9676 | 2.9676 | 2.9676
9.992e-14% | 4391.7028 | 3.9233e-14 | 4.3491e-14 | 4.3964e-14 | 4.4567e-14 | 4.5354e-14 | 4.6087e-14 | 4.7364e-14 | 5.0599e-14 | 5.234e-14 | 5.1029e-14 | 5.4993e-14 | 5.5674e-14 | 5.6143e-14 | 5.8558e-14 | 5.8963e-14 | 5.8963e-14 | 5.8963e-14 | 5.8963e-14 | 5.8963e-14 | 5.8963e-14 | 5.8963e-14 | 5.8963e-14 | 5.8963e-14 | 5.8963e-14 | 5.8963e-14 | 5.8963e-14 | 5.8963e-14 | 5.8963e-14 | 5.8963e-14 | 5.8963e-14 | 9.992e-14% | 4391.7028 | 4.3401e-14 | 4.7449e-14 | 4.7889e-14 | 4.9444e-14 | 4.9404e-14 | 4.9729e-14 | 5.1028e-14 | 5.4793e-14 | 5.6342e-14 | 5.4829e-14 | 5.892e-14 | 5.715e-14 | 5.866e-14 | 5.9757e-14 | 5.9304e-14 | 5.9304e-14 | 5.9304e-14 | 5.9304e-14 | 5.9304e-14 | 5.9304e-14 | 5.9304e-14 | 5.9304e-14 | 5.9304e-14 | 5.9304e-14 | 5.9304e-14 | 5.9304e-14 | 5.9304e-14 | 5.9304e-14 | 5.9304e-14 | 5.9304e-14
Summer Season | [31 empty] | Summer Season
P50 | [31 empty] | P10
% of MD | Summer - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Summer - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 41.4552 | 44.5824 | 44.9169 | 44.7574 | 44.9148 | 44.9651 | 45.1444 | 45.5221 | 45.8571 | 46.004 | 45.824 | 46.4095 | 46.4609 | 46.3186 | 46.5619 | 46.6719 | 46.6719 | 46.6719 | 46.6719 | 46.6719 | 46.6719 | 46.6719 | 46.6719 | 46.6719 | 46.6719 | 46.6719 | 46.6719 | 46.6719 | 46.6719 | 46.6719 | 100% | 0 | 51.943 | 55.4705 | 55.5678 | 55.4629 | 55.4899 | 55.6825 | 56.0729 | 56.7604 | 57.1186 | 57.3778 | 57.77 | 58.2708 | 58.8763 | 59.1936 | 59.0908 | 59.2008 | 59.2008 | 59.2008 | 59.2008 | 59.2008 | 59.2008 | 59.2008 | 59.2008 | 59.2008 | 59.2008 | 59.2008 | 59.2008 | 59.2008 | 59.2008 | 59.2008
99% | 0.37816 | 41.0407 | 44.1366 | 44.4677 | 44.3099 | 44.4656 | 44.5155 | 44.693 | 45.0669 | 45.3986 | 45.5439 | 45.3658 | 45.9454 | 45.9963 | 45.8555 | 46.0963 | 46.2052 | 46.2052 | 46.2052 | 46.2052 | 46.2052 | 46.2052 | 46.2052 | 46.2052 | 46.2052 | 46.2052 | 46.2052 | 46.2052 | 46.2052 | 46.2052 | 46.2052 | 99% | 0 | 51.4236 | 54.9158 | 55.0121 | 54.9082 | 54.935 | 55.1257 | 55.5121 | 56.1928 | 56.5474 | 56.804 | 57.1923 | 57.6881 | 58.2875 | 58.6017 | 58.4999 | 58.6088 | 58.6088 | 58.6088 | 58.6088 | 58.6088 | 58.6088 | 58.6088 | 58.6088 | 58.6088 | 58.6088 | 58.6088 | 58.6088 | 58.6088 | 58.6088 | 58.6088
98% | 0.37816 | 40.6261 | 43.6908 | 44.0186 | 43.8623 | 44.0165 | 44.0658 | 44.2415 | 44.6116 | 44.94 | 45.0839 | 44.9076 | 45.4813 | 45.5317 | 45.3923 | 45.6307 | 45.7385 | 45.7385 | 45.7385 | 45.7385 | 45.7385 | 45.7385 | 45.7385 | 45.7385 | 45.7385 | 45.7385 | 45.7385 | 45.7385 | 45.7385 | 45.7385 | 45.7385 | 98% | 0 | 50.9042 | 54.3611 | 54.4565 | 54.3536 | 54.3801 | 54.5688 | 54.9514 | 55.6252 | 55.9762 | 56.2302 | 56.6146 | 57.1053 | 57.6988 | 58.0098 | 57.909 | 58.0168 | 58.0168 | 58.0168 | 58.0168 | 58.0168 | 58.0168 | 58.0168 | 58.0168 | 58.0168 | 58.0168 | 58.0168 | 58.0168 | 58.0168 | 58.0168 | 58.0168
97% | 0.37816 | 40.2116 | 43.2449 | 43.5694 | 43.4147 | 43.5673 | 43.6162 | 43.7901 | 44.1564 | 44.4814 | 44.6238 | 44.4493 | 45.0172 | 45.0671 | 44.9291 | 45.1651 | 45.2718 | 45.2718 | 45.2718 | 45.2718 | 45.2718 | 45.2718 | 45.2718 | 45.2718 | 45.2718 | 45.2718 | 45.2718 | 45.2718 | 45.2718 | 45.2718 | 45.2718 | 97% | 0.37816 | 50.3847 | 53.8064 | 53.9008 | 53.799 | 53.8252 | 54.012 | 54.3907 | 55.0576 | 55.405 | 55.6564 | 56.0369 | 56.5226 | 57.11 | 57.4178 | 57.318 | 57.4247 | 57.4247 | 57.4247 | 57.4247 | 57.4247 | 57.4247 | 57.4247 | 57.4247 | 57.4247 | 57.4247 | 57.4247 | 57.4247 | 57.4247 | 57.4247 | 57.4247
95% | 0.75633 | 39.3825 | 42.3533 | 42.671 | 42.5196 | 42.669 | 42.7169 | 42.8872 | 43.246 | 43.5643 | 43.7038 | 43.5328 | 44.089 | 44.1379 | 44.0027 | 44.2338 | 44.3383 | 44.3383 | 44.3383 | 44.3383 | 44.3383 | 44.3383 | 44.3383 | 44.3383 | 44.3383 | 44.3383 | 44.3383 | 44.3383 | 44.3383 | 44.3383 | 44.3383 | 95% | 0.37816 | 49.3459 | 52.697 | 52.7894 | 52.6897 | 52.7154 | 52.8984 | 53.2692 | 53.9223 | 54.2627 | 54.5089 | 54.8815 | 55.3572 | 55.9325 | 56.234 | 56.1362 | 56.2407 | 56.2407 | 56.2407 | 56.2407 | 56.2407 | 56.2407 | 56.2407 | 56.2407 | 56.2407 | 56.2407 | 56.2407 | 56.2407 | 56.2407 | 56.2407 | 56.2407
90% | 9.0759 | 37.3097 | 40.1242 | 40.4252 | 40.2817 | 40.4233 | 40.4686 | 40.63 | 40.9699 | 41.2714 | 41.4036 | 41.2416 | 41.7685 | 41.8148 | 41.6868 | 41.9057 | 42.0047 | 42.0047 | 42.0047 | 42.0047 | 42.0047 | 42.0047 | 42.0047 | 42.0047 | 42.0047 | 42.0047 | 42.0047 | 42.0047 | 42.0047 | 42.0047 | 42.0047 | 90% | 0.75633 | 46.7487 | 49.9234 | 50.011 | 49.9166 | 49.9409 | 50.1142 | 50.4656 | 51.0843 | 51.4067 | 51.64 | 51.993 | 52.4437 | 52.9887 | 53.2743 | 53.1817 | 53.2807 | 53.2807 | 53.2807 | 53.2807 | 53.2807 | 53.2807 | 53.2807 | 53.2807 | 53.2807 | 53.2807 | 53.2807 | 53.2807 | 53.2807 | 53.2807 | 53.2807
85% | 40.4636 | 35.2369 | 37.895 | 38.1794 | 38.0438 | 38.1776 | 38.2204 | 38.3727 | 38.6938 | 38.9786 | 39.1034 | 38.9504 | 39.4481 | 39.4918 | 39.3708 | 39.5776 | 39.6711 | 39.6711 | 39.6711 | 39.6711 | 39.6711 | 39.6711 | 39.6711 | 39.6711 | 39.6711 | 39.6711 | 39.6711 | 39.6711 | 39.6711 | 39.6711 | 39.6711 | 85% | 1.1345 | 44.1516 | 47.1499 | 47.2326 | 47.1434 | 47.1664 | 47.3301 | 47.6619 | 48.2463 | 48.5508 | 48.7711 | 49.1045 | 49.5302 | 50.0449 | 50.3146 | 50.2272 | 50.3207 | 50.3207 | 50.3207 | 50.3207 | 50.3207 | 50.3207 | 50.3207 | 50.3207 | 50.3207 | 50.3207 | 50.3207 | 50.3207 | 50.3207 | 50.3207 | 50.3207
80% | 94.5411 | 33.1642 | 35.6659 | 35.9335 | 35.806 | 35.9318 | 35.9721 | 36.1155 | 36.4177 | 36.6857 | 36.8032 | 36.6592 | 37.1276 | 37.1687 | 37.0549 | 37.2495 | 37.3375 | 37.3375 | 37.3375 | 37.3375 | 37.3375 | 37.3375 | 37.3375 | 37.3375 | 37.3375 | 37.3375 | 37.3375 | 37.3375 | 37.3375 | 37.3375 | 37.3375 | 80% | 2.6471 | 41.5544 | 44.3764 | 44.4543 | 44.3703 | 44.3919 | 44.546 | 44.8583 | 45.4083 | 45.6949 | 45.9022 | 46.216 | 46.6166 | 47.101 | 47.3549 | 47.2726 | 47.3606 | 47.3606 | 47.3606 | 47.3606 | 47.3606 | 47.3606 | 47.3606 | 47.3606 | 47.3606 | 47.3606 | 47.3606 | 47.3606 | 47.3606 | 47.3606 | 47.3606
75% | 197.0236 | 31.0914 | 33.4368 | 33.6877 | 33.5681 | 33.6861 | 33.7239 | 33.8583 | 34.1416 | 34.3929 | 34.503 | 34.368 | 34.8071 | 34.8457 | 34.739 | 34.9214 | 35.0039 | 35.0039 | 35.0039 | 35.0039 | 35.0039 | 35.0039 | 35.0039 | 35.0039 | 35.0039 | 35.0039 | 35.0039 | 35.0039 | 35.0039 | 35.0039 | 35.0039 | 75% | 3.4035 | 38.9573 | 41.6029 | 41.6759 | 41.5972 | 41.6174 | 41.7619 | 42.0547 | 42.5703 | 42.8389 | 43.0333 | 43.3275 | 43.7031 | 44.1572 | 44.3952 | 44.3181 | 44.4006 | 44.4006 | 44.4006 | 44.4006 | 44.4006 | 44.4006 | 44.4006 | 44.4006 | 44.4006 | 44.4006 | 44.4006 | 44.4006 | 44.4006 | 44.4006 | 44.4006
70% | 336.9444 | 29.0187 | 31.2077 | 31.4418 | 31.3302 | 31.4403 | 31.4756 | 31.6011 | 31.8655 | 32.1 | 32.2028 | 32.0768 | 32.4866 | 32.5226 | 32.423 | 32.5933 | 32.6703 | 32.6703 | 32.6703 | 32.6703 | 32.6703 | 32.6703 | 32.6703 | 32.6703 | 32.6703 | 32.6703 | 32.6703 | 32.6703 | 32.6703 | 32.6703 | 32.6703 | 70% | 5.6725 | 36.3601 | 38.8293 | 38.8975 | 38.824 | 38.8429 | 38.9777 | 39.251 | 39.7323 | 39.983 | 40.1644 | 40.439 | 40.7895 | 41.2134 | 41.4356 | 41.3635 | 41.4405 | 41.4405 | 41.4405 | 41.4405 | 41.4405 | 41.4405 | 41.4405 | 41.4405 | 41.4405 | 41.4405 | 41.4405 | 41.4405 | 41.4405 | 41.4405 | 41.4405
65% | 521.4885 | 26.9459 | 28.9786 | 29.196 | 29.0923 | 29.1946 | 29.2273 | 29.3439 | 29.5894 | 29.8071 | 29.9026 | 29.7856 | 30.1662 | 30.1996 | 30.1071 | 30.2653 | 30.3368 | 30.3368 | 30.3368 | 30.3368 | 30.3368 | 30.3368 | 30.3368 | 30.3368 | 30.3368 | 30.3368 | 30.3368 | 30.3368 | 30.3368 | 30.3368 | 30.3368 | 65% | 6.4288 | 33.763 | 36.0558 | 36.1191 | 36.0509 | 36.0684 | 36.1936 | 36.4474 | 36.8942 | 37.1271 | 37.2955 | 37.5505 | 37.876 | 38.2696 | 38.4759 | 38.409 | 38.4805 | 38.4805 | 38.4805 | 38.4805 | 38.4805 | 38.4805 | 38.4805 | 38.4805 | 38.4805 | 38.4805 | 38.4805 | 38.4805 | 38.4805 | 38.4805 | 38.4805
60% | 812.675 | 24.8731 | 26.7494 | 26.9501 | 26.8545 | 26.9489 | 26.9791 | 27.0866 | 27.3133 | 27.5143 | 27.6024 | 27.4944 | 27.8457 | 27.8765 | 27.7912 | 27.9372 | 28.0032 | 28.0032 | 28.0032 | 28.0032 | 28.0032 | 28.0032 | 28.0032 | 28.0032 | 28.0032 | 28.0032 | 28.0032 | 28.0032 | 28.0032 | 28.0032 | 28.0032 | 60% | 11.3449 | 31.1658 | 33.2823 | 33.3407 | 33.2777 | 33.2939 | 33.4095 | 33.6437 | 34.0562 | 34.2712 | 34.4267 | 34.662 | 34.9625 | 35.3258 | 35.5162 | 35.4545 | 35.5205 | 35.5205 | 35.5205 | 35.5205 | 35.5205 | 35.5205 | 35.5205 | 35.5205 | 35.5205 | 35.5205 | 35.5205 | 35.5205 | 35.5205 | 35.5205 | 35.5205
55% | 1202.1843 | 22.8004 | 24.5203 | 24.7043 | 24.6166 | 24.7031 | 24.7308 | 24.8294 | 25.0371 | 25.2214 | 25.3022 | 25.2032 | 25.5252 | 25.5535 | 25.4753 | 25.6091 | 25.6696 | 25.6696 | 25.6696 | 25.6696 | 25.6696 | 25.6696 | 25.6696 | 25.6696 | 25.6696 | 25.6696 | 25.6696 | 25.6696 | 25.6696 | 25.6696 | 25.6696 | 55% | 35.5474 | 28.5687 | 30.5088 | 30.5623 | 30.5046 | 30.5194 | 30.6254 | 30.8401 | 31.2182 | 31.4152 | 31.5578 | 31.7735 | 32.0489 | 32.382 | 32.5565 | 32.4999 | 32.5604 | 32.5604 | 32.5604 | 32.5604 | 32.5604 | 32.5604 | 32.5604 | 32.5604 | 32.5604 | 32.5604 | 32.5604 | 32.5604 | 32.5604 | 32.5604 | 32.5604
50% | 1686.2345 | 20.7276 | 22.2912 | 22.4584 | 22.3787 | 22.4574 | 22.4826 | 22.5722 | 22.761 | 22.9286 | 23.002 | 22.912 | 23.2047 | 23.2305 | 23.1593 | 23.281 | 23.336 | 23.336 | 23.336 | 23.336 | 23.336 | 23.336 | 23.336 | 23.336 | 23.336 | 23.336 | 23.336 | 23.336 | 23.336 | 23.336 | 23.336 | 50% | 95.2974 | 25.9715 | 27.7352 | 27.7839 | 27.7314 | 27.7449 | 27.8412 | 28.0364 | 28.3802 | 28.5593 | 28.6889 | 28.885 | 29.1354 | 29.4382 | 29.5968 | 29.5454 | 29.6004 | 29.6004 | 29.6004 | 29.6004 | 29.6004 | 29.6004 | 29.6004 | 29.6004 | 29.6004 | 29.6004 | 29.6004 | 29.6004 | 29.6004 | 29.6004 | 29.6004
45% | 2129.0649 | 18.6549 | 20.0621 | 20.2126 | 20.1408 | 20.2117 | 20.2343 | 20.315 | 20.4849 | 20.6357 | 20.7018 | 20.6208 | 20.8843 | 20.9074 | 20.8434 | 20.9529 | 21.0024 | 21.0024 | 21.0024 | 21.0024 | 21.0024 | 21.0024 | 21.0024 | 21.0024 | 21.0024 | 21.0024 | 21.0024 | 21.0024 | 21.0024 | 21.0024 | 21.0024 | 45% | 208.7467 | 23.3744 | 24.9617 | 25.0055 | 24.9583 | 24.9704 | 25.0571 | 25.2328 | 25.5422 | 25.7034 | 25.82 | 25.9965 | 26.2218 | 26.4943 | 26.6371 | 26.5908 | 26.6403 | 26.6403 | 26.6403 | 26.6403 | 26.6403 | 26.6403 | 26.6403 | 26.6403 | 26.6403 | 26.6403 | 26.6403 | 26.6403 | 26.6403 | 26.6403 | 26.6403
40% | 2484.5393 | 16.5821 | 17.833 | 17.9668 | 17.903 | 17.9659 | 17.9861 | 18.0578 | 18.2088 | 18.3429 | 18.4016 | 18.3296 | 18.5638 | 18.5844 | 18.5275 | 18.6248 | 18.6688 | 18.6688 | 18.6688 | 18.6688 | 18.6688 | 18.6688 | 18.6688 | 18.6688 | 18.6688 | 18.6688 | 18.6688 | 18.6688 | 18.6688 | 18.6688 | 18.6688 | 40% | 380.4333 | 20.7772 | 22.1882 | 22.2271 | 22.1851 | 22.1959 | 22.273 | 22.4291 | 22.7041 | 22.8474 | 22.9511 | 23.108 | 23.3083 | 23.5505 | 23.6775 | 23.6363 | 23.6803 | 23.6803 | 23.6803 | 23.6803 | 23.6803 | 23.6803 | 23.6803 | 23.6803 | 23.6803 | 23.6803 | 23.6803 | 23.6803 | 23.6803 | 23.6803 | 23.6803
35% | 2808.248 | 14.5093 | 15.6038 | 15.7209 | 15.6651 | 15.7202 | 15.7378 | 15.8005 | 15.9327 | 16.05 | 16.1014 | 16.0384 | 16.2433 | 16.2613 | 16.2115 | 16.2967 | 16.3352 | 16.3352 | 16.3352 | 16.3352 | 16.3352 | 16.3352 | 16.3352 | 16.3352 | 16.3352 | 16.3352 | 16.3352 | 16.3352 | 16.3352 | 16.3352 | 16.3352 | 35% | 696.5786 | 18.1801 | 19.4147 | 19.4487 | 19.412 | 19.4215 | 19.4889 | 19.6255 | 19.8661 | 19.9915 | 20.0822 | 20.2195 | 20.3948 | 20.6067 | 20.7178 | 20.6818 | 20.7203 | 20.7203 | 20.7203 | 20.7203 | 20.7203 | 20.7203 | 20.7203 | 20.7203 | 20.7203 | 20.7203 | 20.7203 | 20.7203 | 20.7203 | 20.7203 | 20.7203
30% | 3095.6528 | 12.4366 | 13.3747 | 13.4751 | 13.4272 | 13.4744 | 13.4895 | 13.5433 | 13.6566 | 13.7571 | 13.8012 | 13.7472 | 13.9228 | 13.9383 | 13.8956 | 13.9686 | 14.0016 | 14.0016 | 14.0016 | 14.0016 | 14.0016 | 14.0016 | 14.0016 | 14.0016 | 14.0016 | 14.0016 | 14.0016 | 14.0016 | 14.0016 | 14.0016 | 14.0016 | 30% | 1260.7997 | 15.5829 | 16.6411 | 16.6703 | 16.6389 | 16.647 | 16.7047 | 16.8219 | 17.0281 | 17.1356 | 17.2133 | 17.331 | 17.4812 | 17.6629 | 17.7581 | 17.7272 | 17.7602 | 17.7602 | 17.7602 | 17.7602 | 17.7602 | 17.7602 | 17.7602 | 17.7602 | 17.7602 | 17.7602 | 17.7602 | 17.7602 | 17.7602 | 17.7602 | 17.7602
25% | 3358.8552 | 10.3638 | 11.1456 | 11.2292 | 11.1894 | 11.2287 | 11.2413 | 11.2861 | 11.3805 | 11.4643 | 11.501 | 11.456 | 11.6024 | 11.6152 | 11.5797 | 11.6405 | 11.668 | 11.668 | 11.668 | 11.668 | 11.668 | 11.668 | 11.668 | 11.668 | 11.668 | 11.668 | 11.668 | 11.668 | 11.668 | 11.668 | 11.668 | 25% | 1965.3198 | 12.9858 | 13.8676 | 13.892 | 13.8657 | 13.8725 | 13.9206 | 14.0182 | 14.1901 | 14.2796 | 14.3444 | 14.4425 | 14.5677 | 14.7191 | 14.7984 | 14.7727 | 14.8002 | 14.8002 | 14.8002 | 14.8002 | 14.8002 | 14.8002 | 14.8002 | 14.8002 | 14.8002 | 14.8002 | 14.8002 | 14.8002 | 14.8002 | 14.8002 | 14.8002
20% | 3588.7791 | 8.291 | 8.9165 | 8.9834 | 8.9515 | 8.983 | 8.993 | 9.0289 | 9.1044 | 9.1714 | 9.2008 | 9.1648 | 9.2819 | 9.2922 | 9.2637 | 9.3124 | 9.3344 | 9.3344 | 9.3344 | 9.3344 | 9.3344 | 9.3344 | 9.3344 | 9.3344 | 9.3344 | 9.3344 | 9.3344 | 9.3344 | 9.3344 | 9.3344 | 9.3344 | 20% | 2490.2118 | 10.3886 | 11.0941 | 11.1136 | 11.0926 | 11.098 | 11.1365 | 11.2146 | 11.3521 | 11.4237 | 11.4756 | 11.554 | 11.6542 | 11.7753 | 11.8387 | 11.8182 | 11.8402 | 11.8402 | 11.8402 | 11.8402 | 11.8402 | 11.8402 | 11.8402 | 11.8402 | 11.8402 | 11.8402 | 11.8402 | 11.8402 | 11.8402 | 11.8402 | 11.8402
15% | 3802.4419 | 6.2183 | 6.6874 | 6.7375 | 6.7136 | 6.7372 | 6.7448 | 6.7717 | 6.8283 | 6.8786 | 6.9006 | 6.8736 | 6.9614 | 6.9691 | 6.9478 | 6.9843 | 7.0008 | 7.0008 | 7.0008 | 7.0008 | 7.0008 | 7.0008 | 7.0008 | 7.0008 | 7.0008 | 7.0008 | 7.0008 | 7.0008 | 7.0008 | 7.0008 | 7.0008 | 15% | 2997.7083 | 7.7915 | 8.3206 | 8.3352 | 8.3194 | 8.3235 | 8.3524 | 8.4109 | 8.5141 | 8.5678 | 8.6067 | 8.6655 | 8.7406 | 8.8314 | 8.879 | 8.8636 | 8.8801 | 8.8801 | 8.8801 | 8.8801 | 8.8801 | 8.8801 | 8.8801 | 8.8801 | 8.8801 | 8.8801 | 8.8801 | 8.8801 | 8.8801 | 8.8801 | 8.8801
10% | 4024.8025 | 4.1455 | 4.4582 | 4.4917 | 4.4757 | 4.4915 | 4.4965 | 4.5144 | 4.5522 | 4.5857 | 4.6004 | 4.5824 | 4.6409 | 4.6461 | 4.6319 | 4.6562 | 4.6672 | 4.6672 | 4.6672 | 4.6672 | 4.6672 | 4.6672 | 4.6672 | 4.6672 | 4.6672 | 4.6672 | 4.6672 | 4.6672 | 4.6672 | 4.6672 | 4.6672 | 10% | 3491.5908 | 5.1943 | 5.547 | 5.5568 | 5.5463 | 5.549 | 5.5682 | 5.6073 | 5.676 | 5.7119 | 5.7378 | 5.777 | 5.8271 | 5.8876 | 5.9194 | 5.9091 | 5.9201 | 5.9201 | 5.9201 | 5.9201 | 5.9201 | 5.9201 | 5.9201 | 5.9201 | 5.9201 | 5.9201 | 5.9201 | 5.9201 | 5.9201 | 5.9201 | 5.9201
5% | 4239.978 | 2.0728 | 2.2291 | 2.2458 | 2.2379 | 2.2457 | 2.2483 | 2.2572 | 2.2761 | 2.2929 | 2.3002 | 2.2912 | 2.3205 | 2.323 | 2.3159 | 2.3281 | 2.3336 | 2.3336 | 2.3336 | 2.3336 | 2.3336 | 2.3336 | 2.3336 | 2.3336 | 2.3336 | 2.3336 | 2.3336 | 2.3336 | 2.3336 | 2.3336 | 2.3336 | 5% | 3955.9766 | 2.5972 | 2.7735 | 2.7784 | 2.7731 | 2.7745 | 2.7841 | 2.8036 | 2.838 | 2.8559 | 2.8689 | 2.8885 | 2.9135 | 2.9438 | 2.9597 | 2.9545 | 2.96 | 2.96 | 2.96 | 2.96 | 2.96 | 2.96 | 2.96 | 2.96 | 2.96 | 2.96 | 2.96 | 2.96 | 2.96 | 2.96 | 2.96
9.992e-14% | 4391.6218 | 4.1422e-14 | 4.4547e-14 | 4.4881e-14 | 4.4722e-14 | 4.4879e-14 | 4.4929e-14 | 4.5108e-14 | 4.5486e-14 | 4.582e-14 | 4.5967e-14 | 4.5787e-14 | 4.6372e-14 | 4.6424e-14 | 4.6282e-14 | 4.6525e-14 | 4.6635e-14 | 4.6635e-14 | 4.6635e-14 | 4.6635e-14 | 4.6635e-14 | 4.6635e-14 | 4.6635e-14 | 4.6635e-14 | 4.6635e-14 | 4.6635e-14 | 4.6635e-14 | 4.6635e-14 | 4.6635e-14 | 4.6635e-14 | 4.6635e-14 | 9.992e-14% | 4391.6218 | 5.1901e-14 | 5.5426e-14 | 5.5523e-14 | 5.5419e-14 | 5.5446e-14 | 5.5638e-14 | 5.6028e-14 | 5.6715e-14 | 5.7073e-14 | 5.7332e-14 | 5.7724e-14 | 5.8224e-14 | 5.8829e-14 | 5.9146e-14 | 5.9044e-14 | 5.9153e-14 | 5.9153e-14 | 5.9153e-14 | 5.9153e-14 | 5.9153e-14 | 5.9153e-14 | 5.9153e-14 | 5.9153e-14 | 5.9153e-14 | 5.9153e-14 | 5.9153e-14 | 5.9153e-14 | 5.9153e-14 | 5.9153e-14 | 5.9153e-14
Option 6
Winter Season | [31 empty] | Winter Season
P50 | [31 empty] | P10
% of MD | Winter - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Winter - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 43.3628 | 47.9013 | 48.3825 | 48.9775 | 49.7674 | 50.5163 | 51.825 | 55.1166 | 56.887 | 55.5954 | 59.594 | 60.3144 | 60.8323 | 63.2734 | 63.6707 | 63.6707 | 63.6707 | 63.6707 | 63.6707 | 63.6707 | 63.6707 | 63.6707 | 63.6707 | 63.6707 | 63.6707 | 63.6707 | 63.6707 | 63.6707 | 63.6707 | 63.6707 | 100% | 0 | 47.5339 | 51.863 | 52.3113 | 53.8585 | 53.8208 | 54.161 | 55.4916 | 59.3146 | 60.8922 | 59.3989 | 63.524 | 61.792 | 63.3504 | 64.4734 | 64.012 | 64.012 | 64.012 | 64.012 | 64.012 | 64.012 | 64.012 | 64.012 | 64.012 | 64.012 | 64.012 | 64.012 | 64.012 | 64.012 | 64.012 | 64.012
99% | 0.2972 | 42.9291 | 47.4223 | 47.8987 | 48.4877 | 49.2697 | 50.0111 | 51.3068 | 54.5654 | 56.3182 | 55.0395 | 58.9981 | 59.7113 | 60.224 | 62.6406 | 63.034 | 63.034 | 63.034 | 63.034 | 63.034 | 63.034 | 63.034 | 63.034 | 63.034 | 63.034 | 63.034 | 63.034 | 63.034 | 63.034 | 63.034 | 63.034 | 99% | 0.2972 | 47.0586 | 51.3443 | 51.7882 | 53.3199 | 53.2826 | 53.6194 | 54.9367 | 58.7214 | 60.2833 | 58.8049 | 62.8887 | 61.1741 | 62.7169 | 63.8287 | 63.3719 | 63.3719 | 63.3719 | 63.3719 | 63.3719 | 63.3719 | 63.3719 | 63.3719 | 63.3719 | 63.3719 | 63.3719 | 63.3719 | 63.3719 | 63.3719 | 63.3719 | 63.3719
98% | 0.2972 | 42.4955 | 46.9432 | 47.4149 | 47.9979 | 48.7721 | 49.506 | 50.7885 | 54.0143 | 55.7493 | 54.4835 | 58.4021 | 59.1081 | 59.6156 | 62.0079 | 62.3973 | 62.3973 | 62.3973 | 62.3973 | 62.3973 | 62.3973 | 62.3973 | 62.3973 | 62.3973 | 62.3973 | 62.3973 | 62.3973 | 62.3973 | 62.3973 | 62.3973 | 62.3973 | 98% | 0.2972 | 46.5832 | 50.8257 | 51.2651 | 52.7813 | 52.7443 | 53.0778 | 54.3818 | 58.1283 | 59.6743 | 58.2109 | 62.2535 | 60.5562 | 62.0834 | 63.184 | 62.7318 | 62.7318 | 62.7318 | 62.7318 | 62.7318 | 62.7318 | 62.7318 | 62.7318 | 62.7318 | 62.7318 | 62.7318 | 62.7318 | 62.7318 | 62.7318 | 62.7318 | 62.7318
97% | 0.2972 | 42.0619 | 46.4642 | 46.931 | 47.5082 | 48.2744 | 49.0008 | 50.2703 | 53.4631 | 55.1804 | 53.9276 | 57.8062 | 58.505 | 59.0073 | 61.3752 | 61.7606 | 61.7606 | 61.7606 | 61.7606 | 61.7606 | 61.7606 | 61.7606 | 61.7606 | 61.7606 | 61.7606 | 61.7606 | 61.7606 | 61.7606 | 61.7606 | 61.7606 | 61.7606 | 97% | 0.2972 | 46.1079 | 50.3071 | 50.7419 | 52.2427 | 52.2061 | 52.5362 | 53.8269 | 57.5352 | 59.0654 | 57.6169 | 61.6183 | 59.9383 | 61.4499 | 62.5392 | 62.0917 | 62.0917 | 62.0917 | 62.0917 | 62.0917 | 62.0917 | 62.0917 | 62.0917 | 62.0917 | 62.0917 | 62.0917 | 62.0917 | 62.0917 | 62.0917 | 62.0917 | 62.0917
95% | 1.486 | 41.1946 | 45.5062 | 45.9634 | 46.5286 | 47.2791 | 47.9905 | 49.2338 | 52.3608 | 54.0427 | 52.8157 | 56.6143 | 57.2987 | 57.7907 | 60.1097 | 60.4871 | 60.4871 | 60.4871 | 60.4871 | 60.4871 | 60.4871 | 60.4871 | 60.4871 | 60.4871 | 60.4871 | 60.4871 | 60.4871 | 60.4871 | 60.4871 | 60.4871 | 60.4871 | 95% | 1.486 | 45.1572 | 49.2698 | 49.6957 | 51.1655 | 51.1297 | 51.4529 | 52.717 | 56.3489 | 57.8476 | 56.4289 | 60.3478 | 58.7024 | 60.1829 | 61.2498 | 60.8114 | 60.8114 | 60.8114 | 60.8114 | 60.8114 | 60.8114 | 60.8114 | 60.8114 | 60.8114 | 60.8114 | 60.8114 | 60.8114 | 60.8114 | 60.8114 | 60.8114 | 60.8114
90% | 8.6188 | 39.0265 | 43.1111 | 43.5443 | 44.0797 | 44.7907 | 45.4647 | 46.6425 | 49.6049 | 51.1983 | 50.0359 | 53.6346 | 54.283 | 54.7491 | 56.946 | 57.3036 | 57.3036 | 57.3036 | 57.3036 | 57.3036 | 57.3036 | 57.3036 | 57.3036 | 57.3036 | 57.3036 | 57.3036 | 57.3036 | 57.3036 | 57.3036 | 57.3036 | 57.3036 | 90% | 8.6188 | 42.7805 | 46.6767 | 47.0802 | 48.4726 | 48.4387 | 48.7449 | 49.9425 | 53.3831 | 54.803 | 53.459 | 57.1716 | 55.6128 | 57.0154 | 58.0261 | 57.6108 | 57.6108 | 57.6108 | 57.6108 | 57.6108 | 57.6108 | 57.6108 | 57.6108 | 57.6108 | 57.6108 | 57.6108 | 57.6108 | 57.6108 | 57.6108 | 57.6108 | 57.6108
85% | 40.1218 | 36.8584 | 40.7161 | 41.1251 | 41.6309 | 42.3023 | 42.9389 | 44.0513 | 46.8491 | 48.354 | 47.2561 | 50.6549 | 51.2673 | 51.7074 | 53.7823 | 54.1201 | 54.1201 | 54.1201 | 54.1201 | 54.1201 | 54.1201 | 54.1201 | 54.1201 | 54.1201 | 54.1201 | 54.1201 | 54.1201 | 54.1201 | 54.1201 | 54.1201 | 54.1201 | 85% | 40.1218 | 40.4038 | 44.0835 | 44.4646 | 45.7797 | 45.7477 | 46.0368 | 47.1679 | 50.4174 | 51.7583 | 50.489 | 53.9954 | 52.5232 | 53.8479 | 54.8024 | 54.4102 | 54.4102 | 54.4102 | 54.4102 | 54.4102 | 54.4102 | 54.4102 | 54.4102 | 54.4102 | 54.4102 | 54.4102 | 54.4102 | 54.4102 | 54.4102 | 54.4102 | 54.4102
80% | 93.0231 | 34.6902 | 38.321 | 38.706 | 39.182 | 39.8139 | 40.413 | 41.46 | 44.0933 | 45.5096 | 44.4764 | 47.6752 | 48.2515 | 48.6658 | 50.6187 | 50.9365 | 50.9365 | 50.9365 | 50.9365 | 50.9365 | 50.9365 | 50.9365 | 50.9365 | 50.9365 | 50.9365 | 50.9365 | 50.9365 | 50.9365 | 50.9365 | 50.9365 | 50.9365 | 80% | 93.0231 | 38.0271 | 41.4904 | 41.849 | 43.0868 | 43.0566 | 43.3288 | 44.3933 | 47.4517 | 48.7137 | 47.5191 | 50.8192 | 49.4336 | 50.6803 | 51.5787 | 51.2096 | 51.2096 | 51.2096 | 51.2096 | 51.2096 | 51.2096 | 51.2096 | 51.2096 | 51.2096 | 51.2096 | 51.2096 | 51.2096 | 51.2096 | 51.2096 | 51.2096 | 51.2096
75% | 197.0426 | 32.5221 | 35.926 | 36.2869 | 36.7331 | 37.3256 | 37.8872 | 38.8688 | 41.3374 | 42.6653 | 41.6966 | 44.6955 | 45.2358 | 45.6242 | 47.455 | 47.753 | 47.753 | 47.753 | 47.753 | 47.753 | 47.753 | 47.753 | 47.753 | 47.753 | 47.753 | 47.753 | 47.753 | 47.753 | 47.753 | 47.753 | 47.753 | 75% | 197.0426 | 35.6504 | 38.8972 | 39.2335 | 40.3939 | 40.3656 | 40.6207 | 41.6187 | 44.4859 | 45.6691 | 44.5491 | 47.643 | 46.344 | 47.5128 | 48.3551 | 48.009 | 48.009 | 48.009 | 48.009 | 48.009 | 48.009 | 48.009 | 48.009 | 48.009 | 48.009 | 48.009 | 48.009 | 48.009 | 48.009 | 48.009 | 48.009
70% | 378.0365 | 30.3539 | 33.5309 | 33.8678 | 34.2842 | 34.8372 | 35.3614 | 36.2775 | 38.5816 | 39.8209 | 38.9168 | 41.7158 | 42.2201 | 42.5826 | 44.2913 | 44.5695 | 44.5695 | 44.5695 | 44.5695 | 44.5695 | 44.5695 | 44.5695 | 44.5695 | 44.5695 | 44.5695 | 44.5695 | 44.5695 | 44.5695 | 44.5695 | 44.5695 | 44.5695 | 70% | 378.0365 | 33.2737 | 36.3041 | 36.6179 | 37.7009 | 37.6745 | 37.9127 | 38.8441 | 41.5202 | 42.6245 | 41.5792 | 44.4668 | 43.2544 | 44.3453 | 45.1314 | 44.8084 | 44.8084 | 44.8084 | 44.8084 | 44.8084 | 44.8084 | 44.8084 | 44.8084 | 44.8084 | 44.8084 | 44.8084 | 44.8084 | 44.8084 | 44.8084 | 44.8084 | 44.8084
65% | 616.0926 | 28.1858 | 31.1358 | 31.4486 | 31.8354 | 32.3488 | 32.8356 | 33.6863 | 35.8258 | 36.9766 | 36.137 | 38.7361 | 39.2044 | 39.541 | 41.1277 | 41.3859 | 41.3859 | 41.3859 | 41.3859 | 41.3859 | 41.3859 | 41.3859 | 41.3859 | 41.3859 | 41.3859 | 41.3859 | 41.3859 | 41.3859 | 41.3859 | 41.3859 | 41.3859 | 65% | 616.0926 | 30.897 | 33.7109 | 34.0023 | 35.008 | 34.9835 | 35.2046 | 36.0696 | 38.5545 | 39.5799 | 38.6093 | 41.2906 | 40.1648 | 41.1778 | 41.9077 | 41.6078 | 41.6078 | 41.6078 | 41.6078 | 41.6078 | 41.6078 | 41.6078 | 41.6078 | 41.6078 | 41.6078 | 41.6078 | 41.6078 | 41.6078 | 41.6078 | 41.6078 | 41.6078
60% | 934.9866 | 26.0177 | 28.7408 | 29.0295 | 29.3865 | 29.8605 | 30.3098 | 31.095 | 33.07 | 34.1322 | 33.3573 | 35.7564 | 36.1887 | 36.4994 | 37.964 | 38.2024 | 38.2024 | 38.2024 | 38.2024 | 38.2024 | 38.2024 | 38.2024 | 38.2024 | 38.2024 | 38.2024 | 38.2024 | 38.2024 | 38.2024 | 38.2024 | 38.2024 | 38.2024 | 60% | 934.9866 | 28.5203 | 31.1178 | 31.3868 | 32.3151 | 32.2925 | 32.4966 | 33.295 | 35.5888 | 36.5353 | 35.6393 | 38.1144 | 37.0752 | 38.0103 | 38.6841 | 38.4072 | 38.4072 | 38.4072 | 38.4072 | 38.4072 | 38.4072 | 38.4072 | 38.4072 | 38.4072 | 38.4072 | 38.4072 | 38.4072 | 38.4072 | 38.4072 | 38.4072 | 38.4072
55% | 1310.9428 | 23.8495 | 26.3457 | 26.6104 | 26.9376 | 27.3721 | 27.784 | 28.5038 | 30.3141 | 31.2879 | 30.5775 | 32.7767 | 33.1729 | 33.4578 | 34.8003 | 35.0189 | 35.0189 | 35.0189 | 35.0189 | 35.0189 | 35.0189 | 35.0189 | 35.0189 | 35.0189 | 35.0189 | 35.0189 | 35.0189 | 35.0189 | 35.0189 | 35.0189 | 35.0189 | 55% | 1310.9428 | 26.1436 | 28.5246 | 28.7712 | 29.6222 | 29.6014 | 29.7885 | 30.5204 | 32.623 | 33.4907 | 32.6694 | 34.9382 | 33.9856 | 34.8427 | 35.4604 | 35.2066 | 35.2066 | 35.2066 | 35.2066 | 35.2066 | 35.2066 | 35.2066 | 35.2066 | 35.2066 | 35.2066 | 35.2066 | 35.2066 | 35.2066 | 35.2066 | 35.2066 | 35.2066
50% | 1730.2899 | 21.6814 | 23.9506 | 24.1913 | 24.4887 | 24.8837 | 25.2582 | 25.9125 | 27.5583 | 28.4435 | 27.7977 | 29.797 | 30.1572 | 30.4161 | 31.6367 | 31.8353 | 31.8353 | 31.8353 | 31.8353 | 31.8353 | 31.8353 | 31.8353 | 31.8353 | 31.8353 | 31.8353 | 31.8353 | 31.8353 | 31.8353 | 31.8353 | 31.8353 | 31.8353 | 50% | 1730.2899 | 23.7669 | 25.9315 | 26.1556 | 26.9292 | 26.9104 | 27.0805 | 27.7458 | 29.6573 | 30.4461 | 29.6994 | 31.762 | 30.896 | 31.6752 | 32.2367 | 32.006 | 32.006 | 32.006 | 32.006 | 32.006 | 32.006 | 32.006 | 32.006 | 32.006 | 32.006 | 32.006 | 32.006 | 32.006 | 32.006 | 32.006 | 32.006
45% | 2168.0633 | 19.5132 | 21.5556 | 21.7721 | 22.0399 | 22.3953 | 22.7323 | 23.3213 | 24.8025 | 25.5992 | 25.0179 | 26.8173 | 27.1415 | 27.3745 | 28.473 | 28.6518 | 28.6518 | 28.6518 | 28.6518 | 28.6518 | 28.6518 | 28.6518 | 28.6518 | 28.6518 | 28.6518 | 28.6518 | 28.6518 | 28.6518 | 28.6518 | 28.6518 | 28.6518 | 45% | 2168.0633 | 21.3903 | 23.3383 | 23.5401 | 24.2363 | 24.2193 | 24.3724 | 24.9712 | 26.6916 | 27.4015 | 26.7295 | 28.5858 | 27.8064 | 28.5077 | 29.013 | 28.8054 | 28.8054 | 28.8054 | 28.8054 | 28.8054 | 28.8054 | 28.8054 | 28.8054 | 28.8054 | 28.8054 | 28.8054 | 28.8054 | 28.8054 | 28.8054 | 28.8054 | 28.8054
40% | 2609.7004 | 17.3451 | 19.1605 | 19.353 | 19.591 | 19.907 | 20.2065 | 20.73 | 22.0466 | 22.7548 | 22.2382 | 23.8376 | 24.1258 | 24.3329 | 25.3093 | 25.4683 | 25.4683 | 25.4683 | 25.4683 | 25.4683 | 25.4683 | 25.4683 | 25.4683 | 25.4683 | 25.4683 | 25.4683 | 25.4683 | 25.4683 | 25.4683 | 25.4683 | 25.4683 | 40% | 2609.7004 | 19.0136 | 20.7452 | 20.9245 | 21.5434 | 21.5283 | 21.6644 | 22.1966 | 23.7258 | 24.3569 | 23.7595 | 25.4096 | 24.7168 | 25.3402 | 25.7894 | 25.6048 | 25.6048 | 25.6048 | 25.6048 | 25.6048 | 25.6048 | 25.6048 | 25.6048 | 25.6048 | 25.6048 | 25.6048 | 25.6048 | 25.6048 | 25.6048 | 25.6048 | 25.6048
35% | 2998.1389 | 15.177 | 16.7654 | 16.9339 | 17.1421 | 17.4186 | 17.6807 | 18.1388 | 19.2908 | 19.9105 | 19.4584 | 20.8579 | 21.1101 | 21.2913 | 22.1457 | 22.2847 | 22.2847 | 22.2847 | 22.2847 | 22.2847 | 22.2847 | 22.2847 | 22.2847 | 22.2847 | 22.2847 | 22.2847 | 22.2847 | 22.2847 | 22.2847 | 22.2847 | 22.2847 | 35% | 2998.1389 | 16.6369 | 18.152 | 18.3089 | 18.8505 | 18.8373 | 18.9563 | 19.4221 | 20.7601 | 21.3123 | 20.7896 | 22.2334 | 21.6272 | 22.1726 | 22.5657 | 22.4042 | 22.4042 | 22.4042 | 22.4042 | 22.4042 | 22.4042 | 22.4042 | 22.4042 | 22.4042 | 22.4042 | 22.4042 | 22.4042 | 22.4042 | 22.4042 | 22.4042 | 22.4042
30% | 3309.3057 | 13.0088 | 14.3704 | 14.5148 | 14.6932 | 14.9302 | 15.1549 | 15.5475 | 16.535 | 17.0661 | 16.6786 | 17.8782 | 18.0943 | 18.2497 | 18.982 | 19.1012 | 19.1012 | 19.1012 | 19.1012 | 19.1012 | 19.1012 | 19.1012 | 19.1012 | 19.1012 | 19.1012 | 19.1012 | 19.1012 | 19.1012 | 19.1012 | 19.1012 | 19.1012 | 30% | 3309.3057 | 14.2602 | 15.5589 | 15.6934 | 16.1575 | 16.1462 | 16.2483 | 16.6475 | 17.7944 | 18.2677 | 17.8197 | 19.0572 | 18.5376 | 19.0051 | 19.342 | 19.2036 | 19.2036 | 19.2036 | 19.2036 | 19.2036 | 19.2036 | 19.2036 | 19.2036 | 19.2036 | 19.2036 | 19.2036 | 19.2036 | 19.2036 | 19.2036 | 19.2036 | 19.2036
25% | 3537.8514 | 10.8407 | 11.9753 | 12.0956 | 12.2444 | 12.4419 | 12.6291 | 12.9563 | 13.7791 | 14.2218 | 13.8989 | 14.8985 | 15.0786 | 15.2081 | 15.8183 | 15.9177 | 15.9177 | 15.9177 | 15.9177 | 15.9177 | 15.9177 | 15.9177 | 15.9177 | 15.9177 | 15.9177 | 15.9177 | 15.9177 | 15.9177 | 15.9177 | 15.9177 | 15.9177 | 25% | 3537.8514 | 11.8835 | 12.9657 | 13.0778 | 13.4646 | 13.4552 | 13.5402 | 13.8729 | 14.8286 | 15.223 | 14.8497 | 15.881 | 15.448 | 15.8376 | 16.1184 | 16.003 | 16.003 | 16.003 | 16.003 | 16.003 | 16.003 | 16.003 | 16.003 | 16.003 | 16.003 | 16.003 | 16.003 | 16.003 | 16.003 | 16.003 | 16.003
20% | 3731.0305 | 8.6726 | 9.5803 | 9.6765 | 9.7955 | 9.9535 | 10.1033 | 10.365 | 11.0233 | 11.3774 | 11.1191 | 11.9188 | 12.0629 | 12.1665 | 12.6547 | 12.7341 | 12.7341 | 12.7341 | 12.7341 | 12.7341 | 12.7341 | 12.7341 | 12.7341 | 12.7341 | 12.7341 | 12.7341 | 12.7341 | 12.7341 | 12.7341 | 12.7341 | 12.7341 | 20% | 3731.0305 | 9.5068 | 10.3726 | 10.4623 | 10.7717 | 10.7642 | 10.8322 | 11.0983 | 11.8629 | 12.1784 | 11.8798 | 12.7048 | 12.3584 | 12.6701 | 12.8947 | 12.8024 | 12.8024 | 12.8024 | 12.8024 | 12.8024 | 12.8024 | 12.8024 | 12.8024 | 12.8024 | 12.8024 | 12.8024 | 12.8024 | 12.8024 | 12.8024 | 12.8024 | 12.8024
15% | 3910.2412 | 6.5044 | 7.1852 | 7.2574 | 7.3466 | 7.4651 | 7.5774 | 7.7738 | 8.2675 | 8.5331 | 8.3393 | 8.9391 | 9.0472 | 9.1248 | 9.491 | 9.5506 | 9.5506 | 9.5506 | 9.5506 | 9.5506 | 9.5506 | 9.5506 | 9.5506 | 9.5506 | 9.5506 | 9.5506 | 9.5506 | 9.5506 | 9.5506 | 9.5506 | 9.5506 | 15% | 3910.2412 | 7.1301 | 7.7794 | 7.8467 | 8.0788 | 8.0731 | 8.1241 | 8.3237 | 8.8972 | 9.1338 | 8.9098 | 9.5286 | 9.2688 | 9.5026 | 9.671 | 9.6018 | 9.6018 | 9.6018 | 9.6018 | 9.6018 | 9.6018 | 9.6018 | 9.6018 | 9.6018 | 9.6018 | 9.6018 | 9.6018 | 9.6018 | 9.6018 | 9.6018 | 9.6018
10% | 4075.1864 | 4.3363 | 4.7901 | 4.8383 | 4.8977 | 4.9767 | 5.0516 | 5.1825 | 5.5117 | 5.6887 | 5.5595 | 5.9594 | 6.0314 | 6.0832 | 6.3273 | 6.3671 | 6.3671 | 6.3671 | 6.3671 | 6.3671 | 6.3671 | 6.3671 | 6.3671 | 6.3671 | 6.3671 | 6.3671 | 6.3671 | 6.3671 | 6.3671 | 6.3671 | 6.3671 | 10% | 4075.1864 | 4.7534 | 5.1863 | 5.2311 | 5.3858 | 5.3821 | 5.4161 | 5.5492 | 5.9315 | 6.0892 | 5.9399 | 6.3524 | 6.1792 | 6.335 | 6.4473 | 6.4012 | 6.4012 | 6.4012 | 6.4012 | 6.4012 | 6.4012 | 6.4012 | 6.4012 | 6.4012 | 6.4012 | 6.4012 | 6.4012 | 6.4012 | 6.4012 | 6.4012 | 6.4012
5% | 4251.7223 | 2.1681 | 2.3951 | 2.4191 | 2.4489 | 2.4884 | 2.5258 | 2.5913 | 2.7558 | 2.8444 | 2.7798 | 2.9797 | 3.0157 | 3.0416 | 3.1637 | 3.1835 | 3.1835 | 3.1835 | 3.1835 | 3.1835 | 3.1835 | 3.1835 | 3.1835 | 3.1835 | 3.1835 | 3.1835 | 3.1835 | 3.1835 | 3.1835 | 3.1835 | 3.1835 | 5% | 4251.7223 | 2.3767 | 2.5931 | 2.6156 | 2.6929 | 2.691 | 2.708 | 2.7746 | 2.9657 | 3.0446 | 2.9699 | 3.1762 | 3.0896 | 3.1675 | 3.2237 | 3.2006 | 3.2006 | 3.2006 | 3.2006 | 3.2006 | 3.2006 | 3.2006 | 3.2006 | 3.2006 | 3.2006 | 3.2006 | 3.2006 | 3.2006 | 3.2006 | 3.2006 | 3.2006
9.992e-14% | 4391.7028 | 4.3328e-14 | 4.7863e-14 | 4.8344e-14 | 4.8938e-14 | 4.9728e-14 | 5.0476e-14 | 5.1784e-14 | 5.5073e-14 | 5.6842e-14 | 5.5551e-14 | 5.9546e-14 | 6.0266e-14 | 6.0784e-14 | 6.3223e-14 | 6.362e-14 | 6.362e-14 | 6.362e-14 | 6.362e-14 | 6.362e-14 | 6.362e-14 | 6.362e-14 | 6.362e-14 | 6.362e-14 | 6.362e-14 | 6.362e-14 | 6.362e-14 | 6.362e-14 | 6.362e-14 | 6.362e-14 | 6.362e-14 | 9.992e-14% | 4391.7028 | 4.7496e-14 | 5.1822e-14 | 5.2269e-14 | 5.3815e-14 | 5.3778e-14 | 5.4118e-14 | 5.5447e-14 | 5.9267e-14 | 6.0844e-14 | 5.9351e-14 | 6.3473e-14 | 6.1743e-14 | 6.33e-14 | 6.4422e-14 | 6.3961e-14 | 6.3961e-14 | 6.3961e-14 | 6.3961e-14 | 6.3961e-14 | 6.3961e-14 | 6.3961e-14 | 6.3961e-14 | 6.3961e-14 | 6.3961e-14 | 6.3961e-14 | 6.3961e-14 | 6.3961e-14 | 6.3961e-14 | 6.3961e-14 | 6.3961e-14
Summer Season | [31 empty] | Summer Season
P50 | [31 empty] | P10
% of MD | Summer - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Summer - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 45.5533 | 48.9582 | 49.3004 | 49.1327 | 49.2921 | 49.3577 | 49.5677 | 49.9995 | 50.3627 | 50.5299 | 50.3809 | 51.0058 | 51.1049 | 50.9876 | 51.2228 | 51.3328 | 51.3328 | 51.3328 | 51.3328 | 51.3328 | 51.3328 | 51.3328 | 51.3328 | 51.3328 | 51.3328 | 51.3328 | 51.3328 | 51.3328 | 51.3328 | 51.3328 | 100% | 0 | 56.0411 | 59.8463 | 59.9513 | 59.8381 | 59.8672 | 60.075 | 60.4961 | 61.2377 | 61.6242 | 61.9037 | 62.3269 | 62.867 | 63.5203 | 63.8626 | 63.7516 | 63.8616 | 63.8616 | 63.8616 | 63.8616 | 63.8616 | 63.8616 | 63.8616 | 63.8616 | 63.8616 | 63.8616 | 63.8616 | 63.8616 | 63.8616 | 63.8616 | 63.8616
99% | 0.37816 | 45.0978 | 48.4686 | 48.8074 | 48.6413 | 48.7992 | 48.8641 | 49.072 | 49.4995 | 49.8591 | 50.0246 | 49.8771 | 50.4957 | 50.5938 | 50.4777 | 50.7105 | 50.8194 | 50.8194 | 50.8194 | 50.8194 | 50.8194 | 50.8194 | 50.8194 | 50.8194 | 50.8194 | 50.8194 | 50.8194 | 50.8194 | 50.8194 | 50.8194 | 50.8194 | 99% | 0 | 55.4807 | 59.2478 | 59.3518 | 59.2397 | 59.2685 | 59.4742 | 59.8911 | 60.6254 | 61.0079 | 61.2847 | 61.7036 | 62.2384 | 62.8851 | 63.224 | 63.1141 | 63.223 | 63.223 | 63.223 | 63.223 | 63.223 | 63.223 | 63.223 | 63.223 | 63.223 | 63.223 | 63.223 | 63.223 | 63.223 | 63.223 | 63.223
98% | 0.37816 | 44.6423 | 47.9791 | 48.3144 | 48.15 | 48.3063 | 48.3705 | 48.5763 | 48.9995 | 49.3555 | 49.5193 | 49.3733 | 49.9856 | 50.0828 | 49.9678 | 50.1983 | 50.3061 | 50.3061 | 50.3061 | 50.3061 | 50.3061 | 50.3061 | 50.3061 | 50.3061 | 50.3061 | 50.3061 | 50.3061 | 50.3061 | 50.3061 | 50.3061 | 50.3061 | 98% | 0 | 54.9203 | 58.6494 | 58.7523 | 58.6413 | 58.6699 | 58.8735 | 59.2862 | 60.013 | 60.3917 | 60.6657 | 61.0803 | 61.6097 | 62.2499 | 62.5853 | 62.4766 | 62.5844 | 62.5844 | 62.5844 | 62.5844 | 62.5844 | 62.5844 | 62.5844 | 62.5844 | 62.5844 | 62.5844 | 62.5844 | 62.5844 | 62.5844 | 62.5844 | 62.5844
97% | 0.37816 | 44.1867 | 47.4895 | 47.8214 | 47.6587 | 47.8134 | 47.8769 | 48.0806 | 48.4995 | 48.8518 | 49.014 | 48.8695 | 49.4756 | 49.5717 | 49.458 | 49.6861 | 49.7928 | 49.7928 | 49.7928 | 49.7928 | 49.7928 | 49.7928 | 49.7928 | 49.7928 | 49.7928 | 49.7928 | 49.7928 | 49.7928 | 49.7928 | 49.7928 | 49.7928 | 97% | 0.37816 | 54.3599 | 58.0509 | 58.1528 | 58.0429 | 58.0712 | 58.2727 | 58.6812 | 59.4006 | 59.7754 | 60.0466 | 60.457 | 60.981 | 61.6146 | 61.9467 | 61.8391 | 61.9458 | 61.9458 | 61.9458 | 61.9458 | 61.9458 | 61.9458 | 61.9458 | 61.9458 | 61.9458 | 61.9458 | 61.9458 | 61.9458 | 61.9458 | 61.9458 | 61.9458
95% | 0.75633 | 43.2757 | 46.5103 | 46.8354 | 46.676 | 46.8275 | 46.8898 | 47.0893 | 47.4995 | 47.8446 | 48.0034 | 47.8618 | 48.4555 | 48.5496 | 48.4382 | 48.6616 | 48.7661 | 48.7661 | 48.7661 | 48.7661 | 48.7661 | 48.7661 | 48.7661 | 48.7661 | 48.7661 | 48.7661 | 48.7661 | 48.7661 | 48.7661 | 48.7661 | 48.7661 | 95% | 0.37816 | 53.2391 | 56.854 | 56.9537 | 56.8462 | 56.8738 | 57.0712 | 57.4713 | 58.1758 | 58.543 | 58.8086 | 59.2105 | 59.7237 | 60.3442 | 60.6695 | 60.564 | 60.6685 | 60.6685 | 60.6685 | 60.6685 | 60.6685 | 60.6685 | 60.6685 | 60.6685 | 60.6685 | 60.6685 | 60.6685 | 60.6685 | 60.6685 | 60.6685 | 60.6685
90% | 9.0759 | 40.998 | 44.0624 | 44.3703 | 44.2194 | 44.3629 | 44.4219 | 44.6109 | 44.9995 | 45.3264 | 45.4769 | 45.3428 | 45.9052 | 45.9944 | 45.8888 | 46.1005 | 46.1995 | 46.1995 | 46.1995 | 46.1995 | 46.1995 | 46.1995 | 46.1995 | 46.1995 | 46.1995 | 46.1995 | 46.1995 | 46.1995 | 46.1995 | 46.1995 | 46.1995 | 90% | 0.75633 | 50.437 | 53.8617 | 53.9562 | 53.8543 | 53.8805 | 54.0675 | 54.4465 | 55.114 | 55.4618 | 55.7134 | 56.0942 | 56.5803 | 57.1682 | 57.4763 | 57.3764 | 57.4754 | 57.4754 | 57.4754 | 57.4754 | 57.4754 | 57.4754 | 57.4754 | 57.4754 | 57.4754 | 57.4754 | 57.4754 | 57.4754 | 57.4754 | 57.4754 | 57.4754
85% | 40.4636 | 38.7203 | 41.6145 | 41.9053 | 41.7628 | 41.8983 | 41.954 | 42.1325 | 42.4995 | 42.8083 | 42.9504 | 42.8238 | 43.3549 | 43.4391 | 43.3394 | 43.5393 | 43.6328 | 43.6328 | 43.6328 | 43.6328 | 43.6328 | 43.6328 | 43.6328 | 43.6328 | 43.6328 | 43.6328 | 43.6328 | 43.6328 | 43.6328 | 43.6328 | 43.6328 | 85% | 1.1345 | 47.6349 | 50.8694 | 50.9586 | 50.8624 | 50.8871 | 51.0637 | 51.4217 | 52.0521 | 52.3805 | 52.6182 | 52.9778 | 53.437 | 53.9922 | 54.2832 | 54.1889 | 54.2824 | 54.2824 | 54.2824 | 54.2824 | 54.2824 | 54.2824 | 54.2824 | 54.2824 | 54.2824 | 54.2824 | 54.2824 | 54.2824 | 54.2824 | 54.2824 | 54.2824
80% | 94.5411 | 36.4427 | 39.1666 | 39.4403 | 39.3061 | 39.4337 | 39.4861 | 39.6541 | 39.9996 | 40.2902 | 40.4239 | 40.3047 | 40.8046 | 40.8839 | 40.7901 | 40.9782 | 41.0662 | 41.0662 | 41.0662 | 41.0662 | 41.0662 | 41.0662 | 41.0662 | 41.0662 | 41.0662 | 41.0662 | 41.0662 | 41.0662 | 41.0662 | 41.0662 | 41.0662 | 80% | 2.6471 | 44.8329 | 47.877 | 47.961 | 47.8705 | 47.8938 | 48.06 | 48.3969 | 48.9902 | 49.2993 | 49.523 | 49.8615 | 50.2936 | 50.8162 | 51.0901 | 51.0013 | 51.0893 | 51.0893 | 51.0893 | 51.0893 | 51.0893 | 51.0893 | 51.0893 | 51.0893 | 51.0893 | 51.0893 | 51.0893 | 51.0893 | 51.0893 | 51.0893 | 51.0893
75% | 197.0236 | 34.165 | 36.7187 | 36.9753 | 36.8495 | 36.9691 | 37.0182 | 37.1757 | 37.4996 | 37.772 | 37.8974 | 37.7857 | 38.2543 | 38.3286 | 38.2407 | 38.4171 | 38.4996 | 38.4996 | 38.4996 | 38.4996 | 38.4996 | 38.4996 | 38.4996 | 38.4996 | 38.4996 | 38.4996 | 38.4996 | 38.4996 | 38.4996 | 38.4996 | 38.4996 | 75% | 3.4035 | 42.0308 | 44.8847 | 44.9635 | 44.8786 | 44.9004 | 45.0562 | 45.3721 | 45.9283 | 46.2181 | 46.4278 | 46.7451 | 47.1503 | 47.6402 | 47.8969 | 47.8137 | 47.8962 | 47.8962 | 47.8962 | 47.8962 | 47.8962 | 47.8962 | 47.8962 | 47.8962 | 47.8962 | 47.8962 | 47.8962 | 47.8962 | 47.8962 | 47.8962 | 47.8962
70% | 336.9444 | 31.8873 | 34.2708 | 34.5103 | 34.3929 | 34.5045 | 34.5504 | 34.6974 | 34.9996 | 35.2539 | 35.371 | 35.2666 | 35.704 | 35.7734 | 35.6913 | 35.8559 | 35.9329 | 35.9329 | 35.9329 | 35.9329 | 35.9329 | 35.9329 | 35.9329 | 35.9329 | 35.9329 | 35.9329 | 35.9329 | 35.9329 | 35.9329 | 35.9329 | 35.9329 | 70% | 5.6725 | 39.2288 | 41.8924 | 41.9659 | 41.8867 | 41.907 | 42.0525 | 42.3473 | 42.8664 | 43.1369 | 43.3326 | 43.6288 | 44.0069 | 44.4642 | 44.7038 | 44.6261 | 44.7031 | 44.7031 | 44.7031 | 44.7031 | 44.7031 | 44.7031 | 44.7031 | 44.7031 | 44.7031 | 44.7031 | 44.7031 | 44.7031 | 44.7031 | 44.7031 | 44.7031
65% | 521.4885 | 29.6097 | 31.8228 | 32.0452 | 31.9362 | 32.0399 | 32.0825 | 32.219 | 32.4996 | 32.7358 | 32.8445 | 32.7476 | 33.1537 | 33.2182 | 33.1419 | 33.2948 | 33.3663 | 33.3663 | 33.3663 | 33.3663 | 33.3663 | 33.3663 | 33.3663 | 33.3663 | 33.3663 | 33.3663 | 33.3663 | 33.3663 | 33.3663 | 33.3663 | 33.3663 | 65% | 6.4288 | 36.4267 | 38.9001 | 38.9683 | 38.8948 | 38.9137 | 39.0487 | 39.3225 | 39.8045 | 40.0557 | 40.2374 | 40.5125 | 40.8636 | 41.2882 | 41.5107 | 41.4385 | 41.51 | 41.51 | 41.51 | 41.51 | 41.51 | 41.51 | 41.51 | 41.51 | 41.51 | 41.51 | 41.51 | 41.51 | 41.51 | 41.51 | 41.51
60% | 812.675 | 27.332 | 29.3749 | 29.5802 | 29.4796 | 29.5753 | 29.6146 | 29.7406 | 29.9997 | 30.2176 | 30.318 | 30.2285 | 30.6035 | 30.6629 | 30.5925 | 30.7337 | 30.7997 | 30.7997 | 30.7997 | 30.7997 | 30.7997 | 30.7997 | 30.7997 | 30.7997 | 30.7997 | 30.7997 | 30.7997 | 30.7997 | 30.7997 | 30.7997 | 30.7997 | 60% | 11.3449 | 33.6247 | 35.9078 | 35.9708 | 35.9029 | 35.9203 | 36.045 | 36.2977 | 36.7426 | 36.9745 | 37.1422 | 37.3961 | 37.7202 | 38.1122 | 38.3176 | 38.251 | 38.317 | 38.317 | 38.317 | 38.317 | 38.317 | 38.317 | 38.317 | 38.317 | 38.317 | 38.317 | 38.317 | 38.317 | 38.317 | 38.317 | 38.317
55% | 1202.1843 | 25.0543 | 26.927 | 27.1152 | 27.023 | 27.1107 | 27.1467 | 27.2622 | 27.4997 | 27.6995 | 27.7915 | 27.7095 | 28.0532 | 28.1077 | 28.0432 | 28.1725 | 28.233 | 28.233 | 28.233 | 28.233 | 28.233 | 28.233 | 28.233 | 28.233 | 28.233 | 28.233 | 28.233 | 28.233 | 28.233 | 28.233 | 28.233 | 55% | 35.5474 | 30.8226 | 32.9155 | 32.9732 | 32.911 | 32.927 | 33.0412 | 33.2729 | 33.6808 | 33.8933 | 34.0471 | 34.2798 | 34.5769 | 34.9361 | 35.1244 | 35.0634 | 35.1239 | 35.1239 | 35.1239 | 35.1239 | 35.1239 | 35.1239 | 35.1239 | 35.1239 | 35.1239 | 35.1239 | 35.1239 | 35.1239 | 35.1239 | 35.1239 | 35.1239
50% | 1686.2345 | 22.7767 | 24.4791 | 24.6502 | 24.5663 | 24.6461 | 24.6788 | 24.7838 | 24.9997 | 25.1814 | 25.265 | 25.1904 | 25.5029 | 25.5524 | 25.4938 | 25.6114 | 25.6664 | 25.6664 | 25.6664 | 25.6664 | 25.6664 | 25.6664 | 25.6664 | 25.6664 | 25.6664 | 25.6664 | 25.6664 | 25.6664 | 25.6664 | 25.6664 | 25.6664 | 50% | 95.2974 | 28.0206 | 29.9231 | 29.9756 | 29.919 | 29.9336 | 30.0375 | 30.2481 | 30.6189 | 30.8121 | 30.9519 | 31.1634 | 31.4335 | 31.7601 | 31.9313 | 31.8758 | 31.9308 | 31.9308 | 31.9308 | 31.9308 | 31.9308 | 31.9308 | 31.9308 | 31.9308 | 31.9308 | 31.9308 | 31.9308 | 31.9308 | 31.9308 | 31.9308 | 31.9308
45% | 2129.0649 | 20.499 | 22.0312 | 22.1852 | 22.1097 | 22.1815 | 22.2109 | 22.3054 | 22.4998 | 22.6632 | 22.7385 | 22.6714 | 22.9526 | 22.9972 | 22.9444 | 23.0502 | 23.0997 | 23.0997 | 23.0997 | 23.0997 | 23.0997 | 23.0997 | 23.0997 | 23.0997 | 23.0997 | 23.0997 | 23.0997 | 23.0997 | 23.0997 | 23.0997 | 23.0997 | 45% | 208.7467 | 25.2185 | 26.9308 | 26.9781 | 26.9271 | 26.9402 | 27.0337 | 27.2232 | 27.557 | 27.7309 | 27.8567 | 28.0471 | 28.2902 | 28.5841 | 28.7382 | 28.6882 | 28.7377 | 28.7377 | 28.7377 | 28.7377 | 28.7377 | 28.7377 | 28.7377 | 28.7377 | 28.7377 | 28.7377 | 28.7377 | 28.7377 | 28.7377 | 28.7377 | 28.7377
40% | 2484.5393 | 18.2213 | 19.5833 | 19.7201 | 19.6531 | 19.7169 | 19.7431 | 19.8271 | 19.9998 | 20.1451 | 20.212 | 20.1524 | 20.4023 | 20.4419 | 20.395 | 20.4891 | 20.5331 | 20.5331 | 20.5331 | 20.5331 | 20.5331 | 20.5331 | 20.5331 | 20.5331 | 20.5331 | 20.5331 | 20.5331 | 20.5331 | 20.5331 | 20.5331 | 20.5331 | 40% | 380.4333 | 22.4164 | 23.9385 | 23.9805 | 23.9352 | 23.9469 | 24.03 | 24.1984 | 24.4951 | 24.6497 | 24.7615 | 24.9307 | 25.1468 | 25.4081 | 25.545 | 25.5006 | 25.5446 | 25.5446 | 25.5446 | 25.5446 | 25.5446 | 25.5446 | 25.5446 | 25.5446 | 25.5446 | 25.5446 | 25.5446 | 25.5446 | 25.5446 | 25.5446 | 25.5446
35% | 2808.248 | 15.9437 | 17.1354 | 17.2551 | 17.1964 | 17.2522 | 17.2752 | 17.3487 | 17.4998 | 17.6269 | 17.6855 | 17.6333 | 17.852 | 17.8867 | 17.8457 | 17.928 | 17.9665 | 17.9665 | 17.9665 | 17.9665 | 17.9665 | 17.9665 | 17.9665 | 17.9665 | 17.9665 | 17.9665 | 17.9665 | 17.9665 | 17.9665 | 17.9665 | 17.9665 | 35% | 696.5786 | 19.6144 | 20.9462 | 20.983 | 20.9433 | 20.9535 | 21.0262 | 21.1736 | 21.4332 | 21.5685 | 21.6663 | 21.8144 | 22.0035 | 22.2321 | 22.3519 | 22.3131 | 22.3516 | 22.3516 | 22.3516 | 22.3516 | 22.3516 | 22.3516 | 22.3516 | 22.3516 | 22.3516 | 22.3516 | 22.3516 | 22.3516 | 22.3516 | 22.3516 | 22.3516
30% | 3095.6528 | 13.666 | 14.6875 | 14.7901 | 14.7398 | 14.7876 | 14.8073 | 14.8703 | 14.9998 | 15.1088 | 15.159 | 15.1143 | 15.3017 | 15.3315 | 15.2963 | 15.3668 | 15.3998 | 15.3998 | 15.3998 | 15.3998 | 15.3998 | 15.3998 | 15.3998 | 15.3998 | 15.3998 | 15.3998 | 15.3998 | 15.3998 | 15.3998 | 15.3998 | 15.3998 | 30% | 1260.7997 | 16.8123 | 17.9539 | 17.9854 | 17.9514 | 17.9602 | 18.0225 | 18.1488 | 18.3713 | 18.4873 | 18.5711 | 18.6981 | 18.8601 | 19.0561 | 19.1588 | 19.1255 | 19.1585 | 19.1585 | 19.1585 | 19.1585 | 19.1585 | 19.1585 | 19.1585 | 19.1585 | 19.1585 | 19.1585 | 19.1585 | 19.1585 | 19.1585 | 19.1585 | 19.1585
25% | 3358.8552 | 11.3883 | 12.2396 | 12.3251 | 12.2832 | 12.323 | 12.3394 | 12.3919 | 12.4999 | 12.5907 | 12.6325 | 12.5952 | 12.7514 | 12.7762 | 12.7469 | 12.8057 | 12.8332 | 12.8332 | 12.8332 | 12.8332 | 12.8332 | 12.8332 | 12.8332 | 12.8332 | 12.8332 | 12.8332 | 12.8332 | 12.8332 | 12.8332 | 12.8332 | 12.8332 | 25% | 1965.3198 | 14.0103 | 14.9616 | 14.9878 | 14.9595 | 14.9668 | 15.0187 | 15.124 | 15.3094 | 15.406 | 15.4759 | 15.5817 | 15.7168 | 15.8801 | 15.9656 | 15.9379 | 15.9654 | 15.9654 | 15.9654 | 15.9654 | 15.9654 | 15.9654 | 15.9654 | 15.9654 | 15.9654 | 15.9654 | 15.9654 | 15.9654 | 15.9654 | 15.9654 | 15.9654
20% | 3588.7791 | 9.1107 | 9.7916 | 9.8601 | 9.8265 | 9.8584 | 9.8715 | 9.9135 | 9.9999 | 10.0725 | 10.106 | 10.0762 | 10.2012 | 10.221 | 10.1975 | 10.2446 | 10.2666 | 10.2666 | 10.2666 | 10.2666 | 10.2666 | 10.2666 | 10.2666 | 10.2666 | 10.2666 | 10.2666 | 10.2666 | 10.2666 | 10.2666 | 10.2666 | 10.2666 | 20% | 2490.2118 | 11.2082 | 11.9693 | 11.9903 | 11.9676 | 11.9734 | 12.015 | 12.0992 | 12.2475 | 12.3248 | 12.3807 | 12.4654 | 12.5734 | 12.7041 | 12.7725 | 12.7503 | 12.7723 | 12.7723 | 12.7723 | 12.7723 | 12.7723 | 12.7723 | 12.7723 | 12.7723 | 12.7723 | 12.7723 | 12.7723 | 12.7723 | 12.7723 | 12.7723 | 12.7723
15% | 3802.4419 | 6.833 | 7.3437 | 7.3951 | 7.3699 | 7.3938 | 7.4036 | 7.4351 | 7.4999 | 7.5544 | 7.5795 | 7.5571 | 7.6509 | 7.6657 | 7.6481 | 7.6834 | 7.6999 | 7.6999 | 7.6999 | 7.6999 | 7.6999 | 7.6999 | 7.6999 | 7.6999 | 7.6999 | 7.6999 | 7.6999 | 7.6999 | 7.6999 | 7.6999 | 7.6999 | 15% | 2997.7083 | 8.4062 | 8.9769 | 8.9927 | 8.9757 | 8.9801 | 9.0112 | 9.0744 | 9.1857 | 9.2436 | 9.2856 | 9.349 | 9.4301 | 9.528 | 9.5794 | 9.5627 | 9.5792 | 9.5792 | 9.5792 | 9.5792 | 9.5792 | 9.5792 | 9.5792 | 9.5792 | 9.5792 | 9.5792 | 9.5792 | 9.5792 | 9.5792 | 9.5792 | 9.5792
10% | 4024.8025 | 4.5553 | 4.8958 | 4.93 | 4.9133 | 4.9292 | 4.9358 | 4.9568 | 4.9999 | 5.0363 | 5.053 | 5.0381 | 5.1006 | 5.1105 | 5.0988 | 5.1223 | 5.1333 | 5.1333 | 5.1333 | 5.1333 | 5.1333 | 5.1333 | 5.1333 | 5.1333 | 5.1333 | 5.1333 | 5.1333 | 5.1333 | 5.1333 | 5.1333 | 5.1333 | 10% | 3491.5908 | 5.6041 | 5.9846 | 5.9951 | 5.9838 | 5.9867 | 6.0075 | 6.0496 | 6.1238 | 6.1624 | 6.1904 | 6.2327 | 6.2867 | 6.352 | 6.3863 | 6.3752 | 6.3862 | 6.3862 | 6.3862 | 6.3862 | 6.3862 | 6.3862 | 6.3862 | 6.3862 | 6.3862 | 6.3862 | 6.3862 | 6.3862 | 6.3862 | 6.3862 | 6.3862
5% | 4239.978 | 2.2777 | 2.4479 | 2.465 | 2.4566 | 2.4646 | 2.4679 | 2.4784 | 2.5 | 2.5181 | 2.5265 | 2.519 | 2.5503 | 2.5552 | 2.5494 | 2.5611 | 2.5666 | 2.5666 | 2.5666 | 2.5666 | 2.5666 | 2.5666 | 2.5666 | 2.5666 | 2.5666 | 2.5666 | 2.5666 | 2.5666 | 2.5666 | 2.5666 | 2.5666 | 5% | 3955.9766 | 2.8021 | 2.9923 | 2.9976 | 2.9919 | 2.9934 | 3.0037 | 3.0248 | 3.0619 | 3.0812 | 3.0952 | 3.1163 | 3.1434 | 3.176 | 3.1931 | 3.1876 | 3.1931 | 3.1931 | 3.1931 | 3.1931 | 3.1931 | 3.1931 | 3.1931 | 3.1931 | 3.1931 | 3.1931 | 3.1931 | 3.1931 | 3.1931 | 3.1931 | 3.1931
9.992e-14% | 4391.6218 | 4.5517e-14 | 4.8919e-14 | 4.9261e-14 | 4.9093e-14 | 4.9253e-14 | 4.9318e-14 | 4.9528e-14 | 4.9959e-14 | 5.0322e-14 | 5.049e-14 | 5.0341e-14 | 5.0965e-14 | 5.1064e-14 | 5.0947e-14 | 5.1182e-14 | 5.1292e-14 | 5.1292e-14 | 5.1292e-14 | 5.1292e-14 | 5.1292e-14 | 5.1292e-14 | 5.1292e-14 | 5.1292e-14 | 5.1292e-14 | 5.1292e-14 | 5.1292e-14 | 5.1292e-14 | 5.1292e-14 | 5.1292e-14 | 5.1292e-14 | 9.992e-14% | 4391.6218 | 5.5996e-14 | 5.9798e-14 | 5.9903e-14 | 5.979e-14 | 5.9819e-14 | 6.0027e-14 | 6.0448e-14 | 6.1189e-14 | 6.1575e-14 | 6.1854e-14 | 6.2277e-14 | 6.2817e-14 | 6.3469e-14 | 6.3812e-14 | 6.3701e-14 | 6.3811e-14 | 6.3811e-14 | 6.3811e-14 | 6.3811e-14 | 6.3811e-14 | 6.3811e-14 | 6.3811e-14 | 6.3811e-14 | 6.3811e-14 | 6.3811e-14 | 6.3811e-14 | 6.3811e-14 | 6.3811e-14 | 6.3811e-14 | 6.3811e-14
Option 7
Winter Season | [31 empty] | Winter Season
P50 | [31 empty] | P10
% of MD | Winter - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Winter - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 43.3628 | 47.9013 | 48.3825 | 48.9775 | 49.7674 | 50.5163 | 51.825 | 55.1166 | 56.887 | 55.5954 | 59.594 | 60.3144 | 60.8323 | 63.2734 | 63.6707 | 63.6707 | 63.6707 | 63.6707 | 63.6707 | 63.6707 | 63.6707 | 63.6707 | 63.6707 | 63.6707 | 63.6707 | 63.6707 | 63.6707 | 63.6707 | 63.6707 | 63.6707 | 100% | 0 | 47.5339 | 51.863 | 52.3113 | 53.8585 | 53.8208 | 54.161 | 55.4916 | 59.3146 | 60.8922 | 59.3989 | 63.524 | 61.792 | 63.3504 | 64.4734 | 64.012 | 64.012 | 64.012 | 64.012 | 64.012 | 64.012 | 64.012 | 64.012 | 64.012 | 64.012 | 64.012 | 64.012 | 64.012 | 64.012 | 64.012 | 64.012
99% | 0.2972 | 42.9291 | 47.4223 | 47.8987 | 48.4877 | 49.2697 | 50.0111 | 51.3068 | 54.5654 | 56.3182 | 55.0395 | 58.9981 | 59.7113 | 60.224 | 62.6406 | 63.034 | 63.034 | 63.034 | 63.034 | 63.034 | 63.034 | 63.034 | 63.034 | 63.034 | 63.034 | 63.034 | 63.034 | 63.034 | 63.034 | 63.034 | 63.034 | 99% | 0.2972 | 47.0586 | 51.3443 | 51.7882 | 53.3199 | 53.2826 | 53.6194 | 54.9367 | 58.7214 | 60.2833 | 58.8049 | 62.8887 | 61.1741 | 62.7169 | 63.8287 | 63.3719 | 63.3719 | 63.3719 | 63.3719 | 63.3719 | 63.3719 | 63.3719 | 63.3719 | 63.3719 | 63.3719 | 63.3719 | 63.3719 | 63.3719 | 63.3719 | 63.3719 | 63.3719
98% | 0.2972 | 42.4955 | 46.9432 | 47.4149 | 47.9979 | 48.7721 | 49.506 | 50.7885 | 54.0143 | 55.7493 | 54.4835 | 58.4021 | 59.1081 | 59.6156 | 62.0079 | 62.3973 | 62.3973 | 62.3973 | 62.3973 | 62.3973 | 62.3973 | 62.3973 | 62.3973 | 62.3973 | 62.3973 | 62.3973 | 62.3973 | 62.3973 | 62.3973 | 62.3973 | 62.3973 | 98% | 0.2972 | 46.5832 | 50.8257 | 51.2651 | 52.7813 | 52.7443 | 53.0778 | 54.3818 | 58.1283 | 59.6743 | 58.2109 | 62.2535 | 60.5562 | 62.0834 | 63.184 | 62.7318 | 62.7318 | 62.7318 | 62.7318 | 62.7318 | 62.7318 | 62.7318 | 62.7318 | 62.7318 | 62.7318 | 62.7318 | 62.7318 | 62.7318 | 62.7318 | 62.7318 | 62.7318
97% | 0.2972 | 42.0619 | 46.4642 | 46.931 | 47.5082 | 48.2744 | 49.0008 | 50.2703 | 53.4631 | 55.1804 | 53.9276 | 57.8062 | 58.505 | 59.0073 | 61.3752 | 61.7606 | 61.7606 | 61.7606 | 61.7606 | 61.7606 | 61.7606 | 61.7606 | 61.7606 | 61.7606 | 61.7606 | 61.7606 | 61.7606 | 61.7606 | 61.7606 | 61.7606 | 61.7606 | 97% | 0.2972 | 46.1079 | 50.3071 | 50.7419 | 52.2427 | 52.2061 | 52.5362 | 53.8269 | 57.5352 | 59.0654 | 57.6169 | 61.6183 | 59.9383 | 61.4499 | 62.5392 | 62.0917 | 62.0917 | 62.0917 | 62.0917 | 62.0917 | 62.0917 | 62.0917 | 62.0917 | 62.0917 | 62.0917 | 62.0917 | 62.0917 | 62.0917 | 62.0917 | 62.0917 | 62.0917
95% | 1.486 | 41.1946 | 45.5062 | 45.9634 | 46.5286 | 47.2791 | 47.9905 | 49.2338 | 52.3608 | 54.0427 | 52.8157 | 56.6143 | 57.2987 | 57.7907 | 60.1097 | 60.4871 | 60.4871 | 60.4871 | 60.4871 | 60.4871 | 60.4871 | 60.4871 | 60.4871 | 60.4871 | 60.4871 | 60.4871 | 60.4871 | 60.4871 | 60.4871 | 60.4871 | 60.4871 | 95% | 1.486 | 45.1572 | 49.2698 | 49.6957 | 51.1655 | 51.1297 | 51.4529 | 52.717 | 56.3489 | 57.8476 | 56.4289 | 60.3478 | 58.7024 | 60.1829 | 61.2498 | 60.8114 | 60.8114 | 60.8114 | 60.8114 | 60.8114 | 60.8114 | 60.8114 | 60.8114 | 60.8114 | 60.8114 | 60.8114 | 60.8114 | 60.8114 | 60.8114 | 60.8114 | 60.8114
90% | 8.6188 | 39.0265 | 43.1111 | 43.5443 | 44.0797 | 44.7907 | 45.4647 | 46.6425 | 49.6049 | 51.1983 | 50.0359 | 53.6346 | 54.283 | 54.7491 | 56.946 | 57.3036 | 57.3036 | 57.3036 | 57.3036 | 57.3036 | 57.3036 | 57.3036 | 57.3036 | 57.3036 | 57.3036 | 57.3036 | 57.3036 | 57.3036 | 57.3036 | 57.3036 | 57.3036 | 90% | 8.6188 | 42.7805 | 46.6767 | 47.0802 | 48.4726 | 48.4387 | 48.7449 | 49.9425 | 53.3831 | 54.803 | 53.459 | 57.1716 | 55.6128 | 57.0154 | 58.0261 | 57.6108 | 57.6108 | 57.6108 | 57.6108 | 57.6108 | 57.6108 | 57.6108 | 57.6108 | 57.6108 | 57.6108 | 57.6108 | 57.6108 | 57.6108 | 57.6108 | 57.6108 | 57.6108
85% | 40.1218 | 36.8584 | 40.7161 | 41.1251 | 41.6309 | 42.3023 | 42.9389 | 44.0513 | 46.8491 | 48.354 | 47.2561 | 50.6549 | 51.2673 | 51.7074 | 53.7823 | 54.1201 | 54.1201 | 54.1201 | 54.1201 | 54.1201 | 54.1201 | 54.1201 | 54.1201 | 54.1201 | 54.1201 | 54.1201 | 54.1201 | 54.1201 | 54.1201 | 54.1201 | 54.1201 | 85% | 40.1218 | 40.4038 | 44.0835 | 44.4646 | 45.7797 | 45.7477 | 46.0368 | 47.1679 | 50.4174 | 51.7583 | 50.489 | 53.9954 | 52.5232 | 53.8479 | 54.8024 | 54.4102 | 54.4102 | 54.4102 | 54.4102 | 54.4102 | 54.4102 | 54.4102 | 54.4102 | 54.4102 | 54.4102 | 54.4102 | 54.4102 | 54.4102 | 54.4102 | 54.4102 | 54.4102
80% | 93.0231 | 34.6902 | 38.321 | 38.706 | 39.182 | 39.8139 | 40.413 | 41.46 | 44.0933 | 45.5096 | 44.4764 | 47.6752 | 48.2515 | 48.6658 | 50.6187 | 50.9365 | 50.9365 | 50.9365 | 50.9365 | 50.9365 | 50.9365 | 50.9365 | 50.9365 | 50.9365 | 50.9365 | 50.9365 | 50.9365 | 50.9365 | 50.9365 | 50.9365 | 50.9365 | 80% | 93.0231 | 38.0271 | 41.4904 | 41.849 | 43.0868 | 43.0566 | 43.3288 | 44.3933 | 47.4517 | 48.7137 | 47.5191 | 50.8192 | 49.4336 | 50.6803 | 51.5787 | 51.2096 | 51.2096 | 51.2096 | 51.2096 | 51.2096 | 51.2096 | 51.2096 | 51.2096 | 51.2096 | 51.2096 | 51.2096 | 51.2096 | 51.2096 | 51.2096 | 51.2096 | 51.2096
75% | 197.0426 | 32.5221 | 35.926 | 36.2869 | 36.7331 | 37.3256 | 37.8872 | 38.8688 | 41.3374 | 42.6653 | 41.6966 | 44.6955 | 45.2358 | 45.6242 | 47.455 | 47.753 | 47.753 | 47.753 | 47.753 | 47.753 | 47.753 | 47.753 | 47.753 | 47.753 | 47.753 | 47.753 | 47.753 | 47.753 | 47.753 | 47.753 | 47.753 | 75% | 197.0426 | 35.6504 | 38.8972 | 39.2335 | 40.3939 | 40.3656 | 40.6207 | 41.6187 | 44.4859 | 45.6691 | 44.5491 | 47.643 | 46.344 | 47.5128 | 48.3551 | 48.009 | 48.009 | 48.009 | 48.009 | 48.009 | 48.009 | 48.009 | 48.009 | 48.009 | 48.009 | 48.009 | 48.009 | 48.009 | 48.009 | 48.009 | 48.009
70% | 378.0365 | 30.3539 | 33.5309 | 33.8678 | 34.2842 | 34.8372 | 35.3614 | 36.2775 | 38.5816 | 39.8209 | 38.9168 | 41.7158 | 42.2201 | 42.5826 | 44.2913 | 44.5695 | 44.5695 | 44.5695 | 44.5695 | 44.5695 | 44.5695 | 44.5695 | 44.5695 | 44.5695 | 44.5695 | 44.5695 | 44.5695 | 44.5695 | 44.5695 | 44.5695 | 44.5695 | 70% | 378.0365 | 33.2737 | 36.3041 | 36.6179 | 37.7009 | 37.6745 | 37.9127 | 38.8441 | 41.5202 | 42.6245 | 41.5792 | 44.4668 | 43.2544 | 44.3453 | 45.1314 | 44.8084 | 44.8084 | 44.8084 | 44.8084 | 44.8084 | 44.8084 | 44.8084 | 44.8084 | 44.8084 | 44.8084 | 44.8084 | 44.8084 | 44.8084 | 44.8084 | 44.8084 | 44.8084
65% | 616.0926 | 28.1858 | 31.1358 | 31.4486 | 31.8354 | 32.3488 | 32.8356 | 33.6863 | 35.8258 | 36.9766 | 36.137 | 38.7361 | 39.2044 | 39.541 | 41.1277 | 41.3859 | 41.3859 | 41.3859 | 41.3859 | 41.3859 | 41.3859 | 41.3859 | 41.3859 | 41.3859 | 41.3859 | 41.3859 | 41.3859 | 41.3859 | 41.3859 | 41.3859 | 41.3859 | 65% | 616.0926 | 30.897 | 33.7109 | 34.0023 | 35.008 | 34.9835 | 35.2046 | 36.0696 | 38.5545 | 39.5799 | 38.6093 | 41.2906 | 40.1648 | 41.1778 | 41.9077 | 41.6078 | 41.6078 | 41.6078 | 41.6078 | 41.6078 | 41.6078 | 41.6078 | 41.6078 | 41.6078 | 41.6078 | 41.6078 | 41.6078 | 41.6078 | 41.6078 | 41.6078 | 41.6078
60% | 934.9866 | 26.0177 | 28.7408 | 29.0295 | 29.3865 | 29.8605 | 30.3098 | 31.095 | 33.07 | 34.1322 | 33.3573 | 35.7564 | 36.1887 | 36.4994 | 37.964 | 38.2024 | 38.2024 | 38.2024 | 38.2024 | 38.2024 | 38.2024 | 38.2024 | 38.2024 | 38.2024 | 38.2024 | 38.2024 | 38.2024 | 38.2024 | 38.2024 | 38.2024 | 38.2024 | 60% | 934.9866 | 28.5203 | 31.1178 | 31.3868 | 32.3151 | 32.2925 | 32.4966 | 33.295 | 35.5888 | 36.5353 | 35.6393 | 38.1144 | 37.0752 | 38.0103 | 38.6841 | 38.4072 | 38.4072 | 38.4072 | 38.4072 | 38.4072 | 38.4072 | 38.4072 | 38.4072 | 38.4072 | 38.4072 | 38.4072 | 38.4072 | 38.4072 | 38.4072 | 38.4072 | 38.4072
55% | 1310.9428 | 23.8495 | 26.3457 | 26.6104 | 26.9376 | 27.3721 | 27.784 | 28.5038 | 30.3141 | 31.2879 | 30.5775 | 32.7767 | 33.1729 | 33.4578 | 34.8003 | 35.0189 | 35.0189 | 35.0189 | 35.0189 | 35.0189 | 35.0189 | 35.0189 | 35.0189 | 35.0189 | 35.0189 | 35.0189 | 35.0189 | 35.0189 | 35.0189 | 35.0189 | 35.0189 | 55% | 1310.9428 | 26.1436 | 28.5246 | 28.7712 | 29.6222 | 29.6014 | 29.7885 | 30.5204 | 32.623 | 33.4907 | 32.6694 | 34.9382 | 33.9856 | 34.8427 | 35.4604 | 35.2066 | 35.2066 | 35.2066 | 35.2066 | 35.2066 | 35.2066 | 35.2066 | 35.2066 | 35.2066 | 35.2066 | 35.2066 | 35.2066 | 35.2066 | 35.2066 | 35.2066 | 35.2066
50% | 1730.2899 | 21.6814 | 23.9506 | 24.1913 | 24.4887 | 24.8837 | 25.2582 | 25.9125 | 27.5583 | 28.4435 | 27.7977 | 29.797 | 30.1572 | 30.4161 | 31.6367 | 31.8353 | 31.8353 | 31.8353 | 31.8353 | 31.8353 | 31.8353 | 31.8353 | 31.8353 | 31.8353 | 31.8353 | 31.8353 | 31.8353 | 31.8353 | 31.8353 | 31.8353 | 31.8353 | 50% | 1730.2899 | 23.7669 | 25.9315 | 26.1556 | 26.9292 | 26.9104 | 27.0805 | 27.7458 | 29.6573 | 30.4461 | 29.6994 | 31.762 | 30.896 | 31.6752 | 32.2367 | 32.006 | 32.006 | 32.006 | 32.006 | 32.006 | 32.006 | 32.006 | 32.006 | 32.006 | 32.006 | 32.006 | 32.006 | 32.006 | 32.006 | 32.006 | 32.006
45% | 2168.0633 | 19.5132 | 21.5556 | 21.7721 | 22.0399 | 22.3953 | 22.7323 | 23.3213 | 24.8025 | 25.5992 | 25.0179 | 26.8173 | 27.1415 | 27.3745 | 28.473 | 28.6518 | 28.6518 | 28.6518 | 28.6518 | 28.6518 | 28.6518 | 28.6518 | 28.6518 | 28.6518 | 28.6518 | 28.6518 | 28.6518 | 28.6518 | 28.6518 | 28.6518 | 28.6518 | 45% | 2168.0633 | 21.3903 | 23.3383 | 23.5401 | 24.2363 | 24.2193 | 24.3724 | 24.9712 | 26.6916 | 27.4015 | 26.7295 | 28.5858 | 27.8064 | 28.5077 | 29.013 | 28.8054 | 28.8054 | 28.8054 | 28.8054 | 28.8054 | 28.8054 | 28.8054 | 28.8054 | 28.8054 | 28.8054 | 28.8054 | 28.8054 | 28.8054 | 28.8054 | 28.8054 | 28.8054
40% | 2609.7004 | 17.3451 | 19.1605 | 19.353 | 19.591 | 19.907 | 20.2065 | 20.73 | 22.0466 | 22.7548 | 22.2382 | 23.8376 | 24.1258 | 24.3329 | 25.3093 | 25.4683 | 25.4683 | 25.4683 | 25.4683 | 25.4683 | 25.4683 | 25.4683 | 25.4683 | 25.4683 | 25.4683 | 25.4683 | 25.4683 | 25.4683 | 25.4683 | 25.4683 | 25.4683 | 40% | 2609.7004 | 19.0136 | 20.7452 | 20.9245 | 21.5434 | 21.5283 | 21.6644 | 22.1966 | 23.7258 | 24.3569 | 23.7595 | 25.4096 | 24.7168 | 25.3402 | 25.7894 | 25.6048 | 25.6048 | 25.6048 | 25.6048 | 25.6048 | 25.6048 | 25.6048 | 25.6048 | 25.6048 | 25.6048 | 25.6048 | 25.6048 | 25.6048 | 25.6048 | 25.6048 | 25.6048
35% | 2998.1389 | 15.177 | 16.7654 | 16.9339 | 17.1421 | 17.4186 | 17.6807 | 18.1388 | 19.2908 | 19.9105 | 19.4584 | 20.8579 | 21.1101 | 21.2913 | 22.1457 | 22.2847 | 22.2847 | 22.2847 | 22.2847 | 22.2847 | 22.2847 | 22.2847 | 22.2847 | 22.2847 | 22.2847 | 22.2847 | 22.2847 | 22.2847 | 22.2847 | 22.2847 | 22.2847 | 35% | 2998.1389 | 16.6369 | 18.152 | 18.3089 | 18.8505 | 18.8373 | 18.9563 | 19.4221 | 20.7601 | 21.3123 | 20.7896 | 22.2334 | 21.6272 | 22.1726 | 22.5657 | 22.4042 | 22.4042 | 22.4042 | 22.4042 | 22.4042 | 22.4042 | 22.4042 | 22.4042 | 22.4042 | 22.4042 | 22.4042 | 22.4042 | 22.4042 | 22.4042 | 22.4042 | 22.4042
30% | 3309.3057 | 13.0088 | 14.3704 | 14.5148 | 14.6932 | 14.9302 | 15.1549 | 15.5475 | 16.535 | 17.0661 | 16.6786 | 17.8782 | 18.0943 | 18.2497 | 18.982 | 19.1012 | 19.1012 | 19.1012 | 19.1012 | 19.1012 | 19.1012 | 19.1012 | 19.1012 | 19.1012 | 19.1012 | 19.1012 | 19.1012 | 19.1012 | 19.1012 | 19.1012 | 19.1012 | 30% | 3309.3057 | 14.2602 | 15.5589 | 15.6934 | 16.1575 | 16.1462 | 16.2483 | 16.6475 | 17.7944 | 18.2677 | 17.8197 | 19.0572 | 18.5376 | 19.0051 | 19.342 | 19.2036 | 19.2036 | 19.2036 | 19.2036 | 19.2036 | 19.2036 | 19.2036 | 19.2036 | 19.2036 | 19.2036 | 19.2036 | 19.2036 | 19.2036 | 19.2036 | 19.2036 | 19.2036
25% | 3537.8514 | 10.8407 | 11.9753 | 12.0956 | 12.2444 | 12.4419 | 12.6291 | 12.9563 | 13.7791 | 14.2218 | 13.8989 | 14.8985 | 15.0786 | 15.2081 | 15.8183 | 15.9177 | 15.9177 | 15.9177 | 15.9177 | 15.9177 | 15.9177 | 15.9177 | 15.9177 | 15.9177 | 15.9177 | 15.9177 | 15.9177 | 15.9177 | 15.9177 | 15.9177 | 15.9177 | 25% | 3537.8514 | 11.8835 | 12.9657 | 13.0778 | 13.4646 | 13.4552 | 13.5402 | 13.8729 | 14.8286 | 15.223 | 14.8497 | 15.881 | 15.448 | 15.8376 | 16.1184 | 16.003 | 16.003 | 16.003 | 16.003 | 16.003 | 16.003 | 16.003 | 16.003 | 16.003 | 16.003 | 16.003 | 16.003 | 16.003 | 16.003 | 16.003 | 16.003
20% | 3731.0305 | 8.6726 | 9.5803 | 9.6765 | 9.7955 | 9.9535 | 10.1033 | 10.365 | 11.0233 | 11.3774 | 11.1191 | 11.9188 | 12.0629 | 12.1665 | 12.6547 | 12.7341 | 12.7341 | 12.7341 | 12.7341 | 12.7341 | 12.7341 | 12.7341 | 12.7341 | 12.7341 | 12.7341 | 12.7341 | 12.7341 | 12.7341 | 12.7341 | 12.7341 | 12.7341 | 20% | 3731.0305 | 9.5068 | 10.3726 | 10.4623 | 10.7717 | 10.7642 | 10.8322 | 11.0983 | 11.8629 | 12.1784 | 11.8798 | 12.7048 | 12.3584 | 12.6701 | 12.8947 | 12.8024 | 12.8024 | 12.8024 | 12.8024 | 12.8024 | 12.8024 | 12.8024 | 12.8024 | 12.8024 | 12.8024 | 12.8024 | 12.8024 | 12.8024 | 12.8024 | 12.8024 | 12.8024
15% | 3910.2412 | 6.5044 | 7.1852 | 7.2574 | 7.3466 | 7.4651 | 7.5774 | 7.7738 | 8.2675 | 8.5331 | 8.3393 | 8.9391 | 9.0472 | 9.1248 | 9.491 | 9.5506 | 9.5506 | 9.5506 | 9.5506 | 9.5506 | 9.5506 | 9.5506 | 9.5506 | 9.5506 | 9.5506 | 9.5506 | 9.5506 | 9.5506 | 9.5506 | 9.5506 | 9.5506 | 15% | 3910.2412 | 7.1301 | 7.7794 | 7.8467 | 8.0788 | 8.0731 | 8.1241 | 8.3237 | 8.8972 | 9.1338 | 8.9098 | 9.5286 | 9.2688 | 9.5026 | 9.671 | 9.6018 | 9.6018 | 9.6018 | 9.6018 | 9.6018 | 9.6018 | 9.6018 | 9.6018 | 9.6018 | 9.6018 | 9.6018 | 9.6018 | 9.6018 | 9.6018 | 9.6018 | 9.6018
10% | 4075.1864 | 4.3363 | 4.7901 | 4.8383 | 4.8977 | 4.9767 | 5.0516 | 5.1825 | 5.5117 | 5.6887 | 5.5595 | 5.9594 | 6.0314 | 6.0832 | 6.3273 | 6.3671 | 6.3671 | 6.3671 | 6.3671 | 6.3671 | 6.3671 | 6.3671 | 6.3671 | 6.3671 | 6.3671 | 6.3671 | 6.3671 | 6.3671 | 6.3671 | 6.3671 | 6.3671 | 10% | 4075.1864 | 4.7534 | 5.1863 | 5.2311 | 5.3858 | 5.3821 | 5.4161 | 5.5492 | 5.9315 | 6.0892 | 5.9399 | 6.3524 | 6.1792 | 6.335 | 6.4473 | 6.4012 | 6.4012 | 6.4012 | 6.4012 | 6.4012 | 6.4012 | 6.4012 | 6.4012 | 6.4012 | 6.4012 | 6.4012 | 6.4012 | 6.4012 | 6.4012 | 6.4012 | 6.4012
5% | 4251.7223 | 2.1681 | 2.3951 | 2.4191 | 2.4489 | 2.4884 | 2.5258 | 2.5913 | 2.7558 | 2.8444 | 2.7798 | 2.9797 | 3.0157 | 3.0416 | 3.1637 | 3.1835 | 3.1835 | 3.1835 | 3.1835 | 3.1835 | 3.1835 | 3.1835 | 3.1835 | 3.1835 | 3.1835 | 3.1835 | 3.1835 | 3.1835 | 3.1835 | 3.1835 | 3.1835 | 5% | 4251.7223 | 2.3767 | 2.5931 | 2.6156 | 2.6929 | 2.691 | 2.708 | 2.7746 | 2.9657 | 3.0446 | 2.9699 | 3.1762 | 3.0896 | 3.1675 | 3.2237 | 3.2006 | 3.2006 | 3.2006 | 3.2006 | 3.2006 | 3.2006 | 3.2006 | 3.2006 | 3.2006 | 3.2006 | 3.2006 | 3.2006 | 3.2006 | 3.2006 | 3.2006 | 3.2006
9.992e-14% | 4391.7028 | 4.3328e-14 | 4.7863e-14 | 4.8344e-14 | 4.8938e-14 | 4.9728e-14 | 5.0476e-14 | 5.1784e-14 | 5.5073e-14 | 5.6842e-14 | 5.5551e-14 | 5.9546e-14 | 6.0266e-14 | 6.0784e-14 | 6.3223e-14 | 6.362e-14 | 6.362e-14 | 6.362e-14 | 6.362e-14 | 6.362e-14 | 6.362e-14 | 6.362e-14 | 6.362e-14 | 6.362e-14 | 6.362e-14 | 6.362e-14 | 6.362e-14 | 6.362e-14 | 6.362e-14 | 6.362e-14 | 6.362e-14 | 9.992e-14% | 4391.7028 | 4.7496e-14 | 5.1822e-14 | 5.2269e-14 | 5.3815e-14 | 5.3778e-14 | 5.4118e-14 | 5.5447e-14 | 5.9267e-14 | 6.0844e-14 | 5.9351e-14 | 6.3473e-14 | 6.1743e-14 | 6.33e-14 | 6.4422e-14 | 6.3961e-14 | 6.3961e-14 | 6.3961e-14 | 6.3961e-14 | 6.3961e-14 | 6.3961e-14 | 6.3961e-14 | 6.3961e-14 | 6.3961e-14 | 6.3961e-14 | 6.3961e-14 | 6.3961e-14 | 6.3961e-14 | 6.3961e-14 | 6.3961e-14 | 6.3961e-14
Summer Season | [31 empty] | Summer Season
P50 | [31 empty] | P10
% of MD | Summer - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Summer - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 45.5533 | 48.9582 | 49.3004 | 49.1327 | 49.2921 | 49.3577 | 49.5677 | 49.9995 | 50.3627 | 50.5299 | 50.3809 | 51.0058 | 51.1049 | 50.9876 | 51.2228 | 51.3328 | 51.3328 | 51.3328 | 51.3328 | 51.3328 | 51.3328 | 51.3328 | 51.3328 | 51.3328 | 51.3328 | 51.3328 | 51.3328 | 51.3328 | 51.3328 | 51.3328 | 100% | 0 | 56.0411 | 59.8463 | 59.9513 | 59.8381 | 59.8672 | 60.075 | 60.4961 | 61.2377 | 61.6242 | 61.9037 | 62.3269 | 62.867 | 63.5203 | 63.8626 | 63.7516 | 63.8616 | 63.8616 | 63.8616 | 63.8616 | 63.8616 | 63.8616 | 63.8616 | 63.8616 | 63.8616 | 63.8616 | 63.8616 | 63.8616 | 63.8616 | 63.8616 | 63.8616
99% | 0.37816 | 45.0978 | 48.4686 | 48.8074 | 48.6413 | 48.7992 | 48.8641 | 49.072 | 49.4995 | 49.8591 | 50.0246 | 49.8771 | 50.4957 | 50.5938 | 50.4777 | 50.7105 | 50.8194 | 50.8194 | 50.8194 | 50.8194 | 50.8194 | 50.8194 | 50.8194 | 50.8194 | 50.8194 | 50.8194 | 50.8194 | 50.8194 | 50.8194 | 50.8194 | 50.8194 | 99% | 0 | 55.4807 | 59.2478 | 59.3518 | 59.2397 | 59.2685 | 59.4742 | 59.8911 | 60.6254 | 61.0079 | 61.2847 | 61.7036 | 62.2384 | 62.8851 | 63.224 | 63.1141 | 63.223 | 63.223 | 63.223 | 63.223 | 63.223 | 63.223 | 63.223 | 63.223 | 63.223 | 63.223 | 63.223 | 63.223 | 63.223 | 63.223 | 63.223
98% | 0.37816 | 44.6423 | 47.9791 | 48.3144 | 48.15 | 48.3063 | 48.3705 | 48.5763 | 48.9995 | 49.3555 | 49.5193 | 49.3733 | 49.9856 | 50.0828 | 49.9678 | 50.1983 | 50.3061 | 50.3061 | 50.3061 | 50.3061 | 50.3061 | 50.3061 | 50.3061 | 50.3061 | 50.3061 | 50.3061 | 50.3061 | 50.3061 | 50.3061 | 50.3061 | 50.3061 | 98% | 0 | 54.9203 | 58.6494 | 58.7523 | 58.6413 | 58.6699 | 58.8735 | 59.2862 | 60.013 | 60.3917 | 60.6657 | 61.0803 | 61.6097 | 62.2499 | 62.5853 | 62.4766 | 62.5844 | 62.5844 | 62.5844 | 62.5844 | 62.5844 | 62.5844 | 62.5844 | 62.5844 | 62.5844 | 62.5844 | 62.5844 | 62.5844 | 62.5844 | 62.5844 | 62.5844
97% | 0.37816 | 44.1867 | 47.4895 | 47.8214 | 47.6587 | 47.8134 | 47.8769 | 48.0806 | 48.4995 | 48.8518 | 49.014 | 48.8695 | 49.4756 | 49.5717 | 49.458 | 49.6861 | 49.7928 | 49.7928 | 49.7928 | 49.7928 | 49.7928 | 49.7928 | 49.7928 | 49.7928 | 49.7928 | 49.7928 | 49.7928 | 49.7928 | 49.7928 | 49.7928 | 49.7928 | 97% | 0.37816 | 54.3599 | 58.0509 | 58.1528 | 58.0429 | 58.0712 | 58.2727 | 58.6812 | 59.4006 | 59.7754 | 60.0466 | 60.457 | 60.981 | 61.6146 | 61.9467 | 61.8391 | 61.9458 | 61.9458 | 61.9458 | 61.9458 | 61.9458 | 61.9458 | 61.9458 | 61.9458 | 61.9458 | 61.9458 | 61.9458 | 61.9458 | 61.9458 | 61.9458 | 61.9458
95% | 0.75633 | 43.2757 | 46.5103 | 46.8354 | 46.676 | 46.8275 | 46.8898 | 47.0893 | 47.4995 | 47.8446 | 48.0034 | 47.8618 | 48.4555 | 48.5496 | 48.4382 | 48.6616 | 48.7661 | 48.7661 | 48.7661 | 48.7661 | 48.7661 | 48.7661 | 48.7661 | 48.7661 | 48.7661 | 48.7661 | 48.7661 | 48.7661 | 48.7661 | 48.7661 | 48.7661 | 95% | 0.37816 | 53.2391 | 56.854 | 56.9537 | 56.8462 | 56.8738 | 57.0712 | 57.4713 | 58.1758 | 58.543 | 58.8086 | 59.2105 | 59.7237 | 60.3442 | 60.6695 | 60.564 | 60.6685 | 60.6685 | 60.6685 | 60.6685 | 60.6685 | 60.6685 | 60.6685 | 60.6685 | 60.6685 | 60.6685 | 60.6685 | 60.6685 | 60.6685 | 60.6685 | 60.6685
90% | 9.0759 | 40.998 | 44.0624 | 44.3703 | 44.2194 | 44.3629 | 44.4219 | 44.6109 | 44.9995 | 45.3264 | 45.4769 | 45.3428 | 45.9052 | 45.9944 | 45.8888 | 46.1005 | 46.1995 | 46.1995 | 46.1995 | 46.1995 | 46.1995 | 46.1995 | 46.1995 | 46.1995 | 46.1995 | 46.1995 | 46.1995 | 46.1995 | 46.1995 | 46.1995 | 46.1995 | 90% | 0.75633 | 50.437 | 53.8617 | 53.9562 | 53.8543 | 53.8805 | 54.0675 | 54.4465 | 55.114 | 55.4618 | 55.7134 | 56.0942 | 56.5803 | 57.1682 | 57.4763 | 57.3764 | 57.4754 | 57.4754 | 57.4754 | 57.4754 | 57.4754 | 57.4754 | 57.4754 | 57.4754 | 57.4754 | 57.4754 | 57.4754 | 57.4754 | 57.4754 | 57.4754 | 57.4754
85% | 40.4636 | 38.7203 | 41.6145 | 41.9053 | 41.7628 | 41.8983 | 41.954 | 42.1325 | 42.4995 | 42.8083 | 42.9504 | 42.8238 | 43.3549 | 43.4391 | 43.3394 | 43.5393 | 43.6328 | 43.6328 | 43.6328 | 43.6328 | 43.6328 | 43.6328 | 43.6328 | 43.6328 | 43.6328 | 43.6328 | 43.6328 | 43.6328 | 43.6328 | 43.6328 | 43.6328 | 85% | 1.1345 | 47.6349 | 50.8694 | 50.9586 | 50.8624 | 50.8871 | 51.0637 | 51.4217 | 52.0521 | 52.3805 | 52.6182 | 52.9778 | 53.437 | 53.9922 | 54.2832 | 54.1889 | 54.2824 | 54.2824 | 54.2824 | 54.2824 | 54.2824 | 54.2824 | 54.2824 | 54.2824 | 54.2824 | 54.2824 | 54.2824 | 54.2824 | 54.2824 | 54.2824 | 54.2824
80% | 94.5411 | 36.4427 | 39.1666 | 39.4403 | 39.3061 | 39.4337 | 39.4861 | 39.6541 | 39.9996 | 40.2902 | 40.4239 | 40.3047 | 40.8046 | 40.8839 | 40.7901 | 40.9782 | 41.0662 | 41.0662 | 41.0662 | 41.0662 | 41.0662 | 41.0662 | 41.0662 | 41.0662 | 41.0662 | 41.0662 | 41.0662 | 41.0662 | 41.0662 | 41.0662 | 41.0662 | 80% | 2.6471 | 44.8329 | 47.877 | 47.961 | 47.8705 | 47.8938 | 48.06 | 48.3969 | 48.9902 | 49.2993 | 49.523 | 49.8615 | 50.2936 | 50.8162 | 51.0901 | 51.0013 | 51.0893 | 51.0893 | 51.0893 | 51.0893 | 51.0893 | 51.0893 | 51.0893 | 51.0893 | 51.0893 | 51.0893 | 51.0893 | 51.0893 | 51.0893 | 51.0893 | 51.0893
75% | 197.0236 | 34.165 | 36.7187 | 36.9753 | 36.8495 | 36.9691 | 37.0182 | 37.1757 | 37.4996 | 37.772 | 37.8974 | 37.7857 | 38.2543 | 38.3286 | 38.2407 | 38.4171 | 38.4996 | 38.4996 | 38.4996 | 38.4996 | 38.4996 | 38.4996 | 38.4996 | 38.4996 | 38.4996 | 38.4996 | 38.4996 | 38.4996 | 38.4996 | 38.4996 | 38.4996 | 75% | 3.4035 | 42.0308 | 44.8847 | 44.9635 | 44.8786 | 44.9004 | 45.0562 | 45.3721 | 45.9283 | 46.2181 | 46.4278 | 46.7451 | 47.1503 | 47.6402 | 47.8969 | 47.8137 | 47.8962 | 47.8962 | 47.8962 | 47.8962 | 47.8962 | 47.8962 | 47.8962 | 47.8962 | 47.8962 | 47.8962 | 47.8962 | 47.8962 | 47.8962 | 47.8962 | 47.8962
70% | 336.9444 | 31.8873 | 34.2708 | 34.5103 | 34.3929 | 34.5045 | 34.5504 | 34.6974 | 34.9996 | 35.2539 | 35.371 | 35.2666 | 35.704 | 35.7734 | 35.6913 | 35.8559 | 35.9329 | 35.9329 | 35.9329 | 35.9329 | 35.9329 | 35.9329 | 35.9329 | 35.9329 | 35.9329 | 35.9329 | 35.9329 | 35.9329 | 35.9329 | 35.9329 | 35.9329 | 70% | 5.6725 | 39.2288 | 41.8924 | 41.9659 | 41.8867 | 41.907 | 42.0525 | 42.3473 | 42.8664 | 43.1369 | 43.3326 | 43.6288 | 44.0069 | 44.4642 | 44.7038 | 44.6261 | 44.7031 | 44.7031 | 44.7031 | 44.7031 | 44.7031 | 44.7031 | 44.7031 | 44.7031 | 44.7031 | 44.7031 | 44.7031 | 44.7031 | 44.7031 | 44.7031 | 44.7031
65% | 521.4885 | 29.6097 | 31.8228 | 32.0452 | 31.9362 | 32.0399 | 32.0825 | 32.219 | 32.4996 | 32.7358 | 32.8445 | 32.7476 | 33.1537 | 33.2182 | 33.1419 | 33.2948 | 33.3663 | 33.3663 | 33.3663 | 33.3663 | 33.3663 | 33.3663 | 33.3663 | 33.3663 | 33.3663 | 33.3663 | 33.3663 | 33.3663 | 33.3663 | 33.3663 | 33.3663 | 65% | 6.4288 | 36.4267 | 38.9001 | 38.9683 | 38.8948 | 38.9137 | 39.0487 | 39.3225 | 39.8045 | 40.0557 | 40.2374 | 40.5125 | 40.8636 | 41.2882 | 41.5107 | 41.4385 | 41.51 | 41.51 | 41.51 | 41.51 | 41.51 | 41.51 | 41.51 | 41.51 | 41.51 | 41.51 | 41.51 | 41.51 | 41.51 | 41.51 | 41.51
60% | 812.675 | 27.332 | 29.3749 | 29.5802 | 29.4796 | 29.5753 | 29.6146 | 29.7406 | 29.9997 | 30.2176 | 30.318 | 30.2285 | 30.6035 | 30.6629 | 30.5925 | 30.7337 | 30.7997 | 30.7997 | 30.7997 | 30.7997 | 30.7997 | 30.7997 | 30.7997 | 30.7997 | 30.7997 | 30.7997 | 30.7997 | 30.7997 | 30.7997 | 30.7997 | 30.7997 | 60% | 11.3449 | 33.6247 | 35.9078 | 35.9708 | 35.9029 | 35.9203 | 36.045 | 36.2977 | 36.7426 | 36.9745 | 37.1422 | 37.3961 | 37.7202 | 38.1122 | 38.3176 | 38.251 | 38.317 | 38.317 | 38.317 | 38.317 | 38.317 | 38.317 | 38.317 | 38.317 | 38.317 | 38.317 | 38.317 | 38.317 | 38.317 | 38.317 | 38.317
55% | 1202.1843 | 25.0543 | 26.927 | 27.1152 | 27.023 | 27.1107 | 27.1467 | 27.2622 | 27.4997 | 27.6995 | 27.7915 | 27.7095 | 28.0532 | 28.1077 | 28.0432 | 28.1725 | 28.233 | 28.233 | 28.233 | 28.233 | 28.233 | 28.233 | 28.233 | 28.233 | 28.233 | 28.233 | 28.233 | 28.233 | 28.233 | 28.233 | 28.233 | 55% | 35.5474 | 30.8226 | 32.9155 | 32.9732 | 32.911 | 32.927 | 33.0412 | 33.2729 | 33.6808 | 33.8933 | 34.0471 | 34.2798 | 34.5769 | 34.9361 | 35.1244 | 35.0634 | 35.1239 | 35.1239 | 35.1239 | 35.1239 | 35.1239 | 35.1239 | 35.1239 | 35.1239 | 35.1239 | 35.1239 | 35.1239 | 35.1239 | 35.1239 | 35.1239 | 35.1239
50% | 1686.2345 | 22.7767 | 24.4791 | 24.6502 | 24.5663 | 24.6461 | 24.6788 | 24.7838 | 24.9997 | 25.1814 | 25.265 | 25.1904 | 25.5029 | 25.5524 | 25.4938 | 25.6114 | 25.6664 | 25.6664 | 25.6664 | 25.6664 | 25.6664 | 25.6664 | 25.6664 | 25.6664 | 25.6664 | 25.6664 | 25.6664 | 25.6664 | 25.6664 | 25.6664 | 25.6664 | 50% | 95.2974 | 28.0206 | 29.9231 | 29.9756 | 29.919 | 29.9336 | 30.0375 | 30.2481 | 30.6189 | 30.8121 | 30.9519 | 31.1634 | 31.4335 | 31.7601 | 31.9313 | 31.8758 | 31.9308 | 31.9308 | 31.9308 | 31.9308 | 31.9308 | 31.9308 | 31.9308 | 31.9308 | 31.9308 | 31.9308 | 31.9308 | 31.9308 | 31.9308 | 31.9308 | 31.9308
45% | 2129.0649 | 20.499 | 22.0312 | 22.1852 | 22.1097 | 22.1815 | 22.2109 | 22.3054 | 22.4998 | 22.6632 | 22.7385 | 22.6714 | 22.9526 | 22.9972 | 22.9444 | 23.0502 | 23.0997 | 23.0997 | 23.0997 | 23.0997 | 23.0997 | 23.0997 | 23.0997 | 23.0997 | 23.0997 | 23.0997 | 23.0997 | 23.0997 | 23.0997 | 23.0997 | 23.0997 | 45% | 208.7467 | 25.2185 | 26.9308 | 26.9781 | 26.9271 | 26.9402 | 27.0337 | 27.2232 | 27.557 | 27.7309 | 27.8567 | 28.0471 | 28.2902 | 28.5841 | 28.7382 | 28.6882 | 28.7377 | 28.7377 | 28.7377 | 28.7377 | 28.7377 | 28.7377 | 28.7377 | 28.7377 | 28.7377 | 28.7377 | 28.7377 | 28.7377 | 28.7377 | 28.7377 | 28.7377
40% | 2484.5393 | 18.2213 | 19.5833 | 19.7201 | 19.6531 | 19.7169 | 19.7431 | 19.8271 | 19.9998 | 20.1451 | 20.212 | 20.1524 | 20.4023 | 20.4419 | 20.395 | 20.4891 | 20.5331 | 20.5331 | 20.5331 | 20.5331 | 20.5331 | 20.5331 | 20.5331 | 20.5331 | 20.5331 | 20.5331 | 20.5331 | 20.5331 | 20.5331 | 20.5331 | 20.5331 | 40% | 380.4333 | 22.4164 | 23.9385 | 23.9805 | 23.9352 | 23.9469 | 24.03 | 24.1984 | 24.4951 | 24.6497 | 24.7615 | 24.9307 | 25.1468 | 25.4081 | 25.545 | 25.5006 | 25.5446 | 25.5446 | 25.5446 | 25.5446 | 25.5446 | 25.5446 | 25.5446 | 25.5446 | 25.5446 | 25.5446 | 25.5446 | 25.5446 | 25.5446 | 25.5446 | 25.5446
35% | 2808.248 | 15.9437 | 17.1354 | 17.2551 | 17.1964 | 17.2522 | 17.2752 | 17.3487 | 17.4998 | 17.6269 | 17.6855 | 17.6333 | 17.852 | 17.8867 | 17.8457 | 17.928 | 17.9665 | 17.9665 | 17.9665 | 17.9665 | 17.9665 | 17.9665 | 17.9665 | 17.9665 | 17.9665 | 17.9665 | 17.9665 | 17.9665 | 17.9665 | 17.9665 | 17.9665 | 35% | 696.5786 | 19.6144 | 20.9462 | 20.983 | 20.9433 | 20.9535 | 21.0262 | 21.1736 | 21.4332 | 21.5685 | 21.6663 | 21.8144 | 22.0035 | 22.2321 | 22.3519 | 22.3131 | 22.3516 | 22.3516 | 22.3516 | 22.3516 | 22.3516 | 22.3516 | 22.3516 | 22.3516 | 22.3516 | 22.3516 | 22.3516 | 22.3516 | 22.3516 | 22.3516 | 22.3516
30% | 3095.6528 | 13.666 | 14.6875 | 14.7901 | 14.7398 | 14.7876 | 14.8073 | 14.8703 | 14.9998 | 15.1088 | 15.159 | 15.1143 | 15.3017 | 15.3315 | 15.2963 | 15.3668 | 15.3998 | 15.3998 | 15.3998 | 15.3998 | 15.3998 | 15.3998 | 15.3998 | 15.3998 | 15.3998 | 15.3998 | 15.3998 | 15.3998 | 15.3998 | 15.3998 | 15.3998 | 30% | 1260.7997 | 16.8123 | 17.9539 | 17.9854 | 17.9514 | 17.9602 | 18.0225 | 18.1488 | 18.3713 | 18.4873 | 18.5711 | 18.6981 | 18.8601 | 19.0561 | 19.1588 | 19.1255 | 19.1585 | 19.1585 | 19.1585 | 19.1585 | 19.1585 | 19.1585 | 19.1585 | 19.1585 | 19.1585 | 19.1585 | 19.1585 | 19.1585 | 19.1585 | 19.1585 | 19.1585
25% | 3358.8552 | 11.3883 | 12.2396 | 12.3251 | 12.2832 | 12.323 | 12.3394 | 12.3919 | 12.4999 | 12.5907 | 12.6325 | 12.5952 | 12.7514 | 12.7762 | 12.7469 | 12.8057 | 12.8332 | 12.8332 | 12.8332 | 12.8332 | 12.8332 | 12.8332 | 12.8332 | 12.8332 | 12.8332 | 12.8332 | 12.8332 | 12.8332 | 12.8332 | 12.8332 | 12.8332 | 25% | 1965.3198 | 14.0103 | 14.9616 | 14.9878 | 14.9595 | 14.9668 | 15.0187 | 15.124 | 15.3094 | 15.406 | 15.4759 | 15.5817 | 15.7168 | 15.8801 | 15.9656 | 15.9379 | 15.9654 | 15.9654 | 15.9654 | 15.9654 | 15.9654 | 15.9654 | 15.9654 | 15.9654 | 15.9654 | 15.9654 | 15.9654 | 15.9654 | 15.9654 | 15.9654 | 15.9654
20% | 3588.7791 | 9.1107 | 9.7916 | 9.8601 | 9.8265 | 9.8584 | 9.8715 | 9.9135 | 9.9999 | 10.0725 | 10.106 | 10.0762 | 10.2012 | 10.221 | 10.1975 | 10.2446 | 10.2666 | 10.2666 | 10.2666 | 10.2666 | 10.2666 | 10.2666 | 10.2666 | 10.2666 | 10.2666 | 10.2666 | 10.2666 | 10.2666 | 10.2666 | 10.2666 | 10.2666 | 20% | 2490.2118 | 11.2082 | 11.9693 | 11.9903 | 11.9676 | 11.9734 | 12.015 | 12.0992 | 12.2475 | 12.3248 | 12.3807 | 12.4654 | 12.5734 | 12.7041 | 12.7725 | 12.7503 | 12.7723 | 12.7723 | 12.7723 | 12.7723 | 12.7723 | 12.7723 | 12.7723 | 12.7723 | 12.7723 | 12.7723 | 12.7723 | 12.7723 | 12.7723 | 12.7723 | 12.7723
15% | 3802.4419 | 6.833 | 7.3437 | 7.3951 | 7.3699 | 7.3938 | 7.4036 | 7.4351 | 7.4999 | 7.5544 | 7.5795 | 7.5571 | 7.6509 | 7.6657 | 7.6481 | 7.6834 | 7.6999 | 7.6999 | 7.6999 | 7.6999 | 7.6999 | 7.6999 | 7.6999 | 7.6999 | 7.6999 | 7.6999 | 7.6999 | 7.6999 | 7.6999 | 7.6999 | 7.6999 | 15% | 2997.7083 | 8.4062 | 8.9769 | 8.9927 | 8.9757 | 8.9801 | 9.0112 | 9.0744 | 9.1857 | 9.2436 | 9.2856 | 9.349 | 9.4301 | 9.528 | 9.5794 | 9.5627 | 9.5792 | 9.5792 | 9.5792 | 9.5792 | 9.5792 | 9.5792 | 9.5792 | 9.5792 | 9.5792 | 9.5792 | 9.5792 | 9.5792 | 9.5792 | 9.5792 | 9.5792
10% | 4024.8025 | 4.5553 | 4.8958 | 4.93 | 4.9133 | 4.9292 | 4.9358 | 4.9568 | 4.9999 | 5.0363 | 5.053 | 5.0381 | 5.1006 | 5.1105 | 5.0988 | 5.1223 | 5.1333 | 5.1333 | 5.1333 | 5.1333 | 5.1333 | 5.1333 | 5.1333 | 5.1333 | 5.1333 | 5.1333 | 5.1333 | 5.1333 | 5.1333 | 5.1333 | 5.1333 | 10% | 3491.5908 | 5.6041 | 5.9846 | 5.9951 | 5.9838 | 5.9867 | 6.0075 | 6.0496 | 6.1238 | 6.1624 | 6.1904 | 6.2327 | 6.2867 | 6.352 | 6.3863 | 6.3752 | 6.3862 | 6.3862 | 6.3862 | 6.3862 | 6.3862 | 6.3862 | 6.3862 | 6.3862 | 6.3862 | 6.3862 | 6.3862 | 6.3862 | 6.3862 | 6.3862 | 6.3862
5% | 4239.978 | 2.2777 | 2.4479 | 2.465 | 2.4566 | 2.4646 | 2.4679 | 2.4784 | 2.5 | 2.5181 | 2.5265 | 2.519 | 2.5503 | 2.5552 | 2.5494 | 2.5611 | 2.5666 | 2.5666 | 2.5666 | 2.5666 | 2.5666 | 2.5666 | 2.5666 | 2.5666 | 2.5666 | 2.5666 | 2.5666 | 2.5666 | 2.5666 | 2.5666 | 2.5666 | 5% | 3955.9766 | 2.8021 | 2.9923 | 2.9976 | 2.9919 | 2.9934 | 3.0037 | 3.0248 | 3.0619 | 3.0812 | 3.0952 | 3.1163 | 3.1434 | 3.176 | 3.1931 | 3.1876 | 3.1931 | 3.1931 | 3.1931 | 3.1931 | 3.1931 | 3.1931 | 3.1931 | 3.1931 | 3.1931 | 3.1931 | 3.1931 | 3.1931 | 3.1931 | 3.1931 | 3.1931
9.992e-14% | 4391.6218 | 4.5517e-14 | 4.8919e-14 | 4.9261e-14 | 4.9093e-14 | 4.9253e-14 | 4.9318e-14 | 4.9528e-14 | 4.9959e-14 | 5.0322e-14 | 5.049e-14 | 5.0341e-14 | 5.0965e-14 | 5.1064e-14 | 5.0947e-14 | 5.1182e-14 | 5.1292e-14 | 5.1292e-14 | 5.1292e-14 | 5.1292e-14 | 5.1292e-14 | 5.1292e-14 | 5.1292e-14 | 5.1292e-14 | 5.1292e-14 | 5.1292e-14 | 5.1292e-14 | 5.1292e-14 | 5.1292e-14 | 5.1292e-14 | 5.1292e-14 | 9.992e-14% | 4391.6218 | 5.5996e-14 | 5.9798e-14 | 5.9903e-14 | 5.979e-14 | 5.9819e-14 | 6.0027e-14 | 6.0448e-14 | 6.1189e-14 | 6.1575e-14 | 6.1854e-14 | 6.2277e-14 | 6.2817e-14 | 6.3469e-14 | 6.3812e-14 | 6.3701e-14 | 6.3811e-14 | 6.3811e-14 | 6.3811e-14 | 6.3811e-14 | 6.3811e-14 | 6.3811e-14 | 6.3811e-14 | 6.3811e-14 | 6.3811e-14 | 6.3811e-14 | 6.3811e-14 | 6.3811e-14 | 6.3811e-14 | 6.3811e-14 | 6.3811e-14
Option 8
Winter Season | [31 empty] | Winter Season
P50 | [31 empty] | P10
% of MD | Winter - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Winter - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 43.3628 | 47.9013 | 48.3825 | 48.9775 | 49.7674 | 50.5163 | 51.825 | 55.1166 | 56.887 | 55.5954 | 59.594 | 60.3144 | 60.8323 | 63.2734 | 63.6707 | 63.6707 | 63.6707 | 63.6707 | 63.6707 | 63.6707 | 63.6707 | 63.6707 | 63.6707 | 63.6707 | 63.6707 | 63.6707 | 63.6707 | 63.6707 | 63.6707 | 63.6707 | 100% | 0 | 47.5339 | 51.863 | 52.3113 | 53.8585 | 53.8208 | 54.161 | 55.4916 | 59.3146 | 60.8922 | 59.3989 | 63.524 | 61.792 | 63.3504 | 64.4734 | 64.012 | 64.012 | 64.012 | 64.012 | 64.012 | 64.012 | 64.012 | 64.012 | 64.012 | 64.012 | 64.012 | 64.012 | 64.012 | 64.012 | 64.012 | 64.012
99% | 0.2972 | 42.9291 | 47.4223 | 47.8987 | 48.4877 | 49.2697 | 50.0111 | 51.3068 | 54.5654 | 56.3182 | 55.0395 | 58.9981 | 59.7113 | 60.224 | 62.6406 | 63.034 | 63.034 | 63.034 | 63.034 | 63.034 | 63.034 | 63.034 | 63.034 | 63.034 | 63.034 | 63.034 | 63.034 | 63.034 | 63.034 | 63.034 | 63.034 | 99% | 0.2972 | 47.0586 | 51.3443 | 51.7882 | 53.3199 | 53.2826 | 53.6194 | 54.9367 | 58.7214 | 60.2833 | 58.8049 | 62.8887 | 61.1741 | 62.7169 | 63.8287 | 63.3719 | 63.3719 | 63.3719 | 63.3719 | 63.3719 | 63.3719 | 63.3719 | 63.3719 | 63.3719 | 63.3719 | 63.3719 | 63.3719 | 63.3719 | 63.3719 | 63.3719 | 63.3719
98% | 0.2972 | 42.4955 | 46.9432 | 47.4149 | 47.9979 | 48.7721 | 49.506 | 50.7885 | 54.0143 | 55.7493 | 54.4835 | 58.4021 | 59.1081 | 59.6156 | 62.0079 | 62.3973 | 62.3973 | 62.3973 | 62.3973 | 62.3973 | 62.3973 | 62.3973 | 62.3973 | 62.3973 | 62.3973 | 62.3973 | 62.3973 | 62.3973 | 62.3973 | 62.3973 | 62.3973 | 98% | 0.2972 | 46.5832 | 50.8257 | 51.2651 | 52.7813 | 52.7443 | 53.0778 | 54.3818 | 58.1283 | 59.6743 | 58.2109 | 62.2535 | 60.5562 | 62.0834 | 63.184 | 62.7318 | 62.7318 | 62.7318 | 62.7318 | 62.7318 | 62.7318 | 62.7318 | 62.7318 | 62.7318 | 62.7318 | 62.7318 | 62.7318 | 62.7318 | 62.7318 | 62.7318 | 62.7318
97% | 0.2972 | 42.0619 | 46.4642 | 46.931 | 47.5082 | 48.2744 | 49.0008 | 50.2703 | 53.4631 | 55.1804 | 53.9276 | 57.8062 | 58.505 | 59.0073 | 61.3752 | 61.7606 | 61.7606 | 61.7606 | 61.7606 | 61.7606 | 61.7606 | 61.7606 | 61.7606 | 61.7606 | 61.7606 | 61.7606 | 61.7606 | 61.7606 | 61.7606 | 61.7606 | 61.7606 | 97% | 0.2972 | 46.1079 | 50.3071 | 50.7419 | 52.2427 | 52.2061 | 52.5362 | 53.8269 | 57.5352 | 59.0654 | 57.6169 | 61.6183 | 59.9383 | 61.4499 | 62.5392 | 62.0917 | 62.0917 | 62.0917 | 62.0917 | 62.0917 | 62.0917 | 62.0917 | 62.0917 | 62.0917 | 62.0917 | 62.0917 | 62.0917 | 62.0917 | 62.0917 | 62.0917 | 62.0917
95% | 1.486 | 41.1946 | 45.5062 | 45.9634 | 46.5286 | 47.2791 | 47.9905 | 49.2338 | 52.3608 | 54.0427 | 52.8157 | 56.6143 | 57.2987 | 57.7907 | 60.1097 | 60.4871 | 60.4871 | 60.4871 | 60.4871 | 60.4871 | 60.4871 | 60.4871 | 60.4871 | 60.4871 | 60.4871 | 60.4871 | 60.4871 | 60.4871 | 60.4871 | 60.4871 | 60.4871 | 95% | 1.486 | 45.1572 | 49.2698 | 49.6957 | 51.1655 | 51.1297 | 51.4529 | 52.717 | 56.3489 | 57.8476 | 56.4289 | 60.3478 | 58.7024 | 60.1829 | 61.2498 | 60.8114 | 60.8114 | 60.8114 | 60.8114 | 60.8114 | 60.8114 | 60.8114 | 60.8114 | 60.8114 | 60.8114 | 60.8114 | 60.8114 | 60.8114 | 60.8114 | 60.8114 | 60.8114
90% | 8.6188 | 39.0265 | 43.1111 | 43.5443 | 44.0797 | 44.7907 | 45.4647 | 46.6425 | 49.6049 | 51.1983 | 50.0359 | 53.6346 | 54.283 | 54.7491 | 56.946 | 57.3036 | 57.3036 | 57.3036 | 57.3036 | 57.3036 | 57.3036 | 57.3036 | 57.3036 | 57.3036 | 57.3036 | 57.3036 | 57.3036 | 57.3036 | 57.3036 | 57.3036 | 57.3036 | 90% | 8.6188 | 42.7805 | 46.6767 | 47.0802 | 48.4726 | 48.4387 | 48.7449 | 49.9425 | 53.3831 | 54.803 | 53.459 | 57.1716 | 55.6128 | 57.0154 | 58.0261 | 57.6108 | 57.6108 | 57.6108 | 57.6108 | 57.6108 | 57.6108 | 57.6108 | 57.6108 | 57.6108 | 57.6108 | 57.6108 | 57.6108 | 57.6108 | 57.6108 | 57.6108 | 57.6108
85% | 40.1218 | 36.8584 | 40.7161 | 41.1251 | 41.6309 | 42.3023 | 42.9389 | 44.0513 | 46.8491 | 48.354 | 47.2561 | 50.6549 | 51.2673 | 51.7074 | 53.7823 | 54.1201 | 54.1201 | 54.1201 | 54.1201 | 54.1201 | 54.1201 | 54.1201 | 54.1201 | 54.1201 | 54.1201 | 54.1201 | 54.1201 | 54.1201 | 54.1201 | 54.1201 | 54.1201 | 85% | 40.1218 | 40.4038 | 44.0835 | 44.4646 | 45.7797 | 45.7477 | 46.0368 | 47.1679 | 50.4174 | 51.7583 | 50.489 | 53.9954 | 52.5232 | 53.8479 | 54.8024 | 54.4102 | 54.4102 | 54.4102 | 54.4102 | 54.4102 | 54.4102 | 54.4102 | 54.4102 | 54.4102 | 54.4102 | 54.4102 | 54.4102 | 54.4102 | 54.4102 | 54.4102 | 54.4102
80% | 93.0231 | 34.6902 | 38.321 | 38.706 | 39.182 | 39.8139 | 40.413 | 41.46 | 44.0933 | 45.5096 | 44.4764 | 47.6752 | 48.2515 | 48.6658 | 50.6187 | 50.9365 | 50.9365 | 50.9365 | 50.9365 | 50.9365 | 50.9365 | 50.9365 | 50.9365 | 50.9365 | 50.9365 | 50.9365 | 50.9365 | 50.9365 | 50.9365 | 50.9365 | 50.9365 | 80% | 93.0231 | 38.0271 | 41.4904 | 41.849 | 43.0868 | 43.0566 | 43.3288 | 44.3933 | 47.4517 | 48.7137 | 47.5191 | 50.8192 | 49.4336 | 50.6803 | 51.5787 | 51.2096 | 51.2096 | 51.2096 | 51.2096 | 51.2096 | 51.2096 | 51.2096 | 51.2096 | 51.2096 | 51.2096 | 51.2096 | 51.2096 | 51.2096 | 51.2096 | 51.2096 | 51.2096
75% | 197.0426 | 32.5221 | 35.926 | 36.2869 | 36.7331 | 37.3256 | 37.8872 | 38.8688 | 41.3374 | 42.6653 | 41.6966 | 44.6955 | 45.2358 | 45.6242 | 47.455 | 47.753 | 47.753 | 47.753 | 47.753 | 47.753 | 47.753 | 47.753 | 47.753 | 47.753 | 47.753 | 47.753 | 47.753 | 47.753 | 47.753 | 47.753 | 47.753 | 75% | 197.0426 | 35.6504 | 38.8972 | 39.2335 | 40.3939 | 40.3656 | 40.6207 | 41.6187 | 44.4859 | 45.6691 | 44.5491 | 47.643 | 46.344 | 47.5128 | 48.3551 | 48.009 | 48.009 | 48.009 | 48.009 | 48.009 | 48.009 | 48.009 | 48.009 | 48.009 | 48.009 | 48.009 | 48.009 | 48.009 | 48.009 | 48.009 | 48.009
70% | 378.0365 | 30.3539 | 33.5309 | 33.8678 | 34.2842 | 34.8372 | 35.3614 | 36.2775 | 38.5816 | 39.8209 | 38.9168 | 41.7158 | 42.2201 | 42.5826 | 44.2913 | 44.5695 | 44.5695 | 44.5695 | 44.5695 | 44.5695 | 44.5695 | 44.5695 | 44.5695 | 44.5695 | 44.5695 | 44.5695 | 44.5695 | 44.5695 | 44.5695 | 44.5695 | 44.5695 | 70% | 378.0365 | 33.2737 | 36.3041 | 36.6179 | 37.7009 | 37.6745 | 37.9127 | 38.8441 | 41.5202 | 42.6245 | 41.5792 | 44.4668 | 43.2544 | 44.3453 | 45.1314 | 44.8084 | 44.8084 | 44.8084 | 44.8084 | 44.8084 | 44.8084 | 44.8084 | 44.8084 | 44.8084 | 44.8084 | 44.8084 | 44.8084 | 44.8084 | 44.8084 | 44.8084 | 44.8084
65% | 616.0926 | 28.1858 | 31.1358 | 31.4486 | 31.8354 | 32.3488 | 32.8356 | 33.6863 | 35.8258 | 36.9766 | 36.137 | 38.7361 | 39.2044 | 39.541 | 41.1277 | 41.3859 | 41.3859 | 41.3859 | 41.3859 | 41.3859 | 41.3859 | 41.3859 | 41.3859 | 41.3859 | 41.3859 | 41.3859 | 41.3859 | 41.3859 | 41.3859 | 41.3859 | 41.3859 | 65% | 616.0926 | 30.897 | 33.7109 | 34.0023 | 35.008 | 34.9835 | 35.2046 | 36.0696 | 38.5545 | 39.5799 | 38.6093 | 41.2906 | 40.1648 | 41.1778 | 41.9077 | 41.6078 | 41.6078 | 41.6078 | 41.6078 | 41.6078 | 41.6078 | 41.6078 | 41.6078 | 41.6078 | 41.6078 | 41.6078 | 41.6078 | 41.6078 | 41.6078 | 41.6078 | 41.6078
60% | 934.9866 | 26.0177 | 28.7408 | 29.0295 | 29.3865 | 29.8605 | 30.3098 | 31.095 | 33.07 | 34.1322 | 33.3573 | 35.7564 | 36.1887 | 36.4994 | 37.964 | 38.2024 | 38.2024 | 38.2024 | 38.2024 | 38.2024 | 38.2024 | 38.2024 | 38.2024 | 38.2024 | 38.2024 | 38.2024 | 38.2024 | 38.2024 | 38.2024 | 38.2024 | 38.2024 | 60% | 934.9866 | 28.5203 | 31.1178 | 31.3868 | 32.3151 | 32.2925 | 32.4966 | 33.295 | 35.5888 | 36.5353 | 35.6393 | 38.1144 | 37.0752 | 38.0103 | 38.6841 | 38.4072 | 38.4072 | 38.4072 | 38.4072 | 38.4072 | 38.4072 | 38.4072 | 38.4072 | 38.4072 | 38.4072 | 38.4072 | 38.4072 | 38.4072 | 38.4072 | 38.4072 | 38.4072
55% | 1310.9428 | 23.8495 | 26.3457 | 26.6104 | 26.9376 | 27.3721 | 27.784 | 28.5038 | 30.3141 | 31.2879 | 30.5775 | 32.7767 | 33.1729 | 33.4578 | 34.8003 | 35.0189 | 35.0189 | 35.0189 | 35.0189 | 35.0189 | 35.0189 | 35.0189 | 35.0189 | 35.0189 | 35.0189 | 35.0189 | 35.0189 | 35.0189 | 35.0189 | 35.0189 | 35.0189 | 55% | 1310.9428 | 26.1436 | 28.5246 | 28.7712 | 29.6222 | 29.6014 | 29.7885 | 30.5204 | 32.623 | 33.4907 | 32.6694 | 34.9382 | 33.9856 | 34.8427 | 35.4604 | 35.2066 | 35.2066 | 35.2066 | 35.2066 | 35.2066 | 35.2066 | 35.2066 | 35.2066 | 35.2066 | 35.2066 | 35.2066 | 35.2066 | 35.2066 | 35.2066 | 35.2066 | 35.2066
50% | 1730.2899 | 21.6814 | 23.9506 | 24.1913 | 24.4887 | 24.8837 | 25.2582 | 25.9125 | 27.5583 | 28.4435 | 27.7977 | 29.797 | 30.1572 | 30.4161 | 31.6367 | 31.8353 | 31.8353 | 31.8353 | 31.8353 | 31.8353 | 31.8353 | 31.8353 | 31.8353 | 31.8353 | 31.8353 | 31.8353 | 31.8353 | 31.8353 | 31.8353 | 31.8353 | 31.8353 | 50% | 1730.2899 | 23.7669 | 25.9315 | 26.1556 | 26.9292 | 26.9104 | 27.0805 | 27.7458 | 29.6573 | 30.4461 | 29.6994 | 31.762 | 30.896 | 31.6752 | 32.2367 | 32.006 | 32.006 | 32.006 | 32.006 | 32.006 | 32.006 | 32.006 | 32.006 | 32.006 | 32.006 | 32.006 | 32.006 | 32.006 | 32.006 | 32.006 | 32.006
45% | 2168.0633 | 19.5132 | 21.5556 | 21.7721 | 22.0399 | 22.3953 | 22.7323 | 23.3213 | 24.8025 | 25.5992 | 25.0179 | 26.8173 | 27.1415 | 27.3745 | 28.473 | 28.6518 | 28.6518 | 28.6518 | 28.6518 | 28.6518 | 28.6518 | 28.6518 | 28.6518 | 28.6518 | 28.6518 | 28.6518 | 28.6518 | 28.6518 | 28.6518 | 28.6518 | 28.6518 | 45% | 2168.0633 | 21.3903 | 23.3383 | 23.5401 | 24.2363 | 24.2193 | 24.3724 | 24.9712 | 26.6916 | 27.4015 | 26.7295 | 28.5858 | 27.8064 | 28.5077 | 29.013 | 28.8054 | 28.8054 | 28.8054 | 28.8054 | 28.8054 | 28.8054 | 28.8054 | 28.8054 | 28.8054 | 28.8054 | 28.8054 | 28.8054 | 28.8054 | 28.8054 | 28.8054 | 28.8054
40% | 2609.7004 | 17.3451 | 19.1605 | 19.353 | 19.591 | 19.907 | 20.2065 | 20.73 | 22.0466 | 22.7548 | 22.2382 | 23.8376 | 24.1258 | 24.3329 | 25.3093 | 25.4683 | 25.4683 | 25.4683 | 25.4683 | 25.4683 | 25.4683 | 25.4683 | 25.4683 | 25.4683 | 25.4683 | 25.4683 | 25.4683 | 25.4683 | 25.4683 | 25.4683 | 25.4683 | 40% | 2609.7004 | 19.0136 | 20.7452 | 20.9245 | 21.5434 | 21.5283 | 21.6644 | 22.1966 | 23.7258 | 24.3569 | 23.7595 | 25.4096 | 24.7168 | 25.3402 | 25.7894 | 25.6048 | 25.6048 | 25.6048 | 25.6048 | 25.6048 | 25.6048 | 25.6048 | 25.6048 | 25.6048 | 25.6048 | 25.6048 | 25.6048 | 25.6048 | 25.6048 | 25.6048 | 25.6048
35% | 2998.1389 | 15.177 | 16.7654 | 16.9339 | 17.1421 | 17.4186 | 17.6807 | 18.1388 | 19.2908 | 19.9105 | 19.4584 | 20.8579 | 21.1101 | 21.2913 | 22.1457 | 22.2847 | 22.2847 | 22.2847 | 22.2847 | 22.2847 | 22.2847 | 22.2847 | 22.2847 | 22.2847 | 22.2847 | 22.2847 | 22.2847 | 22.2847 | 22.2847 | 22.2847 | 22.2847 | 35% | 2998.1389 | 16.6369 | 18.152 | 18.3089 | 18.8505 | 18.8373 | 18.9563 | 19.4221 | 20.7601 | 21.3123 | 20.7896 | 22.2334 | 21.6272 | 22.1726 | 22.5657 | 22.4042 | 22.4042 | 22.4042 | 22.4042 | 22.4042 | 22.4042 | 22.4042 | 22.4042 | 22.4042 | 22.4042 | 22.4042 | 22.4042 | 22.4042 | 22.4042 | 22.4042 | 22.4042
30% | 3309.3057 | 13.0088 | 14.3704 | 14.5148 | 14.6932 | 14.9302 | 15.1549 | 15.5475 | 16.535 | 17.0661 | 16.6786 | 17.8782 | 18.0943 | 18.2497 | 18.982 | 19.1012 | 19.1012 | 19.1012 | 19.1012 | 19.1012 | 19.1012 | 19.1012 | 19.1012 | 19.1012 | 19.1012 | 19.1012 | 19.1012 | 19.1012 | 19.1012 | 19.1012 | 19.1012 | 30% | 3309.3057 | 14.2602 | 15.5589 | 15.6934 | 16.1575 | 16.1462 | 16.2483 | 16.6475 | 17.7944 | 18.2677 | 17.8197 | 19.0572 | 18.5376 | 19.0051 | 19.342 | 19.2036 | 19.2036 | 19.2036 | 19.2036 | 19.2036 | 19.2036 | 19.2036 | 19.2036 | 19.2036 | 19.2036 | 19.2036 | 19.2036 | 19.2036 | 19.2036 | 19.2036 | 19.2036
25% | 3537.8514 | 10.8407 | 11.9753 | 12.0956 | 12.2444 | 12.4419 | 12.6291 | 12.9563 | 13.7791 | 14.2218 | 13.8989 | 14.8985 | 15.0786 | 15.2081 | 15.8183 | 15.9177 | 15.9177 | 15.9177 | 15.9177 | 15.9177 | 15.9177 | 15.9177 | 15.9177 | 15.9177 | 15.9177 | 15.9177 | 15.9177 | 15.9177 | 15.9177 | 15.9177 | 15.9177 | 25% | 3537.8514 | 11.8835 | 12.9657 | 13.0778 | 13.4646 | 13.4552 | 13.5402 | 13.8729 | 14.8286 | 15.223 | 14.8497 | 15.881 | 15.448 | 15.8376 | 16.1184 | 16.003 | 16.003 | 16.003 | 16.003 | 16.003 | 16.003 | 16.003 | 16.003 | 16.003 | 16.003 | 16.003 | 16.003 | 16.003 | 16.003 | 16.003 | 16.003
20% | 3731.0305 | 8.6726 | 9.5803 | 9.6765 | 9.7955 | 9.9535 | 10.1033 | 10.365 | 11.0233 | 11.3774 | 11.1191 | 11.9188 | 12.0629 | 12.1665 | 12.6547 | 12.7341 | 12.7341 | 12.7341 | 12.7341 | 12.7341 | 12.7341 | 12.7341 | 12.7341 | 12.7341 | 12.7341 | 12.7341 | 12.7341 | 12.7341 | 12.7341 | 12.7341 | 12.7341 | 20% | 3731.0305 | 9.5068 | 10.3726 | 10.4623 | 10.7717 | 10.7642 | 10.8322 | 11.0983 | 11.8629 | 12.1784 | 11.8798 | 12.7048 | 12.3584 | 12.6701 | 12.8947 | 12.8024 | 12.8024 | 12.8024 | 12.8024 | 12.8024 | 12.8024 | 12.8024 | 12.8024 | 12.8024 | 12.8024 | 12.8024 | 12.8024 | 12.8024 | 12.8024 | 12.8024 | 12.8024
15% | 3910.2412 | 6.5044 | 7.1852 | 7.2574 | 7.3466 | 7.4651 | 7.5774 | 7.7738 | 8.2675 | 8.5331 | 8.3393 | 8.9391 | 9.0472 | 9.1248 | 9.491 | 9.5506 | 9.5506 | 9.5506 | 9.5506 | 9.5506 | 9.5506 | 9.5506 | 9.5506 | 9.5506 | 9.5506 | 9.5506 | 9.5506 | 9.5506 | 9.5506 | 9.5506 | 9.5506 | 15% | 3910.2412 | 7.1301 | 7.7794 | 7.8467 | 8.0788 | 8.0731 | 8.1241 | 8.3237 | 8.8972 | 9.1338 | 8.9098 | 9.5286 | 9.2688 | 9.5026 | 9.671 | 9.6018 | 9.6018 | 9.6018 | 9.6018 | 9.6018 | 9.6018 | 9.6018 | 9.6018 | 9.6018 | 9.6018 | 9.6018 | 9.6018 | 9.6018 | 9.6018 | 9.6018 | 9.6018
10% | 4075.1864 | 4.3363 | 4.7901 | 4.8383 | 4.8977 | 4.9767 | 5.0516 | 5.1825 | 5.5117 | 5.6887 | 5.5595 | 5.9594 | 6.0314 | 6.0832 | 6.3273 | 6.3671 | 6.3671 | 6.3671 | 6.3671 | 6.3671 | 6.3671 | 6.3671 | 6.3671 | 6.3671 | 6.3671 | 6.3671 | 6.3671 | 6.3671 | 6.3671 | 6.3671 | 6.3671 | 10% | 4075.1864 | 4.7534 | 5.1863 | 5.2311 | 5.3858 | 5.3821 | 5.4161 | 5.5492 | 5.9315 | 6.0892 | 5.9399 | 6.3524 | 6.1792 | 6.335 | 6.4473 | 6.4012 | 6.4012 | 6.4012 | 6.4012 | 6.4012 | 6.4012 | 6.4012 | 6.4012 | 6.4012 | 6.4012 | 6.4012 | 6.4012 | 6.4012 | 6.4012 | 6.4012 | 6.4012
5% | 4251.7223 | 2.1681 | 2.3951 | 2.4191 | 2.4489 | 2.4884 | 2.5258 | 2.5913 | 2.7558 | 2.8444 | 2.7798 | 2.9797 | 3.0157 | 3.0416 | 3.1637 | 3.1835 | 3.1835 | 3.1835 | 3.1835 | 3.1835 | 3.1835 | 3.1835 | 3.1835 | 3.1835 | 3.1835 | 3.1835 | 3.1835 | 3.1835 | 3.1835 | 3.1835 | 3.1835 | 5% | 4251.7223 | 2.3767 | 2.5931 | 2.6156 | 2.6929 | 2.691 | 2.708 | 2.7746 | 2.9657 | 3.0446 | 2.9699 | 3.1762 | 3.0896 | 3.1675 | 3.2237 | 3.2006 | 3.2006 | 3.2006 | 3.2006 | 3.2006 | 3.2006 | 3.2006 | 3.2006 | 3.2006 | 3.2006 | 3.2006 | 3.2006 | 3.2006 | 3.2006 | 3.2006 | 3.2006
9.992e-14% | 4391.7028 | 4.3328e-14 | 4.7863e-14 | 4.8344e-14 | 4.8938e-14 | 4.9728e-14 | 5.0476e-14 | 5.1784e-14 | 5.5073e-14 | 5.6842e-14 | 5.5551e-14 | 5.9546e-14 | 6.0266e-14 | 6.0784e-14 | 6.3223e-14 | 6.362e-14 | 6.362e-14 | 6.362e-14 | 6.362e-14 | 6.362e-14 | 6.362e-14 | 6.362e-14 | 6.362e-14 | 6.362e-14 | 6.362e-14 | 6.362e-14 | 6.362e-14 | 6.362e-14 | 6.362e-14 | 6.362e-14 | 6.362e-14 | 9.992e-14% | 4391.7028 | 4.7496e-14 | 5.1822e-14 | 5.2269e-14 | 5.3815e-14 | 5.3778e-14 | 5.4118e-14 | 5.5447e-14 | 5.9267e-14 | 6.0844e-14 | 5.9351e-14 | 6.3473e-14 | 6.1743e-14 | 6.33e-14 | 6.4422e-14 | 6.3961e-14 | 6.3961e-14 | 6.3961e-14 | 6.3961e-14 | 6.3961e-14 | 6.3961e-14 | 6.3961e-14 | 6.3961e-14 | 6.3961e-14 | 6.3961e-14 | 6.3961e-14 | 6.3961e-14 | 6.3961e-14 | 6.3961e-14 | 6.3961e-14 | 6.3961e-14
Summer Season | [31 empty] | Summer Season
P50 | [31 empty] | P10
% of MD | Summer - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Summer - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 45.5533 | 48.9582 | 49.3004 | 49.1327 | 49.2921 | 49.3577 | 49.5677 | 49.9995 | 50.3627 | 50.5299 | 50.3809 | 51.0058 | 51.1049 | 50.9876 | 51.2228 | 51.3328 | 51.3328 | 51.3328 | 51.3328 | 51.3328 | 51.3328 | 51.3328 | 51.3328 | 51.3328 | 51.3328 | 51.3328 | 51.3328 | 51.3328 | 51.3328 | 51.3328 | 100% | 0 | 56.0411 | 59.8463 | 59.9513 | 59.8381 | 59.8672 | 60.075 | 60.4961 | 61.2377 | 61.6242 | 61.9037 | 62.3269 | 62.867 | 63.5203 | 63.8626 | 63.7516 | 63.8616 | 63.8616 | 63.8616 | 63.8616 | 63.8616 | 63.8616 | 63.8616 | 63.8616 | 63.8616 | 63.8616 | 63.8616 | 63.8616 | 63.8616 | 63.8616 | 63.8616
99% | 0.37816 | 45.0978 | 48.4686 | 48.8074 | 48.6413 | 48.7992 | 48.8641 | 49.072 | 49.4995 | 49.8591 | 50.0246 | 49.8771 | 50.4957 | 50.5938 | 50.4777 | 50.7105 | 50.8194 | 50.8194 | 50.8194 | 50.8194 | 50.8194 | 50.8194 | 50.8194 | 50.8194 | 50.8194 | 50.8194 | 50.8194 | 50.8194 | 50.8194 | 50.8194 | 50.8194 | 99% | 0 | 55.4807 | 59.2478 | 59.3518 | 59.2397 | 59.2685 | 59.4742 | 59.8911 | 60.6254 | 61.0079 | 61.2847 | 61.7036 | 62.2384 | 62.8851 | 63.224 | 63.1141 | 63.223 | 63.223 | 63.223 | 63.223 | 63.223 | 63.223 | 63.223 | 63.223 | 63.223 | 63.223 | 63.223 | 63.223 | 63.223 | 63.223 | 63.223
98% | 0.37816 | 44.6423 | 47.9791 | 48.3144 | 48.15 | 48.3063 | 48.3705 | 48.5763 | 48.9995 | 49.3555 | 49.5193 | 49.3733 | 49.9856 | 50.0828 | 49.9678 | 50.1983 | 50.3061 | 50.3061 | 50.3061 | 50.3061 | 50.3061 | 50.3061 | 50.3061 | 50.3061 | 50.3061 | 50.3061 | 50.3061 | 50.3061 | 50.3061 | 50.3061 | 50.3061 | 98% | 0 | 54.9203 | 58.6494 | 58.7523 | 58.6413 | 58.6699 | 58.8735 | 59.2862 | 60.013 | 60.3917 | 60.6657 | 61.0803 | 61.6097 | 62.2499 | 62.5853 | 62.4766 | 62.5844 | 62.5844 | 62.5844 | 62.5844 | 62.5844 | 62.5844 | 62.5844 | 62.5844 | 62.5844 | 62.5844 | 62.5844 | 62.5844 | 62.5844 | 62.5844 | 62.5844
97% | 0.37816 | 44.1867 | 47.4895 | 47.8214 | 47.6587 | 47.8134 | 47.8769 | 48.0806 | 48.4995 | 48.8518 | 49.014 | 48.8695 | 49.4756 | 49.5717 | 49.458 | 49.6861 | 49.7928 | 49.7928 | 49.7928 | 49.7928 | 49.7928 | 49.7928 | 49.7928 | 49.7928 | 49.7928 | 49.7928 | 49.7928 | 49.7928 | 49.7928 | 49.7928 | 49.7928 | 97% | 0.37816 | 54.3599 | 58.0509 | 58.1528 | 58.0429 | 58.0712 | 58.2727 | 58.6812 | 59.4006 | 59.7754 | 60.0466 | 60.457 | 60.981 | 61.6146 | 61.9467 | 61.8391 | 61.9458 | 61.9458 | 61.9458 | 61.9458 | 61.9458 | 61.9458 | 61.9458 | 61.9458 | 61.9458 | 61.9458 | 61.9458 | 61.9458 | 61.9458 | 61.9458 | 61.9458
95% | 0.75633 | 43.2757 | 46.5103 | 46.8354 | 46.676 | 46.8275 | 46.8898 | 47.0893 | 47.4995 | 47.8446 | 48.0034 | 47.8618 | 48.4555 | 48.5496 | 48.4382 | 48.6616 | 48.7661 | 48.7661 | 48.7661 | 48.7661 | 48.7661 | 48.7661 | 48.7661 | 48.7661 | 48.7661 | 48.7661 | 48.7661 | 48.7661 | 48.7661 | 48.7661 | 48.7661 | 95% | 0.37816 | 53.2391 | 56.854 | 56.9537 | 56.8462 | 56.8738 | 57.0712 | 57.4713 | 58.1758 | 58.543 | 58.8086 | 59.2105 | 59.7237 | 60.3442 | 60.6695 | 60.564 | 60.6685 | 60.6685 | 60.6685 | 60.6685 | 60.6685 | 60.6685 | 60.6685 | 60.6685 | 60.6685 | 60.6685 | 60.6685 | 60.6685 | 60.6685 | 60.6685 | 60.6685
90% | 9.0759 | 40.998 | 44.0624 | 44.3703 | 44.2194 | 44.3629 | 44.4219 | 44.6109 | 44.9995 | 45.3264 | 45.4769 | 45.3428 | 45.9052 | 45.9944 | 45.8888 | 46.1005 | 46.1995 | 46.1995 | 46.1995 | 46.1995 | 46.1995 | 46.1995 | 46.1995 | 46.1995 | 46.1995 | 46.1995 | 46.1995 | 46.1995 | 46.1995 | 46.1995 | 46.1995 | 90% | 0.75633 | 50.437 | 53.8617 | 53.9562 | 53.8543 | 53.8805 | 54.0675 | 54.4465 | 55.114 | 55.4618 | 55.7134 | 56.0942 | 56.5803 | 57.1682 | 57.4763 | 57.3764 | 57.4754 | 57.4754 | 57.4754 | 57.4754 | 57.4754 | 57.4754 | 57.4754 | 57.4754 | 57.4754 | 57.4754 | 57.4754 | 57.4754 | 57.4754 | 57.4754 | 57.4754
85% | 40.4636 | 38.7203 | 41.6145 | 41.9053 | 41.7628 | 41.8983 | 41.954 | 42.1325 | 42.4995 | 42.8083 | 42.9504 | 42.8238 | 43.3549 | 43.4391 | 43.3394 | 43.5393 | 43.6328 | 43.6328 | 43.6328 | 43.6328 | 43.6328 | 43.6328 | 43.6328 | 43.6328 | 43.6328 | 43.6328 | 43.6328 | 43.6328 | 43.6328 | 43.6328 | 43.6328 | 85% | 1.1345 | 47.6349 | 50.8694 | 50.9586 | 50.8624 | 50.8871 | 51.0637 | 51.4217 | 52.0521 | 52.3805 | 52.6182 | 52.9778 | 53.437 | 53.9922 | 54.2832 | 54.1889 | 54.2824 | 54.2824 | 54.2824 | 54.2824 | 54.2824 | 54.2824 | 54.2824 | 54.2824 | 54.2824 | 54.2824 | 54.2824 | 54.2824 | 54.2824 | 54.2824 | 54.2824
80% | 94.5411 | 36.4427 | 39.1666 | 39.4403 | 39.3061 | 39.4337 | 39.4861 | 39.6541 | 39.9996 | 40.2902 | 40.4239 | 40.3047 | 40.8046 | 40.8839 | 40.7901 | 40.9782 | 41.0662 | 41.0662 | 41.0662 | 41.0662 | 41.0662 | 41.0662 | 41.0662 | 41.0662 | 41.0662 | 41.0662 | 41.0662 | 41.0662 | 41.0662 | 41.0662 | 41.0662 | 80% | 2.6471 | 44.8329 | 47.877 | 47.961 | 47.8705 | 47.8938 | 48.06 | 48.3969 | 48.9902 | 49.2993 | 49.523 | 49.8615 | 50.2936 | 50.8162 | 51.0901 | 51.0013 | 51.0893 | 51.0893 | 51.0893 | 51.0893 | 51.0893 | 51.0893 | 51.0893 | 51.0893 | 51.0893 | 51.0893 | 51.0893 | 51.0893 | 51.0893 | 51.0893 | 51.0893
75% | 197.0236 | 34.165 | 36.7187 | 36.9753 | 36.8495 | 36.9691 | 37.0182 | 37.1757 | 37.4996 | 37.772 | 37.8974 | 37.7857 | 38.2543 | 38.3286 | 38.2407 | 38.4171 | 38.4996 | 38.4996 | 38.4996 | 38.4996 | 38.4996 | 38.4996 | 38.4996 | 38.4996 | 38.4996 | 38.4996 | 38.4996 | 38.4996 | 38.4996 | 38.4996 | 38.4996 | 75% | 3.4035 | 42.0308 | 44.8847 | 44.9635 | 44.8786 | 44.9004 | 45.0562 | 45.3721 | 45.9283 | 46.2181 | 46.4278 | 46.7451 | 47.1503 | 47.6402 | 47.8969 | 47.8137 | 47.8962 | 47.8962 | 47.8962 | 47.8962 | 47.8962 | 47.8962 | 47.8962 | 47.8962 | 47.8962 | 47.8962 | 47.8962 | 47.8962 | 47.8962 | 47.8962 | 47.8962
70% | 336.9444 | 31.8873 | 34.2708 | 34.5103 | 34.3929 | 34.5045 | 34.5504 | 34.6974 | 34.9996 | 35.2539 | 35.371 | 35.2666 | 35.704 | 35.7734 | 35.6913 | 35.8559 | 35.9329 | 35.9329 | 35.9329 | 35.9329 | 35.9329 | 35.9329 | 35.9329 | 35.9329 | 35.9329 | 35.9329 | 35.9329 | 35.9329 | 35.9329 | 35.9329 | 35.9329 | 70% | 5.6725 | 39.2288 | 41.8924 | 41.9659 | 41.8867 | 41.907 | 42.0525 | 42.3473 | 42.8664 | 43.1369 | 43.3326 | 43.6288 | 44.0069 | 44.4642 | 44.7038 | 44.6261 | 44.7031 | 44.7031 | 44.7031 | 44.7031 | 44.7031 | 44.7031 | 44.7031 | 44.7031 | 44.7031 | 44.7031 | 44.7031 | 44.7031 | 44.7031 | 44.7031 | 44.7031
65% | 521.4885 | 29.6097 | 31.8228 | 32.0452 | 31.9362 | 32.0399 | 32.0825 | 32.219 | 32.4996 | 32.7358 | 32.8445 | 32.7476 | 33.1537 | 33.2182 | 33.1419 | 33.2948 | 33.3663 | 33.3663 | 33.3663 | 33.3663 | 33.3663 | 33.3663 | 33.3663 | 33.3663 | 33.3663 | 33.3663 | 33.3663 | 33.3663 | 33.3663 | 33.3663 | 33.3663 | 65% | 6.4288 | 36.4267 | 38.9001 | 38.9683 | 38.8948 | 38.9137 | 39.0487 | 39.3225 | 39.8045 | 40.0557 | 40.2374 | 40.5125 | 40.8636 | 41.2882 | 41.5107 | 41.4385 | 41.51 | 41.51 | 41.51 | 41.51 | 41.51 | 41.51 | 41.51 | 41.51 | 41.51 | 41.51 | 41.51 | 41.51 | 41.51 | 41.51 | 41.51
60% | 812.675 | 27.332 | 29.3749 | 29.5802 | 29.4796 | 29.5753 | 29.6146 | 29.7406 | 29.9997 | 30.2176 | 30.318 | 30.2285 | 30.6035 | 30.6629 | 30.5925 | 30.7337 | 30.7997 | 30.7997 | 30.7997 | 30.7997 | 30.7997 | 30.7997 | 30.7997 | 30.7997 | 30.7997 | 30.7997 | 30.7997 | 30.7997 | 30.7997 | 30.7997 | 30.7997 | 60% | 11.3449 | 33.6247 | 35.9078 | 35.9708 | 35.9029 | 35.9203 | 36.045 | 36.2977 | 36.7426 | 36.9745 | 37.1422 | 37.3961 | 37.7202 | 38.1122 | 38.3176 | 38.251 | 38.317 | 38.317 | 38.317 | 38.317 | 38.317 | 38.317 | 38.317 | 38.317 | 38.317 | 38.317 | 38.317 | 38.317 | 38.317 | 38.317 | 38.317
55% | 1202.1843 | 25.0543 | 26.927 | 27.1152 | 27.023 | 27.1107 | 27.1467 | 27.2622 | 27.4997 | 27.6995 | 27.7915 | 27.7095 | 28.0532 | 28.1077 | 28.0432 | 28.1725 | 28.233 | 28.233 | 28.233 | 28.233 | 28.233 | 28.233 | 28.233 | 28.233 | 28.233 | 28.233 | 28.233 | 28.233 | 28.233 | 28.233 | 28.233 | 55% | 35.5474 | 30.8226 | 32.9155 | 32.9732 | 32.911 | 32.927 | 33.0412 | 33.2729 | 33.6808 | 33.8933 | 34.0471 | 34.2798 | 34.5769 | 34.9361 | 35.1244 | 35.0634 | 35.1239 | 35.1239 | 35.1239 | 35.1239 | 35.1239 | 35.1239 | 35.1239 | 35.1239 | 35.1239 | 35.1239 | 35.1239 | 35.1239 | 35.1239 | 35.1239 | 35.1239
50% | 1686.2345 | 22.7767 | 24.4791 | 24.6502 | 24.5663 | 24.6461 | 24.6788 | 24.7838 | 24.9997 | 25.1814 | 25.265 | 25.1904 | 25.5029 | 25.5524 | 25.4938 | 25.6114 | 25.6664 | 25.6664 | 25.6664 | 25.6664 | 25.6664 | 25.6664 | 25.6664 | 25.6664 | 25.6664 | 25.6664 | 25.6664 | 25.6664 | 25.6664 | 25.6664 | 25.6664 | 50% | 95.2974 | 28.0206 | 29.9231 | 29.9756 | 29.919 | 29.9336 | 30.0375 | 30.2481 | 30.6189 | 30.8121 | 30.9519 | 31.1634 | 31.4335 | 31.7601 | 31.9313 | 31.8758 | 31.9308 | 31.9308 | 31.9308 | 31.9308 | 31.9308 | 31.9308 | 31.9308 | 31.9308 | 31.9308 | 31.9308 | 31.9308 | 31.9308 | 31.9308 | 31.9308 | 31.9308
45% | 2129.0649 | 20.499 | 22.0312 | 22.1852 | 22.1097 | 22.1815 | 22.2109 | 22.3054 | 22.4998 | 22.6632 | 22.7385 | 22.6714 | 22.9526 | 22.9972 | 22.9444 | 23.0502 | 23.0997 | 23.0997 | 23.0997 | 23.0997 | 23.0997 | 23.0997 | 23.0997 | 23.0997 | 23.0997 | 23.0997 | 23.0997 | 23.0997 | 23.0997 | 23.0997 | 23.0997 | 45% | 208.7467 | 25.2185 | 26.9308 | 26.9781 | 26.9271 | 26.9402 | 27.0337 | 27.2232 | 27.557 | 27.7309 | 27.8567 | 28.0471 | 28.2902 | 28.5841 | 28.7382 | 28.6882 | 28.7377 | 28.7377 | 28.7377 | 28.7377 | 28.7377 | 28.7377 | 28.7377 | 28.7377 | 28.7377 | 28.7377 | 28.7377 | 28.7377 | 28.7377 | 28.7377 | 28.7377
40% | 2484.5393 | 18.2213 | 19.5833 | 19.7201 | 19.6531 | 19.7169 | 19.7431 | 19.8271 | 19.9998 | 20.1451 | 20.212 | 20.1524 | 20.4023 | 20.4419 | 20.395 | 20.4891 | 20.5331 | 20.5331 | 20.5331 | 20.5331 | 20.5331 | 20.5331 | 20.5331 | 20.5331 | 20.5331 | 20.5331 | 20.5331 | 20.5331 | 20.5331 | 20.5331 | 20.5331 | 40% | 380.4333 | 22.4164 | 23.9385 | 23.9805 | 23.9352 | 23.9469 | 24.03 | 24.1984 | 24.4951 | 24.6497 | 24.7615 | 24.9307 | 25.1468 | 25.4081 | 25.545 | 25.5006 | 25.5446 | 25.5446 | 25.5446 | 25.5446 | 25.5446 | 25.5446 | 25.5446 | 25.5446 | 25.5446 | 25.5446 | 25.5446 | 25.5446 | 25.5446 | 25.5446 | 25.5446
35% | 2808.248 | 15.9437 | 17.1354 | 17.2551 | 17.1964 | 17.2522 | 17.2752 | 17.3487 | 17.4998 | 17.6269 | 17.6855 | 17.6333 | 17.852 | 17.8867 | 17.8457 | 17.928 | 17.9665 | 17.9665 | 17.9665 | 17.9665 | 17.9665 | 17.9665 | 17.9665 | 17.9665 | 17.9665 | 17.9665 | 17.9665 | 17.9665 | 17.9665 | 17.9665 | 17.9665 | 35% | 696.5786 | 19.6144 | 20.9462 | 20.983 | 20.9433 | 20.9535 | 21.0262 | 21.1736 | 21.4332 | 21.5685 | 21.6663 | 21.8144 | 22.0035 | 22.2321 | 22.3519 | 22.3131 | 22.3516 | 22.3516 | 22.3516 | 22.3516 | 22.3516 | 22.3516 | 22.3516 | 22.3516 | 22.3516 | 22.3516 | 22.3516 | 22.3516 | 22.3516 | 22.3516 | 22.3516
30% | 3095.6528 | 13.666 | 14.6875 | 14.7901 | 14.7398 | 14.7876 | 14.8073 | 14.8703 | 14.9998 | 15.1088 | 15.159 | 15.1143 | 15.3017 | 15.3315 | 15.2963 | 15.3668 | 15.3998 | 15.3998 | 15.3998 | 15.3998 | 15.3998 | 15.3998 | 15.3998 | 15.3998 | 15.3998 | 15.3998 | 15.3998 | 15.3998 | 15.3998 | 15.3998 | 15.3998 | 30% | 1260.7997 | 16.8123 | 17.9539 | 17.9854 | 17.9514 | 17.9602 | 18.0225 | 18.1488 | 18.3713 | 18.4873 | 18.5711 | 18.6981 | 18.8601 | 19.0561 | 19.1588 | 19.1255 | 19.1585 | 19.1585 | 19.1585 | 19.1585 | 19.1585 | 19.1585 | 19.1585 | 19.1585 | 19.1585 | 19.1585 | 19.1585 | 19.1585 | 19.1585 | 19.1585 | 19.1585
25% | 3358.8552 | 11.3883 | 12.2396 | 12.3251 | 12.2832 | 12.323 | 12.3394 | 12.3919 | 12.4999 | 12.5907 | 12.6325 | 12.5952 | 12.7514 | 12.7762 | 12.7469 | 12.8057 | 12.8332 | 12.8332 | 12.8332 | 12.8332 | 12.8332 | 12.8332 | 12.8332 | 12.8332 | 12.8332 | 12.8332 | 12.8332 | 12.8332 | 12.8332 | 12.8332 | 12.8332 | 25% | 1965.3198 | 14.0103 | 14.9616 | 14.9878 | 14.9595 | 14.9668 | 15.0187 | 15.124 | 15.3094 | 15.406 | 15.4759 | 15.5817 | 15.7168 | 15.8801 | 15.9656 | 15.9379 | 15.9654 | 15.9654 | 15.9654 | 15.9654 | 15.9654 | 15.9654 | 15.9654 | 15.9654 | 15.9654 | 15.9654 | 15.9654 | 15.9654 | 15.9654 | 15.9654 | 15.9654
20% | 3588.7791 | 9.1107 | 9.7916 | 9.8601 | 9.8265 | 9.8584 | 9.8715 | 9.9135 | 9.9999 | 10.0725 | 10.106 | 10.0762 | 10.2012 | 10.221 | 10.1975 | 10.2446 | 10.2666 | 10.2666 | 10.2666 | 10.2666 | 10.2666 | 10.2666 | 10.2666 | 10.2666 | 10.2666 | 10.2666 | 10.2666 | 10.2666 | 10.2666 | 10.2666 | 10.2666 | 20% | 2490.2118 | 11.2082 | 11.9693 | 11.9903 | 11.9676 | 11.9734 | 12.015 | 12.0992 | 12.2475 | 12.3248 | 12.3807 | 12.4654 | 12.5734 | 12.7041 | 12.7725 | 12.7503 | 12.7723 | 12.7723 | 12.7723 | 12.7723 | 12.7723 | 12.7723 | 12.7723 | 12.7723 | 12.7723 | 12.7723 | 12.7723 | 12.7723 | 12.7723 | 12.7723 | 12.7723
15% | 3802.4419 | 6.833 | 7.3437 | 7.3951 | 7.3699 | 7.3938 | 7.4036 | 7.4351 | 7.4999 | 7.5544 | 7.5795 | 7.5571 | 7.6509 | 7.6657 | 7.6481 | 7.6834 | 7.6999 | 7.6999 | 7.6999 | 7.6999 | 7.6999 | 7.6999 | 7.6999 | 7.6999 | 7.6999 | 7.6999 | 7.6999 | 7.6999 | 7.6999 | 7.6999 | 7.6999 | 15% | 2997.7083 | 8.4062 | 8.9769 | 8.9927 | 8.9757 | 8.9801 | 9.0112 | 9.0744 | 9.1857 | 9.2436 | 9.2856 | 9.349 | 9.4301 | 9.528 | 9.5794 | 9.5627 | 9.5792 | 9.5792 | 9.5792 | 9.5792 | 9.5792 | 9.5792 | 9.5792 | 9.5792 | 9.5792 | 9.5792 | 9.5792 | 9.5792 | 9.5792 | 9.5792 | 9.5792
10% | 4024.8025 | 4.5553 | 4.8958 | 4.93 | 4.9133 | 4.9292 | 4.9358 | 4.9568 | 4.9999 | 5.0363 | 5.053 | 5.0381 | 5.1006 | 5.1105 | 5.0988 | 5.1223 | 5.1333 | 5.1333 | 5.1333 | 5.1333 | 5.1333 | 5.1333 | 5.1333 | 5.1333 | 5.1333 | 5.1333 | 5.1333 | 5.1333 | 5.1333 | 5.1333 | 5.1333 | 10% | 3491.5908 | 5.6041 | 5.9846 | 5.9951 | 5.9838 | 5.9867 | 6.0075 | 6.0496 | 6.1238 | 6.1624 | 6.1904 | 6.2327 | 6.2867 | 6.352 | 6.3863 | 6.3752 | 6.3862 | 6.3862 | 6.3862 | 6.3862 | 6.3862 | 6.3862 | 6.3862 | 6.3862 | 6.3862 | 6.3862 | 6.3862 | 6.3862 | 6.3862 | 6.3862 | 6.3862
5% | 4239.978 | 2.2777 | 2.4479 | 2.465 | 2.4566 | 2.4646 | 2.4679 | 2.4784 | 2.5 | 2.5181 | 2.5265 | 2.519 | 2.5503 | 2.5552 | 2.5494 | 2.5611 | 2.5666 | 2.5666 | 2.5666 | 2.5666 | 2.5666 | 2.5666 | 2.5666 | 2.5666 | 2.5666 | 2.5666 | 2.5666 | 2.5666 | 2.5666 | 2.5666 | 2.5666 | 5% | 3955.9766 | 2.8021 | 2.9923 | 2.9976 | 2.9919 | 2.9934 | 3.0037 | 3.0248 | 3.0619 | 3.0812 | 3.0952 | 3.1163 | 3.1434 | 3.176 | 3.1931 | 3.1876 | 3.1931 | 3.1931 | 3.1931 | 3.1931 | 3.1931 | 3.1931 | 3.1931 | 3.1931 | 3.1931 | 3.1931 | 3.1931 | 3.1931 | 3.1931 | 3.1931 | 3.1931
9.992e-14% | 4391.6218 | 4.5517e-14 | 4.8919e-14 | 4.9261e-14 | 4.9093e-14 | 4.9253e-14 | 4.9318e-14 | 4.9528e-14 | 4.9959e-14 | 5.0322e-14 | 5.049e-14 | 5.0341e-14 | 5.0965e-14 | 5.1064e-14 | 5.0947e-14 | 5.1182e-14 | 5.1292e-14 | 5.1292e-14 | 5.1292e-14 | 5.1292e-14 | 5.1292e-14 | 5.1292e-14 | 5.1292e-14 | 5.1292e-14 | 5.1292e-14 | 5.1292e-14 | 5.1292e-14 | 5.1292e-14 | 5.1292e-14 | 5.1292e-14 | 5.1292e-14 | 9.992e-14% | 4391.6218 | 5.5996e-14 | 5.9798e-14 | 5.9903e-14 | 5.979e-14 | 5.9819e-14 | 6.0027e-14 | 6.0448e-14 | 6.1189e-14 | 6.1575e-14 | 6.1854e-14 | 6.2277e-14 | 6.2817e-14 | 6.3469e-14 | 6.3812e-14 | 6.3701e-14 | 6.3811e-14 | 6.3811e-14 | 6.3811e-14 | 6.3811e-14 | 6.3811e-14 | 6.3811e-14 | 6.3811e-14 | 6.3811e-14 | 6.3811e-14 | 6.3811e-14 | 6.3811e-14 | 6.3811e-14 | 6.3811e-14 | 6.3811e-14 | 6.3811e-14

## Locational VCR
Base case |  | Energy Usage (CY 2024 kWh) | Energy Usage (CY 2024 %) | Tailored VCR
Dec 24 AER VCR ($/kWh) - Res | 49.23 | 88661416.1819 | 59.86% | 29.4686
Dec 24 AER VCR ($/kWh) - Com | 34.39 | 45585213.1364 | 30.78% | 10.584
Dec 24 AER VCR ($/kWh) - Ind | 33.49 | 5851096.6819 | 3.95% | 1.323
Dec 24 AER VCR ($/kWh) - Agr | 22.25 | 8019086.0298 | 5.414% | 1.2046
|  | 148116812.03 |  | 42.5803 | KW/h
|  |  |  | 42580.277 | MW/h

## E@R N
Option 1 - Do Nothing
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | [8 empty] | 0.0019784 |  | 0.74182 | 0.95486 | 1.108 | 1.8298 | 1.9473 | 1.9473 | 1.9473 | 1.9473 | 1.9473 | 1.9473 | 1.9473 | 1.9473 | 1.9473 | 1.9473 | 1.9473 | 1.9473 | 1.9473 | 1.9473 | 1.9473 | 1.9473 | [8 empty] | 0.65919 | 1.1257 | 0.68411 | 1.904 | 1.3918 | 1.8526 | 2.1847 | 2.0483 | 2.0483 | 2.0483 | 2.0483 | 2.0483 | 2.0483 | 2.0483 | 2.0483 | 2.0483 | 2.0483 | 2.0483 | 2.0483 | 2.0483 | 2.0483 | 2.0483 | 2.0483
98% | [10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
97% | [10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
95% | [10 empty] | 0.5049 | 1.3099 | 1.9009 | 4.6867 | 5.1402 | 5.1402 | 5.1402 | 5.1402 | 5.1402 | 5.1402 | 5.1402 | 5.1402 | 5.1402 | 5.1402 | 5.1402 | 5.1402 | 5.1402 | 5.1402 | 5.1402 | 5.1402 | [8 empty] | 0.27079 | 1.9692 | 0.33389 | 4.9727 | 2.9962 | 4.7747 | 6.0563 | 5.5297 | 5.5297 | 5.5297 | 5.5297 | 5.5297 | 5.5297 | 5.5297 | 5.5297 | 5.5297 | 5.5297 | 5.5297 | 5.5297 | 5.5297 | 5.5297 | 5.5297 | 5.5297
90% | [11 empty] | 0.29412 | 1.1508 | 12.3243 | 14.9458 | 14.9458 | 14.9458 | 14.9458 | 14.9458 | 14.9458 | 14.9458 | 14.9458 | 14.9458 | 14.9458 | 14.9458 | 14.9458 | 14.9458 | 14.9458 | 14.9458 | 14.9458 | [9 empty] | 1.2855 |  | 13.9779 | 4.1777 | 12.8328 | 20.2422 | 17.1981 | 17.1981 | 17.1981 | 17.1981 | 17.1981 | 17.1981 | 17.1981 | 17.1981 | 17.1981 | 17.1981 | 17.1981 | 17.1981 | 17.1981 | 17.1981 | 17.1981 | 17.1981
85% | FY38: 0.10615; FY39: 1.2549; FY40: 1.2549; FY41: 1.2549; FY42: 1.2549; FY43: 1.2549; FY44: 1.2549; FY45: 1.2549; FY46: 1.2549; FY47: 1.2549; FY48: 1.2549; FY49: 1.2549; FY50: 1.2549; FY51: 1.2549; FY52: 1.2549; FY53: 1.2549; FY54: 1.2549 | [11 empty] | 0.68472 |  | 0.23068 | 7.3453 | 3.2356 | 3.2356 | 3.2356 | 3.2356 | 3.2356 | 3.2356 | 3.2356 | 3.2356 | 3.2356 | 3.2356 | 3.2356 | 3.2356 | 3.2356 | 3.2356 | 3.2356 | 3.2356
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0019586 | 0 | 1.2342 | 2.5333 | 4.1181 | 18.7576 | 23.0554 | 23.0554 | 23.0554 | 23.0554 | 23.0554 | 23.0554 | 23.0554 | 23.0554 | 23.0554 | 23.0554 | 23.0554 | 23.0554 | 23.0554 | 23.0554 | 23.0554 | 23.0554 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.92068 | 4.3366 | 1.0078 | 21.3239 | 8.4801 | 19.4939 | 35.4703 | 27.7316 | 27.7316 | 27.7316 | 27.7316 | 27.7316 | 27.7316 | 27.7316 | 27.7316 | 27.7316 | 27.7316 | 27.7316 | 27.7316 | 27.7316 | 27.7316 | 27.7316 | 27.7316
Option 1 Winter POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.001371 | 0 | 0.86397 | 1.7733 | 2.8826 | 13.1303 | 16.1388 | 16.1388 | 16.1388 | 16.1388 | 16.1388 | 16.1388 | 16.1388 | 16.1388 | 16.1388 | 16.1388 | 16.1388 | 16.1388 | 16.1388 | 16.1388 | 16.1388 | 16.1388 | Option 1 Winter POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.27621 | 1.301 | 0.30235 | 6.3972 | 2.544 | 5.8482 | 10.6411 | 8.3195 | 8.3195 | 8.3195 | 8.3195 | 8.3195 | 8.3195 | 8.3195 | 8.3195 | 8.3195 | 8.3195 | 8.3195 | 8.3195 | 8.3195 | 8.3195 | 8.3195 | 8.3195
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | [31 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
98% | [32 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
97% | [32 empty] | 0.96437 | 1.0031 | 0.96135 | 0.97208 | 1.0487 | 1.204 | 1.4774 | 1.6199 | 1.723 | 1.879 | 2.0782 | 2.319 | 2.4452 | 2.4043 | 2.4449 | 2.4449 | 2.4449 | 2.4449 | 2.4449 | 2.4449 | 2.4449 | 2.4449 | 2.4449 | 2.4449 | 2.4449 | 2.4449 | 2.4449 | 2.4449 | 2.4449
95% | [32 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
90% | [32 empty] | 0.070196 | 0.083964 | 0.069171 | 0.072841 | 0.10173 | 0.17461 | 0.34858 | 0.46171 | 0.55294 | 0.70049 | 0.88945 | 1.1179 | 1.2377 | 1.1989 | 1.2373 | 1.2373 | 1.2373 | 1.2373 | 1.2373 | 1.2373 | 1.2373 | 1.2373 | 1.2373 | 1.2373 | 1.2373 | 1.2373 | 1.2373 | 1.2373 | 1.2373
85% | [41 empty] | 0.0052505 | 0.036629 | 0.11145 | 0.1664 | 0.14742 | 0.16623 | 0.16623 | 0.16623 | 0.16623 | 0.16623 | 0.16623 | 0.16623 | 0.16623 | 0.16623 | 0.16623 | 0.16623 | 0.16623 | 0.16623 | 0.16623 | 0.16623
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 1.0242 | 1.0762 | 1.0202 | 1.0345 | 1.1389 | 1.3648 | 1.8077 | 2.0608 | 2.2532 | 2.5589 | 2.9742 | 3.5129 | 3.8108 | 3.7131 | 3.81 | 3.81 | 3.81 | 3.81 | 3.81 | 3.81 | 3.81 | 3.81 | 3.81 | 3.81 | 3.81 | 3.81 | 3.81 | 3.81 | 3.81
Option 1 Summer POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 1 Summer POE10 W E @ R (MWh) | 0 | 0.30727 | 0.32285 | 0.30606 | 0.31034 | 0.34168 | 0.40944 | 0.54232 | 0.61823 | 0.67595 | 0.76766 | 0.89226 | 1.0539 | 1.1432 | 1.1139 | 1.143 | 1.143 | 1.143 | 1.143 | 1.143 | 1.143 | 1.143 | 1.143 | 1.143 | 1.143 | 1.143 | 1.143 | 1.143 | 1.143 | 1.143
Option 2 - Replace 3 x 10/13.5 MVA Tx with 3 x 20/33 MVA Tx
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99%
98%
97%
95%
90%
85%
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2 Winter POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 2 Winter POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | [31 empty] | 0 | 0 | 0
98% | [32 empty] | 0 | 0
97% | [32 empty] | 0.96437 | 1.0031
95% | [32 empty] | 0 | 0
90% | [32 empty] | 0.070196 | 0.083964
85%
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 1.0242 | 1.0762 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2 Summer POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 2 Summer POE10 W E @ R (MWh) | 0 | 0.30727 | 0.32285 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 - Replace 1 x 10/13.5 MVA Tx with 1 x 20/33 MVA Tx
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99%
98%
97%
95%
90%
85%
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 Winter POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 3 Winter POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | [31 empty] | 0 | 0 | 0
98% | [32 empty] | 0 | 0
97% | [32 empty] | 0.96437 | 1.0031
95% | [32 empty] | 0 | 0
90% | [32 empty] | 0.070196 | 0.083964
85%
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 1.0242 | 1.0762 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 Summer POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 3 Summer POE10 W E @ R (MWh) | 0 | 0.30727 | 0.32285 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 - Construct 2x 20/33MVA zone substation in Inverloch
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99%
98%
97%
95%
90%
85%
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 Winter POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 4 Winter POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | [31 empty] | 0 | 0 | 0
98% | [32 empty] | 0 | 0
97% | [32 empty] | 0.96437 | 1.0031
95% | [32 empty] | 0 | 0
90% | [32 empty] | 0.070196 | 0.083964
85%
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 1.0242 | 1.0762 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 Summer POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 4 Summer POE10 W E @ R (MWh) | 0 | 0.30727 | 0.32285 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 - Contract network support services to defer network investment
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | FY38: 0.44918; FY39: 0.56907; FY40: 0.56907; FY41: 0.56907; FY42: 0.56907; FY43: 0.56907; FY44: 0.56907; FY45: 0.56907; FY46: 0.56907; FY47: 0.56907; FY48: 0.56907; FY49: 0.56907; FY50: 0.56907; FY51: 0.56907; FY52: 0.56907; FY53: 0.56907; FY54: 0.56907 | [11 empty] | 0.55644 | 0.040691 | 0.47936 | 0.80406 | 0.67002 | 0.67002 | 0.67002 | 0.67002 | 0.67002 | 0.67002 | 0.67002 | 0.67002 | 0.67002 | 0.67002 | 0.67002 | 0.67002 | 0.67002 | 0.67002 | 0.67002 | 0.67002
98% | FY38: 0; FY39: 0; FY40: 0; FY41: 0; FY42: 0; FY43: 0; FY44: 0; FY45: 0; FY46: 0; FY47: 0; FY48: 0; FY49: 0; FY50: 0; FY51: 0; FY52: 0; FY53: 0; FY54: 0 | [11 empty] | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
97% | FY38: 0; FY39: 0; FY40: 0; FY41: 0; FY42: 0; FY43: 0; FY44: 0; FY45: 0; FY46: 0; FY47: 0; FY48: 0; FY49: 0; FY50: 0; FY51: 0; FY52: 0; FY53: 0; FY54: 0 | [11 empty] | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
95% | FY38: 0.0010862; FY39: 0.097304; FY40: 0.097304; FY41: 0.097304; FY42: 0.097304; FY43: 0.097304; FY44: 0.097304; FY45: 0.097304; FY46: 0.097304; FY47: 0.097304; FY48: 0.097304; FY49: 0.097304; FY50: 0.097304; FY51: 0.097304; FY52: 0.097304; FY53: 0.097304; FY54: 0.097304 | [11 empty] | 0.079879 |  | 0.010684 | 0.72791 | 0.29741 | 0.29741 | 0.29741 | 0.29741 | 0.29741 | 0.29741 | 0.29741 | 0.29741 | 0.29741 | 0.29741 | 0.29741 | 0.29741 | 0.29741 | 0.29741 | 0.29741 | 0.29741
90% | [44 empty] | 0.00024263
85%
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.44577 | 0.65971 | 0.65971 | 0.65971 | 0.65971 | 0.65971 | 0.65971 | 0.65971 | 0.65971 | 0.65971 | 0.65971 | 0.65971 | 0.65971 | 0.65971 | 0.65971 | 0.65971 | 0.65971 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.62996 | 0.040284 | 0.48514 | 1.5169 | 0.95775 | 0.95775 | 0.95775 | 0.95775 | 0.95775 | 0.95775 | 0.95775 | 0.95775 | 0.95775 | 0.95775 | 0.95775 | 0.95775 | 0.95775 | 0.95775 | 0.95775 | 0.95775
Option 5 Winter POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.31204 | 0.4618 | 0.4618 | 0.4618 | 0.4618 | 0.4618 | 0.4618 | 0.4618 | 0.4618 | 0.4618 | 0.4618 | 0.4618 | 0.4618 | 0.4618 | 0.4618 | 0.4618 | 0.4618 | Option 5 Winter POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.18899 | 0.012085 | 0.14554 | 0.45507 | 0.28733 | 0.28733 | 0.28733 | 0.28733 | 0.28733 | 0.28733 | 0.28733 | 0.28733 | 0.28733 | 0.28733 | 0.28733 | 0.28733 | 0.28733 | 0.28733 | 0.28733 | 0.28733
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | [37 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
98% | [38 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
97% | [39 empty] | 0.01028 | 0.060991 | 0.19882 | 0.38346 | 0.60673 | 0.72373 | 0.6858 | 0.72636 | 0.72636 | 0.72636 | 0.72636 | 0.72636 | 0.72636 | 0.72636 | 0.72636 | 0.72636 | 0.72636 | 0.72636 | 0.72636 | 0.72636 | 0.72636 | 0.72636
95% | [41 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
90% | [43 empty] | 0.0011274 | 0.012031 | 0.007235 | 0.012408 | 0.012408 | 0.012408 | 0.012408 | 0.012408 | 0.012408 | 0.012408 | 0.012408 | 0.012408 | 0.012408 | 0.012408 | 0.012408 | 0.012408 | 0.012408 | 0.012408
85%
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.010177 | 0.060381 | 0.19683 | 0.37962 | 0.60177 | 0.72841 | 0.68611 | 0.73138 | 0.73138 | 0.73138 | 0.73138 | 0.73138 | 0.73138 | 0.73138 | 0.73138 | 0.73138 | 0.73138 | 0.73138 | 0.73138 | 0.73138 | 0.73138 | 0.73138
Option 5 Summer POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 5 Summer POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0030532 | 0.018114 | 0.059049 | 0.11389 | 0.18053 | 0.21852 | 0.20583 | 0.21941 | 0.21941 | 0.21941 | 0.21941 | 0.21941 | 0.21941 | 0.21941 | 0.21941 | 0.21941 | 0.21941 | 0.21941 | 0.21941 | 0.21941 | 0.21941 | 0.21941
Option 6 -
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | [8 empty] | 0.0019784 |  | 0.74182 | 0.95486 | 1.108 | 1.8298 | 1.9473 | 1.9473 | 1.9473 | 1.9473 | 1.9473 | 1.9473 | 1.9473 | 1.9473 | 1.9473 | 1.9473 | 1.9473 | 1.9473 | 1.9473 | 1.9473 | 1.9473 | 1.9473 | [8 empty] | 0.65919 | 1.1257 | 0.68411 | 1.904 | 1.3918 | 1.8526 | 2.1847 | 2.0483 | 2.0483 | 2.0483 | 2.0483 | 2.0483 | 2.0483 | 2.0483 | 2.0483 | 2.0483 | 2.0483 | 2.0483 | 2.0483 | 2.0483 | 2.0483 | 2.0483 | 2.0483
98% | [10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
97% | [10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
95% | [10 empty] | 0.5049 | 1.3099 | 1.9009 | 4.6867 | 5.1402 | 5.1402 | 5.1402 | 5.1402 | 5.1402 | 5.1402 | 5.1402 | 5.1402 | 5.1402 | 5.1402 | 5.1402 | 5.1402 | 5.1402 | 5.1402 | 5.1402 | 5.1402 | [8 empty] | 0.27079 | 1.9692 | 0.33389 | 4.9727 | 2.9962 | 4.7747 | 6.0563 | 5.5297 | 5.5297 | 5.5297 | 5.5297 | 5.5297 | 5.5297 | 5.5297 | 5.5297 | 5.5297 | 5.5297 | 5.5297 | 5.5297 | 5.5297 | 5.5297 | 5.5297 | 5.5297
90% | [11 empty] | 0.29412 | 1.1508 | 12.3243 | 14.9458 | 14.9458 | 14.9458 | 14.9458 | 14.9458 | 14.9458 | 14.9458 | 14.9458 | 14.9458 | 14.9458 | 14.9458 | 14.9458 | 14.9458 | 14.9458 | 14.9458 | 14.9458 | [9 empty] | 1.2855 |  | 13.9779 | 4.1777 | 12.8328 | 20.2422 | 17.1981 | 17.1981 | 17.1981 | 17.1981 | 17.1981 | 17.1981 | 17.1981 | 17.1981 | 17.1981 | 17.1981 | 17.1981 | 17.1981 | 17.1981 | 17.1981 | 17.1981 | 17.1981
85% | FY38: 0.10615; FY39: 1.2549; FY40: 1.2549; FY41: 1.2549; FY42: 1.2549; FY43: 1.2549; FY44: 1.2549; FY45: 1.2549; FY46: 1.2549; FY47: 1.2549; FY48: 1.2549; FY49: 1.2549; FY50: 1.2549; FY51: 1.2549; FY52: 1.2549; FY53: 1.2549; FY54: 1.2549 | [11 empty] | 0.68472 |  | 0.23068 | 7.3453 | 3.2356 | 3.2356 | 3.2356 | 3.2356 | 3.2356 | 3.2356 | 3.2356 | 3.2356 | 3.2356 | 3.2356 | 3.2356 | 3.2356 | 3.2356 | 3.2356 | 3.2356 | 3.2356
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0019586 | 0 | 1.2342 | 2.5333 | 4.1181 | 18.7576 | 23.0554 | 23.0554 | 23.0554 | 23.0554 | 23.0554 | 23.0554 | 23.0554 | 23.0554 | 23.0554 | 23.0554 | 23.0554 | 23.0554 | 23.0554 | 23.0554 | 23.0554 | 23.0554 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.92068 | 4.3366 | 1.0078 | 21.3239 | 8.4801 | 19.4939 | 35.4703 | 27.7316 | 27.7316 | 27.7316 | 27.7316 | 27.7316 | 27.7316 | 27.7316 | 27.7316 | 27.7316 | 27.7316 | 27.7316 | 27.7316 | 27.7316 | 27.7316 | 27.7316 | 27.7316
Option 6 Winter POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.001371 | 0 | 0.86397 | 1.7733 | 2.8826 | 13.1303 | 16.1388 | 16.1388 | 16.1388 | 16.1388 | 16.1388 | 16.1388 | 16.1388 | 16.1388 | 16.1388 | 16.1388 | 16.1388 | 16.1388 | 16.1388 | 16.1388 | 16.1388 | 16.1388 | Option 6 Winter POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.27621 | 1.301 | 0.30235 | 6.3972 | 2.544 | 5.8482 | 10.6411 | 8.3195 | 8.3195 | 8.3195 | 8.3195 | 8.3195 | 8.3195 | 8.3195 | 8.3195 | 8.3195 | 8.3195 | 8.3195 | 8.3195 | 8.3195 | 8.3195 | 8.3195 | 8.3195
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | [31 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
98% | [32 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
97% | [32 empty] | 0.96437 | 1.0031 | 0.96135 | 0.97208 | 1.0487 | 1.204 | 1.4774 | 1.6199 | 1.723 | 1.879 | 2.0782 | 2.319 | 2.4452 | 2.4043 | 2.4449 | 2.4449 | 2.4449 | 2.4449 | 2.4449 | 2.4449 | 2.4449 | 2.4449 | 2.4449 | 2.4449 | 2.4449 | 2.4449 | 2.4449 | 2.4449 | 2.4449
95% | [32 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
90% | [32 empty] | 0.070196 | 0.083964 | 0.069171 | 0.072841 | 0.10173 | 0.17461 | 0.34858 | 0.46171 | 0.55294 | 0.70049 | 0.88945 | 1.1179 | 1.2377 | 1.1989 | 1.2373 | 1.2373 | 1.2373 | 1.2373 | 1.2373 | 1.2373 | 1.2373 | 1.2373 | 1.2373 | 1.2373 | 1.2373 | 1.2373 | 1.2373 | 1.2373 | 1.2373
85% | [41 empty] | 0.0052505 | 0.036629 | 0.11145 | 0.1664 | 0.14742 | 0.16623 | 0.16623 | 0.16623 | 0.16623 | 0.16623 | 0.16623 | 0.16623 | 0.16623 | 0.16623 | 0.16623 | 0.16623 | 0.16623 | 0.16623 | 0.16623 | 0.16623
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 1.0242 | 1.0762 | 1.0202 | 1.0345 | 1.1389 | 1.3648 | 1.8077 | 2.0608 | 2.2532 | 2.5589 | 2.9742 | 3.5129 | 3.8108 | 3.7131 | 3.81 | 3.81 | 3.81 | 3.81 | 3.81 | 3.81 | 3.81 | 3.81 | 3.81 | 3.81 | 3.81 | 3.81 | 3.81 | 3.81 | 3.81
Option 6 Summer POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 6 Summer POE10 W E @ R (MWh) | 0 | 0.30727 | 0.32285 | 0.30606 | 0.31034 | 0.34168 | 0.40944 | 0.54232 | 0.61823 | 0.67595 | 0.76766 | 0.89226 | 1.0539 | 1.1432 | 1.1139 | 1.143 | 1.143 | 1.143 | 1.143 | 1.143 | 1.143 | 1.143 | 1.143 | 1.143 | 1.143 | 1.143 | 1.143 | 1.143 | 1.143 | 1.143
Option 7 -
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | [8 empty] | 0.0019784 |  | 0.74182 | 0.95486 | 1.108 | 1.8298 | 1.9473 | 1.9473 | 1.9473 | 1.9473 | 1.9473 | 1.9473 | 1.9473 | 1.9473 | 1.9473 | 1.9473 | 1.9473 | 1.9473 | 1.9473 | 1.9473 | 1.9473 | 1.9473 | [8 empty] | 0.65919 | 1.1257 | 0.68411 | 1.904 | 1.3918 | 1.8526 | 2.1847 | 2.0483 | 2.0483 | 2.0483 | 2.0483 | 2.0483 | 2.0483 | 2.0483 | 2.0483 | 2.0483 | 2.0483 | 2.0483 | 2.0483 | 2.0483 | 2.0483 | 2.0483 | 2.0483
98% | [10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
97% | [10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
95% | [10 empty] | 0.5049 | 1.3099 | 1.9009 | 4.6867 | 5.1402 | 5.1402 | 5.1402 | 5.1402 | 5.1402 | 5.1402 | 5.1402 | 5.1402 | 5.1402 | 5.1402 | 5.1402 | 5.1402 | 5.1402 | 5.1402 | 5.1402 | 5.1402 | [8 empty] | 0.27079 | 1.9692 | 0.33389 | 4.9727 | 2.9962 | 4.7747 | 6.0563 | 5.5297 | 5.5297 | 5.5297 | 5.5297 | 5.5297 | 5.5297 | 5.5297 | 5.5297 | 5.5297 | 5.5297 | 5.5297 | 5.5297 | 5.5297 | 5.5297 | 5.5297 | 5.5297
90% | [11 empty] | 0.29412 | 1.1508 | 12.3243 | 14.9458 | 14.9458 | 14.9458 | 14.9458 | 14.9458 | 14.9458 | 14.9458 | 14.9458 | 14.9458 | 14.9458 | 14.9458 | 14.9458 | 14.9458 | 14.9458 | 14.9458 | 14.9458 | [9 empty] | 1.2855 |  | 13.9779 | 4.1777 | 12.8328 | 20.2422 | 17.1981 | 17.1981 | 17.1981 | 17.1981 | 17.1981 | 17.1981 | 17.1981 | 17.1981 | 17.1981 | 17.1981 | 17.1981 | 17.1981 | 17.1981 | 17.1981 | 17.1981 | 17.1981
85% | FY38: 0.10615; FY39: 1.2549; FY40: 1.2549; FY41: 1.2549; FY42: 1.2549; FY43: 1.2549; FY44: 1.2549; FY45: 1.2549; FY46: 1.2549; FY47: 1.2549; FY48: 1.2549; FY49: 1.2549; FY50: 1.2549; FY51: 1.2549; FY52: 1.2549; FY53: 1.2549; FY54: 1.2549 | [11 empty] | 0.68472 |  | 0.23068 | 7.3453 | 3.2356 | 3.2356 | 3.2356 | 3.2356 | 3.2356 | 3.2356 | 3.2356 | 3.2356 | 3.2356 | 3.2356 | 3.2356 | 3.2356 | 3.2356 | 3.2356 | 3.2356 | 3.2356
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0019586 | 0 | 1.2342 | 2.5333 | 4.1181 | 18.7576 | 23.0554 | 23.0554 | 23.0554 | 23.0554 | 23.0554 | 23.0554 | 23.0554 | 23.0554 | 23.0554 | 23.0554 | 23.0554 | 23.0554 | 23.0554 | 23.0554 | 23.0554 | 23.0554 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.92068 | 4.3366 | 1.0078 | 21.3239 | 8.4801 | 19.4939 | 35.4703 | 27.7316 | 27.7316 | 27.7316 | 27.7316 | 27.7316 | 27.7316 | 27.7316 | 27.7316 | 27.7316 | 27.7316 | 27.7316 | 27.7316 | 27.7316 | 27.7316 | 27.7316 | 27.7316
Option 7 Winter POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.001371 | 0 | 0.86397 | 1.7733 | 2.8826 | 13.1303 | 16.1388 | 16.1388 | 16.1388 | 16.1388 | 16.1388 | 16.1388 | 16.1388 | 16.1388 | 16.1388 | 16.1388 | 16.1388 | 16.1388 | 16.1388 | 16.1388 | 16.1388 | 16.1388 | Option 7 Winter POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.27621 | 1.301 | 0.30235 | 6.3972 | 2.544 | 5.8482 | 10.6411 | 8.3195 | 8.3195 | 8.3195 | 8.3195 | 8.3195 | 8.3195 | 8.3195 | 8.3195 | 8.3195 | 8.3195 | 8.3195 | 8.3195 | 8.3195 | 8.3195 | 8.3195 | 8.3195
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | [31 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
98% | [32 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
97% | [32 empty] | 0.96437 | 1.0031 | 0.96135 | 0.97208 | 1.0487 | 1.204 | 1.4774 | 1.6199 | 1.723 | 1.879 | 2.0782 | 2.319 | 2.4452 | 2.4043 | 2.4449 | 2.4449 | 2.4449 | 2.4449 | 2.4449 | 2.4449 | 2.4449 | 2.4449 | 2.4449 | 2.4449 | 2.4449 | 2.4449 | 2.4449 | 2.4449 | 2.4449
95% | [32 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
90% | [32 empty] | 0.070196 | 0.083964 | 0.069171 | 0.072841 | 0.10173 | 0.17461 | 0.34858 | 0.46171 | 0.55294 | 0.70049 | 0.88945 | 1.1179 | 1.2377 | 1.1989 | 1.2373 | 1.2373 | 1.2373 | 1.2373 | 1.2373 | 1.2373 | 1.2373 | 1.2373 | 1.2373 | 1.2373 | 1.2373 | 1.2373 | 1.2373 | 1.2373 | 1.2373
85% | [41 empty] | 0.0052505 | 0.036629 | 0.11145 | 0.1664 | 0.14742 | 0.16623 | 0.16623 | 0.16623 | 0.16623 | 0.16623 | 0.16623 | 0.16623 | 0.16623 | 0.16623 | 0.16623 | 0.16623 | 0.16623 | 0.16623 | 0.16623 | 0.16623
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 1.0242 | 1.0762 | 1.0202 | 1.0345 | 1.1389 | 1.3648 | 1.8077 | 2.0608 | 2.2532 | 2.5589 | 2.9742 | 3.5129 | 3.8108 | 3.7131 | 3.81 | 3.81 | 3.81 | 3.81 | 3.81 | 3.81 | 3.81 | 3.81 | 3.81 | 3.81 | 3.81 | 3.81 | 3.81 | 3.81 | 3.81
Option 7 Summer POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 7 Summer POE10 W E @ R (MWh) | 0 | 0.30727 | 0.32285 | 0.30606 | 0.31034 | 0.34168 | 0.40944 | 0.54232 | 0.61823 | 0.67595 | 0.76766 | 0.89226 | 1.0539 | 1.1432 | 1.1139 | 1.143 | 1.143 | 1.143 | 1.143 | 1.143 | 1.143 | 1.143 | 1.143 | 1.143 | 1.143 | 1.143 | 1.143 | 1.143 | 1.143 | 1.143
Option 8 -
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | [8 empty] | 0.0019784 |  | 0.74182 | 0.95486 | 1.108 | 1.8298 | 1.9473 | 1.9473 | 1.9473 | 1.9473 | 1.9473 | 1.9473 | 1.9473 | 1.9473 | 1.9473 | 1.9473 | 1.9473 | 1.9473 | 1.9473 | 1.9473 | 1.9473 | 1.9473 | [8 empty] | 0.65919 | 1.1257 | 0.68411 | 1.904 | 1.3918 | 1.8526 | 2.1847 | 2.0483 | 2.0483 | 2.0483 | 2.0483 | 2.0483 | 2.0483 | 2.0483 | 2.0483 | 2.0483 | 2.0483 | 2.0483 | 2.0483 | 2.0483 | 2.0483 | 2.0483 | 2.0483
98% | [10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
97% | [10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
95% | [10 empty] | 0.5049 | 1.3099 | 1.9009 | 4.6867 | 5.1402 | 5.1402 | 5.1402 | 5.1402 | 5.1402 | 5.1402 | 5.1402 | 5.1402 | 5.1402 | 5.1402 | 5.1402 | 5.1402 | 5.1402 | 5.1402 | 5.1402 | 5.1402 | [8 empty] | 0.27079 | 1.9692 | 0.33389 | 4.9727 | 2.9962 | 4.7747 | 6.0563 | 5.5297 | 5.5297 | 5.5297 | 5.5297 | 5.5297 | 5.5297 | 5.5297 | 5.5297 | 5.5297 | 5.5297 | 5.5297 | 5.5297 | 5.5297 | 5.5297 | 5.5297 | 5.5297
90% | [11 empty] | 0.29412 | 1.1508 | 12.3243 | 14.9458 | 14.9458 | 14.9458 | 14.9458 | 14.9458 | 14.9458 | 14.9458 | 14.9458 | 14.9458 | 14.9458 | 14.9458 | 14.9458 | 14.9458 | 14.9458 | 14.9458 | 14.9458 | [9 empty] | 1.2855 |  | 13.9779 | 4.1777 | 12.8328 | 20.2422 | 17.1981 | 17.1981 | 17.1981 | 17.1981 | 17.1981 | 17.1981 | 17.1981 | 17.1981 | 17.1981 | 17.1981 | 17.1981 | 17.1981 | 17.1981 | 17.1981 | 17.1981 | 17.1981
85% | FY38: 0.10615; FY39: 1.2549; FY40: 1.2549; FY41: 1.2549; FY42: 1.2549; FY43: 1.2549; FY44: 1.2549; FY45: 1.2549; FY46: 1.2549; FY47: 1.2549; FY48: 1.2549; FY49: 1.2549; FY50: 1.2549; FY51: 1.2549; FY52: 1.2549; FY53: 1.2549; FY54: 1.2549 | [11 empty] | 0.68472 |  | 0.23068 | 7.3453 | 3.2356 | 3.2356 | 3.2356 | 3.2356 | 3.2356 | 3.2356 | 3.2356 | 3.2356 | 3.2356 | 3.2356 | 3.2356 | 3.2356 | 3.2356 | 3.2356 | 3.2356 | 3.2356
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0019586 | 0 | 1.2342 | 2.5333 | 4.1181 | 18.7576 | 23.0554 | 23.0554 | 23.0554 | 23.0554 | 23.0554 | 23.0554 | 23.0554 | 23.0554 | 23.0554 | 23.0554 | 23.0554 | 23.0554 | 23.0554 | 23.0554 | 23.0554 | 23.0554 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.92068 | 4.3366 | 1.0078 | 21.3239 | 8.4801 | 19.4939 | 35.4703 | 27.7316 | 27.7316 | 27.7316 | 27.7316 | 27.7316 | 27.7316 | 27.7316 | 27.7316 | 27.7316 | 27.7316 | 27.7316 | 27.7316 | 27.7316 | 27.7316 | 27.7316 | 27.7316
Option 8 Winter POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.001371 | 0 | 0.86397 | 1.7733 | 2.8826 | 13.1303 | 16.1388 | 16.1388 | 16.1388 | 16.1388 | 16.1388 | 16.1388 | 16.1388 | 16.1388 | 16.1388 | 16.1388 | 16.1388 | 16.1388 | 16.1388 | 16.1388 | 16.1388 | 16.1388 | Option 8 Winter POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.27621 | 1.301 | 0.30235 | 6.3972 | 2.544 | 5.8482 | 10.6411 | 8.3195 | 8.3195 | 8.3195 | 8.3195 | 8.3195 | 8.3195 | 8.3195 | 8.3195 | 8.3195 | 8.3195 | 8.3195 | 8.3195 | 8.3195 | 8.3195 | 8.3195 | 8.3195
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | [31 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
98% | [32 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
97% | [32 empty] | 0.96437 | 1.0031 | 0.96135 | 0.97208 | 1.0487 | 1.204 | 1.4774 | 1.6199 | 1.723 | 1.879 | 2.0782 | 2.319 | 2.4452 | 2.4043 | 2.4449 | 2.4449 | 2.4449 | 2.4449 | 2.4449 | 2.4449 | 2.4449 | 2.4449 | 2.4449 | 2.4449 | 2.4449 | 2.4449 | 2.4449 | 2.4449 | 2.4449
95% | [32 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
90% | [32 empty] | 0.070196 | 0.083964 | 0.069171 | 0.072841 | 0.10173 | 0.17461 | 0.34858 | 0.46171 | 0.55294 | 0.70049 | 0.88945 | 1.1179 | 1.2377 | 1.1989 | 1.2373 | 1.2373 | 1.2373 | 1.2373 | 1.2373 | 1.2373 | 1.2373 | 1.2373 | 1.2373 | 1.2373 | 1.2373 | 1.2373 | 1.2373 | 1.2373 | 1.2373
85% | [41 empty] | 0.0052505 | 0.036629 | 0.11145 | 0.1664 | 0.14742 | 0.16623 | 0.16623 | 0.16623 | 0.16623 | 0.16623 | 0.16623 | 0.16623 | 0.16623 | 0.16623 | 0.16623 | 0.16623 | 0.16623 | 0.16623 | 0.16623 | 0.16623
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 1.0242 | 1.0762 | 1.0202 | 1.0345 | 1.1389 | 1.3648 | 1.8077 | 2.0608 | 2.2532 | 2.5589 | 2.9742 | 3.5129 | 3.8108 | 3.7131 | 3.81 | 3.81 | 3.81 | 3.81 | 3.81 | 3.81 | 3.81 | 3.81 | 3.81 | 3.81 | 3.81 | 3.81 | 3.81 | 3.81 | 3.81
Option 8 Summer POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 8 Summer POE10 W E @ R (MWh) | 0 | 0.30727 | 0.32285 | 0.30606 | 0.31034 | 0.34168 | 0.40944 | 0.54232 | 0.61823 | 0.67595 | 0.76766 | 0.89226 | 1.0539 | 1.1432 | 1.1139 | 1.143 | 1.143 | 1.143 | 1.143 | 1.143 | 1.143 | 1.143 | 1.143 | 1.143 | 1.143 | 1.143 | 1.143 | 1.143 | 1.143 | 1.143

## E@R N-1
Option 1 - Do Nothing
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | 2.094 | 3.4361 | 3.5785 | 3.7544 | 3.988 | 4.2094 | 4.5964 | 5.5698 | 6.0933 | 5.7114 | 6.8938 | 7.1069 | 7.26 | 7.9819 | 8.0994 | 8.0994 | 8.0994 | 8.0994 | 8.0994 | 8.0994 | 8.0994 | 8.0994 | 8.0994 | 8.0994 | 8.0994 | 8.0994 | 8.0994 | 8.0994 | 8.0994 | 8.0994 |  | 3.3275 | 4.6077 | 4.7402 | 5.1978 | 5.1866 | 5.2872 | 5.6807 | 6.8112 | 7.2777 | 6.8361 | 8.056 | 7.5438 | 8.0046 | 8.3367 | 8.2003 | 8.2003 | 8.2003 | 8.2003 | 8.2003 | 8.2003 | 8.2003 | 8.2003 | 8.2003 | 8.2003 | 8.2003 | 8.2003 | 8.2003 | 8.2003 | 8.2003 | 8.2003
98% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
97% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
95% | 6.572 | 11.7515 | 12.3007 | 12.9797 | 13.8812 | 14.7359 | 16.2295 | 19.9859 | 22.0064 | 20.5324 | 25.0957 | 25.9179 | 26.5089 | 29.2948 | 29.7482 | 29.7482 | 29.7482 | 29.7482 | 29.7482 | 29.7482 | 29.7482 | 29.7482 | 29.7482 | 29.7482 | 29.7482 | 29.7482 | 29.7482 | 29.7482 | 29.7482 | 29.7482 |  | 11.3322 | 16.2727 | 16.7844 | 18.5501 | 18.5071 | 18.8953 | 20.4139 | 24.7769 | 26.5773 | 24.873 | 29.5808 | 27.6042 | 29.3827 | 30.6643 | 30.1378 | 30.1378 | 30.1378 | 30.1378 | 30.1378 | 30.1378 | 30.1378 | 30.1378 | 30.1378 | 30.1378 | 30.1378 | 30.1378 | 30.1378 | 30.1378 | 30.1378 | 30.1378
90% | 28.6064 | 58.5505 | 61.7257 | 65.6512 | 70.8631 | 75.804 | 84.4388 | 106.1559 | 117.8368 | 109.3152 | 135.697 | 140.4502 | 143.8669 | 159.9726 | 162.5941 | 162.5941 | 162.5941 | 162.5941 | 162.5941 | 162.5941 | 162.5941 | 162.5941 | 162.5941 | 162.5941 | 162.5941 | 162.5941 | 162.5941 | 162.5941 | 162.5941 | 162.5941 |  | 56.1267 | 84.6891 | 87.6469 | 97.855 | 97.6062 | 99.8509 | 108.6302 | 133.8534 | 144.262 | 134.4095 | 161.6261 | 150.1991 | 160.4811 | 167.8904 | 164.8463 | 164.8463 | 164.8463 | 164.8463 | 164.8463 | 164.8463 | 164.8463 | 164.8463 | 164.8463 | 164.8463 | 164.8463 | 164.8463 | 164.8463 | 164.8463 | 164.8463 | 164.8463
85% | 58.0421 | 183.1465 | 196.4122 | 212.8125 | 234.5872 | 255.2303 | 291.3058 | 382.038 | 430.8403 | 395.2376 | 505.4587 | 525.3172 | 539.5922 | 606.8804 | 617.8328 | 617.8328 | 617.8328 | 617.8328 | 617.8328 | 617.8328 | 617.8328 | 617.8328 | 617.8328 | 617.8328 | 617.8328 | 617.8328 | 617.8328 | 617.8328 | 617.8328 | 617.8328 |  | 173.0196 | 292.3513 | 304.7091 | 347.3577 | 346.3183 | 355.6965 | 392.3758 | 497.7564 | 541.2429 | 500.0796 | 613.7889 | 566.0476 | 609.0048 | 639.9607 | 627.2425 | 627.2425 | 627.2425 | 627.2425 | 627.2425 | 627.2425 | 627.2425 | 627.2425 | 627.2425 | 627.2425 | 627.2425 | 627.2425 | 627.2425 | 627.2425 | 627.2425 | 627.2425
80% | 7.0161 | 180.8458 | 201.8492 | 227.8157 | 262.2914 | 294.9752 | 352.0931 | 495.7485 | 573.0166 | 516.6472 | 691.159 | 722.6008 | 745.2022 | 851.7388 | 869.0797 | 869.0797 | 869.0797 | 869.0797 | 869.0797 | 869.0797 | 869.0797 | 869.0797 | 869.0797 | 869.0797 | 869.0797 | 869.0797 | 869.0797 | 869.0797 | 869.0797 | 869.0797 |  | 164.8121 | 353.7485 | 373.3145 | 440.8395 | 439.1939 | 454.0422 | 512.1161 | 678.9641 | 747.8157 | 682.6423 | 862.6769 | 787.0886 | 855.1023 | 904.1144 | 883.9779 | 883.9779 | 883.9779 | 883.9779 | 883.9779 | 883.9779 | 883.9779 | 883.9779 | 883.9779 | 883.9779 | 883.9779 | 883.9779 | 883.9779 | 883.9779 | 883.9779 | 883.9779
75% |  | 107.1201 | 145.2583 | 193.2216 | 256.9023 | 317.2734 | 422.7773 | 688.1264 | 830.8501 | 726.7289 | 1049.0735 | 1107.1504 | 1148.898 | 1345.6842 | 1377.715 | 1377.715 | 1377.715 | 1377.715 | 1377.715 | 1377.715 | 1377.715 | 1377.715 | 1377.715 | 1377.715 | 1377.715 | 1377.715 | 1377.715 | 1377.715 | 1377.715 | 1377.715 |  | 81.2692 | 425.8349 | 461.9758 | 586.7028 | 583.663 | 611.0897 | 718.3593 | 1026.5481 | 1153.7254 | 1033.3422 | 1365.8883 | 1226.2674 | 1351.8971 | 1442.4284 | 1405.2338 | 1405.2338 | 1405.2338 | 1405.2338 | 1405.2338 | 1405.2338 | 1405.2338 | 1405.2338 | 1405.2338 | 1405.2338 | 1405.2338 | 1405.2338 | 1405.2338 | 1405.2338 | 1405.2338 | 1405.2338
70% |  |  | 1.3066 | 14.8126 | 54.6251 | 114.4437 | 266.6317 | 698.5515 | 930.8688 | 761.3864 | 1286.0803 | 1380.6144 | 1448.5689 | 1768.886 | 1821.0238 | 1821.0238 | 1821.0238 | 1821.0238 | 1821.0238 | 1821.0238 | 1821.0238 | 1821.0238 | 1821.0238 | 1821.0238 | 1821.0238 | 1821.0238 | 1821.0238 | 1821.0238 | 1821.0238 | 1821.0238 |  |  | 271.6087 | 330.4367 | 533.4601 | 528.5121 | 573.1557 | 747.7629 | 1249.4148 | 1456.4266 | 1260.4738 | 1801.773 | 1574.5062 | 1778.9989 | 1926.3605 | 1865.8173 | 1865.8173 | 1865.8173 | 1865.8173 | 1865.8173 | 1865.8173 | 1865.8173 | 1865.8173 | 1865.8173 | 1865.8173 | 1865.8173 | 1865.8173 | 1865.8173 | 1865.8173 | 1865.8173 | 1865.8173
65% | [6 empty] | 1.4477 | 265.9903 | 547.2297 | 339.6879 | 982.2084 | 1097.9714 | 1181.1858 | 1573.4342 | 1637.2802 | 1637.2802 | 1637.2802 | 1637.2802 | 1637.2802 | 1637.2802 | 1637.2802 | 1637.2802 | 1637.2802 | 1637.2802 | 1637.2802 | 1637.2802 | 1637.2802 | 1637.2802 | 1637.2802 | 1637.2802 |  |  | 1.9117 | 12.2059 | 113.2844 | 109.6564 | 144.4238 | 323.0448 | 937.3092 | 1190.8081 | 950.8517 | 1613.7064 | 1335.404 | 1585.8181 | 1766.2716 | 1692.1327 | 1692.1327 | 1692.1327 | 1692.1327 | 1692.1327 | 1692.1327 | 1692.1327 | 1692.1327 | 1692.1327 | 1692.1327 | 1692.1327 | 1692.1327 | 1692.1327 | 1692.1327 | 1692.1327 | 1692.1327
60% | [8 empty] | 43.0729 | 0.078688 | 371.8511 | 509.12 | 612.3349 | 1098.8592 | 1178.0505 | 1178.0505 | 1178.0505 | 1178.0505 | 1178.0505 | 1178.0505 | 1178.0505 | 1178.0505 | 1178.0505 | 1178.0505 | 1178.0505 | 1178.0505 | 1178.0505 | 1178.0505 | 1178.0505 | 1178.0505 | [8 empty] | 323.8953 | 624.2698 | 338.0342 | 1148.8107 | 803.6191 | 1114.2195 | 1338.0446 | 1246.0867 | 1246.0867 | 1246.0867 | 1246.0867 | 1246.0867 | 1246.0867 | 1246.0867 | 1246.0867 | 1246.0867 | 1246.0867 | 1246.0867 | 1246.0867 | 1246.0867 | 1246.0867 | 1246.0867 | 1246.0867
55% | [11 empty] | 0.48994 | 9.8575 | 206.4492 | 260.9948 | 260.9948 | 260.9948 | 260.9948 | 260.9948 | 260.9948 | 260.9948 | 260.9948 | 260.9948 | 260.9948 | 260.9948 | 260.9948 | 260.9948 | 260.9948 | 260.9948 | 260.9948 | [9 empty] | 11.6994 |  | 240.151 | 57.864 | 216.5553 | 389.3679 | 312.6478 | 312.6478 | 312.6478 | 312.6478 | 312.6478 | 312.6478 | 312.6478 | 312.6478 | 312.6478 | 312.6478 | 312.6478 | 312.6478 | 312.6478 | 312.6478 | 312.6478 | 312.6478
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 101.3074 | 539.402 | 616.207 | 723.7373 | 888.1669 | 1065.9052 | 1425.125 | 2635.5446 | 3466.7969 | 2846.5726 | 5002.9824 | 5461.5717 | 5804.6426 | 7572.6894 | 7882.7941 | 7882.7941 | 7882.7941 | 7882.7941 | 7882.7941 | 7882.7941 | 7882.7941 | 7882.7941 | 7882.7941 | 7882.7941 | 7882.7941 | 7882.7941 | 7882.7941 | 7882.7941 | 7882.7941 | 7882.7941 | E @ R (MWh) | 484.9884 | 1436.5143 | 1575.8954 | 2121.815 | 2107.3572 | 2239.8169 | 2800.0998 | 4830.5361 | 5845.0638 | 4882.227 | 7767.5974 | 6470.7827 | 7632.3697 | 8527.3051 | 8153.9599 | 8153.9599 | 8153.9599 | 8153.9599 | 8153.9599 | 8153.9599 | 8153.9599 | 8153.9599 | 8153.9599 | 8153.9599 | 8153.9599 | 8153.9599 | 8153.9599 | 8153.9599 | 8153.9599 | 8153.9599
Option 1 Winter POE50 W E @ R (MWh) N 1 | 70.9151 | 377.5814 | 431.3449 | 506.6161 | 621.7169 | 746.1337 | 997.5875 | 1844.8812 | 2426.7579 | 1992.6008 | 3502.0877 | 3823.1002 | 4063.2498 | 5300.8826 | 5517.9559 | 5517.9559 | 5517.9559 | 5517.9559 | 5517.9559 | 5517.9559 | 5517.9559 | 5517.9559 | 5517.9559 | 5517.9559 | 5517.9559 | 5517.9559 | 5517.9559 | 5517.9559 | 5517.9559 | 5517.9559 | Option 1 Winter POE10 W E @ R (MWh) N 1 | 145.4965 | 430.9543 | 472.7686 | 636.5445 | 632.2071 | 671.9451 | 840.03 | 1449.1608 | 1753.5191 | 1464.6681 | 2330.2792 | 1941.2348 | 2289.7109 | 2558.1915 | 2446.188 | 2446.188 | 2446.188 | 2446.188 | 2446.188 | 2446.188 | 2446.188 | 2446.188 | 2446.188 | 2446.188 | 2446.188 | 2446.188 | 2446.188 | 2446.188 | 2446.188 | 2446.188
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | 3.7913 | 5.0725 | 5.2012 | 5.1381 | 5.1981 | 5.2228 | 5.3018 | 5.4643 | 5.601 | 5.6639 | 5.6078 | 5.8429 | 5.8802 | 5.8361 | 5.9246 | 5.966 | 5.966 | 5.966 | 5.966 | 5.966 | 5.966 | 5.966 | 5.966 | 5.966 | 5.966 | 5.966 | 5.966 | 5.966 | 5.966 | 5.966 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
98% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
97% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 7.3137 | 8.7167 | 8.7555 | 8.7137 | 8.7244 | 8.8011 | 8.9563 | 9.2298 | 9.3723 | 9.4753 | 9.6313 | 9.8305 | 10.0714 | 10.1976 | 10.1567 | 10.1972 | 10.1972 | 10.1972 | 10.1972 | 10.1972 | 10.1972 | 10.1972 | 10.1972 | 10.1972 | 10.1972 | 10.1972 | 10.1972 | 10.1972 | 10.1972 | 10.1972
95% | 3.1884 | 4.4245 | 4.5487 | 4.4878 | 4.5457 | 4.5695 | 4.6457 | 4.8025 | 4.9344 | 4.9951 | 4.941 | 5.1678 | 5.2038 | 5.1612 | 5.2466 | 5.2865 | 5.2865 | 5.2865 | 5.2865 | 5.2865 | 5.2865 | 5.2865 | 5.2865 | 5.2865 | 5.2865 | 5.2865 | 5.2865 | 5.2865 | 5.2865 | 5.2865 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
90% | 56.8798 | 83.0826 | 85.7157 | 84.425 | 85.6522 | 86.1565 | 87.7726 | 91.0956 | 93.8911 | 95.1779 | 94.031 | 98.8398 | 99.6024 | 98.6998 | 100.5097 | 101.3563 | 101.3563 | 101.3563 | 101.3563 | 101.3563 | 101.3563 | 101.3563 | 101.3563 | 101.3563 | 101.3563 | 101.3563 | 101.3563 | 101.3563 | 101.3563 | 101.3563 |  | 6.2541 | 7.5852 | 7.6219 | 7.5823 | 7.5925 | 7.6652 | 7.8125 | 8.0719 | 8.2071 | 8.3048 | 8.4529 | 8.6418 | 8.8703 | 8.9901 | 8.9512 | 8.9897 | 8.9897 | 8.9897 | 8.9897 | 8.9897 | 8.9897 | 8.9897 | 8.9897 | 8.9897 | 8.9897 | 8.9897 | 8.9897 | 8.9897 | 8.9897 | 8.9897
85% | 143.1015 | 236.6138 | 246.0108 | 241.4046 | 245.7844 | 247.5839 | 253.3514 | 265.2106 | 275.1871 | 279.7796 | 275.6863 | 292.8479 | 295.5698 | 292.3486 | 298.8077 | 301.8288 | 301.8288 | 301.8288 | 301.8288 | 301.8288 | 301.8288 | 301.8288 | 301.8288 | 301.8288 | 301.8288 | 301.8288 | 301.8288 | 301.8288 | 301.8288 | 301.8288 |  | 5.1945 | 6.4536 | 6.4883 | 6.4509 | 6.4605 | 6.5292 | 6.6686 | 6.914 | 7.0419 | 7.1344 | 7.2744 | 7.4531 | 7.6693 | 7.7825 | 7.7458 | 7.7822 | 7.7822 | 7.7822 | 7.7822 | 7.7822 | 7.7822 | 7.7822 | 7.7822 | 7.7822 | 7.7822 | 7.7822 | 7.7822 | 7.7822 | 7.7822 | 7.7822
80% | 123.3778 | 275.2831 | 290.5479 | 283.0655 | 290.1801 | 293.1034 | 302.4723 | 321.7369 | 337.9431 | 345.4033 | 338.7541 | 366.632 | 371.0535 | 365.821 | 376.3134 | 381.2209 | 381.2209 | 381.2209 | 381.2209 | 381.2209 | 381.2209 | 381.2209 | 381.2209 | 381.2209 | 381.2209 | 381.2209 | 381.2209 | 381.2209 | 381.2209 | 381.2209 |  | 16.5393 | 21.2879 | 21.419 | 21.2777 | 21.314 | 21.5733 | 22.0988 | 23.0244 | 23.5066 | 23.8555 | 24.3835 | 25.0576 | 25.8728 | 26.3 | 26.1615 | 26.2988 | 26.2988 | 26.2988 | 26.2988 | 26.2988 | 26.2988 | 26.2988 | 26.2988 | 26.2988 | 26.2988 | 26.2988 | 26.2988 | 26.2988 | 26.2988 | 26.2988
75% | 29.3744 | 270.8222 | 297.9974 | 284.6768 | 297.3427 | 302.5468 | 319.2259 | 353.5216 | 382.3727 | 395.6538 | 383.8165 | 433.4462 | 441.3175 | 432.0023 | 450.6815 | 459.4181 | 459.4181 | 459.4181 | 459.4181 | 459.4181 | 459.4181 | 459.4181 | 459.4181 | 459.4181 | 459.4181 | 459.4181 | 459.4181 | 459.4181 | 459.4181 | 459.4181 |  | 6.1504 | 8.3808 | 8.4423 | 8.376 | 8.393 | 8.5148 | 8.7617 | 9.1964 | 9.4229 | 9.5868 | 9.8348 | 10.1514 | 10.5343 | 10.735 | 10.6699 | 10.7344 | 10.7344 | 10.7344 | 10.7344 | 10.7344 | 10.7344 | 10.7344 | 10.7344 | 10.7344 | 10.7344 | 10.7344 | 10.7344 | 10.7344 | 10.7344 | 10.7344
70% |  | 57.5195 | 79.6537 | 68.3739 | 79.0801 | 83.6941 | 99.3182 | 135.3947 | 169.7783 | 186.6822 | 171.5941 | 234.9517 | 245.0052 | 233.1075 | 256.9651 | 268.1238 | 268.1238 | 268.1238 | 268.1238 | 268.1238 | 268.1238 | 268.1238 | 268.1238 | 268.1238 | 268.1238 | 268.1238 | 268.1238 | 268.1238 | 268.1238 | 268.1238 |  | 12.0933 | 18.3528 | 18.5256 | 18.3393 | 18.3872 | 18.7291 | 19.4218 | 20.6418 | 21.2775 | 21.7374 | 22.4334 | 23.322 | 24.3966 | 24.9597 | 24.7771 | 24.9581 | 24.9581 | 24.9581 | 24.9581 | 24.9581 | 24.9581 | 24.9581 | 24.9581 | 24.9581 | 24.9581 | 24.9581 | 24.9581 | 24.9581 | 24.9581 | 24.9581
65% | [9 empty] | 0.18385 |  | 5.9063 | 8.0929 | 5.5421 | 11.1349 | 14.402 | 14.402 | 14.402 | 14.402 | 14.402 | 14.402 | 14.402 | 14.402 | 14.402 | 14.402 | 14.402 | 14.402 | 14.402 | 14.402 | 14.402 |  | 1.9118 | 3.8544 | 3.908 | 3.8503 | 3.8651 | 3.9712 | 4.1862 | 4.5648 | 4.7621 | 4.9048 | 5.1208 | 5.3966 | 5.7301 | 5.9048 | 5.8482 | 5.9043 | 5.9043 | 5.9043 | 5.9043 | 5.9043 | 5.9043 | 5.9043 | 5.9043 | 5.9043 | 5.9043 | 5.9043 | 5.9043 | 5.9043 | 5.9043 | 5.9043
60% | [31 empty] | 1.1137 | 10.3432 | 10.6659 | 10.318 | 10.4075 | 11.0459 | 12.3398 | 14.6185 | 15.8059 | 16.6649 | 17.965 | 19.6247 | 21.6318 | 22.6836 | 22.3426 | 22.6806 | 22.6806 | 22.6806 | 22.6806 | 22.6806 | 22.6806 | 22.6806 | 22.6806 | 22.6806 | 22.6806 | 22.6806 | 22.6806 | 22.6806 | 22.6806 | 22.6806
55% | [32 empty] | 1.4939 | 1.8164 | 1.47 | 1.5556 | 2.236 | 3.982 | 8.2254 | 11.0123 | 13.269 | 17.0614 | 22.5502 | 30.1319 | 34.5083 | 33.0596 | 34.4954 | 34.4954 | 34.4954 | 34.4954 | 34.4954 | 34.4954 | 34.4954 | 34.4954 | 34.4954 | 34.4954 | 34.4954 | 34.4954 | 34.4954 | 34.4954 | 34.4954
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 356.116 | 923.49 | 999.5787 | 961.856 | 997.7055 | 1012.6482 | 1061.367 | 1165.454 | 1257.0106 | 1300.4043 | 1261.6864 | 1429.1982 | 1457.0082 | 1424.1334 | 1490.5277 | 1522.2264 | 1522.2264 | 1522.2264 | 1522.2264 | 1522.2264 | 1522.2264 | 1522.2264 | 1522.2264 | 1522.2264 | 1522.2264 | 1522.2264 | 1522.2264 | 1522.2264 | 1522.2264 | 1522.2264 | E @ R (MWh) | 56.5706 | 85.6039 | 86.7664 | 85.5143 | 85.8329 | 88.1752 | 93.2854 | 103.442 | 109.3043 | 113.7835 | 120.9358 | 130.7077 | 143.4593 | 150.541 | 148.2156 | 150.5204 | 150.5204 | 150.5204 | 150.5204 | 150.5204 | 150.5204 | 150.5204 | 150.5204 | 150.5204 | 150.5204 | 150.5204 | 150.5204 | 150.5204 | 150.5204 | 150.5204
Option 1 Summer POE50 W E @ R (MWh) N 1 | 249.2812 | 646.443 | 699.7051 | 673.2992 | 698.3938 | 708.8538 | 742.9569 | 815.8178 | 879.9074 | 910.283 | 883.1805 | 1000.4387 | 1019.9057 | 996.8934 | 1043.3694 | 1065.5585 | 1065.5585 | 1065.5585 | 1065.5585 | 1065.5585 | 1065.5585 | 1065.5585 | 1065.5585 | 1065.5585 | 1065.5585 | 1065.5585 | 1065.5585 | 1065.5585 | 1065.5585 | 1065.5585 | Option 1 Summer POE10 W E @ R (MWh) N 1 | 16.9712 | 25.6812 | 26.0299 | 25.6543 | 25.7499 | 26.4526 | 27.9856 | 31.0326 | 32.7913 | 34.1351 | 36.2807 | 39.2123 | 43.0378 | 45.1623 | 44.4647 | 45.1561 | 45.1561 | 45.1561 | 45.1561 | 45.1561 | 45.1561 | 45.1561 | 45.1561 | 45.1561 | 45.1561 | 45.1561 | 45.1561 | 45.1561 | 45.1561 | 45.1561
Option 2 - Replace 3 x 10/13.5 MVA Tx with 3 x 20/33 MVA Tx
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | FY25: 2.094; FY26: 3.4361; FY27: 3.5785 |  | 3.3275 | 4.6077 | 4.7402
98% | FY25: 0; FY26: 0; FY27: 0 |  | 0 | 0 | 0
97% | FY25: 0; FY26: 0; FY27: 0 |  | 0 | 0 | 0
95% | FY25: 6.572; FY26: 11.7515; FY27: 12.3007 |  | 11.3322 | 16.2727 | 16.7844
90% | FY25: 28.6064; FY26: 58.5505; FY27: 61.7257 |  | 56.1267 | 84.6891 | 87.6469
85% | FY25: 58.0421; FY26: 183.1465; FY27: 196.4122 |  | 173.0196 | 292.3513 | 304.7091
80% | FY25: 7.0161; FY26: 180.8458; FY27: 201.8492 |  | 164.8121 | 353.7485 | 373.3145
75% | FY26: 107.1201; FY27: 145.2583 |  | 81.2692 | 425.8349 | 461.9758
70% | FY27: 1.3066 |  |  | 271.6087 | 330.4367
65% | [32 empty] | 1.9117 | 12.2059
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 101.3074 | 539.402 | 616.207 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 484.9884 | 1436.5143 | 1575.8954 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2 Winter POE50 W E @ R (MWh) N 1 | 70.9151 | 377.5814 | 431.3449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 2 Winter POE10 W E @ R (MWh) N 1 | 145.4965 | 430.9543 | 472.7686 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | FY25: 3.7913; FY26: 5.0725; FY27: 5.2012 |  | 0 | 0 | 0
98% | FY25: 0; FY26: 0; FY27: 0 |  | 0 | 0 | 0
97% | FY25: 0; FY26: 0; FY27: 0 |  | 7.3137 | 8.7167 | 8.7555
95% | FY25: 3.1884; FY26: 4.4245; FY27: 4.5487 |  | 0 | 0 | 0
90% | FY25: 56.8798; FY26: 83.0826; FY27: 85.7157 |  | 6.2541 | 7.5852 | 7.6219
85% | FY25: 143.1015; FY26: 236.6138; FY27: 246.0108 |  | 5.1945 | 6.4536 | 6.4883
80% | FY25: 123.3778; FY26: 275.2831; FY27: 290.5479 |  | 16.5393 | 21.2879 | 21.419
75% | FY25: 29.3744; FY26: 270.8222; FY27: 297.9974 |  | 6.1504 | 8.3808 | 8.4423
70% | FY26: 57.5195; FY27: 79.6537 |  | 12.0933 | 18.3528 | 18.5256
65% | [31 empty] | 1.9118 | 3.8544 | 3.908
60% | [31 empty] | 1.1137 | 10.3432 | 10.6659
55% | [32 empty] | 1.4939 | 1.8164
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 356.116 | 923.49 | 999.5787 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 56.0049 | 85.6039 | 86.7664 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2 Summer POE50 W E @ R (MWh) N 1 | 249.2812 | 646.443 | 699.7051 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 2 Summer POE10 W E @ R (MWh) N 1 | 16.8015 | 25.6812 | 26.0299 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 - Replace 1 x 10/13.5 MVA Tx with 1 x 20/33 MVA Tx
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | 2.094 | 3.4361 | 3.5785 |  |  |  | 0.04033 | 1.0078 | 1.5313 | 1.1494 | 2.3318 | 2.5449 | 2.698 | 3.4199 | 3.5374 | 3.5374 | 3.5374 | 3.5374 | 3.5374 | 3.5374 | 3.5374 | 3.5374 | 3.5374 | 3.5374 | 3.5374 | 3.5374 | 3.5374 | 3.5374 | 3.5374 | 3.5374 |  | 3.3275 | 4.6077 | 4.7402 | 0.63576 | 0.62461 | 0.72522 | 1.1187 | 2.2492 | 2.7157 | 2.2741 | 3.494 | 2.9818 | 3.4426 | 3.7747 | 3.6383 | 3.6383 | 3.6383 | 3.6383 | 3.6383 | 3.6383 | 3.6383 | 3.6383 | 3.6383 | 3.6383 | 3.6383 | 3.6383 | 3.6383 | 3.6383 | 3.6383 | 3.6383
98% | 0 | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
97% | 0 | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
95% | 6.572 | 11.7515 | 12.3007 |  |  |  |  | 1.7379 | 3.7584 | 2.2844 | 6.8477 | 7.6699 | 8.2609 | 11.0468 | 11.5002 | 11.5002 | 11.5002 | 11.5002 | 11.5002 | 11.5002 | 11.5002 | 11.5002 | 11.5002 | 11.5002 | 11.5002 | 11.5002 | 11.5002 | 11.5002 | 11.5002 | 11.5002 |  | 11.3322 | 16.2727 | 16.7844 | 0.34676 | 0.31572 | 0.64735 | 2.1659 | 6.5289 | 8.3293 | 6.625 | 11.3328 | 9.3562 | 11.1347 | 12.4163 | 11.8898 | 11.8898 | 11.8898 | 11.8898 | 11.8898 | 11.8898 | 11.8898 | 11.8898 | 11.8898 | 11.8898 | 11.8898 | 11.8898 | 11.8898 | 11.8898 | 11.8898 | 11.8898
90% | 28.6064 | 58.5505 | 61.7257 |  |  |  |  | 1.0735 | 8.4283 | 2.3928 | 26.209 | 30.9622 | 34.379 | 50.4846 | 53.1061 | 53.1061 | 53.1061 | 53.1061 | 53.1061 | 53.1061 | 53.1061 | 53.1061 | 53.1061 | 53.1061 | 53.1061 | 53.1061 | 53.1061 | 53.1061 | 53.1061 | 53.1061 |  | 56.1267 | 84.6891 | 87.6469 |  |  | 1.1333e-05 | 2.0635 | 24.3655 | 34.7741 | 24.9215 | 52.1382 | 40.7112 | 50.9931 | 58.4025 | 55.3584 | 55.3584 | 55.3584 | 55.3584 | 55.3584 | 55.3584 | 55.3584 | 55.3584 | 55.3584 | 55.3584 | 55.3584 | 55.3584 | 55.3584 | 55.3584 | 55.3584 | 55.3584
85% | 58.0421 | 183.1465 | 196.4122 | [7 empty] | 25.2288 | 41.9199 | 56.0205 | 123.3087 | 134.2611 | 134.2611 | 134.2611 | 134.2611 | 134.2611 | 134.2611 | 134.2611 | 134.2611 | 134.2611 | 134.2611 | 134.2611 | 134.2611 | 134.2611 | 134.2611 | 134.2611 | 134.2611 |  | 173.0196 | 292.3513 | 304.7091 |  |  |  |  | 19.8478 | 57.6711 | 21.4055 | 130.2171 | 82.4758 | 125.433 | 156.3889 | 143.6708 | 143.6708 | 143.6708 | 143.6708 | 143.6708 | 143.6708 | 143.6708 | 143.6708 | 143.6708 | 143.6708 | 143.6708 | 143.6708 | 143.6708 | 143.6708 | 143.6708 | 143.6708
80% | 7.0161 | 180.8458 | 201.8492 | [9 empty] | 0.57639 | 45.4813 | 59.2346 | 59.2346 | 59.2346 | 59.2346 | 59.2346 | 59.2346 | 59.2346 | 59.2346 | 59.2346 | 59.2346 | 59.2346 | 59.2346 | 59.2346 | 59.2346 | 59.2346 | 59.2346 |  | 164.8121 | 353.7485 | 373.3145 | [5 empty] | 0.82602 |  | 53.9553 | 9.8609 | 48.0135 | 92.0788 | 72.4198 | 72.4198 | 72.4198 | 72.4198 | 72.4198 | 72.4198 | 72.4198 | 72.4198 | 72.4198 | 72.4198 | 72.4198 | 72.4198 | 72.4198 | 72.4198 | 72.4198 | 72.4198
75% | FY26: 107.1201; FY27: 145.2583 |  | 81.2692 | 425.8349 | 461.9758 | [10 empty] | 0.2674
70% | FY27: 1.3066 |  |  | 271.6087 | 330.4367
65% | [32 empty] | 1.9117 | 12.2059
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 101.3074 | 539.402 | 616.207 | 0 | 0 | 0 | 0.039927 | 3.781 | 13.5809 | 5.7684 | 60.0112 | 82.2659 | 100.9155 | 231.4038 | 259.023 | 259.023 | 259.023 | 259.023 | 259.023 | 259.023 | 259.023 | 259.023 | 259.023 | 259.023 | 259.023 | 259.023 | 259.023 | 259.023 | 259.023 | 259.023 | E @ R (MWh) | 484.9884 | 1436.5143 | 1575.8954 | 0.9727 | 0.93093 | 1.3589 | 5.2947 | 52.4615 | 103.2731 | 54.6739 | 248.626 | 143.9321 | 236.6269 | 320.0954 | 284.1073 | 284.1073 | 284.1073 | 284.1073 | 284.1073 | 284.1073 | 284.1073 | 284.1073 | 284.1073 | 284.1073 | 284.1073 | 284.1073 | 284.1073 | 284.1073 | 284.1073 | 284.1073
Option 3 Winter POE50 W E @ R (MWh) N 1 | 70.9151 | 377.5814 | 431.3449 | 0 | 0 | 0 | 0.027949 | 2.6467 | 9.5066 | 4.0379 | 42.0079 | 57.5862 | 70.6408 | 161.9827 | 181.3161 | 181.3161 | 181.3161 | 181.3161 | 181.3161 | 181.3161 | 181.3161 | 181.3161 | 181.3161 | 181.3161 | 181.3161 | 181.3161 | 181.3161 | 181.3161 | 181.3161 | 181.3161 | Option 3 Winter POE10 W E @ R (MWh) N 1 | 145.4965 | 430.9543 | 472.7686 | 0.29181 | 0.27928 | 0.40766 | 1.5884 | 15.7384 | 30.9819 | 16.4022 | 74.5878 | 43.1796 | 70.9881 | 96.0286 | 85.2322 | 85.2322 | 85.2322 | 85.2322 | 85.2322 | 85.2322 | 85.2322 | 85.2322 | 85.2322 | 85.2322 | 85.2322 | 85.2322 | 85.2322 | 85.2322 | 85.2322 | 85.2322
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | 3.7913 | 5.0725 | 5.2012 | [8 empty] | 0.046919 | 0.076552 | 0.042261 | 0.11975 | 0.16114 | 0.16114 | 0.16114 | 0.16114 | 0.16114 | 0.16114 | 0.16114 | 0.16114 | 0.16114 | 0.16114 | 0.16114 | 0.16114 | 0.16114 | 0.16114 | 0.16114 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
98% | 0 | 0 | 0 | [11 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
97% | FY25: 0; FY26: 0; FY27: 0 |  | 7.3137 | 8.7167 | 8.7555 | 2.9089 | 2.9196 | 2.9962 | 3.1515 | 3.425 | 3.5674 | 3.6705 | 3.8265 | 4.0257 | 4.2665 | 4.3928 | 4.3518 | 4.3924 | 4.3924 | 4.3924 | 4.3924 | 4.3924 | 4.3924 | 4.3924 | 4.3924 | 4.3924 | 4.3924 | 4.3924 | 4.3924 | 4.3924 | 4.3924 | 4.3924
95% | FY25: 3.1884; FY26: 4.4245; FY27: 4.5487 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
90% | FY25: 56.8798; FY26: 83.0826; FY27: 85.7157 |  | 6.2541 | 7.5852 | 7.6219 | 1.7775 | 1.7876 | 1.8603 | 2.0076 | 2.2671 | 2.4022 | 2.5 | 2.648 | 2.837 | 3.0655 | 3.1852 | 3.1464 | 3.1849 | 3.1849 | 3.1849 | 3.1849 | 3.1849 | 3.1849 | 3.1849 | 3.1849 | 3.1849 | 3.1849 | 3.1849 | 3.1849 | 3.1849 | 3.1849 | 3.1849
85% | FY25: 143.1015; FY26: 236.6138; FY27: 246.0108 |  | 5.1945 | 6.4536 | 6.4883 | 0.64603 | 0.65566 | 0.72442 | 0.86376 | 1.1092 | 1.237 | 1.3295 | 1.4695 | 1.6483 | 1.8644 | 1.9777 | 1.941 | 1.9774 | 1.9774 | 1.9774 | 1.9774 | 1.9774 | 1.9774 | 1.9774 | 1.9774 | 1.9774 | 1.9774 | 1.9774 | 1.9774 | 1.9774 | 1.9774 | 1.9774
80% | FY25: 123.3778; FY26: 275.2831; FY27: 290.5479 |  | 16.5393 | 21.2879 | 21.419 | 0.011402 | 0.014207 | 0.043104 | 0.1489 | 0.48558 | 0.73511 | 0.94657 | 1.3151 | 1.8689 | 2.6535 | 3.0807 | 2.9422 | 3.0795 | 3.0795 | 3.0795 | 3.0795 | 3.0795 | 3.0795 | 3.0795 | 3.0795 | 3.0795 | 3.0795 | 3.0795 | 3.0795 | 3.0795 | 3.0795 | 3.0795
75% | FY25: 29.3744; FY26: 270.8222; FY27: 297.9974 |  | 6.1504 | 8.3808 | 8.4423 | [9 empty] | 0.0032892 | 0.022936 | 0.01464 | 0.022854 | 0.022854 | 0.022854 | 0.022854 | 0.022854 | 0.022854 | 0.022854 | 0.022854 | 0.022854 | 0.022854 | 0.022854 | 0.022854 | 0.022854 | 0.022854 | 0.022854
70% | FY26: 57.5195; FY27: 79.6537 |  | 12.0933 | 18.3528 | 18.5256
65% | [31 empty] | 1.9118 | 3.8544 | 3.908
60% | [31 empty] | 1.1137 | 10.3432 | 10.6659
55% | [32 empty] | 1.4939 | 1.8164
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 356.116 | 923.49 | 999.5787 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.04645 | 0.075786 | 0.041839 | 0.11855 | 0.15952 | 0.15952 | 0.15952 | 0.15952 | 0.15952 | 0.15952 | 0.15952 | 0.15952 | 0.15952 | 0.15952 | 0.15952 | 0.15952 | 0.15952 | 0.15952 | 0.15952 | E @ R (MWh) | 56.0049 | 85.6039 | 86.7664 | 5.2903 | 5.3234 | 5.5679 | 6.1101 | 7.2139 | 7.8624 | 8.3622 | 9.1666 | 10.2761 | 11.7347 | 12.5328 | 12.2722 | 12.5305 | 12.5305 | 12.5305 | 12.5305 | 12.5305 | 12.5305 | 12.5305 | 12.5305 | 12.5305 | 12.5305 | 12.5305 | 12.5305 | 12.5305 | 12.5305 | 12.5305
Option 3 Summer POE50 W E @ R (MWh) N 1 | 249.2812 | 646.443 | 699.7051 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.032515 | 0.05305 | 0.029287 | 0.082984 | 0.11167 | 0.11167 | 0.11167 | 0.11167 | 0.11167 | 0.11167 | 0.11167 | 0.11167 | 0.11167 | 0.11167 | 0.11167 | 0.11167 | 0.11167 | 0.11167 | 0.11167 | Option 3 Summer POE10 W E @ R (MWh) N 1 | 16.8015 | 25.6812 | 26.0299 | 1.5871 | 1.597 | 1.6704 | 1.833 | 2.1642 | 2.3587 | 2.5087 | 2.75 | 3.0828 | 3.5204 | 3.7598 | 3.6816 | 3.7591 | 3.7591 | 3.7591 | 3.7591 | 3.7591 | 3.7591 | 3.7591 | 3.7591 | 3.7591 | 3.7591 | 3.7591 | 3.7591 | 3.7591 | 3.7591 | 3.7591
Option 4 - Construct 2x 20/33MVA zone substation in Inverloch
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | FY25: 2.094; FY26: 3.4361; FY27: 3.5785 |  | 3.3275 | 4.6077 | 4.7402
98% | FY25: 0; FY26: 0; FY27: 0 |  | 0 | 0 | 0
97% | FY25: 0; FY26: 0; FY27: 0 |  | 0 | 0 | 0
95% | FY25: 6.572; FY26: 11.7515; FY27: 12.3007 |  | 11.3322 | 16.2727 | 16.7844
90% | FY25: 28.6064; FY26: 58.5505; FY27: 61.7257 |  | 56.1267 | 84.6891 | 87.6469
85% | FY25: 58.0421; FY26: 183.1465; FY27: 196.4122 |  | 173.0196 | 292.3513 | 304.7091
80% | FY25: 7.0161; FY26: 180.8458; FY27: 201.8492 |  | 164.8121 | 353.7485 | 373.3145
75% | FY26: 107.1201; FY27: 145.2583 |  | 81.2692 | 425.8349 | 461.9758
70% | FY27: 1.3066 |  |  | 271.6087 | 330.4367
65% | [32 empty] | 1.9117 | 12.2059
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 101.3074 | 539.402 | 616.207 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 484.9884 | 1436.5143 | 1575.8954 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 Winter POE50 W E @ R (MWh) N 1 | 70.9151 | 377.5814 | 431.3449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 4 Winter POE10 W E @ R (MWh) N 1 | 145.4965 | 430.9543 | 472.7686 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | FY25: 3.7913; FY26: 5.0725; FY27: 5.2012 |  | 0 | 0 | 0
98% | FY25: 0; FY26: 0; FY27: 0 |  | 0 | 0 | 0
97% | FY25: 0; FY26: 0; FY27: 0 |  | 7.3137 | 8.7167 | 8.7555
95% | FY25: 3.1884; FY26: 4.4245; FY27: 4.5487 |  | 0 | 0 | 0
90% | FY25: 56.8798; FY26: 83.0826; FY27: 85.7157 |  | 6.2541 | 7.5852 | 7.6219
85% | FY25: 143.1015; FY26: 236.6138; FY27: 246.0108 |  | 5.1945 | 6.4536 | 6.4883
80% | FY25: 123.3778; FY26: 275.2831; FY27: 290.5479 |  | 16.5393 | 21.2879 | 21.419
75% | FY25: 29.3744; FY26: 270.8222; FY27: 297.9974 |  | 6.1504 | 8.3808 | 8.4423
70% | FY26: 57.5195; FY27: 79.6537 |  | 12.0933 | 18.3528 | 18.5256
65% | [31 empty] | 1.9118 | 3.8544 | 3.908
60% | [31 empty] | 1.1137 | 10.3432 | 10.6659
55% | [32 empty] | 1.4939 | 1.8164
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 356.116 | 923.49 | 999.5787 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 56.0049 | 85.6039 | 86.7664 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 Summer POE50 W E @ R (MWh) N 1 | 249.2812 | 646.443 | 699.7051 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 4 Summer POE10 W E @ R (MWh) N 1 | 16.8015 | 25.6812 | 26.0299 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 - Contract network support services to defer network investment
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | 0.88219 | 2.1422 | 2.2822 | 2.4606 | 2.6935 | 2.9105 | 3.2884 | 4.2458 | 4.761 | 4.373 | 5.5463 | 5.7477 | 5.8867 | 6.6012 | 6.7211 | 6.7211 | 6.7211 | 6.7211 | 6.7211 | 6.7211 | 6.7211 | 6.7211 | 6.7211 | 6.7211 | 6.7211 | 6.7211 | 6.7211 | 6.7211 | 6.7211 | 6.7211 |  | 2.1156 | 3.3137 | 3.444 | 3.904 | 3.8922 | 3.9883 | 4.3727 | 5.4872 | 5.9454 | 5.4977 | 6.7084 | 6.1846 | 6.6314 | 6.9561 | 6.822 | 6.822 | 6.822 | 6.822 | 6.822 | 6.822 | 6.822 | 6.822 | 6.822 | 6.822 | 6.822 | 6.822 | 6.822 | 6.822 | 6.822 | 6.822
98% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
97% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
95% | 1.895 | 6.7576 | 7.2981 | 7.9865 | 8.8856 | 9.723 | 11.1815 | 14.8762 | 16.8645 | 15.3672 | 19.8953 | 20.6724 | 21.209 | 23.9664 | 24.4291 | 24.4291 | 24.4291 | 24.4291 | 24.4291 | 24.4291 | 24.4291 | 24.4291 | 24.4291 | 24.4291 | 24.4291 | 24.4291 | 24.4291 | 24.4291 | 24.4291 | 24.4291 |  | 6.6553 | 11.2789 | 11.7818 | 13.5569 | 13.5115 | 13.8824 | 15.3659 | 19.6671 | 21.4353 | 19.7078 | 24.3803 | 22.3587 | 24.0828 | 25.3359 | 24.8186 | 24.8186 | 24.8186 | 24.8186 | 24.8186 | 24.8186 | 24.8186 | 24.8186 | 24.8186 | 24.8186 | 24.8186 | 24.8186 | 24.8186 | 24.8186 | 24.8186 | 24.8186
90% | 2.6222 | 29.6798 | 32.8044 | 36.7844 | 41.9822 | 46.8231 | 55.2551 | 76.6151 | 88.11 | 79.4537 | 105.6317 | 110.1248 | 113.227 | 129.1678 | 131.8428 | 131.8428 | 131.8428 | 131.8428 | 131.8428 | 131.8428 | 131.8428 | 131.8428 | 131.8428 | 131.8428 | 131.8428 | 131.8428 | 131.8428 | 131.8428 | 131.8428 | 131.8428 |  | 29.0882 | 55.8183 | 58.7256 | 68.9882 | 68.7254 | 70.87 | 79.4465 | 104.3126 | 114.5351 | 104.548 | 131.5609 | 119.8737 | 129.8411 | 137.0857 | 134.095 | 134.095 | 134.095 | 134.095 | 134.095 | 134.095 | 134.095 | 134.095 | 134.095 | 134.095 | 134.095 | 134.095 | 134.095 | 134.095 | 134.095 | 134.095
85% |  | 62.5264 | 75.5809 | 92.209 | 113.9251 | 134.1501 | 169.3784 | 258.6187 | 306.6435 | 270.4784 | 379.8482 | 398.62 | 411.5809 | 478.1803 | 489.3561 | 489.3561 | 489.3561 | 489.3561 | 489.3561 | 489.3561 | 489.3561 | 489.3561 | 489.3561 | 489.3561 | 489.3561 | 489.3561 | 489.3561 | 489.3561 | 489.3561 | 489.3561 |  | 60.0548 | 171.7312 | 183.8778 | 226.7541 | 225.6562 | 234.6163 | 270.4484 | 374.3371 | 417.0461 | 375.3203 | 488.1784 | 439.3503 | 480.9934 | 511.2606 | 498.7657 | 498.7657 | 498.7657 | 498.7657 | 498.7657 | 498.7657 | 498.7657 | 498.7657 | 498.7657 | 498.7657 | 498.7657 | 498.7657 | 498.7657 | 498.7657 | 498.7657 | 498.7657
80% |  | 9.7714 | 20.2939 | 38.9396 | 71.2484 | 103.2704 | 159.0469 | 300.34 | 376.3772 | 319.1174 | 492.2814 | 522.0025 | 542.5233 | 647.9695 | 665.6639 | 665.6639 | 665.6639 | 665.6639 | 665.6639 | 665.6639 | 665.6639 | 665.6639 | 665.6639 | 665.6639 | 665.6639 | 665.6639 | 665.6639 | 665.6639 | 665.6639 | 665.6639 |  | 8.1978 | 162.7721 | 182.0037 | 249.8893 | 248.1509 | 262.3373 | 319.0699 | 483.5556 | 551.1763 | 485.1124 | 663.7993 | 586.4904 | 652.4234 | 700.3451 | 680.5621 | 680.5621 | 680.5621 | 680.5621 | 680.5621 | 680.5621 | 680.5621 | 680.5621 | 680.5621 | 680.5621 | 680.5621 | 680.5621 | 680.5621 | 680.5621 | 680.5621 | 680.5621
75% |  |  |  |  | 1.0306 | 14.3987 | 72.8029 | 327.1829 | 467.633 | 361.867 | 681.7222 | 736.6208 | 774.5252 | 969.2973 | 1001.981 | 1001.981 | 1001.981 | 1001.981 | 1001.981 | 1001.981 | 1001.981 | 1001.981 | 1001.981 | 1001.981 | 1001.981 | 1001.981 | 1001.981 | 1001.981 | 1001.981 | 1001.981 |  |  | 78.2229 | 109.1168 | 233.9942 | 230.7831 | 256.9873 | 361.7792 | 665.6047 | 790.5084 | 668.4803 | 998.5369 | 855.7378 | 977.5242 | 1066.0414 | 1029.4998 | 1029.4998 | 1029.4998 | 1029.4998 | 1029.4998 | 1029.4998 | 1029.4998 | 1029.4998 | 1029.4998 | 1029.4998 | 1029.4998 | 1029.4998 | 1029.4998 | 1029.4998 | 1029.4998 | 1029.4998
70% | [7 empty] | 126.2479 | 339.6452 | 171.861 | 688.1271 | 777.4878 | 839.1865 | 1156.2251 | 1209.4258 | 1209.4258 | 1209.4258 | 1209.4258 | 1209.4258 | 1209.4258 | 1209.4258 | 1209.4258 | 1209.4258 | 1209.4258 | 1209.4258 | 1209.4258 | 1209.4258 | 1209.4258 | 1209.4258 | 1209.4258 |  |  |  |  | 37.4926 | 35.3411 | 54.6944 | 171.7373 | 661.892 | 865.2029 | 666.5727 | 1203.8197 | 971.3797 | 1169.6165 | 1313.6996 | 1254.2193 | 1254.2193 | 1254.2193 | 1254.2193 | 1254.2193 | 1254.2193 | 1254.2193 | 1254.2193 | 1254.2193 | 1254.2193 | 1254.2193 | 1254.2193 | 1254.2193 | 1254.2193 | 1254.2193 | 1254.2193
65% | [8 empty] | 14.6116 |  | 254.5699 | 359.4051 | 434.959 | 823.1926 | 888.3401 | 888.3401 | 888.3401 | 888.3401 | 888.3401 | 888.3401 | 888.3401 | 888.3401 | 888.3401 | 888.3401 | 888.3401 | 888.3401 | 888.3401 | 888.3401 | 888.3401 | 888.3401 | [8 empty] | 226.8699 | 466.8177 | 231.7022 | 881.4752 | 596.8378 | 839.5912 | 1016.03 | 943.1927 | 943.1927 | 943.1927 | 943.1927 | 943.1927 | 943.1927 | 943.1927 | 943.1927 | 943.1927 | 943.1927 | 943.1927 | 943.1927 | 943.1927 | 943.1927 | 943.1927 | 943.1927
60% | [11 empty] | 0.78074 | 10.1272 | 216.1092 | 275.1395 | 275.1395 | 275.1395 | 275.1395 | 275.1395 | 275.1395 | 275.1395 | 275.1395 | 275.1395 | 275.1395 | 275.1395 | 275.1395 | 275.1395 | 275.1395 | 275.1395 | 275.1395 | [9 empty] | 17.1884 |  | 268.6034 | 64.7002 | 230.3342 | 410.0023 | 330.0032 | 330.0032 | 330.0032 | 330.0032 | 330.0032 | 330.0032 | 330.0032 | 330.0032 | 330.0032 | 330.0032 | 330.0032 | 330.0032 | 330.0032 | 330.0032 | 330.0032 | 330.0032
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 5.3454 | 109.7685 | 136.8769 | 176.5963 | 237.3678 | 308.163 | 466.2437 | 1097.0453 | 1598.4996 | 1210.2924 | 2601.3458 | 2902.1473 | 3121.6926 | 4406.2024 | 4645.9703 | 4645.9703 | 4645.9703 | 4645.9703 | 4645.9703 | 4645.9703 | 4645.9703 | 4645.9703 | 4645.9703 | 4645.9703 | 4645.9703 | 4645.9703 | 4645.9703 | 4645.9703 | 4645.9703 | 4645.9703 | E @ R (MWh) | 105.0506 | 478.3057 | 543.4602 | 826.2336 | 817.7997 | 888.4023 | 1209.9977 | 2516.3089 | 3217.3571 | 2531.3721 | 4620.392 | 3626.2841 | 4465.928 | 5134.8892 | 4852.9588 | 4852.9588 | 4852.9588 | 4852.9588 | 4852.9588 | 4852.9588 | 4852.9588 | 4852.9588 | 4852.9588 | 4852.9588 | 4852.9588 | 4852.9588 | 4852.9588 | 4852.9588 | 4852.9588 | 4852.9588
Option 5 Winter POE50 W E @ R (MWh) N 1 | 3.7418 | 76.838 | 95.8138 | 123.6174 | 166.1574 | 215.7141 | 326.3706 | 767.9317 | 1118.9497 | 847.2047 | 1820.9421 | 2031.5031 | 2185.1848 | 3084.3417 | 3252.1792 | 3252.1792 | 3252.1792 | 3252.1792 | 3252.1792 | 3252.1792 | 3252.1792 | 3252.1792 | 3252.1792 | 3252.1792 | 3252.1792 | 3252.1792 | 3252.1792 | 3252.1792 | 3252.1792 | 3252.1792 | Option 5 Winter POE10 W E @ R (MWh) N 1 | 31.5152 | 143.4917 | 163.0381 | 247.8701 | 245.3399 | 266.5207 | 362.9993 | 754.8927 | 965.2071 | 759.4116 | 1386.1176 | 1087.8852 | 1339.7784 | 1540.4668 | 1455.8876 | 1455.8876 | 1455.8876 | 1455.8876 | 1455.8876 | 1455.8876 | 1455.8876 | 1455.8876 | 1455.8876 | 1455.8876 | 1455.8876 | 1455.8876 | 1455.8876 | 1455.8876 | 1455.8876 | 1455.8876
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | 2.2493 | 3.426 | 3.5518 | 3.4918 | 3.551 | 3.57 | 3.6374 | 3.7796 | 3.9056 | 3.9609 | 3.8932 | 4.1135 | 4.1328 | 4.0793 | 4.1708 | 4.2122 | 4.2122 | 4.2122 | 4.2122 | 4.2122 | 4.2122 | 4.2122 | 4.2122 | 4.2122 | 4.2122 | 4.2122 | 4.2122 | 4.2122 | 4.2122 | 4.2122 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
98% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
97% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 5.8027 | 7.1033 | 7.1392 | 7.1005 | 7.1105 | 7.1815 | 7.3254 | 7.5789 | 7.711 | 7.8066 | 7.9512 | 8.1358 | 8.3591 | 8.4761 | 8.4382 | 8.4787 | 8.4787 | 8.4787 | 8.4787 | 8.4787 | 8.4787 | 8.4787 | 8.4787 | 8.4787 | 8.4787 | 8.4787 | 8.4787 | 8.4787 | 8.4787 | 8.4787
95% | 1.7006 | 2.8359 | 2.9573 | 2.8994 | 2.9566 | 2.9748 | 3.0399 | 3.177 | 3.2987 | 3.352 | 3.2867 | 3.4992 | 3.5179 | 3.4662 | 3.5545 | 3.5945 | 3.5945 | 3.5945 | 3.5945 | 3.5945 | 3.5945 | 3.5945 | 3.5945 | 3.5945 | 3.5945 | 3.5945 | 3.5945 | 3.5945 | 3.5945 | 3.5945 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
90% | 25.3423 | 49.4079 | 51.982 | 50.7549 | 51.9658 | 52.3533 | 53.7329 | 56.6394 | 59.2178 | 60.3476 | 58.963 | 63.4684 | 63.8642 | 62.7694 | 64.6416 | 65.4881 | 65.4881 | 65.4881 | 65.4881 | 65.4881 | 65.4881 | 65.4881 | 65.4881 | 65.4881 | 65.4881 | 65.4881 | 65.4881 | 65.4881 | 65.4881 | 65.4881 |  | 4.8206 | 6.0545 | 6.0885 | 6.0518 | 6.0613 | 6.1286 | 6.2652 | 6.5057 | 6.631 | 6.7217 | 6.8589 | 7.034 | 7.2458 | 7.3569 | 7.3209 | 7.3593 | 7.3593 | 7.3593 | 7.3593 | 7.3593 | 7.3593 | 7.3593 | 7.3593 | 7.3593 | 7.3593 | 7.3593 | 7.3593 | 7.3593 | 7.3593 | 7.3593
85% | 30.5806 | 116.4356 | 125.6221 | 121.2429 | 125.5643 | 126.9473 | 131.8707 | 142.2434 | 151.4453 | 155.4774 | 150.536 | 166.6148 | 168.0274 | 164.1201 | 170.8016 | 173.8227 | 173.8227 | 173.8227 | 173.8227 | 173.8227 | 173.8227 | 173.8227 | 173.8227 | 173.8227 | 173.8227 | 173.8227 | 173.8227 | 173.8227 | 173.8227 | 173.8227 |  | 3.8384 | 5.0056 | 5.0378 | 5.0031 | 5.012 | 5.0758 | 5.205 | 5.4325 | 5.551 | 5.6367 | 5.7665 | 5.9322 | 6.1326 | 6.2376 | 6.2036 | 6.24 | 6.24 | 6.24 | 6.24 | 6.24 | 6.24 | 6.24 | 6.24 | 6.24 | 6.24 | 6.24 | 6.24 | 6.24 | 6.24 | 6.24
80% |  | 80.0607 | 94.9837 | 87.8698 | 94.8897 | 97.1364 | 105.1341 | 121.9839 | 136.9319 | 143.4818 | 135.4548 | 161.5739 | 163.8685 | 157.5213 | 168.3751 | 173.2826 | 173.2826 | 173.2826 | 173.2826 | 173.2826 | 173.2826 | 173.2826 | 173.2826 | 173.2826 | 173.2826 | 173.2826 | 173.2826 | 173.2826 | 173.2826 | 173.2826 |  | 11.4251 | 15.8272 | 15.9486 | 15.8177 | 15.8513 | 16.0917 | 16.5789 | 17.4369 | 17.8839 | 18.2073 | 18.6968 | 19.3217 | 20.0774 | 20.4735 | 20.3451 | 20.4823 | 20.4823 | 20.4823 | 20.4823 | 20.4823 | 20.4823 | 20.4823 | 20.4823 | 20.4823 | 20.4823 | 20.4823 | 20.4823 | 20.4823 | 20.4823 | 20.4823
75% |  | 3.078 | 9.157 | 5.8614 | 9.1088 | 10.2958 | 15.0982 | 28.1227 | 42.9131 | 50.3347 | 41.3181 | 73.7561 | 77.0292 | 68.1406 | 83.6533 | 91.1605 | 91.1605 | 91.1605 | 91.1605 | 91.1605 | 91.1605 | 91.1605 | 91.1605 | 91.1605 | 91.1605 | 91.1605 | 91.1605 | 91.1605 | 91.1605 | 91.1605 |  | 3.7482 | 5.8159 | 5.8729 | 5.8114 | 5.8272 | 5.9402 | 6.169 | 6.572 | 6.7819 | 6.9338 | 7.1638 | 7.4573 | 7.8122 | 7.9982 | 7.9379 | 8.0024 | 8.0024 | 8.0024 | 8.0024 | 8.0024 | 8.0024 | 8.0024 | 8.0024 | 8.0024 | 8.0024 | 8.0024 | 8.0024 | 8.0024 | 8.0024 | 8.0024
70% | [31 empty] | 5.3518 | 11.1546 | 11.3147 | 11.142 | 11.1864 | 11.5033 | 12.1455 | 13.2764 | 13.8657 | 14.2921 | 14.9373 | 15.7611 | 16.7572 | 17.2792 | 17.11 | 17.2909 | 17.2909 | 17.2909 | 17.2909 | 17.2909 | 17.2909 | 17.2909 | 17.2909 | 17.2909 | 17.2909 | 17.2909 | 17.2909 | 17.2909 | 17.2909 | 17.2909
65% | [31 empty] | 0.16364 | 1.6205 | 1.6702 | 1.6166 | 1.6304 | 1.7287 | 1.928 | 2.279 | 2.4619 | 2.5942 | 2.7944 | 3.0501 | 3.3592 | 3.5212 | 3.4687 | 3.5249 | 3.5249 | 3.5249 | 3.5249 | 3.5249 | 3.5249 | 3.5249 | 3.5249 | 3.5249 | 3.5249 | 3.5249 | 3.5249 | 3.5249 | 3.5249 | 3.5249
60% | [32 empty] | 0.50628 | 0.59355 | 0.49975 | 0.52312 | 0.70503 | 1.1542 | 2.2013 | 2.8732 | 3.412 | 4.31 | 5.5984 | 7.3628 | 8.3379 | 8.0218 | 8.3598 | 8.3598 | 8.3598 | 8.3598 | 8.3598 | 8.3598 | 8.3598 | 8.3598 | 8.3598 | 8.3598 | 8.3598 | 8.3598 | 8.3598 | 8.3598 | 8.3598
55% | [43 empty] | 0.0027324 | 0.1911 | 0.09772 | 0.1987 | 0.1987 | 0.1987 | 0.1987 | 0.1987 | 0.1987 | 0.1987 | 0.1987 | 0.1987 | 0.1987 | 0.1987 | 0.1987 | 0.1987 | 0.1987 | 0.1987
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 59.2741 | 252.6916 | 285.3714 | 269.3991 | 285.1557 | 290.3449 | 309.3882 | 352.3865 | 393.7352 | 412.7848 | 389.5174 | 468.2956 | 475.6355 | 455.4958 | 490.245 | 506.4449 | 506.4449 | 506.4449 | 506.4449 | 506.4449 | 506.4449 | 506.4449 | 506.4449 | 506.4449 | 506.4449 | 506.4449 | 506.4449 | 506.4449 | 506.4449 | 506.4449 | E @ R (MWh) | 34.799 | 52.5569 | 53.1289 | 52.5125 | 52.6703 | 53.8113 | 56.2034 | 60.6698 | 63.122 | 64.9483 | 67.7941 | 71.5678 | 76.3381 | 79.073 | 78.1544 | 79.1377 | 79.1377 | 79.1377 | 79.1377 | 79.1377 | 79.1377 | 79.1377 | 79.1377 | 79.1377 | 79.1377 | 79.1377 | 79.1377 | 79.1377 | 79.1377 | 79.1377
Option 5 Summer POE50 W E @ R (MWh) N 1 | 41.4919 | 176.8841 | 199.76 | 188.5794 | 199.609 | 203.2415 | 216.5717 | 246.6706 | 275.6147 | 288.9494 | 272.6622 | 327.8069 | 332.9448 | 318.847 | 343.1715 | 354.5114 | 354.5114 | 354.5114 | 354.5114 | 354.5114 | 354.5114 | 354.5114 | 354.5114 | 354.5114 | 354.5114 | 354.5114 | 354.5114 | 354.5114 | 354.5114 | 354.5114 | Option 5 Summer POE10 W E @ R (MWh) N 1 | 10.4397 | 15.7671 | 15.9387 | 15.7538 | 15.8011 | 16.1434 | 16.861 | 18.2009 | 18.9366 | 19.4845 | 20.3382 | 21.4703 | 22.9014 | 23.7219 | 23.4463 | 23.7413 | 23.7413 | 23.7413 | 23.7413 | 23.7413 | 23.7413 | 23.7413 | 23.7413 | 23.7413 | 23.7413 | 23.7413 | 23.7413 | 23.7413 | 23.7413 | 23.7413
Option 6 -
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | 2.094 | 3.4361 | 3.5785 | 3.7544 | 3.988 | 4.2094 | 4.5964 | 5.5698 | 6.0933 | 5.7114 | 6.8938 | 7.1069 | 7.26 | 7.9819 | 8.0994 | 8.0994 | 8.0994 | 8.0994 | 8.0994 | 8.0994 | 8.0994 | 8.0994 | 8.0994 | 8.0994 | 8.0994 | 8.0994 | 8.0994 | 8.0994 | 8.0994 | 8.0994 |  | 3.3275 | 4.6077 | 4.7402 | 5.1978 | 5.1866 | 5.2872 | 5.6807 | 6.8112 | 7.2777 | 6.8361 | 8.056 | 7.5438 | 8.0046 | 8.3367 | 8.2003 | 8.2003 | 8.2003 | 8.2003 | 8.2003 | 8.2003 | 8.2003 | 8.2003 | 8.2003 | 8.2003 | 8.2003 | 8.2003 | 8.2003 | 8.2003 | 8.2003 | 8.2003
98% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
97% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
95% | 6.572 | 11.7515 | 12.3007 | 12.9797 | 13.8812 | 14.7359 | 16.2295 | 19.9859 | 22.0064 | 20.5324 | 25.0957 | 25.9179 | 26.5089 | 29.2948 | 29.7482 | 29.7482 | 29.7482 | 29.7482 | 29.7482 | 29.7482 | 29.7482 | 29.7482 | 29.7482 | 29.7482 | 29.7482 | 29.7482 | 29.7482 | 29.7482 | 29.7482 | 29.7482 |  | 11.3322 | 16.2727 | 16.7844 | 18.5501 | 18.5071 | 18.8953 | 20.4139 | 24.7769 | 26.5773 | 24.873 | 29.5808 | 27.6042 | 29.3827 | 30.6643 | 30.1378 | 30.1378 | 30.1378 | 30.1378 | 30.1378 | 30.1378 | 30.1378 | 30.1378 | 30.1378 | 30.1378 | 30.1378 | 30.1378 | 30.1378 | 30.1378 | 30.1378 | 30.1378
90% | 28.6064 | 58.5505 | 61.7257 | 65.6512 | 70.8631 | 75.804 | 84.4388 | 106.1559 | 117.8368 | 109.3152 | 135.697 | 140.4502 | 143.8669 | 159.9726 | 162.5941 | 162.5941 | 162.5941 | 162.5941 | 162.5941 | 162.5941 | 162.5941 | 162.5941 | 162.5941 | 162.5941 | 162.5941 | 162.5941 | 162.5941 | 162.5941 | 162.5941 | 162.5941 |  | 56.1267 | 84.6891 | 87.6469 | 97.855 | 97.6062 | 99.8509 | 108.6302 | 133.8534 | 144.262 | 134.4095 | 161.6261 | 150.1991 | 160.4811 | 167.8904 | 164.8463 | 164.8463 | 164.8463 | 164.8463 | 164.8463 | 164.8463 | 164.8463 | 164.8463 | 164.8463 | 164.8463 | 164.8463 | 164.8463 | 164.8463 | 164.8463 | 164.8463 | 164.8463
85% | 58.0421 | 183.1465 | 196.4122 | 212.8125 | 234.5872 | 255.2303 | 291.3058 | 382.038 | 430.8403 | 395.2376 | 505.4587 | 525.3172 | 539.5922 | 606.8804 | 617.8328 | 617.8328 | 617.8328 | 617.8328 | 617.8328 | 617.8328 | 617.8328 | 617.8328 | 617.8328 | 617.8328 | 617.8328 | 617.8328 | 617.8328 | 617.8328 | 617.8328 | 617.8328 |  | 173.0196 | 292.3513 | 304.7091 | 347.3577 | 346.3183 | 355.6965 | 392.3758 | 497.7564 | 541.2429 | 500.0796 | 613.7889 | 566.0476 | 609.0048 | 639.9607 | 627.2425 | 627.2425 | 627.2425 | 627.2425 | 627.2425 | 627.2425 | 627.2425 | 627.2425 | 627.2425 | 627.2425 | 627.2425 | 627.2425 | 627.2425 | 627.2425 | 627.2425 | 627.2425
80% | 7.0161 | 180.8458 | 201.8492 | 227.8157 | 262.2914 | 294.9752 | 352.0931 | 495.7485 | 573.0166 | 516.6472 | 691.159 | 722.6008 | 745.2022 | 851.7388 | 869.0797 | 869.0797 | 869.0797 | 869.0797 | 869.0797 | 869.0797 | 869.0797 | 869.0797 | 869.0797 | 869.0797 | 869.0797 | 869.0797 | 869.0797 | 869.0797 | 869.0797 | 869.0797 |  | 164.8121 | 353.7485 | 373.3145 | 440.8395 | 439.1939 | 454.0422 | 512.1161 | 678.9641 | 747.8157 | 682.6423 | 862.6769 | 787.0886 | 855.1023 | 904.1144 | 883.9779 | 883.9779 | 883.9779 | 883.9779 | 883.9779 | 883.9779 | 883.9779 | 883.9779 | 883.9779 | 883.9779 | 883.9779 | 883.9779 | 883.9779 | 883.9779 | 883.9779 | 883.9779
75% |  | 107.1201 | 145.2583 | 193.2216 | 256.9023 | 317.2734 | 422.7773 | 688.1264 | 830.8501 | 726.7289 | 1049.0735 | 1107.1504 | 1148.898 | 1345.6842 | 1377.715 | 1377.715 | 1377.715 | 1377.715 | 1377.715 | 1377.715 | 1377.715 | 1377.715 | 1377.715 | 1377.715 | 1377.715 | 1377.715 | 1377.715 | 1377.715 | 1377.715 | 1377.715 |  | 81.2692 | 425.8349 | 461.9758 | 586.7028 | 583.663 | 611.0897 | 718.3593 | 1026.5481 | 1153.7254 | 1033.3422 | 1365.8883 | 1226.2674 | 1351.8971 | 1442.4284 | 1405.2338 | 1405.2338 | 1405.2338 | 1405.2338 | 1405.2338 | 1405.2338 | 1405.2338 | 1405.2338 | 1405.2338 | 1405.2338 | 1405.2338 | 1405.2338 | 1405.2338 | 1405.2338 | 1405.2338 | 1405.2338
70% |  |  | 1.3066 | 14.8126 | 54.6251 | 114.4437 | 266.6317 | 698.5515 | 930.8688 | 761.3864 | 1286.0803 | 1380.6144 | 1448.5689 | 1768.886 | 1821.0238 | 1821.0238 | 1821.0238 | 1821.0238 | 1821.0238 | 1821.0238 | 1821.0238 | 1821.0238 | 1821.0238 | 1821.0238 | 1821.0238 | 1821.0238 | 1821.0238 | 1821.0238 | 1821.0238 | 1821.0238 |  |  | 271.6087 | 330.4367 | 533.4601 | 528.5121 | 573.1557 | 747.7629 | 1249.4148 | 1456.4266 | 1260.4738 | 1801.773 | 1574.5062 | 1778.9989 | 1926.3605 | 1865.8173 | 1865.8173 | 1865.8173 | 1865.8173 | 1865.8173 | 1865.8173 | 1865.8173 | 1865.8173 | 1865.8173 | 1865.8173 | 1865.8173 | 1865.8173 | 1865.8173 | 1865.8173 | 1865.8173 | 1865.8173
65% | [6 empty] | 1.4477 | 265.9903 | 547.2297 | 339.6879 | 982.2084 | 1097.9714 | 1181.1858 | 1573.4342 | 1637.2802 | 1637.2802 | 1637.2802 | 1637.2802 | 1637.2802 | 1637.2802 | 1637.2802 | 1637.2802 | 1637.2802 | 1637.2802 | 1637.2802 | 1637.2802 | 1637.2802 | 1637.2802 | 1637.2802 | 1637.2802 |  |  | 1.9117 | 12.2059 | 113.2844 | 109.6564 | 144.4238 | 323.0448 | 937.3092 | 1190.8081 | 950.8517 | 1613.7064 | 1335.404 | 1585.8181 | 1766.2716 | 1692.1327 | 1692.1327 | 1692.1327 | 1692.1327 | 1692.1327 | 1692.1327 | 1692.1327 | 1692.1327 | 1692.1327 | 1692.1327 | 1692.1327 | 1692.1327 | 1692.1327 | 1692.1327 | 1692.1327 | 1692.1327
60% | [8 empty] | 43.0729 | 0.078688 | 371.8511 | 509.12 | 612.3349 | 1098.8592 | 1178.0505 | 1178.0505 | 1178.0505 | 1178.0505 | 1178.0505 | 1178.0505 | 1178.0505 | 1178.0505 | 1178.0505 | 1178.0505 | 1178.0505 | 1178.0505 | 1178.0505 | 1178.0505 | 1178.0505 | 1178.0505 | [8 empty] | 323.8953 | 624.2698 | 338.0342 | 1148.8107 | 803.6191 | 1114.2195 | 1338.0446 | 1246.0867 | 1246.0867 | 1246.0867 | 1246.0867 | 1246.0867 | 1246.0867 | 1246.0867 | 1246.0867 | 1246.0867 | 1246.0867 | 1246.0867 | 1246.0867 | 1246.0867 | 1246.0867 | 1246.0867 | 1246.0867
55% | [11 empty] | 0.48994 | 9.8575 | 206.4492 | 260.9948 | 260.9948 | 260.9948 | 260.9948 | 260.9948 | 260.9948 | 260.9948 | 260.9948 | 260.9948 | 260.9948 | 260.9948 | 260.9948 | 260.9948 | 260.9948 | 260.9948 | 260.9948 | [9 empty] | 11.6994 |  | 240.151 | 57.864 | 216.5553 | 389.3679 | 312.6478 | 312.6478 | 312.6478 | 312.6478 | 312.6478 | 312.6478 | 312.6478 | 312.6478 | 312.6478 | 312.6478 | 312.6478 | 312.6478 | 312.6478 | 312.6478 | 312.6478 | 312.6478
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 101.3074 | 539.402 | 616.207 | 723.7373 | 888.1669 | 1065.9052 | 1425.125 | 2635.5446 | 3466.7969 | 2846.5726 | 5002.9824 | 5461.5717 | 5804.6426 | 7572.6894 | 7882.7941 | 7882.7941 | 7882.7941 | 7882.7941 | 7882.7941 | 7882.7941 | 7882.7941 | 7882.7941 | 7882.7941 | 7882.7941 | 7882.7941 | 7882.7941 | 7882.7941 | 7882.7941 | 7882.7941 | 7882.7941 | E @ R (MWh) | 484.9884 | 1436.5143 | 1575.8954 | 2121.815 | 2107.3572 | 2239.8169 | 2800.0998 | 4830.5361 | 5845.0638 | 4882.227 | 7767.5974 | 6470.7827 | 7632.3697 | 8527.3051 | 8153.9599 | 8153.9599 | 8153.9599 | 8153.9599 | 8153.9599 | 8153.9599 | 8153.9599 | 8153.9599 | 8153.9599 | 8153.9599 | 8153.9599 | 8153.9599 | 8153.9599 | 8153.9599 | 8153.9599 | 8153.9599
Option 6 Winter POE50 W E @ R (MWh) N 1 | 70.9151 | 377.5814 | 431.3449 | 506.6161 | 621.7169 | 746.1337 | 997.5875 | 1844.8812 | 2426.7579 | 1992.6008 | 3502.0877 | 3823.1002 | 4063.2498 | 5300.8826 | 5517.9559 | 5517.9559 | 5517.9559 | 5517.9559 | 5517.9559 | 5517.9559 | 5517.9559 | 5517.9559 | 5517.9559 | 5517.9559 | 5517.9559 | 5517.9559 | 5517.9559 | 5517.9559 | 5517.9559 | 5517.9559 | Option 6 Winter POE10 W E @ R (MWh) N 1 | 145.4965 | 430.9543 | 472.7686 | 636.5445 | 632.2071 | 671.9451 | 840.03 | 1449.1608 | 1753.5191 | 1464.6681 | 2330.2792 | 1941.2348 | 2289.7109 | 2558.1915 | 2446.188 | 2446.188 | 2446.188 | 2446.188 | 2446.188 | 2446.188 | 2446.188 | 2446.188 | 2446.188 | 2446.188 | 2446.188 | 2446.188 | 2446.188 | 2446.188 | 2446.188 | 2446.188
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | 3.7913 | 5.0725 | 5.2012 | 5.1381 | 5.1981 | 5.2228 | 5.3018 | 5.4643 | 5.601 | 5.6639 | 5.6078 | 5.8429 | 5.8802 | 5.8361 | 5.9246 | 5.966 | 5.966 | 5.966 | 5.966 | 5.966 | 5.966 | 5.966 | 5.966 | 5.966 | 5.966 | 5.966 | 5.966 | 5.966 | 5.966 | 5.966 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
98% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
97% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 7.3137 | 8.7167 | 8.7555 | 8.7137 | 8.7244 | 8.8011 | 8.9563 | 9.2298 | 9.3723 | 9.4753 | 9.6313 | 9.8305 | 10.0714 | 10.1976 | 10.1567 | 10.1972 | 10.1972 | 10.1972 | 10.1972 | 10.1972 | 10.1972 | 10.1972 | 10.1972 | 10.1972 | 10.1972 | 10.1972 | 10.1972 | 10.1972 | 10.1972 | 10.1972
95% | 3.1884 | 4.4245 | 4.5487 | 4.4878 | 4.5457 | 4.5695 | 4.6457 | 4.8025 | 4.9344 | 4.9951 | 4.941 | 5.1678 | 5.2038 | 5.1612 | 5.2466 | 5.2865 | 5.2865 | 5.2865 | 5.2865 | 5.2865 | 5.2865 | 5.2865 | 5.2865 | 5.2865 | 5.2865 | 5.2865 | 5.2865 | 5.2865 | 5.2865 | 5.2865 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
90% | 56.8798 | 83.0826 | 85.7157 | 84.425 | 85.6522 | 86.1565 | 87.7726 | 91.0956 | 93.8911 | 95.1779 | 94.031 | 98.8398 | 99.6024 | 98.6998 | 100.5097 | 101.3563 | 101.3563 | 101.3563 | 101.3563 | 101.3563 | 101.3563 | 101.3563 | 101.3563 | 101.3563 | 101.3563 | 101.3563 | 101.3563 | 101.3563 | 101.3563 | 101.3563 |  | 6.2541 | 7.5852 | 7.6219 | 7.5823 | 7.5925 | 7.6652 | 7.8125 | 8.0719 | 8.2071 | 8.3048 | 8.4529 | 8.6418 | 8.8703 | 8.9901 | 8.9512 | 8.9897 | 8.9897 | 8.9897 | 8.9897 | 8.9897 | 8.9897 | 8.9897 | 8.9897 | 8.9897 | 8.9897 | 8.9897 | 8.9897 | 8.9897 | 8.9897 | 8.9897
85% | 143.1015 | 236.6138 | 246.0108 | 241.4046 | 245.7844 | 247.5839 | 253.3514 | 265.2106 | 275.1871 | 279.7796 | 275.6863 | 292.8479 | 295.5698 | 292.3486 | 298.8077 | 301.8288 | 301.8288 | 301.8288 | 301.8288 | 301.8288 | 301.8288 | 301.8288 | 301.8288 | 301.8288 | 301.8288 | 301.8288 | 301.8288 | 301.8288 | 301.8288 | 301.8288 |  | 5.1945 | 6.4536 | 6.4883 | 6.4509 | 6.4605 | 6.5292 | 6.6686 | 6.914 | 7.0419 | 7.1344 | 7.2744 | 7.4531 | 7.6693 | 7.7825 | 7.7458 | 7.7822 | 7.7822 | 7.7822 | 7.7822 | 7.7822 | 7.7822 | 7.7822 | 7.7822 | 7.7822 | 7.7822 | 7.7822 | 7.7822 | 7.7822 | 7.7822 | 7.7822
80% | 123.3778 | 275.2831 | 290.5479 | 283.0655 | 290.1801 | 293.1034 | 302.4723 | 321.7369 | 337.9431 | 345.4033 | 338.7541 | 366.632 | 371.0535 | 365.821 | 376.3134 | 381.2209 | 381.2209 | 381.2209 | 381.2209 | 381.2209 | 381.2209 | 381.2209 | 381.2209 | 381.2209 | 381.2209 | 381.2209 | 381.2209 | 381.2209 | 381.2209 | 381.2209 |  | 16.5393 | 21.2879 | 21.419 | 21.2777 | 21.314 | 21.5733 | 22.0988 | 23.0244 | 23.5066 | 23.8555 | 24.3835 | 25.0576 | 25.8728 | 26.3 | 26.1615 | 26.2988 | 26.2988 | 26.2988 | 26.2988 | 26.2988 | 26.2988 | 26.2988 | 26.2988 | 26.2988 | 26.2988 | 26.2988 | 26.2988 | 26.2988 | 26.2988 | 26.2988
75% | 29.3744 | 270.8222 | 297.9974 | 284.6768 | 297.3427 | 302.5468 | 319.2259 | 353.5216 | 382.3727 | 395.6538 | 383.8165 | 433.4462 | 441.3175 | 432.0023 | 450.6815 | 459.4181 | 459.4181 | 459.4181 | 459.4181 | 459.4181 | 459.4181 | 459.4181 | 459.4181 | 459.4181 | 459.4181 | 459.4181 | 459.4181 | 459.4181 | 459.4181 | 459.4181 |  | 6.1504 | 8.3808 | 8.4423 | 8.376 | 8.393 | 8.5148 | 8.7617 | 9.1964 | 9.4229 | 9.5868 | 9.8348 | 10.1514 | 10.5343 | 10.735 | 10.6699 | 10.7344 | 10.7344 | 10.7344 | 10.7344 | 10.7344 | 10.7344 | 10.7344 | 10.7344 | 10.7344 | 10.7344 | 10.7344 | 10.7344 | 10.7344 | 10.7344 | 10.7344
70% |  | 57.5195 | 79.6537 | 68.3739 | 79.0801 | 83.6941 | 99.3182 | 135.3947 | 169.7783 | 186.6822 | 171.5941 | 234.9517 | 245.0052 | 233.1075 | 256.9651 | 268.1238 | 268.1238 | 268.1238 | 268.1238 | 268.1238 | 268.1238 | 268.1238 | 268.1238 | 268.1238 | 268.1238 | 268.1238 | 268.1238 | 268.1238 | 268.1238 | 268.1238 |  | 12.0933 | 18.3528 | 18.5256 | 18.3393 | 18.3872 | 18.7291 | 19.4218 | 20.6418 | 21.2775 | 21.7374 | 22.4334 | 23.322 | 24.3966 | 24.9597 | 24.7771 | 24.9581 | 24.9581 | 24.9581 | 24.9581 | 24.9581 | 24.9581 | 24.9581 | 24.9581 | 24.9581 | 24.9581 | 24.9581 | 24.9581 | 24.9581 | 24.9581 | 24.9581
65% | [9 empty] | 0.18385 |  | 5.9063 | 8.0929 | 5.5421 | 11.1349 | 14.402 | 14.402 | 14.402 | 14.402 | 14.402 | 14.402 | 14.402 | 14.402 | 14.402 | 14.402 | 14.402 | 14.402 | 14.402 | 14.402 | 14.402 |  | 1.9118 | 3.8544 | 3.908 | 3.8503 | 3.8651 | 3.9712 | 4.1862 | 4.5648 | 4.7621 | 4.9048 | 5.1208 | 5.3966 | 5.7301 | 5.9048 | 5.8482 | 5.9043 | 5.9043 | 5.9043 | 5.9043 | 5.9043 | 5.9043 | 5.9043 | 5.9043 | 5.9043 | 5.9043 | 5.9043 | 5.9043 | 5.9043 | 5.9043 | 5.9043
60% | [31 empty] | 1.1137 | 10.3432 | 10.6659 | 10.318 | 10.4075 | 11.0459 | 12.3398 | 14.6185 | 15.8059 | 16.6649 | 17.965 | 19.6247 | 21.6318 | 22.6836 | 22.3426 | 22.6806 | 22.6806 | 22.6806 | 22.6806 | 22.6806 | 22.6806 | 22.6806 | 22.6806 | 22.6806 | 22.6806 | 22.6806 | 22.6806 | 22.6806 | 22.6806 | 22.6806
55% | [32 empty] | 1.4939 | 1.8164 | 1.47 | 1.5556 | 2.236 | 3.982 | 8.2254 | 11.0123 | 13.269 | 17.0614 | 22.5502 | 30.1319 | 34.5083 | 33.0596 | 34.4954 | 34.4954 | 34.4954 | 34.4954 | 34.4954 | 34.4954 | 34.4954 | 34.4954 | 34.4954 | 34.4954 | 34.4954 | 34.4954 | 34.4954 | 34.4954 | 34.4954
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 356.116 | 923.49 | 999.5787 | 961.856 | 997.7055 | 1012.6482 | 1061.367 | 1165.454 | 1257.0106 | 1300.4043 | 1261.6864 | 1429.1982 | 1457.0082 | 1424.1334 | 1490.5277 | 1522.2264 | 1522.2264 | 1522.2264 | 1522.2264 | 1522.2264 | 1522.2264 | 1522.2264 | 1522.2264 | 1522.2264 | 1522.2264 | 1522.2264 | 1522.2264 | 1522.2264 | 1522.2264 | 1522.2264 | E @ R (MWh) | 56.0049 | 85.6039 | 86.7664 | 85.5143 | 85.8329 | 88.1752 | 93.2854 | 103.442 | 109.3043 | 113.7835 | 120.9358 | 130.7077 | 143.4593 | 150.541 | 148.2156 | 150.5204 | 150.5204 | 150.5204 | 150.5204 | 150.5204 | 150.5204 | 150.5204 | 150.5204 | 150.5204 | 150.5204 | 150.5204 | 150.5204 | 150.5204 | 150.5204 | 150.5204
Option 6 Summer POE50 W E @ R (MWh) N 1 | 249.2812 | 646.443 | 699.7051 | 673.2992 | 698.3938 | 708.8538 | 742.9569 | 815.8178 | 879.9074 | 910.283 | 883.1805 | 1000.4387 | 1019.9057 | 996.8934 | 1043.3694 | 1065.5585 | 1065.5585 | 1065.5585 | 1065.5585 | 1065.5585 | 1065.5585 | 1065.5585 | 1065.5585 | 1065.5585 | 1065.5585 | 1065.5585 | 1065.5585 | 1065.5585 | 1065.5585 | 1065.5585 | Option 6 Summer POE10 W E @ R (MWh) N 1 | 16.8015 | 25.6812 | 26.0299 | 25.6543 | 25.7499 | 26.4526 | 27.9856 | 31.0326 | 32.7913 | 34.1351 | 36.2807 | 39.2123 | 43.0378 | 45.1623 | 44.4647 | 45.1561 | 45.1561 | 45.1561 | 45.1561 | 45.1561 | 45.1561 | 45.1561 | 45.1561 | 45.1561 | 45.1561 | 45.1561 | 45.1561 | 45.1561 | 45.1561 | 45.1561
Option 7 -
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | 2.094 | 3.4361 | 3.5785 | 3.7544 | 3.988 | 4.2094 | 4.5964 | 5.5698 | 6.0933 | 5.7114 | 6.8938 | 7.1069 | 7.26 | 7.9819 | 8.0994 | 8.0994 | 8.0994 | 8.0994 | 8.0994 | 8.0994 | 8.0994 | 8.0994 | 8.0994 | 8.0994 | 8.0994 | 8.0994 | 8.0994 | 8.0994 | 8.0994 | 8.0994 |  | 3.3275 | 4.6077 | 4.7402 | 5.1978 | 5.1866 | 5.2872 | 5.6807 | 6.8112 | 7.2777 | 6.8361 | 8.056 | 7.5438 | 8.0046 | 8.3367 | 8.2003 | 8.2003 | 8.2003 | 8.2003 | 8.2003 | 8.2003 | 8.2003 | 8.2003 | 8.2003 | 8.2003 | 8.2003 | 8.2003 | 8.2003 | 8.2003 | 8.2003 | 8.2003
98% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
97% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
95% | 6.572 | 11.7515 | 12.3007 | 12.9797 | 13.8812 | 14.7359 | 16.2295 | 19.9859 | 22.0064 | 20.5324 | 25.0957 | 25.9179 | 26.5089 | 29.2948 | 29.7482 | 29.7482 | 29.7482 | 29.7482 | 29.7482 | 29.7482 | 29.7482 | 29.7482 | 29.7482 | 29.7482 | 29.7482 | 29.7482 | 29.7482 | 29.7482 | 29.7482 | 29.7482 |  | 11.3322 | 16.2727 | 16.7844 | 18.5501 | 18.5071 | 18.8953 | 20.4139 | 24.7769 | 26.5773 | 24.873 | 29.5808 | 27.6042 | 29.3827 | 30.6643 | 30.1378 | 30.1378 | 30.1378 | 30.1378 | 30.1378 | 30.1378 | 30.1378 | 30.1378 | 30.1378 | 30.1378 | 30.1378 | 30.1378 | 30.1378 | 30.1378 | 30.1378 | 30.1378
90% | 28.6064 | 58.5505 | 61.7257 | 65.6512 | 70.8631 | 75.804 | 84.4388 | 106.1559 | 117.8368 | 109.3152 | 135.697 | 140.4502 | 143.8669 | 159.9726 | 162.5941 | 162.5941 | 162.5941 | 162.5941 | 162.5941 | 162.5941 | 162.5941 | 162.5941 | 162.5941 | 162.5941 | 162.5941 | 162.5941 | 162.5941 | 162.5941 | 162.5941 | 162.5941 |  | 56.1267 | 84.6891 | 87.6469 | 97.855 | 97.6062 | 99.8509 | 108.6302 | 133.8534 | 144.262 | 134.4095 | 161.6261 | 150.1991 | 160.4811 | 167.8904 | 164.8463 | 164.8463 | 164.8463 | 164.8463 | 164.8463 | 164.8463 | 164.8463 | 164.8463 | 164.8463 | 164.8463 | 164.8463 | 164.8463 | 164.8463 | 164.8463 | 164.8463 | 164.8463
85% | 58.0421 | 183.1465 | 196.4122 | 212.8125 | 234.5872 | 255.2303 | 291.3058 | 382.038 | 430.8403 | 395.2376 | 505.4587 | 525.3172 | 539.5922 | 606.8804 | 617.8328 | 617.8328 | 617.8328 | 617.8328 | 617.8328 | 617.8328 | 617.8328 | 617.8328 | 617.8328 | 617.8328 | 617.8328 | 617.8328 | 617.8328 | 617.8328 | 617.8328 | 617.8328 |  | 173.0196 | 292.3513 | 304.7091 | 347.3577 | 346.3183 | 355.6965 | 392.3758 | 497.7564 | 541.2429 | 500.0796 | 613.7889 | 566.0476 | 609.0048 | 639.9607 | 627.2425 | 627.2425 | 627.2425 | 627.2425 | 627.2425 | 627.2425 | 627.2425 | 627.2425 | 627.2425 | 627.2425 | 627.2425 | 627.2425 | 627.2425 | 627.2425 | 627.2425 | 627.2425
80% | 7.0161 | 180.8458 | 201.8492 | 227.8157 | 262.2914 | 294.9752 | 352.0931 | 495.7485 | 573.0166 | 516.6472 | 691.159 | 722.6008 | 745.2022 | 851.7388 | 869.0797 | 869.0797 | 869.0797 | 869.0797 | 869.0797 | 869.0797 | 869.0797 | 869.0797 | 869.0797 | 869.0797 | 869.0797 | 869.0797 | 869.0797 | 869.0797 | 869.0797 | 869.0797 |  | 164.8121 | 353.7485 | 373.3145 | 440.8395 | 439.1939 | 454.0422 | 512.1161 | 678.9641 | 747.8157 | 682.6423 | 862.6769 | 787.0886 | 855.1023 | 904.1144 | 883.9779 | 883.9779 | 883.9779 | 883.9779 | 883.9779 | 883.9779 | 883.9779 | 883.9779 | 883.9779 | 883.9779 | 883.9779 | 883.9779 | 883.9779 | 883.9779 | 883.9779 | 883.9779
75% |  | 107.1201 | 145.2583 | 193.2216 | 256.9023 | 317.2734 | 422.7773 | 688.1264 | 830.8501 | 726.7289 | 1049.0735 | 1107.1504 | 1148.898 | 1345.6842 | 1377.715 | 1377.715 | 1377.715 | 1377.715 | 1377.715 | 1377.715 | 1377.715 | 1377.715 | 1377.715 | 1377.715 | 1377.715 | 1377.715 | 1377.715 | 1377.715 | 1377.715 | 1377.715 |  | 81.2692 | 425.8349 | 461.9758 | 586.7028 | 583.663 | 611.0897 | 718.3593 | 1026.5481 | 1153.7254 | 1033.3422 | 1365.8883 | 1226.2674 | 1351.8971 | 1442.4284 | 1405.2338 | 1405.2338 | 1405.2338 | 1405.2338 | 1405.2338 | 1405.2338 | 1405.2338 | 1405.2338 | 1405.2338 | 1405.2338 | 1405.2338 | 1405.2338 | 1405.2338 | 1405.2338 | 1405.2338 | 1405.2338
70% |  |  | 1.3066 | 14.8126 | 54.6251 | 114.4437 | 266.6317 | 698.5515 | 930.8688 | 761.3864 | 1286.0803 | 1380.6144 | 1448.5689 | 1768.886 | 1821.0238 | 1821.0238 | 1821.0238 | 1821.0238 | 1821.0238 | 1821.0238 | 1821.0238 | 1821.0238 | 1821.0238 | 1821.0238 | 1821.0238 | 1821.0238 | 1821.0238 | 1821.0238 | 1821.0238 | 1821.0238 |  |  | 271.6087 | 330.4367 | 533.4601 | 528.5121 | 573.1557 | 747.7629 | 1249.4148 | 1456.4266 | 1260.4738 | 1801.773 | 1574.5062 | 1778.9989 | 1926.3605 | 1865.8173 | 1865.8173 | 1865.8173 | 1865.8173 | 1865.8173 | 1865.8173 | 1865.8173 | 1865.8173 | 1865.8173 | 1865.8173 | 1865.8173 | 1865.8173 | 1865.8173 | 1865.8173 | 1865.8173 | 1865.8173
65% | [6 empty] | 1.4477 | 265.9903 | 547.2297 | 339.6879 | 982.2084 | 1097.9714 | 1181.1858 | 1573.4342 | 1637.2802 | 1637.2802 | 1637.2802 | 1637.2802 | 1637.2802 | 1637.2802 | 1637.2802 | 1637.2802 | 1637.2802 | 1637.2802 | 1637.2802 | 1637.2802 | 1637.2802 | 1637.2802 | 1637.2802 | 1637.2802 |  |  | 1.9117 | 12.2059 | 113.2844 | 109.6564 | 144.4238 | 323.0448 | 937.3092 | 1190.8081 | 950.8517 | 1613.7064 | 1335.404 | 1585.8181 | 1766.2716 | 1692.1327 | 1692.1327 | 1692.1327 | 1692.1327 | 1692.1327 | 1692.1327 | 1692.1327 | 1692.1327 | 1692.1327 | 1692.1327 | 1692.1327 | 1692.1327 | 1692.1327 | 1692.1327 | 1692.1327 | 1692.1327
60% | [8 empty] | 43.0729 | 0.078688 | 371.8511 | 509.12 | 612.3349 | 1098.8592 | 1178.0505 | 1178.0505 | 1178.0505 | 1178.0505 | 1178.0505 | 1178.0505 | 1178.0505 | 1178.0505 | 1178.0505 | 1178.0505 | 1178.0505 | 1178.0505 | 1178.0505 | 1178.0505 | 1178.0505 | 1178.0505 | [8 empty] | 323.8953 | 624.2698 | 338.0342 | 1148.8107 | 803.6191 | 1114.2195 | 1338.0446 | 1246.0867 | 1246.0867 | 1246.0867 | 1246.0867 | 1246.0867 | 1246.0867 | 1246.0867 | 1246.0867 | 1246.0867 | 1246.0867 | 1246.0867 | 1246.0867 | 1246.0867 | 1246.0867 | 1246.0867 | 1246.0867
55% | [11 empty] | 0.48994 | 9.8575 | 206.4492 | 260.9948 | 260.9948 | 260.9948 | 260.9948 | 260.9948 | 260.9948 | 260.9948 | 260.9948 | 260.9948 | 260.9948 | 260.9948 | 260.9948 | 260.9948 | 260.9948 | 260.9948 | 260.9948 | [9 empty] | 11.6994 |  | 240.151 | 57.864 | 216.5553 | 389.3679 | 312.6478 | 312.6478 | 312.6478 | 312.6478 | 312.6478 | 312.6478 | 312.6478 | 312.6478 | 312.6478 | 312.6478 | 312.6478 | 312.6478 | 312.6478 | 312.6478 | 312.6478 | 312.6478
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 101.3074 | 539.402 | 616.207 | 723.7373 | 888.1669 | 1065.9052 | 1425.125 | 2635.5446 | 3466.7969 | 2846.5726 | 5002.9824 | 5461.5717 | 5804.6426 | 7572.6894 | 7882.7941 | 7882.7941 | 7882.7941 | 7882.7941 | 7882.7941 | 7882.7941 | 7882.7941 | 7882.7941 | 7882.7941 | 7882.7941 | 7882.7941 | 7882.7941 | 7882.7941 | 7882.7941 | 7882.7941 | 7882.7941 | E @ R (MWh) | 484.9884 | 1436.5143 | 1575.8954 | 2121.815 | 2107.3572 | 2239.8169 | 2800.0998 | 4830.5361 | 5845.0638 | 4882.227 | 7767.5974 | 6470.7827 | 7632.3697 | 8527.3051 | 8153.9599 | 8153.9599 | 8153.9599 | 8153.9599 | 8153.9599 | 8153.9599 | 8153.9599 | 8153.9599 | 8153.9599 | 8153.9599 | 8153.9599 | 8153.9599 | 8153.9599 | 8153.9599 | 8153.9599 | 8153.9599
Option 7 Winter POE50 W E @ R (MWh) N 1 | 70.9151 | 377.5814 | 431.3449 | 506.6161 | 621.7169 | 746.1337 | 997.5875 | 1844.8812 | 2426.7579 | 1992.6008 | 3502.0877 | 3823.1002 | 4063.2498 | 5300.8826 | 5517.9559 | 5517.9559 | 5517.9559 | 5517.9559 | 5517.9559 | 5517.9559 | 5517.9559 | 5517.9559 | 5517.9559 | 5517.9559 | 5517.9559 | 5517.9559 | 5517.9559 | 5517.9559 | 5517.9559 | 5517.9559 | Option 7 Winter POE10 W E @ R (MWh) N 1 | 145.4965 | 430.9543 | 472.7686 | 636.5445 | 632.2071 | 671.9451 | 840.03 | 1449.1608 | 1753.5191 | 1464.6681 | 2330.2792 | 1941.2348 | 2289.7109 | 2558.1915 | 2446.188 | 2446.188 | 2446.188 | 2446.188 | 2446.188 | 2446.188 | 2446.188 | 2446.188 | 2446.188 | 2446.188 | 2446.188 | 2446.188 | 2446.188 | 2446.188 | 2446.188 | 2446.188
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | 3.7913 | 5.0725 | 5.2012 | 5.1381 | 5.1981 | 5.2228 | 5.3018 | 5.4643 | 5.601 | 5.6639 | 5.6078 | 5.8429 | 5.8802 | 5.8361 | 5.9246 | 5.966 | 5.966 | 5.966 | 5.966 | 5.966 | 5.966 | 5.966 | 5.966 | 5.966 | 5.966 | 5.966 | 5.966 | 5.966 | 5.966 | 5.966 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
98% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
97% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 7.3137 | 8.7167 | 8.7555 | 8.7137 | 8.7244 | 8.8011 | 8.9563 | 9.2298 | 9.3723 | 9.4753 | 9.6313 | 9.8305 | 10.0714 | 10.1976 | 10.1567 | 10.1972 | 10.1972 | 10.1972 | 10.1972 | 10.1972 | 10.1972 | 10.1972 | 10.1972 | 10.1972 | 10.1972 | 10.1972 | 10.1972 | 10.1972 | 10.1972 | 10.1972
95% | 3.1884 | 4.4245 | 4.5487 | 4.4878 | 4.5457 | 4.5695 | 4.6457 | 4.8025 | 4.9344 | 4.9951 | 4.941 | 5.1678 | 5.2038 | 5.1612 | 5.2466 | 5.2865 | 5.2865 | 5.2865 | 5.2865 | 5.2865 | 5.2865 | 5.2865 | 5.2865 | 5.2865 | 5.2865 | 5.2865 | 5.2865 | 5.2865 | 5.2865 | 5.2865 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
90% | 56.8798 | 83.0826 | 85.7157 | 84.425 | 85.6522 | 86.1565 | 87.7726 | 91.0956 | 93.8911 | 95.1779 | 94.031 | 98.8398 | 99.6024 | 98.6998 | 100.5097 | 101.3563 | 101.3563 | 101.3563 | 101.3563 | 101.3563 | 101.3563 | 101.3563 | 101.3563 | 101.3563 | 101.3563 | 101.3563 | 101.3563 | 101.3563 | 101.3563 | 101.3563 |  | 6.2541 | 7.5852 | 7.6219 | 7.5823 | 7.5925 | 7.6652 | 7.8125 | 8.0719 | 8.2071 | 8.3048 | 8.4529 | 8.6418 | 8.8703 | 8.9901 | 8.9512 | 8.9897 | 8.9897 | 8.9897 | 8.9897 | 8.9897 | 8.9897 | 8.9897 | 8.9897 | 8.9897 | 8.9897 | 8.9897 | 8.9897 | 8.9897 | 8.9897 | 8.9897
85% | 143.1015 | 236.6138 | 246.0108 | 241.4046 | 245.7844 | 247.5839 | 253.3514 | 265.2106 | 275.1871 | 279.7796 | 275.6863 | 292.8479 | 295.5698 | 292.3486 | 298.8077 | 301.8288 | 301.8288 | 301.8288 | 301.8288 | 301.8288 | 301.8288 | 301.8288 | 301.8288 | 301.8288 | 301.8288 | 301.8288 | 301.8288 | 301.8288 | 301.8288 | 301.8288 |  | 5.1945 | 6.4536 | 6.4883 | 6.4509 | 6.4605 | 6.5292 | 6.6686 | 6.914 | 7.0419 | 7.1344 | 7.2744 | 7.4531 | 7.6693 | 7.7825 | 7.7458 | 7.7822 | 7.7822 | 7.7822 | 7.7822 | 7.7822 | 7.7822 | 7.7822 | 7.7822 | 7.7822 | 7.7822 | 7.7822 | 7.7822 | 7.7822 | 7.7822 | 7.7822
80% | 123.3778 | 275.2831 | 290.5479 | 283.0655 | 290.1801 | 293.1034 | 302.4723 | 321.7369 | 337.9431 | 345.4033 | 338.7541 | 366.632 | 371.0535 | 365.821 | 376.3134 | 381.2209 | 381.2209 | 381.2209 | 381.2209 | 381.2209 | 381.2209 | 381.2209 | 381.2209 | 381.2209 | 381.2209 | 381.2209 | 381.2209 | 381.2209 | 381.2209 | 381.2209 |  | 16.5393 | 21.2879 | 21.419 | 21.2777 | 21.314 | 21.5733 | 22.0988 | 23.0244 | 23.5066 | 23.8555 | 24.3835 | 25.0576 | 25.8728 | 26.3 | 26.1615 | 26.2988 | 26.2988 | 26.2988 | 26.2988 | 26.2988 | 26.2988 | 26.2988 | 26.2988 | 26.2988 | 26.2988 | 26.2988 | 26.2988 | 26.2988 | 26.2988 | 26.2988
75% | 29.3744 | 270.8222 | 297.9974 | 284.6768 | 297.3427 | 302.5468 | 319.2259 | 353.5216 | 382.3727 | 395.6538 | 383.8165 | 433.4462 | 441.3175 | 432.0023 | 450.6815 | 459.4181 | 459.4181 | 459.4181 | 459.4181 | 459.4181 | 459.4181 | 459.4181 | 459.4181 | 459.4181 | 459.4181 | 459.4181 | 459.4181 | 459.4181 | 459.4181 | 459.4181 |  | 6.1504 | 8.3808 | 8.4423 | 8.376 | 8.393 | 8.5148 | 8.7617 | 9.1964 | 9.4229 | 9.5868 | 9.8348 | 10.1514 | 10.5343 | 10.735 | 10.6699 | 10.7344 | 10.7344 | 10.7344 | 10.7344 | 10.7344 | 10.7344 | 10.7344 | 10.7344 | 10.7344 | 10.7344 | 10.7344 | 10.7344 | 10.7344 | 10.7344 | 10.7344
70% |  | 57.5195 | 79.6537 | 68.3739 | 79.0801 | 83.6941 | 99.3182 | 135.3947 | 169.7783 | 186.6822 | 171.5941 | 234.9517 | 245.0052 | 233.1075 | 256.9651 | 268.1238 | 268.1238 | 268.1238 | 268.1238 | 268.1238 | 268.1238 | 268.1238 | 268.1238 | 268.1238 | 268.1238 | 268.1238 | 268.1238 | 268.1238 | 268.1238 | 268.1238 |  | 12.0933 | 18.3528 | 18.5256 | 18.3393 | 18.3872 | 18.7291 | 19.4218 | 20.6418 | 21.2775 | 21.7374 | 22.4334 | 23.322 | 24.3966 | 24.9597 | 24.7771 | 24.9581 | 24.9581 | 24.9581 | 24.9581 | 24.9581 | 24.9581 | 24.9581 | 24.9581 | 24.9581 | 24.9581 | 24.9581 | 24.9581 | 24.9581 | 24.9581 | 24.9581
65% | [9 empty] | 0.18385 |  | 5.9063 | 8.0929 | 5.5421 | 11.1349 | 14.402 | 14.402 | 14.402 | 14.402 | 14.402 | 14.402 | 14.402 | 14.402 | 14.402 | 14.402 | 14.402 | 14.402 | 14.402 | 14.402 | 14.402 |  | 1.9118 | 3.8544 | 3.908 | 3.8503 | 3.8651 | 3.9712 | 4.1862 | 4.5648 | 4.7621 | 4.9048 | 5.1208 | 5.3966 | 5.7301 | 5.9048 | 5.8482 | 5.9043 | 5.9043 | 5.9043 | 5.9043 | 5.9043 | 5.9043 | 5.9043 | 5.9043 | 5.9043 | 5.9043 | 5.9043 | 5.9043 | 5.9043 | 5.9043 | 5.9043
60% | [31 empty] | 1.1137 | 10.3432 | 10.6659 | 10.318 | 10.4075 | 11.0459 | 12.3398 | 14.6185 | 15.8059 | 16.6649 | 17.965 | 19.6247 | 21.6318 | 22.6836 | 22.3426 | 22.6806 | 22.6806 | 22.6806 | 22.6806 | 22.6806 | 22.6806 | 22.6806 | 22.6806 | 22.6806 | 22.6806 | 22.6806 | 22.6806 | 22.6806 | 22.6806 | 22.6806
55% | [32 empty] | 1.4939 | 1.8164 | 1.47 | 1.5556 | 2.236 | 3.982 | 8.2254 | 11.0123 | 13.269 | 17.0614 | 22.5502 | 30.1319 | 34.5083 | 33.0596 | 34.4954 | 34.4954 | 34.4954 | 34.4954 | 34.4954 | 34.4954 | 34.4954 | 34.4954 | 34.4954 | 34.4954 | 34.4954 | 34.4954 | 34.4954 | 34.4954 | 34.4954
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 356.116 | 923.49 | 999.5787 | 961.856 | 997.7055 | 1012.6482 | 1061.367 | 1165.454 | 1257.0106 | 1300.4043 | 1261.6864 | 1429.1982 | 1457.0082 | 1424.1334 | 1490.5277 | 1522.2264 | 1522.2264 | 1522.2264 | 1522.2264 | 1522.2264 | 1522.2264 | 1522.2264 | 1522.2264 | 1522.2264 | 1522.2264 | 1522.2264 | 1522.2264 | 1522.2264 | 1522.2264 | 1522.2264 | E @ R (MWh) | 56.0049 | 85.6039 | 86.7664 | 85.5143 | 85.8329 | 88.1752 | 93.2854 | 103.442 | 109.3043 | 113.7835 | 120.9358 | 130.7077 | 143.4593 | 150.541 | 148.2156 | 150.5204 | 150.5204 | 150.5204 | 150.5204 | 150.5204 | 150.5204 | 150.5204 | 150.5204 | 150.5204 | 150.5204 | 150.5204 | 150.5204 | 150.5204 | 150.5204 | 150.5204
Option 7 Summer POE50 W E @ R (MWh) N 1 | 249.2812 | 646.443 | 699.7051 | 673.2992 | 698.3938 | 708.8538 | 742.9569 | 815.8178 | 879.9074 | 910.283 | 883.1805 | 1000.4387 | 1019.9057 | 996.8934 | 1043.3694 | 1065.5585 | 1065.5585 | 1065.5585 | 1065.5585 | 1065.5585 | 1065.5585 | 1065.5585 | 1065.5585 | 1065.5585 | 1065.5585 | 1065.5585 | 1065.5585 | 1065.5585 | 1065.5585 | 1065.5585 | Option 7 Summer POE10 W E @ R (MWh) N 1 | 16.8015 | 25.6812 | 26.0299 | 25.6543 | 25.7499 | 26.4526 | 27.9856 | 31.0326 | 32.7913 | 34.1351 | 36.2807 | 39.2123 | 43.0378 | 45.1623 | 44.4647 | 45.1561 | 45.1561 | 45.1561 | 45.1561 | 45.1561 | 45.1561 | 45.1561 | 45.1561 | 45.1561 | 45.1561 | 45.1561 | 45.1561 | 45.1561 | 45.1561 | 45.1561
Option 8 -
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | 2.094 | 3.4361 | 3.5785 | 3.7544 | 3.988 | 4.2094 | 4.5964 | 5.5698 | 6.0933 | 5.7114 | 6.8938 | 7.1069 | 7.26 | 7.9819 | 8.0994 | 8.0994 | 8.0994 | 8.0994 | 8.0994 | 8.0994 | 8.0994 | 8.0994 | 8.0994 | 8.0994 | 8.0994 | 8.0994 | 8.0994 | 8.0994 | 8.0994 | 8.0994 |  | 3.3275 | 4.6077 | 4.7402 | 5.1978 | 5.1866 | 5.2872 | 5.6807 | 6.8112 | 7.2777 | 6.8361 | 8.056 | 7.5438 | 8.0046 | 8.3367 | 8.2003 | 8.2003 | 8.2003 | 8.2003 | 8.2003 | 8.2003 | 8.2003 | 8.2003 | 8.2003 | 8.2003 | 8.2003 | 8.2003 | 8.2003 | 8.2003 | 8.2003 | 8.2003
98% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
97% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
95% | 6.572 | 11.7515 | 12.3007 | 12.9797 | 13.8812 | 14.7359 | 16.2295 | 19.9859 | 22.0064 | 20.5324 | 25.0957 | 25.9179 | 26.5089 | 29.2948 | 29.7482 | 29.7482 | 29.7482 | 29.7482 | 29.7482 | 29.7482 | 29.7482 | 29.7482 | 29.7482 | 29.7482 | 29.7482 | 29.7482 | 29.7482 | 29.7482 | 29.7482 | 29.7482 |  | 11.3322 | 16.2727 | 16.7844 | 18.5501 | 18.5071 | 18.8953 | 20.4139 | 24.7769 | 26.5773 | 24.873 | 29.5808 | 27.6042 | 29.3827 | 30.6643 | 30.1378 | 30.1378 | 30.1378 | 30.1378 | 30.1378 | 30.1378 | 30.1378 | 30.1378 | 30.1378 | 30.1378 | 30.1378 | 30.1378 | 30.1378 | 30.1378 | 30.1378 | 30.1378
90% | 28.6064 | 58.5505 | 61.7257 | 65.6512 | 70.8631 | 75.804 | 84.4388 | 106.1559 | 117.8368 | 109.3152 | 135.697 | 140.4502 | 143.8669 | 159.9726 | 162.5941 | 162.5941 | 162.5941 | 162.5941 | 162.5941 | 162.5941 | 162.5941 | 162.5941 | 162.5941 | 162.5941 | 162.5941 | 162.5941 | 162.5941 | 162.5941 | 162.5941 | 162.5941 |  | 56.1267 | 84.6891 | 87.6469 | 97.855 | 97.6062 | 99.8509 | 108.6302 | 133.8534 | 144.262 | 134.4095 | 161.6261 | 150.1991 | 160.4811 | 167.8904 | 164.8463 | 164.8463 | 164.8463 | 164.8463 | 164.8463 | 164.8463 | 164.8463 | 164.8463 | 164.8463 | 164.8463 | 164.8463 | 164.8463 | 164.8463 | 164.8463 | 164.8463 | 164.8463
85% | 58.0421 | 183.1465 | 196.4122 | 212.8125 | 234.5872 | 255.2303 | 291.3058 | 382.038 | 430.8403 | 395.2376 | 505.4587 | 525.3172 | 539.5922 | 606.8804 | 617.8328 | 617.8328 | 617.8328 | 617.8328 | 617.8328 | 617.8328 | 617.8328 | 617.8328 | 617.8328 | 617.8328 | 617.8328 | 617.8328 | 617.8328 | 617.8328 | 617.8328 | 617.8328 |  | 173.0196 | 292.3513 | 304.7091 | 347.3577 | 346.3183 | 355.6965 | 392.3758 | 497.7564 | 541.2429 | 500.0796 | 613.7889 | 566.0476 | 609.0048 | 639.9607 | 627.2425 | 627.2425 | 627.2425 | 627.2425 | 627.2425 | 627.2425 | 627.2425 | 627.2425 | 627.2425 | 627.2425 | 627.2425 | 627.2425 | 627.2425 | 627.2425 | 627.2425 | 627.2425
80% | 7.0161 | 180.8458 | 201.8492 | 227.8157 | 262.2914 | 294.9752 | 352.0931 | 495.7485 | 573.0166 | 516.6472 | 691.159 | 722.6008 | 745.2022 | 851.7388 | 869.0797 | 869.0797 | 869.0797 | 869.0797 | 869.0797 | 869.0797 | 869.0797 | 869.0797 | 869.0797 | 869.0797 | 869.0797 | 869.0797 | 869.0797 | 869.0797 | 869.0797 | 869.0797 |  | 164.8121 | 353.7485 | 373.3145 | 440.8395 | 439.1939 | 454.0422 | 512.1161 | 678.9641 | 747.8157 | 682.6423 | 862.6769 | 787.0886 | 855.1023 | 904.1144 | 883.9779 | 883.9779 | 883.9779 | 883.9779 | 883.9779 | 883.9779 | 883.9779 | 883.9779 | 883.9779 | 883.9779 | 883.9779 | 883.9779 | 883.9779 | 883.9779 | 883.9779 | 883.9779
75% |  | 107.1201 | 145.2583 | 193.2216 | 256.9023 | 317.2734 | 422.7773 | 688.1264 | 830.8501 | 726.7289 | 1049.0735 | 1107.1504 | 1148.898 | 1345.6842 | 1377.715 | 1377.715 | 1377.715 | 1377.715 | 1377.715 | 1377.715 | 1377.715 | 1377.715 | 1377.715 | 1377.715 | 1377.715 | 1377.715 | 1377.715 | 1377.715 | 1377.715 | 1377.715 |  | 81.2692 | 425.8349 | 461.9758 | 586.7028 | 583.663 | 611.0897 | 718.3593 | 1026.5481 | 1153.7254 | 1033.3422 | 1365.8883 | 1226.2674 | 1351.8971 | 1442.4284 | 1405.2338 | 1405.2338 | 1405.2338 | 1405.2338 | 1405.2338 | 1405.2338 | 1405.2338 | 1405.2338 | 1405.2338 | 1405.2338 | 1405.2338 | 1405.2338 | 1405.2338 | 1405.2338 | 1405.2338 | 1405.2338
70% |  |  | 1.3066 | 14.8126 | 54.6251 | 114.4437 | 266.6317 | 698.5515 | 930.8688 | 761.3864 | 1286.0803 | 1380.6144 | 1448.5689 | 1768.886 | 1821.0238 | 1821.0238 | 1821.0238 | 1821.0238 | 1821.0238 | 1821.0238 | 1821.0238 | 1821.0238 | 1821.0238 | 1821.0238 | 1821.0238 | 1821.0238 | 1821.0238 | 1821.0238 | 1821.0238 | 1821.0238 |  |  | 271.6087 | 330.4367 | 533.4601 | 528.5121 | 573.1557 | 747.7629 | 1249.4148 | 1456.4266 | 1260.4738 | 1801.773 | 1574.5062 | 1778.9989 | 1926.3605 | 1865.8173 | 1865.8173 | 1865.8173 | 1865.8173 | 1865.8173 | 1865.8173 | 1865.8173 | 1865.8173 | 1865.8173 | 1865.8173 | 1865.8173 | 1865.8173 | 1865.8173 | 1865.8173 | 1865.8173 | 1865.8173
65% | [6 empty] | 1.4477 | 265.9903 | 547.2297 | 339.6879 | 982.2084 | 1097.9714 | 1181.1858 | 1573.4342 | 1637.2802 | 1637.2802 | 1637.2802 | 1637.2802 | 1637.2802 | 1637.2802 | 1637.2802 | 1637.2802 | 1637.2802 | 1637.2802 | 1637.2802 | 1637.2802 | 1637.2802 | 1637.2802 | 1637.2802 | 1637.2802 |  |  | 1.9117 | 12.2059 | 113.2844 | 109.6564 | 144.4238 | 323.0448 | 937.3092 | 1190.8081 | 950.8517 | 1613.7064 | 1335.404 | 1585.8181 | 1766.2716 | 1692.1327 | 1692.1327 | 1692.1327 | 1692.1327 | 1692.1327 | 1692.1327 | 1692.1327 | 1692.1327 | 1692.1327 | 1692.1327 | 1692.1327 | 1692.1327 | 1692.1327 | 1692.1327 | 1692.1327 | 1692.1327
60% | [8 empty] | 43.0729 | 0.078688 | 371.8511 | 509.12 | 612.3349 | 1098.8592 | 1178.0505 | 1178.0505 | 1178.0505 | 1178.0505 | 1178.0505 | 1178.0505 | 1178.0505 | 1178.0505 | 1178.0505 | 1178.0505 | 1178.0505 | 1178.0505 | 1178.0505 | 1178.0505 | 1178.0505 | 1178.0505 | [8 empty] | 323.8953 | 624.2698 | 338.0342 | 1148.8107 | 803.6191 | 1114.2195 | 1338.0446 | 1246.0867 | 1246.0867 | 1246.0867 | 1246.0867 | 1246.0867 | 1246.0867 | 1246.0867 | 1246.0867 | 1246.0867 | 1246.0867 | 1246.0867 | 1246.0867 | 1246.0867 | 1246.0867 | 1246.0867 | 1246.0867
55% | [11 empty] | 0.48994 | 9.8575 | 206.4492 | 260.9948 | 260.9948 | 260.9948 | 260.9948 | 260.9948 | 260.9948 | 260.9948 | 260.9948 | 260.9948 | 260.9948 | 260.9948 | 260.9948 | 260.9948 | 260.9948 | 260.9948 | 260.9948 | [9 empty] | 11.6994 |  | 240.151 | 57.864 | 216.5553 | 389.3679 | 312.6478 | 312.6478 | 312.6478 | 312.6478 | 312.6478 | 312.6478 | 312.6478 | 312.6478 | 312.6478 | 312.6478 | 312.6478 | 312.6478 | 312.6478 | 312.6478 | 312.6478 | 312.6478
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 101.3074 | 539.402 | 616.207 | 723.7373 | 888.1669 | 1065.9052 | 1425.125 | 2635.5446 | 3466.7969 | 2846.5726 | 5002.9824 | 5461.5717 | 5804.6426 | 7572.6894 | 7882.7941 | 7882.7941 | 7882.7941 | 7882.7941 | 7882.7941 | 7882.7941 | 7882.7941 | 7882.7941 | 7882.7941 | 7882.7941 | 7882.7941 | 7882.7941 | 7882.7941 | 7882.7941 | 7882.7941 | 7882.7941 | E @ R (MWh) | 484.9884 | 1436.5143 | 1575.8954 | 2121.815 | 2107.3572 | 2239.8169 | 2800.0998 | 4830.5361 | 5845.0638 | 4882.227 | 7767.5974 | 6470.7827 | 7632.3697 | 8527.3051 | 8153.9599 | 8153.9599 | 8153.9599 | 8153.9599 | 8153.9599 | 8153.9599 | 8153.9599 | 8153.9599 | 8153.9599 | 8153.9599 | 8153.9599 | 8153.9599 | 8153.9599 | 8153.9599 | 8153.9599 | 8153.9599
Option 8 Winter POE50 W E @ R (MWh) N 1 | 70.9151 | 377.5814 | 431.3449 | 506.6161 | 621.7169 | 746.1337 | 997.5875 | 1844.8812 | 2426.7579 | 1992.6008 | 3502.0877 | 3823.1002 | 4063.2498 | 5300.8826 | 5517.9559 | 5517.9559 | 5517.9559 | 5517.9559 | 5517.9559 | 5517.9559 | 5517.9559 | 5517.9559 | 5517.9559 | 5517.9559 | 5517.9559 | 5517.9559 | 5517.9559 | 5517.9559 | 5517.9559 | 5517.9559 | Option 8 Winter POE10 W E @ R (MWh) N 1 | 145.4965 | 430.9543 | 472.7686 | 636.5445 | 632.2071 | 671.9451 | 840.03 | 1449.1608 | 1753.5191 | 1464.6681 | 2330.2792 | 1941.2348 | 2289.7109 | 2558.1915 | 2446.188 | 2446.188 | 2446.188 | 2446.188 | 2446.188 | 2446.188 | 2446.188 | 2446.188 | 2446.188 | 2446.188 | 2446.188 | 2446.188 | 2446.188 | 2446.188 | 2446.188 | 2446.188
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | 3.7913 | 5.0725 | 5.2012 | 5.1381 | 5.1981 | 5.2228 | 5.3018 | 5.4643 | 5.601 | 5.6639 | 5.6078 | 5.8429 | 5.8802 | 5.8361 | 5.9246 | 5.966 | 5.966 | 5.966 | 5.966 | 5.966 | 5.966 | 5.966 | 5.966 | 5.966 | 5.966 | 5.966 | 5.966 | 5.966 | 5.966 | 5.966 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
98% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
97% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 7.3137 | 8.7167 | 8.7555 | 8.7137 | 8.7244 | 8.8011 | 8.9563 | 9.2298 | 9.3723 | 9.4753 | 9.6313 | 9.8305 | 10.0714 | 10.1976 | 10.1567 | 10.1972 | 10.1972 | 10.1972 | 10.1972 | 10.1972 | 10.1972 | 10.1972 | 10.1972 | 10.1972 | 10.1972 | 10.1972 | 10.1972 | 10.1972 | 10.1972 | 10.1972
95% | 3.1884 | 4.4245 | 4.5487 | 4.4878 | 4.5457 | 4.5695 | 4.6457 | 4.8025 | 4.9344 | 4.9951 | 4.941 | 5.1678 | 5.2038 | 5.1612 | 5.2466 | 5.2865 | 5.2865 | 5.2865 | 5.2865 | 5.2865 | 5.2865 | 5.2865 | 5.2865 | 5.2865 | 5.2865 | 5.2865 | 5.2865 | 5.2865 | 5.2865 | 5.2865 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
90% | 56.8798 | 83.0826 | 85.7157 | 84.425 | 85.6522 | 86.1565 | 87.7726 | 91.0956 | 93.8911 | 95.1779 | 94.031 | 98.8398 | 99.6024 | 98.6998 | 100.5097 | 101.3563 | 101.3563 | 101.3563 | 101.3563 | 101.3563 | 101.3563 | 101.3563 | 101.3563 | 101.3563 | 101.3563 | 101.3563 | 101.3563 | 101.3563 | 101.3563 | 101.3563 |  | 6.2541 | 7.5852 | 7.6219 | 7.5823 | 7.5925 | 7.6652 | 7.8125 | 8.0719 | 8.2071 | 8.3048 | 8.4529 | 8.6418 | 8.8703 | 8.9901 | 8.9512 | 8.9897 | 8.9897 | 8.9897 | 8.9897 | 8.9897 | 8.9897 | 8.9897 | 8.9897 | 8.9897 | 8.9897 | 8.9897 | 8.9897 | 8.9897 | 8.9897 | 8.9897
85% | 143.1015 | 236.6138 | 246.0108 | 241.4046 | 245.7844 | 247.5839 | 253.3514 | 265.2106 | 275.1871 | 279.7796 | 275.6863 | 292.8479 | 295.5698 | 292.3486 | 298.8077 | 301.8288 | 301.8288 | 301.8288 | 301.8288 | 301.8288 | 301.8288 | 301.8288 | 301.8288 | 301.8288 | 301.8288 | 301.8288 | 301.8288 | 301.8288 | 301.8288 | 301.8288 |  | 5.1945 | 6.4536 | 6.4883 | 6.4509 | 6.4605 | 6.5292 | 6.6686 | 6.914 | 7.0419 | 7.1344 | 7.2744 | 7.4531 | 7.6693 | 7.7825 | 7.7458 | 7.7822 | 7.7822 | 7.7822 | 7.7822 | 7.7822 | 7.7822 | 7.7822 | 7.7822 | 7.7822 | 7.7822 | 7.7822 | 7.7822 | 7.7822 | 7.7822 | 7.7822
80% | 123.3778 | 275.2831 | 290.5479 | 283.0655 | 290.1801 | 293.1034 | 302.4723 | 321.7369 | 337.9431 | 345.4033 | 338.7541 | 366.632 | 371.0535 | 365.821 | 376.3134 | 381.2209 | 381.2209 | 381.2209 | 381.2209 | 381.2209 | 381.2209 | 381.2209 | 381.2209 | 381.2209 | 381.2209 | 381.2209 | 381.2209 | 381.2209 | 381.2209 | 381.2209 |  | 16.5393 | 21.2879 | 21.419 | 21.2777 | 21.314 | 21.5733 | 22.0988 | 23.0244 | 23.5066 | 23.8555 | 24.3835 | 25.0576 | 25.8728 | 26.3 | 26.1615 | 26.2988 | 26.2988 | 26.2988 | 26.2988 | 26.2988 | 26.2988 | 26.2988 | 26.2988 | 26.2988 | 26.2988 | 26.2988 | 26.2988 | 26.2988 | 26.2988 | 26.2988
75% | 29.3744 | 270.8222 | 297.9974 | 284.6768 | 297.3427 | 302.5468 | 319.2259 | 353.5216 | 382.3727 | 395.6538 | 383.8165 | 433.4462 | 441.3175 | 432.0023 | 450.6815 | 459.4181 | 459.4181 | 459.4181 | 459.4181 | 459.4181 | 459.4181 | 459.4181 | 459.4181 | 459.4181 | 459.4181 | 459.4181 | 459.4181 | 459.4181 | 459.4181 | 459.4181 |  | 6.1504 | 8.3808 | 8.4423 | 8.376 | 8.393 | 8.5148 | 8.7617 | 9.1964 | 9.4229 | 9.5868 | 9.8348 | 10.1514 | 10.5343 | 10.735 | 10.6699 | 10.7344 | 10.7344 | 10.7344 | 10.7344 | 10.7344 | 10.7344 | 10.7344 | 10.7344 | 10.7344 | 10.7344 | 10.7344 | 10.7344 | 10.7344 | 10.7344 | 10.7344
70% |  | 57.5195 | 79.6537 | 68.3739 | 79.0801 | 83.6941 | 99.3182 | 135.3947 | 169.7783 | 186.6822 | 171.5941 | 234.9517 | 245.0052 | 233.1075 | 256.9651 | 268.1238 | 268.1238 | 268.1238 | 268.1238 | 268.1238 | 268.1238 | 268.1238 | 268.1238 | 268.1238 | 268.1238 | 268.1238 | 268.1238 | 268.1238 | 268.1238 | 268.1238 |  | 12.0933 | 18.3528 | 18.5256 | 18.3393 | 18.3872 | 18.7291 | 19.4218 | 20.6418 | 21.2775 | 21.7374 | 22.4334 | 23.322 | 24.3966 | 24.9597 | 24.7771 | 24.9581 | 24.9581 | 24.9581 | 24.9581 | 24.9581 | 24.9581 | 24.9581 | 24.9581 | 24.9581 | 24.9581 | 24.9581 | 24.9581 | 24.9581 | 24.9581 | 24.9581
65% | [9 empty] | 0.18385 |  | 5.9063 | 8.0929 | 5.5421 | 11.1349 | 14.402 | 14.402 | 14.402 | 14.402 | 14.402 | 14.402 | 14.402 | 14.402 | 14.402 | 14.402 | 14.402 | 14.402 | 14.402 | 14.402 | 14.402 |  | 1.9118 | 3.8544 | 3.908 | 3.8503 | 3.8651 | 3.9712 | 4.1862 | 4.5648 | 4.7621 | 4.9048 | 5.1208 | 5.3966 | 5.7301 | 5.9048 | 5.8482 | 5.9043 | 5.9043 | 5.9043 | 5.9043 | 5.9043 | 5.9043 | 5.9043 | 5.9043 | 5.9043 | 5.9043 | 5.9043 | 5.9043 | 5.9043 | 5.9043 | 5.9043
60% | [31 empty] | 1.1137 | 10.3432 | 10.6659 | 10.318 | 10.4075 | 11.0459 | 12.3398 | 14.6185 | 15.8059 | 16.6649 | 17.965 | 19.6247 | 21.6318 | 22.6836 | 22.3426 | 22.6806 | 22.6806 | 22.6806 | 22.6806 | 22.6806 | 22.6806 | 22.6806 | 22.6806 | 22.6806 | 22.6806 | 22.6806 | 22.6806 | 22.6806 | 22.6806 | 22.6806
55% | [32 empty] | 1.4939 | 1.8164 | 1.47 | 1.5556 | 2.236 | 3.982 | 8.2254 | 11.0123 | 13.269 | 17.0614 | 22.5502 | 30.1319 | 34.5083 | 33.0596 | 34.4954 | 34.4954 | 34.4954 | 34.4954 | 34.4954 | 34.4954 | 34.4954 | 34.4954 | 34.4954 | 34.4954 | 34.4954 | 34.4954 | 34.4954 | 34.4954 | 34.4954
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 356.116 | 923.49 | 999.5787 | 961.856 | 997.7055 | 1012.6482 | 1061.367 | 1165.454 | 1257.0106 | 1300.4043 | 1261.6864 | 1429.1982 | 1457.0082 | 1424.1334 | 1490.5277 | 1522.2264 | 1522.2264 | 1522.2264 | 1522.2264 | 1522.2264 | 1522.2264 | 1522.2264 | 1522.2264 | 1522.2264 | 1522.2264 | 1522.2264 | 1522.2264 | 1522.2264 | 1522.2264 | 1522.2264 | E @ R (MWh) | 56.0049 | 85.6039 | 86.7664 | 85.5143 | 85.8329 | 88.1752 | 93.2854 | 103.442 | 109.3043 | 113.7835 | 120.9358 | 130.7077 | 143.4593 | 150.541 | 148.2156 | 150.5204 | 150.5204 | 150.5204 | 150.5204 | 150.5204 | 150.5204 | 150.5204 | 150.5204 | 150.5204 | 150.5204 | 150.5204 | 150.5204 | 150.5204 | 150.5204 | 150.5204
Option 8 Summer POE50 W E @ R (MWh) N 1 | 249.2812 | 646.443 | 699.7051 | 673.2992 | 698.3938 | 708.8538 | 742.9569 | 815.8178 | 879.9074 | 910.283 | 883.1805 | 1000.4387 | 1019.9057 | 996.8934 | 1043.3694 | 1065.5585 | 1065.5585 | 1065.5585 | 1065.5585 | 1065.5585 | 1065.5585 | 1065.5585 | 1065.5585 | 1065.5585 | 1065.5585 | 1065.5585 | 1065.5585 | 1065.5585 | 1065.5585 | 1065.5585 | Option 8 Summer POE10 W E @ R (MWh) N 1 | 16.8015 | 25.6812 | 26.0299 | 25.6543 | 25.7499 | 26.4526 | 27.9856 | 31.0326 | 32.7913 | 34.1351 | 36.2807 | 39.2123 | 43.0378 | 45.1623 | 44.4647 | 45.1561 | 45.1561 | 45.1561 | 45.1561 | 45.1561 | 45.1561 | 45.1561 | 45.1561 | 45.1561 | 45.1561 | 45.1561 | 45.1561 | 45.1561 | 45.1561 | 45.1561

## POF N,N-1 & N-2 Risk
N-2 Method 1
| Asset name | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Tx 1 Pof | DS-WGI-TRNFMR-9000004493 | 1.976% | 1.976% | 2.058% | 2.142% | 2.227% | 2.315% | 2.405% | 2.496% | 2.59% | 2.686% | 2.783% | 2.883% | 2.985% | 3.089% | 3.195% | 3.195% | 3.195% | 3.195% | 3.195% | 3.195% | 3.195% | 3.195% | 3.195% | 3.195% | 3.195% | 3.195% | 3.195% | 3.195% | 3.195% | 3.195%
Tx 2 Pof | DS-WGI-TRNFMR-9000003147 | 0.9218% | 0.9218% | 0.9742% | 1.028% | 1.084% | 1.142% | 1.201% | 1.262% | 1.325% | 1.39% | 1.457% | 1.525% | 1.596% | 1.668% | 1.742% | 1.742% | 1.742% | 1.742% | 1.742% | 1.742% | 1.742% | 1.742% | 1.742% | 1.742% | 1.742% | 1.742% | 1.742% | 1.742% | 1.742% | 1.742%
Tx 3 Pof | DS-WGI-TRNFMR-9000007146 | 0.9218% | 0.9218% | 0.9742% | 1.028% | 1.084% | 1.142% | 1.201% | 1.262% | 1.325% | 1.39% | 1.457% | 1.525% | 1.596% | 1.668% | 1.742% | 1.742% | 1.742% | 1.742% | 1.742% | 1.742% | 1.742% | 1.742% | 1.742% | 1.742% | 1.742% | 1.742% | 1.742% | 1.742% | 1.742% | 1.742%
Tx 4 Pof
Tx 5 Pof
Total Tx Pof |  | 3.82% | 3.82% | 4.006% | 4.198% | 4.396% | 4.599% | 4.807% | 5.021% | 5.241% | 5.466% | 5.697% | 5.934% | 6.177% | 6.425% | 6.679% | 6.679% | 6.679% | 6.679% | 6.679% | 6.679% | 6.679% | 6.679% | 6.679% | 6.679% | 6.679% | 6.679% | 6.679% | 6.679% | 6.679% | 6.679%
N-1 Risk |  | 1.474% | 1.474% | 1.546% | 1.62% | 1.696% | 1.774% | 1.855% | 1.937% | 2.022% | 2.109% | 2.198% | 2.289% | 2.383% | 2.479% | 2.577% | 2.577% | 2.577% | 2.577% | 2.577% | 2.577% | 2.577% | 2.577% | 2.577% | 2.577% | 2.577% | 2.577% | 2.577% | 2.577% | 2.577% | 2.577%
N-2 Risk |  | 0.01053% | 0.01053% | 0.01162% | 0.0128% | 0.01408% | 0.01545% | 0.01692% | 0.01851% | 0.02021% | 0.02204% | 0.02399% | 0.02607% | 0.0283% | 0.03068% | 0.03321% | 0.03321% | 0.03321% | 0.03321% | 0.03321% | 0.03321% | 0.03321% | 0.03321% | 0.03321% | 0.03321% | 0.03321% | 0.03321% | 0.03321% | 0.03321% | 0.03321% | 0.03321%
N Risk |  | 98.52% | 98.52% | 98.44% | 98.37% | 98.29% | 98.21% | 98.13% | 98.04% | 97.96% | 97.87% | 97.78% | 97.68% | 97.59% | 97.49% | 97.39% | 97.39% | 97.39% | 97.39% | 97.39% | 97.39% | 97.39% | 97.39% | 97.39% | 97.39% | 97.39% | 97.39% | 97.39% | 97.39% | 97.39% | 97.39%

## Summary
Involuntary load shedding (NER 5.17.1(c)(4)(ii))
Option 1 - Do Nothing | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Weighted Energy @ Risk (MWh) under N Conditions | 0 | 0.4026 | 0.42271 | 0.40042 | 0.4057 | 0.4463 | 0.53436 | 1.0132 | 2.2471 | 1.2142 | 9.0211 | 5.9248 | 10.9958 | 27.67 | 28.3593 | 28.397 | 28.397 | 28.397 | 28.397 | 28.397 | 28.397 | 28.397 | 28.397 | 28.397 | 28.397 | 28.397 | 28.397 | 28.397 | 28.397 | 28.397
Weighted Energy @ Risk (MWh) under N-1 Conditions | 8.8221 | 26.637 | 30.7098 | 35.98 | 40.3631 | 45.7812 | 57.5282 | 93.9277 | 120.0566 | 108.8782 | 171.7421 | 180.7783 | 204.7543 | 254.4826 | 269.177 | 269.9612 | 269.9612 | 269.9612 | 269.9612 | 269.9612 | 269.9612 | 269.9612 | 269.9612 | 269.9612 | 269.9612 | 269.9612 | 269.9612 | 269.9612 | 269.9612 | 269.9612
Weighted Energy @ Risk (MWh) under N-2 Conditions | 4.4227 | 5.786 | 6.5405 | 7.3752 | 8.2759 | 9.2773 | 10.6353 | 12.9659 | 14.9351 | 15.7801 | 19.006 | 20.9096 | 23.2341 | 26.3815 | 28.7509 | 28.8111 | 28.8111 | 28.8111 | 28.8111 | 28.8111 | 28.8111 | 28.8111 | 28.8111 | 28.8111 | 28.8111 | 28.8111 | 28.8111 | 28.8111 | 28.8111 | 28.8111
Total EUE (MWh) - Option 1 | 13.2448 | 32.8256 | 37.6731 | 43.7557 | 49.0447 | 55.5048 | 68.6979 | 107.9068 | 137.2388 | 125.8725 | 199.7693 | 207.6126 | 238.9842 | 308.5341 | 326.2872 | 327.1692 | 327.1692 | 327.1692 | 327.1692 | 327.1692 | 327.1692 | 327.1692 | 327.1692 | 327.1692 | 327.1692 | 327.1692 | 327.1692 | 327.1692 | 327.1692 | 327.1692
Cost of EUE ($) - Option 1 | 563965.373 | 1397725.1532 | 1604130.1584 | 1863128.5674 | 2088336.779 | 2363410.6349 | 2925174.5028 | 4594700.3671 | 5843666.0853 | 5359686.4739 | 8506230.3148 | 8840203.7268 | 10176011.8056 | 13137465.6371 | 13893400.5332 | 13930955.0496 | 13930955.0496 | 13930955.0496 | 13930955.0496 | 13930955.0496 | 13930955.0496 | 13930955.0496 | 13930955.0496 | 13930955.0496 | 13930955.0496 | 13930955.0496 | 13930955.0496 | 13930955.0496 | 13930955.0496 | 13930955.0496
Hours at Risk pA. (Hrs) (N) | 0.2972 | 1.0535 | 1.0535 | 1.0535 | 1.0535 | 1.0535 | 1.0535 | 9.3751 | 40.8781 | 9.3751 | 94.1576 | 41.2563 | 94.1576 | 94.1576 | 94.1576 | 94.1576 | 94.1576 | 94.1576 | 94.1576 | 94.1576 | 94.1576 | 94.1576 | 94.1576 | 94.1576 | 94.1576 | 94.1576 | 94.1576 | 94.1576 | 94.1576 | 94.1576
Option 2 - Replace 3 x 10/13.5 MVA Tx with 3 x 20/33 MVA Tx | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Weighted Energy @ Risk (MWh) under N Conditions | 0 | 0.4026 | 0.42271 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Weighted Energy @ Risk (MWh) under N-1 Conditions | 8.8188 | 26.637 | 30.7098 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Weighted Energy @ Risk (MWh) under N-2 Conditions | 4.4227 | 5.786 | 6.5405 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3439e-05 | 2.3528e-05 | 9.7881e-05 | 0.00035616 | 0.00037652 | 0.00038184 | 0.00038184 | 0.00038184 | 0.00038184 | 0.00038184 | 0.00038184 | 0.00038184 | 0.00038184 | 0.00038184 | 0.00038184 | 0.00038184 | 0.00038184 | 0.00038184 | 0.00038184 | 0.00038184
Total EUE (MWh) - Option 2 | 13.2414 | 32.8256 | 37.6731 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3439e-05 | 2.3528e-05 | 9.7881e-05 | 0.00035616 | 0.00037652 | 0.00038184 | 0.00038184 | 0.00038184 | 0.00038184 | 0.00038184 | 0.00038184 | 0.00038184 | 0.00038184 | 0.00038184 | 0.00038184 | 0.00038184 | 0.00038184 | 0.00038184 | 0.00038184 | 0.00038184
Cost of EUE ($) - Option 2 | 563823.7405 | 1397725.1532 | 1604130.1584 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.2754 | 1.0018 | 4.1678 | 15.1654 | 16.0324 | 16.259 | 16.259 | 16.259 | 16.259 | 16.259 | 16.259 | 16.259 | 16.259 | 16.259 | 16.259 | 16.259 | 16.259 | 16.259 | 16.259 | 16.259
Option 3 - Replace 1 x 10/13.5 MVA Tx with 1 x 20/33 MVA Tx | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Weighted Energy @ Risk (MWh) under N Conditions | 0 | 0.4026 | 0.42271 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Weighted Energy @ Risk (MWh) under N-1 Conditions | 8.8188 | 26.637 | 30.7098 | 0.039531 | 0.041373 | 0.047588 | 0.079089 | 0.45822 | 0.98852 | 0.55746 | 2.9764 | 2.7017 | 3.9269 | 7.3517 | 7.8902 | 7.8939 | 7.8939 | 7.8939 | 7.8939 | 7.8939 | 7.8939 | 7.8939 | 7.8939 | 7.8939 | 7.8939 | 7.8939 | 7.8939 | 7.8939 | 7.8939 | 7.8939
Weighted Energy @ Risk (MWh) under N-2 Conditions | 4.4227 | 5.786 | 6.5405 | 0.55439 | 0.64754 | 0.76066 | 0.96883 | 1.5248 | 1.9681 | 1.9147 | 2.9259 | 3.2203 | 3.7467 | 4.7039 | 5.1695 | 5.1839 | 5.1839 | 5.1839 | 5.1839 | 5.1839 | 5.1839 | 5.1839 | 5.1839 | 5.1839 | 5.1839 | 5.1839 | 5.1839 | 5.1839 | 5.1839 | 5.1839
Total EUE (MWh) - Option 3 | 13.2414 | 32.8256 | 37.6731 | 0.59392 | 0.68891 | 0.80824 | 1.0479 | 1.9831 | 2.9566 | 2.4722 | 5.9023 | 5.9219 | 7.6736 | 12.0556 | 13.0597 | 13.0778 | 13.0778 | 13.0778 | 13.0778 | 13.0778 | 13.0778 | 13.0778 | 13.0778 | 13.0778 | 13.0778 | 13.0778 | 13.0778 | 13.0778 | 13.0778 | 13.0778
Cost of EUE ($) - Option 3 | 563823.7405 | 1397725.1532 | 1604130.1584 | 25289.2882 | 29334.094 | 34415.2356 | 44620.7576 | 84439.2497 | 125894.9484 | 105265.4422 | 251319.4755 | 252156.4122 | 326744.2549 | 513332.1486 | 556086.3363 | 556855.7413 | 556855.7413 | 556855.7413 | 556855.7413 | 556855.7413 | 556855.7413 | 556855.7413 | 556855.7413 | 556855.7413 | 556855.7413 | 556855.7413 | 556855.7413 | 556855.7413 | 556855.7413 | 556855.7413
Option 4 - Construct 2x 20/33MVA zone substation in Inverloch | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Weighted Energy @ Risk (MWh) under N Conditions | 0 | 0.4026 | 0.42271 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Weighted Energy @ Risk (MWh) under N-1 Conditions | 8.8188 | 26.637 | 30.7098 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Weighted Energy @ Risk (MWh) under N-2 Conditions | 4.4227 | 5.786 | 6.5405 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total EUE (MWh) - Option 4 | 13.2414 | 32.8256 | 37.6731 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cost of EUE ($) - Option 4 | 563823.7405 | 1397725.1532 | 1604130.1584 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 - Contract network support services to defer network investment | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Weighted Energy @ Risk (MWh) under N Conditions | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0039779 | 0.023579 | 0.2856 | 0.1613 | 0.39482 | 1.1284 | 1.091 | 1.1086 | 1.1086 | 1.1086 | 1.1086 | 1.1086 | 1.1086 | 1.1086 | 1.1086 | 1.1086 | 1.1086 | 1.1086 | 1.1086 | 1.1086 | 1.1086 | 1.1086
Weighted Energy @ Risk (MWh) under N-1 Conditions | 1.6049 | 7.4448 | 8.9551 | 11.201 | 12.7445 | 14.8449 | 20.2054 | 40.1599 | 55.5405 | 46.9377 | 88.2216 | 91.333 | 106.1947 | 140.8323 | 149.6514 | 150.0502 | 150.0502 | 150.0502 | 150.0502 | 150.0502 | 150.0502 | 150.0502 | 150.0502 | 150.0502 | 150.0502 | 150.0502 | 150.0502 | 150.0502 | 150.0502 | 150.0502
Weighted Energy @ Risk (MWh) under N-2 Conditions | 3.1339 | 4.2945 | 4.8813 | 5.5409 | 6.2471 | 7.0311 | 8.131 | 10.1334 | 11.7931 | 12.3529 | 15.1946 | 16.7129 | 18.6132 | 21.3181 | 23.2727 | 23.3289 | 23.3289 | 23.3289 | 23.3289 | 23.3289 | 23.3289 | 23.3289 | 23.3289 | 23.3289 | 23.3289 | 23.3289 | 23.3289 | 23.3289 | 23.3289 | 23.3289
Total EUE (MWh) - Option 5 | 4.7389 | 11.7393 | 13.8364 | 16.742 | 18.9916 | 21.876 | 28.3364 | 50.2933 | 67.3376 | 59.3142 | 103.7018 | 108.2072 | 125.2027 | 163.2788 | 174.0151 | 174.4877 | 174.4877 | 174.4877 | 174.4877 | 174.4877 | 174.4877 | 174.4877 | 174.4877 | 174.4877 | 174.4877 | 174.4877 | 174.4877 | 174.4877 | 174.4877 | 174.4877
Cost of EUE ($) - Option 5 | 201781.6093 | 499863.5521 | 589157.2871 | 712877.5434 | 808666.9373 | 931484.1897 | 1206572.5337 | 2141502.9575 | 2867252.6098 | 2525613.3148 | 4415651.2752 | 4607492.4484 | 5331166.6493 | 6952457.2023 | 7409612.9322 | 7429735.7934 | 7429735.7934 | 7429735.7934 | 7429735.7934 | 7429735.7934 | 7429735.7934 | 7429735.7934 | 7429735.7934 | 7429735.7934 | 7429735.7934 | 7429735.7934 | 7429735.7934 | 7429735.7934 | 7429735.7934 | 7429735.7934
Option 6 - | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Weighted Energy @ Risk (MWh) under N Conditions | 0 | 0.4026 | 0.42271 | 0.40042 | 0.4057 | 0.4463 | 0.53436 | 1.0132 | 2.2471 | 1.2142 | 9.0211 | 5.9248 | 10.9958 | 27.67 | 28.3593 | 28.397 | 28.397 | 28.397 | 28.397 | 28.397 | 28.397 | 28.397 | 28.397 | 28.397 | 28.397 | 28.397 | 28.397 | 28.397 | 28.397 | 28.397
Weighted Energy @ Risk (MWh) under N-1 Conditions | 8.8188 | 26.637 | 30.7098 | 35.98 | 40.3631 | 45.7812 | 57.5282 | 93.9277 | 120.0566 | 108.8782 | 171.7421 | 180.7783 | 204.7543 | 254.4826 | 269.177 | 269.9612 | 269.9612 | 269.9612 | 269.9612 | 269.9612 | 269.9612 | 269.9612 | 269.9612 | 269.9612 | 269.9612 | 269.9612 | 269.9612 | 269.9612 | 269.9612 | 269.9612
Weighted Energy @ Risk (MWh) under N-2 Conditions | 4.4227 | 5.786 | 6.5405 | 7.3752 | 8.2759 | 9.2773 | 10.6353 | 12.9659 | 14.9351 | 15.7801 | 19.006 | 20.9096 | 23.2341 | 26.3815 | 28.7509 | 28.8111 | 28.8111 | 28.8111 | 28.8111 | 28.8111 | 28.8111 | 28.8111 | 28.8111 | 28.8111 | 28.8111 | 28.8111 | 28.8111 | 28.8111 | 28.8111 | 28.8111
Total EUE (MWh) - Option 6 | 13.2414 | 32.8256 | 37.6731 | 43.7557 | 49.0447 | 55.5048 | 68.6979 | 107.9068 | 137.2388 | 125.8725 | 199.7693 | 207.6126 | 238.9842 | 308.5341 | 326.2872 | 327.1692 | 327.1692 | 327.1692 | 327.1692 | 327.1692 | 327.1692 | 327.1692 | 327.1692 | 327.1692 | 327.1692 | 327.1692 | 327.1692 | 327.1692 | 327.1692 | 327.1692
Cost of EUE ($) - Option 6 | 563823.7405 | 1397725.1532 | 1604130.1584 | 1863128.5674 | 2088336.779 | 2363410.6349 | 2925174.5028 | 4594700.3671 | 5843666.0853 | 5359686.4739 | 8506230.3148 | 8840203.7268 | 10176011.8056 | 13137465.6371 | 13893400.5332 | 13930955.0496 | 13930955.0496 | 13930955.0496 | 13930955.0496 | 13930955.0496 | 13930955.0496 | 13930955.0496 | 13930955.0496 | 13930955.0496 | 13930955.0496 | 13930955.0496 | 13930955.0496 | 13930955.0496 | 13930955.0496 | 13930955.0496
Option 7 - | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Weighted Energy @ Risk (MWh) under N Conditions | 0 | 0.4026 | 0.42271 | 0.40042 | 0.4057 | 0.4463 | 0.53436 | 1.0132 | 2.2471 | 1.2142 | 9.0211 | 5.9248 | 10.9958 | 27.67 | 28.3593 | 28.397 | 28.397 | 28.397 | 28.397 | 28.397 | 28.397 | 28.397 | 28.397 | 28.397 | 28.397 | 28.397 | 28.397 | 28.397 | 28.397 | 28.397
Weighted Energy @ Risk (MWh) under N-1 Conditions | 8.8188 | 26.637 | 30.7098 | 35.98 | 40.3631 | 45.7812 | 57.5282 | 93.9277 | 120.0566 | 108.8782 | 171.7421 | 180.7783 | 204.7543 | 254.4826 | 269.177 | 269.9612 | 269.9612 | 269.9612 | 269.9612 | 269.9612 | 269.9612 | 269.9612 | 269.9612 | 269.9612 | 269.9612 | 269.9612 | 269.9612 | 269.9612 | 269.9612 | 269.9612
Weighted Energy @ Risk (MWh) under N-2 Conditions | 4.4227 | 5.786 | 6.5405 | 7.3752 | 8.2759 | 9.2773 | 10.6353 | 12.9659 | 14.9351 | 15.7801 | 19.006 | 20.9096 | 23.2341 | 26.3815 | 28.7509 | 28.8111 | 28.8111 | 28.8111 | 28.8111 | 28.8111 | 28.8111 | 28.8111 | 28.8111 | 28.8111 | 28.8111 | 28.8111 | 28.8111 | 28.8111 | 28.8111 | 28.8111
Total EUE (MWh) - Option 7 | 13.2414 | 32.8256 | 37.6731 | 43.7557 | 49.0447 | 55.5048 | 68.6979 | 107.9068 | 137.2388 | 125.8725 | 199.7693 | 207.6126 | 238.9842 | 308.5341 | 326.2872 | 327.1692 | 327.1692 | 327.1692 | 327.1692 | 327.1692 | 327.1692 | 327.1692 | 327.1692 | 327.1692 | 327.1692 | 327.1692 | 327.1692 | 327.1692 | 327.1692 | 327.1692
Cost of EUE ($) - Option 7 | 563823.7405 | 1397725.1532 | 1604130.1584 | 1863128.5674 | 2088336.779 | 2363410.6349 | 2925174.5028 | 4594700.3671 | 5843666.0853 | 5359686.4739 | 8506230.3148 | 8840203.7268 | 10176011.8056 | 13137465.6371 | 13893400.5332 | 13930955.0496 | 13930955.0496 | 13930955.0496 | 13930955.0496 | 13930955.0496 | 13930955.0496 | 13930955.0496 | 13930955.0496 | 13930955.0496 | 13930955.0496 | 13930955.0496 | 13930955.0496 | 13930955.0496 | 13930955.0496 | 13930955.0496
Option 8 - | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Weighted Energy @ Risk (MWh) under N Conditions | 0 | 0.4026 | 0.42271 | 0.40042 | 0.4057 | 0.4463 | 0.53436 | 1.0132 | 2.2471 | 1.2142 | 9.0211 | 5.9248 | 10.9958 | 27.67 | 28.3593 | 28.397 | 28.397 | 28.397 | 28.397 | 28.397 | 28.397 | 28.397 | 28.397 | 28.397 | 28.397 | 28.397 | 28.397 | 28.397 | 28.397 | 28.397
Weighted Energy @ Risk (MWh) under N-1 Conditions | 8.8188 | 26.637 | 30.7098 | 35.98 | 40.3631 | 45.7812 | 57.5282 | 93.9277 | 120.0566 | 108.8782 | 171.7421 | 180.7783 | 204.7543 | 254.4826 | 269.177 | 269.9612 | 269.9612 | 269.9612 | 269.9612 | 269.9612 | 269.9612 | 269.9612 | 269.9612 | 269.9612 | 269.9612 | 269.9612 | 269.9612 | 269.9612 | 269.9612 | 269.9612
Weighted Energy @ Risk (MWh) under N-2 Conditions | 4.4227 | 5.786 | 6.5405 | 7.3752 | 8.2759 | 9.2773 | 10.6353 | 12.9659 | 14.9351 | 15.7801 | 19.006 | 20.9096 | 23.2341 | 26.3815 | 28.7509 | 28.8111 | 28.8111 | 28.8111 | 28.8111 | 28.8111 | 28.8111 | 28.8111 | 28.8111 | 28.8111 | 28.8111 | 28.8111 | 28.8111 | 28.8111 | 28.8111 | 28.8111
Total EUE (MWh) - Option 8 | 13.2414 | 32.8256 | 37.6731 | 43.7557 | 49.0447 | 55.5048 | 68.6979 | 107.9068 | 137.2388 | 125.8725 | 199.7693 | 207.6126 | 238.9842 | 308.5341 | 326.2872 | 327.1692 | 327.1692 | 327.1692 | 327.1692 | 327.1692 | 327.1692 | 327.1692 | 327.1692 | 327.1692 | 327.1692 | 327.1692 | 327.1692 | 327.1692 | 327.1692 | 327.1692
Cost of EUE ($) - Option 8 | 563823.7405 | 1397725.1532 | 1604130.1584 | 1863128.5674 | 2088336.779 | 2363410.6349 | 2925174.5028 | 4594700.3671 | 5843666.0853 | 5359686.4739 | 8506230.3148 | 8840203.7268 | 10176011.8056 | 13137465.6371 | 13893400.5332 | 13930955.0496 | 13930955.0496 | 13930955.0496 | 13930955.0496 | 13930955.0496 | 13930955.0496 | 13930955.0496 | 13930955.0496 | 13930955.0496 | 13930955.0496 | 13930955.0496 | 13930955.0496 | 13930955.0496 | 13930955.0496 | 13930955.0496

## E@R N-2
Option 1 - Do Nothing
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | 7.4585 | 8.8006 | 8.9429 | 9.1188 | 9.3524 | 9.5739 | 9.9609 | 10.9342 | 11.4578 | 11.0758 | 12.2583 | 12.4713 | 12.6244 | 13.3463 | 13.4638 | 13.4638 | 13.4638 | 13.4638 | 13.4638 | 13.4638 | 13.4638 | 13.4638 | 13.4638 | 13.4638 | 13.4638 | 13.4638 | 13.4638 | 13.4638 | 13.4638 | 13.4638 |  | 8.6919 | 9.9721 | 10.1047 | 10.5622 | 10.551 | 10.6516 | 11.0451 | 12.1756 | 12.6421 | 12.2006 | 13.4204 | 12.9082 | 13.3691 | 13.7012 | 13.5647 | 13.5647 | 13.5647 | 13.5647 | 13.5647 | 13.5647 | 13.5647 | 13.5647 | 13.5647 | 13.5647 | 13.5647 | 13.5647 | 13.5647 | 13.5647 | 13.5647 | 13.5647
98% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
97% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
95% | 28.0297 | 33.2092 | 33.7584 | 34.4374 | 35.339 | 36.1936 | 37.6872 | 41.4437 | 43.4642 | 41.9901 | 46.5535 | 47.3756 | 47.9667 | 50.7525 | 51.2059 | 51.2059 | 51.2059 | 51.2059 | 51.2059 | 51.2059 | 51.2059 | 51.2059 | 51.2059 | 51.2059 | 51.2059 | 51.2059 | 51.2059 | 51.2059 | 51.2059 | 51.2059 |  | 32.79 | 37.7305 | 38.2421 | 40.0078 | 39.9648 | 40.3531 | 41.8717 | 46.2346 | 48.035 | 46.3308 | 51.0385 | 49.062 | 50.8404 | 52.1221 | 51.5955 | 51.5955 | 51.5955 | 51.5955 | 51.5955 | 51.5955 | 51.5955 | 51.5955 | 51.5955 | 51.5955 | 51.5955 | 51.5955 | 51.5955 | 51.5955 | 51.5955 | 51.5955
90% | 157.3528 | 187.297 | 190.4721 | 194.3976 | 199.6095 | 204.5504 | 213.1852 | 234.9023 | 246.5833 | 238.0616 | 264.4434 | 269.1966 | 272.6134 | 288.719 | 291.3405 | 291.3405 | 291.3405 | 291.3405 | 291.3405 | 291.3405 | 291.3405 | 291.3405 | 291.3405 | 291.3405 | 291.3405 | 291.3405 | 291.3405 | 291.3405 | 291.3405 | 291.3405 |  | 184.8731 | 213.4355 | 216.3934 | 226.6014 | 226.3526 | 228.5973 | 237.3766 | 262.5998 | 273.0084 | 263.1559 | 290.3726 | 278.9455 | 289.2275 | 296.6368 | 293.5927 | 293.5927 | 293.5927 | 293.5927 | 293.5927 | 293.5927 | 293.5927 | 293.5927 | 293.5927 | 293.5927 | 293.5927 | 293.5927 | 293.5927 | 293.5927 | 293.5927 | 293.5927
85% | 626.672 | 751.7764 | 765.0422 | 781.4425 | 803.2172 | 823.8602 | 859.9357 | 950.668 | 999.4703 | 963.8676 | 1074.0886 | 1093.9472 | 1108.2222 | 1175.5104 | 1186.4628 | 1186.4628 | 1186.4628 | 1186.4628 | 1186.4628 | 1186.4628 | 1186.4628 | 1186.4628 | 1186.4628 | 1186.4628 | 1186.4628 | 1186.4628 | 1186.4628 | 1186.4628 | 1186.4628 | 1186.4628 |  | 741.6496 | 860.9812 | 873.3391 | 915.9877 | 914.9483 | 924.3264 | 961.0057 | 1066.3864 | 1109.8728 | 1068.7096 | 1182.4188 | 1134.6775 | 1177.6348 | 1208.5906 | 1195.8725 | 1195.8725 | 1195.8725 | 1195.8725 | 1195.8725 | 1195.8725 | 1195.8725 | 1195.8725 | 1195.8725 | 1195.8725 | 1195.8725 | 1195.8725 | 1195.8725 | 1195.8725 | 1195.8725 | 1195.8725
80% | 937.6386 | 1135.7149 | 1156.7184 | 1182.6849 | 1217.1605 | 1249.8444 | 1306.9623 | 1450.6177 | 1527.8858 | 1471.5164 | 1646.0281 | 1677.4699 | 1700.0714 | 1806.608 | 1823.9489 | 1823.9489 | 1823.9489 | 1823.9489 | 1823.9489 | 1823.9489 | 1823.9489 | 1823.9489 | 1823.9489 | 1823.9489 | 1823.9489 | 1823.9489 | 1823.9489 | 1823.9489 | 1823.9489 | 1823.9489 |  | 1119.6813 | 1308.6177 | 1328.1837 | 1395.7087 | 1394.063 | 1408.9114 | 1466.9853 | 1633.8333 | 1702.6848 | 1637.5115 | 1817.5461 | 1741.9578 | 1809.9715 | 1858.9836 | 1838.8471 | 1838.8471 | 1838.8471 | 1838.8471 | 1838.8471 | 1838.8471 | 1838.8471 | 1838.8471 | 1838.8471 | 1838.8471 | 1838.8471 | 1838.8471 | 1838.8471 | 1838.8471 | 1838.8471 | 1838.8471
75% | 1618.1428 | 1984.0141 | 2022.8101 | 2070.7733 | 2134.4541 | 2194.8252 | 2300.329 | 2565.6781 | 2708.4018 | 2604.2807 | 2926.6253 | 2984.7021 | 3026.4498 | 3223.236 | 3255.2667 | 3255.2667 | 3255.2667 | 3255.2667 | 3255.2667 | 3255.2667 | 3255.2667 | 3255.2667 | 3255.2667 | 3255.2667 | 3255.2667 | 3255.2667 | 3255.2667 | 3255.2667 | 3255.2667 | 3255.2667 |  | 1954.3979 | 2303.3867 | 2339.5275 | 2464.2546 | 2461.2148 | 2488.6415 | 2595.9111 | 2904.0999 | 3031.2772 | 2910.894 | 3243.44 | 3103.8192 | 3229.4488 | 3319.9801 | 3282.7856 | 3282.7856 | 3282.7856 | 3282.7856 | 3282.7856 | 3282.7856 | 3282.7856 | 3282.7856 | 3282.7856 | 3282.7856 | 3282.7856 | 3282.7856 | 3282.7856 | 3282.7856 | 3282.7856 | 3282.7856
70% | 2423.1485 | 3018.6926 | 3081.8425 | 3159.9143 | 3263.5701 | 3361.8387 | 3533.5717 | 3965.4915 | 4197.8089 | 4028.3265 | 4553.0204 | 4647.5545 | 4715.5089 | 5035.8261 | 5087.9638 | 5087.9638 | 5087.9638 | 5087.9638 | 5087.9638 | 5087.9638 | 5087.9638 | 5087.9638 | 5087.9638 | 5087.9638 | 5087.9638 | 5087.9638 | 5087.9638 | 5087.9638 | 5087.9638 | 5087.9638 |  | 2970.4851 | 3538.5488 | 3597.3768 | 3800.4002 | 3795.4522 | 3840.0957 | 4014.703 | 4516.3548 | 4723.3667 | 4527.4139 | 5068.713 | 4841.4463 | 5045.9389 | 5193.3006 | 5132.7574 | 5132.7574 | 5132.7574 | 5132.7574 | 5132.7574 | 5132.7574 | 5132.7574 | 5132.7574 | 5132.7574 | 5132.7574 | 5132.7574 | 5132.7574 | 5132.7574 | 5132.7574 | 5132.7574 | 5132.7574
65% | 2670.9583 | 3400.2393 | 3477.5703 | 3573.1741 | 3700.1072 | 3820.4432 | 4030.7411 | 4559.6539 | 4844.1411 | 4636.5993 | 5279.1198 | 5394.8827 | 5478.0971 | 5870.3455 | 5934.1915 | 5934.1915 | 5934.1915 | 5934.1915 | 5934.1915 | 5934.1915 | 5934.1915 | 5934.1915 | 5934.1915 | 5934.1915 | 5934.1915 | 5934.1915 | 5934.1915 | 5934.1915 | 5934.1915 | 5934.1915 |  | 3341.2062 | 4036.8358 | 4108.8743 | 4357.4892 | 4351.43 | 4406.0989 | 4619.9164 | 5234.2205 | 5487.7194 | 5247.763 | 5910.6177 | 5632.3154 | 5882.7294 | 6063.1829 | 5989.044 | 5989.044 | 5989.044 | 5989.044 | 5989.044 | 5989.044 | 5989.044 | 5989.044 | 5989.044 | 5989.044 | 5989.044 | 5989.044 | 5989.044 | 5989.044 | 5989.044 | 5989.044
60% | 2886.5439 | 3791.1059 | 3887.0233 | 4005.6052 | 4163.0464 | 4312.3049 | 4573.1473 | 5229.1832 | 5582.0462 | 5324.6222 | 6121.571 | 6265.1573 | 6368.3721 | 6854.8965 | 6934.0877 | 6934.0877 | 6934.0877 | 6934.0877 | 6934.0877 | 6934.0877 | 6934.0877 | 6934.0877 | 6934.0877 | 6934.0877 | 6934.0877 | 6934.0877 | 6934.0877 | 6934.0877 | 6934.0877 | 6934.0877 |  | 3717.8843 | 4580.7069 | 4670.0597 | 4978.4286 | 4970.9132 | 5038.7216 | 5303.9296 | 6065.8803 | 6380.3071 | 6082.6777 | 6904.848 | 6559.6564 | 6870.2568 | 7094.0819 | 7002.1239 | 7002.1239 | 7002.1239 | 7002.1239 | 7002.1239 | 7002.1239 | 7002.1239 | 7002.1239 | 7002.1239 | 7002.1239 | 7002.1239 | 7002.1239 | 7002.1239 | 7002.1239 | 7002.1239 | 7002.1239
55% | 2587.93 | 3569.0383 | 3673.0724 | 3801.6891 | 3972.4533 | 4134.3425 | 4417.258 | 5128.8093 | 5511.5325 | 5232.3246 | 6096.7133 | 6252.4502 | 6364.3994 | 6892.0947 | 6977.9873 | 6977.9873 | 6977.9873 | 6977.9873 | 6977.9873 | 6977.9873 | 6977.9873 | 6977.9873 | 6977.9873 | 6977.9873 | 6977.9873 | 6977.9873 | 6977.9873 | 6977.9873 | 6977.9873 | 6977.9873 |  | 3489.6205 | 4425.4573 | 4522.3714 | 4856.8353 | 4848.6838 | 4922.2304 | 5209.881 | 6036.3099 | 6377.3443 | 6054.5287 | 6946.2732 | 6571.8705 | 6908.7548 | 7151.5206 | 7051.7809 | 7051.7809 | 7051.7809 | 7051.7809 | 7051.7809 | 7051.7809 | 7051.7809 | 7051.7809 | 7051.7809 | 7051.7809 | 7051.7809 | 7051.7809 | 7051.7809 | 7051.7809 | 7051.7809 | 7051.7809
50% | 1977.4132 | 2976.5959 | 3082.5466 | 3213.5326 | 3387.4428 | 3552.3143 | 3840.4419 | 4565.1017 | 4954.8755 | 4670.5239 | 5550.8367 | 5709.4427 | 5823.4542 | 6360.871 | 6448.3459 | 6448.3459 | 6448.3459 | 6448.3459 | 6448.3459 | 6448.3459 | 6448.3459 | 6448.3459 | 6448.3459 | 6448.3459 | 6448.3459 | 6448.3459 | 6448.3459 | 6448.3459 | 6448.3459 | 6448.3459 |  | 2895.7151 | 3848.7922 | 3947.4917 | 4288.1172 | 4279.8156 | 4354.717 | 4647.6668 | 5489.3206 | 5836.6377 | 5507.875 | 6416.0476 | 6034.7475 | 6377.838 | 6625.0761 | 6523.499 | 6523.499 | 6523.499 | 6523.499 | 6523.499 | 6523.499 | 6523.499 | 6523.499 | 6523.499 | 6523.499 | 6523.499 | 6523.499 | 6523.499 | 6523.499 | 6523.499 | 6523.499
45% | 1115.1481 | 2058.8937 | 2158.966 | 2282.6846 | 2446.9458 | 2602.6699 | 2874.8114 | 3559.2653 | 3927.4136 | 3658.8385 | 4490.3094 | 4640.1156 | 4747.8014 | 5255.401 | 5338.0226 | 5338.0226 | 5338.0226 | 5338.0226 | 5338.0226 | 5338.0226 | 5338.0226 | 5338.0226 | 5338.0226 | 5338.0226 | 5338.0226 | 5338.0226 | 5338.0226 | 5338.0226 | 5338.0226 | 5338.0226 |  | 1982.5003 | 2882.6984 | 2975.9219 | 3297.6486 | 3289.8076 | 3360.5533 | 3637.2496 | 4432.2063 | 4760.2534 | 4449.7313 | 5307.5163 | 4947.3717 | 5271.4266 | 5504.9474 | 5409.006 | 5409.006 | 5409.006 | 5409.006 | 5409.006 | 5409.006 | 5409.006 | 5409.006 | 5409.006 | 5409.006 | 5409.006 | 5409.006 | 5409.006 | 5409.006 | 5409.006 | 5409.006
40% | 218.0643 | 1019.3158 | 1109.6444 | 1221.317 | 1369.5846 | 1510.1463 | 1755.7904 | 2373.6013 | 2705.9042 | 2463.4794 | 3213.9927 | 3349.2128 | 3446.4136 | 3904.5899 | 3979.1669 | 3979.1669 | 3979.1669 | 3979.1669 | 3979.1669 | 3979.1669 | 3979.1669 | 3979.1669 | 3979.1669 | 3979.1669 | 3979.1669 | 3979.1669 | 3979.1669 | 3979.1669 | 3979.1669 | 3979.1669 |  | 950.3606 | 1762.9094 | 1847.056 | 2137.4573 | 2130.3798 | 2194.2372 | 2443.9925 | 3161.5469 | 3457.6532 | 3177.3656 | 3951.6309 | 3626.5524 | 3919.0552 | 4129.8388 | 4043.2389 | 4043.2389 | 4043.2389 | 4043.2389 | 4043.2389 | 4043.2389 | 4043.2389 | 4043.2389 | 4043.2389 | 4043.2389 | 4043.2389 | 4043.2389 | 4043.2389 | 4043.2389 | 4043.2389 | 4043.2389
35% |  | 100.0043 | 136.3101 | 188.3336 | 269.145 | 357.6005 | 537.7501 | 1017.2126 | 1275.1019 | 1086.964 | 1669.4126 | 1774.3523 | 1849.7867 | 2205.3621 | 2263.2389 | 2263.2389 | 2263.2389 | 2263.2389 | 2263.2389 | 2263.2389 | 2263.2389 | 2263.2389 | 2263.2389 | 2263.2389 | 2263.2389 | 2263.2389 | 2263.2389 | 2263.2389 | 2263.2389 | 2263.2389 |  | 75.8706 | 543.275 | 608.5783 | 833.9491 | 828.4565 | 878.0141 | 1071.8409 | 1628.7111 | 1858.5094 | 1640.9875 | 2241.8691 | 1989.5864 | 2216.5882 | 2380.1703 | 2312.963 | 2312.963 | 2312.963 | 2312.963 | 2312.963 | 2312.963 | 2312.963 | 2312.963 | 2312.963 | 2312.963 | 2312.963 | 2312.963 | 2312.963 | 2312.963 | 2312.963 | 2312.963
30% | [6 empty] | 0.47307 | 86.92 | 189.3305 | 111.0221 | 411.6753 | 482.9899 | 535.3611 | 782.2235 | 822.4051 | 822.4051 | 822.4051 | 822.4051 | 822.4051 | 822.4051 | 822.4051 | 822.4051 | 822.4051 | 822.4051 | 822.4051 | 822.4051 | 822.4051 | 822.4051 | 822.4051 | 822.4051 |  |  | 0.62469 | 3.9886 | 37.019 | 35.8334 | 47.1947 | 105.5643 | 385.3047 | 541.4169 | 393.1792 | 807.5688 | 632.4187 | 790.0173 | 903.5861 | 856.9266 | 856.9266 | 856.9266 | 856.9266 | 856.9266 | 856.9266 | 856.9266 | 856.9266 | 856.9266 | 856.9266 | 856.9266 | 856.9266 | 856.9266 | 856.9266 | 856.9266 | 856.9266
25% | [11 empty] | 0.074459 | 1.4981 | 31.3754 | 39.665 | 39.665 | 39.665 | 39.665 | 39.665 | 39.665 | 39.665 | 39.665 | 39.665 | 39.665 | 39.665 | 39.665 | 39.665 | 39.665 | 39.665 | 39.665 | [9 empty] | 1.778 |  | 36.4973 | 8.794 | 32.9113 | 59.1747 | 47.515 | 47.515 | 47.515 | 47.515 | 47.515 | 47.515 | 47.515 | 47.515 | 47.515 | 47.515 | 47.515 | 47.515 | 47.515 | 47.515 | 47.515 | 47.515
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 17081.9558 | 23794.351 | 24536.8726 | 25461.914 | 26701.7135 | 27888.803 | 29989.1249 | 35382.088 | 38338.1632 | 36178.0578 | 42923.0818 | 44155.3813 | 45043.6541 | 49253.6461 | 49942.2957 | 49942.2957 | 49942.2957 | 49942.2957 | 49942.2957 | 49942.2957 | 49942.2957 | 49942.2957 | 49942.2957 | 49942.2957 | 49942.2957 | 49942.2957 | 49942.2957 | 49942.2957 | 49942.2957 | 49942.2957 | E @ R (MWh) | 23231.0692 | 30050.4324 | 30776.634 | 33304.0623 | 33242.0879 | 33801.9108 | 36005.2501 | 42446.433 | 45146.4814 | 42590.1209 | 49687.9201 | 46694.4681 | 49387.1485 | 51336.3448 | 50534.6619 | 50534.6619 | 50534.6619 | 50534.6619 | 50534.6619 | 50534.6619 | 50534.6619 | 50534.6619 | 50534.6619 | 50534.6619 | 50534.6619 | 50534.6619 | 50534.6619 | 50534.6619 | 50534.6619 | 50534.6619
Option 1 Winter POE50 W E @ R (MWh) N 2 | 11957.3691 | 16656.0457 | 17175.8108 | 17823.3398 | 18691.1994 | 19522.1621 | 20992.3874 | 24767.4616 | 26836.7142 | 25324.6404 | 30046.1573 | 30908.7669 | 31530.5579 | 34477.5523 | 34959.607 | 34959.607 | 34959.607 | 34959.607 | 34959.607 | 34959.607 | 34959.607 | 34959.607 | 34959.607 | 34959.607 | 34959.607 | 34959.607 | 34959.607 | 34959.607 | 34959.607 | 34959.607 | Option 1 Winter POE10 W E @ R (MWh) N 2 | 6969.3207 | 9015.1297 | 9232.9902 | 9991.2187 | 9972.6264 | 10140.5732 | 10801.575 | 12733.9299 | 13543.9444 | 12777.0363 | 14906.376 | 14008.3404 | 14816.1446 | 15400.9034 | 15160.3986 | 15160.3986 | 15160.3986 | 15160.3986 | 15160.3986 | 15160.3986 | 15160.3986 | 15160.3986 | 15160.3986 | 15160.3986 | 15160.3986 | 15160.3986 | 15160.3986 | 15160.3986 | 15160.3986 | 15160.3986
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | 10.4659 | 11.7471 | 11.8758 | 11.8127 | 11.8727 | 11.8974 | 11.9764 | 12.1389 | 12.2756 | 12.3385 | 12.2824 | 12.5175 | 12.5548 | 12.5107 | 12.5992 | 12.6406 | 12.6406 | 12.6406 | 12.6406 | 12.6406 | 12.6406 | 12.6406 | 12.6406 | 12.6406 | 12.6406 | 12.6406 | 12.6406 | 12.6406 | 12.6406 | 12.6406 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
98% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
97% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 13.9883 | 15.3913 | 15.4301 | 15.3883 | 15.399 | 15.4757 | 15.6309 | 15.9044 | 16.0469 | 16.1499 | 16.3059 | 16.5051 | 16.746 | 16.8722 | 16.8313 | 16.8718 | 16.8718 | 16.8718 | 16.8718 | 16.8718 | 16.8718 | 16.8718 | 16.8718 | 16.8718 | 16.8718 | 16.8718 | 16.8718 | 16.8718 | 16.8718 | 16.8718
95% | 9.863 | 11.0991 | 11.2233 | 11.1624 | 11.2203 | 11.2441 | 11.3203 | 11.4771 | 11.609 | 11.6697 | 11.6156 | 11.8424 | 11.8784 | 11.8358 | 11.9212 | 11.9611 | 11.9611 | 11.9611 | 11.9611 | 11.9611 | 11.9611 | 11.9611 | 11.9611 | 11.9611 | 11.9611 | 11.9611 | 11.9611 | 11.9611 | 11.9611 | 11.9611 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
90% | 203.721 | 229.9238 | 232.5569 | 231.2662 | 232.4934 | 232.9977 | 234.6138 | 237.9368 | 240.7323 | 242.0191 | 240.8722 | 245.6809 | 246.4436 | 245.541 | 247.3509 | 248.1974 | 248.1974 | 248.1974 | 248.1974 | 248.1974 | 248.1974 | 248.1974 | 248.1974 | 248.1974 | 248.1974 | 248.1974 | 248.1974 | 248.1974 | 248.1974 | 248.1974 |  | 12.9287 | 14.2598 | 14.2965 | 14.2569 | 14.2671 | 14.3398 | 14.4871 | 14.7465 | 14.8817 | 14.9794 | 15.1275 | 15.3164 | 15.5449 | 15.6647 | 15.6258 | 15.6643 | 15.6643 | 15.6643 | 15.6643 | 15.6643 | 15.6643 | 15.6643 | 15.6643 | 15.6643 | 15.6643 | 15.6643 | 15.6643 | 15.6643 | 15.6643 | 15.6643
85% | 697.0932 | 790.6056 | 800.0026 | 795.3964 | 799.7762 | 801.5757 | 807.3432 | 819.2024 | 829.1789 | 833.7714 | 829.6781 | 846.8397 | 849.5615 | 846.3404 | 852.7995 | 855.8206 | 855.8206 | 855.8206 | 855.8206 | 855.8206 | 855.8206 | 855.8206 | 855.8206 | 855.8206 | 855.8206 | 855.8206 | 855.8206 | 855.8206 | 855.8206 | 855.8206 |  | 11.8691 | 13.1282 | 13.1629 | 13.1255 | 13.1351 | 13.2038 | 13.3432 | 13.5886 | 13.7165 | 13.809 | 13.949 | 14.1277 | 14.3439 | 14.4571 | 14.4204 | 14.4568 | 14.4568 | 14.4568 | 14.4568 | 14.4568 | 14.4568 | 14.4568 | 14.4568 | 14.4568 | 14.4568 | 14.4568 | 14.4568 | 14.4568 | 14.4568 | 14.4568
80% | 1077.8455 | 1229.7508 | 1245.0156 | 1237.5332 | 1244.6479 | 1247.5711 | 1256.9401 | 1276.2046 | 1292.4109 | 1299.8711 | 1293.2218 | 1321.0998 | 1325.5213 | 1320.2887 | 1330.7811 | 1335.6887 | 1335.6887 | 1335.6887 | 1335.6887 | 1335.6887 | 1335.6887 | 1335.6887 | 1335.6887 | 1335.6887 | 1335.6887 | 1335.6887 | 1335.6887 | 1335.6887 | 1335.6887 | 1335.6887 |  | 43.2377 | 47.9863 | 48.1174 | 47.9761 | 48.0124 | 48.2717 | 48.7972 | 49.7227 | 50.205 | 50.5539 | 51.0819 | 51.756 | 52.5712 | 52.9984 | 52.8599 | 52.9972 | 52.9972 | 52.9972 | 52.9972 | 52.9972 | 52.9972 | 52.9972 | 52.9972 | 52.9972 | 52.9972 | 52.9972 | 52.9972 | 52.9972 | 52.9972 | 52.9972
75% | 1809.2093 | 2079.6387 | 2106.8139 | 2093.4933 | 2106.1592 | 2111.3633 | 2128.0424 | 2162.3381 | 2191.1892 | 2204.4703 | 2192.633 | 2242.2627 | 2250.134 | 2240.8188 | 2259.498 | 2268.2346 | 2268.2346 | 2268.2346 | 2268.2346 | 2268.2346 | 2268.2346 | 2268.2346 | 2268.2346 | 2268.2346 | 2268.2346 | 2268.2346 | 2268.2346 | 2268.2346 | 2268.2346 | 2268.2346 |  | 19.4996 | 21.73 | 21.7915 | 21.7252 | 21.7422 | 21.864 | 22.1109 | 22.5456 | 22.7721 | 22.936 | 23.184 | 23.5006 | 23.8835 | 24.0842 | 24.0191 | 24.0836 | 24.0836 | 24.0836 | 24.0836 | 24.0836 | 24.0836 | 24.0836 | 24.0836 | 24.0836 | 24.0836 | 24.0836 | 24.0836 | 24.0836 | 24.0836 | 24.0836
70% | 2151.4453 | 2496.8455 | 2531.5545 | 2514.541 | 2530.7182 | 2537.3651 | 2558.6681 | 2602.4716 | 2639.3211 | 2656.284 | 2641.165 | 2704.5535 | 2714.6071 | 2702.7094 | 2726.567 | 2737.7256 | 2737.7256 | 2737.7256 | 2737.7256 | 2737.7256 | 2737.7256 | 2737.7256 | 2737.7256 | 2737.7256 | 2737.7256 | 2737.7256 | 2737.7256 | 2737.7256 | 2737.7256 | 2737.7256 |  | 52.1409 | 58.4004 | 58.5732 | 58.3869 | 58.4348 | 58.7767 | 59.4694 | 60.6894 | 61.3251 | 61.785 | 62.481 | 63.3696 | 64.4442 | 65.0073 | 64.8247 | 65.0057 | 65.0057 | 65.0057 | 65.0057 | 65.0057 | 65.0057 | 65.0057 | 65.0057 | 65.0057 | 65.0057 | 65.0057 | 65.0057 | 65.0057 | 65.0057 | 65.0057
65% | 2417.2518 | 2841.3891 | 2884.0103 | 2863.1184 | 2882.9834 | 2891.1455 | 2917.3047 | 2971.0936 | 3016.3433 | 3037.1731 | 3018.6076 | 3096.446 | 3108.7914 | 3094.1815 | 3123.4776 | 3137.18 | 3137.18 | 3137.18 | 3137.18 | 3137.18 | 3137.18 | 3137.18 | 3137.18 | 3137.18 | 3137.18 | 3137.18 | 3137.18 | 3137.18 | 3137.18 | 3137.18 |  | 15.261 | 17.2036 | 17.2572 | 17.1994 | 17.2143 | 17.3204 | 17.5354 | 17.914 | 18.1113 | 18.254 | 18.47 | 18.7458 | 19.0793 | 19.254 | 19.1974 | 19.2535 | 19.2535 | 19.2535 | 19.2535 | 19.2535 | 19.2535 | 19.2535 | 19.2535 | 19.2535 | 19.2535 | 19.2535 | 19.2535 | 19.2535 | 19.2535 | 19.2535
60% | 3150.8806 | 3770.5408 | 3832.8099 | 3802.2871 | 3831.3096 | 3843.2344 | 3881.4527 | 3960.0377 | 4026.147 | 4056.5791 | 4029.4551 | 4143.1763 | 4161.2127 | 4139.8678 | 4182.6692 | 4202.6882 | 4202.6882 | 4202.6882 | 4202.6882 | 4202.6882 | 4202.6882 | 4202.6882 | 4202.6882 | 4202.6882 | 4202.6882 | 4202.6882 | 4202.6882 | 4202.6882 | 4202.6882 | 4202.6882 |  | 85.4213 | 97.113 | 97.4357 | 97.0878 | 97.1773 | 97.8157 | 99.1096 | 101.3883 | 102.5757 | 103.4347 | 104.7347 | 106.3945 | 108.4016 | 109.4534 | 109.1124 | 109.4504 | 109.4504 | 109.4504 | 109.4504 | 109.4504 | 109.4504 | 109.4504 | 109.4504 | 109.4504 | 109.4504 | 109.4504 | 109.4504 | 109.4504 | 109.4504 | 109.4504
55% | 3327.6421 | 4090.2265 | 4166.858 | 4129.2951 | 4165.0116 | 4179.6869 | 4226.7202 | 4323.4309 | 4404.7881 | 4442.2395 | 4408.8593 | 4548.8102 | 4571.0067 | 4544.7386 | 4597.4121 | 4622.0485 | 4622.0485 | 4622.0485 | 4622.0485 | 4622.0485 | 4622.0485 | 4622.0485 | 4622.0485 | 4622.0485 | 4622.0485 | 4622.0485 | 4622.0485 | 4622.0485 | 4622.0485 | 4622.0485 |  | 352.7187 | 405.6734 | 407.1346 | 405.5592 | 405.9643 | 408.8561 | 414.7164 | 425.0372 | 430.415 | 434.3056 | 440.1939 | 447.7114 | 456.8018 | 461.5659 | 460.0214 | 461.5522 | 461.5522 | 461.5522 | 461.5522 | 461.5522 | 461.5522 | 461.5522 | 461.5522 | 461.5522 | 461.5522 | 461.5522 | 461.5522 | 461.5522 | 461.5522 | 461.5522
50% | 3032.8171 | 3898.088 | 3985.0383 | 3942.4174 | 3982.9433 | 3999.5947 | 4052.9614 | 4162.6947 | 4255.0072 | 4297.5016 | 4259.6266 | 4418.4227 | 4443.6081 | 4413.8029 | 4473.5691 | 4501.523 | 4501.523 | 4501.523 | 4501.523 | 4501.523 | 4501.523 | 4501.523 | 4501.523 | 4501.523 | 4501.523 | 4501.523 | 4501.523 | 4501.523 | 4501.523 | 4501.523 |  | 703.3516 | 822.7155 | 826.0092 | 822.458 | 823.3713 | 829.8895 | 843.0992 | 866.363 | 878.4849 | 887.2547 | 900.5273 | 917.4725 | 937.9629 | 948.7014 | 945.2201 | 948.6707 | 948.6707 | 948.6707 | 948.6707 | 948.6707 | 948.6707 | 948.6707 | 948.6707 | 948.6707 | 948.6707 | 948.6707 | 948.6707 | 948.6707 | 948.6707 | 948.6707
45% | 1765.9337 | 2482.1322 | 2554.1023 | 2518.8243 | 2552.3683 | 2566.1509 | 2610.3233 | 2701.1513 | 2777.5598 | 2812.7331 | 2781.3834 | 2912.8214 | 2933.6678 | 2908.9975 | 2958.467 | 2981.6048 | 2981.6048 | 2981.6048 | 2981.6048 | 2981.6048 | 2981.6048 | 2981.6048 | 2981.6048 | 2981.6048 | 2981.6048 | 2981.6048 | 2981.6048 | 2981.6048 | 2981.6048 | 2981.6048 |  | 1017.5865 | 1222.642 | 1228.3004 | 1222.1997 | 1223.7687 | 1234.9662 | 1257.6592 | 1297.6242 | 1318.4485 | 1333.5141 | 1356.3152 | 1385.4253 | 1420.6258 | 1439.0735 | 1433.093 | 1439.0207 | 1439.0207 | 1439.0207 | 1439.0207 | 1439.0207 | 1439.0207 | 1439.0207 | 1439.0207 | 1439.0207 | 1439.0207 | 1439.0207 | 1439.0207 | 1439.0207 | 1439.0207 | 1439.0207
40% | 607.9205 | 1122.3189 | 1174.0104 | 1148.6725 | 1172.7649 | 1182.6641 | 1214.3902 | 1279.626 | 1334.5053 | 1359.768 | 1337.2515 | 1431.6548 | 1446.6274 | 1428.9084 | 1464.439 | 1481.0575 | 1481.0575 | 1481.0575 | 1481.0575 | 1481.0575 | 1481.0575 | 1481.0575 | 1481.0575 | 1481.0575 | 1481.0575 | 1481.0575 | 1481.0575 | 1481.0575 | 1481.0575 | 1481.0575 |  | 1058.8722 | 1336.5245 | 1344.1862 | 1335.9257 | 1338.0501 | 1353.212 | 1383.9391 | 1438.0532 | 1466.2499 | 1486.6493 | 1517.5228 | 1556.9388 | 1604.6016 | 1629.5804 | 1621.4826 | 1629.509 | 1629.509 | 1629.509 | 1629.509 | 1629.509 | 1629.509 | 1629.509 | 1629.509 | 1629.509 | 1629.509 | 1629.509 | 1629.509 | 1629.509 | 1629.509 | 1629.509
35% | 23.196 | 247.1276 | 281.389 | 264.3461 | 280.5402 | 287.3184 | 309.5259 | 357.4741 | 400.1436 | 420.4081 | 402.3339 | 478.1695 | 490.2 | 475.9627 | 504.5117 | 517.8647 | 517.8647 | 517.8647 | 517.8647 | 517.8647 | 517.8647 | 517.8647 | 517.8647 | 517.8647 | 517.8647 | 517.8647 | 517.8647 | 517.8647 | 517.8647 | 517.8647 |  | 1063.9608 | 1515.0828 | 1527.5312 | 1514.1099 | 1517.5615 | 1542.1962 | 1592.1207 | 1680.0438 | 1725.8572 | 1759.0016 | 1809.1639 | 1873.2061 | 1950.6472 | 1991.2321 | 1978.0751 | 1991.1161 | 1991.1161 | 1991.1161 | 1991.1161 | 1991.1161 | 1991.1161 | 1991.1161 | 1991.1161 | 1991.1161 | 1991.1161 | 1991.1161 | 1991.1161 | 1991.1161 | 1991.1161 | 1991.1161
30% | [9 empty] | 0.071582 |  | 2.2996 | 3.1509 | 2.1578 | 4.3353 | 5.6074 | 5.6074 | 5.6074 | 5.6074 | 5.6074 | 5.6074 | 5.6074 | 5.6074 | 5.6074 | 5.6074 | 5.6074 | 5.6074 | 5.6074 | 5.6074 | 5.6074 |  | 388.5058 | 1015.6243 | 1034.8788 | 1014.1196 | 1019.4583 | 1057.5615 | 1134.7813 | 1270.7746 | 1341.6355 | 1392.901 | 1470.4886 | 1569.5445 | 1689.3252 | 1752.0991 | 1731.7486 | 1751.9195 | 1751.9195 | 1751.9195 | 1751.9195 | 1751.9195 | 1751.9195 | 1751.9195 | 1751.9195 | 1751.9195 | 1751.9195 | 1751.9195 | 1751.9195 | 1751.9195 | 1751.9195 | 1751.9195
25% | [32 empty] | 10.8714 | 13.2189 | 10.6975 | 11.3209 | 16.2724 | 28.9785 | 59.8591 | 80.1406 | 96.5629 | 124.1616 | 164.1053 | 219.2802 | 251.1289 | 240.5861 | 251.035 | 251.035 | 251.035 | 251.035 | 251.035 | 251.035 | 251.035 | 251.035 | 251.035 | 251.035 | 251.035 | 251.035 | 251.035 | 251.035 | 251.035
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 20082.4323 | 25048.4194 | 25559.0881 | 25308.5245 | 25546.761 | 25644.7713 | 25959.3667 | 26608.5051 | 27156.899 | 27410.0291 | 27184.3956 | 28132.4312 | 28283.2762 | 28104.7752 | 28462.8939 | 28630.6444 | 28630.6444 | 28630.6444 | 28630.6444 | 28630.6444 | 28630.6444 | 28630.6444 | 28630.6444 | 28630.6444 | 28630.6444 | 28630.6444 | 28630.6444 | 28630.6444 | 28630.6444 | 28630.6444 | E @ R (MWh) | 4790.9487 | 6548.203 | 6600.6505 | 6544.1136 | 6558.6286 | 6662.7214 | 6876.3204 | 7260.9121 | 7465.4571 | 7615.1702 | 7844.4702 | 8141.8786 | 8508.3166 | 8703.2608 | 8639.8468 | 8702.7004 | 8702.7004 | 8702.7004 | 8702.7004 | 8702.7004 | 8702.7004 | 8702.7004 | 8702.7004 | 8702.7004 | 8702.7004 | 8702.7004 | 8702.7004 | 8702.7004 | 8702.7004 | 8702.7004
Option 1 Summer POE50 W E @ R (MWh) N 2 | 14057.7026 | 17533.8936 | 17891.3617 | 17715.9672 | 17882.7327 | 17951.3399 | 18171.5567 | 18625.9536 | 19009.8293 | 19187.0204 | 19029.0769 | 19692.7018 | 19798.2933 | 19673.3426 | 19924.0258 | 20041.4511 | 20041.4511 | 20041.4511 | 20041.4511 | 20041.4511 | 20041.4511 | 20041.4511 | 20041.4511 | 20041.4511 | 20041.4511 | 20041.4511 | 20041.4511 | 20041.4511 | 20041.4511 | 20041.4511 | Option 1 Summer POE10 W E @ R (MWh) N 2 | 1437.2846 | 1964.4609 | 1980.1951 | 1963.2341 | 1967.5886 | 1998.8164 | 2062.8961 | 2178.2736 | 2239.6371 | 2284.5511 | 2353.341 | 2442.5636 | 2552.495 | 2610.9782 | 2591.954 | 2610.8101 | 2610.8101 | 2610.8101 | 2610.8101 | 2610.8101 | 2610.8101 | 2610.8101 | 2610.8101 | 2610.8101 | 2610.8101 | 2610.8101 | 2610.8101 | 2610.8101 | 2610.8101 | 2610.8101
Option 2 - Replace 3 x 10/13.5 MVA Tx with 3 x 20/33 MVA Tx
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | 7.4585 | 8.8006 | 8.9429 | [10 empty] | 0.50731 | 0.62481 | 0.62481 | 0.62481 | 0.62481 | 0.62481 | 0.62481 | 0.62481 | 0.62481 | 0.62481 | 0.62481 | 0.62481 | 0.62481 | 0.62481 | 0.62481 | 0.62481 | 0.62481 |  | 8.6919 | 9.9721 | 10.1047 | [7 empty] | 0.58143 | 0.070653 | 0.5301 | 0.86219 | 0.72575 | 0.72575 | 0.72575 | 0.72575 | 0.72575 | 0.72575 | 0.72575 | 0.72575 | 0.72575 | 0.72575 | 0.72575 | 0.72575 | 0.72575 | 0.72575 | 0.72575 | 0.72575
98% | 0 | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | [7 empty] | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
97% | 0 | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | [7 empty] | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
95% | 28.0297 | 33.2092 | 33.7584 | [10 empty] | 0.0073568 | 0.12167 | 0.12167 | 0.12167 | 0.12167 | 0.12167 | 0.12167 | 0.12167 | 0.12167 | 0.12167 | 0.12167 | 0.12167 | 0.12167 | 0.12167 | 0.12167 | 0.12167 | 0.12167 |  | 32.79 | 37.7305 | 38.2421 | [7 empty] | 0.063446 |  | 0.018748 | 0.76616 | 0.32891 | 0.32891 | 0.32891 | 0.32891 | 0.32891 | 0.32891 | 0.32891 | 0.32891 | 0.32891 | 0.32891 | 0.32891 | 0.32891 | 0.32891 | 0.32891 | 0.32891 | 0.32891
90% | FY25: 157.3528; FY26: 187.297; FY27: 190.4721 |  | 184.8731 | 213.4355 | 216.3934
85% | FY25: 626.672; FY26: 751.7764; FY27: 765.0422 |  | 741.6496 | 860.9812 | 873.3391
80% | FY25: 937.6386; FY26: 1135.7149; FY27: 1156.7184 |  | 1119.6813 | 1308.6177 | 1328.1837
75% | FY25: 1618.1428; FY26: 1984.0141; FY27: 2022.8101 |  | 1954.3979 | 2303.3867 | 2339.5275
70% | FY25: 2423.1485; FY26: 3018.6926; FY27: 3081.8425 |  | 2970.4851 | 3538.5488 | 3597.3768
65% | FY25: 2670.9583; FY26: 3400.2393; FY27: 3477.5703 |  | 3341.2062 | 4036.8358 | 4108.8743
60% | FY25: 2886.5439; FY26: 3791.1059; FY27: 3887.0233 |  | 3717.8843 | 4580.7069 | 4670.0597
55% | FY25: 2587.93; FY26: 3569.0383; FY27: 3673.0724 |  | 3489.6205 | 4425.4573 | 4522.3714
50% | FY25: 1977.4132; FY26: 2976.5959; FY27: 3082.5466 |  | 2895.7151 | 3848.7922 | 3947.4917
45% | FY25: 1115.1481; FY26: 2058.8937; FY27: 2158.966 |  | 1982.5003 | 2882.6984 | 2975.9219
40% | FY25: 218.0643; FY26: 1019.3158; FY27: 1109.6444 |  | 950.3606 | 1762.9094 | 1847.056
35% | FY26: 100.0043; FY27: 136.3101 |  | 75.8706 | 543.275 | 608.5783
30% | [32 empty] | 0.62469 | 3.9886
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 17081.9558 | 23794.351 | 24536.8726 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.50952 | 0.73902 | 0.73902 | 0.73902 | 0.73902 | 0.73902 | 0.73902 | 0.73902 | 0.73902 | 0.73902 | 0.73902 | 0.73902 | 0.73902 | 0.73902 | 0.73902 | 0.73902 | 0.73902 | E @ R (MWh) | 23231.0692 | 30050.4324 | 30776.634 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.63842 | 0.069947 | 0.54336 | 1.6121 | 1.0441 | 1.0441 | 1.0441 | 1.0441 | 1.0441 | 1.0441 | 1.0441 | 1.0441 | 1.0441 | 1.0441 | 1.0441 | 1.0441 | 1.0441 | 1.0441 | 1.0441 | 1.0441
Option 2 Winter POE50 W E @ R (MWh) N 2 | 11957.3691 | 16656.0457 | 17175.8108 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.35667 | 0.51731 | 0.51731 | 0.51731 | 0.51731 | 0.51731 | 0.51731 | 0.51731 | 0.51731 | 0.51731 | 0.51731 | 0.51731 | 0.51731 | 0.51731 | 0.51731 | 0.51731 | 0.51731 | Option 2 Winter POE10 W E @ R (MWh) N 2 | 6969.3207 | 9015.1297 | 9232.9902 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.19153 | 0.020984 | 0.16301 | 0.48362 | 0.31324 | 0.31324 | 0.31324 | 0.31324 | 0.31324 | 0.31324 | 0.31324 | 0.31324 | 0.31324 | 0.31324 | 0.31324 | 0.31324 | 0.31324 | 0.31324 | 0.31324 | 0.31324
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | FY25: 10.4659; FY26: 11.7471; FY27: 11.8758 |  | 0 | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
98% | FY25: 0; FY26: 0; FY27: 0 |  | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
97% | FY25: 0; FY26: 0; FY27: 0 |  | 13.9883 | 15.3913 | 15.4301 | [7 empty] | 0.016093 | 0.16842 | 0.40927 | 0.53549 | 0.49457 | 0.53513 | 0.53513 | 0.53513 | 0.53513 | 0.53513 | 0.53513 | 0.53513 | 0.53513 | 0.53513 | 0.53513 | 0.53513 | 0.53513 | 0.53513 | 0.53513 | 0.53513
95% | FY25: 9.863; FY26: 11.0991; FY27: 11.2233 |  | 0 | 0 | 0 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
90% | FY25: 203.721; FY26: 229.9238; FY27: 232.5569 |  | 12.9287 | 14.2598 | 14.2965
85% | FY25: 697.0932; FY26: 790.6056; FY27: 800.0026 |  | 11.8691 | 13.1282 | 13.1629
80% | FY25: 1077.8455; FY26: 1229.7508; FY27: 1245.0156 |  | 43.2377 | 47.9863 | 48.1174
75% | FY25: 1809.2093; FY26: 2079.6387; FY27: 2106.8139 |  | 19.4996 | 21.73 | 21.7915
70% | FY25: 2151.4453; FY26: 2496.8455; FY27: 2531.5545 |  | 52.1409 | 58.4004 | 58.5732
65% | FY25: 2417.2518; FY26: 2841.3891; FY27: 2884.0103 |  | 15.261 | 17.2036 | 17.2572
60% | FY25: 3150.8806; FY26: 3770.5408; FY27: 3832.8099 |  | 85.4213 | 97.113 | 97.4357
55% | FY25: 3327.6421; FY26: 4090.2265; FY27: 4166.858 |  | 352.7187 | 405.6734 | 407.1346
50% | FY25: 3032.8171; FY26: 3898.088; FY27: 3985.0383 |  | 703.3516 | 822.7155 | 826.0092
45% | FY25: 1765.9337; FY26: 2482.1322; FY27: 2554.1023 |  | 1017.5865 | 1222.642 | 1228.3004
40% | FY25: 607.9205; FY26: 1122.3189; FY27: 1174.0104 |  | 1058.8722 | 1336.5245 | 1344.1862
35% | FY25: 23.196; FY26: 247.1276; FY27: 281.389 |  | 1063.9608 | 1515.0828 | 1527.5312
30% | [31 empty] | 388.5058 | 1015.6243 | 1034.8788
25% | [32 empty] | 10.8714 | 13.2189
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 20082.4323 | 25048.4194 | 25559.0881 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 4790.9487 | 6548.203 | 6600.6505 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.015932 | 0.16674 | 0.40518 | 0.53013 | 0.48962 | 0.52978 | 0.52978 | 0.52978 | 0.52978 | 0.52978 | 0.52978 | 0.52978 | 0.52978 | 0.52978 | 0.52978 | 0.52978 | 0.52978 | 0.52978 | 0.52978 | 0.52978
Option 2 Summer POE50 W E @ R (MWh) N 2 | 14057.7026 | 17533.8936 | 17891.3617 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 2 Summer POE10 W E @ R (MWh) N 2 | 1437.2846 | 1964.4609 | 1980.1951 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0047795 | 0.050022 | 0.12155 | 0.15904 | 0.14689 | 0.15893 | 0.15893 | 0.15893 | 0.15893 | 0.15893 | 0.15893 | 0.15893 | 0.15893 | 0.15893 | 0.15893 | 0.15893 | 0.15893 | 0.15893 | 0.15893 | 0.15893
Option 3 - Replace 1 x 10/13.5 MVA Tx with 1 x 20/33 MVA Tx
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | 7.4585 | 8.8006 | 8.9429 | 4.5568 | 4.7904 | 5.0119 | 5.3989 | 6.3722 | 6.8958 | 6.5138 | 7.6963 | 7.9093 | 8.0624 | 8.7843 | 8.9018 | 8.9018 | 8.9018 | 8.9018 | 8.9018 | 8.9018 | 8.9018 | 8.9018 | 8.9018 | 8.9018 | 8.9018 | 8.9018 | 8.9018 | 8.9018 | 8.9018 | 8.9018 |  | 8.6919 | 9.9721 | 10.1047 | 6.0002 | 5.989 | 6.0897 | 6.4831 | 7.6136 | 8.0801 | 7.6386 | 8.8584 | 8.3462 | 8.8071 | 9.1392 | 9.0027 | 9.0027 | 9.0027 | 9.0027 | 9.0027 | 9.0027 | 9.0027 | 9.0027 | 9.0027 | 9.0027 | 9.0027 | 9.0027 | 9.0027 | 9.0027 | 9.0027 | 9.0027
98% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
97% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
95% | 28.0297 | 33.2092 | 33.7584 | 16.1895 | 17.091 | 17.9456 | 19.4392 | 23.1957 | 25.2162 | 23.7422 | 28.3055 | 29.1277 | 29.7187 | 32.5045 | 32.958 | 32.958 | 32.958 | 32.958 | 32.958 | 32.958 | 32.958 | 32.958 | 32.958 | 32.958 | 32.958 | 32.958 | 32.958 | 32.958 | 32.958 | 32.958 |  | 32.79 | 37.7305 | 38.2421 | 21.7598 | 21.7168 | 22.1051 | 23.6237 | 27.9866 | 29.787 | 28.0828 | 32.7905 | 30.814 | 32.5925 | 33.8741 | 33.3475 | 33.3475 | 33.3475 | 33.3475 | 33.3475 | 33.3475 | 33.3475 | 33.3475 | 33.3475 | 33.3475 | 33.3475 | 33.3475 | 33.3475 | 33.3475 | 33.3475 | 33.3475
90% | 157.3528 | 187.297 | 190.4721 | 84.9097 | 90.1215 | 95.0625 | 103.6973 | 125.4143 | 137.0953 | 128.5737 | 154.9554 | 159.7086 | 163.1254 | 179.231 | 181.8525 | 181.8525 | 181.8525 | 181.8525 | 181.8525 | 181.8525 | 181.8525 | 181.8525 | 181.8525 | 181.8525 | 181.8525 | 181.8525 | 181.8525 | 181.8525 | 181.8525 | 181.8525 |  | 184.8731 | 213.4355 | 216.3934 | 117.1135 | 116.8647 | 119.1094 | 127.8887 | 153.1119 | 163.5205 | 153.6679 | 180.8846 | 169.4576 | 179.7395 | 187.1489 | 184.1048 | 184.1048 | 184.1048 | 184.1048 | 184.1048 | 184.1048 | 184.1048 | 184.1048 | 184.1048 | 184.1048 | 184.1048 | 184.1048 | 184.1048 | 184.1048 | 184.1048 | 184.1048
85% | 626.672 | 751.7764 | 765.0422 | 297.8707 | 319.6455 | 340.2885 | 376.364 | 467.0963 | 515.8986 | 480.2958 | 590.5169 | 610.3754 | 624.6504 | 691.9386 | 702.8911 | 702.8911 | 702.8911 | 702.8911 | 702.8911 | 702.8911 | 702.8911 | 702.8911 | 702.8911 | 702.8911 | 702.8911 | 702.8911 | 702.8911 | 702.8911 | 702.8911 | 702.8911 |  | 741.6496 | 860.9812 | 873.3391 | 432.4159 | 431.3765 | 440.7547 | 477.434 | 582.8147 | 626.3011 | 585.1378 | 698.8471 | 651.1058 | 694.063 | 725.0189 | 712.3007 | 712.3007 | 712.3007 | 712.3007 | 712.3007 | 712.3007 | 712.3007 | 712.3007 | 712.3007 | 712.3007 | 712.3007 | 712.3007 | 712.3007 | 712.3007 | 712.3007 | 712.3007
80% | 937.6386 | 1135.7149 | 1156.7184 | 370.6493 | 405.125 | 437.8088 | 494.9268 | 638.5821 | 715.8502 | 659.4808 | 833.9926 | 865.4344 | 888.0358 | 994.5724 | 1011.9133 | 1011.9133 | 1011.9133 | 1011.9133 | 1011.9133 | 1011.9133 | 1011.9133 | 1011.9133 | 1011.9133 | 1011.9133 | 1011.9133 | 1011.9133 | 1011.9133 | 1011.9133 | 1011.9133 | 1011.9133 |  | 1119.6813 | 1308.6177 | 1328.1837 | 583.6732 | 582.0275 | 596.8758 | 654.9497 | 821.7977 | 890.6493 | 825.4759 | 1005.5105 | 929.9223 | 997.9359 | 1046.948 | 1026.8115 | 1026.8115 | 1026.8115 | 1026.8115 | 1026.8115 | 1026.8115 | 1026.8115 | 1026.8115 | 1026.8115 | 1026.8115 | 1026.8115 | 1026.8115 | 1026.8115 | 1026.8115 | 1026.8115 | 1026.8115
75% | 1618.1428 | 1984.0141 | 2022.8101 | 474.0742 | 537.755 | 598.1261 | 703.6299 | 968.979 | 1111.7027 | 1007.5815 | 1329.9261 | 1388.003 | 1429.7506 | 1626.5368 | 1658.5676 | 1658.5676 | 1658.5676 | 1658.5676 | 1658.5676 | 1658.5676 | 1658.5676 | 1658.5676 | 1658.5676 | 1658.5676 | 1658.5676 | 1658.5676 | 1658.5676 | 1658.5676 | 1658.5676 | 1658.5676 |  | 1954.3979 | 2303.3867 | 2339.5275 | 867.5554 | 864.5156 | 891.9423 | 999.2119 | 1307.4007 | 1434.578 | 1314.1948 | 1646.7409 | 1507.12 | 1632.7497 | 1723.281 | 1686.0864 | 1686.0864 | 1686.0864 | 1686.0864 | 1686.0864 | 1686.0864 | 1686.0864 | 1686.0864 | 1686.0864 | 1686.0864 | 1686.0864 | 1686.0864 | 1686.0864 | 1686.0864 | 1686.0864 | 1686.0864
70% | 2423.1485 | 3018.6926 | 3081.8425 | 381.6578 | 485.3136 | 583.5822 | 755.3152 | 1187.235 | 1419.5524 | 1250.07 | 1774.7639 | 1869.298 | 1937.2524 | 2257.5695 | 2309.7073 | 2309.7073 | 2309.7073 | 2309.7073 | 2309.7073 | 2309.7073 | 2309.7073 | 2309.7073 | 2309.7073 | 2309.7073 | 2309.7073 | 2309.7073 | 2309.7073 | 2309.7073 | 2309.7073 | 2309.7073 |  | 2970.4851 | 3538.5488 | 3597.3768 | 1022.1437 | 1017.1956 | 1061.8392 | 1236.4465 | 1738.0983 | 1945.1101 | 1749.1574 | 2290.4565 | 2063.1898 | 2267.6824 | 2415.044 | 2354.5009 | 2354.5009 | 2354.5009 | 2354.5009 | 2354.5009 | 2354.5009 | 2354.5009 | 2354.5009 | 2354.5009 | 2354.5009 | 2354.5009 | 2354.5009 | 2354.5009 | 2354.5009 | 2354.5009 | 2354.5009
65% | 2670.9583 | 3400.2393 | 3477.5703 | 38.0035 | 98.802 | 181.2948 | 376.581 | 905.4939 | 1189.981 | 982.4392 | 1624.9597 | 1740.7227 | 1823.9371 | 2216.1855 | 2280.0314 | 2280.0314 | 2280.0314 | 2280.0314 | 2280.0314 | 2280.0314 | 2280.0314 | 2280.0314 | 2280.0314 | 2280.0314 | 2280.0314 | 2280.0314 | 2280.0314 | 2280.0314 | 2280.0314 | 2280.0314 |  | 3341.2062 | 4036.8358 | 4108.8743 | 703.3291 | 697.27 | 751.9388 | 965.7563 | 1580.0604 | 1833.5594 | 1593.6029 | 2256.4576 | 1978.1553 | 2228.5693 | 2409.0228 | 2334.884 | 2334.884 | 2334.884 | 2334.884 | 2334.884 | 2334.884 | 2334.884 | 2334.884 | 2334.884 | 2334.884 | 2334.884 | 2334.884 | 2334.884 | 2334.884 | 2334.884 | 2334.884
60% | 2886.5439 | 3791.1059 | 3887.0233 |  |  |  | 5.0428 | 340.4622 | 687.0228 | 429.7035 | 1226.5476 | 1370.1339 | 1473.3487 | 1959.8731 | 2039.0643 | 2039.0643 | 2039.0643 | 2039.0643 | 2039.0643 | 2039.0643 | 2039.0643 | 2039.0643 | 2039.0643 | 2039.0643 | 2039.0643 | 2039.0643 | 2039.0643 | 2039.0643 | 2039.0643 | 2039.0643 |  | 3717.8843 | 4580.7069 | 4670.0597 | 153.0976 | 148.57 | 191.7522 | 409.5401 | 1170.8569 | 1485.2837 | 1187.6543 | 2009.8246 | 1664.633 | 1975.2334 | 2199.0585 | 2107.1006 | 2107.1006 | 2107.1006 | 2107.1006 | 2107.1006 | 2107.1006 | 2107.1006 | 2107.1006 | 2107.1006 | 2107.1006 | 2107.1006 | 2107.1006 | 2107.1006 | 2107.1006 | 2107.1006 | 2107.1006
55% | 2587.93 | 3569.0383 | 3673.0724 | [5 empty] | 35.4326 |  | 350.2952 | 484.7371 | 593.4724 | 1121.1678 | 1207.0603 | 1207.0603 | 1207.0603 | 1207.0603 | 1207.0603 | 1207.0603 | 1207.0603 | 1207.0603 | 1207.0603 | 1207.0603 | 1207.0603 | 1207.0603 | 1207.0603 | 1207.0603 | 1207.0603 | 1207.0603 |  | 3489.6205 | 4425.4573 | 4522.3714 |  |  |  |  | 303.6471 | 606.4174 | 317.3885 | 1175.3463 | 800.9436 | 1137.8279 | 1380.5936 | 1280.854 | 1280.854 | 1280.854 | 1280.854 | 1280.854 | 1280.854 | 1280.854 | 1280.854 | 1280.854 | 1280.854 | 1280.854 | 1280.854 | 1280.854 | 1280.854 | 1280.854 | 1280.854
50% | 1977.4132 | 2976.5959 | 3082.5466 | [9 empty] | 0.22999 | 129.9636 | 172.6078 | 172.6078 | 172.6078 | 172.6078 | 172.6078 | 172.6078 | 172.6078 | 172.6078 | 172.6078 | 172.6078 | 172.6078 | 172.6078 | 172.6078 | 172.6078 | 172.6078 | 172.6078 |  | 2895.7151 | 3848.7922 | 3947.4917 | [5 empty] | 0.56648 |  | 156.1902 | 23.2739 | 137.7827 | 276.1146 | 213.8193 | 213.8193 | 213.8193 | 213.8193 | 213.8193 | 213.8193 | 213.8193 | 213.8193 | 213.8193 | 213.8193 | 213.8193 | 213.8193 | 213.8193 | 213.8193 | 213.8193 | 213.8193
45% | FY25: 1115.1481; FY26: 2058.8937; FY27: 2158.966 |  | 1982.5003 | 2882.6984 | 2975.9219
40% | FY25: 218.0643; FY26: 1019.3158; FY27: 1109.6444 |  | 950.3606 | 1762.9094 | 1847.056
35% | FY26: 100.0043; FY27: 136.3101 |  | 75.8706 | 543.275 | 608.5783
30% | [32 empty] | 0.62469 | 3.9886
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 17081.9558 | 23794.351 | 24536.8726 | 1651.2323 | 1939.0574 | 2236.5291 | 2811.9911 | 4616.2024 | 5786.201 | 4918.7166 | 7842.7396 | 8440.1955 | 8881.8682 | 11106.1439 | 11489.4999 | 11489.4999 | 11489.4999 | 11489.4999 | 11489.4999 | 11489.4999 | 11489.4999 | 11489.4999 | 11489.4999 | 11489.4999 | 11489.4999 | 11489.4999 | 11489.4999 | 11489.4999 | 11489.4999 | 11489.4999 | E @ R (MWh) | 23231.0692 | 30050.4324 | 30776.634 | 3868.0175 | 3846.6705 | 4041.5832 | 4852.3206 | 7616.4541 | 8933.6146 | 7684.381 | 11347.2882 | 9728.6918 | 11180.0536 | 12281.1912 | 11823.3844 | 11823.3844 | 11823.3844 | 11823.3844 | 11823.3844 | 11823.3844 | 11823.3844 | 11823.3844 | 11823.3844 | 11823.3844 | 11823.3844 | 11823.3844 | 11823.3844 | 11823.3844 | 11823.3844 | 11823.3844
Option 3 Winter POE50 W E @ R (MWh) N 2 | 11957.3691 | 16656.0457 | 17175.8108 | 1155.8626 | 1357.3402 | 1565.5704 | 1968.3938 | 3231.3417 | 4050.3407 | 3443.1016 | 5489.9177 | 5908.1369 | 6217.3078 | 7774.3008 | 8042.65 | 8042.65 | 8042.65 | 8042.65 | 8042.65 | 8042.65 | 8042.65 | 8042.65 | 8042.65 | 8042.65 | 8042.65 | 8042.65 | 8042.65 | 8042.65 | 8042.65 | 8042.65 | Option 3 Winter POE10 W E @ R (MWh) N 2 | 6969.3207 | 9015.1297 | 9232.9902 | 1160.4053 | 1154.0012 | 1212.4749 | 1455.6962 | 2284.9362 | 2680.0844 | 2305.3143 | 3404.1865 | 2918.6075 | 3354.0161 | 3684.3574 | 3547.0153 | 3547.0153 | 3547.0153 | 3547.0153 | 3547.0153 | 3547.0153 | 3547.0153 | 3547.0153 | 3547.0153 | 3547.0153 | 3547.0153 | 3547.0153 | 3547.0153 | 3547.0153 | 3547.0153 | 3547.0153
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | 10.4659 | 11.7471 | 11.8758 | 6.0079 | 6.0679 | 6.0926 | 6.1716 | 6.334 | 6.4707 | 6.5337 | 6.4776 | 6.7127 | 6.75 | 6.7059 | 6.7943 | 6.8357 | 6.8357 | 6.8357 | 6.8357 | 6.8357 | 6.8357 | 6.8357 | 6.8357 | 6.8357 | 6.8357 | 6.8357 | 6.8357 | 6.8357 | 6.8357 | 6.8357 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
98% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
97% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 13.9883 | 15.3913 | 15.4301 | 9.5835 | 9.5942 | 9.6708 | 9.8261 | 10.0996 | 10.242 | 10.3451 | 10.5011 | 10.7003 | 10.9411 | 11.0674 | 11.0264 | 11.067 | 11.067 | 11.067 | 11.067 | 11.067 | 11.067 | 11.067 | 11.067 | 11.067 | 11.067 | 11.067 | 11.067 | 11.067 | 11.067 | 11.067
95% | 9.863 | 11.0991 | 11.2233 | 5.3576 | 5.4155 | 5.4393 | 5.5155 | 5.6723 | 5.8041 | 5.8648 | 5.8107 | 6.0376 | 6.0736 | 6.031 | 6.1164 | 6.1563 | 6.1563 | 6.1563 | 6.1563 | 6.1563 | 6.1563 | 6.1563 | 6.1563 | 6.1563 | 6.1563 | 6.1563 | 6.1563 | 6.1563 | 6.1563 | 6.1563 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
90% | 203.721 | 229.9238 | 232.5569 | 103.5601 | 104.7874 | 105.2916 | 106.9077 | 110.2307 | 113.0262 | 114.313 | 113.1661 | 117.9749 | 118.7375 | 117.835 | 119.6448 | 120.4914 | 120.4914 | 120.4914 | 120.4914 | 120.4914 | 120.4914 | 120.4914 | 120.4914 | 120.4914 | 120.4914 | 120.4914 | 120.4914 | 120.4914 | 120.4914 | 120.4914 |  | 12.9287 | 14.2598 | 14.2965 | 8.4521 | 8.4622 | 8.5349 | 8.6822 | 8.9417 | 9.0768 | 9.1746 | 9.3226 | 9.5116 | 9.7401 | 9.8598 | 9.821 | 9.8595 | 9.8595 | 9.8595 | 9.8595 | 9.8595 | 9.8595 | 9.8595 | 9.8595 | 9.8595 | 9.8595 | 9.8595 | 9.8595 | 9.8595 | 9.8595 | 9.8595
85% | 697.0932 | 790.6056 | 800.0026 | 313.5962 | 317.9759 | 319.7755 | 325.543 | 337.4022 | 347.3787 | 351.9712 | 347.8779 | 365.0395 | 367.7613 | 364.5402 | 370.9993 | 374.0204 | 374.0204 | 374.0204 | 374.0204 | 374.0204 | 374.0204 | 374.0204 | 374.0204 | 374.0204 | 374.0204 | 374.0204 | 374.0204 | 374.0204 | 374.0204 | 374.0204 |  | 11.8691 | 13.1282 | 13.1629 | 7.3206 | 7.3303 | 7.399 | 7.5384 | 7.7838 | 7.9116 | 8.0041 | 8.1441 | 8.3229 | 8.539 | 8.6523 | 8.6156 | 8.652 | 8.652 | 8.652 | 8.652 | 8.652 | 8.652 | 8.652 | 8.652 | 8.652 | 8.652 | 8.652 | 8.652 | 8.652 | 8.652 | 8.652
80% | 1077.8455 | 1229.7508 | 1245.0156 | 407.4437 | 414.5583 | 417.4816 | 426.8506 | 446.1151 | 462.3213 | 469.7816 | 463.1323 | 491.0102 | 495.4317 | 490.1992 | 500.6916 | 505.5992 | 505.5992 | 505.5992 | 505.5992 | 505.5992 | 505.5992 | 505.5992 | 505.5992 | 505.5992 | 505.5992 | 505.5992 | 505.5992 | 505.5992 | 505.5992 | 505.5992 |  | 43.2377 | 47.9863 | 48.1174 | 24.7568 | 24.7931 | 25.0524 | 25.578 | 26.5035 | 26.9857 | 27.3346 | 27.8626 | 28.5367 | 29.3519 | 29.7791 | 29.6406 | 29.7779 | 29.7779 | 29.7779 | 29.7779 | 29.7779 | 29.7779 | 29.7779 | 29.7779 | 29.7779 | 29.7779 | 29.7779 | 29.7779 | 29.7779 | 29.7779 | 29.7779
75% | 1809.2093 | 2079.6387 | 2106.8139 | 520.3866 | 533.0525 | 538.2566 | 554.9357 | 589.2314 | 618.0825 | 631.3636 | 619.5263 | 669.156 | 677.0273 | 667.7121 | 686.3913 | 695.1279 | 695.1279 | 695.1279 | 695.1279 | 695.1279 | 695.1279 | 695.1279 | 695.1279 | 695.1279 | 695.1279 | 695.1279 | 695.1279 | 695.1279 | 695.1279 | 695.1279 |  | 19.4996 | 21.73 | 21.7915 | 10.1155 | 10.1326 | 10.2544 | 10.5012 | 10.9359 | 11.1624 | 11.3263 | 11.5743 | 11.891 | 12.2739 | 12.4745 | 12.4095 | 12.4739 | 12.4739 | 12.4739 | 12.4739 | 12.4739 | 12.4739 | 12.4739 | 12.4739 | 12.4739 | 12.4739 | 12.4739 | 12.4739 | 12.4739 | 12.4739 | 12.4739
70% | 2151.4453 | 2496.8455 | 2531.5545 | 366.7569 | 382.9341 | 389.5811 | 410.884 | 454.6876 | 491.537 | 508.5 | 493.381 | 556.7695 | 566.823 | 554.9253 | 578.7829 | 589.9416 | 589.9416 | 589.9416 | 589.9416 | 589.9416 | 589.9416 | 589.9416 | 589.9416 | 589.9416 | 589.9416 | 589.9416 | 589.9416 | 589.9416 | 589.9416 | 589.9416 |  | 52.1409 | 58.4004 | 58.5732 | 23.558 | 23.6059 | 23.9477 | 24.6405 | 25.8604 | 26.4961 | 26.956 | 27.6521 | 28.5407 | 29.6152 | 30.1784 | 29.9958 | 30.1768 | 30.1768 | 30.1768 | 30.1768 | 30.1768 | 30.1768 | 30.1768 | 30.1768 | 30.1768 | 30.1768 | 30.1768 | 30.1768 | 30.1768 | 30.1768 | 30.1768
65% | 2417.2518 | 2841.3891 | 2884.0103 | 72.8693 | 84.7424 | 89.8688 | 107.2625 | 147.5809 | 186.1487 | 205.3037 | 188.1885 | 263.693 | 276.0384 | 261.4284 | 290.7246 | 304.427 | 304.427 | 304.427 | 304.427 | 304.427 | 304.427 | 304.427 | 304.427 | 304.427 | 304.427 | 304.427 | 304.427 | 304.427 | 304.427 | 304.427 |  | 15.261 | 17.2036 | 17.2572 | 5.5898 | 5.6047 | 5.7108 | 5.9257 | 6.3044 | 6.5016 | 6.6444 | 6.8604 | 7.1362 | 7.4696 | 7.6444 | 7.5877 | 7.6439 | 7.6439 | 7.6439 | 7.6439 | 7.6439 | 7.6439 | 7.6439 | 7.6439 | 7.6439 | 7.6439 | 7.6439 | 7.6439 | 7.6439 | 7.6439 | 7.6439
60% | 3150.8806 | 3770.5408 | 3832.8099 | [8 empty] | 1.3494 | 2.7119 | 1.1504 | 4.9403 | 7.611 | 7.611 | 7.611 | 7.611 | 7.611 | 7.611 | 7.611 | 7.611 | 7.611 | 7.611 | 7.611 | 7.611 | 7.611 | 7.611 | 7.611 |  | 85.4213 | 97.113 | 97.4357 | 21.6251 | 21.7146 | 22.353 | 23.6469 | 25.9257 | 27.113 | 27.972 | 29.2721 | 30.9319 | 32.9389 | 33.9907 | 33.6497 | 33.9877 | 33.9877 | 33.9877 | 33.9877 | 33.9877 | 33.9877 | 33.9877 | 33.9877 | 33.9877 | 33.9877 | 33.9877 | 33.9877 | 33.9877 | 33.9877 | 33.9877
55% | FY25: 3327.6421; FY26: 4090.2265; FY27: 4166.858 |  | 352.7187 | 405.6734 | 407.1346 | 34.0827 | 34.4773 | 37.3475 | 43.2078 | 53.5286 | 58.9064 | 62.797 | 68.6853 | 76.2029 | 85.2932 | 90.0573 | 88.5128 | 90.0436 | 90.0436 | 90.0436 | 90.0436 | 90.0436 | 90.0436 | 90.0436 | 90.0436 | 90.0436 | 90.0436 | 90.0436 | 90.0436 | 90.0436 | 90.0436 | 90.0436
50% | FY25: 3032.8171; FY26: 3898.088; FY27: 3985.0383 |  | 703.3516 | 822.7155 | 826.0092 |  |  | 0.016922 | 0.73534 | 4.5217 | 7.737 | 10.5818 | 15.7009 | 23.6325 | 35.2614 | 42.2254 | 39.9031 | 42.2046 | 42.2046 | 42.2046 | 42.2046 | 42.2046 | 42.2046 | 42.2046 | 42.2046 | 42.2046 | 42.2046 | 42.2046 | 42.2046 | 42.2046 | 42.2046 | 42.2046
45% | FY25: 1765.9337; FY26: 2482.1322; FY27: 2554.1023 |  | 1017.5865 | 1222.642 | 1228.3004
40% | FY25: 607.9205; FY26: 1122.3189; FY27: 1174.0104 |  | 1058.8722 | 1336.5245 | 1344.1862
35% | FY25: 23.196; FY26: 247.1276; FY27: 281.389 |  | 1063.9608 | 1515.0828 | 1527.5312
30% | [31 empty] | 388.5058 | 1015.6243 | 1034.8788
25% | [32 empty] | 10.8714 | 13.2189
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 20082.4323 | 25048.4194 | 25559.0881 | 1778.0185 | 1831.0387 | 1853.0692 | 1924.6299 | 2076.2817 | 2208.4617 | 2270.6953 | 2215.1848 | 2452.9653 | 2492.1812 | 2445.8221 | 2539.4347 | 2584.1083 | 2584.1083 | 2584.1083 | 2584.1083 | 2584.1083 | 2584.1083 | 2584.1083 | 2584.1083 | 2584.1083 | 2584.1083 | 2584.1083 | 2584.1083 | 2584.1083 | 2584.1083 | 2584.1083 | E @ R (MWh) | 4790.9487 | 6548.203 | 6600.6505 | 143.6333 | 144.2578 | 148.7847 | 158.6794 | 178.6011 | 190.2115 | 199.1247 | 213.4199 | 233.0524 | 258.8102 | 273.17 | 268.4508 | 273.1281 | 273.1281 | 273.1281 | 273.1281 | 273.1281 | 273.1281 | 273.1281 | 273.1281 | 273.1281 | 273.1281 | 273.1281 | 273.1281 | 273.1281 | 273.1281 | 273.1281
Option 3 Summer POE50 W E @ R (MWh) N 2 | 14057.7026 | 17533.8936 | 17891.3617 | 1244.613 | 1281.7271 | 1297.1484 | 1347.2409 | 1453.3972 | 1545.9232 | 1589.4867 | 1550.6293 | 1717.0757 | 1744.5269 | 1712.0755 | 1777.6043 | 1808.8758 | 1808.8758 | 1808.8758 | 1808.8758 | 1808.8758 | 1808.8758 | 1808.8758 | 1808.8758 | 1808.8758 | 1808.8758 | 1808.8758 | 1808.8758 | 1808.8758 | 1808.8758 | 1808.8758 | Option 3 Summer POE10 W E @ R (MWh) N 2 | 1437.2846 | 1964.4609 | 1980.1951 | 43.09 | 43.2773 | 44.6354 | 47.6038 | 53.5803 | 57.0635 | 59.7374 | 64.026 | 69.9157 | 77.6431 | 81.951 | 80.5352 | 81.9384 | 81.9384 | 81.9384 | 81.9384 | 81.9384 | 81.9384 | 81.9384 | 81.9384 | 81.9384 | 81.9384 | 81.9384 | 81.9384 | 81.9384 | 81.9384 | 81.9384
Option 4 - Construct 2x 20/33MVA zone substation in Inverloch
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | FY25: 7.4585; FY26: 8.8006; FY27: 8.9429 |  | 8.6919 | 9.9721 | 10.1047
98% | FY25: 0; FY26: 0; FY27: 0 |  | 0 | 0 | 0
97% | FY25: 0; FY26: 0; FY27: 0 |  | 0 | 0 | 0
95% | FY25: 28.0297; FY26: 33.2092; FY27: 33.7584 |  | 32.79 | 37.7305 | 38.2421
90% | FY25: 157.3528; FY26: 187.297; FY27: 190.4721 |  | 184.8731 | 213.4355 | 216.3934
85% | FY25: 626.672; FY26: 751.7764; FY27: 765.0422 |  | 741.6496 | 860.9812 | 873.3391
80% | FY25: 937.6386; FY26: 1135.7149; FY27: 1156.7184 |  | 1119.6813 | 1308.6177 | 1328.1837
75% | FY25: 1618.1428; FY26: 1984.0141; FY27: 2022.8101 |  | 1954.3979 | 2303.3867 | 2339.5275
70% | FY25: 2423.1485; FY26: 3018.6926; FY27: 3081.8425 |  | 2970.4851 | 3538.5488 | 3597.3768
65% | FY25: 2670.9583; FY26: 3400.2393; FY27: 3477.5703 |  | 3341.2062 | 4036.8358 | 4108.8743
60% | FY25: 2886.5439; FY26: 3791.1059; FY27: 3887.0233 |  | 3717.8843 | 4580.7069 | 4670.0597
55% | FY25: 2587.93; FY26: 3569.0383; FY27: 3673.0724 |  | 3489.6205 | 4425.4573 | 4522.3714
50% | FY25: 1977.4132; FY26: 2976.5959; FY27: 3082.5466 |  | 2895.7151 | 3848.7922 | 3947.4917
45% | FY25: 1115.1481; FY26: 2058.8937; FY27: 2158.966 |  | 1982.5003 | 2882.6984 | 2975.9219
40% | FY25: 218.0643; FY26: 1019.3158; FY27: 1109.6444 |  | 950.3606 | 1762.9094 | 1847.056
35% | FY26: 100.0043; FY27: 136.3101 |  | 75.8706 | 543.275 | 608.5783
30% | [32 empty] | 0.62469 | 3.9886
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 17081.9558 | 23794.351 | 24536.8726 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 23231.0692 | 30050.4324 | 30776.634 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 Winter POE50 W E @ R (MWh) N 2 | 11957.3691 | 16656.0457 | 17175.8108 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 4 Winter POE10 W E @ R (MWh) N 2 | 6969.3207 | 9015.1297 | 9232.9902 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | FY25: 10.4659; FY26: 11.7471; FY27: 11.8758 |  | 0 | 0 | 0
98% | FY25: 0; FY26: 0; FY27: 0 |  | 0 | 0 | 0
97% | FY25: 0; FY26: 0; FY27: 0 |  | 13.9883 | 15.3913 | 15.4301
95% | FY25: 9.863; FY26: 11.0991; FY27: 11.2233 |  | 0 | 0 | 0
90% | FY25: 203.721; FY26: 229.9238; FY27: 232.5569 |  | 12.9287 | 14.2598 | 14.2965
85% | FY25: 697.0932; FY26: 790.6056; FY27: 800.0026 |  | 11.8691 | 13.1282 | 13.1629
80% | FY25: 1077.8455; FY26: 1229.7508; FY27: 1245.0156 |  | 43.2377 | 47.9863 | 48.1174
75% | FY25: 1809.2093; FY26: 2079.6387; FY27: 2106.8139 |  | 19.4996 | 21.73 | 21.7915
70% | FY25: 2151.4453; FY26: 2496.8455; FY27: 2531.5545 |  | 52.1409 | 58.4004 | 58.5732
65% | FY25: 2417.2518; FY26: 2841.3891; FY27: 2884.0103 |  | 15.261 | 17.2036 | 17.2572
60% | FY25: 3150.8806; FY26: 3770.5408; FY27: 3832.8099 |  | 85.4213 | 97.113 | 97.4357
55% | FY25: 3327.6421; FY26: 4090.2265; FY27: 4166.858 |  | 352.7187 | 405.6734 | 407.1346
50% | FY25: 3032.8171; FY26: 3898.088; FY27: 3985.0383 |  | 703.3516 | 822.7155 | 826.0092
45% | FY25: 1765.9337; FY26: 2482.1322; FY27: 2554.1023 |  | 1017.5865 | 1222.642 | 1228.3004
40% | FY25: 607.9205; FY26: 1122.3189; FY27: 1174.0104 |  | 1058.8722 | 1336.5245 | 1344.1862
35% | FY25: 23.196; FY26: 247.1276; FY27: 281.389 |  | 1063.9608 | 1515.0828 | 1527.5312
30% | [31 empty] | 388.5058 | 1015.6243 | 1034.8788
25% | [32 empty] | 10.8714 | 13.2189
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 20082.4323 | 25048.4194 | 25559.0881 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 4790.9487 | 6548.203 | 6600.6505 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 Summer POE50 W E @ R (MWh) N 2 | 14057.7026 | 17533.8936 | 17891.3617 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 4 Summer POE10 W E @ R (MWh) N 2 | 1437.2846 | 1964.4609 | 1980.1951 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 - Contract network support services to defer network investment
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | 6.2466 | 7.5066 | 7.6466 | 7.825 | 8.058 | 8.275 | 8.6529 | 9.6102 | 10.1254 | 9.7374 | 10.9107 | 11.1121 | 11.2512 | 11.9656 | 12.0855 | 12.0855 | 12.0855 | 12.0855 | 12.0855 | 12.0855 | 12.0855 | 12.0855 | 12.0855 | 12.0855 | 12.0855 | 12.0855 | 12.0855 | 12.0855 | 12.0855 | 12.0855 |  | 7.4801 | 8.6781 | 8.8084 | 9.2684 | 9.2566 | 9.3527 | 9.7371 | 10.8516 | 11.3098 | 10.8622 | 12.0729 | 11.5491 | 11.9958 | 12.3205 | 12.1865 | 12.1865 | 12.1865 | 12.1865 | 12.1865 | 12.1865 | 12.1865 | 12.1865 | 12.1865 | 12.1865 | 12.1865 | 12.1865 | 12.1865 | 12.1865 | 12.1865 | 12.1865
98% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
97% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
95% | 23.3528 | 28.2154 | 28.7558 | 29.4443 | 30.3433 | 31.1807 | 32.6392 | 36.3339 | 38.3222 | 36.8249 | 41.353 | 42.1302 | 42.6668 | 45.4241 | 45.8868 | 45.8868 | 45.8868 | 45.8868 | 45.8868 | 45.8868 | 45.8868 | 45.8868 | 45.8868 | 45.8868 | 45.8868 | 45.8868 | 45.8868 | 45.8868 | 45.8868 | 45.8868 |  | 28.113 | 32.7366 | 33.2395 | 35.0147 | 34.9692 | 35.3402 | 36.8237 | 41.1248 | 42.893 | 41.1655 | 45.838 | 43.8165 | 45.5406 | 46.7937 | 46.2764 | 46.2764 | 46.2764 | 46.2764 | 46.2764 | 46.2764 | 46.2764 | 46.2764 | 46.2764 | 46.2764 | 46.2764 | 46.2764 | 46.2764 | 46.2764 | 46.2764 | 46.2764
90% | 130.3144 | 158.4262 | 161.5508 | 165.5308 | 170.7286 | 175.5695 | 184.0015 | 205.3615 | 216.8564 | 208.2001 | 234.3781 | 238.8712 | 241.9734 | 257.9142 | 260.5892 | 260.5892 | 260.5892 | 260.5892 | 260.5892 | 260.5892 | 260.5892 | 260.5892 | 260.5892 | 260.5892 | 260.5892 | 260.5892 | 260.5892 | 260.5892 | 260.5892 | 260.5892 |  | 157.8346 | 184.5647 | 187.472 | 197.7346 | 197.4718 | 199.6164 | 208.1929 | 233.059 | 243.2816 | 233.2944 | 260.3073 | 248.6201 | 258.5876 | 265.8321 | 262.8414 | 262.8414 | 262.8414 | 262.8414 | 262.8414 | 262.8414 | 262.8414 | 262.8414 | 262.8414 | 262.8414 | 262.8414 | 262.8414 | 262.8414 | 262.8414 | 262.8414 | 262.8414
85% | 513.7072 | 631.1563 | 644.2108 | 660.8389 | 682.5551 | 702.78 | 738.0084 | 827.2486 | 875.2735 | 839.1083 | 948.4782 | 967.25 | 980.2108 | 1046.8103 | 1057.986 | 1057.986 | 1057.986 | 1057.986 | 1057.986 | 1057.986 | 1057.986 | 1057.986 | 1057.986 | 1057.986 | 1057.986 | 1057.986 | 1057.986 | 1057.986 | 1057.986 | 1057.986 |  | 628.6848 | 740.3612 | 752.5078 | 795.3841 | 794.2861 | 803.2462 | 839.0783 | 942.967 | 985.676 | 943.9503 | 1056.8084 | 1007.9803 | 1049.6234 | 1079.8906 | 1067.3957 | 1067.3957 | 1067.3957 | 1067.3957 | 1067.3957 | 1067.3957 | 1067.3957 | 1067.3957 | 1067.3957 | 1067.3957 | 1067.3957 | 1067.3957 | 1067.3957 | 1067.3957 | 1067.3957 | 1067.3957
80% | 758.7828 | 944.7386 | 965.4076 | 991.7346 | 1026.1176 | 1058.1395 | 1113.9161 | 1255.2092 | 1331.2464 | 1273.9865 | 1447.1506 | 1476.8717 | 1497.3925 | 1602.8387 | 1620.5331 | 1620.5331 | 1620.5331 | 1620.5331 | 1620.5331 | 1620.5331 | 1620.5331 | 1620.5331 | 1620.5331 | 1620.5331 | 1620.5331 | 1620.5331 | 1620.5331 | 1620.5331 | 1620.5331 | 1620.5331 |  | 940.8254 | 1117.6413 | 1136.8729 | 1204.7585 | 1203.0201 | 1217.2065 | 1273.9391 | 1438.4248 | 1506.0455 | 1439.9816 | 1618.6685 | 1541.3596 | 1607.2926 | 1655.2143 | 1635.4313 | 1635.4313 | 1635.4313 | 1635.4313 | 1635.4313 | 1635.4313 | 1635.4313 | 1635.4313 | 1635.4313 | 1635.4313 | 1635.4313 | 1635.4313 | 1635.4313 | 1635.4313 | 1635.4313 | 1635.4313
75% | 1287.774 | 1631.2572 | 1669.4355 | 1718.0648 | 1781.5742 | 1840.7228 | 1943.749 | 2204.7347 | 2345.1848 | 2239.4187 | 2559.2739 | 2614.1725 | 2652.077 | 2846.849 | 2879.5327 | 2879.5327 | 2879.5327 | 2879.5327 | 2879.5327 | 2879.5327 | 2879.5327 | 2879.5327 | 2879.5327 | 2879.5327 | 2879.5327 | 2879.5327 | 2879.5327 | 2879.5327 | 2879.5327 | 2879.5327 |  | 1624.0291 | 1950.6298 | 1986.1529 | 2111.546 | 2108.3349 | 2134.539 | 2239.331 | 2543.1564 | 2668.0601 | 2546.0321 | 2876.0887 | 2733.2896 | 2855.076 | 2943.5932 | 2907.0516 | 2907.0516 | 2907.0516 | 2907.0516 | 2907.0516 | 2907.0516 | 2907.0516 | 2907.0516 | 2907.0516 | 2907.0516 | 2907.0516 | 2907.0516 | 2907.0516 | 2907.0516 | 2907.0516 | 2907.0516
70% | 1885.3934 | 2444.4955 | 2506.6398 | 2585.7957 | 2689.1728 | 2785.4514 | 2953.1514 | 3377.9688 | 3606.5853 | 3434.4254 | 3955.0672 | 4044.4279 | 4106.1266 | 4423.1652 | 4476.3658 | 4476.3658 | 4476.3658 | 4476.3658 | 4476.3658 | 4476.3658 | 4476.3658 | 4476.3658 | 4476.3658 | 4476.3658 | 4476.3658 | 4476.3658 | 4476.3658 | 4476.3658 | 4476.3658 | 4476.3658 |  | 2432.73 | 2964.3517 | 3022.174 | 3226.2816 | 3221.0548 | 3263.7084 | 3434.2827 | 3928.832 | 4132.143 | 3933.5128 | 4470.7598 | 4238.3197 | 4436.5566 | 4580.6397 | 4521.1594 | 4521.1594 | 4521.1594 | 4521.1594 | 4521.1594 | 4521.1594 | 4521.1594 | 4521.1594 | 4521.1594 | 4521.1594 | 4521.1594 | 4521.1594 | 4521.1594 | 4521.1594 | 4521.1594 | 4521.1594
65% | 2012.4435 | 2697.099 | 2773.1986 | 2870.13 | 2996.7217 | 3114.6208 | 3319.9801 | 3840.1955 | 4120.1507 | 3909.3302 | 4546.8886 | 4656.3164 | 4731.8703 | 5120.104 | 5185.2515 | 5185.2515 | 5185.2515 | 5185.2515 | 5185.2515 | 5185.2515 | 5185.2515 | 5185.2515 | 5185.2515 | 5185.2515 | 5185.2515 | 5185.2515 | 5185.2515 | 5185.2515 | 5185.2515 | 5185.2515 |  | 2682.6914 | 3333.6955 | 3404.5026 | 3654.4451 | 3648.0445 | 3700.2765 | 3909.1554 | 4514.7621 | 4763.7291 | 4520.4939 | 5178.3865 | 4893.7491 | 5136.5025 | 5312.9414 | 5240.104 | 5240.104 | 5240.104 | 5240.104 | 5240.104 | 5240.104 | 5240.104 | 5240.104 | 5240.104 | 5240.104 | 5240.104 | 5240.104 | 5240.104 | 5240.104 | 5240.104 | 5240.104
60% | 2069.7566 | 2918.9674 | 3013.3574 | 3133.5861 | 3290.6038 | 3436.8397 | 3691.5565 | 4336.8045 | 4684.0464 | 4422.5557 | 5213.3498 | 5349.0783 | 5442.7914 | 5924.3361 | 6005.1417 | 6005.1417 | 6005.1417 | 6005.1417 | 6005.1417 | 6005.1417 | 6005.1417 | 6005.1417 | 6005.1417 | 6005.1417 | 6005.1417 | 6005.1417 | 6005.1417 | 6005.1417 | 6005.1417 | 6005.1417 |  | 2901.097 | 3708.5684 | 3796.3939 | 4106.4095 | 4098.4706 | 4163.2564 | 4422.3388 | 5173.5017 | 5482.3073 | 5180.6112 | 5996.6268 | 5643.5774 | 5944.6761 | 6163.5215 | 6073.1779 | 6073.1779 | 6073.1779 | 6073.1779 | 6073.1779 | 6073.1779 | 6073.1779 | 6073.1779 | 6073.1779 | 6073.1779 | 6073.1779 | 6073.1779 | 6073.1779 | 6073.1779 | 6073.1779 | 6073.1779
55% | 1702.024 | 2623.0972 | 2725.4747 | 2855.8775 | 3026.1824 | 3184.7932 | 3461.0648 | 4160.9153 | 4537.5417 | 4253.9229 | 5111.636 | 5258.8503 | 5360.4936 | 5882.7879 | 5970.4314 | 5970.4314 | 5970.4314 | 5970.4314 | 5970.4314 | 5970.4314 | 5970.4314 | 5970.4314 | 5970.4314 | 5970.4314 | 5970.4314 | 5970.4314 | 5970.4314 | 5970.4314 | 5970.4314 | 5970.4314 |  | 2603.7146 | 3479.5162 | 3574.7737 | 3911.0237 | 3902.4129 | 3972.6811 | 4253.6877 | 5068.4159 | 5403.3535 | 5076.1271 | 5961.196 | 5578.2706 | 5904.849 | 6142.2138 | 6044.225 | 6044.225 | 6044.225 | 6044.225 | 6044.225 | 6044.225 | 6044.225 | 6044.225 | 6044.225 | 6044.225 | 6044.225 | 6044.225 | 6044.225 | 6044.225 | 6044.225 | 6044.225
50% | 1075.1867 | 2013.2283 | 2117.4919 | 2250.2969 | 2423.7393 | 2585.272 | 2866.6333 | 3579.3767 | 3962.9414 | 3674.0978 | 4547.612 | 4697.5383 | 4801.0541 | 5332.9703 | 5422.2285 | 5422.2285 | 5422.2285 | 5422.2285 | 5422.2285 | 5422.2285 | 5422.2285 | 5422.2285 | 5422.2285 | 5422.2285 | 5422.2285 | 5422.2285 | 5422.2285 | 5422.2285 | 5422.2285 | 5422.2285 |  | 1993.4886 | 2885.4246 | 2982.437 | 3324.8815 | 3316.1121 | 3387.6747 | 3673.8582 | 4503.5957 | 4844.7036 | 4511.4489 | 5412.8229 | 5022.8431 | 5355.4379 | 5597.1755 | 5497.3815 | 5497.3815 | 5497.3815 | 5497.3815 | 5497.3815 | 5497.3815 | 5497.3815 | 5497.3815 | 5497.3815 | 5497.3815 | 5497.3815 | 5497.3815 | 5497.3815 | 5497.3815 | 5497.3815 | 5497.3815
45% | 279.155 | 1148.9761 | 1247.4549 | 1372.8916 | 1536.7109 | 1689.2815 | 1955.0321 | 2628.2308 | 2990.5144 | 2717.6965 | 3542.746 | 3684.354 | 3782.1265 | 4284.5308 | 4368.8366 | 4368.8366 | 4368.8366 | 4368.8366 | 4368.8366 | 4368.8366 | 4368.8366 | 4368.8366 | 4368.8366 | 4368.8366 | 4368.8366 | 4368.8366 | 4368.8366 | 4368.8366 | 4368.8366 | 4368.8366 |  | 1130.3316 | 1972.7809 | 2064.4107 | 2387.8556 | 2379.5727 | 2447.1649 | 2717.4702 | 3501.1718 | 3823.3543 | 3508.5893 | 4359.9529 | 3991.6102 | 4305.7518 | 4534.0772 | 4439.82 | 4439.82 | 4439.82 | 4439.82 | 4439.82 | 4439.82 | 4439.82 | 4439.82 | 4439.82 | 4439.82 | 4439.82 | 4439.82 | 4439.82 | 4439.82 | 4439.82 | 4439.82
40% |  | 239.5309 | 307.2445 | 404.4364 | 547.9762 | 685.6915 | 925.5668 | 1533.2185 | 1860.2277 | 1613.9732 | 2358.6904 | 2486.5105 | 2574.7633 | 3028.2501 | 3104.3474 | 3104.3474 | 3104.3474 | 3104.3474 | 3104.3474 | 3104.3474 | 3104.3474 | 3104.3474 | 3104.3474 | 3104.3474 | 3104.3474 | 3104.3474 | 3104.3474 | 3104.3474 | 3104.3474 | 3104.3474 |  | 227.5845 | 941.5875 | 1024.2956 | 1316.2478 | 1308.7714 | 1369.7823 | 1613.769 | 2321.1641 | 2611.9768 | 2327.8594 | 3096.3286 | 2763.8502 | 3047.4049 | 3253.499 | 3168.4193 | 3168.4193 | 3168.4193 | 3168.4193 | 3168.4193 | 3168.4193 | 3168.4193 | 3168.4193 | 3168.4193 | 3168.4193 | 3168.4193 | 3168.4193 | 3168.4193 | 3168.4193 | 3168.4193 | 3168.4193
35% |  |  |  |  | 0.96213 | 13.4422 | 67.9667 | 373.1851 | 618.8005 | 430.0381 | 1005.6408 | 1104.8378 | 1173.3278 | 1525.2638 | 1584.3204 | 1584.3204 | 1584.3204 | 1584.3204 | 1584.3204 | 1584.3204 | 1584.3204 | 1584.3204 | 1584.3204 | 1584.3204 | 1584.3204 | 1584.3204 | 1584.3204 | 1584.3204 | 1584.3204 | 1584.3204 |  |  | 73.0267 | 101.8684 | 238.5664 | 234.4143 | 269.2615 | 429.8899 | 976.5179 | 1202.2079 | 981.7139 | 1578.0973 | 1320.0718 | 1540.1292 | 1700.072 | 1634.0446 | 1634.0446 | 1634.0446 | 1634.0446 | 1634.0446 | 1634.0446 | 1634.0446 | 1634.0446 | 1634.0446 | 1634.0446 | 1634.0446 | 1634.0446 | 1634.0446 | 1634.0446 | 1634.0446 | 1634.0446
30% | [8 empty] | 4.7748 |  | 83.1881 | 117.6365 | 144.6059 | 321.7202 | 357.4091 | 357.4091 | 357.4091 | 357.4091 | 357.4091 | 357.4091 | 357.4091 | 357.4091 | 357.4091 | 357.4091 | 357.4091 | 357.4091 | 357.4091 | 357.4091 | 357.4091 | 357.4091 | [8 empty] | 74.1363 | 156.7392 | 75.7154 | 353.5713 | 210.8172 | 330.549 | 432.0342 | 388.7173 | 388.7173 | 388.7173 | 388.7173 | 388.7173 | 388.7173 | 388.7173 | 388.7173 | 388.7173 | 388.7173 | 388.7173 | 388.7173 | 388.7173 | 388.7173 | 388.7173 | 388.7173
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 11626.6956 | 17311.8278 | 17986.1903 | 18855.9881 | 20009.3314 | 21098.9391 | 23029.2996 | 28084.7093 | 30890.5657 | 28772.6828 | 35250.2998 | 36382.4582 | 37167.3038 | 41238.3811 | 41927.4362 | 41927.4362 | 41927.4362 | 41927.4362 | 41927.4362 | 41927.4362 | 41927.4362 | 41927.4362 | 41927.4362 | 41927.4362 | 41927.4362 | 41927.4362 | 41927.4362 | 41927.4362 | 41927.4362 | 41927.4362 | E @ R (MWh) | 17185.0185 | 23159.6275 | 23835.1502 | 26254.2233 | 26191.63 | 26703.3758 | 28770.9385 | 34918.9644 | 37499.0029 | 34978.0445 | 41854.7506 | 38857.2271 | 41411.6732 | 43282.6203 | 42508.8496 | 42508.8496 | 42508.8496 | 42508.8496 | 42508.8496 | 42508.8496 | 42508.8496 | 42508.8496 | 42508.8496 | 42508.8496 | 42508.8496 | 42508.8496 | 42508.8496 | 42508.8496 | 42508.8496 | 42508.8496
Option 5 Winter POE50 W E @ R (MWh) N 2 | 8138.6869 | 12118.2795 | 12590.3332 | 13199.1917 | 14006.532 | 14769.2574 | 16120.5097 | 19659.2965 | 21623.396 | 20140.878 | 24675.2099 | 25467.7208 | 26017.1127 | 28866.8668 | 29349.2053 | 29349.2053 | 29349.2053 | 29349.2053 | 29349.2053 | 29349.2053 | 29349.2053 | 29349.2053 | 29349.2053 | 29349.2053 | 29349.2053 | 29349.2053 | 29349.2053 | 29349.2053 | 29349.2053 | 29349.2053 | Option 5 Winter POE10 W E @ R (MWh) N 2 | 5155.5055 | 6947.8882 | 7150.5451 | 7876.267 | 7857.489 | 8011.0128 | 8631.2816 | 10475.6893 | 11249.7009 | 10493.4133 | 12556.4252 | 11657.1681 | 12423.502 | 12984.7861 | 12752.6549 | 12752.6549 | 12752.6549 | 12752.6549 | 12752.6549 | 12752.6549 | 12752.6549 | 12752.6549 | 12752.6549 | 12752.6549 | 12752.6549 | 12752.6549 | 12752.6549 | 12752.6549 | 12752.6549 | 12752.6549
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | 8.9239 | 10.1006 | 10.2264 | 10.1664 | 10.2256 | 10.2446 | 10.312 | 10.4542 | 10.5802 | 10.6355 | 10.5678 | 10.7881 | 10.8074 | 10.7539 | 10.8454 | 10.8868 | 10.8868 | 10.8868 | 10.8868 | 10.8868 | 10.8868 | 10.8868 | 10.8868 | 10.8868 | 10.8868 | 10.8868 | 10.8868 | 10.8868 | 10.8868 | 10.8868 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
98% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
97% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 12.4773 | 13.7779 | 13.8138 | 13.7751 | 13.7851 | 13.8561 | 14 | 14.2535 | 14.3856 | 14.4812 | 14.6258 | 14.8104 | 15.0337 | 15.1507 | 15.1128 | 15.1533 | 15.1533 | 15.1533 | 15.1533 | 15.1533 | 15.1533 | 15.1533 | 15.1533 | 15.1533 | 15.1533 | 15.1533 | 15.1533 | 15.1533 | 15.1533 | 15.1533
95% | 8.3752 | 9.5105 | 9.6319 | 9.574 | 9.6312 | 9.6494 | 9.7145 | 9.8516 | 9.9733 | 10.0266 | 9.9613 | 10.1738 | 10.1925 | 10.1408 | 10.2291 | 10.2691 | 10.2691 | 10.2691 | 10.2691 | 10.2691 | 10.2691 | 10.2691 | 10.2691 | 10.2691 | 10.2691 | 10.2691 | 10.2691 | 10.2691 | 10.2691 | 10.2691 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
90% | 172.1835 | 196.2491 | 198.8232 | 197.5961 | 198.807 | 199.1945 | 200.5741 | 203.4806 | 206.059 | 207.1888 | 205.8042 | 210.3096 | 210.7054 | 209.6106 | 211.4828 | 212.3293 | 212.3293 | 212.3293 | 212.3293 | 212.3293 | 212.3293 | 212.3293 | 212.3293 | 212.3293 | 212.3293 | 212.3293 | 212.3293 | 212.3293 | 212.3293 | 212.3293 |  | 11.4952 | 12.7291 | 12.7631 | 12.7264 | 12.7359 | 12.8032 | 12.9398 | 13.1803 | 13.3056 | 13.3963 | 13.5335 | 13.7086 | 13.9204 | 14.0315 | 13.9955 | 14.0339 | 14.0339 | 14.0339 | 14.0339 | 14.0339 | 14.0339 | 14.0339 | 14.0339 | 14.0339 | 14.0339 | 14.0339 | 14.0339 | 14.0339 | 14.0339 | 14.0339
85% | 584.5423 | 670.4274 | 679.6139 | 675.2346 | 679.556 | 680.9391 | 685.8625 | 696.2352 | 705.4371 | 709.4692 | 704.5278 | 720.6066 | 722.0191 | 718.1118 | 724.7934 | 727.8144 | 727.8144 | 727.8144 | 727.8144 | 727.8144 | 727.8144 | 727.8144 | 727.8144 | 727.8144 | 727.8144 | 727.8144 | 727.8144 | 727.8144 | 727.8144 | 727.8144 |  | 10.513 | 11.6802 | 11.7124 | 11.6777 | 11.6866 | 11.7504 | 11.8796 | 12.1071 | 12.2256 | 12.3113 | 12.4411 | 12.6068 | 12.8072 | 12.9122 | 12.8782 | 12.9146 | 12.9146 | 12.9146 | 12.9146 | 12.9146 | 12.9146 | 12.9146 | 12.9146 | 12.9146 | 12.9146 | 12.9146 | 12.9146 | 12.9146 | 12.9146 | 12.9146
80% | 895.0132 | 1034.5285 | 1049.4514 | 1042.3376 | 1049.3574 | 1051.6041 | 1059.6019 | 1076.4517 | 1091.3996 | 1097.9495 | 1089.9226 | 1116.0416 | 1118.3362 | 1111.989 | 1122.8428 | 1127.7503 | 1127.7503 | 1127.7503 | 1127.7503 | 1127.7503 | 1127.7503 | 1127.7503 | 1127.7503 | 1127.7503 | 1127.7503 | 1127.7503 | 1127.7503 | 1127.7503 | 1127.7503 | 1127.7503 |  | 38.1235 | 42.5256 | 42.647 | 42.5161 | 42.5497 | 42.7901 | 43.2773 | 44.1353 | 44.5823 | 44.9057 | 45.3952 | 46.0201 | 46.7758 | 47.1719 | 47.0435 | 47.1807 | 47.1807 | 47.1807 | 47.1807 | 47.1807 | 47.1807 | 47.1807 | 47.1807 | 47.1807 | 47.1807 | 47.1807 | 47.1807 | 47.1807 | 47.1807 | 47.1807
75% | 1483.722 | 1732.0941 | 1758.6607 | 1745.9963 | 1758.4934 | 1762.4931 | 1776.7311 | 1806.7279 | 1833.339 | 1844.9995 | 1830.7095 | 1877.2079 | 1881.2929 | 1869.9932 | 1889.3157 | 1898.0524 | 1898.0524 | 1898.0524 | 1898.0524 | 1898.0524 | 1898.0524 | 1898.0524 | 1898.0524 | 1898.0524 | 1898.0524 | 1898.0524 | 1898.0524 | 1898.0524 | 1898.0524 | 1898.0524 |  | 17.0974 | 19.1651 | 19.2221 | 19.1606 | 19.1764 | 19.2894 | 19.5182 | 19.9212 | 20.1311 | 20.283 | 20.513 | 20.8065 | 21.1614 | 21.3474 | 21.2871 | 21.3516 | 21.3516 | 21.3516 | 21.3516 | 21.3516 | 21.3516 | 21.3516 | 21.3516 | 21.3516 | 21.3516 | 21.3516 | 21.3516 | 21.3516 | 21.3516 | 21.3516
70% | 1735.7235 | 2052.9515 | 2086.8831 | 2070.7077 | 2086.6694 | 2091.7779 | 2109.9631 | 2148.2759 | 2182.2644 | 2197.1575 | 2178.9059 | 2238.295 | 2243.5125 | 2229.0802 | 2253.7595 | 2264.9182 | 2264.9182 | 2264.9182 | 2264.9182 | 2264.9182 | 2264.9182 | 2264.9182 | 2264.9182 | 2264.9182 | 2264.9182 | 2264.9182 | 2264.9182 | 2264.9182 | 2264.9182 | 2264.9182 |  | 45.3994 | 51.2022 | 51.3623 | 51.1896 | 51.234 | 51.5509 | 52.1931 | 53.324 | 53.9133 | 54.3397 | 54.9849 | 55.8087 | 56.8048 | 57.3268 | 57.1576 | 57.3385 | 57.3385 | 57.3385 | 57.3385 | 57.3385 | 57.3385 | 57.3385 | 57.3385 | 57.3385 | 57.3385 | 57.3385 | 57.3385 | 57.3385 | 57.3385 | 57.3385
65% | 1906.7625 | 2296.3055 | 2337.972 | 2318.1094 | 2337.7097 | 2343.9827 | 2366.3134 | 2413.36 | 2455.0964 | 2473.3845 | 2450.9723 | 2523.8997 | 2530.3065 | 2512.5843 | 2542.8894 | 2556.5918 | 2556.5918 | 2556.5918 | 2556.5918 | 2556.5918 | 2556.5918 | 2556.5918 | 2556.5918 | 2556.5918 | 2556.5918 | 2556.5918 | 2556.5918 | 2556.5918 | 2556.5918 | 2556.5918 |  | 13.1688 | 14.9697 | 15.0194 | 14.9658 | 14.9796 | 15.0779 | 15.2772 | 15.6282 | 15.8111 | 15.9434 | 16.1436 | 16.3993 | 16.7084 | 16.8704 | 16.8179 | 16.8741 | 16.8741 | 16.8741 | 16.8741 | 16.8741 | 16.8741 | 16.8741 | 16.8741 | 16.8741 | 16.8741 | 16.8741 | 16.8741 | 16.8741 | 16.8741 | 16.8741
60% | 2405.0609 | 2974.1792 | 3035.0536 | 3006.0345 | 3034.6703 | 3043.8352 | 3076.4601 | 3145.1946 | 3206.1711 | 3232.8899 | 3200.1459 | 3306.6921 | 3316.0523 | 3290.1604 | 3334.4358 | 3354.4549 | 3354.4549 | 3354.4549 | 3354.4549 | 3354.4549 | 3354.4549 | 3354.4549 | 3354.4549 | 3354.4549 | 3354.4549 | 3354.4549 | 3354.4549 | 3354.4549 | 3354.4549 | 3354.4549 |  | 72.8295 | 83.668 | 83.967 | 83.6446 | 83.7275 | 84.3194 | 85.5188 | 87.6312 | 88.7319 | 89.5282 | 90.7334 | 92.2721 | 94.1326 | 95.1077 | 94.7916 | 95.1296 | 95.1296 | 95.1296 | 95.1296 | 95.1296 | 95.1296 | 95.1296 | 95.1296 | 95.1296 | 95.1296 | 95.1296 | 95.1296 | 95.1296 | 95.1296 | 95.1296
55% | 2409.7996 | 3110.1847 | 3185.0998 | 3149.3874 | 3184.628 | 3195.9067 | 3236.0566 | 3320.6447 | 3395.6854 | 3428.5669 | 3388.2705 | 3519.3914 | 3530.9106 | 3499.0468 | 3553.5343 | 3578.1707 | 3578.1707 | 3578.1707 | 3578.1707 | 3578.1707 | 3578.1707 | 3578.1707 | 3578.1707 | 3578.1707 | 3578.1707 | 3578.1707 | 3578.1707 | 3578.1707 | 3578.1707 | 3578.1707 |  | 295.6877 | 344.7776 | 346.1322 | 344.6717 | 345.0473 | 347.728 | 353.1606 | 362.7282 | 367.7135 | 371.3201 | 376.7787 | 383.7476 | 392.1745 | 396.5908 | 395.1591 | 396.6899 | 396.6899 | 396.6899 | 396.6899 | 396.6899 | 396.6899 | 396.6899 | 396.6899 | 396.6899 | 396.6899 | 396.6899 | 396.6899 | 396.6899 | 396.6899 | 396.6899
50% | 1991.3816 | 2786.0777 | 2871.0805 | 2830.5593 | 2870.5452 | 2883.3427 | 2928.899 | 3024.8774 | 3110.0227 | 3147.3319 | 3101.6094 | 3250.3866 | 3263.4568 | 3227.3023 | 3289.1269 | 3317.0808 | 3317.0808 | 3317.0808 | 3317.0808 | 3317.0808 | 3317.0808 | 3317.0808 | 3317.0808 | 3317.0808 | 3317.0808 | 3317.0808 | 3317.0808 | 3317.0808 | 3317.0808 | 3317.0808 |  | 574.7994 | 685.4517 | 688.5051 | 685.213 | 686.0597 | 692.1021 | 704.3477 | 725.9137 | 737.1509 | 745.2807 | 757.5846 | 773.293 | 792.288 | 802.2427 | 799.0155 | 802.4661 | 802.4661 | 802.4661 | 802.4661 | 802.4661 | 802.4661 | 802.4661 | 802.4661 | 802.4661 | 802.4661 | 802.4661 | 802.4661 | 802.4661 | 802.4661 | 802.4661
45% | 903.9212 | 1561.7037 | 1632.0619 | 1598.5218 | 1631.6188 | 1642.2115 | 1679.9191 | 1759.3619 | 1829.8381 | 1860.7195 | 1822.8742 | 1946.0194 | 1956.8379 | 1926.9123 | 1978.0855 | 2001.2234 | 2001.2234 | 2001.2234 | 2001.2234 | 2001.2234 | 2001.2234 | 2001.2234 | 2001.2234 | 2001.2234 | 2001.2234 | 2001.2234 | 2001.2234 | 2001.2234 | 2001.2234 | 2001.2234 |  | 796.7464 | 986.8362 | 992.0816 | 986.4263 | 987.8807 | 998.261 | 1019.2978 | 1056.346 | 1075.6505 | 1089.6166 | 1110.7535 | 1137.739 | 1170.3705 | 1187.4718 | 1181.9278 | 1187.8555 | 1187.8555 | 1187.8555 | 1187.8555 | 1187.8555 | 1187.8555 | 1187.8555 | 1187.8555 | 1187.8555 | 1187.8555 | 1187.8555 | 1187.8555 | 1187.8555 | 1187.8555 | 1187.8555
40% | 86.5836 | 461.2354 | 511.7691 | 487.6795 | 511.4509 | 519.0589 | 546.1418 | 603.2004 | 653.8188 | 675.9989 | 648.8171 | 737.2643 | 745.0345 | 723.5409 | 760.2952 | 776.9136 | 776.9136 | 776.9136 | 776.9136 | 776.9136 | 776.9136 | 776.9136 | 776.9136 | 776.9136 | 776.9136 | 776.9136 | 776.9136 | 776.9136 | 776.9136 | 776.9136 |  | 759.847 | 1017.2352 | 1024.3377 | 1016.6802 | 1018.6495 | 1032.7048 | 1061.1894 | 1111.354 | 1137.4929 | 1156.4034 | 1185.0236 | 1221.563 | 1265.7471 | 1288.9029 | 1281.3961 | 1289.4225 | 1289.4225 | 1289.4225 | 1289.4225 | 1289.4225 | 1289.4225 | 1289.4225 | 1289.4225 | 1289.4225 | 1289.4225 | 1289.4225 | 1289.4225 | 1289.4225 | 1289.4225 | 1289.4225
35% |  | 2.4306 | 7.231 | 4.6286 | 7.1929 | 8.1303 | 11.9225 | 22.2076 | 33.8871 | 39.7477 | 32.6276 | 58.2428 | 60.8274 | 53.8084 | 66.0584 | 71.9865 | 71.9865 | 71.9865 | 71.9865 | 71.9865 | 71.9865 | 71.9865 | 71.9865 | 71.9865 | 71.9865 | 71.9865 | 71.9865 | 71.9865 | 71.9865 | 71.9865 |  | 578.1126 | 996.3101 | 1007.85 | 995.4082 | 998.6079 | 1021.4447 | 1067.7256 | 1149.2317 | 1191.7015 | 1222.4269 | 1268.9282 | 1328.2963 | 1400.0856 | 1437.7085 | 1425.5116 | 1438.5526 | 1438.5526 | 1438.5526 | 1438.5526 | 1438.5526 | 1438.5526 | 1438.5526 | 1438.5526 | 1438.5526 | 1438.5526 | 1438.5526 | 1438.5526 | 1438.5526 | 1438.5526 | 1438.5526
30% | [31 empty] | 30.5184 | 316.7479 | 328.5197 | 315.8361 | 319.0763 | 342.6364 | 392.6921 | 488.1956 | 541.5809 | 581.7151 | 644.8282 | 729.474 | 837.7547 | 895.9471 | 877.0819 | 897.2528 | 897.2528 | 897.2528 | 897.2528 | 897.2528 | 897.2528 | 897.2528 | 897.2528 | 897.2528 | 897.2528 | 897.2528 | 897.2528 | 897.2528 | 897.2528 | 897.2528
25% | [43 empty] | 0.019885 | 1.3907 | 0.71115 | 1.446 | 1.446 | 1.446 | 1.446 | 1.446 | 1.446 | 1.446 | 1.446 | 1.446 | 1.446 | 1.446 | 1.446 | 1.446 | 1.446 | 1.446
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 14446.073 | 18708.9986 | 19179.8229 | 18955.0679 | 19176.8503 | 19247.947 | 19501.4871 | 20037.9204 | 20516.3365 | 20726.7053 | 20468.959 | 21310.0658 | 21384.2891 | 21179.1046 | 21530.2173 | 21689.3579 | 21689.3579 | 21689.3579 | 21689.3579 | 21689.3579 | 21689.3579 | 21689.3579 | 21689.3579 | 21689.3579 | 21689.3579 | 21689.3579 | 21689.3579 | 21689.3579 | 21689.3579 | 21689.3579 | E @ R (MWh) | 3224.2475 | 4551.1056 | 4591.5542 | 4547.9526 | 4559.1443 | 4639.4513 | 4804.487 | 5102.4105 | 5261.2328 | 5377.6321 | 5556.1446 | 5788.08 | 6074.4268 | 6227.2714 | 6177.4885 | 6230.7253 | 6230.7253 | 6230.7253 | 6230.7253 | 6230.7253 | 6230.7253 | 6230.7253 | 6230.7253 | 6230.7253 | 6230.7253 | 6230.7253 | 6230.7253 | 6230.7253 | 6230.7253 | 6230.7253
Option 5 Summer POE50 W E @ R (MWh) N 2 | 10112.2511 | 13096.299 | 13425.876 | 13268.5476 | 13423.7952 | 13473.5629 | 13651.041 | 14026.5443 | 14361.4355 | 14508.6937 | 14328.2713 | 14917.046 | 14969.0024 | 14825.3732 | 15071.1521 | 15182.5505 | 15182.5505 | 15182.5505 | 15182.5505 | 15182.5505 | 15182.5505 | 15182.5505 | 15182.5505 | 15182.5505 | 15182.5505 | 15182.5505 | 15182.5505 | 15182.5505 | 15182.5505 | 15182.5505 | Option 5 Summer POE10 W E @ R (MWh) N 2 | 967.2743 | 1365.3317 | 1377.4663 | 1364.3858 | 1367.7433 | 1391.8354 | 1441.3461 | 1530.7231 | 1578.3699 | 1613.2896 | 1666.8434 | 1736.424 | 1822.3281 | 1868.1814 | 1853.2466 | 1869.2176 | 1869.2176 | 1869.2176 | 1869.2176 | 1869.2176 | 1869.2176 | 1869.2176 | 1869.2176 | 1869.2176 | 1869.2176 | 1869.2176 | 1869.2176 | 1869.2176 | 1869.2176 | 1869.2176
Option 6 -
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | 7.4585 | 8.8006 | 8.9429 | 9.1188 | 9.3524 | 9.5739 | 9.9609 | 10.9342 | 11.4578 | 11.0758 | 12.2583 | 12.4713 | 12.6244 | 13.3463 | 13.4638 | 13.4638 | 13.4638 | 13.4638 | 13.4638 | 13.4638 | 13.4638 | 13.4638 | 13.4638 | 13.4638 | 13.4638 | 13.4638 | 13.4638 | 13.4638 | 13.4638 | 13.4638 |  | 8.6919 | 9.9721 | 10.1047 | 10.5622 | 10.551 | 10.6516 | 11.0451 | 12.1756 | 12.6421 | 12.2006 | 13.4204 | 12.9082 | 13.3691 | 13.7012 | 13.5647 | 13.5647 | 13.5647 | 13.5647 | 13.5647 | 13.5647 | 13.5647 | 13.5647 | 13.5647 | 13.5647 | 13.5647 | 13.5647 | 13.5647 | 13.5647 | 13.5647 | 13.5647
98% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
97% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
95% | 28.0297 | 33.2092 | 33.7584 | 34.4374 | 35.339 | 36.1936 | 37.6872 | 41.4437 | 43.4642 | 41.9901 | 46.5535 | 47.3756 | 47.9667 | 50.7525 | 51.2059 | 51.2059 | 51.2059 | 51.2059 | 51.2059 | 51.2059 | 51.2059 | 51.2059 | 51.2059 | 51.2059 | 51.2059 | 51.2059 | 51.2059 | 51.2059 | 51.2059 | 51.2059 |  | 32.79 | 37.7305 | 38.2421 | 40.0078 | 39.9648 | 40.3531 | 41.8717 | 46.2346 | 48.035 | 46.3308 | 51.0385 | 49.062 | 50.8404 | 52.1221 | 51.5955 | 51.5955 | 51.5955 | 51.5955 | 51.5955 | 51.5955 | 51.5955 | 51.5955 | 51.5955 | 51.5955 | 51.5955 | 51.5955 | 51.5955 | 51.5955 | 51.5955 | 51.5955
90% | 157.3528 | 187.297 | 190.4721 | 194.3976 | 199.6095 | 204.5504 | 213.1852 | 234.9023 | 246.5833 | 238.0616 | 264.4434 | 269.1966 | 272.6134 | 288.719 | 291.3405 | 291.3405 | 291.3405 | 291.3405 | 291.3405 | 291.3405 | 291.3405 | 291.3405 | 291.3405 | 291.3405 | 291.3405 | 291.3405 | 291.3405 | 291.3405 | 291.3405 | 291.3405 |  | 184.8731 | 213.4355 | 216.3934 | 226.6014 | 226.3526 | 228.5973 | 237.3766 | 262.5998 | 273.0084 | 263.1559 | 290.3726 | 278.9455 | 289.2275 | 296.6368 | 293.5927 | 293.5927 | 293.5927 | 293.5927 | 293.5927 | 293.5927 | 293.5927 | 293.5927 | 293.5927 | 293.5927 | 293.5927 | 293.5927 | 293.5927 | 293.5927 | 293.5927 | 293.5927
85% | 626.672 | 751.7764 | 765.0422 | 781.4425 | 803.2172 | 823.8602 | 859.9357 | 950.668 | 999.4703 | 963.8676 | 1074.0886 | 1093.9472 | 1108.2222 | 1175.5104 | 1186.4628 | 1186.4628 | 1186.4628 | 1186.4628 | 1186.4628 | 1186.4628 | 1186.4628 | 1186.4628 | 1186.4628 | 1186.4628 | 1186.4628 | 1186.4628 | 1186.4628 | 1186.4628 | 1186.4628 | 1186.4628 |  | 741.6496 | 860.9812 | 873.3391 | 915.9877 | 914.9483 | 924.3264 | 961.0057 | 1066.3864 | 1109.8728 | 1068.7096 | 1182.4188 | 1134.6775 | 1177.6348 | 1208.5906 | 1195.8725 | 1195.8725 | 1195.8725 | 1195.8725 | 1195.8725 | 1195.8725 | 1195.8725 | 1195.8725 | 1195.8725 | 1195.8725 | 1195.8725 | 1195.8725 | 1195.8725 | 1195.8725 | 1195.8725 | 1195.8725
80% | 937.6386 | 1135.7149 | 1156.7184 | 1182.6849 | 1217.1605 | 1249.8444 | 1306.9623 | 1450.6177 | 1527.8858 | 1471.5164 | 1646.0281 | 1677.4699 | 1700.0714 | 1806.608 | 1823.9489 | 1823.9489 | 1823.9489 | 1823.9489 | 1823.9489 | 1823.9489 | 1823.9489 | 1823.9489 | 1823.9489 | 1823.9489 | 1823.9489 | 1823.9489 | 1823.9489 | 1823.9489 | 1823.9489 | 1823.9489 |  | 1119.6813 | 1308.6177 | 1328.1837 | 1395.7087 | 1394.063 | 1408.9114 | 1466.9853 | 1633.8333 | 1702.6848 | 1637.5115 | 1817.5461 | 1741.9578 | 1809.9715 | 1858.9836 | 1838.8471 | 1838.8471 | 1838.8471 | 1838.8471 | 1838.8471 | 1838.8471 | 1838.8471 | 1838.8471 | 1838.8471 | 1838.8471 | 1838.8471 | 1838.8471 | 1838.8471 | 1838.8471 | 1838.8471 | 1838.8471
75% | 1618.1428 | 1984.0141 | 2022.8101 | 2070.7733 | 2134.4541 | 2194.8252 | 2300.329 | 2565.6781 | 2708.4018 | 2604.2807 | 2926.6253 | 2984.7021 | 3026.4498 | 3223.236 | 3255.2667 | 3255.2667 | 3255.2667 | 3255.2667 | 3255.2667 | 3255.2667 | 3255.2667 | 3255.2667 | 3255.2667 | 3255.2667 | 3255.2667 | 3255.2667 | 3255.2667 | 3255.2667 | 3255.2667 | 3255.2667 |  | 1954.3979 | 2303.3867 | 2339.5275 | 2464.2546 | 2461.2148 | 2488.6415 | 2595.9111 | 2904.0999 | 3031.2772 | 2910.894 | 3243.44 | 3103.8192 | 3229.4488 | 3319.9801 | 3282.7856 | 3282.7856 | 3282.7856 | 3282.7856 | 3282.7856 | 3282.7856 | 3282.7856 | 3282.7856 | 3282.7856 | 3282.7856 | 3282.7856 | 3282.7856 | 3282.7856 | 3282.7856 | 3282.7856 | 3282.7856
70% | 2423.1485 | 3018.6926 | 3081.8425 | 3159.9143 | 3263.5701 | 3361.8387 | 3533.5717 | 3965.4915 | 4197.8089 | 4028.3265 | 4553.0204 | 4647.5545 | 4715.5089 | 5035.8261 | 5087.9638 | 5087.9638 | 5087.9638 | 5087.9638 | 5087.9638 | 5087.9638 | 5087.9638 | 5087.9638 | 5087.9638 | 5087.9638 | 5087.9638 | 5087.9638 | 5087.9638 | 5087.9638 | 5087.9638 | 5087.9638 |  | 2970.4851 | 3538.5488 | 3597.3768 | 3800.4002 | 3795.4522 | 3840.0957 | 4014.703 | 4516.3548 | 4723.3667 | 4527.4139 | 5068.713 | 4841.4463 | 5045.9389 | 5193.3006 | 5132.7574 | 5132.7574 | 5132.7574 | 5132.7574 | 5132.7574 | 5132.7574 | 5132.7574 | 5132.7574 | 5132.7574 | 5132.7574 | 5132.7574 | 5132.7574 | 5132.7574 | 5132.7574 | 5132.7574 | 5132.7574
65% | 2670.9583 | 3400.2393 | 3477.5703 | 3573.1741 | 3700.1072 | 3820.4432 | 4030.7411 | 4559.6539 | 4844.1411 | 4636.5993 | 5279.1198 | 5394.8827 | 5478.0971 | 5870.3455 | 5934.1915 | 5934.1915 | 5934.1915 | 5934.1915 | 5934.1915 | 5934.1915 | 5934.1915 | 5934.1915 | 5934.1915 | 5934.1915 | 5934.1915 | 5934.1915 | 5934.1915 | 5934.1915 | 5934.1915 | 5934.1915 |  | 3341.2062 | 4036.8358 | 4108.8743 | 4357.4892 | 4351.43 | 4406.0989 | 4619.9164 | 5234.2205 | 5487.7194 | 5247.763 | 5910.6177 | 5632.3154 | 5882.7294 | 6063.1829 | 5989.044 | 5989.044 | 5989.044 | 5989.044 | 5989.044 | 5989.044 | 5989.044 | 5989.044 | 5989.044 | 5989.044 | 5989.044 | 5989.044 | 5989.044 | 5989.044 | 5989.044 | 5989.044
60% | 2886.5439 | 3791.1059 | 3887.0233 | 4005.6052 | 4163.0464 | 4312.3049 | 4573.1473 | 5229.1832 | 5582.0462 | 5324.6222 | 6121.571 | 6265.1573 | 6368.3721 | 6854.8965 | 6934.0877 | 6934.0877 | 6934.0877 | 6934.0877 | 6934.0877 | 6934.0877 | 6934.0877 | 6934.0877 | 6934.0877 | 6934.0877 | 6934.0877 | 6934.0877 | 6934.0877 | 6934.0877 | 6934.0877 | 6934.0877 |  | 3717.8843 | 4580.7069 | 4670.0597 | 4978.4286 | 4970.9132 | 5038.7216 | 5303.9296 | 6065.8803 | 6380.3071 | 6082.6777 | 6904.848 | 6559.6564 | 6870.2568 | 7094.0819 | 7002.1239 | 7002.1239 | 7002.1239 | 7002.1239 | 7002.1239 | 7002.1239 | 7002.1239 | 7002.1239 | 7002.1239 | 7002.1239 | 7002.1239 | 7002.1239 | 7002.1239 | 7002.1239 | 7002.1239 | 7002.1239
55% | 2587.93 | 3569.0383 | 3673.0724 | 3801.6891 | 3972.4533 | 4134.3425 | 4417.258 | 5128.8093 | 5511.5325 | 5232.3246 | 6096.7133 | 6252.4502 | 6364.3994 | 6892.0947 | 6977.9873 | 6977.9873 | 6977.9873 | 6977.9873 | 6977.9873 | 6977.9873 | 6977.9873 | 6977.9873 | 6977.9873 | 6977.9873 | 6977.9873 | 6977.9873 | 6977.9873 | 6977.9873 | 6977.9873 | 6977.9873 |  | 3489.6205 | 4425.4573 | 4522.3714 | 4856.8353 | 4848.6838 | 4922.2304 | 5209.881 | 6036.3099 | 6377.3443 | 6054.5287 | 6946.2732 | 6571.8705 | 6908.7548 | 7151.5206 | 7051.7809 | 7051.7809 | 7051.7809 | 7051.7809 | 7051.7809 | 7051.7809 | 7051.7809 | 7051.7809 | 7051.7809 | 7051.7809 | 7051.7809 | 7051.7809 | 7051.7809 | 7051.7809 | 7051.7809 | 7051.7809
50% | 1977.4132 | 2976.5959 | 3082.5466 | 3213.5326 | 3387.4428 | 3552.3143 | 3840.4419 | 4565.1017 | 4954.8755 | 4670.5239 | 5550.8367 | 5709.4427 | 5823.4542 | 6360.871 | 6448.3459 | 6448.3459 | 6448.3459 | 6448.3459 | 6448.3459 | 6448.3459 | 6448.3459 | 6448.3459 | 6448.3459 | 6448.3459 | 6448.3459 | 6448.3459 | 6448.3459 | 6448.3459 | 6448.3459 | 6448.3459 |  | 2895.7151 | 3848.7922 | 3947.4917 | 4288.1172 | 4279.8156 | 4354.717 | 4647.6668 | 5489.3206 | 5836.6377 | 5507.875 | 6416.0476 | 6034.7475 | 6377.838 | 6625.0761 | 6523.499 | 6523.499 | 6523.499 | 6523.499 | 6523.499 | 6523.499 | 6523.499 | 6523.499 | 6523.499 | 6523.499 | 6523.499 | 6523.499 | 6523.499 | 6523.499 | 6523.499 | 6523.499
45% | 1115.1481 | 2058.8937 | 2158.966 | 2282.6846 | 2446.9458 | 2602.6699 | 2874.8114 | 3559.2653 | 3927.4136 | 3658.8385 | 4490.3094 | 4640.1156 | 4747.8014 | 5255.401 | 5338.0226 | 5338.0226 | 5338.0226 | 5338.0226 | 5338.0226 | 5338.0226 | 5338.0226 | 5338.0226 | 5338.0226 | 5338.0226 | 5338.0226 | 5338.0226 | 5338.0226 | 5338.0226 | 5338.0226 | 5338.0226 |  | 1982.5003 | 2882.6984 | 2975.9219 | 3297.6486 | 3289.8076 | 3360.5533 | 3637.2496 | 4432.2063 | 4760.2534 | 4449.7313 | 5307.5163 | 4947.3717 | 5271.4266 | 5504.9474 | 5409.006 | 5409.006 | 5409.006 | 5409.006 | 5409.006 | 5409.006 | 5409.006 | 5409.006 | 5409.006 | 5409.006 | 5409.006 | 5409.006 | 5409.006 | 5409.006 | 5409.006 | 5409.006
40% | 218.0643 | 1019.3158 | 1109.6444 | 1221.317 | 1369.5846 | 1510.1463 | 1755.7904 | 2373.6013 | 2705.9042 | 2463.4794 | 3213.9927 | 3349.2128 | 3446.4136 | 3904.5899 | 3979.1669 | 3979.1669 | 3979.1669 | 3979.1669 | 3979.1669 | 3979.1669 | 3979.1669 | 3979.1669 | 3979.1669 | 3979.1669 | 3979.1669 | 3979.1669 | 3979.1669 | 3979.1669 | 3979.1669 | 3979.1669 |  | 950.3606 | 1762.9094 | 1847.056 | 2137.4573 | 2130.3798 | 2194.2372 | 2443.9925 | 3161.5469 | 3457.6532 | 3177.3656 | 3951.6309 | 3626.5524 | 3919.0552 | 4129.8388 | 4043.2389 | 4043.2389 | 4043.2389 | 4043.2389 | 4043.2389 | 4043.2389 | 4043.2389 | 4043.2389 | 4043.2389 | 4043.2389 | 4043.2389 | 4043.2389 | 4043.2389 | 4043.2389 | 4043.2389 | 4043.2389
35% |  | 100.0043 | 136.3101 | 188.3336 | 269.145 | 357.6005 | 537.7501 | 1017.2126 | 1275.1019 | 1086.964 | 1669.4126 | 1774.3523 | 1849.7867 | 2205.3621 | 2263.2389 | 2263.2389 | 2263.2389 | 2263.2389 | 2263.2389 | 2263.2389 | 2263.2389 | 2263.2389 | 2263.2389 | 2263.2389 | 2263.2389 | 2263.2389 | 2263.2389 | 2263.2389 | 2263.2389 | 2263.2389 |  | 75.8706 | 543.275 | 608.5783 | 833.9491 | 828.4565 | 878.0141 | 1071.8409 | 1628.7111 | 1858.5094 | 1640.9875 | 2241.8691 | 1989.5864 | 2216.5882 | 2380.1703 | 2312.963 | 2312.963 | 2312.963 | 2312.963 | 2312.963 | 2312.963 | 2312.963 | 2312.963 | 2312.963 | 2312.963 | 2312.963 | 2312.963 | 2312.963 | 2312.963 | 2312.963 | 2312.963
30% | [6 empty] | 0.47307 | 86.92 | 189.3305 | 111.0221 | 411.6753 | 482.9899 | 535.3611 | 782.2235 | 822.4051 | 822.4051 | 822.4051 | 822.4051 | 822.4051 | 822.4051 | 822.4051 | 822.4051 | 822.4051 | 822.4051 | 822.4051 | 822.4051 | 822.4051 | 822.4051 | 822.4051 | 822.4051 |  |  | 0.62469 | 3.9886 | 37.019 | 35.8334 | 47.1947 | 105.5643 | 385.3047 | 541.4169 | 393.1792 | 807.5688 | 632.4187 | 790.0173 | 903.5861 | 856.9266 | 856.9266 | 856.9266 | 856.9266 | 856.9266 | 856.9266 | 856.9266 | 856.9266 | 856.9266 | 856.9266 | 856.9266 | 856.9266 | 856.9266 | 856.9266 | 856.9266 | 856.9266
25% | [11 empty] | 0.074459 | 1.4981 | 31.3754 | 39.665 | 39.665 | 39.665 | 39.665 | 39.665 | 39.665 | 39.665 | 39.665 | 39.665 | 39.665 | 39.665 | 39.665 | 39.665 | 39.665 | 39.665 | 39.665 | [9 empty] | 1.778 |  | 36.4973 | 8.794 | 32.9113 | 59.1747 | 47.515 | 47.515 | 47.515 | 47.515 | 47.515 | 47.515 | 47.515 | 47.515 | 47.515 | 47.515 | 47.515 | 47.515 | 47.515 | 47.515 | 47.515 | 47.515
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 17081.9558 | 23794.351 | 24536.8726 | 25461.914 | 26701.7135 | 27888.803 | 29989.1249 | 35382.088 | 38338.1632 | 36178.0578 | 42923.0818 | 44155.3813 | 45043.6541 | 49253.6461 | 49942.2957 | 49942.2957 | 49942.2957 | 49942.2957 | 49942.2957 | 49942.2957 | 49942.2957 | 49942.2957 | 49942.2957 | 49942.2957 | 49942.2957 | 49942.2957 | 49942.2957 | 49942.2957 | 49942.2957 | 49942.2957 | E @ R (MWh) | 23231.0692 | 30050.4324 | 30776.634 | 33304.0623 | 33242.0879 | 33801.9108 | 36005.2501 | 42446.433 | 45146.4814 | 42590.1209 | 49687.9201 | 46694.4681 | 49387.1485 | 51336.3448 | 50534.6619 | 50534.6619 | 50534.6619 | 50534.6619 | 50534.6619 | 50534.6619 | 50534.6619 | 50534.6619 | 50534.6619 | 50534.6619 | 50534.6619 | 50534.6619 | 50534.6619 | 50534.6619 | 50534.6619 | 50534.6619
Option 6 Winter POE50 W E @ R (MWh) N 2 | 11957.3691 | 16656.0457 | 17175.8108 | 17823.3398 | 18691.1994 | 19522.1621 | 20992.3874 | 24767.4616 | 26836.7142 | 25324.6404 | 30046.1573 | 30908.7669 | 31530.5579 | 34477.5523 | 34959.607 | 34959.607 | 34959.607 | 34959.607 | 34959.607 | 34959.607 | 34959.607 | 34959.607 | 34959.607 | 34959.607 | 34959.607 | 34959.607 | 34959.607 | 34959.607 | 34959.607 | 34959.607 | Option 6 Winter POE10 W E @ R (MWh) N 2 | 6969.3207 | 9015.1297 | 9232.9902 | 9991.2187 | 9972.6264 | 10140.5732 | 10801.575 | 12733.9299 | 13543.9444 | 12777.0363 | 14906.376 | 14008.3404 | 14816.1446 | 15400.9034 | 15160.3986 | 15160.3986 | 15160.3986 | 15160.3986 | 15160.3986 | 15160.3986 | 15160.3986 | 15160.3986 | 15160.3986 | 15160.3986 | 15160.3986 | 15160.3986 | 15160.3986 | 15160.3986 | 15160.3986 | 15160.3986
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | 10.4659 | 11.7471 | 11.8758 | 11.8127 | 11.8727 | 11.8974 | 11.9764 | 12.1389 | 12.2756 | 12.3385 | 12.2824 | 12.5175 | 12.5548 | 12.5107 | 12.5992 | 12.6406 | 12.6406 | 12.6406 | 12.6406 | 12.6406 | 12.6406 | 12.6406 | 12.6406 | 12.6406 | 12.6406 | 12.6406 | 12.6406 | 12.6406 | 12.6406 | 12.6406 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
98% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
97% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 13.9883 | 15.3913 | 15.4301 | 15.3883 | 15.399 | 15.4757 | 15.6309 | 15.9044 | 16.0469 | 16.1499 | 16.3059 | 16.5051 | 16.746 | 16.8722 | 16.8313 | 16.8718 | 16.8718 | 16.8718 | 16.8718 | 16.8718 | 16.8718 | 16.8718 | 16.8718 | 16.8718 | 16.8718 | 16.8718 | 16.8718 | 16.8718 | 16.8718 | 16.8718
95% | 9.863 | 11.0991 | 11.2233 | 11.1624 | 11.2203 | 11.2441 | 11.3203 | 11.4771 | 11.609 | 11.6697 | 11.6156 | 11.8424 | 11.8784 | 11.8358 | 11.9212 | 11.9611 | 11.9611 | 11.9611 | 11.9611 | 11.9611 | 11.9611 | 11.9611 | 11.9611 | 11.9611 | 11.9611 | 11.9611 | 11.9611 | 11.9611 | 11.9611 | 11.9611 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
90% | 203.721 | 229.9238 | 232.5569 | 231.2662 | 232.4934 | 232.9977 | 234.6138 | 237.9368 | 240.7323 | 242.0191 | 240.8722 | 245.6809 | 246.4436 | 245.541 | 247.3509 | 248.1974 | 248.1974 | 248.1974 | 248.1974 | 248.1974 | 248.1974 | 248.1974 | 248.1974 | 248.1974 | 248.1974 | 248.1974 | 248.1974 | 248.1974 | 248.1974 | 248.1974 |  | 12.9287 | 14.2598 | 14.2965 | 14.2569 | 14.2671 | 14.3398 | 14.4871 | 14.7465 | 14.8817 | 14.9794 | 15.1275 | 15.3164 | 15.5449 | 15.6647 | 15.6258 | 15.6643 | 15.6643 | 15.6643 | 15.6643 | 15.6643 | 15.6643 | 15.6643 | 15.6643 | 15.6643 | 15.6643 | 15.6643 | 15.6643 | 15.6643 | 15.6643 | 15.6643
85% | 697.0932 | 790.6056 | 800.0026 | 795.3964 | 799.7762 | 801.5757 | 807.3432 | 819.2024 | 829.1789 | 833.7714 | 829.6781 | 846.8397 | 849.5615 | 846.3404 | 852.7995 | 855.8206 | 855.8206 | 855.8206 | 855.8206 | 855.8206 | 855.8206 | 855.8206 | 855.8206 | 855.8206 | 855.8206 | 855.8206 | 855.8206 | 855.8206 | 855.8206 | 855.8206 |  | 11.8691 | 13.1282 | 13.1629 | 13.1255 | 13.1351 | 13.2038 | 13.3432 | 13.5886 | 13.7165 | 13.809 | 13.949 | 14.1277 | 14.3439 | 14.4571 | 14.4204 | 14.4568 | 14.4568 | 14.4568 | 14.4568 | 14.4568 | 14.4568 | 14.4568 | 14.4568 | 14.4568 | 14.4568 | 14.4568 | 14.4568 | 14.4568 | 14.4568 | 14.4568
80% | 1077.8455 | 1229.7508 | 1245.0156 | 1237.5332 | 1244.6479 | 1247.5711 | 1256.9401 | 1276.2046 | 1292.4109 | 1299.8711 | 1293.2218 | 1321.0998 | 1325.5213 | 1320.2887 | 1330.7811 | 1335.6887 | 1335.6887 | 1335.6887 | 1335.6887 | 1335.6887 | 1335.6887 | 1335.6887 | 1335.6887 | 1335.6887 | 1335.6887 | 1335.6887 | 1335.6887 | 1335.6887 | 1335.6887 | 1335.6887 |  | 43.2377 | 47.9863 | 48.1174 | 47.9761 | 48.0124 | 48.2717 | 48.7972 | 49.7227 | 50.205 | 50.5539 | 51.0819 | 51.756 | 52.5712 | 52.9984 | 52.8599 | 52.9972 | 52.9972 | 52.9972 | 52.9972 | 52.9972 | 52.9972 | 52.9972 | 52.9972 | 52.9972 | 52.9972 | 52.9972 | 52.9972 | 52.9972 | 52.9972 | 52.9972
75% | 1809.2093 | 2079.6387 | 2106.8139 | 2093.4933 | 2106.1592 | 2111.3633 | 2128.0424 | 2162.3381 | 2191.1892 | 2204.4703 | 2192.633 | 2242.2627 | 2250.134 | 2240.8188 | 2259.498 | 2268.2346 | 2268.2346 | 2268.2346 | 2268.2346 | 2268.2346 | 2268.2346 | 2268.2346 | 2268.2346 | 2268.2346 | 2268.2346 | 2268.2346 | 2268.2346 | 2268.2346 | 2268.2346 | 2268.2346 |  | 19.4996 | 21.73 | 21.7915 | 21.7252 | 21.7422 | 21.864 | 22.1109 | 22.5456 | 22.7721 | 22.936 | 23.184 | 23.5006 | 23.8835 | 24.0842 | 24.0191 | 24.0836 | 24.0836 | 24.0836 | 24.0836 | 24.0836 | 24.0836 | 24.0836 | 24.0836 | 24.0836 | 24.0836 | 24.0836 | 24.0836 | 24.0836 | 24.0836 | 24.0836
70% | 2151.4453 | 2496.8455 | 2531.5545 | 2514.541 | 2530.7182 | 2537.3651 | 2558.6681 | 2602.4716 | 2639.3211 | 2656.284 | 2641.165 | 2704.5535 | 2714.6071 | 2702.7094 | 2726.567 | 2737.7256 | 2737.7256 | 2737.7256 | 2737.7256 | 2737.7256 | 2737.7256 | 2737.7256 | 2737.7256 | 2737.7256 | 2737.7256 | 2737.7256 | 2737.7256 | 2737.7256 | 2737.7256 | 2737.7256 |  | 52.1409 | 58.4004 | 58.5732 | 58.3869 | 58.4348 | 58.7767 | 59.4694 | 60.6894 | 61.3251 | 61.785 | 62.481 | 63.3696 | 64.4442 | 65.0073 | 64.8247 | 65.0057 | 65.0057 | 65.0057 | 65.0057 | 65.0057 | 65.0057 | 65.0057 | 65.0057 | 65.0057 | 65.0057 | 65.0057 | 65.0057 | 65.0057 | 65.0057 | 65.0057
65% | 2417.2518 | 2841.3891 | 2884.0103 | 2863.1184 | 2882.9834 | 2891.1455 | 2917.3047 | 2971.0936 | 3016.3433 | 3037.1731 | 3018.6076 | 3096.446 | 3108.7914 | 3094.1815 | 3123.4776 | 3137.18 | 3137.18 | 3137.18 | 3137.18 | 3137.18 | 3137.18 | 3137.18 | 3137.18 | 3137.18 | 3137.18 | 3137.18 | 3137.18 | 3137.18 | 3137.18 | 3137.18 |  | 15.261 | 17.2036 | 17.2572 | 17.1994 | 17.2143 | 17.3204 | 17.5354 | 17.914 | 18.1113 | 18.254 | 18.47 | 18.7458 | 19.0793 | 19.254 | 19.1974 | 19.2535 | 19.2535 | 19.2535 | 19.2535 | 19.2535 | 19.2535 | 19.2535 | 19.2535 | 19.2535 | 19.2535 | 19.2535 | 19.2535 | 19.2535 | 19.2535 | 19.2535
60% | 3150.8806 | 3770.5408 | 3832.8099 | 3802.2871 | 3831.3096 | 3843.2344 | 3881.4527 | 3960.0377 | 4026.147 | 4056.5791 | 4029.4551 | 4143.1763 | 4161.2127 | 4139.8678 | 4182.6692 | 4202.6882 | 4202.6882 | 4202.6882 | 4202.6882 | 4202.6882 | 4202.6882 | 4202.6882 | 4202.6882 | 4202.6882 | 4202.6882 | 4202.6882 | 4202.6882 | 4202.6882 | 4202.6882 | 4202.6882 |  | 85.4213 | 97.113 | 97.4357 | 97.0878 | 97.1773 | 97.8157 | 99.1096 | 101.3883 | 102.5757 | 103.4347 | 104.7347 | 106.3945 | 108.4016 | 109.4534 | 109.1124 | 109.4504 | 109.4504 | 109.4504 | 109.4504 | 109.4504 | 109.4504 | 109.4504 | 109.4504 | 109.4504 | 109.4504 | 109.4504 | 109.4504 | 109.4504 | 109.4504 | 109.4504
55% | 3327.6421 | 4090.2265 | 4166.858 | 4129.2951 | 4165.0116 | 4179.6869 | 4226.7202 | 4323.4309 | 4404.7881 | 4442.2395 | 4408.8593 | 4548.8102 | 4571.0067 | 4544.7386 | 4597.4121 | 4622.0485 | 4622.0485 | 4622.0485 | 4622.0485 | 4622.0485 | 4622.0485 | 4622.0485 | 4622.0485 | 4622.0485 | 4622.0485 | 4622.0485 | 4622.0485 | 4622.0485 | 4622.0485 | 4622.0485 |  | 352.7187 | 405.6734 | 407.1346 | 405.5592 | 405.9643 | 408.8561 | 414.7164 | 425.0372 | 430.415 | 434.3056 | 440.1939 | 447.7114 | 456.8018 | 461.5659 | 460.0214 | 461.5522 | 461.5522 | 461.5522 | 461.5522 | 461.5522 | 461.5522 | 461.5522 | 461.5522 | 461.5522 | 461.5522 | 461.5522 | 461.5522 | 461.5522 | 461.5522 | 461.5522
50% | 3032.8171 | 3898.088 | 3985.0383 | 3942.4174 | 3982.9433 | 3999.5947 | 4052.9614 | 4162.6947 | 4255.0072 | 4297.5016 | 4259.6266 | 4418.4227 | 4443.6081 | 4413.8029 | 4473.5691 | 4501.523 | 4501.523 | 4501.523 | 4501.523 | 4501.523 | 4501.523 | 4501.523 | 4501.523 | 4501.523 | 4501.523 | 4501.523 | 4501.523 | 4501.523 | 4501.523 | 4501.523 |  | 703.3516 | 822.7155 | 826.0092 | 822.458 | 823.3713 | 829.8895 | 843.0992 | 866.363 | 878.4849 | 887.2547 | 900.5273 | 917.4725 | 937.9629 | 948.7014 | 945.2201 | 948.6707 | 948.6707 | 948.6707 | 948.6707 | 948.6707 | 948.6707 | 948.6707 | 948.6707 | 948.6707 | 948.6707 | 948.6707 | 948.6707 | 948.6707 | 948.6707 | 948.6707
45% | 1765.9337 | 2482.1322 | 2554.1023 | 2518.8243 | 2552.3683 | 2566.1509 | 2610.3233 | 2701.1513 | 2777.5598 | 2812.7331 | 2781.3834 | 2912.8214 | 2933.6678 | 2908.9975 | 2958.467 | 2981.6048 | 2981.6048 | 2981.6048 | 2981.6048 | 2981.6048 | 2981.6048 | 2981.6048 | 2981.6048 | 2981.6048 | 2981.6048 | 2981.6048 | 2981.6048 | 2981.6048 | 2981.6048 | 2981.6048 |  | 1017.5865 | 1222.642 | 1228.3004 | 1222.1997 | 1223.7687 | 1234.9662 | 1257.6592 | 1297.6242 | 1318.4485 | 1333.5141 | 1356.3152 | 1385.4253 | 1420.6258 | 1439.0735 | 1433.093 | 1439.0207 | 1439.0207 | 1439.0207 | 1439.0207 | 1439.0207 | 1439.0207 | 1439.0207 | 1439.0207 | 1439.0207 | 1439.0207 | 1439.0207 | 1439.0207 | 1439.0207 | 1439.0207 | 1439.0207
40% | 607.9205 | 1122.3189 | 1174.0104 | 1148.6725 | 1172.7649 | 1182.6641 | 1214.3902 | 1279.626 | 1334.5053 | 1359.768 | 1337.2515 | 1431.6548 | 1446.6274 | 1428.9084 | 1464.439 | 1481.0575 | 1481.0575 | 1481.0575 | 1481.0575 | 1481.0575 | 1481.0575 | 1481.0575 | 1481.0575 | 1481.0575 | 1481.0575 | 1481.0575 | 1481.0575 | 1481.0575 | 1481.0575 | 1481.0575 |  | 1058.8722 | 1336.5245 | 1344.1862 | 1335.9257 | 1338.0501 | 1353.212 | 1383.9391 | 1438.0532 | 1466.2499 | 1486.6493 | 1517.5228 | 1556.9388 | 1604.6016 | 1629.5804 | 1621.4826 | 1629.509 | 1629.509 | 1629.509 | 1629.509 | 1629.509 | 1629.509 | 1629.509 | 1629.509 | 1629.509 | 1629.509 | 1629.509 | 1629.509 | 1629.509 | 1629.509 | 1629.509
35% | 23.196 | 247.1276 | 281.389 | 264.3461 | 280.5402 | 287.3184 | 309.5259 | 357.4741 | 400.1436 | 420.4081 | 402.3339 | 478.1695 | 490.2 | 475.9627 | 504.5117 | 517.8647 | 517.8647 | 517.8647 | 517.8647 | 517.8647 | 517.8647 | 517.8647 | 517.8647 | 517.8647 | 517.8647 | 517.8647 | 517.8647 | 517.8647 | 517.8647 | 517.8647 |  | 1063.9608 | 1515.0828 | 1527.5312 | 1514.1099 | 1517.5615 | 1542.1962 | 1592.1207 | 1680.0438 | 1725.8572 | 1759.0016 | 1809.1639 | 1873.2061 | 1950.6472 | 1991.2321 | 1978.0751 | 1991.1161 | 1991.1161 | 1991.1161 | 1991.1161 | 1991.1161 | 1991.1161 | 1991.1161 | 1991.1161 | 1991.1161 | 1991.1161 | 1991.1161 | 1991.1161 | 1991.1161 | 1991.1161 | 1991.1161
30% | [9 empty] | 0.071582 |  | 2.2996 | 3.1509 | 2.1578 | 4.3353 | 5.6074 | 5.6074 | 5.6074 | 5.6074 | 5.6074 | 5.6074 | 5.6074 | 5.6074 | 5.6074 | 5.6074 | 5.6074 | 5.6074 | 5.6074 | 5.6074 | 5.6074 |  | 388.5058 | 1015.6243 | 1034.8788 | 1014.1196 | 1019.4583 | 1057.5615 | 1134.7813 | 1270.7746 | 1341.6355 | 1392.901 | 1470.4886 | 1569.5445 | 1689.3252 | 1752.0991 | 1731.7486 | 1751.9195 | 1751.9195 | 1751.9195 | 1751.9195 | 1751.9195 | 1751.9195 | 1751.9195 | 1751.9195 | 1751.9195 | 1751.9195 | 1751.9195 | 1751.9195 | 1751.9195 | 1751.9195 | 1751.9195
25% | [32 empty] | 10.8714 | 13.2189 | 10.6975 | 11.3209 | 16.2724 | 28.9785 | 59.8591 | 80.1406 | 96.5629 | 124.1616 | 164.1053 | 219.2802 | 251.1289 | 240.5861 | 251.035 | 251.035 | 251.035 | 251.035 | 251.035 | 251.035 | 251.035 | 251.035 | 251.035 | 251.035 | 251.035 | 251.035 | 251.035 | 251.035 | 251.035
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 20082.4323 | 25048.4194 | 25559.0881 | 25308.5245 | 25546.761 | 25644.7713 | 25959.3667 | 26608.5051 | 27156.899 | 27410.0291 | 27184.3956 | 28132.4312 | 28283.2762 | 28104.7752 | 28462.8939 | 28630.6444 | 28630.6444 | 28630.6444 | 28630.6444 | 28630.6444 | 28630.6444 | 28630.6444 | 28630.6444 | 28630.6444 | 28630.6444 | 28630.6444 | 28630.6444 | 28630.6444 | 28630.6444 | 28630.6444 | E @ R (MWh) | 4790.9487 | 6548.203 | 6600.6505 | 6544.1136 | 6558.6286 | 6662.7214 | 6876.3204 | 7260.9121 | 7465.4571 | 7615.1702 | 7844.4702 | 8141.8786 | 8508.3166 | 8703.2608 | 8639.8468 | 8702.7004 | 8702.7004 | 8702.7004 | 8702.7004 | 8702.7004 | 8702.7004 | 8702.7004 | 8702.7004 | 8702.7004 | 8702.7004 | 8702.7004 | 8702.7004 | 8702.7004 | 8702.7004 | 8702.7004
Option 6 Summer POE50 W E @ R (MWh) N 2 | 14057.7026 | 17533.8936 | 17891.3617 | 17715.9672 | 17882.7327 | 17951.3399 | 18171.5567 | 18625.9536 | 19009.8293 | 19187.0204 | 19029.0769 | 19692.7018 | 19798.2933 | 19673.3426 | 19924.0258 | 20041.4511 | 20041.4511 | 20041.4511 | 20041.4511 | 20041.4511 | 20041.4511 | 20041.4511 | 20041.4511 | 20041.4511 | 20041.4511 | 20041.4511 | 20041.4511 | 20041.4511 | 20041.4511 | 20041.4511 | Option 6 Summer POE10 W E @ R (MWh) N 2 | 1437.2846 | 1964.4609 | 1980.1951 | 1963.2341 | 1967.5886 | 1998.8164 | 2062.8961 | 2178.2736 | 2239.6371 | 2284.5511 | 2353.341 | 2442.5636 | 2552.495 | 2610.9782 | 2591.954 | 2610.8101 | 2610.8101 | 2610.8101 | 2610.8101 | 2610.8101 | 2610.8101 | 2610.8101 | 2610.8101 | 2610.8101 | 2610.8101 | 2610.8101 | 2610.8101 | 2610.8101 | 2610.8101 | 2610.8101
Option 7 -
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | 7.4585 | 8.8006 | 8.9429 | 9.1188 | 9.3524 | 9.5739 | 9.9609 | 10.9342 | 11.4578 | 11.0758 | 12.2583 | 12.4713 | 12.6244 | 13.3463 | 13.4638 | 13.4638 | 13.4638 | 13.4638 | 13.4638 | 13.4638 | 13.4638 | 13.4638 | 13.4638 | 13.4638 | 13.4638 | 13.4638 | 13.4638 | 13.4638 | 13.4638 | 13.4638 |  | 8.6919 | 9.9721 | 10.1047 | 10.5622 | 10.551 | 10.6516 | 11.0451 | 12.1756 | 12.6421 | 12.2006 | 13.4204 | 12.9082 | 13.3691 | 13.7012 | 13.5647 | 13.5647 | 13.5647 | 13.5647 | 13.5647 | 13.5647 | 13.5647 | 13.5647 | 13.5647 | 13.5647 | 13.5647 | 13.5647 | 13.5647 | 13.5647 | 13.5647 | 13.5647
98% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
97% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
95% | 28.0297 | 33.2092 | 33.7584 | 34.4374 | 35.339 | 36.1936 | 37.6872 | 41.4437 | 43.4642 | 41.9901 | 46.5535 | 47.3756 | 47.9667 | 50.7525 | 51.2059 | 51.2059 | 51.2059 | 51.2059 | 51.2059 | 51.2059 | 51.2059 | 51.2059 | 51.2059 | 51.2059 | 51.2059 | 51.2059 | 51.2059 | 51.2059 | 51.2059 | 51.2059 |  | 32.79 | 37.7305 | 38.2421 | 40.0078 | 39.9648 | 40.3531 | 41.8717 | 46.2346 | 48.035 | 46.3308 | 51.0385 | 49.062 | 50.8404 | 52.1221 | 51.5955 | 51.5955 | 51.5955 | 51.5955 | 51.5955 | 51.5955 | 51.5955 | 51.5955 | 51.5955 | 51.5955 | 51.5955 | 51.5955 | 51.5955 | 51.5955 | 51.5955 | 51.5955
90% | 157.3528 | 187.297 | 190.4721 | 194.3976 | 199.6095 | 204.5504 | 213.1852 | 234.9023 | 246.5833 | 238.0616 | 264.4434 | 269.1966 | 272.6134 | 288.719 | 291.3405 | 291.3405 | 291.3405 | 291.3405 | 291.3405 | 291.3405 | 291.3405 | 291.3405 | 291.3405 | 291.3405 | 291.3405 | 291.3405 | 291.3405 | 291.3405 | 291.3405 | 291.3405 |  | 184.8731 | 213.4355 | 216.3934 | 226.6014 | 226.3526 | 228.5973 | 237.3766 | 262.5998 | 273.0084 | 263.1559 | 290.3726 | 278.9455 | 289.2275 | 296.6368 | 293.5927 | 293.5927 | 293.5927 | 293.5927 | 293.5927 | 293.5927 | 293.5927 | 293.5927 | 293.5927 | 293.5927 | 293.5927 | 293.5927 | 293.5927 | 293.5927 | 293.5927 | 293.5927
85% | 626.672 | 751.7764 | 765.0422 | 781.4425 | 803.2172 | 823.8602 | 859.9357 | 950.668 | 999.4703 | 963.8676 | 1074.0886 | 1093.9472 | 1108.2222 | 1175.5104 | 1186.4628 | 1186.4628 | 1186.4628 | 1186.4628 | 1186.4628 | 1186.4628 | 1186.4628 | 1186.4628 | 1186.4628 | 1186.4628 | 1186.4628 | 1186.4628 | 1186.4628 | 1186.4628 | 1186.4628 | 1186.4628 |  | 741.6496 | 860.9812 | 873.3391 | 915.9877 | 914.9483 | 924.3264 | 961.0057 | 1066.3864 | 1109.8728 | 1068.7096 | 1182.4188 | 1134.6775 | 1177.6348 | 1208.5906 | 1195.8725 | 1195.8725 | 1195.8725 | 1195.8725 | 1195.8725 | 1195.8725 | 1195.8725 | 1195.8725 | 1195.8725 | 1195.8725 | 1195.8725 | 1195.8725 | 1195.8725 | 1195.8725 | 1195.8725 | 1195.8725
80% | 937.6386 | 1135.7149 | 1156.7184 | 1182.6849 | 1217.1605 | 1249.8444 | 1306.9623 | 1450.6177 | 1527.8858 | 1471.5164 | 1646.0281 | 1677.4699 | 1700.0714 | 1806.608 | 1823.9489 | 1823.9489 | 1823.9489 | 1823.9489 | 1823.9489 | 1823.9489 | 1823.9489 | 1823.9489 | 1823.9489 | 1823.9489 | 1823.9489 | 1823.9489 | 1823.9489 | 1823.9489 | 1823.9489 | 1823.9489 |  | 1119.6813 | 1308.6177 | 1328.1837 | 1395.7087 | 1394.063 | 1408.9114 | 1466.9853 | 1633.8333 | 1702.6848 | 1637.5115 | 1817.5461 | 1741.9578 | 1809.9715 | 1858.9836 | 1838.8471 | 1838.8471 | 1838.8471 | 1838.8471 | 1838.8471 | 1838.8471 | 1838.8471 | 1838.8471 | 1838.8471 | 1838.8471 | 1838.8471 | 1838.8471 | 1838.8471 | 1838.8471 | 1838.8471 | 1838.8471
75% | 1618.1428 | 1984.0141 | 2022.8101 | 2070.7733 | 2134.4541 | 2194.8252 | 2300.329 | 2565.6781 | 2708.4018 | 2604.2807 | 2926.6253 | 2984.7021 | 3026.4498 | 3223.236 | 3255.2667 | 3255.2667 | 3255.2667 | 3255.2667 | 3255.2667 | 3255.2667 | 3255.2667 | 3255.2667 | 3255.2667 | 3255.2667 | 3255.2667 | 3255.2667 | 3255.2667 | 3255.2667 | 3255.2667 | 3255.2667 |  | 1954.3979 | 2303.3867 | 2339.5275 | 2464.2546 | 2461.2148 | 2488.6415 | 2595.9111 | 2904.0999 | 3031.2772 | 2910.894 | 3243.44 | 3103.8192 | 3229.4488 | 3319.9801 | 3282.7856 | 3282.7856 | 3282.7856 | 3282.7856 | 3282.7856 | 3282.7856 | 3282.7856 | 3282.7856 | 3282.7856 | 3282.7856 | 3282.7856 | 3282.7856 | 3282.7856 | 3282.7856 | 3282.7856 | 3282.7856
70% | 2423.1485 | 3018.6926 | 3081.8425 | 3159.9143 | 3263.5701 | 3361.8387 | 3533.5717 | 3965.4915 | 4197.8089 | 4028.3265 | 4553.0204 | 4647.5545 | 4715.5089 | 5035.8261 | 5087.9638 | 5087.9638 | 5087.9638 | 5087.9638 | 5087.9638 | 5087.9638 | 5087.9638 | 5087.9638 | 5087.9638 | 5087.9638 | 5087.9638 | 5087.9638 | 5087.9638 | 5087.9638 | 5087.9638 | 5087.9638 |  | 2970.4851 | 3538.5488 | 3597.3768 | 3800.4002 | 3795.4522 | 3840.0957 | 4014.703 | 4516.3548 | 4723.3667 | 4527.4139 | 5068.713 | 4841.4463 | 5045.9389 | 5193.3006 | 5132.7574 | 5132.7574 | 5132.7574 | 5132.7574 | 5132.7574 | 5132.7574 | 5132.7574 | 5132.7574 | 5132.7574 | 5132.7574 | 5132.7574 | 5132.7574 | 5132.7574 | 5132.7574 | 5132.7574 | 5132.7574
65% | 2670.9583 | 3400.2393 | 3477.5703 | 3573.1741 | 3700.1072 | 3820.4432 | 4030.7411 | 4559.6539 | 4844.1411 | 4636.5993 | 5279.1198 | 5394.8827 | 5478.0971 | 5870.3455 | 5934.1915 | 5934.1915 | 5934.1915 | 5934.1915 | 5934.1915 | 5934.1915 | 5934.1915 | 5934.1915 | 5934.1915 | 5934.1915 | 5934.1915 | 5934.1915 | 5934.1915 | 5934.1915 | 5934.1915 | 5934.1915 |  | 3341.2062 | 4036.8358 | 4108.8743 | 4357.4892 | 4351.43 | 4406.0989 | 4619.9164 | 5234.2205 | 5487.7194 | 5247.763 | 5910.6177 | 5632.3154 | 5882.7294 | 6063.1829 | 5989.044 | 5989.044 | 5989.044 | 5989.044 | 5989.044 | 5989.044 | 5989.044 | 5989.044 | 5989.044 | 5989.044 | 5989.044 | 5989.044 | 5989.044 | 5989.044 | 5989.044 | 5989.044
60% | 2886.5439 | 3791.1059 | 3887.0233 | 4005.6052 | 4163.0464 | 4312.3049 | 4573.1473 | 5229.1832 | 5582.0462 | 5324.6222 | 6121.571 | 6265.1573 | 6368.3721 | 6854.8965 | 6934.0877 | 6934.0877 | 6934.0877 | 6934.0877 | 6934.0877 | 6934.0877 | 6934.0877 | 6934.0877 | 6934.0877 | 6934.0877 | 6934.0877 | 6934.0877 | 6934.0877 | 6934.0877 | 6934.0877 | 6934.0877 |  | 3717.8843 | 4580.7069 | 4670.0597 | 4978.4286 | 4970.9132 | 5038.7216 | 5303.9296 | 6065.8803 | 6380.3071 | 6082.6777 | 6904.848 | 6559.6564 | 6870.2568 | 7094.0819 | 7002.1239 | 7002.1239 | 7002.1239 | 7002.1239 | 7002.1239 | 7002.1239 | 7002.1239 | 7002.1239 | 7002.1239 | 7002.1239 | 7002.1239 | 7002.1239 | 7002.1239 | 7002.1239 | 7002.1239 | 7002.1239
55% | 2587.93 | 3569.0383 | 3673.0724 | 3801.6891 | 3972.4533 | 4134.3425 | 4417.258 | 5128.8093 | 5511.5325 | 5232.3246 | 6096.7133 | 6252.4502 | 6364.3994 | 6892.0947 | 6977.9873 | 6977.9873 | 6977.9873 | 6977.9873 | 6977.9873 | 6977.9873 | 6977.9873 | 6977.9873 | 6977.9873 | 6977.9873 | 6977.9873 | 6977.9873 | 6977.9873 | 6977.9873 | 6977.9873 | 6977.9873 |  | 3489.6205 | 4425.4573 | 4522.3714 | 4856.8353 | 4848.6838 | 4922.2304 | 5209.881 | 6036.3099 | 6377.3443 | 6054.5287 | 6946.2732 | 6571.8705 | 6908.7548 | 7151.5206 | 7051.7809 | 7051.7809 | 7051.7809 | 7051.7809 | 7051.7809 | 7051.7809 | 7051.7809 | 7051.7809 | 7051.7809 | 7051.7809 | 7051.7809 | 7051.7809 | 7051.7809 | 7051.7809 | 7051.7809 | 7051.7809
50% | 1977.4132 | 2976.5959 | 3082.5466 | 3213.5326 | 3387.4428 | 3552.3143 | 3840.4419 | 4565.1017 | 4954.8755 | 4670.5239 | 5550.8367 | 5709.4427 | 5823.4542 | 6360.871 | 6448.3459 | 6448.3459 | 6448.3459 | 6448.3459 | 6448.3459 | 6448.3459 | 6448.3459 | 6448.3459 | 6448.3459 | 6448.3459 | 6448.3459 | 6448.3459 | 6448.3459 | 6448.3459 | 6448.3459 | 6448.3459 |  | 2895.7151 | 3848.7922 | 3947.4917 | 4288.1172 | 4279.8156 | 4354.717 | 4647.6668 | 5489.3206 | 5836.6377 | 5507.875 | 6416.0476 | 6034.7475 | 6377.838 | 6625.0761 | 6523.499 | 6523.499 | 6523.499 | 6523.499 | 6523.499 | 6523.499 | 6523.499 | 6523.499 | 6523.499 | 6523.499 | 6523.499 | 6523.499 | 6523.499 | 6523.499 | 6523.499 | 6523.499
45% | 1115.1481 | 2058.8937 | 2158.966 | 2282.6846 | 2446.9458 | 2602.6699 | 2874.8114 | 3559.2653 | 3927.4136 | 3658.8385 | 4490.3094 | 4640.1156 | 4747.8014 | 5255.401 | 5338.0226 | 5338.0226 | 5338.0226 | 5338.0226 | 5338.0226 | 5338.0226 | 5338.0226 | 5338.0226 | 5338.0226 | 5338.0226 | 5338.0226 | 5338.0226 | 5338.0226 | 5338.0226 | 5338.0226 | 5338.0226 |  | 1982.5003 | 2882.6984 | 2975.9219 | 3297.6486 | 3289.8076 | 3360.5533 | 3637.2496 | 4432.2063 | 4760.2534 | 4449.7313 | 5307.5163 | 4947.3717 | 5271.4266 | 5504.9474 | 5409.006 | 5409.006 | 5409.006 | 5409.006 | 5409.006 | 5409.006 | 5409.006 | 5409.006 | 5409.006 | 5409.006 | 5409.006 | 5409.006 | 5409.006 | 5409.006 | 5409.006 | 5409.006
40% | 218.0643 | 1019.3158 | 1109.6444 | 1221.317 | 1369.5846 | 1510.1463 | 1755.7904 | 2373.6013 | 2705.9042 | 2463.4794 | 3213.9927 | 3349.2128 | 3446.4136 | 3904.5899 | 3979.1669 | 3979.1669 | 3979.1669 | 3979.1669 | 3979.1669 | 3979.1669 | 3979.1669 | 3979.1669 | 3979.1669 | 3979.1669 | 3979.1669 | 3979.1669 | 3979.1669 | 3979.1669 | 3979.1669 | 3979.1669 |  | 950.3606 | 1762.9094 | 1847.056 | 2137.4573 | 2130.3798 | 2194.2372 | 2443.9925 | 3161.5469 | 3457.6532 | 3177.3656 | 3951.6309 | 3626.5524 | 3919.0552 | 4129.8388 | 4043.2389 | 4043.2389 | 4043.2389 | 4043.2389 | 4043.2389 | 4043.2389 | 4043.2389 | 4043.2389 | 4043.2389 | 4043.2389 | 4043.2389 | 4043.2389 | 4043.2389 | 4043.2389 | 4043.2389 | 4043.2389
35% |  | 100.0043 | 136.3101 | 188.3336 | 269.145 | 357.6005 | 537.7501 | 1017.2126 | 1275.1019 | 1086.964 | 1669.4126 | 1774.3523 | 1849.7867 | 2205.3621 | 2263.2389 | 2263.2389 | 2263.2389 | 2263.2389 | 2263.2389 | 2263.2389 | 2263.2389 | 2263.2389 | 2263.2389 | 2263.2389 | 2263.2389 | 2263.2389 | 2263.2389 | 2263.2389 | 2263.2389 | 2263.2389 |  | 75.8706 | 543.275 | 608.5783 | 833.9491 | 828.4565 | 878.0141 | 1071.8409 | 1628.7111 | 1858.5094 | 1640.9875 | 2241.8691 | 1989.5864 | 2216.5882 | 2380.1703 | 2312.963 | 2312.963 | 2312.963 | 2312.963 | 2312.963 | 2312.963 | 2312.963 | 2312.963 | 2312.963 | 2312.963 | 2312.963 | 2312.963 | 2312.963 | 2312.963 | 2312.963 | 2312.963
30% | [6 empty] | 0.47307 | 86.92 | 189.3305 | 111.0221 | 411.6753 | 482.9899 | 535.3611 | 782.2235 | 822.4051 | 822.4051 | 822.4051 | 822.4051 | 822.4051 | 822.4051 | 822.4051 | 822.4051 | 822.4051 | 822.4051 | 822.4051 | 822.4051 | 822.4051 | 822.4051 | 822.4051 | 822.4051 |  |  | 0.62469 | 3.9886 | 37.019 | 35.8334 | 47.1947 | 105.5643 | 385.3047 | 541.4169 | 393.1792 | 807.5688 | 632.4187 | 790.0173 | 903.5861 | 856.9266 | 856.9266 | 856.9266 | 856.9266 | 856.9266 | 856.9266 | 856.9266 | 856.9266 | 856.9266 | 856.9266 | 856.9266 | 856.9266 | 856.9266 | 856.9266 | 856.9266 | 856.9266
25% | [11 empty] | 0.074459 | 1.4981 | 31.3754 | 39.665 | 39.665 | 39.665 | 39.665 | 39.665 | 39.665 | 39.665 | 39.665 | 39.665 | 39.665 | 39.665 | 39.665 | 39.665 | 39.665 | 39.665 | 39.665 | [9 empty] | 1.778 |  | 36.4973 | 8.794 | 32.9113 | 59.1747 | 47.515 | 47.515 | 47.515 | 47.515 | 47.515 | 47.515 | 47.515 | 47.515 | 47.515 | 47.515 | 47.515 | 47.515 | 47.515 | 47.515 | 47.515 | 47.515
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 17081.9558 | 23794.351 | 24536.8726 | 25461.914 | 26701.7135 | 27888.803 | 29989.1249 | 35382.088 | 38338.1632 | 36178.0578 | 42923.0818 | 44155.3813 | 45043.6541 | 49253.6461 | 49942.2957 | 49942.2957 | 49942.2957 | 49942.2957 | 49942.2957 | 49942.2957 | 49942.2957 | 49942.2957 | 49942.2957 | 49942.2957 | 49942.2957 | 49942.2957 | 49942.2957 | 49942.2957 | 49942.2957 | 49942.2957 | E @ R (MWh) | 23231.0692 | 30050.4324 | 30776.634 | 33304.0623 | 33242.0879 | 33801.9108 | 36005.2501 | 42446.433 | 45146.4814 | 42590.1209 | 49687.9201 | 46694.4681 | 49387.1485 | 51336.3448 | 50534.6619 | 50534.6619 | 50534.6619 | 50534.6619 | 50534.6619 | 50534.6619 | 50534.6619 | 50534.6619 | 50534.6619 | 50534.6619 | 50534.6619 | 50534.6619 | 50534.6619 | 50534.6619 | 50534.6619 | 50534.6619
Option 7 Winter POE50 W E @ R (MWh) N 2 | 11957.3691 | 16656.0457 | 17175.8108 | 17823.3398 | 18691.1994 | 19522.1621 | 20992.3874 | 24767.4616 | 26836.7142 | 25324.6404 | 30046.1573 | 30908.7669 | 31530.5579 | 34477.5523 | 34959.607 | 34959.607 | 34959.607 | 34959.607 | 34959.607 | 34959.607 | 34959.607 | 34959.607 | 34959.607 | 34959.607 | 34959.607 | 34959.607 | 34959.607 | 34959.607 | 34959.607 | 34959.607 | Option 7 Winter POE10 W E @ R (MWh) N 2 | 6969.3207 | 9015.1297 | 9232.9902 | 9991.2187 | 9972.6264 | 10140.5732 | 10801.575 | 12733.9299 | 13543.9444 | 12777.0363 | 14906.376 | 14008.3404 | 14816.1446 | 15400.9034 | 15160.3986 | 15160.3986 | 15160.3986 | 15160.3986 | 15160.3986 | 15160.3986 | 15160.3986 | 15160.3986 | 15160.3986 | 15160.3986 | 15160.3986 | 15160.3986 | 15160.3986 | 15160.3986 | 15160.3986 | 15160.3986
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | 10.4659 | 11.7471 | 11.8758 | 11.8127 | 11.8727 | 11.8974 | 11.9764 | 12.1389 | 12.2756 | 12.3385 | 12.2824 | 12.5175 | 12.5548 | 12.5107 | 12.5992 | 12.6406 | 12.6406 | 12.6406 | 12.6406 | 12.6406 | 12.6406 | 12.6406 | 12.6406 | 12.6406 | 12.6406 | 12.6406 | 12.6406 | 12.6406 | 12.6406 | 12.6406 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
98% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
97% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 13.9883 | 15.3913 | 15.4301 | 15.3883 | 15.399 | 15.4757 | 15.6309 | 15.9044 | 16.0469 | 16.1499 | 16.3059 | 16.5051 | 16.746 | 16.8722 | 16.8313 | 16.8718 | 16.8718 | 16.8718 | 16.8718 | 16.8718 | 16.8718 | 16.8718 | 16.8718 | 16.8718 | 16.8718 | 16.8718 | 16.8718 | 16.8718 | 16.8718 | 16.8718
95% | 9.863 | 11.0991 | 11.2233 | 11.1624 | 11.2203 | 11.2441 | 11.3203 | 11.4771 | 11.609 | 11.6697 | 11.6156 | 11.8424 | 11.8784 | 11.8358 | 11.9212 | 11.9611 | 11.9611 | 11.9611 | 11.9611 | 11.9611 | 11.9611 | 11.9611 | 11.9611 | 11.9611 | 11.9611 | 11.9611 | 11.9611 | 11.9611 | 11.9611 | 11.9611 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
90% | 203.721 | 229.9238 | 232.5569 | 231.2662 | 232.4934 | 232.9977 | 234.6138 | 237.9368 | 240.7323 | 242.0191 | 240.8722 | 245.6809 | 246.4436 | 245.541 | 247.3509 | 248.1974 | 248.1974 | 248.1974 | 248.1974 | 248.1974 | 248.1974 | 248.1974 | 248.1974 | 248.1974 | 248.1974 | 248.1974 | 248.1974 | 248.1974 | 248.1974 | 248.1974 |  | 12.9287 | 14.2598 | 14.2965 | 14.2569 | 14.2671 | 14.3398 | 14.4871 | 14.7465 | 14.8817 | 14.9794 | 15.1275 | 15.3164 | 15.5449 | 15.6647 | 15.6258 | 15.6643 | 15.6643 | 15.6643 | 15.6643 | 15.6643 | 15.6643 | 15.6643 | 15.6643 | 15.6643 | 15.6643 | 15.6643 | 15.6643 | 15.6643 | 15.6643 | 15.6643
85% | 697.0932 | 790.6056 | 800.0026 | 795.3964 | 799.7762 | 801.5757 | 807.3432 | 819.2024 | 829.1789 | 833.7714 | 829.6781 | 846.8397 | 849.5615 | 846.3404 | 852.7995 | 855.8206 | 855.8206 | 855.8206 | 855.8206 | 855.8206 | 855.8206 | 855.8206 | 855.8206 | 855.8206 | 855.8206 | 855.8206 | 855.8206 | 855.8206 | 855.8206 | 855.8206 |  | 11.8691 | 13.1282 | 13.1629 | 13.1255 | 13.1351 | 13.2038 | 13.3432 | 13.5886 | 13.7165 | 13.809 | 13.949 | 14.1277 | 14.3439 | 14.4571 | 14.4204 | 14.4568 | 14.4568 | 14.4568 | 14.4568 | 14.4568 | 14.4568 | 14.4568 | 14.4568 | 14.4568 | 14.4568 | 14.4568 | 14.4568 | 14.4568 | 14.4568 | 14.4568
80% | 1077.8455 | 1229.7508 | 1245.0156 | 1237.5332 | 1244.6479 | 1247.5711 | 1256.9401 | 1276.2046 | 1292.4109 | 1299.8711 | 1293.2218 | 1321.0998 | 1325.5213 | 1320.2887 | 1330.7811 | 1335.6887 | 1335.6887 | 1335.6887 | 1335.6887 | 1335.6887 | 1335.6887 | 1335.6887 | 1335.6887 | 1335.6887 | 1335.6887 | 1335.6887 | 1335.6887 | 1335.6887 | 1335.6887 | 1335.6887 |  | 43.2377 | 47.9863 | 48.1174 | 47.9761 | 48.0124 | 48.2717 | 48.7972 | 49.7227 | 50.205 | 50.5539 | 51.0819 | 51.756 | 52.5712 | 52.9984 | 52.8599 | 52.9972 | 52.9972 | 52.9972 | 52.9972 | 52.9972 | 52.9972 | 52.9972 | 52.9972 | 52.9972 | 52.9972 | 52.9972 | 52.9972 | 52.9972 | 52.9972 | 52.9972
75% | 1809.2093 | 2079.6387 | 2106.8139 | 2093.4933 | 2106.1592 | 2111.3633 | 2128.0424 | 2162.3381 | 2191.1892 | 2204.4703 | 2192.633 | 2242.2627 | 2250.134 | 2240.8188 | 2259.498 | 2268.2346 | 2268.2346 | 2268.2346 | 2268.2346 | 2268.2346 | 2268.2346 | 2268.2346 | 2268.2346 | 2268.2346 | 2268.2346 | 2268.2346 | 2268.2346 | 2268.2346 | 2268.2346 | 2268.2346 |  | 19.4996 | 21.73 | 21.7915 | 21.7252 | 21.7422 | 21.864 | 22.1109 | 22.5456 | 22.7721 | 22.936 | 23.184 | 23.5006 | 23.8835 | 24.0842 | 24.0191 | 24.0836 | 24.0836 | 24.0836 | 24.0836 | 24.0836 | 24.0836 | 24.0836 | 24.0836 | 24.0836 | 24.0836 | 24.0836 | 24.0836 | 24.0836 | 24.0836 | 24.0836
70% | 2151.4453 | 2496.8455 | 2531.5545 | 2514.541 | 2530.7182 | 2537.3651 | 2558.6681 | 2602.4716 | 2639.3211 | 2656.284 | 2641.165 | 2704.5535 | 2714.6071 | 2702.7094 | 2726.567 | 2737.7256 | 2737.7256 | 2737.7256 | 2737.7256 | 2737.7256 | 2737.7256 | 2737.7256 | 2737.7256 | 2737.7256 | 2737.7256 | 2737.7256 | 2737.7256 | 2737.7256 | 2737.7256 | 2737.7256 |  | 52.1409 | 58.4004 | 58.5732 | 58.3869 | 58.4348 | 58.7767 | 59.4694 | 60.6894 | 61.3251 | 61.785 | 62.481 | 63.3696 | 64.4442 | 65.0073 | 64.8247 | 65.0057 | 65.0057 | 65.0057 | 65.0057 | 65.0057 | 65.0057 | 65.0057 | 65.0057 | 65.0057 | 65.0057 | 65.0057 | 65.0057 | 65.0057 | 65.0057 | 65.0057
65% | 2417.2518 | 2841.3891 | 2884.0103 | 2863.1184 | 2882.9834 | 2891.1455 | 2917.3047 | 2971.0936 | 3016.3433 | 3037.1731 | 3018.6076 | 3096.446 | 3108.7914 | 3094.1815 | 3123.4776 | 3137.18 | 3137.18 | 3137.18 | 3137.18 | 3137.18 | 3137.18 | 3137.18 | 3137.18 | 3137.18 | 3137.18 | 3137.18 | 3137.18 | 3137.18 | 3137.18 | 3137.18 |  | 15.261 | 17.2036 | 17.2572 | 17.1994 | 17.2143 | 17.3204 | 17.5354 | 17.914 | 18.1113 | 18.254 | 18.47 | 18.7458 | 19.0793 | 19.254 | 19.1974 | 19.2535 | 19.2535 | 19.2535 | 19.2535 | 19.2535 | 19.2535 | 19.2535 | 19.2535 | 19.2535 | 19.2535 | 19.2535 | 19.2535 | 19.2535 | 19.2535 | 19.2535
60% | 3150.8806 | 3770.5408 | 3832.8099 | 3802.2871 | 3831.3096 | 3843.2344 | 3881.4527 | 3960.0377 | 4026.147 | 4056.5791 | 4029.4551 | 4143.1763 | 4161.2127 | 4139.8678 | 4182.6692 | 4202.6882 | 4202.6882 | 4202.6882 | 4202.6882 | 4202.6882 | 4202.6882 | 4202.6882 | 4202.6882 | 4202.6882 | 4202.6882 | 4202.6882 | 4202.6882 | 4202.6882 | 4202.6882 | 4202.6882 |  | 85.4213 | 97.113 | 97.4357 | 97.0878 | 97.1773 | 97.8157 | 99.1096 | 101.3883 | 102.5757 | 103.4347 | 104.7347 | 106.3945 | 108.4016 | 109.4534 | 109.1124 | 109.4504 | 109.4504 | 109.4504 | 109.4504 | 109.4504 | 109.4504 | 109.4504 | 109.4504 | 109.4504 | 109.4504 | 109.4504 | 109.4504 | 109.4504 | 109.4504 | 109.4504
55% | 3327.6421 | 4090.2265 | 4166.858 | 4129.2951 | 4165.0116 | 4179.6869 | 4226.7202 | 4323.4309 | 4404.7881 | 4442.2395 | 4408.8593 | 4548.8102 | 4571.0067 | 4544.7386 | 4597.4121 | 4622.0485 | 4622.0485 | 4622.0485 | 4622.0485 | 4622.0485 | 4622.0485 | 4622.0485 | 4622.0485 | 4622.0485 | 4622.0485 | 4622.0485 | 4622.0485 | 4622.0485 | 4622.0485 | 4622.0485 |  | 352.7187 | 405.6734 | 407.1346 | 405.5592 | 405.9643 | 408.8561 | 414.7164 | 425.0372 | 430.415 | 434.3056 | 440.1939 | 447.7114 | 456.8018 | 461.5659 | 460.0214 | 461.5522 | 461.5522 | 461.5522 | 461.5522 | 461.5522 | 461.5522 | 461.5522 | 461.5522 | 461.5522 | 461.5522 | 461.5522 | 461.5522 | 461.5522 | 461.5522 | 461.5522
50% | 3032.8171 | 3898.088 | 3985.0383 | 3942.4174 | 3982.9433 | 3999.5947 | 4052.9614 | 4162.6947 | 4255.0072 | 4297.5016 | 4259.6266 | 4418.4227 | 4443.6081 | 4413.8029 | 4473.5691 | 4501.523 | 4501.523 | 4501.523 | 4501.523 | 4501.523 | 4501.523 | 4501.523 | 4501.523 | 4501.523 | 4501.523 | 4501.523 | 4501.523 | 4501.523 | 4501.523 | 4501.523 |  | 703.3516 | 822.7155 | 826.0092 | 822.458 | 823.3713 | 829.8895 | 843.0992 | 866.363 | 878.4849 | 887.2547 | 900.5273 | 917.4725 | 937.9629 | 948.7014 | 945.2201 | 948.6707 | 948.6707 | 948.6707 | 948.6707 | 948.6707 | 948.6707 | 948.6707 | 948.6707 | 948.6707 | 948.6707 | 948.6707 | 948.6707 | 948.6707 | 948.6707 | 948.6707
45% | 1765.9337 | 2482.1322 | 2554.1023 | 2518.8243 | 2552.3683 | 2566.1509 | 2610.3233 | 2701.1513 | 2777.5598 | 2812.7331 | 2781.3834 | 2912.8214 | 2933.6678 | 2908.9975 | 2958.467 | 2981.6048 | 2981.6048 | 2981.6048 | 2981.6048 | 2981.6048 | 2981.6048 | 2981.6048 | 2981.6048 | 2981.6048 | 2981.6048 | 2981.6048 | 2981.6048 | 2981.6048 | 2981.6048 | 2981.6048 |  | 1017.5865 | 1222.642 | 1228.3004 | 1222.1997 | 1223.7687 | 1234.9662 | 1257.6592 | 1297.6242 | 1318.4485 | 1333.5141 | 1356.3152 | 1385.4253 | 1420.6258 | 1439.0735 | 1433.093 | 1439.0207 | 1439.0207 | 1439.0207 | 1439.0207 | 1439.0207 | 1439.0207 | 1439.0207 | 1439.0207 | 1439.0207 | 1439.0207 | 1439.0207 | 1439.0207 | 1439.0207 | 1439.0207 | 1439.0207
40% | 607.9205 | 1122.3189 | 1174.0104 | 1148.6725 | 1172.7649 | 1182.6641 | 1214.3902 | 1279.626 | 1334.5053 | 1359.768 | 1337.2515 | 1431.6548 | 1446.6274 | 1428.9084 | 1464.439 | 1481.0575 | 1481.0575 | 1481.0575 | 1481.0575 | 1481.0575 | 1481.0575 | 1481.0575 | 1481.0575 | 1481.0575 | 1481.0575 | 1481.0575 | 1481.0575 | 1481.0575 | 1481.0575 | 1481.0575 |  | 1058.8722 | 1336.5245 | 1344.1862 | 1335.9257 | 1338.0501 | 1353.212 | 1383.9391 | 1438.0532 | 1466.2499 | 1486.6493 | 1517.5228 | 1556.9388 | 1604.6016 | 1629.5804 | 1621.4826 | 1629.509 | 1629.509 | 1629.509 | 1629.509 | 1629.509 | 1629.509 | 1629.509 | 1629.509 | 1629.509 | 1629.509 | 1629.509 | 1629.509 | 1629.509 | 1629.509 | 1629.509
35% | 23.196 | 247.1276 | 281.389 | 264.3461 | 280.5402 | 287.3184 | 309.5259 | 357.4741 | 400.1436 | 420.4081 | 402.3339 | 478.1695 | 490.2 | 475.9627 | 504.5117 | 517.8647 | 517.8647 | 517.8647 | 517.8647 | 517.8647 | 517.8647 | 517.8647 | 517.8647 | 517.8647 | 517.8647 | 517.8647 | 517.8647 | 517.8647 | 517.8647 | 517.8647 |  | 1063.9608 | 1515.0828 | 1527.5312 | 1514.1099 | 1517.5615 | 1542.1962 | 1592.1207 | 1680.0438 | 1725.8572 | 1759.0016 | 1809.1639 | 1873.2061 | 1950.6472 | 1991.2321 | 1978.0751 | 1991.1161 | 1991.1161 | 1991.1161 | 1991.1161 | 1991.1161 | 1991.1161 | 1991.1161 | 1991.1161 | 1991.1161 | 1991.1161 | 1991.1161 | 1991.1161 | 1991.1161 | 1991.1161 | 1991.1161
30% | [9 empty] | 0.071582 |  | 2.2996 | 3.1509 | 2.1578 | 4.3353 | 5.6074 | 5.6074 | 5.6074 | 5.6074 | 5.6074 | 5.6074 | 5.6074 | 5.6074 | 5.6074 | 5.6074 | 5.6074 | 5.6074 | 5.6074 | 5.6074 | 5.6074 |  | 388.5058 | 1015.6243 | 1034.8788 | 1014.1196 | 1019.4583 | 1057.5615 | 1134.7813 | 1270.7746 | 1341.6355 | 1392.901 | 1470.4886 | 1569.5445 | 1689.3252 | 1752.0991 | 1731.7486 | 1751.9195 | 1751.9195 | 1751.9195 | 1751.9195 | 1751.9195 | 1751.9195 | 1751.9195 | 1751.9195 | 1751.9195 | 1751.9195 | 1751.9195 | 1751.9195 | 1751.9195 | 1751.9195 | 1751.9195
25% | [32 empty] | 10.8714 | 13.2189 | 10.6975 | 11.3209 | 16.2724 | 28.9785 | 59.8591 | 80.1406 | 96.5629 | 124.1616 | 164.1053 | 219.2802 | 251.1289 | 240.5861 | 251.035 | 251.035 | 251.035 | 251.035 | 251.035 | 251.035 | 251.035 | 251.035 | 251.035 | 251.035 | 251.035 | 251.035 | 251.035 | 251.035 | 251.035
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 20082.4323 | 25048.4194 | 25559.0881 | 25308.5245 | 25546.761 | 25644.7713 | 25959.3667 | 26608.5051 | 27156.899 | 27410.0291 | 27184.3956 | 28132.4312 | 28283.2762 | 28104.7752 | 28462.8939 | 28630.6444 | 28630.6444 | 28630.6444 | 28630.6444 | 28630.6444 | 28630.6444 | 28630.6444 | 28630.6444 | 28630.6444 | 28630.6444 | 28630.6444 | 28630.6444 | 28630.6444 | 28630.6444 | 28630.6444 | E @ R (MWh) | 4790.9487 | 6548.203 | 6600.6505 | 6544.1136 | 6558.6286 | 6662.7214 | 6876.3204 | 7260.9121 | 7465.4571 | 7615.1702 | 7844.4702 | 8141.8786 | 8508.3166 | 8703.2608 | 8639.8468 | 8702.7004 | 8702.7004 | 8702.7004 | 8702.7004 | 8702.7004 | 8702.7004 | 8702.7004 | 8702.7004 | 8702.7004 | 8702.7004 | 8702.7004 | 8702.7004 | 8702.7004 | 8702.7004 | 8702.7004
Option 7 Summer POE50 W E @ R (MWh) N 2 | 14057.7026 | 17533.8936 | 17891.3617 | 17715.9672 | 17882.7327 | 17951.3399 | 18171.5567 | 18625.9536 | 19009.8293 | 19187.0204 | 19029.0769 | 19692.7018 | 19798.2933 | 19673.3426 | 19924.0258 | 20041.4511 | 20041.4511 | 20041.4511 | 20041.4511 | 20041.4511 | 20041.4511 | 20041.4511 | 20041.4511 | 20041.4511 | 20041.4511 | 20041.4511 | 20041.4511 | 20041.4511 | 20041.4511 | 20041.4511 | Option 7 Summer POE10 W E @ R (MWh) N 2 | 1437.2846 | 1964.4609 | 1980.1951 | 1963.2341 | 1967.5886 | 1998.8164 | 2062.8961 | 2178.2736 | 2239.6371 | 2284.5511 | 2353.341 | 2442.5636 | 2552.495 | 2610.9782 | 2591.954 | 2610.8101 | 2610.8101 | 2610.8101 | 2610.8101 | 2610.8101 | 2610.8101 | 2610.8101 | 2610.8101 | 2610.8101 | 2610.8101 | 2610.8101 | 2610.8101 | 2610.8101 | 2610.8101 | 2610.8101
Option 8 -
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | 7.4585 | 8.8006 | 8.9429 | 9.1188 | 9.3524 | 9.5739 | 9.9609 | 10.9342 | 11.4578 | 11.0758 | 12.2583 | 12.4713 | 12.6244 | 13.3463 | 13.4638 | 13.4638 | 13.4638 | 13.4638 | 13.4638 | 13.4638 | 13.4638 | 13.4638 | 13.4638 | 13.4638 | 13.4638 | 13.4638 | 13.4638 | 13.4638 | 13.4638 | 13.4638 |  | 8.6919 | 9.9721 | 10.1047 | 10.5622 | 10.551 | 10.6516 | 11.0451 | 12.1756 | 12.6421 | 12.2006 | 13.4204 | 12.9082 | 13.3691 | 13.7012 | 13.5647 | 13.5647 | 13.5647 | 13.5647 | 13.5647 | 13.5647 | 13.5647 | 13.5647 | 13.5647 | 13.5647 | 13.5647 | 13.5647 | 13.5647 | 13.5647 | 13.5647 | 13.5647
98% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
97% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
95% | 28.0297 | 33.2092 | 33.7584 | 34.4374 | 35.339 | 36.1936 | 37.6872 | 41.4437 | 43.4642 | 41.9901 | 46.5535 | 47.3756 | 47.9667 | 50.7525 | 51.2059 | 51.2059 | 51.2059 | 51.2059 | 51.2059 | 51.2059 | 51.2059 | 51.2059 | 51.2059 | 51.2059 | 51.2059 | 51.2059 | 51.2059 | 51.2059 | 51.2059 | 51.2059 |  | 32.79 | 37.7305 | 38.2421 | 40.0078 | 39.9648 | 40.3531 | 41.8717 | 46.2346 | 48.035 | 46.3308 | 51.0385 | 49.062 | 50.8404 | 52.1221 | 51.5955 | 51.5955 | 51.5955 | 51.5955 | 51.5955 | 51.5955 | 51.5955 | 51.5955 | 51.5955 | 51.5955 | 51.5955 | 51.5955 | 51.5955 | 51.5955 | 51.5955 | 51.5955
90% | 157.3528 | 187.297 | 190.4721 | 194.3976 | 199.6095 | 204.5504 | 213.1852 | 234.9023 | 246.5833 | 238.0616 | 264.4434 | 269.1966 | 272.6134 | 288.719 | 291.3405 | 291.3405 | 291.3405 | 291.3405 | 291.3405 | 291.3405 | 291.3405 | 291.3405 | 291.3405 | 291.3405 | 291.3405 | 291.3405 | 291.3405 | 291.3405 | 291.3405 | 291.3405 |  | 184.8731 | 213.4355 | 216.3934 | 226.6014 | 226.3526 | 228.5973 | 237.3766 | 262.5998 | 273.0084 | 263.1559 | 290.3726 | 278.9455 | 289.2275 | 296.6368 | 293.5927 | 293.5927 | 293.5927 | 293.5927 | 293.5927 | 293.5927 | 293.5927 | 293.5927 | 293.5927 | 293.5927 | 293.5927 | 293.5927 | 293.5927 | 293.5927 | 293.5927 | 293.5927
85% | 626.672 | 751.7764 | 765.0422 | 781.4425 | 803.2172 | 823.8602 | 859.9357 | 950.668 | 999.4703 | 963.8676 | 1074.0886 | 1093.9472 | 1108.2222 | 1175.5104 | 1186.4628 | 1186.4628 | 1186.4628 | 1186.4628 | 1186.4628 | 1186.4628 | 1186.4628 | 1186.4628 | 1186.4628 | 1186.4628 | 1186.4628 | 1186.4628 | 1186.4628 | 1186.4628 | 1186.4628 | 1186.4628 |  | 741.6496 | 860.9812 | 873.3391 | 915.9877 | 914.9483 | 924.3264 | 961.0057 | 1066.3864 | 1109.8728 | 1068.7096 | 1182.4188 | 1134.6775 | 1177.6348 | 1208.5906 | 1195.8725 | 1195.8725 | 1195.8725 | 1195.8725 | 1195.8725 | 1195.8725 | 1195.8725 | 1195.8725 | 1195.8725 | 1195.8725 | 1195.8725 | 1195.8725 | 1195.8725 | 1195.8725 | 1195.8725 | 1195.8725
80% | 937.6386 | 1135.7149 | 1156.7184 | 1182.6849 | 1217.1605 | 1249.8444 | 1306.9623 | 1450.6177 | 1527.8858 | 1471.5164 | 1646.0281 | 1677.4699 | 1700.0714 | 1806.608 | 1823.9489 | 1823.9489 | 1823.9489 | 1823.9489 | 1823.9489 | 1823.9489 | 1823.9489 | 1823.9489 | 1823.9489 | 1823.9489 | 1823.9489 | 1823.9489 | 1823.9489 | 1823.9489 | 1823.9489 | 1823.9489 |  | 1119.6813 | 1308.6177 | 1328.1837 | 1395.7087 | 1394.063 | 1408.9114 | 1466.9853 | 1633.8333 | 1702.6848 | 1637.5115 | 1817.5461 | 1741.9578 | 1809.9715 | 1858.9836 | 1838.8471 | 1838.8471 | 1838.8471 | 1838.8471 | 1838.8471 | 1838.8471 | 1838.8471 | 1838.8471 | 1838.8471 | 1838.8471 | 1838.8471 | 1838.8471 | 1838.8471 | 1838.8471 | 1838.8471 | 1838.8471
75% | 1618.1428 | 1984.0141 | 2022.8101 | 2070.7733 | 2134.4541 | 2194.8252 | 2300.329 | 2565.6781 | 2708.4018 | 2604.2807 | 2926.6253 | 2984.7021 | 3026.4498 | 3223.236 | 3255.2667 | 3255.2667 | 3255.2667 | 3255.2667 | 3255.2667 | 3255.2667 | 3255.2667 | 3255.2667 | 3255.2667 | 3255.2667 | 3255.2667 | 3255.2667 | 3255.2667 | 3255.2667 | 3255.2667 | 3255.2667 |  | 1954.3979 | 2303.3867 | 2339.5275 | 2464.2546 | 2461.2148 | 2488.6415 | 2595.9111 | 2904.0999 | 3031.2772 | 2910.894 | 3243.44 | 3103.8192 | 3229.4488 | 3319.9801 | 3282.7856 | 3282.7856 | 3282.7856 | 3282.7856 | 3282.7856 | 3282.7856 | 3282.7856 | 3282.7856 | 3282.7856 | 3282.7856 | 3282.7856 | 3282.7856 | 3282.7856 | 3282.7856 | 3282.7856 | 3282.7856
70% | 2423.1485 | 3018.6926 | 3081.8425 | 3159.9143 | 3263.5701 | 3361.8387 | 3533.5717 | 3965.4915 | 4197.8089 | 4028.3265 | 4553.0204 | 4647.5545 | 4715.5089 | 5035.8261 | 5087.9638 | 5087.9638 | 5087.9638 | 5087.9638 | 5087.9638 | 5087.9638 | 5087.9638 | 5087.9638 | 5087.9638 | 5087.9638 | 5087.9638 | 5087.9638 | 5087.9638 | 5087.9638 | 5087.9638 | 5087.9638 |  | 2970.4851 | 3538.5488 | 3597.3768 | 3800.4002 | 3795.4522 | 3840.0957 | 4014.703 | 4516.3548 | 4723.3667 | 4527.4139 | 5068.713 | 4841.4463 | 5045.9389 | 5193.3006 | 5132.7574 | 5132.7574 | 5132.7574 | 5132.7574 | 5132.7574 | 5132.7574 | 5132.7574 | 5132.7574 | 5132.7574 | 5132.7574 | 5132.7574 | 5132.7574 | 5132.7574 | 5132.7574 | 5132.7574 | 5132.7574
65% | 2670.9583 | 3400.2393 | 3477.5703 | 3573.1741 | 3700.1072 | 3820.4432 | 4030.7411 | 4559.6539 | 4844.1411 | 4636.5993 | 5279.1198 | 5394.8827 | 5478.0971 | 5870.3455 | 5934.1915 | 5934.1915 | 5934.1915 | 5934.1915 | 5934.1915 | 5934.1915 | 5934.1915 | 5934.1915 | 5934.1915 | 5934.1915 | 5934.1915 | 5934.1915 | 5934.1915 | 5934.1915 | 5934.1915 | 5934.1915 |  | 3341.2062 | 4036.8358 | 4108.8743 | 4357.4892 | 4351.43 | 4406.0989 | 4619.9164 | 5234.2205 | 5487.7194 | 5247.763 | 5910.6177 | 5632.3154 | 5882.7294 | 6063.1829 | 5989.044 | 5989.044 | 5989.044 | 5989.044 | 5989.044 | 5989.044 | 5989.044 | 5989.044 | 5989.044 | 5989.044 | 5989.044 | 5989.044 | 5989.044 | 5989.044 | 5989.044 | 5989.044
60% | 2886.5439 | 3791.1059 | 3887.0233 | 4005.6052 | 4163.0464 | 4312.3049 | 4573.1473 | 5229.1832 | 5582.0462 | 5324.6222 | 6121.571 | 6265.1573 | 6368.3721 | 6854.8965 | 6934.0877 | 6934.0877 | 6934.0877 | 6934.0877 | 6934.0877 | 6934.0877 | 6934.0877 | 6934.0877 | 6934.0877 | 6934.0877 | 6934.0877 | 6934.0877 | 6934.0877 | 6934.0877 | 6934.0877 | 6934.0877 |  | 3717.8843 | 4580.7069 | 4670.0597 | 4978.4286 | 4970.9132 | 5038.7216 | 5303.9296 | 6065.8803 | 6380.3071 | 6082.6777 | 6904.848 | 6559.6564 | 6870.2568 | 7094.0819 | 7002.1239 | 7002.1239 | 7002.1239 | 7002.1239 | 7002.1239 | 7002.1239 | 7002.1239 | 7002.1239 | 7002.1239 | 7002.1239 | 7002.1239 | 7002.1239 | 7002.1239 | 7002.1239 | 7002.1239 | 7002.1239
55% | 2587.93 | 3569.0383 | 3673.0724 | 3801.6891 | 3972.4533 | 4134.3425 | 4417.258 | 5128.8093 | 5511.5325 | 5232.3246 | 6096.7133 | 6252.4502 | 6364.3994 | 6892.0947 | 6977.9873 | 6977.9873 | 6977.9873 | 6977.9873 | 6977.9873 | 6977.9873 | 6977.9873 | 6977.9873 | 6977.9873 | 6977.9873 | 6977.9873 | 6977.9873 | 6977.9873 | 6977.9873 | 6977.9873 | 6977.9873 |  | 3489.6205 | 4425.4573 | 4522.3714 | 4856.8353 | 4848.6838 | 4922.2304 | 5209.881 | 6036.3099 | 6377.3443 | 6054.5287 | 6946.2732 | 6571.8705 | 6908.7548 | 7151.5206 | 7051.7809 | 7051.7809 | 7051.7809 | 7051.7809 | 7051.7809 | 7051.7809 | 7051.7809 | 7051.7809 | 7051.7809 | 7051.7809 | 7051.7809 | 7051.7809 | 7051.7809 | 7051.7809 | 7051.7809 | 7051.7809
50% | 1977.4132 | 2976.5959 | 3082.5466 | 3213.5326 | 3387.4428 | 3552.3143 | 3840.4419 | 4565.1017 | 4954.8755 | 4670.5239 | 5550.8367 | 5709.4427 | 5823.4542 | 6360.871 | 6448.3459 | 6448.3459 | 6448.3459 | 6448.3459 | 6448.3459 | 6448.3459 | 6448.3459 | 6448.3459 | 6448.3459 | 6448.3459 | 6448.3459 | 6448.3459 | 6448.3459 | 6448.3459 | 6448.3459 | 6448.3459 |  | 2895.7151 | 3848.7922 | 3947.4917 | 4288.1172 | 4279.8156 | 4354.717 | 4647.6668 | 5489.3206 | 5836.6377 | 5507.875 | 6416.0476 | 6034.7475 | 6377.838 | 6625.0761 | 6523.499 | 6523.499 | 6523.499 | 6523.499 | 6523.499 | 6523.499 | 6523.499 | 6523.499 | 6523.499 | 6523.499 | 6523.499 | 6523.499 | 6523.499 | 6523.499 | 6523.499 | 6523.499
45% | 1115.1481 | 2058.8937 | 2158.966 | 2282.6846 | 2446.9458 | 2602.6699 | 2874.8114 | 3559.2653 | 3927.4136 | 3658.8385 | 4490.3094 | 4640.1156 | 4747.8014 | 5255.401 | 5338.0226 | 5338.0226 | 5338.0226 | 5338.0226 | 5338.0226 | 5338.0226 | 5338.0226 | 5338.0226 | 5338.0226 | 5338.0226 | 5338.0226 | 5338.0226 | 5338.0226 | 5338.0226 | 5338.0226 | 5338.0226 |  | 1982.5003 | 2882.6984 | 2975.9219 | 3297.6486 | 3289.8076 | 3360.5533 | 3637.2496 | 4432.2063 | 4760.2534 | 4449.7313 | 5307.5163 | 4947.3717 | 5271.4266 | 5504.9474 | 5409.006 | 5409.006 | 5409.006 | 5409.006 | 5409.006 | 5409.006 | 5409.006 | 5409.006 | 5409.006 | 5409.006 | 5409.006 | 5409.006 | 5409.006 | 5409.006 | 5409.006 | 5409.006
40% | 218.0643 | 1019.3158 | 1109.6444 | 1221.317 | 1369.5846 | 1510.1463 | 1755.7904 | 2373.6013 | 2705.9042 | 2463.4794 | 3213.9927 | 3349.2128 | 3446.4136 | 3904.5899 | 3979.1669 | 3979.1669 | 3979.1669 | 3979.1669 | 3979.1669 | 3979.1669 | 3979.1669 | 3979.1669 | 3979.1669 | 3979.1669 | 3979.1669 | 3979.1669 | 3979.1669 | 3979.1669 | 3979.1669 | 3979.1669 |  | 950.3606 | 1762.9094 | 1847.056 | 2137.4573 | 2130.3798 | 2194.2372 | 2443.9925 | 3161.5469 | 3457.6532 | 3177.3656 | 3951.6309 | 3626.5524 | 3919.0552 | 4129.8388 | 4043.2389 | 4043.2389 | 4043.2389 | 4043.2389 | 4043.2389 | 4043.2389 | 4043.2389 | 4043.2389 | 4043.2389 | 4043.2389 | 4043.2389 | 4043.2389 | 4043.2389 | 4043.2389 | 4043.2389 | 4043.2389
35% |  | 100.0043 | 136.3101 | 188.3336 | 269.145 | 357.6005 | 537.7501 | 1017.2126 | 1275.1019 | 1086.964 | 1669.4126 | 1774.3523 | 1849.7867 | 2205.3621 | 2263.2389 | 2263.2389 | 2263.2389 | 2263.2389 | 2263.2389 | 2263.2389 | 2263.2389 | 2263.2389 | 2263.2389 | 2263.2389 | 2263.2389 | 2263.2389 | 2263.2389 | 2263.2389 | 2263.2389 | 2263.2389 |  | 75.8706 | 543.275 | 608.5783 | 833.9491 | 828.4565 | 878.0141 | 1071.8409 | 1628.7111 | 1858.5094 | 1640.9875 | 2241.8691 | 1989.5864 | 2216.5882 | 2380.1703 | 2312.963 | 2312.963 | 2312.963 | 2312.963 | 2312.963 | 2312.963 | 2312.963 | 2312.963 | 2312.963 | 2312.963 | 2312.963 | 2312.963 | 2312.963 | 2312.963 | 2312.963 | 2312.963
30% | [6 empty] | 0.47307 | 86.92 | 189.3305 | 111.0221 | 411.6753 | 482.9899 | 535.3611 | 782.2235 | 822.4051 | 822.4051 | 822.4051 | 822.4051 | 822.4051 | 822.4051 | 822.4051 | 822.4051 | 822.4051 | 822.4051 | 822.4051 | 822.4051 | 822.4051 | 822.4051 | 822.4051 | 822.4051 |  |  | 0.62469 | 3.9886 | 37.019 | 35.8334 | 47.1947 | 105.5643 | 385.3047 | 541.4169 | 393.1792 | 807.5688 | 632.4187 | 790.0173 | 903.5861 | 856.9266 | 856.9266 | 856.9266 | 856.9266 | 856.9266 | 856.9266 | 856.9266 | 856.9266 | 856.9266 | 856.9266 | 856.9266 | 856.9266 | 856.9266 | 856.9266 | 856.9266 | 856.9266
25% | [11 empty] | 0.074459 | 1.4981 | 31.3754 | 39.665 | 39.665 | 39.665 | 39.665 | 39.665 | 39.665 | 39.665 | 39.665 | 39.665 | 39.665 | 39.665 | 39.665 | 39.665 | 39.665 | 39.665 | 39.665 | [9 empty] | 1.778 |  | 36.4973 | 8.794 | 32.9113 | 59.1747 | 47.515 | 47.515 | 47.515 | 47.515 | 47.515 | 47.515 | 47.515 | 47.515 | 47.515 | 47.515 | 47.515 | 47.515 | 47.515 | 47.515 | 47.515 | 47.515
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 17081.9558 | 23794.351 | 24536.8726 | 25461.914 | 26701.7135 | 27888.803 | 29989.1249 | 35382.088 | 38338.1632 | 36178.0578 | 42923.0818 | 44155.3813 | 45043.6541 | 49253.6461 | 49942.2957 | 49942.2957 | 49942.2957 | 49942.2957 | 49942.2957 | 49942.2957 | 49942.2957 | 49942.2957 | 49942.2957 | 49942.2957 | 49942.2957 | 49942.2957 | 49942.2957 | 49942.2957 | 49942.2957 | 49942.2957 | E @ R (MWh) | 23231.0692 | 30050.4324 | 30776.634 | 33304.0623 | 33242.0879 | 33801.9108 | 36005.2501 | 42446.433 | 45146.4814 | 42590.1209 | 49687.9201 | 46694.4681 | 49387.1485 | 51336.3448 | 50534.6619 | 50534.6619 | 50534.6619 | 50534.6619 | 50534.6619 | 50534.6619 | 50534.6619 | 50534.6619 | 50534.6619 | 50534.6619 | 50534.6619 | 50534.6619 | 50534.6619 | 50534.6619 | 50534.6619 | 50534.6619
Option 8 Winter POE50 W E @ R (MWh) N 2 | 11957.3691 | 16656.0457 | 17175.8108 | 17823.3398 | 18691.1994 | 19522.1621 | 20992.3874 | 24767.4616 | 26836.7142 | 25324.6404 | 30046.1573 | 30908.7669 | 31530.5579 | 34477.5523 | 34959.607 | 34959.607 | 34959.607 | 34959.607 | 34959.607 | 34959.607 | 34959.607 | 34959.607 | 34959.607 | 34959.607 | 34959.607 | 34959.607 | 34959.607 | 34959.607 | 34959.607 | 34959.607 | Option 8 Winter POE10 W E @ R (MWh) N 2 | 6969.3207 | 9015.1297 | 9232.9902 | 9991.2187 | 9972.6264 | 10140.5732 | 10801.575 | 12733.9299 | 13543.9444 | 12777.0363 | 14906.376 | 14008.3404 | 14816.1446 | 15400.9034 | 15160.3986 | 15160.3986 | 15160.3986 | 15160.3986 | 15160.3986 | 15160.3986 | 15160.3986 | 15160.3986 | 15160.3986 | 15160.3986 | 15160.3986 | 15160.3986 | 15160.3986 | 15160.3986 | 15160.3986 | 15160.3986
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | 10.4659 | 11.7471 | 11.8758 | 11.8127 | 11.8727 | 11.8974 | 11.9764 | 12.1389 | 12.2756 | 12.3385 | 12.2824 | 12.5175 | 12.5548 | 12.5107 | 12.5992 | 12.6406 | 12.6406 | 12.6406 | 12.6406 | 12.6406 | 12.6406 | 12.6406 | 12.6406 | 12.6406 | 12.6406 | 12.6406 | 12.6406 | 12.6406 | 12.6406 | 12.6406 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
98% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
97% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 13.9883 | 15.3913 | 15.4301 | 15.3883 | 15.399 | 15.4757 | 15.6309 | 15.9044 | 16.0469 | 16.1499 | 16.3059 | 16.5051 | 16.746 | 16.8722 | 16.8313 | 16.8718 | 16.8718 | 16.8718 | 16.8718 | 16.8718 | 16.8718 | 16.8718 | 16.8718 | 16.8718 | 16.8718 | 16.8718 | 16.8718 | 16.8718 | 16.8718 | 16.8718
95% | 9.863 | 11.0991 | 11.2233 | 11.1624 | 11.2203 | 11.2441 | 11.3203 | 11.4771 | 11.609 | 11.6697 | 11.6156 | 11.8424 | 11.8784 | 11.8358 | 11.9212 | 11.9611 | 11.9611 | 11.9611 | 11.9611 | 11.9611 | 11.9611 | 11.9611 | 11.9611 | 11.9611 | 11.9611 | 11.9611 | 11.9611 | 11.9611 | 11.9611 | 11.9611 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
90% | 203.721 | 229.9238 | 232.5569 | 231.2662 | 232.4934 | 232.9977 | 234.6138 | 237.9368 | 240.7323 | 242.0191 | 240.8722 | 245.6809 | 246.4436 | 245.541 | 247.3509 | 248.1974 | 248.1974 | 248.1974 | 248.1974 | 248.1974 | 248.1974 | 248.1974 | 248.1974 | 248.1974 | 248.1974 | 248.1974 | 248.1974 | 248.1974 | 248.1974 | 248.1974 |  | 12.9287 | 14.2598 | 14.2965 | 14.2569 | 14.2671 | 14.3398 | 14.4871 | 14.7465 | 14.8817 | 14.9794 | 15.1275 | 15.3164 | 15.5449 | 15.6647 | 15.6258 | 15.6643 | 15.6643 | 15.6643 | 15.6643 | 15.6643 | 15.6643 | 15.6643 | 15.6643 | 15.6643 | 15.6643 | 15.6643 | 15.6643 | 15.6643 | 15.6643 | 15.6643
85% | 697.0932 | 790.6056 | 800.0026 | 795.3964 | 799.7762 | 801.5757 | 807.3432 | 819.2024 | 829.1789 | 833.7714 | 829.6781 | 846.8397 | 849.5615 | 846.3404 | 852.7995 | 855.8206 | 855.8206 | 855.8206 | 855.8206 | 855.8206 | 855.8206 | 855.8206 | 855.8206 | 855.8206 | 855.8206 | 855.8206 | 855.8206 | 855.8206 | 855.8206 | 855.8206 |  | 11.8691 | 13.1282 | 13.1629 | 13.1255 | 13.1351 | 13.2038 | 13.3432 | 13.5886 | 13.7165 | 13.809 | 13.949 | 14.1277 | 14.3439 | 14.4571 | 14.4204 | 14.4568 | 14.4568 | 14.4568 | 14.4568 | 14.4568 | 14.4568 | 14.4568 | 14.4568 | 14.4568 | 14.4568 | 14.4568 | 14.4568 | 14.4568 | 14.4568 | 14.4568
80% | 1077.8455 | 1229.7508 | 1245.0156 | 1237.5332 | 1244.6479 | 1247.5711 | 1256.9401 | 1276.2046 | 1292.4109 | 1299.8711 | 1293.2218 | 1321.0998 | 1325.5213 | 1320.2887 | 1330.7811 | 1335.6887 | 1335.6887 | 1335.6887 | 1335.6887 | 1335.6887 | 1335.6887 | 1335.6887 | 1335.6887 | 1335.6887 | 1335.6887 | 1335.6887 | 1335.6887 | 1335.6887 | 1335.6887 | 1335.6887 |  | 43.2377 | 47.9863 | 48.1174 | 47.9761 | 48.0124 | 48.2717 | 48.7972 | 49.7227 | 50.205 | 50.5539 | 51.0819 | 51.756 | 52.5712 | 52.9984 | 52.8599 | 52.9972 | 52.9972 | 52.9972 | 52.9972 | 52.9972 | 52.9972 | 52.9972 | 52.9972 | 52.9972 | 52.9972 | 52.9972 | 52.9972 | 52.9972 | 52.9972 | 52.9972
75% | 1809.2093 | 2079.6387 | 2106.8139 | 2093.4933 | 2106.1592 | 2111.3633 | 2128.0424 | 2162.3381 | 2191.1892 | 2204.4703 | 2192.633 | 2242.2627 | 2250.134 | 2240.8188 | 2259.498 | 2268.2346 | 2268.2346 | 2268.2346 | 2268.2346 | 2268.2346 | 2268.2346 | 2268.2346 | 2268.2346 | 2268.2346 | 2268.2346 | 2268.2346 | 2268.2346 | 2268.2346 | 2268.2346 | 2268.2346 |  | 19.4996 | 21.73 | 21.7915 | 21.7252 | 21.7422 | 21.864 | 22.1109 | 22.5456 | 22.7721 | 22.936 | 23.184 | 23.5006 | 23.8835 | 24.0842 | 24.0191 | 24.0836 | 24.0836 | 24.0836 | 24.0836 | 24.0836 | 24.0836 | 24.0836 | 24.0836 | 24.0836 | 24.0836 | 24.0836 | 24.0836 | 24.0836 | 24.0836 | 24.0836
70% | 2151.4453 | 2496.8455 | 2531.5545 | 2514.541 | 2530.7182 | 2537.3651 | 2558.6681 | 2602.4716 | 2639.3211 | 2656.284 | 2641.165 | 2704.5535 | 2714.6071 | 2702.7094 | 2726.567 | 2737.7256 | 2737.7256 | 2737.7256 | 2737.7256 | 2737.7256 | 2737.7256 | 2737.7256 | 2737.7256 | 2737.7256 | 2737.7256 | 2737.7256 | 2737.7256 | 2737.7256 | 2737.7256 | 2737.7256 |  | 52.1409 | 58.4004 | 58.5732 | 58.3869 | 58.4348 | 58.7767 | 59.4694 | 60.6894 | 61.3251 | 61.785 | 62.481 | 63.3696 | 64.4442 | 65.0073 | 64.8247 | 65.0057 | 65.0057 | 65.0057 | 65.0057 | 65.0057 | 65.0057 | 65.0057 | 65.0057 | 65.0057 | 65.0057 | 65.0057 | 65.0057 | 65.0057 | 65.0057 | 65.0057
65% | 2417.2518 | 2841.3891 | 2884.0103 | 2863.1184 | 2882.9834 | 2891.1455 | 2917.3047 | 2971.0936 | 3016.3433 | 3037.1731 | 3018.6076 | 3096.446 | 3108.7914 | 3094.1815 | 3123.4776 | 3137.18 | 3137.18 | 3137.18 | 3137.18 | 3137.18 | 3137.18 | 3137.18 | 3137.18 | 3137.18 | 3137.18 | 3137.18 | 3137.18 | 3137.18 | 3137.18 | 3137.18 |  | 15.261 | 17.2036 | 17.2572 | 17.1994 | 17.2143 | 17.3204 | 17.5354 | 17.914 | 18.1113 | 18.254 | 18.47 | 18.7458 | 19.0793 | 19.254 | 19.1974 | 19.2535 | 19.2535 | 19.2535 | 19.2535 | 19.2535 | 19.2535 | 19.2535 | 19.2535 | 19.2535 | 19.2535 | 19.2535 | 19.2535 | 19.2535 | 19.2535 | 19.2535
60% | 3150.8806 | 3770.5408 | 3832.8099 | 3802.2871 | 3831.3096 | 3843.2344 | 3881.4527 | 3960.0377 | 4026.147 | 4056.5791 | 4029.4551 | 4143.1763 | 4161.2127 | 4139.8678 | 4182.6692 | 4202.6882 | 4202.6882 | 4202.6882 | 4202.6882 | 4202.6882 | 4202.6882 | 4202.6882 | 4202.6882 | 4202.6882 | 4202.6882 | 4202.6882 | 4202.6882 | 4202.6882 | 4202.6882 | 4202.6882 |  | 85.4213 | 97.113 | 97.4357 | 97.0878 | 97.1773 | 97.8157 | 99.1096 | 101.3883 | 102.5757 | 103.4347 | 104.7347 | 106.3945 | 108.4016 | 109.4534 | 109.1124 | 109.4504 | 109.4504 | 109.4504 | 109.4504 | 109.4504 | 109.4504 | 109.4504 | 109.4504 | 109.4504 | 109.4504 | 109.4504 | 109.4504 | 109.4504 | 109.4504 | 109.4504
55% | 3327.6421 | 4090.2265 | 4166.858 | 4129.2951 | 4165.0116 | 4179.6869 | 4226.7202 | 4323.4309 | 4404.7881 | 4442.2395 | 4408.8593 | 4548.8102 | 4571.0067 | 4544.7386 | 4597.4121 | 4622.0485 | 4622.0485 | 4622.0485 | 4622.0485 | 4622.0485 | 4622.0485 | 4622.0485 | 4622.0485 | 4622.0485 | 4622.0485 | 4622.0485 | 4622.0485 | 4622.0485 | 4622.0485 | 4622.0485 |  | 352.7187 | 405.6734 | 407.1346 | 405.5592 | 405.9643 | 408.8561 | 414.7164 | 425.0372 | 430.415 | 434.3056 | 440.1939 | 447.7114 | 456.8018 | 461.5659 | 460.0214 | 461.5522 | 461.5522 | 461.5522 | 461.5522 | 461.5522 | 461.5522 | 461.5522 | 461.5522 | 461.5522 | 461.5522 | 461.5522 | 461.5522 | 461.5522 | 461.5522 | 461.5522
50% | 3032.8171 | 3898.088 | 3985.0383 | 3942.4174 | 3982.9433 | 3999.5947 | 4052.9614 | 4162.6947 | 4255.0072 | 4297.5016 | 4259.6266 | 4418.4227 | 4443.6081 | 4413.8029 | 4473.5691 | 4501.523 | 4501.523 | 4501.523 | 4501.523 | 4501.523 | 4501.523 | 4501.523 | 4501.523 | 4501.523 | 4501.523 | 4501.523 | 4501.523 | 4501.523 | 4501.523 | 4501.523 |  | 703.3516 | 822.7155 | 826.0092 | 822.458 | 823.3713 | 829.8895 | 843.0992 | 866.363 | 878.4849 | 887.2547 | 900.5273 | 917.4725 | 937.9629 | 948.7014 | 945.2201 | 948.6707 | 948.6707 | 948.6707 | 948.6707 | 948.6707 | 948.6707 | 948.6707 | 948.6707 | 948.6707 | 948.6707 | 948.6707 | 948.6707 | 948.6707 | 948.6707 | 948.6707
45% | 1765.9337 | 2482.1322 | 2554.1023 | 2518.8243 | 2552.3683 | 2566.1509 | 2610.3233 | 2701.1513 | 2777.5598 | 2812.7331 | 2781.3834 | 2912.8214 | 2933.6678 | 2908.9975 | 2958.467 | 2981.6048 | 2981.6048 | 2981.6048 | 2981.6048 | 2981.6048 | 2981.6048 | 2981.6048 | 2981.6048 | 2981.6048 | 2981.6048 | 2981.6048 | 2981.6048 | 2981.6048 | 2981.6048 | 2981.6048 |  | 1017.5865 | 1222.642 | 1228.3004 | 1222.1997 | 1223.7687 | 1234.9662 | 1257.6592 | 1297.6242 | 1318.4485 | 1333.5141 | 1356.3152 | 1385.4253 | 1420.6258 | 1439.0735 | 1433.093 | 1439.0207 | 1439.0207 | 1439.0207 | 1439.0207 | 1439.0207 | 1439.0207 | 1439.0207 | 1439.0207 | 1439.0207 | 1439.0207 | 1439.0207 | 1439.0207 | 1439.0207 | 1439.0207 | 1439.0207
40% | 607.9205 | 1122.3189 | 1174.0104 | 1148.6725 | 1172.7649 | 1182.6641 | 1214.3902 | 1279.626 | 1334.5053 | 1359.768 | 1337.2515 | 1431.6548 | 1446.6274 | 1428.9084 | 1464.439 | 1481.0575 | 1481.0575 | 1481.0575 | 1481.0575 | 1481.0575 | 1481.0575 | 1481.0575 | 1481.0575 | 1481.0575 | 1481.0575 | 1481.0575 | 1481.0575 | 1481.0575 | 1481.0575 | 1481.0575 |  | 1058.8722 | 1336.5245 | 1344.1862 | 1335.9257 | 1338.0501 | 1353.212 | 1383.9391 | 1438.0532 | 1466.2499 | 1486.6493 | 1517.5228 | 1556.9388 | 1604.6016 | 1629.5804 | 1621.4826 | 1629.509 | 1629.509 | 1629.509 | 1629.509 | 1629.509 | 1629.509 | 1629.509 | 1629.509 | 1629.509 | 1629.509 | 1629.509 | 1629.509 | 1629.509 | 1629.509 | 1629.509
35% | 23.196 | 247.1276 | 281.389 | 264.3461 | 280.5402 | 287.3184 | 309.5259 | 357.4741 | 400.1436 | 420.4081 | 402.3339 | 478.1695 | 490.2 | 475.9627 | 504.5117 | 517.8647 | 517.8647 | 517.8647 | 517.8647 | 517.8647 | 517.8647 | 517.8647 | 517.8647 | 517.8647 | 517.8647 | 517.8647 | 517.8647 | 517.8647 | 517.8647 | 517.8647 |  | 1063.9608 | 1515.0828 | 1527.5312 | 1514.1099 | 1517.5615 | 1542.1962 | 1592.1207 | 1680.0438 | 1725.8572 | 1759.0016 | 1809.1639 | 1873.2061 | 1950.6472 | 1991.2321 | 1978.0751 | 1991.1161 | 1991.1161 | 1991.1161 | 1991.1161 | 1991.1161 | 1991.1161 | 1991.1161 | 1991.1161 | 1991.1161 | 1991.1161 | 1991.1161 | 1991.1161 | 1991.1161 | 1991.1161 | 1991.1161
30% | [9 empty] | 0.071582 |  | 2.2996 | 3.1509 | 2.1578 | 4.3353 | 5.6074 | 5.6074 | 5.6074 | 5.6074 | 5.6074 | 5.6074 | 5.6074 | 5.6074 | 5.6074 | 5.6074 | 5.6074 | 5.6074 | 5.6074 | 5.6074 | 5.6074 |  | 388.5058 | 1015.6243 | 1034.8788 | 1014.1196 | 1019.4583 | 1057.5615 | 1134.7813 | 1270.7746 | 1341.6355 | 1392.901 | 1470.4886 | 1569.5445 | 1689.3252 | 1752.0991 | 1731.7486 | 1751.9195 | 1751.9195 | 1751.9195 | 1751.9195 | 1751.9195 | 1751.9195 | 1751.9195 | 1751.9195 | 1751.9195 | 1751.9195 | 1751.9195 | 1751.9195 | 1751.9195 | 1751.9195 | 1751.9195
25% | [32 empty] | 10.8714 | 13.2189 | 10.6975 | 11.3209 | 16.2724 | 28.9785 | 59.8591 | 80.1406 | 96.5629 | 124.1616 | 164.1053 | 219.2802 | 251.1289 | 240.5861 | 251.035 | 251.035 | 251.035 | 251.035 | 251.035 | 251.035 | 251.035 | 251.035 | 251.035 | 251.035 | 251.035 | 251.035 | 251.035 | 251.035 | 251.035
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 20082.4323 | 25048.4194 | 25559.0881 | 25308.5245 | 25546.761 | 25644.7713 | 25959.3667 | 26608.5051 | 27156.899 | 27410.0291 | 27184.3956 | 28132.4312 | 28283.2762 | 28104.7752 | 28462.8939 | 28630.6444 | 28630.6444 | 28630.6444 | 28630.6444 | 28630.6444 | 28630.6444 | 28630.6444 | 28630.6444 | 28630.6444 | 28630.6444 | 28630.6444 | 28630.6444 | 28630.6444 | 28630.6444 | 28630.6444 | E @ R (MWh) | 4790.9487 | 6548.203 | 6600.6505 | 6544.1136 | 6558.6286 | 6662.7214 | 6876.3204 | 7260.9121 | 7465.4571 | 7615.1702 | 7844.4702 | 8141.8786 | 8508.3166 | 8703.2608 | 8639.8468 | 8702.7004 | 8702.7004 | 8702.7004 | 8702.7004 | 8702.7004 | 8702.7004 | 8702.7004 | 8702.7004 | 8702.7004 | 8702.7004 | 8702.7004 | 8702.7004 | 8702.7004 | 8702.7004 | 8702.7004
Option 8 Summer POE50 W E @ R (MWh) N 2 | 14057.7026 | 17533.8936 | 17891.3617 | 17715.9672 | 17882.7327 | 17951.3399 | 18171.5567 | 18625.9536 | 19009.8293 | 19187.0204 | 19029.0769 | 19692.7018 | 19798.2933 | 19673.3426 | 19924.0258 | 20041.4511 | 20041.4511 | 20041.4511 | 20041.4511 | 20041.4511 | 20041.4511 | 20041.4511 | 20041.4511 | 20041.4511 | 20041.4511 | 20041.4511 | 20041.4511 | 20041.4511 | 20041.4511 | 20041.4511 | Option 8 Summer POE10 W E @ R (MWh) N 2 | 1437.2846 | 1964.4609 | 1980.1951 | 1963.2341 | 1967.5886 | 1998.8164 | 2062.8961 | 2178.2736 | 2239.6371 | 2284.5511 | 2353.341 | 2442.5636 | 2552.495 | 2610.9782 | 2591.954 | 2610.8101 | 2610.8101 | 2610.8101 | 2610.8101 | 2610.8101 | 2610.8101 | 2610.8101 | 2610.8101 | 2610.8101 | 2610.8101 | 2610.8101 | 2610.8101 | 2610.8101 | 2610.8101 | 2610.8101