## Info
Document description
This model Energy at Risk model has been developed to calculated Energy at Risk (EaR) in terms of Expected Unsureved Energy (EUE) and the cost of EUE. The modelling inputs, calculation steps and outputs are described in the 'Modelling Steps' tab. Further detail on EaR/EUE calculations can be found in AusNet's Network Planning Policy and Guidelines.
Tab # | Tab Name | Description | Source/ Inputs
0.1 | Modelling Steps | E@R model process flowchart and underlying equations | N/A
0.2 | Modelling Example & QA | Example E@R model calculations and data flow; also used to validate base case | N/A
0.3 | QA | Quality assurance and data validation | Entire workbook
1.1 | Output for AusNet's NPV Model | Aggregates Supply Risk ($M) and EUE (MWh) for input into AusNet’s NPV model | Summary tab
2.1 | Key Model Assumptions & Inputs | E@R model inputs and asset selection | Augmentation plans from RPs/EPCs, Embedded Generation DB, Demand Management DB
2.2 | Tx PoF | Transformer Probabilities of Failure | Provided by Asset Management Team
2.3 | Customer No. and Volume per Feeder | Customer consumption data | Provided by Finance Team
2.4 | AER VCR Rates (2024) | AER 2024 VCR rates | AER VCR Factsheet
2.5 | Forecast - Summer | Summer Forecast Data | Extract from Forecasting Toolbox
2.6 | Forecast- Winter | Winter Forecast Data | Extract from Forecasting Toolbox
2.7 | Ratings | Station Rating Data | AMS 20-101 / Provided by Asset mangement Team
2.8 | FT (Forecast & Transfers) | Forecast, transfer & PF inputs | Forecast Summer , Forecast Winter , NP Transfer Sheet, PF = avg. max demand PF across stations
2.9 | Load Duration Curves | Load duration curve data | LDC Tool; data sourced from PI SCADA Historian and AEMO
3.1 | Capacity N | Option N capacity calculated | FT Sheet, Ratings & Key Model Assumptions
3.2 | Capacity N-1 | Option N-1 capacity calculated | FT Sheet, Ratings & Key Model Assumptions
3.3 | Capacity N-1 | Option N-2 capacity calculated | FT Sheet, Ratings & Key Model Assumptions
3.4 | Demand | Calculates maximum demand | FT Sheet & Key Model Assumptions
3.5 | MD Weighted LDC | Maps maximum demand forecast to load duration curve | Demand Sheet & Load Duration Curve Sheet
3.6 | Locational VCR | Calculates tailored VCR by location using feeder energy mix and AER rates | AER VCR Rates (2024) & Customer No./Volume per Feeder
3.7 | E@R N | Calculates N EUE using capacity and demand inputs | MD Weighted LDC & Capacity N
3.8 | E@R N-1 | Calculates N-1 EUE using capacity and demand inputs | MD Weighted LDC & Capacity N-1
3.9 | E@R N-2 | Calculates N-2 EUE using capacity and demand inputs | MD Weighted LDC & Capacity N-2
4 | POF N,N-1 & N-2 Risk | Calculates Station N , N-1 & N-2 PoF's from Tx PoF Data & MTTR | TX PoF & Key Model Assumptions
4.1 | Summary | Collates weighted EUE and calculates supply risk | E@R & Locational VCR
Revision table
Date | Editted by | Change
2025-10-14 | HT | Draft Version 2.1
2025-10-20 | HT | Version 2.2
2025-11-10 | HT | Version 2.3 Example Page Update and General Refinements

## Modelling Steps
Eq1. Locational VCR |  | Data Inputs |  |  | Calculations |  |  |  |  | Outputs
|  |  | Customer No. and Vol per Feeder |  | Eq1.
Locational VCR
Eq2. Maximum Demand
AER Latetst VCR Rates
Eq3. Options & Do nothing Capacity
Eq6. & Eq7.
Load Forecast
[9 empty] | Summary Sheet | Output for AusNet's NPV Model
Eq4. Help Sheet | Re Name Forecasted LDC add Forecast MD to eq
Transfer Capacity
Eq2.
Eq5. Energy at Risk ( Option/ Do Nothing Capacity) |  |  |  |  | Options & Do Nothing Max Demand
Embeded Generation
Eq6. Weighted Expected Unserved Energy
[6 empty] | Eq.4 | Eq.5
Demand Mangement Capacity
[6 empty] | Forecasted LDC |  | Energy @ Risk Sheet
Eq7. Supply Risk
Load Duration Curves
|  |  | Asset Ratings |  | Eq3.
Options & Do Nothing Capacity
Planned & Proposed Works

## Modelling Steps Example & QA
End of Sheet
Data Inputs |  |  | Calculations | [12 empty] | Outputs
AER VCR Rates(2024 |  |  | Locational (Tailored VCR)
Category | Rate |  | Base case |  | Energy Usage (CY 2024 kWh) | Energy Usage (CY 2024 %) | Tailored VCR
Dec 24 AER VCR ($/kWh) - Res | 49.23 |  | Dec 24 AER VCR ($/kWh) - Res | 49.23 | 88661416.1819 | 59.86% | 29.4686
Dec 24 AER VCR ($/kWh) - Com | 34.39 |  | Dec 24 AER VCR ($/kWh) - Com | 34.39 | 45585213.1364 | 30.78% | 10.584
Dec 24 AER VCR ($/kWh) - Ind | 33.49 |  | Dec 24 AER VCR ($/kWh) - Ind | 33.49 | 5851096.6819 | 3.95% | 1.323
Dec 24 AER VCR ($/kWh) - Agr | 22.25 |  | Dec 24 AER VCR ($/kWh) - Agr | 22.25 | 8019086.0298 | 5.414% | 1.2046
[5 empty] | 148116812.03 |  | 42.5803
Customer No. and Vol per Feeder | [6 empty] | 42580.277 | [8 empty] | Summary |  | Outputs for NPV model
COMMERCIAL | 45585213.1364 | [14 empty] | Year | 2031 | Year | 2031
[16 empty] | E@R MWh | 45.4503 | E@R MWh | 45.4503
RESIDENTL | 88661416.1819 | [14 empty] | cost of EUE ($) | 1935286.2231 | cost of EUE ($M) | 1.9353
FARM | 8019086.0298
INDUSTRIAL | 5851096.6819
Forecast (FCT)
Forecast | 2031
Summer POE50 | 45.1615
Summer POE10 | 55.0965
Winter POE50 | 47.2137
Winter POE10 | 50.5469
Transfer Capacity |  |  | Option Max Demand |  |  |  | MD Weighted LDC |  |  | E@R (N) |  | E@R (N-1) |  | E@R (N-2)
Year | 2031 |  | Forecast | 2031 |  |  | % of MD | Summer - AD - Hours | FY31 | % of MD | FY31 | % of MD | FY31 | % of MD | FY31
Capacity | 0 |  | Summer POE50 | 45.0515 |  |  | 100% | 0 | 45.0515 | 100% |  | 100% |  | 100%
|  |  | Summer POE10 | 54.9865 |  |  | 99% | 0.37816 | 44.601 | 99% |  | 99% | 3.6025 | 99% | 10.2771
Embedded Generation |  |  | Winter POE50 | 47.1037 |  |  | 98% | 0.37816 | 44.1505 | 98% |  | 98% | 0 | 98% | 0
|  |  | Winter POE10 | 50.4369 |  |  | 97% | 0.37816 | 43.7 | 97% |  | 97% | 0 | 97% | 0
Year | 2031 | [5 empty] | 95% | 0.75633 | 42.7989 | 95% |  | 95% | 3.0062 | 95% | 9.6808
Capacity | 0.11 | [5 empty] | 90% | 9.0759 | 40.5464 | 90% |  | 90% | 53.0179 | 90% | 199.8591
[7 empty] | 85% | 40.4636 | 38.2938 | 85% |  | 85% | 129.3191 | 85% | 683.3108
Demand Mangement | [6 empty] | 80% | 94.5411 | 36.0412 | 80% |  | 80% | 100.9891 | 80% | 1055.4569
[7 empty] | 75% | 197.0236 | 33.7886 | 75% |  | 75% | 12.4972 | 75% | 1769.3519
Year | 2031 | [5 empty] | 70% | 336.9444 | 31.5361 | 70% |  | 70% |  | 70% | 2100.5382
Capacity | 0 | [5 empty] | 65% | 521.4885 | 29.2835 | 65% |  | 65% |  | 65% | 2354.74
[7 empty] | 60% | 812.675 | 27.0309 | 60% |  | 60% |  | 60% | 3059.5514
LDC | [6 empty] | 55% | 1202.1843 | 24.7783 | 55% |  | 55% |  | 55% | 3215.248
[7 empty] | 50% | 1686.2345 | 22.5258 | 50% |  | 50% |  | 50% | 2905.2884
% of MD | Summer - AD - Duration % | Summer - AD - Hours |  |  |  |  | 45% | 2129.0649 | 20.2732 | 45% |  | 45% |  | 45% | 1660.3762
100% | 0% | 0 |  |  |  |  | 40% | 2484.5393 | 18.0206 | 40% |  | 40% |  | 40% | 532.1055
99% | 0.00861% | 0.37816 |  |  |  |  | 35% | 2808.248 | 15.768 | 35% |  | 35% |  | 35% | 9.8686
98% | 0.00861% | 0.37816 |  |  |  |  | 30% | 3095.6528 | 13.5155 | 30% |  | 30% |  | 30%
97% | 0.00861% | 0.37816 |  |  |  |  | 25% | 3358.8552 | 11.2629 | 25% |  | 25% |  | 25%
95% | 0.01722% | 0.75633 |  |  |  |  | 20% | 3588.7791 | 9.0103 | 20% |  | 20% |  | 20%
90% | 0.2066% | 9.0759 |  |  |  |  | 15% | 3802.4419 | 6.7577 | 15% |  | 15% |  | 15%
85% | 0.9213% | 40.4636 |  |  |  |  | 10% | 4024.8025 | 4.5052 | 10% |  | 10% |  | 10%
80% | 2.153% | 94.5411 |  |  |  |  | 5% | 4239.978 | 2.2526 | 5% |  | 5% |  | 5%
75% | 4.486% | 197.0236 |  |  |  |  | 9.992e-14% | 4391.6218 | 4.5015e-14 | 9.992e-14% |  | 9.992e-14% |  | 9.992e-14%
70% | 7.672% | 336.9444 | [7 empty] | Total E@R | 0 | Total E@R | 299.4076 | Total E@R | 19369.9964
65% | 11.87% | 521.4885 | [7 empty] | Total WE@R | 0 | Total WE@R | 7.7547 | Total WE@R | 6.8672
60% | 18.5% | 812.675 |  |  |  |  | MD Weighted LDC
55% | 27.37% | 1202.1843
50% | 38.39% | 1686.2345 |  |  |  |  | % of MD | Summer - MD - Hours | FY31
45% | 48.48% | 2129.0649 |  |  |  |  | 100% | 0 | 54.9865 | E@R (N) |  | E@R (N) |  | E@R (N-2)
40% | 56.57% | 2484.5393 |  |  |  |  | 99% | 0 | 54.4366
35% | 63.94% | 2808.248 |  |  |  |  | 98% | 0 | 53.8867 | % of MD | FY31 | % of MD | FY31 | % of MD | FY31
30% | 70.48% | 3095.6528 |  |  |  |  | 97% | 0.37816 | 53.3369 | 100% |  | 100% |  | 100%
25% | 76.48% | 3358.8552 |  |  |  |  | 95% | 0.37816 | 52.2371 | 99% |  | 99% | 0 | 99% | 0
20% | 81.71% | 3588.7791 |  |  |  |  | 90% | 0.75633 | 49.4878 | 98% |  | 98% | 0 | 98% | 0
15% | 86.58% | 3802.4419 |  |  |  |  | 85% | 1.1345 | 46.7385 | 97% |  | 97% | 6.9249 | 97% | 13.5995
10% | 91.64% | 4024.8025 |  |  |  |  | 80% | 2.6471 | 43.9892 | 95% |  | 95% | 0 | 95% | 0
5% | 96.54% | 4239.978 |  |  |  |  | 75% | 3.4035 | 41.2398 | 90% |  | 90% | 5.8852 | 90% | 12.5598
9.992e-14% | 99.99% | 4391.6218 |  |  |  |  | 70% | 5.6725 | 38.4905 | 85% |  | 85% | 4.8455 | 85% | 11.5201
[7 empty] | 65% | 6.4288 | 35.7412 | 80% |  | 80% | 15.2231 | 80% | 41.9215
[7 empty] | 60% | 11.3449 | 32.9919 | 75% |  | 75% | 5.5322 | 75% | 18.8814
[7 empty] | 55% | 35.5474 | 30.2426 | 70% |  | 70% | 10.3583 | 70% | 50.4059
LDC | [6 empty] | 50% | 95.2974 | 27.4932 | 65% |  | 65% | 1.3734 | 65% | 14.7226
[7 empty] | 45% | 208.7467 | 24.7439 | 60% |  | 60% | 0.17404 | 60% | 82.1808
% of MD | Summer - MD - Duration % | Summer - MD - Hours |  |  |  |  | 40% | 380.4333 | 21.9946 | 55% |  | 55% |  | 55% | 338.0417
100% | 0% | 0 |  |  |  |  | 35% | 696.5786 | 19.2453 | 50% |  | 50% |  | 50% | 670.2686
99% | 0% | 0 |  |  |  |  | 30% | 1260.7997 | 16.4959 | 45% |  | 45% |  | 45% | 960.7531
98% | 0% | 0 |  |  |  |  | 25% | 1965.3198 | 13.7466 | 40% |  | 40% |  | 40% | 981.9179
97% | 0.00861% | 0.37816 |  |  |  |  | 20% | 2490.2118 | 10.9973 | 35% |  | 35% |  | 35% | 938.9274
95% | 0.00861% | 0.37816 |  |  |  |  | 15% | 2997.7083 | 8.248 | 30% |  | 30% |  | 30% | 261.1304
90% | 0.01722% | 0.75633 |  |  |  |  | 10% | 3491.5908 | 5.4986 | 25% |  | 25% |  | 25%
85% | 0.02583% | 1.1345 |  |  |  |  | 5% | 3955.9766 | 2.7493 | 20% |  | 20% |  | 20%
80% | 0.06027% | 2.6471 |  |  |  |  | 9.992e-14% | 4391.6218 | 5.4943e-14 | 15% |  | 15% |  | 15%
75% | 0.07749% | 3.4035 | [7 empty] | 10% |  | 10% |  | 10%
70% | 0.1292% | 5.6725 | [7 empty] | 5% |  | 5% |  | 5%
65% | 0.1464% | 6.4288 | [7 empty] | 9.992e-14% |  | 9.992e-14% |  | 9.992e-14%
60% | 0.2583% | 11.3449 | [7 empty] | Total E@R | 0 | Total E@R | 49.8134 | Total E@R | 4352.8623
55% | 0.8094% | 35.5474 |  |  |  |  | MD Weighted LDC |  |  | Total WE@R | 0 | Total WE@R | 0.55293 | Total WE@R | 0.66138
50% | 2.17% | 95.2974
45% | 4.753% | 208.7467 |  |  |  |  | % of MD | Winter - AD - Hours | FY31
40% | 8.662% | 380.4333 |  |  |  |  | 100% | 0 | 47.1037
35% | 15.86% | 696.5786 |  |  |  |  | 99% | 0.2972 | 46.6326 | E@R (N) |  | E@R (N-1) |  | E@R (N-2)
30% | 28.71% | 1260.7997 |  |  |  |  | 98% | 0.2972 | 46.1616
25% | 44.75% | 1965.3198 |  |  |  |  | 97% | 0.2972 | 45.6906 | % of MD | FY31 | % of MD | FY31 | % of MD | FY31
20% | 56.7% | 2490.2118 |  |  |  |  | 95% | 1.486 | 44.7485 | 100% |  | 100% |  | 100%
15% | 68.25% | 2997.7083 |  |  |  |  | 90% | 8.6188 | 42.3933 | 99% |  | 99% | 3.2003 | 99% | 8.5647
10% | 79.5% | 3491.5908 |  |  |  |  | 85% | 40.1218 | 40.0381 | 98% |  | 98% | 0 | 98% | 0
5% | 90.07% | 3955.9766 |  |  |  |  | 80% | 93.0231 | 37.6829 | 97% |  | 97% | 0 | 97% | 0
9.992e-14% | 99.99% | 4391.6218 |  |  |  |  | 75% | 197.0426 | 35.3278 | 95% |  | 95% | 10.8412 | 95% | 32.299
[7 empty] | 70% | 378.0365 | 32.9726 | 90% |  | 90% | 53.2881 | 90% | 182.0345
[7 empty] | 65% | 616.0926 | 30.6174 | 85% |  | 85% | 161.1605 | 85% | 729.7905
[7 empty] | 60% | 934.9866 | 28.2622 | 80% |  | 80% | 146.0357 | 80% | 1100.9048
LDC | [6 empty] | 55% | 1310.9428 | 25.907 | 75% |  | 75% | 55.3334 | 75% | 1919.7155
[7 empty] | 50% | 1730.2899 | 23.5518 | 70% |  | 70% |  | 70% | 2914.0312
% of MD | Winter - AD (P50) - Duration % | Winter - AD - Hours |  |  |  |  | 45% | 2168.0633 | 21.1967 | 65% |  | 65% |  | 65% | 3272.0749
100% | 0% | 0 |  |  |  |  | 40% | 2609.7004 | 18.8415 | 60% |  | 60% |  | 60% | 3632.1374
99% | 0.006767% | 0.2972 |  |  |  |  | 35% | 2998.1389 | 16.4863 | 55% |  | 55% |  | 55% | 3396.6175
98% | 0.006767% | 0.2972 |  |  |  |  | 30% | 3309.3057 | 14.1311 | 50% |  | 50% |  | 50% | 2800.9987
97% | 0.006767% | 0.2972 |  |  |  |  | 25% | 3537.8514 | 11.7759 | 45% |  | 45% |  | 45% | 1893.0391
95% | 0.03383% | 1.486 |  |  |  |  | 20% | 3731.0305 | 9.4207 | 40% |  | 40% |  | 40% | 869.6099
90% | 0.1962% | 8.6188 |  |  |  |  | 15% | 3910.2412 | 7.0656 | 35% |  | 35% |  | 35% | 51.6577
85% | 0.9135% | 40.1218 |  |  |  |  | 10% | 4075.1864 | 4.7104 | 30% |  | 30% |  | 30%
80% | 2.118% | 93.0231 |  |  |  |  | 5% | 4251.7223 | 2.3552 | 25% |  | 25% |  | 25%
75% | 4.486% | 197.0426 |  |  |  |  | 9.992e-14% | 4391.7028 | 4.7066e-14 | 20% |  | 20% |  | 20%
70% | 8.607% | 378.0365 | [7 empty] | 15% |  | 15% |  | 15%
65% | 14.03% | 616.0926 | [7 empty] | 10% |  | 10% |  | 10%
60% | 21.29% | 934.9866 | [7 empty] | 5% |  | 5% |  | 5%
55% | 29.85% | 1310.9428 | [7 empty] | 9.992e-14% |  | 9.992e-14% |  | 9.992e-14%
50% | 39.4% | 1730.2899 |  |  |  |  | MD Weighted LDC |  |  | Total E@R | 0 | Total E@R | 425.5606 | Total E@R | 22575.4407
45% | 49.36% | 2168.0633 | [7 empty] | Total WE@R | 0 | Total WE@R | 9.3646 | Total WE@R | 6.8001
40% | 59.42% | 2609.7004 |  |  |  |  | % of MD | Winter - MD - Hours | FY31
35% | 68.26% | 2998.1389 |  |  |  |  | 100% | 0 | 50.4369 | E@R (N) |  | E@R (N-1) |  | E@R (N-2)
30% | 75.35% | 3309.3057 |  |  |  |  | 99% | 0.2972 | 49.9326
25% | 80.55% | 3537.8514 |  |  |  |  | 98% | 0.2972 | 49.4282 | % of MD | FY31 | % of MD | FY31 | % of MD | FY31
20% | 84.95% | 3731.0305 |  |  |  |  | 97% | 0.2972 | 48.9238 | 100% |  | 100% |  | 100%
15% | 89.03% | 3910.2412 |  |  |  |  | 95% | 1.486 | 47.9151 | 99% |  | 99% | 4.186 | 99% | 9.5504
10% | 92.79% | 4075.1864 |  |  |  |  | 90% | 8.6188 | 45.3932 | 98% |  | 98% | 0 | 98% | 0
5% | 96.81% | 4251.7223 |  |  |  |  | 85% | 40.1218 | 42.8714 | 97% |  | 97% | 0 | 97% | 0
9.992e-14% | 99.99% | 4391.7028 |  |  |  |  | 80% | 93.0231 | 40.3495 | 95% |  | 95% | 14.6453 | 95% | 36.103
[7 empty] | 75% | 197.0426 | 37.8277 | 90% |  | 90% | 75.2803 | 90% | 204.0267
[7 empty] | 70% | 378.0365 | 35.3059 | 85% |  | 85% | 253.0423 | 85% | 821.6723
[7 empty] | 65% | 616.0926 | 32.784 | 80% |  | 80% | 291.511 | 80% | 1246.3802
LDC | [6 empty] | 60% | 934.9866 | 30.2622 | 75% |  | 75% | 310.8747 | 75% | 2188.4265
[7 empty] | 55% | 1310.9428 | 27.7403 | 70% |  | 70% | 107.115 | 70% | 3351.4232
% of MD | Winter - MD (P10) - Duration % | Winter - MD - Hours |  |  |  |  | 50% | 1730.2899 | 25.2185 | 65% |  | 65% |  | 65% | 3807.6888
100% | 0% | 0 |  |  |  |  | 45% | 2168.0633 | 22.6966 | 60% |  | 60% |  | 60% | 4296.485
99% | 0.006767% | 0.2972 |  |  |  |  | 40% | 2609.7004 | 20.1748 | 55% |  | 55% |  | 55% | 4117.1838
98% | 0.006767% | 0.2972 |  |  |  |  | 35% | 2998.1389 | 17.6529 | 50% |  | 50% |  | 50% | 3534.8396
97% | 0.006767% | 0.2972 |  |  |  |  | 30% | 3309.3057 | 15.1311 | 45% |  | 45% |  | 45% | 2586.1647
95% | 0.03383% | 1.486 |  |  |  |  | 25% | 3537.8514 | 12.6092 | 40% |  | 40% |  | 40% | 1495.2482
90% | 0.1962% | 8.6188 |  |  |  |  | 20% | 3731.0305 | 10.0874 | 35% |  | 35% |  | 35% | 347.6947
85% | 0.9135% | 40.1218 |  |  |  |  | 15% | 3910.2412 | 7.5655 | 30% |  | 30% |  | 30%
80% | 2.118% | 93.0231 |  |  |  |  | 10% | 4075.1864 | 5.0437 | 25% |  | 25% |  | 25%
75% | 4.486% | 197.0426 |  |  |  |  | 5% | 4251.7223 | 2.5218 | 20% |  | 20% |  | 20%
70% | 8.607% | 378.0365 |  |  |  |  | 9.992e-14% | 4391.7028 | 5.0397e-14 | 15% |  | 15% |  | 15%
65% | 14.03% | 616.0926 | [7 empty] | 10% |  | 10% |  | 10%
60% | 21.29% | 934.9866 | [7 empty] | 5% |  | 5% |  | 5%
55% | 29.85% | 1310.9428 | [7 empty] | 9.992e-14% |  | 9.992e-14% |  | 9.992e-14%
50% | 39.4% | 1730.2899 | [7 empty] | Total E@R | 0 | Total E@R | 1046.0881 | Total E@R | 27762.4582
45% | 49.36% | 2168.0633 | [7 empty] | Total WE@R | 0 | Total WE@R | 9.8655 | Total WE@R | 3.5839
40% | 59.42% | 2609.7004
35% | 68.26% | 2998.1389
30% | 75.35% | 3309.3057
25% | 80.55% | 3537.8514
20% | 84.95% | 3731.0305
15% | 89.03% | 3910.2412
10% | 92.79% | 4075.1864
5% | 96.81% | 4251.7223
9.992e-14% | 99.99% | 4391.7028
Ratings (MVA) |  |  |  | Option Capacity
SCR (N) | 55.8 |  |  | Year | 2031
SCR (N-1) | 35.3 |  |  | SCR (N) | 55.8
SCR (N-2) | 17.65 |  |  | SCR (N-1) | 35.3
WCR (N) | 56.8 |  |  | SCR (N-2) | 17.65
WCR (N-1) | 36.1 |  |  | WCR (N) | 56.8
WCR (N-2) | 18.05 |  |  | WCR (N-1) | 36.1
|  |  |  | WCR (N-2) | 18.05
Planned Works
Year | 2031
Capacity (N) | 0
Capacity (N-1) | 0
Capacity (N-2) | 0
Power Factor
Value | 0.99
End of Sheet

## QA
Overall Status
Good
Number | Check Name | Status | Info
1 | Forecast | Good | Confirms POE10 forecast is higher than POE50
2 | Option Maximum Demand | Good | Confirms whether transfers, embedded generation, and demand management contribute to demand reduction when present
3 | EUE Base Case | Good | Confirms Do Nothing/Base Case EUE for FY31 is the same as the example / checks model in Modelling Steps Example Sheet
4 | Feeder Consumption | Good | Confirms if aggregated feeder energy consumption by customer category matches with total feeder energy consumption (excluding uncategorised consumption)

## Output for AusNet's NPV model
Involuntary load shedding (NER 5.17.1(c)(4)(ii))
Base Case
Cost
Option 1 - Do Nothing | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Cost of EUE ($M) | 0.39479 | 0.85843 | 1.001 | 1.1834 | 1.3378 | 1.5314 | 1.9353 | 3.208 | 4.2027 | 3.8197 | 6.3014 | 6.6596 | 7.6867 | 9.8238 | 10.482 | 10.5134 | 10.5134 | 10.5134 | 10.5134 | 10.5134 | 10.5134 | 10.5134 | 10.5134 | 10.5134 | 10.5134 | 10.5134 | 10.5134 | 10.5134 | 10.5134 | 10.5134
Total EUE (MWh) | 9.2716 | 20.1604 | 23.5084 | 27.7911 | 31.4188 | 35.9641 | 45.4503 | 75.3394 | 98.6997 | 89.7066 | 147.9896 | 156.401 | 180.5228 | 230.7123 | 246.1711 | 246.9075 | 246.9075 | 246.9075 | 246.9075 | 246.9075 | 246.9075 | 246.9075 | 246.9075 | 246.9075 | 246.9075 | 246.9075 | 246.9075 | 246.9075 | 246.9075 | 246.9075
Residual Values
Option 2 - Replace 3 x 10/13.5 MVA Tx with 3 x 20/33 MVA Tx | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Cost of Avoided EUE ($M) | 0.39467 | 0.85843 | 1.001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total EUE (MWh) | 9.2689 | 20.1604 | 23.5084 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 - Replace 1 x 10/13.5 MVA Tx with 1 x 20/33 MVA Tx | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Cost of Avoided EUE ($M) | 0.39467 | 0.85843 | 1.001 | 0.020015 | 0.0236 | 0.028253 | 0.037842 | 0.067359 | 0.092732 | 0.085664 | 0.15595 | 0.16578 | 0.20349 | 0.28897 | 0.3171 | 0.31798 | 0.31798 | 0.31798 | 0.31798 | 0.31798 | 0.31798 | 0.31798 | 0.31798 | 0.31798 | 0.31798 | 0.31798 | 0.31798 | 0.31798 | 0.31798 | 0.31798
Total EUE (MWh) | 9.2689 | 20.1604 | 23.5084 | 0.47005 | 0.55425 | 0.66352 | 0.88873 | 1.5819 | 2.1778 | 2.0118 | 3.6626 | 3.8932 | 4.779 | 6.7865 | 7.447 | 7.4677 | 7.4677 | 7.4677 | 7.4677 | 7.4677 | 7.4677 | 7.4677 | 7.4677 | 7.4677 | 7.4677 | 7.4677 | 7.4677 | 7.4677 | 7.4677 | 7.4677
Option 4 - Construct 2x 20/33MVA zone substation in Inverloch | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Cost of Avoided EUE ($M) | 0.39467 | 0.85843 | 1.001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total EUE (MWh) | 9.2689 | 20.1604 | 23.5084 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 - Contract network support services to defer network investment | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Cost of Avoided EUE ($M) | 0.19807 | 0.33438 | 0.39081 | 0.46869 | 0.53187 | 0.61312 | 0.7784 | 1.3521 | 1.846 | 1.6267 | 2.9904 | 3.1092 | 3.6818 | 4.9892 | 5.3629 | 5.3754 | 5.3754 | 5.3754 | 5.3754 | 5.3754 | 5.3754 | 5.3754 | 5.3754 | 5.3754 | 5.3754 | 5.3754 | 5.3754 | 5.3754 | 5.3754 | 5.3754
Total EUE (MWh) | 4.6517 | 7.853 | 9.1782 | 11.0071 | 12.4909 | 14.3991 | 18.2808 | 31.7536 | 43.3527 | 38.2027 | 70.2291 | 73.0196 | 86.4684 | 117.1724 | 125.9471 | 126.2407 | 126.2407 | 126.2407 | 126.2407 | 126.2407 | 126.2407 | 126.2407 | 126.2407 | 126.2407 | 126.2407 | 126.2407 | 126.2407 | 126.2407 | 126.2407 | 126.2407
Option 6 - | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Cost of Avoided EUE ($M) | 0.39467 | 0.85843 | 1.001 | 1.1834 | 1.3378 | 1.5314 | 1.9353 | 3.208 | 4.2027 | 3.8197 | 6.3014 | 6.6596 | 7.6867 | 9.8238 | 10.482 | 10.5134 | 10.5134 | 10.5134 | 10.5134 | 10.5134 | 10.5134 | 10.5134 | 10.5134 | 10.5134 | 10.5134 | 10.5134 | 10.5134 | 10.5134 | 10.5134 | 10.5134
Total EUE (MWh) | 9.2689 | 20.1604 | 23.5084 | 27.7911 | 31.4188 | 35.9641 | 45.4503 | 75.3394 | 98.6997 | 89.7066 | 147.9896 | 156.401 | 180.5228 | 230.7123 | 246.1711 | 246.9075 | 246.9075 | 246.9075 | 246.9075 | 246.9075 | 246.9075 | 246.9075 | 246.9075 | 246.9075 | 246.9075 | 246.9075 | 246.9075 | 246.9075 | 246.9075 | 246.9075
Option 7 - | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Cost of Avoided EUE ($M) | 0.39467 | 0.85843 | 1.001 | 1.1834 | 1.3378 | 1.5314 | 1.9353 | 3.208 | 4.2027 | 3.8197 | 6.3014 | 6.6596 | 7.6867 | 9.8238 | 10.482 | 10.5134 | 10.5134 | 10.5134 | 10.5134 | 10.5134 | 10.5134 | 10.5134 | 10.5134 | 10.5134 | 10.5134 | 10.5134 | 10.5134 | 10.5134 | 10.5134 | 10.5134
Total EUE (MWh) | 9.2689 | 20.1604 | 23.5084 | 27.7911 | 31.4188 | 35.9641 | 45.4503 | 75.3394 | 98.6997 | 89.7066 | 147.9896 | 156.401 | 180.5228 | 230.7123 | 246.1711 | 246.9075 | 246.9075 | 246.9075 | 246.9075 | 246.9075 | 246.9075 | 246.9075 | 246.9075 | 246.9075 | 246.9075 | 246.9075 | 246.9075 | 246.9075 | 246.9075 | 246.9075
Option 8 - | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Cost of Avoided EUE ($M) | 0.39467 | 0.85843 | 1.001 | 1.1834 | 1.3378 | 1.5314 | 1.9353 | 3.208 | 4.2027 | 3.8197 | 6.3014 | 6.6596 | 7.6867 | 9.8238 | 10.482 | 10.5134 | 10.5134 | 10.5134 | 10.5134 | 10.5134 | 10.5134 | 10.5134 | 10.5134 | 10.5134 | 10.5134 | 10.5134 | 10.5134 | 10.5134 | 10.5134 | 10.5134
Total EUE (MWh) | 9.2689 | 20.1604 | 23.5084 | 27.7911 | 31.4188 | 35.9641 | 45.4503 | 75.3394 | 98.6997 | 89.7066 | 147.9896 | 156.401 | 180.5228 | 230.7123 | 246.1711 | 246.9075 | 246.9075 | 246.9075 | 246.9075 | 246.9075 | 246.9075 | 246.9075 | 246.9075 | 246.9075 | 246.9075 | 246.9075 | 246.9075 | 246.9075 | 246.9075 | 246.9075

## Key Model Assumption & Inputs
Select ZSS & Region | WGI | East | MTTR
Probability Weighting for 10% POE MDs | 30% |  |  | Central | North | East | For Analysis
Probability Weighting for 50% POE MDs | 70% |  | N-1 MTTR (years) | 0.3858 | 0.1418 | 0.3858 | 0.3858
First year of analysis | FY25 |  | N-2 MTTR (years) | 0.2344 | 0.049 | 0.2344 | 0.2344
Select Sensitivity Variant | Forecast Sensitivity
Base | 100% |  | PV Factor's |  |  | PoF Sensitvity
Options | Name |  | Summer | 1.33 |  | Varaint
Option 1 - Do Nothing | Do Nothing |  | Winter | 1.13 |  | High | 150%
Option 2 - Replace 3 x 10/13.5 MVA Tx with 3 x 20/33 MVA Tx | Replace 3 x 10/13.5 MVA Tx with 3 x 20/33 MVA Tx
Option 3 - Replace 1 x 10/13.5 MVA Tx with 1 x 20/33 MVA Tx | Replace 1 x 10/13.5 MVA Tx with 1 x 20/33 MVA Tx |  | Demand Response
Option 4 - Construct 2x 20/33MVA zone substation in Inverloch | Construct 2x 20/33MVA zone substation in Inverloch |  | Average Rate % | 20%
Option 5 - Contract network support services to defer network investment | Contract network support services to defer network investment
Option 6 -
Option 7 -
Option 8 -
Added Capacity (MVA) | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39
Added Capacity (MVA) Option 1 N | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 1 N-1 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 1 N-2 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 2 N |  |  |  | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2
Added Capacity (MVA) Option 2 N-1 |  |  |  | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2
Added Capacity (MVA) Option 2 N-2 |  |  |  | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2
Added Capacity (MVA) Option 3 N |  |  |  | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35
Added Capacity (MVA) Option 3 N-1 |  |  |  | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35
Added Capacity (MVA) Option 3 N-2 |  |  |  | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35
Added Capacity (MVA) Option 4 N | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 4 N-1 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 4 N-2 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 5 N | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 5 N-1 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 5 N-2 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 6 N | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 6 N-1 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 6 N-2 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 7 N | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 7 N-1 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 7 N-2 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 8 N | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 8 N-1 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 8 N-2 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Embedded Generation (MVA) | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39
Avaliable Embedded Generation (MVA) Option 1 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11
Added Embedded Generation (MVA) Option 2 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Embedded Generation (MVA) Option 3 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Embedded Generation (MVA) Option 4 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Embedded Generation (MVA) Option 5 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Embedded Generation (MVA) Option 6 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Embedded Generation (MVA) Option 7 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Embedded Generation (MVA) Option 8 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Demand Management (MVA) | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39
Avaliable Demand Management (MVA) Option 1 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Demand Management (MVA) Option 2 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Demand Management (MVA) Option 3 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Demand Management (MVA) Option 4 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Demand Management (MVA) Option 5 | 4.0981 | 4.3758 | 4.3835 | 4.3752 | 4.3773 | 4.3925 | 4.4232 | 4.4774 | 4.5056 | 4.526 | 4.5569 | 4.5963 | 4.644 | 4.6689 | 4.6608
Added Demand Management (MVA) Option 6 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Demand Management (MVA) Option 7 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Demand Management (MVA) Option 8 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Transfers (MVA) | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39
Planned Transfers (MVA) Option 1 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Transfers (MVA) Option 2 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Transfers (MVA) Option 3 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Transfers (MVA) Option 4 |  |  |  | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66
Added Transfers (MVA) Option 5 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Transfers (MVA) Option 6 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Transfers (MVA) Option 7 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Transfers (MVA) Option 8 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Block Loads Not in Forecast (MVA) | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39
Block Loads (MVA) | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Base | FY25: 100%
High | FY25: 110%
Low | FY25: 90%

## Tx PoF
Transformer Failure Rates for individual Transformers
[5 empty] | 10 | 8 | 10 | 6 | 8 | 6 | 6 | 10 | 6
Zone | arm_asset_id | floc | user_status | Age | Major Winding insulation | Accelerated cellulose Aging | Winding insulating liquid | Hot metal fault covered by paper | Chemical contamination, degradation | Physical & chemical contamination, degradation | Physical contamination | Short Circuit Concern | OLTC | WMA Health Score | WMA CS | WMA effective age | WMA Beta | WMA Eta | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WGI | 30192717 | DS-WGI-TRNFMR-9000004493 |  | 59 | 5 | 3 | 1 | 5 | 2 | 1 | 5 | 5 | 5 | 351.4286 | 4 | 60 | 3.5 | 82 | 1.976% | 1.976% | 2.058% | 2.142% | 2.227% | 2.315% | 2.405% | 2.496% | 2.59% | 2.686% | 2.783% | 2.883% | 2.985% | 3.089% | 3.195% | 3.303% | 3.413% | 3.525% | 3.639% | 3.755% | 3.873% | 3.994% | 4.116% | 4.241% | 4.368% | 4.497% | 4.628% | 4.761% | 4.897% | 5.034%
WGI | 30111322 | DS-WGI-TRNFMR-9000003147 |  | 59 | 5 | 5 | 1 | 3 | 2 | 1 | 4 | 5 | 5 | 348.5714 | 3 | 44 | 3.5 | 82 | 0.9218% | 0.9218% | 0.9742% | 1.028% | 1.084% | 1.142% | 1.201% | 1.262% | 1.325% | 1.39% | 1.457% | 1.525% | 1.596% | 1.668% | 1.742% | 1.818% | 1.896% | 1.976% | 2.058% | 2.142% | 2.227% | 2.315% | 2.405% | 2.496% | 2.59% | 2.686% | 2.783% | 2.883% | 2.985% | 3.089%
EPG | 30026486 | DS-EPG-TRNFMR-9000010175 |  | 45 | 5 | 3 | 2 | 1 | 2 | 1 | 4 | 5 | 5 | 322.8571 | 3 | 44 | 3.5 | 84.05 | 0.8458% | 0.8458% | 0.8939% | 0.9436% | 0.9949% | 1.048% | 1.102% | 1.159% | 1.216% | 1.276% | 1.337% | 1.4% | 1.465% | 1.531% | 1.599% | 1.669% | 1.741% | 1.814% | 1.889% | 1.966% | 2.045% | 2.125% | 2.208% | 2.292% | 2.378% | 2.466% | 2.556% | 2.648% | 2.741% | 2.837%
EPG | 30058367 | DS-EPG-TRNFMR-9000010174 |  | 45 | 5 | 3 | 2 | 1 | 2 | 1 | 4 | 5 | 5 | 322.8571 | 3 | 44 | 3.5 | 84.05 | 0.8458% | 0.8458% | 0.8939% | 0.9436% | 0.9949% | 1.048% | 1.102% | 1.159% | 1.216% | 1.276% | 1.337% | 1.4% | 1.465% | 1.531% | 1.599% | 1.669% | 1.741% | 1.814% | 1.889% | 1.966% | 2.045% | 2.125% | 2.208% | 2.292% | 2.378% | 2.466% | 2.556% | 2.648% | 2.741% | 2.837%
WGI | 30475971 | DS-WGI-TRNFMR-9000007146 |  | 49 | 5 | 5 | 1 | 1 | 1 | 1 | 2 | 5 | 1 | 268.5714 | 3 | 44 | 3.5 | 82 | 0.9218% | 0.9218% | 0.9742% | 1.028% | 1.084% | 1.142% | 1.201% | 1.262% | 1.325% | 1.39% | 1.457% | 1.525% | 1.596% | 1.668% | 1.742% | 1.818% | 1.896% | 1.976% | 2.058% | 2.142% | 2.227% | 2.315% | 2.405% | 2.496% | 2.59% | 2.686% | 2.783% | 2.883% | 2.985% | 3.089%
EPG | 30209984 | DS-EPG-TRNFMR-9000007095 |  | 24 | 3 | 3 | 1 | 3 | 2 | 1 | 4 | 3 | 3 | 251.4286 | 3 | 44 | 3.5 | 84.05 | 0.8458% | 0.8458% | 0.8939% | 0.9436% | 0.9949% | 1.048% | 1.102% | 1.159% | 1.216% | 1.276% | 1.337% | 1.4% | 1.465% | 1.531% | 1.599% | 1.669% | 1.741% | 1.814% | 1.889% | 1.966% | 2.045% | 2.125% | 2.208% | 2.292% | 2.378% | 2.466% | 2.556% | 2.648% | 2.741% | 2.837%
CLN | 30338702 | DS-CLN-TRNFMR-9000006730 |  | 21 | 3 | 2 | 2 | 3 | 1 | 1 | 3 | 3 | 2 | 225.7143 | 2 | 24 | 3.5 | 84.05 | 0.1909% | 0.1909% | 0.211% | 0.2322% | 0.2547% | 0.2785% | 0.3035% | 0.3298% | 0.3575% | 0.3865% | 0.4168% | 0.4486% | 0.4817% | 0.5162% | 0.5522% | 0.5897% | 0.6286% | 0.669% | 0.7109% | 0.7543% | 0.7993% | 0.8458% | 0.8939% | 0.9436% | 0.9949% | 1.048% | 1.102% | 1.159% | 1.216% | 1.276%
CRE | 30165029 | DS-CRE-TRNFMR-9000525811 |  | 13 | 3 | 2 | 1 | 3 | 2 | 1 | 4 | 2 | 2 | 217.1429 | 2 | 24 | 3.5 | 84.05 | 0.1909% | 0.1909% | 0.211% | 0.2322% | 0.2547% | 0.2785% | 0.3035% | 0.3298% | 0.3575% | 0.3865% | 0.4168% | 0.4486% | 0.4817% | 0.5162% | 0.5522% | 0.5897% | 0.6286% | 0.669% | 0.7109% | 0.7543% | 0.7993% | 0.8458% | 0.8939% | 0.9436% | 0.9949% | 1.048% | 1.102% | 1.159% | 1.216% | 1.276%
LLG | 30359074 | DS-LLG-TRNFMR-9000007796 |  | 20 | 1 | 2 | 1 | 2 | 1 | 1 | 5 | 3 | 2 | 191.4286 | 2 | 24 | 3.5 | 84.05 | 0.1909% | 0.1909% | 0.211% | 0.2322% | 0.2547% | 0.2785% | 0.3035% | 0.3298% | 0.3575% | 0.3865% | 0.4168% | 0.4486% | 0.4817% | 0.5162% | 0.5522% | 0.5897% | 0.6286% | 0.669% | 0.7109% | 0.7543% | 0.7993% | 0.8458% | 0.8939% | 0.9436% | 0.9949% | 1.048% | 1.102% | 1.159% | 1.216% | 1.276%
CRE | 30380287 | DS-CRE-TRNFMR-9000525810 |  | 13 | 2 | 2 | 1 | 1 | 2 | 1 | 3 | 2 | 2 | 177.1429 | 2 | 24 | 3.5 | 84.05 | 0.1909% | 0.1909% | 0.211% | 0.2322% | 0.2547% | 0.2785% | 0.3035% | 0.3298% | 0.3575% | 0.3865% | 0.4168% | 0.4486% | 0.4817% | 0.5162% | 0.5522% | 0.5897% | 0.6286% | 0.669% | 0.7109% | 0.7543% | 0.7993% | 0.8458% | 0.8939% | 0.9436% | 0.9949% | 1.048% | 1.102% | 1.159% | 1.216% | 1.276%
CLN | 30000439 | DS-CLN-TRNFMR-9000001306 |  | 19 | 2 | 2 | 1 | 1 | 1 | 1 | 3 | 2 | 2 | 165.7143 | 2 | 24 | 3.5 | 84.05 | 0.1909% | 0.1909% | 0.211% | 0.2322% | 0.2547% | 0.2785% | 0.3035% | 0.3298% | 0.3575% | 0.3865% | 0.4168% | 0.4486% | 0.4817% | 0.5162% | 0.5522% | 0.5897% | 0.6286% | 0.669% | 0.7109% | 0.7543% | 0.7993% | 0.8458% | 0.8939% | 0.9436% | 0.9949% | 1.048% | 1.102% | 1.159% | 1.216% | 1.276%
OFR | 30035965 | DS-OFR-TRNFMR-9000014181 |  | 16 | 2 | 2 | 1 | 1 | 1 | 1 | 3 | 2 | 2 | 165.7143 | 2 | 24 | 3.5 | 84.05 | 0.1909% | 0.1909% | 0.211% | 0.2322% | 0.2547% | 0.2785% | 0.3035% | 0.3298% | 0.3575% | 0.3865% | 0.4168% | 0.4486% | 0.4817% | 0.5162% | 0.5522% | 0.5897% | 0.6286% | 0.669% | 0.7109% | 0.7543% | 0.7993% | 0.8458% | 0.8939% | 0.9436% | 0.9949% | 1.048% | 1.102% | 1.159% | 1.216% | 1.276%
KLO | 30002764 | DS-KLO-TRNFMR-9000412348 |  | 15 | 1 | 2 | 1 | 1 | 1 | 1 | 4 | 2 | 2 | 160 | 2 | 24 | 3.5 | 84.05 | 0.1909% | 0.1909% | 0.211% | 0.2322% | 0.2547% | 0.2785% | 0.3035% | 0.3298% | 0.3575% | 0.3865% | 0.4168% | 0.4486% | 0.4817% | 0.5162% | 0.5522% | 0.5897% | 0.6286% | 0.669% | 0.7109% | 0.7543% | 0.7993% | 0.8458% | 0.8939% | 0.9436% | 0.9949% | 1.048% | 1.102% | 1.159% | 1.216% | 1.276%
OFR | 30221642 | DS-OFR-TRNFMR-9000016122 |  | 16 | 1 | 2 | 1 | 1 | 1 | 1 | 3 | 2 | 2 | 151.4286 | 2 | 24 | 3.5 | 84.05 | 0.1909% | 0.1909% | 0.211% | 0.2322% | 0.2547% | 0.2785% | 0.3035% | 0.3298% | 0.3575% | 0.3865% | 0.4168% | 0.4486% | 0.4817% | 0.5162% | 0.5522% | 0.5897% | 0.6286% | 0.669% | 0.7109% | 0.7543% | 0.7993% | 0.8458% | 0.8939% | 0.9436% | 0.9949% | 1.048% | 1.102% | 1.159% | 1.216% | 1.276%
KLO | 30208816 | DS-KLO-TRNFMR-9000412347 |  | 15 | 1 | 2 | 1 | 1 | 1 | 1 | 3 | 2 | 2 | 151.4286 | 2 | 24 | 3.5 | 84.05 | 0.1909% | 0.1909% | 0.211% | 0.2322% | 0.2547% | 0.2785% | 0.3035% | 0.3298% | 0.3575% | 0.3865% | 0.4168% | 0.4486% | 0.4817% | 0.5162% | 0.5522% | 0.5897% | 0.6286% | 0.669% | 0.7109% | 0.7543% | 0.7993% | 0.8458% | 0.8939% | 0.9436% | 0.9949% | 1.048% | 1.102% | 1.159% | 1.216% | 1.276%
PHM | 32944656 | DS-PHM-TRNFMR-9000004393 |  | 8 | 2 | 2 | 1 | 1 | 1 | 1 | 3 | 1 | 1 | 142.8571 | 1 | 8 | 3.5 | 84.05 | 0.01357% | 0.01357% | 0.01791% | 0.023% | 0.02887% | 0.03555% | 0.04308% | 0.0515% | 0.06084% | 0.07112% | 0.08238% | 0.09465% | 0.1079% | 0.1223% | 0.1378% | 0.1543% | 0.172% | 0.1909% | 0.211% | 0.2322% | 0.2547% | 0.2785% | 0.3035% | 0.3298% | 0.3575% | 0.3865% | 0.4168% | 0.4486% | 0.4817% | 0.5162%
PHM | 32944654 | DS-PHM-TRNFMR-9000007050 |  | 8 | 2 | 2 | 1 | 1 | 1 | 1 | 3 | 1 | 1 | 142.8571 | 1 | 8 | 3.5 | 84.05 | 0.01357% | 0.01357% | 0.01791% | 0.023% | 0.02887% | 0.03555% | 0.04308% | 0.0515% | 0.06084% | 0.07112% | 0.08238% | 0.09465% | 0.1079% | 0.1223% | 0.1378% | 0.1543% | 0.172% | 0.1909% | 0.211% | 0.2322% | 0.2547% | 0.2785% | 0.3035% | 0.3298% | 0.3575% | 0.3865% | 0.4168% | 0.4486% | 0.4817% | 0.5162%

## AER VCR Rates(2024)
Category | Rate | Notes
Dec 24 AER VCR ($/kWh) - Res | 49.23 | Vic Av Res
Dec 24 AER VCR ($/kWh) - Com | 34.39 | Vic Av Com
Dec 24 AER VCR ($/kWh) - Ind | 33.49 | Vic Av Ind
Dec 24 AER VCR ($/kWh) - Agr | 22.25 | Vic Av Agr

## Customer No. and Vol per Feeder
CUSTOMER_CLASS | Feeder | VOL | CUST_NO | ZSS | Customer mix received from AusNet Financial Planning & Strategy on 25/7/2025
COMMERCIAL | bra11 | 9860526.7854 | 168 | bra
COMMERCIAL | bge13 | 654988.62 | 45 | bge
COMMERCIAL | phi11 | 1878610.03 | 37 | phi
NCONUML | moe11 | 47447.48 | 18 | moe
NCONUML | drn13 | 27414.73 | 17 | drn
COMMERCIAL | smg34 | 5224461.8 | 1 | smg
FARM | wgl13 | 901266.5312 | 97 | wgl
FARM | msd2 | 2808295.5668 | 471 | msd
NCONUML | elm34 | 86758.8 | 34 | elm
| rwt36 | 703.54 | 2 | rwt
COMMERCIAL | lga41 | 1099100.22 | 2 | lga
| bdl33 | 4298.82 | 8 | bdl
NCONUML | smr14 | 27225.34 | 18 | smr
COMMERCIAL | cln24 | 4484028.8333 | 290 | cln
RESIDENTL | ofr14 | 13024383.6958 | 3554 | ofr
NCONUML | bdl43 | 100361.9983 | 38 | bdl
| ofr22 | 16469.09 | 22 | ofr
NCONUML | rwn33 | 8721.79 | 7 | rwn
LIGHTING | hpk12 | 342838 | 1 | hpk
COMMERCIAL | bra23 | 6262297.01 | 84 | bra
FARM | tt1 | 1865.76 | 1 | tt
LIGHTING | mfa14 | 787800.53 | 1 | mfa
RESIDENTL | brt22 | 9968534.1043 | 1376 | brt
RESIDENTL | mwl25 | 4092575.372 | 493 | mwl
NCONUML | wgi22 | 83961.44 | 23 | wgi
INDUSTRIAL | ldl22 | 4379901.5885 | 45 | ldl
RESIDENTL | phm22 | 3628742.5283 | 796 | phm
FARM | mfa23 | 2691321.6324 | 201 | mfa
NCONUML | rwn32 | 60415.37 | 23 | rwn
FARM | cre22 | 55644.16 | 17 | cre
RESIDENTL | elm24 | 17367685.5307 | 2999 | elm
COMMERCIAL | tt9 | 7181168.3052 | 213 | tt
COMMERCIAL | kms12 | 15257134.8455 | 395 | kms
NCONUML | cyn31 | 24759.23 | 14 | cyn
| llg12 | 26420.7189 | 15 | llg
LIGHTING | ruba22 | 247422.69 | 1 | ruba
RESIDENTL | wt12 | 10803758.701 | 2579 | wt
COMMERCIAL | bwn14 | 6975240.1 | 156 | bwn
NCONUML | bge12 | 37366.03 | 11 | bge
NCONUML | rwn24 | 30489.76 | 21 | rwn
FARM | sfs1 | 113380.09 | 9 | sfs
| bwr13 | 80076.52 | 46 | bwr
FARM | wt13 | 37228.86 | 3 | wt
FARM | cre23 | 226478.55 | 9 | cre
COMMERCIAL | rwn22 | 1886562.0146 | 72 | rwn
| tgn23 | 13898.1302 | 15 | tgn
FARM | ldl22 | 7887.95 | 1 | ldl
RESIDENTL | fgy21 | 7153989.4877 | 1047 | fgy
FARM | mjg11 | 735019.886 | 74 | mjg
| ldl14 | 17432.2687 | 11 | ldl
INDUSTRIAL | ldl24 | 64751.4 | 12 | ldl
| sle13 | 253.3245 | 2 | sle
FARM | moe21 | 6301170.9744 | 504 | moe
FARM | bge23 | 671977.1074 | 66 | bge
RESIDENTL | elm32 | 19949095.4752 | 2463 | elm
COMMERCIAL | ftr12 | 1975462.7263 | 113 | ftr
RESIDENTL | lyd12 | 6657897.88 | 1592 | lyd
RESIDENTL | epg31 | 11862355.3417 | 3027 | epg
NCONUML | ofr11 | 57102.89 | 18 | ofr
FARM | moe11 | 65350.2807 | 7 | moe
FARM | nla32 | 1181128.1259 | 84 | nla
FARM | smr24 | 4141783.4574 | 392 | smr
RESIDENTL | fgy13 | 7970231.1446 | 1518 | fgy
FARM | bdl41 | 1305847.5951 | 258 | bdl
NCONUML | elm23 | 62172.37 | 40 | elm
| elm22 | 20617.5429 | 26 | elm
NCONUML | cre21 | 58240.1 | 18 | cre
FARM | phm32 | 50851.13 | 8 | phm
INDUSTRIAL | lga21 | 208132.02 | 16 | lga
INDUSTRIAL | nrn13 | 39703.59 | 6 | nrn
RESIDENTL | hpk22 | 18949862.0449 | 4569 | hpk
NCONUML | cyn13 | 17637.49 | 6 | cyn
COMMERCIAL | cre31 | 14851829.6913 | 363 | cre
COMMERCIAL | epg32 | 5001490.9226 | 156 | epg
| phm32 | 41386.12 | 47 | phm
NCONUML | wo33 | 6875.31 | 2 | wo
FARM | wgl21 | 5056187.7677 | 366 | wgl
INDUSTRIAL | cre22 | 240829.25 | 4 | cre
RESIDENTL | wgi34 | 3671110.7601 | 570 | wgi
INDUSTRIAL | ldl12 | 10352583.7 | 7 | ldl
INDUSTRIAL | wyk12 | 149433.7 | 6 | wyk
INDUSTRIAL | cyn14 | 23200.151 | 3 | cyn
| wo11 | 4136.2425 | 3 | wo
| msd4 | 20521.76 | 37 | msd
FARM | mby12 | 52034.88 | 19 | mby
COMMERCIAL | rwt22 | 7145877.6761 | 143 | rwt
COMMERCIAL | wo12 | 23719023.8 | 1 | wo
RESIDENTL | wn2 | 17414453.5902 | 3500 | wn
COMMERCIAL | wots25 | 3483725.2811 | 72 | wots
RESIDENTL | bwr33 | 46024.67 | 2 | bwr
RESIDENTL | wn3 | 12349888.6736 | 2099 | wn
RESIDENTL | bn24 | 2992797.8263 | 559 | bn
| bra21 | 41455.7142 | 65 | bra
INDUSTRIAL | hpk14 | 16381.88 | 4 | hpk
RESIDENTL | epg32 | 14811809.1158 | 3829 | epg
COMMERCIAL | cln14 | 10141314.5039 | 129 | cln
FARM | smg31 | 14995.46 | 5 | smg
INDUSTRIAL | drn22 | 2117102.6666 | 12 | drn
NCONUML | drn12 | 43785.8374 | 16 | drn
INDUSTRIAL | fgy34 | 128392.6893 | 5 | fgy
NCONUML | fgy31 | 6707.46 | 4 | fgy
| wt8 | 7059.0655 | 13 | wt
| bwn12 | 6521.57 | 6 | bwn
COMMERCIAL | myt12 | 10774273.2986 | 307 | myt
COMMERCIAL | ldl21 | 5339830.9491 | 117 | ldl
| cln21 | 32425.72 | 66 | cln
INDUSTRIAL | fgy14 | 162921.94 | 7 | fgy
| tgn12 | 22490.11 | 3 | tgn
COMMERCIAL | epg12 | 8214339.5389 | 163 | epg
NCONUML | moe23 | 69334.91 | 17 | moe
FARM | cyn14 | 7715.15 | 1 | cyn
RESIDENTL | lyd14 | 10580841.4317 | 1203 | lyd
COMMERCIAL | smg23 | 21963007.1063 | 434 | smg
INDUSTRIAL | bra33 | 2076536.62 | 34 | bra
INDUSTRIAL | rwt14 | 2271244.55 | 44 | rwt
COMMERCIAL | lga14 | 2174194.9787 | 115 | lga
INDUSTRIAL | myt22 | 3176.32 | 3 | myt
FARM | cyn21 | 10230.57 | 2 | cyn
| klo24 | 65411.35 | 119 | klo
COMMERCIAL | brt21 | 6571769.7252 | 216 | brt
FARM | kms11 | 665243.0597 | 75 | kms
| elm34 | 25999.6869 | 33 | elm
INDUSTRIAL | mwl11 | 366139.79 | 15 | mwl
INDUSTRIAL | lyd14 | 80895.88 | 12 | lyd
LIGHTING | cpk11 | 1086.88 | 1 | cpk
NCONUML | fgy23 | 34402.31 | 12 | fgy
| bra32 | 15753.982 | 22 | bra
RESIDENTL | epg12 | 26391788.5687 | 6905 | epg
COMMERCIAL | cyn24 | 15647575.1097 | 304 | cyn
INDUSTRIAL | phm21 | 511727.73 | 19 | phm
NCONUML | ftr12 | 5424.58 | 5 | ftr
| bwa23 | 5447.575 | 8 | bwa
NCONUML | llg12 | 4182.92 | 3 | llg
COMMERCIAL | drn13 | 5299129.684 | 96 | drn
INDUSTRIAL | hpk21 | 31624.71 | 8 | hpk
INDUSTRIAL | wyk23 | 1500537.4334 | 28 | wyk
RESIDENTL | lga12 | 4152631.2896 | 644 | lga
RESIDENTL | cyn11 | 6009338.551 | 1440 | cyn
NCONUML | fgy24 | 70027.41 | 43 | fgy
| moe23 | 74726.3012 | 22 | moe
COMMERCIAL | elm24 | 3531802.26 | 46 | elm
LIGHTING | elm33 | 1000.47 | 1 | elm
RESIDENTL | smg23 | 6500499.5996 | 1411 | smg
FARM | msd4 | 1851245.0012 | 252 | msd
COMMERCIAL | lga24 | 21693950.3379 | 92 | lga
COMMERCIAL | ldl11 | 7360578.73 | 74 | ldl
NCONUML | rve13 | 29515.6981 | 24 | rve
COMMERCIAL | trc01 | 365242.5067 | 42 | trc
COMMERCIAL | wt15 | 1164715.6471 | 30 | wt
COMMERCIAL | bra14 | 811059.401 | 59 | bra
| ftr21 | 17034.7542 | 20 | ftr
RESIDENTL | bra23 | 7643359.408 | 1736 | bra
INDUSTRIAL | cpk11 | 59065.36 | 14 | cpk
INDUSTRIAL | hpk12 | 531460.54 | 46 | hpk
FARM | fgy23 | 137430.23 | 3 | fgy
INDUSTRIAL | tt4 | 77015.1997 | 16 | tt
FARM | cpk22 | 45399.86 | 6 | cpk
INDUSTRIAL | yn31 | 1004932.7745 | 6 | yn
FARM | myt22 | 1873055.6433 | 191 | myt
| cpk12 | 20188.43 | 32 | cpk
RESIDENTL | bwa22 | 6606654.3694 | 1106 | bwa
| mfa34 | 1434.55 | 6 | mfa
| nla31 | 4780.58 | 5 | nla
FARM | mdg1 | 36782.2 | 6 | mdg
RESIDENTL | mwl21 | 3605605.4081 | 859 | mwl
COMMERCIAL | phm33 | 14452041.4603 | 180 | phm
INDUSTRIAL | ofr23 | 154535.41 | 17 | ofr
INDUSTRIAL | elm21 | 177435.466 | 7 | elm
INDUSTRIAL | wt5 | 89.11 | 1 | wt
FARM | llg13 | 1917532.2118 | 152 | llg
INDUSTRIAL | klk21 | 41156.68 | 10 | klk
NCONUML | wt9 | 48247.64 | 17 | wt
FARM | mdi1 | 153288.2952 | 21 | mdi
INDUSTRIAL | nrn14 | 19245.31 | 5 | nrn
INDUSTRIAL | wgl12 | 500659.11 | 16 | wgl
FARM | fgy13 | 80534.51 | 6 | fgy
INDUSTRIAL | bwr14 | 1597974.48 | 1 | bwr
LIGHTING | bn11 | 103048.5 | 1 | bn
RESIDENTL | klo14 | 40411755.0117 | 10946 | klo
RESIDENTL | fgy33 | 9101921.8028 | 1763 | fgy
LIGHTING | cre31 | 2308168.51 | 1 | cre
RESIDENTL | wn5 | 8555201.9981 | 1156 | wn
COMMERCIAL | mfa22 | 5299491.9938 | 179 | mfa
COMMERCIAL | lyd11 | 3798691.89 | 62 | lyd
LIGHTING | bn24 | 2014.81 | 1 | bn
COMMERCIAL | cf1 | 9360587.4941 | 189 | cf
FARM | lga11 | 4665290.6529 | 555 | lga
RESIDENTL | lyd13 | 10895753.2364 | 2051 | lyd
NCONUML | cre33 | 35388.67 | 19 | cre
| smg32 | 685.05 | 3 | smg
INDUSTRIAL | cyn11 | 1966971.1028 | 55 | cyn
COMMERCIAL | wn2 | 10157994.9798 | 156 | wn
| phm21 | 32464.7212 | 22 | phm
| sfs1 | 13890.635 | 10 | sfs
NCONUML | tt12 | 15011.94 | 8 | tt
FARM | lga21 | 1065599.6961 | 147 | lga
| ldl12 | 52350.63 | 6 | ldl
INDUSTRIAL | smg31 | 231921 | 9 | smg
LIGHTING | myt12 | 813470.88 | 6 | myt
| smr24 | 66801.9 | 34 | smr
NCONUML | cre32 | 49453.4427 | 23 | cre
INDUSTRIAL | bdl44 | 2337630.2078 | 41 | bdl
| rve11 | 302066.1 | 12 | rve
FARM | wo31 | 3245.01 | 1 | wo
LIGHTING | ofr13 | 171706.2 | 2 | ofr
RESIDENTL | tt9 | 13181645.445 | 3553 | tt
COMMERCIAL | wgl11 | 13522117.9742 | 216 | wgl
COMMERCIAL | hpk24 | 15242696.9791 | 271 | hpk
COMMERCIAL | bwr34 | 12222544.1423 | 437 | bwr
NCONUML | nla34 | 19980.17 | 11 | nla
FARM | bwr24 | 9303.26 | 1 | bwr
| wgi23 | 15962.8799 | 36 | wgi
RESIDENTL | cln13 | 18593732.5659 | 6830 | cln
RESIDENTL | lga13 | 1879247.7046 | 295 | lga
RESIDENTL | cnr3 | 108696.4186 | 22 | cnr
| wgl12 | 112644.3661 | 43 | wgl
COMMERCIAL | cln12 | 8203266.5202 | 86 | cln
NCONUML | ofr21 | 100427.35 | 34 | ofr
RESIDENTL | drn24 | 10021102.8231 | 2473 | drn
COMMERCIAL | cyn31 | 1940881.6507 | 53 | cyn
NCONUML | ldl24 | 34534.3 | 19 | ldl
COMMERCIAL | ofr13 | 9302944.2987 | 197 | ofr
| wots13 | 58538.6484 | 32 | wots
| cpk23 | 23360.0808 | 24 | cpk
NCONUML | cln11 | 4587.8606 | 9 | cln
| wt15 | 51811.4 | 11 | wt
COMMERCIAL | epg24 | 26841528 | 1 | epg
FARM | drn22 | 329138.5031 | 52 | drn
| mfa31 | 16838.31 | 22 | mfa
COMMERCIAL | bra32 | 4055727.3404 | 158 | bra
COMMERCIAL | cpk21 | 14974774.5549 | 258 | cpk
INDUSTRIAL | myt21 | 335981.9667 | 19 | myt
FARM | nrn14 | 139044.47 | 14 | nrn
| wt5 | 22324.85 | 13 | wt
INDUSTRIAL | mfa23 | 139940.33 | 14 | mfa
FARM | wyk12 | 2634438.6357 | 233 | wyk
RESIDENTL | epg23 | 3653084.6682 | 932 | epg
COMMERCIAL | tgn11 | 2525258.71 | 85 | tgn
| wt13 | 22551.0062 | 37 | wt
| cyn13 | 10533.28 | 7 | cyn
INDUSTRIAL | fgy13 | 259435.94 | 2 | fgy
RESIDENTL | cln12 | 23908773.0216 | 6775 | cln
COMMERCIAL | brt22 | 9042592.2197 | 210 | brt
COMMERCIAL | rwt25 | 7526054.6961 | 146 | rwt
FARM | mfa31 | 218040.8355 | 21 | mfa
COMMERCIAL | cln22 | 3248277.4443 | 37 | cln
NCONUML | bdl33 | 22970.8 | 8 | bdl
COMMERCIAL | fgy12 | 74427.591 | 4 | fgy
RESIDENTL | mwl16 | 8188909.2298 | 1700 | mwl
INDUSTRIAL | moe25 | 612177.9824 | 16 | moe
COMMERCIAL | tt7 | 24970154.3491 | 341 | tt
INDUSTRIAL | bwr24 | 4118148.7987 | 125 | bwr
RESIDENTL | moe13 | 2791200.4315 | 357 | moe
FARM | wyk24 | 694188.3378 | 94 | wyk
NCONUML | wo14 | 36996.26 | 12 | wo
RESIDENTL | bra13 | 6470560.8911 | 1572 | bra
RESIDENTL | tt7 | 39398.92 | 9 | tt
FARM | epg34 | 15821.91 | 5 | epg
INDUSTRIAL | yn35 | 6582.38 | 2 | yn
NCONUML | bwa23 | 749.23 | 1 | bwa
FARM | sle13 | 1461316.56 | 213 | sle
COMMERCIAL | cpk13 | 4127340.5971 | 198 | cpk
INDUSTRIAL | ldl14 | 1064067.7426 | 16 | ldl
| rwt14 | 62105.3312 | 18 | rwt
LIGHTING | hpk13 | 14513.85 | 1 | hpk
RESIDENTL | klk22 | 940238.19 | 128 | klk
COMMERCIAL | mwl25 | 259300.06 | 16 | mwl
| mjg11 | 96977.3135 | 7 | mjg
RESIDENTL | hpk24 | 4867180.3451 | 1284 | hpk
FARM | ftr21 | 6703423.0704 | 705 | ftr
FARM | smr12 | 441800.25 | 44 | smr
FARM | bwr13 | 73574.54 | 13 | bwr
| ldl22 | 9241.11 | 9 | ldl
FARM | wo22 | 35676.335 | 7 | wo
NCONUML | moe12 | 9318.9 | 3 | moe
INDUSTRIAL | bdl31 | 1561951.6978 | 44 | bdl
COMMERCIAL | ofr14 | 8393968.2568 | 77 | ofr
NCONUML | tgn23 | 48562.71 | 16 | tgn
NCONUML | cyn21 | 25127.29 | 5 | cyn
FARM | phm34 | 22945.58 | 3 | phm
INDUSTRIAL | cyn33 | 36519.92 | 4 | cyn
LIGHTING | bm8b32 | 1070.04 | 1 | bmb
FARM | llg12 | 5311057.9488 | 488 | llg
NCONUML | rwt32 | 94072.85 | 46 | rwt
COMMERCIAL | myt11 | 912988.53 | 42 | myt
INDUSTRIAL | cpk22 | 129954.91 | 11 | cpk
| cre22 | 20388.051 | 33 | cre
RESIDENTL | ldl21 | 5451727.7741 | 1502 | ldl
FARM | bdl44 | 8189534.7866 | 736 | bdl
INDUSTRIAL | bn11 | 1899511.3657 | 45 | bn
INDUSTRIAL | wgi31 | 152399.6 | 19 | wgi
INDUSTRIAL | mdi1 | 16.0426 | 1 | mdi
| ofr11 | 90492.4817 | 79 | ofr
LIGHTING | kms11 | 547479.19 | 1 | kms
RESIDENTL | phi12 | 18738852.0082 | 4967 | phi
COMMERCIAL | bwr12 | 7897915.6022 | 287 | bwr
FARM | msd1 | 2520603.4144 | 354 | msd
COMMERCIAL | tgn44 | 4662112.18 | 89 | tgn
NCONUML | uwy1 | 29815.85 | 15 | uwy
NCONUML | lga22 | 54192.29 | 17 | lga
NCONUML | lga23 | 17186.13 | 6 | lga
INDUSTRIAL | hpk13 | 1952010.47 | 3 | hpk
FARM | drn23 | 391232.6382 | 58 | drn
FARM | ldl23 | 5910515.5529 | 453 | ldl
FARM | bdl31 | 55336.85 | 12 | bdl
RESIDENTL | bwr34 | 11176240.016 | 2984 | bwr
RESIDENTL | ofr13 | 5689359.8131 | 1445 | ofr
NCONUML | bra21 | 145563.002 | 72 | bra
COMMERCIAL | cf2 | 1114027.3697 | 138 | cf
RESIDENTL | bdl32 | 16368580.902 | 3124 | bdl
COMMERCIAL | smr22 | 10240657.5236 | 95 | smr
NCONUML | rve12 | 34563.18 | 21 | rve
COMMERCIAL | cnr3 | 208527.63 | 11 | cnr
| elm25 | 9741.0155 | 15 | elm
INDUSTRIAL | lyd13 | 30651.21 | 5 | lyd
INDUSTRIAL | mby12 | 279353.09 | 7 | mby
INDUSTRIAL | epg21 | 31298.6803 | 2 | epg
FARM | wgl12 | 7817936.5802 | 624 | wgl
COMMERCIAL | moe13 | 1401894.0174 | 82 | moe
RESIDENTL | lga14 | 7239522.4699 | 1158 | lga
RESIDENTL | epg35 | 308209.78 | 22 | epg
FARM | hpk14 | 29274.39 | 5 | hpk
LIGHTING | bn22 | 341591.58 | 1 | bn
NCONUML | bge11 | 85890.46 | 45 | bge
NCONUML | wt7 | 26985.19 | 18 | wt
| wo31 | 27869.149 | 41 | wo
INDUSTRIAL | elm32 | 759094.4258 | 68 | elm
NCONUML | cre23 | 95638.5 | 25 | cre
RESIDENTL | cln23 | 19292170.1488 | 4992 | cln
| lga21 | 17263.28 | 18 | lga
NCONUML | bwn12 | 35975.24 | 12 | bwn
| fgy31 | 1671.76 | 6 | fgy
NCONUML | ftr23 | 39743.6852 | 30 | ftr
NCONUML | smg21 | 9405.11 | 5 | smg
RESIDENTL | epg13 | 24819451.0174 | 7299 | epg
RESIDENTL | ruba22 | 5955886.59 | 1080 | ruba
INDUSTRIAL | bwr23 | 1917390.4058 | 110 | bwr
COMMERCIAL | bn23 | 4585306.9 | 117 | bn
| fgy24 | 60212.15 | 95 | fgy
LIGHTING | brt21 | 27441.26 | 1 | brt
COMMERCIAL | mby14 | 13812.56 | 3 | mby
RESIDENTL | drn21 | 15235611.8074 | 3585 | drn
RESIDENTL | nrn11 | 3368324.1063 | 703 | nrn
NCONUML | cln21 | 97183.1897 | 28 | cln
NCONUML | tgn12 | 26909.78 | 9 | tgn
FARM | moe22 | 48531.59 | 7 | moe
RESIDENTL | bra14 | 17287022.2386 | 4193 | bra
RESIDENTL | brt21 | 8587133.8204 | 1368 | brt
INDUSTRIAL | ldl23 | 2181365.61 | 45 | ldl
NCONUML | klo24 | 121410.57 | 41 | klo
INDUSTRIAL | wt8 | 22231.36 | 5 | wt
| bdl41 | 27628.4721 | 32 | bdl
COMMERCIAL | sle14 | 13227565.7623 | 343 | sle
| smr14 | 17300.3116 | 19 | smr
INDUSTRIAL | llg11 | 439641.21 | 9 | llg
| wgi22 | 13903.1 | 35 | wgi
NCONUML | moe22 | 34069.45 | 10 | moe
| ftr12 | 15921.46 | 17 | ftr
COMMERCIAL | epg11 | 902129.45 | 16 | epg
RESIDENTL | cpk13 | 21255549.7429 | 4974 | cpk
| fgy23 | 9273.25 | 10 | fgy
FARM | cyn12 | 9105.46 | 2 | cyn
INDUSTRIAL | rwn31 | 527467.66 | 22 | rwn
RESIDENTL | bm8b32 | 357081.227 | 62 | bmb
FARM | ruba22 | 1060033.1321 | 158 | ruba
INDUSTRIAL | cnr1 | 88077.93 | 3 | cnr
FARM | cpk12 | 972803.9358 | 91 | cpk
COMMERCIAL | wo14 | 14658340.7796 | 304 | wo
COMMERCIAL | tt5 | 6134357.4395 | 224 | tt
INDUSTRIAL | wo11 | 18559582.74 | 7 | wo
| wgl23 | 17798.7289 | 12 | wgl
NCONUML | cyn12 | 64730.9 | 21 | cyn
COMMERCIAL | bwr33 | 3515549.759 | 83 | bwr
COMMERCIAL | cyn22 | 10287381.4837 | 183 | cyn
COMMERCIAL | rwt32 | 5482054.6843 | 198 | rwt
INDUSTRIAL | nrn12 | 7260.73 | 2 | nrn
RESIDENTL | cln22 | 8137131.1146 | 3340 | cln
| kms12 | 36774.1343 | 44 | kms
| cyn24 | 12784.0842 | 11 | cyn
| smg33 | 11524.64 | 21 | smg
COMMERCIAL | rve11 | 18192998.0721 | 274 | rve
FARM | wt5 | 8146.48 | 2 | wt
INDUSTRIAL | bge23 | 983662.8538 | 7 | bge
| msd2 | 9983.6 | 13 | msd
| bra12 | 98134.87 | 2 | bra
RESIDENTL | hpk23 | 13762355.5073 | 3377 | hpk
COMMERCIAL | smr13 | 15057236.7589 | 394 | smr
INDUSTRIAL | rwt21 | 372221.49 | 45 | rwt
FARM | rve12 | 22362.86 | 5 | rve
NCONUML | fgy32 | 32042.28 | 18 | fgy
INDUSTRIAL | smr12 | 37387308.69 | 3 | smr
NCONUML | mfa34 | 19451.19 | 8 | mfa
FARM | wots13 | 4844280.0942 | 510 | wots
COMMERCIAL | drn21 | 3220798.94 | 52 | drn
INDUSTRIAL | wo31 | 765.77 | 1 | wo
| fgy32 | 8528.5063 | 10 | fgy
INDUSTRIAL | bwr32 | 3058614 | 72 | bwr
| elm23 | 20831.6 | 30 | elm
INDUSTRIAL | mwl12 | 574569.29 | 12 | mwl
RESIDENTL | cpk21 | 7771248.352 | 1679 | cpk
COMMERCIAL | wots11 | 6621581.9604 | 243 | wots
INDUSTRIAL | ftr21 | 313604.8 | 24 | ftr
NCONUML | lyd11 | 43059.75 | 9 | lyd
FARM | phm21 | 25361.56 | 3 | phm
INDUSTRIAL | wyk13 | 453974.55 | 15 | wyk
INDUSTRIAL | mdg1 | 21781.42 | 1 | mdg
INDUSTRIAL | tt1 | 7434378.9861 | 77 | tt
INDUSTRIAL | wgi34 | 1206209.57 | 8 | wgi
LIGHTING | wgi33 | 1050486.0487 | 2 | wgi
COMMERCIAL | wgl15 | 27996457.3831 | 596 | wgl
RESIDENTL | bge23 | 16900476.9279 | 2094 | bge
INDUSTRIAL | bwr13 | 2417661.2776 | 147 | bwr
NCONUML | epg23 | 28250.73 | 7 | epg
INDUSTRIAL | drn14 | 25996.95 | 2 | drn
RESIDENTL | drn14 | 23831050.9741 | 4399 | drn
RESIDENTL | rwt31 | 5842296.4371 | 1436 | rwt
COMMERCIAL | drn24 | 1717660.9 | 35 | drn
FARM | epg14 | 3614.72 | 1 | epg
RESIDENTL | smr13 | 11225814.5464 | 2447 | smr
COMMERCIAL | wots12 | 14359758.4732 | 371 | wots
COMMERCIAL | klk11 | 3080934.4269 | 114 | klk
NCONUML | mwl14 | 31252.61 | 13 | mwl
INDUSTRIAL | sle11 | 266690.1 | 32 | sle
NCONUML | epg31 | 41319.36 | 24 | epg
RESIDENTL | cf1 | 4176161.3871 | 493 | cf
INDUSTRIAL | phm34 | 816155.12 | 6 | phm
FARM | rwn34 | 20402.21 | 4 | rwn
| mby12 | 1524.95 | 3 | mby
RESIDENTL | wgi31 | 14866992.8529 | 3617 | wgi
RESIDENTL | wots25 | 16858284.9544 | 3532 | wots
RESIDENTL | cre33 | 21876811.5892 | 4235 | cre
RESIDENTL | fgy34 | 4606270.9018 | 975 | fgy
RESIDENTL | cyn32 | 15011504.2579 | 3573 | cyn
RESIDENTL | klk11 | 9194980.7775 | 1227 | klk
INDUSTRIAL | fgy33 | 1452360.19 | 13 | fgy
INDUSTRIAL | wgl13 | 6688610.4344 | 14 | wgl
| tgn41 | 12751.16 | 13 | tgn
COMMERCIAL | klk22 | 85830.78 | 8 | klk
| mby11 | 4292.69 | 12 | mby
FARM | drn12 | 9939.61 | 1 | drn
RESIDENTL | rwn24 | 15617115.6722 | 2794 | rwn
RESIDENTL | cre32 | 8053371.5554 | 2218 | cre
COMMERCIAL | bwn11 | 5920812.2037 | 76 | bwn
NCONUML | smg33 | 19709.42 | 12 | smg
INDUSTRIAL | mby11 | 90387.22 | 16 | mby
COMMERCIAL | tgn41 | 8173213.7745 | 338 | tgn
INDUSTRIAL | wn7 | 3582803.57 | 9 | wn
FARM | bwr23 | 29264.76 | 8 | bwr
RESIDENTL | bwn13 | 8026926.4045 | 1629 | bwn
FARM | wgi24 | 1757204.2906 | 142 | wgi
| rve13 | 21148.03 | 29 | rve
RESIDENTL | wgl21 | 23764201.6622 | 4642 | wgl
COMMERCIAL | wn1 | 22168293.2818 | 620 | wn
INDUSTRIAL | cyn32 | 738566.1077 | 85 | cyn
| hpk21 | 27858.58 | 57 | hpk
COMMERCIAL | klo11 | 2030116.61 | 11 | klo
INDUSTRIAL | bn22 | 260832.7234 | 23 | bn
| ofr24 | 25053.77 | 43 | ofr
| drn12 | 30292.1138 | 29 | drn
COMMERCIAL | smg22 | 18806077.0677 | 136 | smg
COMMERCIAL | bwa22 | 4509592.2057 | 144 | bwa
COMMERCIAL | drn12 | 15118769.4919 | 112 | drn
| ldl23 | 80304.9161 | 48 | ldl
| rwn32 | 14306.27 | 22 | rwn
| drn23 | 12868.4314 | 15 | drn
RESIDENTL | mwl22 | 12904194.2639 | 2809 | mwl
COMMERCIAL | tt6 | 3682930.1298 | 115 | tt
COMMERCIAL | bra24 | 3429037.1414 | 127 | bra
NCONUML | hpk11 | 112614.82 | 31 | hpk
RESIDENTL | mfa21 | 12551518.2306 | 1921 | mfa
RESIDENTL | bge22 | 19945240.9452 | 3164 | bge
| tt4 | 9710.0483 | 41 | tt
NCONUML | phm22 | 22255.8232 | 9 | phm
COMMERCIAL | fgy21 | 1241019.6707 | 34 | fgy
INDUSTRIAL | nla31 | 516137.35 | 16 | nla
FARM | wyk13 | 707273.0378 | 84 | wyk
NCONUML | elm25 | 44655.33 | 20 | elm
| ofr23 | 28214.1089 | 26 | ofr
INDUSTRIAL | ruba22 | 167892.49 | 8 | ruba
FARM | hpk21 | 3124.97 | 1 | hpk
FARM | wn4 | 999664.927 | 129 | wn
COMMERCIAL | wn6 | 8795190.5545 | 246 | wn
| cre23 | 50195.43 | 25 | cre
COMMERCIAL | bwr22 | 15914202.1636 | 269 | bwr
INDUSTRIAL | elm22 | 545216.4127 | 27 | elm
NCONUML | bwr32 | 46210.27 | 31 | bwr
COMMERCIAL | moe12 | 4799517.76 | 51 | moe
| drn22 | 43438.5 | 28 | drn
FARM | bn22 | 13032.09 | 3 | bn
FARM | ldl24 | 222231.4641 | 11 | ldl
| bdl31 | 24144.6762 | 16 | bdl
FARM | cpk11 | 227979.0877 | 18 | cpk
FARM | elm33 | 50441.5205 | 4 | elm
INDUSTRIAL | rve13 | 147824.4003 | 10 | rve
COMMERCIAL | uwy1 | 603856.89 | 33 | uwy
FARM | mfa21 | 13347321.3386 | 701 | mfa
RESIDENTL | wo14 | 1446838.665 | 266 | wo
NCONUML | rwt14 | 102266.96 | 37 | rwt
| kms11 | 9612.23 | 20 | kms
RESIDENTL | phi11 | 5828644.3864 | 1391 | phi
COMMERCIAL | tgn12 | 10174331.2835 | 242 | tgn
LIGHTING | drn21 | 522455.53 | 1 | drn
INDUSTRIAL | smr22 | 2060432.23 | 13 | smr
| moe21 | 19173.8011 | 29 | moe
NCONUML | fgy12 | 1668.8419 | 4 | fgy
COMMERCIAL | elm25 | 2590499.6378 | 73 | elm
| epg34 | 11737.1961 | 27 | epg
COMMERCIAL | cpk23 | 2022573.8223 | 44 | cpk
COMMERCIAL | sle31 | 4198591.4215 | 178 | sle
FARM | nrn13 | 23844.37 | 5 | nrn
FARM | elm26 | 83060.0495 | 12 | elm
INDUSTRIAL | rve12 | 67014.5 | 12 | rve
INDUSTRIAL | moe21 | 304282.5341 | 37 | moe
COMMERCIAL | ofr21 | 9424773.56 | 126 | ofr
FARM | wn3 | 4385381.9629 | 585 | wn
FARM | klk21 | 574949.1868 | 82 | klk
NCONUML | wyk13 | 97422.66 | 49 | wyk
FARM | bwn12 | 14573.05 | 3 | bwn
NCONUML | msd2 | 8161.26 | 6 | msd
COMMERCIAL | elm31 | 474386.1613 | 1 | elm
RESIDENTL | rwt35 | 12065.95 | 2 | rwt
RESIDENTL | wt6 | 15702930.1084 | 3397 | wt
RESIDENTL | cln24 | 3991370.9732 | 1090 | cln
COMMERCIAL | smg21 | 2744632.8687 | 43 | smg
| myt21 | 64545.94 | 22 | myt
RESIDENTL | lga22 | 9862202.3617 | 1608 | lga
INDUSTRIAL | cyn13 | 4447831.06 | 67 | cyn
COMMERCIAL | ruba12 | 6703349.3664 | 290 | ruba
| smr23 | 7378.7014 | 9 | smr
FARM | phi13 | 230339.12 | 15 | phi
RESIDENTL | wt11 | 8665012.8839 | 2213 | wt
RESIDENTL | bge13 | 9255563.8982 | 1458 | bge
COMMERCIAL | bge11 | 11367890.3817 | 330 | bge
COMMERCIAL | wgi23 | 2290528.82 | 95 | wgi
COMMERCIAL | epg35 | 29855241.8371 | 304 | epg
NCONUML | mwl23 | 55631.52 | 20 | mwl
RESIDENTL | tgn11 | 18615536.7391 | 4196 | tgn
RESIDENTL | klo24 | 35150523.3753 | 8219 | klo
| wgi32 | 32777.55 | 36 | wgi
| uwy1 | 1895.86 | 6 | uwy
COMMERCIAL | wots24 | 5008654.6646 | 265 | wots
INDUSTRIAL | phi13 | 601326.64 | 38 | phi
LIGHTING | cf1 | 76883.018 | 3 | cf
RESIDENTL | cre21 | 18876617.5647 | 4715 | cre
INDUSTRIAL | wo32 | 73086.25 | 1 | wo
COMMERCIAL | lga13 | 621321.4861 | 47 | lga
FARM | cnr2 | 245915.51 | 48 | cnr
COMMERCIAL | bge22 | 4521687.9575 | 100 | bge
INDUSTRIAL | cyn12 | 101425.5 | 5 | cyn
FARM | drn11 | 51881.33 | 8 | drn
INDUSTRIAL | wo23 | 212041.78 | 1 | wo
RESIDENTL | lga23 | 5064870.5947 | 821 | lga
RESIDENTL | bn12 | 3438265.7182 | 625 | bn
RESIDENTL | bra21 | 23268334.8963 | 5707 | bra
| bdl42 | 11198.42 | 14 | bdl
FARM | cnr1 | 2440.03 | 2 | cnr
| phm34 | 68320.3174 | 32 | phm
FARM | rwt31 | 12148.87 | 1 | rwt
| smg31 | 8879.89 | 17 | smg
LIGHTING | tgn11 | 1064655.8 | 1 | tgn
FARM | llg14 | 4195351.6172 | 347 | llg
FARM | mwl11 | 2401732.236 | 295 | mwl
INDUSTRIAL | brt22 | 103539.39 | 15 | brt
COMMERCIAL | mwl14 | 15268408.4249 | 139 | mwl
RESIDENTL | wn1 | 4757807.4084 | 1039 | wn
COMMERCIAL | wo33 | 4706642.85 | 27 | wo
| nrn14 | 10562.91 | 10 | nrn
RESIDENTL | wgl15 | 10836827.2608 | 2158 | wgl
RESIDENTL | mfa22 | 4069843.249 | 701 | mfa
NCONUML | wyk24 | 96009.71 | 32 | wyk
NCONUML | rwn34 | 17137.95 | 21 | rwn
NCONUML | rve11 | 32578.28 | 16 | rve
INDUSTRIAL | klk11 | 54511.69 | 7 | klk
RESIDENTL | tt2 | 73044.37 | 7 | tt
COMMERCIAL | rwn32 | 3002784.6794 | 97 | rwn
NCONUML | tt1 | 9612.49 | 4 | tt
NCONUML | bwr23 | 79898.93 | 30 | bwr
NCONUML | epg14 | 19866.64 | 14 | epg
| elm26 | 27328.755 | 32 | elm
INDUSTRIAL | bdl32 | 418697.92 | 34 | bdl
FARM | wt11 | 3746.97 | 1 | wt
NCONUML | ofr23 | 50364.93 | 30 | ofr
INDUSTRIAL | smg23 | 412547.84 | 9 | smg
LIGHTING | klo14 | 3058096.87 | 1 | klo
| nrn13 | 13473.67 | 22 | nrn
FARM | bra12 | 12444.91 | 1 | bra
COMMERCIAL | cre21 | 15222170.3645 | 489 | cre
INDUSTRIAL | wgi32 | 984365.53 | 33 | wgi
NCONUML | rwt25 | 118451.05 | 54 | rwt
INDUSTRIAL | mwe236 | 280541.09 | 16 | mwe
RESIDENTL | epg33 | 183201.2006 | 6 | epg
INDUSTRIAL | elm33 | 243571.284 | 12 | elm
RESIDENTL | ldl11 | 13512975.3636 | 2241 | ldl
| mwl12 | 15850.97 | 9 | mwl
INDUSTRIAL | fgy21 | 6595081.67 | 18 | fgy
LIGHTING | smr24 | 109914.08 | 1 | smr
RESIDENTL | rwt25 | 10768082.8154 | 2324 | rwt
INDUSTRIAL | rwt15 | 3409961.2906 | 83 | rwt
INDUSTRIAL | phi12 | 3418741.3516 | 25 | phi
INDUSTRIAL | bwa22 | 1592049.74 | 9 | bwa
NCONUML | wo22 | 90587.46 | 26 | wo
INDUSTRIAL | ldl21 | 599666.7 | 44 | ldl
INDUSTRIAL | wt6 | 1814.16 | 1 | wt
NCONUML | ofr22 | 9198.59 | 2 | ofr
INDUSTRIAL | bra13 | 1860337.5903 | 47 | bra
COMMERCIAL | fgy24 | 2616699.5517 | 109 | fgy
RESIDENTL | epg11 | 6094828.0666 | 1503 | epg
NCONUML | rwt36 | 1279.88 | 1 | rwt
RESIDENTL | bwn14 | 23184606.5946 | 3016 | bwn
COMMERCIAL | bra31 | 7996775.7312 | 141 | bra
| nla32 | 13550.62 | 15 | nla
FARM | brt11 | 223967.42 | 33 | brt
| hpk12 | 10433.13 | 13 | hpk
INDUSTRIAL | llg13 | 899195.7591 | 21 | llg
INDUSTRIAL | wgl21 | 1687828.17 | 29 | wgl
INDUSTRIAL | cnr2 | 615523.18 | 19 | cnr
INDUSTRIAL | mfa14 | 499885.98 | 5 | mfa
RESIDENTL | drn13 | 15714620.5428 | 2698 | drn
FARM | kms12 | 1180373.8068 | 156 | kms
COMMERCIAL | rwn24 | 15303994.2605 | 63 | rwn
NCONUML | wn4 | 65357.11 | 21 | wn
COMMERCIAL | rwn33 | 562037.42 | 22 | rwn
| moe22 | 3614.75 | 12 | moe
| wgl13 | 39374.2 | 44 | wgl
| moe11 | 8193.3901 | 21 | moe
COMMERCIAL | wt7 | 4475658.5866 | 198 | wt
NCONUML | bwr13 | 106489.72 | 46 | bwr
NCONUML | kms12 | 115620.45 | 45 | kms
NCONUML | cyn24 | 41312.6858 | 21 | cyn
COMMERCIAL | mwl13 | 8520395.3383 | 232 | mwl
COMMERCIAL | cyn32 | 10902527.7138 | 351 | cyn
INDUSTRIAL | tgn31 | 3050316.88 | 29 | tgn
| wo13 | 12961.22 | 9 | wo
NCONUML | bra12 | 30121.15 | 6 | bra
| mwl24 | 4141.68 | 3 | mwl
RESIDENTL | ftr22 | 5196242.6186 | 1010 | ftr
| cyn12 | 33132.831 | 28 | cyn
| mwl11 | 4217.9 | 11 | mwl
NCONUML | sle13 | 9744.3474 | 7 | sle
RESIDENTL | sle14 | 16027394.2978 | 4223 | sle
RESIDENTL | wgl23 | 5362246.1099 | 739 | wgl
COMMERCIAL | cre23 | 25513720.5265 | 132 | cre
RESIDENTL | bdl43 | 5886157.096 | 1122 | bdl
RESIDENTL | bge21 | 100743.92 | 11 | bge
RESIDENTL | smg22 | 10427736.14 | 2476 | smg
FARM | rwn31 | 347566.14 | 21 | rwn
INDUSTRIAL | bn12 | 8173831.79 | 6 | bn
| wgi24 | 27543.5394 | 32 | wgi
| mfa23 | 2828.28 | 3 | mfa
NCONUML | elm22 | 93887.89 | 42 | elm
INDUSTRIAL | wots13 | 2426481.9937 | 28 | wots
RESIDENTL | mwl13 | 9372820.2657 | 1896 | mwl
COMMERCIAL | epg31 | 8736205.1691 | 170 | epg
| bdl44 | 43009.9658 | 33 | bdl
COMMERCIAL | wgl24 | 14484234.4559 | 200 | wgl
INDUSTRIAL | wn3 | 1104797.78 | 30 | wn
| wgi33 | 38017.7186 | 28 | wgi
NCONUML | wo31 | 91536.41 | 24 | wo
FARM | ldl14 | 3990495.203 | 142 | ldl
NCONUML | wyk12 | 43139.17 | 24 | wyk
INDUSTRIAL | mwl15 | 15961047.4 | 1 | mwl
LIGHTING | bdl32 | 23514.52 | 1 | bdl
| rve12 | 15159.19 | 33 | rve
NCONUML | phm34 | 55440.25 | 17 | phm
COMMERCIAL | phm22 | 18761180.3018 | 732 | phm
RESIDENTL | cyn22 | 8715945.6121 | 2142 | cyn
FARM | fgy31 | 3345.68 | 2 | fgy
RESIDENTL | smr22 | 8159798.5324 | 1327 | smr
RESIDENTL | cyn23 | 7298806.6664 | 1621 | cyn
FARM | bdl42 | 2407309.4815 | 483 | bdl
| wyk23 | 31976.68 | 33 | wyk
INDUSTRIAL | rwn26 | 257525.5397 | 10 | rwn
NCONUML | bwn11 | 91006.47 | 23 | bwn
COMMERCIAL | cyn23 | 7883296.3431 | 299 | cyn
| moe15 | 19145.0797 | 16 | moe
| drn11 | 44271.4909 | 65 | drn
INDUSTRIAL | moe22 | 88009.47 | 4 | moe
NCONUML | mdg1 | 4146.1 | 9 | mdg
FARM | bra33 | 5568.67 | 1 | bra
LIGHTING | bwa22 | 75542.46 | 1 | bwa
NCONUML | hpk14 | 64164.68 | 20 | hpk
NCONUML |  | 262.3928 | 5 | #REF!
INDUSTRIAL | cln13 | 2016187.9013 | 2 | cln
FARM | ofr11 | 1184021.9516 | 51 | ofr
FARM | phm31 | 2011038.4476 | 90 | phm
NCONUML | elm21 | 62554.36 | 23 | elm
NCONUML | wt8 | 36862.33 | 14 | wt
NCONUML | cnr1 | 1922.85 | 2 | cnr
INDUSTRIAL | cre31 | 212230.18 | 2 | cre
COMMERCIAL | mfa34 | 8313764.4144 | 170 | mfa
INDUSTRIAL | tt5 | 637183.9506 | 23 | tt
INDUSTRIAL | llg14 | 1201432.9268 | 29 | llg
RESIDENTL | wo23 | 1549813.7708 | 361 | wo
| bwr23 | 25383.1703 | 47 | bwr
| sle11 | 3997.21 | 10 | sle
NCONUML | epg22 | 8538.04 | 7 | epg
NCONUML | bwr24 | 20744.02 | 14 | bwr
INDUSTRIAL | myt12 | 952524.23 | 20 | myt
| ftr23 | 53453.1274 | 33 | ftr
RESIDENTL | bra11 | 9331476.9371 | 2277 | bra
FARM | ldl13 | 3504918.0126 | 302 | ldl
| brt11 | 8693.81 | 14 | brt
INDUSTRIAL | phm31 | 91642.7039 | 2 | phm
COMMERCIAL | bdl43 | 22280533.2345 | 523 | bdl
FARM | moe23 | 4928404.5033 | 365 | moe
| klk21 | 7164.56 | 8 | klk
| wt7 | 8483.27 | 17 | wt
FARM | llg11 | 4501914.1562 | 365 | llg
LIGHTING | cf2 | 13221.322 | 1 | cf
| tgn31 | 23134.1673 | 13 | tgn
RESIDENTL | nla31 | 3471883.5329 | 742 | nla
COMMERCIAL | bdl31 | 6479518.62 | 206 | bdl
COMMERCIAL | smr23 | 799486.21 | 26 | smr
INDUSTRIAL | rve11 | 154936.16 | 21 | rve
RESIDENTL | bm8b33 | 130717.0048 | 17 | bmb
FARM | phi12 | 364625.9 | 40 | phi
INDUSTRIAL | klk22 | 5518.6 | 1 | klk
RESIDENTL | llg12 | 7619865.2998 | 1210 | llg
RESIDENTL | cln21 | 24090170.4832 | 5877 | cln
NCONUML | cpk11 | 17830.25 | 17 | cpk
COMMERCIAL | ruba22 | 3463594.5603 | 120 | ruba
NCONUML | brt22 | 9306.55 | 7 | brt
INDUSTRIAL | epg32 | 7635590.16 | 5 | epg
INDUSTRIAL | cln12 | 360384.55 | 1 | cln
COMMERCIAL | bwr13 | 10101102.0366 | 288 | bwr
COMMERCIAL | wo22 | 9017310.64 | 153 | wo
INDUSTRIAL | hpk24 | 9439809.63 | 31 | hpk
COMMERCIAL | cpk12 | 5057421.24 | 115 | cpk
| lyd14 | 55928.8081 | 17 | lyd
INDUSTRIAL | klo11 | 67703.26 | 1 | klo
RESIDENTL | ldl14 | 11349760.1474 | 1905 | ldl
LIGHTING | myt21 | 2294.9 | 1 | myt
RESIDENTL | rwn22 | 13452598.5118 | 2640 | rwn
COMMERCIAL | bm8b32 | 168652.4116 | 16 | bmb
INDUSTRIAL | bdl34 | 328519.77 | 31 | bdl
| tt12 | 16952.1045 | 5 | tt
RESIDENTL | wots24 | 6979604.5034 | 1172 | wots
INDUSTRIAL | wyk24 | 160679.33 | 16 | wyk
COMMERCIAL | klo12 | 12237846.22 | 9 | klo
RESIDENTL | wo33 | 232024.16 | 58 | wo
COMMERCIAL | bn24 | 3468313.5774 | 163 | bn
COMMERCIAL | lga12 | 9341312.33 | 61 | lga
| msd1 | 16071.3636 | 20 | msd
INDUSTRIAL | ofr24 | 300622.14 | 4 | ofr
INDUSTRIAL | bwn13 | 24333.45 | 4 | bwn
| tt1 | 26786.62 | 3 | tt
INDUSTRIAL | rwt31 | 22449174.23 | 3 | rwt
FARM | mfa14 | 28798.91 | 1 | mfa
| bwr32 | 10607.4826 | 52 | bwr
INDUSTRIAL | wn4 | 1120535.2101 | 54 | wn
RESIDENTL | bwr12 | 975012.274 | 199 | bwr
INDUSTRIAL | wgi24 | 1432383.73 | 33 | wgi
| llg13 | 135285.4952 | 24 | llg
| rwn34 | 10950.9 | 10 | rwn
FARM | elm34 | 16399.68 | 6 | elm
RESIDENTL | ruba12 | 12797333.4035 | 1890 | ruba
COMMERCIAL | hpk22 | 5875279.82 | 181 | hpk
| cln11 | 262675.9461 | 229 | cln
RESIDENTL | cf2 | 494427.3912 | 409 | cf
FARM | elm22 | 15544.2323 | 4 | elm
INDUSTRIAL | smg32 | 67645.78 | 1 | smg
FARM | bwa23 | 3495492.525 | 169 | bwa
NCONUML | phm24 | 66511.6 | 15 | phm
NCONUML | wgi23 | 35701.3 | 15 | wgi
NCONUML | epg35 | 18576.68 | 9 | epg
NCONUML | llg13 | 26801.83 | 12 | llg
LIGHTING | phi13 | 74566.47 | 1 | phi
| ldl24 | 28689.7774 | 48 | ldl
| bge11 | 41147.6131 | 30 | bge
RESIDENTL | ofr21 | 18456788.2346 | 4412 | ofr
INDUSTRIAL | ofr11 | 52339.71 | 6 | ofr
COMMERCIAL | nrn11 | 8254682.48 | 13 | nrn
FARM | moe15 | 1053275.4428 | 126 | moe
INDUSTRIAL | lyd12 | 15947.41 | 3 | lyd
INDUSTRIAL | wt10 | 5540.7 | 1 | wt
RESIDENTL | rwt21 | 965731.93 | 282 | rwt
FARM | wo13 | 51683.13 | 6 | wo
INDUSTRIAL | epg34 | 25722.81 | 2 | epg
COMMERCIAL | lys36 | 31611.41 | 1 | lys
RESIDENTL | wn6 | 17451542.0984 | 3750 | wn
NCONUML | hpk12 | 23613.79 | 7 | hpk
INDUSTRIAL | ruba24 | 189283.4035 | 13 | ruba
| nrn12 | 36108.6 | 9 | nrn
NCONUML | nla32 | 30069.03 | 18 | nla
COMMERCIAL | bm8b31 | 174913.9253 | 14 | bmb
| wo22 | 26321.2427 | 38 | wo
INDUSTRIAL | fgy31 | 4952.61 | 1 | fgy
RESIDENTL | cln14 | 25051991.2109 | 8311 | cln
RESIDENTL | lga24 | 3807672.9803 | 653 | lga
RESIDENTL | bra31 | 2624204.8049 | 649 | bra
COMMERCIAL | cln21 | 7282112.3749 | 104 | cln
COMMERCIAL | ftr23 | 8984637.4811 | 336 | ftr
RESIDENTL | klo13 | 97850.5847 | 89 | klo
INDUSTRIAL | ofr14 | 250.62 | 1 | ofr
FARM | mwl24 | 966080.4815 | 75 | mwl
NCONUML | bdl41 | 86032.0652 | 28 | bdl
INDUSTRIAL | epg13 | 201122.3196 | 20 | epg
COMMERCIAL | tgn23 | 6173474.1124 | 95 | tgn
| moe12 | 11374.0239 | 16 | moe
INDUSTRIAL | drn11 | 8297.91 | 2 | drn
| wn4 | 46461.2191 | 29 | wn
NCONUML | wgl13 | 85005.64 | 23 | wgl
INDUSTRIAL | ftr22 | 264831.3749 | 23 | ftr
NCONUML | mjg11 | 5653.43 | 3 | mjg
RESIDENTL | klo12 | 526.2 | 1 | klo
COMMERCIAL | cln11 | 18408618.7138 | 182 | cln
NCONUML | wo13 | 11132.69 | 4 | wo
COMMERCIAL | yn38 | 28127.08 | 5 | yn
NCONUML | mwl24 | 19701.6 | 5 | mwl
RESIDENTL | wots12 | 7880580.6899 | 1786 | wots
COMMERCIAL | tgn43 | 5598797.62 | 126 | tgn
NCONUML | mfa23 | 6277.17 | 3 | mfa
NCONUML | bra32 | 63005.82 | 38 | bra
FARM | bdl34 | 247623.03 | 51 | bdl
INDUSTRIAL | wn5 | 6299826.69 | 33 | wn
| mby13 | 155.9226 | 1 | mby
FARM | ofr23 | 2419763.5413 | 305 | ofr
NCONUML | cre22 | 86458.6773 | 42 | cre
NCONUML | hpk23 | 84001.53 | 23 | hpk
RESIDENTL | bra24 | 8260262.5707 | 1824 | bra
| cyn14 | 12637.7523 | 26 | cyn
LIGHTING | wgl11 | 2443513.25 | 2 | wgl
NCONUML | wgi24 | 69610.83 | 24 | wgi
COMMERCIAL | klo14 | 11961206.944 | 269 | klo
FARM | drn14 | 379625.3327 | 36 | drn
RESIDENTL | bwr22 | 1941843.629 | 510 | bwr
| llg14 | 42684.6726 | 22 | llg
INDUSTRIAL | drn21 | 709809.96 | 3 | drn
INDUSTRIAL | tgn42 | 199383.97 | 5 | tgn
RESIDENTL | sle32 | 6677118.757 | 1350 | sle
RESIDENTL | myt12 | 14552002.0991 | 2380 | myt
FARM | myt21 | 821475.54 | 124 | myt
| bn11 | 39921.12 | 40 | bn
NCONUML | mby12 | 15769.2 | 4 | mby
NCONUML | bdl44 | 1602.59 | 5 | bdl
COMMERCIAL | tt12 | 10810239.5174 | 467 | tt
NCONUML | wn7 | 7884.6 | 2 | wn
| bdl34 | 14430.17 | 36 | bdl
RESIDENTL | lyd11 | 11014119.7855 | 2574 | lyd
FARM | wyk23 | 2329152.6841 | 202 | wyk
| epg23 | 66262.7623 | 20 | epg
RESIDENTL | rwt32 | 15157646.1346 | 3808 | rwt
RESIDENTL | cre31 | 23125994.5084 | 5990 | cre
FARM | bn11 | 9012293.1298 | 1372 | bn
COMMERCIAL |  | 2470964.7554 | 79 | #REF!
INDUSTRIAL | kms11 | 3849512.37 | 9 | kms
RESIDENTL | sle31 | 15232222.0022 | 4728 | sle
RESIDENTL | myt11 | 3230941.4261 | 365 | myt
| wyk12 | 33744.4845 | 17 | wyk
| lga11 | 13750.1489 | 25 | lga
COMMERCIAL | cre33 | 14716025.8299 | 132 | cre
RESIDENTL | trc01 | 404888.8876 | 85 | trc
| moe25 | 10579.3743 | 23 | moe
NCONUML | msd1 | 8725.66 | 9 | msd
RESIDENTL | mwl14 | 1637810.9082 | 178 | mwl
FARM | wn5 | 10157746.9699 | 1090 | wn
INDUSTRIAL | bwr33 | 13101695.07 | 41 | bwr
NCONUML | ofr24 | 72292.73 | 18 | ofr
| mdg1 | 5594.13 | 4 | mdg
FARM | wgi33 | 86057.74 | 7 | wgi
RESIDENTL | rwt22 | 12512450.4989 | 3066 | rwt
RESIDENTL | cnr2 | 3844076.3719 | 1054 | cnr
| hpk14 | 17565.23 | 35 | hpk
NCONUML | drn23 | 37389.78 | 20 | drn
RESIDENTL | tgn44 | 11943542.7304 | 2804 | tgn
| tgn42 | 0 | 1 | tgn
NCONUML | rwt22 | 27503.296 | 22 | rwt
FARM | mwl16 | 172184.54 | 14 | mwl
COMMERCIAL | nla34 | 1413700.5844 | 93 | nla
| epg22 | 2049.9261 | 2 | epg
FARM | tgn41 | 3728231.4432 | 423 | tgn
COMMERCIAL | lga23 | 3382991.9134 | 119 | lga
NCONUML | sle31 | 61055.23 | 20 | sle
NCONUML | tgn44 | 66469.79 | 20 | tgn
| phm24 | 18272.6834 | 34 | phm
RESIDENTL | hpk11 | 16523367.4098 | 4141 | hpk
| hpk13 | 40054.7485 | 22 | hpk
| bwr24 | 10180.34 | 28 | bwr
COMMERCIAL | bdl33 | 34051046.7333 | 257 | bdl
COMMERCIAL | wt9 | 7035668.1433 | 128 | wt
NCONUML | wt15 | 16005.53 | 14 | wt
FARM | ruba24 | 730484.142 | 55 | ruba
NCONUML | cpk23 | 20021.69 | 18 | cpk
INDUSTRIAL | mwl21 | 320021.87 | 5 | mwl
COMMERCIAL | hpk23 | 12064171.7331 | 206 | hpk
INDUSTRIAL | wt11 | 2563605.84 | 2 | wt
RESIDENTL | wt15 | 8580853.2399 | 1947 | wt
| elm21 | 24345.52 | 16 | elm
INDUSTRIAL | mwl16 | 183545.9668 | 9 | mwl
FARM | rve13 | 9637.99 | 1 | rve
NCONUML | drn22 | 69938.3 | 27 | drn
NCONUML | bdl31 | 70697.58 | 29 | bdl
NCONUML | bwa24 | 1320.25 | 1 | bwa
COMMERCIAL | mwl23 | 10773058.8537 | 154 | mwl
COMMERCIAL | elm23 | 5093994.3825 | 95 | elm
FARM | smr23 | 1078615.6398 | 156 | smr
| cpk11 | 37835.6667 | 47 | cpk
INDUSTRIAL | bra14 | 14750.52 | 4 | bra
RESIDENTL | rwn33 | 5693275.4596 | 1153 | rwn
| bn22 | 41634.09 | 21 | bn
INDUSTRIAL | tt2 | 11531135.8238 | 100 | tt
INDUSTRIAL | wt12 | 3871876.0911 | 67 | wt
INDUSTRIAL | mwl22 | 292678.42 | 8 | mwl
RESIDENTL | bn23 | 8695284.412 | 1665 | bn
COMMERCIAL | cyn11 | 9621618.8569 | 233 | cyn
| cyn21 | 22400.14 | 28 | cyn
INDUSTRIAL | mjg11 | 1321804.29 | 13 | mjg
INDUSTRIAL | cf2 | 1970.494 | 2 | cf
RESIDENTL | tt5 | 6560032.4165 | 1633 | tt
COMMERCIAL | smr14 | 6818307.6657 | 239 | smr
COMMERCIAL | smg33 | 1348313.99 | 14 | smg
RESIDENTL | rwt15 | 11066767.0768 | 2454 | rwt
COMMERCIAL | cre32 | 14440881.1645 | 427 | cre
INDUSTRIAL | smr24 | 4639865.5557 | 45 | smr
COMMERCIAL | fgy23 | 10185283.97 | 98 | fgy
COMMERCIAL | hpk11 | 3476478.711 | 53 | hpk
| cre32 | 19011.64 | 13 | cre
NCONUML | wgl23 | 12760.41 | 6 | wgl
COMMERCIAL | nrn15 | 84419.81 | 3 | nrn
NCONUML | moe15 | 22748.39 | 11 | moe
RESIDENTL | tt12 | 86039.86 | 6 | tt
RESIDENTL | cyn31 | 8632445.7043 | 2077 | cyn
RESIDENTL | wgl24 | 16633542.8094 | 2715 | wgl
COMMERCIAL | wgi22 | 6881286.006 | 159 | wgi
INDUSTRIAL | smr13 | 992080.85 | 26 | smr
NCONUML | cpk12 | 17033.61 | 10 | cpk
NCONUML | ftr21 | 16597.26 | 11 | ftr
FARM | mwl12 | 18529.37 | 2 | mwl
INDUSTRIAL | epg33 | 1129768.4897 | 4 | epg
| wyk13 | 9658.4809 | 15 | wyk
LIGHTING | trc01 | 669938.2281 | 2 | trc
FARM | hpk13 | 2305.94 | 1 | hpk
RESIDENTL | tt6 | 19150788.3328 | 4695 | tt
FARM | tgn31 | 5369095.0164 | 562 | tgn
NCONUML | wgl24 | 11028.97 | 10 | wgl
INDUSTRIAL | brt11 | 82545.9018 | 12 | brt
LIGHTING | mby11 | 10728.24 | 1 | mby
NCONUML | myt21 | 24178.1 | 12 | myt
| wt10 | 6115.9374 | 5 | wt
RESIDENTL | bge12 | 9796026.1467 | 1789 | bge
FARM | myt11 | 2640136.7565 | 257 | myt
NCONUML | cyn11 | 21168.08 | 13 | cyn
INDUSTRIAL |  | 942329979.1078 | 12 | #REF!
INDUSTRIAL | elm34 | 168803.0667 | 15 | elm
| brt22 | 30486.3216 | 18 | brt
INDUSTRIAL | epg11 | 6777.42 | 2 | epg
RESIDENTL | elm34 | 19825611.7814 | 4189 | elm
COMMERCIAL | sle13 | 974523.8832 | 109 | sle
INDUSTRIAL | lga13 | 207007.5439 | 9 | lga
RESIDENTL | mwl23 | 3618535.6291 | 812 | mwl
| fgy14 | 28887.99 | 26 | fgy
COMMERCIAL | mby13 | 2521770.2974 | 71 | mby
| lga12 | 14720.56 | 12 | lga
RESIDENTL | cpk12 | 17343162.547 | 2927 | cpk
COMMERCIAL | wt5 | 19785711.5258 | 118 | wt
INDUSTRIAL | drn24 | 4643890.64 | 3 | drn
FARM | drn21 | 13254.24 | 1 | drn
NCONUML | mwl11 | 360.93 | 3 | mwl
RESIDENTL | epg34 | 15669683.4078 | 3862 | epg
NCONUML | wt10 | 27658.61 | 16 | wt
LIGHTING | rwt14 | 962126.36 | 3 | rwt
COMMERCIAL | drn23 | 5472888.3558 | 161 | drn
LIGHTING | bwn11 | 6340546.01 | 1 | bwn
INDUSTRIAL | sfs1 | 80102.39 | 5 | sfs
COMMERCIAL | phm34 | 4610839.9937 | 66 | phm
COMMERCIAL | mfa31 | 3803351.87 | 100 | mfa
INDUSTRIAL | rwt25 | 2203508.65 | 42 | rwt
| bwa22 | 41045.3074 | 24 | bwa
FARM | smr13 | 139441.5096 | 27 | smr
NCONUML | phi12 | 84007.84 | 24 | phi
| fgy21 | 10377.87 | 9 | fgy
NCONUML | rwt15 | 44056.974 | 28 | rwt
LIGHTING | nla34 | 5187.52 | 1 | nla
RESIDENTL | sfs1 | 6449039.4989 | 958 | sfs
RESIDENTL | msd4 | 16354350.3097 | 2395 | msd
INDUSTRIAL | phm33 | 724516.58 | 21 | phm
COMMERCIAL | wgl14 | 59932538.6 | 1 | wgl
COMMERCIAL | rwt31 | 3904134.109 | 54 | rwt
RESIDENTL | wt5 | 5466545.168 | 1335 | wt
FARM | ftr22 | 3872176.8459 | 271 | ftr
| wn5 | 51237.831 | 23 | wn
INDUSTRIAL | kms12 | 880994.04 | 26 | kms
NCONUML | rwt31 | 27889.28 | 18 | rwt
RESIDENTL | elm22 | 20622579.4478 | 3120 | elm
| bn24 | 7126.586 | 9 | bn
FARM | wots11 | 7572710.4051 | 689 | wots
INDUSTRIAL | myt11 | 122662.09 | 11 | myt
NCONUML | bdl32 | 81716.25 | 38 | bdl
NCONUML | cyn33 | 39860.39 | 20 | cyn
| lga13 | 7900.07 | 12 | lga
COMMERCIAL | wn7 | 705796.26 | 31 | wn
RESIDENTL | tgn23 | 12995258.1614 | 2157 | tgn
RESIDENTL | wgl12 | 18309192.1093 | 3011 | wgl
NCONUML | drn14 | 58816.42 | 20 | drn
INDUSTRIAL | tt9 | 1853761.73 | 4 | tt
RESIDENTL | kms12 | 23913269.0041 | 4277 | kms
COMMERCIAL | wgi33 | 13737748.8552 | 364 | wgi
COMMERCIAL | phm21 | 28428865.0993 | 838 | phm
FARM | sle32 | 5441049.7096 | 310 | sle
NCONUML | cyn32 | 58907.16 | 38 | cyn
INDUSTRIAL | msd2 | 165834.72 | 18 | msd
COMMERCIAL | bwr23 | 26845428.111 | 233 | bwr
RESIDENTL | msd2 | 5810770.2828 | 1153 | msd
FARM | klk11 | 2014936.8264 | 177 | klk
| wots12 | 13459.1171 | 22 | wots
INDUSTRIAL | rwn24 | 4339629.96 | 13 | rwn
INDUSTRIAL | tgn41 | 1853911.3546 | 62 | tgn
COMMERCIAL | smg32 | 6595824.87 | 22 | smg
| wgi34 | 86239.94 | 15 | wgi
RESIDENTL | bn22 | 13286130.4589 | 3118 | bn
RESIDENTL | mfa31 | 9237847.4317 | 2206 | mfa
COMMERCIAL | wgi34 | 9571334.08 | 60 | wgi
RESIDENTL | mdi1 | 176577.17 | 31 | mdi
NCONUML | rwn31 | 16738.19 | 15 | rwn
INDUSTRIAL | drn13 | 239296.9 | 11 | drn
INDUSTRIAL | bdl43 | 306419.52 | 21 | bdl
NCONUML | wo23 | 56204.51 | 16 | wo
COMMERCIAL | ftr21 | 2804675.8206 | 100 | ftr
COMMERCIAL | bwa23 | 206762.2501 | 23 | bwa
NCONUML | mfa21 | 28416.84 | 12 | mfa
| cln23 | 52144.7804 | 85 | cln
RESIDENTL | rve11 | 2276471.0008 | 508 | rve
COMMERCIAL | ofr24 | 6649904.8426 | 113 | ofr
NCONUML | phi13 | 105028.33 | 33 | phi
FARM | smg22 | 25054.15 | 4 | smg
FARM | bwn11 | 18419.1 | 1 | bwn
INDUSTRIAL | epg31 | 360181.3871 | 31 | epg
COMMERCIAL | fgy14 | 7872993.2117 | 231 | fgy
| ldl11 | 24480.7 | 22 | ldl
INDUSTRIAL | wgl24 | 939120.3004 | 39 | wgl
| phm22 | 31542.7748 | 10 | phm
COMMERCIAL | moe15 | 2469270.3666 | 172 | moe
| cnr3 | 100.0469 | 1 | cnr
RESIDENTL | bwn12 | 4456239.3509 | 1013 | bwn
COMMERCIAL | mwl24 | 5791496.4979 | 78 | mwl
COMMERCIAL | wo13 | 2493976.37 | 46 | wo
RESIDENTL | elm25 | 10534980.5572 | 2009 | elm
RESIDENTL | phm32 | 14466986.7977 | 3288 | phm
COMMERCIAL | ofr11 | 14130002.2904 | 224 | ofr
INDUSTRIAL | bge13 | 1057475.88 | 11 | bge
RESIDENTL | ofr22 | 7907197.5875 | 2174 | ofr
INDUSTRIAL | lga22 | 745287.81 | 44 | lga
FARM | hpk22 | 33600.65 | 5 | hpk
COMMERCIAL | epg23 | 63543126.9632 | 711 | epg
NCONUML | epg34 | 29379.47 | 21 | epg
| mwl23 | 14018.9088 | 10 | mwl
FARM | lyd14 | 350081.37 | 31 | lyd
| elm33 | 18371.0537 | 30 | elm
RESIDENTL | bwn11 | 14758921.2622 | 2984 | bwn
| cyn33 | 33636.86 | 37 | cyn
INDUSTRIAL | ldl13 | 1566146.5513 | 31 | ldl
NCONUML | smg32 | 19512.15 | 10 | smg
NCONUML | lga21 | 24931.49 | 9 | lga
RESIDENTL | mfa34 | 6438005.323 | 995 | mfa
COMMERCIAL | lga22 | 10229963.6597 | 340 | lga
COMMERCIAL | wgi31 | 4363035.5887 | 128 | wgi
| wt9 | 17175.83 | 21 | wt
INDUSTRIAL | mfa21 | 1292894.4886 | 57 | mfa
FARM | wgi32 | 343056.5273 | 19 | wgi
COMMERCIAL | bge21 | 44944.8 | 1 | bge
INDUSTRIAL | elm26 | 46289.86 | 5 | elm
NCONUML | msd4 | 12187.83 | 6 | msd
COMMERCIAL | bra21 | 14789918.5926 | 289 | bra
| cpk22 | 7305.07 | 12 | cpk
NCONUML | phm32 | 76324.09 | 20 | phm
NCONUML | sfs1 | 44865.78 | 10 | sfs
COMMERCIAL | lyd13 | 6072257.17 | 42 | lyd
FARM | cyn33 | 36456.98 | 4 | cyn
NCONUML | phm21 | 71428.0533 | 24 | phm
COMMERCIAL | sle32 | 5434267.6149 | 190 | sle
NCONUML | smg31 | 21751.86 | 17 | smg
NCONUML | wots11 | 25057.91 | 11 | wots
RESIDENTL | tgn43 | 15724147.9465 | 3608 | tgn
INDUSTRIAL | cyn21 | 9259443.95 | 23 | cyn
INDUSTRIAL | bn23 | 1923467.13 | 19 | bn
NCONUML | nrn14 | 79150.17 | 17 | nrn
NCONUML | cyn22 | 32483.16 | 10 | cyn
NCONUML | wgl12 | 47271.49 | 20 | wgl
COMMERCIAL | phm24 | 600129.57 | 25 | phm
NCONUML | lga11 | 25837.14 | 8 | lga
NCONUML | tgn41 | 7415.11 | 5 | tgn
RESIDENTL | wgl11 | 17118670.1537 | 3818 | wgl
RESIDENTL | wots11 | 15871220.8415 | 2910 | wots
| rwn31 | 40233.5106 | 27 | rwn
COMMERCIAL | elm32 | 8171019.0636 | 263 | elm
FARM | mby11 | 1335559.7721 | 187 | mby
INDUSTRIAL | mwl25 | 33119.15 | 8 | mwl
FARM | rwn26 | 5055.63 | 2 | rwn
| nla34 | 8234.98 | 10 | nla
RESIDENTL |  | 349105.8277 | 492 | #REF!
FARM | epg13 | 82815.8863 | 12 | epg
| wyk24 | 32167.14 | 30 | wyk
FARM | sle11 | 16862.17 | 6 | sle
COMMERCIAL | bm8b33 | 3349.12 | 2 | bmb
RESIDENTL | smg21 | 17914575.4009 | 3718 | smg
INDUSTRIAL | bdl42 | 622534.62 | 24 | bdl
| yn38 | 7519.7419 | 1 | yn
| phi13 | 28221.5917 | 27 | phi
| epg14 | 9258.9052 | 38 | epg
FARM | nla31 | 1791184.5035 | 140 | nla
INDUSTRIAL | wgi33 | 1188063.8119 | 37 | wgi
LIGHTING | phm33 | 4303153.65 | 2 | phm
RESIDENTL | phm33 | 12878778.4238 | 2134 | phm
COMMERCIAL | wgl23 | 3870974.8784 | 252 | wgl
NCONUML | wt5 | 58508.56 | 14 | wt
NCONUML | bwn14 | 81385.02 | 37 | bwn
NCONUML | mfa31 | 49958.93 | 14 | mfa
COMMERCIAL | bra12 | 23355928.37 | 122 | bra
NCONUML | wt13 | 98966.19 | 41 | wt
COMMERCIAL | klo24 | 13267963.2484 | 244 | klo
COMMERCIAL | bge12 | 6262328.83 | 64 | bge
COMMERCIAL | wn4 | 10511680.2174 | 332 | wn
INDUSTRIAL | tt6 | 2940006.87 | 14 | tt
FARM | cln13 | 4519.0334 | 1 | cln
RESIDENTL | bwa23 | 1839261.5711 | 259 | bwa
RESIDENTL | smr12 | 601661.7559 | 102 | smr
NCONUML | bra31 | 17155.48 | 11 | bra
FARM | cln22 | 84599.56 | 6 | cln
RESIDENTL | moe23 | 10757204.18 | 1872 | moe
FARM | bn23 | 4995698.9571 | 709 | bn
INDUSTRIAL | bwr12 | 7576207.2428 | 317 | bwr
COMMERCIAL | elm33 | 8652520.7547 | 229 | elm
RESIDENTL | tgn12 | 769554.192 | 239 | tgn
NCONUML | bn23 | 5729.17 | 9 | bn
| cyn11 | 35169.6447 | 13 | cyn
INDUSTRIAL | wots12 | 5742170.47 | 22 | wots
INDUSTRIAL | llg12 | 8080777.31 | 18 | llg
NCONUML | ofr14 | 11958.45 | 3 | ofr
RESIDENTL | rwn34 | 11161403.5989 | 1490 | rwn
RESIDENTL | fgy12 | 975691.3435 | 398 | fgy
COMMERCIAL | wyk24 | 11852940.7836 | 290 | wyk
COMMERCIAL | smr12 | 1199230.8 | 20 | smr
INDUSTRIAL | wgl11 | 590499.13 | 17 | wgl
INDUSTRIAL | moe13 | 8896507.14 | 13 | moe
INDUSTRIAL | wots11 | 14616083.73 | 22 | wots
NCONUML | epg13 | 4325.18 | 2 | epg
NCONUML | bn22 | 72789.04 | 38 | bn
RESIDENTL | bwr23 | 15381612.1105 | 3589 | bwr
NCONUML | cln13 | 19538.3161 | 10 | cln
COMMERCIAL | bwa24 | 4350900.07 | 4 | bwa
COMMERCIAL | bwr32 | 11258727.4704 | 251 | bwr
RESIDENTL | bra32 | 8710928.5985 | 2041 | bra
FARM | klo14 | 681766.459 | 92 | klo
INDUSTRIAL | tt7 | 9353368.9205 | 125 | tt
RESIDENTL | wo11 | 815896.564 | 156 | wo
LIGHTING | mwl24 | 803944.3 | 2 | mwl
COMMERCIAL | bwr24 | 7860784.794 | 262 | bwr
COMMERCIAL | drn14 | 5284276.4061 | 147 | drn
NCONUML | hpk24 | 27055.52 | 10 | hpk
| cyn32 | 34865.18 | 48 | cyn
| bra23 | 7974.72 | 25 | bra
RESIDENTL | rve13 | 16767421.4281 | 3587 | rve
COMMERCIAL | bwn13 | 11531398.8601 | 263 | bwn
FARM | cln23 | 76487.94 | 5 | cln
NCONUML | ruba24 | 1482.28 | 4 | ruba
COMMERCIAL | msd1 | 4448954.738 | 126 | msd
| phm31 | 2299.25 | 4 | phm
LIGHTING | wn1 | 677520.74 | 1 | wn
COMMERCIAL | wt8 | 2125517.5597 | 71 | wt
RESIDENTL | bdl33 | 5101200.3632 | 906 | bdl
COMMERCIAL | rwt21 | 33203170.5825 | 281 | rwt
FARM |  | 15223.9488 | 53 | #REF!
| fgy13 | 16173.63 | 19 | fgy
| wt11 | 14907.843 | 20 | wt
RESIDENTL | mwl24 | 4259131.5949 | 729 | mwl
INDUSTRIAL | bwn12 | 375603.57 | 33 | bwn
| lyd12 | 10355.6 | 16 | lyd
| lyd13 | 31235.27 | 24 | lyd
| elm32 | 28931.8643 | 22 | elm
RESIDENTL | ldl13 | 20183081.1078 | 3515 | ldl
COMMERCIAL | epg14 | 4722560.1631 | 66 | epg
FARM | epg32 | 616929.8369 | 16 | epg
| smg23 | 6841.4304 | 12 | smg
NCONUML | mwl16 | 31954.29 | 10 | mwl
COMMERCIAL | ofr22 | 3955299.41 | 63 | ofr
FARM | wgl24 | 9990463.449 | 886 | wgl
COMMERCIAL | llg14 | 8402501.0583 | 280 | llg
COMMERCIAL | wgi24 | 3234685.3433 | 136 | wgi
FARM | cnr3 | 47812.597 | 17 | cnr
| epg33 | 55263.0616 | 6 | epg
INDUSTRIAL | bra24 | 1115020.317 | 14 | bra
NCONUML | wgi33 | 84992.31 | 23 | wgi
FARM | rwt15 | 1849.17 | 1 | rwt
RESIDENTL | ldl12 | 620798.3677 | 119 | ldl
INDUSTRIAL | bwr22 | 8606432.4227 | 334 | bwr
FARM | cf2 | 2033.193 | 1 | cf
NCONUML | klo14 | 36515.49 | 28 | klo
INDUSTRIAL | trc01 | 31629.57 | 2 | trc
RESIDENTL | lga21 | 9412760.8279 | 1623 | lga
RESIDENTL | wt13 | 15834142.0313 | 3223 | wt
RESIDENTL | cyn13 | 3260017.5153 | 858 | cyn
INDUSTRIAL | ofr21 | 138382.59 | 9 | ofr
NCONUML | sle32 | 22407.43 | 13 | sle
COMMERCIAL | lyd12 | 210380 | 9 | lyd
NCONUML | wyk23 | 87622.06 | 45 | wyk
| fgy33 | 11652.67 | 18 | fgy
INDUSTRIAL | hpk22 | 98414.21 | 14 | hpk
NCONUML | sle11 | 59204.61 | 19 | sle
RESIDENTL | bwr13 | 20902397.8318 | 4170 | bwr
COMMERCIAL | rwn34 | 3999387.7688 | 144 | rwn
| hpk22 | 19671.58 | 41 | hpk
FARM | klk22 | 332413.14 | 10 | klk
INDUSTRIAL | wn1 | 2988984.92 | 20 | wn
NCONUML | rwn26 | 27156.61 | 25 | rwn
| bwr33 | 13120.641 | 3 | bwr
NCONUML | mby11 | 20114.34 | 7 | mby
RESIDENTL | smg33 | 11198068.0634 | 2626 | smg
FARM | bn12 | 813334.585 | 146 | bn
FARM | bdl32 | 1026406.0127 | 170 | bdl
FARM | drn24 | 15422429 | 2 | drn
LIGHTING | cre21 | 378603.77 | 3 | cre
RESIDENTL | smg32 | 834640.09 | 219 | smg
| wt12 | 39199.7023 | 19 | wt
FARM | bwn14 | 804408.7 | 76 | bwn
NCONUML | bwr33 | 16865.43 | 3 | bwr
INDUSTRIAL | rwn22 | 12871.85 | 4 | rwn
NCONUML | drn11 | 63307.01 | 20 | drn
INDUSTRIAL | mwl13 | 228128.43 | 11 | mwl
COMMERCIAL | elm22 | 6567142.5918 | 154 | elm
FARM | trc01 | 521142.3328 | 100 | trc
COMMERCIAL | rwt14 | 11855990.576 | 301 | rwt
INDUSTRIAL | sle14 | 1780526.4437 | 64 | sle
RESIDENTL | smr24 | 17064871.7804 | 2952 | smr
FARM | bwa22 | 1586063.9755 | 254 | bwa
NCONUML | tt4 | 37478.54 | 17 | tt
| tt9 | 28146.8116 | 74 | tt
COMMERCIAL | epg34 | 4040655.8363 | 65 | epg
FARM | nrn11 | 7816.07 | 2 | nrn
LIGHTING | cpk23 | 1632459.3 | 1 | cpk
RESIDENTL | fgy31 | 4476808.4262 | 913 | fgy
COMMERCIAL | fgy33 | 6399813.6929 | 132 | fgy
| cnr2 | 20535.9245 | 15 | cnr
INDUSTRIAL | sle32 | 10933678.58 | 25 | sle
| bra13 | 120577.89 | 18 | bra
RESIDENTL | wgi23 | 12118480.0079 | 2685 | wgi
INDUSTRIAL | wn6 | 922850.6842 | 19 | wn
LIGHTING | tgn44 | 752.53 | 1 | tgn
RESIDENTL | wt8 | 8250779.9392 | 1851 | wt
COMMERCIAL | moe25 | 5695010.3572 | 176 | moe
FARM | wgi34 | 4315044.5216 | 374 | wgi
INDUSTRIAL | fgy32 | 667572.7217 | 61 | fgy
NCONUML | wo32 | 55386.46 | 14 | wo
INDUSTRIAL | lys36 | 1267258.48 | 1 | lys
| bn12 | 10728.35 | 13 | bn
NCONUML | brt11 | 10828.27 | 7 | brt
| drn21 | 27694.76 | 39 | drn
| drn24 | 16030.7 | 26 | drn
RESIDENTL | cpk23 | 11646034.7633 | 2466 | cpk
RESIDENTL | wots13 | 7948103.7952 | 1344 | wots
FARM | wgl23 | 3908847.1376 | 390 | wgl
COMMERCIAL | wyk13 | 4417313.7071 | 191 | wyk
NCONUML | klk21 | 10664.54 | 6 | klk
INDUSTRIAL | smg22 | 31514.93 | 2 | smg
RESIDENTL | wgi22 | 12719214.8315 | 3088 | wgi
| cpk13 | 49314.0333 | 41 | cpk
COMMERCIAL | bdl41 | 11311068.2286 | 367 | bdl
NCONUML | nrn12 | 43208.48 | 18 | nrn
RESIDENTL | fgy23 | 5177398.3937 | 1023 | fgy
NCONUML | brt21 | 3240.29 | 5 | brt
NCONUML | tgn31 | 2100.01 | 7 | tgn
RESIDENTL | mjg11 | 6256821.3625 | 1064 | mjg
INDUSTRIAL | lga24 | 175905.212 | 21 | lga
COMMERCIAL | moe21 | 6644337.36 | 291 | moe
INDUSTRIAL | bwn14 | 326743.47 | 17 | bwn
INDUSTRIAL | phm22 | 15545673.5732 | 29 | phm
LIGHTING | klo24 | 2201282.63 | 3 | klo
FARM | epg12 | 13782.33 | 2 | epg
INDUSTRIAL | cln14 | 247.5387 | 1 | cln
FARM | bge13 | 383352.554 | 75 | bge
NCONUML | bra14 | 25509.54 | 26 | bra
RESIDENTL | fgy24 | 17189073.2659 | 3574 | fgy
NCONUML | lyd14 | 37348.84 | 18 | lyd
FARM | fgy21 | 91303 | 9 | fgy
INDUSTRIAL | elm24 | 6476.78 | 2 | elm
FARM | bra24 | 985.88 | 1 | bra
COMMERCIAL | ldl24 | 1420329.0926 | 55 | ldl
INDUSTRIAL | wots24 | 329358.8434 | 32 | wots
| moe13 | 6325.43 | 5 | moe
COMMERCIAL | cyn14 | 5422735.5047 | 221 | cyn
LIGHTING | smg21 | 4640189.26 | 4 | smg
COMMERCIAL | tgn42 | 24454733.755 | 420 | tgn
INDUSTRIAL | lga14 | 502652.15 | 16 | lga
INDUSTRIAL | cre33 | 377497.19 | 17 | cre
FARM | ldl11 | 223383.36 | 16 | ldl
INDUSTRIAL | bn24 | 28582582.13 | 34 | bn
COMMERCIAL | tt1 | 14308038.8686 | 155 | tt
| wn3 | 30735.58 | 33 | wn
NCONUML | ldl21 | 10778.31 | 7 | ldl
NCONUML | wt6 | 188781.23 | 35 | wt
RESIDENTL | elm23 | 20356024.4153 | 3325 | elm
COMMERCIAL | drn11 | 4003224.2127 | 79 | drn
COMMERCIAL | bra34 | 7850026.49 | 9 | bra
FARM | cyn32 | 3133.97 | 2 | cyn
FARM | cpk23 | 18946.87 | 2 | cpk
FARM | wt15 | 5251.96 | 1 | wt
NCONUML | wgi32 | 95036.63 | 31 | wgi
COMMERCIAL | phm32 | 13343791.1884 | 221 | phm
COMMERCIAL | epg22 | 38007492.3668 | 89 | epg
INDUSTRIAL | wgl15 | 1553419.6108 | 26 | wgl
FARM | phm33 | 7138587.5126 | 545 | phm
LIGHTING | bra32 | 1301740.84 | 1 | bra
COMMERCIAL | bra22 | 30448240 | 1 | bra
COMMERCIAL | msd4 | 11090376.2999 | 395 | msd
COMMERCIAL | lyd14 | 7038791.6959 | 51 | lyd
| phi12 | 701365.4285 | 34 | phi
| nrn11 | 5120.38 | 9 | nrn
INDUSTRIAL | smg21 | 777155.28 | 5 | smg
NCONUML | nla31 | 5002.08 | 5 | nla
RESIDENTL | wyk13 | 19583843.7522 | 3346 | wyk
RESIDENTL | tgn41 | 6800482.2089 | 1104 | tgn
COMMERCIAL | fgy34 | 7285642.6158 | 201 | fgy
FARM | wgl11 | 5210774.8775 | 355 | wgl
FARM | tgn11 | 616949.6887 | 82 | tgn
NCONUML | wn5 | 5268.61 | 9 | wn
NCONUML | bdl42 | 6088.6 | 9 | bdl
INDUSTRIAL | hpk23 | 515987.93 | 6 | hpk
FARM | tgn44 | 47621.17 | 6 | tgn
| smr13 | 35140.976 | 19 | smr
| wgi31 | 18377.08 | 37 | wgi
NCONUML | bwr34 | 85519.21 | 30 | bwr
| bdl32 | 24365.9844 | 40 | bdl
COMMERCIAL | fgy13 | 5672167.28 | 57 | fgy
INDUSTRIAL | sle31 | 621920.2305 | 85 | sle
NCONUML | cyn23 | 72679.67 | 24 | cyn
NCONUML | hpk22 | 92149.17 | 38 | hpk
RESIDENTL | cre23 | 13902510.3441 | 3180 | cre
COMMERCIAL | lga21 | 4415159.211 | 179 | lga
| cre33 | 51988.0123 | 70 | cre
INDUSTRIAL | bra32 | 800790.5812 | 33 | bra
| rwn26 | 43959.1499 | 36 | rwn
NCONUML | ftr22 | 27457.1971 | 11 | ftr
FARM | cyn23 | 28738.28 | 3 | cyn
FARM | wn2 | 2722540.844 | 262 | wn
FARM | wots25 | 1192605.1156 | 155 | wots
COMMERCIAL | lga11 | 2601951.4442 | 115 | lga
COMMERCIAL | cnr1 | 836269.15 | 40 | cnr
RESIDENTL | cre22 | 15737441.9951 | 3931 | cre
RESIDENTL | cyn24 | 3227627.7482 | 729 | cyn
| drn14 | 42739.5968 | 43 | drn
NCONUML | wgi34 | 240.62 | 2 | wgi
COMMERCIAL | mdi1 | 200221.43 | 4 | mdi
LIGHTING | lga22 | 290997.27 | 1 | lga
RESIDENTL | sle13 | 2426821.6594 | 1643 | sle
RESIDENTL | mby12 | 3267894.3821 | 609 | mby
FARM | wgi31 | 368672.79 | 43 | wgi
INDUSTRIAL | cyn24 | 15644182.2427 | 207 | cyn
| fgy34 | 3433.61 | 11 | fgy
RESIDENTL | bge11 | 15368827.4604 | 2654 | bge
RESIDENTL | ftr12 | 3825364.7454 | 636 | ftr
| mfa21 | 17049.39 | 26 | mfa
COMMERCIAL | wgi21 | 45541.7604 | 2 | wgi
INDUSTRIAL | wo14 | 2975508 | 24 | wo
COMMERCIAL | wgl12 | 5759083.9004 | 210 | wgl
INDUSTRIAL | moe23 | 765740.5661 | 26 | moe
COMMERCIAL | hpk14 | 5487941.7 | 85 | hpk
NCONUML | tt2 | 10017.24 | 3 | tt
INDUSTRIAL | cpk13 | 1507420.269 | 6 | cpk
INDUSTRIAL | lga41 | 52440142.6 | 1 | lga
NCONUML | elm26 | 60173.53 | 25 | elm
FARM | cf1 | 12492.747 | 1 | cf
RESIDENTL | bwr32 | 11435795.4629 | 2903 | bwr
NCONUML | cln23 | 19017.15 | 5 | cln
RESIDENTL | bdl41 | 18711766.0554 | 3582 | bdl
RESIDENTL | tt4 | 9918702.5206 | 2673 | tt
NCONUML | nrn13 | 44749.68 | 14 | nrn
NCONUML | mwl12 | 43601.75 | 11 | mwl
FARM | cln12 | 30466.72 | 1 | cln
INDUSTRIAL | cpk21 | 122110.94 | 5 | cpk
NCONUML | epg11 | 2275 | 2 | epg
FARM | brt22 | 1064314.9433 | 146 | brt
NCONUML | moe21 | 60919.67 | 15 | moe
RESIDENTL | ldl22 | 4948357.507 | 1104 | ldl
INDUSTRIAL | epg22 | 206880.17 | 13 | epg
NCONUML | cln12 | 55224.6632 | 17 | cln
| wo14 | 16653.0726 | 14 | wo
INDUSTRIAL | wo13 | 14774006.15 | 3 | wo
INDUSTRIAL | wgi22 | 729700.7 | 28 | wgi
COMMERCIAL | msd2 | 2629949.014 | 87 | msd
NCONUML | ldl22 | 11421.24 | 5 | ldl
RESIDENTL | wo22 | 17812297.6729 | 4125 | wo
FARM | mwl25 | 2028215.2676 | 224 | mwl
| cln14 | 46492.03 | 68 | cln
INDUSTRIAL | smr14 | 413387.45 | 34 | smr
FARM | rwn33 | 39914.72 | 5 | rwn
NCONUML | tt7 | 28203.83 | 11 | tt
INDUSTRIAL | lga11 | 317451.8284 | 16 | lga
INDUSTRIAL | tt12 | 6074893.6495 | 86 | tt
INDUSTRIAL | rwn32 | 87972.96 | 1 | rwn
RESIDENTL | myt21 | 10899844.0445 | 1487 | myt
RESIDENTL | cyn14 | 9596207.6734 | 2758 | cyn
RESIDENTL | kms11 | 9874885.3712 | 1972 | kms
COMMERCIAL | wo32 | 9961950.2687 | 147 | wo
NCONUML | hpk21 | 96497.83 | 40 | hpk
FARM | mwl13 | 248036.6173 | 7 | mwl
RESIDENTL | smr23 | 3447913.5369 | 523 | smr
INDUSTRIAL | nla32 | 1443086.18 | 25 | nla
| rwt32 | 35174.87 | 36 | rwt
INDUSTRIAL | moe11 | 65970.59 | 6 | moe
INDUSTRIAL | wo33 | 33298223.9508 | 7 | wo
INDUSTRIAL | bra31 | 2919.84 | 1 | bra
RESIDENTL | moe15 | 9740983.6859 | 1552 | moe
RESIDENTL | moe12 | 4538532.291 | 887 | moe
INDUSTRIAL | bdl41 | 1328921.5447 | 34 | bdl
NCONUML | tt6 | 36560.52 | 20 | tt
RESIDENTL | uwy1 | 6496143.3356 | 1032 | uwy
RESIDENTL | wgi32 | 16438958.2366 | 3917 | wgi
COMMERCIAL | rwn31 | 2125446.8547 | 72 | rwn
| ldl13 | 45979.2126 | 34 | ldl
LIGHTING | hpk23 | 2010173.36 | 1 | hpk
RESIDENTL | fgy14 | 9703108.5669 | 2483 | fgy
FARM | rwn24 | 30208.83 | 4 | rwn
COMMERCIAL | wo23 | 11409957.4027 | 304 | wo
| myt12 | 115131.3847 | 34 | myt
| bge13 | 13458.3255 | 19 | bge
| sle32 | 15918.6359 | 20 | sle
FARM | epg11 | 14625.27 | 2 | epg
NCONUML | mwl21 | 34561.25 | 17 | mwl
COMMERCIAL | nrn12 | 21654160.6835 | 271 | nrn
COMMERCIAL | llg13 | 15983000.2277 | 99 | llg
| lga22 | 14116.8478 | 12 | lga
FARM | hpk11 | 14620.89 | 5 | hpk
RESIDENTL | ofr11 | 25072251.243 | 5672 | ofr
FARM | ftr12 | 9732520.1395 | 879 | ftr
RESIDENTL | epg21 | 580054.4394 | 151 | epg
FARM | bge22 | 343097.1961 | 60 | bge
COMMERCIAL | sfs1 | 1879673.1771 | 124 | sfs
| cln24 | 61460.6675 | 37 | cln
NCONUML | smg22 | 48204.28 | 25 | smg
RESIDENTL | phm34 | 11301839.7716 | 2904 | phm
RESIDENTL | phm31 | 2762476.4376 | 550 | phm
NCONUML | smr13 | 69764.68 | 26 | smr
RESIDENTL | wyk12 | 12357178.5976 | 1789 | wyk
INDUSTRIAL | sle13 | 125251.914 | 47 | sle
FARM | phm24 | 689286.43 | 52 | phm
| cre31 | 63798.4484 | 85 | cre
INDUSTRIAL | bge12 | 121322.77 | 7 | bge
FARM | wots12 | 5076.62 | 1 | wots
NCONUML | cf1 | 1922.85 | 2 | cf
RESIDENTL | wo31 | 20016820.444 | 4554 | wo
FARM | smr22 | 1275801.32 | 154 | smr
FARM | lga22 | 1443457.6222 | 105 | lga
COMMERCIAL | mwl22 | 10003347.9587 | 192 | mwl
FARM | bn24 | 2239563.0749 | 370 | bn
NCONUML | wots25 | 45798.68 | 13 | wots
NCONUML | wgi31 | 79233.36 | 21 | wgi
FARM | epg23 | 30049.96 | 2 | epg
NCONUML | klk11 | 24723.1 | 13 | klk
| mwl14 | 3593.32 | 2 | mwl
RESIDENTL | mdg1 | 4384126.608 | 684 | mdg
RESIDENTL | nrn14 | 9562152.1887 | 1877 | nrn
LIGHTING | msd4 | 139319.89 | 1 | msd
LIGHTING | sfs1 | 1558457.9 | 1 | sfs
| klo14 | 120043.1087 | 185 | klo
RESIDENTL | hpk14 | 17025183.7337 | 3944 | hpk
FARM | lga12 | 4046898.7707 | 351 | lga
COMMERCIAL | ldl14 | 12475957.7156 | 266 | ldl
RESIDENTL | bn11 | 14382992.5485 | 2912 | bn
COMMERCIAL | bdl34 | 6213094.4744 | 204 | bdl
FARM | lyd11 | 23799.7 | 3 | lyd
| mwl22 | 10189.434 | 23 | mwl
NCONUML | cf2 | 120.31 | 1 | cf
| epg32 | 18473.04 | 31 | epg
RESIDENTL | bdl34 | 21922135.2151 | 5106 | bdl
COMMERCIAL | rwn26 | 3719056.4225 | 81 | rwn
INDUSTRIAL | mby13 | 219583.33 | 2 | mby
NCONUML | fgy33 | 40029.49 | 14 | fgy
| ftr22 | 13372.1897 | 14 | ftr
NCONUML | mwl13 | 53127.87 | 17 | mwl
INDUSTRIAL | rwt32 | 132361.99 | 4 | rwt
COMMERCIAL | phm23 | 17053480.4 | 2 | phm
COMMERCIAL | bra13 | 19208526.3529 | 181 | bra
FARM | wn1 | 37241.96 | 7 | wn
FARM | bm8b33 | 1540.9 | 2 | bmb
COMMERCIAL | wt10 | 13883699.3972 | 155 | wt
INDUSTRIAL | uwy1 | 90405.23 | 3 | uwy
RESIDENTL | ldl23 | 26005181.5029 | 4084 | ldl
FARM | klo24 | 194259.84 | 22 | klo
| hpk11 | 33718.6052 | 42 | hpk
NCONUML | phm33 | 47915.862 | 19 | phm
FARM | wn6 | 4543418.3442 | 605 | wn
COMMERCIAL | cyn21 | 3633643.5973 | 195 | cyn
INDUSTRIAL | wo22 | 393144.5 | 11 | wo
RESIDENTL | tgn42 | 795534.2193 | 223 | tgn
INDUSTRIAL | mwl23 | 715134.0252 | 54 | mwl
| rwt22 | 26934.55 | 52 | rwt
COMMERCIAL | phm31 | 4117822.4369 | 32 | phm
RESIDENTL | epg22 | 39578.43 | 14 | epg
RESIDENTL | nla32 | 6559402.1513 | 1220 | nla
RESIDENTL | myt22 | 1017937.6841 | 120 | myt
| wgl15 | 30619.4 | 19 | wgl
LIGHTING | mjg11 | 68938.73 | 1 | mjg
COMMERCIAL | phi12 | 2400712.314 | 73 | phi
COMMERCIAL | rwt36 | 2264519.95 | 43 | rwt
INDUSTRIAL | wgi23 | 157973.74 | 15 | wgi
NCONUML | elm24 | 74942.52 | 25 | elm
RESIDENTL | wt10 | 3332972.5881 | 860 | wt
NCONUML | ruba22 | 360.93 | 3 | ruba
FARM | phi11 | 82538.05 | 19 | phi
| bra11 | 11169.2884 | 32 | bra
INDUSTRIAL | moe15 | 1465208.8927 | 46 | moe
| tt5 | 13084.5535 | 33 | tt
LIGHTING | elm34 | 2971413.79 | 6 | elm
FARM | rwt25 | 33966.32 | 4 | rwt
RESIDENTL | moe11 | 9711471.9521 | 1967 | moe
INDUSTRIAL | rwt22 | 12240.297 | 2 | rwt
FARM | tgn23 | 1979366.6929 | 215 | tgn
COMMERCIAL | elm34 | 4840398.0166 | 153 | elm
NCONUML | phi11 | 19831.48 | 5 | phi
NCONUML | bra13 | 31922.03 | 14 | bra
RESIDENTL | mwl11 | 7113484.1589 | 1047 | mwl
| sle14 | 9929.5555 | 28 | sle
COMMERCIAL | cpk11 | 7316179.79 | 51 | cpk
| cyn31 | 5192.9 | 11 | cyn
NCONUML | epg12 | 1563.57 | 9 | epg
| epg11 | 4794.77 | 9 | epg
INDUSTRIAL | bwa23 | 17470876.21 | 8 | bwa
FARM | cln21 | 792.83 | 1 | cln
COMMERCIAL | wn3 | 8489705.5245 | 275 | wn
COMMERCIAL | bwn12 | 29123057.9665 | 274 | bwn
NCONUML | bra23 | 28962.5293 | 21 | bra
| bge12 | 5967.8256 | 14 | bge
INDUSTRIAL | tgn12 | 464065.58 | 15 | tgn
LIGHTING | fgy31 | 1047083.29 | 1 | fgy
NCONUML | moe25 | 63582.44 | 18 | moe
NCONUML | fgy21 | 30728.13 | 12 | fgy
INDUSTRIAL | lyd11 | 151654.68 | 9 | lyd
FARM | bwn13 | 5960.02 | 1 | bwn
RESIDENTL | lga11 | 6965787.8425 | 1044 | lga
NCONUML | bwr22 | 31744.79 | 14 | bwr
COMMERCIAL | llg12 | 3977405.3306 | 115 | llg
COMMERCIAL | mfa21 | 3716072.0048 | 197 | mfa
INDUSTRIAL | phm32 | 1008.48 | 1 | phm
COMMERCIAL | nrn13 | 3605622.38 | 41 | nrn
FARM | cyn22 | 1131.4275 | 1 | cyn
INDUSTRIAL | ftr23 | 1828762.8842 | 76 | ftr
INDUSTRIAL | mfa31 | 463955.39 | 14 | mfa
INDUSTRIAL | bge11 | 395339.98 | 10 | bge
RESIDENTL | wo13 | 2691801.805 | 586 | wo
RESIDENTL | llg11 | 4969161.4408 | 709 | llg
| cpk21 | 8908.612 | 12 | cpk
INDUSTRIAL | cre23 | 238715.04 | 8 | cre
COMMERCIAL | epg33 | 43303826.6612 | 357 | epg
FARM | ofr21 | 60907.55 | 6 | ofr
COMMERCIAL | cpk22 | 8802072.7366 | 32 | cpk
NCONUML | bra24 | 34184.91 | 27 | bra
NCONUML | wn6 | 84222.69 | 35 | wn
FARM | mfa22 | 15017348.1505 | 702 | mfa
FARM | lga24 | 2675198.7919 | 323 | lga
COMMERCIAL | phi13 | 13565764.588 | 480 | phi
FARM | lga13 | 6142984.8245 | 572 | lga
NCONUML | wn2 | 74469.51 | 25 | wn
COMMERCIAL | wyk23 | 9043742.9219 | 306 | wyk
INDUSTRIAL | cyn31 | 110897.03 | 2 | cyn
RESIDENTL | wt7 | 9398293.9689 | 2293 | wt
COMMERCIAL | rwt15 | 2407529.701 | 118 | rwt
| wots11 | 29868.01 | 43 | wots
COMMERCIAL | wt12 | 9788397.4198 | 246 | wt
FARM | wots24 | 5049980.8194 | 706 | wots
COMMERCIAL | ftr22 | 3919173.7529 | 139 | ftr
INDUSTRIAL | ruba12 | 859698.6565 | 35 | ruba
| wots25 | 37134.4365 | 43 | wots
RESIDENTL | ofr24 | 14317680.0438 | 3420 | ofr
COMMERCIAL | bdl32 | 9327480.3168 | 349 | bdl
NCONUML | trc01 | 2600.11 | 1 | trc
RESIDENTL | wgi33 | 15074294.4922 | 2906 | wgi
RESIDENTL | wyk24 | 16651462.561 | 3130 | wyk
NCONUML | wn1 | 109135.95 | 32 | wn
NCONUML | fgy34 | 69468.4 | 26 | fgy
| tgn43 | 23585.3 | 37 | tgn
| bwn11 | 22540.96 | 33 | bwn
COMMERCIAL | bn11 | 11469939.8143 | 448 | bn
RESIDENTL | wn7 | 334597.06 | 81 | wn
FARM | lga23 | 6580772.0568 | 604 | lga
RESIDENTL | mby13 | 1114988.13 | 129 | mby
INDUSTRIAL | moe12 | 309363.05 | 10 | moe
NCONUML | wgl21 | 72341.71 | 26 | wgl
| rwn22 | 13422.17 | 20 | rwn
FARM | ofr13 | 1726.88 | 2 | ofr
INDUSTRIAL | smg33 | 3791.86 | 1 | smg
COMMERCIAL | cnr2 | 2241662.7301 | 123 | cnr
NCONUML | bwn13 | 114734.08 | 27 | bwn
INDUSTRIAL | tgn43 | 8336.37 | 2 | tgn
NCONUML | bra33 | 54640.5039 | 38 | bra
LIGHTING | drn23 | 137376.82 | 1 | drn
COMMERCIAL | wt11 | 6045415.4763 | 137 | wt
| wo23 | 3425.76 | 13 | wo
RESIDENTL | drn11 | 23689909.4015 | 5897 | drn
RESIDENTL | bra33 | 17227071.6094 | 3920 | bra
FARM | cre21 | 1165190.53 | 9 | cre
| wo32 | 20472.5797 | 26 | wo
NCONUML | mfa22 | 12133.93 | 8 | mfa
COMMERCIAL | fgy32 | 10874129.2215 | 316 | fgy
INDUSTRIAL | bdl33 | 6444229.03 | 34 | bdl
NCONUML | cnr3 | 880.96 | 3 | cnr
COMMERCIAL | bwr14 | 64319.73 | 1 | bwr
NCONUML | ldl11 | 15379.88 | 9 | ldl
FARM | bdl33 | 333127.23 | 48 | bdl
INDUSTRIAL | elm23 | 351538.3612 | 12 | elm
NCONUML | lga14 | 16509.29 | 6 | lga
NCONUML | rwt21 | 45520.76 | 13 | rwt
INDUSTRIAL | mwl24 | 3823292.43 | 15 | mwl
RESIDENTL | epg14 | 8906284.5994 | 2218 | epg
NCONUML | drn21 | 11559.57 | 6 | drn
FARM | ldl21 | 4274.77 | 1 | ldl
| lga14 | 13272.15 | 11 | lga
LIGHTING | wo22 | 1145144.2306 | 3 | wo
LIGHTING | bdl33 | 755365.47 | 1 | bdl
INDUSTRIAL | lga12 | 340570.559 | 7 | lga
RESIDENTL | ofr23 | 20573594.8025 | 3065 | ofr
LIGHTING | tgn12 | 393.8997 | 1 | tgn
RESIDENTL | fgy32 | 4718000.0914 | 1180 | fgy
COMMERCIAL | moe11 | 6876107.6583 | 169 | moe
COMMERCIAL | wgl13 | 16726185.3211 | 289 | wgl
COMMERCIAL | cre22 | 19152716.1468 | 212 | cre
RESIDENTL | drn12 | 16081122.8597 | 3986 | drn
COMMERCIAL | mfa23 | 8005013.26 | 78 | mfa
| cln13 | 39224.5517 | 61 | cln
INDUSTRIAL | mfa22 | 1793714.26 | 36 | mfa
LIGHTING | smr23 | 37560.88 | 1 | smr
RESIDENTL | rwn32 | 6727398.7344 | 1603 | rwn
FARM | lga14 | 4550189.1065 | 436 | lga
| cln12 | 24735.6225 | 51 | cln
COMMERCIAL | kms11 | 4936701.5866 | 120 | kms
RESIDENTL | smr14 | 10997106.9114 | 1697 | smr
| epg13 | 194183.3358 | 102 | epg
| brt21 | 9723.1397 | 7 | brt
INDUSTRIAL | drn12 | 10032.09 | 2 | drn
| tt7 | 34871.95 | 3 | tt
INDUSTRIAL | wots25 | 7153785.931 | 7 | wots
FARM | tgn43 | 14451.81 | 2 | tgn
NCONUML | ldl14 | 38917.21 | 26 | ldl
INDUSTRIAL | brt21 | 238786.6 | 10 | brt
| llg11 | 8477.8 | 10 | llg
RESIDENTL | wgi24 | 12721878.952 | 3596 | wgi
RESIDENTL | cyn21 | 10508542.767 | 2257 | cyn
INDUSTRIAL | bra11 | 3982632.29 | 3 | bra
INDUSTRIAL | phi11 | 184139.3994 | 13 | phi
| hpk24 | 8609.4373 | 14 | hpk
NCONUML | ldl13 | 24965.12 | 22 | ldl
RESIDENTL | hpk21 | 20637351.8958 | 5254 | hpk
RESIDENTL | wgl13 | 19626090.0794 | 4751 | wgl
COMMERCIAL | elm21 | 12124007.57 | 258 | elm
COMMERCIAL | wt13 | 23168272.4303 | 498 | wt
| hpk23 | 55023.71 | 41 | hpk
COMMERCIAL | mdg1 | 1157212.0402 | 52 | mdg
NCONUML | wt11 | 64055.27 | 25 | wt
NCONUML | phm31 | 9383.328 | 4 | phm
COMMERCIAL | bge23 | 4904566.2339 | 176 | bge
NCONUML | smg23 | 17942.69 | 11 | smg
| mwl16 | 4764.4783 | 12 | mwl
COMMERCIAL | hpk12 | 20352329.5415 | 361 | hpk
RESIDENTL | ruba24 | 4395729.6843 | 894 | ruba
COMMERCIAL | nla32 | 3390681.6399 | 175 | nla
NCONUML | lyd12 | 44439.84 | 9 | lyd
| cln22 | 289385.5413 | 85 | cln
NCONUML | cpk21 | 53769.1 | 26 | cpk
| ruba22 | 8482.6526 | 15 | ruba
COMMERCIAL | myt22 | 191990.12 | 18 | myt
RESIDENTL | mby11 | 5261006.6685 | 922 | mby
RESIDENTL | rwn26 | 21195116.3973 | 2454 | rwn
| rwt31 | 14608.62 | 19 | rwt
INDUSTRIAL | epg35 | 1615230.05 | 4 | epg
| bge23 | 30837.693 | 28 | bge
NCONUML | bdl34 | 70291.97 | 25 | bdl
NCONUML | ofr13 | 30258.73 | 11 | ofr
| klk11 | 25230.2094 | 21 | klk
NCONUML | bn12 | 1241.66 | 2 | bn
COMMERCIAL | wgi32 | 5461052.6827 | 195 | wgi
NCONUML | ldl12 | 45990.38 | 14 | ldl
INDUSTRIAL | bra23 | 3394433.4433 | 42 | bra
| wo33 | 4138.8 | 1 | wo
NCONUML | myt12 | 33269.22 | 16 | myt
INDUSTRIAL | ldl11 | 1468879.69 | 10 | ldl
RESIDENTL | msd1 | 8481569.4252 | 1750 | msd
NCONUML | bn11 | 57126.91 | 28 | bn
INDUSTRIAL | ftr12 | 2824402.5 | 31 | ftr
INDUSTRIAL | hpk11 | 29483.41 | 8 | hpk
NCONUML | epg33 | 5589.26 | 2 | epg
COMMERCIAL | wo31 | 10532525.1457 | 139 | wo
| wgl21 | 38182.04 | 53 | wgl
| bge22 | 25062.3495 | 31 | bge
RESIDENTL | tt1 | 171030.69 | 8 | tt
INDUSTRIAL | bwr34 | 134229.36 | 26 | bwr
COMMERCIAL | bra33 | 14409139.6368 | 303 | bra
COMMERCIAL | bdl44 | 4495186.894 | 197 | bdl
| bwn13 | 12482.8878 | 14 | bwn
NCONUML | wn3 | 40552.61 | 16 | wn
NCONUML | smr24 | 41055.27 | 16 | smr
INDUSTRIAL | mwl14 | 4499194.0326 | 50 | mwl
| wots24 | 36833.8626 | 36 | wots
NCONUML | wt12 | 74491.29 | 36 | wt
COMMERCIAL | smg31 | 17181337.4 | 81 | smg
FARM | lyd13 | 146611.14 | 18 | lyd
NCONUML | wots12 | 53576.05 | 15 | wots
INDUSTRIAL | fgy12 | 30820.7097 | 2 | fgy
FARM | myt12 | 4025860.4278 | 600 | myt
INDUSTRIAL | cyn22 | 204983.76 | 12 | cyn
COMMERCIAL | cyn33 | 3196035.4476 | 122 | cyn
COMMERCIAL | mby12 | 1853426.4391 | 89 | mby
NCONUML | tgn43 | 111938.06 | 34 | tgn
NCONUML | wo11 | 17571.55 | 5 | wo
INDUSTRIAL | epg12 | 1405424.52 | 3 | epg
| cf2 | 30699.57 | 2 | cf
COMMERCIAL | llg11 | 3213282.749 | 85 | llg
LIGHTING | rwn24 | 1936572.72 | 3 | rwn
INDUSTRIAL | cln24 | 15633.29 | 3 | cln
FARM | sle31 | 4999785.6618 | 315 | sle
INDUSTRIAL | cf1 | 129164.746 | 4 | cf
| ruba12 | 126134.0367 | 24 | ruba
| bwr12 | 18318.3952 | 15 | bwr
FARM | elm32 | 382389.8968 | 32 | elm
| ofr21 | 113717.1 | 52 | ofr
INDUSTRIAL | wn2 | 282430.54 | 13 | wn
NCONUML | bge22 | 82280.88 | 49 | bge
NCONUML | cnr2 | 33661.17 | 17 | cnr
NCONUML | wots13 | 10386.18 | 6 | wots
FARM | elm24 | 39172.3194 | 4 | elm
COMMERCIAL | nrn14 | 6896476.1265 | 116 | nrn
NCONUML | ruba12 | 27603.68 | 16 | ruba
NCONUML | hpk13 | 50290.3 | 16 | hpk
NCONUML | bra11 | 44798.92 | 35 | bra
| rwt21 | 23376.2409 | 6 | rwt
RESIDENTL | drn23 | 20613814.4846 | 2434 | drn
RESIDENTL | rwt36 | 2676215.9999 | 821 | rwt
RESIDENTL | llg13 | 6857833.0372 | 1230 | llg
COMMERCIAL | wyk12 | 4295149.2844 | 131 | wyk
INDUSTRIAL | ofr13 | 1622296.11 | 21 | ofr
| bra14 | 30334.7783 | 42 | bra
INDUSTRIAL | tgn11 | 3321263.75 | 18 | tgn
LIGHTING | mby13 | 9944.78 | 1 | mby
RESIDENTL | cln11 | 39284605.9906 | 12154 | cln
COMMERCIAL | drn22 | 10741065.2473 | 246 | drn
RESIDENTL | wo32 | 11244170.0715 | 2343 | wo
| bra33 | 27895.4569 | 47 | bra
COMMERCIAL | epg21 | 21867278.1603 | 75 | epg
INDUSTRIAL | cre21 | 293542.6 | 2 | cre
RESIDENTL | bwr24 | 1834966.95 | 415 | bwr
RESIDENTL | hpk13 | 8888406.848 | 2283 | hpk
NCONUML | moe13 | 240.62 | 2 | moe
RESIDENTL | mwl12 | 3605926.3697 | 887 | mwl
| elm24 | 29520.3106 | 27 | elm
COMMERCIAL | tgn31 | 5251765.7474 | 163 | tgn
| rwt25 | 17882.0217 | 23 | rwt
RESIDENTL | moe21 | 9438147.1697 | 1978 | moe
COMMERCIAL | mjg11 | 16973320.0649 | 258 | mjg
COMMERCIAL | moe22 | 1619971.835 | 34 | moe
NCONUML | cpk13 | 44472.2623 | 32 | cpk
| phi11 | 13149.9006 | 9 | phi
FARM | cyn11 | 2814.65 | 1 | cyn
FARM | cyn24 | 25049.8 | 2 | cyn
FARM | drn13 | 379220.8035 | 25 | drn
COMMERCIAL | mwe236 | 663523.2 | 21 | mwe
INDUSTRIAL | phm24 | 35612.08 | 4 | phm
INDUSTRIAL | bge22 | 36211.2493 | 9 | bge
RESIDENTL | cnr1 | 478523.9112 | 104 | cnr
| lga24 | 10918.35 | 11 | lga
NCONUML | sle14 | 98131.7526 | 34 | sle
NCONUML | tt5 | 14462.54 | 12 | tt
| epg12 | 53720.6497 | 70 | epg
NCONUML | kms11 | 42647.24 | 13 | kms
FARM | elm23 | 38507.8 | 8 | elm
COMMERCIAL | cyn12 | 12045879.7132 | 241 | cyn
INDUSTRIAL | fgy23 | 1420677.79 | 11 | fgy
COMMERCIAL | mfa14 | 259168.13 | 17 | mfa
| bra31 | 49797.7422 | 13 | bra
COMMERCIAL | mwl12 | 1780079.4127 | 78 | mwl
| bwr22 | 2405.71 | 25 | bwr
INDUSTRIAL | fgy24 | 415478.9 | 15 | fgy
COMMERCIAL | hpk13 | 9763023.5697 | 134 | hpk
| cyn22 | 22272.33 | 22 | cyn
| ldl21 | 13369.5383 | 42 | ldl
| wt6 | 17591.4373 | 23 | wt
RESIDENTL | wn4 | 11276854.4814 | 2349 | wn
FARM | mwl14 | 451834.7532 | 54 | mwl
RESIDENTL | bm8b31 | 357131.6719 | 111 | bmb
NCONUML | cyn14 | 48577.9677 | 22 | cyn
FARM | cre32 | 5136.47 | 1 | cre
FARM | bwr34 | 4550.33 | 1 | bwr
RESIDENTL | llg14 | 14855712.1657 | 2170 | llg
FARM | smg33 | 29400.19 | 7 | smg
RESIDENTL | drn22 | 21996972.8148 | 3999 | drn
NCONUML | elm32 | 42948.38 | 25 | elm
INDUSTRIAL | klo14 | 587332.99 | 17 | klo
| tgn11 | 22256.53 | 32 | tgn
INDUSTRIAL | tgn44 | 4536032.57 | 9 | tgn
COMMERCIAL | ldl23 | 15994398.5627 | 272 | ldl
| wn6 | 146062.0009 | 59 | wn
COMMERCIAL | tt2 | 18806104.6367 | 399 | tt
COMMERCIAL | brt11 | 4047117.81 | 129 | brt
NCONUML | llg14 | 65195.01 | 40 | llg
FARM | fgy24 | 95940.3 | 9 | fgy
NCONUML | fgy14 | 61562.37 | 33 | fgy
COMMERCIAL | rve12 | 3272242.91 | 54 | rve
INDUSTRIAL | cpk23 | 208291.634 | 5 | cpk
| lga23 | 41697.3391 | 21 | lga
INDUSTRIAL | yn38 | 642769.3081 | 6 | yn
COMMERCIAL | bwa21 | 7920817.52 | 6 | bwa
INDUSTRIAL | elm25 | 2097.04 | 1 | elm
COMMERCIAL | wots13 | 3416108.1488 | 213 | wots
FARM | wgi22 | 191494.2501 | 24 | wgi
NCONUML | fgy13 | 27847.71 | 7 | fgy
| bra24 | 9840.15 | 27 | bra
FARM | ofr14 | 100163.6258 | 21 | ofr
NCONUML | nrn11 | 16820.36 | 5 | nrn
RESIDENTL | smg31 | 12434679.8443 | 2879 | smg
COMMERCIAL | smr24 | 15083854.4686 | 348 | smr
| lyd11 | 12152.66 | 25 | lyd
INDUSTRIAL | bra12 | 1282907.1727 | 55 | bra
FARM | wgl15 | 3297105.6723 | 233 | wgl
INDUSTRIAL | msd1 | 544058.7154 | 15 | msd
| epg31 | 13971.3347 | 31 | epg
INDUSTRIAL | wgl23 | 572354.5027 | 44 | wgl
INDUSTRIAL | cpk12 | 343353.79 | 14 | cpk
INDUSTRIAL | mfa34 | 4790944.63 | 37 | mfa
| wn2 | 65478.1843 | 60 | wn
INDUSTRIAL | drn23 | 222019.33 | 21 | drn
| klo11 | 24997.4 | 1 | klo
COMMERCIAL | cyn13 | 11562540.4133 | 213 | cyn
| tgn44 | 15598.29 | 27 | tgn
| wn1 | 5093 | 9 | wn
NCONUML | wots24 | 22958.48 | 11 | wots
RESIDENTL | ftr21 | 5974099.1685 | 1654 | ftr
NCONUML | wgl11 | 116770.29 | 32 | wgl
FARM | phm22 | 2513172.8482 | 159 | phm
| mfa22 | 25912.0235 | 15 | mfa
| tt2 | 5693.01 | 1 | tt
RESIDENTL | cyn12 | 11384819.6049 | 2642 | cyn
COMMERCIAL | mby11 | 1920906.95 | 83 | mby
RESIDENTL | bdl42 | 7579399.6648 | 1528 | bdl
COMMERCIAL | sle11 | 16789466.3124 | 430 | sle
COMMERCIAL | bdl42 | 3935066.2305 | 228 | bdl
NCONUML | rwn22 | 25304.89 | 19 | rwn
INDUSTRIAL | cre32 | 1414910.91 | 33 | cre
INDUSTRIAL | bwn11 | 121807.37 | 8 | bwn
NCONUML | smr22 | 29006.3 | 13 | smr
RESIDENTL | phm24 | 12991887.5254 | 2975 | phm
RESIDENTL | phm21 | 5600884.0097 | 1319 | phm
NCONUML | ldl23 | 93357.12 | 44 | ldl
RESIDENTL | ldl24 | 19255310.9766 | 3964 | ldl
INDUSTRIAL | bra21 | 9682528.358 | 10 | bra
| sle31 | 21276.5675 | 34 | sle
| myt11 | 11671.01 | 10 | myt
RESIDENTL | elm21 | 10927220.6891 | 2208 | elm
COMMERCIAL | epg13 | 13081700.0195 | 121 | epg
COMMERCIAL | hpk21 | 6771211.022 | 80 | hpk
NCONUML | bwr12 | 55323.1848 | 22 | bwr
| trc01 | 7370.1419 | 1 | trc
| epg35 | 12733.43 | 3 | epg
INDUSTRIAL | bge21 | 30163.23 | 3 | bge
RESIDENTL | tgn31 | 10330935.5842 | 1504 | tgn
COMMERCIAL | moe23 | 8180066.6029 | 204 | moe
FARM | bra21 | 5211.11 | 2 | bra
LIGHTING | llg12 | 9573.66 | 1 | llg
RESIDENTL | bdl31 | 18828777.9984 | 3534 | bdl
COMMERCIAL | nla31 | 1365542.8767 | 73 | nla
INDUSTRIAL | klo24 | 421040.3606 | 14 | klo
FARM | bdl43 | 35833.9 | 4 | bdl
FARM | cyn31 | 3324.08 | 1 | cyn
FARM | sle14 | 508528.62 | 59 | sle
FARM | fgy34 | 3609.3 | 1 | fgy
RESIDENTL | elm26 | 19204314.084 | 3128 | elm
COMMERCIAL | ldl13 | 4974121.0157 | 271 | ldl
NCONUML | tgn42 | 32526.3 | 9 | tgn
RESIDENTL | nrn13 | 11128338.9236 | 2708 | nrn
| drn13 | 33230.29 | 35 | drn
RESIDENTL | mfa14 | 15628.16 | 8 | mfa
RESIDENTL | rwt14 | 5266292.5405 | 1232 | rwt
FARM | ftr23 | 7584335.745 | 587 | ftr
FARM | moe12 | 2890738.1544 | 266 | moe
RESIDENTL | klk21 | 6022162.144 | 692 | klk
COMMERCIAL | bn22 | 11917129.8815 | 407 | bn
COMMERCIAL | cln13 | 10498926.3291 | 102 | cln
INDUSTRIAL | cln11 | 955300.36 | 11 | cln
FARM | bge11 | 1450445.3683 | 132 | bge
| mwl25 | 368.2898 | 2 | mwl
| rwn33 | 13688.96 | 19 | rwn
| bdl43 | 33766.9817 | 15 | bdl
NCONUML | cln14 | 95979.5703 | 31 | cln
NCONUML | lga24 | 7306.35 | 4 | lga
| bn23 | 36133.4118 | 23 | bn
| ofr14 | 18460.3638 | 32 | ofr
FARM | wo14 | 29381.84 | 3 | wo
FARM | cln24 | 15169.45 | 1 | cln
FARM | smg21 | 2813.13 | 1 | smg
FARM | uwy1 | 50419.26 | 6 | uwy
RESIDENTL | cpk11 | 18255270.9798 | 3705 | cpk
INDUSTRIAL | rwn34 | 151721.8975 | 12 | rwn
FARM | mfa34 | 8352796.4311 | 398 | mfa
INDUSTRIAL | cyn23 | 283668.3977 | 39 | cyn
COMMERCIAL | cln23 | 7919442.4187 | 94 | cln
| rwn24 | 145239.1574 | 36 | rwn
INDUSTRIAL | cln21 | 91173.7471 | 8 | cln
INDUSTRIAL | wots23 | 9771996.01 | 2 | wots
COMMERCIAL | ofr23 | 7962081.4442 | 137 | ofr
FARM | cln11 | 5358747.3528 | 175 | cln
INDUSTRIAL | epg23 | 1603069.098 | 49 | epg
NCONUML | elm33 | 106570.09 | 33 | elm
| tt6 | 16214.4725 | 50 | tt
NCONUML | lga12 | 120.31 | 1 | lga
RESIDENTL | moe25 | 15202048.016 | 3044 | moe
RESIDENTL | moe22 | 6183768.6959 | 1343 | moe
RESIDENTL | mfa23 | 1535883.9368 | 206 | mfa
FARM | rwn22 | 76017.25 | 13 | rwn
COMMERCIAL | fgy31 | 26687.08 | 5 | fgy
RESIDENTL | elm33 | 17751529.9107 | 3238 | elm
COMMERCIAL | ldl22 | 7642772.3181 | 272 | ldl
NCONUML | llg11 | 13058.17 | 7 | llg
| ruba24 | 72607.09 | 10 | ruba
FARM | rwt32 | 21924.18 | 3 | rwt
FARM | ruba12 | 5735958.293 | 534 | ruba
FARM | brt21 | 526055.8565 | 65 | brt
| rwt15 | 24735.76 | 50 | rwt
NCONUML | bge13 | 40077 | 45 | bge
COMMERCIAL | klk21 | 1344972.0506 | 75 | klk
INDUSTRIAL | msd4 | 532825.24 | 27 | msd
| mwl21 | 2371.576 | 7 | mwl
RESIDENTL | wt9 | 13126762.7947 | 2901 | wt
FARM | wgi23 | 957555.9102 | 143 | wgi
| wgl24 | 12928.4076 | 27 | wgl
NCONUML | tgn11 | 50804.93 | 14 | tgn
LIGHTING | hpk22 | 402155.12 | 2 | hpk
INDUSTRIAL | wt13 | 198794.34 | 24 | wt
LIGHTING | wots24 | 69082.45 | 1 | wots
| ofr13 | 25120.5182 | 29 | ofr
| cre21 | 98632.2224 | 69 | cre
| smg22 | 13378.71 | 23 | smg
COMMERCIAL | tt4 | 4770691.1401 | 169 | tt
COMMERCIAL | elm26 | 2765254.86 | 47 | elm
NCONUML | bwa22 | 120.31 | 1 | bwa
| cyn23 | 386495.78 | 52 | cyn
INDUSTRIAL | nla34 | 227255.6563 | 13 | nla
FARM | mwl22 | 63.01 | 1 | mwl
| cf1 | 5771.13 | 3 | cf
NCONUML | cpk22 | 15413.02 | 10 | cpk
NCONUML | lyd13 | 28195.47 | 10 | lyd
NCONUML | cre31 | 35482.06 | 18 | cre
COMMERCIAL | wo11 | 6006584.4175 | 54 | wo
INDUSTRIAL | wt7 | 2382042.5333 | 25 | wt
| bwr34 | 19530.96 | 64 | bwr
NCONUML | bge23 | 57838.96 | 34 | bge
INDUSTRIAL | tgn23 | 187420.5 | 24 | tgn
RESIDENTL | cyn33 | 17836008.3498 | 3662 | cyn
RESIDENTL | nla34 | 7124747.0562 | 1408 | nla
| wgl11 | 21820.8596 | 38 | wgl
COMMERCIAL | bn12 | 3658135.6563 | 31 | bn
| mwl13 | 7054.2121 | 17 | mwl
COMMERCIAL | rwt26 | 65754589.65 | 1 | rwt
FARM | wt9 | 2789.4 | 1 | wt
RESIDENTL | bdl44 | 10906570.4152 | 1766 | bdl
FARM | cre33 | 2156267.3416 | 81 | cre
COMMERCIAL | wgl21 | 7364849.9167 | 150 | wgl
COMMERCIAL | wn5 | 3727109.367 | 208 | wn
NCONUML | mwl22 | 81020 | 27 | mwl
NCONUML | bn24 | 14677.57 | 9 | bn
| smr22 | 9887.67 | 15 | smr
|  | 8782.36 | 2 | #REF!
RESIDENTL | sle11 | 5311421.2716 | 1344 | sle
RESIDENTL | nw13 | 126364.0108 | 18 | nw
RESIDENTL | ftr23 | 12909653.9148 | 2620 | ftr
COMMERCIAL | mwl11 | 1278518.3133 | 72 | mwl
LIGHTING | llg13 | 66328.6913 | 1 | llg
NCONUML | klk22 | 2600.11 | 1 | klk
RESIDENTL | wyk23 | 22445865.182 | 3391 | wyk
COMMERCIAL | wt6 | 6354339.6482 | 191 | wt
RESIDENTL | brt11 | 6592458.6386 | 1001 | brt
NCONUML | tt9 | 66916.75 | 41 | tt
FARM | smr14 | 4406259.38 | 487 | smr
NCONUML | epg32 | 55568.91 | 13 | epg
RESIDENTL | rwn31 | 17135173.2235 | 2210 | rwn
| phm33 | 20993.1171 | 27 | phm
NCONUML | myt11 | 6079.5 | 6 | myt
RESIDENTL | nrn12 | 2807836.1314 | 591 | nrn
COMMERCIAL | mwl16 | 411566.3345 | 42 | mwl
INDUSTRIAL | lga23 | 1068068.6578 | 23 | lga
COMMERCIAL | ldl12 | 15390056.6509 | 380 | ldl
FARM | nla34 | 624678.3932 | 78 | nla
COMMERCIAL | rve13 | 1685040.429 | 44 | rve
NCONUML | drn24 | 11009.3526 | 4 | drn
COMMERCIAL | myt21 | 6919383.7104 | 251 | myt
FARM | moe13 | 3478506.4958 | 306 | moe
COMMERCIAL | mwl21 | 9182796.6603 | 240 | mwl
NCONUML | wgl15 | 97647.0301 | 36 | wgl
| bwn14 | 31300.22 | 31 | bwn
RESIDENTL | cpk22 | 8203984.593 | 1482 | cpk
RESIDENTL | rve12 | 17634581.2748 | 3656 | rve
RESIDENTL | phi13 | 17016004.0328 | 4317 | phi
RESIDENTL | hpk12 | 5058413.1519 | 1238 | hpk
COMMERCIAL | ruba24 | 4555190.3466 | 105 | ruba
FARM | cln14 | 51639.06 | 13 | cln
INDUSTRIAL | wt9 | 148098.11 | 5 | wt
| smg21 | 44014.37 | 27 | smg
INDUSTRIAL | smr23 | 883845.12 | 6 | smr

## Forecast - Summer
Forecasting Application - 13/10/2025
asset_type | asset | extremum | scenario | demand_year | season | poe | customer_count | pv_capacity | value | forecast_round | unit | region
zone_sub | cln | maximum |  | 2022 | Summer | 50 | 38619 | 72.2578 | 77.9086 | 202503 | MVA | central
zone_sub | cln | maximum |  | 2022 | Summer | 10 | 38619 | 72.2578 | 91.3183 | 202503 | MVA | central
zone_sub | cln | maximum |  | 2023 | Summer | 10 | 41429 | 81.3604 | 97.5884 | 202503 | MVA | central
zone_sub | cln | maximum |  | 2023 | Summer | 50 | 41429 | 81.3604 | 83.3369 | 202503 | MVA | central
zone_sub | cln | maximum |  | 2024 | Summer | 10 | 44846 | 94.6588 | 104.9463 | 202503 | MVA | central
zone_sub | cln | maximum |  | 2024 | Summer | 50 | 44846 | 94.6588 | 89.7351 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2025 | Summer | 10 |  |  | 119.6766 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2025 | Summer | 50 |  |  | 104.3341 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2026 | Summer | 10 |  |  | 124.2514 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2026 | Summer | 50 |  |  | 108.3435 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2027 | Summer | 10 |  |  | 128.0364 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2027 | Summer | 50 |  |  | 111.4611 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2028 | Summer | 10 |  |  | 131.3686 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2028 | Summer | 50 |  |  | 115.2173 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2029 | Summer | 10 |  |  | 136.7682 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2029 | Summer | 50 |  |  | 119.0984 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2030 | Summer | 10 |  |  | 141.634 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2030 | Summer | 50 |  |  | 123.2461 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2031 | Summer | 10 |  |  | 148.4809 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2031 | Summer | 50 |  |  | 128.0275 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2032 | Summer | 10 |  |  | 155.6302 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2032 | Summer | 50 |  |  | 133.6994 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2033 | Summer | 10 |  |  | 161.4365 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2033 | Summer | 50 |  |  | 139.0092 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2034 | Summer | 10 |  |  | 166.8996 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2034 | Summer | 50 |  |  | 144.6013 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2035 | Summer | 10 |  |  | 175.1342 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2035 | Summer | 50 |  |  | 154.2938 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2036 | Summer | 10 |  |  | 181.0486 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2036 | Summer | 50 |  |  | 157.43 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2037 | Summer | 10 |  |  | 187.0195 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2037 | Summer | 50 |  |  | 163.5566 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2038 | Summer | 10 |  |  | 193.3671 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2038 | Summer | 50 |  |  | 168.1999 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2039 | Summer | 10 |  |  | 192.0421 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2039 | Summer | 50 |  |  | 167.0472 | 202503 | MVA | central
zone_sub | cre | maximum |  | 2022 | Summer | 10 | 24937 | 39.5122 | 71.3044 | 202503 | MVA | central
zone_sub | cre | maximum |  | 2022 | Summer | 50 | 24937 | 39.5122 | 64.1683 | 202503 | MVA | central
zone_sub | cre | maximum |  | 2023 | Summer | 10 | 25835 | 43.8704 | 73.6781 | 202503 | MVA | central
zone_sub | cre | maximum |  | 2023 | Summer | 50 | 25835 | 43.8704 | 65.8328 | 202503 | MVA | central
zone_sub | cre | maximum |  | 2024 | Summer | 10 | 26314 | 48.9572 | 74.7994 | 202503 | MVA | central
zone_sub | cre | maximum |  | 2024 | Summer | 50 | 26314 | 48.9572 | 66.0879 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2025 | Summer | 10 |  |  | 89.8342 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2025 | Summer | 50 |  |  | 80.6612 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2026 | Summer | 10 |  |  | 90.653 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2026 | Summer | 50 |  |  | 81.4056 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2027 | Summer | 10 |  |  | 89.7773 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2027 | Summer | 50 |  |  | 80.6131 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2028 | Summer | 10 |  |  | 94.9573 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2028 | Summer | 50 |  |  | 85.9509 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2029 | Summer | 10 |  |  | 94.8385 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2029 | Summer | 50 |  |  | 85.6114 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2030 | Summer | 10 |  |  | 96.1186 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2030 | Summer | 50 |  |  | 85.7941 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2031 | Summer | 10 |  |  | 97.2062 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2031 | Summer | 50 |  |  | 86.4866 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2032 | Summer | 10 |  |  | 98.0786 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2032 | Summer | 50 |  |  | 87.2925 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2033 | Summer | 10 |  |  | 98.8781 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2033 | Summer | 50 |  |  | 88.2343 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2034 | Summer | 10 |  |  | 99.6475 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2034 | Summer | 50 |  |  | 88.9575 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2035 | Summer | 10 |  |  | 99.2707 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2035 | Summer | 50 |  |  | 89.8044 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2036 | Summer | 10 |  |  | 99.9981 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2036 | Summer | 50 |  |  | 89.5675 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2037 | Summer | 10 |  |  | 101.1509 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2037 | Summer | 50 |  |  | 90.5821 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2038 | Summer | 10 |  |  | 101.3208 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2038 | Summer | 50 |  |  | 90.3196 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2039 | Summer | 10 |  |  | 99.6095 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2039 | Summer | 50 |  |  | 88.5146 | 202503 | MVA | central
zone_sub | epg | maximum |  | 2022 | Summer | 10 | 29371 | 40.0067 | 87.2498 | 202503 | MVA | central
zone_sub | epg | maximum |  | 2022 | Summer | 50 | 29371 | 40.0067 | 72.9666 | 202503 | MVA | central
zone_sub | epg | maximum |  | 2023 | Summer | 10 | 30422 | 45.1511 | 90.3071 | 202503 | MVA | central
zone_sub | epg | maximum |  | 2023 | Summer | 50 | 30422 | 45.1511 | 75.7012 | 202503 | MVA | central
zone_sub | epg | maximum |  | 2024 | Summer | 10 | 32118 | 51.557 | 95.8895 | 202503 | MVA | central
zone_sub | epg | maximum |  | 2024 | Summer | 50 | 32118 | 51.557 | 79.9844 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2025 | Summer | 10 |  |  | 109.0669 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2025 | Summer | 50 |  |  | 92.5622 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2026 | Summer | 10 |  |  | 118.5447 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2026 | Summer | 50 |  |  | 101.6723 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2027 | Summer | 10 |  |  | 121.4869 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2027 | Summer | 50 |  |  | 104.4042 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2028 | Summer | 10 |  |  | 119.8786 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2028 | Summer | 50 |  |  | 102.6031 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2029 | Summer | 10 |  |  | 121.9204 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2029 | Summer | 50 |  |  | 105.5757 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2030 | Summer | 10 |  |  | 124.6444 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2030 | Summer | 50 |  |  | 106.371 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2031 | Summer | 10 |  |  | 127.5507 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2031 | Summer | 50 |  |  | 110.1341 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2032 | Summer | 10 |  |  | 131.8742 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2032 | Summer | 50 |  |  | 112.2581 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2033 | Summer | 10 |  |  | 136.3355 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2033 | Summer | 50 |  |  | 113.9316 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2034 | Summer | 10 |  |  | 140.9437 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2034 | Summer | 50 |  |  | 117.5793 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2035 | Summer | 10 |  |  | 144.5914 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2035 | Summer | 50 |  |  | 120.4726 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2036 | Summer | 50 |  |  | 128.0797 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2036 | Summer | 10 |  |  | 149.6115 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2037 | Summer | 10 |  |  | 152.9797 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2037 | Summer | 50 |  |  | 129.922 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2038 | Summer | 10 |  |  | 155.1715 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2038 | Summer | 50 |  |  | 132.5568 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2039 | Summer | 10 |  |  | 152.1644 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2039 | Summer | 50 |  |  | 125.7761 | 202503 | MVA | central
zone_sub | klo | maximum |  | 2022 | Summer | 10 | 14879 | 23.0226 | 53.5677 | 202503 | MVA | central
zone_sub | klo | maximum |  | 2022 | Summer | 50 | 14879 | 23.0226 | 41.9423 | 202503 | MVA | central
zone_sub | klo | maximum |  | 2023 | Summer | 10 | 17175 | 27.7177 | 61.121 | 202503 | MVA | central
zone_sub | klo | maximum |  | 2023 | Summer | 50 | 17175 | 27.7177 | 48.3019 | 202503 | MVA | central
zone_sub | klo | maximum |  | 2024 | Summer | 10 | 19951 | 34.2052 | 70.1897 | 202503 | MVA | central
zone_sub | klo | maximum |  | 2024 | Summer | 50 | 19951 | 34.2052 | 55.7613 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2025 | Summer | 10 |  |  | 83.6879 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2025 | Summer | 50 |  |  | 68.2523 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2026 | Summer | 10 |  |  | 94.1984 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2026 | Summer | 50 |  |  | 77.9353 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2027 | Summer | 10 |  |  | 102.4436 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2027 | Summer | 50 |  |  | 84.7194 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2028 | Summer | 10 |  |  | 118.3247 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2028 | Summer | 50 |  |  | 99.6669 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2029 | Summer | 10 |  |  | 126.3487 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2029 | Summer | 50 |  |  | 106.8624 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2030 | Summer | 10 |  |  | 135.5692 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2030 | Summer | 50 |  |  | 115.5707 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2031 | Summer | 10 |  |  | 148.561 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2031 | Summer | 50 |  |  | 127.0156 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2032 | Summer | 10 |  |  | 164.8827 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2032 | Summer | 50 |  |  | 137.8179 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2033 | Summer | 10 |  |  | 180.5841 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2033 | Summer | 50 |  |  | 151.2391 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2034 | Summer | 10 |  |  | 196.9964 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2034 | Summer | 50 |  |  | 164.8814 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2035 | Summer | 10 |  |  | 212.9758 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2035 | Summer | 50 |  |  | 181.5355 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2036 | Summer | 10 |  |  | 230.0573 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2036 | Summer | 50 |  |  | 195.8954 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2037 | Summer | 10 |  |  | 248.4456 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2037 | Summer | 50 |  |  | 212.2991 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2038 | Summer | 10 |  |  | 266.5409 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2038 | Summer | 50 |  |  | 225.6959 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2039 | Summer | 10 |  |  | 272.6357 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2039 | Summer | 50 |  |  | 228.9049 | 202503 | MVA | central
zone_sub | ofr | maximum |  | 2022 | Summer | 10 | 23246 | 35.5119 | 59.9776 | 202503 | MVA | central
zone_sub | ofr | maximum |  | 2022 | Summer | 50 | 23246 | 35.5119 | 53.856 | 202503 | MVA | central
zone_sub | ofr | maximum |  | 2023 | Summer | 10 | 24109 | 39.5748 | 62.0639 | 202503 | MVA | central
zone_sub | ofr | maximum |  | 2023 | Summer | 50 | 24109 | 39.5748 | 55.451 | 202503 | MVA | central
zone_sub | ofr | maximum |  | 2024 | Summer | 10 | 24997 | 44.4669 | 64.073 | 202503 | MVA | central
zone_sub | ofr | maximum |  | 2024 | Summer | 50 | 24997 | 44.4669 | 56.9594 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2025 | Summer | 10 |  |  | 69.589 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2025 | Summer | 50 |  |  | 61.9907 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2026 | Summer | 10 |  |  | 76.597 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2026 | Summer | 50 |  |  | 68.9791 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2027 | Summer | 10 |  |  | 81.5678 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2027 | Summer | 50 |  |  | 74.0072 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2028 | Summer | 10 |  |  | 84.5283 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2028 | Summer | 50 |  |  | 76.6284 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2029 | Summer | 10 |  |  | 86.8984 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2029 | Summer | 50 |  |  | 78.9811 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2030 | Summer | 10 |  |  | 88.8048 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2030 | Summer | 50 |  |  | 80.4506 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2031 | Summer | 10 |  |  | 90.6365 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2031 | Summer | 50 |  |  | 82.1352 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2032 | Summer | 10 |  |  | 92.2256 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2032 | Summer | 50 |  |  | 83.4813 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2033 | Summer | 10 |  |  | 92.9929 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2033 | Summer | 50 |  |  | 84.3346 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2034 | Summer | 10 |  |  | 94.1573 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2034 | Summer | 50 |  |  | 86.446 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2035 | Summer | 10 |  |  | 95.4952 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2035 | Summer | 50 |  |  | 87.894 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2036 | Summer | 10 |  |  | 96.8516 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2036 | Summer | 50 |  |  | 88.627 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2037 | Summer | 10 |  |  | 98.5806 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2037 | Summer | 50 |  |  | 90.0391 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2038 | Summer | 10 |  |  | 98.8168 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2038 | Summer | 50 |  |  | 89.5765 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2039 | Summer | 10 |  |  | 97.8239 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2039 | Summer | 50 |  |  | 88.3981 | 202503 | MVA | central
zone_sub | phm | maximum |  | 2022 | Summer | 50 | 16270 | 23.521 | 51.4174 | 202503 | MVA | central
zone_sub | phm | maximum |  | 2022 | Summer | 10 | 16270 | 23.521 | 56.9097 | 202503 | MVA | central
zone_sub | phm | maximum |  | 2023 | Summer | 10 | 16562 | 25.5412 | 57.758 | 202503 | MVA | central
zone_sub | phm | maximum |  | 2023 | Summer | 50 | 16562 | 25.5412 | 52.1386 | 202503 | MVA | central
zone_sub | phm | maximum |  | 2024 | Summer | 10 | 16854 | 27.7496 | 58.7282 | 202503 | MVA | central
zone_sub | phm | maximum |  | 2024 | Summer | 50 | 16854 | 27.7496 | 52.8621 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2025 | Summer | 10 |  |  | 75.5207 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2025 | Summer | 50 |  |  | 69.621 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2026 | Summer | 10 |  |  | 79.8845 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2026 | Summer | 50 |  |  | 74.1527 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2027 | Summer | 10 |  |  | 79.6008 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2027 | Summer | 50 |  |  | 73.9998 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2028 | Summer | 10 |  |  | 79.5894 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2028 | Summer | 50 |  |  | 73.965 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2029 | Summer | 10 |  |  | 80.0199 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2029 | Summer | 50 |  |  | 74.4648 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2030 | Summer | 10 |  |  | 81.1895 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2030 | Summer | 50 |  |  | 75.0153 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2031 | Summer | 10 |  |  | 81.9552 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2031 | Summer | 50 |  |  | 76.1566 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2032 | Summer | 10 |  |  | 82.7146 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2032 | Summer | 50 |  |  | 76.9783 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2033 | Summer | 10 |  |  | 83.6062 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2033 | Summer | 50 |  |  | 77.4148 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2034 | Summer | 10 |  |  | 84.4206 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2034 | Summer | 50 |  |  | 77.8841 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2035 | Summer | 10 |  |  | 85.2206 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2035 | Summer | 50 |  |  | 78.3211 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2036 | Summer | 10 |  |  | 85.2937 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2036 | Summer | 50 |  |  | 79.127 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2037 | Summer | 10 |  |  | 86.2309 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2037 | Summer | 50 |  |  | 80.1321 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2038 | Summer | 10 |  |  | 85.4841 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2038 | Summer | 50 |  |  | 80.0404 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2039 | Summer | 10 |  |  | 79.3417 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2039 | Summer | 50 |  |  | 73.3195 | 202503 | MVA | central
zone_sub | llg | maximum |  | 2022 | Summer | 10 | 7174 | 11.5134 | 25.3928 | 202503 | MVA | central
zone_sub | llg | maximum |  | 2022 | Summer | 50 | 7174 | 11.5134 | 23.4346 | 202503 | MVA | central
zone_sub | llg | maximum |  | 2023 | Summer | 10 | 7235 | 12.7349 | 25.4543 | 202503 | MVA | central
zone_sub | llg | maximum |  | 2023 | Summer | 50 | 7235 | 12.7349 | 23.4406 | 202503 | MVA | central
zone_sub | llg | maximum |  | 2024 | Summer | 10 | 7295 | 13.7538 | 25.544 | 202503 | MVA | central
zone_sub | llg | maximum |  | 2024 | Summer | 50 | 7295 | 13.7538 | 23.5081 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2025 | Summer | 10 |  |  | 28.7312 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2025 | Summer | 50 |  |  | 26.0976 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2026 | Summer | 10 |  |  | 33.0834 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2026 | Summer | 50 |  |  | 30.4575 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2027 | Summer | 10 |  |  | 33.0249 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2027 | Summer | 50 |  |  | 30.4247 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2028 | Summer | 10 |  |  | 33.0633 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2028 | Summer | 50 |  |  | 30.3952 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2029 | Summer | 10 |  |  | 33.1822 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2029 | Summer | 50 |  |  | 30.8677 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2030 | Summer | 10 |  |  | 33.5865 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2030 | Summer | 50 |  |  | 31.5616 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2031 | Summer | 10 |  |  | 33.8573 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2031 | Summer | 50 |  |  | 32.037 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2032 | Summer | 10 |  |  | 34.0794 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2032 | Summer | 50 |  |  | 31.4591 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2033 | Summer | 10 |  |  | 34.1121 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2033 | Summer | 50 |  |  | 31.5166 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2034 | Summer | 10 |  |  | 34.3124 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2034 | Summer | 50 |  |  | 31.792 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2035 | Summer | 10 |  |  | 34.3834 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2035 | Summer | 50 |  |  | 32.8827 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2036 | Summer | 10 |  |  | 34.3832 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2036 | Summer | 50 |  |  | 31.8492 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2037 | Summer | 10 |  |  | 34.3374 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2037 | Summer | 50 |  |  | 31.7885 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2038 | Summer | 10 |  |  | 34.3276 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2038 | Summer | 50 |  |  | 31.7234 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2039 | Summer | 10 |  |  | 32.6827 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2039 | Summer | 50 |  |  | 30.3101 | 202503 | MVA | central
zone_sub | wgi | maximum |  | 2022 | Summer | 10 | 21696 | 27.3902 | 50.299 | 202503 | MVA | east
zone_sub | wgi | maximum |  | 2022 | Summer | 50 | 21696 | 27.3902 | 41.2414 | 202503 | MVA | east
zone_sub | wgi | maximum |  | 2023 | Summer | 10 | 22045 | 30.4273 | 50.6919 | 202503 | MVA | east
zone_sub | wgi | maximum |  | 2023 | Summer | 50 | 22045 | 30.4273 | 41.4384 | 202503 | MVA | east
zone_sub | wgi | maximum |  | 2024 | Summer | 10 | 22388 | 33.5461 | 51.0465 | 202503 | MVA | east
zone_sub | wgi | maximum |  | 2024 | Summer | 50 | 22388 | 33.5461 | 41.5121 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2025 | Summer | 10 |  |  | 54.5057 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2025 | Summer | 50 |  |  | 44.6075 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2026 | Summer | 10 |  |  | 54.6012 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2026 | Summer | 50 |  |  | 44.9185 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2027 | Summer | 10 |  |  | 54.4983 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2027 | Summer | 50 |  |  | 44.7661 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2028 | Summer | 10 |  |  | 54.5247 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2028 | Summer | 50 |  |  | 44.911 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2029 | Summer | 10 |  |  | 54.7136 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2029 | Summer | 50 |  |  | 44.9706 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2030 | Summer | 10 |  |  | 55.0965 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2030 | Summer | 50 |  |  | 45.1615 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2031 | Summer | 10 |  |  | 55.7707 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2031 | Summer | 50 |  |  | 45.5541 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2032 | Summer | 50 |  |  | 45.8843 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2032 | Summer | 10 |  |  | 56.122 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2033 | Summer | 10 |  |  | 56.3761 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2033 | Summer | 50 |  |  | 46.0363 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2034 | Summer | 10 |  |  | 56.7608 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2034 | Summer | 50 |  |  | 45.9008 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2035 | Summer | 10 |  |  | 57.2519 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2035 | Summer | 50 |  |  | 46.4689 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2036 | Summer | 10 |  |  | 57.8457 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2036 | Summer | 50 |  |  | 46.559 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2037 | Summer | 10 |  |  | 58.1569 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2037 | Summer | 50 |  |  | 46.4523 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2038 | Summer | 10 |  |  | 58.056 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2038 | Summer | 50 |  |  | 46.6661 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2039 | Summer | 10 |  |  | 56.811 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2039 | Summer | 50 |  |  | 45.5652 | 202503 | MVA | east

## Forecast- Winter
Forecasting Application - 13/10/2025
asset_type | asset | extremum | scenario | demand_year | season | poe | customer_count | pv_capacity | value | forecast_round | unit | region
zone_sub | cln | maximum |  | 2022 | Winter | 10 | 38619 | 72.2578 | 63.0362 | 202503 | MVA | central
zone_sub | cln | maximum |  | 2022 | Winter | 50 | 38619 | 72.2578 | 58.8161 | 202503 | MVA | central
zone_sub | cln | maximum |  | 2023 | Winter | 10 | 41429 | 81.3604 | 67.9918 | 202503 | MVA | central
zone_sub | cln | maximum |  | 2023 | Winter | 50 | 41429 | 81.3604 | 63.4647 | 202503 | MVA | central
zone_sub | cln | maximum |  | 2024 | Winter | 10 | 44846 | 94.6588 | 74.018 | 202503 | MVA | central
zone_sub | cln | maximum |  | 2024 | Winter | 50 | 44846 | 94.6588 | 69.1182 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2025 | Winter | 10 |  |  | 89.4372 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2025 | Winter | 50 |  |  | 84.5179 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2026 | Winter | 10 |  |  | 93.2911 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2026 | Winter | 50 |  |  | 88.1502 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2027 | Winter | 10 |  |  | 98.0701 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2027 | Winter | 50 |  |  | 92.8679 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2028 | Winter | 10 |  |  | 102.5171 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2028 | Winter | 50 |  |  | 97.437 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2029 | Winter | 10 |  |  | 107.2692 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2029 | Winter | 50 |  |  | 101.4753 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2030 | Winter | 10 |  |  | 112.2902 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2030 | Winter | 50 |  |  | 107.1286 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2031 | Winter | 10 |  |  | 119.5588 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2031 | Winter | 50 |  |  | 113.3315 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2032 | Winter | 10 |  |  | 125.8642 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2032 | Winter | 50 |  |  | 119.6901 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2033 | Winter | 10 |  |  | 131.807 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2033 | Winter | 50 |  |  | 125.9989 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2034 | Winter | 10 |  |  | 137.993 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2034 | Winter | 50 |  |  | 131.579 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2035 | Winter | 10 |  |  | 145.465 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2035 | Winter | 50 |  |  | 137.6925 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2036 | Winter | 10 |  |  | 147.8036 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2036 | Winter | 50 |  |  | 139.8743 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2037 | Winter | 10 |  |  | 155.8793 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2037 | Winter | 50 |  |  | 147.8441 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2038 | Winter | 10 |  |  | 163.4009 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2038 | Winter | 50 |  |  | 156.1056 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2039 | Winter | 10 |  |  | 133.5693 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2039 | Winter | 50 |  |  | 127.2077 | 202503 | MVA | central
zone_sub | cre | maximum |  | 2022 | Winter | 10 | 24937 | 39.5122 | 50.635 | 202503 | MVA | central
zone_sub | cre | maximum |  | 2022 | Winter | 50 | 24937 | 39.5122 | 48.3881 | 202503 | MVA | central
zone_sub | cre | maximum |  | 2023 | Winter | 10 | 25835 | 43.8704 | 52.4586 | 202503 | MVA | central
zone_sub | cre | maximum |  | 2023 | Winter | 50 | 25835 | 43.8704 | 50.1308 | 202503 | MVA | central
zone_sub | cre | maximum |  | 2024 | Winter | 10 | 26314 | 48.9572 | 53.4328 | 202503 | MVA | central
zone_sub | cre | maximum |  | 2024 | Winter | 50 | 26314 | 48.9572 | 51.0617 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2025 | Winter | 10 |  |  | 68.4471 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2025 | Winter | 50 |  |  | 65.7336 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2026 | Winter | 10 |  |  | 69.4459 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2026 | Winter | 50 |  |  | 66.605 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2027 | Winter | 10 |  |  | 69.249 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2027 | Winter | 50 |  |  | 66.728 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2028 | Winter | 10 |  |  | 74.3386 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2028 | Winter | 50 |  |  | 72.0847 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2029 | Winter | 10 |  |  | 74.5773 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2029 | Winter | 50 |  |  | 72.2361 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2030 | Winter | 10 |  |  | 76.3193 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2030 | Winter | 50 |  |  | 74.0669 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2031 | Winter | 10 |  |  | 77.7248 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2031 | Winter | 50 |  |  | 75.6012 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2032 | Winter | 10 |  |  | 79.2116 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2032 | Winter | 50 |  |  | 76.7507 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2033 | Winter | 10 |  |  | 79.7367 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2033 | Winter | 50 |  |  | 77.8762 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2034 | Winter | 10 |  |  | 80.3545 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2034 | Winter | 50 |  |  | 78.6625 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2035 | Winter | 10 |  |  | 81.081 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2035 | Winter | 50 |  |  | 79.0014 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2036 | Winter | 10 |  |  | 80.0375 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2036 | Winter | 50 |  |  | 78.1499 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2037 | Winter | 10 |  |  | 83.4116 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2037 | Winter | 50 |  |  | 80.9567 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2038 | Winter | 10 |  |  | 84.3767 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2038 | Winter | 50 |  |  | 81.4995 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2039 | Winter | 10 |  |  | 72.4681 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2039 | Winter | 50 |  |  | 69.0004 | 202503 | MVA | central
zone_sub | epg | maximum |  | 2022 | Winter | 10 | 29371 | 40.0067 | 65.9271 | 202503 | MVA | central
zone_sub | epg | maximum |  | 2022 | Winter | 50 | 29371 | 40.0067 | 59.4269 | 202503 | MVA | central
zone_sub | epg | maximum |  | 2023 | Winter | 10 | 30422 | 45.1511 | 68.3101 | 202503 | MVA | central
zone_sub | epg | maximum |  | 2023 | Winter | 50 | 30422 | 45.1511 | 61.7598 | 202503 | MVA | central
zone_sub | epg | maximum |  | 2024 | Winter | 50 | 32118 | 51.557 | 65.5719 | 202503 | MVA | central
zone_sub | epg | maximum |  | 2024 | Winter | 10 | 32118 | 51.557 | 72.1952 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2025 | Winter | 10 |  |  | 85.9871 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2025 | Winter | 50 |  |  | 79.3939 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2026 | Winter | 10 |  |  | 95.0802 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2026 | Winter | 50 |  |  | 89.3565 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2027 | Winter | 10 |  |  | 100.5082 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2027 | Winter | 50 |  |  | 92.7492 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2028 | Winter | 10 |  |  | 99.8778 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2028 | Winter | 50 |  |  | 93.3308 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2029 | Winter | 10 |  |  | 103.1049 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2029 | Winter | 50 |  |  | 96.5577 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2030 | Winter | 10 |  |  | 109.1359 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2030 | Winter | 50 |  |  | 102.3455 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2031 | Winter | 10 |  |  | 112.51 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2031 | Winter | 50 |  |  | 104.2867 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2032 | Winter | 10 |  |  | 121.7799 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2032 | Winter | 50 |  |  | 114.0182 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2033 | Winter | 10 |  |  | 127.6696 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2033 | Winter | 50 |  |  | 119.7255 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2034 | Winter | 10 |  |  | 133.3287 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2034 | Winter | 50 |  |  | 125.5482 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2035 | Winter | 10 |  |  | 135.1129 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2035 | Winter | 50 |  |  | 126.6853 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2036 | Winter | 10 |  |  | 142.2751 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2036 | Winter | 50 |  |  | 134.3407 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2037 | Winter | 10 |  |  | 149.629 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2037 | Winter | 50 |  |  | 142.1357 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2038 | Winter | 10 |  |  | 150.109 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2038 | Winter | 50 |  |  | 141.9626 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2039 | Winter | 10 |  |  | 116.0207 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2039 | Winter | 50 |  |  | 101.3122 | 202503 | MVA | central
zone_sub | klo | maximum |  | 2022 | Winter | 10 | 14879 | 23.0226 | 48.7862 | 202503 | MVA | central
zone_sub | klo | maximum |  | 2022 | Winter | 50 | 14879 | 23.0226 | 43.3886 | 202503 | MVA | central
zone_sub | klo | maximum |  | 2023 | Winter | 10 | 17175 | 27.7177 | 56.3067 | 202503 | MVA | central
zone_sub | klo | maximum |  | 2023 | Winter | 50 | 17175 | 27.7177 | 50.077 | 202503 | MVA | central
zone_sub | klo | maximum |  | 2024 | Winter | 10 | 19951 | 34.2052 | 65.4015 | 202503 | MVA | central
zone_sub | klo | maximum |  | 2024 | Winter | 50 | 19951 | 34.2052 | 58.1655 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2025 | Winter | 10 |  |  | 79.8942 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2025 | Winter | 50 |  |  | 72.3119 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2026 | Winter | 10 |  |  | 92.3723 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2026 | Winter | 50 |  |  | 83.7626 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2027 | Winter | 10 |  |  | 102.9502 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2027 | Winter | 50 |  |  | 93.3778 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2028 | Winter | 10 |  |  | 120.3965 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2028 | Winter | 50 |  |  | 109.8362 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2029 | Winter | 10 |  |  | 129.7211 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2029 | Winter | 50 |  |  | 118.6301 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2030 | Winter | 10 |  |  | 142.5707 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2030 | Winter | 50 |  |  | 129.8167 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2031 | Winter | 10 |  |  | 159.4027 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2031 | Winter | 50 |  |  | 143.8497 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2032 | Winter | 10 |  |  | 178.8568 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2032 | Winter | 50 |  |  | 161.743 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2033 | Winter | 10 |  |  | 196.8658 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2033 | Winter | 50 |  |  | 178.8635 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2034 | Winter | 10 |  |  | 214.3536 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2034 | Winter | 50 |  |  | 194.8729 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2035 | Winter | 10 |  |  | 235.0946 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2035 | Winter | 50 |  |  | 213.0243 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2036 | Winter | 10 |  |  | 246.5584 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2036 | Winter | 50 |  |  | 225.0657 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2037 | Winter | 10 |  |  | 273.2503 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2037 | Winter | 50 |  |  | 249.8153 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2038 | Winter | 10 |  |  | 298.8878 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2038 | Winter | 50 |  |  | 271.7276 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2039 | Winter | 10 |  |  | 252.4111 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2039 | Winter | 50 |  |  | 227.0702 | 202503 | MVA | central
zone_sub | llg | maximum |  | 2022 | Winter | 10 | 7174 | 11.5134 | 22.426 | 202503 | MVA | central
zone_sub | llg | maximum |  | 2022 | Winter | 50 | 7174 | 11.5134 | 20.2322 | 202503 | MVA | central
zone_sub | llg | maximum |  | 2023 | Winter | 10 | 7235 | 12.7349 | 22.5982 | 202503 | MVA | central
zone_sub | llg | maximum |  | 2023 | Winter | 50 | 7235 | 12.7349 | 20.4035 | 202503 | MVA | central
zone_sub | llg | maximum |  | 2024 | Winter | 10 | 7295 | 13.7538 | 22.7705 | 202503 | MVA | central
zone_sub | llg | maximum |  | 2024 | Winter | 50 | 7295 | 13.7538 | 20.5738 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2025 | Winter | 10 |  |  | 26.1225 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2025 | Winter | 50 |  |  | 23.9159 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2026 | Winter | 10 |  |  | 30.6829 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2026 | Winter | 50 |  |  | 28.4398 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2027 | Winter | 10 |  |  | 31.049 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2027 | Winter | 50 |  |  | 28.8402 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2028 | Winter | 10 |  |  | 31.3064 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2028 | Winter | 50 |  |  | 29.108 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2029 | Winter | 10 |  |  | 31.5714 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2029 | Winter | 50 |  |  | 29.4846 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2030 | Winter | 10 |  |  | 32.5932 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2030 | Winter | 50 |  |  | 30.3426 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2031 | Winter | 10 |  |  | 33.1905 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2031 | Winter | 50 |  |  | 31.0163 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2032 | Winter | 10 |  |  | 33.8014 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2032 | Winter | 50 |  |  | 31.6154 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2033 | Winter | 10 |  |  | 34.0793 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2033 | Winter | 50 |  |  | 31.8255 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2034 | Winter | 10 |  |  | 34.2253 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2034 | Winter | 50 |  |  | 32.0656 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2035 | Winter | 10 |  |  | 33.7185 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2035 | Winter | 50 |  |  | 31.7299 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2036 | Winter | 10 |  |  | 33.9832 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2036 | Winter | 50 |  |  | 31.9069 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2037 | Winter | 10 |  |  | 34.9987 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2037 | Winter | 50 |  |  | 32.7389 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2038 | Winter | 10 |  |  | 34.5209 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2038 | Winter | 50 |  |  | 32.3709 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2039 | Winter | 10 |  |  | 28.3277 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2039 | Winter | 50 |  |  | 26.2847 | 202503 | MVA | central
zone_sub | ofr | maximum |  | 2022 | Winter | 10 | 23246 | 35.5119 | 49.8939 | 202503 | MVA | central
zone_sub | ofr | maximum |  | 2022 | Winter | 50 | 23246 | 35.5119 | 46.8764 | 202503 | MVA | central
zone_sub | ofr | maximum |  | 2023 | Winter | 10 | 24109 | 39.5748 | 51.7437 | 202503 | MVA | central
zone_sub | ofr | maximum |  | 2023 | Winter | 50 | 24109 | 39.5748 | 48.6149 | 202503 | MVA | central
zone_sub | ofr | maximum |  | 2024 | Winter | 10 | 24997 | 44.4669 | 53.6497 | 202503 | MVA | central
zone_sub | ofr | maximum |  | 2024 | Winter | 50 | 24997 | 44.4669 | 50.4065 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2025 | Winter | 10 |  |  | 59.4536 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2025 | Winter | 50 |  |  | 56.1183 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2026 | Winter | 10 |  |  | 66.5595 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2026 | Winter | 50 |  |  | 63.2802 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2027 | Winter | 10 |  |  | 72.8129 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2027 | Winter | 50 |  |  | 69.3039 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2028 | Winter | 10 |  |  | 76.0509 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2028 | Winter | 50 |  |  | 72.5305 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2029 | Winter | 10 |  |  | 78.6773 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2029 | Winter | 50 |  |  | 74.8582 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2030 | Winter | 10 |  |  | 81.1629 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2030 | Winter | 50 |  |  | 77.5373 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2031 | Winter | 10 |  |  | 83.2732 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2031 | Winter | 50 |  |  | 79.5294 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2032 | Winter | 10 |  |  | 85.4834 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2032 | Winter | 50 |  |  | 81.7407 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2033 | Winter | 10 |  |  | 86.4197 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2033 | Winter | 50 |  |  | 82.8706 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2034 | Winter | 10 |  |  | 87.7259 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2034 | Winter | 50 |  |  | 83.8526 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2035 | Winter | 10 |  |  | 90.1815 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2035 | Winter | 50 |  |  | 86.3425 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2036 | Winter | 10 |  |  | 89.3155 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2036 | Winter | 50 |  |  | 84.7668 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2037 | Winter | 10 |  |  | 92.5351 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2037 | Winter | 50 |  |  | 88.8524 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2038 | Winter | 10 |  |  | 94.3753 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2038 | Winter | 50 |  |  | 94.1939 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2039 | Winter | 10 |  |  | 80.6717 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2039 | Winter | 50 |  |  | 77.1549 | 202503 | MVA | central
zone_sub | phm | maximum |  | 2022 | Winter | 10 | 16270 | 23.521 | 48.1658 | 202503 | MVA | central
zone_sub | phm | maximum |  | 2022 | Winter | 50 | 16270 | 23.521 | 45.1092 | 202503 | MVA | central
zone_sub | phm | maximum |  | 2023 | Winter | 10 | 16562 | 25.5412 | 49.0318 | 202503 | MVA | central
zone_sub | phm | maximum |  | 2023 | Winter | 50 | 16562 | 25.5412 | 45.9202 | 202503 | MVA | central
zone_sub | phm | maximum |  | 2024 | Winter | 10 | 16854 | 27.7496 | 49.8978 | 202503 | MVA | central
zone_sub | phm | maximum |  | 2024 | Winter | 50 | 16854 | 27.7496 | 46.7311 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2025 | Winter | 10 |  |  | 67.0847 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2025 | Winter | 50 |  |  | 64.1376 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2026 | Winter | 10 |  |  | 71.7531 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2026 | Winter | 50 |  |  | 68.6294 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2027 | Winter | 10 |  |  | 72.4584 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2027 | Winter | 50 |  |  | 69.3785 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2028 | Winter | 10 |  |  | 72.887 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2028 | Winter | 50 |  |  | 69.9467 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2029 | Winter | 10 |  |  | 73.8781 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2029 | Winter | 50 |  |  | 70.9603 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2030 | Winter | 10 |  |  | 76.2493 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2030 | Winter | 50 |  |  | 73.2946 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2031 | Winter | 10 |  |  | 77.5227 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2031 | Winter | 50 |  |  | 74.8388 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2032 | Winter | 10 |  |  | 79.9897 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2032 | Winter | 50 |  |  | 76.8149 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2033 | Winter | 10 |  |  | 87.5343 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2033 | Winter | 50 |  |  | 77.8299 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2034 | Winter | 10 |  |  | 81.2629 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2034 | Winter | 50 |  |  | 78.7091 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2035 | Winter | 10 |  |  | 80.0205 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2035 | Winter | 50 |  |  | 77.0055 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2036 | Winter | 10 |  |  | 81.6454 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2036 | Winter | 50 |  |  | 78.9538 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2037 | Winter | 10 |  |  | 85.2253 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2037 | Winter | 50 |  |  | 82.0295 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2038 | Winter | 10 |  |  | 82.7648 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2038 | Winter | 50 |  |  | 79.6564 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2039 | Winter | 10 |  |  | 67.0558 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2039 | Winter | 50 |  |  | 63.9852 | 202503 | MVA | central
zone_sub | wgi | maximum |  | 2022 | Winter | 10 | 21696 | 27.3902 | 41.941 | 202503 | MVA | east
zone_sub | wgi | maximum |  | 2022 | Winter | 50 | 21696 | 27.3902 | 38.234 | 202503 | MVA | east
zone_sub | wgi | maximum |  | 2023 | Winter | 10 | 22045 | 30.4273 | 42.6315 | 202503 | MVA | east
zone_sub | wgi | maximum |  | 2023 | Winter | 50 | 22045 | 30.4273 | 38.883 | 202503 | MVA | east
zone_sub | wgi | maximum |  | 2024 | Winter | 10 | 22388 | 33.5461 | 43.3126 | 202503 | MVA | east
zone_sub | wgi | maximum |  | 2024 | Winter | 50 | 22388 | 33.5461 | 39.5207 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2025 | Winter | 10 |  |  | 47.2482 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2025 | Winter | 50 |  |  | 43.6466 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2026 | Winter | 10 |  |  | 47.6557 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2026 | Winter | 50 |  |  | 44.0841 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2027 | Winter | 10 |  |  | 49.0622 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2027 | Winter | 50 |  |  | 44.625 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2028 | Winter | 10 |  |  | 49.028 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2028 | Winter | 50 |  |  | 45.3431 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2029 | Winter | 10 |  |  | 49.3373 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2029 | Winter | 50 |  |  | 46.0239 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2030 | Winter | 10 |  |  | 50.5469 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2030 | Winter | 50 |  |  | 47.2137 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2031 | Winter | 10 |  |  | 54.0224 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2031 | Winter | 50 |  |  | 50.206 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2032 | Winter | 10 |  |  | 55.4565 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2032 | Winter | 50 |  |  | 51.8155 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2033 | Winter | 10 |  |  | 54.099 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2033 | Winter | 50 |  |  | 50.6413 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2034 | Winter | 10 |  |  | 57.8491 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2034 | Winter | 50 |  |  | 54.2764 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2035 | Winter | 10 |  |  | 56.2746 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2035 | Winter | 50 |  |  | 54.9313 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2036 | Winter | 10 |  |  | 57.6913 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2036 | Winter | 50 |  |  | 55.4021 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2037 | Winter | 10 |  |  | 58.7122 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2037 | Winter | 50 |  |  | 57.6212 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2038 | Winter | 10 |  |  | 58.2928 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2038 | Winter | 50 |  |  | 57.9824 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2039 | Winter | 10 |  |  | 49.2493 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2039 | Winter | 50 |  |  | 45.4578 | 202503 | MVA | east

## Ratings
STATION OUTPUT RATING (TRANSFORMER SUMMATION) SUMMARY
|  |  | Station N Rating |  | Station N-1 Rating |  | Station N-2 Rating
|  |  | SCR | WCR | SCR | WCR | SCR | WCR | Remarks | Remarks | Bus Target | Station Cap Bank
S/S Name | No. TX | Name Plate MVA | MVA | MVA | MVA | MVA | MVA | MVA | For N-1 Ratings | N-2 | Voltage kV | MVAr
CLN_Old | 2 | 66 | 87.3 | 95.3 | 44.6 | 48.9 | 0 | 0 | Loss of T1 |  | 22 | 12
CLN | 3 | 99 | 130.95 | 142.95 | 89.2 | 97.8 | 44.6 | 48.9
CRE | 2 | 66 | 84.3 | 93.8 | 41.1 | 46.3 | 0 | 0 | Loss of T2 or T3 |  | 22 | 12
EPG | 3 | 99 | 123.1 | 139.9 | 87.8 | 98.1 | 43.9 | 49.05 | Loss of T3 | Using Highest value | 22
KLO | 2 | 66 | 97.5 | 97.5 | 49.1 | 49.1 | 0 | 0 | Loss of T1 or T2 |  | 22.44 | 6
LLG | 1 | 33 | 47.4 | 48.3 | 0 | 0 | 0 | 0 | N rating only |  | 22 | 4
OFR | 2 | 66 | 93.2 | 93.2 | 45.2 | 48 | 0 | 0 | Loss of T1 or T2 |  | 22 | 6
PHM | 2 | 66 | 91.9 | 95.7 | 45 | 49.1 | 0 | 0 | Loss of T1 or T2 |  | 22 | 12
WGI | 3 | 40.5 | 55.8 | 56.8 | 35.3 | 36.1 | 17.65 | 18.05

## Power Factor
asset_type | asset | PF
zone_sub | cln | 1
zone_sub | cre | 1
zone_sub | cyn | 1
zone_sub | epg | 1
zone_sub | klo | 0.99
zone_sub | llg | 0.99
zone_sub | ofr | 1
zone_sub | phm | 1
zone_sub | wgi | 0.99

## FT
Forecast tool (MVA) |  | Forecast Capacity & Transfers
ZSS |  | WGI
Summer
[5 empty] | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads
DY (Apr 1 to Mar 30) |  | 2022/23 | 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2028/29 | 2029/30 | 2030/31 | 2031/32 | 2032/33 | 2033/34 | 2034/35 | 2035/36 | 2036/37 | 2037/38 | 2038/39
DY (Apr 1 to Mar 30) |  | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038
FY (Jul 1 to Jun 30) |  | 2022/23 | 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2028/29 | 2029/30 | 2030/31 | 2031/32 | 2032/33 | 2033/34 | 2034/35 | 2035/36 | 2036/37 | 2037/38 | 2038/39
FY (Jul 1 to Jun 30) |  |  |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39
Summer POE50 | 50 |  |  | 41.5121 | 44.6075 | 44.9185 | 44.7661 | 44.911 | 44.9706 | 45.1615 | 45.5541 | 45.8843 | 46.0363 | 45.9008 | 46.4689 | 46.559 | 46.4523 | 46.6661
Summer POE10 | 10 |  |  | 51.0465 | 54.5057 | 54.6012 | 54.4983 | 54.5247 | 54.7136 | 55.0965 | 55.7707 | 56.122 | 56.3761 | 56.7608 | 57.2519 | 57.8457 | 58.1569 | 58.056
Winter
[5 empty] | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads
DM (Apr 1 to Mar 30) |  |  |  | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2028/29 | 2029/30 | 2030/31 | 2031/32 | 2032/33 | 2033/34 | 2034/35 | 2035/36 | 2036/37 | 2037/38 | 2038/39
DY (Apr 1 to Mar 30) |  |  |  | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038
FY (Jul 1 to Jun 30) |  |  |  | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2028/29 | 2029/30 | 2030/31 | 2031/32 | 2032/33 | 2033/34 | 2034/35 | 2035/36 | 2036/37 | 2037/38 | 2038/39
FY (Jul 1 to Jun 30) |  |  |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39
Winter POE50 | 50 |  |  | 39.5207 | 43.6466 | 44.0841 | 44.625 | 45.3431 | 46.0239 | 47.2137 | 50.206 | 51.8155 | 50.6413 | 54.2764 | 54.9313 | 55.4021 | 57.6212 | 57.9824
Winter POE10 | 10 |  |  | 43.3126 | 47.2482 | 47.6557 | 49.0622 | 49.028 | 49.3373 | 50.5469 | 54.0224 | 55.4565 | 54.099 | 57.8491 | 56.2746 | 57.6913 | 58.7122 | 58.2928
Transfers (MVA)
|  | Feeder | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39
|  | WGI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | PowerFactor | 0.99

## Load Duration Curves
Station
WGI
POE10
[6 empty] | Stations | KLO |  | EPG |  | CRE |  | CLN |  | PHM |  | OFR |  | LLG |  | WGI
| % of MD | Winter - MD (P10) - Duration % | Winter - MD - Hours | Summer - MD - Duration % | Summer - MD - Hours | %MD | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration %
| 100% | 0% | 0 | 0% | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| 99% | 0.006767% | 0.2972 | 0% | 0 | 99% | 0.01722% | 0.02707% | 0% | 0.04737% | 0% | 0% | 0.00861% | 0.01353% | 0.03444% | 0.03383% | 0.01722% | 0.0203% | 0.02583% | 0.006767% | 0% | 0.006767%
| 98% | 0.006767% | 0.2972 | 0% | 0 | 98% | 0.01722% | 0.07443% | 0.00861% | 0.08797% | 0.02583% | 0.01353% | 0.02583% | 0.0203% | 0.05166% | 0.07443% | 0.02583% | 0.0812% | 0.04305% | 0.0203% | 0% | 0.006767%
| 97% | 0.006767% | 0.2972 | 0.00861% | 0.37816 | 97% | 0.02583% | 0.09474% | 0.02583% | 0.1421% | 0.04305% | 0.02707% | 0.05166% | 0.03383% | 0.0861% | 0.1556% | 0.04305% | 0.1083% | 0.05166% | 0.04737% | 0.00861% | 0.006767%
| 95% | 0.03383% | 1.486 | 0.00861% | 0.37816 | 95% | 0.05166% | 0.1895% | 0.09471% | 0.3519% | 0.0861% | 0.08797% | 0.1033% | 0.05413% | 0.1378% | 0.3992% | 0.07749% | 0.1759% | 0.09471% | 0.09474% | 0.00861% | 0.03383%
| 90% | 0.1962% | 8.6188 | 0.01722% | 0.75633 | 90% | 0.0861% | 0.9135% | 0.1894% | 1.786% | 0.1894% | 0.7579% | 0.1808% | 0.07443% | 0.3702% | 1.793% | 0.2066% | 0.8932% | 0.353% | 0.2639% | 0.01722% | 0.1962%
| 85% | 0.9135% | 40.1218 | 0.02583% | 1.1345 | 85% | 0.1205% | 2.355% | 0.353% | 4.588% | 0.2669% | 2.761% | 0.3272% | 0.318% | 0.6027% | 5.393% | 0.3702% | 2.68% | 0.7147% | 0.7443% | 0.02583% | 0.9135%
| 80% | 2.118% | 93.0231 | 0.06027% | 2.6471 | 80% | 0.31% | 5.616% | 0.6458% | 8.885% | 0.4219% | 6.787% | 0.4477% | 0.9406% | 0.7749% | 11.33% | 0.5683% | 6.11% | 1.317% | 1.915% | 0.06027% | 2.118%
| 75% | 4.486% | 197.0426 | 0.07749% | 3.4035 | 75% | 0.4822% | 9.995% | 0.9988% | 14.05% | 0.5338% | 11.76% | 0.5855% | 2.876% | 1.102% | 18.3% | 0.7491% | 10.38% | 2.764% | 4.601% | 0.07749% | 4.486%
| 70% | 8.607% | 378.0365 | 0.1292% | 5.6725 | 70% | 0.7491% | 14.12% | 1.498% | 19.88% | 0.8438% | 17.56% | 0.7921% | 7.376% | 1.739% | 26.3% | 0.9557% | 15.73% | 6.225% | 8.837% | 0.1292% | 8.607%
| 65% | 14.03% | 616.0926 | 0.1464% | 6.4288 | 65% | 1.154% | 18.84% | 2.265% | 27.11% | 1.102% | 25.21% | 1.05% | 12.51% | 2.6% | 35.36% | 1.541% | 22.03% | 12.05% | 15.25% | 0.1464% | 14.03%
| 60% | 21.29% | 934.9866 | 0.2583% | 11.3449 | 60% | 1.602% | 25.14% | 3.203% | 35.21% | 1.627% | 33.62% | 1.748% | 18.2% | 4.055% | 46.14% | 2.247% | 29.44% | 20.92% | 25.15% | 0.2583% | 21.29%
| 55% | 29.85% | 1310.9428 | 0.8094% | 35.5474 | 55% | 2.411% | 33.56% | 4.357% | 45.33% | 2.48% | 42.68% | 2.419% | 25.42% | 7.095% | 59.16% | 3.496% | 37.5% | 33.11% | 37.15% | 0.8094% | 29.85%
| 50% | 39.4% | 1730.2899 | 2.17% | 95.2974 | 50% | 4.598% | 44.25% | 6.303% | 58.26% | 3.84% | 54.87% | 4.064% | 34.04% | 14.48% | 73.62% | 5.881% | 47.91% | 47.93% | 51.32% | 2.17% | 39.4%
| 45% | 49.36% | 2168.0633 | 4.753% | 208.7467 | 45% | 9.592% | 58.98% | 10.8% | 69.36% | 6.535% | 71.48% | 8.378% | 45.63% | 26.86% | 85.96% | 11.13% | 62.3% | 62.8% | 65.85% | 4.753% | 49.36%
| 40% | 59.42% | 2609.7004 | 8.662% | 380.4333 | 40% | 19.83% | 71.65% | 21.2% | 75.98% | 14.01% | 84.31% | 16.88% | 65.51% | 41.17% | 92.73% | 21.13% | 79.32% | 76.24% | 79.08% | 8.662% | 59.42%
| 35% | 68.26% | 2998.1389 | 15.86% | 696.5786 | 35% | 37.74% | 78.94% | 37.58% | 85.16% | 27.53% | 88.52% | 26.59% | 78.66% | 63.28% | 95.6% | 34.85% | 87.21% | 86.9% | 88.41% | 15.86% | 68.26%
| 30% | 75.35% | 3309.3057 | 28.71% | 1260.7997 | 30% | 66.82% | 83.24% | 57.09% | 93.38% | 49.73% | 90.98% | 45.59% | 83.41% | 86.84% | 97.25% | 59.02% | 90.02% | 92.6% | 93.97% | 28.71% | 75.35%
| 25% | 80.55% | 3537.8514 | 44.75% | 1965.3198 | 25% | 77.33% | 87.43% | 77.75% | 96.1% | 81.07% | 93.44% | 72.26% | 87.95% | 94.88% | 98.4% | 83.32% | 92.46% | 96.47% | 96.66% | 44.75% | 80.55%
| 20% | 84.95% | 3731.0305 | 56.7% | 2490.2118 | 20% | 85.59% | 92.06% | 96.84% | 97.65% | 89.22% | 95.65% | 79.18% | 93.87% | 97.51% | 99.11% | 91.2% | 94.84% | 98.65% | 98.41% | 56.7% | 84.95%
| 15% | 89.03% | 3910.2412 | 68.25% | 2997.7083 | 15% | 96.14% | 98.9% | 99.64% | 98.65% | 96.11% | 97.43% | 86.26% | 99.55% | 99.38% | 99.49% | 97.48% | 97.23% | 99.31% | 99.14% | 68.25% | 89.03%
| 10% | 92.79% | 4075.1864 | 79.5% | 3491.5908 | 10% | 99.99% | 99.99% | 99.99% | 99.16% | 99.9% | 98.78% | 98.3% | 99.6% | 99.99% | 99.7% | 99.99% | 99.59% | 99.63% | 99.41% | 79.5% | 92.79%
| 5% | 96.81% | 4251.7223 | 90.07% | 3955.9766 | 5% | 99.99% | 99.99% | 99.99% | 99.49% | 99.99% | 99.76% | 99.99% | 99.61% | 99.99% | 99.99% | 99.99% | 99.99% | 99.68% | 99.6% | 90.07% | 96.81%
| 9.992e-14% | 99.99% | 4391.7028 | 99.99% | 4391.6218 | 0% | 99.99% | 99.99% | 99.99% | 99.99% | 99.99% | 99.99% | 99.99% | 99.63% | 99.99% | 99.99% | 99.99% | 99.99% | 99.71% | 99.63% | 99.99% | 99.99%
POE 50
[6 empty] | Stations | KLO |  | EPG |  | CRE |  | CLN |  | PHM |  | OFR |  | LLG |  | WGI
| % of MD | Winter - AD (P50) - Duration % | Winter - AD - Hours | Summer - AD - Duration % | Summer - AD - Hours | %MD | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration %
| 100% | 0% | 0 | 0% | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| 99% | 0.006767% | 0.2972 | 0.00861% | 0.37816 | 99% | 0.03444% | 0.02707% | 0.04305% | 0.04737% | 0% | 0% | 0% | 0.01353% | 0% | 0.03383% | 0% | 0.0203% | 0.00861% | 0.006767% | 0.00861% | 0.006767%
| 98% | 0.006767% | 0.2972 | 0.00861% | 0.37816 | 98% | 0.05166% | 0.07443% | 0.07749% | 0.08797% | 0% | 0.01353% | 0.00861% | 0.0203% | 0% | 0.07443% | 0.00861% | 0.0812% | 0.00861% | 0.0203% | 0.00861% | 0.006767%
| 97% | 0.006767% | 0.2972 | 0.00861% | 0.37816 | 97% | 0.06888% | 0.09474% | 0.07749% | 0.1421% | 0.02583% | 0.02707% | 0.01722% | 0.03383% | 0.00861% | 0.1556% | 0.01722% | 0.1083% | 0.01722% | 0.0406% | 0.00861% | 0.006767%
| 95% | 0.03383% | 1.486 | 0.01722% | 0.75633 | 95% | 0.0861% | 0.1895% | 0.1378% | 0.3519% | 0.04305% | 0.08797% | 0.02583% | 0.05413% | 0.05166% | 0.3992% | 0.04305% | 0.1759% | 0.01722% | 0.1015% | 0.01722% | 0.03383%
| 90% | 0.1962% | 8.6188 | 0.2066% | 9.0759 | 90% | 0.1292% | 0.9135% | 0.2583% | 1.786% | 0.1119% | 0.7579% | 0.1033% | 0.07443% | 0.1292% | 1.793% | 0.1033% | 0.8932% | 0.0861% | 0.3451% | 0.2066% | 0.1962%
| 85% | 0.9135% | 40.1218 | 0.9213% | 40.4636 | 85% | 0.2497% | 2.355% | 0.465% | 4.588% | 0.2755% | 2.761% | 0.1808% | 0.318% | 0.3616% | 5.393% | 0.2066% | 2.68% | 0.31% | 0.9% | 0.9213% | 0.9135%
| 80% | 2.118% | 93.0231 | 2.153% | 94.5411 | 80% | 0.4133% | 5.616% | 0.7835% | 8.885% | 0.6113% | 6.787% | 0.2669% | 0.9406% | 0.706% | 11.33% | 0.6286% | 6.11% | 0.8008% | 2.517% | 2.153% | 2.118%
| 75% | 4.486% | 197.0426 | 4.486% | 197.0236 | 75% | 0.8352% | 9.995% | 1.257% | 14.05% | 0.9902% | 11.76% | 0.4047% | 2.876% | 1.662% | 18.3% | 1.309% | 10.38% | 1.834% | 5.562% | 4.486% | 4.486%
| 70% | 8.607% | 378.0365 | 7.672% | 336.9444 | 70% | 1.619% | 14.12% | 2.101% | 19.88% | 1.911% | 17.56% | 0.8008% | 7.376% | 3.427% | 26.3% | 2.419% | 15.73% | 4.374% | 10.11% | 7.672% | 8.607%
| 65% | 14.03% | 616.0926 | 11.87% | 521.4885 | 65% | 3.057% | 18.84% | 4.288% | 27.11% | 3.504% | 25.21% | 1.352% | 12.51% | 8.188% | 35.36% | 4.598% | 22.03% | 9.179% | 17.54% | 11.87% | 14.03%
| 60% | 21.29% | 934.9866 | 18.5% | 812.675 | 60% | 5.528% | 25.14% | 9.342% | 35.21% | 7.758% | 33.62% | 3.573% | 18.2% | 15.71% | 46.14% | 9.17% | 29.44% | 16.83% | 27.53% | 18.5% | 21.29%
| 55% | 29.85% | 1310.9428 | 27.37% | 1202.1843 | 55% | 11.8% | 33.56% | 17.61% | 45.33% | 16.05% | 42.68% | 8.283% | 25.42% | 24.94% | 59.16% | 14.93% | 37.5% | 27.43% | 40.02% | 27.37% | 29.85%
| 50% | 39.4% | 1730.2899 | 38.39% | 1686.2345 | 50% | 21.47% | 44.25% | 28.46% | 58.26% | 24.85% | 54.87% | 17.57% | 34.04% | 37.94% | 73.62% | 22.35% | 47.91% | 40.6% | 54.15% | 38.39% | 39.4%
| 45% | 49.36% | 2168.0633 | 48.48% | 2129.0649 | 45% | 35.07% | 58.98% | 42.44% | 69.36% | 37.15% | 71.48% | 28.59% | 45.63% | 57.06% | 85.96% | 36.95% | 62.3% | 53.97% | 68.39% | 48.48% | 49.36%
| 40% | 59.42% | 2609.7004 | 56.57% | 2484.5393 | 40% | 60.78% | 71.65% | 63.35% | 75.98% | 61.17% | 84.31% | 46.88% | 65.51% | 72.05% | 92.73% | 55.62% | 79.32% | 65.21% | 80.79% | 56.57% | 59.42%
| 35% | 68.26% | 2998.1389 | 63.94% | 2808.248 | 35% | 70.59% | 78.94% | 76.04% | 85.16% | 71.05% | 88.52% | 69.68% | 78.66% | 80.86% | 95.6% | 68.46% | 87.21% | 75.09% | 89.43% | 63.94% | 68.26%
| 30% | 75.35% | 3309.3057 | 70.48% | 3095.6528 | 30% | 76.73% | 83.24% | 80.97% | 93.38% | 75.06% | 90.98% | 76.64% | 83.41% | 85.59% | 97.25% | 74.6% | 90.02% | 81.51% | 94.17% | 70.48% | 75.35%
| 25% | 80.55% | 3537.8514 | 76.48% | 3358.8552 | 25% | 83.08% | 87.43% | 85.41% | 96.1% | 78.56% | 93.44% | 83.93% | 87.95% | 89.4% | 98.4% | 78.93% | 92.46% | 86.44% | 96.81% | 76.48% | 80.55%
| 20% | 84.95% | 3731.0305 | 81.71% | 3588.7791 | 20% | 91.12% | 92.06% | 89.28% | 97.65% | 81.79% | 95.65% | 91.73% | 93.87% | 92.22% | 99.11% | 84.56% | 94.84% | 90.52% | 98.48% | 81.71% | 84.95%
| 15% | 89.03% | 3910.2412 | 86.58% | 3802.4419 | 15% | 99.18% | 98.9% | 92.61% | 98.65% | 86.18% | 97.43% | 98.93% | 99.55% | 94.55% | 99.49% | 92.06% | 97.23% | 93.75% | 99.28% | 86.58% | 89.03%
| 10% | 92.79% | 4075.1864 | 91.64% | 4024.8025 | 10% | 99.99% | 99.99% | 95.16% | 99.16% | 91.73% | 98.78% | 99.75% | 99.6% | 96.73% | 99.7% | 99.06% | 99.59% | 96.19% | 99.59% | 91.64% | 92.79%
| 5% | 96.81% | 4251.7223 | 96.54% | 4239.978 | 5% | 99.99% | 99.99% | 97.15% | 99.49% | 97.84% | 99.76% | 99.99% | 99.61% | 99.31% | 99.99% | 99.99% | 99.99% | 98.14% | 99.77% | 96.54% | 96.81%
| 9.992e-14% | 99.99% | 4391.7028 | 99.99% | 4391.6218 | 0% | 99.99% | 99.99% | 99.99% | 99.99% | 99.99% | 99.99% | 99.99% | 99.63% | 99.99% | 99.99% | 99.99% | 99.99% | 99.78% | 99.99% | 99.99% | 99.99%
POE10
|  | Summer | Winter
| Year | 2019/2020 | 2023
| Start | 2024-10-01 | 2024-04-01
| End | 2025-04-01 | 2024-10-01
| Days | 183 | 183
| Hours | 4392 | 4392
POE50
|  | Summer | Winter
| Year | 2023/2024 | 2023
| Start | 2023-10-01 | 2024-04-01
| End | 2024-04-01 | 2024-10-01
| Days | 183 | 183
| Hours | 4392 | 4392

## Capacity N
Option 1 - Do Nothing - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N Rating (MVA) - Option 1 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8
SCR N Rating (MVA) - Option 1 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8
Planned Additional Capacity (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2 - Replace 3 x 10/13.5 MVA Tx with 3 x 20/33 MVA Tx - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N Rating (MVA) - Option 2 | 56.8 | 56.8 | 56.8 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
SCR N Rating (MVA) - Option 2 | 55.8 | 55.8 | 55.8 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99
Capacity Added (MVA) | 0 | 0 | 0 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2
Option 3 - Replace 1 x 10/13.5 MVA Tx with 1 x 20/33 MVA Tx - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N Rating (MVA) - Option 3 | 56.8 | 56.8 | 56.8 | 72.15 | 72.15 | 72.15 | 72.15 | 72.15 | 72.15 | 72.15 | 72.15 | 72.15 | 72.15 | 72.15 | 72.15 | 72.15 | 72.15 | 72.15 | 72.15 | 72.15 | 72.15 | 72.15 | 72.15 | 72.15 | 72.15 | 72.15 | 72.15 | 72.15 | 72.15 | 72.15
SCR N Rating (MVA) - Option 3 | 55.8 | 55.8 | 55.8 | 71.15 | 71.15 | 71.15 | 71.15 | 71.15 | 71.15 | 71.15 | 71.15 | 71.15 | 71.15 | 71.15 | 71.15 | 71.15 | 71.15 | 71.15 | 71.15 | 71.15 | 71.15 | 71.15 | 71.15 | 71.15 | 71.15 | 71.15 | 71.15 | 71.15 | 71.15 | 71.15
Capacity Added (MVA) | 0 | 0 | 0 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35
Option 4 - Construct 2x 20/33MVA zone substation in Inverloch - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N Rating (MVA) - Option 4 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8
SCR N Rating (MVA) - Option 4 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 - Contract network support services to defer network investment - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N Rating (MVA) - Option 5 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8
SCR N Rating (MVA) - Option 5 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 6 - - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N Rating (MVA) - Option 6 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8
SCR N Rating (MVA) - Option 6 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 7 - - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N Rating (MVA) - Option 7 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8
SCR N Rating (MVA) - Option 7 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 8 - - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N Rating (MVA) - Option 8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8
SCR N Rating (MVA) - Option 8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Capacity N-1
Option 1 - Do Nothing - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-1 Rating (MVA) - Option 1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1
SCR N-1 Rating (MVA) - Option 1 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3
Planned Additional Capacity (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2 - Replace 3 x 10/13.5 MVA Tx with 3 x 20/33 MVA Tx - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-1 Rating (MVA) - Option 2 | 36.1 | 36.1 | 36.1 | 79.3 | 79.3 | 79.3 | 79.3 | 79.3 | 79.3 | 79.3 | 79.3 | 79.3 | 79.3 | 79.3 | 79.3 | 79.3 | 79.3 | 79.3 | 79.3 | 79.3 | 79.3 | 79.3 | 79.3 | 79.3 | 79.3 | 79.3 | 79.3 | 79.3 | 79.3 | 79.3
SCR N-1 Rating (MVA) - Option 2 | 35.3 | 35.3 | 35.3 | 78.5 | 78.5 | 78.5 | 78.5 | 78.5 | 78.5 | 78.5 | 78.5 | 78.5 | 78.5 | 78.5 | 78.5 | 78.5 | 78.5 | 78.5 | 78.5 | 78.5 | 78.5 | 78.5 | 78.5 | 78.5 | 78.5 | 78.5 | 78.5 | 78.5 | 78.5 | 78.5
Capacity Added (MVA) | 0 | 0 | 0 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2
Option 3 - Replace 1 x 10/13.5 MVA Tx with 1 x 20/33 MVA Tx - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-1 Rating (MVA) - Option 3 | 36.1 | 36.1 | 36.1 | 51.45 | 51.45 | 51.45 | 51.45 | 51.45 | 51.45 | 51.45 | 51.45 | 51.45 | 51.45 | 51.45 | 51.45 | 51.45 | 51.45 | 51.45 | 51.45 | 51.45 | 51.45 | 51.45 | 51.45 | 51.45 | 51.45 | 51.45 | 51.45 | 51.45 | 51.45 | 51.45
SCR N-1 Rating (MVA) - Option 3 | 35.3 | 35.3 | 35.3 | 50.65 | 50.65 | 50.65 | 50.65 | 50.65 | 50.65 | 50.65 | 50.65 | 50.65 | 50.65 | 50.65 | 50.65 | 50.65 | 50.65 | 50.65 | 50.65 | 50.65 | 50.65 | 50.65 | 50.65 | 50.65 | 50.65 | 50.65 | 50.65 | 50.65 | 50.65 | 50.65
Capacity Added (MVA) | 0 | 0 | 0 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35
Option 4 - Construct 2x 20/33MVA zone substation in Inverloch - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-1 Rating (MVA) - Option 4 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1
SCR N-1 Rating (MVA) - Option 4 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 - Contract network support services to defer network investment - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-1 Rating (MVA) - Option 5 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1
SCR N-1 Rating (MVA) - Option 5 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 6 - - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-1 Rating (MVA) - Option 6 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1
SCR N-1 Rating (MVA) - Option 6 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 7 - - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-1 Rating (MVA) - Option 7 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1
SCR N-1 Rating (MVA) - Option 7 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 8 - - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-1 Rating (MVA) - Option 8 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1
SCR N-1 Rating (MVA) - Option 8 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Capacity N-2
Option 1 - Do Nothing - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-2 Rating (MVA) - Option 1 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05
SCR N-2 Rating (MVA) - Option 1 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65
Planned Additional Capacity (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2 - Replace 3 x 10/13.5 MVA Tx with 3 x 20/33 MVA Tx - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-2 Rating (MVA) - Option 2 | 18.05 | 18.05 | 18.05 | 61.25 | 61.25 | 61.25 | 61.25 | 61.25 | 61.25 | 61.25 | 61.25 | 61.25 | 61.25 | 61.25 | 61.25 | 61.25 | 61.25 | 61.25 | 61.25 | 61.25 | 61.25 | 61.25 | 61.25 | 61.25 | 61.25 | 61.25 | 61.25 | 61.25 | 61.25 | 61.25
SCR N-2 Rating (MVA) - Option 2 | 17.65 | 17.65 | 17.65 | 60.85 | 60.85 | 60.85 | 60.85 | 60.85 | 60.85 | 60.85 | 60.85 | 60.85 | 60.85 | 60.85 | 60.85 | 60.85 | 60.85 | 60.85 | 60.85 | 60.85 | 60.85 | 60.85 | 60.85 | 60.85 | 60.85 | 60.85 | 60.85 | 60.85 | 60.85 | 60.85
Capacity Added (MVA) | 0 | 0 | 0 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2
Option 3 - Replace 1 x 10/13.5 MVA Tx with 1 x 20/33 MVA Tx - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-2 Rating (MVA) - Option 3 | 18.05 | 18.05 | 18.05 | 33.4 | 33.4 | 33.4 | 33.4 | 33.4 | 33.4 | 33.4 | 33.4 | 33.4 | 33.4 | 33.4 | 33.4 | 33.4 | 33.4 | 33.4 | 33.4 | 33.4 | 33.4 | 33.4 | 33.4 | 33.4 | 33.4 | 33.4 | 33.4 | 33.4 | 33.4 | 33.4
SCR N-2 Rating (MVA) - Option 3 | 17.65 | 17.65 | 17.65 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33
Capacity Added (MVA) | 0 | 0 | 0 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35
Option 4 - Construct 2x 20/33MVA zone substation in Inverloch - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-2 Rating (MVA) - Option 4 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05
SCR N-2 Rating (MVA) - Option 4 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 - Contract network support services to defer network investment - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-2 Rating (MVA) - Option 5 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05
SCR N-2 Rating (MVA) - Option 5 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 6 - - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-2 Rating (MVA) - Option 6 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05
SCR N-2 Rating (MVA) - Option 6 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 7 - - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-2 Rating (MVA) - Option 7 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05
SCR N-2 Rating (MVA) - Option 7 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 8 - - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-2 Rating (MVA) - Option 8 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05
SCR N-2 Rating (MVA) - Option 8 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Demand
Option 1 - Do Nothing
Winter Season | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Maximum Demand (MVA) - P50 | 39.5207 | 43.6466 | 44.0841 | 44.625 | 45.3431 | 46.0239 | 47.2137 | 50.206 | 51.8155 | 50.6413 | 54.2764 | 54.9313 | 55.4021 | 57.6212 | 57.9824 | 57.9824 | 57.9824 | 57.9824 | 57.9824 | 57.9824 | 57.9824 | 57.9824 | 57.9824 | 57.9824 | 57.9824 | 57.9824 | 57.9824 | 57.9824 | 57.9824 | 57.9824
Maximum Demand (MVA) - P10 | 43.3126 | 47.2482 | 47.6557 | 49.0622 | 49.028 | 49.3373 | 50.5469 | 54.0224 | 55.4565 | 54.099 | 57.8491 | 56.2746 | 57.6913 | 58.7122 | 58.2928 | 58.2928 | 58.2928 | 58.2928 | 58.2928 | 58.2928 | 58.2928 | 58.2928 | 58.2928 | 58.2928 | 58.2928 | 58.2928 | 58.2928 | 58.2928 | 58.2928 | 58.2928
Block loads (MVA) not in the forecast | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Available Transfers (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Demand management (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Embedded generation (MVA) | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11
Total Maximum Demand (MVA) - Option 1 Winter POE50 | 39.4107 | 43.5366 | 43.9741 | 44.515 | 45.2331 | 45.9139 | 47.1037 | 50.096 | 51.7055 | 50.5313 | 54.1664 | 54.8213 | 55.2921 | 57.5112 | 57.8724 | 57.8724 | 57.8724 | 57.8724 | 57.8724 | 57.8724 | 57.8724 | 57.8724 | 57.8724 | 57.8724 | 57.8724 | 57.8724 | 57.8724 | 57.8724 | 57.8724 | 57.8724
Total Maximum Demand (MVA) - Option 1 Winter POE10 | 43.2026 | 47.1382 | 47.5457 | 48.9522 | 48.918 | 49.2273 | 50.4369 | 53.9124 | 55.3465 | 53.989 | 57.7391 | 56.1646 | 57.5813 | 58.6022 | 58.1828 | 58.1828 | 58.1828 | 58.1828 | 58.1828 | 58.1828 | 58.1828 | 58.1828 | 58.1828 | 58.1828 | 58.1828 | 58.1828 | 58.1828 | 58.1828 | 58.1828 | 58.1828
Summer Season | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Maximum Demand (MVA) - P50 | 41.5121 | 44.6075 | 44.9185 | 44.7661 | 44.911 | 44.9706 | 45.1615 | 45.5541 | 45.8843 | 46.0363 | 45.9008 | 46.4689 | 46.559 | 46.4523 | 46.6661 | 46.6661 | 46.6661 | 46.6661 | 46.6661 | 46.6661 | 46.6661 | 46.6661 | 46.6661 | 46.6661 | 46.6661 | 46.6661 | 46.6661 | 46.6661 | 46.6661 | 46.6661
Maximum Demand (MVA) - P10 | 51.0465 | 54.5057 | 54.6012 | 54.4983 | 54.5247 | 54.7136 | 55.0965 | 55.7707 | 56.122 | 56.3761 | 56.7608 | 57.2519 | 57.8457 | 58.1569 | 58.056 | 58.056 | 58.056 | 58.056 | 58.056 | 58.056 | 58.056 | 58.056 | 58.056 | 58.056 | 58.056 | 58.056 | 58.056 | 58.056 | 58.056 | 58.056
Block loads (MVA) not in the forecast | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Available Transfers (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Demand management (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Embedded generation (MVA) | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Maximum Demand (MVA) - Option 1 Summer POE50 | 41.4021 | 44.4975 | 44.8085 | 44.6561 | 44.801 | 44.8606 | 45.0515 | 45.4441 | 45.7743 | 45.9263 | 45.7908 | 46.3589 | 46.449 | 46.3423 | 46.5561 | 46.6661 | 46.6661 | 46.6661 | 46.6661 | 46.6661 | 46.6661 | 46.6661 | 46.6661 | 46.6661 | 46.6661 | 46.6661 | 46.6661 | 46.6661 | 46.6661 | 46.6661
Total Maximum Demand (MVA) - Option 1 Summer POE10 | 50.9365 | 54.3957 | 54.4912 | 54.3883 | 54.4147 | 54.6036 | 54.9865 | 55.6607 | 56.012 | 56.2661 | 56.6508 | 57.1419 | 57.7357 | 58.0469 | 57.946 | 58.056 | 58.056 | 58.056 | 58.056 | 58.056 | 58.056 | 58.056 | 58.056 | 58.056 | 58.056 | 58.056 | 58.056 | 58.056 | 58.056 | 58.056
Option 2 - Replace 3 x 10/13.5 MVA Tx with 3 x 20/33 MVA Tx
Year | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Added Transfers (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Added Demand management (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Added Embedded generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Maximum Demand (MVA) - Option 2 Winter POE50 | 39.4107 | 43.5366 | 43.9741 | 44.515 | 45.2331 | 45.9139 | 47.1037 | 50.096 | 51.7055 | 50.5313 | 54.1664 | 54.8213 | 55.2921 | 57.5112 | 57.8724 | 57.8724 | 57.8724 | 57.8724 | 57.8724 | 57.8724 | 57.8724 | 57.8724 | 57.8724 | 57.8724 | 57.8724 | 57.8724 | 57.8724 | 57.8724 | 57.8724 | 57.8724
Total Maximum Demand (MVA) - Option 2 Winter POE10 | 43.2026 | 47.1382 | 47.5457 | 48.9522 | 48.918 | 49.2273 | 50.4369 | 53.9124 | 55.3465 | 53.989 | 57.7391 | 56.1646 | 57.5813 | 58.6022 | 58.1828 | 58.1828 | 58.1828 | 58.1828 | 58.1828 | 58.1828 | 58.1828 | 58.1828 | 58.1828 | 58.1828 | 58.1828 | 58.1828 | 58.1828 | 58.1828 | 58.1828 | 58.1828
Total Maximum Demand (MVA) - Option 2 Summer POE50 | 41.4021 | 44.4975 | 44.8085 | 44.6561 | 44.801 | 44.8606 | 45.0515 | 45.4441 | 45.7743 | 45.9263 | 45.7908 | 46.3589 | 46.449 | 46.3423 | 46.5561 | 46.6661 | 46.6661 | 46.6661 | 46.6661 | 46.6661 | 46.6661 | 46.6661 | 46.6661 | 46.6661 | 46.6661 | 46.6661 | 46.6661 | 46.6661 | 46.6661 | 46.6661
Total Maximum Demand (MVA) - Option 2 Summer POE10 | 50.9365 | 54.3957 | 54.4912 | 54.3883 | 54.4147 | 54.6036 | 54.9865 | 55.6607 | 56.012 | 56.2661 | 56.6508 | 57.1419 | 57.7357 | 58.0469 | 57.946 | 58.056 | 58.056 | 58.056 | 58.056 | 58.056 | 58.056 | 58.056 | 58.056 | 58.056 | 58.056 | 58.056 | 58.056 | 58.056 | 58.056 | 58.056
Option 3 - Replace 1 x 10/13.5 MVA Tx with 1 x 20/33 MVA Tx
Year | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Added Transfers (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Added Demand management (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Added Embedded generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Maximum Demand (MVA) - Option 3 Winter POE50 | 39.4107 | 43.5366 | 43.9741 | 44.515 | 45.2331 | 45.9139 | 47.1037 | 50.096 | 51.7055 | 50.5313 | 54.1664 | 54.8213 | 55.2921 | 57.5112 | 57.8724 | 57.8724 | 57.8724 | 57.8724 | 57.8724 | 57.8724 | 57.8724 | 57.8724 | 57.8724 | 57.8724 | 57.8724 | 57.8724 | 57.8724 | 57.8724 | 57.8724 | 57.8724
Total Maximum Demand (MVA) - Option 3 Winter POE10 | 43.2026 | 47.1382 | 47.5457 | 48.9522 | 48.918 | 49.2273 | 50.4369 | 53.9124 | 55.3465 | 53.989 | 57.7391 | 56.1646 | 57.5813 | 58.6022 | 58.1828 | 58.1828 | 58.1828 | 58.1828 | 58.1828 | 58.1828 | 58.1828 | 58.1828 | 58.1828 | 58.1828 | 58.1828 | 58.1828 | 58.1828 | 58.1828 | 58.1828 | 58.1828
Total Maximum Demand (MVA) - Option 3 Summer POE50 | 41.4021 | 44.4975 | 44.8085 | 44.6561 | 44.801 | 44.8606 | 45.0515 | 45.4441 | 45.7743 | 45.9263 | 45.7908 | 46.3589 | 46.449 | 46.3423 | 46.5561 | 46.6661 | 46.6661 | 46.6661 | 46.6661 | 46.6661 | 46.6661 | 46.6661 | 46.6661 | 46.6661 | 46.6661 | 46.6661 | 46.6661 | 46.6661 | 46.6661 | 46.6661
Total Maximum Demand (MVA) - Option 3 Summer POE10 | 50.9365 | 54.3957 | 54.4912 | 54.3883 | 54.4147 | 54.6036 | 54.9865 | 55.6607 | 56.012 | 56.2661 | 56.6508 | 57.1419 | 57.7357 | 58.0469 | 57.946 | 58.056 | 58.056 | 58.056 | 58.056 | 58.056 | 58.056 | 58.056 | 58.056 | 58.056 | 58.056 | 58.056 | 58.056 | 58.056 | 58.056 | 58.056
Option 4 - Construct 2x 20/33MVA zone substation in Inverloch
Year | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Added Transfers (MVA) | 0 | 0 | 0 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66
Added Demand management (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Added Embedded generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Maximum Demand (MVA) - Option 4 Winter POE50 | 39.4107 | 43.5366 | 43.9741 | -21.485 | -20.7669 | -20.0861 | -18.8963 | -15.904 | -14.2945 | -15.4687 | -11.8336 | -11.1787 | -10.7079 | -8.4888 | -8.1276 | -8.1276 | -8.1276 | -8.1276 | -8.1276 | -8.1276 | -8.1276 | -8.1276 | -8.1276 | -8.1276 | -8.1276 | -8.1276 | -8.1276 | -8.1276 | -8.1276 | -8.1276
Total Maximum Demand (MVA) - Option 4 Winter POE10 | 43.2026 | 47.1382 | 47.5457 | -17.0478 | -17.082 | -16.7727 | -15.5631 | -12.0876 | -10.6535 | -12.011 | -8.2609 | -9.8354 | -8.4187 | -7.3978 | -7.8172 | -7.8172 | -7.8172 | -7.8172 | -7.8172 | -7.8172 | -7.8172 | -7.8172 | -7.8172 | -7.8172 | -7.8172 | -7.8172 | -7.8172 | -7.8172 | -7.8172 | -7.8172
Total Maximum Demand (MVA) - Option 4 Summer POE50 | 41.4021 | 44.4975 | 44.8085 | -21.3439 | -21.199 | -21.1394 | -20.9485 | -20.5559 | -20.2257 | -20.0737 | -20.2092 | -19.6411 | -19.551 | -19.6577 | -19.4439 | -19.3339 | -19.3339 | -19.3339 | -19.3339 | -19.3339 | -19.3339 | -19.3339 | -19.3339 | -19.3339 | -19.3339 | -19.3339 | -19.3339 | -19.3339 | -19.3339 | -19.3339
Total Maximum Demand (MVA) - Option 4 Summer POE10 | 50.9365 | 54.3957 | 54.4912 | -11.6117 | -11.5853 | -11.3964 | -11.0135 | -10.3393 | -9.988 | -9.7339 | -9.3492 | -8.8581 | -8.2643 | -7.9531 | -8.054 | -7.944 | -7.944 | -7.944 | -7.944 | -7.944 | -7.944 | -7.944 | -7.944 | -7.944 | -7.944 | -7.944 | -7.944 | -7.944 | -7.944 | -7.944
Option 5 - Contract network support services to defer network investment
Year | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Added Transfers (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Added Demand management (MVA) | 4.0981 | 4.3758 | 4.3835 | 4.3752 | 4.3773 | 4.3925 | 4.4232 | 4.4774 | 4.5056 | 4.526 | 4.5569 | 4.5963 | 4.644 | 4.6689 | 4.6608 | 4.6608 | 4.6608 | 4.6608 | 4.6608 | 4.6608 | 4.6608 | 4.6608 | 4.6608 | 4.6608 | 4.6608 | 4.6608 | 4.6608 | 4.6608 | 4.6608 | 4.6608
Added Embedded generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Maximum Demand (MVA) - Option 5 Winter POE50 | 35.3126 | 39.1608 | 39.5906 | 40.1398 | 40.8558 | 41.5214 | 42.6804 | 45.6186 | 47.1999 | 46.0053 | 49.6095 | 50.225 | 50.6481 | 52.8423 | 53.2116 | 53.2116 | 53.2116 | 53.2116 | 53.2116 | 53.2116 | 53.2116 | 53.2116 | 53.2116 | 53.2116 | 53.2116 | 53.2116 | 53.2116 | 53.2116 | 53.2116 | 53.2116
Total Maximum Demand (MVA) - Option 5 Winter POE10 | 39.1045 | 42.7623 | 43.1622 | 44.577 | 44.5406 | 44.8347 | 46.0137 | 49.435 | 50.841 | 49.463 | 53.1822 | 51.5683 | 52.9373 | 53.9333 | 53.5219 | 53.5219 | 53.5219 | 53.5219 | 53.5219 | 53.5219 | 53.5219 | 53.5219 | 53.5219 | 53.5219 | 53.5219 | 53.5219 | 53.5219 | 53.5219 | 53.5219 | 53.5219
Total Maximum Demand (MVA) - Option 5 Summer POE50 | 37.304 | 40.1217 | 40.425 | 40.2808 | 40.4237 | 40.4681 | 40.6283 | 40.9667 | 41.2687 | 41.4003 | 41.234 | 41.7626 | 41.805 | 41.6734 | 41.8953 | 42.0053 | 42.0053 | 42.0053 | 42.0053 | 42.0053 | 42.0053 | 42.0053 | 42.0053 | 42.0053 | 42.0053 | 42.0053 | 42.0053 | 42.0053 | 42.0053 | 42.0053
Total Maximum Demand (MVA) - Option 5 Summer POE10 | 46.8384 | 50.0199 | 50.1077 | 50.013 | 50.0374 | 50.2111 | 50.5632 | 51.1833 | 51.5064 | 51.7402 | 52.0939 | 52.5456 | 53.0917 | 53.378 | 53.2852 | 53.3952 | 53.3952 | 53.3952 | 53.3952 | 53.3952 | 53.3952 | 53.3952 | 53.3952 | 53.3952 | 53.3952 | 53.3952 | 53.3952 | 53.3952 | 53.3952 | 53.3952
Option 6 -
Year | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Added Transfers (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Added Demand management (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Added Embedded generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Maximum Demand (MVA) - Option 6 Winter POE50 | 39.4107 | 43.5366 | 43.9741 | 44.515 | 45.2331 | 45.9139 | 47.1037 | 50.096 | 51.7055 | 50.5313 | 54.1664 | 54.8213 | 55.2921 | 57.5112 | 57.8724 | 57.8724 | 57.8724 | 57.8724 | 57.8724 | 57.8724 | 57.8724 | 57.8724 | 57.8724 | 57.8724 | 57.8724 | 57.8724 | 57.8724 | 57.8724 | 57.8724 | 57.8724
Total Maximum Demand (MVA) - Option 6 Winter POE10 | 43.2026 | 47.1382 | 47.5457 | 48.9522 | 48.918 | 49.2273 | 50.4369 | 53.9124 | 55.3465 | 53.989 | 57.7391 | 56.1646 | 57.5813 | 58.6022 | 58.1828 | 58.1828 | 58.1828 | 58.1828 | 58.1828 | 58.1828 | 58.1828 | 58.1828 | 58.1828 | 58.1828 | 58.1828 | 58.1828 | 58.1828 | 58.1828 | 58.1828 | 58.1828
Total Maximum Demand (MVA) - Option 6 Summer POE50 | 41.4021 | 44.4975 | 44.8085 | 44.6561 | 44.801 | 44.8606 | 45.0515 | 45.4441 | 45.7743 | 45.9263 | 45.7908 | 46.3589 | 46.449 | 46.3423 | 46.5561 | 46.6661 | 46.6661 | 46.6661 | 46.6661 | 46.6661 | 46.6661 | 46.6661 | 46.6661 | 46.6661 | 46.6661 | 46.6661 | 46.6661 | 46.6661 | 46.6661 | 46.6661
Total Maximum Demand (MVA) - Option 6 Summer POE10 | 50.9365 | 54.3957 | 54.4912 | 54.3883 | 54.4147 | 54.6036 | 54.9865 | 55.6607 | 56.012 | 56.2661 | 56.6508 | 57.1419 | 57.7357 | 58.0469 | 57.946 | 58.056 | 58.056 | 58.056 | 58.056 | 58.056 | 58.056 | 58.056 | 58.056 | 58.056 | 58.056 | 58.056 | 58.056 | 58.056 | 58.056 | 58.056
Option 7 -
Year | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Added Transfers (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Added Demand management (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Added Embedded generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Maximum Demand (MVA) - Option 7 Winter POE50 | 39.4107 | 43.5366 | 43.9741 | 44.515 | 45.2331 | 45.9139 | 47.1037 | 50.096 | 51.7055 | 50.5313 | 54.1664 | 54.8213 | 55.2921 | 57.5112 | 57.8724 | 57.8724 | 57.8724 | 57.8724 | 57.8724 | 57.8724 | 57.8724 | 57.8724 | 57.8724 | 57.8724 | 57.8724 | 57.8724 | 57.8724 | 57.8724 | 57.8724 | 57.8724
Total Maximum Demand (MVA) - Option 7 Winter POE10 | 43.2026 | 47.1382 | 47.5457 | 48.9522 | 48.918 | 49.2273 | 50.4369 | 53.9124 | 55.3465 | 53.989 | 57.7391 | 56.1646 | 57.5813 | 58.6022 | 58.1828 | 58.1828 | 58.1828 | 58.1828 | 58.1828 | 58.1828 | 58.1828 | 58.1828 | 58.1828 | 58.1828 | 58.1828 | 58.1828 | 58.1828 | 58.1828 | 58.1828 | 58.1828
Total Maximum Demand (MVA) - Option 7 Summer POE50 | 41.4021 | 44.4975 | 44.8085 | 44.6561 | 44.801 | 44.8606 | 45.0515 | 45.4441 | 45.7743 | 45.9263 | 45.7908 | 46.3589 | 46.449 | 46.3423 | 46.5561 | 46.6661 | 46.6661 | 46.6661 | 46.6661 | 46.6661 | 46.6661 | 46.6661 | 46.6661 | 46.6661 | 46.6661 | 46.6661 | 46.6661 | 46.6661 | 46.6661 | 46.6661
Total Maximum Demand (MVA) - Option 7 Summer POE10 | 50.9365 | 54.3957 | 54.4912 | 54.3883 | 54.4147 | 54.6036 | 54.9865 | 55.6607 | 56.012 | 56.2661 | 56.6508 | 57.1419 | 57.7357 | 58.0469 | 57.946 | 58.056 | 58.056 | 58.056 | 58.056 | 58.056 | 58.056 | 58.056 | 58.056 | 58.056 | 58.056 | 58.056 | 58.056 | 58.056 | 58.056 | 58.056
Option 8 -
Year | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Added Transfers (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Added Demand management (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Added Embedded generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Maximum Demand (MVA) - Option 8 Winter POE50 | 39.4107 | 43.5366 | 43.9741 | 44.515 | 45.2331 | 45.9139 | 47.1037 | 50.096 | 51.7055 | 50.5313 | 54.1664 | 54.8213 | 55.2921 | 57.5112 | 57.8724 | 57.8724 | 57.8724 | 57.8724 | 57.8724 | 57.8724 | 57.8724 | 57.8724 | 57.8724 | 57.8724 | 57.8724 | 57.8724 | 57.8724 | 57.8724 | 57.8724 | 57.8724
Total Maximum Demand (MVA) - Option 8 Winter POE10 | 43.2026 | 47.1382 | 47.5457 | 48.9522 | 48.918 | 49.2273 | 50.4369 | 53.9124 | 55.3465 | 53.989 | 57.7391 | 56.1646 | 57.5813 | 58.6022 | 58.1828 | 58.1828 | 58.1828 | 58.1828 | 58.1828 | 58.1828 | 58.1828 | 58.1828 | 58.1828 | 58.1828 | 58.1828 | 58.1828 | 58.1828 | 58.1828 | 58.1828 | 58.1828
Total Maximum Demand (MVA) - Option 8 Summer POE50 | 41.4021 | 44.4975 | 44.8085 | 44.6561 | 44.801 | 44.8606 | 45.0515 | 45.4441 | 45.7743 | 45.9263 | 45.7908 | 46.3589 | 46.449 | 46.3423 | 46.5561 | 46.6661 | 46.6661 | 46.6661 | 46.6661 | 46.6661 | 46.6661 | 46.6661 | 46.6661 | 46.6661 | 46.6661 | 46.6661 | 46.6661 | 46.6661 | 46.6661 | 46.6661
Total Maximum Demand (MVA) - Option 8 Summer POE10 | 50.9365 | 54.3957 | 54.4912 | 54.3883 | 54.4147 | 54.6036 | 54.9865 | 55.6607 | 56.012 | 56.2661 | 56.6508 | 57.1419 | 57.7357 | 58.0469 | 57.946 | 58.056 | 58.056 | 58.056 | 58.056 | 58.056 | 58.056 | 58.056 | 58.056 | 58.056 | 58.056 | 58.056 | 58.056 | 58.056 | 58.056 | 58.056

## Forecasted LDC
Option 1 - Do Nothing
Winter Season | [31 empty] | Winter Season
P50 | [31 empty] | P10
% of MD | Winter - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Winter - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 39.4107 | 43.5366 | 43.9741 | 44.515 | 45.2331 | 45.9139 | 47.1037 | 50.096 | 51.7055 | 50.5313 | 54.1664 | 54.8213 | 55.2921 | 57.5112 | 57.8724 | 57.8724 | 57.8724 | 57.8724 | 57.8724 | 57.8724 | 57.8724 | 57.8724 | 57.8724 | 57.8724 | 57.8724 | 57.8724 | 57.8724 | 57.8724 | 57.8724 | 57.8724 | 100% | 0 | 43.2026 | 47.1382 | 47.5457 | 48.9522 | 48.918 | 49.2273 | 50.4369 | 53.9124 | 55.3465 | 53.989 | 57.7391 | 56.1646 | 57.5813 | 58.6022 | 58.1828 | 58.1828 | 58.1828 | 58.1828 | 58.1828 | 58.1828 | 58.1828 | 58.1828 | 58.1828 | 58.1828 | 58.1828 | 58.1828 | 58.1828 | 58.1828 | 58.1828 | 58.1828
99% | 0.2972 | 39.0166 | 43.1012 | 43.5344 | 44.0698 | 44.7808 | 45.4548 | 46.6326 | 49.595 | 51.1884 | 50.026 | 53.6247 | 54.2731 | 54.7392 | 56.9361 | 57.2937 | 57.2937 | 57.2937 | 57.2937 | 57.2937 | 57.2937 | 57.2937 | 57.2937 | 57.2937 | 57.2937 | 57.2937 | 57.2937 | 57.2937 | 57.2937 | 57.2937 | 57.2937 | 99% | 0.2972 | 42.7706 | 46.6668 | 47.0703 | 48.4627 | 48.4288 | 48.735 | 49.9326 | 53.3732 | 54.7931 | 53.4491 | 57.1617 | 55.6029 | 57.0055 | 58.0162 | 57.6009 | 57.6009 | 57.6009 | 57.6009 | 57.6009 | 57.6009 | 57.6009 | 57.6009 | 57.6009 | 57.6009 | 57.6009 | 57.6009 | 57.6009 | 57.6009 | 57.6009 | 57.6009
98% | 0.2972 | 38.6225 | 42.6659 | 43.0946 | 43.6247 | 44.3284 | 44.9956 | 46.1616 | 49.0941 | 50.6714 | 49.5207 | 53.083 | 53.7249 | 54.1862 | 56.361 | 56.715 | 56.715 | 56.715 | 56.715 | 56.715 | 56.715 | 56.715 | 56.715 | 56.715 | 56.715 | 56.715 | 56.715 | 56.715 | 56.715 | 56.715 | 56.715 | 98% | 0.2972 | 42.3386 | 46.1954 | 46.5948 | 47.9732 | 47.9396 | 48.2427 | 49.4282 | 52.8341 | 54.2396 | 52.9092 | 56.5843 | 55.0413 | 56.4297 | 57.4302 | 57.0191 | 57.0191 | 57.0191 | 57.0191 | 57.0191 | 57.0191 | 57.0191 | 57.0191 | 57.0191 | 57.0191 | 57.0191 | 57.0191 | 57.0191 | 57.0191 | 57.0191 | 57.0191
97% | 0.2972 | 38.2284 | 42.2305 | 42.6549 | 43.1795 | 43.8761 | 44.5365 | 45.6906 | 48.5931 | 50.1543 | 49.0154 | 52.5414 | 53.1767 | 53.6333 | 55.7859 | 56.1363 | 56.1363 | 56.1363 | 56.1363 | 56.1363 | 56.1363 | 56.1363 | 56.1363 | 56.1363 | 56.1363 | 56.1363 | 56.1363 | 56.1363 | 56.1363 | 56.1363 | 56.1363 | 97% | 0.2972 | 41.9066 | 45.724 | 46.1193 | 47.4837 | 47.4504 | 47.7504 | 48.9238 | 52.295 | 53.6861 | 52.3693 | 56.0069 | 54.4796 | 55.8539 | 56.8441 | 56.4373 | 56.4373 | 56.4373 | 56.4373 | 56.4373 | 56.4373 | 56.4373 | 56.4373 | 56.4373 | 56.4373 | 56.4373 | 56.4373 | 56.4373 | 56.4373 | 56.4373 | 56.4373
95% | 1.486 | 37.4402 | 41.3598 | 41.7754 | 42.2892 | 42.9715 | 43.6182 | 44.7485 | 47.5912 | 49.1202 | 48.0047 | 51.4581 | 52.0802 | 52.5275 | 54.6357 | 54.9788 | 54.9788 | 54.9788 | 54.9788 | 54.9788 | 54.9788 | 54.9788 | 54.9788 | 54.9788 | 54.9788 | 54.9788 | 54.9788 | 54.9788 | 54.9788 | 54.9788 | 54.9788 | 95% | 1.486 | 41.0425 | 44.7812 | 45.1684 | 46.5046 | 46.4721 | 46.7659 | 47.9151 | 51.2167 | 52.5792 | 51.2895 | 54.8521 | 53.3563 | 54.7022 | 55.6721 | 55.2736 | 55.2736 | 55.2736 | 55.2736 | 55.2736 | 55.2736 | 55.2736 | 55.2736 | 55.2736 | 55.2736 | 55.2736 | 55.2736 | 55.2736 | 55.2736 | 55.2736 | 55.2736
90% | 8.6188 | 35.4696 | 39.1829 | 39.5767 | 40.0635 | 40.7098 | 41.3225 | 42.3933 | 45.0864 | 46.5349 | 45.4782 | 48.7497 | 49.3392 | 49.7629 | 51.7601 | 52.0852 | 52.0852 | 52.0852 | 52.0852 | 52.0852 | 52.0852 | 52.0852 | 52.0852 | 52.0852 | 52.0852 | 52.0852 | 52.0852 | 52.0852 | 52.0852 | 52.0852 | 52.0852 | 90% | 8.6188 | 38.8824 | 42.4243 | 42.7911 | 44.057 | 44.0262 | 44.3045 | 45.3932 | 48.5211 | 49.8119 | 48.5901 | 51.9652 | 50.5481 | 51.8232 | 52.742 | 52.3645 | 52.3645 | 52.3645 | 52.3645 | 52.3645 | 52.3645 | 52.3645 | 52.3645 | 52.3645 | 52.3645 | 52.3645 | 52.3645 | 52.3645 | 52.3645 | 52.3645 | 52.3645
85% | 40.1218 | 33.4991 | 37.0061 | 37.378 | 37.8377 | 38.4481 | 39.0268 | 40.0381 | 42.5816 | 43.9497 | 42.9516 | 46.0414 | 46.5981 | 46.9983 | 48.8845 | 49.1916 | 49.1916 | 49.1916 | 49.1916 | 49.1916 | 49.1916 | 49.1916 | 49.1916 | 49.1916 | 49.1916 | 49.1916 | 49.1916 | 49.1916 | 49.1916 | 49.1916 | 49.1916 | 85% | 40.1218 | 36.7222 | 40.0674 | 40.4139 | 41.6094 | 41.5803 | 41.8432 | 42.8714 | 45.8255 | 47.0445 | 45.8906 | 49.0782 | 47.7399 | 48.9441 | 49.8119 | 49.4554 | 49.4554 | 49.4554 | 49.4554 | 49.4554 | 49.4554 | 49.4554 | 49.4554 | 49.4554 | 49.4554 | 49.4554 | 49.4554 | 49.4554 | 49.4554 | 49.4554 | 49.4554
80% | 93.0231 | 31.5286 | 34.8293 | 35.1793 | 35.612 | 36.1865 | 36.7311 | 37.6829 | 40.0768 | 41.3644 | 40.425 | 43.3331 | 43.857 | 44.2337 | 46.009 | 46.2979 | 46.2979 | 46.2979 | 46.2979 | 46.2979 | 46.2979 | 46.2979 | 46.2979 | 46.2979 | 46.2979 | 46.2979 | 46.2979 | 46.2979 | 46.2979 | 46.2979 | 46.2979 | 80% | 93.0231 | 34.5621 | 37.7105 | 38.0366 | 39.1618 | 39.1344 | 39.3818 | 40.3495 | 43.1299 | 44.2772 | 43.1912 | 46.1913 | 44.9317 | 46.065 | 46.8818 | 46.5462 | 46.5462 | 46.5462 | 46.5462 | 46.5462 | 46.5462 | 46.5462 | 46.5462 | 46.5462 | 46.5462 | 46.5462 | 46.5462 | 46.5462 | 46.5462 | 46.5462 | 46.5462
75% | 197.0426 | 29.558 | 32.6525 | 32.9806 | 33.3862 | 33.9248 | 34.4354 | 35.3278 | 37.572 | 38.7791 | 37.8985 | 40.6248 | 41.116 | 41.4691 | 43.1334 | 43.4043 | 43.4043 | 43.4043 | 43.4043 | 43.4043 | 43.4043 | 43.4043 | 43.4043 | 43.4043 | 43.4043 | 43.4043 | 43.4043 | 43.4043 | 43.4043 | 43.4043 | 43.4043 | 75% | 197.0426 | 32.402 | 35.3536 | 35.6593 | 36.7142 | 36.6885 | 36.9204 | 37.8277 | 40.4343 | 41.5099 | 40.4917 | 43.3043 | 42.1234 | 43.186 | 43.9517 | 43.6371 | 43.6371 | 43.6371 | 43.6371 | 43.6371 | 43.6371 | 43.6371 | 43.6371 | 43.6371 | 43.6371 | 43.6371 | 43.6371 | 43.6371 | 43.6371 | 43.6371 | 43.6371
70% | 378.0365 | 27.5875 | 30.4756 | 30.7819 | 31.1605 | 31.6632 | 32.1397 | 32.9726 | 35.0672 | 36.1938 | 35.3719 | 37.9165 | 38.3749 | 38.7045 | 40.2579 | 40.5107 | 40.5107 | 40.5107 | 40.5107 | 40.5107 | 40.5107 | 40.5107 | 40.5107 | 40.5107 | 40.5107 | 40.5107 | 40.5107 | 40.5107 | 40.5107 | 40.5107 | 40.5107 | 70% | 378.0365 | 30.2418 | 32.9967 | 33.282 | 34.2666 | 34.2426 | 34.4591 | 35.3059 | 37.7386 | 38.7426 | 37.7923 | 40.4173 | 39.3152 | 40.3069 | 41.0215 | 40.7279 | 40.7279 | 40.7279 | 40.7279 | 40.7279 | 40.7279 | 40.7279 | 40.7279 | 40.7279 | 40.7279 | 40.7279 | 40.7279 | 40.7279 | 40.7279 | 40.7279 | 40.7279
65% | 616.0926 | 25.617 | 28.2988 | 28.5832 | 28.9347 | 29.4015 | 29.844 | 30.6174 | 32.5624 | 33.6086 | 32.8454 | 35.2081 | 35.6338 | 35.9399 | 37.3823 | 37.6171 | 37.6171 | 37.6171 | 37.6171 | 37.6171 | 37.6171 | 37.6171 | 37.6171 | 37.6171 | 37.6171 | 37.6171 | 37.6171 | 37.6171 | 37.6171 | 37.6171 | 37.6171 | 65% | 616.0926 | 28.0817 | 30.6398 | 30.9047 | 31.819 | 31.7967 | 31.9977 | 32.784 | 35.043 | 35.9752 | 35.0928 | 37.5304 | 36.507 | 37.4278 | 38.0914 | 37.8188 | 37.8188 | 37.8188 | 37.8188 | 37.8188 | 37.8188 | 37.8188 | 37.8188 | 37.8188 | 37.8188 | 37.8188 | 37.8188 | 37.8188 | 37.8188 | 37.8188 | 37.8188
60% | 934.9866 | 23.6464 | 26.122 | 26.3845 | 26.709 | 27.1399 | 27.5483 | 28.2622 | 30.0576 | 31.0233 | 30.3188 | 32.4998 | 32.8928 | 33.1753 | 34.5067 | 34.7235 | 34.7235 | 34.7235 | 34.7235 | 34.7235 | 34.7235 | 34.7235 | 34.7235 | 34.7235 | 34.7235 | 34.7235 | 34.7235 | 34.7235 | 34.7235 | 34.7235 | 34.7235 | 60% | 934.9866 | 25.9216 | 28.2829 | 28.5274 | 29.3713 | 29.3508 | 29.5364 | 30.2622 | 32.3474 | 33.2079 | 32.3934 | 34.6434 | 33.6987 | 34.5488 | 35.1613 | 34.9097 | 34.9097 | 34.9097 | 34.9097 | 34.9097 | 34.9097 | 34.9097 | 34.9097 | 34.9097 | 34.9097 | 34.9097 | 34.9097 | 34.9097 | 34.9097 | 34.9097 | 34.9097
55% | 1310.9428 | 21.6759 | 23.9451 | 24.1858 | 24.4832 | 24.8782 | 25.2527 | 25.907 | 27.5528 | 28.438 | 27.7922 | 29.7915 | 30.1517 | 30.4106 | 31.6312 | 31.8298 | 31.8298 | 31.8298 | 31.8298 | 31.8298 | 31.8298 | 31.8298 | 31.8298 | 31.8298 | 31.8298 | 31.8298 | 31.8298 | 31.8298 | 31.8298 | 31.8298 | 31.8298 | 55% | 1310.9428 | 23.7614 | 25.926 | 26.1501 | 26.9237 | 26.9049 | 27.075 | 27.7403 | 29.6518 | 30.4406 | 29.6939 | 31.7565 | 30.8905 | 31.6697 | 32.2312 | 32.0005 | 32.0005 | 32.0005 | 32.0005 | 32.0005 | 32.0005 | 32.0005 | 32.0005 | 32.0005 | 32.0005 | 32.0005 | 32.0005 | 32.0005 | 32.0005 | 32.0005 | 32.0005
50% | 1730.2899 | 19.7054 | 21.7683 | 21.9871 | 22.2575 | 22.6166 | 22.957 | 23.5518 | 25.048 | 25.8527 | 25.2657 | 27.0832 | 27.4106 | 27.646 | 28.7556 | 28.9362 | 28.9362 | 28.9362 | 28.9362 | 28.9362 | 28.9362 | 28.9362 | 28.9362 | 28.9362 | 28.9362 | 28.9362 | 28.9362 | 28.9362 | 28.9362 | 28.9362 | 28.9362 | 50% | 1730.2899 | 21.6013 | 23.5691 | 23.7729 | 24.4761 | 24.459 | 24.6136 | 25.2185 | 26.9562 | 27.6733 | 26.9945 | 28.8695 | 28.0823 | 28.7906 | 29.3011 | 29.0914 | 29.0914 | 29.0914 | 29.0914 | 29.0914 | 29.0914 | 29.0914 | 29.0914 | 29.0914 | 29.0914 | 29.0914 | 29.0914 | 29.0914 | 29.0914 | 29.0914 | 29.0914
45% | 2168.0633 | 17.7348 | 19.5915 | 19.7883 | 20.0317 | 20.3549 | 20.6613 | 21.1967 | 22.5432 | 23.2675 | 22.7391 | 24.3749 | 24.6696 | 24.8814 | 25.8801 | 26.0426 | 26.0426 | 26.0426 | 26.0426 | 26.0426 | 26.0426 | 26.0426 | 26.0426 | 26.0426 | 26.0426 | 26.0426 | 26.0426 | 26.0426 | 26.0426 | 26.0426 | 26.0426 | 45% | 2168.0633 | 19.4412 | 21.2122 | 21.3956 | 22.0285 | 22.0131 | 22.1523 | 22.6966 | 24.2606 | 24.9059 | 24.295 | 25.9826 | 25.2741 | 25.9116 | 26.371 | 26.1822 | 26.1822 | 26.1822 | 26.1822 | 26.1822 | 26.1822 | 26.1822 | 26.1822 | 26.1822 | 26.1822 | 26.1822 | 26.1822 | 26.1822 | 26.1822 | 26.1822 | 26.1822
40% | 2609.7004 | 15.7643 | 17.4146 | 17.5896 | 17.806 | 18.0932 | 18.3656 | 18.8415 | 20.0384 | 20.6822 | 20.2125 | 21.6665 | 21.9285 | 22.1168 | 23.0045 | 23.149 | 23.149 | 23.149 | 23.149 | 23.149 | 23.149 | 23.149 | 23.149 | 23.149 | 23.149 | 23.149 | 23.149 | 23.149 | 23.149 | 23.149 | 23.149 | 40% | 2609.7004 | 17.2811 | 18.8553 | 19.0183 | 19.5809 | 19.5672 | 19.6909 | 20.1748 | 21.5649 | 22.1386 | 21.5956 | 23.0956 | 22.4658 | 23.0325 | 23.4409 | 23.2731 | 23.2731 | 23.2731 | 23.2731 | 23.2731 | 23.2731 | 23.2731 | 23.2731 | 23.2731 | 23.2731 | 23.2731 | 23.2731 | 23.2731 | 23.2731 | 23.2731 | 23.2731
35% | 2998.1389 | 13.7937 | 15.2378 | 15.3909 | 15.5802 | 15.8316 | 16.0699 | 16.4863 | 17.5336 | 18.0969 | 17.686 | 18.9582 | 19.1875 | 19.3522 | 20.1289 | 20.2554 | 20.2554 | 20.2554 | 20.2554 | 20.2554 | 20.2554 | 20.2554 | 20.2554 | 20.2554 | 20.2554 | 20.2554 | 20.2554 | 20.2554 | 20.2554 | 20.2554 | 20.2554 | 35% | 2998.1389 | 15.1209 | 16.4984 | 16.641 | 17.1333 | 17.1213 | 17.2295 | 17.6529 | 18.8693 | 19.3713 | 18.8961 | 20.2087 | 19.6576 | 20.1535 | 20.5108 | 20.364 | 20.364 | 20.364 | 20.364 | 20.364 | 20.364 | 20.364 | 20.364 | 20.364 | 20.364 | 20.364 | 20.364 | 20.364 | 20.364 | 20.364 | 20.364
30% | 3309.3057 | 11.8232 | 13.061 | 13.1922 | 13.3545 | 13.5699 | 13.7742 | 14.1311 | 15.0288 | 15.5116 | 15.1594 | 16.2499 | 16.4464 | 16.5876 | 17.2534 | 17.3617 | 17.3617 | 17.3617 | 17.3617 | 17.3617 | 17.3617 | 17.3617 | 17.3617 | 17.3617 | 17.3617 | 17.3617 | 17.3617 | 17.3617 | 17.3617 | 17.3617 | 17.3617 | 30% | 3309.3057 | 12.9608 | 14.1414 | 14.2637 | 14.6857 | 14.6754 | 14.7682 | 15.1311 | 16.1737 | 16.604 | 16.1967 | 17.3217 | 16.8494 | 17.2744 | 17.5807 | 17.4548 | 17.4548 | 17.4548 | 17.4548 | 17.4548 | 17.4548 | 17.4548 | 17.4548 | 17.4548 | 17.4548 | 17.4548 | 17.4548 | 17.4548 | 17.4548 | 17.4548 | 17.4548
25% | 3537.8514 | 9.8527 | 10.8842 | 10.9935 | 11.1287 | 11.3083 | 11.4785 | 11.7759 | 12.524 | 12.9264 | 12.6328 | 13.5416 | 13.7053 | 13.823 | 14.3778 | 14.4681 | 14.4681 | 14.4681 | 14.4681 | 14.4681 | 14.4681 | 14.4681 | 14.4681 | 14.4681 | 14.4681 | 14.4681 | 14.4681 | 14.4681 | 14.4681 | 14.4681 | 14.4681 | 25% | 3537.8514 | 10.8007 | 11.7845 | 11.8864 | 12.2381 | 12.2295 | 12.3068 | 12.6092 | 13.4781 | 13.8366 | 13.4972 | 14.4348 | 14.0411 | 14.3953 | 14.6506 | 14.5457 | 14.5457 | 14.5457 | 14.5457 | 14.5457 | 14.5457 | 14.5457 | 14.5457 | 14.5457 | 14.5457 | 14.5457 | 14.5457 | 14.5457 | 14.5457 | 14.5457 | 14.5457
20% | 3731.0305 | 7.8821 | 8.7073 | 8.7948 | 8.903 | 9.0466 | 9.1828 | 9.4207 | 10.0192 | 10.3411 | 10.1063 | 10.8333 | 10.9643 | 11.0584 | 11.5022 | 11.5745 | 11.5745 | 11.5745 | 11.5745 | 11.5745 | 11.5745 | 11.5745 | 11.5745 | 11.5745 | 11.5745 | 11.5745 | 11.5745 | 11.5745 | 11.5745 | 11.5745 | 11.5745 | 20% | 3731.0305 | 8.6405 | 9.4276 | 9.5091 | 9.7904 | 9.7836 | 9.8455 | 10.0874 | 10.7825 | 11.0693 | 10.7978 | 11.5478 | 11.2329 | 11.5163 | 11.7204 | 11.6366 | 11.6366 | 11.6366 | 11.6366 | 11.6366 | 11.6366 | 11.6366 | 11.6366 | 11.6366 | 11.6366 | 11.6366 | 11.6366 | 11.6366 | 11.6366 | 11.6366 | 11.6366
15% | 3910.2412 | 5.9116 | 6.5305 | 6.5961 | 6.6772 | 6.785 | 6.8871 | 7.0656 | 7.5144 | 7.7558 | 7.5797 | 8.125 | 8.2232 | 8.2938 | 8.6267 | 8.6809 | 8.6809 | 8.6809 | 8.6809 | 8.6809 | 8.6809 | 8.6809 | 8.6809 | 8.6809 | 8.6809 | 8.6809 | 8.6809 | 8.6809 | 8.6809 | 8.6809 | 8.6809 | 15% | 3910.2412 | 6.4804 | 7.0707 | 7.1319 | 7.3428 | 7.3377 | 7.3841 | 7.5655 | 8.0869 | 8.302 | 8.0983 | 8.6609 | 8.4247 | 8.6372 | 8.7903 | 8.7274 | 8.7274 | 8.7274 | 8.7274 | 8.7274 | 8.7274 | 8.7274 | 8.7274 | 8.7274 | 8.7274 | 8.7274 | 8.7274 | 8.7274 | 8.7274 | 8.7274 | 8.7274
10% | 4075.1864 | 3.9411 | 4.3537 | 4.3974 | 4.4515 | 4.5233 | 4.5914 | 4.7104 | 5.0096 | 5.1705 | 5.0531 | 5.4166 | 5.4821 | 5.5292 | 5.7511 | 5.7872 | 5.7872 | 5.7872 | 5.7872 | 5.7872 | 5.7872 | 5.7872 | 5.7872 | 5.7872 | 5.7872 | 5.7872 | 5.7872 | 5.7872 | 5.7872 | 5.7872 | 5.7872 | 10% | 4075.1864 | 4.3203 | 4.7138 | 4.7546 | 4.8952 | 4.8918 | 4.9227 | 5.0437 | 5.3912 | 5.5347 | 5.3989 | 5.7739 | 5.6165 | 5.7581 | 5.8602 | 5.8183 | 5.8183 | 5.8183 | 5.8183 | 5.8183 | 5.8183 | 5.8183 | 5.8183 | 5.8183 | 5.8183 | 5.8183 | 5.8183 | 5.8183 | 5.8183 | 5.8183 | 5.8183
5% | 4251.7223 | 1.9705 | 2.1768 | 2.1987 | 2.2257 | 2.2617 | 2.2957 | 2.3552 | 2.5048 | 2.5853 | 2.5266 | 2.7083 | 2.7411 | 2.7646 | 2.8756 | 2.8936 | 2.8936 | 2.8936 | 2.8936 | 2.8936 | 2.8936 | 2.8936 | 2.8936 | 2.8936 | 2.8936 | 2.8936 | 2.8936 | 2.8936 | 2.8936 | 2.8936 | 2.8936 | 5% | 4251.7223 | 2.1601 | 2.3569 | 2.3773 | 2.4476 | 2.4459 | 2.4614 | 2.5218 | 2.6956 | 2.7673 | 2.6994 | 2.887 | 2.8082 | 2.8791 | 2.9301 | 2.9091 | 2.9091 | 2.9091 | 2.9091 | 2.9091 | 2.9091 | 2.9091 | 2.9091 | 2.9091 | 2.9091 | 2.9091 | 2.9091 | 2.9091 | 2.9091 | 2.9091 | 2.9091
9.992e-14% | 4391.7028 | 3.9379e-14 | 4.3502e-14 | 4.3939e-14 | 4.4479e-14 | 4.5197e-14 | 4.5877e-14 | 4.7066e-14 | 5.0056e-14 | 5.1664e-14 | 5.0491e-14 | 5.4123e-14 | 5.4777e-14 | 5.5248e-14 | 5.7465e-14 | 5.7826e-14 | 5.7826e-14 | 5.7826e-14 | 5.7826e-14 | 5.7826e-14 | 5.7826e-14 | 5.7826e-14 | 5.7826e-14 | 5.7826e-14 | 5.7826e-14 | 5.7826e-14 | 5.7826e-14 | 5.7826e-14 | 5.7826e-14 | 5.7826e-14 | 5.7826e-14 | 9.992e-14% | 4391.7028 | 4.3168e-14 | 4.71e-14 | 4.7508e-14 | 4.8913e-14 | 4.8879e-14 | 4.9188e-14 | 5.0397e-14 | 5.3869e-14 | 5.5302e-14 | 5.3946e-14 | 5.7693e-14 | 5.612e-14 | 5.7535e-14 | 5.8555e-14 | 5.8136e-14 | 5.8136e-14 | 5.8136e-14 | 5.8136e-14 | 5.8136e-14 | 5.8136e-14 | 5.8136e-14 | 5.8136e-14 | 5.8136e-14 | 5.8136e-14 | 5.8136e-14 | 5.8136e-14 | 5.8136e-14 | 5.8136e-14 | 5.8136e-14 | 5.8136e-14
Summer Season | [31 empty] | Summer Season
P50 | [31 empty] | P10
% of MD | Summer - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Summer - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 41.4021 | 44.4975 | 44.8085 | 44.6561 | 44.801 | 44.8606 | 45.0515 | 45.4441 | 45.7743 | 45.9263 | 45.7908 | 46.3589 | 46.449 | 46.3423 | 46.5561 | 46.6661 | 46.6661 | 46.6661 | 46.6661 | 46.6661 | 46.6661 | 46.6661 | 46.6661 | 46.6661 | 46.6661 | 46.6661 | 46.6661 | 46.6661 | 46.6661 | 46.6661 | 100% | 0 | 50.9365 | 54.3957 | 54.4912 | 54.3883 | 54.4147 | 54.6036 | 54.9865 | 55.6607 | 56.012 | 56.2661 | 56.6508 | 57.1419 | 57.7357 | 58.0469 | 57.946 | 58.056 | 58.056 | 58.056 | 58.056 | 58.056 | 58.056 | 58.056 | 58.056 | 58.056 | 58.056 | 58.056 | 58.056 | 58.056 | 58.056 | 58.056
99% | 0.37816 | 40.9881 | 44.0525 | 44.3604 | 44.2095 | 44.353 | 44.412 | 44.601 | 44.9896 | 45.3165 | 45.467 | 45.3329 | 45.8953 | 45.9845 | 45.8789 | 46.0906 | 46.1995 | 46.1995 | 46.1995 | 46.1995 | 46.1995 | 46.1995 | 46.1995 | 46.1995 | 46.1995 | 46.1995 | 46.1995 | 46.1995 | 46.1995 | 46.1995 | 46.1995 | 99% | 0 | 50.4271 | 53.8518 | 53.9463 | 53.8444 | 53.8706 | 54.0576 | 54.4366 | 55.1041 | 55.4519 | 55.7035 | 56.0843 | 56.5704 | 57.1583 | 57.4664 | 57.3665 | 57.4754 | 57.4754 | 57.4754 | 57.4754 | 57.4754 | 57.4754 | 57.4754 | 57.4754 | 57.4754 | 57.4754 | 57.4754 | 57.4754 | 57.4754 | 57.4754 | 57.4754
98% | 0.37816 | 40.5741 | 43.6075 | 43.9123 | 43.7629 | 43.905 | 43.9634 | 44.1505 | 44.5352 | 44.8588 | 45.0078 | 44.875 | 45.4317 | 45.52 | 45.4155 | 45.625 | 45.7328 | 45.7328 | 45.7328 | 45.7328 | 45.7328 | 45.7328 | 45.7328 | 45.7328 | 45.7328 | 45.7328 | 45.7328 | 45.7328 | 45.7328 | 45.7328 | 45.7328 | 98% | 0 | 49.9177 | 53.3078 | 53.4014 | 53.3005 | 53.3264 | 53.5116 | 53.8867 | 54.5475 | 54.8917 | 55.1408 | 55.5178 | 55.999 | 56.581 | 56.886 | 56.7871 | 56.8949 | 56.8949 | 56.8949 | 56.8949 | 56.8949 | 56.8949 | 56.8949 | 56.8949 | 56.8949 | 56.8949 | 56.8949 | 56.8949 | 56.8949 | 56.8949 | 56.8949
97% | 0.37816 | 40.1601 | 43.1625 | 43.4643 | 43.3164 | 43.457 | 43.5148 | 43.7 | 44.0807 | 44.4011 | 44.5485 | 44.4171 | 44.9681 | 45.0555 | 44.9521 | 45.1595 | 45.2662 | 45.2662 | 45.2662 | 45.2662 | 45.2662 | 45.2662 | 45.2662 | 45.2662 | 45.2662 | 45.2662 | 45.2662 | 45.2662 | 45.2662 | 45.2662 | 45.2662 | 97% | 0.37816 | 49.4084 | 52.7639 | 52.8564 | 52.7566 | 52.7823 | 52.9655 | 53.3369 | 53.9908 | 54.3316 | 54.5781 | 54.9513 | 55.4276 | 56.0036 | 56.3055 | 56.2076 | 56.3143 | 56.3143 | 56.3143 | 56.3143 | 56.3143 | 56.3143 | 56.3143 | 56.3143 | 56.3143 | 56.3143 | 56.3143 | 56.3143 | 56.3143 | 56.3143 | 56.3143
95% | 0.75633 | 39.332 | 42.2726 | 42.5681 | 42.4232 | 42.561 | 42.6176 | 42.7989 | 43.1719 | 43.4856 | 43.63 | 43.5013 | 44.0409 | 44.1265 | 44.0252 | 44.2283 | 44.3328 | 44.3328 | 44.3328 | 44.3328 | 44.3328 | 44.3328 | 44.3328 | 44.3328 | 44.3328 | 44.3328 | 44.3328 | 44.3328 | 44.3328 | 44.3328 | 44.3328 | 95% | 0.37816 | 48.3896 | 51.6759 | 51.7666 | 51.6689 | 51.694 | 51.8735 | 52.2371 | 52.8776 | 53.2114 | 53.4528 | 53.8182 | 54.2848 | 54.8489 | 55.1446 | 55.0487 | 55.1532 | 55.1532 | 55.1532 | 55.1532 | 55.1532 | 55.1532 | 55.1532 | 55.1532 | 55.1532 | 55.1532 | 55.1532 | 55.1532 | 55.1532 | 55.1532 | 55.1532
90% | 9.0759 | 37.2619 | 40.0477 | 40.3277 | 40.1904 | 40.3209 | 40.3745 | 40.5464 | 40.8996 | 41.1969 | 41.3337 | 41.2117 | 41.723 | 41.8041 | 41.7081 | 41.9005 | 41.9995 | 41.9995 | 41.9995 | 41.9995 | 41.9995 | 41.9995 | 41.9995 | 41.9995 | 41.9995 | 41.9995 | 41.9995 | 41.9995 | 41.9995 | 41.9995 | 41.9995 | 90% | 0.75633 | 45.8428 | 48.9562 | 49.0421 | 48.9494 | 48.9733 | 49.1433 | 49.4878 | 50.0946 | 50.4108 | 50.6395 | 50.9857 | 51.4277 | 51.9621 | 52.2422 | 52.1514 | 52.2504 | 52.2504 | 52.2504 | 52.2504 | 52.2504 | 52.2504 | 52.2504 | 52.2504 | 52.2504 | 52.2504 | 52.2504 | 52.2504 | 52.2504 | 52.2504 | 52.2504
85% | 40.4636 | 35.1918 | 37.8228 | 38.0872 | 37.9576 | 38.0809 | 38.1315 | 38.2938 | 38.6274 | 38.9081 | 39.0374 | 38.9222 | 39.405 | 39.4816 | 39.391 | 39.5727 | 39.6662 | 39.6662 | 39.6662 | 39.6662 | 39.6662 | 39.6662 | 39.6662 | 39.6662 | 39.6662 | 39.6662 | 39.6662 | 39.6662 | 39.6662 | 39.6662 | 39.6662 | 85% | 1.1345 | 43.296 | 46.2364 | 46.3175 | 46.23 | 46.2525 | 46.4131 | 46.7385 | 47.3116 | 47.6102 | 47.8262 | 48.1532 | 48.5706 | 49.0753 | 49.3399 | 49.2541 | 49.3476 | 49.3476 | 49.3476 | 49.3476 | 49.3476 | 49.3476 | 49.3476 | 49.3476 | 49.3476 | 49.3476 | 49.3476 | 49.3476 | 49.3476 | 49.3476 | 49.3476
80% | 94.5411 | 33.1217 | 35.598 | 35.8468 | 35.7248 | 35.8408 | 35.8885 | 36.0412 | 36.3552 | 36.6194 | 36.741 | 36.6326 | 37.0871 | 37.1592 | 37.0739 | 37.2449 | 37.3329 | 37.3329 | 37.3329 | 37.3329 | 37.3329 | 37.3329 | 37.3329 | 37.3329 | 37.3329 | 37.3329 | 37.3329 | 37.3329 | 37.3329 | 37.3329 | 37.3329 | 80% | 2.6471 | 40.7492 | 43.5166 | 43.5929 | 43.5106 | 43.5318 | 43.6829 | 43.9892 | 44.5285 | 44.8096 | 45.0129 | 45.3206 | 45.7135 | 46.1886 | 46.4375 | 46.3568 | 46.4448 | 46.4448 | 46.4448 | 46.4448 | 46.4448 | 46.4448 | 46.4448 | 46.4448 | 46.4448 | 46.4448 | 46.4448 | 46.4448 | 46.4448 | 46.4448 | 46.4448
75% | 197.0236 | 31.0516 | 33.3731 | 33.6064 | 33.492 | 33.6008 | 33.6454 | 33.7886 | 34.083 | 34.3307 | 34.4447 | 34.3431 | 34.7692 | 34.8367 | 34.7568 | 34.9171 | 34.9996 | 34.9996 | 34.9996 | 34.9996 | 34.9996 | 34.9996 | 34.9996 | 34.9996 | 34.9996 | 34.9996 | 34.9996 | 34.9996 | 34.9996 | 34.9996 | 34.9996 | 75% | 3.4035 | 38.2023 | 40.7968 | 40.8684 | 40.7912 | 40.811 | 40.9527 | 41.2398 | 41.7455 | 42.009 | 42.1996 | 42.4881 | 42.8564 | 43.3018 | 43.5352 | 43.4595 | 43.542 | 43.542 | 43.542 | 43.542 | 43.542 | 43.542 | 43.542 | 43.542 | 43.542 | 43.542 | 43.542 | 43.542 | 43.542 | 43.542 | 43.542
70% | 336.9444 | 28.9815 | 31.1482 | 31.366 | 31.2592 | 31.3607 | 31.4024 | 31.5361 | 31.8108 | 32.042 | 32.1484 | 32.0536 | 32.4512 | 32.5143 | 32.4396 | 32.5893 | 32.6663 | 32.6663 | 32.6663 | 32.6663 | 32.6663 | 32.6663 | 32.6663 | 32.6663 | 32.6663 | 32.6663 | 32.6663 | 32.6663 | 32.6663 | 32.6663 | 32.6663 | 70% | 5.6725 | 35.6555 | 38.077 | 38.1438 | 38.0718 | 38.0903 | 38.2225 | 38.4905 | 38.9625 | 39.2084 | 39.3863 | 39.6555 | 39.9993 | 40.415 | 40.6328 | 40.5622 | 40.6392 | 40.6392 | 40.6392 | 40.6392 | 40.6392 | 40.6392 | 40.6392 | 40.6392 | 40.6392 | 40.6392 | 40.6392 | 40.6392 | 40.6392 | 40.6392 | 40.6392
65% | 521.4885 | 26.9114 | 28.9234 | 29.1255 | 29.0264 | 29.1207 | 29.1594 | 29.2835 | 29.5386 | 29.7533 | 29.8521 | 29.764 | 30.1333 | 30.1918 | 30.1225 | 30.2615 | 30.333 | 30.333 | 30.333 | 30.333 | 30.333 | 30.333 | 30.333 | 30.333 | 30.333 | 30.333 | 30.333 | 30.333 | 30.333 | 30.333 | 30.333 | 65% | 6.4288 | 33.1087 | 35.3572 | 35.4193 | 35.3524 | 35.3696 | 35.4924 | 35.7412 | 36.1794 | 36.4078 | 36.573 | 36.823 | 37.1422 | 37.5282 | 37.7305 | 37.6649 | 37.7364 | 37.7364 | 37.7364 | 37.7364 | 37.7364 | 37.7364 | 37.7364 | 37.7364 | 37.7364 | 37.7364 | 37.7364 | 37.7364 | 37.7364 | 37.7364 | 37.7364
60% | 812.675 | 24.8413 | 26.6985 | 26.8851 | 26.7936 | 26.8806 | 26.9164 | 27.0309 | 27.2664 | 27.4646 | 27.5558 | 27.4745 | 27.8153 | 27.8694 | 27.8054 | 27.9337 | 27.9997 | 27.9997 | 27.9997 | 27.9997 | 27.9997 | 27.9997 | 27.9997 | 27.9997 | 27.9997 | 27.9997 | 27.9997 | 27.9997 | 27.9997 | 27.9997 | 27.9997 | 60% | 11.3449 | 30.5619 | 32.6374 | 32.6947 | 32.633 | 32.6488 | 32.7622 | 32.9919 | 33.3964 | 33.6072 | 33.7597 | 33.9905 | 34.2851 | 34.6414 | 34.8281 | 34.7676 | 34.8336 | 34.8336 | 34.8336 | 34.8336 | 34.8336 | 34.8336 | 34.8336 | 34.8336 | 34.8336 | 34.8336 | 34.8336 | 34.8336 | 34.8336 | 34.8336 | 34.8336
55% | 1202.1843 | 22.7712 | 24.4736 | 24.6447 | 24.5608 | 24.6406 | 24.6733 | 24.7783 | 24.9942 | 25.1759 | 25.2595 | 25.1849 | 25.4974 | 25.5469 | 25.4883 | 25.6059 | 25.6664 | 25.6664 | 25.6664 | 25.6664 | 25.6664 | 25.6664 | 25.6664 | 25.6664 | 25.6664 | 25.6664 | 25.6664 | 25.6664 | 25.6664 | 25.6664 | 25.6664 | 55% | 35.5474 | 28.0151 | 29.9176 | 29.9701 | 29.9135 | 29.9281 | 30.032 | 30.2426 | 30.6134 | 30.8066 | 30.9464 | 31.1579 | 31.428 | 31.7546 | 31.9258 | 31.8703 | 31.9308 | 31.9308 | 31.9308 | 31.9308 | 31.9308 | 31.9308 | 31.9308 | 31.9308 | 31.9308 | 31.9308 | 31.9308 | 31.9308 | 31.9308 | 31.9308 | 31.9308
50% | 1686.2345 | 20.7011 | 22.2487 | 22.4043 | 22.328 | 22.4005 | 22.4303 | 22.5258 | 22.722 | 22.8871 | 22.9631 | 22.8954 | 23.1794 | 23.2245 | 23.1712 | 23.2781 | 23.3331 | 23.3331 | 23.3331 | 23.3331 | 23.3331 | 23.3331 | 23.3331 | 23.3331 | 23.3331 | 23.3331 | 23.3331 | 23.3331 | 23.3331 | 23.3331 | 23.3331 | 50% | 95.2974 | 25.4682 | 27.1979 | 27.2456 | 27.1941 | 27.2074 | 27.3018 | 27.4932 | 27.8303 | 28.006 | 28.1331 | 28.3254 | 28.5709 | 28.8678 | 29.0234 | 28.973 | 29.028 | 29.028 | 29.028 | 29.028 | 29.028 | 29.028 | 29.028 | 29.028 | 29.028 | 29.028 | 29.028 | 29.028 | 29.028 | 29.028 | 29.028
45% | 2129.0649 | 18.631 | 20.0239 | 20.1638 | 20.0952 | 20.1605 | 20.1873 | 20.2732 | 20.4498 | 20.5984 | 20.6668 | 20.6059 | 20.8615 | 20.902 | 20.8541 | 20.9503 | 20.9998 | 20.9998 | 20.9998 | 20.9998 | 20.9998 | 20.9998 | 20.9998 | 20.9998 | 20.9998 | 20.9998 | 20.9998 | 20.9998 | 20.9998 | 20.9998 | 20.9998 | 45% | 208.7467 | 22.9214 | 24.4781 | 24.521 | 24.4747 | 24.4866 | 24.5716 | 24.7439 | 25.0473 | 25.2054 | 25.3198 | 25.4928 | 25.7138 | 25.9811 | 26.1211 | 26.0757 | 26.1252 | 26.1252 | 26.1252 | 26.1252 | 26.1252 | 26.1252 | 26.1252 | 26.1252 | 26.1252 | 26.1252 | 26.1252 | 26.1252 | 26.1252 | 26.1252 | 26.1252
40% | 2484.5393 | 16.5608 | 17.799 | 17.9234 | 17.8624 | 17.9204 | 17.9442 | 18.0206 | 18.1776 | 18.3097 | 18.3705 | 18.3163 | 18.5435 | 18.5796 | 18.5369 | 18.6225 | 18.6665 | 18.6665 | 18.6665 | 18.6665 | 18.6665 | 18.6665 | 18.6665 | 18.6665 | 18.6665 | 18.6665 | 18.6665 | 18.6665 | 18.6665 | 18.6665 | 18.6665 | 40% | 380.4333 | 20.3746 | 21.7583 | 21.7965 | 21.7553 | 21.7659 | 21.8415 | 21.9946 | 22.2643 | 22.4048 | 22.5065 | 22.6603 | 22.8567 | 23.0943 | 23.2188 | 23.1784 | 23.2224 | 23.2224 | 23.2224 | 23.2224 | 23.2224 | 23.2224 | 23.2224 | 23.2224 | 23.2224 | 23.2224 | 23.2224 | 23.2224 | 23.2224 | 23.2224 | 23.2224
35% | 2808.248 | 14.4907 | 15.5741 | 15.683 | 15.6296 | 15.6804 | 15.7012 | 15.768 | 15.9054 | 16.021 | 16.0742 | 16.0268 | 16.2256 | 16.2571 | 16.2198 | 16.2947 | 16.3332 | 16.3332 | 16.3332 | 16.3332 | 16.3332 | 16.3332 | 16.3332 | 16.3332 | 16.3332 | 16.3332 | 16.3332 | 16.3332 | 16.3332 | 16.3332 | 16.3332 | 35% | 696.5786 | 17.8278 | 19.0385 | 19.0719 | 19.0359 | 19.0452 | 19.1113 | 19.2453 | 19.4812 | 19.6042 | 19.6931 | 19.8278 | 19.9997 | 20.2075 | 20.3164 | 20.2811 | 20.3196 | 20.3196 | 20.3196 | 20.3196 | 20.3196 | 20.3196 | 20.3196 | 20.3196 | 20.3196 | 20.3196 | 20.3196 | 20.3196 | 20.3196 | 20.3196 | 20.3196
30% | 3095.6528 | 12.4206 | 13.3492 | 13.4426 | 13.3968 | 13.4403 | 13.4582 | 13.5155 | 13.6332 | 13.7323 | 13.7779 | 13.7372 | 13.9077 | 13.9347 | 13.9027 | 13.9668 | 13.9998 | 13.9998 | 13.9998 | 13.9998 | 13.9998 | 13.9998 | 13.9998 | 13.9998 | 13.9998 | 13.9998 | 13.9998 | 13.9998 | 13.9998 | 13.9998 | 13.9998 | 30% | 1260.7997 | 15.2809 | 16.3187 | 16.3474 | 16.3165 | 16.3244 | 16.3811 | 16.4959 | 16.6982 | 16.8036 | 16.8798 | 16.9952 | 17.1426 | 17.3207 | 17.4141 | 17.3838 | 17.4168 | 17.4168 | 17.4168 | 17.4168 | 17.4168 | 17.4168 | 17.4168 | 17.4168 | 17.4168 | 17.4168 | 17.4168 | 17.4168 | 17.4168 | 17.4168 | 17.4168
25% | 3358.8552 | 10.3505 | 11.1244 | 11.2021 | 11.164 | 11.2003 | 11.2151 | 11.2629 | 11.361 | 11.4436 | 11.4816 | 11.4477 | 11.5897 | 11.6122 | 11.5856 | 11.639 | 11.6665 | 11.6665 | 11.6665 | 11.6665 | 11.6665 | 11.6665 | 11.6665 | 11.6665 | 11.6665 | 11.6665 | 11.6665 | 11.6665 | 11.6665 | 11.6665 | 11.6665 | 25% | 1965.3198 | 12.7341 | 13.5989 | 13.6228 | 13.5971 | 13.6037 | 13.6509 | 13.7466 | 13.9152 | 14.003 | 14.0665 | 14.1627 | 14.2855 | 14.4339 | 14.5117 | 14.4865 | 14.514 | 14.514 | 14.514 | 14.514 | 14.514 | 14.514 | 14.514 | 14.514 | 14.514 | 14.514 | 14.514 | 14.514 | 14.514 | 14.514 | 14.514
20% | 3588.7791 | 8.2804 | 8.8995 | 8.9617 | 8.9312 | 8.9602 | 8.9721 | 9.0103 | 9.0888 | 9.1549 | 9.1853 | 9.1582 | 9.2718 | 9.2898 | 9.2685 | 9.3112 | 9.3332 | 9.3332 | 9.3332 | 9.3332 | 9.3332 | 9.3332 | 9.3332 | 9.3332 | 9.3332 | 9.3332 | 9.3332 | 9.3332 | 9.3332 | 9.3332 | 9.3332 | 20% | 2490.2118 | 10.1873 | 10.8791 | 10.8982 | 10.8777 | 10.8829 | 10.9207 | 10.9973 | 11.1321 | 11.2024 | 11.2532 | 11.3302 | 11.4284 | 11.5471 | 11.6094 | 11.5892 | 11.6112 | 11.6112 | 11.6112 | 11.6112 | 11.6112 | 11.6112 | 11.6112 | 11.6112 | 11.6112 | 11.6112 | 11.6112 | 11.6112 | 11.6112 | 11.6112 | 11.6112
15% | 3802.4419 | 6.2103 | 6.6746 | 6.7213 | 6.6984 | 6.7202 | 6.7291 | 6.7577 | 6.8166 | 6.8661 | 6.8889 | 6.8686 | 6.9538 | 6.9673 | 6.9514 | 6.9834 | 6.9999 | 6.9999 | 6.9999 | 6.9999 | 6.9999 | 6.9999 | 6.9999 | 6.9999 | 6.9999 | 6.9999 | 6.9999 | 6.9999 | 6.9999 | 6.9999 | 6.9999 | 15% | 2997.7083 | 7.6405 | 8.1594 | 8.1737 | 8.1582 | 8.1622 | 8.1905 | 8.248 | 8.3491 | 8.4018 | 8.4399 | 8.4976 | 8.5713 | 8.6604 | 8.707 | 8.6919 | 8.7084 | 8.7084 | 8.7084 | 8.7084 | 8.7084 | 8.7084 | 8.7084 | 8.7084 | 8.7084 | 8.7084 | 8.7084 | 8.7084 | 8.7084 | 8.7084 | 8.7084
10% | 4024.8025 | 4.1402 | 4.4497 | 4.4809 | 4.4656 | 4.4801 | 4.4861 | 4.5052 | 4.5444 | 4.5774 | 4.5926 | 4.5791 | 4.6359 | 4.6449 | 4.6342 | 4.6556 | 4.6666 | 4.6666 | 4.6666 | 4.6666 | 4.6666 | 4.6666 | 4.6666 | 4.6666 | 4.6666 | 4.6666 | 4.6666 | 4.6666 | 4.6666 | 4.6666 | 4.6666 | 10% | 3491.5908 | 5.0936 | 5.4396 | 5.4491 | 5.4388 | 5.4415 | 5.4604 | 5.4986 | 5.5661 | 5.6012 | 5.6266 | 5.6651 | 5.7142 | 5.7736 | 5.8047 | 5.7946 | 5.8056 | 5.8056 | 5.8056 | 5.8056 | 5.8056 | 5.8056 | 5.8056 | 5.8056 | 5.8056 | 5.8056 | 5.8056 | 5.8056 | 5.8056 | 5.8056 | 5.8056
5% | 4239.978 | 2.0701 | 2.2249 | 2.2404 | 2.2328 | 2.2401 | 2.243 | 2.2526 | 2.2722 | 2.2887 | 2.2963 | 2.2895 | 2.3179 | 2.3224 | 2.3171 | 2.3278 | 2.3333 | 2.3333 | 2.3333 | 2.3333 | 2.3333 | 2.3333 | 2.3333 | 2.3333 | 2.3333 | 2.3333 | 2.3333 | 2.3333 | 2.3333 | 2.3333 | 2.3333 | 5% | 3955.9766 | 2.5468 | 2.7198 | 2.7246 | 2.7194 | 2.7207 | 2.7302 | 2.7493 | 2.783 | 2.8006 | 2.8133 | 2.8325 | 2.8571 | 2.8868 | 2.9023 | 2.8973 | 2.9028 | 2.9028 | 2.9028 | 2.9028 | 2.9028 | 2.9028 | 2.9028 | 2.9028 | 2.9028 | 2.9028 | 2.9028 | 2.9028 | 2.9028 | 2.9028 | 2.9028
9.992e-14% | 4391.6218 | 4.1369e-14 | 4.4462e-14 | 4.4773e-14 | 4.462e-14 | 4.4765e-14 | 4.4825e-14 | 4.5015e-14 | 4.5408e-14 | 4.5738e-14 | 4.589e-14 | 4.5754e-14 | 4.6322e-14 | 4.6412e-14 | 4.6305e-14 | 4.6519e-14 | 4.6629e-14 | 4.6629e-14 | 4.6629e-14 | 4.6629e-14 | 4.6629e-14 | 4.6629e-14 | 4.6629e-14 | 4.6629e-14 | 4.6629e-14 | 4.6629e-14 | 4.6629e-14 | 4.6629e-14 | 4.6629e-14 | 4.6629e-14 | 4.6629e-14 | 9.992e-14% | 4391.6218 | 5.0896e-14 | 5.4352e-14 | 5.4448e-14 | 5.4345e-14 | 5.4371e-14 | 5.456e-14 | 5.4943e-14 | 5.5616e-14 | 5.5967e-14 | 5.6221e-14 | 5.6605e-14 | 5.7096e-14 | 5.769e-14 | 5.8001e-14 | 5.79e-14 | 5.801e-14 | 5.801e-14 | 5.801e-14 | 5.801e-14 | 5.801e-14 | 5.801e-14 | 5.801e-14 | 5.801e-14 | 5.801e-14 | 5.801e-14 | 5.801e-14 | 5.801e-14 | 5.801e-14 | 5.801e-14 | 5.801e-14
Option 2
Winter Season | [31 empty] | Winter Season
P50 | [31 empty] | P10
% of MD | Winter - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Winter - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 39.4107 | 43.5366 | 43.9741 | 44.515 | 45.2331 | 45.9139 | 47.1037 | 50.096 | 51.7055 | 50.5313 | 54.1664 | 54.8213 | 55.2921 | 57.5112 | 57.8724 | 57.8724 | 57.8724 | 57.8724 | 57.8724 | 57.8724 | 57.8724 | 57.8724 | 57.8724 | 57.8724 | 57.8724 | 57.8724 | 57.8724 | 57.8724 | 57.8724 | 57.8724 | 100% | 0 | 43.2026 | 47.1382 | 47.5457 | 48.9522 | 48.918 | 49.2273 | 50.4369 | 53.9124 | 55.3465 | 53.989 | 57.7391 | 56.1646 | 57.5813 | 58.6022 | 58.1828 | 58.1828 | 58.1828 | 58.1828 | 58.1828 | 58.1828 | 58.1828 | 58.1828 | 58.1828 | 58.1828 | 58.1828 | 58.1828 | 58.1828 | 58.1828 | 58.1828 | 58.1828
99% | 0.2972 | 39.0166 | 43.1012 | 43.5344 | 44.0698 | 44.7808 | 45.4548 | 46.6326 | 49.595 | 51.1884 | 50.026 | 53.6247 | 54.2731 | 54.7392 | 56.9361 | 57.2937 | 57.2937 | 57.2937 | 57.2937 | 57.2937 | 57.2937 | 57.2937 | 57.2937 | 57.2937 | 57.2937 | 57.2937 | 57.2937 | 57.2937 | 57.2937 | 57.2937 | 57.2937 | 99% | 0.2972 | 42.7706 | 46.6668 | 47.0703 | 48.4627 | 48.4288 | 48.735 | 49.9326 | 53.3732 | 54.7931 | 53.4491 | 57.1617 | 55.6029 | 57.0055 | 58.0162 | 57.6009 | 57.6009 | 57.6009 | 57.6009 | 57.6009 | 57.6009 | 57.6009 | 57.6009 | 57.6009 | 57.6009 | 57.6009 | 57.6009 | 57.6009 | 57.6009 | 57.6009 | 57.6009
98% | 0.2972 | 38.6225 | 42.6659 | 43.0946 | 43.6247 | 44.3284 | 44.9956 | 46.1616 | 49.0941 | 50.6714 | 49.5207 | 53.083 | 53.7249 | 54.1862 | 56.361 | 56.715 | 56.715 | 56.715 | 56.715 | 56.715 | 56.715 | 56.715 | 56.715 | 56.715 | 56.715 | 56.715 | 56.715 | 56.715 | 56.715 | 56.715 | 56.715 | 98% | 0.2972 | 42.3386 | 46.1954 | 46.5948 | 47.9732 | 47.9396 | 48.2427 | 49.4282 | 52.8341 | 54.2396 | 52.9092 | 56.5843 | 55.0413 | 56.4297 | 57.4302 | 57.0191 | 57.0191 | 57.0191 | 57.0191 | 57.0191 | 57.0191 | 57.0191 | 57.0191 | 57.0191 | 57.0191 | 57.0191 | 57.0191 | 57.0191 | 57.0191 | 57.0191 | 57.0191
97% | 0.2972 | 38.2284 | 42.2305 | 42.6549 | 43.1795 | 43.8761 | 44.5365 | 45.6906 | 48.5931 | 50.1543 | 49.0154 | 52.5414 | 53.1767 | 53.6333 | 55.7859 | 56.1363 | 56.1363 | 56.1363 | 56.1363 | 56.1363 | 56.1363 | 56.1363 | 56.1363 | 56.1363 | 56.1363 | 56.1363 | 56.1363 | 56.1363 | 56.1363 | 56.1363 | 56.1363 | 97% | 0.2972 | 41.9066 | 45.724 | 46.1193 | 47.4837 | 47.4504 | 47.7504 | 48.9238 | 52.295 | 53.6861 | 52.3693 | 56.0069 | 54.4796 | 55.8539 | 56.8441 | 56.4373 | 56.4373 | 56.4373 | 56.4373 | 56.4373 | 56.4373 | 56.4373 | 56.4373 | 56.4373 | 56.4373 | 56.4373 | 56.4373 | 56.4373 | 56.4373 | 56.4373 | 56.4373
95% | 1.486 | 37.4402 | 41.3598 | 41.7754 | 42.2892 | 42.9715 | 43.6182 | 44.7485 | 47.5912 | 49.1202 | 48.0047 | 51.4581 | 52.0802 | 52.5275 | 54.6357 | 54.9788 | 54.9788 | 54.9788 | 54.9788 | 54.9788 | 54.9788 | 54.9788 | 54.9788 | 54.9788 | 54.9788 | 54.9788 | 54.9788 | 54.9788 | 54.9788 | 54.9788 | 54.9788 | 95% | 1.486 | 41.0425 | 44.7812 | 45.1684 | 46.5046 | 46.4721 | 46.7659 | 47.9151 | 51.2167 | 52.5792 | 51.2895 | 54.8521 | 53.3563 | 54.7022 | 55.6721 | 55.2736 | 55.2736 | 55.2736 | 55.2736 | 55.2736 | 55.2736 | 55.2736 | 55.2736 | 55.2736 | 55.2736 | 55.2736 | 55.2736 | 55.2736 | 55.2736 | 55.2736 | 55.2736
90% | 8.6188 | 35.4696 | 39.1829 | 39.5767 | 40.0635 | 40.7098 | 41.3225 | 42.3933 | 45.0864 | 46.5349 | 45.4782 | 48.7497 | 49.3392 | 49.7629 | 51.7601 | 52.0852 | 52.0852 | 52.0852 | 52.0852 | 52.0852 | 52.0852 | 52.0852 | 52.0852 | 52.0852 | 52.0852 | 52.0852 | 52.0852 | 52.0852 | 52.0852 | 52.0852 | 52.0852 | 90% | 8.6188 | 38.8824 | 42.4243 | 42.7911 | 44.057 | 44.0262 | 44.3045 | 45.3932 | 48.5211 | 49.8119 | 48.5901 | 51.9652 | 50.5481 | 51.8232 | 52.742 | 52.3645 | 52.3645 | 52.3645 | 52.3645 | 52.3645 | 52.3645 | 52.3645 | 52.3645 | 52.3645 | 52.3645 | 52.3645 | 52.3645 | 52.3645 | 52.3645 | 52.3645 | 52.3645
85% | 40.1218 | 33.4991 | 37.0061 | 37.378 | 37.8377 | 38.4481 | 39.0268 | 40.0381 | 42.5816 | 43.9497 | 42.9516 | 46.0414 | 46.5981 | 46.9983 | 48.8845 | 49.1916 | 49.1916 | 49.1916 | 49.1916 | 49.1916 | 49.1916 | 49.1916 | 49.1916 | 49.1916 | 49.1916 | 49.1916 | 49.1916 | 49.1916 | 49.1916 | 49.1916 | 49.1916 | 85% | 40.1218 | 36.7222 | 40.0674 | 40.4139 | 41.6094 | 41.5803 | 41.8432 | 42.8714 | 45.8255 | 47.0445 | 45.8906 | 49.0782 | 47.7399 | 48.9441 | 49.8119 | 49.4554 | 49.4554 | 49.4554 | 49.4554 | 49.4554 | 49.4554 | 49.4554 | 49.4554 | 49.4554 | 49.4554 | 49.4554 | 49.4554 | 49.4554 | 49.4554 | 49.4554 | 49.4554
80% | 93.0231 | 31.5286 | 34.8293 | 35.1793 | 35.612 | 36.1865 | 36.7311 | 37.6829 | 40.0768 | 41.3644 | 40.425 | 43.3331 | 43.857 | 44.2337 | 46.009 | 46.2979 | 46.2979 | 46.2979 | 46.2979 | 46.2979 | 46.2979 | 46.2979 | 46.2979 | 46.2979 | 46.2979 | 46.2979 | 46.2979 | 46.2979 | 46.2979 | 46.2979 | 46.2979 | 80% | 93.0231 | 34.5621 | 37.7105 | 38.0366 | 39.1618 | 39.1344 | 39.3818 | 40.3495 | 43.1299 | 44.2772 | 43.1912 | 46.1913 | 44.9317 | 46.065 | 46.8818 | 46.5462 | 46.5462 | 46.5462 | 46.5462 | 46.5462 | 46.5462 | 46.5462 | 46.5462 | 46.5462 | 46.5462 | 46.5462 | 46.5462 | 46.5462 | 46.5462 | 46.5462 | 46.5462
75% | 197.0426 | 29.558 | 32.6525 | 32.9806 | 33.3862 | 33.9248 | 34.4354 | 35.3278 | 37.572 | 38.7791 | 37.8985 | 40.6248 | 41.116 | 41.4691 | 43.1334 | 43.4043 | 43.4043 | 43.4043 | 43.4043 | 43.4043 | 43.4043 | 43.4043 | 43.4043 | 43.4043 | 43.4043 | 43.4043 | 43.4043 | 43.4043 | 43.4043 | 43.4043 | 43.4043 | 75% | 197.0426 | 32.402 | 35.3536 | 35.6593 | 36.7142 | 36.6885 | 36.9204 | 37.8277 | 40.4343 | 41.5099 | 40.4917 | 43.3043 | 42.1234 | 43.186 | 43.9517 | 43.6371 | 43.6371 | 43.6371 | 43.6371 | 43.6371 | 43.6371 | 43.6371 | 43.6371 | 43.6371 | 43.6371 | 43.6371 | 43.6371 | 43.6371 | 43.6371 | 43.6371 | 43.6371
70% | 378.0365 | 27.5875 | 30.4756 | 30.7819 | 31.1605 | 31.6632 | 32.1397 | 32.9726 | 35.0672 | 36.1938 | 35.3719 | 37.9165 | 38.3749 | 38.7045 | 40.2579 | 40.5107 | 40.5107 | 40.5107 | 40.5107 | 40.5107 | 40.5107 | 40.5107 | 40.5107 | 40.5107 | 40.5107 | 40.5107 | 40.5107 | 40.5107 | 40.5107 | 40.5107 | 40.5107 | 70% | 378.0365 | 30.2418 | 32.9967 | 33.282 | 34.2666 | 34.2426 | 34.4591 | 35.3059 | 37.7386 | 38.7426 | 37.7923 | 40.4173 | 39.3152 | 40.3069 | 41.0215 | 40.7279 | 40.7279 | 40.7279 | 40.7279 | 40.7279 | 40.7279 | 40.7279 | 40.7279 | 40.7279 | 40.7279 | 40.7279 | 40.7279 | 40.7279 | 40.7279 | 40.7279 | 40.7279
65% | 616.0926 | 25.617 | 28.2988 | 28.5832 | 28.9347 | 29.4015 | 29.844 | 30.6174 | 32.5624 | 33.6086 | 32.8454 | 35.2081 | 35.6338 | 35.9399 | 37.3823 | 37.6171 | 37.6171 | 37.6171 | 37.6171 | 37.6171 | 37.6171 | 37.6171 | 37.6171 | 37.6171 | 37.6171 | 37.6171 | 37.6171 | 37.6171 | 37.6171 | 37.6171 | 37.6171 | 65% | 616.0926 | 28.0817 | 30.6398 | 30.9047 | 31.819 | 31.7967 | 31.9977 | 32.784 | 35.043 | 35.9752 | 35.0928 | 37.5304 | 36.507 | 37.4278 | 38.0914 | 37.8188 | 37.8188 | 37.8188 | 37.8188 | 37.8188 | 37.8188 | 37.8188 | 37.8188 | 37.8188 | 37.8188 | 37.8188 | 37.8188 | 37.8188 | 37.8188 | 37.8188 | 37.8188
60% | 934.9866 | 23.6464 | 26.122 | 26.3845 | 26.709 | 27.1399 | 27.5483 | 28.2622 | 30.0576 | 31.0233 | 30.3188 | 32.4998 | 32.8928 | 33.1753 | 34.5067 | 34.7235 | 34.7235 | 34.7235 | 34.7235 | 34.7235 | 34.7235 | 34.7235 | 34.7235 | 34.7235 | 34.7235 | 34.7235 | 34.7235 | 34.7235 | 34.7235 | 34.7235 | 34.7235 | 60% | 934.9866 | 25.9216 | 28.2829 | 28.5274 | 29.3713 | 29.3508 | 29.5364 | 30.2622 | 32.3474 | 33.2079 | 32.3934 | 34.6434 | 33.6987 | 34.5488 | 35.1613 | 34.9097 | 34.9097 | 34.9097 | 34.9097 | 34.9097 | 34.9097 | 34.9097 | 34.9097 | 34.9097 | 34.9097 | 34.9097 | 34.9097 | 34.9097 | 34.9097 | 34.9097 | 34.9097
55% | 1310.9428 | 21.6759 | 23.9451 | 24.1858 | 24.4832 | 24.8782 | 25.2527 | 25.907 | 27.5528 | 28.438 | 27.7922 | 29.7915 | 30.1517 | 30.4106 | 31.6312 | 31.8298 | 31.8298 | 31.8298 | 31.8298 | 31.8298 | 31.8298 | 31.8298 | 31.8298 | 31.8298 | 31.8298 | 31.8298 | 31.8298 | 31.8298 | 31.8298 | 31.8298 | 31.8298 | 55% | 1310.9428 | 23.7614 | 25.926 | 26.1501 | 26.9237 | 26.9049 | 27.075 | 27.7403 | 29.6518 | 30.4406 | 29.6939 | 31.7565 | 30.8905 | 31.6697 | 32.2312 | 32.0005 | 32.0005 | 32.0005 | 32.0005 | 32.0005 | 32.0005 | 32.0005 | 32.0005 | 32.0005 | 32.0005 | 32.0005 | 32.0005 | 32.0005 | 32.0005 | 32.0005 | 32.0005
50% | 1730.2899 | 19.7054 | 21.7683 | 21.9871 | 22.2575 | 22.6166 | 22.957 | 23.5518 | 25.048 | 25.8527 | 25.2657 | 27.0832 | 27.4106 | 27.646 | 28.7556 | 28.9362 | 28.9362 | 28.9362 | 28.9362 | 28.9362 | 28.9362 | 28.9362 | 28.9362 | 28.9362 | 28.9362 | 28.9362 | 28.9362 | 28.9362 | 28.9362 | 28.9362 | 28.9362 | 50% | 1730.2899 | 21.6013 | 23.5691 | 23.7729 | 24.4761 | 24.459 | 24.6136 | 25.2185 | 26.9562 | 27.6733 | 26.9945 | 28.8695 | 28.0823 | 28.7906 | 29.3011 | 29.0914 | 29.0914 | 29.0914 | 29.0914 | 29.0914 | 29.0914 | 29.0914 | 29.0914 | 29.0914 | 29.0914 | 29.0914 | 29.0914 | 29.0914 | 29.0914 | 29.0914 | 29.0914
45% | 2168.0633 | 17.7348 | 19.5915 | 19.7883 | 20.0317 | 20.3549 | 20.6613 | 21.1967 | 22.5432 | 23.2675 | 22.7391 | 24.3749 | 24.6696 | 24.8814 | 25.8801 | 26.0426 | 26.0426 | 26.0426 | 26.0426 | 26.0426 | 26.0426 | 26.0426 | 26.0426 | 26.0426 | 26.0426 | 26.0426 | 26.0426 | 26.0426 | 26.0426 | 26.0426 | 26.0426 | 45% | 2168.0633 | 19.4412 | 21.2122 | 21.3956 | 22.0285 | 22.0131 | 22.1523 | 22.6966 | 24.2606 | 24.9059 | 24.295 | 25.9826 | 25.2741 | 25.9116 | 26.371 | 26.1822 | 26.1822 | 26.1822 | 26.1822 | 26.1822 | 26.1822 | 26.1822 | 26.1822 | 26.1822 | 26.1822 | 26.1822 | 26.1822 | 26.1822 | 26.1822 | 26.1822 | 26.1822
40% | 2609.7004 | 15.7643 | 17.4146 | 17.5896 | 17.806 | 18.0932 | 18.3656 | 18.8415 | 20.0384 | 20.6822 | 20.2125 | 21.6665 | 21.9285 | 22.1168 | 23.0045 | 23.149 | 23.149 | 23.149 | 23.149 | 23.149 | 23.149 | 23.149 | 23.149 | 23.149 | 23.149 | 23.149 | 23.149 | 23.149 | 23.149 | 23.149 | 23.149 | 40% | 2609.7004 | 17.2811 | 18.8553 | 19.0183 | 19.5809 | 19.5672 | 19.6909 | 20.1748 | 21.5649 | 22.1386 | 21.5956 | 23.0956 | 22.4658 | 23.0325 | 23.4409 | 23.2731 | 23.2731 | 23.2731 | 23.2731 | 23.2731 | 23.2731 | 23.2731 | 23.2731 | 23.2731 | 23.2731 | 23.2731 | 23.2731 | 23.2731 | 23.2731 | 23.2731 | 23.2731
35% | 2998.1389 | 13.7937 | 15.2378 | 15.3909 | 15.5802 | 15.8316 | 16.0699 | 16.4863 | 17.5336 | 18.0969 | 17.686 | 18.9582 | 19.1875 | 19.3522 | 20.1289 | 20.2554 | 20.2554 | 20.2554 | 20.2554 | 20.2554 | 20.2554 | 20.2554 | 20.2554 | 20.2554 | 20.2554 | 20.2554 | 20.2554 | 20.2554 | 20.2554 | 20.2554 | 20.2554 | 35% | 2998.1389 | 15.1209 | 16.4984 | 16.641 | 17.1333 | 17.1213 | 17.2295 | 17.6529 | 18.8693 | 19.3713 | 18.8961 | 20.2087 | 19.6576 | 20.1535 | 20.5108 | 20.364 | 20.364 | 20.364 | 20.364 | 20.364 | 20.364 | 20.364 | 20.364 | 20.364 | 20.364 | 20.364 | 20.364 | 20.364 | 20.364 | 20.364 | 20.364
30% | 3309.3057 | 11.8232 | 13.061 | 13.1922 | 13.3545 | 13.5699 | 13.7742 | 14.1311 | 15.0288 | 15.5116 | 15.1594 | 16.2499 | 16.4464 | 16.5876 | 17.2534 | 17.3617 | 17.3617 | 17.3617 | 17.3617 | 17.3617 | 17.3617 | 17.3617 | 17.3617 | 17.3617 | 17.3617 | 17.3617 | 17.3617 | 17.3617 | 17.3617 | 17.3617 | 17.3617 | 30% | 3309.3057 | 12.9608 | 14.1414 | 14.2637 | 14.6857 | 14.6754 | 14.7682 | 15.1311 | 16.1737 | 16.604 | 16.1967 | 17.3217 | 16.8494 | 17.2744 | 17.5807 | 17.4548 | 17.4548 | 17.4548 | 17.4548 | 17.4548 | 17.4548 | 17.4548 | 17.4548 | 17.4548 | 17.4548 | 17.4548 | 17.4548 | 17.4548 | 17.4548 | 17.4548 | 17.4548
25% | 3537.8514 | 9.8527 | 10.8842 | 10.9935 | 11.1287 | 11.3083 | 11.4785 | 11.7759 | 12.524 | 12.9264 | 12.6328 | 13.5416 | 13.7053 | 13.823 | 14.3778 | 14.4681 | 14.4681 | 14.4681 | 14.4681 | 14.4681 | 14.4681 | 14.4681 | 14.4681 | 14.4681 | 14.4681 | 14.4681 | 14.4681 | 14.4681 | 14.4681 | 14.4681 | 14.4681 | 25% | 3537.8514 | 10.8007 | 11.7845 | 11.8864 | 12.2381 | 12.2295 | 12.3068 | 12.6092 | 13.4781 | 13.8366 | 13.4972 | 14.4348 | 14.0411 | 14.3953 | 14.6506 | 14.5457 | 14.5457 | 14.5457 | 14.5457 | 14.5457 | 14.5457 | 14.5457 | 14.5457 | 14.5457 | 14.5457 | 14.5457 | 14.5457 | 14.5457 | 14.5457 | 14.5457 | 14.5457
20% | 3731.0305 | 7.8821 | 8.7073 | 8.7948 | 8.903 | 9.0466 | 9.1828 | 9.4207 | 10.0192 | 10.3411 | 10.1063 | 10.8333 | 10.9643 | 11.0584 | 11.5022 | 11.5745 | 11.5745 | 11.5745 | 11.5745 | 11.5745 | 11.5745 | 11.5745 | 11.5745 | 11.5745 | 11.5745 | 11.5745 | 11.5745 | 11.5745 | 11.5745 | 11.5745 | 11.5745 | 20% | 3731.0305 | 8.6405 | 9.4276 | 9.5091 | 9.7904 | 9.7836 | 9.8455 | 10.0874 | 10.7825 | 11.0693 | 10.7978 | 11.5478 | 11.2329 | 11.5163 | 11.7204 | 11.6366 | 11.6366 | 11.6366 | 11.6366 | 11.6366 | 11.6366 | 11.6366 | 11.6366 | 11.6366 | 11.6366 | 11.6366 | 11.6366 | 11.6366 | 11.6366 | 11.6366 | 11.6366
15% | 3910.2412 | 5.9116 | 6.5305 | 6.5961 | 6.6772 | 6.785 | 6.8871 | 7.0656 | 7.5144 | 7.7558 | 7.5797 | 8.125 | 8.2232 | 8.2938 | 8.6267 | 8.6809 | 8.6809 | 8.6809 | 8.6809 | 8.6809 | 8.6809 | 8.6809 | 8.6809 | 8.6809 | 8.6809 | 8.6809 | 8.6809 | 8.6809 | 8.6809 | 8.6809 | 8.6809 | 15% | 3910.2412 | 6.4804 | 7.0707 | 7.1319 | 7.3428 | 7.3377 | 7.3841 | 7.5655 | 8.0869 | 8.302 | 8.0983 | 8.6609 | 8.4247 | 8.6372 | 8.7903 | 8.7274 | 8.7274 | 8.7274 | 8.7274 | 8.7274 | 8.7274 | 8.7274 | 8.7274 | 8.7274 | 8.7274 | 8.7274 | 8.7274 | 8.7274 | 8.7274 | 8.7274 | 8.7274
10% | 4075.1864 | 3.9411 | 4.3537 | 4.3974 | 4.4515 | 4.5233 | 4.5914 | 4.7104 | 5.0096 | 5.1705 | 5.0531 | 5.4166 | 5.4821 | 5.5292 | 5.7511 | 5.7872 | 5.7872 | 5.7872 | 5.7872 | 5.7872 | 5.7872 | 5.7872 | 5.7872 | 5.7872 | 5.7872 | 5.7872 | 5.7872 | 5.7872 | 5.7872 | 5.7872 | 5.7872 | 10% | 4075.1864 | 4.3203 | 4.7138 | 4.7546 | 4.8952 | 4.8918 | 4.9227 | 5.0437 | 5.3912 | 5.5347 | 5.3989 | 5.7739 | 5.6165 | 5.7581 | 5.8602 | 5.8183 | 5.8183 | 5.8183 | 5.8183 | 5.8183 | 5.8183 | 5.8183 | 5.8183 | 5.8183 | 5.8183 | 5.8183 | 5.8183 | 5.8183 | 5.8183 | 5.8183 | 5.8183
5% | 4251.7223 | 1.9705 | 2.1768 | 2.1987 | 2.2257 | 2.2617 | 2.2957 | 2.3552 | 2.5048 | 2.5853 | 2.5266 | 2.7083 | 2.7411 | 2.7646 | 2.8756 | 2.8936 | 2.8936 | 2.8936 | 2.8936 | 2.8936 | 2.8936 | 2.8936 | 2.8936 | 2.8936 | 2.8936 | 2.8936 | 2.8936 | 2.8936 | 2.8936 | 2.8936 | 2.8936 | 5% | 4251.7223 | 2.1601 | 2.3569 | 2.3773 | 2.4476 | 2.4459 | 2.4614 | 2.5218 | 2.6956 | 2.7673 | 2.6994 | 2.887 | 2.8082 | 2.8791 | 2.9301 | 2.9091 | 2.9091 | 2.9091 | 2.9091 | 2.9091 | 2.9091 | 2.9091 | 2.9091 | 2.9091 | 2.9091 | 2.9091 | 2.9091 | 2.9091 | 2.9091 | 2.9091 | 2.9091
9.992e-14% | 4391.7028 | 3.9379e-14 | 4.3502e-14 | 4.3939e-14 | 4.4479e-14 | 4.5197e-14 | 4.5877e-14 | 4.7066e-14 | 5.0056e-14 | 5.1664e-14 | 5.0491e-14 | 5.4123e-14 | 5.4777e-14 | 5.5248e-14 | 5.7465e-14 | 5.7826e-14 | 5.7826e-14 | 5.7826e-14 | 5.7826e-14 | 5.7826e-14 | 5.7826e-14 | 5.7826e-14 | 5.7826e-14 | 5.7826e-14 | 5.7826e-14 | 5.7826e-14 | 5.7826e-14 | 5.7826e-14 | 5.7826e-14 | 5.7826e-14 | 5.7826e-14 | 9.992e-14% | 4391.7028 | 4.3168e-14 | 4.71e-14 | 4.7508e-14 | 4.8913e-14 | 4.8879e-14 | 4.9188e-14 | 5.0397e-14 | 5.3869e-14 | 5.5302e-14 | 5.3946e-14 | 5.7693e-14 | 5.612e-14 | 5.7535e-14 | 5.8555e-14 | 5.8136e-14 | 5.8136e-14 | 5.8136e-14 | 5.8136e-14 | 5.8136e-14 | 5.8136e-14 | 5.8136e-14 | 5.8136e-14 | 5.8136e-14 | 5.8136e-14 | 5.8136e-14 | 5.8136e-14 | 5.8136e-14 | 5.8136e-14 | 5.8136e-14 | 5.8136e-14
Summer Season | [31 empty] | Summer Season
P50 | [31 empty] | P10
% of MD | Summer - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Summer - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 41.4021 | 44.4975 | 44.8085 | 44.6561 | 44.801 | 44.8606 | 45.0515 | 45.4441 | 45.7743 | 45.9263 | 45.7908 | 46.3589 | 46.449 | 46.3423 | 46.5561 | 46.6661 | 46.6661 | 46.6661 | 46.6661 | 46.6661 | 46.6661 | 46.6661 | 46.6661 | 46.6661 | 46.6661 | 46.6661 | 46.6661 | 46.6661 | 46.6661 | 46.6661 | 100% | 0 | 50.9365 | 54.3957 | 54.4912 | 54.3883 | 54.4147 | 54.6036 | 54.9865 | 55.6607 | 56.012 | 56.2661 | 56.6508 | 57.1419 | 57.7357 | 58.0469 | 57.946 | 58.056 | 58.056 | 58.056 | 58.056 | 58.056 | 58.056 | 58.056 | 58.056 | 58.056 | 58.056 | 58.056 | 58.056 | 58.056 | 58.056 | 58.056
99% | 0.37816 | 40.9881 | 44.0525 | 44.3604 | 44.2095 | 44.353 | 44.412 | 44.601 | 44.9896 | 45.3165 | 45.467 | 45.3329 | 45.8953 | 45.9845 | 45.8789 | 46.0906 | 46.1995 | 46.1995 | 46.1995 | 46.1995 | 46.1995 | 46.1995 | 46.1995 | 46.1995 | 46.1995 | 46.1995 | 46.1995 | 46.1995 | 46.1995 | 46.1995 | 46.1995 | 99% | 0 | 50.4271 | 53.8518 | 53.9463 | 53.8444 | 53.8706 | 54.0576 | 54.4366 | 55.1041 | 55.4519 | 55.7035 | 56.0843 | 56.5704 | 57.1583 | 57.4664 | 57.3665 | 57.4754 | 57.4754 | 57.4754 | 57.4754 | 57.4754 | 57.4754 | 57.4754 | 57.4754 | 57.4754 | 57.4754 | 57.4754 | 57.4754 | 57.4754 | 57.4754 | 57.4754
98% | 0.37816 | 40.5741 | 43.6075 | 43.9123 | 43.7629 | 43.905 | 43.9634 | 44.1505 | 44.5352 | 44.8588 | 45.0078 | 44.875 | 45.4317 | 45.52 | 45.4155 | 45.625 | 45.7328 | 45.7328 | 45.7328 | 45.7328 | 45.7328 | 45.7328 | 45.7328 | 45.7328 | 45.7328 | 45.7328 | 45.7328 | 45.7328 | 45.7328 | 45.7328 | 45.7328 | 98% | 0 | 49.9177 | 53.3078 | 53.4014 | 53.3005 | 53.3264 | 53.5116 | 53.8867 | 54.5475 | 54.8917 | 55.1408 | 55.5178 | 55.999 | 56.581 | 56.886 | 56.7871 | 56.8949 | 56.8949 | 56.8949 | 56.8949 | 56.8949 | 56.8949 | 56.8949 | 56.8949 | 56.8949 | 56.8949 | 56.8949 | 56.8949 | 56.8949 | 56.8949 | 56.8949
97% | 0.37816 | 40.1601 | 43.1625 | 43.4643 | 43.3164 | 43.457 | 43.5148 | 43.7 | 44.0807 | 44.4011 | 44.5485 | 44.4171 | 44.9681 | 45.0555 | 44.9521 | 45.1595 | 45.2662 | 45.2662 | 45.2662 | 45.2662 | 45.2662 | 45.2662 | 45.2662 | 45.2662 | 45.2662 | 45.2662 | 45.2662 | 45.2662 | 45.2662 | 45.2662 | 45.2662 | 97% | 0.37816 | 49.4084 | 52.7639 | 52.8564 | 52.7566 | 52.7823 | 52.9655 | 53.3369 | 53.9908 | 54.3316 | 54.5781 | 54.9513 | 55.4276 | 56.0036 | 56.3055 | 56.2076 | 56.3143 | 56.3143 | 56.3143 | 56.3143 | 56.3143 | 56.3143 | 56.3143 | 56.3143 | 56.3143 | 56.3143 | 56.3143 | 56.3143 | 56.3143 | 56.3143 | 56.3143
95% | 0.75633 | 39.332 | 42.2726 | 42.5681 | 42.4232 | 42.561 | 42.6176 | 42.7989 | 43.1719 | 43.4856 | 43.63 | 43.5013 | 44.0409 | 44.1265 | 44.0252 | 44.2283 | 44.3328 | 44.3328 | 44.3328 | 44.3328 | 44.3328 | 44.3328 | 44.3328 | 44.3328 | 44.3328 | 44.3328 | 44.3328 | 44.3328 | 44.3328 | 44.3328 | 44.3328 | 95% | 0.37816 | 48.3896 | 51.6759 | 51.7666 | 51.6689 | 51.694 | 51.8735 | 52.2371 | 52.8776 | 53.2114 | 53.4528 | 53.8182 | 54.2848 | 54.8489 | 55.1446 | 55.0487 | 55.1532 | 55.1532 | 55.1532 | 55.1532 | 55.1532 | 55.1532 | 55.1532 | 55.1532 | 55.1532 | 55.1532 | 55.1532 | 55.1532 | 55.1532 | 55.1532 | 55.1532
90% | 9.0759 | 37.2619 | 40.0477 | 40.3277 | 40.1904 | 40.3209 | 40.3745 | 40.5464 | 40.8996 | 41.1969 | 41.3337 | 41.2117 | 41.723 | 41.8041 | 41.7081 | 41.9005 | 41.9995 | 41.9995 | 41.9995 | 41.9995 | 41.9995 | 41.9995 | 41.9995 | 41.9995 | 41.9995 | 41.9995 | 41.9995 | 41.9995 | 41.9995 | 41.9995 | 41.9995 | 90% | 0.75633 | 45.8428 | 48.9562 | 49.0421 | 48.9494 | 48.9733 | 49.1433 | 49.4878 | 50.0946 | 50.4108 | 50.6395 | 50.9857 | 51.4277 | 51.9621 | 52.2422 | 52.1514 | 52.2504 | 52.2504 | 52.2504 | 52.2504 | 52.2504 | 52.2504 | 52.2504 | 52.2504 | 52.2504 | 52.2504 | 52.2504 | 52.2504 | 52.2504 | 52.2504 | 52.2504
85% | 40.4636 | 35.1918 | 37.8228 | 38.0872 | 37.9576 | 38.0809 | 38.1315 | 38.2938 | 38.6274 | 38.9081 | 39.0374 | 38.9222 | 39.405 | 39.4816 | 39.391 | 39.5727 | 39.6662 | 39.6662 | 39.6662 | 39.6662 | 39.6662 | 39.6662 | 39.6662 | 39.6662 | 39.6662 | 39.6662 | 39.6662 | 39.6662 | 39.6662 | 39.6662 | 39.6662 | 85% | 1.1345 | 43.296 | 46.2364 | 46.3175 | 46.23 | 46.2525 | 46.4131 | 46.7385 | 47.3116 | 47.6102 | 47.8262 | 48.1532 | 48.5706 | 49.0753 | 49.3399 | 49.2541 | 49.3476 | 49.3476 | 49.3476 | 49.3476 | 49.3476 | 49.3476 | 49.3476 | 49.3476 | 49.3476 | 49.3476 | 49.3476 | 49.3476 | 49.3476 | 49.3476 | 49.3476
80% | 94.5411 | 33.1217 | 35.598 | 35.8468 | 35.7248 | 35.8408 | 35.8885 | 36.0412 | 36.3552 | 36.6194 | 36.741 | 36.6326 | 37.0871 | 37.1592 | 37.0739 | 37.2449 | 37.3329 | 37.3329 | 37.3329 | 37.3329 | 37.3329 | 37.3329 | 37.3329 | 37.3329 | 37.3329 | 37.3329 | 37.3329 | 37.3329 | 37.3329 | 37.3329 | 37.3329 | 80% | 2.6471 | 40.7492 | 43.5166 | 43.5929 | 43.5106 | 43.5318 | 43.6829 | 43.9892 | 44.5285 | 44.8096 | 45.0129 | 45.3206 | 45.7135 | 46.1886 | 46.4375 | 46.3568 | 46.4448 | 46.4448 | 46.4448 | 46.4448 | 46.4448 | 46.4448 | 46.4448 | 46.4448 | 46.4448 | 46.4448 | 46.4448 | 46.4448 | 46.4448 | 46.4448 | 46.4448
75% | 197.0236 | 31.0516 | 33.3731 | 33.6064 | 33.492 | 33.6008 | 33.6454 | 33.7886 | 34.083 | 34.3307 | 34.4447 | 34.3431 | 34.7692 | 34.8367 | 34.7568 | 34.9171 | 34.9996 | 34.9996 | 34.9996 | 34.9996 | 34.9996 | 34.9996 | 34.9996 | 34.9996 | 34.9996 | 34.9996 | 34.9996 | 34.9996 | 34.9996 | 34.9996 | 34.9996 | 75% | 3.4035 | 38.2023 | 40.7968 | 40.8684 | 40.7912 | 40.811 | 40.9527 | 41.2398 | 41.7455 | 42.009 | 42.1996 | 42.4881 | 42.8564 | 43.3018 | 43.5352 | 43.4595 | 43.542 | 43.542 | 43.542 | 43.542 | 43.542 | 43.542 | 43.542 | 43.542 | 43.542 | 43.542 | 43.542 | 43.542 | 43.542 | 43.542 | 43.542
70% | 336.9444 | 28.9815 | 31.1482 | 31.366 | 31.2592 | 31.3607 | 31.4024 | 31.5361 | 31.8108 | 32.042 | 32.1484 | 32.0536 | 32.4512 | 32.5143 | 32.4396 | 32.5893 | 32.6663 | 32.6663 | 32.6663 | 32.6663 | 32.6663 | 32.6663 | 32.6663 | 32.6663 | 32.6663 | 32.6663 | 32.6663 | 32.6663 | 32.6663 | 32.6663 | 32.6663 | 70% | 5.6725 | 35.6555 | 38.077 | 38.1438 | 38.0718 | 38.0903 | 38.2225 | 38.4905 | 38.9625 | 39.2084 | 39.3863 | 39.6555 | 39.9993 | 40.415 | 40.6328 | 40.5622 | 40.6392 | 40.6392 | 40.6392 | 40.6392 | 40.6392 | 40.6392 | 40.6392 | 40.6392 | 40.6392 | 40.6392 | 40.6392 | 40.6392 | 40.6392 | 40.6392 | 40.6392
65% | 521.4885 | 26.9114 | 28.9234 | 29.1255 | 29.0264 | 29.1207 | 29.1594 | 29.2835 | 29.5386 | 29.7533 | 29.8521 | 29.764 | 30.1333 | 30.1918 | 30.1225 | 30.2615 | 30.333 | 30.333 | 30.333 | 30.333 | 30.333 | 30.333 | 30.333 | 30.333 | 30.333 | 30.333 | 30.333 | 30.333 | 30.333 | 30.333 | 30.333 | 65% | 6.4288 | 33.1087 | 35.3572 | 35.4193 | 35.3524 | 35.3696 | 35.4924 | 35.7412 | 36.1794 | 36.4078 | 36.573 | 36.823 | 37.1422 | 37.5282 | 37.7305 | 37.6649 | 37.7364 | 37.7364 | 37.7364 | 37.7364 | 37.7364 | 37.7364 | 37.7364 | 37.7364 | 37.7364 | 37.7364 | 37.7364 | 37.7364 | 37.7364 | 37.7364 | 37.7364
60% | 812.675 | 24.8413 | 26.6985 | 26.8851 | 26.7936 | 26.8806 | 26.9164 | 27.0309 | 27.2664 | 27.4646 | 27.5558 | 27.4745 | 27.8153 | 27.8694 | 27.8054 | 27.9337 | 27.9997 | 27.9997 | 27.9997 | 27.9997 | 27.9997 | 27.9997 | 27.9997 | 27.9997 | 27.9997 | 27.9997 | 27.9997 | 27.9997 | 27.9997 | 27.9997 | 27.9997 | 60% | 11.3449 | 30.5619 | 32.6374 | 32.6947 | 32.633 | 32.6488 | 32.7622 | 32.9919 | 33.3964 | 33.6072 | 33.7597 | 33.9905 | 34.2851 | 34.6414 | 34.8281 | 34.7676 | 34.8336 | 34.8336 | 34.8336 | 34.8336 | 34.8336 | 34.8336 | 34.8336 | 34.8336 | 34.8336 | 34.8336 | 34.8336 | 34.8336 | 34.8336 | 34.8336 | 34.8336
55% | 1202.1843 | 22.7712 | 24.4736 | 24.6447 | 24.5608 | 24.6406 | 24.6733 | 24.7783 | 24.9942 | 25.1759 | 25.2595 | 25.1849 | 25.4974 | 25.5469 | 25.4883 | 25.6059 | 25.6664 | 25.6664 | 25.6664 | 25.6664 | 25.6664 | 25.6664 | 25.6664 | 25.6664 | 25.6664 | 25.6664 | 25.6664 | 25.6664 | 25.6664 | 25.6664 | 25.6664 | 55% | 35.5474 | 28.0151 | 29.9176 | 29.9701 | 29.9135 | 29.9281 | 30.032 | 30.2426 | 30.6134 | 30.8066 | 30.9464 | 31.1579 | 31.428 | 31.7546 | 31.9258 | 31.8703 | 31.9308 | 31.9308 | 31.9308 | 31.9308 | 31.9308 | 31.9308 | 31.9308 | 31.9308 | 31.9308 | 31.9308 | 31.9308 | 31.9308 | 31.9308 | 31.9308 | 31.9308
50% | 1686.2345 | 20.7011 | 22.2487 | 22.4043 | 22.328 | 22.4005 | 22.4303 | 22.5258 | 22.722 | 22.8871 | 22.9631 | 22.8954 | 23.1794 | 23.2245 | 23.1712 | 23.2781 | 23.3331 | 23.3331 | 23.3331 | 23.3331 | 23.3331 | 23.3331 | 23.3331 | 23.3331 | 23.3331 | 23.3331 | 23.3331 | 23.3331 | 23.3331 | 23.3331 | 23.3331 | 50% | 95.2974 | 25.4682 | 27.1979 | 27.2456 | 27.1941 | 27.2074 | 27.3018 | 27.4932 | 27.8303 | 28.006 | 28.1331 | 28.3254 | 28.5709 | 28.8678 | 29.0234 | 28.973 | 29.028 | 29.028 | 29.028 | 29.028 | 29.028 | 29.028 | 29.028 | 29.028 | 29.028 | 29.028 | 29.028 | 29.028 | 29.028 | 29.028 | 29.028
45% | 2129.0649 | 18.631 | 20.0239 | 20.1638 | 20.0952 | 20.1605 | 20.1873 | 20.2732 | 20.4498 | 20.5984 | 20.6668 | 20.6059 | 20.8615 | 20.902 | 20.8541 | 20.9503 | 20.9998 | 20.9998 | 20.9998 | 20.9998 | 20.9998 | 20.9998 | 20.9998 | 20.9998 | 20.9998 | 20.9998 | 20.9998 | 20.9998 | 20.9998 | 20.9998 | 20.9998 | 45% | 208.7467 | 22.9214 | 24.4781 | 24.521 | 24.4747 | 24.4866 | 24.5716 | 24.7439 | 25.0473 | 25.2054 | 25.3198 | 25.4928 | 25.7138 | 25.9811 | 26.1211 | 26.0757 | 26.1252 | 26.1252 | 26.1252 | 26.1252 | 26.1252 | 26.1252 | 26.1252 | 26.1252 | 26.1252 | 26.1252 | 26.1252 | 26.1252 | 26.1252 | 26.1252 | 26.1252
40% | 2484.5393 | 16.5608 | 17.799 | 17.9234 | 17.8624 | 17.9204 | 17.9442 | 18.0206 | 18.1776 | 18.3097 | 18.3705 | 18.3163 | 18.5435 | 18.5796 | 18.5369 | 18.6225 | 18.6665 | 18.6665 | 18.6665 | 18.6665 | 18.6665 | 18.6665 | 18.6665 | 18.6665 | 18.6665 | 18.6665 | 18.6665 | 18.6665 | 18.6665 | 18.6665 | 18.6665 | 40% | 380.4333 | 20.3746 | 21.7583 | 21.7965 | 21.7553 | 21.7659 | 21.8415 | 21.9946 | 22.2643 | 22.4048 | 22.5065 | 22.6603 | 22.8567 | 23.0943 | 23.2188 | 23.1784 | 23.2224 | 23.2224 | 23.2224 | 23.2224 | 23.2224 | 23.2224 | 23.2224 | 23.2224 | 23.2224 | 23.2224 | 23.2224 | 23.2224 | 23.2224 | 23.2224 | 23.2224
35% | 2808.248 | 14.4907 | 15.5741 | 15.683 | 15.6296 | 15.6804 | 15.7012 | 15.768 | 15.9054 | 16.021 | 16.0742 | 16.0268 | 16.2256 | 16.2571 | 16.2198 | 16.2947 | 16.3332 | 16.3332 | 16.3332 | 16.3332 | 16.3332 | 16.3332 | 16.3332 | 16.3332 | 16.3332 | 16.3332 | 16.3332 | 16.3332 | 16.3332 | 16.3332 | 16.3332 | 35% | 696.5786 | 17.8278 | 19.0385 | 19.0719 | 19.0359 | 19.0452 | 19.1113 | 19.2453 | 19.4812 | 19.6042 | 19.6931 | 19.8278 | 19.9997 | 20.2075 | 20.3164 | 20.2811 | 20.3196 | 20.3196 | 20.3196 | 20.3196 | 20.3196 | 20.3196 | 20.3196 | 20.3196 | 20.3196 | 20.3196 | 20.3196 | 20.3196 | 20.3196 | 20.3196 | 20.3196
30% | 3095.6528 | 12.4206 | 13.3492 | 13.4426 | 13.3968 | 13.4403 | 13.4582 | 13.5155 | 13.6332 | 13.7323 | 13.7779 | 13.7372 | 13.9077 | 13.9347 | 13.9027 | 13.9668 | 13.9998 | 13.9998 | 13.9998 | 13.9998 | 13.9998 | 13.9998 | 13.9998 | 13.9998 | 13.9998 | 13.9998 | 13.9998 | 13.9998 | 13.9998 | 13.9998 | 13.9998 | 30% | 1260.7997 | 15.2809 | 16.3187 | 16.3474 | 16.3165 | 16.3244 | 16.3811 | 16.4959 | 16.6982 | 16.8036 | 16.8798 | 16.9952 | 17.1426 | 17.3207 | 17.4141 | 17.3838 | 17.4168 | 17.4168 | 17.4168 | 17.4168 | 17.4168 | 17.4168 | 17.4168 | 17.4168 | 17.4168 | 17.4168 | 17.4168 | 17.4168 | 17.4168 | 17.4168 | 17.4168
25% | 3358.8552 | 10.3505 | 11.1244 | 11.2021 | 11.164 | 11.2003 | 11.2151 | 11.2629 | 11.361 | 11.4436 | 11.4816 | 11.4477 | 11.5897 | 11.6122 | 11.5856 | 11.639 | 11.6665 | 11.6665 | 11.6665 | 11.6665 | 11.6665 | 11.6665 | 11.6665 | 11.6665 | 11.6665 | 11.6665 | 11.6665 | 11.6665 | 11.6665 | 11.6665 | 11.6665 | 25% | 1965.3198 | 12.7341 | 13.5989 | 13.6228 | 13.5971 | 13.6037 | 13.6509 | 13.7466 | 13.9152 | 14.003 | 14.0665 | 14.1627 | 14.2855 | 14.4339 | 14.5117 | 14.4865 | 14.514 | 14.514 | 14.514 | 14.514 | 14.514 | 14.514 | 14.514 | 14.514 | 14.514 | 14.514 | 14.514 | 14.514 | 14.514 | 14.514 | 14.514
20% | 3588.7791 | 8.2804 | 8.8995 | 8.9617 | 8.9312 | 8.9602 | 8.9721 | 9.0103 | 9.0888 | 9.1549 | 9.1853 | 9.1582 | 9.2718 | 9.2898 | 9.2685 | 9.3112 | 9.3332 | 9.3332 | 9.3332 | 9.3332 | 9.3332 | 9.3332 | 9.3332 | 9.3332 | 9.3332 | 9.3332 | 9.3332 | 9.3332 | 9.3332 | 9.3332 | 9.3332 | 20% | 2490.2118 | 10.1873 | 10.8791 | 10.8982 | 10.8777 | 10.8829 | 10.9207 | 10.9973 | 11.1321 | 11.2024 | 11.2532 | 11.3302 | 11.4284 | 11.5471 | 11.6094 | 11.5892 | 11.6112 | 11.6112 | 11.6112 | 11.6112 | 11.6112 | 11.6112 | 11.6112 | 11.6112 | 11.6112 | 11.6112 | 11.6112 | 11.6112 | 11.6112 | 11.6112 | 11.6112
15% | 3802.4419 | 6.2103 | 6.6746 | 6.7213 | 6.6984 | 6.7202 | 6.7291 | 6.7577 | 6.8166 | 6.8661 | 6.8889 | 6.8686 | 6.9538 | 6.9673 | 6.9514 | 6.9834 | 6.9999 | 6.9999 | 6.9999 | 6.9999 | 6.9999 | 6.9999 | 6.9999 | 6.9999 | 6.9999 | 6.9999 | 6.9999 | 6.9999 | 6.9999 | 6.9999 | 6.9999 | 15% | 2997.7083 | 7.6405 | 8.1594 | 8.1737 | 8.1582 | 8.1622 | 8.1905 | 8.248 | 8.3491 | 8.4018 | 8.4399 | 8.4976 | 8.5713 | 8.6604 | 8.707 | 8.6919 | 8.7084 | 8.7084 | 8.7084 | 8.7084 | 8.7084 | 8.7084 | 8.7084 | 8.7084 | 8.7084 | 8.7084 | 8.7084 | 8.7084 | 8.7084 | 8.7084 | 8.7084
10% | 4024.8025 | 4.1402 | 4.4497 | 4.4809 | 4.4656 | 4.4801 | 4.4861 | 4.5052 | 4.5444 | 4.5774 | 4.5926 | 4.5791 | 4.6359 | 4.6449 | 4.6342 | 4.6556 | 4.6666 | 4.6666 | 4.6666 | 4.6666 | 4.6666 | 4.6666 | 4.6666 | 4.6666 | 4.6666 | 4.6666 | 4.6666 | 4.6666 | 4.6666 | 4.6666 | 4.6666 | 10% | 3491.5908 | 5.0936 | 5.4396 | 5.4491 | 5.4388 | 5.4415 | 5.4604 | 5.4986 | 5.5661 | 5.6012 | 5.6266 | 5.6651 | 5.7142 | 5.7736 | 5.8047 | 5.7946 | 5.8056 | 5.8056 | 5.8056 | 5.8056 | 5.8056 | 5.8056 | 5.8056 | 5.8056 | 5.8056 | 5.8056 | 5.8056 | 5.8056 | 5.8056 | 5.8056 | 5.8056
5% | 4239.978 | 2.0701 | 2.2249 | 2.2404 | 2.2328 | 2.2401 | 2.243 | 2.2526 | 2.2722 | 2.2887 | 2.2963 | 2.2895 | 2.3179 | 2.3224 | 2.3171 | 2.3278 | 2.3333 | 2.3333 | 2.3333 | 2.3333 | 2.3333 | 2.3333 | 2.3333 | 2.3333 | 2.3333 | 2.3333 | 2.3333 | 2.3333 | 2.3333 | 2.3333 | 2.3333 | 5% | 3955.9766 | 2.5468 | 2.7198 | 2.7246 | 2.7194 | 2.7207 | 2.7302 | 2.7493 | 2.783 | 2.8006 | 2.8133 | 2.8325 | 2.8571 | 2.8868 | 2.9023 | 2.8973 | 2.9028 | 2.9028 | 2.9028 | 2.9028 | 2.9028 | 2.9028 | 2.9028 | 2.9028 | 2.9028 | 2.9028 | 2.9028 | 2.9028 | 2.9028 | 2.9028 | 2.9028
9.992e-14% | 4391.6218 | 4.1369e-14 | 4.4462e-14 | 4.4773e-14 | 4.462e-14 | 4.4765e-14 | 4.4825e-14 | 4.5015e-14 | 4.5408e-14 | 4.5738e-14 | 4.589e-14 | 4.5754e-14 | 4.6322e-14 | 4.6412e-14 | 4.6305e-14 | 4.6519e-14 | 4.6629e-14 | 4.6629e-14 | 4.6629e-14 | 4.6629e-14 | 4.6629e-14 | 4.6629e-14 | 4.6629e-14 | 4.6629e-14 | 4.6629e-14 | 4.6629e-14 | 4.6629e-14 | 4.6629e-14 | 4.6629e-14 | 4.6629e-14 | 4.6629e-14 | 9.992e-14% | 4391.6218 | 5.0896e-14 | 5.4352e-14 | 5.4448e-14 | 5.4345e-14 | 5.4371e-14 | 5.456e-14 | 5.4943e-14 | 5.5616e-14 | 5.5967e-14 | 5.6221e-14 | 5.6605e-14 | 5.7096e-14 | 5.769e-14 | 5.8001e-14 | 5.79e-14 | 5.801e-14 | 5.801e-14 | 5.801e-14 | 5.801e-14 | 5.801e-14 | 5.801e-14 | 5.801e-14 | 5.801e-14 | 5.801e-14 | 5.801e-14 | 5.801e-14 | 5.801e-14 | 5.801e-14 | 5.801e-14 | 5.801e-14
Option 3
Winter Season | [31 empty] | Winter Season
P50 | [31 empty] | P10
% of MD | Winter - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Winter - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 39.4107 | 43.5366 | 43.9741 | 44.515 | 45.2331 | 45.9139 | 47.1037 | 50.096 | 51.7055 | 50.5313 | 54.1664 | 54.8213 | 55.2921 | 57.5112 | 57.8724 | 57.8724 | 57.8724 | 57.8724 | 57.8724 | 57.8724 | 57.8724 | 57.8724 | 57.8724 | 57.8724 | 57.8724 | 57.8724 | 57.8724 | 57.8724 | 57.8724 | 57.8724 | 100% | 0 | 43.2026 | 47.1382 | 47.5457 | 48.9522 | 48.918 | 49.2273 | 50.4369 | 53.9124 | 55.3465 | 53.989 | 57.7391 | 56.1646 | 57.5813 | 58.6022 | 58.1828 | 58.1828 | 58.1828 | 58.1828 | 58.1828 | 58.1828 | 58.1828 | 58.1828 | 58.1828 | 58.1828 | 58.1828 | 58.1828 | 58.1828 | 58.1828 | 58.1828 | 58.1828
99% | 0.2972 | 39.0166 | 43.1012 | 43.5344 | 44.0698 | 44.7808 | 45.4548 | 46.6326 | 49.595 | 51.1884 | 50.026 | 53.6247 | 54.2731 | 54.7392 | 56.9361 | 57.2937 | 57.2937 | 57.2937 | 57.2937 | 57.2937 | 57.2937 | 57.2937 | 57.2937 | 57.2937 | 57.2937 | 57.2937 | 57.2937 | 57.2937 | 57.2937 | 57.2937 | 57.2937 | 99% | 0.2972 | 42.7706 | 46.6668 | 47.0703 | 48.4627 | 48.4288 | 48.735 | 49.9326 | 53.3732 | 54.7931 | 53.4491 | 57.1617 | 55.6029 | 57.0055 | 58.0162 | 57.6009 | 57.6009 | 57.6009 | 57.6009 | 57.6009 | 57.6009 | 57.6009 | 57.6009 | 57.6009 | 57.6009 | 57.6009 | 57.6009 | 57.6009 | 57.6009 | 57.6009 | 57.6009
98% | 0.2972 | 38.6225 | 42.6659 | 43.0946 | 43.6247 | 44.3284 | 44.9956 | 46.1616 | 49.0941 | 50.6714 | 49.5207 | 53.083 | 53.7249 | 54.1862 | 56.361 | 56.715 | 56.715 | 56.715 | 56.715 | 56.715 | 56.715 | 56.715 | 56.715 | 56.715 | 56.715 | 56.715 | 56.715 | 56.715 | 56.715 | 56.715 | 56.715 | 98% | 0.2972 | 42.3386 | 46.1954 | 46.5948 | 47.9732 | 47.9396 | 48.2427 | 49.4282 | 52.8341 | 54.2396 | 52.9092 | 56.5843 | 55.0413 | 56.4297 | 57.4302 | 57.0191 | 57.0191 | 57.0191 | 57.0191 | 57.0191 | 57.0191 | 57.0191 | 57.0191 | 57.0191 | 57.0191 | 57.0191 | 57.0191 | 57.0191 | 57.0191 | 57.0191 | 57.0191
97% | 0.2972 | 38.2284 | 42.2305 | 42.6549 | 43.1795 | 43.8761 | 44.5365 | 45.6906 | 48.5931 | 50.1543 | 49.0154 | 52.5414 | 53.1767 | 53.6333 | 55.7859 | 56.1363 | 56.1363 | 56.1363 | 56.1363 | 56.1363 | 56.1363 | 56.1363 | 56.1363 | 56.1363 | 56.1363 | 56.1363 | 56.1363 | 56.1363 | 56.1363 | 56.1363 | 56.1363 | 97% | 0.2972 | 41.9066 | 45.724 | 46.1193 | 47.4837 | 47.4504 | 47.7504 | 48.9238 | 52.295 | 53.6861 | 52.3693 | 56.0069 | 54.4796 | 55.8539 | 56.8441 | 56.4373 | 56.4373 | 56.4373 | 56.4373 | 56.4373 | 56.4373 | 56.4373 | 56.4373 | 56.4373 | 56.4373 | 56.4373 | 56.4373 | 56.4373 | 56.4373 | 56.4373 | 56.4373
95% | 1.486 | 37.4402 | 41.3598 | 41.7754 | 42.2892 | 42.9715 | 43.6182 | 44.7485 | 47.5912 | 49.1202 | 48.0047 | 51.4581 | 52.0802 | 52.5275 | 54.6357 | 54.9788 | 54.9788 | 54.9788 | 54.9788 | 54.9788 | 54.9788 | 54.9788 | 54.9788 | 54.9788 | 54.9788 | 54.9788 | 54.9788 | 54.9788 | 54.9788 | 54.9788 | 54.9788 | 95% | 1.486 | 41.0425 | 44.7812 | 45.1684 | 46.5046 | 46.4721 | 46.7659 | 47.9151 | 51.2167 | 52.5792 | 51.2895 | 54.8521 | 53.3563 | 54.7022 | 55.6721 | 55.2736 | 55.2736 | 55.2736 | 55.2736 | 55.2736 | 55.2736 | 55.2736 | 55.2736 | 55.2736 | 55.2736 | 55.2736 | 55.2736 | 55.2736 | 55.2736 | 55.2736 | 55.2736
90% | 8.6188 | 35.4696 | 39.1829 | 39.5767 | 40.0635 | 40.7098 | 41.3225 | 42.3933 | 45.0864 | 46.5349 | 45.4782 | 48.7497 | 49.3392 | 49.7629 | 51.7601 | 52.0852 | 52.0852 | 52.0852 | 52.0852 | 52.0852 | 52.0852 | 52.0852 | 52.0852 | 52.0852 | 52.0852 | 52.0852 | 52.0852 | 52.0852 | 52.0852 | 52.0852 | 52.0852 | 90% | 8.6188 | 38.8824 | 42.4243 | 42.7911 | 44.057 | 44.0262 | 44.3045 | 45.3932 | 48.5211 | 49.8119 | 48.5901 | 51.9652 | 50.5481 | 51.8232 | 52.742 | 52.3645 | 52.3645 | 52.3645 | 52.3645 | 52.3645 | 52.3645 | 52.3645 | 52.3645 | 52.3645 | 52.3645 | 52.3645 | 52.3645 | 52.3645 | 52.3645 | 52.3645 | 52.3645
85% | 40.1218 | 33.4991 | 37.0061 | 37.378 | 37.8377 | 38.4481 | 39.0268 | 40.0381 | 42.5816 | 43.9497 | 42.9516 | 46.0414 | 46.5981 | 46.9983 | 48.8845 | 49.1916 | 49.1916 | 49.1916 | 49.1916 | 49.1916 | 49.1916 | 49.1916 | 49.1916 | 49.1916 | 49.1916 | 49.1916 | 49.1916 | 49.1916 | 49.1916 | 49.1916 | 49.1916 | 85% | 40.1218 | 36.7222 | 40.0674 | 40.4139 | 41.6094 | 41.5803 | 41.8432 | 42.8714 | 45.8255 | 47.0445 | 45.8906 | 49.0782 | 47.7399 | 48.9441 | 49.8119 | 49.4554 | 49.4554 | 49.4554 | 49.4554 | 49.4554 | 49.4554 | 49.4554 | 49.4554 | 49.4554 | 49.4554 | 49.4554 | 49.4554 | 49.4554 | 49.4554 | 49.4554 | 49.4554
80% | 93.0231 | 31.5286 | 34.8293 | 35.1793 | 35.612 | 36.1865 | 36.7311 | 37.6829 | 40.0768 | 41.3644 | 40.425 | 43.3331 | 43.857 | 44.2337 | 46.009 | 46.2979 | 46.2979 | 46.2979 | 46.2979 | 46.2979 | 46.2979 | 46.2979 | 46.2979 | 46.2979 | 46.2979 | 46.2979 | 46.2979 | 46.2979 | 46.2979 | 46.2979 | 46.2979 | 80% | 93.0231 | 34.5621 | 37.7105 | 38.0366 | 39.1618 | 39.1344 | 39.3818 | 40.3495 | 43.1299 | 44.2772 | 43.1912 | 46.1913 | 44.9317 | 46.065 | 46.8818 | 46.5462 | 46.5462 | 46.5462 | 46.5462 | 46.5462 | 46.5462 | 46.5462 | 46.5462 | 46.5462 | 46.5462 | 46.5462 | 46.5462 | 46.5462 | 46.5462 | 46.5462 | 46.5462
75% | 197.0426 | 29.558 | 32.6525 | 32.9806 | 33.3862 | 33.9248 | 34.4354 | 35.3278 | 37.572 | 38.7791 | 37.8985 | 40.6248 | 41.116 | 41.4691 | 43.1334 | 43.4043 | 43.4043 | 43.4043 | 43.4043 | 43.4043 | 43.4043 | 43.4043 | 43.4043 | 43.4043 | 43.4043 | 43.4043 | 43.4043 | 43.4043 | 43.4043 | 43.4043 | 43.4043 | 75% | 197.0426 | 32.402 | 35.3536 | 35.6593 | 36.7142 | 36.6885 | 36.9204 | 37.8277 | 40.4343 | 41.5099 | 40.4917 | 43.3043 | 42.1234 | 43.186 | 43.9517 | 43.6371 | 43.6371 | 43.6371 | 43.6371 | 43.6371 | 43.6371 | 43.6371 | 43.6371 | 43.6371 | 43.6371 | 43.6371 | 43.6371 | 43.6371 | 43.6371 | 43.6371 | 43.6371
70% | 378.0365 | 27.5875 | 30.4756 | 30.7819 | 31.1605 | 31.6632 | 32.1397 | 32.9726 | 35.0672 | 36.1938 | 35.3719 | 37.9165 | 38.3749 | 38.7045 | 40.2579 | 40.5107 | 40.5107 | 40.5107 | 40.5107 | 40.5107 | 40.5107 | 40.5107 | 40.5107 | 40.5107 | 40.5107 | 40.5107 | 40.5107 | 40.5107 | 40.5107 | 40.5107 | 40.5107 | 70% | 378.0365 | 30.2418 | 32.9967 | 33.282 | 34.2666 | 34.2426 | 34.4591 | 35.3059 | 37.7386 | 38.7426 | 37.7923 | 40.4173 | 39.3152 | 40.3069 | 41.0215 | 40.7279 | 40.7279 | 40.7279 | 40.7279 | 40.7279 | 40.7279 | 40.7279 | 40.7279 | 40.7279 | 40.7279 | 40.7279 | 40.7279 | 40.7279 | 40.7279 | 40.7279 | 40.7279
65% | 616.0926 | 25.617 | 28.2988 | 28.5832 | 28.9347 | 29.4015 | 29.844 | 30.6174 | 32.5624 | 33.6086 | 32.8454 | 35.2081 | 35.6338 | 35.9399 | 37.3823 | 37.6171 | 37.6171 | 37.6171 | 37.6171 | 37.6171 | 37.6171 | 37.6171 | 37.6171 | 37.6171 | 37.6171 | 37.6171 | 37.6171 | 37.6171 | 37.6171 | 37.6171 | 37.6171 | 65% | 616.0926 | 28.0817 | 30.6398 | 30.9047 | 31.819 | 31.7967 | 31.9977 | 32.784 | 35.043 | 35.9752 | 35.0928 | 37.5304 | 36.507 | 37.4278 | 38.0914 | 37.8188 | 37.8188 | 37.8188 | 37.8188 | 37.8188 | 37.8188 | 37.8188 | 37.8188 | 37.8188 | 37.8188 | 37.8188 | 37.8188 | 37.8188 | 37.8188 | 37.8188 | 37.8188
60% | 934.9866 | 23.6464 | 26.122 | 26.3845 | 26.709 | 27.1399 | 27.5483 | 28.2622 | 30.0576 | 31.0233 | 30.3188 | 32.4998 | 32.8928 | 33.1753 | 34.5067 | 34.7235 | 34.7235 | 34.7235 | 34.7235 | 34.7235 | 34.7235 | 34.7235 | 34.7235 | 34.7235 | 34.7235 | 34.7235 | 34.7235 | 34.7235 | 34.7235 | 34.7235 | 34.7235 | 60% | 934.9866 | 25.9216 | 28.2829 | 28.5274 | 29.3713 | 29.3508 | 29.5364 | 30.2622 | 32.3474 | 33.2079 | 32.3934 | 34.6434 | 33.6987 | 34.5488 | 35.1613 | 34.9097 | 34.9097 | 34.9097 | 34.9097 | 34.9097 | 34.9097 | 34.9097 | 34.9097 | 34.9097 | 34.9097 | 34.9097 | 34.9097 | 34.9097 | 34.9097 | 34.9097 | 34.9097
55% | 1310.9428 | 21.6759 | 23.9451 | 24.1858 | 24.4832 | 24.8782 | 25.2527 | 25.907 | 27.5528 | 28.438 | 27.7922 | 29.7915 | 30.1517 | 30.4106 | 31.6312 | 31.8298 | 31.8298 | 31.8298 | 31.8298 | 31.8298 | 31.8298 | 31.8298 | 31.8298 | 31.8298 | 31.8298 | 31.8298 | 31.8298 | 31.8298 | 31.8298 | 31.8298 | 31.8298 | 55% | 1310.9428 | 23.7614 | 25.926 | 26.1501 | 26.9237 | 26.9049 | 27.075 | 27.7403 | 29.6518 | 30.4406 | 29.6939 | 31.7565 | 30.8905 | 31.6697 | 32.2312 | 32.0005 | 32.0005 | 32.0005 | 32.0005 | 32.0005 | 32.0005 | 32.0005 | 32.0005 | 32.0005 | 32.0005 | 32.0005 | 32.0005 | 32.0005 | 32.0005 | 32.0005 | 32.0005
50% | 1730.2899 | 19.7054 | 21.7683 | 21.9871 | 22.2575 | 22.6166 | 22.957 | 23.5518 | 25.048 | 25.8527 | 25.2657 | 27.0832 | 27.4106 | 27.646 | 28.7556 | 28.9362 | 28.9362 | 28.9362 | 28.9362 | 28.9362 | 28.9362 | 28.9362 | 28.9362 | 28.9362 | 28.9362 | 28.9362 | 28.9362 | 28.9362 | 28.9362 | 28.9362 | 28.9362 | 50% | 1730.2899 | 21.6013 | 23.5691 | 23.7729 | 24.4761 | 24.459 | 24.6136 | 25.2185 | 26.9562 | 27.6733 | 26.9945 | 28.8695 | 28.0823 | 28.7906 | 29.3011 | 29.0914 | 29.0914 | 29.0914 | 29.0914 | 29.0914 | 29.0914 | 29.0914 | 29.0914 | 29.0914 | 29.0914 | 29.0914 | 29.0914 | 29.0914 | 29.0914 | 29.0914 | 29.0914
45% | 2168.0633 | 17.7348 | 19.5915 | 19.7883 | 20.0317 | 20.3549 | 20.6613 | 21.1967 | 22.5432 | 23.2675 | 22.7391 | 24.3749 | 24.6696 | 24.8814 | 25.8801 | 26.0426 | 26.0426 | 26.0426 | 26.0426 | 26.0426 | 26.0426 | 26.0426 | 26.0426 | 26.0426 | 26.0426 | 26.0426 | 26.0426 | 26.0426 | 26.0426 | 26.0426 | 26.0426 | 45% | 2168.0633 | 19.4412 | 21.2122 | 21.3956 | 22.0285 | 22.0131 | 22.1523 | 22.6966 | 24.2606 | 24.9059 | 24.295 | 25.9826 | 25.2741 | 25.9116 | 26.371 | 26.1822 | 26.1822 | 26.1822 | 26.1822 | 26.1822 | 26.1822 | 26.1822 | 26.1822 | 26.1822 | 26.1822 | 26.1822 | 26.1822 | 26.1822 | 26.1822 | 26.1822 | 26.1822
40% | 2609.7004 | 15.7643 | 17.4146 | 17.5896 | 17.806 | 18.0932 | 18.3656 | 18.8415 | 20.0384 | 20.6822 | 20.2125 | 21.6665 | 21.9285 | 22.1168 | 23.0045 | 23.149 | 23.149 | 23.149 | 23.149 | 23.149 | 23.149 | 23.149 | 23.149 | 23.149 | 23.149 | 23.149 | 23.149 | 23.149 | 23.149 | 23.149 | 23.149 | 40% | 2609.7004 | 17.2811 | 18.8553 | 19.0183 | 19.5809 | 19.5672 | 19.6909 | 20.1748 | 21.5649 | 22.1386 | 21.5956 | 23.0956 | 22.4658 | 23.0325 | 23.4409 | 23.2731 | 23.2731 | 23.2731 | 23.2731 | 23.2731 | 23.2731 | 23.2731 | 23.2731 | 23.2731 | 23.2731 | 23.2731 | 23.2731 | 23.2731 | 23.2731 | 23.2731 | 23.2731
35% | 2998.1389 | 13.7937 | 15.2378 | 15.3909 | 15.5802 | 15.8316 | 16.0699 | 16.4863 | 17.5336 | 18.0969 | 17.686 | 18.9582 | 19.1875 | 19.3522 | 20.1289 | 20.2554 | 20.2554 | 20.2554 | 20.2554 | 20.2554 | 20.2554 | 20.2554 | 20.2554 | 20.2554 | 20.2554 | 20.2554 | 20.2554 | 20.2554 | 20.2554 | 20.2554 | 20.2554 | 35% | 2998.1389 | 15.1209 | 16.4984 | 16.641 | 17.1333 | 17.1213 | 17.2295 | 17.6529 | 18.8693 | 19.3713 | 18.8961 | 20.2087 | 19.6576 | 20.1535 | 20.5108 | 20.364 | 20.364 | 20.364 | 20.364 | 20.364 | 20.364 | 20.364 | 20.364 | 20.364 | 20.364 | 20.364 | 20.364 | 20.364 | 20.364 | 20.364 | 20.364
30% | 3309.3057 | 11.8232 | 13.061 | 13.1922 | 13.3545 | 13.5699 | 13.7742 | 14.1311 | 15.0288 | 15.5116 | 15.1594 | 16.2499 | 16.4464 | 16.5876 | 17.2534 | 17.3617 | 17.3617 | 17.3617 | 17.3617 | 17.3617 | 17.3617 | 17.3617 | 17.3617 | 17.3617 | 17.3617 | 17.3617 | 17.3617 | 17.3617 | 17.3617 | 17.3617 | 17.3617 | 30% | 3309.3057 | 12.9608 | 14.1414 | 14.2637 | 14.6857 | 14.6754 | 14.7682 | 15.1311 | 16.1737 | 16.604 | 16.1967 | 17.3217 | 16.8494 | 17.2744 | 17.5807 | 17.4548 | 17.4548 | 17.4548 | 17.4548 | 17.4548 | 17.4548 | 17.4548 | 17.4548 | 17.4548 | 17.4548 | 17.4548 | 17.4548 | 17.4548 | 17.4548 | 17.4548 | 17.4548
25% | 3537.8514 | 9.8527 | 10.8842 | 10.9935 | 11.1287 | 11.3083 | 11.4785 | 11.7759 | 12.524 | 12.9264 | 12.6328 | 13.5416 | 13.7053 | 13.823 | 14.3778 | 14.4681 | 14.4681 | 14.4681 | 14.4681 | 14.4681 | 14.4681 | 14.4681 | 14.4681 | 14.4681 | 14.4681 | 14.4681 | 14.4681 | 14.4681 | 14.4681 | 14.4681 | 14.4681 | 25% | 3537.8514 | 10.8007 | 11.7845 | 11.8864 | 12.2381 | 12.2295 | 12.3068 | 12.6092 | 13.4781 | 13.8366 | 13.4972 | 14.4348 | 14.0411 | 14.3953 | 14.6506 | 14.5457 | 14.5457 | 14.5457 | 14.5457 | 14.5457 | 14.5457 | 14.5457 | 14.5457 | 14.5457 | 14.5457 | 14.5457 | 14.5457 | 14.5457 | 14.5457 | 14.5457 | 14.5457
20% | 3731.0305 | 7.8821 | 8.7073 | 8.7948 | 8.903 | 9.0466 | 9.1828 | 9.4207 | 10.0192 | 10.3411 | 10.1063 | 10.8333 | 10.9643 | 11.0584 | 11.5022 | 11.5745 | 11.5745 | 11.5745 | 11.5745 | 11.5745 | 11.5745 | 11.5745 | 11.5745 | 11.5745 | 11.5745 | 11.5745 | 11.5745 | 11.5745 | 11.5745 | 11.5745 | 11.5745 | 20% | 3731.0305 | 8.6405 | 9.4276 | 9.5091 | 9.7904 | 9.7836 | 9.8455 | 10.0874 | 10.7825 | 11.0693 | 10.7978 | 11.5478 | 11.2329 | 11.5163 | 11.7204 | 11.6366 | 11.6366 | 11.6366 | 11.6366 | 11.6366 | 11.6366 | 11.6366 | 11.6366 | 11.6366 | 11.6366 | 11.6366 | 11.6366 | 11.6366 | 11.6366 | 11.6366 | 11.6366
15% | 3910.2412 | 5.9116 | 6.5305 | 6.5961 | 6.6772 | 6.785 | 6.8871 | 7.0656 | 7.5144 | 7.7558 | 7.5797 | 8.125 | 8.2232 | 8.2938 | 8.6267 | 8.6809 | 8.6809 | 8.6809 | 8.6809 | 8.6809 | 8.6809 | 8.6809 | 8.6809 | 8.6809 | 8.6809 | 8.6809 | 8.6809 | 8.6809 | 8.6809 | 8.6809 | 8.6809 | 15% | 3910.2412 | 6.4804 | 7.0707 | 7.1319 | 7.3428 | 7.3377 | 7.3841 | 7.5655 | 8.0869 | 8.302 | 8.0983 | 8.6609 | 8.4247 | 8.6372 | 8.7903 | 8.7274 | 8.7274 | 8.7274 | 8.7274 | 8.7274 | 8.7274 | 8.7274 | 8.7274 | 8.7274 | 8.7274 | 8.7274 | 8.7274 | 8.7274 | 8.7274 | 8.7274 | 8.7274
10% | 4075.1864 | 3.9411 | 4.3537 | 4.3974 | 4.4515 | 4.5233 | 4.5914 | 4.7104 | 5.0096 | 5.1705 | 5.0531 | 5.4166 | 5.4821 | 5.5292 | 5.7511 | 5.7872 | 5.7872 | 5.7872 | 5.7872 | 5.7872 | 5.7872 | 5.7872 | 5.7872 | 5.7872 | 5.7872 | 5.7872 | 5.7872 | 5.7872 | 5.7872 | 5.7872 | 5.7872 | 10% | 4075.1864 | 4.3203 | 4.7138 | 4.7546 | 4.8952 | 4.8918 | 4.9227 | 5.0437 | 5.3912 | 5.5347 | 5.3989 | 5.7739 | 5.6165 | 5.7581 | 5.8602 | 5.8183 | 5.8183 | 5.8183 | 5.8183 | 5.8183 | 5.8183 | 5.8183 | 5.8183 | 5.8183 | 5.8183 | 5.8183 | 5.8183 | 5.8183 | 5.8183 | 5.8183 | 5.8183
5% | 4251.7223 | 1.9705 | 2.1768 | 2.1987 | 2.2257 | 2.2617 | 2.2957 | 2.3552 | 2.5048 | 2.5853 | 2.5266 | 2.7083 | 2.7411 | 2.7646 | 2.8756 | 2.8936 | 2.8936 | 2.8936 | 2.8936 | 2.8936 | 2.8936 | 2.8936 | 2.8936 | 2.8936 | 2.8936 | 2.8936 | 2.8936 | 2.8936 | 2.8936 | 2.8936 | 2.8936 | 5% | 4251.7223 | 2.1601 | 2.3569 | 2.3773 | 2.4476 | 2.4459 | 2.4614 | 2.5218 | 2.6956 | 2.7673 | 2.6994 | 2.887 | 2.8082 | 2.8791 | 2.9301 | 2.9091 | 2.9091 | 2.9091 | 2.9091 | 2.9091 | 2.9091 | 2.9091 | 2.9091 | 2.9091 | 2.9091 | 2.9091 | 2.9091 | 2.9091 | 2.9091 | 2.9091 | 2.9091
9.992e-14% | 4391.7028 | 3.9379e-14 | 4.3502e-14 | 4.3939e-14 | 4.4479e-14 | 4.5197e-14 | 4.5877e-14 | 4.7066e-14 | 5.0056e-14 | 5.1664e-14 | 5.0491e-14 | 5.4123e-14 | 5.4777e-14 | 5.5248e-14 | 5.7465e-14 | 5.7826e-14 | 5.7826e-14 | 5.7826e-14 | 5.7826e-14 | 5.7826e-14 | 5.7826e-14 | 5.7826e-14 | 5.7826e-14 | 5.7826e-14 | 5.7826e-14 | 5.7826e-14 | 5.7826e-14 | 5.7826e-14 | 5.7826e-14 | 5.7826e-14 | 5.7826e-14 | 9.992e-14% | 4391.7028 | 4.3168e-14 | 4.71e-14 | 4.7508e-14 | 4.8913e-14 | 4.8879e-14 | 4.9188e-14 | 5.0397e-14 | 5.3869e-14 | 5.5302e-14 | 5.3946e-14 | 5.7693e-14 | 5.612e-14 | 5.7535e-14 | 5.8555e-14 | 5.8136e-14 | 5.8136e-14 | 5.8136e-14 | 5.8136e-14 | 5.8136e-14 | 5.8136e-14 | 5.8136e-14 | 5.8136e-14 | 5.8136e-14 | 5.8136e-14 | 5.8136e-14 | 5.8136e-14 | 5.8136e-14 | 5.8136e-14 | 5.8136e-14 | 5.8136e-14
Summer Season | [31 empty] | Summer Season
P50 | [31 empty] | P10
% of MD | Summer - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Summer - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 41.4021 | 44.4975 | 44.8085 | 44.6561 | 44.801 | 44.8606 | 45.0515 | 45.4441 | 45.7743 | 45.9263 | 45.7908 | 46.3589 | 46.449 | 46.3423 | 46.5561 | 46.6661 | 46.6661 | 46.6661 | 46.6661 | 46.6661 | 46.6661 | 46.6661 | 46.6661 | 46.6661 | 46.6661 | 46.6661 | 46.6661 | 46.6661 | 46.6661 | 46.6661 | 100% | 0 | 50.9365 | 54.3957 | 54.4912 | 54.3883 | 54.4147 | 54.6036 | 54.9865 | 55.6607 | 56.012 | 56.2661 | 56.6508 | 57.1419 | 57.7357 | 58.0469 | 57.946 | 58.056 | 58.056 | 58.056 | 58.056 | 58.056 | 58.056 | 58.056 | 58.056 | 58.056 | 58.056 | 58.056 | 58.056 | 58.056 | 58.056 | 58.056
99% | 0.37816 | 40.9881 | 44.0525 | 44.3604 | 44.2095 | 44.353 | 44.412 | 44.601 | 44.9896 | 45.3165 | 45.467 | 45.3329 | 45.8953 | 45.9845 | 45.8789 | 46.0906 | 46.1995 | 46.1995 | 46.1995 | 46.1995 | 46.1995 | 46.1995 | 46.1995 | 46.1995 | 46.1995 | 46.1995 | 46.1995 | 46.1995 | 46.1995 | 46.1995 | 46.1995 | 99% | 0 | 50.4271 | 53.8518 | 53.9463 | 53.8444 | 53.8706 | 54.0576 | 54.4366 | 55.1041 | 55.4519 | 55.7035 | 56.0843 | 56.5704 | 57.1583 | 57.4664 | 57.3665 | 57.4754 | 57.4754 | 57.4754 | 57.4754 | 57.4754 | 57.4754 | 57.4754 | 57.4754 | 57.4754 | 57.4754 | 57.4754 | 57.4754 | 57.4754 | 57.4754 | 57.4754
98% | 0.37816 | 40.5741 | 43.6075 | 43.9123 | 43.7629 | 43.905 | 43.9634 | 44.1505 | 44.5352 | 44.8588 | 45.0078 | 44.875 | 45.4317 | 45.52 | 45.4155 | 45.625 | 45.7328 | 45.7328 | 45.7328 | 45.7328 | 45.7328 | 45.7328 | 45.7328 | 45.7328 | 45.7328 | 45.7328 | 45.7328 | 45.7328 | 45.7328 | 45.7328 | 45.7328 | 98% | 0 | 49.9177 | 53.3078 | 53.4014 | 53.3005 | 53.3264 | 53.5116 | 53.8867 | 54.5475 | 54.8917 | 55.1408 | 55.5178 | 55.999 | 56.581 | 56.886 | 56.7871 | 56.8949 | 56.8949 | 56.8949 | 56.8949 | 56.8949 | 56.8949 | 56.8949 | 56.8949 | 56.8949 | 56.8949 | 56.8949 | 56.8949 | 56.8949 | 56.8949 | 56.8949
97% | 0.37816 | 40.1601 | 43.1625 | 43.4643 | 43.3164 | 43.457 | 43.5148 | 43.7 | 44.0807 | 44.4011 | 44.5485 | 44.4171 | 44.9681 | 45.0555 | 44.9521 | 45.1595 | 45.2662 | 45.2662 | 45.2662 | 45.2662 | 45.2662 | 45.2662 | 45.2662 | 45.2662 | 45.2662 | 45.2662 | 45.2662 | 45.2662 | 45.2662 | 45.2662 | 45.2662 | 97% | 0.37816 | 49.4084 | 52.7639 | 52.8564 | 52.7566 | 52.7823 | 52.9655 | 53.3369 | 53.9908 | 54.3316 | 54.5781 | 54.9513 | 55.4276 | 56.0036 | 56.3055 | 56.2076 | 56.3143 | 56.3143 | 56.3143 | 56.3143 | 56.3143 | 56.3143 | 56.3143 | 56.3143 | 56.3143 | 56.3143 | 56.3143 | 56.3143 | 56.3143 | 56.3143 | 56.3143
95% | 0.75633 | 39.332 | 42.2726 | 42.5681 | 42.4232 | 42.561 | 42.6176 | 42.7989 | 43.1719 | 43.4856 | 43.63 | 43.5013 | 44.0409 | 44.1265 | 44.0252 | 44.2283 | 44.3328 | 44.3328 | 44.3328 | 44.3328 | 44.3328 | 44.3328 | 44.3328 | 44.3328 | 44.3328 | 44.3328 | 44.3328 | 44.3328 | 44.3328 | 44.3328 | 44.3328 | 95% | 0.37816 | 48.3896 | 51.6759 | 51.7666 | 51.6689 | 51.694 | 51.8735 | 52.2371 | 52.8776 | 53.2114 | 53.4528 | 53.8182 | 54.2848 | 54.8489 | 55.1446 | 55.0487 | 55.1532 | 55.1532 | 55.1532 | 55.1532 | 55.1532 | 55.1532 | 55.1532 | 55.1532 | 55.1532 | 55.1532 | 55.1532 | 55.1532 | 55.1532 | 55.1532 | 55.1532
90% | 9.0759 | 37.2619 | 40.0477 | 40.3277 | 40.1904 | 40.3209 | 40.3745 | 40.5464 | 40.8996 | 41.1969 | 41.3337 | 41.2117 | 41.723 | 41.8041 | 41.7081 | 41.9005 | 41.9995 | 41.9995 | 41.9995 | 41.9995 | 41.9995 | 41.9995 | 41.9995 | 41.9995 | 41.9995 | 41.9995 | 41.9995 | 41.9995 | 41.9995 | 41.9995 | 41.9995 | 90% | 0.75633 | 45.8428 | 48.9562 | 49.0421 | 48.9494 | 48.9733 | 49.1433 | 49.4878 | 50.0946 | 50.4108 | 50.6395 | 50.9857 | 51.4277 | 51.9621 | 52.2422 | 52.1514 | 52.2504 | 52.2504 | 52.2504 | 52.2504 | 52.2504 | 52.2504 | 52.2504 | 52.2504 | 52.2504 | 52.2504 | 52.2504 | 52.2504 | 52.2504 | 52.2504 | 52.2504
85% | 40.4636 | 35.1918 | 37.8228 | 38.0872 | 37.9576 | 38.0809 | 38.1315 | 38.2938 | 38.6274 | 38.9081 | 39.0374 | 38.9222 | 39.405 | 39.4816 | 39.391 | 39.5727 | 39.6662 | 39.6662 | 39.6662 | 39.6662 | 39.6662 | 39.6662 | 39.6662 | 39.6662 | 39.6662 | 39.6662 | 39.6662 | 39.6662 | 39.6662 | 39.6662 | 39.6662 | 85% | 1.1345 | 43.296 | 46.2364 | 46.3175 | 46.23 | 46.2525 | 46.4131 | 46.7385 | 47.3116 | 47.6102 | 47.8262 | 48.1532 | 48.5706 | 49.0753 | 49.3399 | 49.2541 | 49.3476 | 49.3476 | 49.3476 | 49.3476 | 49.3476 | 49.3476 | 49.3476 | 49.3476 | 49.3476 | 49.3476 | 49.3476 | 49.3476 | 49.3476 | 49.3476 | 49.3476
80% | 94.5411 | 33.1217 | 35.598 | 35.8468 | 35.7248 | 35.8408 | 35.8885 | 36.0412 | 36.3552 | 36.6194 | 36.741 | 36.6326 | 37.0871 | 37.1592 | 37.0739 | 37.2449 | 37.3329 | 37.3329 | 37.3329 | 37.3329 | 37.3329 | 37.3329 | 37.3329 | 37.3329 | 37.3329 | 37.3329 | 37.3329 | 37.3329 | 37.3329 | 37.3329 | 37.3329 | 80% | 2.6471 | 40.7492 | 43.5166 | 43.5929 | 43.5106 | 43.5318 | 43.6829 | 43.9892 | 44.5285 | 44.8096 | 45.0129 | 45.3206 | 45.7135 | 46.1886 | 46.4375 | 46.3568 | 46.4448 | 46.4448 | 46.4448 | 46.4448 | 46.4448 | 46.4448 | 46.4448 | 46.4448 | 46.4448 | 46.4448 | 46.4448 | 46.4448 | 46.4448 | 46.4448 | 46.4448
75% | 197.0236 | 31.0516 | 33.3731 | 33.6064 | 33.492 | 33.6008 | 33.6454 | 33.7886 | 34.083 | 34.3307 | 34.4447 | 34.3431 | 34.7692 | 34.8367 | 34.7568 | 34.9171 | 34.9996 | 34.9996 | 34.9996 | 34.9996 | 34.9996 | 34.9996 | 34.9996 | 34.9996 | 34.9996 | 34.9996 | 34.9996 | 34.9996 | 34.9996 | 34.9996 | 34.9996 | 75% | 3.4035 | 38.2023 | 40.7968 | 40.8684 | 40.7912 | 40.811 | 40.9527 | 41.2398 | 41.7455 | 42.009 | 42.1996 | 42.4881 | 42.8564 | 43.3018 | 43.5352 | 43.4595 | 43.542 | 43.542 | 43.542 | 43.542 | 43.542 | 43.542 | 43.542 | 43.542 | 43.542 | 43.542 | 43.542 | 43.542 | 43.542 | 43.542 | 43.542
70% | 336.9444 | 28.9815 | 31.1482 | 31.366 | 31.2592 | 31.3607 | 31.4024 | 31.5361 | 31.8108 | 32.042 | 32.1484 | 32.0536 | 32.4512 | 32.5143 | 32.4396 | 32.5893 | 32.6663 | 32.6663 | 32.6663 | 32.6663 | 32.6663 | 32.6663 | 32.6663 | 32.6663 | 32.6663 | 32.6663 | 32.6663 | 32.6663 | 32.6663 | 32.6663 | 32.6663 | 70% | 5.6725 | 35.6555 | 38.077 | 38.1438 | 38.0718 | 38.0903 | 38.2225 | 38.4905 | 38.9625 | 39.2084 | 39.3863 | 39.6555 | 39.9993 | 40.415 | 40.6328 | 40.5622 | 40.6392 | 40.6392 | 40.6392 | 40.6392 | 40.6392 | 40.6392 | 40.6392 | 40.6392 | 40.6392 | 40.6392 | 40.6392 | 40.6392 | 40.6392 | 40.6392 | 40.6392
65% | 521.4885 | 26.9114 | 28.9234 | 29.1255 | 29.0264 | 29.1207 | 29.1594 | 29.2835 | 29.5386 | 29.7533 | 29.8521 | 29.764 | 30.1333 | 30.1918 | 30.1225 | 30.2615 | 30.333 | 30.333 | 30.333 | 30.333 | 30.333 | 30.333 | 30.333 | 30.333 | 30.333 | 30.333 | 30.333 | 30.333 | 30.333 | 30.333 | 30.333 | 65% | 6.4288 | 33.1087 | 35.3572 | 35.4193 | 35.3524 | 35.3696 | 35.4924 | 35.7412 | 36.1794 | 36.4078 | 36.573 | 36.823 | 37.1422 | 37.5282 | 37.7305 | 37.6649 | 37.7364 | 37.7364 | 37.7364 | 37.7364 | 37.7364 | 37.7364 | 37.7364 | 37.7364 | 37.7364 | 37.7364 | 37.7364 | 37.7364 | 37.7364 | 37.7364 | 37.7364
60% | 812.675 | 24.8413 | 26.6985 | 26.8851 | 26.7936 | 26.8806 | 26.9164 | 27.0309 | 27.2664 | 27.4646 | 27.5558 | 27.4745 | 27.8153 | 27.8694 | 27.8054 | 27.9337 | 27.9997 | 27.9997 | 27.9997 | 27.9997 | 27.9997 | 27.9997 | 27.9997 | 27.9997 | 27.9997 | 27.9997 | 27.9997 | 27.9997 | 27.9997 | 27.9997 | 27.9997 | 60% | 11.3449 | 30.5619 | 32.6374 | 32.6947 | 32.633 | 32.6488 | 32.7622 | 32.9919 | 33.3964 | 33.6072 | 33.7597 | 33.9905 | 34.2851 | 34.6414 | 34.8281 | 34.7676 | 34.8336 | 34.8336 | 34.8336 | 34.8336 | 34.8336 | 34.8336 | 34.8336 | 34.8336 | 34.8336 | 34.8336 | 34.8336 | 34.8336 | 34.8336 | 34.8336 | 34.8336
55% | 1202.1843 | 22.7712 | 24.4736 | 24.6447 | 24.5608 | 24.6406 | 24.6733 | 24.7783 | 24.9942 | 25.1759 | 25.2595 | 25.1849 | 25.4974 | 25.5469 | 25.4883 | 25.6059 | 25.6664 | 25.6664 | 25.6664 | 25.6664 | 25.6664 | 25.6664 | 25.6664 | 25.6664 | 25.6664 | 25.6664 | 25.6664 | 25.6664 | 25.6664 | 25.6664 | 25.6664 | 55% | 35.5474 | 28.0151 | 29.9176 | 29.9701 | 29.9135 | 29.9281 | 30.032 | 30.2426 | 30.6134 | 30.8066 | 30.9464 | 31.1579 | 31.428 | 31.7546 | 31.9258 | 31.8703 | 31.9308 | 31.9308 | 31.9308 | 31.9308 | 31.9308 | 31.9308 | 31.9308 | 31.9308 | 31.9308 | 31.9308 | 31.9308 | 31.9308 | 31.9308 | 31.9308 | 31.9308
50% | 1686.2345 | 20.7011 | 22.2487 | 22.4043 | 22.328 | 22.4005 | 22.4303 | 22.5258 | 22.722 | 22.8871 | 22.9631 | 22.8954 | 23.1794 | 23.2245 | 23.1712 | 23.2781 | 23.3331 | 23.3331 | 23.3331 | 23.3331 | 23.3331 | 23.3331 | 23.3331 | 23.3331 | 23.3331 | 23.3331 | 23.3331 | 23.3331 | 23.3331 | 23.3331 | 23.3331 | 50% | 95.2974 | 25.4682 | 27.1979 | 27.2456 | 27.1941 | 27.2074 | 27.3018 | 27.4932 | 27.8303 | 28.006 | 28.1331 | 28.3254 | 28.5709 | 28.8678 | 29.0234 | 28.973 | 29.028 | 29.028 | 29.028 | 29.028 | 29.028 | 29.028 | 29.028 | 29.028 | 29.028 | 29.028 | 29.028 | 29.028 | 29.028 | 29.028 | 29.028
45% | 2129.0649 | 18.631 | 20.0239 | 20.1638 | 20.0952 | 20.1605 | 20.1873 | 20.2732 | 20.4498 | 20.5984 | 20.6668 | 20.6059 | 20.8615 | 20.902 | 20.8541 | 20.9503 | 20.9998 | 20.9998 | 20.9998 | 20.9998 | 20.9998 | 20.9998 | 20.9998 | 20.9998 | 20.9998 | 20.9998 | 20.9998 | 20.9998 | 20.9998 | 20.9998 | 20.9998 | 45% | 208.7467 | 22.9214 | 24.4781 | 24.521 | 24.4747 | 24.4866 | 24.5716 | 24.7439 | 25.0473 | 25.2054 | 25.3198 | 25.4928 | 25.7138 | 25.9811 | 26.1211 | 26.0757 | 26.1252 | 26.1252 | 26.1252 | 26.1252 | 26.1252 | 26.1252 | 26.1252 | 26.1252 | 26.1252 | 26.1252 | 26.1252 | 26.1252 | 26.1252 | 26.1252 | 26.1252
40% | 2484.5393 | 16.5608 | 17.799 | 17.9234 | 17.8624 | 17.9204 | 17.9442 | 18.0206 | 18.1776 | 18.3097 | 18.3705 | 18.3163 | 18.5435 | 18.5796 | 18.5369 | 18.6225 | 18.6665 | 18.6665 | 18.6665 | 18.6665 | 18.6665 | 18.6665 | 18.6665 | 18.6665 | 18.6665 | 18.6665 | 18.6665 | 18.6665 | 18.6665 | 18.6665 | 18.6665 | 40% | 380.4333 | 20.3746 | 21.7583 | 21.7965 | 21.7553 | 21.7659 | 21.8415 | 21.9946 | 22.2643 | 22.4048 | 22.5065 | 22.6603 | 22.8567 | 23.0943 | 23.2188 | 23.1784 | 23.2224 | 23.2224 | 23.2224 | 23.2224 | 23.2224 | 23.2224 | 23.2224 | 23.2224 | 23.2224 | 23.2224 | 23.2224 | 23.2224 | 23.2224 | 23.2224 | 23.2224
35% | 2808.248 | 14.4907 | 15.5741 | 15.683 | 15.6296 | 15.6804 | 15.7012 | 15.768 | 15.9054 | 16.021 | 16.0742 | 16.0268 | 16.2256 | 16.2571 | 16.2198 | 16.2947 | 16.3332 | 16.3332 | 16.3332 | 16.3332 | 16.3332 | 16.3332 | 16.3332 | 16.3332 | 16.3332 | 16.3332 | 16.3332 | 16.3332 | 16.3332 | 16.3332 | 16.3332 | 35% | 696.5786 | 17.8278 | 19.0385 | 19.0719 | 19.0359 | 19.0452 | 19.1113 | 19.2453 | 19.4812 | 19.6042 | 19.6931 | 19.8278 | 19.9997 | 20.2075 | 20.3164 | 20.2811 | 20.3196 | 20.3196 | 20.3196 | 20.3196 | 20.3196 | 20.3196 | 20.3196 | 20.3196 | 20.3196 | 20.3196 | 20.3196 | 20.3196 | 20.3196 | 20.3196 | 20.3196
30% | 3095.6528 | 12.4206 | 13.3492 | 13.4426 | 13.3968 | 13.4403 | 13.4582 | 13.5155 | 13.6332 | 13.7323 | 13.7779 | 13.7372 | 13.9077 | 13.9347 | 13.9027 | 13.9668 | 13.9998 | 13.9998 | 13.9998 | 13.9998 | 13.9998 | 13.9998 | 13.9998 | 13.9998 | 13.9998 | 13.9998 | 13.9998 | 13.9998 | 13.9998 | 13.9998 | 13.9998 | 30% | 1260.7997 | 15.2809 | 16.3187 | 16.3474 | 16.3165 | 16.3244 | 16.3811 | 16.4959 | 16.6982 | 16.8036 | 16.8798 | 16.9952 | 17.1426 | 17.3207 | 17.4141 | 17.3838 | 17.4168 | 17.4168 | 17.4168 | 17.4168 | 17.4168 | 17.4168 | 17.4168 | 17.4168 | 17.4168 | 17.4168 | 17.4168 | 17.4168 | 17.4168 | 17.4168 | 17.4168
25% | 3358.8552 | 10.3505 | 11.1244 | 11.2021 | 11.164 | 11.2003 | 11.2151 | 11.2629 | 11.361 | 11.4436 | 11.4816 | 11.4477 | 11.5897 | 11.6122 | 11.5856 | 11.639 | 11.6665 | 11.6665 | 11.6665 | 11.6665 | 11.6665 | 11.6665 | 11.6665 | 11.6665 | 11.6665 | 11.6665 | 11.6665 | 11.6665 | 11.6665 | 11.6665 | 11.6665 | 25% | 1965.3198 | 12.7341 | 13.5989 | 13.6228 | 13.5971 | 13.6037 | 13.6509 | 13.7466 | 13.9152 | 14.003 | 14.0665 | 14.1627 | 14.2855 | 14.4339 | 14.5117 | 14.4865 | 14.514 | 14.514 | 14.514 | 14.514 | 14.514 | 14.514 | 14.514 | 14.514 | 14.514 | 14.514 | 14.514 | 14.514 | 14.514 | 14.514 | 14.514
20% | 3588.7791 | 8.2804 | 8.8995 | 8.9617 | 8.9312 | 8.9602 | 8.9721 | 9.0103 | 9.0888 | 9.1549 | 9.1853 | 9.1582 | 9.2718 | 9.2898 | 9.2685 | 9.3112 | 9.3332 | 9.3332 | 9.3332 | 9.3332 | 9.3332 | 9.3332 | 9.3332 | 9.3332 | 9.3332 | 9.3332 | 9.3332 | 9.3332 | 9.3332 | 9.3332 | 9.3332 | 20% | 2490.2118 | 10.1873 | 10.8791 | 10.8982 | 10.8777 | 10.8829 | 10.9207 | 10.9973 | 11.1321 | 11.2024 | 11.2532 | 11.3302 | 11.4284 | 11.5471 | 11.6094 | 11.5892 | 11.6112 | 11.6112 | 11.6112 | 11.6112 | 11.6112 | 11.6112 | 11.6112 | 11.6112 | 11.6112 | 11.6112 | 11.6112 | 11.6112 | 11.6112 | 11.6112 | 11.6112
15% | 3802.4419 | 6.2103 | 6.6746 | 6.7213 | 6.6984 | 6.7202 | 6.7291 | 6.7577 | 6.8166 | 6.8661 | 6.8889 | 6.8686 | 6.9538 | 6.9673 | 6.9514 | 6.9834 | 6.9999 | 6.9999 | 6.9999 | 6.9999 | 6.9999 | 6.9999 | 6.9999 | 6.9999 | 6.9999 | 6.9999 | 6.9999 | 6.9999 | 6.9999 | 6.9999 | 6.9999 | 15% | 2997.7083 | 7.6405 | 8.1594 | 8.1737 | 8.1582 | 8.1622 | 8.1905 | 8.248 | 8.3491 | 8.4018 | 8.4399 | 8.4976 | 8.5713 | 8.6604 | 8.707 | 8.6919 | 8.7084 | 8.7084 | 8.7084 | 8.7084 | 8.7084 | 8.7084 | 8.7084 | 8.7084 | 8.7084 | 8.7084 | 8.7084 | 8.7084 | 8.7084 | 8.7084 | 8.7084
10% | 4024.8025 | 4.1402 | 4.4497 | 4.4809 | 4.4656 | 4.4801 | 4.4861 | 4.5052 | 4.5444 | 4.5774 | 4.5926 | 4.5791 | 4.6359 | 4.6449 | 4.6342 | 4.6556 | 4.6666 | 4.6666 | 4.6666 | 4.6666 | 4.6666 | 4.6666 | 4.6666 | 4.6666 | 4.6666 | 4.6666 | 4.6666 | 4.6666 | 4.6666 | 4.6666 | 4.6666 | 10% | 3491.5908 | 5.0936 | 5.4396 | 5.4491 | 5.4388 | 5.4415 | 5.4604 | 5.4986 | 5.5661 | 5.6012 | 5.6266 | 5.6651 | 5.7142 | 5.7736 | 5.8047 | 5.7946 | 5.8056 | 5.8056 | 5.8056 | 5.8056 | 5.8056 | 5.8056 | 5.8056 | 5.8056 | 5.8056 | 5.8056 | 5.8056 | 5.8056 | 5.8056 | 5.8056 | 5.8056
5% | 4239.978 | 2.0701 | 2.2249 | 2.2404 | 2.2328 | 2.2401 | 2.243 | 2.2526 | 2.2722 | 2.2887 | 2.2963 | 2.2895 | 2.3179 | 2.3224 | 2.3171 | 2.3278 | 2.3333 | 2.3333 | 2.3333 | 2.3333 | 2.3333 | 2.3333 | 2.3333 | 2.3333 | 2.3333 | 2.3333 | 2.3333 | 2.3333 | 2.3333 | 2.3333 | 2.3333 | 5% | 3955.9766 | 2.5468 | 2.7198 | 2.7246 | 2.7194 | 2.7207 | 2.7302 | 2.7493 | 2.783 | 2.8006 | 2.8133 | 2.8325 | 2.8571 | 2.8868 | 2.9023 | 2.8973 | 2.9028 | 2.9028 | 2.9028 | 2.9028 | 2.9028 | 2.9028 | 2.9028 | 2.9028 | 2.9028 | 2.9028 | 2.9028 | 2.9028 | 2.9028 | 2.9028 | 2.9028
9.992e-14% | 4391.6218 | 4.1369e-14 | 4.4462e-14 | 4.4773e-14 | 4.462e-14 | 4.4765e-14 | 4.4825e-14 | 4.5015e-14 | 4.5408e-14 | 4.5738e-14 | 4.589e-14 | 4.5754e-14 | 4.6322e-14 | 4.6412e-14 | 4.6305e-14 | 4.6519e-14 | 4.6629e-14 | 4.6629e-14 | 4.6629e-14 | 4.6629e-14 | 4.6629e-14 | 4.6629e-14 | 4.6629e-14 | 4.6629e-14 | 4.6629e-14 | 4.6629e-14 | 4.6629e-14 | 4.6629e-14 | 4.6629e-14 | 4.6629e-14 | 4.6629e-14 | 9.992e-14% | 4391.6218 | 5.0896e-14 | 5.4352e-14 | 5.4448e-14 | 5.4345e-14 | 5.4371e-14 | 5.456e-14 | 5.4943e-14 | 5.5616e-14 | 5.5967e-14 | 5.6221e-14 | 5.6605e-14 | 5.7096e-14 | 5.769e-14 | 5.8001e-14 | 5.79e-14 | 5.801e-14 | 5.801e-14 | 5.801e-14 | 5.801e-14 | 5.801e-14 | 5.801e-14 | 5.801e-14 | 5.801e-14 | 5.801e-14 | 5.801e-14 | 5.801e-14 | 5.801e-14 | 5.801e-14 | 5.801e-14 | 5.801e-14
Option 4
Winter Season | [31 empty] | Winter Season
P50 | [31 empty] | P10
% of MD | Winter - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Winter - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 39.4107 | 43.5366 | 43.9741 | -21.485 | -20.7669 | -20.0861 | -18.8963 | -15.904 | -14.2945 | -15.4687 | -11.8336 | -11.1787 | -10.7079 | -8.4888 | -8.1276 | -8.1276 | -8.1276 | -8.1276 | -8.1276 | -8.1276 | -8.1276 | -8.1276 | -8.1276 | -8.1276 | -8.1276 | -8.1276 | -8.1276 | -8.1276 | -8.1276 | -8.1276 | 100% | 0 | 43.2026 | 47.1382 | 47.5457 | -17.0478 | -17.082 | -16.7727 | -15.5631 | -12.0876 | -10.6535 | -12.011 | -8.2609 | -9.8354 | -8.4187 | -7.3978 | -7.8172 | -7.8172 | -7.8172 | -7.8172 | -7.8172 | -7.8172 | -7.8172 | -7.8172 | -7.8172 | -7.8172 | -7.8172 | -7.8172 | -7.8172 | -7.8172 | -7.8172 | -7.8172
99% | 0.2972 | 39.0166 | 43.1012 | 43.5344 | -21.2702 | -20.5592 | -19.8852 | -18.7074 | -15.745 | -14.1516 | -15.314 | -11.7153 | -11.0669 | -10.6008 | -8.4039 | -8.0463 | -8.0463 | -8.0463 | -8.0463 | -8.0463 | -8.0463 | -8.0463 | -8.0463 | -8.0463 | -8.0463 | -8.0463 | -8.0463 | -8.0463 | -8.0463 | -8.0463 | -8.0463 | 99% | 0.2972 | 42.7706 | 46.6668 | 47.0703 | -16.8773 | -16.9112 | -16.605 | -15.4074 | -11.9668 | -10.5469 | -11.8909 | -8.1783 | -9.7371 | -8.3345 | -7.3238 | -7.7391 | -7.7391 | -7.7391 | -7.7391 | -7.7391 | -7.7391 | -7.7391 | -7.7391 | -7.7391 | -7.7391 | -7.7391 | -7.7391 | -7.7391 | -7.7391 | -7.7391 | -7.7391
98% | 0.2972 | 38.6225 | 42.6659 | 43.0946 | -21.0553 | -20.3516 | -19.6844 | -18.5184 | -15.5859 | -14.0086 | -15.1593 | -11.597 | -10.9551 | -10.4938 | -8.319 | -7.965 | -7.965 | -7.965 | -7.965 | -7.965 | -7.965 | -7.965 | -7.965 | -7.965 | -7.965 | -7.965 | -7.965 | -7.965 | -7.965 | -7.965 | -7.965 | 98% | 0.2972 | 42.3386 | 46.1954 | 46.5948 | -16.7068 | -16.7404 | -16.4373 | -15.2518 | -11.8459 | -10.4404 | -11.7708 | -8.0957 | -9.6387 | -8.2503 | -7.2498 | -7.6609 | -7.6609 | -7.6609 | -7.6609 | -7.6609 | -7.6609 | -7.6609 | -7.6609 | -7.6609 | -7.6609 | -7.6609 | -7.6609 | -7.6609 | -7.6609 | -7.6609 | -7.6609
97% | 0.2972 | 38.2284 | 42.2305 | 42.6549 | -20.8405 | -20.1439 | -19.4835 | -18.3294 | -15.4269 | -13.8657 | -15.0046 | -11.4786 | -10.8433 | -10.3867 | -8.2341 | -7.8837 | -7.8837 | -7.8837 | -7.8837 | -7.8837 | -7.8837 | -7.8837 | -7.8837 | -7.8837 | -7.8837 | -7.8837 | -7.8837 | -7.8837 | -7.8837 | -7.8837 | -7.8837 | 97% | 0.2972 | 41.9066 | 45.724 | 46.1193 | -16.5363 | -16.5696 | -16.2696 | -15.0962 | -11.725 | -10.3339 | -11.6507 | -8.0131 | -9.5404 | -8.1661 | -7.1759 | -7.5827 | -7.5827 | -7.5827 | -7.5827 | -7.5827 | -7.5827 | -7.5827 | -7.5827 | -7.5827 | -7.5827 | -7.5827 | -7.5827 | -7.5827 | -7.5827 | -7.5827 | -7.5827
95% | 1.486 | 37.4402 | 41.3598 | 41.7754 | -20.4108 | -19.7285 | -19.0818 | -17.9515 | -15.1088 | -13.5798 | -14.6953 | -11.2419 | -10.6198 | -10.1725 | -8.0643 | -7.7212 | -7.7212 | -7.7212 | -7.7212 | -7.7212 | -7.7212 | -7.7212 | -7.7212 | -7.7212 | -7.7212 | -7.7212 | -7.7212 | -7.7212 | -7.7212 | -7.7212 | -7.7212 | 95% | 1.486 | 41.0425 | 44.7812 | 45.1684 | -16.1954 | -16.2279 | -15.9341 | -14.7849 | -11.4833 | -10.1208 | -11.4105 | -7.8479 | -9.3437 | -7.9978 | -7.0279 | -7.4264 | -7.4264 | -7.4264 | -7.4264 | -7.4264 | -7.4264 | -7.4264 | -7.4264 | -7.4264 | -7.4264 | -7.4264 | -7.4264 | -7.4264 | -7.4264 | -7.4264 | -7.4264
90% | 8.6188 | 35.4696 | 39.1829 | 39.5767 | -19.3365 | -18.6902 | -18.0775 | -17.0067 | -14.3136 | -12.8651 | -13.9218 | -10.6503 | -10.0608 | -9.6371 | -7.6399 | -7.3148 | -7.3148 | -7.3148 | -7.3148 | -7.3148 | -7.3148 | -7.3148 | -7.3148 | -7.3148 | -7.3148 | -7.3148 | -7.3148 | -7.3148 | -7.3148 | -7.3148 | -7.3148 | 90% | 8.6188 | 38.8824 | 42.4243 | 42.7911 | -15.343 | -15.3738 | -15.0955 | -14.0068 | -10.8789 | -9.5881 | -10.8099 | -7.4348 | -8.8519 | -7.5768 | -6.658 | -7.0355 | -7.0355 | -7.0355 | -7.0355 | -7.0355 | -7.0355 | -7.0355 | -7.0355 | -7.0355 | -7.0355 | -7.0355 | -7.0355 | -7.0355 | -7.0355 | -7.0355 | -7.0355
85% | 40.1218 | 33.4991 | 37.0061 | 37.378 | -18.2623 | -17.6519 | -17.0732 | -16.0619 | -13.5184 | -12.1503 | -13.1484 | -10.0586 | -9.5019 | -9.1017 | -7.2155 | -6.9084 | -6.9084 | -6.9084 | -6.9084 | -6.9084 | -6.9084 | -6.9084 | -6.9084 | -6.9084 | -6.9084 | -6.9084 | -6.9084 | -6.9084 | -6.9084 | -6.9084 | -6.9084 | 85% | 40.1218 | 36.7222 | 40.0674 | 40.4139 | -14.4906 | -14.5197 | -14.2568 | -13.2286 | -10.2745 | -9.0555 | -10.2094 | -7.0218 | -8.3601 | -7.1559 | -6.2881 | -6.6446 | -6.6446 | -6.6446 | -6.6446 | -6.6446 | -6.6446 | -6.6446 | -6.6446 | -6.6446 | -6.6446 | -6.6446 | -6.6446 | -6.6446 | -6.6446 | -6.6446 | -6.6446
80% | 93.0231 | 31.5286 | 34.8293 | 35.1793 | -17.188 | -16.6135 | -16.0689 | -15.1171 | -12.7232 | -11.4356 | -12.375 | -9.4669 | -8.943 | -8.5663 | -6.791 | -6.5021 | -6.5021 | -6.5021 | -6.5021 | -6.5021 | -6.5021 | -6.5021 | -6.5021 | -6.5021 | -6.5021 | -6.5021 | -6.5021 | -6.5021 | -6.5021 | -6.5021 | -6.5021 | 80% | 93.0231 | 34.5621 | 37.7105 | 38.0366 | -13.6382 | -13.6656 | -13.4182 | -12.4505 | -9.6701 | -8.5228 | -9.6088 | -6.6087 | -7.8683 | -6.735 | -5.9182 | -6.2538 | -6.2538 | -6.2538 | -6.2538 | -6.2538 | -6.2538 | -6.2538 | -6.2538 | -6.2538 | -6.2538 | -6.2538 | -6.2538 | -6.2538 | -6.2538 | -6.2538 | -6.2538
75% | 197.0426 | 29.558 | 32.6525 | 32.9806 | -16.1138 | -15.5752 | -15.0646 | -14.1722 | -11.928 | -10.7209 | -11.6015 | -8.8752 | -8.384 | -8.0309 | -6.3666 | -6.0957 | -6.0957 | -6.0957 | -6.0957 | -6.0957 | -6.0957 | -6.0957 | -6.0957 | -6.0957 | -6.0957 | -6.0957 | -6.0957 | -6.0957 | -6.0957 | -6.0957 | -6.0957 | 75% | 197.0426 | 32.402 | 35.3536 | 35.6593 | -12.7858 | -12.8115 | -12.5796 | -11.6723 | -9.0657 | -7.9901 | -9.0083 | -6.1957 | -7.3766 | -6.314 | -5.5483 | -5.8629 | -5.8629 | -5.8629 | -5.8629 | -5.8629 | -5.8629 | -5.8629 | -5.8629 | -5.8629 | -5.8629 | -5.8629 | -5.8629 | -5.8629 | -5.8629 | -5.8629 | -5.8629
70% | 378.0365 | 27.5875 | 30.4756 | 30.7819 | -15.0395 | -14.5368 | -14.0603 | -13.2274 | -11.1328 | -10.0062 | -10.8281 | -8.2835 | -7.8251 | -7.4955 | -5.9421 | -5.6893 | -5.6893 | -5.6893 | -5.6893 | -5.6893 | -5.6893 | -5.6893 | -5.6893 | -5.6893 | -5.6893 | -5.6893 | -5.6893 | -5.6893 | -5.6893 | -5.6893 | -5.6893 | 70% | 378.0365 | 30.2418 | 32.9967 | 33.282 | -11.9334 | -11.9574 | -11.7409 | -10.8941 | -8.4614 | -7.4574 | -8.4077 | -5.7827 | -6.8848 | -5.8931 | -5.1785 | -5.4721 | -5.4721 | -5.4721 | -5.4721 | -5.4721 | -5.4721 | -5.4721 | -5.4721 | -5.4721 | -5.4721 | -5.4721 | -5.4721 | -5.4721 | -5.4721 | -5.4721 | -5.4721
65% | 616.0926 | 25.617 | 28.2988 | 28.5832 | -13.9653 | -13.4985 | -13.056 | -12.2826 | -10.3376 | -9.2914 | -10.0546 | -7.6919 | -7.2662 | -6.9601 | -5.5177 | -5.2829 | -5.2829 | -5.2829 | -5.2829 | -5.2829 | -5.2829 | -5.2829 | -5.2829 | -5.2829 | -5.2829 | -5.2829 | -5.2829 | -5.2829 | -5.2829 | -5.2829 | -5.2829 | 65% | 616.0926 | 28.0817 | 30.6398 | 30.9047 | -11.081 | -11.1033 | -10.9023 | -10.116 | -7.857 | -6.9248 | -7.8072 | -5.3696 | -6.393 | -5.4722 | -4.8086 | -5.0812 | -5.0812 | -5.0812 | -5.0812 | -5.0812 | -5.0812 | -5.0812 | -5.0812 | -5.0812 | -5.0812 | -5.0812 | -5.0812 | -5.0812 | -5.0812 | -5.0812 | -5.0812
60% | 934.9866 | 23.6464 | 26.122 | 26.3845 | -12.891 | -12.4601 | -12.0517 | -11.3378 | -9.5424 | -8.5767 | -9.2812 | -7.1002 | -6.7072 | -6.4247 | -5.0933 | -4.8765 | -4.8765 | -4.8765 | -4.8765 | -4.8765 | -4.8765 | -4.8765 | -4.8765 | -4.8765 | -4.8765 | -4.8765 | -4.8765 | -4.8765 | -4.8765 | -4.8765 | -4.8765 | 60% | 934.9866 | 25.9216 | 28.2829 | 28.5274 | -10.2287 | -10.2492 | -10.0636 | -9.3378 | -7.2526 | -6.3921 | -7.2066 | -4.9566 | -5.9013 | -5.0512 | -4.4387 | -4.6903 | -4.6903 | -4.6903 | -4.6903 | -4.6903 | -4.6903 | -4.6903 | -4.6903 | -4.6903 | -4.6903 | -4.6903 | -4.6903 | -4.6903 | -4.6903 | -4.6903 | -4.6903
55% | 1310.9428 | 21.6759 | 23.9451 | 24.1858 | -11.8168 | -11.4218 | -11.0473 | -10.393 | -8.7472 | -7.862 | -8.5078 | -6.5085 | -6.1483 | -5.8894 | -4.6688 | -4.4702 | -4.4702 | -4.4702 | -4.4702 | -4.4702 | -4.4702 | -4.4702 | -4.4702 | -4.4702 | -4.4702 | -4.4702 | -4.4702 | -4.4702 | -4.4702 | -4.4702 | -4.4702 | 55% | 1310.9428 | 23.7614 | 25.926 | 26.1501 | -9.3763 | -9.3951 | -9.225 | -8.5597 | -6.6482 | -5.8594 | -6.6061 | -4.5435 | -5.4095 | -4.6303 | -4.0688 | -4.2995 | -4.2995 | -4.2995 | -4.2995 | -4.2995 | -4.2995 | -4.2995 | -4.2995 | -4.2995 | -4.2995 | -4.2995 | -4.2995 | -4.2995 | -4.2995 | -4.2995 | -4.2995
50% | 1730.2899 | 19.7054 | 21.7683 | 21.9871 | -10.7425 | -10.3834 | -10.043 | -9.4482 | -7.952 | -7.1473 | -7.7343 | -5.9168 | -5.5894 | -5.354 | -4.2444 | -4.0638 | -4.0638 | -4.0638 | -4.0638 | -4.0638 | -4.0638 | -4.0638 | -4.0638 | -4.0638 | -4.0638 | -4.0638 | -4.0638 | -4.0638 | -4.0638 | -4.0638 | -4.0638 | 50% | 1730.2899 | 21.6013 | 23.5691 | 23.7729 | -8.5239 | -8.541 | -8.3864 | -7.7815 | -6.0438 | -5.3267 | -6.0055 | -4.1305 | -4.9177 | -4.2094 | -3.6989 | -3.9086 | -3.9086 | -3.9086 | -3.9086 | -3.9086 | -3.9086 | -3.9086 | -3.9086 | -3.9086 | -3.9086 | -3.9086 | -3.9086 | -3.9086 | -3.9086 | -3.9086 | -3.9086
45% | 2168.0633 | 17.7348 | 19.5915 | 19.7883 | -9.6683 | -9.3451 | -9.0387 | -8.5033 | -7.1568 | -6.4325 | -6.9609 | -5.3251 | -5.0304 | -4.8186 | -3.8199 | -3.6574 | -3.6574 | -3.6574 | -3.6574 | -3.6574 | -3.6574 | -3.6574 | -3.6574 | -3.6574 | -3.6574 | -3.6574 | -3.6574 | -3.6574 | -3.6574 | -3.6574 | -3.6574 | 45% | 2168.0633 | 19.4412 | 21.2122 | 21.3956 | -7.6715 | -7.6869 | -7.5477 | -7.0034 | -5.4394 | -4.7941 | -5.405 | -3.7174 | -4.4259 | -3.7884 | -3.329 | -3.5178 | -3.5178 | -3.5178 | -3.5178 | -3.5178 | -3.5178 | -3.5178 | -3.5178 | -3.5178 | -3.5178 | -3.5178 | -3.5178 | -3.5178 | -3.5178 | -3.5178 | -3.5178
40% | 2609.7004 | 15.7643 | 17.4146 | 17.5896 | -8.594 | -8.3068 | -8.0344 | -7.5585 | -6.3616 | -5.7178 | -6.1875 | -4.7335 | -4.4715 | -4.2832 | -3.3955 | -3.251 | -3.251 | -3.251 | -3.251 | -3.251 | -3.251 | -3.251 | -3.251 | -3.251 | -3.251 | -3.251 | -3.251 | -3.251 | -3.251 | -3.251 | -3.251 | 40% | 2609.7004 | 17.2811 | 18.8553 | 19.0183 | -6.8191 | -6.8328 | -6.7091 | -6.2252 | -4.8351 | -4.2614 | -4.8044 | -3.3044 | -3.9342 | -3.3675 | -2.9591 | -3.1269 | -3.1269 | -3.1269 | -3.1269 | -3.1269 | -3.1269 | -3.1269 | -3.1269 | -3.1269 | -3.1269 | -3.1269 | -3.1269 | -3.1269 | -3.1269 | -3.1269 | -3.1269
35% | 2998.1389 | 13.7937 | 15.2378 | 15.3909 | -7.5198 | -7.2684 | -7.0301 | -6.6137 | -5.5664 | -5.0031 | -5.414 | -4.1418 | -3.9125 | -3.7478 | -2.9711 | -2.8446 | -2.8446 | -2.8446 | -2.8446 | -2.8446 | -2.8446 | -2.8446 | -2.8446 | -2.8446 | -2.8446 | -2.8446 | -2.8446 | -2.8446 | -2.8446 | -2.8446 | -2.8446 | 35% | 2998.1389 | 15.1209 | 16.4984 | 16.641 | -5.9667 | -5.9787 | -5.8705 | -5.4471 | -4.2307 | -3.7287 | -4.2039 | -2.8913 | -3.4424 | -2.9465 | -2.5892 | -2.736 | -2.736 | -2.736 | -2.736 | -2.736 | -2.736 | -2.736 | -2.736 | -2.736 | -2.736 | -2.736 | -2.736 | -2.736 | -2.736 | -2.736 | -2.736
30% | 3309.3057 | 11.8232 | 13.061 | 13.1922 | -6.4455 | -6.2301 | -6.0258 | -5.6689 | -4.7712 | -4.2884 | -4.6406 | -3.5501 | -3.3536 | -3.2124 | -2.5466 | -2.4383 | -2.4383 | -2.4383 | -2.4383 | -2.4383 | -2.4383 | -2.4383 | -2.4383 | -2.4383 | -2.4383 | -2.4383 | -2.4383 | -2.4383 | -2.4383 | -2.4383 | -2.4383 | 30% | 3309.3057 | 12.9608 | 14.1414 | 14.2637 | -5.1143 | -5.1246 | -5.0318 | -4.6689 | -3.6263 | -3.196 | -3.6033 | -2.4783 | -2.9506 | -2.5256 | -2.2193 | -2.3452 | -2.3452 | -2.3452 | -2.3452 | -2.3452 | -2.3452 | -2.3452 | -2.3452 | -2.3452 | -2.3452 | -2.3452 | -2.3452 | -2.3452 | -2.3452 | -2.3452 | -2.3452
25% | 3537.8514 | 9.8527 | 10.8842 | 10.9935 | -5.3713 | -5.1917 | -5.0215 | -4.7241 | -3.976 | -3.5736 | -3.8672 | -2.9584 | -2.7947 | -2.677 | -2.1222 | -2.0319 | -2.0319 | -2.0319 | -2.0319 | -2.0319 | -2.0319 | -2.0319 | -2.0319 | -2.0319 | -2.0319 | -2.0319 | -2.0319 | -2.0319 | -2.0319 | -2.0319 | -2.0319 | 25% | 3537.8514 | 10.8007 | 11.7845 | 11.8864 | -4.2619 | -4.2705 | -4.1932 | -3.8908 | -3.0219 | -2.6634 | -3.0028 | -2.0652 | -2.4589 | -2.1047 | -1.8494 | -1.9543 | -1.9543 | -1.9543 | -1.9543 | -1.9543 | -1.9543 | -1.9543 | -1.9543 | -1.9543 | -1.9543 | -1.9543 | -1.9543 | -1.9543 | -1.9543 | -1.9543 | -1.9543
20% | 3731.0305 | 7.8821 | 8.7073 | 8.7948 | -4.297 | -4.1534 | -4.0172 | -3.7793 | -3.1808 | -2.8589 | -3.0937 | -2.3667 | -2.2357 | -2.1416 | -1.6978 | -1.6255 | -1.6255 | -1.6255 | -1.6255 | -1.6255 | -1.6255 | -1.6255 | -1.6255 | -1.6255 | -1.6255 | -1.6255 | -1.6255 | -1.6255 | -1.6255 | -1.6255 | -1.6255 | 20% | 3731.0305 | 8.6405 | 9.4276 | 9.5091 | -3.4096 | -3.4164 | -3.3545 | -3.1126 | -2.4175 | -2.1307 | -2.4022 | -1.6522 | -1.9671 | -1.6837 | -1.4796 | -1.5634 | -1.5634 | -1.5634 | -1.5634 | -1.5634 | -1.5634 | -1.5634 | -1.5634 | -1.5634 | -1.5634 | -1.5634 | -1.5634 | -1.5634 | -1.5634 | -1.5634 | -1.5634
15% | 3910.2412 | 5.9116 | 6.5305 | 6.5961 | -3.2228 | -3.115 | -3.0129 | -2.8344 | -2.3856 | -2.1442 | -2.3203 | -1.775 | -1.6768 | -1.6062 | -1.2733 | -1.2191 | -1.2191 | -1.2191 | -1.2191 | -1.2191 | -1.2191 | -1.2191 | -1.2191 | -1.2191 | -1.2191 | -1.2191 | -1.2191 | -1.2191 | -1.2191 | -1.2191 | -1.2191 | 15% | 3910.2412 | 6.4804 | 7.0707 | 7.1319 | -2.5572 | -2.5623 | -2.5159 | -2.3345 | -1.8131 | -1.598 | -1.8017 | -1.2391 | -1.4753 | -1.2628 | -1.1097 | -1.1726 | -1.1726 | -1.1726 | -1.1726 | -1.1726 | -1.1726 | -1.1726 | -1.1726 | -1.1726 | -1.1726 | -1.1726 | -1.1726 | -1.1726 | -1.1726 | -1.1726 | -1.1726
10% | 4075.1864 | 3.9411 | 4.3537 | 4.3974 | -2.1485 | -2.0767 | -2.0086 | -1.8896 | -1.5904 | -1.4295 | -1.5469 | -1.1834 | -1.1179 | -1.0708 | -0.84888 | -0.81276 | -0.81276 | -0.81276 | -0.81276 | -0.81276 | -0.81276 | -0.81276 | -0.81276 | -0.81276 | -0.81276 | -0.81276 | -0.81276 | -0.81276 | -0.81276 | -0.81276 | -0.81276 | 10% | 4075.1864 | 4.3203 | 4.7138 | 4.7546 | -1.7048 | -1.7082 | -1.6773 | -1.5563 | -1.2088 | -1.0653 | -1.2011 | -0.82609 | -0.98354 | -0.84187 | -0.73978 | -0.78172 | -0.78172 | -0.78172 | -0.78172 | -0.78172 | -0.78172 | -0.78172 | -0.78172 | -0.78172 | -0.78172 | -0.78172 | -0.78172 | -0.78172 | -0.78172 | -0.78172 | -0.78172
5% | 4251.7223 | 1.9705 | 2.1768 | 2.1987 | -1.0743 | -1.0383 | -1.0043 | -0.94482 | -0.7952 | -0.71473 | -0.77343 | -0.59168 | -0.55894 | -0.5354 | -0.42444 | -0.40638 | -0.40638 | -0.40638 | -0.40638 | -0.40638 | -0.40638 | -0.40638 | -0.40638 | -0.40638 | -0.40638 | -0.40638 | -0.40638 | -0.40638 | -0.40638 | -0.40638 | -0.40638 | 5% | 4251.7223 | 2.1601 | 2.3569 | 2.3773 | -0.85239 | -0.8541 | -0.83864 | -0.77815 | -0.60438 | -0.53267 | -0.60055 | -0.41305 | -0.49177 | -0.42094 | -0.36989 | -0.39086 | -0.39086 | -0.39086 | -0.39086 | -0.39086 | -0.39086 | -0.39086 | -0.39086 | -0.39086 | -0.39086 | -0.39086 | -0.39086 | -0.39086 | -0.39086 | -0.39086 | -0.39086
9.992e-14% | 4391.7028 | 3.9379e-14 | 4.3502e-14 | 4.3939e-14 | -2.1468e-14 | -2.075e-14 | -2.007e-14 | -1.8881e-14 | -1.5891e-14 | -1.4283e-14 | -1.5456e-14 | -1.1824e-14 | -1.117e-14 | -1.0699e-14 | -8.482e-15 | -8.1211e-15 | -8.1211e-15 | -8.1211e-15 | -8.1211e-15 | -8.1211e-15 | -8.1211e-15 | -8.1211e-15 | -8.1211e-15 | -8.1211e-15 | -8.1211e-15 | -8.1211e-15 | -8.1211e-15 | -8.1211e-15 | -8.1211e-15 | -8.1211e-15 | -8.1211e-15 | 9.992e-14% | 4391.7028 | 4.3168e-14 | 4.71e-14 | 4.7508e-14 | -1.7034e-14 | -1.7068e-14 | -1.6759e-14 | -1.5551e-14 | -1.2078e-14 | -1.0645e-14 | -1.2001e-14 | -8.2543e-15 | -9.8276e-15 | -8.412e-15 | -7.3919e-15 | -7.811e-15 | -7.811e-15 | -7.811e-15 | -7.811e-15 | -7.811e-15 | -7.811e-15 | -7.811e-15 | -7.811e-15 | -7.811e-15 | -7.811e-15 | -7.811e-15 | -7.811e-15 | -7.811e-15 | -7.811e-15 | -7.811e-15 | -7.811e-15
Summer Season | [31 empty] | Summer Season
P50 | [31 empty] | P10
% of MD | Summer - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Summer - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 41.4021 | 44.4975 | 44.8085 | -21.3439 | -21.199 | -21.1394 | -20.9485 | -20.5559 | -20.2257 | -20.0737 | -20.2092 | -19.6411 | -19.551 | -19.6577 | -19.4439 | -19.3339 | -19.3339 | -19.3339 | -19.3339 | -19.3339 | -19.3339 | -19.3339 | -19.3339 | -19.3339 | -19.3339 | -19.3339 | -19.3339 | -19.3339 | -19.3339 | -19.3339 | 100% | 0 | 50.9365 | 54.3957 | 54.4912 | -11.6117 | -11.5853 | -11.3964 | -11.0135 | -10.3393 | -9.988 | -9.7339 | -9.3492 | -8.8581 | -8.2643 | -7.9531 | -8.054 | -7.944 | -7.944 | -7.944 | -7.944 | -7.944 | -7.944 | -7.944 | -7.944 | -7.944 | -7.944 | -7.944 | -7.944 | -7.944 | -7.944 | -7.944
99% | 0.37816 | 40.9881 | 44.0525 | 44.3604 | -21.1305 | -20.987 | -20.928 | -20.739 | -20.3504 | -20.0235 | -19.873 | -20.0071 | -19.4447 | -19.3555 | -19.4611 | -19.2494 | -19.1405 | -19.1405 | -19.1405 | -19.1405 | -19.1405 | -19.1405 | -19.1405 | -19.1405 | -19.1405 | -19.1405 | -19.1405 | -19.1405 | -19.1405 | -19.1405 | -19.1405 | 99% | 0 | 50.4271 | 53.8518 | 53.9463 | -11.4956 | -11.4694 | -11.2824 | -10.9034 | -10.2359 | -9.8881 | -9.6365 | -9.2557 | -8.7696 | -8.1817 | -7.8736 | -7.9735 | -7.8646 | -7.8646 | -7.8646 | -7.8646 | -7.8646 | -7.8646 | -7.8646 | -7.8646 | -7.8646 | -7.8646 | -7.8646 | -7.8646 | -7.8646 | -7.8646 | -7.8646
98% | 0.37816 | 40.5741 | 43.6075 | 43.9123 | -20.9171 | -20.775 | -20.7166 | -20.5295 | -20.1448 | -19.8212 | -19.6722 | -19.805 | -19.2483 | -19.16 | -19.2645 | -19.055 | -18.9472 | -18.9472 | -18.9472 | -18.9472 | -18.9472 | -18.9472 | -18.9472 | -18.9472 | -18.9472 | -18.9472 | -18.9472 | -18.9472 | -18.9472 | -18.9472 | -18.9472 | 98% | 0 | 49.9177 | 53.3078 | 53.4014 | -11.3795 | -11.3536 | -11.1684 | -10.7933 | -10.1325 | -9.7883 | -9.5392 | -9.1622 | -8.681 | -8.099 | -7.794 | -7.8929 | -7.7851 | -7.7851 | -7.7851 | -7.7851 | -7.7851 | -7.7851 | -7.7851 | -7.7851 | -7.7851 | -7.7851 | -7.7851 | -7.7851 | -7.7851 | -7.7851 | -7.7851
97% | 0.37816 | 40.1601 | 43.1625 | 43.4643 | -20.7036 | -20.563 | -20.5052 | -20.32 | -19.9393 | -19.6189 | -19.4715 | -19.6029 | -19.0519 | -18.9645 | -19.0679 | -18.8605 | -18.7538 | -18.7538 | -18.7538 | -18.7538 | -18.7538 | -18.7538 | -18.7538 | -18.7538 | -18.7538 | -18.7538 | -18.7538 | -18.7538 | -18.7538 | -18.7538 | -18.7538 | 97% | 0.37816 | 49.4084 | 52.7639 | 52.8564 | -11.2634 | -11.2377 | -11.0545 | -10.6831 | -10.0292 | -9.6884 | -9.4419 | -9.0687 | -8.5924 | -8.0164 | -7.7145 | -7.8124 | -7.7057 | -7.7057 | -7.7057 | -7.7057 | -7.7057 | -7.7057 | -7.7057 | -7.7057 | -7.7057 | -7.7057 | -7.7057 | -7.7057 | -7.7057 | -7.7057 | -7.7057
95% | 0.75633 | 39.332 | 42.2726 | 42.5681 | -20.2768 | -20.139 | -20.0824 | -19.9011 | -19.5281 | -19.2144 | -19.07 | -19.1987 | -18.6591 | -18.5735 | -18.6748 | -18.4717 | -18.3672 | -18.3672 | -18.3672 | -18.3672 | -18.3672 | -18.3672 | -18.3672 | -18.3672 | -18.3672 | -18.3672 | -18.3672 | -18.3672 | -18.3672 | -18.3672 | -18.3672 | 95% | 0.37816 | 48.3896 | 51.6759 | 51.7666 | -11.0311 | -11.006 | -10.8265 | -10.4629 | -9.8224 | -9.4886 | -9.2472 | -8.8818 | -8.4152 | -7.8511 | -7.5554 | -7.6513 | -7.5468 | -7.5468 | -7.5468 | -7.5468 | -7.5468 | -7.5468 | -7.5468 | -7.5468 | -7.5468 | -7.5468 | -7.5468 | -7.5468 | -7.5468 | -7.5468 | -7.5468
90% | 9.0759 | 37.2619 | 40.0477 | 40.3277 | -19.2096 | -19.0791 | -19.0255 | -18.8536 | -18.5004 | -18.2031 | -18.0663 | -18.1883 | -17.677 | -17.5959 | -17.6919 | -17.4995 | -17.4005 | -17.4005 | -17.4005 | -17.4005 | -17.4005 | -17.4005 | -17.4005 | -17.4005 | -17.4005 | -17.4005 | -17.4005 | -17.4005 | -17.4005 | -17.4005 | -17.4005 | 90% | 0.75633 | 45.8428 | 48.9562 | 49.0421 | -10.4506 | -10.4267 | -10.2567 | -9.9122 | -9.3054 | -8.9892 | -8.7605 | -8.4143 | -7.9723 | -7.4379 | -7.1578 | -7.2486 | -7.1496 | -7.1496 | -7.1496 | -7.1496 | -7.1496 | -7.1496 | -7.1496 | -7.1496 | -7.1496 | -7.1496 | -7.1496 | -7.1496 | -7.1496 | -7.1496 | -7.1496
85% | 40.4636 | 35.1918 | 37.8228 | 38.0872 | -18.1424 | -18.0191 | -17.9685 | -17.8062 | -17.4726 | -17.1919 | -17.0626 | -17.1778 | -16.695 | -16.6184 | -16.709 | -16.5273 | -16.4338 | -16.4338 | -16.4338 | -16.4338 | -16.4338 | -16.4338 | -16.4338 | -16.4338 | -16.4338 | -16.4338 | -16.4338 | -16.4338 | -16.4338 | -16.4338 | -16.4338 | 85% | 1.1345 | 43.296 | 46.2364 | 46.3175 | -9.87 | -9.8475 | -9.6869 | -9.3615 | -8.7884 | -8.4898 | -8.2738 | -7.9468 | -7.5294 | -7.0247 | -6.7601 | -6.8459 | -6.7524 | -6.7524 | -6.7524 | -6.7524 | -6.7524 | -6.7524 | -6.7524 | -6.7524 | -6.7524 | -6.7524 | -6.7524 | -6.7524 | -6.7524 | -6.7524 | -6.7524
80% | 94.5411 | 33.1217 | 35.598 | 35.8468 | -17.0752 | -16.9592 | -16.9115 | -16.7588 | -16.4448 | -16.1806 | -16.059 | -16.1674 | -15.7129 | -15.6408 | -15.7261 | -15.5551 | -15.4671 | -15.4671 | -15.4671 | -15.4671 | -15.4671 | -15.4671 | -15.4671 | -15.4671 | -15.4671 | -15.4671 | -15.4671 | -15.4671 | -15.4671 | -15.4671 | -15.4671 | 80% | 2.6471 | 40.7492 | 43.5166 | 43.5929 | -9.2894 | -9.2682 | -9.1171 | -8.8108 | -8.2715 | -7.9904 | -7.7871 | -7.4794 | -7.0865 | -6.6114 | -6.3625 | -6.4432 | -6.3552 | -6.3552 | -6.3552 | -6.3552 | -6.3552 | -6.3552 | -6.3552 | -6.3552 | -6.3552 | -6.3552 | -6.3552 | -6.3552 | -6.3552 | -6.3552 | -6.3552
75% | 197.0236 | 31.0516 | 33.3731 | 33.6064 | -16.008 | -15.8992 | -15.8546 | -15.7114 | -15.417 | -15.1693 | -15.0553 | -15.1569 | -14.7308 | -14.6633 | -14.7432 | -14.5829 | -14.5004 | -14.5004 | -14.5004 | -14.5004 | -14.5004 | -14.5004 | -14.5004 | -14.5004 | -14.5004 | -14.5004 | -14.5004 | -14.5004 | -14.5004 | -14.5004 | -14.5004 | 75% | 3.4035 | 38.2023 | 40.7968 | 40.8684 | -8.7088 | -8.689 | -8.5473 | -8.2602 | -7.7545 | -7.491 | -7.3004 | -7.0119 | -6.6436 | -6.1982 | -5.9648 | -6.0405 | -5.958 | -5.958 | -5.958 | -5.958 | -5.958 | -5.958 | -5.958 | -5.958 | -5.958 | -5.958 | -5.958 | -5.958 | -5.958 | -5.958 | -5.958
70% | 336.9444 | 28.9815 | 31.1482 | 31.366 | -14.9408 | -14.8393 | -14.7976 | -14.6639 | -14.3892 | -14.158 | -14.0516 | -14.1464 | -13.7488 | -13.6857 | -13.7604 | -13.6107 | -13.5337 | -13.5337 | -13.5337 | -13.5337 | -13.5337 | -13.5337 | -13.5337 | -13.5337 | -13.5337 | -13.5337 | -13.5337 | -13.5337 | -13.5337 | -13.5337 | -13.5337 | 70% | 5.6725 | 35.6555 | 38.077 | 38.1438 | -8.1282 | -8.1097 | -7.9775 | -7.7095 | -7.2375 | -6.9916 | -6.8137 | -6.5445 | -6.2007 | -5.785 | -5.5672 | -5.6378 | -5.5608 | -5.5608 | -5.5608 | -5.5608 | -5.5608 | -5.5608 | -5.5608 | -5.5608 | -5.5608 | -5.5608 | -5.5608 | -5.5608 | -5.5608 | -5.5608 | -5.5608
65% | 521.4885 | 26.9114 | 28.9234 | 29.1255 | -13.8736 | -13.7793 | -13.7406 | -13.6165 | -13.3614 | -13.1467 | -13.0479 | -13.136 | -12.7667 | -12.7082 | -12.7775 | -12.6385 | -12.567 | -12.567 | -12.567 | -12.567 | -12.567 | -12.567 | -12.567 | -12.567 | -12.567 | -12.567 | -12.567 | -12.567 | -12.567 | -12.567 | -12.567 | 65% | 6.4288 | 33.1087 | 35.3572 | 35.4193 | -7.5476 | -7.5304 | -7.4076 | -7.1588 | -6.7206 | -6.4922 | -6.327 | -6.077 | -5.7578 | -5.3718 | -5.1695 | -5.2351 | -5.1636 | -5.1636 | -5.1636 | -5.1636 | -5.1636 | -5.1636 | -5.1636 | -5.1636 | -5.1636 | -5.1636 | -5.1636 | -5.1636 | -5.1636 | -5.1636 | -5.1636
60% | 812.675 | 24.8413 | 26.6985 | 26.8851 | -12.8064 | -12.7194 | -12.6836 | -12.5691 | -12.3336 | -12.1354 | -12.0442 | -12.1255 | -11.7847 | -11.7306 | -11.7946 | -11.6663 | -11.6003 | -11.6003 | -11.6003 | -11.6003 | -11.6003 | -11.6003 | -11.6003 | -11.6003 | -11.6003 | -11.6003 | -11.6003 | -11.6003 | -11.6003 | -11.6003 | -11.6003 | 60% | 11.3449 | 30.5619 | 32.6374 | 32.6947 | -6.967 | -6.9512 | -6.8378 | -6.6081 | -6.2036 | -5.9928 | -5.8403 | -5.6095 | -5.3149 | -4.9586 | -4.7719 | -4.8324 | -4.7664 | -4.7664 | -4.7664 | -4.7664 | -4.7664 | -4.7664 | -4.7664 | -4.7664 | -4.7664 | -4.7664 | -4.7664 | -4.7664 | -4.7664 | -4.7664 | -4.7664
55% | 1202.1843 | 22.7712 | 24.4736 | 24.6447 | -11.7392 | -11.6594 | -11.6267 | -11.5217 | -11.3058 | -11.1241 | -11.0405 | -11.1151 | -10.8026 | -10.7531 | -10.8117 | -10.6941 | -10.6336 | -10.6336 | -10.6336 | -10.6336 | -10.6336 | -10.6336 | -10.6336 | -10.6336 | -10.6336 | -10.6336 | -10.6336 | -10.6336 | -10.6336 | -10.6336 | -10.6336 | 55% | 35.5474 | 28.0151 | 29.9176 | 29.9701 | -6.3865 | -6.3719 | -6.268 | -6.0574 | -5.6866 | -5.4934 | -5.3536 | -5.1421 | -4.872 | -4.5454 | -4.3742 | -4.4297 | -4.3692 | -4.3692 | -4.3692 | -4.3692 | -4.3692 | -4.3692 | -4.3692 | -4.3692 | -4.3692 | -4.3692 | -4.3692 | -4.3692 | -4.3692 | -4.3692 | -4.3692
50% | 1686.2345 | 20.7011 | 22.2487 | 22.4043 | -10.672 | -10.5995 | -10.5697 | -10.4742 | -10.278 | -10.1129 | -10.0369 | -10.1046 | -9.8206 | -9.7755 | -9.8288 | -9.7219 | -9.6669 | -9.6669 | -9.6669 | -9.6669 | -9.6669 | -9.6669 | -9.6669 | -9.6669 | -9.6669 | -9.6669 | -9.6669 | -9.6669 | -9.6669 | -9.6669 | -9.6669 | 50% | 95.2974 | 25.4682 | 27.1979 | 27.2456 | -5.8059 | -5.7926 | -5.6982 | -5.5068 | -5.1697 | -4.994 | -4.8669 | -4.6746 | -4.4291 | -4.1322 | -3.9766 | -4.027 | -3.972 | -3.972 | -3.972 | -3.972 | -3.972 | -3.972 | -3.972 | -3.972 | -3.972 | -3.972 | -3.972 | -3.972 | -3.972 | -3.972 | -3.972
45% | 2129.0649 | 18.631 | 20.0239 | 20.1638 | -9.6048 | -9.5395 | -9.5127 | -9.4268 | -9.2502 | -9.1016 | -9.0332 | -9.0941 | -8.8385 | -8.798 | -8.8459 | -8.7497 | -8.7002 | -8.7002 | -8.7002 | -8.7002 | -8.7002 | -8.7002 | -8.7002 | -8.7002 | -8.7002 | -8.7002 | -8.7002 | -8.7002 | -8.7002 | -8.7002 | -8.7002 | 45% | 208.7467 | 22.9214 | 24.4781 | 24.521 | -5.2253 | -5.2134 | -5.1284 | -4.9561 | -4.6527 | -4.4946 | -4.3802 | -4.2072 | -3.9862 | -3.7189 | -3.5789 | -3.6243 | -3.5748 | -3.5748 | -3.5748 | -3.5748 | -3.5748 | -3.5748 | -3.5748 | -3.5748 | -3.5748 | -3.5748 | -3.5748 | -3.5748 | -3.5748 | -3.5748 | -3.5748
40% | 2484.5393 | 16.5608 | 17.799 | 17.9234 | -8.5376 | -8.4796 | -8.4558 | -8.3794 | -8.2224 | -8.0903 | -8.0295 | -8.0837 | -7.8565 | -7.8204 | -7.8631 | -7.7775 | -7.7335 | -7.7335 | -7.7335 | -7.7335 | -7.7335 | -7.7335 | -7.7335 | -7.7335 | -7.7335 | -7.7335 | -7.7335 | -7.7335 | -7.7335 | -7.7335 | -7.7335 | 40% | 380.4333 | 20.3746 | 21.7583 | 21.7965 | -4.6447 | -4.6341 | -4.5585 | -4.4054 | -4.1357 | -3.9952 | -3.8935 | -3.7397 | -3.5433 | -3.3057 | -3.1812 | -3.2216 | -3.1776 | -3.1776 | -3.1776 | -3.1776 | -3.1776 | -3.1776 | -3.1776 | -3.1776 | -3.1776 | -3.1776 | -3.1776 | -3.1776 | -3.1776 | -3.1776 | -3.1776
35% | 2808.248 | 14.4907 | 15.5741 | 15.683 | -7.4704 | -7.4196 | -7.3988 | -7.332 | -7.1946 | -7.079 | -7.0258 | -7.0732 | -6.8744 | -6.8429 | -6.8802 | -6.8053 | -6.7668 | -6.7668 | -6.7668 | -6.7668 | -6.7668 | -6.7668 | -6.7668 | -6.7668 | -6.7668 | -6.7668 | -6.7668 | -6.7668 | -6.7668 | -6.7668 | -6.7668 | 35% | 696.5786 | 17.8278 | 19.0385 | 19.0719 | -4.0641 | -4.0548 | -3.9887 | -3.8547 | -3.6188 | -3.4958 | -3.4069 | -3.2722 | -3.1003 | -2.8925 | -2.7836 | -2.8189 | -2.7804 | -2.7804 | -2.7804 | -2.7804 | -2.7804 | -2.7804 | -2.7804 | -2.7804 | -2.7804 | -2.7804 | -2.7804 | -2.7804 | -2.7804 | -2.7804 | -2.7804
30% | 3095.6528 | 12.4206 | 13.3492 | 13.4426 | -6.4032 | -6.3597 | -6.3418 | -6.2845 | -6.1668 | -6.0677 | -6.0221 | -6.0628 | -5.8923 | -5.8653 | -5.8973 | -5.8332 | -5.8002 | -5.8002 | -5.8002 | -5.8002 | -5.8002 | -5.8002 | -5.8002 | -5.8002 | -5.8002 | -5.8002 | -5.8002 | -5.8002 | -5.8002 | -5.8002 | -5.8002 | 30% | 1260.7997 | 15.2809 | 16.3187 | 16.3474 | -3.4835 | -3.4756 | -3.4189 | -3.3041 | -3.1018 | -2.9964 | -2.9202 | -2.8048 | -2.6574 | -2.4793 | -2.3859 | -2.4162 | -2.3832 | -2.3832 | -2.3832 | -2.3832 | -2.3832 | -2.3832 | -2.3832 | -2.3832 | -2.3832 | -2.3832 | -2.3832 | -2.3832 | -2.3832 | -2.3832 | -2.3832
25% | 3358.8552 | 10.3505 | 11.1244 | 11.2021 | -5.336 | -5.2997 | -5.2849 | -5.2371 | -5.139 | -5.0564 | -5.0184 | -5.0523 | -4.9103 | -4.8878 | -4.9144 | -4.861 | -4.8335 | -4.8335 | -4.8335 | -4.8335 | -4.8335 | -4.8335 | -4.8335 | -4.8335 | -4.8335 | -4.8335 | -4.8335 | -4.8335 | -4.8335 | -4.8335 | -4.8335 | 25% | 1965.3198 | 12.7341 | 13.5989 | 13.6228 | -2.9029 | -2.8963 | -2.8491 | -2.7534 | -2.5848 | -2.497 | -2.4335 | -2.3373 | -2.2145 | -2.0661 | -1.9883 | -2.0135 | -1.986 | -1.986 | -1.986 | -1.986 | -1.986 | -1.986 | -1.986 | -1.986 | -1.986 | -1.986 | -1.986 | -1.986 | -1.986 | -1.986 | -1.986
20% | 3588.7791 | 8.2804 | 8.8995 | 8.9617 | -4.2688 | -4.2398 | -4.2279 | -4.1897 | -4.1112 | -4.0451 | -4.0147 | -4.0418 | -3.9282 | -3.9102 | -3.9315 | -3.8888 | -3.8668 | -3.8668 | -3.8668 | -3.8668 | -3.8668 | -3.8668 | -3.8668 | -3.8668 | -3.8668 | -3.8668 | -3.8668 | -3.8668 | -3.8668 | -3.8668 | -3.8668 | 20% | 2490.2118 | 10.1873 | 10.8791 | 10.8982 | -2.3223 | -2.3171 | -2.2793 | -2.2027 | -2.0679 | -1.9976 | -1.9468 | -1.8698 | -1.7716 | -1.6529 | -1.5906 | -1.6108 | -1.5888 | -1.5888 | -1.5888 | -1.5888 | -1.5888 | -1.5888 | -1.5888 | -1.5888 | -1.5888 | -1.5888 | -1.5888 | -1.5888 | -1.5888 | -1.5888 | -1.5888
15% | 3802.4419 | 6.2103 | 6.6746 | 6.7213 | -3.2016 | -3.1798 | -3.1709 | -3.1423 | -3.0834 | -3.0339 | -3.0111 | -3.0314 | -2.9462 | -2.9327 | -2.9486 | -2.9166 | -2.9001 | -2.9001 | -2.9001 | -2.9001 | -2.9001 | -2.9001 | -2.9001 | -2.9001 | -2.9001 | -2.9001 | -2.9001 | -2.9001 | -2.9001 | -2.9001 | -2.9001 | 15% | 2997.7083 | 7.6405 | 8.1594 | 8.1737 | -1.7418 | -1.7378 | -1.7095 | -1.652 | -1.5509 | -1.4982 | -1.4601 | -1.4024 | -1.3287 | -1.2396 | -1.193 | -1.2081 | -1.1916 | -1.1916 | -1.1916 | -1.1916 | -1.1916 | -1.1916 | -1.1916 | -1.1916 | -1.1916 | -1.1916 | -1.1916 | -1.1916 | -1.1916 | -1.1916 | -1.1916
10% | 4024.8025 | 4.1402 | 4.4497 | 4.4809 | -2.1344 | -2.1199 | -2.1139 | -2.0948 | -2.0556 | -2.0226 | -2.0074 | -2.0209 | -1.9641 | -1.9551 | -1.9658 | -1.9444 | -1.9334 | -1.9334 | -1.9334 | -1.9334 | -1.9334 | -1.9334 | -1.9334 | -1.9334 | -1.9334 | -1.9334 | -1.9334 | -1.9334 | -1.9334 | -1.9334 | -1.9334 | 10% | 3491.5908 | 5.0936 | 5.4396 | 5.4491 | -1.1612 | -1.1585 | -1.1396 | -1.1014 | -1.0339 | -0.9988 | -0.97339 | -0.93492 | -0.88581 | -0.82643 | -0.79531 | -0.8054 | -0.7944 | -0.7944 | -0.7944 | -0.7944 | -0.7944 | -0.7944 | -0.7944 | -0.7944 | -0.7944 | -0.7944 | -0.7944 | -0.7944 | -0.7944 | -0.7944 | -0.7944
5% | 4239.978 | 2.0701 | 2.2249 | 2.2404 | -1.0672 | -1.0599 | -1.057 | -1.0474 | -1.0278 | -1.0113 | -1.0037 | -1.0105 | -0.98206 | -0.97755 | -0.98288 | -0.97219 | -0.96669 | -0.96669 | -0.96669 | -0.96669 | -0.96669 | -0.96669 | -0.96669 | -0.96669 | -0.96669 | -0.96669 | -0.96669 | -0.96669 | -0.96669 | -0.96669 | -0.96669 | 5% | 3955.9766 | 2.5468 | 2.7198 | 2.7246 | -0.58059 | -0.57926 | -0.56982 | -0.55068 | -0.51697 | -0.4994 | -0.48669 | -0.46746 | -0.44291 | -0.41322 | -0.39766 | -0.4027 | -0.3972 | -0.3972 | -0.3972 | -0.3972 | -0.3972 | -0.3972 | -0.3972 | -0.3972 | -0.3972 | -0.3972 | -0.3972 | -0.3972 | -0.3972 | -0.3972 | -0.3972
9.992e-14% | 4391.6218 | 4.1369e-14 | 4.4462e-14 | 4.4773e-14 | -2.1327e-14 | -2.1182e-14 | -2.1123e-14 | -2.0932e-14 | -2.054e-14 | -2.021e-14 | -2.0058e-14 | -2.0193e-14 | -1.9625e-14 | -1.9535e-14 | -1.9642e-14 | -1.9428e-14 | -1.9318e-14 | -1.9318e-14 | -1.9318e-14 | -1.9318e-14 | -1.9318e-14 | -1.9318e-14 | -1.9318e-14 | -1.9318e-14 | -1.9318e-14 | -1.9318e-14 | -1.9318e-14 | -1.9318e-14 | -1.9318e-14 | -1.9318e-14 | -1.9318e-14 | 9.992e-14% | 4391.6218 | 5.0896e-14 | 5.4352e-14 | 5.4448e-14 | -1.1602e-14 | -1.1576e-14 | -1.1387e-14 | -1.1005e-14 | -1.0331e-14 | -9.98e-15 | -9.7261e-15 | -9.3418e-15 | -8.8511e-15 | -8.2577e-15 | -7.9467e-15 | -8.0476e-15 | -7.9376e-15 | -7.9376e-15 | -7.9376e-15 | -7.9376e-15 | -7.9376e-15 | -7.9376e-15 | -7.9376e-15 | -7.9376e-15 | -7.9376e-15 | -7.9376e-15 | -7.9376e-15 | -7.9376e-15 | -7.9376e-15 | -7.9376e-15 | -7.9376e-15
Option 5
Winter Season | [31 empty] | Winter Season
P50 | [31 empty] | P10
% of MD | Winter - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Winter - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 35.3126 | 39.1608 | 39.5906 | 40.1398 | 40.8558 | 41.5214 | 42.6804 | 45.6186 | 47.1999 | 46.0053 | 49.6095 | 50.225 | 50.6481 | 52.8423 | 53.2116 | 53.2116 | 53.2116 | 53.2116 | 53.2116 | 53.2116 | 53.2116 | 53.2116 | 53.2116 | 53.2116 | 53.2116 | 53.2116 | 53.2116 | 53.2116 | 53.2116 | 53.2116 | 100% | 0 | 39.1045 | 42.7623 | 43.1622 | 44.577 | 44.5406 | 44.8347 | 46.0137 | 49.435 | 50.841 | 49.463 | 53.1822 | 51.5683 | 52.9373 | 53.9333 | 53.5219 | 53.5219 | 53.5219 | 53.5219 | 53.5219 | 53.5219 | 53.5219 | 53.5219 | 53.5219 | 53.5219 | 53.5219 | 53.5219 | 53.5219 | 53.5219 | 53.5219 | 53.5219
99% | 0.2972 | 34.9595 | 38.7692 | 39.1947 | 39.7384 | 40.4472 | 41.1062 | 42.2536 | 45.1624 | 46.7279 | 45.5453 | 49.1134 | 49.7228 | 50.1416 | 52.3139 | 52.6795 | 52.6795 | 52.6795 | 52.6795 | 52.6795 | 52.6795 | 52.6795 | 52.6795 | 52.6795 | 52.6795 | 52.6795 | 52.6795 | 52.6795 | 52.6795 | 52.6795 | 52.6795 | 99% | 0.2972 | 38.7135 | 42.3347 | 42.7306 | 44.1313 | 44.0952 | 44.3864 | 45.5536 | 48.9406 | 50.3325 | 48.9684 | 52.6504 | 51.0526 | 52.408 | 53.3939 | 52.9867 | 52.9867 | 52.9867 | 52.9867 | 52.9867 | 52.9867 | 52.9867 | 52.9867 | 52.9867 | 52.9867 | 52.9867 | 52.9867 | 52.9867 | 52.9867 | 52.9867 | 52.9867
98% | 0.2972 | 34.6064 | 38.3776 | 38.7988 | 39.337 | 40.0387 | 40.691 | 41.8268 | 44.7063 | 46.2559 | 45.0852 | 48.6173 | 49.2205 | 49.6352 | 51.7854 | 52.1474 | 52.1474 | 52.1474 | 52.1474 | 52.1474 | 52.1474 | 52.1474 | 52.1474 | 52.1474 | 52.1474 | 52.1474 | 52.1474 | 52.1474 | 52.1474 | 52.1474 | 52.1474 | 98% | 0.2972 | 38.3224 | 41.9071 | 42.299 | 43.6855 | 43.6498 | 43.9381 | 45.0934 | 48.4463 | 49.8241 | 48.4737 | 52.1186 | 50.5369 | 51.8786 | 52.8546 | 52.4515 | 52.4515 | 52.4515 | 52.4515 | 52.4515 | 52.4515 | 52.4515 | 52.4515 | 52.4515 | 52.4515 | 52.4515 | 52.4515 | 52.4515 | 52.4515 | 52.4515 | 52.4515
97% | 0.2972 | 34.2532 | 37.986 | 38.4029 | 38.9356 | 39.6301 | 40.2758 | 41.4 | 44.2501 | 45.7839 | 44.6252 | 48.1212 | 48.7183 | 49.1287 | 51.257 | 51.6153 | 51.6153 | 51.6153 | 51.6153 | 51.6153 | 51.6153 | 51.6153 | 51.6153 | 51.6153 | 51.6153 | 51.6153 | 51.6153 | 51.6153 | 51.6153 | 51.6153 | 51.6153 | 97% | 0.2972 | 37.9314 | 41.4795 | 41.8674 | 43.2397 | 43.2044 | 43.4897 | 44.6333 | 47.9519 | 49.3157 | 47.9791 | 51.5867 | 50.0212 | 51.3492 | 52.3153 | 51.9163 | 51.9163 | 51.9163 | 51.9163 | 51.9163 | 51.9163 | 51.9163 | 51.9163 | 51.9163 | 51.9163 | 51.9163 | 51.9163 | 51.9163 | 51.9163 | 51.9163 | 51.9163
95% | 1.486 | 33.547 | 37.2028 | 37.6111 | 38.1328 | 38.813 | 39.4453 | 40.5464 | 43.3377 | 44.8399 | 43.7051 | 47.129 | 47.7138 | 48.1157 | 50.2002 | 50.551 | 50.551 | 50.551 | 50.551 | 50.551 | 50.551 | 50.551 | 50.551 | 50.551 | 50.551 | 50.551 | 50.551 | 50.551 | 50.551 | 50.551 | 50.551 | 95% | 1.486 | 37.1493 | 40.6242 | 41.0041 | 42.3482 | 42.3136 | 42.593 | 43.713 | 46.9632 | 48.2989 | 46.9898 | 50.5231 | 48.9899 | 50.2905 | 51.2366 | 50.8458 | 50.8458 | 50.8458 | 50.8458 | 50.8458 | 50.8458 | 50.8458 | 50.8458 | 50.8458 | 50.8458 | 50.8458 | 50.8458 | 50.8458 | 50.8458 | 50.8458 | 50.8458
90% | 8.6188 | 31.7813 | 35.2447 | 35.6316 | 36.1258 | 36.7702 | 37.3693 | 38.4124 | 41.0568 | 42.4799 | 41.4048 | 44.6486 | 45.2025 | 45.5833 | 47.5581 | 47.8904 | 47.8904 | 47.8904 | 47.8904 | 47.8904 | 47.8904 | 47.8904 | 47.8904 | 47.8904 | 47.8904 | 47.8904 | 47.8904 | 47.8904 | 47.8904 | 47.8904 | 47.8904 | 90% | 8.6188 | 35.1941 | 38.4861 | 38.846 | 40.1193 | 40.0866 | 40.3513 | 41.4123 | 44.4915 | 45.7569 | 44.5167 | 47.864 | 46.4115 | 47.6436 | 48.5399 | 48.1697 | 48.1697 | 48.1697 | 48.1697 | 48.1697 | 48.1697 | 48.1697 | 48.1697 | 48.1697 | 48.1697 | 48.1697 | 48.1697 | 48.1697 | 48.1697 | 48.1697 | 48.1697
85% | 40.1218 | 30.0157 | 33.2867 | 33.652 | 34.1188 | 34.7274 | 35.2932 | 36.2784 | 38.7758 | 40.1199 | 39.1045 | 42.1681 | 42.6913 | 43.0509 | 44.9159 | 45.2299 | 45.2299 | 45.2299 | 45.2299 | 45.2299 | 45.2299 | 45.2299 | 45.2299 | 45.2299 | 45.2299 | 45.2299 | 45.2299 | 45.2299 | 45.2299 | 45.2299 | 45.2299 | 85% | 40.1218 | 33.2388 | 36.348 | 36.6879 | 37.8905 | 37.8595 | 38.1095 | 39.1116 | 42.0197 | 43.2148 | 42.0435 | 45.2049 | 43.833 | 44.9967 | 45.8433 | 45.4936 | 45.4936 | 45.4936 | 45.4936 | 45.4936 | 45.4936 | 45.4936 | 45.4936 | 45.4936 | 45.4936 | 45.4936 | 45.4936 | 45.4936 | 45.4936 | 45.4936 | 45.4936
80% | 93.0231 | 28.2501 | 31.3286 | 31.6725 | 32.1118 | 32.6846 | 33.2171 | 34.1443 | 36.4949 | 37.7599 | 36.8043 | 39.6876 | 40.18 | 40.5185 | 42.2738 | 42.5693 | 42.5693 | 42.5693 | 42.5693 | 42.5693 | 42.5693 | 42.5693 | 42.5693 | 42.5693 | 42.5693 | 42.5693 | 42.5693 | 42.5693 | 42.5693 | 42.5693 | 42.5693 | 80% | 93.0231 | 31.2836 | 34.2099 | 34.5298 | 35.6616 | 35.6325 | 35.8678 | 36.811 | 39.548 | 40.6728 | 39.5704 | 42.5458 | 41.2546 | 42.3499 | 43.1466 | 42.8175 | 42.8175 | 42.8175 | 42.8175 | 42.8175 | 42.8175 | 42.8175 | 42.8175 | 42.8175 | 42.8175 | 42.8175 | 42.8175 | 42.8175 | 42.8175 | 42.8175 | 42.8175
75% | 197.0426 | 26.4845 | 29.3706 | 29.693 | 30.1048 | 30.6418 | 31.1411 | 32.0103 | 34.214 | 35.3999 | 34.504 | 37.2071 | 37.6688 | 37.9861 | 39.6317 | 39.9087 | 39.9087 | 39.9087 | 39.9087 | 39.9087 | 39.9087 | 39.9087 | 39.9087 | 39.9087 | 39.9087 | 39.9087 | 39.9087 | 39.9087 | 39.9087 | 39.9087 | 39.9087 | 75% | 197.0426 | 29.3284 | 32.0718 | 32.3717 | 33.4328 | 33.4055 | 33.6261 | 34.5103 | 37.0762 | 38.1307 | 37.0972 | 39.8867 | 38.6762 | 39.703 | 40.45 | 40.1414 | 40.1414 | 40.1414 | 40.1414 | 40.1414 | 40.1414 | 40.1414 | 40.1414 | 40.1414 | 40.1414 | 40.1414 | 40.1414 | 40.1414 | 40.1414 | 40.1414 | 40.1414
70% | 378.0365 | 24.7188 | 27.4126 | 27.7134 | 28.0978 | 28.599 | 29.065 | 29.8763 | 31.933 | 33.0399 | 32.2037 | 34.7267 | 35.1575 | 35.4537 | 36.9896 | 37.2481 | 37.2481 | 37.2481 | 37.2481 | 37.2481 | 37.2481 | 37.2481 | 37.2481 | 37.2481 | 37.2481 | 37.2481 | 37.2481 | 37.2481 | 37.2481 | 37.2481 | 37.2481 | 70% | 378.0365 | 27.3732 | 29.9336 | 30.2136 | 31.2039 | 31.1784 | 31.3843 | 32.2096 | 34.6045 | 35.5887 | 34.6241 | 37.2275 | 36.0978 | 37.0561 | 37.7533 | 37.4653 | 37.4653 | 37.4653 | 37.4653 | 37.4653 | 37.4653 | 37.4653 | 37.4653 | 37.4653 | 37.4653 | 37.4653 | 37.4653 | 37.4653 | 37.4653 | 37.4653 | 37.4653
65% | 616.0926 | 22.9532 | 25.4545 | 25.7339 | 26.0909 | 26.5562 | 26.9889 | 27.7423 | 29.6521 | 30.6799 | 29.9035 | 32.2462 | 32.6463 | 32.9213 | 34.3475 | 34.5875 | 34.5875 | 34.5875 | 34.5875 | 34.5875 | 34.5875 | 34.5875 | 34.5875 | 34.5875 | 34.5875 | 34.5875 | 34.5875 | 34.5875 | 34.5875 | 34.5875 | 34.5875 | 65% | 616.0926 | 25.4179 | 27.7955 | 28.0554 | 28.9751 | 28.9514 | 29.1426 | 29.9089 | 32.1327 | 33.0466 | 32.1509 | 34.5684 | 33.5194 | 34.4093 | 35.0566 | 34.7893 | 34.7893 | 34.7893 | 34.7893 | 34.7893 | 34.7893 | 34.7893 | 34.7893 | 34.7893 | 34.7893 | 34.7893 | 34.7893 | 34.7893 | 34.7893 | 34.7893 | 34.7893
60% | 934.9866 | 21.1876 | 23.4965 | 23.7544 | 24.0839 | 24.5135 | 24.9128 | 25.6083 | 27.3712 | 28.3199 | 27.6032 | 29.7657 | 30.135 | 30.3889 | 31.7054 | 31.927 | 31.927 | 31.927 | 31.927 | 31.927 | 31.927 | 31.927 | 31.927 | 31.927 | 31.927 | 31.927 | 31.927 | 31.927 | 31.927 | 31.927 | 31.927 | 60% | 934.9866 | 23.4627 | 25.6574 | 25.8973 | 26.7462 | 26.7244 | 26.9008 | 27.6082 | 29.661 | 30.5046 | 29.6778 | 31.9093 | 30.941 | 31.7624 | 32.36 | 32.1132 | 32.1132 | 32.1132 | 32.1132 | 32.1132 | 32.1132 | 32.1132 | 32.1132 | 32.1132 | 32.1132 | 32.1132 | 32.1132 | 32.1132 | 32.1132 | 32.1132 | 32.1132
55% | 1310.9428 | 19.4219 | 21.5384 | 21.7748 | 22.0769 | 22.4707 | 22.8368 | 23.4742 | 25.0902 | 25.9599 | 25.3029 | 27.2852 | 27.6238 | 27.8565 | 29.0633 | 29.2664 | 29.2664 | 29.2664 | 29.2664 | 29.2664 | 29.2664 | 29.2664 | 29.2664 | 29.2664 | 29.2664 | 29.2664 | 29.2664 | 29.2664 | 29.2664 | 29.2664 | 29.2664 | 55% | 1310.9428 | 21.5075 | 23.5193 | 23.7392 | 24.5174 | 24.4973 | 24.6591 | 25.3075 | 27.1892 | 27.9625 | 27.2046 | 29.2502 | 28.3626 | 29.1155 | 29.6633 | 29.4371 | 29.4371 | 29.4371 | 29.4371 | 29.4371 | 29.4371 | 29.4371 | 29.4371 | 29.4371 | 29.4371 | 29.4371 | 29.4371 | 29.4371 | 29.4371 | 29.4371 | 29.4371
50% | 1730.2899 | 17.6563 | 19.5804 | 19.7953 | 20.0699 | 20.4279 | 20.7607 | 21.3402 | 22.8093 | 23.6 | 23.0027 | 24.8048 | 25.1125 | 25.3241 | 26.4211 | 26.6058 | 26.6058 | 26.6058 | 26.6058 | 26.6058 | 26.6058 | 26.6058 | 26.6058 | 26.6058 | 26.6058 | 26.6058 | 26.6058 | 26.6058 | 26.6058 | 26.6058 | 26.6058 | 50% | 1730.2899 | 19.5523 | 21.3812 | 21.5811 | 22.2885 | 22.2703 | 22.4174 | 23.0068 | 24.7175 | 25.4205 | 24.7315 | 26.5911 | 25.7841 | 26.4687 | 26.9666 | 26.761 | 26.761 | 26.761 | 26.761 | 26.761 | 26.761 | 26.761 | 26.761 | 26.761 | 26.761 | 26.761 | 26.761 | 26.761 | 26.761 | 26.761 | 26.761
45% | 2168.0633 | 15.8907 | 17.6224 | 17.8158 | 18.0629 | 18.3851 | 18.6846 | 19.2062 | 20.5284 | 21.24 | 20.7024 | 22.3243 | 22.6013 | 22.7917 | 23.779 | 23.9452 | 23.9452 | 23.9452 | 23.9452 | 23.9452 | 23.9452 | 23.9452 | 23.9452 | 23.9452 | 23.9452 | 23.9452 | 23.9452 | 23.9452 | 23.9452 | 23.9452 | 23.9452 | 45% | 2168.0633 | 17.597 | 19.2431 | 19.423 | 20.0597 | 20.0433 | 20.1756 | 20.7062 | 22.2457 | 22.8784 | 22.2583 | 23.932 | 23.2057 | 23.8218 | 24.27 | 24.0849 | 24.0849 | 24.0849 | 24.0849 | 24.0849 | 24.0849 | 24.0849 | 24.0849 | 24.0849 | 24.0849 | 24.0849 | 24.0849 | 24.0849 | 24.0849 | 24.0849 | 24.0849
40% | 2609.7004 | 14.125 | 15.6643 | 15.8363 | 16.0559 | 16.3423 | 16.6086 | 17.0722 | 18.2475 | 18.88 | 18.4021 | 19.8438 | 20.09 | 20.2593 | 21.1369 | 21.2846 | 21.2846 | 21.2846 | 21.2846 | 21.2846 | 21.2846 | 21.2846 | 21.2846 | 21.2846 | 21.2846 | 21.2846 | 21.2846 | 21.2846 | 21.2846 | 21.2846 | 21.2846 | 40% | 2609.7004 | 15.6418 | 17.1049 | 17.2649 | 17.8308 | 17.8163 | 17.9339 | 18.4055 | 19.774 | 20.3364 | 19.7852 | 21.2729 | 20.6273 | 21.1749 | 21.5733 | 21.4088 | 21.4088 | 21.4088 | 21.4088 | 21.4088 | 21.4088 | 21.4088 | 21.4088 | 21.4088 | 21.4088 | 21.4088 | 21.4088 | 21.4088 | 21.4088 | 21.4088 | 21.4088
35% | 2998.1389 | 12.3594 | 13.7063 | 13.8567 | 14.0489 | 14.2995 | 14.5325 | 14.9382 | 15.9665 | 16.52 | 16.1019 | 17.3633 | 17.5788 | 17.7268 | 18.4948 | 18.6241 | 18.6241 | 18.6241 | 18.6241 | 18.6241 | 18.6241 | 18.6241 | 18.6241 | 18.6241 | 18.6241 | 18.6241 | 18.6241 | 18.6241 | 18.6241 | 18.6241 | 18.6241 | 35% | 2998.1389 | 13.6866 | 14.9668 | 15.1068 | 15.602 | 15.5892 | 15.6922 | 16.1048 | 17.3022 | 17.7943 | 17.312 | 18.6138 | 18.0489 | 18.5281 | 18.8766 | 18.7327 | 18.7327 | 18.7327 | 18.7327 | 18.7327 | 18.7327 | 18.7327 | 18.7327 | 18.7327 | 18.7327 | 18.7327 | 18.7327 | 18.7327 | 18.7327 | 18.7327 | 18.7327
30% | 3309.3057 | 10.5938 | 11.7482 | 11.8772 | 12.0419 | 12.2567 | 12.4564 | 12.8041 | 13.6856 | 14.16 | 13.8016 | 14.8829 | 15.0675 | 15.1944 | 15.8527 | 15.9635 | 15.9635 | 15.9635 | 15.9635 | 15.9635 | 15.9635 | 15.9635 | 15.9635 | 15.9635 | 15.9635 | 15.9635 | 15.9635 | 15.9635 | 15.9635 | 15.9635 | 15.9635 | 30% | 3309.3057 | 11.7314 | 12.8287 | 12.9487 | 13.3731 | 13.3622 | 13.4504 | 13.8041 | 14.8305 | 15.2523 | 14.8389 | 15.9547 | 15.4705 | 15.8812 | 16.18 | 16.0566 | 16.0566 | 16.0566 | 16.0566 | 16.0566 | 16.0566 | 16.0566 | 16.0566 | 16.0566 | 16.0566 | 16.0566 | 16.0566 | 16.0566 | 16.0566 | 16.0566 | 16.0566
25% | 3537.8514 | 8.8282 | 9.7902 | 9.8977 | 10.0349 | 10.2139 | 10.3804 | 10.6701 | 11.4047 | 11.8 | 11.5013 | 12.4024 | 12.5563 | 12.662 | 13.2106 | 13.3029 | 13.3029 | 13.3029 | 13.3029 | 13.3029 | 13.3029 | 13.3029 | 13.3029 | 13.3029 | 13.3029 | 13.3029 | 13.3029 | 13.3029 | 13.3029 | 13.3029 | 13.3029 | 25% | 3537.8514 | 9.7761 | 10.6906 | 10.7906 | 11.1443 | 11.1352 | 11.2087 | 11.5034 | 12.3587 | 12.7102 | 12.3657 | 13.2956 | 12.8921 | 13.2343 | 13.4833 | 13.3805 | 13.3805 | 13.3805 | 13.3805 | 13.3805 | 13.3805 | 13.3805 | 13.3805 | 13.3805 | 13.3805 | 13.3805 | 13.3805 | 13.3805 | 13.3805 | 13.3805 | 13.3805
20% | 3731.0305 | 7.0625 | 7.8322 | 7.9181 | 8.028 | 8.1712 | 8.3043 | 8.5361 | 9.1237 | 9.44 | 9.2011 | 9.9219 | 10.045 | 10.1296 | 10.5685 | 10.6423 | 10.6423 | 10.6423 | 10.6423 | 10.6423 | 10.6423 | 10.6423 | 10.6423 | 10.6423 | 10.6423 | 10.6423 | 10.6423 | 10.6423 | 10.6423 | 10.6423 | 10.6423 | 20% | 3731.0305 | 7.8209 | 8.5525 | 8.6324 | 8.9154 | 8.9081 | 8.9669 | 9.2027 | 9.887 | 10.1682 | 9.8926 | 10.6364 | 10.3137 | 10.5875 | 10.7867 | 10.7044 | 10.7044 | 10.7044 | 10.7044 | 10.7044 | 10.7044 | 10.7044 | 10.7044 | 10.7044 | 10.7044 | 10.7044 | 10.7044 | 10.7044 | 10.7044 | 10.7044 | 10.7044
15% | 3910.2412 | 5.2969 | 5.8741 | 5.9386 | 6.021 | 6.1284 | 6.2282 | 6.4021 | 6.8428 | 7.08 | 6.9008 | 7.4414 | 7.5338 | 7.5972 | 7.9263 | 7.9817 | 7.9817 | 7.9817 | 7.9817 | 7.9817 | 7.9817 | 7.9817 | 7.9817 | 7.9817 | 7.9817 | 7.9817 | 7.9817 | 7.9817 | 7.9817 | 7.9817 | 7.9817 | 15% | 3910.2412 | 5.8657 | 6.4144 | 6.4743 | 6.6866 | 6.6811 | 6.7252 | 6.9021 | 7.4152 | 7.6261 | 7.4194 | 7.9773 | 7.7352 | 7.9406 | 8.09 | 8.0283 | 8.0283 | 8.0283 | 8.0283 | 8.0283 | 8.0283 | 8.0283 | 8.0283 | 8.0283 | 8.0283 | 8.0283 | 8.0283 | 8.0283 | 8.0283 | 8.0283 | 8.0283
10% | 4075.1864 | 3.5313 | 3.9161 | 3.9591 | 4.014 | 4.0856 | 4.1521 | 4.268 | 4.5619 | 4.72 | 4.6005 | 4.961 | 5.0225 | 5.0648 | 5.2842 | 5.3212 | 5.3212 | 5.3212 | 5.3212 | 5.3212 | 5.3212 | 5.3212 | 5.3212 | 5.3212 | 5.3212 | 5.3212 | 5.3212 | 5.3212 | 5.3212 | 5.3212 | 5.3212 | 10% | 4075.1864 | 3.9105 | 4.2762 | 4.3162 | 4.4577 | 4.4541 | 4.4835 | 4.6014 | 4.9435 | 5.0841 | 4.9463 | 5.3182 | 5.1568 | 5.2937 | 5.3933 | 5.3522 | 5.3522 | 5.3522 | 5.3522 | 5.3522 | 5.3522 | 5.3522 | 5.3522 | 5.3522 | 5.3522 | 5.3522 | 5.3522 | 5.3522 | 5.3522 | 5.3522 | 5.3522
5% | 4251.7223 | 1.7656 | 1.958 | 1.9795 | 2.007 | 2.0428 | 2.0761 | 2.134 | 2.2809 | 2.36 | 2.3003 | 2.4805 | 2.5113 | 2.5324 | 2.6421 | 2.6606 | 2.6606 | 2.6606 | 2.6606 | 2.6606 | 2.6606 | 2.6606 | 2.6606 | 2.6606 | 2.6606 | 2.6606 | 2.6606 | 2.6606 | 2.6606 | 2.6606 | 2.6606 | 5% | 4251.7223 | 1.9552 | 2.1381 | 2.1581 | 2.2289 | 2.227 | 2.2417 | 2.3007 | 2.4717 | 2.542 | 2.4731 | 2.6591 | 2.5784 | 2.6469 | 2.6967 | 2.6761 | 2.6761 | 2.6761 | 2.6761 | 2.6761 | 2.6761 | 2.6761 | 2.6761 | 2.6761 | 2.6761 | 2.6761 | 2.6761 | 2.6761 | 2.6761 | 2.6761 | 2.6761
9.992e-14% | 4391.7028 | 3.5284e-14 | 3.9129e-14 | 3.9559e-14 | 4.0108e-14 | 4.0823e-14 | 4.1488e-14 | 4.2646e-14 | 4.5582e-14 | 4.7162e-14 | 4.5969e-14 | 4.957e-14 | 5.0185e-14 | 5.0608e-14 | 5.28e-14 | 5.3169e-14 | 5.3169e-14 | 5.3169e-14 | 5.3169e-14 | 5.3169e-14 | 5.3169e-14 | 5.3169e-14 | 5.3169e-14 | 5.3169e-14 | 5.3169e-14 | 5.3169e-14 | 5.3169e-14 | 5.3169e-14 | 5.3169e-14 | 5.3169e-14 | 5.3169e-14 | 9.992e-14% | 4391.7028 | 3.9073e-14 | 4.2728e-14 | 4.3128e-14 | 4.4541e-14 | 4.4505e-14 | 4.4799e-14 | 4.5977e-14 | 4.9395e-14 | 5.08e-14 | 4.9423e-14 | 5.314e-14 | 5.1527e-14 | 5.2895e-14 | 5.389e-14 | 5.3479e-14 | 5.3479e-14 | 5.3479e-14 | 5.3479e-14 | 5.3479e-14 | 5.3479e-14 | 5.3479e-14 | 5.3479e-14 | 5.3479e-14 | 5.3479e-14 | 5.3479e-14 | 5.3479e-14 | 5.3479e-14 | 5.3479e-14 | 5.3479e-14 | 5.3479e-14
Summer Season | [31 empty] | Summer Season
P50 | [31 empty] | P10
% of MD | Summer - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Summer - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 37.304 | 40.1217 | 40.425 | 40.2808 | 40.4237 | 40.4681 | 40.6283 | 40.9667 | 41.2687 | 41.4003 | 41.234 | 41.7626 | 41.805 | 41.6734 | 41.8953 | 42.0053 | 42.0053 | 42.0053 | 42.0053 | 42.0053 | 42.0053 | 42.0053 | 42.0053 | 42.0053 | 42.0053 | 42.0053 | 42.0053 | 42.0053 | 42.0053 | 42.0053 | 100% | 0 | 46.8384 | 50.0199 | 50.1077 | 50.013 | 50.0374 | 50.2111 | 50.5632 | 51.1833 | 51.5064 | 51.7402 | 52.0939 | 52.5456 | 53.0917 | 53.378 | 53.2852 | 53.3952 | 53.3952 | 53.3952 | 53.3952 | 53.3952 | 53.3952 | 53.3952 | 53.3952 | 53.3952 | 53.3952 | 53.3952 | 53.3952 | 53.3952 | 53.3952 | 53.3952
99% | 0.37816 | 36.931 | 39.7204 | 40.0208 | 39.878 | 40.0194 | 40.0634 | 40.222 | 40.557 | 40.856 | 40.9863 | 40.8216 | 41.345 | 41.387 | 41.2567 | 41.4764 | 41.5853 | 41.5853 | 41.5853 | 41.5853 | 41.5853 | 41.5853 | 41.5853 | 41.5853 | 41.5853 | 41.5853 | 41.5853 | 41.5853 | 41.5853 | 41.5853 | 41.5853 | 99% | 0 | 46.37 | 49.5197 | 49.6066 | 49.5129 | 49.537 | 49.709 | 50.0576 | 50.6715 | 50.9913 | 51.2227 | 51.573 | 52.0201 | 52.5608 | 52.8442 | 52.7523 | 52.8612 | 52.8612 | 52.8612 | 52.8612 | 52.8612 | 52.8612 | 52.8612 | 52.8612 | 52.8612 | 52.8612 | 52.8612 | 52.8612 | 52.8612 | 52.8612 | 52.8612
98% | 0.37816 | 36.5579 | 39.3192 | 39.6165 | 39.4752 | 39.6152 | 39.6587 | 39.8157 | 40.1474 | 40.4433 | 40.5723 | 40.4093 | 40.9273 | 40.9689 | 40.8399 | 41.0574 | 41.1652 | 41.1652 | 41.1652 | 41.1652 | 41.1652 | 41.1652 | 41.1652 | 41.1652 | 41.1652 | 41.1652 | 41.1652 | 41.1652 | 41.1652 | 41.1652 | 41.1652 | 98% | 0 | 45.9016 | 49.0195 | 49.1055 | 49.0128 | 49.0366 | 49.2069 | 49.552 | 50.1596 | 50.4763 | 50.7053 | 51.052 | 51.4947 | 52.0299 | 52.3104 | 52.2195 | 52.3273 | 52.3273 | 52.3273 | 52.3273 | 52.3273 | 52.3273 | 52.3273 | 52.3273 | 52.3273 | 52.3273 | 52.3273 | 52.3273 | 52.3273 | 52.3273 | 52.3273
97% | 0.37816 | 36.1849 | 38.918 | 39.2123 | 39.0724 | 39.211 | 39.254 | 39.4094 | 39.7377 | 40.0307 | 40.1583 | 39.9969 | 40.5097 | 40.5509 | 40.4232 | 40.6385 | 40.7452 | 40.7452 | 40.7452 | 40.7452 | 40.7452 | 40.7452 | 40.7452 | 40.7452 | 40.7452 | 40.7452 | 40.7452 | 40.7452 | 40.7452 | 40.7452 | 40.7452 | 97% | 0.37816 | 45.4332 | 48.5193 | 48.6045 | 48.5127 | 48.5363 | 48.7048 | 49.0463 | 49.6478 | 49.9612 | 50.1879 | 50.5311 | 50.9692 | 51.499 | 51.7766 | 51.6866 | 51.7933 | 51.7933 | 51.7933 | 51.7933 | 51.7933 | 51.7933 | 51.7933 | 51.7933 | 51.7933 | 51.7933 | 51.7933 | 51.7933 | 51.7933 | 51.7933 | 51.7933
95% | 0.75633 | 35.4388 | 38.1156 | 38.4038 | 38.2668 | 38.4025 | 38.4447 | 38.5968 | 38.9184 | 39.2053 | 39.3303 | 39.1723 | 39.6745 | 39.7148 | 39.5897 | 39.8005 | 39.905 | 39.905 | 39.905 | 39.905 | 39.905 | 39.905 | 39.905 | 39.905 | 39.905 | 39.905 | 39.905 | 39.905 | 39.905 | 39.905 | 39.905 | 95% | 0.37816 | 44.4964 | 47.5189 | 47.6023 | 47.5124 | 47.5355 | 47.7006 | 48.0351 | 48.6241 | 48.9311 | 49.1531 | 49.4892 | 49.9183 | 50.4371 | 50.7091 | 50.6209 | 50.7254 | 50.7254 | 50.7254 | 50.7254 | 50.7254 | 50.7254 | 50.7254 | 50.7254 | 50.7254 | 50.7254 | 50.7254 | 50.7254 | 50.7254 | 50.7254 | 50.7254
90% | 9.0759 | 33.5736 | 36.1095 | 36.3825 | 36.2528 | 36.3813 | 36.4213 | 36.5654 | 36.87 | 37.1418 | 37.2603 | 37.1106 | 37.5863 | 37.6245 | 37.5061 | 37.7058 | 37.8048 | 37.8048 | 37.8048 | 37.8048 | 37.8048 | 37.8048 | 37.8048 | 37.8048 | 37.8048 | 37.8048 | 37.8048 | 37.8048 | 37.8048 | 37.8048 | 37.8048 | 90% | 0.75633 | 42.1545 | 45.0179 | 45.0969 | 45.0117 | 45.0337 | 45.19 | 45.5069 | 46.065 | 46.3558 | 46.5661 | 46.8845 | 47.291 | 47.7826 | 48.0402 | 47.9567 | 48.0557 | 48.0557 | 48.0557 | 48.0557 | 48.0557 | 48.0557 | 48.0557 | 48.0557 | 48.0557 | 48.0557 | 48.0557 | 48.0557 | 48.0557 | 48.0557 | 48.0557
85% | 40.4636 | 31.7084 | 34.1034 | 34.3613 | 34.2387 | 34.3601 | 34.3979 | 34.534 | 34.8217 | 35.0784 | 35.1903 | 35.0489 | 35.4982 | 35.5343 | 35.4224 | 35.611 | 35.7045 | 35.7045 | 35.7045 | 35.7045 | 35.7045 | 35.7045 | 35.7045 | 35.7045 | 35.7045 | 35.7045 | 35.7045 | 35.7045 | 35.7045 | 35.7045 | 35.7045 | 85% | 1.1345 | 39.8126 | 42.5169 | 42.5915 | 42.5111 | 42.5318 | 42.6795 | 42.9787 | 43.5058 | 43.7804 | 43.9791 | 44.2798 | 44.6637 | 45.128 | 45.3713 | 45.2924 | 45.3859 | 45.3859 | 45.3859 | 45.3859 | 45.3859 | 45.3859 | 45.3859 | 45.3859 | 45.3859 | 45.3859 | 45.3859 | 45.3859 | 45.3859 | 45.3859 | 45.3859
80% | 94.5411 | 29.8432 | 32.0973 | 32.34 | 32.2247 | 32.3389 | 32.3745 | 32.5026 | 32.7733 | 33.015 | 33.1203 | 32.9872 | 33.4101 | 33.444 | 33.3387 | 33.5162 | 33.6042 | 33.6042 | 33.6042 | 33.6042 | 33.6042 | 33.6042 | 33.6042 | 33.6042 | 33.6042 | 33.6042 | 33.6042 | 33.6042 | 33.6042 | 33.6042 | 33.6042 | 80% | 2.6471 | 37.4707 | 40.0159 | 40.0862 | 40.0104 | 40.0299 | 40.1689 | 40.4506 | 40.9466 | 41.2051 | 41.3921 | 41.6751 | 42.0365 | 42.4734 | 42.7024 | 42.6281 | 42.7161 | 42.7161 | 42.7161 | 42.7161 | 42.7161 | 42.7161 | 42.7161 | 42.7161 | 42.7161 | 42.7161 | 42.7161 | 42.7161 | 42.7161 | 42.7161 | 42.7161
75% | 197.0236 | 27.978 | 30.0912 | 30.3188 | 30.2106 | 30.3178 | 30.3511 | 30.4712 | 30.725 | 30.9515 | 31.0502 | 30.9255 | 31.3219 | 31.3538 | 31.2551 | 31.4215 | 31.504 | 31.504 | 31.504 | 31.504 | 31.504 | 31.504 | 31.504 | 31.504 | 31.504 | 31.504 | 31.504 | 31.504 | 31.504 | 31.504 | 31.504 | 75% | 3.4035 | 35.1288 | 37.5149 | 37.5808 | 37.5098 | 37.528 | 37.6583 | 37.9224 | 38.3875 | 38.6298 | 38.8051 | 39.0704 | 39.4092 | 39.8188 | 40.0335 | 39.9639 | 40.0464 | 40.0464 | 40.0464 | 40.0464 | 40.0464 | 40.0464 | 40.0464 | 40.0464 | 40.0464 | 40.0464 | 40.0464 | 40.0464 | 40.0464 | 40.0464 | 40.0464
70% | 336.9444 | 26.1128 | 28.0852 | 28.2975 | 28.1966 | 28.2966 | 28.3277 | 28.4398 | 28.6767 | 28.8881 | 28.9802 | 28.8638 | 29.2338 | 29.2635 | 29.1714 | 29.3267 | 29.4037 | 29.4037 | 29.4037 | 29.4037 | 29.4037 | 29.4037 | 29.4037 | 29.4037 | 29.4037 | 29.4037 | 29.4037 | 29.4037 | 29.4037 | 29.4037 | 29.4037 | 70% | 5.6725 | 32.7869 | 35.0139 | 35.0754 | 35.0091 | 35.0262 | 35.1478 | 35.3943 | 35.8283 | 36.0545 | 36.2181 | 36.4657 | 36.7819 | 37.1642 | 37.3646 | 37.2996 | 37.3766 | 37.3766 | 37.3766 | 37.3766 | 37.3766 | 37.3766 | 37.3766 | 37.3766 | 37.3766 | 37.3766 | 37.3766 | 37.3766 | 37.3766 | 37.3766 | 37.3766
65% | 521.4885 | 24.2476 | 26.0791 | 26.2763 | 26.1825 | 26.2754 | 26.3043 | 26.4084 | 26.6283 | 26.8247 | 26.9102 | 26.8021 | 27.1457 | 27.1733 | 27.0877 | 27.232 | 27.3035 | 27.3035 | 27.3035 | 27.3035 | 27.3035 | 27.3035 | 27.3035 | 27.3035 | 27.3035 | 27.3035 | 27.3035 | 27.3035 | 27.3035 | 27.3035 | 27.3035 | 65% | 6.4288 | 30.4449 | 32.5129 | 32.57 | 32.5085 | 32.5243 | 32.6372 | 32.8661 | 33.2691 | 33.4792 | 33.6311 | 33.861 | 34.1546 | 34.5096 | 34.6957 | 34.6354 | 34.7069 | 34.7069 | 34.7069 | 34.7069 | 34.7069 | 34.7069 | 34.7069 | 34.7069 | 34.7069 | 34.7069 | 34.7069 | 34.7069 | 34.7069 | 34.7069 | 34.7069
60% | 812.675 | 22.3824 | 24.073 | 24.255 | 24.1685 | 24.2542 | 24.2809 | 24.377 | 24.58 | 24.7612 | 24.8402 | 24.7404 | 25.0576 | 25.083 | 25.004 | 25.1372 | 25.2032 | 25.2032 | 25.2032 | 25.2032 | 25.2032 | 25.2032 | 25.2032 | 25.2032 | 25.2032 | 25.2032 | 25.2032 | 25.2032 | 25.2032 | 25.2032 | 25.2032 | 60% | 11.3449 | 28.103 | 30.0119 | 30.0646 | 30.0078 | 30.0224 | 30.1267 | 30.3379 | 30.71 | 30.9038 | 31.0441 | 31.2564 | 31.5273 | 31.855 | 32.0268 | 31.9711 | 32.0371 | 32.0371 | 32.0371 | 32.0371 | 32.0371 | 32.0371 | 32.0371 | 32.0371 | 32.0371 | 32.0371 | 32.0371 | 32.0371 | 32.0371 | 32.0371 | 32.0371
55% | 1202.1843 | 20.5172 | 22.0669 | 22.2338 | 22.1545 | 22.233 | 22.2574 | 22.3455 | 22.5317 | 22.6978 | 22.7702 | 22.6787 | 22.9694 | 22.9928 | 22.9204 | 23.0424 | 23.1029 | 23.1029 | 23.1029 | 23.1029 | 23.1029 | 23.1029 | 23.1029 | 23.1029 | 23.1029 | 23.1029 | 23.1029 | 23.1029 | 23.1029 | 23.1029 | 23.1029 | 55% | 35.5474 | 25.7611 | 27.511 | 27.5592 | 27.5072 | 27.5206 | 27.6161 | 27.8098 | 28.1508 | 28.3285 | 28.4571 | 28.6517 | 28.9001 | 29.2005 | 29.3579 | 29.3068 | 29.3673 | 29.3673 | 29.3673 | 29.3673 | 29.3673 | 29.3673 | 29.3673 | 29.3673 | 29.3673 | 29.3673 | 29.3673 | 29.3673 | 29.3673 | 29.3673 | 29.3673
50% | 1686.2345 | 18.652 | 20.0608 | 20.2125 | 20.1404 | 20.2118 | 20.234 | 20.3141 | 20.4833 | 20.6344 | 20.7002 | 20.617 | 20.8813 | 20.9025 | 20.8367 | 20.9477 | 21.0027 | 21.0027 | 21.0027 | 21.0027 | 21.0027 | 21.0027 | 21.0027 | 21.0027 | 21.0027 | 21.0027 | 21.0027 | 21.0027 | 21.0027 | 21.0027 | 21.0027 | 50% | 95.2974 | 23.4192 | 25.01 | 25.0539 | 25.0065 | 25.0187 | 25.1056 | 25.2816 | 25.5916 | 25.7532 | 25.8701 | 26.047 | 26.2728 | 26.5459 | 26.689 | 26.6426 | 26.6976 | 26.6976 | 26.6976 | 26.6976 | 26.6976 | 26.6976 | 26.6976 | 26.6976 | 26.6976 | 26.6976 | 26.6976 | 26.6976 | 26.6976 | 26.6976 | 26.6976
45% | 2129.0649 | 16.7868 | 18.0547 | 18.1913 | 18.1264 | 18.1907 | 18.2106 | 18.2827 | 18.435 | 18.5709 | 18.6301 | 18.5553 | 18.7932 | 18.8123 | 18.753 | 18.8529 | 18.9024 | 18.9024 | 18.9024 | 18.9024 | 18.9024 | 18.9024 | 18.9024 | 18.9024 | 18.9024 | 18.9024 | 18.9024 | 18.9024 | 18.9024 | 18.9024 | 18.9024 | 45% | 208.7467 | 21.0773 | 22.509 | 22.5485 | 22.5059 | 22.5168 | 22.595 | 22.7534 | 23.0325 | 23.1779 | 23.2831 | 23.4423 | 23.6455 | 23.8913 | 24.0201 | 23.9783 | 24.0278 | 24.0278 | 24.0278 | 24.0278 | 24.0278 | 24.0278 | 24.0278 | 24.0278 | 24.0278 | 24.0278 | 24.0278 | 24.0278 | 24.0278 | 24.0278 | 24.0278
40% | 2484.5393 | 14.9216 | 16.0487 | 16.17 | 16.1123 | 16.1695 | 16.1872 | 16.2513 | 16.3867 | 16.5075 | 16.5601 | 16.4936 | 16.705 | 16.722 | 16.6694 | 16.7581 | 16.8021 | 16.8021 | 16.8021 | 16.8021 | 16.8021 | 16.8021 | 16.8021 | 16.8021 | 16.8021 | 16.8021 | 16.8021 | 16.8021 | 16.8021 | 16.8021 | 16.8021 | 40% | 380.4333 | 18.7353 | 20.008 | 20.0431 | 20.0052 | 20.015 | 20.0845 | 20.2253 | 20.4733 | 20.6026 | 20.6961 | 20.8376 | 21.0182 | 21.2367 | 21.3512 | 21.3141 | 21.3581 | 21.3581 | 21.3581 | 21.3581 | 21.3581 | 21.3581 | 21.3581 | 21.3581 | 21.3581 | 21.3581 | 21.3581 | 21.3581 | 21.3581 | 21.3581 | 21.3581
35% | 2808.248 | 13.0564 | 14.0426 | 14.1488 | 14.0983 | 14.1483 | 14.1638 | 14.2199 | 14.3383 | 14.444 | 14.4901 | 14.4319 | 14.6169 | 14.6318 | 14.5857 | 14.6634 | 14.7019 | 14.7019 | 14.7019 | 14.7019 | 14.7019 | 14.7019 | 14.7019 | 14.7019 | 14.7019 | 14.7019 | 14.7019 | 14.7019 | 14.7019 | 14.7019 | 14.7019 | 35% | 696.5786 | 16.3934 | 17.507 | 17.5377 | 17.5046 | 17.5131 | 17.5739 | 17.6971 | 17.9142 | 18.0272 | 18.1091 | 18.2329 | 18.391 | 18.5821 | 18.6823 | 18.6498 | 18.6883 | 18.6883 | 18.6883 | 18.6883 | 18.6883 | 18.6883 | 18.6883 | 18.6883 | 18.6883 | 18.6883 | 18.6883 | 18.6883 | 18.6883 | 18.6883 | 18.6883
30% | 3095.6528 | 11.1912 | 12.0365 | 12.1275 | 12.0843 | 12.1271 | 12.1404 | 12.1885 | 12.29 | 12.3806 | 12.4201 | 12.3702 | 12.5288 | 12.5415 | 12.502 | 12.5686 | 12.6016 | 12.6016 | 12.6016 | 12.6016 | 12.6016 | 12.6016 | 12.6016 | 12.6016 | 12.6016 | 12.6016 | 12.6016 | 12.6016 | 12.6016 | 12.6016 | 12.6016 | 30% | 1260.7997 | 14.0515 | 15.006 | 15.0323 | 15.0039 | 15.0112 | 15.0633 | 15.169 | 15.355 | 15.4519 | 15.522 | 15.6282 | 15.7637 | 15.9275 | 16.0134 | 15.9856 | 16.0186 | 16.0186 | 16.0186 | 16.0186 | 16.0186 | 16.0186 | 16.0186 | 16.0186 | 16.0186 | 16.0186 | 16.0186 | 16.0186 | 16.0186 | 16.0186 | 16.0186
25% | 3358.8552 | 9.326 | 10.0304 | 10.1063 | 10.0702 | 10.1059 | 10.117 | 10.1571 | 10.2417 | 10.3172 | 10.3501 | 10.3085 | 10.4406 | 10.4513 | 10.4184 | 10.4738 | 10.5013 | 10.5013 | 10.5013 | 10.5013 | 10.5013 | 10.5013 | 10.5013 | 10.5013 | 10.5013 | 10.5013 | 10.5013 | 10.5013 | 10.5013 | 10.5013 | 10.5013 | 25% | 1965.3198 | 11.7096 | 12.505 | 12.5269 | 12.5033 | 12.5093 | 12.5528 | 12.6408 | 12.7958 | 12.8766 | 12.935 | 13.0235 | 13.1364 | 13.2729 | 13.3445 | 13.3213 | 13.3488 | 13.3488 | 13.3488 | 13.3488 | 13.3488 | 13.3488 | 13.3488 | 13.3488 | 13.3488 | 13.3488 | 13.3488 | 13.3488 | 13.3488 | 13.3488 | 13.3488
20% | 3588.7791 | 7.4608 | 8.0243 | 8.085 | 8.0562 | 8.0847 | 8.0936 | 8.1257 | 8.1933 | 8.2537 | 8.2801 | 8.2468 | 8.3525 | 8.361 | 8.3347 | 8.3791 | 8.4011 | 8.4011 | 8.4011 | 8.4011 | 8.4011 | 8.4011 | 8.4011 | 8.4011 | 8.4011 | 8.4011 | 8.4011 | 8.4011 | 8.4011 | 8.4011 | 8.4011 | 20% | 2490.2118 | 9.3677 | 10.004 | 10.0215 | 10.0026 | 10.0075 | 10.0422 | 10.1126 | 10.2367 | 10.3013 | 10.348 | 10.4188 | 10.5091 | 10.6183 | 10.6756 | 10.657 | 10.679 | 10.679 | 10.679 | 10.679 | 10.679 | 10.679 | 10.679 | 10.679 | 10.679 | 10.679 | 10.679 | 10.679 | 10.679 | 10.679 | 10.679
15% | 3802.4419 | 5.5956 | 6.0182 | 6.0638 | 6.0421 | 6.0636 | 6.0702 | 6.0942 | 6.145 | 6.1903 | 6.21 | 6.1851 | 6.2644 | 6.2708 | 6.251 | 6.2843 | 6.3008 | 6.3008 | 6.3008 | 6.3008 | 6.3008 | 6.3008 | 6.3008 | 6.3008 | 6.3008 | 6.3008 | 6.3008 | 6.3008 | 6.3008 | 6.3008 | 6.3008 | 15% | 2997.7083 | 7.0258 | 7.503 | 7.5162 | 7.502 | 7.5056 | 7.5317 | 7.5845 | 7.6775 | 7.726 | 7.761 | 7.8141 | 7.8818 | 7.9638 | 8.0067 | 7.9928 | 8.0093 | 8.0093 | 8.0093 | 8.0093 | 8.0093 | 8.0093 | 8.0093 | 8.0093 | 8.0093 | 8.0093 | 8.0093 | 8.0093 | 8.0093 | 8.0093 | 8.0093
10% | 4024.8025 | 3.7304 | 4.0122 | 4.0425 | 4.0281 | 4.0424 | 4.0468 | 4.0628 | 4.0967 | 4.1269 | 4.14 | 4.1234 | 4.1763 | 4.1805 | 4.1673 | 4.1895 | 4.2005 | 4.2005 | 4.2005 | 4.2005 | 4.2005 | 4.2005 | 4.2005 | 4.2005 | 4.2005 | 4.2005 | 4.2005 | 4.2005 | 4.2005 | 4.2005 | 4.2005 | 10% | 3491.5908 | 4.6838 | 5.002 | 5.0108 | 5.0013 | 5.0037 | 5.0211 | 5.0563 | 5.1183 | 5.1506 | 5.174 | 5.2094 | 5.2546 | 5.3092 | 5.3378 | 5.3285 | 5.3395 | 5.3395 | 5.3395 | 5.3395 | 5.3395 | 5.3395 | 5.3395 | 5.3395 | 5.3395 | 5.3395 | 5.3395 | 5.3395 | 5.3395 | 5.3395 | 5.3395
5% | 4239.978 | 1.8652 | 2.0061 | 2.0213 | 2.014 | 2.0212 | 2.0234 | 2.0314 | 2.0483 | 2.0634 | 2.07 | 2.0617 | 2.0881 | 2.0903 | 2.0837 | 2.0948 | 2.1003 | 2.1003 | 2.1003 | 2.1003 | 2.1003 | 2.1003 | 2.1003 | 2.1003 | 2.1003 | 2.1003 | 2.1003 | 2.1003 | 2.1003 | 2.1003 | 2.1003 | 5% | 3955.9766 | 2.3419 | 2.501 | 2.5054 | 2.5007 | 2.5019 | 2.5106 | 2.5282 | 2.5592 | 2.5753 | 2.587 | 2.6047 | 2.6273 | 2.6546 | 2.6689 | 2.6643 | 2.6698 | 2.6698 | 2.6698 | 2.6698 | 2.6698 | 2.6698 | 2.6698 | 2.6698 | 2.6698 | 2.6698 | 2.6698 | 2.6698 | 2.6698 | 2.6698 | 2.6698
9.992e-14% | 4391.6218 | 3.7274e-14 | 4.009e-14 | 4.0393e-14 | 4.0249e-14 | 4.0391e-14 | 4.0436e-14 | 4.0596e-14 | 4.0934e-14 | 4.1236e-14 | 4.1367e-14 | 4.1201e-14 | 4.1729e-14 | 4.1772e-14 | 4.164e-14 | 4.1862e-14 | 4.1972e-14 | 4.1972e-14 | 4.1972e-14 | 4.1972e-14 | 4.1972e-14 | 4.1972e-14 | 4.1972e-14 | 4.1972e-14 | 4.1972e-14 | 4.1972e-14 | 4.1972e-14 | 4.1972e-14 | 4.1972e-14 | 4.1972e-14 | 4.1972e-14 | 9.992e-14% | 4391.6218 | 4.6801e-14 | 4.998e-14 | 5.0068e-14 | 4.9973e-14 | 4.9997e-14 | 5.0171e-14 | 5.0523e-14 | 5.1142e-14 | 5.1465e-14 | 5.1699e-14 | 5.2052e-14 | 5.2504e-14 | 5.3049e-14 | 5.3335e-14 | 5.3243e-14 | 5.3352e-14 | 5.3352e-14 | 5.3352e-14 | 5.3352e-14 | 5.3352e-14 | 5.3352e-14 | 5.3352e-14 | 5.3352e-14 | 5.3352e-14 | 5.3352e-14 | 5.3352e-14 | 5.3352e-14 | 5.3352e-14 | 5.3352e-14 | 5.3352e-14
Option 6
Winter Season | [31 empty] | Winter Season
P50 | [31 empty] | P10
% of MD | Winter - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Winter - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 39.4107 | 43.5366 | 43.9741 | 44.515 | 45.2331 | 45.9139 | 47.1037 | 50.096 | 51.7055 | 50.5313 | 54.1664 | 54.8213 | 55.2921 | 57.5112 | 57.8724 | 57.8724 | 57.8724 | 57.8724 | 57.8724 | 57.8724 | 57.8724 | 57.8724 | 57.8724 | 57.8724 | 57.8724 | 57.8724 | 57.8724 | 57.8724 | 57.8724 | 57.8724 | 100% | 0 | 43.2026 | 47.1382 | 47.5457 | 48.9522 | 48.918 | 49.2273 | 50.4369 | 53.9124 | 55.3465 | 53.989 | 57.7391 | 56.1646 | 57.5813 | 58.6022 | 58.1828 | 58.1828 | 58.1828 | 58.1828 | 58.1828 | 58.1828 | 58.1828 | 58.1828 | 58.1828 | 58.1828 | 58.1828 | 58.1828 | 58.1828 | 58.1828 | 58.1828 | 58.1828
99% | 0.2972 | 39.0166 | 43.1012 | 43.5344 | 44.0698 | 44.7808 | 45.4548 | 46.6326 | 49.595 | 51.1884 | 50.026 | 53.6247 | 54.2731 | 54.7392 | 56.9361 | 57.2937 | 57.2937 | 57.2937 | 57.2937 | 57.2937 | 57.2937 | 57.2937 | 57.2937 | 57.2937 | 57.2937 | 57.2937 | 57.2937 | 57.2937 | 57.2937 | 57.2937 | 57.2937 | 99% | 0.2972 | 42.7706 | 46.6668 | 47.0703 | 48.4627 | 48.4288 | 48.735 | 49.9326 | 53.3732 | 54.7931 | 53.4491 | 57.1617 | 55.6029 | 57.0055 | 58.0162 | 57.6009 | 57.6009 | 57.6009 | 57.6009 | 57.6009 | 57.6009 | 57.6009 | 57.6009 | 57.6009 | 57.6009 | 57.6009 | 57.6009 | 57.6009 | 57.6009 | 57.6009 | 57.6009
98% | 0.2972 | 38.6225 | 42.6659 | 43.0946 | 43.6247 | 44.3284 | 44.9956 | 46.1616 | 49.0941 | 50.6714 | 49.5207 | 53.083 | 53.7249 | 54.1862 | 56.361 | 56.715 | 56.715 | 56.715 | 56.715 | 56.715 | 56.715 | 56.715 | 56.715 | 56.715 | 56.715 | 56.715 | 56.715 | 56.715 | 56.715 | 56.715 | 56.715 | 98% | 0.2972 | 42.3386 | 46.1954 | 46.5948 | 47.9732 | 47.9396 | 48.2427 | 49.4282 | 52.8341 | 54.2396 | 52.9092 | 56.5843 | 55.0413 | 56.4297 | 57.4302 | 57.0191 | 57.0191 | 57.0191 | 57.0191 | 57.0191 | 57.0191 | 57.0191 | 57.0191 | 57.0191 | 57.0191 | 57.0191 | 57.0191 | 57.0191 | 57.0191 | 57.0191 | 57.0191
97% | 0.2972 | 38.2284 | 42.2305 | 42.6549 | 43.1795 | 43.8761 | 44.5365 | 45.6906 | 48.5931 | 50.1543 | 49.0154 | 52.5414 | 53.1767 | 53.6333 | 55.7859 | 56.1363 | 56.1363 | 56.1363 | 56.1363 | 56.1363 | 56.1363 | 56.1363 | 56.1363 | 56.1363 | 56.1363 | 56.1363 | 56.1363 | 56.1363 | 56.1363 | 56.1363 | 56.1363 | 97% | 0.2972 | 41.9066 | 45.724 | 46.1193 | 47.4837 | 47.4504 | 47.7504 | 48.9238 | 52.295 | 53.6861 | 52.3693 | 56.0069 | 54.4796 | 55.8539 | 56.8441 | 56.4373 | 56.4373 | 56.4373 | 56.4373 | 56.4373 | 56.4373 | 56.4373 | 56.4373 | 56.4373 | 56.4373 | 56.4373 | 56.4373 | 56.4373 | 56.4373 | 56.4373 | 56.4373
95% | 1.486 | 37.4402 | 41.3598 | 41.7754 | 42.2892 | 42.9715 | 43.6182 | 44.7485 | 47.5912 | 49.1202 | 48.0047 | 51.4581 | 52.0802 | 52.5275 | 54.6357 | 54.9788 | 54.9788 | 54.9788 | 54.9788 | 54.9788 | 54.9788 | 54.9788 | 54.9788 | 54.9788 | 54.9788 | 54.9788 | 54.9788 | 54.9788 | 54.9788 | 54.9788 | 54.9788 | 95% | 1.486 | 41.0425 | 44.7812 | 45.1684 | 46.5046 | 46.4721 | 46.7659 | 47.9151 | 51.2167 | 52.5792 | 51.2895 | 54.8521 | 53.3563 | 54.7022 | 55.6721 | 55.2736 | 55.2736 | 55.2736 | 55.2736 | 55.2736 | 55.2736 | 55.2736 | 55.2736 | 55.2736 | 55.2736 | 55.2736 | 55.2736 | 55.2736 | 55.2736 | 55.2736 | 55.2736
90% | 8.6188 | 35.4696 | 39.1829 | 39.5767 | 40.0635 | 40.7098 | 41.3225 | 42.3933 | 45.0864 | 46.5349 | 45.4782 | 48.7497 | 49.3392 | 49.7629 | 51.7601 | 52.0852 | 52.0852 | 52.0852 | 52.0852 | 52.0852 | 52.0852 | 52.0852 | 52.0852 | 52.0852 | 52.0852 | 52.0852 | 52.0852 | 52.0852 | 52.0852 | 52.0852 | 52.0852 | 90% | 8.6188 | 38.8824 | 42.4243 | 42.7911 | 44.057 | 44.0262 | 44.3045 | 45.3932 | 48.5211 | 49.8119 | 48.5901 | 51.9652 | 50.5481 | 51.8232 | 52.742 | 52.3645 | 52.3645 | 52.3645 | 52.3645 | 52.3645 | 52.3645 | 52.3645 | 52.3645 | 52.3645 | 52.3645 | 52.3645 | 52.3645 | 52.3645 | 52.3645 | 52.3645 | 52.3645
85% | 40.1218 | 33.4991 | 37.0061 | 37.378 | 37.8377 | 38.4481 | 39.0268 | 40.0381 | 42.5816 | 43.9497 | 42.9516 | 46.0414 | 46.5981 | 46.9983 | 48.8845 | 49.1916 | 49.1916 | 49.1916 | 49.1916 | 49.1916 | 49.1916 | 49.1916 | 49.1916 | 49.1916 | 49.1916 | 49.1916 | 49.1916 | 49.1916 | 49.1916 | 49.1916 | 49.1916 | 85% | 40.1218 | 36.7222 | 40.0674 | 40.4139 | 41.6094 | 41.5803 | 41.8432 | 42.8714 | 45.8255 | 47.0445 | 45.8906 | 49.0782 | 47.7399 | 48.9441 | 49.8119 | 49.4554 | 49.4554 | 49.4554 | 49.4554 | 49.4554 | 49.4554 | 49.4554 | 49.4554 | 49.4554 | 49.4554 | 49.4554 | 49.4554 | 49.4554 | 49.4554 | 49.4554 | 49.4554
80% | 93.0231 | 31.5286 | 34.8293 | 35.1793 | 35.612 | 36.1865 | 36.7311 | 37.6829 | 40.0768 | 41.3644 | 40.425 | 43.3331 | 43.857 | 44.2337 | 46.009 | 46.2979 | 46.2979 | 46.2979 | 46.2979 | 46.2979 | 46.2979 | 46.2979 | 46.2979 | 46.2979 | 46.2979 | 46.2979 | 46.2979 | 46.2979 | 46.2979 | 46.2979 | 46.2979 | 80% | 93.0231 | 34.5621 | 37.7105 | 38.0366 | 39.1618 | 39.1344 | 39.3818 | 40.3495 | 43.1299 | 44.2772 | 43.1912 | 46.1913 | 44.9317 | 46.065 | 46.8818 | 46.5462 | 46.5462 | 46.5462 | 46.5462 | 46.5462 | 46.5462 | 46.5462 | 46.5462 | 46.5462 | 46.5462 | 46.5462 | 46.5462 | 46.5462 | 46.5462 | 46.5462 | 46.5462
75% | 197.0426 | 29.558 | 32.6525 | 32.9806 | 33.3862 | 33.9248 | 34.4354 | 35.3278 | 37.572 | 38.7791 | 37.8985 | 40.6248 | 41.116 | 41.4691 | 43.1334 | 43.4043 | 43.4043 | 43.4043 | 43.4043 | 43.4043 | 43.4043 | 43.4043 | 43.4043 | 43.4043 | 43.4043 | 43.4043 | 43.4043 | 43.4043 | 43.4043 | 43.4043 | 43.4043 | 75% | 197.0426 | 32.402 | 35.3536 | 35.6593 | 36.7142 | 36.6885 | 36.9204 | 37.8277 | 40.4343 | 41.5099 | 40.4917 | 43.3043 | 42.1234 | 43.186 | 43.9517 | 43.6371 | 43.6371 | 43.6371 | 43.6371 | 43.6371 | 43.6371 | 43.6371 | 43.6371 | 43.6371 | 43.6371 | 43.6371 | 43.6371 | 43.6371 | 43.6371 | 43.6371 | 43.6371
70% | 378.0365 | 27.5875 | 30.4756 | 30.7819 | 31.1605 | 31.6632 | 32.1397 | 32.9726 | 35.0672 | 36.1938 | 35.3719 | 37.9165 | 38.3749 | 38.7045 | 40.2579 | 40.5107 | 40.5107 | 40.5107 | 40.5107 | 40.5107 | 40.5107 | 40.5107 | 40.5107 | 40.5107 | 40.5107 | 40.5107 | 40.5107 | 40.5107 | 40.5107 | 40.5107 | 40.5107 | 70% | 378.0365 | 30.2418 | 32.9967 | 33.282 | 34.2666 | 34.2426 | 34.4591 | 35.3059 | 37.7386 | 38.7426 | 37.7923 | 40.4173 | 39.3152 | 40.3069 | 41.0215 | 40.7279 | 40.7279 | 40.7279 | 40.7279 | 40.7279 | 40.7279 | 40.7279 | 40.7279 | 40.7279 | 40.7279 | 40.7279 | 40.7279 | 40.7279 | 40.7279 | 40.7279 | 40.7279
65% | 616.0926 | 25.617 | 28.2988 | 28.5832 | 28.9347 | 29.4015 | 29.844 | 30.6174 | 32.5624 | 33.6086 | 32.8454 | 35.2081 | 35.6338 | 35.9399 | 37.3823 | 37.6171 | 37.6171 | 37.6171 | 37.6171 | 37.6171 | 37.6171 | 37.6171 | 37.6171 | 37.6171 | 37.6171 | 37.6171 | 37.6171 | 37.6171 | 37.6171 | 37.6171 | 37.6171 | 65% | 616.0926 | 28.0817 | 30.6398 | 30.9047 | 31.819 | 31.7967 | 31.9977 | 32.784 | 35.043 | 35.9752 | 35.0928 | 37.5304 | 36.507 | 37.4278 | 38.0914 | 37.8188 | 37.8188 | 37.8188 | 37.8188 | 37.8188 | 37.8188 | 37.8188 | 37.8188 | 37.8188 | 37.8188 | 37.8188 | 37.8188 | 37.8188 | 37.8188 | 37.8188 | 37.8188
60% | 934.9866 | 23.6464 | 26.122 | 26.3845 | 26.709 | 27.1399 | 27.5483 | 28.2622 | 30.0576 | 31.0233 | 30.3188 | 32.4998 | 32.8928 | 33.1753 | 34.5067 | 34.7235 | 34.7235 | 34.7235 | 34.7235 | 34.7235 | 34.7235 | 34.7235 | 34.7235 | 34.7235 | 34.7235 | 34.7235 | 34.7235 | 34.7235 | 34.7235 | 34.7235 | 34.7235 | 60% | 934.9866 | 25.9216 | 28.2829 | 28.5274 | 29.3713 | 29.3508 | 29.5364 | 30.2622 | 32.3474 | 33.2079 | 32.3934 | 34.6434 | 33.6987 | 34.5488 | 35.1613 | 34.9097 | 34.9097 | 34.9097 | 34.9097 | 34.9097 | 34.9097 | 34.9097 | 34.9097 | 34.9097 | 34.9097 | 34.9097 | 34.9097 | 34.9097 | 34.9097 | 34.9097 | 34.9097
55% | 1310.9428 | 21.6759 | 23.9451 | 24.1858 | 24.4832 | 24.8782 | 25.2527 | 25.907 | 27.5528 | 28.438 | 27.7922 | 29.7915 | 30.1517 | 30.4106 | 31.6312 | 31.8298 | 31.8298 | 31.8298 | 31.8298 | 31.8298 | 31.8298 | 31.8298 | 31.8298 | 31.8298 | 31.8298 | 31.8298 | 31.8298 | 31.8298 | 31.8298 | 31.8298 | 31.8298 | 55% | 1310.9428 | 23.7614 | 25.926 | 26.1501 | 26.9237 | 26.9049 | 27.075 | 27.7403 | 29.6518 | 30.4406 | 29.6939 | 31.7565 | 30.8905 | 31.6697 | 32.2312 | 32.0005 | 32.0005 | 32.0005 | 32.0005 | 32.0005 | 32.0005 | 32.0005 | 32.0005 | 32.0005 | 32.0005 | 32.0005 | 32.0005 | 32.0005 | 32.0005 | 32.0005 | 32.0005
50% | 1730.2899 | 19.7054 | 21.7683 | 21.9871 | 22.2575 | 22.6166 | 22.957 | 23.5518 | 25.048 | 25.8527 | 25.2657 | 27.0832 | 27.4106 | 27.646 | 28.7556 | 28.9362 | 28.9362 | 28.9362 | 28.9362 | 28.9362 | 28.9362 | 28.9362 | 28.9362 | 28.9362 | 28.9362 | 28.9362 | 28.9362 | 28.9362 | 28.9362 | 28.9362 | 28.9362 | 50% | 1730.2899 | 21.6013 | 23.5691 | 23.7729 | 24.4761 | 24.459 | 24.6136 | 25.2185 | 26.9562 | 27.6733 | 26.9945 | 28.8695 | 28.0823 | 28.7906 | 29.3011 | 29.0914 | 29.0914 | 29.0914 | 29.0914 | 29.0914 | 29.0914 | 29.0914 | 29.0914 | 29.0914 | 29.0914 | 29.0914 | 29.0914 | 29.0914 | 29.0914 | 29.0914 | 29.0914
45% | 2168.0633 | 17.7348 | 19.5915 | 19.7883 | 20.0317 | 20.3549 | 20.6613 | 21.1967 | 22.5432 | 23.2675 | 22.7391 | 24.3749 | 24.6696 | 24.8814 | 25.8801 | 26.0426 | 26.0426 | 26.0426 | 26.0426 | 26.0426 | 26.0426 | 26.0426 | 26.0426 | 26.0426 | 26.0426 | 26.0426 | 26.0426 | 26.0426 | 26.0426 | 26.0426 | 26.0426 | 45% | 2168.0633 | 19.4412 | 21.2122 | 21.3956 | 22.0285 | 22.0131 | 22.1523 | 22.6966 | 24.2606 | 24.9059 | 24.295 | 25.9826 | 25.2741 | 25.9116 | 26.371 | 26.1822 | 26.1822 | 26.1822 | 26.1822 | 26.1822 | 26.1822 | 26.1822 | 26.1822 | 26.1822 | 26.1822 | 26.1822 | 26.1822 | 26.1822 | 26.1822 | 26.1822 | 26.1822
40% | 2609.7004 | 15.7643 | 17.4146 | 17.5896 | 17.806 | 18.0932 | 18.3656 | 18.8415 | 20.0384 | 20.6822 | 20.2125 | 21.6665 | 21.9285 | 22.1168 | 23.0045 | 23.149 | 23.149 | 23.149 | 23.149 | 23.149 | 23.149 | 23.149 | 23.149 | 23.149 | 23.149 | 23.149 | 23.149 | 23.149 | 23.149 | 23.149 | 23.149 | 40% | 2609.7004 | 17.2811 | 18.8553 | 19.0183 | 19.5809 | 19.5672 | 19.6909 | 20.1748 | 21.5649 | 22.1386 | 21.5956 | 23.0956 | 22.4658 | 23.0325 | 23.4409 | 23.2731 | 23.2731 | 23.2731 | 23.2731 | 23.2731 | 23.2731 | 23.2731 | 23.2731 | 23.2731 | 23.2731 | 23.2731 | 23.2731 | 23.2731 | 23.2731 | 23.2731 | 23.2731
35% | 2998.1389 | 13.7937 | 15.2378 | 15.3909 | 15.5802 | 15.8316 | 16.0699 | 16.4863 | 17.5336 | 18.0969 | 17.686 | 18.9582 | 19.1875 | 19.3522 | 20.1289 | 20.2554 | 20.2554 | 20.2554 | 20.2554 | 20.2554 | 20.2554 | 20.2554 | 20.2554 | 20.2554 | 20.2554 | 20.2554 | 20.2554 | 20.2554 | 20.2554 | 20.2554 | 20.2554 | 35% | 2998.1389 | 15.1209 | 16.4984 | 16.641 | 17.1333 | 17.1213 | 17.2295 | 17.6529 | 18.8693 | 19.3713 | 18.8961 | 20.2087 | 19.6576 | 20.1535 | 20.5108 | 20.364 | 20.364 | 20.364 | 20.364 | 20.364 | 20.364 | 20.364 | 20.364 | 20.364 | 20.364 | 20.364 | 20.364 | 20.364 | 20.364 | 20.364 | 20.364
30% | 3309.3057 | 11.8232 | 13.061 | 13.1922 | 13.3545 | 13.5699 | 13.7742 | 14.1311 | 15.0288 | 15.5116 | 15.1594 | 16.2499 | 16.4464 | 16.5876 | 17.2534 | 17.3617 | 17.3617 | 17.3617 | 17.3617 | 17.3617 | 17.3617 | 17.3617 | 17.3617 | 17.3617 | 17.3617 | 17.3617 | 17.3617 | 17.3617 | 17.3617 | 17.3617 | 17.3617 | 30% | 3309.3057 | 12.9608 | 14.1414 | 14.2637 | 14.6857 | 14.6754 | 14.7682 | 15.1311 | 16.1737 | 16.604 | 16.1967 | 17.3217 | 16.8494 | 17.2744 | 17.5807 | 17.4548 | 17.4548 | 17.4548 | 17.4548 | 17.4548 | 17.4548 | 17.4548 | 17.4548 | 17.4548 | 17.4548 | 17.4548 | 17.4548 | 17.4548 | 17.4548 | 17.4548 | 17.4548
25% | 3537.8514 | 9.8527 | 10.8842 | 10.9935 | 11.1287 | 11.3083 | 11.4785 | 11.7759 | 12.524 | 12.9264 | 12.6328 | 13.5416 | 13.7053 | 13.823 | 14.3778 | 14.4681 | 14.4681 | 14.4681 | 14.4681 | 14.4681 | 14.4681 | 14.4681 | 14.4681 | 14.4681 | 14.4681 | 14.4681 | 14.4681 | 14.4681 | 14.4681 | 14.4681 | 14.4681 | 25% | 3537.8514 | 10.8007 | 11.7845 | 11.8864 | 12.2381 | 12.2295 | 12.3068 | 12.6092 | 13.4781 | 13.8366 | 13.4972 | 14.4348 | 14.0411 | 14.3953 | 14.6506 | 14.5457 | 14.5457 | 14.5457 | 14.5457 | 14.5457 | 14.5457 | 14.5457 | 14.5457 | 14.5457 | 14.5457 | 14.5457 | 14.5457 | 14.5457 | 14.5457 | 14.5457 | 14.5457
20% | 3731.0305 | 7.8821 | 8.7073 | 8.7948 | 8.903 | 9.0466 | 9.1828 | 9.4207 | 10.0192 | 10.3411 | 10.1063 | 10.8333 | 10.9643 | 11.0584 | 11.5022 | 11.5745 | 11.5745 | 11.5745 | 11.5745 | 11.5745 | 11.5745 | 11.5745 | 11.5745 | 11.5745 | 11.5745 | 11.5745 | 11.5745 | 11.5745 | 11.5745 | 11.5745 | 11.5745 | 20% | 3731.0305 | 8.6405 | 9.4276 | 9.5091 | 9.7904 | 9.7836 | 9.8455 | 10.0874 | 10.7825 | 11.0693 | 10.7978 | 11.5478 | 11.2329 | 11.5163 | 11.7204 | 11.6366 | 11.6366 | 11.6366 | 11.6366 | 11.6366 | 11.6366 | 11.6366 | 11.6366 | 11.6366 | 11.6366 | 11.6366 | 11.6366 | 11.6366 | 11.6366 | 11.6366 | 11.6366
15% | 3910.2412 | 5.9116 | 6.5305 | 6.5961 | 6.6772 | 6.785 | 6.8871 | 7.0656 | 7.5144 | 7.7558 | 7.5797 | 8.125 | 8.2232 | 8.2938 | 8.6267 | 8.6809 | 8.6809 | 8.6809 | 8.6809 | 8.6809 | 8.6809 | 8.6809 | 8.6809 | 8.6809 | 8.6809 | 8.6809 | 8.6809 | 8.6809 | 8.6809 | 8.6809 | 8.6809 | 15% | 3910.2412 | 6.4804 | 7.0707 | 7.1319 | 7.3428 | 7.3377 | 7.3841 | 7.5655 | 8.0869 | 8.302 | 8.0983 | 8.6609 | 8.4247 | 8.6372 | 8.7903 | 8.7274 | 8.7274 | 8.7274 | 8.7274 | 8.7274 | 8.7274 | 8.7274 | 8.7274 | 8.7274 | 8.7274 | 8.7274 | 8.7274 | 8.7274 | 8.7274 | 8.7274 | 8.7274
10% | 4075.1864 | 3.9411 | 4.3537 | 4.3974 | 4.4515 | 4.5233 | 4.5914 | 4.7104 | 5.0096 | 5.1705 | 5.0531 | 5.4166 | 5.4821 | 5.5292 | 5.7511 | 5.7872 | 5.7872 | 5.7872 | 5.7872 | 5.7872 | 5.7872 | 5.7872 | 5.7872 | 5.7872 | 5.7872 | 5.7872 | 5.7872 | 5.7872 | 5.7872 | 5.7872 | 5.7872 | 10% | 4075.1864 | 4.3203 | 4.7138 | 4.7546 | 4.8952 | 4.8918 | 4.9227 | 5.0437 | 5.3912 | 5.5347 | 5.3989 | 5.7739 | 5.6165 | 5.7581 | 5.8602 | 5.8183 | 5.8183 | 5.8183 | 5.8183 | 5.8183 | 5.8183 | 5.8183 | 5.8183 | 5.8183 | 5.8183 | 5.8183 | 5.8183 | 5.8183 | 5.8183 | 5.8183 | 5.8183
5% | 4251.7223 | 1.9705 | 2.1768 | 2.1987 | 2.2257 | 2.2617 | 2.2957 | 2.3552 | 2.5048 | 2.5853 | 2.5266 | 2.7083 | 2.7411 | 2.7646 | 2.8756 | 2.8936 | 2.8936 | 2.8936 | 2.8936 | 2.8936 | 2.8936 | 2.8936 | 2.8936 | 2.8936 | 2.8936 | 2.8936 | 2.8936 | 2.8936 | 2.8936 | 2.8936 | 2.8936 | 5% | 4251.7223 | 2.1601 | 2.3569 | 2.3773 | 2.4476 | 2.4459 | 2.4614 | 2.5218 | 2.6956 | 2.7673 | 2.6994 | 2.887 | 2.8082 | 2.8791 | 2.9301 | 2.9091 | 2.9091 | 2.9091 | 2.9091 | 2.9091 | 2.9091 | 2.9091 | 2.9091 | 2.9091 | 2.9091 | 2.9091 | 2.9091 | 2.9091 | 2.9091 | 2.9091 | 2.9091
9.992e-14% | 4391.7028 | 3.9379e-14 | 4.3502e-14 | 4.3939e-14 | 4.4479e-14 | 4.5197e-14 | 4.5877e-14 | 4.7066e-14 | 5.0056e-14 | 5.1664e-14 | 5.0491e-14 | 5.4123e-14 | 5.4777e-14 | 5.5248e-14 | 5.7465e-14 | 5.7826e-14 | 5.7826e-14 | 5.7826e-14 | 5.7826e-14 | 5.7826e-14 | 5.7826e-14 | 5.7826e-14 | 5.7826e-14 | 5.7826e-14 | 5.7826e-14 | 5.7826e-14 | 5.7826e-14 | 5.7826e-14 | 5.7826e-14 | 5.7826e-14 | 5.7826e-14 | 9.992e-14% | 4391.7028 | 4.3168e-14 | 4.71e-14 | 4.7508e-14 | 4.8913e-14 | 4.8879e-14 | 4.9188e-14 | 5.0397e-14 | 5.3869e-14 | 5.5302e-14 | 5.3946e-14 | 5.7693e-14 | 5.612e-14 | 5.7535e-14 | 5.8555e-14 | 5.8136e-14 | 5.8136e-14 | 5.8136e-14 | 5.8136e-14 | 5.8136e-14 | 5.8136e-14 | 5.8136e-14 | 5.8136e-14 | 5.8136e-14 | 5.8136e-14 | 5.8136e-14 | 5.8136e-14 | 5.8136e-14 | 5.8136e-14 | 5.8136e-14 | 5.8136e-14
Summer Season | [31 empty] | Summer Season
P50 | [31 empty] | P10
% of MD | Summer - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Summer - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 41.4021 | 44.4975 | 44.8085 | 44.6561 | 44.801 | 44.8606 | 45.0515 | 45.4441 | 45.7743 | 45.9263 | 45.7908 | 46.3589 | 46.449 | 46.3423 | 46.5561 | 46.6661 | 46.6661 | 46.6661 | 46.6661 | 46.6661 | 46.6661 | 46.6661 | 46.6661 | 46.6661 | 46.6661 | 46.6661 | 46.6661 | 46.6661 | 46.6661 | 46.6661 | 100% | 0 | 50.9365 | 54.3957 | 54.4912 | 54.3883 | 54.4147 | 54.6036 | 54.9865 | 55.6607 | 56.012 | 56.2661 | 56.6508 | 57.1419 | 57.7357 | 58.0469 | 57.946 | 58.056 | 58.056 | 58.056 | 58.056 | 58.056 | 58.056 | 58.056 | 58.056 | 58.056 | 58.056 | 58.056 | 58.056 | 58.056 | 58.056 | 58.056
99% | 0.37816 | 40.9881 | 44.0525 | 44.3604 | 44.2095 | 44.353 | 44.412 | 44.601 | 44.9896 | 45.3165 | 45.467 | 45.3329 | 45.8953 | 45.9845 | 45.8789 | 46.0906 | 46.1995 | 46.1995 | 46.1995 | 46.1995 | 46.1995 | 46.1995 | 46.1995 | 46.1995 | 46.1995 | 46.1995 | 46.1995 | 46.1995 | 46.1995 | 46.1995 | 46.1995 | 99% | 0 | 50.4271 | 53.8518 | 53.9463 | 53.8444 | 53.8706 | 54.0576 | 54.4366 | 55.1041 | 55.4519 | 55.7035 | 56.0843 | 56.5704 | 57.1583 | 57.4664 | 57.3665 | 57.4754 | 57.4754 | 57.4754 | 57.4754 | 57.4754 | 57.4754 | 57.4754 | 57.4754 | 57.4754 | 57.4754 | 57.4754 | 57.4754 | 57.4754 | 57.4754 | 57.4754
98% | 0.37816 | 40.5741 | 43.6075 | 43.9123 | 43.7629 | 43.905 | 43.9634 | 44.1505 | 44.5352 | 44.8588 | 45.0078 | 44.875 | 45.4317 | 45.52 | 45.4155 | 45.625 | 45.7328 | 45.7328 | 45.7328 | 45.7328 | 45.7328 | 45.7328 | 45.7328 | 45.7328 | 45.7328 | 45.7328 | 45.7328 | 45.7328 | 45.7328 | 45.7328 | 45.7328 | 98% | 0 | 49.9177 | 53.3078 | 53.4014 | 53.3005 | 53.3264 | 53.5116 | 53.8867 | 54.5475 | 54.8917 | 55.1408 | 55.5178 | 55.999 | 56.581 | 56.886 | 56.7871 | 56.8949 | 56.8949 | 56.8949 | 56.8949 | 56.8949 | 56.8949 | 56.8949 | 56.8949 | 56.8949 | 56.8949 | 56.8949 | 56.8949 | 56.8949 | 56.8949 | 56.8949
97% | 0.37816 | 40.1601 | 43.1625 | 43.4643 | 43.3164 | 43.457 | 43.5148 | 43.7 | 44.0807 | 44.4011 | 44.5485 | 44.4171 | 44.9681 | 45.0555 | 44.9521 | 45.1595 | 45.2662 | 45.2662 | 45.2662 | 45.2662 | 45.2662 | 45.2662 | 45.2662 | 45.2662 | 45.2662 | 45.2662 | 45.2662 | 45.2662 | 45.2662 | 45.2662 | 45.2662 | 97% | 0.37816 | 49.4084 | 52.7639 | 52.8564 | 52.7566 | 52.7823 | 52.9655 | 53.3369 | 53.9908 | 54.3316 | 54.5781 | 54.9513 | 55.4276 | 56.0036 | 56.3055 | 56.2076 | 56.3143 | 56.3143 | 56.3143 | 56.3143 | 56.3143 | 56.3143 | 56.3143 | 56.3143 | 56.3143 | 56.3143 | 56.3143 | 56.3143 | 56.3143 | 56.3143 | 56.3143
95% | 0.75633 | 39.332 | 42.2726 | 42.5681 | 42.4232 | 42.561 | 42.6176 | 42.7989 | 43.1719 | 43.4856 | 43.63 | 43.5013 | 44.0409 | 44.1265 | 44.0252 | 44.2283 | 44.3328 | 44.3328 | 44.3328 | 44.3328 | 44.3328 | 44.3328 | 44.3328 | 44.3328 | 44.3328 | 44.3328 | 44.3328 | 44.3328 | 44.3328 | 44.3328 | 44.3328 | 95% | 0.37816 | 48.3896 | 51.6759 | 51.7666 | 51.6689 | 51.694 | 51.8735 | 52.2371 | 52.8776 | 53.2114 | 53.4528 | 53.8182 | 54.2848 | 54.8489 | 55.1446 | 55.0487 | 55.1532 | 55.1532 | 55.1532 | 55.1532 | 55.1532 | 55.1532 | 55.1532 | 55.1532 | 55.1532 | 55.1532 | 55.1532 | 55.1532 | 55.1532 | 55.1532 | 55.1532
90% | 9.0759 | 37.2619 | 40.0477 | 40.3277 | 40.1904 | 40.3209 | 40.3745 | 40.5464 | 40.8996 | 41.1969 | 41.3337 | 41.2117 | 41.723 | 41.8041 | 41.7081 | 41.9005 | 41.9995 | 41.9995 | 41.9995 | 41.9995 | 41.9995 | 41.9995 | 41.9995 | 41.9995 | 41.9995 | 41.9995 | 41.9995 | 41.9995 | 41.9995 | 41.9995 | 41.9995 | 90% | 0.75633 | 45.8428 | 48.9562 | 49.0421 | 48.9494 | 48.9733 | 49.1433 | 49.4878 | 50.0946 | 50.4108 | 50.6395 | 50.9857 | 51.4277 | 51.9621 | 52.2422 | 52.1514 | 52.2504 | 52.2504 | 52.2504 | 52.2504 | 52.2504 | 52.2504 | 52.2504 | 52.2504 | 52.2504 | 52.2504 | 52.2504 | 52.2504 | 52.2504 | 52.2504 | 52.2504
85% | 40.4636 | 35.1918 | 37.8228 | 38.0872 | 37.9576 | 38.0809 | 38.1315 | 38.2938 | 38.6274 | 38.9081 | 39.0374 | 38.9222 | 39.405 | 39.4816 | 39.391 | 39.5727 | 39.6662 | 39.6662 | 39.6662 | 39.6662 | 39.6662 | 39.6662 | 39.6662 | 39.6662 | 39.6662 | 39.6662 | 39.6662 | 39.6662 | 39.6662 | 39.6662 | 39.6662 | 85% | 1.1345 | 43.296 | 46.2364 | 46.3175 | 46.23 | 46.2525 | 46.4131 | 46.7385 | 47.3116 | 47.6102 | 47.8262 | 48.1532 | 48.5706 | 49.0753 | 49.3399 | 49.2541 | 49.3476 | 49.3476 | 49.3476 | 49.3476 | 49.3476 | 49.3476 | 49.3476 | 49.3476 | 49.3476 | 49.3476 | 49.3476 | 49.3476 | 49.3476 | 49.3476 | 49.3476
80% | 94.5411 | 33.1217 | 35.598 | 35.8468 | 35.7248 | 35.8408 | 35.8885 | 36.0412 | 36.3552 | 36.6194 | 36.741 | 36.6326 | 37.0871 | 37.1592 | 37.0739 | 37.2449 | 37.3329 | 37.3329 | 37.3329 | 37.3329 | 37.3329 | 37.3329 | 37.3329 | 37.3329 | 37.3329 | 37.3329 | 37.3329 | 37.3329 | 37.3329 | 37.3329 | 37.3329 | 80% | 2.6471 | 40.7492 | 43.5166 | 43.5929 | 43.5106 | 43.5318 | 43.6829 | 43.9892 | 44.5285 | 44.8096 | 45.0129 | 45.3206 | 45.7135 | 46.1886 | 46.4375 | 46.3568 | 46.4448 | 46.4448 | 46.4448 | 46.4448 | 46.4448 | 46.4448 | 46.4448 | 46.4448 | 46.4448 | 46.4448 | 46.4448 | 46.4448 | 46.4448 | 46.4448 | 46.4448
75% | 197.0236 | 31.0516 | 33.3731 | 33.6064 | 33.492 | 33.6008 | 33.6454 | 33.7886 | 34.083 | 34.3307 | 34.4447 | 34.3431 | 34.7692 | 34.8367 | 34.7568 | 34.9171 | 34.9996 | 34.9996 | 34.9996 | 34.9996 | 34.9996 | 34.9996 | 34.9996 | 34.9996 | 34.9996 | 34.9996 | 34.9996 | 34.9996 | 34.9996 | 34.9996 | 34.9996 | 75% | 3.4035 | 38.2023 | 40.7968 | 40.8684 | 40.7912 | 40.811 | 40.9527 | 41.2398 | 41.7455 | 42.009 | 42.1996 | 42.4881 | 42.8564 | 43.3018 | 43.5352 | 43.4595 | 43.542 | 43.542 | 43.542 | 43.542 | 43.542 | 43.542 | 43.542 | 43.542 | 43.542 | 43.542 | 43.542 | 43.542 | 43.542 | 43.542 | 43.542
70% | 336.9444 | 28.9815 | 31.1482 | 31.366 | 31.2592 | 31.3607 | 31.4024 | 31.5361 | 31.8108 | 32.042 | 32.1484 | 32.0536 | 32.4512 | 32.5143 | 32.4396 | 32.5893 | 32.6663 | 32.6663 | 32.6663 | 32.6663 | 32.6663 | 32.6663 | 32.6663 | 32.6663 | 32.6663 | 32.6663 | 32.6663 | 32.6663 | 32.6663 | 32.6663 | 32.6663 | 70% | 5.6725 | 35.6555 | 38.077 | 38.1438 | 38.0718 | 38.0903 | 38.2225 | 38.4905 | 38.9625 | 39.2084 | 39.3863 | 39.6555 | 39.9993 | 40.415 | 40.6328 | 40.5622 | 40.6392 | 40.6392 | 40.6392 | 40.6392 | 40.6392 | 40.6392 | 40.6392 | 40.6392 | 40.6392 | 40.6392 | 40.6392 | 40.6392 | 40.6392 | 40.6392 | 40.6392
65% | 521.4885 | 26.9114 | 28.9234 | 29.1255 | 29.0264 | 29.1207 | 29.1594 | 29.2835 | 29.5386 | 29.7533 | 29.8521 | 29.764 | 30.1333 | 30.1918 | 30.1225 | 30.2615 | 30.333 | 30.333 | 30.333 | 30.333 | 30.333 | 30.333 | 30.333 | 30.333 | 30.333 | 30.333 | 30.333 | 30.333 | 30.333 | 30.333 | 30.333 | 65% | 6.4288 | 33.1087 | 35.3572 | 35.4193 | 35.3524 | 35.3696 | 35.4924 | 35.7412 | 36.1794 | 36.4078 | 36.573 | 36.823 | 37.1422 | 37.5282 | 37.7305 | 37.6649 | 37.7364 | 37.7364 | 37.7364 | 37.7364 | 37.7364 | 37.7364 | 37.7364 | 37.7364 | 37.7364 | 37.7364 | 37.7364 | 37.7364 | 37.7364 | 37.7364 | 37.7364
60% | 812.675 | 24.8413 | 26.6985 | 26.8851 | 26.7936 | 26.8806 | 26.9164 | 27.0309 | 27.2664 | 27.4646 | 27.5558 | 27.4745 | 27.8153 | 27.8694 | 27.8054 | 27.9337 | 27.9997 | 27.9997 | 27.9997 | 27.9997 | 27.9997 | 27.9997 | 27.9997 | 27.9997 | 27.9997 | 27.9997 | 27.9997 | 27.9997 | 27.9997 | 27.9997 | 27.9997 | 60% | 11.3449 | 30.5619 | 32.6374 | 32.6947 | 32.633 | 32.6488 | 32.7622 | 32.9919 | 33.3964 | 33.6072 | 33.7597 | 33.9905 | 34.2851 | 34.6414 | 34.8281 | 34.7676 | 34.8336 | 34.8336 | 34.8336 | 34.8336 | 34.8336 | 34.8336 | 34.8336 | 34.8336 | 34.8336 | 34.8336 | 34.8336 | 34.8336 | 34.8336 | 34.8336 | 34.8336
55% | 1202.1843 | 22.7712 | 24.4736 | 24.6447 | 24.5608 | 24.6406 | 24.6733 | 24.7783 | 24.9942 | 25.1759 | 25.2595 | 25.1849 | 25.4974 | 25.5469 | 25.4883 | 25.6059 | 25.6664 | 25.6664 | 25.6664 | 25.6664 | 25.6664 | 25.6664 | 25.6664 | 25.6664 | 25.6664 | 25.6664 | 25.6664 | 25.6664 | 25.6664 | 25.6664 | 25.6664 | 55% | 35.5474 | 28.0151 | 29.9176 | 29.9701 | 29.9135 | 29.9281 | 30.032 | 30.2426 | 30.6134 | 30.8066 | 30.9464 | 31.1579 | 31.428 | 31.7546 | 31.9258 | 31.8703 | 31.9308 | 31.9308 | 31.9308 | 31.9308 | 31.9308 | 31.9308 | 31.9308 | 31.9308 | 31.9308 | 31.9308 | 31.9308 | 31.9308 | 31.9308 | 31.9308 | 31.9308
50% | 1686.2345 | 20.7011 | 22.2487 | 22.4043 | 22.328 | 22.4005 | 22.4303 | 22.5258 | 22.722 | 22.8871 | 22.9631 | 22.8954 | 23.1794 | 23.2245 | 23.1712 | 23.2781 | 23.3331 | 23.3331 | 23.3331 | 23.3331 | 23.3331 | 23.3331 | 23.3331 | 23.3331 | 23.3331 | 23.3331 | 23.3331 | 23.3331 | 23.3331 | 23.3331 | 23.3331 | 50% | 95.2974 | 25.4682 | 27.1979 | 27.2456 | 27.1941 | 27.2074 | 27.3018 | 27.4932 | 27.8303 | 28.006 | 28.1331 | 28.3254 | 28.5709 | 28.8678 | 29.0234 | 28.973 | 29.028 | 29.028 | 29.028 | 29.028 | 29.028 | 29.028 | 29.028 | 29.028 | 29.028 | 29.028 | 29.028 | 29.028 | 29.028 | 29.028 | 29.028
45% | 2129.0649 | 18.631 | 20.0239 | 20.1638 | 20.0952 | 20.1605 | 20.1873 | 20.2732 | 20.4498 | 20.5984 | 20.6668 | 20.6059 | 20.8615 | 20.902 | 20.8541 | 20.9503 | 20.9998 | 20.9998 | 20.9998 | 20.9998 | 20.9998 | 20.9998 | 20.9998 | 20.9998 | 20.9998 | 20.9998 | 20.9998 | 20.9998 | 20.9998 | 20.9998 | 20.9998 | 45% | 208.7467 | 22.9214 | 24.4781 | 24.521 | 24.4747 | 24.4866 | 24.5716 | 24.7439 | 25.0473 | 25.2054 | 25.3198 | 25.4928 | 25.7138 | 25.9811 | 26.1211 | 26.0757 | 26.1252 | 26.1252 | 26.1252 | 26.1252 | 26.1252 | 26.1252 | 26.1252 | 26.1252 | 26.1252 | 26.1252 | 26.1252 | 26.1252 | 26.1252 | 26.1252 | 26.1252
40% | 2484.5393 | 16.5608 | 17.799 | 17.9234 | 17.8624 | 17.9204 | 17.9442 | 18.0206 | 18.1776 | 18.3097 | 18.3705 | 18.3163 | 18.5435 | 18.5796 | 18.5369 | 18.6225 | 18.6665 | 18.6665 | 18.6665 | 18.6665 | 18.6665 | 18.6665 | 18.6665 | 18.6665 | 18.6665 | 18.6665 | 18.6665 | 18.6665 | 18.6665 | 18.6665 | 18.6665 | 40% | 380.4333 | 20.3746 | 21.7583 | 21.7965 | 21.7553 | 21.7659 | 21.8415 | 21.9946 | 22.2643 | 22.4048 | 22.5065 | 22.6603 | 22.8567 | 23.0943 | 23.2188 | 23.1784 | 23.2224 | 23.2224 | 23.2224 | 23.2224 | 23.2224 | 23.2224 | 23.2224 | 23.2224 | 23.2224 | 23.2224 | 23.2224 | 23.2224 | 23.2224 | 23.2224 | 23.2224
35% | 2808.248 | 14.4907 | 15.5741 | 15.683 | 15.6296 | 15.6804 | 15.7012 | 15.768 | 15.9054 | 16.021 | 16.0742 | 16.0268 | 16.2256 | 16.2571 | 16.2198 | 16.2947 | 16.3332 | 16.3332 | 16.3332 | 16.3332 | 16.3332 | 16.3332 | 16.3332 | 16.3332 | 16.3332 | 16.3332 | 16.3332 | 16.3332 | 16.3332 | 16.3332 | 16.3332 | 35% | 696.5786 | 17.8278 | 19.0385 | 19.0719 | 19.0359 | 19.0452 | 19.1113 | 19.2453 | 19.4812 | 19.6042 | 19.6931 | 19.8278 | 19.9997 | 20.2075 | 20.3164 | 20.2811 | 20.3196 | 20.3196 | 20.3196 | 20.3196 | 20.3196 | 20.3196 | 20.3196 | 20.3196 | 20.3196 | 20.3196 | 20.3196 | 20.3196 | 20.3196 | 20.3196 | 20.3196
30% | 3095.6528 | 12.4206 | 13.3492 | 13.4426 | 13.3968 | 13.4403 | 13.4582 | 13.5155 | 13.6332 | 13.7323 | 13.7779 | 13.7372 | 13.9077 | 13.9347 | 13.9027 | 13.9668 | 13.9998 | 13.9998 | 13.9998 | 13.9998 | 13.9998 | 13.9998 | 13.9998 | 13.9998 | 13.9998 | 13.9998 | 13.9998 | 13.9998 | 13.9998 | 13.9998 | 13.9998 | 30% | 1260.7997 | 15.2809 | 16.3187 | 16.3474 | 16.3165 | 16.3244 | 16.3811 | 16.4959 | 16.6982 | 16.8036 | 16.8798 | 16.9952 | 17.1426 | 17.3207 | 17.4141 | 17.3838 | 17.4168 | 17.4168 | 17.4168 | 17.4168 | 17.4168 | 17.4168 | 17.4168 | 17.4168 | 17.4168 | 17.4168 | 17.4168 | 17.4168 | 17.4168 | 17.4168 | 17.4168
25% | 3358.8552 | 10.3505 | 11.1244 | 11.2021 | 11.164 | 11.2003 | 11.2151 | 11.2629 | 11.361 | 11.4436 | 11.4816 | 11.4477 | 11.5897 | 11.6122 | 11.5856 | 11.639 | 11.6665 | 11.6665 | 11.6665 | 11.6665 | 11.6665 | 11.6665 | 11.6665 | 11.6665 | 11.6665 | 11.6665 | 11.6665 | 11.6665 | 11.6665 | 11.6665 | 11.6665 | 25% | 1965.3198 | 12.7341 | 13.5989 | 13.6228 | 13.5971 | 13.6037 | 13.6509 | 13.7466 | 13.9152 | 14.003 | 14.0665 | 14.1627 | 14.2855 | 14.4339 | 14.5117 | 14.4865 | 14.514 | 14.514 | 14.514 | 14.514 | 14.514 | 14.514 | 14.514 | 14.514 | 14.514 | 14.514 | 14.514 | 14.514 | 14.514 | 14.514 | 14.514
20% | 3588.7791 | 8.2804 | 8.8995 | 8.9617 | 8.9312 | 8.9602 | 8.9721 | 9.0103 | 9.0888 | 9.1549 | 9.1853 | 9.1582 | 9.2718 | 9.2898 | 9.2685 | 9.3112 | 9.3332 | 9.3332 | 9.3332 | 9.3332 | 9.3332 | 9.3332 | 9.3332 | 9.3332 | 9.3332 | 9.3332 | 9.3332 | 9.3332 | 9.3332 | 9.3332 | 9.3332 | 20% | 2490.2118 | 10.1873 | 10.8791 | 10.8982 | 10.8777 | 10.8829 | 10.9207 | 10.9973 | 11.1321 | 11.2024 | 11.2532 | 11.3302 | 11.4284 | 11.5471 | 11.6094 | 11.5892 | 11.6112 | 11.6112 | 11.6112 | 11.6112 | 11.6112 | 11.6112 | 11.6112 | 11.6112 | 11.6112 | 11.6112 | 11.6112 | 11.6112 | 11.6112 | 11.6112 | 11.6112
15% | 3802.4419 | 6.2103 | 6.6746 | 6.7213 | 6.6984 | 6.7202 | 6.7291 | 6.7577 | 6.8166 | 6.8661 | 6.8889 | 6.8686 | 6.9538 | 6.9673 | 6.9514 | 6.9834 | 6.9999 | 6.9999 | 6.9999 | 6.9999 | 6.9999 | 6.9999 | 6.9999 | 6.9999 | 6.9999 | 6.9999 | 6.9999 | 6.9999 | 6.9999 | 6.9999 | 6.9999 | 15% | 2997.7083 | 7.6405 | 8.1594 | 8.1737 | 8.1582 | 8.1622 | 8.1905 | 8.248 | 8.3491 | 8.4018 | 8.4399 | 8.4976 | 8.5713 | 8.6604 | 8.707 | 8.6919 | 8.7084 | 8.7084 | 8.7084 | 8.7084 | 8.7084 | 8.7084 | 8.7084 | 8.7084 | 8.7084 | 8.7084 | 8.7084 | 8.7084 | 8.7084 | 8.7084 | 8.7084
10% | 4024.8025 | 4.1402 | 4.4497 | 4.4809 | 4.4656 | 4.4801 | 4.4861 | 4.5052 | 4.5444 | 4.5774 | 4.5926 | 4.5791 | 4.6359 | 4.6449 | 4.6342 | 4.6556 | 4.6666 | 4.6666 | 4.6666 | 4.6666 | 4.6666 | 4.6666 | 4.6666 | 4.6666 | 4.6666 | 4.6666 | 4.6666 | 4.6666 | 4.6666 | 4.6666 | 4.6666 | 10% | 3491.5908 | 5.0936 | 5.4396 | 5.4491 | 5.4388 | 5.4415 | 5.4604 | 5.4986 | 5.5661 | 5.6012 | 5.6266 | 5.6651 | 5.7142 | 5.7736 | 5.8047 | 5.7946 | 5.8056 | 5.8056 | 5.8056 | 5.8056 | 5.8056 | 5.8056 | 5.8056 | 5.8056 | 5.8056 | 5.8056 | 5.8056 | 5.8056 | 5.8056 | 5.8056 | 5.8056
5% | 4239.978 | 2.0701 | 2.2249 | 2.2404 | 2.2328 | 2.2401 | 2.243 | 2.2526 | 2.2722 | 2.2887 | 2.2963 | 2.2895 | 2.3179 | 2.3224 | 2.3171 | 2.3278 | 2.3333 | 2.3333 | 2.3333 | 2.3333 | 2.3333 | 2.3333 | 2.3333 | 2.3333 | 2.3333 | 2.3333 | 2.3333 | 2.3333 | 2.3333 | 2.3333 | 2.3333 | 5% | 3955.9766 | 2.5468 | 2.7198 | 2.7246 | 2.7194 | 2.7207 | 2.7302 | 2.7493 | 2.783 | 2.8006 | 2.8133 | 2.8325 | 2.8571 | 2.8868 | 2.9023 | 2.8973 | 2.9028 | 2.9028 | 2.9028 | 2.9028 | 2.9028 | 2.9028 | 2.9028 | 2.9028 | 2.9028 | 2.9028 | 2.9028 | 2.9028 | 2.9028 | 2.9028 | 2.9028
9.992e-14% | 4391.6218 | 4.1369e-14 | 4.4462e-14 | 4.4773e-14 | 4.462e-14 | 4.4765e-14 | 4.4825e-14 | 4.5015e-14 | 4.5408e-14 | 4.5738e-14 | 4.589e-14 | 4.5754e-14 | 4.6322e-14 | 4.6412e-14 | 4.6305e-14 | 4.6519e-14 | 4.6629e-14 | 4.6629e-14 | 4.6629e-14 | 4.6629e-14 | 4.6629e-14 | 4.6629e-14 | 4.6629e-14 | 4.6629e-14 | 4.6629e-14 | 4.6629e-14 | 4.6629e-14 | 4.6629e-14 | 4.6629e-14 | 4.6629e-14 | 4.6629e-14 | 9.992e-14% | 4391.6218 | 5.0896e-14 | 5.4352e-14 | 5.4448e-14 | 5.4345e-14 | 5.4371e-14 | 5.456e-14 | 5.4943e-14 | 5.5616e-14 | 5.5967e-14 | 5.6221e-14 | 5.6605e-14 | 5.7096e-14 | 5.769e-14 | 5.8001e-14 | 5.79e-14 | 5.801e-14 | 5.801e-14 | 5.801e-14 | 5.801e-14 | 5.801e-14 | 5.801e-14 | 5.801e-14 | 5.801e-14 | 5.801e-14 | 5.801e-14 | 5.801e-14 | 5.801e-14 | 5.801e-14 | 5.801e-14 | 5.801e-14
Option 7
Winter Season | [31 empty] | Winter Season
P50 | [31 empty] | P10
% of MD | Winter - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Winter - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 39.4107 | 43.5366 | 43.9741 | 44.515 | 45.2331 | 45.9139 | 47.1037 | 50.096 | 51.7055 | 50.5313 | 54.1664 | 54.8213 | 55.2921 | 57.5112 | 57.8724 | 57.8724 | 57.8724 | 57.8724 | 57.8724 | 57.8724 | 57.8724 | 57.8724 | 57.8724 | 57.8724 | 57.8724 | 57.8724 | 57.8724 | 57.8724 | 57.8724 | 57.8724 | 100% | 0 | 43.2026 | 47.1382 | 47.5457 | 48.9522 | 48.918 | 49.2273 | 50.4369 | 53.9124 | 55.3465 | 53.989 | 57.7391 | 56.1646 | 57.5813 | 58.6022 | 58.1828 | 58.1828 | 58.1828 | 58.1828 | 58.1828 | 58.1828 | 58.1828 | 58.1828 | 58.1828 | 58.1828 | 58.1828 | 58.1828 | 58.1828 | 58.1828 | 58.1828 | 58.1828
99% | 0.2972 | 39.0166 | 43.1012 | 43.5344 | 44.0698 | 44.7808 | 45.4548 | 46.6326 | 49.595 | 51.1884 | 50.026 | 53.6247 | 54.2731 | 54.7392 | 56.9361 | 57.2937 | 57.2937 | 57.2937 | 57.2937 | 57.2937 | 57.2937 | 57.2937 | 57.2937 | 57.2937 | 57.2937 | 57.2937 | 57.2937 | 57.2937 | 57.2937 | 57.2937 | 57.2937 | 99% | 0.2972 | 42.7706 | 46.6668 | 47.0703 | 48.4627 | 48.4288 | 48.735 | 49.9326 | 53.3732 | 54.7931 | 53.4491 | 57.1617 | 55.6029 | 57.0055 | 58.0162 | 57.6009 | 57.6009 | 57.6009 | 57.6009 | 57.6009 | 57.6009 | 57.6009 | 57.6009 | 57.6009 | 57.6009 | 57.6009 | 57.6009 | 57.6009 | 57.6009 | 57.6009 | 57.6009
98% | 0.2972 | 38.6225 | 42.6659 | 43.0946 | 43.6247 | 44.3284 | 44.9956 | 46.1616 | 49.0941 | 50.6714 | 49.5207 | 53.083 | 53.7249 | 54.1862 | 56.361 | 56.715 | 56.715 | 56.715 | 56.715 | 56.715 | 56.715 | 56.715 | 56.715 | 56.715 | 56.715 | 56.715 | 56.715 | 56.715 | 56.715 | 56.715 | 56.715 | 98% | 0.2972 | 42.3386 | 46.1954 | 46.5948 | 47.9732 | 47.9396 | 48.2427 | 49.4282 | 52.8341 | 54.2396 | 52.9092 | 56.5843 | 55.0413 | 56.4297 | 57.4302 | 57.0191 | 57.0191 | 57.0191 | 57.0191 | 57.0191 | 57.0191 | 57.0191 | 57.0191 | 57.0191 | 57.0191 | 57.0191 | 57.0191 | 57.0191 | 57.0191 | 57.0191 | 57.0191
97% | 0.2972 | 38.2284 | 42.2305 | 42.6549 | 43.1795 | 43.8761 | 44.5365 | 45.6906 | 48.5931 | 50.1543 | 49.0154 | 52.5414 | 53.1767 | 53.6333 | 55.7859 | 56.1363 | 56.1363 | 56.1363 | 56.1363 | 56.1363 | 56.1363 | 56.1363 | 56.1363 | 56.1363 | 56.1363 | 56.1363 | 56.1363 | 56.1363 | 56.1363 | 56.1363 | 56.1363 | 97% | 0.2972 | 41.9066 | 45.724 | 46.1193 | 47.4837 | 47.4504 | 47.7504 | 48.9238 | 52.295 | 53.6861 | 52.3693 | 56.0069 | 54.4796 | 55.8539 | 56.8441 | 56.4373 | 56.4373 | 56.4373 | 56.4373 | 56.4373 | 56.4373 | 56.4373 | 56.4373 | 56.4373 | 56.4373 | 56.4373 | 56.4373 | 56.4373 | 56.4373 | 56.4373 | 56.4373
95% | 1.486 | 37.4402 | 41.3598 | 41.7754 | 42.2892 | 42.9715 | 43.6182 | 44.7485 | 47.5912 | 49.1202 | 48.0047 | 51.4581 | 52.0802 | 52.5275 | 54.6357 | 54.9788 | 54.9788 | 54.9788 | 54.9788 | 54.9788 | 54.9788 | 54.9788 | 54.9788 | 54.9788 | 54.9788 | 54.9788 | 54.9788 | 54.9788 | 54.9788 | 54.9788 | 54.9788 | 95% | 1.486 | 41.0425 | 44.7812 | 45.1684 | 46.5046 | 46.4721 | 46.7659 | 47.9151 | 51.2167 | 52.5792 | 51.2895 | 54.8521 | 53.3563 | 54.7022 | 55.6721 | 55.2736 | 55.2736 | 55.2736 | 55.2736 | 55.2736 | 55.2736 | 55.2736 | 55.2736 | 55.2736 | 55.2736 | 55.2736 | 55.2736 | 55.2736 | 55.2736 | 55.2736 | 55.2736
90% | 8.6188 | 35.4696 | 39.1829 | 39.5767 | 40.0635 | 40.7098 | 41.3225 | 42.3933 | 45.0864 | 46.5349 | 45.4782 | 48.7497 | 49.3392 | 49.7629 | 51.7601 | 52.0852 | 52.0852 | 52.0852 | 52.0852 | 52.0852 | 52.0852 | 52.0852 | 52.0852 | 52.0852 | 52.0852 | 52.0852 | 52.0852 | 52.0852 | 52.0852 | 52.0852 | 52.0852 | 90% | 8.6188 | 38.8824 | 42.4243 | 42.7911 | 44.057 | 44.0262 | 44.3045 | 45.3932 | 48.5211 | 49.8119 | 48.5901 | 51.9652 | 50.5481 | 51.8232 | 52.742 | 52.3645 | 52.3645 | 52.3645 | 52.3645 | 52.3645 | 52.3645 | 52.3645 | 52.3645 | 52.3645 | 52.3645 | 52.3645 | 52.3645 | 52.3645 | 52.3645 | 52.3645 | 52.3645
85% | 40.1218 | 33.4991 | 37.0061 | 37.378 | 37.8377 | 38.4481 | 39.0268 | 40.0381 | 42.5816 | 43.9497 | 42.9516 | 46.0414 | 46.5981 | 46.9983 | 48.8845 | 49.1916 | 49.1916 | 49.1916 | 49.1916 | 49.1916 | 49.1916 | 49.1916 | 49.1916 | 49.1916 | 49.1916 | 49.1916 | 49.1916 | 49.1916 | 49.1916 | 49.1916 | 49.1916 | 85% | 40.1218 | 36.7222 | 40.0674 | 40.4139 | 41.6094 | 41.5803 | 41.8432 | 42.8714 | 45.8255 | 47.0445 | 45.8906 | 49.0782 | 47.7399 | 48.9441 | 49.8119 | 49.4554 | 49.4554 | 49.4554 | 49.4554 | 49.4554 | 49.4554 | 49.4554 | 49.4554 | 49.4554 | 49.4554 | 49.4554 | 49.4554 | 49.4554 | 49.4554 | 49.4554 | 49.4554
80% | 93.0231 | 31.5286 | 34.8293 | 35.1793 | 35.612 | 36.1865 | 36.7311 | 37.6829 | 40.0768 | 41.3644 | 40.425 | 43.3331 | 43.857 | 44.2337 | 46.009 | 46.2979 | 46.2979 | 46.2979 | 46.2979 | 46.2979 | 46.2979 | 46.2979 | 46.2979 | 46.2979 | 46.2979 | 46.2979 | 46.2979 | 46.2979 | 46.2979 | 46.2979 | 46.2979 | 80% | 93.0231 | 34.5621 | 37.7105 | 38.0366 | 39.1618 | 39.1344 | 39.3818 | 40.3495 | 43.1299 | 44.2772 | 43.1912 | 46.1913 | 44.9317 | 46.065 | 46.8818 | 46.5462 | 46.5462 | 46.5462 | 46.5462 | 46.5462 | 46.5462 | 46.5462 | 46.5462 | 46.5462 | 46.5462 | 46.5462 | 46.5462 | 46.5462 | 46.5462 | 46.5462 | 46.5462
75% | 197.0426 | 29.558 | 32.6525 | 32.9806 | 33.3862 | 33.9248 | 34.4354 | 35.3278 | 37.572 | 38.7791 | 37.8985 | 40.6248 | 41.116 | 41.4691 | 43.1334 | 43.4043 | 43.4043 | 43.4043 | 43.4043 | 43.4043 | 43.4043 | 43.4043 | 43.4043 | 43.4043 | 43.4043 | 43.4043 | 43.4043 | 43.4043 | 43.4043 | 43.4043 | 43.4043 | 75% | 197.0426 | 32.402 | 35.3536 | 35.6593 | 36.7142 | 36.6885 | 36.9204 | 37.8277 | 40.4343 | 41.5099 | 40.4917 | 43.3043 | 42.1234 | 43.186 | 43.9517 | 43.6371 | 43.6371 | 43.6371 | 43.6371 | 43.6371 | 43.6371 | 43.6371 | 43.6371 | 43.6371 | 43.6371 | 43.6371 | 43.6371 | 43.6371 | 43.6371 | 43.6371 | 43.6371
70% | 378.0365 | 27.5875 | 30.4756 | 30.7819 | 31.1605 | 31.6632 | 32.1397 | 32.9726 | 35.0672 | 36.1938 | 35.3719 | 37.9165 | 38.3749 | 38.7045 | 40.2579 | 40.5107 | 40.5107 | 40.5107 | 40.5107 | 40.5107 | 40.5107 | 40.5107 | 40.5107 | 40.5107 | 40.5107 | 40.5107 | 40.5107 | 40.5107 | 40.5107 | 40.5107 | 40.5107 | 70% | 378.0365 | 30.2418 | 32.9967 | 33.282 | 34.2666 | 34.2426 | 34.4591 | 35.3059 | 37.7386 | 38.7426 | 37.7923 | 40.4173 | 39.3152 | 40.3069 | 41.0215 | 40.7279 | 40.7279 | 40.7279 | 40.7279 | 40.7279 | 40.7279 | 40.7279 | 40.7279 | 40.7279 | 40.7279 | 40.7279 | 40.7279 | 40.7279 | 40.7279 | 40.7279 | 40.7279
65% | 616.0926 | 25.617 | 28.2988 | 28.5832 | 28.9347 | 29.4015 | 29.844 | 30.6174 | 32.5624 | 33.6086 | 32.8454 | 35.2081 | 35.6338 | 35.9399 | 37.3823 | 37.6171 | 37.6171 | 37.6171 | 37.6171 | 37.6171 | 37.6171 | 37.6171 | 37.6171 | 37.6171 | 37.6171 | 37.6171 | 37.6171 | 37.6171 | 37.6171 | 37.6171 | 37.6171 | 65% | 616.0926 | 28.0817 | 30.6398 | 30.9047 | 31.819 | 31.7967 | 31.9977 | 32.784 | 35.043 | 35.9752 | 35.0928 | 37.5304 | 36.507 | 37.4278 | 38.0914 | 37.8188 | 37.8188 | 37.8188 | 37.8188 | 37.8188 | 37.8188 | 37.8188 | 37.8188 | 37.8188 | 37.8188 | 37.8188 | 37.8188 | 37.8188 | 37.8188 | 37.8188 | 37.8188
60% | 934.9866 | 23.6464 | 26.122 | 26.3845 | 26.709 | 27.1399 | 27.5483 | 28.2622 | 30.0576 | 31.0233 | 30.3188 | 32.4998 | 32.8928 | 33.1753 | 34.5067 | 34.7235 | 34.7235 | 34.7235 | 34.7235 | 34.7235 | 34.7235 | 34.7235 | 34.7235 | 34.7235 | 34.7235 | 34.7235 | 34.7235 | 34.7235 | 34.7235 | 34.7235 | 34.7235 | 60% | 934.9866 | 25.9216 | 28.2829 | 28.5274 | 29.3713 | 29.3508 | 29.5364 | 30.2622 | 32.3474 | 33.2079 | 32.3934 | 34.6434 | 33.6987 | 34.5488 | 35.1613 | 34.9097 | 34.9097 | 34.9097 | 34.9097 | 34.9097 | 34.9097 | 34.9097 | 34.9097 | 34.9097 | 34.9097 | 34.9097 | 34.9097 | 34.9097 | 34.9097 | 34.9097 | 34.9097
55% | 1310.9428 | 21.6759 | 23.9451 | 24.1858 | 24.4832 | 24.8782 | 25.2527 | 25.907 | 27.5528 | 28.438 | 27.7922 | 29.7915 | 30.1517 | 30.4106 | 31.6312 | 31.8298 | 31.8298 | 31.8298 | 31.8298 | 31.8298 | 31.8298 | 31.8298 | 31.8298 | 31.8298 | 31.8298 | 31.8298 | 31.8298 | 31.8298 | 31.8298 | 31.8298 | 31.8298 | 55% | 1310.9428 | 23.7614 | 25.926 | 26.1501 | 26.9237 | 26.9049 | 27.075 | 27.7403 | 29.6518 | 30.4406 | 29.6939 | 31.7565 | 30.8905 | 31.6697 | 32.2312 | 32.0005 | 32.0005 | 32.0005 | 32.0005 | 32.0005 | 32.0005 | 32.0005 | 32.0005 | 32.0005 | 32.0005 | 32.0005 | 32.0005 | 32.0005 | 32.0005 | 32.0005 | 32.0005
50% | 1730.2899 | 19.7054 | 21.7683 | 21.9871 | 22.2575 | 22.6166 | 22.957 | 23.5518 | 25.048 | 25.8527 | 25.2657 | 27.0832 | 27.4106 | 27.646 | 28.7556 | 28.9362 | 28.9362 | 28.9362 | 28.9362 | 28.9362 | 28.9362 | 28.9362 | 28.9362 | 28.9362 | 28.9362 | 28.9362 | 28.9362 | 28.9362 | 28.9362 | 28.9362 | 28.9362 | 50% | 1730.2899 | 21.6013 | 23.5691 | 23.7729 | 24.4761 | 24.459 | 24.6136 | 25.2185 | 26.9562 | 27.6733 | 26.9945 | 28.8695 | 28.0823 | 28.7906 | 29.3011 | 29.0914 | 29.0914 | 29.0914 | 29.0914 | 29.0914 | 29.0914 | 29.0914 | 29.0914 | 29.0914 | 29.0914 | 29.0914 | 29.0914 | 29.0914 | 29.0914 | 29.0914 | 29.0914
45% | 2168.0633 | 17.7348 | 19.5915 | 19.7883 | 20.0317 | 20.3549 | 20.6613 | 21.1967 | 22.5432 | 23.2675 | 22.7391 | 24.3749 | 24.6696 | 24.8814 | 25.8801 | 26.0426 | 26.0426 | 26.0426 | 26.0426 | 26.0426 | 26.0426 | 26.0426 | 26.0426 | 26.0426 | 26.0426 | 26.0426 | 26.0426 | 26.0426 | 26.0426 | 26.0426 | 26.0426 | 45% | 2168.0633 | 19.4412 | 21.2122 | 21.3956 | 22.0285 | 22.0131 | 22.1523 | 22.6966 | 24.2606 | 24.9059 | 24.295 | 25.9826 | 25.2741 | 25.9116 | 26.371 | 26.1822 | 26.1822 | 26.1822 | 26.1822 | 26.1822 | 26.1822 | 26.1822 | 26.1822 | 26.1822 | 26.1822 | 26.1822 | 26.1822 | 26.1822 | 26.1822 | 26.1822 | 26.1822
40% | 2609.7004 | 15.7643 | 17.4146 | 17.5896 | 17.806 | 18.0932 | 18.3656 | 18.8415 | 20.0384 | 20.6822 | 20.2125 | 21.6665 | 21.9285 | 22.1168 | 23.0045 | 23.149 | 23.149 | 23.149 | 23.149 | 23.149 | 23.149 | 23.149 | 23.149 | 23.149 | 23.149 | 23.149 | 23.149 | 23.149 | 23.149 | 23.149 | 23.149 | 40% | 2609.7004 | 17.2811 | 18.8553 | 19.0183 | 19.5809 | 19.5672 | 19.6909 | 20.1748 | 21.5649 | 22.1386 | 21.5956 | 23.0956 | 22.4658 | 23.0325 | 23.4409 | 23.2731 | 23.2731 | 23.2731 | 23.2731 | 23.2731 | 23.2731 | 23.2731 | 23.2731 | 23.2731 | 23.2731 | 23.2731 | 23.2731 | 23.2731 | 23.2731 | 23.2731 | 23.2731
35% | 2998.1389 | 13.7937 | 15.2378 | 15.3909 | 15.5802 | 15.8316 | 16.0699 | 16.4863 | 17.5336 | 18.0969 | 17.686 | 18.9582 | 19.1875 | 19.3522 | 20.1289 | 20.2554 | 20.2554 | 20.2554 | 20.2554 | 20.2554 | 20.2554 | 20.2554 | 20.2554 | 20.2554 | 20.2554 | 20.2554 | 20.2554 | 20.2554 | 20.2554 | 20.2554 | 20.2554 | 35% | 2998.1389 | 15.1209 | 16.4984 | 16.641 | 17.1333 | 17.1213 | 17.2295 | 17.6529 | 18.8693 | 19.3713 | 18.8961 | 20.2087 | 19.6576 | 20.1535 | 20.5108 | 20.364 | 20.364 | 20.364 | 20.364 | 20.364 | 20.364 | 20.364 | 20.364 | 20.364 | 20.364 | 20.364 | 20.364 | 20.364 | 20.364 | 20.364 | 20.364
30% | 3309.3057 | 11.8232 | 13.061 | 13.1922 | 13.3545 | 13.5699 | 13.7742 | 14.1311 | 15.0288 | 15.5116 | 15.1594 | 16.2499 | 16.4464 | 16.5876 | 17.2534 | 17.3617 | 17.3617 | 17.3617 | 17.3617 | 17.3617 | 17.3617 | 17.3617 | 17.3617 | 17.3617 | 17.3617 | 17.3617 | 17.3617 | 17.3617 | 17.3617 | 17.3617 | 17.3617 | 30% | 3309.3057 | 12.9608 | 14.1414 | 14.2637 | 14.6857 | 14.6754 | 14.7682 | 15.1311 | 16.1737 | 16.604 | 16.1967 | 17.3217 | 16.8494 | 17.2744 | 17.5807 | 17.4548 | 17.4548 | 17.4548 | 17.4548 | 17.4548 | 17.4548 | 17.4548 | 17.4548 | 17.4548 | 17.4548 | 17.4548 | 17.4548 | 17.4548 | 17.4548 | 17.4548 | 17.4548
25% | 3537.8514 | 9.8527 | 10.8842 | 10.9935 | 11.1287 | 11.3083 | 11.4785 | 11.7759 | 12.524 | 12.9264 | 12.6328 | 13.5416 | 13.7053 | 13.823 | 14.3778 | 14.4681 | 14.4681 | 14.4681 | 14.4681 | 14.4681 | 14.4681 | 14.4681 | 14.4681 | 14.4681 | 14.4681 | 14.4681 | 14.4681 | 14.4681 | 14.4681 | 14.4681 | 14.4681 | 25% | 3537.8514 | 10.8007 | 11.7845 | 11.8864 | 12.2381 | 12.2295 | 12.3068 | 12.6092 | 13.4781 | 13.8366 | 13.4972 | 14.4348 | 14.0411 | 14.3953 | 14.6506 | 14.5457 | 14.5457 | 14.5457 | 14.5457 | 14.5457 | 14.5457 | 14.5457 | 14.5457 | 14.5457 | 14.5457 | 14.5457 | 14.5457 | 14.5457 | 14.5457 | 14.5457 | 14.5457
20% | 3731.0305 | 7.8821 | 8.7073 | 8.7948 | 8.903 | 9.0466 | 9.1828 | 9.4207 | 10.0192 | 10.3411 | 10.1063 | 10.8333 | 10.9643 | 11.0584 | 11.5022 | 11.5745 | 11.5745 | 11.5745 | 11.5745 | 11.5745 | 11.5745 | 11.5745 | 11.5745 | 11.5745 | 11.5745 | 11.5745 | 11.5745 | 11.5745 | 11.5745 | 11.5745 | 11.5745 | 20% | 3731.0305 | 8.6405 | 9.4276 | 9.5091 | 9.7904 | 9.7836 | 9.8455 | 10.0874 | 10.7825 | 11.0693 | 10.7978 | 11.5478 | 11.2329 | 11.5163 | 11.7204 | 11.6366 | 11.6366 | 11.6366 | 11.6366 | 11.6366 | 11.6366 | 11.6366 | 11.6366 | 11.6366 | 11.6366 | 11.6366 | 11.6366 | 11.6366 | 11.6366 | 11.6366 | 11.6366
15% | 3910.2412 | 5.9116 | 6.5305 | 6.5961 | 6.6772 | 6.785 | 6.8871 | 7.0656 | 7.5144 | 7.7558 | 7.5797 | 8.125 | 8.2232 | 8.2938 | 8.6267 | 8.6809 | 8.6809 | 8.6809 | 8.6809 | 8.6809 | 8.6809 | 8.6809 | 8.6809 | 8.6809 | 8.6809 | 8.6809 | 8.6809 | 8.6809 | 8.6809 | 8.6809 | 8.6809 | 15% | 3910.2412 | 6.4804 | 7.0707 | 7.1319 | 7.3428 | 7.3377 | 7.3841 | 7.5655 | 8.0869 | 8.302 | 8.0983 | 8.6609 | 8.4247 | 8.6372 | 8.7903 | 8.7274 | 8.7274 | 8.7274 | 8.7274 | 8.7274 | 8.7274 | 8.7274 | 8.7274 | 8.7274 | 8.7274 | 8.7274 | 8.7274 | 8.7274 | 8.7274 | 8.7274 | 8.7274
10% | 4075.1864 | 3.9411 | 4.3537 | 4.3974 | 4.4515 | 4.5233 | 4.5914 | 4.7104 | 5.0096 | 5.1705 | 5.0531 | 5.4166 | 5.4821 | 5.5292 | 5.7511 | 5.7872 | 5.7872 | 5.7872 | 5.7872 | 5.7872 | 5.7872 | 5.7872 | 5.7872 | 5.7872 | 5.7872 | 5.7872 | 5.7872 | 5.7872 | 5.7872 | 5.7872 | 5.7872 | 10% | 4075.1864 | 4.3203 | 4.7138 | 4.7546 | 4.8952 | 4.8918 | 4.9227 | 5.0437 | 5.3912 | 5.5347 | 5.3989 | 5.7739 | 5.6165 | 5.7581 | 5.8602 | 5.8183 | 5.8183 | 5.8183 | 5.8183 | 5.8183 | 5.8183 | 5.8183 | 5.8183 | 5.8183 | 5.8183 | 5.8183 | 5.8183 | 5.8183 | 5.8183 | 5.8183 | 5.8183
5% | 4251.7223 | 1.9705 | 2.1768 | 2.1987 | 2.2257 | 2.2617 | 2.2957 | 2.3552 | 2.5048 | 2.5853 | 2.5266 | 2.7083 | 2.7411 | 2.7646 | 2.8756 | 2.8936 | 2.8936 | 2.8936 | 2.8936 | 2.8936 | 2.8936 | 2.8936 | 2.8936 | 2.8936 | 2.8936 | 2.8936 | 2.8936 | 2.8936 | 2.8936 | 2.8936 | 2.8936 | 5% | 4251.7223 | 2.1601 | 2.3569 | 2.3773 | 2.4476 | 2.4459 | 2.4614 | 2.5218 | 2.6956 | 2.7673 | 2.6994 | 2.887 | 2.8082 | 2.8791 | 2.9301 | 2.9091 | 2.9091 | 2.9091 | 2.9091 | 2.9091 | 2.9091 | 2.9091 | 2.9091 | 2.9091 | 2.9091 | 2.9091 | 2.9091 | 2.9091 | 2.9091 | 2.9091 | 2.9091
9.992e-14% | 4391.7028 | 3.9379e-14 | 4.3502e-14 | 4.3939e-14 | 4.4479e-14 | 4.5197e-14 | 4.5877e-14 | 4.7066e-14 | 5.0056e-14 | 5.1664e-14 | 5.0491e-14 | 5.4123e-14 | 5.4777e-14 | 5.5248e-14 | 5.7465e-14 | 5.7826e-14 | 5.7826e-14 | 5.7826e-14 | 5.7826e-14 | 5.7826e-14 | 5.7826e-14 | 5.7826e-14 | 5.7826e-14 | 5.7826e-14 | 5.7826e-14 | 5.7826e-14 | 5.7826e-14 | 5.7826e-14 | 5.7826e-14 | 5.7826e-14 | 5.7826e-14 | 9.992e-14% | 4391.7028 | 4.3168e-14 | 4.71e-14 | 4.7508e-14 | 4.8913e-14 | 4.8879e-14 | 4.9188e-14 | 5.0397e-14 | 5.3869e-14 | 5.5302e-14 | 5.3946e-14 | 5.7693e-14 | 5.612e-14 | 5.7535e-14 | 5.8555e-14 | 5.8136e-14 | 5.8136e-14 | 5.8136e-14 | 5.8136e-14 | 5.8136e-14 | 5.8136e-14 | 5.8136e-14 | 5.8136e-14 | 5.8136e-14 | 5.8136e-14 | 5.8136e-14 | 5.8136e-14 | 5.8136e-14 | 5.8136e-14 | 5.8136e-14 | 5.8136e-14
Summer Season | [31 empty] | Summer Season
P50 | [31 empty] | P10
% of MD | Summer - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Summer - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 41.4021 | 44.4975 | 44.8085 | 44.6561 | 44.801 | 44.8606 | 45.0515 | 45.4441 | 45.7743 | 45.9263 | 45.7908 | 46.3589 | 46.449 | 46.3423 | 46.5561 | 46.6661 | 46.6661 | 46.6661 | 46.6661 | 46.6661 | 46.6661 | 46.6661 | 46.6661 | 46.6661 | 46.6661 | 46.6661 | 46.6661 | 46.6661 | 46.6661 | 46.6661 | 100% | 0 | 50.9365 | 54.3957 | 54.4912 | 54.3883 | 54.4147 | 54.6036 | 54.9865 | 55.6607 | 56.012 | 56.2661 | 56.6508 | 57.1419 | 57.7357 | 58.0469 | 57.946 | 58.056 | 58.056 | 58.056 | 58.056 | 58.056 | 58.056 | 58.056 | 58.056 | 58.056 | 58.056 | 58.056 | 58.056 | 58.056 | 58.056 | 58.056
99% | 0.37816 | 40.9881 | 44.0525 | 44.3604 | 44.2095 | 44.353 | 44.412 | 44.601 | 44.9896 | 45.3165 | 45.467 | 45.3329 | 45.8953 | 45.9845 | 45.8789 | 46.0906 | 46.1995 | 46.1995 | 46.1995 | 46.1995 | 46.1995 | 46.1995 | 46.1995 | 46.1995 | 46.1995 | 46.1995 | 46.1995 | 46.1995 | 46.1995 | 46.1995 | 46.1995 | 99% | 0 | 50.4271 | 53.8518 | 53.9463 | 53.8444 | 53.8706 | 54.0576 | 54.4366 | 55.1041 | 55.4519 | 55.7035 | 56.0843 | 56.5704 | 57.1583 | 57.4664 | 57.3665 | 57.4754 | 57.4754 | 57.4754 | 57.4754 | 57.4754 | 57.4754 | 57.4754 | 57.4754 | 57.4754 | 57.4754 | 57.4754 | 57.4754 | 57.4754 | 57.4754 | 57.4754
98% | 0.37816 | 40.5741 | 43.6075 | 43.9123 | 43.7629 | 43.905 | 43.9634 | 44.1505 | 44.5352 | 44.8588 | 45.0078 | 44.875 | 45.4317 | 45.52 | 45.4155 | 45.625 | 45.7328 | 45.7328 | 45.7328 | 45.7328 | 45.7328 | 45.7328 | 45.7328 | 45.7328 | 45.7328 | 45.7328 | 45.7328 | 45.7328 | 45.7328 | 45.7328 | 45.7328 | 98% | 0 | 49.9177 | 53.3078 | 53.4014 | 53.3005 | 53.3264 | 53.5116 | 53.8867 | 54.5475 | 54.8917 | 55.1408 | 55.5178 | 55.999 | 56.581 | 56.886 | 56.7871 | 56.8949 | 56.8949 | 56.8949 | 56.8949 | 56.8949 | 56.8949 | 56.8949 | 56.8949 | 56.8949 | 56.8949 | 56.8949 | 56.8949 | 56.8949 | 56.8949 | 56.8949
97% | 0.37816 | 40.1601 | 43.1625 | 43.4643 | 43.3164 | 43.457 | 43.5148 | 43.7 | 44.0807 | 44.4011 | 44.5485 | 44.4171 | 44.9681 | 45.0555 | 44.9521 | 45.1595 | 45.2662 | 45.2662 | 45.2662 | 45.2662 | 45.2662 | 45.2662 | 45.2662 | 45.2662 | 45.2662 | 45.2662 | 45.2662 | 45.2662 | 45.2662 | 45.2662 | 45.2662 | 97% | 0.37816 | 49.4084 | 52.7639 | 52.8564 | 52.7566 | 52.7823 | 52.9655 | 53.3369 | 53.9908 | 54.3316 | 54.5781 | 54.9513 | 55.4276 | 56.0036 | 56.3055 | 56.2076 | 56.3143 | 56.3143 | 56.3143 | 56.3143 | 56.3143 | 56.3143 | 56.3143 | 56.3143 | 56.3143 | 56.3143 | 56.3143 | 56.3143 | 56.3143 | 56.3143 | 56.3143
95% | 0.75633 | 39.332 | 42.2726 | 42.5681 | 42.4232 | 42.561 | 42.6176 | 42.7989 | 43.1719 | 43.4856 | 43.63 | 43.5013 | 44.0409 | 44.1265 | 44.0252 | 44.2283 | 44.3328 | 44.3328 | 44.3328 | 44.3328 | 44.3328 | 44.3328 | 44.3328 | 44.3328 | 44.3328 | 44.3328 | 44.3328 | 44.3328 | 44.3328 | 44.3328 | 44.3328 | 95% | 0.37816 | 48.3896 | 51.6759 | 51.7666 | 51.6689 | 51.694 | 51.8735 | 52.2371 | 52.8776 | 53.2114 | 53.4528 | 53.8182 | 54.2848 | 54.8489 | 55.1446 | 55.0487 | 55.1532 | 55.1532 | 55.1532 | 55.1532 | 55.1532 | 55.1532 | 55.1532 | 55.1532 | 55.1532 | 55.1532 | 55.1532 | 55.1532 | 55.1532 | 55.1532 | 55.1532
90% | 9.0759 | 37.2619 | 40.0477 | 40.3277 | 40.1904 | 40.3209 | 40.3745 | 40.5464 | 40.8996 | 41.1969 | 41.3337 | 41.2117 | 41.723 | 41.8041 | 41.7081 | 41.9005 | 41.9995 | 41.9995 | 41.9995 | 41.9995 | 41.9995 | 41.9995 | 41.9995 | 41.9995 | 41.9995 | 41.9995 | 41.9995 | 41.9995 | 41.9995 | 41.9995 | 41.9995 | 90% | 0.75633 | 45.8428 | 48.9562 | 49.0421 | 48.9494 | 48.9733 | 49.1433 | 49.4878 | 50.0946 | 50.4108 | 50.6395 | 50.9857 | 51.4277 | 51.9621 | 52.2422 | 52.1514 | 52.2504 | 52.2504 | 52.2504 | 52.2504 | 52.2504 | 52.2504 | 52.2504 | 52.2504 | 52.2504 | 52.2504 | 52.2504 | 52.2504 | 52.2504 | 52.2504 | 52.2504
85% | 40.4636 | 35.1918 | 37.8228 | 38.0872 | 37.9576 | 38.0809 | 38.1315 | 38.2938 | 38.6274 | 38.9081 | 39.0374 | 38.9222 | 39.405 | 39.4816 | 39.391 | 39.5727 | 39.6662 | 39.6662 | 39.6662 | 39.6662 | 39.6662 | 39.6662 | 39.6662 | 39.6662 | 39.6662 | 39.6662 | 39.6662 | 39.6662 | 39.6662 | 39.6662 | 39.6662 | 85% | 1.1345 | 43.296 | 46.2364 | 46.3175 | 46.23 | 46.2525 | 46.4131 | 46.7385 | 47.3116 | 47.6102 | 47.8262 | 48.1532 | 48.5706 | 49.0753 | 49.3399 | 49.2541 | 49.3476 | 49.3476 | 49.3476 | 49.3476 | 49.3476 | 49.3476 | 49.3476 | 49.3476 | 49.3476 | 49.3476 | 49.3476 | 49.3476 | 49.3476 | 49.3476 | 49.3476
80% | 94.5411 | 33.1217 | 35.598 | 35.8468 | 35.7248 | 35.8408 | 35.8885 | 36.0412 | 36.3552 | 36.6194 | 36.741 | 36.6326 | 37.0871 | 37.1592 | 37.0739 | 37.2449 | 37.3329 | 37.3329 | 37.3329 | 37.3329 | 37.3329 | 37.3329 | 37.3329 | 37.3329 | 37.3329 | 37.3329 | 37.3329 | 37.3329 | 37.3329 | 37.3329 | 37.3329 | 80% | 2.6471 | 40.7492 | 43.5166 | 43.5929 | 43.5106 | 43.5318 | 43.6829 | 43.9892 | 44.5285 | 44.8096 | 45.0129 | 45.3206 | 45.7135 | 46.1886 | 46.4375 | 46.3568 | 46.4448 | 46.4448 | 46.4448 | 46.4448 | 46.4448 | 46.4448 | 46.4448 | 46.4448 | 46.4448 | 46.4448 | 46.4448 | 46.4448 | 46.4448 | 46.4448 | 46.4448
75% | 197.0236 | 31.0516 | 33.3731 | 33.6064 | 33.492 | 33.6008 | 33.6454 | 33.7886 | 34.083 | 34.3307 | 34.4447 | 34.3431 | 34.7692 | 34.8367 | 34.7568 | 34.9171 | 34.9996 | 34.9996 | 34.9996 | 34.9996 | 34.9996 | 34.9996 | 34.9996 | 34.9996 | 34.9996 | 34.9996 | 34.9996 | 34.9996 | 34.9996 | 34.9996 | 34.9996 | 75% | 3.4035 | 38.2023 | 40.7968 | 40.8684 | 40.7912 | 40.811 | 40.9527 | 41.2398 | 41.7455 | 42.009 | 42.1996 | 42.4881 | 42.8564 | 43.3018 | 43.5352 | 43.4595 | 43.542 | 43.542 | 43.542 | 43.542 | 43.542 | 43.542 | 43.542 | 43.542 | 43.542 | 43.542 | 43.542 | 43.542 | 43.542 | 43.542 | 43.542
70% | 336.9444 | 28.9815 | 31.1482 | 31.366 | 31.2592 | 31.3607 | 31.4024 | 31.5361 | 31.8108 | 32.042 | 32.1484 | 32.0536 | 32.4512 | 32.5143 | 32.4396 | 32.5893 | 32.6663 | 32.6663 | 32.6663 | 32.6663 | 32.6663 | 32.6663 | 32.6663 | 32.6663 | 32.6663 | 32.6663 | 32.6663 | 32.6663 | 32.6663 | 32.6663 | 32.6663 | 70% | 5.6725 | 35.6555 | 38.077 | 38.1438 | 38.0718 | 38.0903 | 38.2225 | 38.4905 | 38.9625 | 39.2084 | 39.3863 | 39.6555 | 39.9993 | 40.415 | 40.6328 | 40.5622 | 40.6392 | 40.6392 | 40.6392 | 40.6392 | 40.6392 | 40.6392 | 40.6392 | 40.6392 | 40.6392 | 40.6392 | 40.6392 | 40.6392 | 40.6392 | 40.6392 | 40.6392
65% | 521.4885 | 26.9114 | 28.9234 | 29.1255 | 29.0264 | 29.1207 | 29.1594 | 29.2835 | 29.5386 | 29.7533 | 29.8521 | 29.764 | 30.1333 | 30.1918 | 30.1225 | 30.2615 | 30.333 | 30.333 | 30.333 | 30.333 | 30.333 | 30.333 | 30.333 | 30.333 | 30.333 | 30.333 | 30.333 | 30.333 | 30.333 | 30.333 | 30.333 | 65% | 6.4288 | 33.1087 | 35.3572 | 35.4193 | 35.3524 | 35.3696 | 35.4924 | 35.7412 | 36.1794 | 36.4078 | 36.573 | 36.823 | 37.1422 | 37.5282 | 37.7305 | 37.6649 | 37.7364 | 37.7364 | 37.7364 | 37.7364 | 37.7364 | 37.7364 | 37.7364 | 37.7364 | 37.7364 | 37.7364 | 37.7364 | 37.7364 | 37.7364 | 37.7364 | 37.7364
60% | 812.675 | 24.8413 | 26.6985 | 26.8851 | 26.7936 | 26.8806 | 26.9164 | 27.0309 | 27.2664 | 27.4646 | 27.5558 | 27.4745 | 27.8153 | 27.8694 | 27.8054 | 27.9337 | 27.9997 | 27.9997 | 27.9997 | 27.9997 | 27.9997 | 27.9997 | 27.9997 | 27.9997 | 27.9997 | 27.9997 | 27.9997 | 27.9997 | 27.9997 | 27.9997 | 27.9997 | 60% | 11.3449 | 30.5619 | 32.6374 | 32.6947 | 32.633 | 32.6488 | 32.7622 | 32.9919 | 33.3964 | 33.6072 | 33.7597 | 33.9905 | 34.2851 | 34.6414 | 34.8281 | 34.7676 | 34.8336 | 34.8336 | 34.8336 | 34.8336 | 34.8336 | 34.8336 | 34.8336 | 34.8336 | 34.8336 | 34.8336 | 34.8336 | 34.8336 | 34.8336 | 34.8336 | 34.8336
55% | 1202.1843 | 22.7712 | 24.4736 | 24.6447 | 24.5608 | 24.6406 | 24.6733 | 24.7783 | 24.9942 | 25.1759 | 25.2595 | 25.1849 | 25.4974 | 25.5469 | 25.4883 | 25.6059 | 25.6664 | 25.6664 | 25.6664 | 25.6664 | 25.6664 | 25.6664 | 25.6664 | 25.6664 | 25.6664 | 25.6664 | 25.6664 | 25.6664 | 25.6664 | 25.6664 | 25.6664 | 55% | 35.5474 | 28.0151 | 29.9176 | 29.9701 | 29.9135 | 29.9281 | 30.032 | 30.2426 | 30.6134 | 30.8066 | 30.9464 | 31.1579 | 31.428 | 31.7546 | 31.9258 | 31.8703 | 31.9308 | 31.9308 | 31.9308 | 31.9308 | 31.9308 | 31.9308 | 31.9308 | 31.9308 | 31.9308 | 31.9308 | 31.9308 | 31.9308 | 31.9308 | 31.9308 | 31.9308
50% | 1686.2345 | 20.7011 | 22.2487 | 22.4043 | 22.328 | 22.4005 | 22.4303 | 22.5258 | 22.722 | 22.8871 | 22.9631 | 22.8954 | 23.1794 | 23.2245 | 23.1712 | 23.2781 | 23.3331 | 23.3331 | 23.3331 | 23.3331 | 23.3331 | 23.3331 | 23.3331 | 23.3331 | 23.3331 | 23.3331 | 23.3331 | 23.3331 | 23.3331 | 23.3331 | 23.3331 | 50% | 95.2974 | 25.4682 | 27.1979 | 27.2456 | 27.1941 | 27.2074 | 27.3018 | 27.4932 | 27.8303 | 28.006 | 28.1331 | 28.3254 | 28.5709 | 28.8678 | 29.0234 | 28.973 | 29.028 | 29.028 | 29.028 | 29.028 | 29.028 | 29.028 | 29.028 | 29.028 | 29.028 | 29.028 | 29.028 | 29.028 | 29.028 | 29.028 | 29.028
45% | 2129.0649 | 18.631 | 20.0239 | 20.1638 | 20.0952 | 20.1605 | 20.1873 | 20.2732 | 20.4498 | 20.5984 | 20.6668 | 20.6059 | 20.8615 | 20.902 | 20.8541 | 20.9503 | 20.9998 | 20.9998 | 20.9998 | 20.9998 | 20.9998 | 20.9998 | 20.9998 | 20.9998 | 20.9998 | 20.9998 | 20.9998 | 20.9998 | 20.9998 | 20.9998 | 20.9998 | 45% | 208.7467 | 22.9214 | 24.4781 | 24.521 | 24.4747 | 24.4866 | 24.5716 | 24.7439 | 25.0473 | 25.2054 | 25.3198 | 25.4928 | 25.7138 | 25.9811 | 26.1211 | 26.0757 | 26.1252 | 26.1252 | 26.1252 | 26.1252 | 26.1252 | 26.1252 | 26.1252 | 26.1252 | 26.1252 | 26.1252 | 26.1252 | 26.1252 | 26.1252 | 26.1252 | 26.1252
40% | 2484.5393 | 16.5608 | 17.799 | 17.9234 | 17.8624 | 17.9204 | 17.9442 | 18.0206 | 18.1776 | 18.3097 | 18.3705 | 18.3163 | 18.5435 | 18.5796 | 18.5369 | 18.6225 | 18.6665 | 18.6665 | 18.6665 | 18.6665 | 18.6665 | 18.6665 | 18.6665 | 18.6665 | 18.6665 | 18.6665 | 18.6665 | 18.6665 | 18.6665 | 18.6665 | 18.6665 | 40% | 380.4333 | 20.3746 | 21.7583 | 21.7965 | 21.7553 | 21.7659 | 21.8415 | 21.9946 | 22.2643 | 22.4048 | 22.5065 | 22.6603 | 22.8567 | 23.0943 | 23.2188 | 23.1784 | 23.2224 | 23.2224 | 23.2224 | 23.2224 | 23.2224 | 23.2224 | 23.2224 | 23.2224 | 23.2224 | 23.2224 | 23.2224 | 23.2224 | 23.2224 | 23.2224 | 23.2224
35% | 2808.248 | 14.4907 | 15.5741 | 15.683 | 15.6296 | 15.6804 | 15.7012 | 15.768 | 15.9054 | 16.021 | 16.0742 | 16.0268 | 16.2256 | 16.2571 | 16.2198 | 16.2947 | 16.3332 | 16.3332 | 16.3332 | 16.3332 | 16.3332 | 16.3332 | 16.3332 | 16.3332 | 16.3332 | 16.3332 | 16.3332 | 16.3332 | 16.3332 | 16.3332 | 16.3332 | 35% | 696.5786 | 17.8278 | 19.0385 | 19.0719 | 19.0359 | 19.0452 | 19.1113 | 19.2453 | 19.4812 | 19.6042 | 19.6931 | 19.8278 | 19.9997 | 20.2075 | 20.3164 | 20.2811 | 20.3196 | 20.3196 | 20.3196 | 20.3196 | 20.3196 | 20.3196 | 20.3196 | 20.3196 | 20.3196 | 20.3196 | 20.3196 | 20.3196 | 20.3196 | 20.3196 | 20.3196
30% | 3095.6528 | 12.4206 | 13.3492 | 13.4426 | 13.3968 | 13.4403 | 13.4582 | 13.5155 | 13.6332 | 13.7323 | 13.7779 | 13.7372 | 13.9077 | 13.9347 | 13.9027 | 13.9668 | 13.9998 | 13.9998 | 13.9998 | 13.9998 | 13.9998 | 13.9998 | 13.9998 | 13.9998 | 13.9998 | 13.9998 | 13.9998 | 13.9998 | 13.9998 | 13.9998 | 13.9998 | 30% | 1260.7997 | 15.2809 | 16.3187 | 16.3474 | 16.3165 | 16.3244 | 16.3811 | 16.4959 | 16.6982 | 16.8036 | 16.8798 | 16.9952 | 17.1426 | 17.3207 | 17.4141 | 17.3838 | 17.4168 | 17.4168 | 17.4168 | 17.4168 | 17.4168 | 17.4168 | 17.4168 | 17.4168 | 17.4168 | 17.4168 | 17.4168 | 17.4168 | 17.4168 | 17.4168 | 17.4168
25% | 3358.8552 | 10.3505 | 11.1244 | 11.2021 | 11.164 | 11.2003 | 11.2151 | 11.2629 | 11.361 | 11.4436 | 11.4816 | 11.4477 | 11.5897 | 11.6122 | 11.5856 | 11.639 | 11.6665 | 11.6665 | 11.6665 | 11.6665 | 11.6665 | 11.6665 | 11.6665 | 11.6665 | 11.6665 | 11.6665 | 11.6665 | 11.6665 | 11.6665 | 11.6665 | 11.6665 | 25% | 1965.3198 | 12.7341 | 13.5989 | 13.6228 | 13.5971 | 13.6037 | 13.6509 | 13.7466 | 13.9152 | 14.003 | 14.0665 | 14.1627 | 14.2855 | 14.4339 | 14.5117 | 14.4865 | 14.514 | 14.514 | 14.514 | 14.514 | 14.514 | 14.514 | 14.514 | 14.514 | 14.514 | 14.514 | 14.514 | 14.514 | 14.514 | 14.514 | 14.514
20% | 3588.7791 | 8.2804 | 8.8995 | 8.9617 | 8.9312 | 8.9602 | 8.9721 | 9.0103 | 9.0888 | 9.1549 | 9.1853 | 9.1582 | 9.2718 | 9.2898 | 9.2685 | 9.3112 | 9.3332 | 9.3332 | 9.3332 | 9.3332 | 9.3332 | 9.3332 | 9.3332 | 9.3332 | 9.3332 | 9.3332 | 9.3332 | 9.3332 | 9.3332 | 9.3332 | 9.3332 | 20% | 2490.2118 | 10.1873 | 10.8791 | 10.8982 | 10.8777 | 10.8829 | 10.9207 | 10.9973 | 11.1321 | 11.2024 | 11.2532 | 11.3302 | 11.4284 | 11.5471 | 11.6094 | 11.5892 | 11.6112 | 11.6112 | 11.6112 | 11.6112 | 11.6112 | 11.6112 | 11.6112 | 11.6112 | 11.6112 | 11.6112 | 11.6112 | 11.6112 | 11.6112 | 11.6112 | 11.6112
15% | 3802.4419 | 6.2103 | 6.6746 | 6.7213 | 6.6984 | 6.7202 | 6.7291 | 6.7577 | 6.8166 | 6.8661 | 6.8889 | 6.8686 | 6.9538 | 6.9673 | 6.9514 | 6.9834 | 6.9999 | 6.9999 | 6.9999 | 6.9999 | 6.9999 | 6.9999 | 6.9999 | 6.9999 | 6.9999 | 6.9999 | 6.9999 | 6.9999 | 6.9999 | 6.9999 | 6.9999 | 15% | 2997.7083 | 7.6405 | 8.1594 | 8.1737 | 8.1582 | 8.1622 | 8.1905 | 8.248 | 8.3491 | 8.4018 | 8.4399 | 8.4976 | 8.5713 | 8.6604 | 8.707 | 8.6919 | 8.7084 | 8.7084 | 8.7084 | 8.7084 | 8.7084 | 8.7084 | 8.7084 | 8.7084 | 8.7084 | 8.7084 | 8.7084 | 8.7084 | 8.7084 | 8.7084 | 8.7084
10% | 4024.8025 | 4.1402 | 4.4497 | 4.4809 | 4.4656 | 4.4801 | 4.4861 | 4.5052 | 4.5444 | 4.5774 | 4.5926 | 4.5791 | 4.6359 | 4.6449 | 4.6342 | 4.6556 | 4.6666 | 4.6666 | 4.6666 | 4.6666 | 4.6666 | 4.6666 | 4.6666 | 4.6666 | 4.6666 | 4.6666 | 4.6666 | 4.6666 | 4.6666 | 4.6666 | 4.6666 | 10% | 3491.5908 | 5.0936 | 5.4396 | 5.4491 | 5.4388 | 5.4415 | 5.4604 | 5.4986 | 5.5661 | 5.6012 | 5.6266 | 5.6651 | 5.7142 | 5.7736 | 5.8047 | 5.7946 | 5.8056 | 5.8056 | 5.8056 | 5.8056 | 5.8056 | 5.8056 | 5.8056 | 5.8056 | 5.8056 | 5.8056 | 5.8056 | 5.8056 | 5.8056 | 5.8056 | 5.8056
5% | 4239.978 | 2.0701 | 2.2249 | 2.2404 | 2.2328 | 2.2401 | 2.243 | 2.2526 | 2.2722 | 2.2887 | 2.2963 | 2.2895 | 2.3179 | 2.3224 | 2.3171 | 2.3278 | 2.3333 | 2.3333 | 2.3333 | 2.3333 | 2.3333 | 2.3333 | 2.3333 | 2.3333 | 2.3333 | 2.3333 | 2.3333 | 2.3333 | 2.3333 | 2.3333 | 2.3333 | 5% | 3955.9766 | 2.5468 | 2.7198 | 2.7246 | 2.7194 | 2.7207 | 2.7302 | 2.7493 | 2.783 | 2.8006 | 2.8133 | 2.8325 | 2.8571 | 2.8868 | 2.9023 | 2.8973 | 2.9028 | 2.9028 | 2.9028 | 2.9028 | 2.9028 | 2.9028 | 2.9028 | 2.9028 | 2.9028 | 2.9028 | 2.9028 | 2.9028 | 2.9028 | 2.9028 | 2.9028
9.992e-14% | 4391.6218 | 4.1369e-14 | 4.4462e-14 | 4.4773e-14 | 4.462e-14 | 4.4765e-14 | 4.4825e-14 | 4.5015e-14 | 4.5408e-14 | 4.5738e-14 | 4.589e-14 | 4.5754e-14 | 4.6322e-14 | 4.6412e-14 | 4.6305e-14 | 4.6519e-14 | 4.6629e-14 | 4.6629e-14 | 4.6629e-14 | 4.6629e-14 | 4.6629e-14 | 4.6629e-14 | 4.6629e-14 | 4.6629e-14 | 4.6629e-14 | 4.6629e-14 | 4.6629e-14 | 4.6629e-14 | 4.6629e-14 | 4.6629e-14 | 4.6629e-14 | 9.992e-14% | 4391.6218 | 5.0896e-14 | 5.4352e-14 | 5.4448e-14 | 5.4345e-14 | 5.4371e-14 | 5.456e-14 | 5.4943e-14 | 5.5616e-14 | 5.5967e-14 | 5.6221e-14 | 5.6605e-14 | 5.7096e-14 | 5.769e-14 | 5.8001e-14 | 5.79e-14 | 5.801e-14 | 5.801e-14 | 5.801e-14 | 5.801e-14 | 5.801e-14 | 5.801e-14 | 5.801e-14 | 5.801e-14 | 5.801e-14 | 5.801e-14 | 5.801e-14 | 5.801e-14 | 5.801e-14 | 5.801e-14 | 5.801e-14
Option 8
Winter Season | [31 empty] | Winter Season
P50 | [31 empty] | P10
% of MD | Winter - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Winter - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 39.4107 | 43.5366 | 43.9741 | 44.515 | 45.2331 | 45.9139 | 47.1037 | 50.096 | 51.7055 | 50.5313 | 54.1664 | 54.8213 | 55.2921 | 57.5112 | 57.8724 | 57.8724 | 57.8724 | 57.8724 | 57.8724 | 57.8724 | 57.8724 | 57.8724 | 57.8724 | 57.8724 | 57.8724 | 57.8724 | 57.8724 | 57.8724 | 57.8724 | 57.8724 | 100% | 0 | 43.2026 | 47.1382 | 47.5457 | 48.9522 | 48.918 | 49.2273 | 50.4369 | 53.9124 | 55.3465 | 53.989 | 57.7391 | 56.1646 | 57.5813 | 58.6022 | 58.1828 | 58.1828 | 58.1828 | 58.1828 | 58.1828 | 58.1828 | 58.1828 | 58.1828 | 58.1828 | 58.1828 | 58.1828 | 58.1828 | 58.1828 | 58.1828 | 58.1828 | 58.1828
99% | 0.2972 | 39.0166 | 43.1012 | 43.5344 | 44.0698 | 44.7808 | 45.4548 | 46.6326 | 49.595 | 51.1884 | 50.026 | 53.6247 | 54.2731 | 54.7392 | 56.9361 | 57.2937 | 57.2937 | 57.2937 | 57.2937 | 57.2937 | 57.2937 | 57.2937 | 57.2937 | 57.2937 | 57.2937 | 57.2937 | 57.2937 | 57.2937 | 57.2937 | 57.2937 | 57.2937 | 99% | 0.2972 | 42.7706 | 46.6668 | 47.0703 | 48.4627 | 48.4288 | 48.735 | 49.9326 | 53.3732 | 54.7931 | 53.4491 | 57.1617 | 55.6029 | 57.0055 | 58.0162 | 57.6009 | 57.6009 | 57.6009 | 57.6009 | 57.6009 | 57.6009 | 57.6009 | 57.6009 | 57.6009 | 57.6009 | 57.6009 | 57.6009 | 57.6009 | 57.6009 | 57.6009 | 57.6009
98% | 0.2972 | 38.6225 | 42.6659 | 43.0946 | 43.6247 | 44.3284 | 44.9956 | 46.1616 | 49.0941 | 50.6714 | 49.5207 | 53.083 | 53.7249 | 54.1862 | 56.361 | 56.715 | 56.715 | 56.715 | 56.715 | 56.715 | 56.715 | 56.715 | 56.715 | 56.715 | 56.715 | 56.715 | 56.715 | 56.715 | 56.715 | 56.715 | 56.715 | 98% | 0.2972 | 42.3386 | 46.1954 | 46.5948 | 47.9732 | 47.9396 | 48.2427 | 49.4282 | 52.8341 | 54.2396 | 52.9092 | 56.5843 | 55.0413 | 56.4297 | 57.4302 | 57.0191 | 57.0191 | 57.0191 | 57.0191 | 57.0191 | 57.0191 | 57.0191 | 57.0191 | 57.0191 | 57.0191 | 57.0191 | 57.0191 | 57.0191 | 57.0191 | 57.0191 | 57.0191
97% | 0.2972 | 38.2284 | 42.2305 | 42.6549 | 43.1795 | 43.8761 | 44.5365 | 45.6906 | 48.5931 | 50.1543 | 49.0154 | 52.5414 | 53.1767 | 53.6333 | 55.7859 | 56.1363 | 56.1363 | 56.1363 | 56.1363 | 56.1363 | 56.1363 | 56.1363 | 56.1363 | 56.1363 | 56.1363 | 56.1363 | 56.1363 | 56.1363 | 56.1363 | 56.1363 | 56.1363 | 97% | 0.2972 | 41.9066 | 45.724 | 46.1193 | 47.4837 | 47.4504 | 47.7504 | 48.9238 | 52.295 | 53.6861 | 52.3693 | 56.0069 | 54.4796 | 55.8539 | 56.8441 | 56.4373 | 56.4373 | 56.4373 | 56.4373 | 56.4373 | 56.4373 | 56.4373 | 56.4373 | 56.4373 | 56.4373 | 56.4373 | 56.4373 | 56.4373 | 56.4373 | 56.4373 | 56.4373
95% | 1.486 | 37.4402 | 41.3598 | 41.7754 | 42.2892 | 42.9715 | 43.6182 | 44.7485 | 47.5912 | 49.1202 | 48.0047 | 51.4581 | 52.0802 | 52.5275 | 54.6357 | 54.9788 | 54.9788 | 54.9788 | 54.9788 | 54.9788 | 54.9788 | 54.9788 | 54.9788 | 54.9788 | 54.9788 | 54.9788 | 54.9788 | 54.9788 | 54.9788 | 54.9788 | 54.9788 | 95% | 1.486 | 41.0425 | 44.7812 | 45.1684 | 46.5046 | 46.4721 | 46.7659 | 47.9151 | 51.2167 | 52.5792 | 51.2895 | 54.8521 | 53.3563 | 54.7022 | 55.6721 | 55.2736 | 55.2736 | 55.2736 | 55.2736 | 55.2736 | 55.2736 | 55.2736 | 55.2736 | 55.2736 | 55.2736 | 55.2736 | 55.2736 | 55.2736 | 55.2736 | 55.2736 | 55.2736
90% | 8.6188 | 35.4696 | 39.1829 | 39.5767 | 40.0635 | 40.7098 | 41.3225 | 42.3933 | 45.0864 | 46.5349 | 45.4782 | 48.7497 | 49.3392 | 49.7629 | 51.7601 | 52.0852 | 52.0852 | 52.0852 | 52.0852 | 52.0852 | 52.0852 | 52.0852 | 52.0852 | 52.0852 | 52.0852 | 52.0852 | 52.0852 | 52.0852 | 52.0852 | 52.0852 | 52.0852 | 90% | 8.6188 | 38.8824 | 42.4243 | 42.7911 | 44.057 | 44.0262 | 44.3045 | 45.3932 | 48.5211 | 49.8119 | 48.5901 | 51.9652 | 50.5481 | 51.8232 | 52.742 | 52.3645 | 52.3645 | 52.3645 | 52.3645 | 52.3645 | 52.3645 | 52.3645 | 52.3645 | 52.3645 | 52.3645 | 52.3645 | 52.3645 | 52.3645 | 52.3645 | 52.3645 | 52.3645
85% | 40.1218 | 33.4991 | 37.0061 | 37.378 | 37.8377 | 38.4481 | 39.0268 | 40.0381 | 42.5816 | 43.9497 | 42.9516 | 46.0414 | 46.5981 | 46.9983 | 48.8845 | 49.1916 | 49.1916 | 49.1916 | 49.1916 | 49.1916 | 49.1916 | 49.1916 | 49.1916 | 49.1916 | 49.1916 | 49.1916 | 49.1916 | 49.1916 | 49.1916 | 49.1916 | 49.1916 | 85% | 40.1218 | 36.7222 | 40.0674 | 40.4139 | 41.6094 | 41.5803 | 41.8432 | 42.8714 | 45.8255 | 47.0445 | 45.8906 | 49.0782 | 47.7399 | 48.9441 | 49.8119 | 49.4554 | 49.4554 | 49.4554 | 49.4554 | 49.4554 | 49.4554 | 49.4554 | 49.4554 | 49.4554 | 49.4554 | 49.4554 | 49.4554 | 49.4554 | 49.4554 | 49.4554 | 49.4554
80% | 93.0231 | 31.5286 | 34.8293 | 35.1793 | 35.612 | 36.1865 | 36.7311 | 37.6829 | 40.0768 | 41.3644 | 40.425 | 43.3331 | 43.857 | 44.2337 | 46.009 | 46.2979 | 46.2979 | 46.2979 | 46.2979 | 46.2979 | 46.2979 | 46.2979 | 46.2979 | 46.2979 | 46.2979 | 46.2979 | 46.2979 | 46.2979 | 46.2979 | 46.2979 | 46.2979 | 80% | 93.0231 | 34.5621 | 37.7105 | 38.0366 | 39.1618 | 39.1344 | 39.3818 | 40.3495 | 43.1299 | 44.2772 | 43.1912 | 46.1913 | 44.9317 | 46.065 | 46.8818 | 46.5462 | 46.5462 | 46.5462 | 46.5462 | 46.5462 | 46.5462 | 46.5462 | 46.5462 | 46.5462 | 46.5462 | 46.5462 | 46.5462 | 46.5462 | 46.5462 | 46.5462 | 46.5462
75% | 197.0426 | 29.558 | 32.6525 | 32.9806 | 33.3862 | 33.9248 | 34.4354 | 35.3278 | 37.572 | 38.7791 | 37.8985 | 40.6248 | 41.116 | 41.4691 | 43.1334 | 43.4043 | 43.4043 | 43.4043 | 43.4043 | 43.4043 | 43.4043 | 43.4043 | 43.4043 | 43.4043 | 43.4043 | 43.4043 | 43.4043 | 43.4043 | 43.4043 | 43.4043 | 43.4043 | 75% | 197.0426 | 32.402 | 35.3536 | 35.6593 | 36.7142 | 36.6885 | 36.9204 | 37.8277 | 40.4343 | 41.5099 | 40.4917 | 43.3043 | 42.1234 | 43.186 | 43.9517 | 43.6371 | 43.6371 | 43.6371 | 43.6371 | 43.6371 | 43.6371 | 43.6371 | 43.6371 | 43.6371 | 43.6371 | 43.6371 | 43.6371 | 43.6371 | 43.6371 | 43.6371 | 43.6371
70% | 378.0365 | 27.5875 | 30.4756 | 30.7819 | 31.1605 | 31.6632 | 32.1397 | 32.9726 | 35.0672 | 36.1938 | 35.3719 | 37.9165 | 38.3749 | 38.7045 | 40.2579 | 40.5107 | 40.5107 | 40.5107 | 40.5107 | 40.5107 | 40.5107 | 40.5107 | 40.5107 | 40.5107 | 40.5107 | 40.5107 | 40.5107 | 40.5107 | 40.5107 | 40.5107 | 40.5107 | 70% | 378.0365 | 30.2418 | 32.9967 | 33.282 | 34.2666 | 34.2426 | 34.4591 | 35.3059 | 37.7386 | 38.7426 | 37.7923 | 40.4173 | 39.3152 | 40.3069 | 41.0215 | 40.7279 | 40.7279 | 40.7279 | 40.7279 | 40.7279 | 40.7279 | 40.7279 | 40.7279 | 40.7279 | 40.7279 | 40.7279 | 40.7279 | 40.7279 | 40.7279 | 40.7279 | 40.7279
65% | 616.0926 | 25.617 | 28.2988 | 28.5832 | 28.9347 | 29.4015 | 29.844 | 30.6174 | 32.5624 | 33.6086 | 32.8454 | 35.2081 | 35.6338 | 35.9399 | 37.3823 | 37.6171 | 37.6171 | 37.6171 | 37.6171 | 37.6171 | 37.6171 | 37.6171 | 37.6171 | 37.6171 | 37.6171 | 37.6171 | 37.6171 | 37.6171 | 37.6171 | 37.6171 | 37.6171 | 65% | 616.0926 | 28.0817 | 30.6398 | 30.9047 | 31.819 | 31.7967 | 31.9977 | 32.784 | 35.043 | 35.9752 | 35.0928 | 37.5304 | 36.507 | 37.4278 | 38.0914 | 37.8188 | 37.8188 | 37.8188 | 37.8188 | 37.8188 | 37.8188 | 37.8188 | 37.8188 | 37.8188 | 37.8188 | 37.8188 | 37.8188 | 37.8188 | 37.8188 | 37.8188 | 37.8188
60% | 934.9866 | 23.6464 | 26.122 | 26.3845 | 26.709 | 27.1399 | 27.5483 | 28.2622 | 30.0576 | 31.0233 | 30.3188 | 32.4998 | 32.8928 | 33.1753 | 34.5067 | 34.7235 | 34.7235 | 34.7235 | 34.7235 | 34.7235 | 34.7235 | 34.7235 | 34.7235 | 34.7235 | 34.7235 | 34.7235 | 34.7235 | 34.7235 | 34.7235 | 34.7235 | 34.7235 | 60% | 934.9866 | 25.9216 | 28.2829 | 28.5274 | 29.3713 | 29.3508 | 29.5364 | 30.2622 | 32.3474 | 33.2079 | 32.3934 | 34.6434 | 33.6987 | 34.5488 | 35.1613 | 34.9097 | 34.9097 | 34.9097 | 34.9097 | 34.9097 | 34.9097 | 34.9097 | 34.9097 | 34.9097 | 34.9097 | 34.9097 | 34.9097 | 34.9097 | 34.9097 | 34.9097 | 34.9097
55% | 1310.9428 | 21.6759 | 23.9451 | 24.1858 | 24.4832 | 24.8782 | 25.2527 | 25.907 | 27.5528 | 28.438 | 27.7922 | 29.7915 | 30.1517 | 30.4106 | 31.6312 | 31.8298 | 31.8298 | 31.8298 | 31.8298 | 31.8298 | 31.8298 | 31.8298 | 31.8298 | 31.8298 | 31.8298 | 31.8298 | 31.8298 | 31.8298 | 31.8298 | 31.8298 | 31.8298 | 55% | 1310.9428 | 23.7614 | 25.926 | 26.1501 | 26.9237 | 26.9049 | 27.075 | 27.7403 | 29.6518 | 30.4406 | 29.6939 | 31.7565 | 30.8905 | 31.6697 | 32.2312 | 32.0005 | 32.0005 | 32.0005 | 32.0005 | 32.0005 | 32.0005 | 32.0005 | 32.0005 | 32.0005 | 32.0005 | 32.0005 | 32.0005 | 32.0005 | 32.0005 | 32.0005 | 32.0005
50% | 1730.2899 | 19.7054 | 21.7683 | 21.9871 | 22.2575 | 22.6166 | 22.957 | 23.5518 | 25.048 | 25.8527 | 25.2657 | 27.0832 | 27.4106 | 27.646 | 28.7556 | 28.9362 | 28.9362 | 28.9362 | 28.9362 | 28.9362 | 28.9362 | 28.9362 | 28.9362 | 28.9362 | 28.9362 | 28.9362 | 28.9362 | 28.9362 | 28.9362 | 28.9362 | 28.9362 | 50% | 1730.2899 | 21.6013 | 23.5691 | 23.7729 | 24.4761 | 24.459 | 24.6136 | 25.2185 | 26.9562 | 27.6733 | 26.9945 | 28.8695 | 28.0823 | 28.7906 | 29.3011 | 29.0914 | 29.0914 | 29.0914 | 29.0914 | 29.0914 | 29.0914 | 29.0914 | 29.0914 | 29.0914 | 29.0914 | 29.0914 | 29.0914 | 29.0914 | 29.0914 | 29.0914 | 29.0914
45% | 2168.0633 | 17.7348 | 19.5915 | 19.7883 | 20.0317 | 20.3549 | 20.6613 | 21.1967 | 22.5432 | 23.2675 | 22.7391 | 24.3749 | 24.6696 | 24.8814 | 25.8801 | 26.0426 | 26.0426 | 26.0426 | 26.0426 | 26.0426 | 26.0426 | 26.0426 | 26.0426 | 26.0426 | 26.0426 | 26.0426 | 26.0426 | 26.0426 | 26.0426 | 26.0426 | 26.0426 | 45% | 2168.0633 | 19.4412 | 21.2122 | 21.3956 | 22.0285 | 22.0131 | 22.1523 | 22.6966 | 24.2606 | 24.9059 | 24.295 | 25.9826 | 25.2741 | 25.9116 | 26.371 | 26.1822 | 26.1822 | 26.1822 | 26.1822 | 26.1822 | 26.1822 | 26.1822 | 26.1822 | 26.1822 | 26.1822 | 26.1822 | 26.1822 | 26.1822 | 26.1822 | 26.1822 | 26.1822
40% | 2609.7004 | 15.7643 | 17.4146 | 17.5896 | 17.806 | 18.0932 | 18.3656 | 18.8415 | 20.0384 | 20.6822 | 20.2125 | 21.6665 | 21.9285 | 22.1168 | 23.0045 | 23.149 | 23.149 | 23.149 | 23.149 | 23.149 | 23.149 | 23.149 | 23.149 | 23.149 | 23.149 | 23.149 | 23.149 | 23.149 | 23.149 | 23.149 | 23.149 | 40% | 2609.7004 | 17.2811 | 18.8553 | 19.0183 | 19.5809 | 19.5672 | 19.6909 | 20.1748 | 21.5649 | 22.1386 | 21.5956 | 23.0956 | 22.4658 | 23.0325 | 23.4409 | 23.2731 | 23.2731 | 23.2731 | 23.2731 | 23.2731 | 23.2731 | 23.2731 | 23.2731 | 23.2731 | 23.2731 | 23.2731 | 23.2731 | 23.2731 | 23.2731 | 23.2731 | 23.2731
35% | 2998.1389 | 13.7937 | 15.2378 | 15.3909 | 15.5802 | 15.8316 | 16.0699 | 16.4863 | 17.5336 | 18.0969 | 17.686 | 18.9582 | 19.1875 | 19.3522 | 20.1289 | 20.2554 | 20.2554 | 20.2554 | 20.2554 | 20.2554 | 20.2554 | 20.2554 | 20.2554 | 20.2554 | 20.2554 | 20.2554 | 20.2554 | 20.2554 | 20.2554 | 20.2554 | 20.2554 | 35% | 2998.1389 | 15.1209 | 16.4984 | 16.641 | 17.1333 | 17.1213 | 17.2295 | 17.6529 | 18.8693 | 19.3713 | 18.8961 | 20.2087 | 19.6576 | 20.1535 | 20.5108 | 20.364 | 20.364 | 20.364 | 20.364 | 20.364 | 20.364 | 20.364 | 20.364 | 20.364 | 20.364 | 20.364 | 20.364 | 20.364 | 20.364 | 20.364 | 20.364
30% | 3309.3057 | 11.8232 | 13.061 | 13.1922 | 13.3545 | 13.5699 | 13.7742 | 14.1311 | 15.0288 | 15.5116 | 15.1594 | 16.2499 | 16.4464 | 16.5876 | 17.2534 | 17.3617 | 17.3617 | 17.3617 | 17.3617 | 17.3617 | 17.3617 | 17.3617 | 17.3617 | 17.3617 | 17.3617 | 17.3617 | 17.3617 | 17.3617 | 17.3617 | 17.3617 | 17.3617 | 30% | 3309.3057 | 12.9608 | 14.1414 | 14.2637 | 14.6857 | 14.6754 | 14.7682 | 15.1311 | 16.1737 | 16.604 | 16.1967 | 17.3217 | 16.8494 | 17.2744 | 17.5807 | 17.4548 | 17.4548 | 17.4548 | 17.4548 | 17.4548 | 17.4548 | 17.4548 | 17.4548 | 17.4548 | 17.4548 | 17.4548 | 17.4548 | 17.4548 | 17.4548 | 17.4548 | 17.4548
25% | 3537.8514 | 9.8527 | 10.8842 | 10.9935 | 11.1287 | 11.3083 | 11.4785 | 11.7759 | 12.524 | 12.9264 | 12.6328 | 13.5416 | 13.7053 | 13.823 | 14.3778 | 14.4681 | 14.4681 | 14.4681 | 14.4681 | 14.4681 | 14.4681 | 14.4681 | 14.4681 | 14.4681 | 14.4681 | 14.4681 | 14.4681 | 14.4681 | 14.4681 | 14.4681 | 14.4681 | 25% | 3537.8514 | 10.8007 | 11.7845 | 11.8864 | 12.2381 | 12.2295 | 12.3068 | 12.6092 | 13.4781 | 13.8366 | 13.4972 | 14.4348 | 14.0411 | 14.3953 | 14.6506 | 14.5457 | 14.5457 | 14.5457 | 14.5457 | 14.5457 | 14.5457 | 14.5457 | 14.5457 | 14.5457 | 14.5457 | 14.5457 | 14.5457 | 14.5457 | 14.5457 | 14.5457 | 14.5457
20% | 3731.0305 | 7.8821 | 8.7073 | 8.7948 | 8.903 | 9.0466 | 9.1828 | 9.4207 | 10.0192 | 10.3411 | 10.1063 | 10.8333 | 10.9643 | 11.0584 | 11.5022 | 11.5745 | 11.5745 | 11.5745 | 11.5745 | 11.5745 | 11.5745 | 11.5745 | 11.5745 | 11.5745 | 11.5745 | 11.5745 | 11.5745 | 11.5745 | 11.5745 | 11.5745 | 11.5745 | 20% | 3731.0305 | 8.6405 | 9.4276 | 9.5091 | 9.7904 | 9.7836 | 9.8455 | 10.0874 | 10.7825 | 11.0693 | 10.7978 | 11.5478 | 11.2329 | 11.5163 | 11.7204 | 11.6366 | 11.6366 | 11.6366 | 11.6366 | 11.6366 | 11.6366 | 11.6366 | 11.6366 | 11.6366 | 11.6366 | 11.6366 | 11.6366 | 11.6366 | 11.6366 | 11.6366 | 11.6366
15% | 3910.2412 | 5.9116 | 6.5305 | 6.5961 | 6.6772 | 6.785 | 6.8871 | 7.0656 | 7.5144 | 7.7558 | 7.5797 | 8.125 | 8.2232 | 8.2938 | 8.6267 | 8.6809 | 8.6809 | 8.6809 | 8.6809 | 8.6809 | 8.6809 | 8.6809 | 8.6809 | 8.6809 | 8.6809 | 8.6809 | 8.6809 | 8.6809 | 8.6809 | 8.6809 | 8.6809 | 15% | 3910.2412 | 6.4804 | 7.0707 | 7.1319 | 7.3428 | 7.3377 | 7.3841 | 7.5655 | 8.0869 | 8.302 | 8.0983 | 8.6609 | 8.4247 | 8.6372 | 8.7903 | 8.7274 | 8.7274 | 8.7274 | 8.7274 | 8.7274 | 8.7274 | 8.7274 | 8.7274 | 8.7274 | 8.7274 | 8.7274 | 8.7274 | 8.7274 | 8.7274 | 8.7274 | 8.7274
10% | 4075.1864 | 3.9411 | 4.3537 | 4.3974 | 4.4515 | 4.5233 | 4.5914 | 4.7104 | 5.0096 | 5.1705 | 5.0531 | 5.4166 | 5.4821 | 5.5292 | 5.7511 | 5.7872 | 5.7872 | 5.7872 | 5.7872 | 5.7872 | 5.7872 | 5.7872 | 5.7872 | 5.7872 | 5.7872 | 5.7872 | 5.7872 | 5.7872 | 5.7872 | 5.7872 | 5.7872 | 10% | 4075.1864 | 4.3203 | 4.7138 | 4.7546 | 4.8952 | 4.8918 | 4.9227 | 5.0437 | 5.3912 | 5.5347 | 5.3989 | 5.7739 | 5.6165 | 5.7581 | 5.8602 | 5.8183 | 5.8183 | 5.8183 | 5.8183 | 5.8183 | 5.8183 | 5.8183 | 5.8183 | 5.8183 | 5.8183 | 5.8183 | 5.8183 | 5.8183 | 5.8183 | 5.8183 | 5.8183
5% | 4251.7223 | 1.9705 | 2.1768 | 2.1987 | 2.2257 | 2.2617 | 2.2957 | 2.3552 | 2.5048 | 2.5853 | 2.5266 | 2.7083 | 2.7411 | 2.7646 | 2.8756 | 2.8936 | 2.8936 | 2.8936 | 2.8936 | 2.8936 | 2.8936 | 2.8936 | 2.8936 | 2.8936 | 2.8936 | 2.8936 | 2.8936 | 2.8936 | 2.8936 | 2.8936 | 2.8936 | 5% | 4251.7223 | 2.1601 | 2.3569 | 2.3773 | 2.4476 | 2.4459 | 2.4614 | 2.5218 | 2.6956 | 2.7673 | 2.6994 | 2.887 | 2.8082 | 2.8791 | 2.9301 | 2.9091 | 2.9091 | 2.9091 | 2.9091 | 2.9091 | 2.9091 | 2.9091 | 2.9091 | 2.9091 | 2.9091 | 2.9091 | 2.9091 | 2.9091 | 2.9091 | 2.9091 | 2.9091
9.992e-14% | 4391.7028 | 3.9379e-14 | 4.3502e-14 | 4.3939e-14 | 4.4479e-14 | 4.5197e-14 | 4.5877e-14 | 4.7066e-14 | 5.0056e-14 | 5.1664e-14 | 5.0491e-14 | 5.4123e-14 | 5.4777e-14 | 5.5248e-14 | 5.7465e-14 | 5.7826e-14 | 5.7826e-14 | 5.7826e-14 | 5.7826e-14 | 5.7826e-14 | 5.7826e-14 | 5.7826e-14 | 5.7826e-14 | 5.7826e-14 | 5.7826e-14 | 5.7826e-14 | 5.7826e-14 | 5.7826e-14 | 5.7826e-14 | 5.7826e-14 | 5.7826e-14 | 9.992e-14% | 4391.7028 | 4.3168e-14 | 4.71e-14 | 4.7508e-14 | 4.8913e-14 | 4.8879e-14 | 4.9188e-14 | 5.0397e-14 | 5.3869e-14 | 5.5302e-14 | 5.3946e-14 | 5.7693e-14 | 5.612e-14 | 5.7535e-14 | 5.8555e-14 | 5.8136e-14 | 5.8136e-14 | 5.8136e-14 | 5.8136e-14 | 5.8136e-14 | 5.8136e-14 | 5.8136e-14 | 5.8136e-14 | 5.8136e-14 | 5.8136e-14 | 5.8136e-14 | 5.8136e-14 | 5.8136e-14 | 5.8136e-14 | 5.8136e-14 | 5.8136e-14
Summer Season | [31 empty] | Summer Season
P50 | [31 empty] | P10
% of MD | Summer - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Summer - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 41.4021 | 44.4975 | 44.8085 | 44.6561 | 44.801 | 44.8606 | 45.0515 | 45.4441 | 45.7743 | 45.9263 | 45.7908 | 46.3589 | 46.449 | 46.3423 | 46.5561 | 46.6661 | 46.6661 | 46.6661 | 46.6661 | 46.6661 | 46.6661 | 46.6661 | 46.6661 | 46.6661 | 46.6661 | 46.6661 | 46.6661 | 46.6661 | 46.6661 | 46.6661 | 100% | 0 | 50.9365 | 54.3957 | 54.4912 | 54.3883 | 54.4147 | 54.6036 | 54.9865 | 55.6607 | 56.012 | 56.2661 | 56.6508 | 57.1419 | 57.7357 | 58.0469 | 57.946 | 58.056 | 58.056 | 58.056 | 58.056 | 58.056 | 58.056 | 58.056 | 58.056 | 58.056 | 58.056 | 58.056 | 58.056 | 58.056 | 58.056 | 58.056
99% | 0.37816 | 40.9881 | 44.0525 | 44.3604 | 44.2095 | 44.353 | 44.412 | 44.601 | 44.9896 | 45.3165 | 45.467 | 45.3329 | 45.8953 | 45.9845 | 45.8789 | 46.0906 | 46.1995 | 46.1995 | 46.1995 | 46.1995 | 46.1995 | 46.1995 | 46.1995 | 46.1995 | 46.1995 | 46.1995 | 46.1995 | 46.1995 | 46.1995 | 46.1995 | 46.1995 | 99% | 0 | 50.4271 | 53.8518 | 53.9463 | 53.8444 | 53.8706 | 54.0576 | 54.4366 | 55.1041 | 55.4519 | 55.7035 | 56.0843 | 56.5704 | 57.1583 | 57.4664 | 57.3665 | 57.4754 | 57.4754 | 57.4754 | 57.4754 | 57.4754 | 57.4754 | 57.4754 | 57.4754 | 57.4754 | 57.4754 | 57.4754 | 57.4754 | 57.4754 | 57.4754 | 57.4754
98% | 0.37816 | 40.5741 | 43.6075 | 43.9123 | 43.7629 | 43.905 | 43.9634 | 44.1505 | 44.5352 | 44.8588 | 45.0078 | 44.875 | 45.4317 | 45.52 | 45.4155 | 45.625 | 45.7328 | 45.7328 | 45.7328 | 45.7328 | 45.7328 | 45.7328 | 45.7328 | 45.7328 | 45.7328 | 45.7328 | 45.7328 | 45.7328 | 45.7328 | 45.7328 | 45.7328 | 98% | 0 | 49.9177 | 53.3078 | 53.4014 | 53.3005 | 53.3264 | 53.5116 | 53.8867 | 54.5475 | 54.8917 | 55.1408 | 55.5178 | 55.999 | 56.581 | 56.886 | 56.7871 | 56.8949 | 56.8949 | 56.8949 | 56.8949 | 56.8949 | 56.8949 | 56.8949 | 56.8949 | 56.8949 | 56.8949 | 56.8949 | 56.8949 | 56.8949 | 56.8949 | 56.8949
97% | 0.37816 | 40.1601 | 43.1625 | 43.4643 | 43.3164 | 43.457 | 43.5148 | 43.7 | 44.0807 | 44.4011 | 44.5485 | 44.4171 | 44.9681 | 45.0555 | 44.9521 | 45.1595 | 45.2662 | 45.2662 | 45.2662 | 45.2662 | 45.2662 | 45.2662 | 45.2662 | 45.2662 | 45.2662 | 45.2662 | 45.2662 | 45.2662 | 45.2662 | 45.2662 | 45.2662 | 97% | 0.37816 | 49.4084 | 52.7639 | 52.8564 | 52.7566 | 52.7823 | 52.9655 | 53.3369 | 53.9908 | 54.3316 | 54.5781 | 54.9513 | 55.4276 | 56.0036 | 56.3055 | 56.2076 | 56.3143 | 56.3143 | 56.3143 | 56.3143 | 56.3143 | 56.3143 | 56.3143 | 56.3143 | 56.3143 | 56.3143 | 56.3143 | 56.3143 | 56.3143 | 56.3143 | 56.3143
95% | 0.75633 | 39.332 | 42.2726 | 42.5681 | 42.4232 | 42.561 | 42.6176 | 42.7989 | 43.1719 | 43.4856 | 43.63 | 43.5013 | 44.0409 | 44.1265 | 44.0252 | 44.2283 | 44.3328 | 44.3328 | 44.3328 | 44.3328 | 44.3328 | 44.3328 | 44.3328 | 44.3328 | 44.3328 | 44.3328 | 44.3328 | 44.3328 | 44.3328 | 44.3328 | 44.3328 | 95% | 0.37816 | 48.3896 | 51.6759 | 51.7666 | 51.6689 | 51.694 | 51.8735 | 52.2371 | 52.8776 | 53.2114 | 53.4528 | 53.8182 | 54.2848 | 54.8489 | 55.1446 | 55.0487 | 55.1532 | 55.1532 | 55.1532 | 55.1532 | 55.1532 | 55.1532 | 55.1532 | 55.1532 | 55.1532 | 55.1532 | 55.1532 | 55.1532 | 55.1532 | 55.1532 | 55.1532
90% | 9.0759 | 37.2619 | 40.0477 | 40.3277 | 40.1904 | 40.3209 | 40.3745 | 40.5464 | 40.8996 | 41.1969 | 41.3337 | 41.2117 | 41.723 | 41.8041 | 41.7081 | 41.9005 | 41.9995 | 41.9995 | 41.9995 | 41.9995 | 41.9995 | 41.9995 | 41.9995 | 41.9995 | 41.9995 | 41.9995 | 41.9995 | 41.9995 | 41.9995 | 41.9995 | 41.9995 | 90% | 0.75633 | 45.8428 | 48.9562 | 49.0421 | 48.9494 | 48.9733 | 49.1433 | 49.4878 | 50.0946 | 50.4108 | 50.6395 | 50.9857 | 51.4277 | 51.9621 | 52.2422 | 52.1514 | 52.2504 | 52.2504 | 52.2504 | 52.2504 | 52.2504 | 52.2504 | 52.2504 | 52.2504 | 52.2504 | 52.2504 | 52.2504 | 52.2504 | 52.2504 | 52.2504 | 52.2504
85% | 40.4636 | 35.1918 | 37.8228 | 38.0872 | 37.9576 | 38.0809 | 38.1315 | 38.2938 | 38.6274 | 38.9081 | 39.0374 | 38.9222 | 39.405 | 39.4816 | 39.391 | 39.5727 | 39.6662 | 39.6662 | 39.6662 | 39.6662 | 39.6662 | 39.6662 | 39.6662 | 39.6662 | 39.6662 | 39.6662 | 39.6662 | 39.6662 | 39.6662 | 39.6662 | 39.6662 | 85% | 1.1345 | 43.296 | 46.2364 | 46.3175 | 46.23 | 46.2525 | 46.4131 | 46.7385 | 47.3116 | 47.6102 | 47.8262 | 48.1532 | 48.5706 | 49.0753 | 49.3399 | 49.2541 | 49.3476 | 49.3476 | 49.3476 | 49.3476 | 49.3476 | 49.3476 | 49.3476 | 49.3476 | 49.3476 | 49.3476 | 49.3476 | 49.3476 | 49.3476 | 49.3476 | 49.3476
80% | 94.5411 | 33.1217 | 35.598 | 35.8468 | 35.7248 | 35.8408 | 35.8885 | 36.0412 | 36.3552 | 36.6194 | 36.741 | 36.6326 | 37.0871 | 37.1592 | 37.0739 | 37.2449 | 37.3329 | 37.3329 | 37.3329 | 37.3329 | 37.3329 | 37.3329 | 37.3329 | 37.3329 | 37.3329 | 37.3329 | 37.3329 | 37.3329 | 37.3329 | 37.3329 | 37.3329 | 80% | 2.6471 | 40.7492 | 43.5166 | 43.5929 | 43.5106 | 43.5318 | 43.6829 | 43.9892 | 44.5285 | 44.8096 | 45.0129 | 45.3206 | 45.7135 | 46.1886 | 46.4375 | 46.3568 | 46.4448 | 46.4448 | 46.4448 | 46.4448 | 46.4448 | 46.4448 | 46.4448 | 46.4448 | 46.4448 | 46.4448 | 46.4448 | 46.4448 | 46.4448 | 46.4448 | 46.4448
75% | 197.0236 | 31.0516 | 33.3731 | 33.6064 | 33.492 | 33.6008 | 33.6454 | 33.7886 | 34.083 | 34.3307 | 34.4447 | 34.3431 | 34.7692 | 34.8367 | 34.7568 | 34.9171 | 34.9996 | 34.9996 | 34.9996 | 34.9996 | 34.9996 | 34.9996 | 34.9996 | 34.9996 | 34.9996 | 34.9996 | 34.9996 | 34.9996 | 34.9996 | 34.9996 | 34.9996 | 75% | 3.4035 | 38.2023 | 40.7968 | 40.8684 | 40.7912 | 40.811 | 40.9527 | 41.2398 | 41.7455 | 42.009 | 42.1996 | 42.4881 | 42.8564 | 43.3018 | 43.5352 | 43.4595 | 43.542 | 43.542 | 43.542 | 43.542 | 43.542 | 43.542 | 43.542 | 43.542 | 43.542 | 43.542 | 43.542 | 43.542 | 43.542 | 43.542 | 43.542
70% | 336.9444 | 28.9815 | 31.1482 | 31.366 | 31.2592 | 31.3607 | 31.4024 | 31.5361 | 31.8108 | 32.042 | 32.1484 | 32.0536 | 32.4512 | 32.5143 | 32.4396 | 32.5893 | 32.6663 | 32.6663 | 32.6663 | 32.6663 | 32.6663 | 32.6663 | 32.6663 | 32.6663 | 32.6663 | 32.6663 | 32.6663 | 32.6663 | 32.6663 | 32.6663 | 32.6663 | 70% | 5.6725 | 35.6555 | 38.077 | 38.1438 | 38.0718 | 38.0903 | 38.2225 | 38.4905 | 38.9625 | 39.2084 | 39.3863 | 39.6555 | 39.9993 | 40.415 | 40.6328 | 40.5622 | 40.6392 | 40.6392 | 40.6392 | 40.6392 | 40.6392 | 40.6392 | 40.6392 | 40.6392 | 40.6392 | 40.6392 | 40.6392 | 40.6392 | 40.6392 | 40.6392 | 40.6392
65% | 521.4885 | 26.9114 | 28.9234 | 29.1255 | 29.0264 | 29.1207 | 29.1594 | 29.2835 | 29.5386 | 29.7533 | 29.8521 | 29.764 | 30.1333 | 30.1918 | 30.1225 | 30.2615 | 30.333 | 30.333 | 30.333 | 30.333 | 30.333 | 30.333 | 30.333 | 30.333 | 30.333 | 30.333 | 30.333 | 30.333 | 30.333 | 30.333 | 30.333 | 65% | 6.4288 | 33.1087 | 35.3572 | 35.4193 | 35.3524 | 35.3696 | 35.4924 | 35.7412 | 36.1794 | 36.4078 | 36.573 | 36.823 | 37.1422 | 37.5282 | 37.7305 | 37.6649 | 37.7364 | 37.7364 | 37.7364 | 37.7364 | 37.7364 | 37.7364 | 37.7364 | 37.7364 | 37.7364 | 37.7364 | 37.7364 | 37.7364 | 37.7364 | 37.7364 | 37.7364
60% | 812.675 | 24.8413 | 26.6985 | 26.8851 | 26.7936 | 26.8806 | 26.9164 | 27.0309 | 27.2664 | 27.4646 | 27.5558 | 27.4745 | 27.8153 | 27.8694 | 27.8054 | 27.9337 | 27.9997 | 27.9997 | 27.9997 | 27.9997 | 27.9997 | 27.9997 | 27.9997 | 27.9997 | 27.9997 | 27.9997 | 27.9997 | 27.9997 | 27.9997 | 27.9997 | 27.9997 | 60% | 11.3449 | 30.5619 | 32.6374 | 32.6947 | 32.633 | 32.6488 | 32.7622 | 32.9919 | 33.3964 | 33.6072 | 33.7597 | 33.9905 | 34.2851 | 34.6414 | 34.8281 | 34.7676 | 34.8336 | 34.8336 | 34.8336 | 34.8336 | 34.8336 | 34.8336 | 34.8336 | 34.8336 | 34.8336 | 34.8336 | 34.8336 | 34.8336 | 34.8336 | 34.8336 | 34.8336
55% | 1202.1843 | 22.7712 | 24.4736 | 24.6447 | 24.5608 | 24.6406 | 24.6733 | 24.7783 | 24.9942 | 25.1759 | 25.2595 | 25.1849 | 25.4974 | 25.5469 | 25.4883 | 25.6059 | 25.6664 | 25.6664 | 25.6664 | 25.6664 | 25.6664 | 25.6664 | 25.6664 | 25.6664 | 25.6664 | 25.6664 | 25.6664 | 25.6664 | 25.6664 | 25.6664 | 25.6664 | 55% | 35.5474 | 28.0151 | 29.9176 | 29.9701 | 29.9135 | 29.9281 | 30.032 | 30.2426 | 30.6134 | 30.8066 | 30.9464 | 31.1579 | 31.428 | 31.7546 | 31.9258 | 31.8703 | 31.9308 | 31.9308 | 31.9308 | 31.9308 | 31.9308 | 31.9308 | 31.9308 | 31.9308 | 31.9308 | 31.9308 | 31.9308 | 31.9308 | 31.9308 | 31.9308 | 31.9308
50% | 1686.2345 | 20.7011 | 22.2487 | 22.4043 | 22.328 | 22.4005 | 22.4303 | 22.5258 | 22.722 | 22.8871 | 22.9631 | 22.8954 | 23.1794 | 23.2245 | 23.1712 | 23.2781 | 23.3331 | 23.3331 | 23.3331 | 23.3331 | 23.3331 | 23.3331 | 23.3331 | 23.3331 | 23.3331 | 23.3331 | 23.3331 | 23.3331 | 23.3331 | 23.3331 | 23.3331 | 50% | 95.2974 | 25.4682 | 27.1979 | 27.2456 | 27.1941 | 27.2074 | 27.3018 | 27.4932 | 27.8303 | 28.006 | 28.1331 | 28.3254 | 28.5709 | 28.8678 | 29.0234 | 28.973 | 29.028 | 29.028 | 29.028 | 29.028 | 29.028 | 29.028 | 29.028 | 29.028 | 29.028 | 29.028 | 29.028 | 29.028 | 29.028 | 29.028 | 29.028
45% | 2129.0649 | 18.631 | 20.0239 | 20.1638 | 20.0952 | 20.1605 | 20.1873 | 20.2732 | 20.4498 | 20.5984 | 20.6668 | 20.6059 | 20.8615 | 20.902 | 20.8541 | 20.9503 | 20.9998 | 20.9998 | 20.9998 | 20.9998 | 20.9998 | 20.9998 | 20.9998 | 20.9998 | 20.9998 | 20.9998 | 20.9998 | 20.9998 | 20.9998 | 20.9998 | 20.9998 | 45% | 208.7467 | 22.9214 | 24.4781 | 24.521 | 24.4747 | 24.4866 | 24.5716 | 24.7439 | 25.0473 | 25.2054 | 25.3198 | 25.4928 | 25.7138 | 25.9811 | 26.1211 | 26.0757 | 26.1252 | 26.1252 | 26.1252 | 26.1252 | 26.1252 | 26.1252 | 26.1252 | 26.1252 | 26.1252 | 26.1252 | 26.1252 | 26.1252 | 26.1252 | 26.1252 | 26.1252
40% | 2484.5393 | 16.5608 | 17.799 | 17.9234 | 17.8624 | 17.9204 | 17.9442 | 18.0206 | 18.1776 | 18.3097 | 18.3705 | 18.3163 | 18.5435 | 18.5796 | 18.5369 | 18.6225 | 18.6665 | 18.6665 | 18.6665 | 18.6665 | 18.6665 | 18.6665 | 18.6665 | 18.6665 | 18.6665 | 18.6665 | 18.6665 | 18.6665 | 18.6665 | 18.6665 | 18.6665 | 40% | 380.4333 | 20.3746 | 21.7583 | 21.7965 | 21.7553 | 21.7659 | 21.8415 | 21.9946 | 22.2643 | 22.4048 | 22.5065 | 22.6603 | 22.8567 | 23.0943 | 23.2188 | 23.1784 | 23.2224 | 23.2224 | 23.2224 | 23.2224 | 23.2224 | 23.2224 | 23.2224 | 23.2224 | 23.2224 | 23.2224 | 23.2224 | 23.2224 | 23.2224 | 23.2224 | 23.2224
35% | 2808.248 | 14.4907 | 15.5741 | 15.683 | 15.6296 | 15.6804 | 15.7012 | 15.768 | 15.9054 | 16.021 | 16.0742 | 16.0268 | 16.2256 | 16.2571 | 16.2198 | 16.2947 | 16.3332 | 16.3332 | 16.3332 | 16.3332 | 16.3332 | 16.3332 | 16.3332 | 16.3332 | 16.3332 | 16.3332 | 16.3332 | 16.3332 | 16.3332 | 16.3332 | 16.3332 | 35% | 696.5786 | 17.8278 | 19.0385 | 19.0719 | 19.0359 | 19.0452 | 19.1113 | 19.2453 | 19.4812 | 19.6042 | 19.6931 | 19.8278 | 19.9997 | 20.2075 | 20.3164 | 20.2811 | 20.3196 | 20.3196 | 20.3196 | 20.3196 | 20.3196 | 20.3196 | 20.3196 | 20.3196 | 20.3196 | 20.3196 | 20.3196 | 20.3196 | 20.3196 | 20.3196 | 20.3196
30% | 3095.6528 | 12.4206 | 13.3492 | 13.4426 | 13.3968 | 13.4403 | 13.4582 | 13.5155 | 13.6332 | 13.7323 | 13.7779 | 13.7372 | 13.9077 | 13.9347 | 13.9027 | 13.9668 | 13.9998 | 13.9998 | 13.9998 | 13.9998 | 13.9998 | 13.9998 | 13.9998 | 13.9998 | 13.9998 | 13.9998 | 13.9998 | 13.9998 | 13.9998 | 13.9998 | 13.9998 | 30% | 1260.7997 | 15.2809 | 16.3187 | 16.3474 | 16.3165 | 16.3244 | 16.3811 | 16.4959 | 16.6982 | 16.8036 | 16.8798 | 16.9952 | 17.1426 | 17.3207 | 17.4141 | 17.3838 | 17.4168 | 17.4168 | 17.4168 | 17.4168 | 17.4168 | 17.4168 | 17.4168 | 17.4168 | 17.4168 | 17.4168 | 17.4168 | 17.4168 | 17.4168 | 17.4168 | 17.4168
25% | 3358.8552 | 10.3505 | 11.1244 | 11.2021 | 11.164 | 11.2003 | 11.2151 | 11.2629 | 11.361 | 11.4436 | 11.4816 | 11.4477 | 11.5897 | 11.6122 | 11.5856 | 11.639 | 11.6665 | 11.6665 | 11.6665 | 11.6665 | 11.6665 | 11.6665 | 11.6665 | 11.6665 | 11.6665 | 11.6665 | 11.6665 | 11.6665 | 11.6665 | 11.6665 | 11.6665 | 25% | 1965.3198 | 12.7341 | 13.5989 | 13.6228 | 13.5971 | 13.6037 | 13.6509 | 13.7466 | 13.9152 | 14.003 | 14.0665 | 14.1627 | 14.2855 | 14.4339 | 14.5117 | 14.4865 | 14.514 | 14.514 | 14.514 | 14.514 | 14.514 | 14.514 | 14.514 | 14.514 | 14.514 | 14.514 | 14.514 | 14.514 | 14.514 | 14.514 | 14.514
20% | 3588.7791 | 8.2804 | 8.8995 | 8.9617 | 8.9312 | 8.9602 | 8.9721 | 9.0103 | 9.0888 | 9.1549 | 9.1853 | 9.1582 | 9.2718 | 9.2898 | 9.2685 | 9.3112 | 9.3332 | 9.3332 | 9.3332 | 9.3332 | 9.3332 | 9.3332 | 9.3332 | 9.3332 | 9.3332 | 9.3332 | 9.3332 | 9.3332 | 9.3332 | 9.3332 | 9.3332 | 20% | 2490.2118 | 10.1873 | 10.8791 | 10.8982 | 10.8777 | 10.8829 | 10.9207 | 10.9973 | 11.1321 | 11.2024 | 11.2532 | 11.3302 | 11.4284 | 11.5471 | 11.6094 | 11.5892 | 11.6112 | 11.6112 | 11.6112 | 11.6112 | 11.6112 | 11.6112 | 11.6112 | 11.6112 | 11.6112 | 11.6112 | 11.6112 | 11.6112 | 11.6112 | 11.6112 | 11.6112
15% | 3802.4419 | 6.2103 | 6.6746 | 6.7213 | 6.6984 | 6.7202 | 6.7291 | 6.7577 | 6.8166 | 6.8661 | 6.8889 | 6.8686 | 6.9538 | 6.9673 | 6.9514 | 6.9834 | 6.9999 | 6.9999 | 6.9999 | 6.9999 | 6.9999 | 6.9999 | 6.9999 | 6.9999 | 6.9999 | 6.9999 | 6.9999 | 6.9999 | 6.9999 | 6.9999 | 6.9999 | 15% | 2997.7083 | 7.6405 | 8.1594 | 8.1737 | 8.1582 | 8.1622 | 8.1905 | 8.248 | 8.3491 | 8.4018 | 8.4399 | 8.4976 | 8.5713 | 8.6604 | 8.707 | 8.6919 | 8.7084 | 8.7084 | 8.7084 | 8.7084 | 8.7084 | 8.7084 | 8.7084 | 8.7084 | 8.7084 | 8.7084 | 8.7084 | 8.7084 | 8.7084 | 8.7084 | 8.7084
10% | 4024.8025 | 4.1402 | 4.4497 | 4.4809 | 4.4656 | 4.4801 | 4.4861 | 4.5052 | 4.5444 | 4.5774 | 4.5926 | 4.5791 | 4.6359 | 4.6449 | 4.6342 | 4.6556 | 4.6666 | 4.6666 | 4.6666 | 4.6666 | 4.6666 | 4.6666 | 4.6666 | 4.6666 | 4.6666 | 4.6666 | 4.6666 | 4.6666 | 4.6666 | 4.6666 | 4.6666 | 10% | 3491.5908 | 5.0936 | 5.4396 | 5.4491 | 5.4388 | 5.4415 | 5.4604 | 5.4986 | 5.5661 | 5.6012 | 5.6266 | 5.6651 | 5.7142 | 5.7736 | 5.8047 | 5.7946 | 5.8056 | 5.8056 | 5.8056 | 5.8056 | 5.8056 | 5.8056 | 5.8056 | 5.8056 | 5.8056 | 5.8056 | 5.8056 | 5.8056 | 5.8056 | 5.8056 | 5.8056
5% | 4239.978 | 2.0701 | 2.2249 | 2.2404 | 2.2328 | 2.2401 | 2.243 | 2.2526 | 2.2722 | 2.2887 | 2.2963 | 2.2895 | 2.3179 | 2.3224 | 2.3171 | 2.3278 | 2.3333 | 2.3333 | 2.3333 | 2.3333 | 2.3333 | 2.3333 | 2.3333 | 2.3333 | 2.3333 | 2.3333 | 2.3333 | 2.3333 | 2.3333 | 2.3333 | 2.3333 | 5% | 3955.9766 | 2.5468 | 2.7198 | 2.7246 | 2.7194 | 2.7207 | 2.7302 | 2.7493 | 2.783 | 2.8006 | 2.8133 | 2.8325 | 2.8571 | 2.8868 | 2.9023 | 2.8973 | 2.9028 | 2.9028 | 2.9028 | 2.9028 | 2.9028 | 2.9028 | 2.9028 | 2.9028 | 2.9028 | 2.9028 | 2.9028 | 2.9028 | 2.9028 | 2.9028 | 2.9028
9.992e-14% | 4391.6218 | 4.1369e-14 | 4.4462e-14 | 4.4773e-14 | 4.462e-14 | 4.4765e-14 | 4.4825e-14 | 4.5015e-14 | 4.5408e-14 | 4.5738e-14 | 4.589e-14 | 4.5754e-14 | 4.6322e-14 | 4.6412e-14 | 4.6305e-14 | 4.6519e-14 | 4.6629e-14 | 4.6629e-14 | 4.6629e-14 | 4.6629e-14 | 4.6629e-14 | 4.6629e-14 | 4.6629e-14 | 4.6629e-14 | 4.6629e-14 | 4.6629e-14 | 4.6629e-14 | 4.6629e-14 | 4.6629e-14 | 4.6629e-14 | 4.6629e-14 | 9.992e-14% | 4391.6218 | 5.0896e-14 | 5.4352e-14 | 5.4448e-14 | 5.4345e-14 | 5.4371e-14 | 5.456e-14 | 5.4943e-14 | 5.5616e-14 | 5.5967e-14 | 5.6221e-14 | 5.6605e-14 | 5.7096e-14 | 5.769e-14 | 5.8001e-14 | 5.79e-14 | 5.801e-14 | 5.801e-14 | 5.801e-14 | 5.801e-14 | 5.801e-14 | 5.801e-14 | 5.801e-14 | 5.801e-14 | 5.801e-14 | 5.801e-14 | 5.801e-14 | 5.801e-14 | 5.801e-14 | 5.801e-14 | 5.801e-14

## Locational VCR
Base case |  | Energy Usage (CY 2024 kWh) | Energy Usage (CY 2024 %) | Tailored VCR
Dec 24 AER VCR ($/kWh) - Res | 49.23 | 88661416.1819 | 59.86% | 29.4686
Dec 24 AER VCR ($/kWh) - Com | 34.39 | 45585213.1364 | 30.78% | 10.584
Dec 24 AER VCR ($/kWh) - Ind | 33.49 | 5851096.6819 | 3.95% | 1.323
Dec 24 AER VCR ($/kWh) - Agr | 22.25 | 8019086.0298 | 5.414% | 1.2046
|  | 148116812.03 |  | 42.5803 | KW/h
|  |  |  | 42580.277 | MW/h

## E@R N
Option 1 - Do Nothing
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | FY38: 0.12591; FY39: 0.23273; FY40: 0.23273; FY41: 0.23273; FY42: 0.23273; FY43: 0.23273; FY44: 0.23273; FY45: 0.23273; FY46: 0.23273; FY47: 0.23273; FY48: 0.23273; FY49: 0.23273; FY50: 0.23273; FY51: 0.23273; FY52: 0.23273; FY53: 0.23273; FY54: 0.23273 | [11 empty] | 0.19329 |  | 0.14663 | 0.44853 | 0.3245 | 0.3245 | 0.3245 | 0.3245 | 0.3245 | 0.3245 | 0.3245 | 0.3245 | 0.3245 | 0.3245 | 0.3245 | 0.3245 | 0.3245 | 0.3245 | 0.3245 | 0.3245
98% | FY38: 0; FY39: 0; FY40: 0; FY41: 0; FY42: 0; FY43: 0; FY44: 0; FY45: 0; FY46: 0; FY47: 0; FY48: 0; FY49: 0; FY50: 0; FY51: 0; FY52: 0; FY53: 0; FY54: 0 | [11 empty] | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
97% | [44 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
95% | [44 empty] | 0.00098805
90%
85%
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.12466 | 0.2304 | 0.2304 | 0.2304 | 0.2304 | 0.2304 | 0.2304 | 0.2304 | 0.2304 | 0.2304 | 0.2304 | 0.2304 | 0.2304 | 0.2304 | 0.2304 | 0.2304 | 0.2304 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.19136 | 0 | 0.14517 | 0.44502 | 0.32125 | 0.32125 | 0.32125 | 0.32125 | 0.32125 | 0.32125 | 0.32125 | 0.32125 | 0.32125 | 0.32125 | 0.32125 | 0.32125 | 0.32125 | 0.32125 | 0.32125 | 0.32125
Option 1 Winter POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.087259 | 0.16128 | 0.16128 | 0.16128 | 0.16128 | 0.16128 | 0.16128 | 0.16128 | 0.16128 | 0.16128 | 0.16128 | 0.16128 | 0.16128 | 0.16128 | 0.16128 | 0.16128 | 0.16128 | Option 1 Winter POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.057407 | 0 | 0.04355 | 0.13351 | 0.096375 | 0.096375 | 0.096375 | 0.096375 | 0.096375 | 0.096375 | 0.096375 | 0.096375 | 0.096375 | 0.096375 | 0.096375 | 0.096375 | 0.096375 | 0.096375 | 0.096375 | 0.096375
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | [39 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
98% | [41 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
97% | [42 empty] | 0.013107 | 0.18617 | 0.30092 | 0.26372 | 0.30427 | 0.30427 | 0.30427 | 0.30427 | 0.30427 | 0.30427 | 0.30427 | 0.30427 | 0.30427 | 0.30427 | 0.30427 | 0.30427 | 0.30427 | 0.30427 | 0.30427
95% | [43 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
90%
85%
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.012976 | 0.18431 | 0.29791 | 0.26108 | 0.30123 | 0.30123 | 0.30123 | 0.30123 | 0.30123 | 0.30123 | 0.30123 | 0.30123 | 0.30123 | 0.30123 | 0.30123 | 0.30123 | 0.30123 | 0.30123 | 0.30123
Option 1 Summer POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 1 Summer POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0038927 | 0.055292 | 0.089372 | 0.078324 | 0.090369 | 0.090369 | 0.090369 | 0.090369 | 0.090369 | 0.090369 | 0.090369 | 0.090369 | 0.090369 | 0.090369 | 0.090369 | 0.090369 | 0.090369 | 0.090369 | 0.090369
Option 2 - Replace 3 x 10/13.5 MVA Tx with 3 x 20/33 MVA Tx
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99%
98%
97%
95%
90%
85%
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2 Winter POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 2 Winter POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99
98%
97%
95%
90%
85%
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2 Summer POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 2 Summer POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 - Replace 1 x 10/13.5 MVA Tx with 1 x 20/33 MVA Tx
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99%
98%
97%
95%
90%
85%
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 Winter POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 3 Winter POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99
98%
97%
95%
90%
85%
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 Summer POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 3 Summer POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 - Construct 2x 20/33MVA zone substation in Inverloch
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99%
98%
97%
95%
90%
85%
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 Winter POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 4 Winter POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99
98%
97%
95%
90%
85%
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 Summer POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 4 Summer POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 - Contract network support services to defer network investment
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99%
98%
97%
95%
90%
85%
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 Winter POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 5 Winter POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99
98%
97%
95%
90%
85%
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 Summer POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 5 Summer POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 6 -
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | FY38: 0.12591; FY39: 0.23273; FY40: 0.23273; FY41: 0.23273; FY42: 0.23273; FY43: 0.23273; FY44: 0.23273; FY45: 0.23273; FY46: 0.23273; FY47: 0.23273; FY48: 0.23273; FY49: 0.23273; FY50: 0.23273; FY51: 0.23273; FY52: 0.23273; FY53: 0.23273; FY54: 0.23273 | [11 empty] | 0.19329 |  | 0.14663 | 0.44853 | 0.3245 | 0.3245 | 0.3245 | 0.3245 | 0.3245 | 0.3245 | 0.3245 | 0.3245 | 0.3245 | 0.3245 | 0.3245 | 0.3245 | 0.3245 | 0.3245 | 0.3245 | 0.3245
98% | FY38: 0; FY39: 0; FY40: 0; FY41: 0; FY42: 0; FY43: 0; FY44: 0; FY45: 0; FY46: 0; FY47: 0; FY48: 0; FY49: 0; FY50: 0; FY51: 0; FY52: 0; FY53: 0; FY54: 0 | [11 empty] | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
97% | [44 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
95% | [44 empty] | 0.00098805
90%
85%
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.12466 | 0.2304 | 0.2304 | 0.2304 | 0.2304 | 0.2304 | 0.2304 | 0.2304 | 0.2304 | 0.2304 | 0.2304 | 0.2304 | 0.2304 | 0.2304 | 0.2304 | 0.2304 | 0.2304 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.19136 | 0 | 0.14517 | 0.44502 | 0.32125 | 0.32125 | 0.32125 | 0.32125 | 0.32125 | 0.32125 | 0.32125 | 0.32125 | 0.32125 | 0.32125 | 0.32125 | 0.32125 | 0.32125 | 0.32125 | 0.32125 | 0.32125
Option 6 Winter POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.087259 | 0.16128 | 0.16128 | 0.16128 | 0.16128 | 0.16128 | 0.16128 | 0.16128 | 0.16128 | 0.16128 | 0.16128 | 0.16128 | 0.16128 | 0.16128 | 0.16128 | 0.16128 | 0.16128 | Option 6 Winter POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.057407 | 0 | 0.04355 | 0.13351 | 0.096375 | 0.096375 | 0.096375 | 0.096375 | 0.096375 | 0.096375 | 0.096375 | 0.096375 | 0.096375 | 0.096375 | 0.096375 | 0.096375 | 0.096375 | 0.096375 | 0.096375 | 0.096375
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | [39 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
98% | [41 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
97% | [42 empty] | 0.013107 | 0.18617 | 0.30092 | 0.26372 | 0.30427 | 0.30427 | 0.30427 | 0.30427 | 0.30427 | 0.30427 | 0.30427 | 0.30427 | 0.30427 | 0.30427 | 0.30427 | 0.30427 | 0.30427 | 0.30427 | 0.30427
95% | [43 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
90%
85%
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.012976 | 0.18431 | 0.29791 | 0.26108 | 0.30123 | 0.30123 | 0.30123 | 0.30123 | 0.30123 | 0.30123 | 0.30123 | 0.30123 | 0.30123 | 0.30123 | 0.30123 | 0.30123 | 0.30123 | 0.30123 | 0.30123
Option 6 Summer POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 6 Summer POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0038927 | 0.055292 | 0.089372 | 0.078324 | 0.090369 | 0.090369 | 0.090369 | 0.090369 | 0.090369 | 0.090369 | 0.090369 | 0.090369 | 0.090369 | 0.090369 | 0.090369 | 0.090369 | 0.090369 | 0.090369 | 0.090369
Option 7 -
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | FY38: 0.12591; FY39: 0.23273; FY40: 0.23273; FY41: 0.23273; FY42: 0.23273; FY43: 0.23273; FY44: 0.23273; FY45: 0.23273; FY46: 0.23273; FY47: 0.23273; FY48: 0.23273; FY49: 0.23273; FY50: 0.23273; FY51: 0.23273; FY52: 0.23273; FY53: 0.23273; FY54: 0.23273 | [11 empty] | 0.19329 |  | 0.14663 | 0.44853 | 0.3245 | 0.3245 | 0.3245 | 0.3245 | 0.3245 | 0.3245 | 0.3245 | 0.3245 | 0.3245 | 0.3245 | 0.3245 | 0.3245 | 0.3245 | 0.3245 | 0.3245 | 0.3245
98% | FY38: 0; FY39: 0; FY40: 0; FY41: 0; FY42: 0; FY43: 0; FY44: 0; FY45: 0; FY46: 0; FY47: 0; FY48: 0; FY49: 0; FY50: 0; FY51: 0; FY52: 0; FY53: 0; FY54: 0 | [11 empty] | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
97% | [44 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
95% | [44 empty] | 0.00098805
90%
85%
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.12466 | 0.2304 | 0.2304 | 0.2304 | 0.2304 | 0.2304 | 0.2304 | 0.2304 | 0.2304 | 0.2304 | 0.2304 | 0.2304 | 0.2304 | 0.2304 | 0.2304 | 0.2304 | 0.2304 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.19136 | 0 | 0.14517 | 0.44502 | 0.32125 | 0.32125 | 0.32125 | 0.32125 | 0.32125 | 0.32125 | 0.32125 | 0.32125 | 0.32125 | 0.32125 | 0.32125 | 0.32125 | 0.32125 | 0.32125 | 0.32125 | 0.32125
Option 7 Winter POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.087259 | 0.16128 | 0.16128 | 0.16128 | 0.16128 | 0.16128 | 0.16128 | 0.16128 | 0.16128 | 0.16128 | 0.16128 | 0.16128 | 0.16128 | 0.16128 | 0.16128 | 0.16128 | 0.16128 | Option 7 Winter POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.057407 | 0 | 0.04355 | 0.13351 | 0.096375 | 0.096375 | 0.096375 | 0.096375 | 0.096375 | 0.096375 | 0.096375 | 0.096375 | 0.096375 | 0.096375 | 0.096375 | 0.096375 | 0.096375 | 0.096375 | 0.096375 | 0.096375
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | [39 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
98% | [41 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
97% | [42 empty] | 0.013107 | 0.18617 | 0.30092 | 0.26372 | 0.30427 | 0.30427 | 0.30427 | 0.30427 | 0.30427 | 0.30427 | 0.30427 | 0.30427 | 0.30427 | 0.30427 | 0.30427 | 0.30427 | 0.30427 | 0.30427 | 0.30427
95% | [43 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
90%
85%
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.012976 | 0.18431 | 0.29791 | 0.26108 | 0.30123 | 0.30123 | 0.30123 | 0.30123 | 0.30123 | 0.30123 | 0.30123 | 0.30123 | 0.30123 | 0.30123 | 0.30123 | 0.30123 | 0.30123 | 0.30123 | 0.30123
Option 7 Summer POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 7 Summer POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0038927 | 0.055292 | 0.089372 | 0.078324 | 0.090369 | 0.090369 | 0.090369 | 0.090369 | 0.090369 | 0.090369 | 0.090369 | 0.090369 | 0.090369 | 0.090369 | 0.090369 | 0.090369 | 0.090369 | 0.090369 | 0.090369
Option 8 -
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | FY38: 0.12591; FY39: 0.23273; FY40: 0.23273; FY41: 0.23273; FY42: 0.23273; FY43: 0.23273; FY44: 0.23273; FY45: 0.23273; FY46: 0.23273; FY47: 0.23273; FY48: 0.23273; FY49: 0.23273; FY50: 0.23273; FY51: 0.23273; FY52: 0.23273; FY53: 0.23273; FY54: 0.23273 | [11 empty] | 0.19329 |  | 0.14663 | 0.44853 | 0.3245 | 0.3245 | 0.3245 | 0.3245 | 0.3245 | 0.3245 | 0.3245 | 0.3245 | 0.3245 | 0.3245 | 0.3245 | 0.3245 | 0.3245 | 0.3245 | 0.3245 | 0.3245
98% | FY38: 0; FY39: 0; FY40: 0; FY41: 0; FY42: 0; FY43: 0; FY44: 0; FY45: 0; FY46: 0; FY47: 0; FY48: 0; FY49: 0; FY50: 0; FY51: 0; FY52: 0; FY53: 0; FY54: 0 | [11 empty] | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
97% | [44 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
95% | [44 empty] | 0.00098805
90%
85%
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.12466 | 0.2304 | 0.2304 | 0.2304 | 0.2304 | 0.2304 | 0.2304 | 0.2304 | 0.2304 | 0.2304 | 0.2304 | 0.2304 | 0.2304 | 0.2304 | 0.2304 | 0.2304 | 0.2304 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.19136 | 0 | 0.14517 | 0.44502 | 0.32125 | 0.32125 | 0.32125 | 0.32125 | 0.32125 | 0.32125 | 0.32125 | 0.32125 | 0.32125 | 0.32125 | 0.32125 | 0.32125 | 0.32125 | 0.32125 | 0.32125 | 0.32125
Option 8 Winter POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.087259 | 0.16128 | 0.16128 | 0.16128 | 0.16128 | 0.16128 | 0.16128 | 0.16128 | 0.16128 | 0.16128 | 0.16128 | 0.16128 | 0.16128 | 0.16128 | 0.16128 | 0.16128 | 0.16128 | Option 8 Winter POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.057407 | 0 | 0.04355 | 0.13351 | 0.096375 | 0.096375 | 0.096375 | 0.096375 | 0.096375 | 0.096375 | 0.096375 | 0.096375 | 0.096375 | 0.096375 | 0.096375 | 0.096375 | 0.096375 | 0.096375 | 0.096375 | 0.096375
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | [39 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
98% | [41 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
97% | [42 empty] | 0.013107 | 0.18617 | 0.30092 | 0.26372 | 0.30427 | 0.30427 | 0.30427 | 0.30427 | 0.30427 | 0.30427 | 0.30427 | 0.30427 | 0.30427 | 0.30427 | 0.30427 | 0.30427 | 0.30427 | 0.30427 | 0.30427
95% | [43 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
90%
85%
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.012976 | 0.18431 | 0.29791 | 0.26108 | 0.30123 | 0.30123 | 0.30123 | 0.30123 | 0.30123 | 0.30123 | 0.30123 | 0.30123 | 0.30123 | 0.30123 | 0.30123 | 0.30123 | 0.30123 | 0.30123 | 0.30123
Option 8 Summer POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 8 Summer POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0038927 | 0.055292 | 0.089372 | 0.078324 | 0.090369 | 0.090369 | 0.090369 | 0.090369 | 0.090369 | 0.090369 | 0.090369 | 0.090369 | 0.090369 | 0.090369 | 0.090369 | 0.090369 | 0.090369 | 0.090369 | 0.090369

## E@R N-1
Option 1 - Do Nothing
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | 0.92537 | 2.1455 | 2.2748 | 2.4348 | 2.6471 | 2.8485 | 3.2003 | 4.0851 | 4.5611 | 4.2139 | 5.2888 | 5.4825 | 5.6217 | 6.2779 | 6.3847 | 6.3847 | 6.3847 | 6.3847 | 6.3847 | 6.3847 | 6.3847 | 6.3847 | 6.3847 | 6.3847 | 6.3847 | 6.3847 | 6.3847 | 6.3847 | 6.3847 | 6.3847 |  | 2.0467 | 3.2105 | 3.331 | 3.7469 | 3.7368 | 3.8283 | 4.186 | 5.2137 | 5.6378 | 5.2363 | 6.3453 | 5.8797 | 6.2986 | 6.6005 | 6.4765 | 6.4765 | 6.4765 | 6.4765 | 6.4765 | 6.4765 | 6.4765 | 6.4765 | 6.4765 | 6.4765 | 6.4765 | 6.4765 | 6.4765 | 6.4765 | 6.4765 | 6.4765
98% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
97% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
95% | 2.0617 | 6.7704 | 7.2696 | 7.8869 | 8.7065 | 9.4834 | 10.8412 | 14.2562 | 16.093 | 14.753 | 18.9015 | 19.6489 | 20.1862 | 22.7188 | 23.131 | 23.131 | 23.131 | 23.131 | 23.131 | 23.131 | 23.131 | 23.131 | 23.131 | 23.131 | 23.131 | 23.131 | 23.131 | 23.131 | 23.131 | 23.131 |  | 6.3892 | 10.8806 | 11.3457 | 12.9509 | 12.9118 | 13.2648 | 14.6453 | 18.6116 | 20.2483 | 18.699 | 22.9788 | 21.1819 | 22.7987 | 23.9639 | 23.4852 | 23.4852 | 23.4852 | 23.4852 | 23.4852 | 23.4852 | 23.4852 | 23.4852 | 23.4852 | 23.4852 | 23.4852 | 23.4852 | 23.4852 | 23.4852 | 23.4852 | 23.4852
90% | 3.2506 | 29.7534 | 32.6399 | 36.2085 | 40.9465 | 45.4383 | 53.2881 | 73.0309 | 83.65 | 75.9031 | 99.8865 | 104.2076 | 107.3137 | 121.9552 | 124.3384 | 124.3384 | 124.3384 | 124.3384 | 124.3384 | 124.3384 | 124.3384 | 124.3384 | 124.3384 | 124.3384 | 124.3384 | 124.3384 | 124.3384 | 124.3384 | 124.3384 | 124.3384 |  | 27.5498 | 53.5156 | 56.2046 | 65.4847 | 65.2585 | 67.2992 | 75.2803 | 98.2105 | 107.6729 | 98.716 | 123.4584 | 113.0702 | 122.4175 | 129.1533 | 126.3859 | 126.3859 | 126.3859 | 126.3859 | 126.3859 | 126.3859 | 126.3859 | 126.3859 | 126.3859 | 126.3859 | 126.3859 | 126.3859 | 126.3859 | 126.3859 | 126.3859 | 126.3859
85% |  | 62.8339 | 74.8936 | 89.803 | 109.5982 | 128.3646 | 161.1605 | 243.6444 | 288.0101 | 255.644 | 355.845 | 373.8982 | 386.8755 | 448.0465 | 458.0033 | 458.0033 | 458.0033 | 458.0033 | 458.0033 | 458.0033 | 458.0033 | 458.0033 | 458.0033 | 458.0033 | 458.0033 | 458.0033 | 458.0033 | 458.0033 | 458.0033 | 458.0033 |  | 53.6277 | 162.111 | 173.3454 | 212.1168 | 211.1719 | 219.6975 | 253.0423 | 348.8429 | 388.3761 | 350.9549 | 454.327 | 410.9258 | 449.9778 | 478.1195 | 466.5576 | 466.5576 | 466.5576 | 466.5576 | 466.5576 | 466.5576 | 466.5576 | 466.5576 | 466.5576 | 466.5576 | 466.5576 | 466.5576 | 466.5576 | 466.5576 | 466.5576 | 466.5576
80% |  | 9.9766 | 19.6484 | 35.8864 | 64.3977 | 94.1103 | 146.0357 | 276.6314 | 346.8752 | 295.6303 | 454.2773 | 482.8608 | 503.4075 | 600.259 | 616.0234 | 616.0234 | 616.0234 | 616.0234 | 616.0234 | 616.0234 | 616.0234 | 616.0234 | 616.0234 | 616.0234 | 616.0234 | 616.0234 | 616.0234 | 616.0234 | 616.0234 | 616.0234 |  | 4.7409 | 147.5405 | 165.3278 | 226.7142 | 225.2181 | 238.7166 | 291.511 | 443.1911 | 505.7834 | 446.5349 | 610.2027 | 541.4861 | 603.3167 | 647.8732 | 629.5673 | 629.5673 | 629.5673 | 629.5673 | 629.5673 | 629.5673 | 629.5673 | 629.5673 | 629.5673 | 629.5673 | 629.5673 | 629.5673 | 629.5673 | 629.5673 | 629.5673 | 629.5673
75% |  |  |  |  | 0.17202 | 9.0242 | 55.3334 | 283.3902 | 413.139 | 318.4834 | 611.524 | 664.3211 | 702.2736 | 881.1701 | 910.289 | 910.289 | 910.289 | 910.289 | 910.289 | 910.289 | 910.289 | 910.289 | 910.289 | 910.289 | 910.289 | 910.289 | 910.289 | 910.289 | 910.289 | 910.289 |  |  | 57.2368 | 82.0481 | 191.187 | 188.4235 | 213.3569 | 310.8747 | 591.0464 | 706.6621 | 597.2228 | 899.5374 | 772.6094 | 886.8181 | 969.1193 | 935.3061 | 935.3061 | 935.3061 | 935.3061 | 935.3061 | 935.3061 | 935.3061 | 935.3061 | 935.3061 | 935.3061 | 935.3061 | 935.3061 | 935.3061 | 935.3061 | 935.3061 | 935.3061
70% | [7 empty] | 78.2842 | 250.9431 | 115.8555 | 573.8626 | 659.8027 | 721.5795 | 1012.7769 | 1060.1748 | 1060.1748 | 1060.1748 | 1060.1748 | 1060.1748 | 1060.1748 | 1060.1748 | 1060.1748 | 1060.1748 | 1060.1748 | 1060.1748 | 1060.1748 | 1060.1748 | 1060.1748 | 1060.1748 | 1060.1748 |  |  |  |  | 13.9473 | 12.8131 | 24.7488 | 107.115 | 540.5303 | 728.7229 | 550.584 | 1042.6741 | 836.068 | 1021.9704 | 1155.9355 | 1100.8963 | 1100.8963 | 1100.8963 | 1100.8963 | 1100.8963 | 1100.8963 | 1100.8963 | 1100.8963 | 1100.8963 | 1100.8963 | 1100.8963 | 1100.8963 | 1100.8963 | 1100.8963 | 1100.8963 | 1100.8963
65% | [8 empty] | 0.40539 |  | 145.0109 | 224.7284 | 292.046 | 647.5312 | 705.573 | 705.573 | 705.573 | 705.573 | 705.573 | 705.573 | 705.573 | 705.573 | 705.573 | 705.573 | 705.573 | 705.573 | 705.573 | 705.573 | 705.573 | 705.573 | [8 empty] | 118.5664 | 300.3588 | 126.2751 | 684.1423 | 431.1402 | 658.7893 | 822.8379 | 755.439 | 755.439 | 755.439 | 755.439 | 755.439 | 755.439 | 755.439 | 755.439 | 755.439 | 755.439 | 755.439 | 755.439 | 755.439 | 755.439 | 755.439 | 755.439
60% | FY38: 91.1742; FY39: 126.8218; FY40: 126.8218; FY41: 126.8218; FY42: 126.8218; FY43: 126.8218; FY44: 126.8218; FY45: 126.8218; FY46: 126.8218; FY47: 126.8218; FY48: 126.8218; FY49: 126.8218; FY50: 126.8218; FY51: 126.8218; FY52: 126.8218; FY53: 126.8218; FY54: 126.8218 | [11 empty] | 113.0025 | 9.404 | 97.6462 | 215.8063 | 161.9203 | 161.9203 | 161.9203 | 161.9203 | 161.9203 | 161.9203 | 161.9203 | 161.9203 | 161.9203 | 161.9203 | 161.9203 | 161.9203 | 161.9203 | 161.9203 | 161.9203 | 161.9203
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 6.1753 | 110.3648 | 135.3591 | 170.4974 | 224.2034 | 286.3766 | 425.5606 | 963.5892 | 1389.6401 | 1069.6783 | 2241.9506 | 2509.6007 | 2711.9106 | 3793.5907 | 3990.4321 | 3990.4321 | 3990.4321 | 3990.4321 | 3990.4321 | 3990.4321 | 3990.4321 | 3990.4321 | 3990.4321 | 3990.4321 | 3990.4321 | 3990.4321 | 3990.4321 | 3990.4321 | 3990.4321 | 3990.4321 | E @ R (MWh) | 93.4108 | 430.15 | 486.6866 | 718.8864 | 712.3384 | 773.1029 | 1046.0881 | 2142.5708 | 2735.8276 | 2172.2809 | 3917.1019 | 3110.3477 | 3831.3331 | 4404.9152 | 4163.9737 | 4163.9737 | 4163.9737 | 4163.9737 | 4163.9737 | 4163.9737 | 4163.9737 | 4163.9737 | 4163.9737 | 4163.9737 | 4163.9737 | 4163.9737 | 4163.9737 | 4163.9737 | 4163.9737 | 4163.9737
Option 1 Winter POE50 W E @ R (MWh) N 1 | 4.3227 | 77.2554 | 94.7514 | 119.3482 | 156.9424 | 200.4636 | 297.8924 | 674.5125 | 972.7481 | 748.7748 | 1569.3654 | 1756.7205 | 1898.3374 | 2655.5135 | 2793.3025 | 2793.3025 | 2793.3025 | 2793.3025 | 2793.3025 | 2793.3025 | 2793.3025 | 2793.3025 | 2793.3025 | 2793.3025 | 2793.3025 | 2793.3025 | 2793.3025 | 2793.3025 | 2793.3025 | 2793.3025 | Option 1 Winter POE10 W E @ R (MWh) N 1 | 28.0232 | 129.045 | 146.006 | 215.6659 | 213.7015 | 231.9309 | 313.8264 | 642.7712 | 820.7483 | 651.6843 | 1175.1306 | 933.1043 | 1149.3999 | 1321.4746 | 1249.1921 | 1249.1921 | 1249.1921 | 1249.1921 | 1249.1921 | 1249.1921 | 1249.1921 | 1249.1921 | 1249.1921 | 1249.1921 | 1249.1921 | 1249.1921 | 1249.1921 | 1249.1921 | 1249.1921 | 1249.1921
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | 2.2293 | 3.394 | 3.5111 | 3.4537 | 3.5082 | 3.5307 | 3.6025 | 3.7502 | 3.8744 | 3.9316 | 3.8807 | 4.0944 | 4.1283 | 4.0882 | 4.1686 | 4.21 | 4.21 | 4.21 | 4.21 | 4.21 | 4.21 | 4.21 | 4.21 | 4.21 | 4.21 | 4.21 | 4.21 | 4.21 | 4.21 | 4.21 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
98% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
97% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 5.4316 | 6.7071 | 6.7423 | 6.7043 | 6.7141 | 6.7837 | 6.9249 | 7.1735 | 7.303 | 7.3967 | 7.5385 | 7.7196 | 7.9385 | 8.0533 | 8.0161 | 8.0566 | 8.0566 | 8.0566 | 8.0566 | 8.0566 | 8.0566 | 8.0566 | 8.0566 | 8.0566 | 8.0566 | 8.0566 | 8.0566 | 8.0566 | 8.0566 | 8.0566
95% | 1.6813 | 2.8051 | 2.918 | 2.8626 | 2.9153 | 2.9369 | 3.0062 | 3.1487 | 3.2686 | 3.3238 | 3.2746 | 3.4808 | 3.5135 | 3.4748 | 3.5524 | 3.5924 | 3.5924 | 3.5924 | 3.5924 | 3.5924 | 3.5924 | 3.5924 | 3.5924 | 3.5924 | 3.5924 | 3.5924 | 3.5924 | 3.5924 | 3.5924 | 3.5924 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
90% | 24.9336 | 48.7543 | 51.148 | 49.9747 | 51.0903 | 51.5487 | 53.0179 | 56.0388 | 58.5802 | 59.75 | 58.7073 | 63.079 | 63.7723 | 62.9518 | 64.5971 | 65.4437 | 65.4437 | 65.4437 | 65.4437 | 65.4437 | 65.4437 | 65.4437 | 65.4437 | 65.4437 | 65.4437 | 65.4437 | 65.4437 | 65.4437 | 65.4437 | 65.4437 |  | 4.4685 | 5.6785 | 5.7119 | 5.6759 | 5.6852 | 5.7513 | 5.8852 | 6.121 | 6.2439 | 6.3328 | 6.4674 | 6.6391 | 6.8469 | 6.9557 | 6.9204 | 6.9589 | 6.9589 | 6.9589 | 6.9589 | 6.9589 | 6.9589 | 6.9589 | 6.9589 | 6.9589 | 6.9589 | 6.9589 | 6.9589 | 6.9589 | 6.9589 | 6.9589
85% | 29.1806 | 114.1031 | 122.6458 | 118.4583 | 122.4399 | 124.0759 | 129.3191 | 140.1002 | 149.1697 | 153.3447 | 149.6235 | 165.225 | 167.6994 | 164.7711 | 170.643 | 173.664 | 173.664 | 173.664 | 173.664 | 173.664 | 173.664 | 173.664 | 173.664 | 173.664 | 173.664 | 173.664 | 173.664 | 173.664 | 173.664 | 173.664 |  | 3.5054 | 4.65 | 4.6816 | 4.6475 | 4.6563 | 4.7188 | 4.8455 | 5.0686 | 5.1848 | 5.2689 | 5.3962 | 5.5587 | 5.7552 | 5.8582 | 5.8248 | 5.8612 | 5.8612 | 5.8612 | 5.8612 | 5.8612 | 5.8612 | 5.8612 | 5.8612 | 5.8612 | 5.8612 | 5.8612 | 5.8612 | 5.8612 | 5.8612 | 5.8612
80% |  | 76.2716 | 90.1487 | 83.3465 | 89.8144 | 92.4719 | 100.9891 | 118.5024 | 133.2353 | 140.0173 | 133.9725 | 159.3161 | 163.3356 | 158.5788 | 168.1174 | 173.0249 | 173.0249 | 173.0249 | 173.0249 | 173.0249 | 173.0249 | 173.0249 | 173.0249 | 173.0249 | 173.0249 | 173.0249 | 173.0249 | 173.0249 | 173.0249 | 173.0249 |  | 10.169 | 14.4859 | 14.605 | 14.4766 | 14.5096 | 14.7454 | 15.2231 | 16.0645 | 16.5029 | 16.8201 | 17.3001 | 17.9129 | 18.654 | 19.0424 | 18.9165 | 19.0537 | 19.0537 | 19.0537 | 19.0537 | 19.0537 | 19.0537 | 19.0537 | 19.0537 | 19.0537 | 19.0537 | 19.0537 | 19.0537 | 19.0537 | 19.0537 | 19.0537
75% |  | 2.0449 | 6.8387 | 4.1421 | 6.6906 | 7.9111 | 12.4972 | 25.1118 | 38.9762 | 46.3383 | 39.7468 | 70.6015 | 76.2631 | 69.5855 | 83.2676 | 90.7587 | 90.7587 | 90.7587 | 90.7587 | 90.7587 | 90.7587 | 90.7587 | 90.7587 | 90.7587 | 90.7587 | 90.7587 | 90.7587 | 90.7587 | 90.7587 | 90.7587 |  | 3.1582 | 5.1859 | 5.2419 | 5.1815 | 5.197 | 5.3078 | 5.5322 | 5.9274 | 6.1333 | 6.2823 | 6.5077 | 6.7956 | 7.1436 | 7.3261 | 7.2669 | 7.3314 | 7.3314 | 7.3314 | 7.3314 | 7.3314 | 7.3314 | 7.3314 | 7.3314 | 7.3314 | 7.3314 | 7.3314 | 7.3314 | 7.3314 | 7.3314 | 7.3314
70% | [31 empty] | 3.696 | 9.3866 | 9.5436 | 9.3743 | 9.4178 | 9.7286 | 10.3583 | 11.4674 | 12.0453 | 12.4634 | 13.0962 | 13.904 | 14.8809 | 15.3928 | 15.2268 | 15.4078 | 15.4078 | 15.4078 | 15.4078 | 15.4078 | 15.4078 | 15.4078 | 15.4078 | 15.4078 | 15.4078 | 15.4078 | 15.4078 | 15.4078 | 15.4078 | 15.4078
65% | [31 empty] | 0.018768 | 1.0718 | 1.1205 | 1.068 | 1.0815 | 1.1779 | 1.3734 | 1.7176 | 1.8969 | 2.0267 | 2.2231 | 2.4738 | 2.7769 | 2.9358 | 2.8843 | 2.9405 | 2.9405 | 2.9405 | 2.9405 | 2.9405 | 2.9405 | 2.9405 | 2.9405 | 2.9405 | 2.9405 | 2.9405 | 2.9405 | 2.9405 | 2.9405 | 2.9405
60% | [32 empty] | 0.0029592 | 0.012833 | 0.0024792 | 0.0043735 | 0.033315 | 0.17404 | 0.6831 | 1.0771 | 1.4159 | 2.0129 | 2.9198 | 4.2275 | 5.003 | 4.7449 | 5.0266 | 5.0266 | 5.0266 | 5.0266 | 5.0266 | 5.0266 | 5.0266 | 5.0266 | 5.0266 | 5.0266 | 5.0266 | 5.0266 | 5.0266 | 5.0266 | 5.0266
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 57.4445 | 244.8992 | 274.4381 | 259.6155 | 273.6942 | 279.6505 | 299.4076 | 343.1855 | 383.2333 | 402.6387 | 385.3134 | 461.1388 | 473.9252 | 458.8156 | 489.4027 | 505.5867 | 505.5867 | 505.5867 | 505.5867 | 505.5867 | 505.5867 | 505.5867 | 505.5867 | 505.5867 | 505.5867 | 505.5867 | 505.5867 | 505.5867 | 505.5867 | 505.5867 | E @ R (MWh) | 30.4474 | 46.6971 | 47.183 | 46.6594 | 46.7933 | 47.7643 | 49.8134 | 53.6808 | 55.8233 | 57.4266 | 59.9366 | 63.2842 | 67.5413 | 69.8615 | 69.1027 | 69.9304 | 69.9304 | 69.9304 | 69.9304 | 69.9304 | 69.9304 | 69.9304 | 69.9304 | 69.9304 | 69.9304 | 69.9304 | 69.9304 | 69.9304 | 69.9304 | 69.9304
Option 1 Summer POE50 W E @ R (MWh) N 1 | 40.2112 | 171.4294 | 192.1066 | 181.7309 | 191.5859 | 195.7553 | 209.5854 | 240.2298 | 268.2633 | 281.8471 | 269.7194 | 322.7971 | 331.7476 | 321.171 | 342.5819 | 353.9107 | 353.9107 | 353.9107 | 353.9107 | 353.9107 | 353.9107 | 353.9107 | 353.9107 | 353.9107 | 353.9107 | 353.9107 | 353.9107 | 353.9107 | 353.9107 | 353.9107 | Option 1 Summer POE10 W E @ R (MWh) N 1 | 9.1342 | 14.0091 | 14.1549 | 13.9978 | 14.038 | 14.3293 | 14.944 | 16.1042 | 16.747 | 17.228 | 17.981 | 18.9853 | 20.2624 | 20.9585 | 20.7308 | 20.9791 | 20.9791 | 20.9791 | 20.9791 | 20.9791 | 20.9791 | 20.9791 | 20.9791 | 20.9791 | 20.9791 | 20.9791 | 20.9791 | 20.9791 | 20.9791 | 20.9791
Option 2 - Replace 3 x 10/13.5 MVA Tx with 3 x 20/33 MVA Tx
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | FY25: 0.92537; FY26: 2.1455; FY27: 2.2748 |  | 2.0467 | 3.2105 | 3.331
98% | FY25: 0; FY26: 0; FY27: 0 |  | 0 | 0 | 0
97% | FY25: 0; FY26: 0; FY27: 0 |  | 0 | 0 | 0
95% | FY25: 2.0617; FY26: 6.7704; FY27: 7.2696 |  | 6.3892 | 10.8806 | 11.3457
90% | FY25: 3.2506; FY26: 29.7534; FY27: 32.6399 |  | 27.5498 | 53.5156 | 56.2046
85% | FY26: 62.8339; FY27: 74.8936 |  | 53.6277 | 162.111 | 173.3454
80% | FY26: 9.9766; FY27: 19.6484 |  | 4.7409 | 147.5405 | 165.3278
75% | [32 empty] | 57.2368 | 82.0481
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 6.1753 | 110.3648 | 135.3591 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 93.4108 | 430.15 | 486.6866 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2 Winter POE50 W E @ R (MWh) N 1 | 4.3227 | 77.2554 | 94.7514 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 2 Winter POE10 W E @ R (MWh) N 1 | 28.0232 | 129.045 | 146.006 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | FY25: 2.2293; FY26: 3.394; FY27: 3.5111 |  | 0 | 0 | 0
98% | FY25: 0; FY26: 0; FY27: 0 |  | 0 | 0 | 0
97% | FY25: 0; FY26: 0; FY27: 0 |  | 5.4316 | 6.7071 | 6.7423
95% | FY25: 1.6813; FY26: 2.8051; FY27: 2.918 |  | 0 | 0 | 0
90% | FY25: 24.9336; FY26: 48.7543; FY27: 51.148 |  | 4.4685 | 5.6785 | 5.7119
85% | FY25: 29.1806; FY26: 114.1031; FY27: 122.6458 |  | 3.5054 | 4.65 | 4.6816
80% | FY26: 76.2716; FY27: 90.1487 |  | 10.169 | 14.4859 | 14.605
75% | FY26: 2.0449; FY27: 6.8387 |  | 3.1582 | 5.1859 | 5.2419
70% | [31 empty] | 3.696 | 9.3866 | 9.5436
65% | [31 empty] | 0.018768 | 1.0718 | 1.1205
60% | [32 empty] | 0.0029592 | 0.012833
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 57.4445 | 244.8992 | 274.4381 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 30.143 | 46.6971 | 47.183 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2 Summer POE50 W E @ R (MWh) N 1 | 40.2112 | 171.4294 | 192.1066 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 2 Summer POE10 W E @ R (MWh) N 1 | 9.0429 | 14.0091 | 14.1549 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 - Replace 1 x 10/13.5 MVA Tx with 1 x 20/33 MVA Tx
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | 0.92537 | 2.1455 | 2.2748 | [5 empty] | 0.018758 |  | 0.72681 | 0.92048 | 1.0597 | 1.7159 | 1.8227 | 1.8227 | 1.8227 | 1.8227 | 1.8227 | 1.8227 | 1.8227 | 1.8227 | 1.8227 | 1.8227 | 1.8227 | 1.8227 | 1.8227 | 1.8227 | 1.8227 | 1.8227 |  | 2.0467 | 3.2105 | 3.331 |  |  |  |  | 0.65169 | 1.0758 | 0.67435 | 1.7833 | 1.3177 | 1.7366 | 2.0385 | 1.9145 | 1.9145 | 1.9145 | 1.9145 | 1.9145 | 1.9145 | 1.9145 | 1.9145 | 1.9145 | 1.9145 | 1.9145 | 1.9145 | 1.9145 | 1.9145 | 1.9145 | 1.9145
98% | 0 | 0 | 0 | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
97% | 0 | 0 | 0 | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
95% | 2.0617 | 6.7704 | 7.2696 | [7 empty] | 0.6535 | 1.4009 | 1.9382 | 4.4708 | 4.883 | 4.883 | 4.883 | 4.883 | 4.883 | 4.883 | 4.883 | 4.883 | 4.883 | 4.883 | 4.883 | 4.883 | 4.883 | 4.883 | 4.883 | 4.883 |  | 6.3892 | 10.8806 | 11.3457 |  |  |  |  | 0.3936 | 2.0003 | 0.46522 | 4.7308 | 2.9339 | 4.5507 | 5.7159 | 5.2372 | 5.2372 | 5.2372 | 5.2372 | 5.2372 | 5.2372 | 5.2372 | 5.2372 | 5.2372 | 5.2372 | 5.2372 | 5.2372 | 5.2372 | 5.2372 | 5.2372 | 5.2372
90% | 3.2506 | 29.7534 | 32.6399 | [7 empty] | 8.5368e-05 | 0.51679 | 1.4977 | 12.4673 | 14.8504 | 14.8504 | 14.8504 | 14.8504 | 14.8504 | 14.8504 | 14.8504 | 14.8504 | 14.8504 | 14.8504 | 14.8504 | 14.8504 | 14.8504 | 14.8504 | 14.8504 | 14.8504 |  | 27.5498 | 53.5156 | 56.2046 | [5 empty] | 1.6433 |  | 13.9705 | 4.6153 | 12.9295 | 19.6653 | 16.8979 | 16.8979 | 16.8979 | 16.8979 | 16.8979 | 16.8979 | 16.8979 | 16.8979 | 16.8979 | 16.8979 | 16.8979 | 16.8979 | 16.8979 | 16.8979 | 16.8979 | 16.8979
85% |  | 62.8339 | 74.8936 | [10 empty] | 0.52677 | 2.1963 | 2.1963 | 2.1963 | 2.1963 | 2.1963 | 2.1963 | 2.1963 | 2.1963 | 2.1963 | 2.1963 | 2.1963 | 2.1963 | 2.1963 | 2.1963 | 2.1963 | 2.1963 |  | 53.6277 | 162.111 | 173.3454 | [7 empty] | 1.448 |  | 0.76184 | 8.9733 | 4.5281 | 4.5281 | 4.5281 | 4.5281 | 4.5281 | 4.5281 | 4.5281 | 4.5281 | 4.5281 | 4.5281 | 4.5281 | 4.5281 | 4.5281 | 4.5281 | 4.5281 | 4.5281
80% | FY26: 9.9766; FY27: 19.6484 |  | 4.7409 | 147.5405 | 165.3278
75% | [32 empty] | 57.2368 | 82.0481
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 6.1753 | 110.3648 | 135.3591 | 0 | 0 | 0 | 0 | 0 | 0.018571 | 0 | 1.3666 | 2.8098 | 4.4506 | 18.9889 | 23.515 | 23.515 | 23.515 | 23.515 | 23.515 | 23.515 | 23.515 | 23.515 | 23.515 | 23.515 | 23.515 | 23.515 | 23.515 | 23.515 | 23.515 | 23.515 | E @ R (MWh) | 93.4108 | 430.15 | 486.6866 | 0 | 0 | 0 | 0 | 1.0348 | 4.6722 | 1.1282 | 21.7133 | 8.7783 | 19.779 | 36.0291 | 28.2919 | 28.2919 | 28.2919 | 28.2919 | 28.2919 | 28.2919 | 28.2919 | 28.2919 | 28.2919 | 28.2919 | 28.2919 | 28.2919 | 28.2919 | 28.2919 | 28.2919 | 28.2919
Option 3 Winter POE50 W E @ R (MWh) N 1 | 4.3227 | 77.2554 | 94.7514 | 0 | 0 | 0 | 0 | 0 | 0.012999 | 0 | 0.95661 | 1.9669 | 3.1154 | 13.2923 | 16.4605 | 16.4605 | 16.4605 | 16.4605 | 16.4605 | 16.4605 | 16.4605 | 16.4605 | 16.4605 | 16.4605 | 16.4605 | 16.4605 | 16.4605 | 16.4605 | 16.4605 | 16.4605 | Option 3 Winter POE10 W E @ R (MWh) N 1 | 28.0232 | 129.045 | 146.006 | 0 | 0 | 0 | 0 | 0.31045 | 1.4017 | 0.33845 | 6.514 | 2.6335 | 5.9337 | 10.8087 | 8.4876 | 8.4876 | 8.4876 | 8.4876 | 8.4876 | 8.4876 | 8.4876 | 8.4876 | 8.4876 | 8.4876 | 8.4876 | 8.4876 | 8.4876 | 8.4876 | 8.4876 | 8.4876
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | FY25: 2.2293; FY26: 3.394; FY27: 3.5111 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
98% | FY25: 0; FY26: 0; FY27: 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
97% | FY25: 0; FY26: 0; FY27: 0 |  | 5.4316 | 6.7071 | 6.7423 | 0.89949 | 0.90924 | 0.97889 | 1.12 | 1.3686 | 1.4982 | 1.5919 | 1.7337 | 1.9148 | 2.1337 | 2.2485 | 2.2113 | 2.2518 | 2.2518 | 2.2518 | 2.2518 | 2.2518 | 2.2518 | 2.2518 | 2.2518 | 2.2518 | 2.2518 | 2.2518 | 2.2518 | 2.2518 | 2.2518 | 2.2518
95% | FY25: 1.6813; FY26: 2.8051; FY27: 2.918 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
90% | FY25: 24.9336; FY26: 48.7543; FY27: 51.148 |  | 4.4685 | 5.6785 | 5.7119 | 0.072177 | 0.075746 | 0.10367 | 0.17324 | 0.33715 | 0.44294 | 0.52799 | 0.66253 | 0.83431 | 1.042 | 1.1509 | 1.1156 | 1.1541 | 1.1541 | 1.1541 | 1.1541 | 1.1541 | 1.1541 | 1.1541 | 1.1541 | 1.1541 | 1.1541 | 1.1541 | 1.1541 | 1.1541 | 1.1541 | 1.1541
85% | FY25: 29.1806; FY26: 114.1031; FY27: 122.6458 |  | 3.5054 | 4.65 | 4.6816 | [7 empty] | 0.0075227 | 0.040024 | 0.11277 | 0.16516 | 0.14711 | 0.16684 | 0.16684 | 0.16684 | 0.16684 | 0.16684 | 0.16684 | 0.16684 | 0.16684 | 0.16684 | 0.16684 | 0.16684 | 0.16684 | 0.16684 | 0.16684 | 0.16684
80% | FY26: 76.2716; FY27: 90.1487 |  | 10.169 | 14.4859 | 14.605
75% | FY26: 2.0449; FY27: 6.8387 |  | 3.1582 | 5.1859 | 5.2419
70% | [31 empty] | 3.696 | 9.3866 | 9.5436
65% | [31 empty] | 0.018768 | 1.0718 | 1.1205
60% | [32 empty] | 0.0029592 | 0.012833
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 57.4445 | 244.8992 | 274.4381 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 30.143 | 46.6971 | 47.183 | 0.96195 | 0.97514 | 1.0717 | 1.2804 | 1.6887 | 1.9217 | 2.0987 | 2.3797 | 2.7612 | 3.2556 | 3.5289 | 3.4392 | 3.537 | 3.537 | 3.537 | 3.537 | 3.537 | 3.537 | 3.537 | 3.537 | 3.537 | 3.537 | 3.537 | 3.537 | 3.537 | 3.537 | 3.537
Option 3 Summer POE50 W E @ R (MWh) N 1 | 40.2112 | 171.4294 | 192.1066 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 3 Summer POE10 W E @ R (MWh) N 1 | 9.0429 | 14.0091 | 14.1549 | 0.28858 | 0.29254 | 0.32152 | 0.38411 | 0.50662 | 0.57651 | 0.6296 | 0.71391 | 0.82836 | 0.97669 | 1.0587 | 1.0318 | 1.0611 | 1.0611 | 1.0611 | 1.0611 | 1.0611 | 1.0611 | 1.0611 | 1.0611 | 1.0611 | 1.0611 | 1.0611 | 1.0611 | 1.0611 | 1.0611 | 1.0611
Option 4 - Construct 2x 20/33MVA zone substation in Inverloch
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | FY25: 0.92537; FY26: 2.1455; FY27: 2.2748 |  | 2.0467 | 3.2105 | 3.331
98% | FY25: 0; FY26: 0; FY27: 0 |  | 0 | 0 | 0
97% | FY25: 0; FY26: 0; FY27: 0 |  | 0 | 0 | 0
95% | FY25: 2.0617; FY26: 6.7704; FY27: 7.2696 |  | 6.3892 | 10.8806 | 11.3457
90% | FY25: 3.2506; FY26: 29.7534; FY27: 32.6399 |  | 27.5498 | 53.5156 | 56.2046
85% | FY26: 62.8339; FY27: 74.8936 |  | 53.6277 | 162.111 | 173.3454
80% | FY26: 9.9766; FY27: 19.6484 |  | 4.7409 | 147.5405 | 165.3278
75% | [32 empty] | 57.2368 | 82.0481
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 6.1753 | 110.3648 | 135.3591 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 93.4108 | 430.15 | 486.6866 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 Winter POE50 W E @ R (MWh) N 1 | 4.3227 | 77.2554 | 94.7514 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 4 Winter POE10 W E @ R (MWh) N 1 | 28.0232 | 129.045 | 146.006 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | FY25: 2.2293; FY26: 3.394; FY27: 3.5111 |  | 0 | 0 | 0
98% | FY25: 0; FY26: 0; FY27: 0 |  | 0 | 0 | 0
97% | FY25: 0; FY26: 0; FY27: 0 |  | 5.4316 | 6.7071 | 6.7423
95% | FY25: 1.6813; FY26: 2.8051; FY27: 2.918 |  | 0 | 0 | 0
90% | FY25: 24.9336; FY26: 48.7543; FY27: 51.148 |  | 4.4685 | 5.6785 | 5.7119
85% | FY25: 29.1806; FY26: 114.1031; FY27: 122.6458 |  | 3.5054 | 4.65 | 4.6816
80% | FY26: 76.2716; FY27: 90.1487 |  | 10.169 | 14.4859 | 14.605
75% | FY26: 2.0449; FY27: 6.8387 |  | 3.1582 | 5.1859 | 5.2419
70% | [31 empty] | 3.696 | 9.3866 | 9.5436
65% | [31 empty] | 0.018768 | 1.0718 | 1.1205
60% | [32 empty] | 0.0029592 | 0.012833
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 57.4445 | 244.8992 | 274.4381 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 30.143 | 46.6971 | 47.183 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 Summer POE50 W E @ R (MWh) N 1 | 40.2112 | 171.4294 | 192.1066 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 4 Summer POE10 W E @ R (MWh) N 1 | 9.0429 | 14.0091 | 14.1549 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 - Contract network support services to defer network investment
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% |  | 0.85147 | 0.97858 | 1.141 | 1.3527 | 1.5495 | 1.8923 | 2.7611 | 3.2287 | 2.8755 | 3.9413 | 4.1233 | 4.2484 | 4.8973 | 5.0065 | 5.0065 | 5.0065 | 5.0065 | 5.0065 | 5.0065 | 5.0065 | 5.0065 | 5.0065 | 5.0065 | 5.0065 | 5.0065 | 5.0065 | 5.0065 | 5.0065 | 5.0065 |  | 0.83483 | 1.9165 | 2.0347 | 2.4531 | 2.4424 | 2.5293 | 2.878 | 3.8897 | 4.3054 | 3.898 | 4.9978 | 4.5205 | 4.9254 | 5.2199 | 5.0982 | 5.0982 | 5.0982 | 5.0982 | 5.0982 | 5.0982 | 5.0982 | 5.0982 | 5.0982 | 5.0982 | 5.0982 | 5.0982 | 5.0982 | 5.0982 | 5.0982 | 5.0982
98% |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
97% |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
95% |  | 1.7765 | 2.267 | 2.8937 | 3.7109 | 4.4705 | 5.7932 | 9.1464 | 10.9511 | 9.5878 | 13.701 | 14.4035 | 14.8863 | 17.3904 | 17.8119 | 17.8119 | 17.8119 | 17.8119 | 17.8119 | 17.8119 | 17.8119 | 17.8119 | 17.8119 | 17.8119 | 17.8119 | 17.8119 | 17.8119 | 17.8119 | 17.8119 | 17.8119 |  | 1.7123 | 5.8867 | 6.3431 | 7.9577 | 7.9162 | 8.2518 | 9.5973 | 13.5018 | 15.1064 | 13.5338 | 17.7783 | 15.9365 | 17.4989 | 18.6355 | 18.166 | 18.166 | 18.166 | 18.166 | 18.166 | 18.166 | 18.166 | 18.166 | 18.166 | 18.166 | 18.166 | 18.166 | 18.166 | 18.166 | 18.166 | 18.166
90% |  | 2.2149 | 4.1139 | 7.3417 | 12.0657 | 16.4574 | 24.1044 | 43.4901 | 53.9231 | 46.0415 | 69.8212 | 73.8822 | 76.6738 | 91.1504 | 93.5871 | 93.5871 | 93.5871 | 93.5871 | 93.5871 | 93.5871 | 93.5871 | 93.5871 | 93.5871 | 93.5871 | 93.5871 | 93.5871 | 93.5871 | 93.5871 | 93.5871 | 93.5871 |  | 2.0083 | 24.6448 | 27.2833 | 36.6179 | 36.3777 | 38.3182 | 46.0966 | 68.6697 | 77.946 | 68.8545 | 93.3932 | 82.7449 | 91.7775 | 98.3485 | 95.6346 | 95.6346 | 95.6346 | 95.6346 | 95.6346 | 95.6346 | 95.6346 | 95.6346 | 95.6346 | 95.6346 | 95.6346 | 95.6346 | 95.6346 | 95.6346 | 95.6346 | 95.6346
85% |  |  |  | 0.0052214 | 3.4634 | 12.2232 | 39.2331 | 120.225 | 163.8133 | 130.8848 | 230.2345 | 247.201 | 258.8641 | 319.3465 | 329.5265 | 329.5265 | 329.5265 | 329.5265 | 329.5265 | 329.5265 | 329.5265 | 329.5265 | 329.5265 | 329.5265 | 329.5265 | 329.5265 | 329.5265 | 329.5265 | 329.5265 | 329.5265 |  |  | 41.4909 | 52.5141 | 91.5133 | 90.5098 | 98.6173 | 131.1149 | 225.4236 | 264.1793 | 226.1956 | 328.7165 | 284.2285 | 321.9664 | 349.4194 | 338.0808 | 338.0808 | 338.0808 | 338.0808 | 338.0808 | 338.0808 | 338.0808 | 338.0808 | 338.0808 | 338.0808 | 338.0808 | 338.0808 | 338.0808 | 338.0808 | 338.0808 | 338.0808
80% | [6 empty] | 0.39433 | 81.223 | 150.2358 | 98.1004 | 255.3997 | 282.2625 | 300.7286 | 396.4897 | 412.6076 | 412.6076 | 412.6076 | 412.6076 | 412.6076 | 412.6076 | 412.6076 | 412.6076 | 412.6076 | 412.6076 | 412.6076 | 412.6076 | 412.6076 | 412.6076 | 412.6076 | 412.6076 |  |  | 0.76078 | 4.2361 | 38.0446 | 36.7709 | 47.6479 | 98.4649 | 247.7826 | 309.1441 | 249.005 | 411.3251 | 340.8879 | 400.6378 | 444.1038 | 426.1515 | 426.1515 | 426.1515 | 426.1515 | 426.1515 | 426.1515 | 426.1515 | 426.1515 | 426.1515 | 426.1515 | 426.1515 | 426.1515 | 426.1515 | 426.1515 | 426.1515 | 426.1515
75% | [7 empty] | 3.5559 | 60.7228 | 11.2146 | 244.1726 | 293.7915 | 327.9007 | 504.7831 | 534.5549 | 534.5549 | 534.5549 | 534.5549 | 534.5549 | 534.5549 | 534.5549 | 534.5549 | 534.5549 | 534.5549 | 534.5549 | 534.5549 | 534.5549 | 534.5549 | 534.5549 | 534.5549 | [7 empty] | 11.4263 | 230.1029 | 343.445 | 232.3609 | 532.186 | 402.0797 | 512.4453 | 592.7324 | 559.5721 | 559.5721 | 559.5721 | 559.5721 | 559.5721 | 559.5721 | 559.5721 | 559.5721 | 559.5721 | 559.5721 | 559.5721 | 559.5721 | 559.5721 | 559.5721 | 559.5721 | 559.5721
70% | [10 empty] | 44.7199 | 88.6868 | 127.1244 | 400.116 | 448.5768 | 448.5768 | 448.5768 | 448.5768 | 448.5768 | 448.5768 | 448.5768 | 448.5768 | 448.5768 | 448.5768 | 448.5768 | 448.5768 | 448.5768 | 448.5768 | 448.5768 | 448.5768 | [8 empty] | 34.8933 | 146.8073 | 36.3905 | 444.7209 | 232.9416 | 412.588 | 543.2747 | 489.2983 | 489.2983 | 489.2983 | 489.2983 | 489.2983 | 489.2983 | 489.2983 | 489.2983 | 489.2983 | 489.2983 | 489.2983 | 489.2983 | 489.2983 | 489.2983 | 489.2983 | 489.2983
65% | FY38: 35.6525; FY39: 58.9721; FY40: 58.9721; FY41: 58.9721; FY42: 58.9721; FY43: 58.9721; FY44: 58.9721; FY45: 58.9721; FY46: 58.9721; FY47: 58.9721; FY48: 58.9721; FY49: 58.9721; FY50: 58.9721; FY51: 58.9721; FY52: 58.9721; FY53: 58.9721; FY54: 58.9721 | [11 empty] | 56.9093 |  | 41.1108 | 120.6476 | 82.9152 | 82.9152 | 82.9152 | 82.9152 | 82.9152 | 82.9152 | 82.9152 | 82.9152 | 82.9152 | 82.9152 | 82.9152 | 82.9152 | 82.9152 | 82.9152 | 82.9152 | 82.9152
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 4.7945 | 7.2859 | 11.2678 | 20.3867 | 34.3537 | 70.7033 | 257.7975 | 438.446 | 295.7176 | 853.3704 | 994.3072 | 1099.3221 | 1752.1276 | 1881.637 | 1881.637 | 1881.637 | 1881.637 | 1881.637 | 1881.637 | 1881.637 | 1881.637 | 1881.637 | 1881.637 | 1881.637 | 1881.637 | 1881.637 | 1881.637 | 1881.637 | 1881.637 | E @ R (MWh) | 4.5099 | 73.9527 | 91.4871 | 174.8207 | 172.2767 | 193.411 | 296.5822 | 816.0209 | 1149.3241 | 821.936 | 1871.1269 | 1349.7062 | 1784.9207 | 2150.658 | 1994.7675 | 1994.7675 | 1994.7675 | 1994.7675 | 1994.7675 | 1994.7675 | 1994.7675 | 1994.7675 | 1994.7675 | 1994.7675 | 1994.7675 | 1994.7675 | 1994.7675 | 1994.7675 | 1994.7675 | 1994.7675
Option 5 Winter POE50 W E @ R (MWh) N 1 | 0 | 3.3561 | 5.1001 | 7.8874 | 14.2707 | 24.0476 | 49.4923 | 180.4583 | 306.9122 | 207.0023 | 597.3593 | 696.0151 | 769.5255 | 1226.4894 | 1317.1459 | 1317.1459 | 1317.1459 | 1317.1459 | 1317.1459 | 1317.1459 | 1317.1459 | 1317.1459 | 1317.1459 | 1317.1459 | 1317.1459 | 1317.1459 | 1317.1459 | 1317.1459 | 1317.1459 | 1317.1459 | Option 5 Winter POE10 W E @ R (MWh) N 1 | 1.353 | 22.1858 | 27.4461 | 52.4462 | 51.683 | 58.0233 | 88.9747 | 244.8063 | 344.7972 | 246.5808 | 561.3381 | 404.9119 | 535.4762 | 645.1974 | 598.4302 | 598.4302 | 598.4302 | 598.4302 | 598.4302 | 598.4302 | 598.4302 | 598.4302 | 598.4302 | 598.4302 | 598.4302 | 598.4302 | 598.4302 | 598.4302 | 598.4302 | 598.4302
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | 0.68731 | 1.7475 | 1.8617 | 1.8074 | 1.8612 | 1.8779 | 1.9381 | 2.0655 | 2.1791 | 2.2286 | 2.166 | 2.365 | 2.3809 | 2.3314 | 2.4149 | 2.4563 | 2.4563 | 2.4563 | 2.4563 | 2.4563 | 2.4563 | 2.4563 | 2.4563 | 2.4563 | 2.4563 | 2.4563 | 2.4563 | 2.4563 | 2.4563 | 2.4563 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
98% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
97% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 3.9206 | 5.0937 | 5.126 | 5.0911 | 5.1001 | 5.1642 | 5.294 | 5.5226 | 5.6417 | 5.7279 | 5.8584 | 6.0249 | 6.2263 | 6.3318 | 6.2976 | 6.3381 | 6.3381 | 6.3381 | 6.3381 | 6.3381 | 6.3381 | 6.3381 | 6.3381 | 6.3381 | 6.3381 | 6.3381 | 6.3381 | 6.3381 | 6.3381 | 6.3381
95% | 0.19357 | 1.2165 | 1.3266 | 1.2743 | 1.3261 | 1.3422 | 1.4004 | 1.5233 | 1.6329 | 1.6807 | 1.6203 | 1.8122 | 1.8276 | 1.7798 | 1.8604 | 1.9003 | 1.9003 | 1.9003 | 1.9003 | 1.9003 | 1.9003 | 1.9003 | 1.9003 | 1.9003 | 1.9003 | 1.9003 | 1.9003 | 1.9003 | 1.9003 | 1.9003 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
90% | 0.042978 | 15.0796 | 17.4143 | 16.3045 | 17.4039 | 17.7456 | 18.9782 | 21.5826 | 23.9069 | 24.9197 | 23.6394 | 27.7076 | 28.0341 | 27.0213 | 28.729 | 29.5755 | 29.5755 | 29.5755 | 29.5755 | 29.5755 | 29.5755 | 29.5755 | 29.5755 | 29.5755 | 29.5755 | 29.5755 | 29.5755 | 29.5755 | 29.5755 | 29.5755 |  | 3.035 | 4.1479 | 4.1786 | 4.1455 | 4.154 | 4.2148 | 4.3379 | 4.5548 | 4.6678 | 4.7496 | 4.8734 | 5.0313 | 5.2224 | 5.3225 | 5.2901 | 5.3285 | 5.3285 | 5.3285 | 5.3285 | 5.3285 | 5.3285 | 5.3285 | 5.3285 | 5.3285 | 5.3285 | 5.3285 | 5.3285 | 5.3285 | 5.3285 | 5.3285
85% |  | 5.1263 | 9.099 | 7.0732 | 9.0788 | 9.7515 | 12.3711 | 18.8858 | 25.8013 | 29.1338 | 24.9533 | 38.9919 | 40.157 | 36.5425 | 42.6369 | 45.6579 | 45.6579 | 45.6579 | 45.6579 | 45.6579 | 45.6579 | 45.6579 | 45.6579 | 45.6579 | 45.6579 | 45.6579 | 45.6579 | 45.6579 | 45.6579 | 45.6579 |  | 2.1493 | 3.2021 | 3.2311 | 3.1998 | 3.2079 | 3.2653 | 3.3819 | 3.587 | 3.6939 | 3.7713 | 3.8884 | 4.0378 | 4.2185 | 4.3132 | 4.2825 | 4.3189 | 4.3189 | 4.3189 | 4.3189 | 4.3189 | 4.3189 | 4.3189 | 4.3189 | 4.3189 | 4.3189 | 4.3189 | 4.3189 | 4.3189 | 4.3189 | 4.3189
80% | [11 empty] | 0.50869 | 0.7099 | 0.1944 | 1.2486 | 2.1066 | 2.1066 | 2.1066 | 2.1066 | 2.1066 | 2.1066 | 2.1066 | 2.1066 | 2.1066 | 2.1066 | 2.1066 | 2.1066 | 2.1066 | 2.1066 | 2.1066 |  | 5.0548 | 9.0252 | 9.1347 | 9.0166 | 9.047 | 9.2638 | 9.7032 | 10.477 | 10.8802 | 11.1719 | 11.6134 | 12.177 | 12.8586 | 13.2158 | 13.1 | 13.2373 | 13.2373 | 13.2373 | 13.2373 | 13.2373 | 13.2373 | 13.2373 | 13.2373 | 13.2373 | 13.2373 | 13.2373 | 13.2373 | 13.2373 | 13.2373 | 13.2373
75% | [31 empty] | 0.76086 | 2.621 | 2.6725 | 2.617 | 2.6313 | 2.7331 | 2.9395 | 3.3029 | 3.4923 | 3.6293 | 3.8367 | 4.1014 | 4.4216 | 4.5893 | 4.535 | 4.5994 | 4.5994 | 4.5994 | 4.5994 | 4.5994 | 4.5994 | 4.5994 | 4.5994 | 4.5994 | 4.5994 | 4.5994 | 4.5994 | 4.5994 | 4.5994 | 4.5994
70% | [32 empty] | 2.2254 | 2.3556 | 2.2154 | 2.251 | 2.5133 | 3.082 | 4.1021 | 4.6336 | 5.0181 | 5.6001 | 6.3431 | 7.2415 | 7.7123 | 7.5597 | 7.7406 | 7.7406 | 7.7406 | 7.7406 | 7.7406 | 7.7406 | 7.7406 | 7.7406 | 7.7406 | 7.7406 | 7.7406 | 7.7406 | 7.7406 | 7.7406 | 7.7406
65% | [37 empty] | 0.0013289 | 0.041244 | 0.083588 | 0.12322 | 0.1973 | 0.31609 | 0.49508 | 0.60396 | 0.56754 | 0.61083 | 0.61083 | 0.61083 | 0.61083 | 0.61083 | 0.61083 | 0.61083 | 0.61083 | 0.61083 | 0.61083 | 0.61083 | 0.61083 | 0.61083 | 0.61083 | 0.61083
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0.91462 | 22.9381 | 29.4046 | 26.1949 | 29.3732 | 30.41 | 34.341 | 43.6166 | 52.9851 | 57.3832 | 51.8553 | 70.6715 | 72.3784 | 67.1907 | 76.1208 | 80.8796 | 80.8796 | 80.8796 | 80.8796 | 80.8796 | 80.8796 | 80.8796 | 80.8796 | 80.8796 | 80.8796 | 80.8796 | 80.8796 | 80.8796 | 80.8796 | 80.8796 | E @ R (MWh) | 14.7713 | 26.052 | 26.4315 | 26.0225 | 26.1273 | 26.8829 | 28.4524 | 31.2718 | 32.7623 | 33.8495 | 35.5089 | 37.6514 | 40.2771 | 41.6681 | 41.216 | 41.7521 | 41.7521 | 41.7521 | 41.7521 | 41.7521 | 41.7521 | 41.7521 | 41.7521 | 41.7521 | 41.7521 | 41.7521 | 41.7521 | 41.7521 | 41.7521 | 41.7521
Option 5 Summer POE50 W E @ R (MWh) N 1 | 0.64023 | 16.0567 | 20.5832 | 18.3364 | 20.5612 | 21.287 | 24.0387 | 30.5316 | 37.0896 | 40.1682 | 36.2987 | 49.47 | 50.6649 | 47.0335 | 53.2845 | 56.6157 | 56.6157 | 56.6157 | 56.6157 | 56.6157 | 56.6157 | 56.6157 | 56.6157 | 56.6157 | 56.6157 | 56.6157 | 56.6157 | 56.6157 | 56.6157 | 56.6157 | Option 5 Summer POE10 W E @ R (MWh) N 1 | 4.4314 | 7.8156 | 7.9294 | 7.8067 | 7.8382 | 8.0649 | 8.5357 | 9.3816 | 9.8287 | 10.1548 | 10.6527 | 11.2954 | 12.0831 | 12.5004 | 12.3648 | 12.5256 | 12.5256 | 12.5256 | 12.5256 | 12.5256 | 12.5256 | 12.5256 | 12.5256 | 12.5256 | 12.5256 | 12.5256 | 12.5256 | 12.5256 | 12.5256 | 12.5256
Option 6 -
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | 0.92537 | 2.1455 | 2.2748 | 2.4348 | 2.6471 | 2.8485 | 3.2003 | 4.0851 | 4.5611 | 4.2139 | 5.2888 | 5.4825 | 5.6217 | 6.2779 | 6.3847 | 6.3847 | 6.3847 | 6.3847 | 6.3847 | 6.3847 | 6.3847 | 6.3847 | 6.3847 | 6.3847 | 6.3847 | 6.3847 | 6.3847 | 6.3847 | 6.3847 | 6.3847 |  | 2.0467 | 3.2105 | 3.331 | 3.7469 | 3.7368 | 3.8283 | 4.186 | 5.2137 | 5.6378 | 5.2363 | 6.3453 | 5.8797 | 6.2986 | 6.6005 | 6.4765 | 6.4765 | 6.4765 | 6.4765 | 6.4765 | 6.4765 | 6.4765 | 6.4765 | 6.4765 | 6.4765 | 6.4765 | 6.4765 | 6.4765 | 6.4765 | 6.4765 | 6.4765
98% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
97% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
95% | 2.0617 | 6.7704 | 7.2696 | 7.8869 | 8.7065 | 9.4834 | 10.8412 | 14.2562 | 16.093 | 14.753 | 18.9015 | 19.6489 | 20.1862 | 22.7188 | 23.131 | 23.131 | 23.131 | 23.131 | 23.131 | 23.131 | 23.131 | 23.131 | 23.131 | 23.131 | 23.131 | 23.131 | 23.131 | 23.131 | 23.131 | 23.131 |  | 6.3892 | 10.8806 | 11.3457 | 12.9509 | 12.9118 | 13.2648 | 14.6453 | 18.6116 | 20.2483 | 18.699 | 22.9788 | 21.1819 | 22.7987 | 23.9639 | 23.4852 | 23.4852 | 23.4852 | 23.4852 | 23.4852 | 23.4852 | 23.4852 | 23.4852 | 23.4852 | 23.4852 | 23.4852 | 23.4852 | 23.4852 | 23.4852 | 23.4852 | 23.4852
90% | 3.2506 | 29.7534 | 32.6399 | 36.2085 | 40.9465 | 45.4383 | 53.2881 | 73.0309 | 83.65 | 75.9031 | 99.8865 | 104.2076 | 107.3137 | 121.9552 | 124.3384 | 124.3384 | 124.3384 | 124.3384 | 124.3384 | 124.3384 | 124.3384 | 124.3384 | 124.3384 | 124.3384 | 124.3384 | 124.3384 | 124.3384 | 124.3384 | 124.3384 | 124.3384 |  | 27.5498 | 53.5156 | 56.2046 | 65.4847 | 65.2585 | 67.2992 | 75.2803 | 98.2105 | 107.6729 | 98.716 | 123.4584 | 113.0702 | 122.4175 | 129.1533 | 126.3859 | 126.3859 | 126.3859 | 126.3859 | 126.3859 | 126.3859 | 126.3859 | 126.3859 | 126.3859 | 126.3859 | 126.3859 | 126.3859 | 126.3859 | 126.3859 | 126.3859 | 126.3859
85% |  | 62.8339 | 74.8936 | 89.803 | 109.5982 | 128.3646 | 161.1605 | 243.6444 | 288.0101 | 255.644 | 355.845 | 373.8982 | 386.8755 | 448.0465 | 458.0033 | 458.0033 | 458.0033 | 458.0033 | 458.0033 | 458.0033 | 458.0033 | 458.0033 | 458.0033 | 458.0033 | 458.0033 | 458.0033 | 458.0033 | 458.0033 | 458.0033 | 458.0033 |  | 53.6277 | 162.111 | 173.3454 | 212.1168 | 211.1719 | 219.6975 | 253.0423 | 348.8429 | 388.3761 | 350.9549 | 454.327 | 410.9258 | 449.9778 | 478.1195 | 466.5576 | 466.5576 | 466.5576 | 466.5576 | 466.5576 | 466.5576 | 466.5576 | 466.5576 | 466.5576 | 466.5576 | 466.5576 | 466.5576 | 466.5576 | 466.5576 | 466.5576 | 466.5576
80% |  | 9.9766 | 19.6484 | 35.8864 | 64.3977 | 94.1103 | 146.0357 | 276.6314 | 346.8752 | 295.6303 | 454.2773 | 482.8608 | 503.4075 | 600.259 | 616.0234 | 616.0234 | 616.0234 | 616.0234 | 616.0234 | 616.0234 | 616.0234 | 616.0234 | 616.0234 | 616.0234 | 616.0234 | 616.0234 | 616.0234 | 616.0234 | 616.0234 | 616.0234 |  | 4.7409 | 147.5405 | 165.3278 | 226.7142 | 225.2181 | 238.7166 | 291.511 | 443.1911 | 505.7834 | 446.5349 | 610.2027 | 541.4861 | 603.3167 | 647.8732 | 629.5673 | 629.5673 | 629.5673 | 629.5673 | 629.5673 | 629.5673 | 629.5673 | 629.5673 | 629.5673 | 629.5673 | 629.5673 | 629.5673 | 629.5673 | 629.5673 | 629.5673 | 629.5673
75% |  |  |  |  | 0.17202 | 9.0242 | 55.3334 | 283.3902 | 413.139 | 318.4834 | 611.524 | 664.3211 | 702.2736 | 881.1701 | 910.289 | 910.289 | 910.289 | 910.289 | 910.289 | 910.289 | 910.289 | 910.289 | 910.289 | 910.289 | 910.289 | 910.289 | 910.289 | 910.289 | 910.289 | 910.289 |  |  | 57.2368 | 82.0481 | 191.187 | 188.4235 | 213.3569 | 310.8747 | 591.0464 | 706.6621 | 597.2228 | 899.5374 | 772.6094 | 886.8181 | 969.1193 | 935.3061 | 935.3061 | 935.3061 | 935.3061 | 935.3061 | 935.3061 | 935.3061 | 935.3061 | 935.3061 | 935.3061 | 935.3061 | 935.3061 | 935.3061 | 935.3061 | 935.3061 | 935.3061
70% | [7 empty] | 78.2842 | 250.9431 | 115.8555 | 573.8626 | 659.8027 | 721.5795 | 1012.7769 | 1060.1748 | 1060.1748 | 1060.1748 | 1060.1748 | 1060.1748 | 1060.1748 | 1060.1748 | 1060.1748 | 1060.1748 | 1060.1748 | 1060.1748 | 1060.1748 | 1060.1748 | 1060.1748 | 1060.1748 | 1060.1748 |  |  |  |  | 13.9473 | 12.8131 | 24.7488 | 107.115 | 540.5303 | 728.7229 | 550.584 | 1042.6741 | 836.068 | 1021.9704 | 1155.9355 | 1100.8963 | 1100.8963 | 1100.8963 | 1100.8963 | 1100.8963 | 1100.8963 | 1100.8963 | 1100.8963 | 1100.8963 | 1100.8963 | 1100.8963 | 1100.8963 | 1100.8963 | 1100.8963 | 1100.8963 | 1100.8963
65% | [8 empty] | 0.40539 |  | 145.0109 | 224.7284 | 292.046 | 647.5312 | 705.573 | 705.573 | 705.573 | 705.573 | 705.573 | 705.573 | 705.573 | 705.573 | 705.573 | 705.573 | 705.573 | 705.573 | 705.573 | 705.573 | 705.573 | 705.573 | [8 empty] | 118.5664 | 300.3588 | 126.2751 | 684.1423 | 431.1402 | 658.7893 | 822.8379 | 755.439 | 755.439 | 755.439 | 755.439 | 755.439 | 755.439 | 755.439 | 755.439 | 755.439 | 755.439 | 755.439 | 755.439 | 755.439 | 755.439 | 755.439 | 755.439
60% | FY38: 91.1742; FY39: 126.8218; FY40: 126.8218; FY41: 126.8218; FY42: 126.8218; FY43: 126.8218; FY44: 126.8218; FY45: 126.8218; FY46: 126.8218; FY47: 126.8218; FY48: 126.8218; FY49: 126.8218; FY50: 126.8218; FY51: 126.8218; FY52: 126.8218; FY53: 126.8218; FY54: 126.8218 | [11 empty] | 113.0025 | 9.404 | 97.6462 | 215.8063 | 161.9203 | 161.9203 | 161.9203 | 161.9203 | 161.9203 | 161.9203 | 161.9203 | 161.9203 | 161.9203 | 161.9203 | 161.9203 | 161.9203 | 161.9203 | 161.9203 | 161.9203 | 161.9203
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 6.1753 | 110.3648 | 135.3591 | 170.4974 | 224.2034 | 286.3766 | 425.5606 | 963.5892 | 1389.6401 | 1069.6783 | 2241.9506 | 2509.6007 | 2711.9106 | 3793.5907 | 3990.4321 | 3990.4321 | 3990.4321 | 3990.4321 | 3990.4321 | 3990.4321 | 3990.4321 | 3990.4321 | 3990.4321 | 3990.4321 | 3990.4321 | 3990.4321 | 3990.4321 | 3990.4321 | 3990.4321 | 3990.4321 | E @ R (MWh) | 93.4108 | 430.15 | 486.6866 | 718.8864 | 712.3384 | 773.1029 | 1046.0881 | 2142.5708 | 2735.8276 | 2172.2809 | 3917.1019 | 3110.3477 | 3831.3331 | 4404.9152 | 4163.9737 | 4163.9737 | 4163.9737 | 4163.9737 | 4163.9737 | 4163.9737 | 4163.9737 | 4163.9737 | 4163.9737 | 4163.9737 | 4163.9737 | 4163.9737 | 4163.9737 | 4163.9737 | 4163.9737 | 4163.9737
Option 6 Winter POE50 W E @ R (MWh) N 1 | 4.3227 | 77.2554 | 94.7514 | 119.3482 | 156.9424 | 200.4636 | 297.8924 | 674.5125 | 972.7481 | 748.7748 | 1569.3654 | 1756.7205 | 1898.3374 | 2655.5135 | 2793.3025 | 2793.3025 | 2793.3025 | 2793.3025 | 2793.3025 | 2793.3025 | 2793.3025 | 2793.3025 | 2793.3025 | 2793.3025 | 2793.3025 | 2793.3025 | 2793.3025 | 2793.3025 | 2793.3025 | 2793.3025 | Option 6 Winter POE10 W E @ R (MWh) N 1 | 28.0232 | 129.045 | 146.006 | 215.6659 | 213.7015 | 231.9309 | 313.8264 | 642.7712 | 820.7483 | 651.6843 | 1175.1306 | 933.1043 | 1149.3999 | 1321.4746 | 1249.1921 | 1249.1921 | 1249.1921 | 1249.1921 | 1249.1921 | 1249.1921 | 1249.1921 | 1249.1921 | 1249.1921 | 1249.1921 | 1249.1921 | 1249.1921 | 1249.1921 | 1249.1921 | 1249.1921 | 1249.1921
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | 2.2293 | 3.394 | 3.5111 | 3.4537 | 3.5082 | 3.5307 | 3.6025 | 3.7502 | 3.8744 | 3.9316 | 3.8807 | 4.0944 | 4.1283 | 4.0882 | 4.1686 | 4.21 | 4.21 | 4.21 | 4.21 | 4.21 | 4.21 | 4.21 | 4.21 | 4.21 | 4.21 | 4.21 | 4.21 | 4.21 | 4.21 | 4.21 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
98% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
97% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 5.4316 | 6.7071 | 6.7423 | 6.7043 | 6.7141 | 6.7837 | 6.9249 | 7.1735 | 7.303 | 7.3967 | 7.5385 | 7.7196 | 7.9385 | 8.0533 | 8.0161 | 8.0566 | 8.0566 | 8.0566 | 8.0566 | 8.0566 | 8.0566 | 8.0566 | 8.0566 | 8.0566 | 8.0566 | 8.0566 | 8.0566 | 8.0566 | 8.0566 | 8.0566
95% | 1.6813 | 2.8051 | 2.918 | 2.8626 | 2.9153 | 2.9369 | 3.0062 | 3.1487 | 3.2686 | 3.3238 | 3.2746 | 3.4808 | 3.5135 | 3.4748 | 3.5524 | 3.5924 | 3.5924 | 3.5924 | 3.5924 | 3.5924 | 3.5924 | 3.5924 | 3.5924 | 3.5924 | 3.5924 | 3.5924 | 3.5924 | 3.5924 | 3.5924 | 3.5924 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
90% | 24.9336 | 48.7543 | 51.148 | 49.9747 | 51.0903 | 51.5487 | 53.0179 | 56.0388 | 58.5802 | 59.75 | 58.7073 | 63.079 | 63.7723 | 62.9518 | 64.5971 | 65.4437 | 65.4437 | 65.4437 | 65.4437 | 65.4437 | 65.4437 | 65.4437 | 65.4437 | 65.4437 | 65.4437 | 65.4437 | 65.4437 | 65.4437 | 65.4437 | 65.4437 |  | 4.4685 | 5.6785 | 5.7119 | 5.6759 | 5.6852 | 5.7513 | 5.8852 | 6.121 | 6.2439 | 6.3328 | 6.4674 | 6.6391 | 6.8469 | 6.9557 | 6.9204 | 6.9589 | 6.9589 | 6.9589 | 6.9589 | 6.9589 | 6.9589 | 6.9589 | 6.9589 | 6.9589 | 6.9589 | 6.9589 | 6.9589 | 6.9589 | 6.9589 | 6.9589
85% | 29.1806 | 114.1031 | 122.6458 | 118.4583 | 122.4399 | 124.0759 | 129.3191 | 140.1002 | 149.1697 | 153.3447 | 149.6235 | 165.225 | 167.6994 | 164.7711 | 170.643 | 173.664 | 173.664 | 173.664 | 173.664 | 173.664 | 173.664 | 173.664 | 173.664 | 173.664 | 173.664 | 173.664 | 173.664 | 173.664 | 173.664 | 173.664 |  | 3.5054 | 4.65 | 4.6816 | 4.6475 | 4.6563 | 4.7188 | 4.8455 | 5.0686 | 5.1848 | 5.2689 | 5.3962 | 5.5587 | 5.7552 | 5.8582 | 5.8248 | 5.8612 | 5.8612 | 5.8612 | 5.8612 | 5.8612 | 5.8612 | 5.8612 | 5.8612 | 5.8612 | 5.8612 | 5.8612 | 5.8612 | 5.8612 | 5.8612 | 5.8612
80% |  | 76.2716 | 90.1487 | 83.3465 | 89.8144 | 92.4719 | 100.9891 | 118.5024 | 133.2353 | 140.0173 | 133.9725 | 159.3161 | 163.3356 | 158.5788 | 168.1174 | 173.0249 | 173.0249 | 173.0249 | 173.0249 | 173.0249 | 173.0249 | 173.0249 | 173.0249 | 173.0249 | 173.0249 | 173.0249 | 173.0249 | 173.0249 | 173.0249 | 173.0249 |  | 10.169 | 14.4859 | 14.605 | 14.4766 | 14.5096 | 14.7454 | 15.2231 | 16.0645 | 16.5029 | 16.8201 | 17.3001 | 17.9129 | 18.654 | 19.0424 | 18.9165 | 19.0537 | 19.0537 | 19.0537 | 19.0537 | 19.0537 | 19.0537 | 19.0537 | 19.0537 | 19.0537 | 19.0537 | 19.0537 | 19.0537 | 19.0537 | 19.0537 | 19.0537
75% |  | 2.0449 | 6.8387 | 4.1421 | 6.6906 | 7.9111 | 12.4972 | 25.1118 | 38.9762 | 46.3383 | 39.7468 | 70.6015 | 76.2631 | 69.5855 | 83.2676 | 90.7587 | 90.7587 | 90.7587 | 90.7587 | 90.7587 | 90.7587 | 90.7587 | 90.7587 | 90.7587 | 90.7587 | 90.7587 | 90.7587 | 90.7587 | 90.7587 | 90.7587 |  | 3.1582 | 5.1859 | 5.2419 | 5.1815 | 5.197 | 5.3078 | 5.5322 | 5.9274 | 6.1333 | 6.2823 | 6.5077 | 6.7956 | 7.1436 | 7.3261 | 7.2669 | 7.3314 | 7.3314 | 7.3314 | 7.3314 | 7.3314 | 7.3314 | 7.3314 | 7.3314 | 7.3314 | 7.3314 | 7.3314 | 7.3314 | 7.3314 | 7.3314 | 7.3314
70% | [31 empty] | 3.696 | 9.3866 | 9.5436 | 9.3743 | 9.4178 | 9.7286 | 10.3583 | 11.4674 | 12.0453 | 12.4634 | 13.0962 | 13.904 | 14.8809 | 15.3928 | 15.2268 | 15.4078 | 15.4078 | 15.4078 | 15.4078 | 15.4078 | 15.4078 | 15.4078 | 15.4078 | 15.4078 | 15.4078 | 15.4078 | 15.4078 | 15.4078 | 15.4078 | 15.4078
65% | [31 empty] | 0.018768 | 1.0718 | 1.1205 | 1.068 | 1.0815 | 1.1779 | 1.3734 | 1.7176 | 1.8969 | 2.0267 | 2.2231 | 2.4738 | 2.7769 | 2.9358 | 2.8843 | 2.9405 | 2.9405 | 2.9405 | 2.9405 | 2.9405 | 2.9405 | 2.9405 | 2.9405 | 2.9405 | 2.9405 | 2.9405 | 2.9405 | 2.9405 | 2.9405 | 2.9405
60% | [32 empty] | 0.0029592 | 0.012833 | 0.0024792 | 0.0043735 | 0.033315 | 0.17404 | 0.6831 | 1.0771 | 1.4159 | 2.0129 | 2.9198 | 4.2275 | 5.003 | 4.7449 | 5.0266 | 5.0266 | 5.0266 | 5.0266 | 5.0266 | 5.0266 | 5.0266 | 5.0266 | 5.0266 | 5.0266 | 5.0266 | 5.0266 | 5.0266 | 5.0266 | 5.0266
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 57.4445 | 244.8992 | 274.4381 | 259.6155 | 273.6942 | 279.6505 | 299.4076 | 343.1855 | 383.2333 | 402.6387 | 385.3134 | 461.1388 | 473.9252 | 458.8156 | 489.4027 | 505.5867 | 505.5867 | 505.5867 | 505.5867 | 505.5867 | 505.5867 | 505.5867 | 505.5867 | 505.5867 | 505.5867 | 505.5867 | 505.5867 | 505.5867 | 505.5867 | 505.5867 | E @ R (MWh) | 30.143 | 46.6971 | 47.183 | 46.6594 | 46.7933 | 47.7643 | 49.8134 | 53.6808 | 55.8233 | 57.4266 | 59.9366 | 63.2842 | 67.5413 | 69.8615 | 69.1027 | 69.9304 | 69.9304 | 69.9304 | 69.9304 | 69.9304 | 69.9304 | 69.9304 | 69.9304 | 69.9304 | 69.9304 | 69.9304 | 69.9304 | 69.9304 | 69.9304 | 69.9304
Option 6 Summer POE50 W E @ R (MWh) N 1 | 40.2112 | 171.4294 | 192.1066 | 181.7309 | 191.5859 | 195.7553 | 209.5854 | 240.2298 | 268.2633 | 281.8471 | 269.7194 | 322.7971 | 331.7476 | 321.171 | 342.5819 | 353.9107 | 353.9107 | 353.9107 | 353.9107 | 353.9107 | 353.9107 | 353.9107 | 353.9107 | 353.9107 | 353.9107 | 353.9107 | 353.9107 | 353.9107 | 353.9107 | 353.9107 | Option 6 Summer POE10 W E @ R (MWh) N 1 | 9.0429 | 14.0091 | 14.1549 | 13.9978 | 14.038 | 14.3293 | 14.944 | 16.1042 | 16.747 | 17.228 | 17.981 | 18.9853 | 20.2624 | 20.9585 | 20.7308 | 20.9791 | 20.9791 | 20.9791 | 20.9791 | 20.9791 | 20.9791 | 20.9791 | 20.9791 | 20.9791 | 20.9791 | 20.9791 | 20.9791 | 20.9791 | 20.9791 | 20.9791
Option 7 -
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | 0.92537 | 2.1455 | 2.2748 | 2.4348 | 2.6471 | 2.8485 | 3.2003 | 4.0851 | 4.5611 | 4.2139 | 5.2888 | 5.4825 | 5.6217 | 6.2779 | 6.3847 | 6.3847 | 6.3847 | 6.3847 | 6.3847 | 6.3847 | 6.3847 | 6.3847 | 6.3847 | 6.3847 | 6.3847 | 6.3847 | 6.3847 | 6.3847 | 6.3847 | 6.3847 |  | 2.0467 | 3.2105 | 3.331 | 3.7469 | 3.7368 | 3.8283 | 4.186 | 5.2137 | 5.6378 | 5.2363 | 6.3453 | 5.8797 | 6.2986 | 6.6005 | 6.4765 | 6.4765 | 6.4765 | 6.4765 | 6.4765 | 6.4765 | 6.4765 | 6.4765 | 6.4765 | 6.4765 | 6.4765 | 6.4765 | 6.4765 | 6.4765 | 6.4765 | 6.4765
98% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
97% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
95% | 2.0617 | 6.7704 | 7.2696 | 7.8869 | 8.7065 | 9.4834 | 10.8412 | 14.2562 | 16.093 | 14.753 | 18.9015 | 19.6489 | 20.1862 | 22.7188 | 23.131 | 23.131 | 23.131 | 23.131 | 23.131 | 23.131 | 23.131 | 23.131 | 23.131 | 23.131 | 23.131 | 23.131 | 23.131 | 23.131 | 23.131 | 23.131 |  | 6.3892 | 10.8806 | 11.3457 | 12.9509 | 12.9118 | 13.2648 | 14.6453 | 18.6116 | 20.2483 | 18.699 | 22.9788 | 21.1819 | 22.7987 | 23.9639 | 23.4852 | 23.4852 | 23.4852 | 23.4852 | 23.4852 | 23.4852 | 23.4852 | 23.4852 | 23.4852 | 23.4852 | 23.4852 | 23.4852 | 23.4852 | 23.4852 | 23.4852 | 23.4852
90% | 3.2506 | 29.7534 | 32.6399 | 36.2085 | 40.9465 | 45.4383 | 53.2881 | 73.0309 | 83.65 | 75.9031 | 99.8865 | 104.2076 | 107.3137 | 121.9552 | 124.3384 | 124.3384 | 124.3384 | 124.3384 | 124.3384 | 124.3384 | 124.3384 | 124.3384 | 124.3384 | 124.3384 | 124.3384 | 124.3384 | 124.3384 | 124.3384 | 124.3384 | 124.3384 |  | 27.5498 | 53.5156 | 56.2046 | 65.4847 | 65.2585 | 67.2992 | 75.2803 | 98.2105 | 107.6729 | 98.716 | 123.4584 | 113.0702 | 122.4175 | 129.1533 | 126.3859 | 126.3859 | 126.3859 | 126.3859 | 126.3859 | 126.3859 | 126.3859 | 126.3859 | 126.3859 | 126.3859 | 126.3859 | 126.3859 | 126.3859 | 126.3859 | 126.3859 | 126.3859
85% |  | 62.8339 | 74.8936 | 89.803 | 109.5982 | 128.3646 | 161.1605 | 243.6444 | 288.0101 | 255.644 | 355.845 | 373.8982 | 386.8755 | 448.0465 | 458.0033 | 458.0033 | 458.0033 | 458.0033 | 458.0033 | 458.0033 | 458.0033 | 458.0033 | 458.0033 | 458.0033 | 458.0033 | 458.0033 | 458.0033 | 458.0033 | 458.0033 | 458.0033 |  | 53.6277 | 162.111 | 173.3454 | 212.1168 | 211.1719 | 219.6975 | 253.0423 | 348.8429 | 388.3761 | 350.9549 | 454.327 | 410.9258 | 449.9778 | 478.1195 | 466.5576 | 466.5576 | 466.5576 | 466.5576 | 466.5576 | 466.5576 | 466.5576 | 466.5576 | 466.5576 | 466.5576 | 466.5576 | 466.5576 | 466.5576 | 466.5576 | 466.5576 | 466.5576
80% |  | 9.9766 | 19.6484 | 35.8864 | 64.3977 | 94.1103 | 146.0357 | 276.6314 | 346.8752 | 295.6303 | 454.2773 | 482.8608 | 503.4075 | 600.259 | 616.0234 | 616.0234 | 616.0234 | 616.0234 | 616.0234 | 616.0234 | 616.0234 | 616.0234 | 616.0234 | 616.0234 | 616.0234 | 616.0234 | 616.0234 | 616.0234 | 616.0234 | 616.0234 |  | 4.7409 | 147.5405 | 165.3278 | 226.7142 | 225.2181 | 238.7166 | 291.511 | 443.1911 | 505.7834 | 446.5349 | 610.2027 | 541.4861 | 603.3167 | 647.8732 | 629.5673 | 629.5673 | 629.5673 | 629.5673 | 629.5673 | 629.5673 | 629.5673 | 629.5673 | 629.5673 | 629.5673 | 629.5673 | 629.5673 | 629.5673 | 629.5673 | 629.5673 | 629.5673
75% |  |  |  |  | 0.17202 | 9.0242 | 55.3334 | 283.3902 | 413.139 | 318.4834 | 611.524 | 664.3211 | 702.2736 | 881.1701 | 910.289 | 910.289 | 910.289 | 910.289 | 910.289 | 910.289 | 910.289 | 910.289 | 910.289 | 910.289 | 910.289 | 910.289 | 910.289 | 910.289 | 910.289 | 910.289 |  |  | 57.2368 | 82.0481 | 191.187 | 188.4235 | 213.3569 | 310.8747 | 591.0464 | 706.6621 | 597.2228 | 899.5374 | 772.6094 | 886.8181 | 969.1193 | 935.3061 | 935.3061 | 935.3061 | 935.3061 | 935.3061 | 935.3061 | 935.3061 | 935.3061 | 935.3061 | 935.3061 | 935.3061 | 935.3061 | 935.3061 | 935.3061 | 935.3061 | 935.3061
70% | [7 empty] | 78.2842 | 250.9431 | 115.8555 | 573.8626 | 659.8027 | 721.5795 | 1012.7769 | 1060.1748 | 1060.1748 | 1060.1748 | 1060.1748 | 1060.1748 | 1060.1748 | 1060.1748 | 1060.1748 | 1060.1748 | 1060.1748 | 1060.1748 | 1060.1748 | 1060.1748 | 1060.1748 | 1060.1748 | 1060.1748 |  |  |  |  | 13.9473 | 12.8131 | 24.7488 | 107.115 | 540.5303 | 728.7229 | 550.584 | 1042.6741 | 836.068 | 1021.9704 | 1155.9355 | 1100.8963 | 1100.8963 | 1100.8963 | 1100.8963 | 1100.8963 | 1100.8963 | 1100.8963 | 1100.8963 | 1100.8963 | 1100.8963 | 1100.8963 | 1100.8963 | 1100.8963 | 1100.8963 | 1100.8963 | 1100.8963
65% | [8 empty] | 0.40539 |  | 145.0109 | 224.7284 | 292.046 | 647.5312 | 705.573 | 705.573 | 705.573 | 705.573 | 705.573 | 705.573 | 705.573 | 705.573 | 705.573 | 705.573 | 705.573 | 705.573 | 705.573 | 705.573 | 705.573 | 705.573 | [8 empty] | 118.5664 | 300.3588 | 126.2751 | 684.1423 | 431.1402 | 658.7893 | 822.8379 | 755.439 | 755.439 | 755.439 | 755.439 | 755.439 | 755.439 | 755.439 | 755.439 | 755.439 | 755.439 | 755.439 | 755.439 | 755.439 | 755.439 | 755.439 | 755.439
60% | FY38: 91.1742; FY39: 126.8218; FY40: 126.8218; FY41: 126.8218; FY42: 126.8218; FY43: 126.8218; FY44: 126.8218; FY45: 126.8218; FY46: 126.8218; FY47: 126.8218; FY48: 126.8218; FY49: 126.8218; FY50: 126.8218; FY51: 126.8218; FY52: 126.8218; FY53: 126.8218; FY54: 126.8218 | [11 empty] | 113.0025 | 9.404 | 97.6462 | 215.8063 | 161.9203 | 161.9203 | 161.9203 | 161.9203 | 161.9203 | 161.9203 | 161.9203 | 161.9203 | 161.9203 | 161.9203 | 161.9203 | 161.9203 | 161.9203 | 161.9203 | 161.9203 | 161.9203
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 6.1753 | 110.3648 | 135.3591 | 170.4974 | 224.2034 | 286.3766 | 425.5606 | 963.5892 | 1389.6401 | 1069.6783 | 2241.9506 | 2509.6007 | 2711.9106 | 3793.5907 | 3990.4321 | 3990.4321 | 3990.4321 | 3990.4321 | 3990.4321 | 3990.4321 | 3990.4321 | 3990.4321 | 3990.4321 | 3990.4321 | 3990.4321 | 3990.4321 | 3990.4321 | 3990.4321 | 3990.4321 | 3990.4321 | E @ R (MWh) | 93.4108 | 430.15 | 486.6866 | 718.8864 | 712.3384 | 773.1029 | 1046.0881 | 2142.5708 | 2735.8276 | 2172.2809 | 3917.1019 | 3110.3477 | 3831.3331 | 4404.9152 | 4163.9737 | 4163.9737 | 4163.9737 | 4163.9737 | 4163.9737 | 4163.9737 | 4163.9737 | 4163.9737 | 4163.9737 | 4163.9737 | 4163.9737 | 4163.9737 | 4163.9737 | 4163.9737 | 4163.9737 | 4163.9737
Option 7 Winter POE50 W E @ R (MWh) N 1 | 4.3227 | 77.2554 | 94.7514 | 119.3482 | 156.9424 | 200.4636 | 297.8924 | 674.5125 | 972.7481 | 748.7748 | 1569.3654 | 1756.7205 | 1898.3374 | 2655.5135 | 2793.3025 | 2793.3025 | 2793.3025 | 2793.3025 | 2793.3025 | 2793.3025 | 2793.3025 | 2793.3025 | 2793.3025 | 2793.3025 | 2793.3025 | 2793.3025 | 2793.3025 | 2793.3025 | 2793.3025 | 2793.3025 | Option 7 Winter POE10 W E @ R (MWh) N 1 | 28.0232 | 129.045 | 146.006 | 215.6659 | 213.7015 | 231.9309 | 313.8264 | 642.7712 | 820.7483 | 651.6843 | 1175.1306 | 933.1043 | 1149.3999 | 1321.4746 | 1249.1921 | 1249.1921 | 1249.1921 | 1249.1921 | 1249.1921 | 1249.1921 | 1249.1921 | 1249.1921 | 1249.1921 | 1249.1921 | 1249.1921 | 1249.1921 | 1249.1921 | 1249.1921 | 1249.1921 | 1249.1921
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | 2.2293 | 3.394 | 3.5111 | 3.4537 | 3.5082 | 3.5307 | 3.6025 | 3.7502 | 3.8744 | 3.9316 | 3.8807 | 4.0944 | 4.1283 | 4.0882 | 4.1686 | 4.21 | 4.21 | 4.21 | 4.21 | 4.21 | 4.21 | 4.21 | 4.21 | 4.21 | 4.21 | 4.21 | 4.21 | 4.21 | 4.21 | 4.21 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
98% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
97% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 5.4316 | 6.7071 | 6.7423 | 6.7043 | 6.7141 | 6.7837 | 6.9249 | 7.1735 | 7.303 | 7.3967 | 7.5385 | 7.7196 | 7.9385 | 8.0533 | 8.0161 | 8.0566 | 8.0566 | 8.0566 | 8.0566 | 8.0566 | 8.0566 | 8.0566 | 8.0566 | 8.0566 | 8.0566 | 8.0566 | 8.0566 | 8.0566 | 8.0566 | 8.0566
95% | 1.6813 | 2.8051 | 2.918 | 2.8626 | 2.9153 | 2.9369 | 3.0062 | 3.1487 | 3.2686 | 3.3238 | 3.2746 | 3.4808 | 3.5135 | 3.4748 | 3.5524 | 3.5924 | 3.5924 | 3.5924 | 3.5924 | 3.5924 | 3.5924 | 3.5924 | 3.5924 | 3.5924 | 3.5924 | 3.5924 | 3.5924 | 3.5924 | 3.5924 | 3.5924 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
90% | 24.9336 | 48.7543 | 51.148 | 49.9747 | 51.0903 | 51.5487 | 53.0179 | 56.0388 | 58.5802 | 59.75 | 58.7073 | 63.079 | 63.7723 | 62.9518 | 64.5971 | 65.4437 | 65.4437 | 65.4437 | 65.4437 | 65.4437 | 65.4437 | 65.4437 | 65.4437 | 65.4437 | 65.4437 | 65.4437 | 65.4437 | 65.4437 | 65.4437 | 65.4437 |  | 4.4685 | 5.6785 | 5.7119 | 5.6759 | 5.6852 | 5.7513 | 5.8852 | 6.121 | 6.2439 | 6.3328 | 6.4674 | 6.6391 | 6.8469 | 6.9557 | 6.9204 | 6.9589 | 6.9589 | 6.9589 | 6.9589 | 6.9589 | 6.9589 | 6.9589 | 6.9589 | 6.9589 | 6.9589 | 6.9589 | 6.9589 | 6.9589 | 6.9589 | 6.9589
85% | 29.1806 | 114.1031 | 122.6458 | 118.4583 | 122.4399 | 124.0759 | 129.3191 | 140.1002 | 149.1697 | 153.3447 | 149.6235 | 165.225 | 167.6994 | 164.7711 | 170.643 | 173.664 | 173.664 | 173.664 | 173.664 | 173.664 | 173.664 | 173.664 | 173.664 | 173.664 | 173.664 | 173.664 | 173.664 | 173.664 | 173.664 | 173.664 |  | 3.5054 | 4.65 | 4.6816 | 4.6475 | 4.6563 | 4.7188 | 4.8455 | 5.0686 | 5.1848 | 5.2689 | 5.3962 | 5.5587 | 5.7552 | 5.8582 | 5.8248 | 5.8612 | 5.8612 | 5.8612 | 5.8612 | 5.8612 | 5.8612 | 5.8612 | 5.8612 | 5.8612 | 5.8612 | 5.8612 | 5.8612 | 5.8612 | 5.8612 | 5.8612
80% |  | 76.2716 | 90.1487 | 83.3465 | 89.8144 | 92.4719 | 100.9891 | 118.5024 | 133.2353 | 140.0173 | 133.9725 | 159.3161 | 163.3356 | 158.5788 | 168.1174 | 173.0249 | 173.0249 | 173.0249 | 173.0249 | 173.0249 | 173.0249 | 173.0249 | 173.0249 | 173.0249 | 173.0249 | 173.0249 | 173.0249 | 173.0249 | 173.0249 | 173.0249 |  | 10.169 | 14.4859 | 14.605 | 14.4766 | 14.5096 | 14.7454 | 15.2231 | 16.0645 | 16.5029 | 16.8201 | 17.3001 | 17.9129 | 18.654 | 19.0424 | 18.9165 | 19.0537 | 19.0537 | 19.0537 | 19.0537 | 19.0537 | 19.0537 | 19.0537 | 19.0537 | 19.0537 | 19.0537 | 19.0537 | 19.0537 | 19.0537 | 19.0537 | 19.0537
75% |  | 2.0449 | 6.8387 | 4.1421 | 6.6906 | 7.9111 | 12.4972 | 25.1118 | 38.9762 | 46.3383 | 39.7468 | 70.6015 | 76.2631 | 69.5855 | 83.2676 | 90.7587 | 90.7587 | 90.7587 | 90.7587 | 90.7587 | 90.7587 | 90.7587 | 90.7587 | 90.7587 | 90.7587 | 90.7587 | 90.7587 | 90.7587 | 90.7587 | 90.7587 |  | 3.1582 | 5.1859 | 5.2419 | 5.1815 | 5.197 | 5.3078 | 5.5322 | 5.9274 | 6.1333 | 6.2823 | 6.5077 | 6.7956 | 7.1436 | 7.3261 | 7.2669 | 7.3314 | 7.3314 | 7.3314 | 7.3314 | 7.3314 | 7.3314 | 7.3314 | 7.3314 | 7.3314 | 7.3314 | 7.3314 | 7.3314 | 7.3314 | 7.3314 | 7.3314
70% | [31 empty] | 3.696 | 9.3866 | 9.5436 | 9.3743 | 9.4178 | 9.7286 | 10.3583 | 11.4674 | 12.0453 | 12.4634 | 13.0962 | 13.904 | 14.8809 | 15.3928 | 15.2268 | 15.4078 | 15.4078 | 15.4078 | 15.4078 | 15.4078 | 15.4078 | 15.4078 | 15.4078 | 15.4078 | 15.4078 | 15.4078 | 15.4078 | 15.4078 | 15.4078 | 15.4078
65% | [31 empty] | 0.018768 | 1.0718 | 1.1205 | 1.068 | 1.0815 | 1.1779 | 1.3734 | 1.7176 | 1.8969 | 2.0267 | 2.2231 | 2.4738 | 2.7769 | 2.9358 | 2.8843 | 2.9405 | 2.9405 | 2.9405 | 2.9405 | 2.9405 | 2.9405 | 2.9405 | 2.9405 | 2.9405 | 2.9405 | 2.9405 | 2.9405 | 2.9405 | 2.9405 | 2.9405
60% | [32 empty] | 0.0029592 | 0.012833 | 0.0024792 | 0.0043735 | 0.033315 | 0.17404 | 0.6831 | 1.0771 | 1.4159 | 2.0129 | 2.9198 | 4.2275 | 5.003 | 4.7449 | 5.0266 | 5.0266 | 5.0266 | 5.0266 | 5.0266 | 5.0266 | 5.0266 | 5.0266 | 5.0266 | 5.0266 | 5.0266 | 5.0266 | 5.0266 | 5.0266 | 5.0266
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 57.4445 | 244.8992 | 274.4381 | 259.6155 | 273.6942 | 279.6505 | 299.4076 | 343.1855 | 383.2333 | 402.6387 | 385.3134 | 461.1388 | 473.9252 | 458.8156 | 489.4027 | 505.5867 | 505.5867 | 505.5867 | 505.5867 | 505.5867 | 505.5867 | 505.5867 | 505.5867 | 505.5867 | 505.5867 | 505.5867 | 505.5867 | 505.5867 | 505.5867 | 505.5867 | E @ R (MWh) | 30.143 | 46.6971 | 47.183 | 46.6594 | 46.7933 | 47.7643 | 49.8134 | 53.6808 | 55.8233 | 57.4266 | 59.9366 | 63.2842 | 67.5413 | 69.8615 | 69.1027 | 69.9304 | 69.9304 | 69.9304 | 69.9304 | 69.9304 | 69.9304 | 69.9304 | 69.9304 | 69.9304 | 69.9304 | 69.9304 | 69.9304 | 69.9304 | 69.9304 | 69.9304
Option 7 Summer POE50 W E @ R (MWh) N 1 | 40.2112 | 171.4294 | 192.1066 | 181.7309 | 191.5859 | 195.7553 | 209.5854 | 240.2298 | 268.2633 | 281.8471 | 269.7194 | 322.7971 | 331.7476 | 321.171 | 342.5819 | 353.9107 | 353.9107 | 353.9107 | 353.9107 | 353.9107 | 353.9107 | 353.9107 | 353.9107 | 353.9107 | 353.9107 | 353.9107 | 353.9107 | 353.9107 | 353.9107 | 353.9107 | Option 7 Summer POE10 W E @ R (MWh) N 1 | 9.0429 | 14.0091 | 14.1549 | 13.9978 | 14.038 | 14.3293 | 14.944 | 16.1042 | 16.747 | 17.228 | 17.981 | 18.9853 | 20.2624 | 20.9585 | 20.7308 | 20.9791 | 20.9791 | 20.9791 | 20.9791 | 20.9791 | 20.9791 | 20.9791 | 20.9791 | 20.9791 | 20.9791 | 20.9791 | 20.9791 | 20.9791 | 20.9791 | 20.9791
Option 8 -
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | 0.92537 | 2.1455 | 2.2748 | 2.4348 | 2.6471 | 2.8485 | 3.2003 | 4.0851 | 4.5611 | 4.2139 | 5.2888 | 5.4825 | 5.6217 | 6.2779 | 6.3847 | 6.3847 | 6.3847 | 6.3847 | 6.3847 | 6.3847 | 6.3847 | 6.3847 | 6.3847 | 6.3847 | 6.3847 | 6.3847 | 6.3847 | 6.3847 | 6.3847 | 6.3847 |  | 2.0467 | 3.2105 | 3.331 | 3.7469 | 3.7368 | 3.8283 | 4.186 | 5.2137 | 5.6378 | 5.2363 | 6.3453 | 5.8797 | 6.2986 | 6.6005 | 6.4765 | 6.4765 | 6.4765 | 6.4765 | 6.4765 | 6.4765 | 6.4765 | 6.4765 | 6.4765 | 6.4765 | 6.4765 | 6.4765 | 6.4765 | 6.4765 | 6.4765 | 6.4765
98% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
97% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
95% | 2.0617 | 6.7704 | 7.2696 | 7.8869 | 8.7065 | 9.4834 | 10.8412 | 14.2562 | 16.093 | 14.753 | 18.9015 | 19.6489 | 20.1862 | 22.7188 | 23.131 | 23.131 | 23.131 | 23.131 | 23.131 | 23.131 | 23.131 | 23.131 | 23.131 | 23.131 | 23.131 | 23.131 | 23.131 | 23.131 | 23.131 | 23.131 |  | 6.3892 | 10.8806 | 11.3457 | 12.9509 | 12.9118 | 13.2648 | 14.6453 | 18.6116 | 20.2483 | 18.699 | 22.9788 | 21.1819 | 22.7987 | 23.9639 | 23.4852 | 23.4852 | 23.4852 | 23.4852 | 23.4852 | 23.4852 | 23.4852 | 23.4852 | 23.4852 | 23.4852 | 23.4852 | 23.4852 | 23.4852 | 23.4852 | 23.4852 | 23.4852
90% | 3.2506 | 29.7534 | 32.6399 | 36.2085 | 40.9465 | 45.4383 | 53.2881 | 73.0309 | 83.65 | 75.9031 | 99.8865 | 104.2076 | 107.3137 | 121.9552 | 124.3384 | 124.3384 | 124.3384 | 124.3384 | 124.3384 | 124.3384 | 124.3384 | 124.3384 | 124.3384 | 124.3384 | 124.3384 | 124.3384 | 124.3384 | 124.3384 | 124.3384 | 124.3384 |  | 27.5498 | 53.5156 | 56.2046 | 65.4847 | 65.2585 | 67.2992 | 75.2803 | 98.2105 | 107.6729 | 98.716 | 123.4584 | 113.0702 | 122.4175 | 129.1533 | 126.3859 | 126.3859 | 126.3859 | 126.3859 | 126.3859 | 126.3859 | 126.3859 | 126.3859 | 126.3859 | 126.3859 | 126.3859 | 126.3859 | 126.3859 | 126.3859 | 126.3859 | 126.3859
85% |  | 62.8339 | 74.8936 | 89.803 | 109.5982 | 128.3646 | 161.1605 | 243.6444 | 288.0101 | 255.644 | 355.845 | 373.8982 | 386.8755 | 448.0465 | 458.0033 | 458.0033 | 458.0033 | 458.0033 | 458.0033 | 458.0033 | 458.0033 | 458.0033 | 458.0033 | 458.0033 | 458.0033 | 458.0033 | 458.0033 | 458.0033 | 458.0033 | 458.0033 |  | 53.6277 | 162.111 | 173.3454 | 212.1168 | 211.1719 | 219.6975 | 253.0423 | 348.8429 | 388.3761 | 350.9549 | 454.327 | 410.9258 | 449.9778 | 478.1195 | 466.5576 | 466.5576 | 466.5576 | 466.5576 | 466.5576 | 466.5576 | 466.5576 | 466.5576 | 466.5576 | 466.5576 | 466.5576 | 466.5576 | 466.5576 | 466.5576 | 466.5576 | 466.5576
80% |  | 9.9766 | 19.6484 | 35.8864 | 64.3977 | 94.1103 | 146.0357 | 276.6314 | 346.8752 | 295.6303 | 454.2773 | 482.8608 | 503.4075 | 600.259 | 616.0234 | 616.0234 | 616.0234 | 616.0234 | 616.0234 | 616.0234 | 616.0234 | 616.0234 | 616.0234 | 616.0234 | 616.0234 | 616.0234 | 616.0234 | 616.0234 | 616.0234 | 616.0234 |  | 4.7409 | 147.5405 | 165.3278 | 226.7142 | 225.2181 | 238.7166 | 291.511 | 443.1911 | 505.7834 | 446.5349 | 610.2027 | 541.4861 | 603.3167 | 647.8732 | 629.5673 | 629.5673 | 629.5673 | 629.5673 | 629.5673 | 629.5673 | 629.5673 | 629.5673 | 629.5673 | 629.5673 | 629.5673 | 629.5673 | 629.5673 | 629.5673 | 629.5673 | 629.5673
75% |  |  |  |  | 0.17202 | 9.0242 | 55.3334 | 283.3902 | 413.139 | 318.4834 | 611.524 | 664.3211 | 702.2736 | 881.1701 | 910.289 | 910.289 | 910.289 | 910.289 | 910.289 | 910.289 | 910.289 | 910.289 | 910.289 | 910.289 | 910.289 | 910.289 | 910.289 | 910.289 | 910.289 | 910.289 |  |  | 57.2368 | 82.0481 | 191.187 | 188.4235 | 213.3569 | 310.8747 | 591.0464 | 706.6621 | 597.2228 | 899.5374 | 772.6094 | 886.8181 | 969.1193 | 935.3061 | 935.3061 | 935.3061 | 935.3061 | 935.3061 | 935.3061 | 935.3061 | 935.3061 | 935.3061 | 935.3061 | 935.3061 | 935.3061 | 935.3061 | 935.3061 | 935.3061 | 935.3061
70% | [7 empty] | 78.2842 | 250.9431 | 115.8555 | 573.8626 | 659.8027 | 721.5795 | 1012.7769 | 1060.1748 | 1060.1748 | 1060.1748 | 1060.1748 | 1060.1748 | 1060.1748 | 1060.1748 | 1060.1748 | 1060.1748 | 1060.1748 | 1060.1748 | 1060.1748 | 1060.1748 | 1060.1748 | 1060.1748 | 1060.1748 |  |  |  |  | 13.9473 | 12.8131 | 24.7488 | 107.115 | 540.5303 | 728.7229 | 550.584 | 1042.6741 | 836.068 | 1021.9704 | 1155.9355 | 1100.8963 | 1100.8963 | 1100.8963 | 1100.8963 | 1100.8963 | 1100.8963 | 1100.8963 | 1100.8963 | 1100.8963 | 1100.8963 | 1100.8963 | 1100.8963 | 1100.8963 | 1100.8963 | 1100.8963 | 1100.8963
65% | [8 empty] | 0.40539 |  | 145.0109 | 224.7284 | 292.046 | 647.5312 | 705.573 | 705.573 | 705.573 | 705.573 | 705.573 | 705.573 | 705.573 | 705.573 | 705.573 | 705.573 | 705.573 | 705.573 | 705.573 | 705.573 | 705.573 | 705.573 | [8 empty] | 118.5664 | 300.3588 | 126.2751 | 684.1423 | 431.1402 | 658.7893 | 822.8379 | 755.439 | 755.439 | 755.439 | 755.439 | 755.439 | 755.439 | 755.439 | 755.439 | 755.439 | 755.439 | 755.439 | 755.439 | 755.439 | 755.439 | 755.439 | 755.439
60% | FY38: 91.1742; FY39: 126.8218; FY40: 126.8218; FY41: 126.8218; FY42: 126.8218; FY43: 126.8218; FY44: 126.8218; FY45: 126.8218; FY46: 126.8218; FY47: 126.8218; FY48: 126.8218; FY49: 126.8218; FY50: 126.8218; FY51: 126.8218; FY52: 126.8218; FY53: 126.8218; FY54: 126.8218 | [11 empty] | 113.0025 | 9.404 | 97.6462 | 215.8063 | 161.9203 | 161.9203 | 161.9203 | 161.9203 | 161.9203 | 161.9203 | 161.9203 | 161.9203 | 161.9203 | 161.9203 | 161.9203 | 161.9203 | 161.9203 | 161.9203 | 161.9203 | 161.9203
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 6.1753 | 110.3648 | 135.3591 | 170.4974 | 224.2034 | 286.3766 | 425.5606 | 963.5892 | 1389.6401 | 1069.6783 | 2241.9506 | 2509.6007 | 2711.9106 | 3793.5907 | 3990.4321 | 3990.4321 | 3990.4321 | 3990.4321 | 3990.4321 | 3990.4321 | 3990.4321 | 3990.4321 | 3990.4321 | 3990.4321 | 3990.4321 | 3990.4321 | 3990.4321 | 3990.4321 | 3990.4321 | 3990.4321 | E @ R (MWh) | 93.4108 | 430.15 | 486.6866 | 718.8864 | 712.3384 | 773.1029 | 1046.0881 | 2142.5708 | 2735.8276 | 2172.2809 | 3917.1019 | 3110.3477 | 3831.3331 | 4404.9152 | 4163.9737 | 4163.9737 | 4163.9737 | 4163.9737 | 4163.9737 | 4163.9737 | 4163.9737 | 4163.9737 | 4163.9737 | 4163.9737 | 4163.9737 | 4163.9737 | 4163.9737 | 4163.9737 | 4163.9737 | 4163.9737
Option 8 Winter POE50 W E @ R (MWh) N 1 | 4.3227 | 77.2554 | 94.7514 | 119.3482 | 156.9424 | 200.4636 | 297.8924 | 674.5125 | 972.7481 | 748.7748 | 1569.3654 | 1756.7205 | 1898.3374 | 2655.5135 | 2793.3025 | 2793.3025 | 2793.3025 | 2793.3025 | 2793.3025 | 2793.3025 | 2793.3025 | 2793.3025 | 2793.3025 | 2793.3025 | 2793.3025 | 2793.3025 | 2793.3025 | 2793.3025 | 2793.3025 | 2793.3025 | Option 8 Winter POE10 W E @ R (MWh) N 1 | 28.0232 | 129.045 | 146.006 | 215.6659 | 213.7015 | 231.9309 | 313.8264 | 642.7712 | 820.7483 | 651.6843 | 1175.1306 | 933.1043 | 1149.3999 | 1321.4746 | 1249.1921 | 1249.1921 | 1249.1921 | 1249.1921 | 1249.1921 | 1249.1921 | 1249.1921 | 1249.1921 | 1249.1921 | 1249.1921 | 1249.1921 | 1249.1921 | 1249.1921 | 1249.1921 | 1249.1921 | 1249.1921
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | 2.2293 | 3.394 | 3.5111 | 3.4537 | 3.5082 | 3.5307 | 3.6025 | 3.7502 | 3.8744 | 3.9316 | 3.8807 | 4.0944 | 4.1283 | 4.0882 | 4.1686 | 4.21 | 4.21 | 4.21 | 4.21 | 4.21 | 4.21 | 4.21 | 4.21 | 4.21 | 4.21 | 4.21 | 4.21 | 4.21 | 4.21 | 4.21 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
98% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
97% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 5.4316 | 6.7071 | 6.7423 | 6.7043 | 6.7141 | 6.7837 | 6.9249 | 7.1735 | 7.303 | 7.3967 | 7.5385 | 7.7196 | 7.9385 | 8.0533 | 8.0161 | 8.0566 | 8.0566 | 8.0566 | 8.0566 | 8.0566 | 8.0566 | 8.0566 | 8.0566 | 8.0566 | 8.0566 | 8.0566 | 8.0566 | 8.0566 | 8.0566 | 8.0566
95% | 1.6813 | 2.8051 | 2.918 | 2.8626 | 2.9153 | 2.9369 | 3.0062 | 3.1487 | 3.2686 | 3.3238 | 3.2746 | 3.4808 | 3.5135 | 3.4748 | 3.5524 | 3.5924 | 3.5924 | 3.5924 | 3.5924 | 3.5924 | 3.5924 | 3.5924 | 3.5924 | 3.5924 | 3.5924 | 3.5924 | 3.5924 | 3.5924 | 3.5924 | 3.5924 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
90% | 24.9336 | 48.7543 | 51.148 | 49.9747 | 51.0903 | 51.5487 | 53.0179 | 56.0388 | 58.5802 | 59.75 | 58.7073 | 63.079 | 63.7723 | 62.9518 | 64.5971 | 65.4437 | 65.4437 | 65.4437 | 65.4437 | 65.4437 | 65.4437 | 65.4437 | 65.4437 | 65.4437 | 65.4437 | 65.4437 | 65.4437 | 65.4437 | 65.4437 | 65.4437 |  | 4.4685 | 5.6785 | 5.7119 | 5.6759 | 5.6852 | 5.7513 | 5.8852 | 6.121 | 6.2439 | 6.3328 | 6.4674 | 6.6391 | 6.8469 | 6.9557 | 6.9204 | 6.9589 | 6.9589 | 6.9589 | 6.9589 | 6.9589 | 6.9589 | 6.9589 | 6.9589 | 6.9589 | 6.9589 | 6.9589 | 6.9589 | 6.9589 | 6.9589 | 6.9589
85% | 29.1806 | 114.1031 | 122.6458 | 118.4583 | 122.4399 | 124.0759 | 129.3191 | 140.1002 | 149.1697 | 153.3447 | 149.6235 | 165.225 | 167.6994 | 164.7711 | 170.643 | 173.664 | 173.664 | 173.664 | 173.664 | 173.664 | 173.664 | 173.664 | 173.664 | 173.664 | 173.664 | 173.664 | 173.664 | 173.664 | 173.664 | 173.664 |  | 3.5054 | 4.65 | 4.6816 | 4.6475 | 4.6563 | 4.7188 | 4.8455 | 5.0686 | 5.1848 | 5.2689 | 5.3962 | 5.5587 | 5.7552 | 5.8582 | 5.8248 | 5.8612 | 5.8612 | 5.8612 | 5.8612 | 5.8612 | 5.8612 | 5.8612 | 5.8612 | 5.8612 | 5.8612 | 5.8612 | 5.8612 | 5.8612 | 5.8612 | 5.8612
80% |  | 76.2716 | 90.1487 | 83.3465 | 89.8144 | 92.4719 | 100.9891 | 118.5024 | 133.2353 | 140.0173 | 133.9725 | 159.3161 | 163.3356 | 158.5788 | 168.1174 | 173.0249 | 173.0249 | 173.0249 | 173.0249 | 173.0249 | 173.0249 | 173.0249 | 173.0249 | 173.0249 | 173.0249 | 173.0249 | 173.0249 | 173.0249 | 173.0249 | 173.0249 |  | 10.169 | 14.4859 | 14.605 | 14.4766 | 14.5096 | 14.7454 | 15.2231 | 16.0645 | 16.5029 | 16.8201 | 17.3001 | 17.9129 | 18.654 | 19.0424 | 18.9165 | 19.0537 | 19.0537 | 19.0537 | 19.0537 | 19.0537 | 19.0537 | 19.0537 | 19.0537 | 19.0537 | 19.0537 | 19.0537 | 19.0537 | 19.0537 | 19.0537 | 19.0537
75% |  | 2.0449 | 6.8387 | 4.1421 | 6.6906 | 7.9111 | 12.4972 | 25.1118 | 38.9762 | 46.3383 | 39.7468 | 70.6015 | 76.2631 | 69.5855 | 83.2676 | 90.7587 | 90.7587 | 90.7587 | 90.7587 | 90.7587 | 90.7587 | 90.7587 | 90.7587 | 90.7587 | 90.7587 | 90.7587 | 90.7587 | 90.7587 | 90.7587 | 90.7587 |  | 3.1582 | 5.1859 | 5.2419 | 5.1815 | 5.197 | 5.3078 | 5.5322 | 5.9274 | 6.1333 | 6.2823 | 6.5077 | 6.7956 | 7.1436 | 7.3261 | 7.2669 | 7.3314 | 7.3314 | 7.3314 | 7.3314 | 7.3314 | 7.3314 | 7.3314 | 7.3314 | 7.3314 | 7.3314 | 7.3314 | 7.3314 | 7.3314 | 7.3314 | 7.3314
70% | [31 empty] | 3.696 | 9.3866 | 9.5436 | 9.3743 | 9.4178 | 9.7286 | 10.3583 | 11.4674 | 12.0453 | 12.4634 | 13.0962 | 13.904 | 14.8809 | 15.3928 | 15.2268 | 15.4078 | 15.4078 | 15.4078 | 15.4078 | 15.4078 | 15.4078 | 15.4078 | 15.4078 | 15.4078 | 15.4078 | 15.4078 | 15.4078 | 15.4078 | 15.4078 | 15.4078
65% | [31 empty] | 0.018768 | 1.0718 | 1.1205 | 1.068 | 1.0815 | 1.1779 | 1.3734 | 1.7176 | 1.8969 | 2.0267 | 2.2231 | 2.4738 | 2.7769 | 2.9358 | 2.8843 | 2.9405 | 2.9405 | 2.9405 | 2.9405 | 2.9405 | 2.9405 | 2.9405 | 2.9405 | 2.9405 | 2.9405 | 2.9405 | 2.9405 | 2.9405 | 2.9405 | 2.9405
60% | [32 empty] | 0.0029592 | 0.012833 | 0.0024792 | 0.0043735 | 0.033315 | 0.17404 | 0.6831 | 1.0771 | 1.4159 | 2.0129 | 2.9198 | 4.2275 | 5.003 | 4.7449 | 5.0266 | 5.0266 | 5.0266 | 5.0266 | 5.0266 | 5.0266 | 5.0266 | 5.0266 | 5.0266 | 5.0266 | 5.0266 | 5.0266 | 5.0266 | 5.0266 | 5.0266
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 57.4445 | 244.8992 | 274.4381 | 259.6155 | 273.6942 | 279.6505 | 299.4076 | 343.1855 | 383.2333 | 402.6387 | 385.3134 | 461.1388 | 473.9252 | 458.8156 | 489.4027 | 505.5867 | 505.5867 | 505.5867 | 505.5867 | 505.5867 | 505.5867 | 505.5867 | 505.5867 | 505.5867 | 505.5867 | 505.5867 | 505.5867 | 505.5867 | 505.5867 | 505.5867 | E @ R (MWh) | 30.143 | 46.6971 | 47.183 | 46.6594 | 46.7933 | 47.7643 | 49.8134 | 53.6808 | 55.8233 | 57.4266 | 59.9366 | 63.2842 | 67.5413 | 69.8615 | 69.1027 | 69.9304 | 69.9304 | 69.9304 | 69.9304 | 69.9304 | 69.9304 | 69.9304 | 69.9304 | 69.9304 | 69.9304 | 69.9304 | 69.9304 | 69.9304 | 69.9304 | 69.9304
Option 8 Summer POE50 W E @ R (MWh) N 1 | 40.2112 | 171.4294 | 192.1066 | 181.7309 | 191.5859 | 195.7553 | 209.5854 | 240.2298 | 268.2633 | 281.8471 | 269.7194 | 322.7971 | 331.7476 | 321.171 | 342.5819 | 353.9107 | 353.9107 | 353.9107 | 353.9107 | 353.9107 | 353.9107 | 353.9107 | 353.9107 | 353.9107 | 353.9107 | 353.9107 | 353.9107 | 353.9107 | 353.9107 | 353.9107 | Option 8 Summer POE10 W E @ R (MWh) N 1 | 9.0429 | 14.0091 | 14.1549 | 13.9978 | 14.038 | 14.3293 | 14.944 | 16.1042 | 16.747 | 17.228 | 17.981 | 18.9853 | 20.2624 | 20.9585 | 20.7308 | 20.9791 | 20.9791 | 20.9791 | 20.9791 | 20.9791 | 20.9791 | 20.9791 | 20.9791 | 20.9791 | 20.9791 | 20.9791 | 20.9791 | 20.9791 | 20.9791 | 20.9791

## E@R N-2
Option 1 - Do Nothing
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | 6.2898 | 7.5099 | 7.6393 | 7.7992 | 8.0116 | 8.2129 | 8.5647 | 9.4496 | 9.9255 | 9.5783 | 10.6532 | 10.8469 | 10.9861 | 11.6424 | 11.7492 | 11.7492 | 11.7492 | 11.7492 | 11.7492 | 11.7492 | 11.7492 | 11.7492 | 11.7492 | 11.7492 | 11.7492 | 11.7492 | 11.7492 | 11.7492 | 11.7492 | 11.7492 |  | 7.4111 | 8.5749 | 8.6954 | 9.1114 | 9.1012 | 9.1927 | 9.5504 | 10.5781 | 11.0022 | 10.6008 | 11.7097 | 11.2441 | 11.6631 | 11.965 | 11.8409 | 11.8409 | 11.8409 | 11.8409 | 11.8409 | 11.8409 | 11.8409 | 11.8409 | 11.8409 | 11.8409 | 11.8409 | 11.8409 | 11.8409 | 11.8409 | 11.8409 | 11.8409
98% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
97% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
95% | 23.5194 | 28.2281 | 28.7274 | 29.3447 | 30.1642 | 30.9412 | 32.299 | 35.7139 | 37.5508 | 36.2107 | 40.3592 | 41.1067 | 41.6439 | 44.1765 | 44.5887 | 44.5887 | 44.5887 | 44.5887 | 44.5887 | 44.5887 | 44.5887 | 44.5887 | 44.5887 | 44.5887 | 44.5887 | 44.5887 | 44.5887 | 44.5887 | 44.5887 | 44.5887 |  | 27.8469 | 32.3383 | 32.8034 | 34.4086 | 34.3695 | 34.7225 | 36.103 | 40.0693 | 41.7061 | 40.1568 | 44.4365 | 42.6397 | 44.2565 | 45.4216 | 44.9429 | 44.9429 | 44.9429 | 44.9429 | 44.9429 | 44.9429 | 44.9429 | 44.9429 | 44.9429 | 44.9429 | 44.9429 | 44.9429 | 44.9429 | 44.9429 | 44.9429 | 44.9429
90% | 131.2778 | 158.4998 | 161.3863 | 164.9549 | 169.693 | 174.1847 | 182.0345 | 201.7773 | 212.3964 | 204.6495 | 228.6329 | 232.954 | 236.0601 | 250.7016 | 253.0848 | 253.0848 | 253.0848 | 253.0848 | 253.0848 | 253.0848 | 253.0848 | 253.0848 | 253.0848 | 253.0848 | 253.0848 | 253.0848 | 253.0848 | 253.0848 | 253.0848 | 253.0848 |  | 156.2962 | 182.262 | 184.951 | 194.2311 | 194.0049 | 196.0456 | 204.0267 | 226.9569 | 236.4193 | 227.4624 | 252.2049 | 241.8166 | 251.1639 | 257.8997 | 255.1323 | 255.1323 | 255.1323 | 255.1323 | 255.1323 | 255.1323 | 255.1323 | 255.1323 | 255.1323 | 255.1323 | 255.1323 | 255.1323 | 255.1323 | 255.1323 | 255.1323 | 255.1323
85% | 517.7326 | 631.4638 | 643.5236 | 658.433 | 678.2282 | 696.9946 | 729.7905 | 812.2744 | 856.6401 | 824.274 | 924.4749 | 942.5282 | 955.5054 | 1016.6765 | 1026.6333 | 1026.6333 | 1026.6333 | 1026.6333 | 1026.6333 | 1026.6333 | 1026.6333 | 1026.6333 | 1026.6333 | 1026.6333 | 1026.6333 | 1026.6333 | 1026.6333 | 1026.6333 | 1026.6333 | 1026.6333 |  | 622.2576 | 730.7409 | 741.9753 | 780.7468 | 779.8019 | 788.3275 | 821.6723 | 917.4729 | 957.006 | 919.5849 | 1022.9569 | 979.5557 | 1018.6078 | 1046.7495 | 1035.1875 | 1035.1875 | 1035.1875 | 1035.1875 | 1035.1875 | 1035.1875 | 1035.1875 | 1035.1875 | 1035.1875 | 1035.1875 | 1035.1875 | 1035.1875 | 1035.1875 | 1035.1875 | 1035.1875 | 1035.1875
80% | 765.156 | 945.2254 | 964.3195 | 987.9254 | 1019.2669 | 1048.9795 | 1100.9048 | 1231.5006 | 1301.7444 | 1250.4995 | 1409.1465 | 1437.7299 | 1458.2767 | 1555.1282 | 1570.8926 | 1570.8926 | 1570.8926 | 1570.8926 | 1570.8926 | 1570.8926 | 1570.8926 | 1570.8926 | 1570.8926 | 1570.8926 | 1570.8926 | 1570.8926 | 1570.8926 | 1570.8926 | 1570.8926 | 1570.8926 |  | 930.6493 | 1102.4097 | 1120.197 | 1181.5834 | 1180.0873 | 1193.5858 | 1246.3802 | 1398.0603 | 1460.6526 | 1401.4041 | 1565.0719 | 1496.3553 | 1558.1859 | 1602.7423 | 1584.4364 | 1584.4364 | 1584.4364 | 1584.4364 | 1584.4364 | 1584.4364 | 1584.4364 | 1584.4364 | 1584.4364 | 1584.4364 | 1584.4364 | 1584.4364 | 1584.4364 | 1584.4364 | 1584.4364 | 1584.4364
75% | 1299.5462 | 1632.1565 | 1667.4256 | 1711.0285 | 1768.9201 | 1823.803 | 1919.7155 | 2160.942 | 2290.6908 | 2196.0352 | 2489.0758 | 2541.8729 | 2579.8253 | 2758.7219 | 2787.8407 | 2787.8407 | 2787.8407 | 2787.8407 | 2787.8407 | 2787.8407 | 2787.8407 | 2787.8407 | 2787.8407 | 2787.8407 | 2787.8407 | 2787.8407 | 2787.8407 | 2787.8407 | 2787.8407 | 2787.8407 |  | 1605.2327 | 1922.4952 | 1955.3505 | 2068.7387 | 2065.9753 | 2090.9087 | 2188.4265 | 2468.5981 | 2584.2139 | 2474.7746 | 2777.0892 | 2650.1611 | 2764.3699 | 2846.6711 | 2812.8578 | 2812.8578 | 2812.8578 | 2812.8578 | 2812.8578 | 2812.8578 | 2812.8578 | 2812.8578 | 2812.8578 | 2812.8578 | 2812.8578 | 2812.8578 | 2812.8578 | 2812.8578 | 2812.8578 | 2812.8578
70% | 1904.5555 | 2445.9592 | 2503.3682 | 2574.3426 | 2668.5752 | 2757.9103 | 2914.0312 | 3306.6856 | 3517.8832 | 3363.8083 | 3840.8027 | 3926.7428 | 3988.5195 | 4279.7169 | 4327.1149 | 4327.1149 | 4327.1149 | 4327.1149 | 4327.1149 | 4327.1149 | 4327.1149 | 4327.1149 | 4327.1149 | 4327.1149 | 4327.1149 | 4327.1149 | 4327.1149 | 4327.1149 | 4327.1149 | 4327.1149 |  | 2402.1342 | 2918.5558 | 2972.0357 | 3156.6025 | 3152.1043 | 3192.6894 | 3351.4232 | 3807.4704 | 3995.6629 | 3817.524 | 4309.6142 | 4103.0081 | 4288.9105 | 4422.8756 | 4367.8364 | 4367.8364 | 4367.8364 | 4367.8364 | 4367.8364 | 4367.8364 | 4367.8364 | 4367.8364 | 4367.8364 | 4367.8364 | 4367.8364 | 4367.8364 | 4367.8364 | 4367.8364 | 4367.8364 | 4367.8364
65% | 2035.9088 | 2698.8915 | 2769.1924 | 2856.1049 | 2971.4986 | 3080.895 | 3272.0749 | 3752.9047 | 4011.5294 | 3822.8551 | 4406.9646 | 4512.2036 | 4587.8531 | 4944.4426 | 5002.4844 | 5002.4844 | 5002.4844 | 5002.4844 | 5002.4844 | 5002.4844 | 5002.4844 | 5002.4844 | 5002.4844 | 5002.4844 | 5002.4844 | 5002.4844 | 5002.4844 | 5002.4844 | 5002.4844 | 5002.4844 |  | 2645.225 | 3277.6155 | 3343.1051 | 3569.1186 | 3563.6103 | 3613.3093 | 3807.6888 | 4366.1471 | 4596.6007 | 4378.4584 | 4981.0536 | 4728.0515 | 4955.7006 | 5119.7493 | 5052.3503 | 5052.3503 | 5052.3503 | 5052.3503 | 5052.3503 | 5052.3503 | 5052.3503 | 5052.3503 | 5052.3503 | 5052.3503 | 5052.3503 | 5052.3503 | 5052.3503 | 5052.3503 | 5052.3503 | 5052.3503
60% | 2098.8616 | 2921.1907 | 3008.3883 | 3116.1901 | 3259.3184 | 3395.008 | 3632.1374 | 4228.5337 | 4549.3182 | 4315.2964 | 5039.7953 | 5170.3283 | 5264.16 | 5706.4549 | 5778.4469 | 5778.4469 | 5778.4469 | 5778.4469 | 5778.4469 | 5778.4469 | 5778.4469 | 5778.4469 | 5778.4469 | 5778.4469 | 5778.4469 | 5778.4469 | 5778.4469 | 5778.4469 | 5778.4469 | 5778.4469 |  | 2854.6256 | 3639.0098 | 3720.2396 | 4000.575 | 3993.7428 | 4055.3868 | 4296.485 | 4989.1674 | 5275.01 | 5004.4378 | 5751.8653 | 5438.0548 | 5720.4188 | 5923.8962 | 5840.298 | 5840.298 | 5840.298 | 5840.298 | 5840.298 | 5840.298 | 5840.298 | 5840.298 | 5840.298 | 5840.298 | 5840.298 | 5840.298 | 5840.298 | 5840.298 | 5840.298 | 5840.298
55% | 1733.592 | 2625.5087 | 2720.0851 | 2837.0093 | 2992.2496 | 3139.4215 | 3396.6175 | 4043.4823 | 4391.4125 | 4137.5871 | 4923.395 | 5064.974 | 5166.746 | 5646.469 | 5724.5532 | 5724.5532 | 5724.5532 | 5724.5532 | 5724.5532 | 5724.5532 | 5724.5532 | 5724.5532 | 5724.5532 | 5724.5532 | 5724.5532 | 5724.5532 | 5724.5532 | 5724.5532 | 5724.5532 | 5724.5532 |  | 2553.3107 | 3404.0714 | 3492.1751 | 3796.2332 | 3788.8228 | 3855.6833 | 4117.1838 | 4868.4828 | 5178.5141 | 4885.0454 | 5695.7222 | 5355.3561 | 5661.6146 | 5882.3107 | 5791.6383 | 5791.6383 | 5791.6383 | 5791.6383 | 5791.6383 | 5791.6383 | 5791.6383 | 5791.6383 | 5791.6383 | 5791.6383 | 5791.6383 | 5791.6383 | 5791.6383 | 5791.6383 | 5791.6383 | 5791.6383
50% | 1107.3363 | 2015.6842 | 2112.003 | 2231.0812 | 2389.1813 | 2539.0646 | 2800.9987 | 3459.7803 | 3814.1202 | 3555.6188 | 4355.9031 | 4500.0904 | 4603.7372 | 5092.2979 | 5171.8205 | 5171.8205 | 5171.8205 | 5171.8205 | 5171.8205 | 5171.8205 | 5171.8205 | 5171.8205 | 5171.8205 | 5171.8205 | 5171.8205 | 5171.8205 | 5171.8205 | 5171.8205 | 5171.8205 | 5171.8205 |  | 1942.1561 | 2808.5899 | 2898.3167 | 3207.9763 | 3200.4293 | 3268.5216 | 3534.8396 | 4299.9793 | 4615.7221 | 4316.847 | 5142.4584 | 4795.822 | 5107.7225 | 5332.4844 | 5240.1415 | 5240.1415 | 5240.1415 | 5240.1415 | 5240.1415 | 5240.1415 | 5240.1415 | 5240.1415 | 5240.1415 | 5240.1415 | 5240.1415 | 5240.1415 | 5240.1415 | 5240.1415 | 5240.1415 | 5240.1415
45% | 304.3799 | 1151.2957 | 1242.2705 | 1354.742 | 1504.0703 | 1645.6377 | 1893.0391 | 2515.2699 | 2849.9501 | 2605.791 | 3361.6736 | 3497.861 | 3595.7573 | 4057.2114 | 4132.3219 | 4132.3219 | 4132.3219 | 4132.3219 | 4132.3219 | 4132.3219 | 4132.3219 | 4132.3219 | 4132.3219 | 4132.3219 | 4132.3219 | 4132.3219 | 4132.3219 | 4132.3219 | 4132.3219 | 4132.3219 |  | 1081.8472 | 1900.2091 | 1984.9576 | 2277.4365 | 2270.3083 | 2334.6226 | 2586.1647 | 3308.8526 | 3607.0772 | 3324.7844 | 4104.5889 | 3777.1848 | 4071.7802 | 4284.0718 | 4196.8523 | 4196.8523 | 4196.8523 | 4196.8523 | 4196.8523 | 4196.8523 | 4196.8523 | 4196.8523 | 4196.8523 | 4196.8523 | 4196.8523 | 4196.8523 | 4196.8523 | 4196.8523 | 4196.8523 | 4196.8523
40% |  | 241.0368 | 303.4886 | 389.6318 | 518.5137 | 646.2971 | 869.6099 | 1431.2562 | 1733.3497 | 1512.9635 | 2195.2484 | 2318.1757 | 2406.5401 | 2823.064 | 2890.8613 | 2890.8613 | 2890.8613 | 2890.8613 | 2890.8613 | 2890.8613 | 2890.8613 | 2890.8613 | 2890.8613 | 2890.8613 | 2890.8613 | 2890.8613 | 2890.8613 | 2890.8613 | 2890.8613 | 2890.8613 |  | 197.8445 | 876.0818 | 952.5787 | 1216.5798 | 1210.1457 | 1268.1979 | 1495.2482 | 2147.5704 | 2416.7579 | 2161.951 | 2865.8286 | 2570.3026 | 2836.2143 | 3027.8357 | 2949.1086 | 2949.1086 | 2949.1086 | 2949.1086 | 2949.1086 | 2949.1086 | 2949.1086 | 2949.1086 | 2949.1086 | 2949.1086 | 2949.1086 | 2949.1086 | 2949.1086 | 2949.1086 | 2949.1086 | 2949.1086
35% |  |  |  |  | 0.16059 | 8.4247 | 51.6577 | 306.5672 | 520.3346 | 359.4876 | 878.7989 | 974.1987 | 1042.7754 | 1366.0258 | 1418.641 | 1418.641 | 1418.641 | 1418.641 | 1418.641 | 1418.641 | 1418.641 | 1418.641 | 1418.641 | 1418.641 | 1418.641 | 1418.641 | 1418.641 | 1418.641 | 1418.641 | 1418.641 |  |  | 53.4346 | 76.5978 | 185.9699 | 182.7815 | 212.4625 | 347.6947 | 841.7976 | 1050.7051 | 852.9579 | 1399.2139 | 1169.866 | 1376.2313 | 1524.9423 | 1463.8448 | 1463.8448 | 1463.8448 | 1463.8448 | 1463.8448 | 1463.8448 | 1463.8448 | 1463.8448 | 1463.8448 | 1463.8448 | 1463.8448 | 1463.8448 | 1463.8448 | 1463.8448 | 1463.8448 | 1463.8448
30% | [8 empty] | 0.13247 |  | 47.3865 | 73.4365 | 95.4345 | 233.8409 | 261.5037 | 261.5037 | 261.5037 | 261.5037 | 261.5037 | 261.5037 | 261.5037 | 261.5037 | 261.5037 | 261.5037 | 261.5037 | 261.5037 | 261.5037 | 261.5037 | 261.5037 | 261.5037 | [8 empty] | 38.745 | 98.151 | 41.2641 | 251.1294 | 143.1816 | 239.0986 | 321.5304 | 286.3608 | 286.3608 | 286.3608 | 286.3608 | 286.3608 | 286.3608 | 286.3608 | 286.3608 | 286.3608 | 286.3608 | 286.3608 | 286.3608 | 286.3608 | 286.3608 | 286.3608 | 286.3608
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 11808.8744 | 17327.6237 | 17950.4997 | 18729.4017 | 19778.0731 | 20785.8168 | 22575.4407 | 27221.1763 | 29796.0085 | 27912.7082 | 33810.7876 | 34892.5992 | 35673.4826 | 39388.7046 | 39998.5117 | 39998.5117 | 39998.5117 | 39998.5117 | 39998.5117 | 39998.5117 | 39998.5117 | 39998.5117 | 39998.5117 | 39998.5117 | 39998.5117 | 39998.5117 | 39998.5117 | 39998.5117 | 39998.5117 | 39998.5117 | E @ R (MWh) | 16856.5689 | 22627.8251 | 23249.1394 | 25422.5188 | 25369.0323 | 25852.5194 | 27762.4582 | 33392.6489 | 35763.9491 | 33518.6811 | 39773.1943 | 37127.5741 | 39506.8788 | 41234.634 | 40523.5006 | 40523.5006 | 40523.5006 | 40523.5006 | 40523.5006 | 40523.5006 | 40523.5006 | 40523.5006 | 40523.5006 | 40523.5006 | 40523.5006 | 40523.5006 | 40523.5006 | 40523.5006 | 40523.5006 | 40523.5006
Option 1 Winter POE50 W E @ R (MWh) N 2 | 8266.2121 | 12129.3366 | 12565.3498 | 13110.5812 | 13844.6511 | 14550.0718 | 15802.8085 | 19054.8234 | 20857.206 | 19538.8958 | 23667.5513 | 24424.8194 | 24971.4378 | 27572.0932 | 27998.9582 | 27998.9582 | 27998.9582 | 27998.9582 | 27998.9582 | 27998.9582 | 27998.9582 | 27998.9582 | 27998.9582 | 27998.9582 | 27998.9582 | 27998.9582 | 27998.9582 | 27998.9582 | 27998.9582 | 27998.9582 | Option 1 Winter POE10 W E @ R (MWh) N 2 | 5056.9707 | 6788.3475 | 6974.7418 | 7626.7556 | 7610.7097 | 7755.7558 | 8328.7375 | 10017.7947 | 10729.1847 | 10055.6043 | 11931.9583 | 11138.2722 | 11852.0637 | 12370.3902 | 12157.0502 | 12157.0502 | 12157.0502 | 12157.0502 | 12157.0502 | 12157.0502 | 12157.0502 | 12157.0502 | 12157.0502 | 12157.0502 | 12157.0502 | 12157.0502 | 12157.0502 | 12157.0502 | 12157.0502 | 12157.0502
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | 8.9039 | 10.0686 | 10.1857 | 10.1283 | 10.1828 | 10.2053 | 10.2771 | 10.4248 | 10.549 | 10.6062 | 10.5553 | 10.769 | 10.8029 | 10.7628 | 10.8432 | 10.8846 | 10.8846 | 10.8846 | 10.8846 | 10.8846 | 10.8846 | 10.8846 | 10.8846 | 10.8846 | 10.8846 | 10.8846 | 10.8846 | 10.8846 | 10.8846 | 10.8846 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
98% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
97% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 12.1062 | 13.3817 | 13.4169 | 13.3789 | 13.3887 | 13.4583 | 13.5995 | 13.8481 | 13.9776 | 14.0713 | 14.2131 | 14.3942 | 14.6131 | 14.7279 | 14.6907 | 14.7312 | 14.7312 | 14.7312 | 14.7312 | 14.7312 | 14.7312 | 14.7312 | 14.7312 | 14.7312 | 14.7312 | 14.7312 | 14.7312 | 14.7312 | 14.7312 | 14.7312
95% | 8.3559 | 9.4797 | 9.5926 | 9.5372 | 9.5899 | 9.6115 | 9.6808 | 9.8233 | 9.9432 | 9.9984 | 9.9492 | 10.1554 | 10.1881 | 10.1494 | 10.227 | 10.267 | 10.267 | 10.267 | 10.267 | 10.267 | 10.267 | 10.267 | 10.267 | 10.267 | 10.267 | 10.267 | 10.267 | 10.267 | 10.267 | 10.267 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
90% | 171.7748 | 195.5955 | 197.9892 | 196.8158 | 197.9315 | 198.3899 | 199.8591 | 202.88 | 205.4214 | 206.5912 | 205.5485 | 209.9202 | 210.6135 | 209.793 | 211.4383 | 212.2848 | 212.2848 | 212.2848 | 212.2848 | 212.2848 | 212.2848 | 212.2848 | 212.2848 | 212.2848 | 212.2848 | 212.2848 | 212.2848 | 212.2848 | 212.2848 | 212.2848 |  | 11.1431 | 12.3531 | 12.3865 | 12.3505 | 12.3598 | 12.4259 | 12.5598 | 12.7956 | 12.9185 | 13.0074 | 13.142 | 13.3137 | 13.5215 | 13.6303 | 13.595 | 13.6335 | 13.6335 | 13.6335 | 13.6335 | 13.6335 | 13.6335 | 13.6335 | 13.6335 | 13.6335 | 13.6335 | 13.6335 | 13.6335 | 13.6335 | 13.6335 | 13.6335
85% | 583.0836 | 668.0948 | 676.6375 | 672.4501 | 676.4317 | 678.0677 | 683.3108 | 694.0919 | 703.1615 | 707.3365 | 703.6153 | 719.2167 | 721.6911 | 718.7628 | 724.6348 | 727.6558 | 727.6558 | 727.6558 | 727.6558 | 727.6558 | 727.6558 | 727.6558 | 727.6558 | 727.6558 | 727.6558 | 727.6558 | 727.6558 | 727.6558 | 727.6558 | 727.6558 |  | 10.18 | 11.3246 | 11.3562 | 11.3221 | 11.3309 | 11.3934 | 11.5201 | 11.7432 | 11.8594 | 11.9435 | 12.0708 | 12.2333 | 12.4298 | 12.5328 | 12.4994 | 12.5358 | 12.5358 | 12.5358 | 12.5358 | 12.5358 | 12.5358 | 12.5358 | 12.5358 | 12.5358 | 12.5358 | 12.5358 | 12.5358 | 12.5358 | 12.5358 | 12.5358
80% | 892.6437 | 1030.7394 | 1044.6165 | 1037.8142 | 1044.2821 | 1046.9396 | 1055.4569 | 1072.9701 | 1087.703 | 1094.485 | 1088.4403 | 1113.7838 | 1117.8034 | 1113.0465 | 1122.5851 | 1127.4926 | 1127.4926 | 1127.4926 | 1127.4926 | 1127.4926 | 1127.4926 | 1127.4926 | 1127.4926 | 1127.4926 | 1127.4926 | 1127.4926 | 1127.4926 | 1127.4926 | 1127.4926 | 1127.4926 |  | 36.8674 | 41.1843 | 41.3034 | 41.175 | 41.208 | 41.4438 | 41.9215 | 42.7629 | 43.2013 | 43.5185 | 43.9985 | 44.6113 | 45.3524 | 45.7408 | 45.6149 | 45.7521 | 45.7521 | 45.7521 | 45.7521 | 45.7521 | 45.7521 | 45.7521 | 45.7521 | 45.7521 | 45.7521 | 45.7521 | 45.7521 | 45.7521 | 45.7521 | 45.7521
75% | 1479.5037 | 1725.3485 | 1750.0533 | 1737.9436 | 1749.458 | 1754.1891 | 1769.3519 | 1800.5298 | 1826.7581 | 1838.8318 | 1828.0706 | 1873.1885 | 1880.3443 | 1871.8759 | 1888.857 | 1897.5936 | 1897.5936 | 1897.5936 | 1897.5936 | 1897.5936 | 1897.5936 | 1897.5936 | 1897.5936 | 1897.5936 | 1897.5936 | 1897.5936 | 1897.5936 | 1897.5936 | 1897.5936 | 1897.5936 |  | 16.5074 | 18.5351 | 18.5911 | 18.5307 | 18.5462 | 18.657 | 18.8814 | 19.2766 | 19.4825 | 19.6315 | 19.8569 | 20.1448 | 20.4928 | 20.6753 | 20.6161 | 20.6806 | 20.6806 | 20.6806 | 20.6806 | 20.6806 | 20.6806 | 20.6806 | 20.6806 | 20.6806 | 20.6806 | 20.6806 | 20.6806 | 20.6806 | 20.6806 | 20.6806
70% | 1730.3357 | 2044.3359 | 2075.8895 | 2060.4227 | 2075.1292 | 2081.1719 | 2100.5382 | 2140.3596 | 2173.8591 | 2189.28 | 2175.5354 | 2233.1613 | 2242.3009 | 2231.4848 | 2253.1735 | 2264.3322 | 2264.3322 | 2264.3322 | 2264.3322 | 2264.3322 | 2264.3322 | 2264.3322 | 2264.3322 | 2264.3322 | 2264.3322 | 2264.3322 | 2264.3322 | 2264.3322 | 2264.3322 | 2264.3322 |  | 43.7436 | 49.4342 | 49.5912 | 49.4219 | 49.4654 | 49.7762 | 50.4059 | 51.515 | 52.0929 | 52.511 | 53.1438 | 53.9516 | 54.9285 | 55.4404 | 55.2744 | 55.4554 | 55.4554 | 55.4554 | 55.4554 | 55.4554 | 55.4554 | 55.4554 | 55.4554 | 55.4554 | 55.4554 | 55.4554 | 55.4554 | 55.4554 | 55.4554 | 55.4554
65% | 1900.1465 | 2285.7258 | 2324.4723 | 2305.4797 | 2323.5388 | 2330.9589 | 2354.74 | 2403.639 | 2444.775 | 2463.7113 | 2446.8335 | 2517.5958 | 2528.8188 | 2515.5371 | 2542.1699 | 2555.8723 | 2555.8723 | 2555.8723 | 2555.8723 | 2555.8723 | 2555.8723 | 2555.8723 | 2555.8723 | 2555.8723 | 2555.8723 | 2555.8723 | 2555.8723 | 2555.8723 | 2555.8723 | 2555.8723 |  | 12.655 | 14.421 | 14.4697 | 14.4172 | 14.4307 | 14.5271 | 14.7226 | 15.0668 | 15.2461 | 15.3759 | 15.5723 | 15.823 | 16.1261 | 16.285 | 16.2335 | 16.2897 | 16.2897 | 16.2897 | 16.2897 | 16.2897 | 16.2897 | 16.2897 | 16.2897 | 16.2897 | 16.2897 | 16.2897 | 16.2897 | 16.2897 | 16.2897 | 16.2897
60% | 2395.395 | 2958.7224 | 3015.3307 | 2987.5827 | 3013.9668 | 3024.8076 | 3059.5514 | 3130.9924 | 3191.0917 | 3218.7573 | 3194.0991 | 3297.482 | 3313.8788 | 3294.4743 | 3333.3846 | 3353.4037 | 3353.4037 | 3353.4037 | 3353.4037 | 3353.4037 | 3353.4037 | 3353.4037 | 3353.4037 | 3353.4037 | 3353.4037 | 3353.4037 | 3353.4037 | 3353.4037 | 3353.4037 | 3353.4037 |  | 69.7368 | 80.3657 | 80.659 | 80.3428 | 80.4241 | 81.0045 | 82.1808 | 84.2523 | 85.3317 | 86.1126 | 87.2945 | 88.8034 | 90.628 | 91.5842 | 91.2742 | 91.6122 | 91.6122 | 91.6122 | 91.6122 | 91.6122 | 91.6122 | 91.6122 | 91.6122 | 91.6122 | 91.6122 | 91.6122 | 91.6122 | 91.6122 | 91.6122 | 91.6122
55% | 2397.9043 | 3091.1628 | 3160.8278 | 3126.6797 | 3159.1493 | 3172.4904 | 3215.248 | 3303.1668 | 3377.1279 | 3411.1746 | 3380.829 | 3508.0571 | 3528.2358 | 3504.3556 | 3552.2406 | 3576.8771 | 3576.8771 | 3576.8771 | 3576.8771 | 3576.8771 | 3576.8771 | 3576.8771 | 3576.8771 | 3576.8771 | 3576.8771 | 3576.8771 | 3576.8771 | 3576.8771 | 3576.8771 | 3576.8771 |  | 281.6802 | 329.8208 | 331.1492 | 329.717 | 330.0853 | 332.7141 | 338.0417 | 347.4243 | 352.3132 | 355.8501 | 361.2031 | 368.0372 | 376.3012 | 380.6321 | 379.2281 | 380.7589 | 380.7589 | 380.7589 | 380.7589 | 380.7589 | 380.7589 | 380.7589 | 380.7589 | 380.7589 | 380.7589 | 380.7589 | 380.7589 | 380.7589 | 380.7589 | 380.7589
50% | 1977.8845 | 2764.4944 | 2843.5402 | 2804.7939 | 2841.6356 | 2856.7733 | 2905.2884 | 3005.046 | 3088.9664 | 3127.5977 | 3093.1659 | 3237.526 | 3260.4218 | 3233.3261 | 3287.6591 | 3315.613 | 3315.613 | 3315.613 | 3315.613 | 3315.613 | 3315.613 | 3315.613 | 3315.613 | 3315.613 | 3315.613 | 3315.613 | 3315.613 | 3315.613 | 3315.613 | 3315.613 |  | 543.2253 | 651.7379 | 654.7323 | 651.5039 | 652.3342 | 658.2598 | 670.2686 | 691.4175 | 702.4375 | 710.41 | 722.476 | 737.8807 | 756.5083 | 766.2706 | 763.1058 | 766.5564 | 766.5564 | 766.5564 | 766.5564 | 766.5564 | 766.5564 | 766.5564 | 766.5564 | 766.5564 | 766.5564 | 766.5564 | 766.5564 | 766.5564 | 766.5564 | 766.5564
45% | 892.7494 | 1543.8389 | 1609.2663 | 1577.1954 | 1607.6899 | 1620.2195 | 1660.3762 | 1742.9472 | 1812.4095 | 1844.3852 | 1815.8854 | 1935.3746 | 1954.3258 | 1931.8982 | 1976.8705 | 2000.0084 | 2000.0084 | 2000.0084 | 2000.0084 | 2000.0084 | 2000.0084 | 2000.0084 | 2000.0084 | 2000.0084 | 2000.0084 | 2000.0084 | 2000.0084 | 2000.0084 | 2000.0084 | 2000.0084 |  | 742.5052 | 928.9193 | 934.0633 | 928.5173 | 929.9435 | 940.1232 | 960.7531 | 997.085 | 1016.0161 | 1029.7122 | 1050.4404 | 1076.9041 | 1108.9046 | 1125.6752 | 1120.2384 | 1126.1661 | 1126.1661 | 1126.1661 | 1126.1661 | 1126.1661 | 1126.1661 | 1126.1661 | 1126.1661 | 1126.1661 | 1126.1661 | 1126.1661 | 1126.1661 | 1126.1661 | 1126.1661 | 1126.1661
40% | 82.6197 | 448.4043 | 495.3965 | 472.3621 | 494.2643 | 503.2635 | 532.1055 | 591.4108 | 641.301 | 664.267 | 643.7975 | 729.6188 | 743.2302 | 727.122 | 759.4226 | 776.041 | 776.041 | 776.041 | 776.041 | 776.041 | 776.041 | 776.041 | 776.041 | 776.041 | 776.041 | 776.041 | 776.041 | 776.041 | 776.041 | 776.041 |  | 686.4025 | 938.8137 | 945.7788 | 938.2693 | 940.2006 | 953.9841 | 981.9179 | 1031.1125 | 1056.7459 | 1075.2908 | 1103.3575 | 1139.1903 | 1182.5201 | 1205.2281 | 1197.8665 | 1205.8928 | 1205.8928 | 1205.8928 | 1205.8928 | 1205.8928 | 1205.8928 | 1205.8928 | 1205.8928 | 1205.8928 | 1205.8928 | 1205.8928 | 1205.8928 | 1205.8928 | 1205.8928 | 1205.8928
35% |  | 1.6148 | 5.4003 | 3.2709 | 5.2834 | 6.2472 | 9.8686 | 19.8299 | 30.7782 | 36.5919 | 31.3867 | 55.7517 | 60.2225 | 54.9494 | 65.7537 | 71.6692 | 71.6692 | 71.6692 | 71.6692 | 71.6692 | 71.6692 | 71.6692 | 71.6692 | 71.6692 | 71.6692 | 71.6692 | 71.6692 | 71.6692 | 71.6692 | 71.6692 |  | 458.782 | 868.8929 | 880.2097 | 868.0084 | 871.1463 | 893.5414 | 938.9274 | 1018.8574 | 1060.506 | 1090.6372 | 1136.2393 | 1194.4595 | 1264.8606 | 1301.7559 | 1289.7949 | 1302.8359 | 1302.8359 | 1302.8359 | 1302.8359 | 1302.8359 | 1302.8359 | 1302.8359 | 1302.8359 | 1302.8359 | 1302.8359 | 1302.8359 | 1302.8359 | 1302.8359 | 1302.8359 | 1302.8359
30% | [31 empty] | 3.5003 | 199.9764 | 209.3483 | 199.2523 | 201.8267 | 220.6429 | 261.1304 | 339.9291 | 384.6819 | 418.6009 | 472.3546 | 545.1319 | 639.1947 | 691.0757 | 674.0645 | 692.6208 | 692.6208 | 692.6208 | 692.6208 | 692.6208 | 692.6208 | 692.6208 | 692.6208 | 692.6208 | 692.6208 | 692.6208 | 692.6208 | 692.6208 | 692.6208 | 692.6208
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 14376.0875 | 18589.8496 | 19027.0063 | 18812.4517 | 19016.448 | 19100.402 | 19369.9964 | 19926.8305 | 20397.8067 | 20615.378 | 20421.4347 | 21237.0849 | 21367.0492 | 21213.2626 | 21521.8675 | 21680.9955 | 21680.9955 | 21680.9955 | 21680.9955 | 21680.9955 | 21680.9955 | 21680.9955 | 21680.9955 | 21680.9955 | 21680.9955 | 21680.9955 | 21680.9955 | 21680.9955 | 21680.9955 | 21680.9955 | E @ R (MWh) | 2899.7446 | 4117.569 | 4155.085 | 4114.6453 | 4125.0234 | 4199.5321 | 4352.8623 | 4630.3154 | 4778.5425 | 4887.3062 | 5054.3091 | 5271.6303 | 5540.4179 | 5683.8418 | 5637.1556 | 5688.0662 | 5688.0662 | 5688.0662 | 5688.0662 | 5688.0662 | 5688.0662 | 5688.0662 | 5688.0662 | 5688.0662 | 5688.0662 | 5688.0662 | 5688.0662 | 5688.0662 | 5688.0662 | 5688.0662
Option 1 Summer POE50 W E @ R (MWh) N 2 | 10063.2613 | 13012.8947 | 13318.9044 | 13168.7162 | 13311.5136 | 13370.2814 | 13558.9975 | 13948.7813 | 14278.4647 | 14430.7646 | 14295.0043 | 14865.9595 | 14956.9344 | 14849.2838 | 15065.3072 | 15176.6968 | 15176.6968 | 15176.6968 | 15176.6968 | 15176.6968 | 15176.6968 | 15176.6968 | 15176.6968 | 15176.6968 | 15176.6968 | 15176.6968 | 15176.6968 | 15176.6968 | 15176.6968 | 15176.6968 | Option 1 Summer POE10 W E @ R (MWh) N 2 | 869.9234 | 1235.2707 | 1246.5255 | 1234.3936 | 1237.507 | 1259.8596 | 1305.8587 | 1389.0946 | 1433.5627 | 1466.1918 | 1516.2927 | 1581.4891 | 1662.1254 | 1705.1525 | 1691.1467 | 1706.4199 | 1706.4199 | 1706.4199 | 1706.4199 | 1706.4199 | 1706.4199 | 1706.4199 | 1706.4199 | 1706.4199 | 1706.4199 | 1706.4199 | 1706.4199 | 1706.4199 | 1706.4199 | 1706.4199
Option 2 - Replace 3 x 10/13.5 MVA Tx with 3 x 20/33 MVA Tx
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | FY25: 6.2898; FY26: 7.5099; FY27: 7.6393 |  | 7.4111 | 8.5749 | 8.6954
98% | FY25: 0; FY26: 0; FY27: 0 |  | 0 | 0 | 0
97% | FY25: 0; FY26: 0; FY27: 0 |  | 0 | 0 | 0
95% | FY25: 23.5194; FY26: 28.2281; FY27: 28.7274 |  | 27.8469 | 32.3383 | 32.8034
90% | FY25: 131.2778; FY26: 158.4998; FY27: 161.3863 |  | 156.2962 | 182.262 | 184.951
85% | FY25: 517.7326; FY26: 631.4638; FY27: 643.5236 |  | 622.2576 | 730.7409 | 741.9753
80% | FY25: 765.156; FY26: 945.2254; FY27: 964.3195 |  | 930.6493 | 1102.4097 | 1120.197
75% | FY25: 1299.5462; FY26: 1632.1565; FY27: 1667.4256 |  | 1605.2327 | 1922.4952 | 1955.3505
70% | FY25: 1904.5555; FY26: 2445.9592; FY27: 2503.3682 |  | 2402.1342 | 2918.5558 | 2972.0357
65% | FY25: 2035.9088; FY26: 2698.8915; FY27: 2769.1924 |  | 2645.225 | 3277.6155 | 3343.1051
60% | FY25: 2098.8616; FY26: 2921.1907; FY27: 3008.3883 |  | 2854.6256 | 3639.0098 | 3720.2396
55% | FY25: 1733.592; FY26: 2625.5087; FY27: 2720.0851 |  | 2553.3107 | 3404.0714 | 3492.1751
50% | FY25: 1107.3363; FY26: 2015.6842; FY27: 2112.003 |  | 1942.1561 | 2808.5899 | 2898.3167
45% | FY25: 304.3799; FY26: 1151.2957; FY27: 1242.2705 |  | 1081.8472 | 1900.2091 | 1984.9576
40% | FY26: 241.0368; FY27: 303.4886 |  | 197.8445 | 876.0818 | 952.5787
35% | [32 empty] | 53.4346 | 76.5978
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 11808.8744 | 17327.6237 | 17950.4997 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 16856.5689 | 22627.8251 | 23249.1394 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2 Winter POE50 W E @ R (MWh) N 2 | 8266.2121 | 12129.3366 | 12565.3498 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 2 Winter POE10 W E @ R (MWh) N 2 | 5056.9707 | 6788.3475 | 6974.7418 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | FY25: 8.9039; FY26: 10.0686; FY27: 10.1857 |  | 0 | 0 | 0
98% | FY25: 0; FY26: 0; FY27: 0 |  | 0 | 0 | 0
97% | FY25: 0; FY26: 0; FY27: 0 |  | 12.1062 | 13.3817 | 13.4169
95% | FY25: 8.3559; FY26: 9.4797; FY27: 9.5926 |  | 0 | 0 | 0
90% | FY25: 171.7748; FY26: 195.5955; FY27: 197.9892 |  | 11.1431 | 12.3531 | 12.3865
85% | FY25: 583.0836; FY26: 668.0948; FY27: 676.6375 |  | 10.18 | 11.3246 | 11.3562
80% | FY25: 892.6437; FY26: 1030.7394; FY27: 1044.6165 |  | 36.8674 | 41.1843 | 41.3034
75% | FY25: 1479.5037; FY26: 1725.3485; FY27: 1750.0533 |  | 16.5074 | 18.5351 | 18.5911
70% | FY25: 1730.3357; FY26: 2044.3359; FY27: 2075.8895 |  | 43.7436 | 49.4342 | 49.5912
65% | FY25: 1900.1465; FY26: 2285.7258; FY27: 2324.4723 |  | 12.655 | 14.421 | 14.4697
60% | FY25: 2395.395; FY26: 2958.7224; FY27: 3015.3307 |  | 69.7368 | 80.3657 | 80.659
55% | FY25: 2397.9043; FY26: 3091.1628; FY27: 3160.8278 |  | 281.6802 | 329.8208 | 331.1492
50% | FY25: 1977.8845; FY26: 2764.4944; FY27: 2843.5402 |  | 543.2253 | 651.7379 | 654.7323
45% | FY25: 892.7494; FY26: 1543.8389; FY27: 1609.2663 |  | 742.5052 | 928.9193 | 934.0633
40% | FY25: 82.6197; FY26: 448.4043; FY27: 495.3965 |  | 686.4025 | 938.8137 | 945.7788
35% | FY26: 1.6148; FY27: 5.4003 |  | 458.782 | 868.8929 | 880.2097
30% | [31 empty] | 3.5003 | 199.9764 | 209.3483
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 14376.0875 | 18589.8496 | 19027.0063 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 2899.7446 | 4117.569 | 4155.085 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2 Summer POE50 W E @ R (MWh) N 2 | 10063.2613 | 13012.8947 | 13318.9044 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 2 Summer POE10 W E @ R (MWh) N 2 | 869.9234 | 1235.2707 | 1246.5255 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 - Replace 1 x 10/13.5 MVA Tx with 1 x 20/33 MVA Tx
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | 6.2898 | 7.5099 | 7.6393 | 3.2372 | 3.4496 | 3.6509 | 4.0027 | 4.8876 | 5.3635 | 5.0163 | 6.0912 | 6.2849 | 6.4241 | 7.0804 | 7.1872 | 7.1872 | 7.1872 | 7.1872 | 7.1872 | 7.1872 | 7.1872 | 7.1872 | 7.1872 | 7.1872 | 7.1872 | 7.1872 | 7.1872 | 7.1872 | 7.1872 | 7.1872 |  | 7.4111 | 8.5749 | 8.6954 | 4.5494 | 4.5392 | 4.6307 | 4.9884 | 6.0161 | 6.4402 | 6.0388 | 7.1477 | 6.6821 | 7.1011 | 7.403 | 7.2789 | 7.2789 | 7.2789 | 7.2789 | 7.2789 | 7.2789 | 7.2789 | 7.2789 | 7.2789 | 7.2789 | 7.2789 | 7.2789 | 7.2789 | 7.2789 | 7.2789 | 7.2789
98% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
97% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
95% | 23.5194 | 28.2281 | 28.7274 | 11.0967 | 11.9162 | 12.6932 | 14.051 | 17.4659 | 19.3028 | 17.9628 | 22.1112 | 22.8587 | 23.3959 | 25.9285 | 26.3408 | 26.3408 | 26.3408 | 26.3408 | 26.3408 | 26.3408 | 26.3408 | 26.3408 | 26.3408 | 26.3408 | 26.3408 | 26.3408 | 26.3408 | 26.3408 | 26.3408 | 26.3408 |  | 27.8469 | 32.3383 | 32.8034 | 16.1607 | 16.1215 | 16.4745 | 17.855 | 21.8213 | 23.4581 | 21.9088 | 26.1885 | 24.3917 | 26.0085 | 27.1736 | 26.6949 | 26.6949 | 26.6949 | 26.6949 | 26.6949 | 26.6949 | 26.6949 | 26.6949 | 26.6949 | 26.6949 | 26.6949 | 26.6949 | 26.6949 | 26.6949 | 26.6949 | 26.6949
90% | 131.2778 | 158.4998 | 161.3863 | 55.467 | 60.205 | 64.6968 | 72.5466 | 92.2894 | 102.9085 | 95.1615 | 119.1449 | 123.466 | 126.5722 | 141.2137 | 143.5969 | 143.5969 | 143.5969 | 143.5969 | 143.5969 | 143.5969 | 143.5969 | 143.5969 | 143.5969 | 143.5969 | 143.5969 | 143.5969 | 143.5969 | 143.5969 | 143.5969 | 143.5969 |  | 156.2962 | 182.262 | 184.951 | 84.7432 | 84.517 | 86.5576 | 94.5388 | 117.469 | 126.9314 | 117.9745 | 142.7169 | 132.3287 | 141.6759 | 148.4117 | 145.6443 | 145.6443 | 145.6443 | 145.6443 | 145.6443 | 145.6443 | 145.6443 | 145.6443 | 145.6443 | 145.6443 | 145.6443 | 145.6443 | 145.6443 | 145.6443 | 145.6443 | 145.6443
85% | 517.7326 | 631.4638 | 643.5236 | 174.8612 | 194.6564 | 213.4228 | 246.2187 | 328.7026 | 373.0683 | 340.7022 | 440.9032 | 458.9564 | 471.9337 | 533.1048 | 543.0615 | 543.0615 | 543.0615 | 543.0615 | 543.0615 | 543.0615 | 543.0615 | 543.0615 | 543.0615 | 543.0615 | 543.0615 | 543.0615 | 543.0615 | 543.0615 | 543.0615 | 543.0615 |  | 622.2576 | 730.7409 | 741.9753 | 297.1751 | 296.2301 | 304.7557 | 338.1005 | 433.9012 | 473.4343 | 436.0131 | 539.3852 | 495.984 | 535.036 | 563.1777 | 551.6158 | 551.6158 | 551.6158 | 551.6158 | 551.6158 | 551.6158 | 551.6158 | 551.6158 | 551.6158 | 551.6158 | 551.6158 | 551.6158 | 551.6158 | 551.6158 | 551.6158 | 551.6158
80% | 765.156 | 945.2254 | 964.3195 | 175.8898 | 207.2313 | 236.9439 | 288.8693 | 419.465 | 489.7088 | 438.4639 | 597.1109 | 625.6944 | 646.2411 | 743.0926 | 758.857 | 758.857 | 758.857 | 758.857 | 758.857 | 758.857 | 758.857 | 758.857 | 758.857 | 758.857 | 758.857 | 758.857 | 758.857 | 758.857 | 758.857 | 758.857 |  | 930.6493 | 1102.4097 | 1120.197 | 369.5478 | 368.0517 | 381.5502 | 434.3447 | 586.0247 | 648.617 | 589.3685 | 753.0363 | 684.3197 | 746.1503 | 790.7068 | 772.4009 | 772.4009 | 772.4009 | 772.4009 | 772.4009 | 772.4009 | 772.4009 | 772.4009 | 772.4009 | 772.4009 | 772.4009 | 772.4009 | 772.4009 | 772.4009 | 772.4009 | 772.4009
75% | 1299.5462 | 1632.1565 | 1667.4256 | 114.3338 | 172.221 | 227.1038 | 323.0164 | 564.2428 | 693.9917 | 599.336 | 892.3766 | 945.1738 | 983.1262 | 1162.0227 | 1191.1416 | 1191.1416 | 1191.1416 | 1191.1416 | 1191.1416 | 1191.1416 | 1191.1416 | 1191.1416 | 1191.1416 | 1191.1416 | 1191.1416 | 1191.1416 | 1191.1416 | 1191.1416 | 1191.1416 | 1191.1416 |  | 1605.2327 | 1922.4952 | 1955.3505 | 472.0396 | 469.2761 | 494.2095 | 591.7273 | 871.899 | 987.5147 | 878.0754 | 1180.39 | 1053.462 | 1167.6707 | 1249.9719 | 1216.1587 | 1216.1587 | 1216.1587 | 1216.1587 | 1216.1587 | 1216.1587 | 1216.1587 | 1216.1587 | 1216.1587 | 1216.1587 | 1216.1587 | 1216.1587 | 1216.1587 | 1216.1587 | 1216.1587 | 1216.1587
70% | 1904.5555 | 2445.9592 | 2503.3682 |  | 11.0217 | 42.2634 | 142.7947 | 528.429 | 739.6266 | 585.5517 | 1062.5462 | 1148.4863 | 1210.263 | 1501.4604 | 1548.8584 | 1548.8584 | 1548.8584 | 1548.8584 | 1548.8584 | 1548.8584 | 1548.8584 | 1548.8584 | 1548.8584 | 1548.8584 | 1548.8584 | 1548.8584 | 1548.8584 | 1548.8584 | 1548.8584 | 1548.8584 |  | 2402.1342 | 2918.5558 | 2972.0357 | 378.346 | 373.8478 | 414.4329 | 573.1667 | 1029.2139 | 1217.4064 | 1039.2675 | 1531.3577 | 1324.7516 | 1510.654 | 1644.6191 | 1589.5798 | 1589.5798 | 1589.5798 | 1589.5798 | 1589.5798 | 1589.5798 | 1589.5798 | 1589.5798 | 1589.5798 | 1589.5798 | 1589.5798 | 1589.5798 | 1589.5798 | 1589.5798 | 1589.5798 | 1589.5798
65% | 2035.9088 | 2698.8915 | 2769.1924 |  |  |  |  | 132.0838 | 357.3694 | 183.1878 | 752.8045 | 858.0436 | 933.6931 | 1290.2825 | 1348.3243 | 1348.3243 | 1348.3243 | 1348.3243 | 1348.3243 | 1348.3243 | 1348.3243 | 1348.3243 | 1348.3243 | 1348.3243 | 1348.3243 | 1348.3243 | 1348.3243 | 1348.3243 | 1348.3243 | 1348.3243 |  | 2645.225 | 3277.6155 | 3343.1051 | 36.5189 | 34.5486 | 54.2414 | 171.4384 | 711.987 | 942.4406 | 724.2984 | 1326.8936 | 1073.8915 | 1301.5406 | 1465.5892 | 1398.1903 | 1398.1903 | 1398.1903 | 1398.1903 | 1398.1903 | 1398.1903 | 1398.1903 | 1398.1903 | 1398.1903 | 1398.1903 | 1398.1903 | 1398.1903 | 1398.1903 | 1398.1903 | 1398.1903 | 1398.1903
60% | 2098.8616 | 2921.1907 | 3008.3883 | [5 empty] | 2.6827 |  | 192.478 | 290.2704 | 372.0499 | 811.4315 | 883.4235 | 883.4235 | 883.4235 | 883.4235 | 883.4235 | 883.4235 | 883.4235 | 883.4235 | 883.4235 | 883.4235 | 883.4235 | 883.4235 | 883.4235 | 883.4235 | 883.4235 | 883.4235 |  | 2854.6256 | 3639.0098 | 3720.2396 |  |  |  |  | 159.6793 | 382.1125 | 169.2654 | 856.842 | 543.0314 | 825.3954 | 1028.8728 | 945.2746 | 945.2746 | 945.2746 | 945.2746 | 945.2746 | 945.2746 | 945.2746 | 945.2746 | 945.2746 | 945.2746 | 945.2746 | 945.2746 | 945.2746 | 945.2746 | 945.2746 | 945.2746
55% | 1733.592 | 2625.5087 | 2720.0851 | [10 empty] | 80.0707 | 113.7859 | 113.7859 | 113.7859 | 113.7859 | 113.7859 | 113.7859 | 113.7859 | 113.7859 | 113.7859 | 113.7859 | 113.7859 | 113.7859 | 113.7859 | 113.7859 | 113.7859 | 113.7859 |  | 2553.3107 | 3404.0714 | 3492.1751 | [7 empty] | 100.6741 | 5.9741 | 86.1638 | 199.0221 | 147.2653 | 147.2653 | 147.2653 | 147.2653 | 147.2653 | 147.2653 | 147.2653 | 147.2653 | 147.2653 | 147.2653 | 147.2653 | 147.2653 | 147.2653 | 147.2653 | 147.2653 | 147.2653
50% | FY25: 1107.3363; FY26: 2015.6842; FY27: 2112.003 |  | 1942.1561 | 2808.5899 | 2898.3167
45% | FY25: 304.3799; FY26: 1151.2957; FY27: 1242.2705 |  | 1081.8472 | 1900.2091 | 1984.9576
40% | FY26: 241.0368; FY27: 303.4886 |  | 197.8445 | 876.0818 | 952.5787
35% | [32 empty] | 53.4346 | 76.5978
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 11808.8744 | 17327.6237 | 17950.4997 | 529.5368 | 654.0942 | 792.767 | 1080.5844 | 2066.6905 | 2756.1821 | 2242.7285 | 4044.7112 | 4434.4421 | 4725.9623 | 6232.7308 | 6498.9313 | 6498.9313 | 6498.9313 | 6498.9313 | 6498.9313 | 6498.9313 | 6498.9313 | 6498.9313 | 6498.9313 | 6498.9313 | 6498.9313 | 6498.9313 | 6498.9313 | 6498.9313 | 6498.9313 | 6498.9313 | E @ R (MWh) | 16856.5689 | 22627.8251 | 23249.1394 | 1642.4897 | 1630.6608 | 1739.284 | 2203.8983 | 3898.6314 | 4760.2717 | 3942.3883 | 6399.9857 | 5291.3685 | 6283.9224 | 7053.6984 | 6732.1026 | 6732.1026 | 6732.1026 | 6732.1026 | 6732.1026 | 6732.1026 | 6732.1026 | 6732.1026 | 6732.1026 | 6732.1026 | 6732.1026 | 6732.1026 | 6732.1026 | 6732.1026 | 6732.1026 | 6732.1026
Option 3 Winter POE50 W E @ R (MWh) N 2 | 8266.2121 | 12129.3366 | 12565.3498 | 370.6758 | 457.866 | 554.9369 | 756.4091 | 1446.6834 | 1929.3275 | 1569.9099 | 2831.2978 | 3104.1095 | 3308.1736 | 4362.9116 | 4549.2519 | 4549.2519 | 4549.2519 | 4549.2519 | 4549.2519 | 4549.2519 | 4549.2519 | 4549.2519 | 4549.2519 | 4549.2519 | 4549.2519 | 4549.2519 | 4549.2519 | 4549.2519 | 4549.2519 | 4549.2519 | Option 3 Winter POE10 W E @ R (MWh) N 2 | 5056.9707 | 6788.3475 | 6974.7418 | 492.7469 | 489.1982 | 521.7852 | 661.1695 | 1169.5894 | 1428.0815 | 1182.7165 | 1919.9957 | 1587.4106 | 1885.1767 | 2116.1095 | 2019.6308 | 2019.6308 | 2019.6308 | 2019.6308 | 2019.6308 | 2019.6308 | 2019.6308 | 2019.6308 | 2019.6308 | 2019.6308 | 2019.6308 | 2019.6308 | 2019.6308 | 2019.6308 | 2019.6308 | 2019.6308
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | 8.9039 | 10.0686 | 10.1857 | 4.3235 | 4.378 | 4.4004 | 4.4723 | 4.62 | 4.7442 | 4.8014 | 4.7504 | 4.9642 | 4.9981 | 4.958 | 5.0384 | 5.0798 | 5.0798 | 5.0798 | 5.0798 | 5.0798 | 5.0798 | 5.0798 | 5.0798 | 5.0798 | 5.0798 | 5.0798 | 5.0798 | 5.0798 | 5.0798 | 5.0798 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
98% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
97% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 12.1062 | 13.3817 | 13.4169 | 7.5741 | 7.5838 | 7.6535 | 7.7946 | 8.0432 | 8.1728 | 8.2665 | 8.4083 | 8.5894 | 8.8083 | 8.9231 | 8.8859 | 8.9264 | 8.9264 | 8.9264 | 8.9264 | 8.9264 | 8.9264 | 8.9264 | 8.9264 | 8.9264 | 8.9264 | 8.9264 | 8.9264 | 8.9264 | 8.9264 | 8.9264
95% | 8.3559 | 9.4797 | 9.5926 | 3.7324 | 3.785 | 3.8067 | 3.876 | 4.0185 | 4.1384 | 4.1936 | 4.1444 | 4.3506 | 4.3833 | 4.3446 | 4.4222 | 4.4622 | 4.4622 | 4.4622 | 4.4622 | 4.4622 | 4.4622 | 4.4622 | 4.4622 | 4.4622 | 4.4622 | 4.4622 | 4.4622 | 4.4622 | 4.4622 | 4.4622 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
90% | 171.7748 | 195.5955 | 197.9892 | 69.1098 | 70.2254 | 70.6838 | 72.153 | 75.1739 | 77.7153 | 78.8851 | 77.8425 | 82.2141 | 82.9074 | 82.0869 | 83.7322 | 84.5788 | 84.5788 | 84.5788 | 84.5788 | 84.5788 | 84.5788 | 84.5788 | 84.5788 | 84.5788 | 84.5788 | 84.5788 | 84.5788 | 84.5788 | 84.5788 | 84.5788 |  | 11.1431 | 12.3531 | 12.3865 | 6.5457 | 6.555 | 6.621 | 6.755 | 6.9908 | 7.1137 | 7.2026 | 7.3371 | 7.5089 | 7.7166 | 7.8255 | 7.7902 | 7.8287 | 7.8287 | 7.8287 | 7.8287 | 7.8287 | 7.8287 | 7.8287 | 7.8287 | 7.8287 | 7.8287 | 7.8287 | 7.8287 | 7.8287 | 7.8287 | 7.8287
85% | 583.0836 | 668.0948 | 676.6375 | 190.6499 | 194.6315 | 196.2675 | 201.5106 | 212.2917 | 221.3613 | 225.5362 | 221.8151 | 237.4165 | 239.8909 | 236.9626 | 242.8345 | 245.8556 | 245.8556 | 245.8556 | 245.8556 | 245.8556 | 245.8556 | 245.8556 | 245.8556 | 245.8556 | 245.8556 | 245.8556 | 245.8556 | 245.8556 | 245.8556 | 245.8556 |  | 10.18 | 11.3246 | 11.3562 | 5.5173 | 5.5261 | 5.5886 | 5.7153 | 5.9383 | 6.0546 | 6.1387 | 6.266 | 6.4285 | 6.625 | 6.7279 | 6.6946 | 6.7309 | 6.7309 | 6.7309 | 6.7309 | 6.7309 | 6.7309 | 6.7309 | 6.7309 | 6.7309 | 6.7309 | 6.7309 | 6.7309 | 6.7309 | 6.7309 | 6.7309
80% | 892.6437 | 1030.7394 | 1044.6165 | 207.7247 | 214.1926 | 216.8501 | 225.3673 | 242.8806 | 257.6135 | 264.3955 | 258.3508 | 283.6943 | 287.7139 | 282.957 | 292.4956 | 297.4031 | 297.4031 | 297.4031 | 297.4031 | 297.4031 | 297.4031 | 297.4031 | 297.4031 | 297.4031 | 297.4031 | 297.4031 | 297.4031 | 297.4031 | 297.4031 | 297.4031 |  | 36.8674 | 41.1843 | 41.3034 | 17.9557 | 17.9888 | 18.2245 | 18.7022 | 19.5436 | 19.982 | 20.2992 | 20.7792 | 21.392 | 22.1331 | 22.5215 | 22.3956 | 22.5329 | 22.5329 | 22.5329 | 22.5329 | 22.5329 | 22.5329 | 22.5329 | 22.5329 | 22.5329 | 22.5329 | 22.5329 | 22.5329 | 22.5329 | 22.5329 | 22.5329
75% | 1479.5037 | 1725.3485 | 1750.0533 | 164.8369 | 176.3513 | 181.0824 | 196.2452 | 227.4231 | 253.6514 | 265.7251 | 254.9639 | 300.0818 | 307.2376 | 298.7692 | 315.7503 | 324.4869 | 324.4869 | 324.4869 | 324.4869 | 324.4869 | 324.4869 | 324.4869 | 324.4869 | 324.4869 | 324.4869 | 324.4869 | 324.4869 | 324.4869 | 324.4869 | 324.4869 |  | 16.5074 | 18.5351 | 18.5911 | 6.9211 | 6.9366 | 7.0473 | 7.2717 | 7.6669 | 7.8728 | 8.0218 | 8.2473 | 8.5351 | 8.8832 | 9.0656 | 9.0065 | 9.071 | 9.071 | 9.071 | 9.071 | 9.071 | 9.071 | 9.071 | 9.071 | 9.071 | 9.071 | 9.071 | 9.071 | 9.071 | 9.071 | 9.071
70% | 1730.3357 | 2044.3359 | 2075.8895 | 7.5858 | 11.2722 | 12.9938 | 19.3159 | 36.1155 | 54.1289 | 63.5903 | 55.122 | 94.4672 | 101.6238 | 93.1813 | 110.4588 | 119.8869 | 119.8869 | 119.8869 | 119.8869 | 119.8869 | 119.8869 | 119.8869 | 119.8869 | 119.8869 | 119.8869 | 119.8869 | 119.8869 | 119.8869 | 119.8869 | 119.8869 |  | 43.7436 | 49.4342 | 49.5912 | 14.593 | 14.6365 | 14.9472 | 15.577 | 16.6861 | 17.264 | 17.6821 | 18.3148 | 19.1227 | 20.0995 | 20.6115 | 20.4455 | 20.6265 | 20.6265 | 20.6265 | 20.6265 | 20.6265 | 20.6265 | 20.6265 | 20.6265 | 20.6265 | 20.6265 | 20.6265 | 20.6265 | 20.6265 | 20.6265 | 20.6265
65% | FY25: 1900.1465; FY26: 2285.7258; FY27: 2324.4723 |  | 12.655 | 14.421 | 14.4697 | 2.8076 | 2.8211 | 2.9175 | 3.1129 | 3.4571 | 3.6365 | 3.7662 | 3.9626 | 4.2133 | 4.5165 | 4.6754 | 4.6239 | 4.68 | 4.68 | 4.68 | 4.68 | 4.68 | 4.68 | 4.68 | 4.68 | 4.68 | 4.68 | 4.68 | 4.68 | 4.68 | 4.68 | 4.68
60% | FY25: 2395.395; FY26: 2958.7224; FY27: 3015.3307 |  | 69.7368 | 80.3657 | 80.659 | 5.0019 | 5.0728 | 5.5927 | 6.7181 | 8.7896 | 9.869 | 10.65 | 11.8318 | 13.3407 | 15.1653 | 16.1215 | 15.8115 | 16.1495 | 16.1495 | 16.1495 | 16.1495 | 16.1495 | 16.1495 | 16.1495 | 16.1495 | 16.1495 | 16.1495 | 16.1495 | 16.1495 | 16.1495 | 16.1495 | 16.1495
55% | FY25: 2397.9043; FY26: 3091.1628; FY27: 3160.8278 |  | 281.6802 | 329.8208 | 331.1492 |  |  |  |  | 0.68325 | 1.593 | 2.4824 | 4.1912 | 6.995 | 11.2941 | 13.9348 | 13.0499 | 14.016 | 14.016 | 14.016 | 14.016 | 14.016 | 14.016 | 14.016 | 14.016 | 14.016 | 14.016 | 14.016 | 14.016 | 14.016 | 14.016 | 14.016
50% | FY25: 1977.8845; FY26: 2764.4944; FY27: 2843.5402 |  | 543.2253 | 651.7379 | 654.7323
45% | FY25: 892.7494; FY26: 1543.8389; FY27: 1609.2663 |  | 742.5052 | 928.9193 | 934.0633
40% | FY25: 82.6197; FY26: 448.4043; FY27: 495.3965 |  | 686.4025 | 938.8137 | 945.7788
35% | FY26: 1.6148; FY27: 5.4003 |  | 458.782 | 868.8929 | 880.2097
30% | [31 empty] | 3.5003 | 199.9764 | 209.3483
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 14376.0875 | 18589.8496 | 19027.0063 | 641.4833 | 668.0878 | 679.2239 | 715.7109 | 794.4981 | 864.6195 | 898.0561 | 868.2191 | 997.1168 | 1018.4675 | 993.227 | 1044.1847 | 1070.9357 | 1070.9357 | 1070.9357 | 1070.9357 | 1070.9357 | 1070.9357 | 1070.9357 | 1070.9357 | 1070.9357 | 1070.9357 | 1070.9357 | 1070.9357 | 1070.9357 | 1070.9357 | 1070.9357 | E @ R (MWh) | 2899.7446 | 4117.569 | 4155.085 | 66.2471 | 66.4494 | 67.9065 | 70.9304 | 77.021 | 80.7428 | 83.6643 | 88.4449 | 95.1644 | 104.1892 | 109.3027 | 107.6165 | 109.4563 | 109.4563 | 109.4563 | 109.4563 | 109.4563 | 109.4563 | 109.4563 | 109.4563 | 109.4563 | 109.4563 | 109.4563 | 109.4563 | 109.4563 | 109.4563 | 109.4563
Option 3 Summer POE50 W E @ R (MWh) N 2 | 10063.2613 | 13012.8947 | 13318.9044 | 449.0383 | 467.6614 | 475.4567 | 500.9976 | 556.1487 | 605.2336 | 628.6393 | 607.7534 | 697.9818 | 712.9272 | 695.2589 | 730.9293 | 749.655 | 749.655 | 749.655 | 749.655 | 749.655 | 749.655 | 749.655 | 749.655 | 749.655 | 749.655 | 749.655 | 749.655 | 749.655 | 749.655 | 749.655 | Option 3 Summer POE10 W E @ R (MWh) N 2 | 869.9234 | 1235.2707 | 1246.5255 | 19.8741 | 19.9348 | 20.3719 | 21.2791 | 23.1063 | 24.2228 | 25.0993 | 26.5335 | 28.5493 | 31.2568 | 32.7908 | 32.2849 | 32.8369 | 32.8369 | 32.8369 | 32.8369 | 32.8369 | 32.8369 | 32.8369 | 32.8369 | 32.8369 | 32.8369 | 32.8369 | 32.8369 | 32.8369 | 32.8369 | 32.8369
Option 4 - Construct 2x 20/33MVA zone substation in Inverloch
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | FY25: 6.2898; FY26: 7.5099; FY27: 7.6393 |  | 7.4111 | 8.5749 | 8.6954
98% | FY25: 0; FY26: 0; FY27: 0 |  | 0 | 0 | 0
97% | FY25: 0; FY26: 0; FY27: 0 |  | 0 | 0 | 0
95% | FY25: 23.5194; FY26: 28.2281; FY27: 28.7274 |  | 27.8469 | 32.3383 | 32.8034
90% | FY25: 131.2778; FY26: 158.4998; FY27: 161.3863 |  | 156.2962 | 182.262 | 184.951
85% | FY25: 517.7326; FY26: 631.4638; FY27: 643.5236 |  | 622.2576 | 730.7409 | 741.9753
80% | FY25: 765.156; FY26: 945.2254; FY27: 964.3195 |  | 930.6493 | 1102.4097 | 1120.197
75% | FY25: 1299.5462; FY26: 1632.1565; FY27: 1667.4256 |  | 1605.2327 | 1922.4952 | 1955.3505
70% | FY25: 1904.5555; FY26: 2445.9592; FY27: 2503.3682 |  | 2402.1342 | 2918.5558 | 2972.0357
65% | FY25: 2035.9088; FY26: 2698.8915; FY27: 2769.1924 |  | 2645.225 | 3277.6155 | 3343.1051
60% | FY25: 2098.8616; FY26: 2921.1907; FY27: 3008.3883 |  | 2854.6256 | 3639.0098 | 3720.2396
55% | FY25: 1733.592; FY26: 2625.5087; FY27: 2720.0851 |  | 2553.3107 | 3404.0714 | 3492.1751
50% | FY25: 1107.3363; FY26: 2015.6842; FY27: 2112.003 |  | 1942.1561 | 2808.5899 | 2898.3167
45% | FY25: 304.3799; FY26: 1151.2957; FY27: 1242.2705 |  | 1081.8472 | 1900.2091 | 1984.9576
40% | FY26: 241.0368; FY27: 303.4886 |  | 197.8445 | 876.0818 | 952.5787
35% | [32 empty] | 53.4346 | 76.5978
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 11808.8744 | 17327.6237 | 17950.4997 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 16856.5689 | 22627.8251 | 23249.1394 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 Winter POE50 W E @ R (MWh) N 2 | 8266.2121 | 12129.3366 | 12565.3498 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 4 Winter POE10 W E @ R (MWh) N 2 | 5056.9707 | 6788.3475 | 6974.7418 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | FY25: 8.9039; FY26: 10.0686; FY27: 10.1857 |  | 0 | 0 | 0
98% | FY25: 0; FY26: 0; FY27: 0 |  | 0 | 0 | 0
97% | FY25: 0; FY26: 0; FY27: 0 |  | 12.1062 | 13.3817 | 13.4169
95% | FY25: 8.3559; FY26: 9.4797; FY27: 9.5926 |  | 0 | 0 | 0
90% | FY25: 171.7748; FY26: 195.5955; FY27: 197.9892 |  | 11.1431 | 12.3531 | 12.3865
85% | FY25: 583.0836; FY26: 668.0948; FY27: 676.6375 |  | 10.18 | 11.3246 | 11.3562
80% | FY25: 892.6437; FY26: 1030.7394; FY27: 1044.6165 |  | 36.8674 | 41.1843 | 41.3034
75% | FY25: 1479.5037; FY26: 1725.3485; FY27: 1750.0533 |  | 16.5074 | 18.5351 | 18.5911
70% | FY25: 1730.3357; FY26: 2044.3359; FY27: 2075.8895 |  | 43.7436 | 49.4342 | 49.5912
65% | FY25: 1900.1465; FY26: 2285.7258; FY27: 2324.4723 |  | 12.655 | 14.421 | 14.4697
60% | FY25: 2395.395; FY26: 2958.7224; FY27: 3015.3307 |  | 69.7368 | 80.3657 | 80.659
55% | FY25: 2397.9043; FY26: 3091.1628; FY27: 3160.8278 |  | 281.6802 | 329.8208 | 331.1492
50% | FY25: 1977.8845; FY26: 2764.4944; FY27: 2843.5402 |  | 543.2253 | 651.7379 | 654.7323
45% | FY25: 892.7494; FY26: 1543.8389; FY27: 1609.2663 |  | 742.5052 | 928.9193 | 934.0633
40% | FY25: 82.6197; FY26: 448.4043; FY27: 495.3965 |  | 686.4025 | 938.8137 | 945.7788
35% | FY26: 1.6148; FY27: 5.4003 |  | 458.782 | 868.8929 | 880.2097
30% | [31 empty] | 3.5003 | 199.9764 | 209.3483
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 14376.0875 | 18589.8496 | 19027.0063 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 2899.7446 | 4117.569 | 4155.085 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 Summer POE50 W E @ R (MWh) N 2 | 10063.2613 | 13012.8947 | 13318.9044 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 4 Summer POE10 W E @ R (MWh) N 2 | 869.9234 | 1235.2707 | 1246.5255 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 - Contract network support services to defer network investment
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | 5.0779 | 6.2159 | 6.343 | 6.5054 | 6.7171 | 6.914 | 7.2567 | 8.1256 | 8.5932 | 8.2399 | 9.3057 | 9.4877 | 9.6129 | 10.2617 | 10.3709 | 10.3709 | 10.3709 | 10.3709 | 10.3709 | 10.3709 | 10.3709 | 10.3709 | 10.3709 | 10.3709 | 10.3709 | 10.3709 | 10.3709 | 10.3709 | 10.3709 | 10.3709 |  | 6.1993 | 7.2809 | 7.3992 | 7.8176 | 7.8068 | 7.8938 | 8.2424 | 9.2541 | 9.6699 | 9.2624 | 10.3622 | 9.885 | 10.2898 | 10.5843 | 10.4627 | 10.4627 | 10.4627 | 10.4627 | 10.4627 | 10.4627 | 10.4627 | 10.4627 | 10.4627 | 10.4627 | 10.4627 | 10.4627 | 10.4627 | 10.4627 | 10.4627 | 10.4627
98% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
97% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
95% | 18.8425 | 23.2342 | 23.7248 | 24.3515 | 25.1686 | 25.9283 | 27.251 | 30.6042 | 32.4088 | 31.0455 | 35.1587 | 35.8612 | 36.3441 | 38.8481 | 39.2696 | 39.2696 | 39.2696 | 39.2696 | 39.2696 | 39.2696 | 39.2696 | 39.2696 | 39.2696 | 39.2696 | 39.2696 | 39.2696 | 39.2696 | 39.2696 | 39.2696 | 39.2696 |  | 23.17 | 27.3445 | 27.8008 | 29.4155 | 29.3739 | 29.7096 | 31.055 | 34.9596 | 36.5641 | 34.9915 | 39.2361 | 37.3942 | 38.9566 | 40.0932 | 39.6238 | 39.6238 | 39.6238 | 39.6238 | 39.6238 | 39.6238 | 39.6238 | 39.6238 | 39.6238 | 39.6238 | 39.6238 | 39.6238 | 39.6238 | 39.6238 | 39.6238 | 39.6238
90% | 104.2394 | 129.629 | 132.465 | 136.0881 | 140.8121 | 145.2038 | 152.8509 | 172.2365 | 182.6695 | 174.788 | 198.5676 | 202.6286 | 205.4202 | 219.8969 | 222.3335 | 222.3335 | 222.3335 | 222.3335 | 222.3335 | 222.3335 | 222.3335 | 222.3335 | 222.3335 | 222.3335 | 222.3335 | 222.3335 | 222.3335 | 222.3335 | 222.3335 | 222.3335 |  | 129.2578 | 153.3913 | 156.0297 | 165.3643 | 165.1241 | 167.0646 | 174.843 | 197.4161 | 206.6924 | 197.6009 | 222.1396 | 211.4913 | 220.5239 | 227.0949 | 224.381 | 224.381 | 224.381 | 224.381 | 224.381 | 224.381 | 224.381 | 224.381 | 224.381 | 224.381 | 224.381 | 224.381 | 224.381 | 224.381 | 224.381 | 224.381
85% | 404.7678 | 510.8437 | 522.6923 | 537.8294 | 557.566 | 575.9144 | 607.8631 | 688.855 | 732.4433 | 699.5147 | 798.8645 | 815.8309 | 827.4941 | 887.9764 | 898.1565 | 898.1565 | 898.1565 | 898.1565 | 898.1565 | 898.1565 | 898.1565 | 898.1565 | 898.1565 | 898.1565 | 898.1565 | 898.1565 | 898.1565 | 898.1565 | 898.1565 | 898.1565 |  | 509.2928 | 610.1209 | 621.144 | 660.1432 | 659.1397 | 667.2473 | 699.7449 | 794.0535 | 832.8092 | 794.8256 | 897.3465 | 852.8585 | 890.5964 | 918.0494 | 906.7107 | 906.7107 | 906.7107 | 906.7107 | 906.7107 | 906.7107 | 906.7107 | 906.7107 | 906.7107 | 906.7107 | 906.7107 | 906.7107 | 906.7107 | 906.7107 | 906.7107 | 906.7107
80% | 586.3002 | 754.249 | 773.0086 | 796.9751 | 828.2239 | 857.2746 | 907.8586 | 1036.0921 | 1105.105 | 1052.9696 | 1210.2689 | 1237.1317 | 1255.5978 | 1351.3589 | 1367.4768 | 1367.4768 | 1367.4768 | 1367.4768 | 1367.4768 | 1367.4768 | 1367.4768 | 1367.4768 | 1367.4768 | 1367.4768 | 1367.4768 | 1367.4768 | 1367.4768 | 1367.4768 | 1367.4768 | 1367.4768 |  | 751.7935 | 911.4333 | 928.8862 | 990.6332 | 989.0443 | 1001.8809 | 1053.334 | 1202.6518 | 1264.0132 | 1203.8742 | 1366.1943 | 1295.757 | 1355.507 | 1398.973 | 1381.0206 | 1381.0206 | 1381.0206 | 1381.0206 | 1381.0206 | 1381.0206 | 1381.0206 | 1381.0206 | 1381.0206 | 1381.0206 | 1381.0206 | 1381.0206 | 1381.0206 | 1381.0206 | 1381.0206 | 1381.0206
75% | 969.1774 | 1279.3996 | 1314.051 | 1358.32 | 1416.0403 | 1469.7006 | 1563.1355 | 1799.9985 | 1927.4738 | 1831.1733 | 2121.7244 | 2171.3433 | 2205.4525 | 2382.3349 | 2412.1067 | 2412.1067 | 2412.1067 | 2412.1067 | 2412.1067 | 2412.1067 | 2412.1067 | 2412.1067 | 2412.1067 | 2412.1067 | 2412.1067 | 2412.1067 | 2412.1067 | 2412.1067 | 2412.1067 | 2412.1067 |  | 1274.8639 | 1569.7384 | 1601.9759 | 1716.0302 | 1713.0954 | 1736.8062 | 1831.8464 | 2107.6547 | 2220.9968 | 2109.9127 | 2409.7378 | 2279.6315 | 2389.9971 | 2470.2841 | 2437.1238 | 2437.1238 | 2437.1238 | 2437.1238 | 2437.1238 | 2437.1238 | 2437.1238 | 2437.1238 | 2437.1238 | 2437.1238 | 2437.1238 | 2437.1238 | 2437.1238 | 2437.1238 | 2437.1238 | 2437.1238
70% | 1366.8004 | 1871.7621 | 1928.1655 | 2000.2241 | 2094.1778 | 2181.5229 | 2333.6109 | 2719.1628 | 2926.6595 | 2769.9072 | 3242.8495 | 3323.6162 | 3379.1372 | 3667.0561 | 3715.5169 | 3715.5169 | 3715.5169 | 3715.5169 | 3715.5169 | 3715.5169 | 3715.5169 | 3715.5169 | 3715.5169 | 3715.5169 | 3715.5169 | 3715.5169 | 3715.5169 | 3715.5169 | 3715.5169 | 3715.5169 |  | 1864.3791 | 2344.3587 | 2396.833 | 2582.484 | 2577.7069 | 2616.302 | 2771.0029 | 3219.9476 | 3404.4393 | 3223.623 | 3711.661 | 3499.8815 | 3679.5281 | 3810.2147 | 3756.2384 | 3756.2384 | 3756.2384 | 3756.2384 | 3756.2384 | 3756.2384 | 3756.2384 | 3756.2384 | 3756.2384 | 3756.2384 | 3756.2384 | 3756.2384 | 3756.2384 | 3756.2384 | 3756.2384 | 3756.2384
65% | 1377.394 | 1995.7512 | 2064.8207 | 2153.0608 | 2268.1131 | 2375.0726 | 2561.3139 | 3033.4463 | 3287.5391 | 3095.586 | 3674.7334 | 3773.6374 | 3841.6263 | 4194.201 | 4253.5443 | 4253.5443 | 4253.5443 | 4253.5443 | 4253.5443 | 4253.5443 | 4253.5443 | 4253.5443 | 4253.5443 | 4253.5443 | 4253.5443 | 4253.5443 | 4253.5443 | 4253.5443 | 4253.5443 | 4253.5443 |  | 1986.7102 | 2574.4752 | 2638.7334 | 2866.0746 | 2860.2248 | 2907.4869 | 3096.9278 | 3646.6886 | 3872.6103 | 3651.1894 | 4248.8225 | 3989.4852 | 4209.4738 | 4369.5077 | 4303.4103 | 4303.4103 | 4303.4103 | 4303.4103 | 4303.4103 | 4303.4103 | 4303.4103 | 4303.4103 | 4303.4103 | 4303.4103 | 4303.4103 | 4303.4103 | 4303.4103 | 4303.4103 | 4303.4103 | 4303.4103
60% | 1282.0743 | 2049.0523 | 2134.7225 | 2244.171 | 2386.8758 | 2519.5428 | 2750.5467 | 3336.1551 | 3651.3184 | 3413.2299 | 4131.5741 | 4254.2494 | 4338.5792 | 4775.8945 | 4849.5009 | 4849.5009 | 4849.5009 | 4849.5009 | 4849.5009 | 4849.5009 | 4849.5009 | 4849.5009 | 4849.5009 | 4849.5009 | 4849.5009 | 4849.5009 | 4849.5009 | 4849.5009 | 4849.5009 | 4849.5009 |  | 2037.8383 | 2766.8713 | 2846.5738 | 3128.5559 | 3121.3002 | 3179.9216 | 3414.8942 | 4096.7888 | 4377.0102 | 4102.3713 | 4843.6441 | 4521.9758 | 4794.838 | 4993.3358 | 4911.352 | 4911.352 | 4911.352 | 4911.352 | 4911.352 | 4911.352 | 4911.352 | 4911.352 | 4911.352 | 4911.352 | 4911.352 | 4911.352 | 4911.352 | 4911.352 | 4911.352 | 4911.352
55% | 847.686 | 1679.5676 | 1772.4875 | 1891.1978 | 2045.9786 | 2189.8722 | 2440.4243 | 3075.5883 | 3417.4217 | 3159.1855 | 3938.3178 | 4071.3741 | 4162.8402 | 4637.1622 | 4716.9973 | 4716.9973 | 4716.9973 | 4716.9973 | 4716.9973 | 4716.9973 | 4716.9973 | 4716.9973 | 4716.9973 | 4716.9973 | 4716.9973 | 4716.9973 | 4716.9973 | 4716.9973 | 4716.9973 | 4716.9973 |  | 1667.4047 | 2458.1303 | 2544.5774 | 2850.4216 | 2842.5519 | 2906.134 | 3160.9906 | 3900.5888 | 4204.5233 | 3906.6438 | 4710.645 | 4361.7562 | 4657.7088 | 4873.0039 | 4784.0824 | 4784.0824 | 4784.0824 | 4784.0824 | 4784.0824 | 4784.0824 | 4784.0824 | 4784.0824 | 4784.0824 | 4784.0824 | 4784.0824 | 4784.0824 | 4784.0824 | 4784.0824 | 4784.0824 | 4784.0824
50% | 223.5163 | 1052.3166 | 1146.9483 | 1267.8455 | 1425.4778 | 1572.0223 | 1827.1901 | 2474.0554 | 2822.1861 | 2559.1926 | 3352.6784 | 3488.186 | 3581.3371 | 4064.3972 | 4145.7031 | 4145.7031 | 4145.7031 | 4145.7031 | 4145.7031 | 4145.7031 | 4145.7031 | 4145.7031 | 4145.7031 | 4145.7031 | 4145.7031 | 4145.7031 | 4145.7031 | 4145.7031 | 4145.7031 | 4145.7031 |  | 1039.9296 | 1845.2223 | 1933.262 | 2244.7405 | 2236.7258 | 2301.4793 | 2561.031 | 3314.2544 | 3623.7881 | 3320.4209 | 4139.2337 | 3783.9176 | 4085.3223 | 4304.5837 | 4214.0241 | 4214.0241 | 4214.0241 | 4214.0241 | 4214.0241 | 4214.0241 | 4214.0241 | 4214.0241 | 4214.0241 | 4214.0241 | 4214.0241 | 4214.0241 | 4214.0241 | 4214.0241 | 4214.0241 | 4214.0241
45% |  | 261.8219 | 336.8252 | 444.9489 | 593.8354 | 732.2492 | 973.2597 | 1584.2354 | 1913.051 | 1664.649 | 2414.1102 | 2542.0995 | 2630.0824 | 3086.3412 | 3163.136 | 3163.136 | 3163.136 | 3163.136 | 3163.136 | 3163.136 | 3163.136 | 3163.136 | 3163.136 | 3163.136 | 3163.136 | 3163.136 | 3163.136 | 3163.136 | 3163.136 | 3163.136 |  | 252.6476 | 990.2915 | 1073.4465 | 1367.6435 | 1360.0734 | 1421.2342 | 1666.3853 | 2377.8181 | 2670.1781 | 2383.6424 | 3157.0255 | 2821.4232 | 3106.1053 | 3313.2015 | 3227.6664 | 3227.6664 | 3227.6664 | 3227.6664 | 3227.6664 | 3227.6664 | 3227.6664 | 3227.6664 | 3227.6664 | 3227.6664 | 3227.6664 | 3227.6664 | 3227.6664 | 3227.6664 | 3227.6664 | 3227.6664
40% |  |  |  | 0.0183 | 12.1381 | 42.8388 | 138.324 | 590.8734 | 887.6733 | 663.4573 | 1339.9461 | 1455.4735 | 1534.8898 | 1946.7242 | 2016.0417 | 2016.0417 | 2016.0417 | 2016.0417 | 2016.0417 | 2016.0417 | 2016.0417 | 2016.0417 | 2016.0417 | 2016.0417 | 2016.0417 | 2016.0417 | 2016.0417 | 2016.0417 | 2016.0417 | 2016.0417 |  |  | 147.0016 | 192.8879 | 400.1301 | 393.955 | 445.0708 | 665.0246 | 1307.1876 | 1571.0815 | 1312.4448 | 2010.5262 | 1707.6004 | 1964.5639 | 2151.4959 | 2074.289 | 2074.289 | 2074.289 | 2074.289 | 2074.289 | 2074.289 | 2074.289 | 2074.289 | 2074.289 | 2074.289 | 2074.289 | 2074.289 | 2074.289 | 2074.289 | 2074.289 | 2074.289
35% | [7 empty] | 3.3197 | 56.689 | 10.4697 | 251.9464 | 321.859 | 374.3255 | 685.9275 | 739.7225 | 739.7225 | 739.7225 | 739.7225 | 739.7225 | 739.7225 | 739.7225 | 739.7225 | 739.7225 | 739.7225 | 739.7225 | 739.7225 | 739.7225 | 739.7225 | 739.7225 | 739.7225 | [7 empty] | 10.6673 | 233.539 | 399.3978 | 236.4503 | 735.4421 | 500.3515 | 699.7723 | 844.844 | 784.9263 | 784.9263 | 784.9263 | 784.9263 | 784.9263 | 784.9263 | 784.9263 | 784.9263 | 784.9263 | 784.9263 | 784.9263 | 784.9263 | 784.9263 | 784.9263 | 784.9263 | 784.9263
30% | FY38: 11.6505; FY39: 19.2708; FY40: 19.2708; FY41: 19.2708; FY42: 19.2708; FY43: 19.2708; FY44: 19.2708; FY45: 19.2708; FY46: 19.2708; FY47: 19.2708; FY48: 19.2708; FY49: 19.2708; FY50: 19.2708; FY51: 19.2708; FY52: 19.2708; FY53: 19.2708; FY54: 19.2708 | [11 empty] | 18.5968 |  | 13.4341 | 39.4251 | 27.095 | 27.095 | 27.095 | 27.095 | 27.095 | 27.095 | 27.095 | 27.095 | 27.095 | 27.095 | 27.095 | 27.095 | 27.095 | 27.095 | 27.095 | 27.095
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 7114.0174 | 11497.7047 | 12034.6917 | 12732.9205 | 13663.1135 | 14547.1159 | 16127.9765 | 20347.2207 | 22721.7193 | 20922.074 | 26452.8453 | 27425.7506 | 28098.9117 | 31640.431 | 32243.4561 | 32243.4561 | 32243.4561 | 32243.4561 | 32243.4561 | 32243.4561 | 32243.4561 | 32243.4561 | 32243.4561 | 32243.4561 | 32243.4561 | 32243.4561 | 32243.4561 | 32243.4561 | 32243.4561 | 32243.4561 | E @ R (MWh) | 11428.0519 | 16241.6036 | 16799.8543 | 18819.3594 | 18766.561 | 19194.3489 | 20934.5297 | 26178.3747 | 28406.8364 | 26222.3806 | 32195.4073 | 29574.6749 | 31795.4515 | 33427.0445 | 32751.5822 | 32751.5822 | 32751.5822 | 32751.5822 | 32751.5822 | 32751.5822 | 32751.5822 | 32751.5822 | 32751.5822 | 32751.5822 | 32751.5822 | 32751.5822 | 32751.5822 | 32751.5822 | 32751.5822 | 32751.5822
Option 5 Winter POE50 W E @ R (MWh) N 2 | 4979.8122 | 8048.3933 | 8424.2842 | 8913.0443 | 9564.1794 | 10182.9811 | 11289.5836 | 14243.0545 | 15905.2035 | 14645.4518 | 18516.9917 | 19198.0254 | 19669.2382 | 22148.3017 | 22570.4193 | 22570.4193 | 22570.4193 | 22570.4193 | 22570.4193 | 22570.4193 | 22570.4193 | 22570.4193 | 22570.4193 | 22570.4193 | 22570.4193 | 22570.4193 | 22570.4193 | 22570.4193 | 22570.4193 | 22570.4193 | Option 5 Winter POE10 W E @ R (MWh) N 2 | 3428.4156 | 4872.4811 | 5039.9563 | 5645.8078 | 5629.9683 | 5758.3047 | 6280.3589 | 7853.5124 | 8522.0509 | 7866.7142 | 9658.6222 | 8872.4025 | 9538.6354 | 10028.1134 | 9825.4747 | 9825.4747 | 9825.4747 | 9825.4747 | 9825.4747 | 9825.4747 | 9825.4747 | 9825.4747 | 9825.4747 | 9825.4747 | 9825.4747 | 9825.4747 | 9825.4747 | 9825.4747 | 9825.4747 | 9825.4747
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | 7.3619 | 8.4221 | 8.5363 | 8.482 | 8.5358 | 8.5525 | 8.6127 | 8.7401 | 8.8537 | 8.9032 | 8.8406 | 9.0396 | 9.0555 | 9.006 | 9.0895 | 9.1309 | 9.1309 | 9.1309 | 9.1309 | 9.1309 | 9.1309 | 9.1309 | 9.1309 | 9.1309 | 9.1309 | 9.1309 | 9.1309 | 9.1309 | 9.1309 | 9.1309 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
98% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
97% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 10.5952 | 11.7682 | 11.8006 | 11.7657 | 11.7747 | 11.8388 | 11.9686 | 12.1972 | 12.3163 | 12.4025 | 12.533 | 12.6995 | 12.9009 | 13.0064 | 12.9722 | 13.0127 | 13.0127 | 13.0127 | 13.0127 | 13.0127 | 13.0127 | 13.0127 | 13.0127 | 13.0127 | 13.0127 | 13.0127 | 13.0127 | 13.0127 | 13.0127 | 13.0127
95% | 6.8682 | 7.8911 | 8.0012 | 7.9489 | 8.0007 | 8.0168 | 8.075 | 8.1979 | 8.3075 | 8.3553 | 8.2949 | 8.4868 | 8.5022 | 8.4544 | 8.535 | 8.5749 | 8.5749 | 8.5749 | 8.5749 | 8.5749 | 8.5749 | 8.5749 | 8.5749 | 8.5749 | 8.5749 | 8.5749 | 8.5749 | 8.5749 | 8.5749 | 8.5749 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
90% | 140.2372 | 161.9207 | 164.2555 | 163.1457 | 164.2451 | 164.5868 | 165.8194 | 168.4238 | 170.7481 | 171.7609 | 170.4806 | 174.5488 | 174.8753 | 173.8625 | 175.5702 | 176.4167 | 176.4167 | 176.4167 | 176.4167 | 176.4167 | 176.4167 | 176.4167 | 176.4167 | 176.4167 | 176.4167 | 176.4167 | 176.4167 | 176.4167 | 176.4167 | 176.4167 |  | 9.7096 | 10.8225 | 10.8532 | 10.8201 | 10.8286 | 10.8894 | 11.0125 | 11.2294 | 11.3424 | 11.4242 | 11.548 | 11.7059 | 11.897 | 11.9971 | 11.9647 | 12.0031 | 12.0031 | 12.0031 | 12.0031 | 12.0031 | 12.0031 | 12.0031 | 12.0031 | 12.0031 | 12.0031 | 12.0031 | 12.0031 | 12.0031 | 12.0031 | 12.0031
85% | 470.5326 | 547.9166 | 556.2489 | 552.2884 | 556.2116 | 557.4311 | 561.8301 | 571.1247 | 579.4196 | 583.0343 | 578.465 | 592.9836 | 594.1487 | 590.5343 | 596.6286 | 599.6497 | 599.6497 | 599.6497 | 599.6497 | 599.6497 | 599.6497 | 599.6497 | 599.6497 | 599.6497 | 599.6497 | 599.6497 | 599.6497 | 599.6497 | 599.6497 | 599.6497 |  | 8.8239 | 9.8767 | 9.9057 | 9.8744 | 9.8825 | 9.9399 | 10.0565 | 10.2616 | 10.3685 | 10.4459 | 10.563 | 10.7124 | 10.8931 | 10.9878 | 10.9571 | 10.9935 | 10.9935 | 10.9935 | 10.9935 | 10.9935 | 10.9935 | 10.9935 | 10.9935 | 10.9935 | 10.9935 | 10.9935 | 10.9935 | 10.9935 | 10.9935 | 10.9935
80% | 709.8113 | 835.517 | 849.0522 | 842.6186 | 848.9917 | 850.9726 | 858.1187 | 873.2171 | 886.6918 | 892.5635 | 885.141 | 908.7257 | 910.6183 | 904.7468 | 914.6468 | 919.5543 | 919.5543 | 919.5543 | 919.5543 | 919.5543 | 919.5543 | 919.5543 | 919.5543 | 919.5543 | 919.5543 | 919.5543 | 919.5543 | 919.5543 | 919.5543 | 919.5543 |  | 31.7532 | 35.7236 | 35.8331 | 35.715 | 35.7454 | 35.9622 | 36.4016 | 37.1754 | 37.5786 | 37.8703 | 38.3118 | 38.8754 | 39.557 | 39.9142 | 39.7984 | 39.9357 | 39.9357 | 39.9357 | 39.9357 | 39.9357 | 39.9357 | 39.9357 | 39.9357 | 39.9357 | 39.9357 | 39.9357 | 39.9357 | 39.9357 | 39.9357 | 39.9357
75% | 1154.0163 | 1377.8039 | 1401.9 | 1390.4466 | 1401.7923 | 1405.3188 | 1418.0406 | 1444.9196 | 1468.9079 | 1479.361 | 1466.1471 | 1508.1337 | 1511.5031 | 1501.0503 | 1518.6747 | 1527.4113 | 1527.4113 | 1527.4113 | 1527.4113 | 1527.4113 | 1527.4113 | 1527.4113 | 1527.4113 | 1527.4113 | 1527.4113 | 1527.4113 | 1527.4113 | 1527.4113 | 1527.4113 | 1527.4113 |  | 14.1053 | 15.9702 | 16.0217 | 15.9662 | 15.9804 | 16.0823 | 16.2887 | 16.6521 | 16.8415 | 16.9785 | 17.1859 | 17.4506 | 17.7708 | 17.9385 | 17.8842 | 17.9486 | 17.9486 | 17.9486 | 17.9486 | 17.9486 | 17.9486 | 17.9486 | 17.9486 | 17.9486 | 17.9486 | 17.9486 | 17.9486 | 17.9486 | 17.9486 | 17.9486
70% | 1314.6139 | 1600.4419 | 1631.2181 | 1616.5894 | 1631.0804 | 1635.5847 | 1651.8333 | 1686.1639 | 1716.8024 | 1730.1535 | 1713.2763 | 1766.9029 | 1771.2063 | 1757.8557 | 1780.3661 | 1791.5248 | 1791.5248 | 1791.5248 | 1791.5248 | 1791.5248 | 1791.5248 | 1791.5248 | 1791.5248 | 1791.5248 | 1791.5248 | 1791.5248 | 1791.5248 | 1791.5248 | 1791.5248 | 1791.5248 |  | 37.0022 | 42.2359 | 42.3803 | 42.2246 | 42.2646 | 42.5504 | 43.1296 | 44.1497 | 44.6812 | 45.0657 | 45.6477 | 46.3906 | 47.2891 | 47.7599 | 47.6073 | 47.7882 | 47.7882 | 47.7882 | 47.7882 | 47.7882 | 47.7882 | 47.7882 | 47.7882 | 47.7882 | 47.7882 | 47.7882 | 47.7882 | 47.7882 | 47.7882 | 47.7882
65% | 1389.6571 | 1740.6422 | 1778.4341 | 1760.4707 | 1778.2651 | 1783.7961 | 1803.7487 | 1845.9054 | 1883.5282 | 1899.9227 | 1879.1983 | 1945.0495 | 1950.3339 | 1933.9399 | 1961.5817 | 1975.2841 | 1975.2841 | 1975.2841 | 1975.2841 | 1975.2841 | 1975.2841 | 1975.2841 | 1975.2841 | 1975.2841 | 1975.2841 | 1975.2841 | 1975.2841 | 1975.2841 | 1975.2841 | 1975.2841 |  | 10.5628 | 12.1871 | 12.2319 | 12.1836 | 12.196 | 12.2847 | 12.4644 | 12.781 | 12.9459 | 13.0653 | 13.2459 | 13.4765 | 13.7553 | 13.9014 | 13.854 | 13.9102 | 13.9102 | 13.9102 | 13.9102 | 13.9102 | 13.9102 | 13.9102 | 13.9102 | 13.9102 | 13.9102 | 13.9102 | 13.9102 | 13.9102 | 13.9102 | 13.9102
60% | 1649.5753 | 2162.3609 | 2217.5745 | 2191.3302 | 2217.3275 | 2225.4083 | 2254.5589 | 2316.1493 | 2371.1159 | 2395.0681 | 2364.7899 | 2460.9978 | 2468.7183 | 2444.7669 | 2485.1513 | 2505.1704 | 2505.1704 | 2505.1704 | 2505.1704 | 2505.1704 | 2505.1704 | 2505.1704 | 2505.1704 | 2505.1704 | 2505.1704 | 2505.1704 | 2505.1704 | 2505.1704 | 2505.1704 | 2505.1704 |  | 57.1451 | 66.9206 | 67.1904 | 66.8995 | 66.9743 | 67.5082 | 68.59 | 70.4952 | 71.488 | 72.2062 | 73.2932 | 74.681 | 76.3591 | 77.2385 | 76.9534 | 77.2914 | 77.2914 | 77.2914 | 77.2914 | 77.2914 | 77.2914 | 77.2914 | 77.2914 | 77.2914 | 77.2914 | 77.2914 | 77.2914 | 77.2914 | 77.2914 | 77.2914
55% | 1480.0618 | 2111.121 | 2179.0696 | 2146.772 | 2178.7657 | 2188.7103 | 2224.5844 | 2300.3806 | 2368.0252 | 2397.502 | 2360.2402 | 2478.6383 | 2488.1396 | 2458.6638 | 2508.3628 | 2532.9993 | 2532.9993 | 2532.9993 | 2532.9993 | 2532.9993 | 2532.9993 | 2532.9993 | 2532.9993 | 2532.9993 | 2532.9993 | 2532.9993 | 2532.9993 | 2532.9993 | 2532.9993 | 2532.9993 |  | 224.6492 | 268.925 | 270.1467 | 268.8295 | 269.1682 | 271.586 | 276.4859 | 285.1152 | 289.6116 | 292.8646 | 297.7878 | 304.0733 | 311.6739 | 315.6571 | 314.3658 | 315.8966 | 315.8966 | 315.8966 | 315.8966 | 315.8966 | 315.8966 | 315.8966 | 315.8966 | 315.8966 | 315.8966 | 315.8966 | 315.8966 | 315.8966 | 315.8966 | 315.8966
50% | 936.449 | 1652.4841 | 1729.5824 | 1692.9358 | 1729.2375 | 1740.5212 | 1781.226 | 1867.2286 | 1943.982 | 1977.428 | 1935.1486 | 2069.4898 | 2080.2705 | 2046.8256 | 2103.2169 | 2131.1708 | 2131.1708 | 2131.1708 | 2131.1708 | 2131.1708 | 2131.1708 | 2131.1708 | 2131.1708 | 2131.1708 | 2131.1708 | 2131.1708 | 2131.1708 | 2131.1708 | 2131.1708 | 2131.1708 |  | 414.6731 | 514.4742 | 517.2281 | 514.2589 | 515.0225 | 520.4724 | 531.5171 | 550.9682 | 561.1034 | 568.4359 | 579.5333 | 593.7012 | 610.8334 | 619.8119 | 616.9012 | 620.3518 | 620.3518 | 620.3518 | 620.3518 | 620.3518 | 620.3518 | 620.3518 | 620.3518 | 620.3518 | 620.3518 | 620.3518 | 620.3518 | 620.3518 | 620.3518 | 620.3518
45% | 119.1863 | 623.4104 | 687.2258 | 656.8929 | 686.9404 | 696.2801 | 729.9721 | 801.1578 | 864.6878 | 892.3716 | 857.3763 | 968.5726 | 977.4959 | 949.813 | 996.489 | 1019.6269 | 1019.6269 | 1019.6269 | 1019.6269 | 1019.6269 | 1019.6269 | 1019.6269 | 1019.6269 | 1019.6269 | 1019.6269 | 1019.6269 | 1019.6269 | 1019.6269 | 1019.6269 | 1019.6269 |  | 521.6651 | 693.1135 | 697.8445 | 692.7438 | 694.0556 | 703.4179 | 722.3917 | 755.8068 | 773.2181 | 785.8146 | 804.8787 | 829.2179 | 858.6493 | 874.0735 | 869.0732 | 875.0009 | 875.0009 | 875.0009 | 875.0009 | 875.0009 | 875.0009 | 875.0009 | 875.0009 | 875.0009 | 875.0009 | 875.0009 | 875.0009 | 875.0009 | 875.0009 | 875.0009
40% |  | 14.5142 | 25.7622 | 20.0266 | 25.705 | 27.6097 | 35.0267 | 53.4719 | 73.052 | 82.4872 | 70.651 | 111.2346 | 114.8641 | 103.7831 | 122.7707 | 132.7343 | 132.7343 | 132.7343 | 132.7343 | 132.7343 | 132.7343 | 132.7343 | 132.7343 | 132.7343 | 132.7343 | 132.7343 | 132.7343 | 132.7343 | 132.7343 | 132.7343 |  | 387.3773 | 619.5244 | 625.9304 | 619.0238 | 620.8 | 633.477 | 659.1681 | 704.4133 | 727.9888 | 745.0449 | 770.8584 | 803.8145 | 843.6657 | 864.5506 | 857.78 | 865.8064 | 865.8064 | 865.8064 | 865.8064 | 865.8064 | 865.8064 | 865.8064 | 865.8064 | 865.8064 | 865.8064 | 865.8064 | 865.8064 | 865.8064 | 865.8064 | 865.8064
35% | [31 empty] | 79.5099 | 351.4132 | 361.3242 | 350.6438 | 353.377 | 373.1546 | 414.5322 | 488.0453 | 526.3502 | 554.0625 | 596.0036 | 649.5498 | 714.2989 | 748.2322 | 737.2315 | 750.2725 | 750.2725 | 750.2725 | 750.2725 | 750.2725 | 750.2725 | 750.2725 | 750.2725 | 750.2725 | 750.2725 | 750.2725 | 750.2725 | 750.2725 | 750.2725 | 750.2725
30% | [37 empty] | 0.24783 | 7.692 | 15.5892 | 22.9798 | 36.7967 | 58.9514 | 92.3324 | 112.6386 | 105.8467 | 113.9202 | 113.9202 | 113.9202 | 113.9202 | 113.9202 | 113.9202 | 113.9202 | 113.9202 | 113.9202 | 113.9202 | 113.9202 | 113.9202 | 113.9202 | 113.9202 | 113.9202
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 9284.5872 | 12716.0016 | 13104.4921 | 12919.4483 | 13102.7477 | 13159.8611 | 13366.4321 | 13805.6299 | 14200.6808 | 14373.7221 | 14155.0694 | 14852.7757 | 14909.1346 | 14734.4694 | 15029.2724 | 15175.9559 | 15175.9559 | 15175.9559 | 15175.9559 | 15175.9559 | 15175.9559 | 15175.9559 | 15175.9559 | 15175.9559 | 15175.9559 | 15175.9559 | 15175.9559 | 15175.9559 | 15175.9559 | 15175.9559 | E @ R (MWh) | 1789.4961 | 2626.4254 | 2651.9039 | 2624.4393 | 2631.4891 | 2682.0721 | 2786.1122 | 2976.9127 | 3080.3097 | 3156.7744 | 3275.105 | 3430.647 | 3625.2569 | 3730.031 | 3695.8578 | 3736.3906 | 3736.3906 | 3736.3906 | 3736.3906 | 3736.3906 | 3736.3906 | 3736.3906 | 3736.3906 | 3736.3906 | 3736.3906 | 3736.3906 | 3736.3906 | 3736.3906 | 3736.3906 | 3736.3906
Option 5 Summer POE50 W E @ R (MWh) N 2 | 6499.2111 | 8901.2011 | 9173.1445 | 9043.6138 | 9171.9234 | 9211.9028 | 9356.5025 | 9663.941 | 9940.4765 | 10061.6055 | 9908.5486 | 10396.943 | 10436.3942 | 10314.1286 | 10520.4907 | 10623.1691 | 10623.1691 | 10623.1691 | 10623.1691 | 10623.1691 | 10623.1691 | 10623.1691 | 10623.1691 | 10623.1691 | 10623.1691 | 10623.1691 | 10623.1691 | 10623.1691 | 10623.1691 | 10623.1691 | Option 5 Summer POE10 W E @ R (MWh) N 2 | 536.8488 | 787.9276 | 795.5712 | 787.3318 | 789.4467 | 804.6216 | 835.8337 | 893.0738 | 924.0929 | 947.0323 | 982.5315 | 1029.1941 | 1087.5771 | 1119.0093 | 1108.7573 | 1120.9172 | 1120.9172 | 1120.9172 | 1120.9172 | 1120.9172 | 1120.9172 | 1120.9172 | 1120.9172 | 1120.9172 | 1120.9172 | 1120.9172 | 1120.9172 | 1120.9172 | 1120.9172 | 1120.9172
Option 6 -
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | 6.2898 | 7.5099 | 7.6393 | 7.7992 | 8.0116 | 8.2129 | 8.5647 | 9.4496 | 9.9255 | 9.5783 | 10.6532 | 10.8469 | 10.9861 | 11.6424 | 11.7492 | 11.7492 | 11.7492 | 11.7492 | 11.7492 | 11.7492 | 11.7492 | 11.7492 | 11.7492 | 11.7492 | 11.7492 | 11.7492 | 11.7492 | 11.7492 | 11.7492 | 11.7492 |  | 7.4111 | 8.5749 | 8.6954 | 9.1114 | 9.1012 | 9.1927 | 9.5504 | 10.5781 | 11.0022 | 10.6008 | 11.7097 | 11.2441 | 11.6631 | 11.965 | 11.8409 | 11.8409 | 11.8409 | 11.8409 | 11.8409 | 11.8409 | 11.8409 | 11.8409 | 11.8409 | 11.8409 | 11.8409 | 11.8409 | 11.8409 | 11.8409 | 11.8409 | 11.8409
98% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
97% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
95% | 23.5194 | 28.2281 | 28.7274 | 29.3447 | 30.1642 | 30.9412 | 32.299 | 35.7139 | 37.5508 | 36.2107 | 40.3592 | 41.1067 | 41.6439 | 44.1765 | 44.5887 | 44.5887 | 44.5887 | 44.5887 | 44.5887 | 44.5887 | 44.5887 | 44.5887 | 44.5887 | 44.5887 | 44.5887 | 44.5887 | 44.5887 | 44.5887 | 44.5887 | 44.5887 |  | 27.8469 | 32.3383 | 32.8034 | 34.4086 | 34.3695 | 34.7225 | 36.103 | 40.0693 | 41.7061 | 40.1568 | 44.4365 | 42.6397 | 44.2565 | 45.4216 | 44.9429 | 44.9429 | 44.9429 | 44.9429 | 44.9429 | 44.9429 | 44.9429 | 44.9429 | 44.9429 | 44.9429 | 44.9429 | 44.9429 | 44.9429 | 44.9429 | 44.9429 | 44.9429
90% | 131.2778 | 158.4998 | 161.3863 | 164.9549 | 169.693 | 174.1847 | 182.0345 | 201.7773 | 212.3964 | 204.6495 | 228.6329 | 232.954 | 236.0601 | 250.7016 | 253.0848 | 253.0848 | 253.0848 | 253.0848 | 253.0848 | 253.0848 | 253.0848 | 253.0848 | 253.0848 | 253.0848 | 253.0848 | 253.0848 | 253.0848 | 253.0848 | 253.0848 | 253.0848 |  | 156.2962 | 182.262 | 184.951 | 194.2311 | 194.0049 | 196.0456 | 204.0267 | 226.9569 | 236.4193 | 227.4624 | 252.2049 | 241.8166 | 251.1639 | 257.8997 | 255.1323 | 255.1323 | 255.1323 | 255.1323 | 255.1323 | 255.1323 | 255.1323 | 255.1323 | 255.1323 | 255.1323 | 255.1323 | 255.1323 | 255.1323 | 255.1323 | 255.1323 | 255.1323
85% | 517.7326 | 631.4638 | 643.5236 | 658.433 | 678.2282 | 696.9946 | 729.7905 | 812.2744 | 856.6401 | 824.274 | 924.4749 | 942.5282 | 955.5054 | 1016.6765 | 1026.6333 | 1026.6333 | 1026.6333 | 1026.6333 | 1026.6333 | 1026.6333 | 1026.6333 | 1026.6333 | 1026.6333 | 1026.6333 | 1026.6333 | 1026.6333 | 1026.6333 | 1026.6333 | 1026.6333 | 1026.6333 |  | 622.2576 | 730.7409 | 741.9753 | 780.7468 | 779.8019 | 788.3275 | 821.6723 | 917.4729 | 957.006 | 919.5849 | 1022.9569 | 979.5557 | 1018.6078 | 1046.7495 | 1035.1875 | 1035.1875 | 1035.1875 | 1035.1875 | 1035.1875 | 1035.1875 | 1035.1875 | 1035.1875 | 1035.1875 | 1035.1875 | 1035.1875 | 1035.1875 | 1035.1875 | 1035.1875 | 1035.1875 | 1035.1875
80% | 765.156 | 945.2254 | 964.3195 | 987.9254 | 1019.2669 | 1048.9795 | 1100.9048 | 1231.5006 | 1301.7444 | 1250.4995 | 1409.1465 | 1437.7299 | 1458.2767 | 1555.1282 | 1570.8926 | 1570.8926 | 1570.8926 | 1570.8926 | 1570.8926 | 1570.8926 | 1570.8926 | 1570.8926 | 1570.8926 | 1570.8926 | 1570.8926 | 1570.8926 | 1570.8926 | 1570.8926 | 1570.8926 | 1570.8926 |  | 930.6493 | 1102.4097 | 1120.197 | 1181.5834 | 1180.0873 | 1193.5858 | 1246.3802 | 1398.0603 | 1460.6526 | 1401.4041 | 1565.0719 | 1496.3553 | 1558.1859 | 1602.7423 | 1584.4364 | 1584.4364 | 1584.4364 | 1584.4364 | 1584.4364 | 1584.4364 | 1584.4364 | 1584.4364 | 1584.4364 | 1584.4364 | 1584.4364 | 1584.4364 | 1584.4364 | 1584.4364 | 1584.4364 | 1584.4364
75% | 1299.5462 | 1632.1565 | 1667.4256 | 1711.0285 | 1768.9201 | 1823.803 | 1919.7155 | 2160.942 | 2290.6908 | 2196.0352 | 2489.0758 | 2541.8729 | 2579.8253 | 2758.7219 | 2787.8407 | 2787.8407 | 2787.8407 | 2787.8407 | 2787.8407 | 2787.8407 | 2787.8407 | 2787.8407 | 2787.8407 | 2787.8407 | 2787.8407 | 2787.8407 | 2787.8407 | 2787.8407 | 2787.8407 | 2787.8407 |  | 1605.2327 | 1922.4952 | 1955.3505 | 2068.7387 | 2065.9753 | 2090.9087 | 2188.4265 | 2468.5981 | 2584.2139 | 2474.7746 | 2777.0892 | 2650.1611 | 2764.3699 | 2846.6711 | 2812.8578 | 2812.8578 | 2812.8578 | 2812.8578 | 2812.8578 | 2812.8578 | 2812.8578 | 2812.8578 | 2812.8578 | 2812.8578 | 2812.8578 | 2812.8578 | 2812.8578 | 2812.8578 | 2812.8578 | 2812.8578
70% | 1904.5555 | 2445.9592 | 2503.3682 | 2574.3426 | 2668.5752 | 2757.9103 | 2914.0312 | 3306.6856 | 3517.8832 | 3363.8083 | 3840.8027 | 3926.7428 | 3988.5195 | 4279.7169 | 4327.1149 | 4327.1149 | 4327.1149 | 4327.1149 | 4327.1149 | 4327.1149 | 4327.1149 | 4327.1149 | 4327.1149 | 4327.1149 | 4327.1149 | 4327.1149 | 4327.1149 | 4327.1149 | 4327.1149 | 4327.1149 |  | 2402.1342 | 2918.5558 | 2972.0357 | 3156.6025 | 3152.1043 | 3192.6894 | 3351.4232 | 3807.4704 | 3995.6629 | 3817.524 | 4309.6142 | 4103.0081 | 4288.9105 | 4422.8756 | 4367.8364 | 4367.8364 | 4367.8364 | 4367.8364 | 4367.8364 | 4367.8364 | 4367.8364 | 4367.8364 | 4367.8364 | 4367.8364 | 4367.8364 | 4367.8364 | 4367.8364 | 4367.8364 | 4367.8364 | 4367.8364
65% | 2035.9088 | 2698.8915 | 2769.1924 | 2856.1049 | 2971.4986 | 3080.895 | 3272.0749 | 3752.9047 | 4011.5294 | 3822.8551 | 4406.9646 | 4512.2036 | 4587.8531 | 4944.4426 | 5002.4844 | 5002.4844 | 5002.4844 | 5002.4844 | 5002.4844 | 5002.4844 | 5002.4844 | 5002.4844 | 5002.4844 | 5002.4844 | 5002.4844 | 5002.4844 | 5002.4844 | 5002.4844 | 5002.4844 | 5002.4844 |  | 2645.225 | 3277.6155 | 3343.1051 | 3569.1186 | 3563.6103 | 3613.3093 | 3807.6888 | 4366.1471 | 4596.6007 | 4378.4584 | 4981.0536 | 4728.0515 | 4955.7006 | 5119.7493 | 5052.3503 | 5052.3503 | 5052.3503 | 5052.3503 | 5052.3503 | 5052.3503 | 5052.3503 | 5052.3503 | 5052.3503 | 5052.3503 | 5052.3503 | 5052.3503 | 5052.3503 | 5052.3503 | 5052.3503 | 5052.3503
60% | 2098.8616 | 2921.1907 | 3008.3883 | 3116.1901 | 3259.3184 | 3395.008 | 3632.1374 | 4228.5337 | 4549.3182 | 4315.2964 | 5039.7953 | 5170.3283 | 5264.16 | 5706.4549 | 5778.4469 | 5778.4469 | 5778.4469 | 5778.4469 | 5778.4469 | 5778.4469 | 5778.4469 | 5778.4469 | 5778.4469 | 5778.4469 | 5778.4469 | 5778.4469 | 5778.4469 | 5778.4469 | 5778.4469 | 5778.4469 |  | 2854.6256 | 3639.0098 | 3720.2396 | 4000.575 | 3993.7428 | 4055.3868 | 4296.485 | 4989.1674 | 5275.01 | 5004.4378 | 5751.8653 | 5438.0548 | 5720.4188 | 5923.8962 | 5840.298 | 5840.298 | 5840.298 | 5840.298 | 5840.298 | 5840.298 | 5840.298 | 5840.298 | 5840.298 | 5840.298 | 5840.298 | 5840.298 | 5840.298 | 5840.298 | 5840.298 | 5840.298
55% | 1733.592 | 2625.5087 | 2720.0851 | 2837.0093 | 2992.2496 | 3139.4215 | 3396.6175 | 4043.4823 | 4391.4125 | 4137.5871 | 4923.395 | 5064.974 | 5166.746 | 5646.469 | 5724.5532 | 5724.5532 | 5724.5532 | 5724.5532 | 5724.5532 | 5724.5532 | 5724.5532 | 5724.5532 | 5724.5532 | 5724.5532 | 5724.5532 | 5724.5532 | 5724.5532 | 5724.5532 | 5724.5532 | 5724.5532 |  | 2553.3107 | 3404.0714 | 3492.1751 | 3796.2332 | 3788.8228 | 3855.6833 | 4117.1838 | 4868.4828 | 5178.5141 | 4885.0454 | 5695.7222 | 5355.3561 | 5661.6146 | 5882.3107 | 5791.6383 | 5791.6383 | 5791.6383 | 5791.6383 | 5791.6383 | 5791.6383 | 5791.6383 | 5791.6383 | 5791.6383 | 5791.6383 | 5791.6383 | 5791.6383 | 5791.6383 | 5791.6383 | 5791.6383 | 5791.6383
50% | 1107.3363 | 2015.6842 | 2112.003 | 2231.0812 | 2389.1813 | 2539.0646 | 2800.9987 | 3459.7803 | 3814.1202 | 3555.6188 | 4355.9031 | 4500.0904 | 4603.7372 | 5092.2979 | 5171.8205 | 5171.8205 | 5171.8205 | 5171.8205 | 5171.8205 | 5171.8205 | 5171.8205 | 5171.8205 | 5171.8205 | 5171.8205 | 5171.8205 | 5171.8205 | 5171.8205 | 5171.8205 | 5171.8205 | 5171.8205 |  | 1942.1561 | 2808.5899 | 2898.3167 | 3207.9763 | 3200.4293 | 3268.5216 | 3534.8396 | 4299.9793 | 4615.7221 | 4316.847 | 5142.4584 | 4795.822 | 5107.7225 | 5332.4844 | 5240.1415 | 5240.1415 | 5240.1415 | 5240.1415 | 5240.1415 | 5240.1415 | 5240.1415 | 5240.1415 | 5240.1415 | 5240.1415 | 5240.1415 | 5240.1415 | 5240.1415 | 5240.1415 | 5240.1415 | 5240.1415
45% | 304.3799 | 1151.2957 | 1242.2705 | 1354.742 | 1504.0703 | 1645.6377 | 1893.0391 | 2515.2699 | 2849.9501 | 2605.791 | 3361.6736 | 3497.861 | 3595.7573 | 4057.2114 | 4132.3219 | 4132.3219 | 4132.3219 | 4132.3219 | 4132.3219 | 4132.3219 | 4132.3219 | 4132.3219 | 4132.3219 | 4132.3219 | 4132.3219 | 4132.3219 | 4132.3219 | 4132.3219 | 4132.3219 | 4132.3219 |  | 1081.8472 | 1900.2091 | 1984.9576 | 2277.4365 | 2270.3083 | 2334.6226 | 2586.1647 | 3308.8526 | 3607.0772 | 3324.7844 | 4104.5889 | 3777.1848 | 4071.7802 | 4284.0718 | 4196.8523 | 4196.8523 | 4196.8523 | 4196.8523 | 4196.8523 | 4196.8523 | 4196.8523 | 4196.8523 | 4196.8523 | 4196.8523 | 4196.8523 | 4196.8523 | 4196.8523 | 4196.8523 | 4196.8523 | 4196.8523
40% |  | 241.0368 | 303.4886 | 389.6318 | 518.5137 | 646.2971 | 869.6099 | 1431.2562 | 1733.3497 | 1512.9635 | 2195.2484 | 2318.1757 | 2406.5401 | 2823.064 | 2890.8613 | 2890.8613 | 2890.8613 | 2890.8613 | 2890.8613 | 2890.8613 | 2890.8613 | 2890.8613 | 2890.8613 | 2890.8613 | 2890.8613 | 2890.8613 | 2890.8613 | 2890.8613 | 2890.8613 | 2890.8613 |  | 197.8445 | 876.0818 | 952.5787 | 1216.5798 | 1210.1457 | 1268.1979 | 1495.2482 | 2147.5704 | 2416.7579 | 2161.951 | 2865.8286 | 2570.3026 | 2836.2143 | 3027.8357 | 2949.1086 | 2949.1086 | 2949.1086 | 2949.1086 | 2949.1086 | 2949.1086 | 2949.1086 | 2949.1086 | 2949.1086 | 2949.1086 | 2949.1086 | 2949.1086 | 2949.1086 | 2949.1086 | 2949.1086 | 2949.1086
35% |  |  |  |  | 0.16059 | 8.4247 | 51.6577 | 306.5672 | 520.3346 | 359.4876 | 878.7989 | 974.1987 | 1042.7754 | 1366.0258 | 1418.641 | 1418.641 | 1418.641 | 1418.641 | 1418.641 | 1418.641 | 1418.641 | 1418.641 | 1418.641 | 1418.641 | 1418.641 | 1418.641 | 1418.641 | 1418.641 | 1418.641 | 1418.641 |  |  | 53.4346 | 76.5978 | 185.9699 | 182.7815 | 212.4625 | 347.6947 | 841.7976 | 1050.7051 | 852.9579 | 1399.2139 | 1169.866 | 1376.2313 | 1524.9423 | 1463.8448 | 1463.8448 | 1463.8448 | 1463.8448 | 1463.8448 | 1463.8448 | 1463.8448 | 1463.8448 | 1463.8448 | 1463.8448 | 1463.8448 | 1463.8448 | 1463.8448 | 1463.8448 | 1463.8448 | 1463.8448
30% | [8 empty] | 0.13247 |  | 47.3865 | 73.4365 | 95.4345 | 233.8409 | 261.5037 | 261.5037 | 261.5037 | 261.5037 | 261.5037 | 261.5037 | 261.5037 | 261.5037 | 261.5037 | 261.5037 | 261.5037 | 261.5037 | 261.5037 | 261.5037 | 261.5037 | 261.5037 | [8 empty] | 38.745 | 98.151 | 41.2641 | 251.1294 | 143.1816 | 239.0986 | 321.5304 | 286.3608 | 286.3608 | 286.3608 | 286.3608 | 286.3608 | 286.3608 | 286.3608 | 286.3608 | 286.3608 | 286.3608 | 286.3608 | 286.3608 | 286.3608 | 286.3608 | 286.3608 | 286.3608
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 11808.8744 | 17327.6237 | 17950.4997 | 18729.4017 | 19778.0731 | 20785.8168 | 22575.4407 | 27221.1763 | 29796.0085 | 27912.7082 | 33810.7876 | 34892.5992 | 35673.4826 | 39388.7046 | 39998.5117 | 39998.5117 | 39998.5117 | 39998.5117 | 39998.5117 | 39998.5117 | 39998.5117 | 39998.5117 | 39998.5117 | 39998.5117 | 39998.5117 | 39998.5117 | 39998.5117 | 39998.5117 | 39998.5117 | 39998.5117 | E @ R (MWh) | 16856.5689 | 22627.8251 | 23249.1394 | 25422.5188 | 25369.0323 | 25852.5194 | 27762.4582 | 33392.6489 | 35763.9491 | 33518.6811 | 39773.1943 | 37127.5741 | 39506.8788 | 41234.634 | 40523.5006 | 40523.5006 | 40523.5006 | 40523.5006 | 40523.5006 | 40523.5006 | 40523.5006 | 40523.5006 | 40523.5006 | 40523.5006 | 40523.5006 | 40523.5006 | 40523.5006 | 40523.5006 | 40523.5006 | 40523.5006
Option 6 Winter POE50 W E @ R (MWh) N 2 | 8266.2121 | 12129.3366 | 12565.3498 | 13110.5812 | 13844.6511 | 14550.0718 | 15802.8085 | 19054.8234 | 20857.206 | 19538.8958 | 23667.5513 | 24424.8194 | 24971.4378 | 27572.0932 | 27998.9582 | 27998.9582 | 27998.9582 | 27998.9582 | 27998.9582 | 27998.9582 | 27998.9582 | 27998.9582 | 27998.9582 | 27998.9582 | 27998.9582 | 27998.9582 | 27998.9582 | 27998.9582 | 27998.9582 | 27998.9582 | Option 6 Winter POE10 W E @ R (MWh) N 2 | 5056.9707 | 6788.3475 | 6974.7418 | 7626.7556 | 7610.7097 | 7755.7558 | 8328.7375 | 10017.7947 | 10729.1847 | 10055.6043 | 11931.9583 | 11138.2722 | 11852.0637 | 12370.3902 | 12157.0502 | 12157.0502 | 12157.0502 | 12157.0502 | 12157.0502 | 12157.0502 | 12157.0502 | 12157.0502 | 12157.0502 | 12157.0502 | 12157.0502 | 12157.0502 | 12157.0502 | 12157.0502 | 12157.0502 | 12157.0502
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | 8.9039 | 10.0686 | 10.1857 | 10.1283 | 10.1828 | 10.2053 | 10.2771 | 10.4248 | 10.549 | 10.6062 | 10.5553 | 10.769 | 10.8029 | 10.7628 | 10.8432 | 10.8846 | 10.8846 | 10.8846 | 10.8846 | 10.8846 | 10.8846 | 10.8846 | 10.8846 | 10.8846 | 10.8846 | 10.8846 | 10.8846 | 10.8846 | 10.8846 | 10.8846 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
98% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
97% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 12.1062 | 13.3817 | 13.4169 | 13.3789 | 13.3887 | 13.4583 | 13.5995 | 13.8481 | 13.9776 | 14.0713 | 14.2131 | 14.3942 | 14.6131 | 14.7279 | 14.6907 | 14.7312 | 14.7312 | 14.7312 | 14.7312 | 14.7312 | 14.7312 | 14.7312 | 14.7312 | 14.7312 | 14.7312 | 14.7312 | 14.7312 | 14.7312 | 14.7312 | 14.7312
95% | 8.3559 | 9.4797 | 9.5926 | 9.5372 | 9.5899 | 9.6115 | 9.6808 | 9.8233 | 9.9432 | 9.9984 | 9.9492 | 10.1554 | 10.1881 | 10.1494 | 10.227 | 10.267 | 10.267 | 10.267 | 10.267 | 10.267 | 10.267 | 10.267 | 10.267 | 10.267 | 10.267 | 10.267 | 10.267 | 10.267 | 10.267 | 10.267 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
90% | 171.7748 | 195.5955 | 197.9892 | 196.8158 | 197.9315 | 198.3899 | 199.8591 | 202.88 | 205.4214 | 206.5912 | 205.5485 | 209.9202 | 210.6135 | 209.793 | 211.4383 | 212.2848 | 212.2848 | 212.2848 | 212.2848 | 212.2848 | 212.2848 | 212.2848 | 212.2848 | 212.2848 | 212.2848 | 212.2848 | 212.2848 | 212.2848 | 212.2848 | 212.2848 |  | 11.1431 | 12.3531 | 12.3865 | 12.3505 | 12.3598 | 12.4259 | 12.5598 | 12.7956 | 12.9185 | 13.0074 | 13.142 | 13.3137 | 13.5215 | 13.6303 | 13.595 | 13.6335 | 13.6335 | 13.6335 | 13.6335 | 13.6335 | 13.6335 | 13.6335 | 13.6335 | 13.6335 | 13.6335 | 13.6335 | 13.6335 | 13.6335 | 13.6335 | 13.6335
85% | 583.0836 | 668.0948 | 676.6375 | 672.4501 | 676.4317 | 678.0677 | 683.3108 | 694.0919 | 703.1615 | 707.3365 | 703.6153 | 719.2167 | 721.6911 | 718.7628 | 724.6348 | 727.6558 | 727.6558 | 727.6558 | 727.6558 | 727.6558 | 727.6558 | 727.6558 | 727.6558 | 727.6558 | 727.6558 | 727.6558 | 727.6558 | 727.6558 | 727.6558 | 727.6558 |  | 10.18 | 11.3246 | 11.3562 | 11.3221 | 11.3309 | 11.3934 | 11.5201 | 11.7432 | 11.8594 | 11.9435 | 12.0708 | 12.2333 | 12.4298 | 12.5328 | 12.4994 | 12.5358 | 12.5358 | 12.5358 | 12.5358 | 12.5358 | 12.5358 | 12.5358 | 12.5358 | 12.5358 | 12.5358 | 12.5358 | 12.5358 | 12.5358 | 12.5358 | 12.5358
80% | 892.6437 | 1030.7394 | 1044.6165 | 1037.8142 | 1044.2821 | 1046.9396 | 1055.4569 | 1072.9701 | 1087.703 | 1094.485 | 1088.4403 | 1113.7838 | 1117.8034 | 1113.0465 | 1122.5851 | 1127.4926 | 1127.4926 | 1127.4926 | 1127.4926 | 1127.4926 | 1127.4926 | 1127.4926 | 1127.4926 | 1127.4926 | 1127.4926 | 1127.4926 | 1127.4926 | 1127.4926 | 1127.4926 | 1127.4926 |  | 36.8674 | 41.1843 | 41.3034 | 41.175 | 41.208 | 41.4438 | 41.9215 | 42.7629 | 43.2013 | 43.5185 | 43.9985 | 44.6113 | 45.3524 | 45.7408 | 45.6149 | 45.7521 | 45.7521 | 45.7521 | 45.7521 | 45.7521 | 45.7521 | 45.7521 | 45.7521 | 45.7521 | 45.7521 | 45.7521 | 45.7521 | 45.7521 | 45.7521 | 45.7521
75% | 1479.5037 | 1725.3485 | 1750.0533 | 1737.9436 | 1749.458 | 1754.1891 | 1769.3519 | 1800.5298 | 1826.7581 | 1838.8318 | 1828.0706 | 1873.1885 | 1880.3443 | 1871.8759 | 1888.857 | 1897.5936 | 1897.5936 | 1897.5936 | 1897.5936 | 1897.5936 | 1897.5936 | 1897.5936 | 1897.5936 | 1897.5936 | 1897.5936 | 1897.5936 | 1897.5936 | 1897.5936 | 1897.5936 | 1897.5936 |  | 16.5074 | 18.5351 | 18.5911 | 18.5307 | 18.5462 | 18.657 | 18.8814 | 19.2766 | 19.4825 | 19.6315 | 19.8569 | 20.1448 | 20.4928 | 20.6753 | 20.6161 | 20.6806 | 20.6806 | 20.6806 | 20.6806 | 20.6806 | 20.6806 | 20.6806 | 20.6806 | 20.6806 | 20.6806 | 20.6806 | 20.6806 | 20.6806 | 20.6806 | 20.6806
70% | 1730.3357 | 2044.3359 | 2075.8895 | 2060.4227 | 2075.1292 | 2081.1719 | 2100.5382 | 2140.3596 | 2173.8591 | 2189.28 | 2175.5354 | 2233.1613 | 2242.3009 | 2231.4848 | 2253.1735 | 2264.3322 | 2264.3322 | 2264.3322 | 2264.3322 | 2264.3322 | 2264.3322 | 2264.3322 | 2264.3322 | 2264.3322 | 2264.3322 | 2264.3322 | 2264.3322 | 2264.3322 | 2264.3322 | 2264.3322 |  | 43.7436 | 49.4342 | 49.5912 | 49.4219 | 49.4654 | 49.7762 | 50.4059 | 51.515 | 52.0929 | 52.511 | 53.1438 | 53.9516 | 54.9285 | 55.4404 | 55.2744 | 55.4554 | 55.4554 | 55.4554 | 55.4554 | 55.4554 | 55.4554 | 55.4554 | 55.4554 | 55.4554 | 55.4554 | 55.4554 | 55.4554 | 55.4554 | 55.4554 | 55.4554
65% | 1900.1465 | 2285.7258 | 2324.4723 | 2305.4797 | 2323.5388 | 2330.9589 | 2354.74 | 2403.639 | 2444.775 | 2463.7113 | 2446.8335 | 2517.5958 | 2528.8188 | 2515.5371 | 2542.1699 | 2555.8723 | 2555.8723 | 2555.8723 | 2555.8723 | 2555.8723 | 2555.8723 | 2555.8723 | 2555.8723 | 2555.8723 | 2555.8723 | 2555.8723 | 2555.8723 | 2555.8723 | 2555.8723 | 2555.8723 |  | 12.655 | 14.421 | 14.4697 | 14.4172 | 14.4307 | 14.5271 | 14.7226 | 15.0668 | 15.2461 | 15.3759 | 15.5723 | 15.823 | 16.1261 | 16.285 | 16.2335 | 16.2897 | 16.2897 | 16.2897 | 16.2897 | 16.2897 | 16.2897 | 16.2897 | 16.2897 | 16.2897 | 16.2897 | 16.2897 | 16.2897 | 16.2897 | 16.2897 | 16.2897
60% | 2395.395 | 2958.7224 | 3015.3307 | 2987.5827 | 3013.9668 | 3024.8076 | 3059.5514 | 3130.9924 | 3191.0917 | 3218.7573 | 3194.0991 | 3297.482 | 3313.8788 | 3294.4743 | 3333.3846 | 3353.4037 | 3353.4037 | 3353.4037 | 3353.4037 | 3353.4037 | 3353.4037 | 3353.4037 | 3353.4037 | 3353.4037 | 3353.4037 | 3353.4037 | 3353.4037 | 3353.4037 | 3353.4037 | 3353.4037 |  | 69.7368 | 80.3657 | 80.659 | 80.3428 | 80.4241 | 81.0045 | 82.1808 | 84.2523 | 85.3317 | 86.1126 | 87.2945 | 88.8034 | 90.628 | 91.5842 | 91.2742 | 91.6122 | 91.6122 | 91.6122 | 91.6122 | 91.6122 | 91.6122 | 91.6122 | 91.6122 | 91.6122 | 91.6122 | 91.6122 | 91.6122 | 91.6122 | 91.6122 | 91.6122
55% | 2397.9043 | 3091.1628 | 3160.8278 | 3126.6797 | 3159.1493 | 3172.4904 | 3215.248 | 3303.1668 | 3377.1279 | 3411.1746 | 3380.829 | 3508.0571 | 3528.2358 | 3504.3556 | 3552.2406 | 3576.8771 | 3576.8771 | 3576.8771 | 3576.8771 | 3576.8771 | 3576.8771 | 3576.8771 | 3576.8771 | 3576.8771 | 3576.8771 | 3576.8771 | 3576.8771 | 3576.8771 | 3576.8771 | 3576.8771 |  | 281.6802 | 329.8208 | 331.1492 | 329.717 | 330.0853 | 332.7141 | 338.0417 | 347.4243 | 352.3132 | 355.8501 | 361.2031 | 368.0372 | 376.3012 | 380.6321 | 379.2281 | 380.7589 | 380.7589 | 380.7589 | 380.7589 | 380.7589 | 380.7589 | 380.7589 | 380.7589 | 380.7589 | 380.7589 | 380.7589 | 380.7589 | 380.7589 | 380.7589 | 380.7589
50% | 1977.8845 | 2764.4944 | 2843.5402 | 2804.7939 | 2841.6356 | 2856.7733 | 2905.2884 | 3005.046 | 3088.9664 | 3127.5977 | 3093.1659 | 3237.526 | 3260.4218 | 3233.3261 | 3287.6591 | 3315.613 | 3315.613 | 3315.613 | 3315.613 | 3315.613 | 3315.613 | 3315.613 | 3315.613 | 3315.613 | 3315.613 | 3315.613 | 3315.613 | 3315.613 | 3315.613 | 3315.613 |  | 543.2253 | 651.7379 | 654.7323 | 651.5039 | 652.3342 | 658.2598 | 670.2686 | 691.4175 | 702.4375 | 710.41 | 722.476 | 737.8807 | 756.5083 | 766.2706 | 763.1058 | 766.5564 | 766.5564 | 766.5564 | 766.5564 | 766.5564 | 766.5564 | 766.5564 | 766.5564 | 766.5564 | 766.5564 | 766.5564 | 766.5564 | 766.5564 | 766.5564 | 766.5564
45% | 892.7494 | 1543.8389 | 1609.2663 | 1577.1954 | 1607.6899 | 1620.2195 | 1660.3762 | 1742.9472 | 1812.4095 | 1844.3852 | 1815.8854 | 1935.3746 | 1954.3258 | 1931.8982 | 1976.8705 | 2000.0084 | 2000.0084 | 2000.0084 | 2000.0084 | 2000.0084 | 2000.0084 | 2000.0084 | 2000.0084 | 2000.0084 | 2000.0084 | 2000.0084 | 2000.0084 | 2000.0084 | 2000.0084 | 2000.0084 |  | 742.5052 | 928.9193 | 934.0633 | 928.5173 | 929.9435 | 940.1232 | 960.7531 | 997.085 | 1016.0161 | 1029.7122 | 1050.4404 | 1076.9041 | 1108.9046 | 1125.6752 | 1120.2384 | 1126.1661 | 1126.1661 | 1126.1661 | 1126.1661 | 1126.1661 | 1126.1661 | 1126.1661 | 1126.1661 | 1126.1661 | 1126.1661 | 1126.1661 | 1126.1661 | 1126.1661 | 1126.1661 | 1126.1661
40% | 82.6197 | 448.4043 | 495.3965 | 472.3621 | 494.2643 | 503.2635 | 532.1055 | 591.4108 | 641.301 | 664.267 | 643.7975 | 729.6188 | 743.2302 | 727.122 | 759.4226 | 776.041 | 776.041 | 776.041 | 776.041 | 776.041 | 776.041 | 776.041 | 776.041 | 776.041 | 776.041 | 776.041 | 776.041 | 776.041 | 776.041 | 776.041 |  | 686.4025 | 938.8137 | 945.7788 | 938.2693 | 940.2006 | 953.9841 | 981.9179 | 1031.1125 | 1056.7459 | 1075.2908 | 1103.3575 | 1139.1903 | 1182.5201 | 1205.2281 | 1197.8665 | 1205.8928 | 1205.8928 | 1205.8928 | 1205.8928 | 1205.8928 | 1205.8928 | 1205.8928 | 1205.8928 | 1205.8928 | 1205.8928 | 1205.8928 | 1205.8928 | 1205.8928 | 1205.8928 | 1205.8928
35% |  | 1.6148 | 5.4003 | 3.2709 | 5.2834 | 6.2472 | 9.8686 | 19.8299 | 30.7782 | 36.5919 | 31.3867 | 55.7517 | 60.2225 | 54.9494 | 65.7537 | 71.6692 | 71.6692 | 71.6692 | 71.6692 | 71.6692 | 71.6692 | 71.6692 | 71.6692 | 71.6692 | 71.6692 | 71.6692 | 71.6692 | 71.6692 | 71.6692 | 71.6692 |  | 458.782 | 868.8929 | 880.2097 | 868.0084 | 871.1463 | 893.5414 | 938.9274 | 1018.8574 | 1060.506 | 1090.6372 | 1136.2393 | 1194.4595 | 1264.8606 | 1301.7559 | 1289.7949 | 1302.8359 | 1302.8359 | 1302.8359 | 1302.8359 | 1302.8359 | 1302.8359 | 1302.8359 | 1302.8359 | 1302.8359 | 1302.8359 | 1302.8359 | 1302.8359 | 1302.8359 | 1302.8359 | 1302.8359
30% | [31 empty] | 3.5003 | 199.9764 | 209.3483 | 199.2523 | 201.8267 | 220.6429 | 261.1304 | 339.9291 | 384.6819 | 418.6009 | 472.3546 | 545.1319 | 639.1947 | 691.0757 | 674.0645 | 692.6208 | 692.6208 | 692.6208 | 692.6208 | 692.6208 | 692.6208 | 692.6208 | 692.6208 | 692.6208 | 692.6208 | 692.6208 | 692.6208 | 692.6208 | 692.6208 | 692.6208
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 14376.0875 | 18589.8496 | 19027.0063 | 18812.4517 | 19016.448 | 19100.402 | 19369.9964 | 19926.8305 | 20397.8067 | 20615.378 | 20421.4347 | 21237.0849 | 21367.0492 | 21213.2626 | 21521.8675 | 21680.9955 | 21680.9955 | 21680.9955 | 21680.9955 | 21680.9955 | 21680.9955 | 21680.9955 | 21680.9955 | 21680.9955 | 21680.9955 | 21680.9955 | 21680.9955 | 21680.9955 | 21680.9955 | 21680.9955 | E @ R (MWh) | 2899.7446 | 4117.569 | 4155.085 | 4114.6453 | 4125.0234 | 4199.5321 | 4352.8623 | 4630.3154 | 4778.5425 | 4887.3062 | 5054.3091 | 5271.6303 | 5540.4179 | 5683.8418 | 5637.1556 | 5688.0662 | 5688.0662 | 5688.0662 | 5688.0662 | 5688.0662 | 5688.0662 | 5688.0662 | 5688.0662 | 5688.0662 | 5688.0662 | 5688.0662 | 5688.0662 | 5688.0662 | 5688.0662 | 5688.0662
Option 6 Summer POE50 W E @ R (MWh) N 2 | 10063.2613 | 13012.8947 | 13318.9044 | 13168.7162 | 13311.5136 | 13370.2814 | 13558.9975 | 13948.7813 | 14278.4647 | 14430.7646 | 14295.0043 | 14865.9595 | 14956.9344 | 14849.2838 | 15065.3072 | 15176.6968 | 15176.6968 | 15176.6968 | 15176.6968 | 15176.6968 | 15176.6968 | 15176.6968 | 15176.6968 | 15176.6968 | 15176.6968 | 15176.6968 | 15176.6968 | 15176.6968 | 15176.6968 | 15176.6968 | Option 6 Summer POE10 W E @ R (MWh) N 2 | 869.9234 | 1235.2707 | 1246.5255 | 1234.3936 | 1237.507 | 1259.8596 | 1305.8587 | 1389.0946 | 1433.5627 | 1466.1918 | 1516.2927 | 1581.4891 | 1662.1254 | 1705.1525 | 1691.1467 | 1706.4199 | 1706.4199 | 1706.4199 | 1706.4199 | 1706.4199 | 1706.4199 | 1706.4199 | 1706.4199 | 1706.4199 | 1706.4199 | 1706.4199 | 1706.4199 | 1706.4199 | 1706.4199 | 1706.4199
Option 7 -
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | 6.2898 | 7.5099 | 7.6393 | 7.7992 | 8.0116 | 8.2129 | 8.5647 | 9.4496 | 9.9255 | 9.5783 | 10.6532 | 10.8469 | 10.9861 | 11.6424 | 11.7492 | 11.7492 | 11.7492 | 11.7492 | 11.7492 | 11.7492 | 11.7492 | 11.7492 | 11.7492 | 11.7492 | 11.7492 | 11.7492 | 11.7492 | 11.7492 | 11.7492 | 11.7492 |  | 7.4111 | 8.5749 | 8.6954 | 9.1114 | 9.1012 | 9.1927 | 9.5504 | 10.5781 | 11.0022 | 10.6008 | 11.7097 | 11.2441 | 11.6631 | 11.965 | 11.8409 | 11.8409 | 11.8409 | 11.8409 | 11.8409 | 11.8409 | 11.8409 | 11.8409 | 11.8409 | 11.8409 | 11.8409 | 11.8409 | 11.8409 | 11.8409 | 11.8409 | 11.8409
98% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
97% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
95% | 23.5194 | 28.2281 | 28.7274 | 29.3447 | 30.1642 | 30.9412 | 32.299 | 35.7139 | 37.5508 | 36.2107 | 40.3592 | 41.1067 | 41.6439 | 44.1765 | 44.5887 | 44.5887 | 44.5887 | 44.5887 | 44.5887 | 44.5887 | 44.5887 | 44.5887 | 44.5887 | 44.5887 | 44.5887 | 44.5887 | 44.5887 | 44.5887 | 44.5887 | 44.5887 |  | 27.8469 | 32.3383 | 32.8034 | 34.4086 | 34.3695 | 34.7225 | 36.103 | 40.0693 | 41.7061 | 40.1568 | 44.4365 | 42.6397 | 44.2565 | 45.4216 | 44.9429 | 44.9429 | 44.9429 | 44.9429 | 44.9429 | 44.9429 | 44.9429 | 44.9429 | 44.9429 | 44.9429 | 44.9429 | 44.9429 | 44.9429 | 44.9429 | 44.9429 | 44.9429
90% | 131.2778 | 158.4998 | 161.3863 | 164.9549 | 169.693 | 174.1847 | 182.0345 | 201.7773 | 212.3964 | 204.6495 | 228.6329 | 232.954 | 236.0601 | 250.7016 | 253.0848 | 253.0848 | 253.0848 | 253.0848 | 253.0848 | 253.0848 | 253.0848 | 253.0848 | 253.0848 | 253.0848 | 253.0848 | 253.0848 | 253.0848 | 253.0848 | 253.0848 | 253.0848 |  | 156.2962 | 182.262 | 184.951 | 194.2311 | 194.0049 | 196.0456 | 204.0267 | 226.9569 | 236.4193 | 227.4624 | 252.2049 | 241.8166 | 251.1639 | 257.8997 | 255.1323 | 255.1323 | 255.1323 | 255.1323 | 255.1323 | 255.1323 | 255.1323 | 255.1323 | 255.1323 | 255.1323 | 255.1323 | 255.1323 | 255.1323 | 255.1323 | 255.1323 | 255.1323
85% | 517.7326 | 631.4638 | 643.5236 | 658.433 | 678.2282 | 696.9946 | 729.7905 | 812.2744 | 856.6401 | 824.274 | 924.4749 | 942.5282 | 955.5054 | 1016.6765 | 1026.6333 | 1026.6333 | 1026.6333 | 1026.6333 | 1026.6333 | 1026.6333 | 1026.6333 | 1026.6333 | 1026.6333 | 1026.6333 | 1026.6333 | 1026.6333 | 1026.6333 | 1026.6333 | 1026.6333 | 1026.6333 |  | 622.2576 | 730.7409 | 741.9753 | 780.7468 | 779.8019 | 788.3275 | 821.6723 | 917.4729 | 957.006 | 919.5849 | 1022.9569 | 979.5557 | 1018.6078 | 1046.7495 | 1035.1875 | 1035.1875 | 1035.1875 | 1035.1875 | 1035.1875 | 1035.1875 | 1035.1875 | 1035.1875 | 1035.1875 | 1035.1875 | 1035.1875 | 1035.1875 | 1035.1875 | 1035.1875 | 1035.1875 | 1035.1875
80% | 765.156 | 945.2254 | 964.3195 | 987.9254 | 1019.2669 | 1048.9795 | 1100.9048 | 1231.5006 | 1301.7444 | 1250.4995 | 1409.1465 | 1437.7299 | 1458.2767 | 1555.1282 | 1570.8926 | 1570.8926 | 1570.8926 | 1570.8926 | 1570.8926 | 1570.8926 | 1570.8926 | 1570.8926 | 1570.8926 | 1570.8926 | 1570.8926 | 1570.8926 | 1570.8926 | 1570.8926 | 1570.8926 | 1570.8926 |  | 930.6493 | 1102.4097 | 1120.197 | 1181.5834 | 1180.0873 | 1193.5858 | 1246.3802 | 1398.0603 | 1460.6526 | 1401.4041 | 1565.0719 | 1496.3553 | 1558.1859 | 1602.7423 | 1584.4364 | 1584.4364 | 1584.4364 | 1584.4364 | 1584.4364 | 1584.4364 | 1584.4364 | 1584.4364 | 1584.4364 | 1584.4364 | 1584.4364 | 1584.4364 | 1584.4364 | 1584.4364 | 1584.4364 | 1584.4364
75% | 1299.5462 | 1632.1565 | 1667.4256 | 1711.0285 | 1768.9201 | 1823.803 | 1919.7155 | 2160.942 | 2290.6908 | 2196.0352 | 2489.0758 | 2541.8729 | 2579.8253 | 2758.7219 | 2787.8407 | 2787.8407 | 2787.8407 | 2787.8407 | 2787.8407 | 2787.8407 | 2787.8407 | 2787.8407 | 2787.8407 | 2787.8407 | 2787.8407 | 2787.8407 | 2787.8407 | 2787.8407 | 2787.8407 | 2787.8407 |  | 1605.2327 | 1922.4952 | 1955.3505 | 2068.7387 | 2065.9753 | 2090.9087 | 2188.4265 | 2468.5981 | 2584.2139 | 2474.7746 | 2777.0892 | 2650.1611 | 2764.3699 | 2846.6711 | 2812.8578 | 2812.8578 | 2812.8578 | 2812.8578 | 2812.8578 | 2812.8578 | 2812.8578 | 2812.8578 | 2812.8578 | 2812.8578 | 2812.8578 | 2812.8578 | 2812.8578 | 2812.8578 | 2812.8578 | 2812.8578
70% | 1904.5555 | 2445.9592 | 2503.3682 | 2574.3426 | 2668.5752 | 2757.9103 | 2914.0312 | 3306.6856 | 3517.8832 | 3363.8083 | 3840.8027 | 3926.7428 | 3988.5195 | 4279.7169 | 4327.1149 | 4327.1149 | 4327.1149 | 4327.1149 | 4327.1149 | 4327.1149 | 4327.1149 | 4327.1149 | 4327.1149 | 4327.1149 | 4327.1149 | 4327.1149 | 4327.1149 | 4327.1149 | 4327.1149 | 4327.1149 |  | 2402.1342 | 2918.5558 | 2972.0357 | 3156.6025 | 3152.1043 | 3192.6894 | 3351.4232 | 3807.4704 | 3995.6629 | 3817.524 | 4309.6142 | 4103.0081 | 4288.9105 | 4422.8756 | 4367.8364 | 4367.8364 | 4367.8364 | 4367.8364 | 4367.8364 | 4367.8364 | 4367.8364 | 4367.8364 | 4367.8364 | 4367.8364 | 4367.8364 | 4367.8364 | 4367.8364 | 4367.8364 | 4367.8364 | 4367.8364
65% | 2035.9088 | 2698.8915 | 2769.1924 | 2856.1049 | 2971.4986 | 3080.895 | 3272.0749 | 3752.9047 | 4011.5294 | 3822.8551 | 4406.9646 | 4512.2036 | 4587.8531 | 4944.4426 | 5002.4844 | 5002.4844 | 5002.4844 | 5002.4844 | 5002.4844 | 5002.4844 | 5002.4844 | 5002.4844 | 5002.4844 | 5002.4844 | 5002.4844 | 5002.4844 | 5002.4844 | 5002.4844 | 5002.4844 | 5002.4844 |  | 2645.225 | 3277.6155 | 3343.1051 | 3569.1186 | 3563.6103 | 3613.3093 | 3807.6888 | 4366.1471 | 4596.6007 | 4378.4584 | 4981.0536 | 4728.0515 | 4955.7006 | 5119.7493 | 5052.3503 | 5052.3503 | 5052.3503 | 5052.3503 | 5052.3503 | 5052.3503 | 5052.3503 | 5052.3503 | 5052.3503 | 5052.3503 | 5052.3503 | 5052.3503 | 5052.3503 | 5052.3503 | 5052.3503 | 5052.3503
60% | 2098.8616 | 2921.1907 | 3008.3883 | 3116.1901 | 3259.3184 | 3395.008 | 3632.1374 | 4228.5337 | 4549.3182 | 4315.2964 | 5039.7953 | 5170.3283 | 5264.16 | 5706.4549 | 5778.4469 | 5778.4469 | 5778.4469 | 5778.4469 | 5778.4469 | 5778.4469 | 5778.4469 | 5778.4469 | 5778.4469 | 5778.4469 | 5778.4469 | 5778.4469 | 5778.4469 | 5778.4469 | 5778.4469 | 5778.4469 |  | 2854.6256 | 3639.0098 | 3720.2396 | 4000.575 | 3993.7428 | 4055.3868 | 4296.485 | 4989.1674 | 5275.01 | 5004.4378 | 5751.8653 | 5438.0548 | 5720.4188 | 5923.8962 | 5840.298 | 5840.298 | 5840.298 | 5840.298 | 5840.298 | 5840.298 | 5840.298 | 5840.298 | 5840.298 | 5840.298 | 5840.298 | 5840.298 | 5840.298 | 5840.298 | 5840.298 | 5840.298
55% | 1733.592 | 2625.5087 | 2720.0851 | 2837.0093 | 2992.2496 | 3139.4215 | 3396.6175 | 4043.4823 | 4391.4125 | 4137.5871 | 4923.395 | 5064.974 | 5166.746 | 5646.469 | 5724.5532 | 5724.5532 | 5724.5532 | 5724.5532 | 5724.5532 | 5724.5532 | 5724.5532 | 5724.5532 | 5724.5532 | 5724.5532 | 5724.5532 | 5724.5532 | 5724.5532 | 5724.5532 | 5724.5532 | 5724.5532 |  | 2553.3107 | 3404.0714 | 3492.1751 | 3796.2332 | 3788.8228 | 3855.6833 | 4117.1838 | 4868.4828 | 5178.5141 | 4885.0454 | 5695.7222 | 5355.3561 | 5661.6146 | 5882.3107 | 5791.6383 | 5791.6383 | 5791.6383 | 5791.6383 | 5791.6383 | 5791.6383 | 5791.6383 | 5791.6383 | 5791.6383 | 5791.6383 | 5791.6383 | 5791.6383 | 5791.6383 | 5791.6383 | 5791.6383 | 5791.6383
50% | 1107.3363 | 2015.6842 | 2112.003 | 2231.0812 | 2389.1813 | 2539.0646 | 2800.9987 | 3459.7803 | 3814.1202 | 3555.6188 | 4355.9031 | 4500.0904 | 4603.7372 | 5092.2979 | 5171.8205 | 5171.8205 | 5171.8205 | 5171.8205 | 5171.8205 | 5171.8205 | 5171.8205 | 5171.8205 | 5171.8205 | 5171.8205 | 5171.8205 | 5171.8205 | 5171.8205 | 5171.8205 | 5171.8205 | 5171.8205 |  | 1942.1561 | 2808.5899 | 2898.3167 | 3207.9763 | 3200.4293 | 3268.5216 | 3534.8396 | 4299.9793 | 4615.7221 | 4316.847 | 5142.4584 | 4795.822 | 5107.7225 | 5332.4844 | 5240.1415 | 5240.1415 | 5240.1415 | 5240.1415 | 5240.1415 | 5240.1415 | 5240.1415 | 5240.1415 | 5240.1415 | 5240.1415 | 5240.1415 | 5240.1415 | 5240.1415 | 5240.1415 | 5240.1415 | 5240.1415
45% | 304.3799 | 1151.2957 | 1242.2705 | 1354.742 | 1504.0703 | 1645.6377 | 1893.0391 | 2515.2699 | 2849.9501 | 2605.791 | 3361.6736 | 3497.861 | 3595.7573 | 4057.2114 | 4132.3219 | 4132.3219 | 4132.3219 | 4132.3219 | 4132.3219 | 4132.3219 | 4132.3219 | 4132.3219 | 4132.3219 | 4132.3219 | 4132.3219 | 4132.3219 | 4132.3219 | 4132.3219 | 4132.3219 | 4132.3219 |  | 1081.8472 | 1900.2091 | 1984.9576 | 2277.4365 | 2270.3083 | 2334.6226 | 2586.1647 | 3308.8526 | 3607.0772 | 3324.7844 | 4104.5889 | 3777.1848 | 4071.7802 | 4284.0718 | 4196.8523 | 4196.8523 | 4196.8523 | 4196.8523 | 4196.8523 | 4196.8523 | 4196.8523 | 4196.8523 | 4196.8523 | 4196.8523 | 4196.8523 | 4196.8523 | 4196.8523 | 4196.8523 | 4196.8523 | 4196.8523
40% |  | 241.0368 | 303.4886 | 389.6318 | 518.5137 | 646.2971 | 869.6099 | 1431.2562 | 1733.3497 | 1512.9635 | 2195.2484 | 2318.1757 | 2406.5401 | 2823.064 | 2890.8613 | 2890.8613 | 2890.8613 | 2890.8613 | 2890.8613 | 2890.8613 | 2890.8613 | 2890.8613 | 2890.8613 | 2890.8613 | 2890.8613 | 2890.8613 | 2890.8613 | 2890.8613 | 2890.8613 | 2890.8613 |  | 197.8445 | 876.0818 | 952.5787 | 1216.5798 | 1210.1457 | 1268.1979 | 1495.2482 | 2147.5704 | 2416.7579 | 2161.951 | 2865.8286 | 2570.3026 | 2836.2143 | 3027.8357 | 2949.1086 | 2949.1086 | 2949.1086 | 2949.1086 | 2949.1086 | 2949.1086 | 2949.1086 | 2949.1086 | 2949.1086 | 2949.1086 | 2949.1086 | 2949.1086 | 2949.1086 | 2949.1086 | 2949.1086 | 2949.1086
35% |  |  |  |  | 0.16059 | 8.4247 | 51.6577 | 306.5672 | 520.3346 | 359.4876 | 878.7989 | 974.1987 | 1042.7754 | 1366.0258 | 1418.641 | 1418.641 | 1418.641 | 1418.641 | 1418.641 | 1418.641 | 1418.641 | 1418.641 | 1418.641 | 1418.641 | 1418.641 | 1418.641 | 1418.641 | 1418.641 | 1418.641 | 1418.641 |  |  | 53.4346 | 76.5978 | 185.9699 | 182.7815 | 212.4625 | 347.6947 | 841.7976 | 1050.7051 | 852.9579 | 1399.2139 | 1169.866 | 1376.2313 | 1524.9423 | 1463.8448 | 1463.8448 | 1463.8448 | 1463.8448 | 1463.8448 | 1463.8448 | 1463.8448 | 1463.8448 | 1463.8448 | 1463.8448 | 1463.8448 | 1463.8448 | 1463.8448 | 1463.8448 | 1463.8448 | 1463.8448
30% | [8 empty] | 0.13247 |  | 47.3865 | 73.4365 | 95.4345 | 233.8409 | 261.5037 | 261.5037 | 261.5037 | 261.5037 | 261.5037 | 261.5037 | 261.5037 | 261.5037 | 261.5037 | 261.5037 | 261.5037 | 261.5037 | 261.5037 | 261.5037 | 261.5037 | 261.5037 | [8 empty] | 38.745 | 98.151 | 41.2641 | 251.1294 | 143.1816 | 239.0986 | 321.5304 | 286.3608 | 286.3608 | 286.3608 | 286.3608 | 286.3608 | 286.3608 | 286.3608 | 286.3608 | 286.3608 | 286.3608 | 286.3608 | 286.3608 | 286.3608 | 286.3608 | 286.3608 | 286.3608
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 11808.8744 | 17327.6237 | 17950.4997 | 18729.4017 | 19778.0731 | 20785.8168 | 22575.4407 | 27221.1763 | 29796.0085 | 27912.7082 | 33810.7876 | 34892.5992 | 35673.4826 | 39388.7046 | 39998.5117 | 39998.5117 | 39998.5117 | 39998.5117 | 39998.5117 | 39998.5117 | 39998.5117 | 39998.5117 | 39998.5117 | 39998.5117 | 39998.5117 | 39998.5117 | 39998.5117 | 39998.5117 | 39998.5117 | 39998.5117 | E @ R (MWh) | 16856.5689 | 22627.8251 | 23249.1394 | 25422.5188 | 25369.0323 | 25852.5194 | 27762.4582 | 33392.6489 | 35763.9491 | 33518.6811 | 39773.1943 | 37127.5741 | 39506.8788 | 41234.634 | 40523.5006 | 40523.5006 | 40523.5006 | 40523.5006 | 40523.5006 | 40523.5006 | 40523.5006 | 40523.5006 | 40523.5006 | 40523.5006 | 40523.5006 | 40523.5006 | 40523.5006 | 40523.5006 | 40523.5006 | 40523.5006
Option 7 Winter POE50 W E @ R (MWh) N 2 | 8266.2121 | 12129.3366 | 12565.3498 | 13110.5812 | 13844.6511 | 14550.0718 | 15802.8085 | 19054.8234 | 20857.206 | 19538.8958 | 23667.5513 | 24424.8194 | 24971.4378 | 27572.0932 | 27998.9582 | 27998.9582 | 27998.9582 | 27998.9582 | 27998.9582 | 27998.9582 | 27998.9582 | 27998.9582 | 27998.9582 | 27998.9582 | 27998.9582 | 27998.9582 | 27998.9582 | 27998.9582 | 27998.9582 | 27998.9582 | Option 7 Winter POE10 W E @ R (MWh) N 2 | 5056.9707 | 6788.3475 | 6974.7418 | 7626.7556 | 7610.7097 | 7755.7558 | 8328.7375 | 10017.7947 | 10729.1847 | 10055.6043 | 11931.9583 | 11138.2722 | 11852.0637 | 12370.3902 | 12157.0502 | 12157.0502 | 12157.0502 | 12157.0502 | 12157.0502 | 12157.0502 | 12157.0502 | 12157.0502 | 12157.0502 | 12157.0502 | 12157.0502 | 12157.0502 | 12157.0502 | 12157.0502 | 12157.0502 | 12157.0502
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | 8.9039 | 10.0686 | 10.1857 | 10.1283 | 10.1828 | 10.2053 | 10.2771 | 10.4248 | 10.549 | 10.6062 | 10.5553 | 10.769 | 10.8029 | 10.7628 | 10.8432 | 10.8846 | 10.8846 | 10.8846 | 10.8846 | 10.8846 | 10.8846 | 10.8846 | 10.8846 | 10.8846 | 10.8846 | 10.8846 | 10.8846 | 10.8846 | 10.8846 | 10.8846 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
98% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
97% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 12.1062 | 13.3817 | 13.4169 | 13.3789 | 13.3887 | 13.4583 | 13.5995 | 13.8481 | 13.9776 | 14.0713 | 14.2131 | 14.3942 | 14.6131 | 14.7279 | 14.6907 | 14.7312 | 14.7312 | 14.7312 | 14.7312 | 14.7312 | 14.7312 | 14.7312 | 14.7312 | 14.7312 | 14.7312 | 14.7312 | 14.7312 | 14.7312 | 14.7312 | 14.7312
95% | 8.3559 | 9.4797 | 9.5926 | 9.5372 | 9.5899 | 9.6115 | 9.6808 | 9.8233 | 9.9432 | 9.9984 | 9.9492 | 10.1554 | 10.1881 | 10.1494 | 10.227 | 10.267 | 10.267 | 10.267 | 10.267 | 10.267 | 10.267 | 10.267 | 10.267 | 10.267 | 10.267 | 10.267 | 10.267 | 10.267 | 10.267 | 10.267 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
90% | 171.7748 | 195.5955 | 197.9892 | 196.8158 | 197.9315 | 198.3899 | 199.8591 | 202.88 | 205.4214 | 206.5912 | 205.5485 | 209.9202 | 210.6135 | 209.793 | 211.4383 | 212.2848 | 212.2848 | 212.2848 | 212.2848 | 212.2848 | 212.2848 | 212.2848 | 212.2848 | 212.2848 | 212.2848 | 212.2848 | 212.2848 | 212.2848 | 212.2848 | 212.2848 |  | 11.1431 | 12.3531 | 12.3865 | 12.3505 | 12.3598 | 12.4259 | 12.5598 | 12.7956 | 12.9185 | 13.0074 | 13.142 | 13.3137 | 13.5215 | 13.6303 | 13.595 | 13.6335 | 13.6335 | 13.6335 | 13.6335 | 13.6335 | 13.6335 | 13.6335 | 13.6335 | 13.6335 | 13.6335 | 13.6335 | 13.6335 | 13.6335 | 13.6335 | 13.6335
85% | 583.0836 | 668.0948 | 676.6375 | 672.4501 | 676.4317 | 678.0677 | 683.3108 | 694.0919 | 703.1615 | 707.3365 | 703.6153 | 719.2167 | 721.6911 | 718.7628 | 724.6348 | 727.6558 | 727.6558 | 727.6558 | 727.6558 | 727.6558 | 727.6558 | 727.6558 | 727.6558 | 727.6558 | 727.6558 | 727.6558 | 727.6558 | 727.6558 | 727.6558 | 727.6558 |  | 10.18 | 11.3246 | 11.3562 | 11.3221 | 11.3309 | 11.3934 | 11.5201 | 11.7432 | 11.8594 | 11.9435 | 12.0708 | 12.2333 | 12.4298 | 12.5328 | 12.4994 | 12.5358 | 12.5358 | 12.5358 | 12.5358 | 12.5358 | 12.5358 | 12.5358 | 12.5358 | 12.5358 | 12.5358 | 12.5358 | 12.5358 | 12.5358 | 12.5358 | 12.5358
80% | 892.6437 | 1030.7394 | 1044.6165 | 1037.8142 | 1044.2821 | 1046.9396 | 1055.4569 | 1072.9701 | 1087.703 | 1094.485 | 1088.4403 | 1113.7838 | 1117.8034 | 1113.0465 | 1122.5851 | 1127.4926 | 1127.4926 | 1127.4926 | 1127.4926 | 1127.4926 | 1127.4926 | 1127.4926 | 1127.4926 | 1127.4926 | 1127.4926 | 1127.4926 | 1127.4926 | 1127.4926 | 1127.4926 | 1127.4926 |  | 36.8674 | 41.1843 | 41.3034 | 41.175 | 41.208 | 41.4438 | 41.9215 | 42.7629 | 43.2013 | 43.5185 | 43.9985 | 44.6113 | 45.3524 | 45.7408 | 45.6149 | 45.7521 | 45.7521 | 45.7521 | 45.7521 | 45.7521 | 45.7521 | 45.7521 | 45.7521 | 45.7521 | 45.7521 | 45.7521 | 45.7521 | 45.7521 | 45.7521 | 45.7521
75% | 1479.5037 | 1725.3485 | 1750.0533 | 1737.9436 | 1749.458 | 1754.1891 | 1769.3519 | 1800.5298 | 1826.7581 | 1838.8318 | 1828.0706 | 1873.1885 | 1880.3443 | 1871.8759 | 1888.857 | 1897.5936 | 1897.5936 | 1897.5936 | 1897.5936 | 1897.5936 | 1897.5936 | 1897.5936 | 1897.5936 | 1897.5936 | 1897.5936 | 1897.5936 | 1897.5936 | 1897.5936 | 1897.5936 | 1897.5936 |  | 16.5074 | 18.5351 | 18.5911 | 18.5307 | 18.5462 | 18.657 | 18.8814 | 19.2766 | 19.4825 | 19.6315 | 19.8569 | 20.1448 | 20.4928 | 20.6753 | 20.6161 | 20.6806 | 20.6806 | 20.6806 | 20.6806 | 20.6806 | 20.6806 | 20.6806 | 20.6806 | 20.6806 | 20.6806 | 20.6806 | 20.6806 | 20.6806 | 20.6806 | 20.6806
70% | 1730.3357 | 2044.3359 | 2075.8895 | 2060.4227 | 2075.1292 | 2081.1719 | 2100.5382 | 2140.3596 | 2173.8591 | 2189.28 | 2175.5354 | 2233.1613 | 2242.3009 | 2231.4848 | 2253.1735 | 2264.3322 | 2264.3322 | 2264.3322 | 2264.3322 | 2264.3322 | 2264.3322 | 2264.3322 | 2264.3322 | 2264.3322 | 2264.3322 | 2264.3322 | 2264.3322 | 2264.3322 | 2264.3322 | 2264.3322 |  | 43.7436 | 49.4342 | 49.5912 | 49.4219 | 49.4654 | 49.7762 | 50.4059 | 51.515 | 52.0929 | 52.511 | 53.1438 | 53.9516 | 54.9285 | 55.4404 | 55.2744 | 55.4554 | 55.4554 | 55.4554 | 55.4554 | 55.4554 | 55.4554 | 55.4554 | 55.4554 | 55.4554 | 55.4554 | 55.4554 | 55.4554 | 55.4554 | 55.4554 | 55.4554
65% | 1900.1465 | 2285.7258 | 2324.4723 | 2305.4797 | 2323.5388 | 2330.9589 | 2354.74 | 2403.639 | 2444.775 | 2463.7113 | 2446.8335 | 2517.5958 | 2528.8188 | 2515.5371 | 2542.1699 | 2555.8723 | 2555.8723 | 2555.8723 | 2555.8723 | 2555.8723 | 2555.8723 | 2555.8723 | 2555.8723 | 2555.8723 | 2555.8723 | 2555.8723 | 2555.8723 | 2555.8723 | 2555.8723 | 2555.8723 |  | 12.655 | 14.421 | 14.4697 | 14.4172 | 14.4307 | 14.5271 | 14.7226 | 15.0668 | 15.2461 | 15.3759 | 15.5723 | 15.823 | 16.1261 | 16.285 | 16.2335 | 16.2897 | 16.2897 | 16.2897 | 16.2897 | 16.2897 | 16.2897 | 16.2897 | 16.2897 | 16.2897 | 16.2897 | 16.2897 | 16.2897 | 16.2897 | 16.2897 | 16.2897
60% | 2395.395 | 2958.7224 | 3015.3307 | 2987.5827 | 3013.9668 | 3024.8076 | 3059.5514 | 3130.9924 | 3191.0917 | 3218.7573 | 3194.0991 | 3297.482 | 3313.8788 | 3294.4743 | 3333.3846 | 3353.4037 | 3353.4037 | 3353.4037 | 3353.4037 | 3353.4037 | 3353.4037 | 3353.4037 | 3353.4037 | 3353.4037 | 3353.4037 | 3353.4037 | 3353.4037 | 3353.4037 | 3353.4037 | 3353.4037 |  | 69.7368 | 80.3657 | 80.659 | 80.3428 | 80.4241 | 81.0045 | 82.1808 | 84.2523 | 85.3317 | 86.1126 | 87.2945 | 88.8034 | 90.628 | 91.5842 | 91.2742 | 91.6122 | 91.6122 | 91.6122 | 91.6122 | 91.6122 | 91.6122 | 91.6122 | 91.6122 | 91.6122 | 91.6122 | 91.6122 | 91.6122 | 91.6122 | 91.6122 | 91.6122
55% | 2397.9043 | 3091.1628 | 3160.8278 | 3126.6797 | 3159.1493 | 3172.4904 | 3215.248 | 3303.1668 | 3377.1279 | 3411.1746 | 3380.829 | 3508.0571 | 3528.2358 | 3504.3556 | 3552.2406 | 3576.8771 | 3576.8771 | 3576.8771 | 3576.8771 | 3576.8771 | 3576.8771 | 3576.8771 | 3576.8771 | 3576.8771 | 3576.8771 | 3576.8771 | 3576.8771 | 3576.8771 | 3576.8771 | 3576.8771 |  | 281.6802 | 329.8208 | 331.1492 | 329.717 | 330.0853 | 332.7141 | 338.0417 | 347.4243 | 352.3132 | 355.8501 | 361.2031 | 368.0372 | 376.3012 | 380.6321 | 379.2281 | 380.7589 | 380.7589 | 380.7589 | 380.7589 | 380.7589 | 380.7589 | 380.7589 | 380.7589 | 380.7589 | 380.7589 | 380.7589 | 380.7589 | 380.7589 | 380.7589 | 380.7589
50% | 1977.8845 | 2764.4944 | 2843.5402 | 2804.7939 | 2841.6356 | 2856.7733 | 2905.2884 | 3005.046 | 3088.9664 | 3127.5977 | 3093.1659 | 3237.526 | 3260.4218 | 3233.3261 | 3287.6591 | 3315.613 | 3315.613 | 3315.613 | 3315.613 | 3315.613 | 3315.613 | 3315.613 | 3315.613 | 3315.613 | 3315.613 | 3315.613 | 3315.613 | 3315.613 | 3315.613 | 3315.613 |  | 543.2253 | 651.7379 | 654.7323 | 651.5039 | 652.3342 | 658.2598 | 670.2686 | 691.4175 | 702.4375 | 710.41 | 722.476 | 737.8807 | 756.5083 | 766.2706 | 763.1058 | 766.5564 | 766.5564 | 766.5564 | 766.5564 | 766.5564 | 766.5564 | 766.5564 | 766.5564 | 766.5564 | 766.5564 | 766.5564 | 766.5564 | 766.5564 | 766.5564 | 766.5564
45% | 892.7494 | 1543.8389 | 1609.2663 | 1577.1954 | 1607.6899 | 1620.2195 | 1660.3762 | 1742.9472 | 1812.4095 | 1844.3852 | 1815.8854 | 1935.3746 | 1954.3258 | 1931.8982 | 1976.8705 | 2000.0084 | 2000.0084 | 2000.0084 | 2000.0084 | 2000.0084 | 2000.0084 | 2000.0084 | 2000.0084 | 2000.0084 | 2000.0084 | 2000.0084 | 2000.0084 | 2000.0084 | 2000.0084 | 2000.0084 |  | 742.5052 | 928.9193 | 934.0633 | 928.5173 | 929.9435 | 940.1232 | 960.7531 | 997.085 | 1016.0161 | 1029.7122 | 1050.4404 | 1076.9041 | 1108.9046 | 1125.6752 | 1120.2384 | 1126.1661 | 1126.1661 | 1126.1661 | 1126.1661 | 1126.1661 | 1126.1661 | 1126.1661 | 1126.1661 | 1126.1661 | 1126.1661 | 1126.1661 | 1126.1661 | 1126.1661 | 1126.1661 | 1126.1661
40% | 82.6197 | 448.4043 | 495.3965 | 472.3621 | 494.2643 | 503.2635 | 532.1055 | 591.4108 | 641.301 | 664.267 | 643.7975 | 729.6188 | 743.2302 | 727.122 | 759.4226 | 776.041 | 776.041 | 776.041 | 776.041 | 776.041 | 776.041 | 776.041 | 776.041 | 776.041 | 776.041 | 776.041 | 776.041 | 776.041 | 776.041 | 776.041 |  | 686.4025 | 938.8137 | 945.7788 | 938.2693 | 940.2006 | 953.9841 | 981.9179 | 1031.1125 | 1056.7459 | 1075.2908 | 1103.3575 | 1139.1903 | 1182.5201 | 1205.2281 | 1197.8665 | 1205.8928 | 1205.8928 | 1205.8928 | 1205.8928 | 1205.8928 | 1205.8928 | 1205.8928 | 1205.8928 | 1205.8928 | 1205.8928 | 1205.8928 | 1205.8928 | 1205.8928 | 1205.8928 | 1205.8928
35% |  | 1.6148 | 5.4003 | 3.2709 | 5.2834 | 6.2472 | 9.8686 | 19.8299 | 30.7782 | 36.5919 | 31.3867 | 55.7517 | 60.2225 | 54.9494 | 65.7537 | 71.6692 | 71.6692 | 71.6692 | 71.6692 | 71.6692 | 71.6692 | 71.6692 | 71.6692 | 71.6692 | 71.6692 | 71.6692 | 71.6692 | 71.6692 | 71.6692 | 71.6692 |  | 458.782 | 868.8929 | 880.2097 | 868.0084 | 871.1463 | 893.5414 | 938.9274 | 1018.8574 | 1060.506 | 1090.6372 | 1136.2393 | 1194.4595 | 1264.8606 | 1301.7559 | 1289.7949 | 1302.8359 | 1302.8359 | 1302.8359 | 1302.8359 | 1302.8359 | 1302.8359 | 1302.8359 | 1302.8359 | 1302.8359 | 1302.8359 | 1302.8359 | 1302.8359 | 1302.8359 | 1302.8359 | 1302.8359
30% | [31 empty] | 3.5003 | 199.9764 | 209.3483 | 199.2523 | 201.8267 | 220.6429 | 261.1304 | 339.9291 | 384.6819 | 418.6009 | 472.3546 | 545.1319 | 639.1947 | 691.0757 | 674.0645 | 692.6208 | 692.6208 | 692.6208 | 692.6208 | 692.6208 | 692.6208 | 692.6208 | 692.6208 | 692.6208 | 692.6208 | 692.6208 | 692.6208 | 692.6208 | 692.6208 | 692.6208
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 14376.0875 | 18589.8496 | 19027.0063 | 18812.4517 | 19016.448 | 19100.402 | 19369.9964 | 19926.8305 | 20397.8067 | 20615.378 | 20421.4347 | 21237.0849 | 21367.0492 | 21213.2626 | 21521.8675 | 21680.9955 | 21680.9955 | 21680.9955 | 21680.9955 | 21680.9955 | 21680.9955 | 21680.9955 | 21680.9955 | 21680.9955 | 21680.9955 | 21680.9955 | 21680.9955 | 21680.9955 | 21680.9955 | 21680.9955 | E @ R (MWh) | 2899.7446 | 4117.569 | 4155.085 | 4114.6453 | 4125.0234 | 4199.5321 | 4352.8623 | 4630.3154 | 4778.5425 | 4887.3062 | 5054.3091 | 5271.6303 | 5540.4179 | 5683.8418 | 5637.1556 | 5688.0662 | 5688.0662 | 5688.0662 | 5688.0662 | 5688.0662 | 5688.0662 | 5688.0662 | 5688.0662 | 5688.0662 | 5688.0662 | 5688.0662 | 5688.0662 | 5688.0662 | 5688.0662 | 5688.0662
Option 7 Summer POE50 W E @ R (MWh) N 2 | 10063.2613 | 13012.8947 | 13318.9044 | 13168.7162 | 13311.5136 | 13370.2814 | 13558.9975 | 13948.7813 | 14278.4647 | 14430.7646 | 14295.0043 | 14865.9595 | 14956.9344 | 14849.2838 | 15065.3072 | 15176.6968 | 15176.6968 | 15176.6968 | 15176.6968 | 15176.6968 | 15176.6968 | 15176.6968 | 15176.6968 | 15176.6968 | 15176.6968 | 15176.6968 | 15176.6968 | 15176.6968 | 15176.6968 | 15176.6968 | Option 7 Summer POE10 W E @ R (MWh) N 2 | 869.9234 | 1235.2707 | 1246.5255 | 1234.3936 | 1237.507 | 1259.8596 | 1305.8587 | 1389.0946 | 1433.5627 | 1466.1918 | 1516.2927 | 1581.4891 | 1662.1254 | 1705.1525 | 1691.1467 | 1706.4199 | 1706.4199 | 1706.4199 | 1706.4199 | 1706.4199 | 1706.4199 | 1706.4199 | 1706.4199 | 1706.4199 | 1706.4199 | 1706.4199 | 1706.4199 | 1706.4199 | 1706.4199 | 1706.4199
Option 8 -
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | 6.2898 | 7.5099 | 7.6393 | 7.7992 | 8.0116 | 8.2129 | 8.5647 | 9.4496 | 9.9255 | 9.5783 | 10.6532 | 10.8469 | 10.9861 | 11.6424 | 11.7492 | 11.7492 | 11.7492 | 11.7492 | 11.7492 | 11.7492 | 11.7492 | 11.7492 | 11.7492 | 11.7492 | 11.7492 | 11.7492 | 11.7492 | 11.7492 | 11.7492 | 11.7492 |  | 7.4111 | 8.5749 | 8.6954 | 9.1114 | 9.1012 | 9.1927 | 9.5504 | 10.5781 | 11.0022 | 10.6008 | 11.7097 | 11.2441 | 11.6631 | 11.965 | 11.8409 | 11.8409 | 11.8409 | 11.8409 | 11.8409 | 11.8409 | 11.8409 | 11.8409 | 11.8409 | 11.8409 | 11.8409 | 11.8409 | 11.8409 | 11.8409 | 11.8409 | 11.8409
98% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
97% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
95% | 23.5194 | 28.2281 | 28.7274 | 29.3447 | 30.1642 | 30.9412 | 32.299 | 35.7139 | 37.5508 | 36.2107 | 40.3592 | 41.1067 | 41.6439 | 44.1765 | 44.5887 | 44.5887 | 44.5887 | 44.5887 | 44.5887 | 44.5887 | 44.5887 | 44.5887 | 44.5887 | 44.5887 | 44.5887 | 44.5887 | 44.5887 | 44.5887 | 44.5887 | 44.5887 |  | 27.8469 | 32.3383 | 32.8034 | 34.4086 | 34.3695 | 34.7225 | 36.103 | 40.0693 | 41.7061 | 40.1568 | 44.4365 | 42.6397 | 44.2565 | 45.4216 | 44.9429 | 44.9429 | 44.9429 | 44.9429 | 44.9429 | 44.9429 | 44.9429 | 44.9429 | 44.9429 | 44.9429 | 44.9429 | 44.9429 | 44.9429 | 44.9429 | 44.9429 | 44.9429
90% | 131.2778 | 158.4998 | 161.3863 | 164.9549 | 169.693 | 174.1847 | 182.0345 | 201.7773 | 212.3964 | 204.6495 | 228.6329 | 232.954 | 236.0601 | 250.7016 | 253.0848 | 253.0848 | 253.0848 | 253.0848 | 253.0848 | 253.0848 | 253.0848 | 253.0848 | 253.0848 | 253.0848 | 253.0848 | 253.0848 | 253.0848 | 253.0848 | 253.0848 | 253.0848 |  | 156.2962 | 182.262 | 184.951 | 194.2311 | 194.0049 | 196.0456 | 204.0267 | 226.9569 | 236.4193 | 227.4624 | 252.2049 | 241.8166 | 251.1639 | 257.8997 | 255.1323 | 255.1323 | 255.1323 | 255.1323 | 255.1323 | 255.1323 | 255.1323 | 255.1323 | 255.1323 | 255.1323 | 255.1323 | 255.1323 | 255.1323 | 255.1323 | 255.1323 | 255.1323
85% | 517.7326 | 631.4638 | 643.5236 | 658.433 | 678.2282 | 696.9946 | 729.7905 | 812.2744 | 856.6401 | 824.274 | 924.4749 | 942.5282 | 955.5054 | 1016.6765 | 1026.6333 | 1026.6333 | 1026.6333 | 1026.6333 | 1026.6333 | 1026.6333 | 1026.6333 | 1026.6333 | 1026.6333 | 1026.6333 | 1026.6333 | 1026.6333 | 1026.6333 | 1026.6333 | 1026.6333 | 1026.6333 |  | 622.2576 | 730.7409 | 741.9753 | 780.7468 | 779.8019 | 788.3275 | 821.6723 | 917.4729 | 957.006 | 919.5849 | 1022.9569 | 979.5557 | 1018.6078 | 1046.7495 | 1035.1875 | 1035.1875 | 1035.1875 | 1035.1875 | 1035.1875 | 1035.1875 | 1035.1875 | 1035.1875 | 1035.1875 | 1035.1875 | 1035.1875 | 1035.1875 | 1035.1875 | 1035.1875 | 1035.1875 | 1035.1875
80% | 765.156 | 945.2254 | 964.3195 | 987.9254 | 1019.2669 | 1048.9795 | 1100.9048 | 1231.5006 | 1301.7444 | 1250.4995 | 1409.1465 | 1437.7299 | 1458.2767 | 1555.1282 | 1570.8926 | 1570.8926 | 1570.8926 | 1570.8926 | 1570.8926 | 1570.8926 | 1570.8926 | 1570.8926 | 1570.8926 | 1570.8926 | 1570.8926 | 1570.8926 | 1570.8926 | 1570.8926 | 1570.8926 | 1570.8926 |  | 930.6493 | 1102.4097 | 1120.197 | 1181.5834 | 1180.0873 | 1193.5858 | 1246.3802 | 1398.0603 | 1460.6526 | 1401.4041 | 1565.0719 | 1496.3553 | 1558.1859 | 1602.7423 | 1584.4364 | 1584.4364 | 1584.4364 | 1584.4364 | 1584.4364 | 1584.4364 | 1584.4364 | 1584.4364 | 1584.4364 | 1584.4364 | 1584.4364 | 1584.4364 | 1584.4364 | 1584.4364 | 1584.4364 | 1584.4364
75% | 1299.5462 | 1632.1565 | 1667.4256 | 1711.0285 | 1768.9201 | 1823.803 | 1919.7155 | 2160.942 | 2290.6908 | 2196.0352 | 2489.0758 | 2541.8729 | 2579.8253 | 2758.7219 | 2787.8407 | 2787.8407 | 2787.8407 | 2787.8407 | 2787.8407 | 2787.8407 | 2787.8407 | 2787.8407 | 2787.8407 | 2787.8407 | 2787.8407 | 2787.8407 | 2787.8407 | 2787.8407 | 2787.8407 | 2787.8407 |  | 1605.2327 | 1922.4952 | 1955.3505 | 2068.7387 | 2065.9753 | 2090.9087 | 2188.4265 | 2468.5981 | 2584.2139 | 2474.7746 | 2777.0892 | 2650.1611 | 2764.3699 | 2846.6711 | 2812.8578 | 2812.8578 | 2812.8578 | 2812.8578 | 2812.8578 | 2812.8578 | 2812.8578 | 2812.8578 | 2812.8578 | 2812.8578 | 2812.8578 | 2812.8578 | 2812.8578 | 2812.8578 | 2812.8578 | 2812.8578
70% | 1904.5555 | 2445.9592 | 2503.3682 | 2574.3426 | 2668.5752 | 2757.9103 | 2914.0312 | 3306.6856 | 3517.8832 | 3363.8083 | 3840.8027 | 3926.7428 | 3988.5195 | 4279.7169 | 4327.1149 | 4327.1149 | 4327.1149 | 4327.1149 | 4327.1149 | 4327.1149 | 4327.1149 | 4327.1149 | 4327.1149 | 4327.1149 | 4327.1149 | 4327.1149 | 4327.1149 | 4327.1149 | 4327.1149 | 4327.1149 |  | 2402.1342 | 2918.5558 | 2972.0357 | 3156.6025 | 3152.1043 | 3192.6894 | 3351.4232 | 3807.4704 | 3995.6629 | 3817.524 | 4309.6142 | 4103.0081 | 4288.9105 | 4422.8756 | 4367.8364 | 4367.8364 | 4367.8364 | 4367.8364 | 4367.8364 | 4367.8364 | 4367.8364 | 4367.8364 | 4367.8364 | 4367.8364 | 4367.8364 | 4367.8364 | 4367.8364 | 4367.8364 | 4367.8364 | 4367.8364
65% | 2035.9088 | 2698.8915 | 2769.1924 | 2856.1049 | 2971.4986 | 3080.895 | 3272.0749 | 3752.9047 | 4011.5294 | 3822.8551 | 4406.9646 | 4512.2036 | 4587.8531 | 4944.4426 | 5002.4844 | 5002.4844 | 5002.4844 | 5002.4844 | 5002.4844 | 5002.4844 | 5002.4844 | 5002.4844 | 5002.4844 | 5002.4844 | 5002.4844 | 5002.4844 | 5002.4844 | 5002.4844 | 5002.4844 | 5002.4844 |  | 2645.225 | 3277.6155 | 3343.1051 | 3569.1186 | 3563.6103 | 3613.3093 | 3807.6888 | 4366.1471 | 4596.6007 | 4378.4584 | 4981.0536 | 4728.0515 | 4955.7006 | 5119.7493 | 5052.3503 | 5052.3503 | 5052.3503 | 5052.3503 | 5052.3503 | 5052.3503 | 5052.3503 | 5052.3503 | 5052.3503 | 5052.3503 | 5052.3503 | 5052.3503 | 5052.3503 | 5052.3503 | 5052.3503 | 5052.3503
60% | 2098.8616 | 2921.1907 | 3008.3883 | 3116.1901 | 3259.3184 | 3395.008 | 3632.1374 | 4228.5337 | 4549.3182 | 4315.2964 | 5039.7953 | 5170.3283 | 5264.16 | 5706.4549 | 5778.4469 | 5778.4469 | 5778.4469 | 5778.4469 | 5778.4469 | 5778.4469 | 5778.4469 | 5778.4469 | 5778.4469 | 5778.4469 | 5778.4469 | 5778.4469 | 5778.4469 | 5778.4469 | 5778.4469 | 5778.4469 |  | 2854.6256 | 3639.0098 | 3720.2396 | 4000.575 | 3993.7428 | 4055.3868 | 4296.485 | 4989.1674 | 5275.01 | 5004.4378 | 5751.8653 | 5438.0548 | 5720.4188 | 5923.8962 | 5840.298 | 5840.298 | 5840.298 | 5840.298 | 5840.298 | 5840.298 | 5840.298 | 5840.298 | 5840.298 | 5840.298 | 5840.298 | 5840.298 | 5840.298 | 5840.298 | 5840.298 | 5840.298
55% | 1733.592 | 2625.5087 | 2720.0851 | 2837.0093 | 2992.2496 | 3139.4215 | 3396.6175 | 4043.4823 | 4391.4125 | 4137.5871 | 4923.395 | 5064.974 | 5166.746 | 5646.469 | 5724.5532 | 5724.5532 | 5724.5532 | 5724.5532 | 5724.5532 | 5724.5532 | 5724.5532 | 5724.5532 | 5724.5532 | 5724.5532 | 5724.5532 | 5724.5532 | 5724.5532 | 5724.5532 | 5724.5532 | 5724.5532 |  | 2553.3107 | 3404.0714 | 3492.1751 | 3796.2332 | 3788.8228 | 3855.6833 | 4117.1838 | 4868.4828 | 5178.5141 | 4885.0454 | 5695.7222 | 5355.3561 | 5661.6146 | 5882.3107 | 5791.6383 | 5791.6383 | 5791.6383 | 5791.6383 | 5791.6383 | 5791.6383 | 5791.6383 | 5791.6383 | 5791.6383 | 5791.6383 | 5791.6383 | 5791.6383 | 5791.6383 | 5791.6383 | 5791.6383 | 5791.6383
50% | 1107.3363 | 2015.6842 | 2112.003 | 2231.0812 | 2389.1813 | 2539.0646 | 2800.9987 | 3459.7803 | 3814.1202 | 3555.6188 | 4355.9031 | 4500.0904 | 4603.7372 | 5092.2979 | 5171.8205 | 5171.8205 | 5171.8205 | 5171.8205 | 5171.8205 | 5171.8205 | 5171.8205 | 5171.8205 | 5171.8205 | 5171.8205 | 5171.8205 | 5171.8205 | 5171.8205 | 5171.8205 | 5171.8205 | 5171.8205 |  | 1942.1561 | 2808.5899 | 2898.3167 | 3207.9763 | 3200.4293 | 3268.5216 | 3534.8396 | 4299.9793 | 4615.7221 | 4316.847 | 5142.4584 | 4795.822 | 5107.7225 | 5332.4844 | 5240.1415 | 5240.1415 | 5240.1415 | 5240.1415 | 5240.1415 | 5240.1415 | 5240.1415 | 5240.1415 | 5240.1415 | 5240.1415 | 5240.1415 | 5240.1415 | 5240.1415 | 5240.1415 | 5240.1415 | 5240.1415
45% | 304.3799 | 1151.2957 | 1242.2705 | 1354.742 | 1504.0703 | 1645.6377 | 1893.0391 | 2515.2699 | 2849.9501 | 2605.791 | 3361.6736 | 3497.861 | 3595.7573 | 4057.2114 | 4132.3219 | 4132.3219 | 4132.3219 | 4132.3219 | 4132.3219 | 4132.3219 | 4132.3219 | 4132.3219 | 4132.3219 | 4132.3219 | 4132.3219 | 4132.3219 | 4132.3219 | 4132.3219 | 4132.3219 | 4132.3219 |  | 1081.8472 | 1900.2091 | 1984.9576 | 2277.4365 | 2270.3083 | 2334.6226 | 2586.1647 | 3308.8526 | 3607.0772 | 3324.7844 | 4104.5889 | 3777.1848 | 4071.7802 | 4284.0718 | 4196.8523 | 4196.8523 | 4196.8523 | 4196.8523 | 4196.8523 | 4196.8523 | 4196.8523 | 4196.8523 | 4196.8523 | 4196.8523 | 4196.8523 | 4196.8523 | 4196.8523 | 4196.8523 | 4196.8523 | 4196.8523
40% |  | 241.0368 | 303.4886 | 389.6318 | 518.5137 | 646.2971 | 869.6099 | 1431.2562 | 1733.3497 | 1512.9635 | 2195.2484 | 2318.1757 | 2406.5401 | 2823.064 | 2890.8613 | 2890.8613 | 2890.8613 | 2890.8613 | 2890.8613 | 2890.8613 | 2890.8613 | 2890.8613 | 2890.8613 | 2890.8613 | 2890.8613 | 2890.8613 | 2890.8613 | 2890.8613 | 2890.8613 | 2890.8613 |  | 197.8445 | 876.0818 | 952.5787 | 1216.5798 | 1210.1457 | 1268.1979 | 1495.2482 | 2147.5704 | 2416.7579 | 2161.951 | 2865.8286 | 2570.3026 | 2836.2143 | 3027.8357 | 2949.1086 | 2949.1086 | 2949.1086 | 2949.1086 | 2949.1086 | 2949.1086 | 2949.1086 | 2949.1086 | 2949.1086 | 2949.1086 | 2949.1086 | 2949.1086 | 2949.1086 | 2949.1086 | 2949.1086 | 2949.1086
35% |  |  |  |  | 0.16059 | 8.4247 | 51.6577 | 306.5672 | 520.3346 | 359.4876 | 878.7989 | 974.1987 | 1042.7754 | 1366.0258 | 1418.641 | 1418.641 | 1418.641 | 1418.641 | 1418.641 | 1418.641 | 1418.641 | 1418.641 | 1418.641 | 1418.641 | 1418.641 | 1418.641 | 1418.641 | 1418.641 | 1418.641 | 1418.641 |  |  | 53.4346 | 76.5978 | 185.9699 | 182.7815 | 212.4625 | 347.6947 | 841.7976 | 1050.7051 | 852.9579 | 1399.2139 | 1169.866 | 1376.2313 | 1524.9423 | 1463.8448 | 1463.8448 | 1463.8448 | 1463.8448 | 1463.8448 | 1463.8448 | 1463.8448 | 1463.8448 | 1463.8448 | 1463.8448 | 1463.8448 | 1463.8448 | 1463.8448 | 1463.8448 | 1463.8448 | 1463.8448
30% | [8 empty] | 0.13247 |  | 47.3865 | 73.4365 | 95.4345 | 233.8409 | 261.5037 | 261.5037 | 261.5037 | 261.5037 | 261.5037 | 261.5037 | 261.5037 | 261.5037 | 261.5037 | 261.5037 | 261.5037 | 261.5037 | 261.5037 | 261.5037 | 261.5037 | 261.5037 | [8 empty] | 38.745 | 98.151 | 41.2641 | 251.1294 | 143.1816 | 239.0986 | 321.5304 | 286.3608 | 286.3608 | 286.3608 | 286.3608 | 286.3608 | 286.3608 | 286.3608 | 286.3608 | 286.3608 | 286.3608 | 286.3608 | 286.3608 | 286.3608 | 286.3608 | 286.3608 | 286.3608
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 11808.8744 | 17327.6237 | 17950.4997 | 18729.4017 | 19778.0731 | 20785.8168 | 22575.4407 | 27221.1763 | 29796.0085 | 27912.7082 | 33810.7876 | 34892.5992 | 35673.4826 | 39388.7046 | 39998.5117 | 39998.5117 | 39998.5117 | 39998.5117 | 39998.5117 | 39998.5117 | 39998.5117 | 39998.5117 | 39998.5117 | 39998.5117 | 39998.5117 | 39998.5117 | 39998.5117 | 39998.5117 | 39998.5117 | 39998.5117 | E @ R (MWh) | 16856.5689 | 22627.8251 | 23249.1394 | 25422.5188 | 25369.0323 | 25852.5194 | 27762.4582 | 33392.6489 | 35763.9491 | 33518.6811 | 39773.1943 | 37127.5741 | 39506.8788 | 41234.634 | 40523.5006 | 40523.5006 | 40523.5006 | 40523.5006 | 40523.5006 | 40523.5006 | 40523.5006 | 40523.5006 | 40523.5006 | 40523.5006 | 40523.5006 | 40523.5006 | 40523.5006 | 40523.5006 | 40523.5006 | 40523.5006
Option 8 Winter POE50 W E @ R (MWh) N 2 | 8266.2121 | 12129.3366 | 12565.3498 | 13110.5812 | 13844.6511 | 14550.0718 | 15802.8085 | 19054.8234 | 20857.206 | 19538.8958 | 23667.5513 | 24424.8194 | 24971.4378 | 27572.0932 | 27998.9582 | 27998.9582 | 27998.9582 | 27998.9582 | 27998.9582 | 27998.9582 | 27998.9582 | 27998.9582 | 27998.9582 | 27998.9582 | 27998.9582 | 27998.9582 | 27998.9582 | 27998.9582 | 27998.9582 | 27998.9582 | Option 8 Winter POE10 W E @ R (MWh) N 2 | 5056.9707 | 6788.3475 | 6974.7418 | 7626.7556 | 7610.7097 | 7755.7558 | 8328.7375 | 10017.7947 | 10729.1847 | 10055.6043 | 11931.9583 | 11138.2722 | 11852.0637 | 12370.3902 | 12157.0502 | 12157.0502 | 12157.0502 | 12157.0502 | 12157.0502 | 12157.0502 | 12157.0502 | 12157.0502 | 12157.0502 | 12157.0502 | 12157.0502 | 12157.0502 | 12157.0502 | 12157.0502 | 12157.0502 | 12157.0502
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | 8.9039 | 10.0686 | 10.1857 | 10.1283 | 10.1828 | 10.2053 | 10.2771 | 10.4248 | 10.549 | 10.6062 | 10.5553 | 10.769 | 10.8029 | 10.7628 | 10.8432 | 10.8846 | 10.8846 | 10.8846 | 10.8846 | 10.8846 | 10.8846 | 10.8846 | 10.8846 | 10.8846 | 10.8846 | 10.8846 | 10.8846 | 10.8846 | 10.8846 | 10.8846 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
98% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
97% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 12.1062 | 13.3817 | 13.4169 | 13.3789 | 13.3887 | 13.4583 | 13.5995 | 13.8481 | 13.9776 | 14.0713 | 14.2131 | 14.3942 | 14.6131 | 14.7279 | 14.6907 | 14.7312 | 14.7312 | 14.7312 | 14.7312 | 14.7312 | 14.7312 | 14.7312 | 14.7312 | 14.7312 | 14.7312 | 14.7312 | 14.7312 | 14.7312 | 14.7312 | 14.7312
95% | 8.3559 | 9.4797 | 9.5926 | 9.5372 | 9.5899 | 9.6115 | 9.6808 | 9.8233 | 9.9432 | 9.9984 | 9.9492 | 10.1554 | 10.1881 | 10.1494 | 10.227 | 10.267 | 10.267 | 10.267 | 10.267 | 10.267 | 10.267 | 10.267 | 10.267 | 10.267 | 10.267 | 10.267 | 10.267 | 10.267 | 10.267 | 10.267 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
90% | 171.7748 | 195.5955 | 197.9892 | 196.8158 | 197.9315 | 198.3899 | 199.8591 | 202.88 | 205.4214 | 206.5912 | 205.5485 | 209.9202 | 210.6135 | 209.793 | 211.4383 | 212.2848 | 212.2848 | 212.2848 | 212.2848 | 212.2848 | 212.2848 | 212.2848 | 212.2848 | 212.2848 | 212.2848 | 212.2848 | 212.2848 | 212.2848 | 212.2848 | 212.2848 |  | 11.1431 | 12.3531 | 12.3865 | 12.3505 | 12.3598 | 12.4259 | 12.5598 | 12.7956 | 12.9185 | 13.0074 | 13.142 | 13.3137 | 13.5215 | 13.6303 | 13.595 | 13.6335 | 13.6335 | 13.6335 | 13.6335 | 13.6335 | 13.6335 | 13.6335 | 13.6335 | 13.6335 | 13.6335 | 13.6335 | 13.6335 | 13.6335 | 13.6335 | 13.6335
85% | 583.0836 | 668.0948 | 676.6375 | 672.4501 | 676.4317 | 678.0677 | 683.3108 | 694.0919 | 703.1615 | 707.3365 | 703.6153 | 719.2167 | 721.6911 | 718.7628 | 724.6348 | 727.6558 | 727.6558 | 727.6558 | 727.6558 | 727.6558 | 727.6558 | 727.6558 | 727.6558 | 727.6558 | 727.6558 | 727.6558 | 727.6558 | 727.6558 | 727.6558 | 727.6558 |  | 10.18 | 11.3246 | 11.3562 | 11.3221 | 11.3309 | 11.3934 | 11.5201 | 11.7432 | 11.8594 | 11.9435 | 12.0708 | 12.2333 | 12.4298 | 12.5328 | 12.4994 | 12.5358 | 12.5358 | 12.5358 | 12.5358 | 12.5358 | 12.5358 | 12.5358 | 12.5358 | 12.5358 | 12.5358 | 12.5358 | 12.5358 | 12.5358 | 12.5358 | 12.5358
80% | 892.6437 | 1030.7394 | 1044.6165 | 1037.8142 | 1044.2821 | 1046.9396 | 1055.4569 | 1072.9701 | 1087.703 | 1094.485 | 1088.4403 | 1113.7838 | 1117.8034 | 1113.0465 | 1122.5851 | 1127.4926 | 1127.4926 | 1127.4926 | 1127.4926 | 1127.4926 | 1127.4926 | 1127.4926 | 1127.4926 | 1127.4926 | 1127.4926 | 1127.4926 | 1127.4926 | 1127.4926 | 1127.4926 | 1127.4926 |  | 36.8674 | 41.1843 | 41.3034 | 41.175 | 41.208 | 41.4438 | 41.9215 | 42.7629 | 43.2013 | 43.5185 | 43.9985 | 44.6113 | 45.3524 | 45.7408 | 45.6149 | 45.7521 | 45.7521 | 45.7521 | 45.7521 | 45.7521 | 45.7521 | 45.7521 | 45.7521 | 45.7521 | 45.7521 | 45.7521 | 45.7521 | 45.7521 | 45.7521 | 45.7521
75% | 1479.5037 | 1725.3485 | 1750.0533 | 1737.9436 | 1749.458 | 1754.1891 | 1769.3519 | 1800.5298 | 1826.7581 | 1838.8318 | 1828.0706 | 1873.1885 | 1880.3443 | 1871.8759 | 1888.857 | 1897.5936 | 1897.5936 | 1897.5936 | 1897.5936 | 1897.5936 | 1897.5936 | 1897.5936 | 1897.5936 | 1897.5936 | 1897.5936 | 1897.5936 | 1897.5936 | 1897.5936 | 1897.5936 | 1897.5936 |  | 16.5074 | 18.5351 | 18.5911 | 18.5307 | 18.5462 | 18.657 | 18.8814 | 19.2766 | 19.4825 | 19.6315 | 19.8569 | 20.1448 | 20.4928 | 20.6753 | 20.6161 | 20.6806 | 20.6806 | 20.6806 | 20.6806 | 20.6806 | 20.6806 | 20.6806 | 20.6806 | 20.6806 | 20.6806 | 20.6806 | 20.6806 | 20.6806 | 20.6806 | 20.6806
70% | 1730.3357 | 2044.3359 | 2075.8895 | 2060.4227 | 2075.1292 | 2081.1719 | 2100.5382 | 2140.3596 | 2173.8591 | 2189.28 | 2175.5354 | 2233.1613 | 2242.3009 | 2231.4848 | 2253.1735 | 2264.3322 | 2264.3322 | 2264.3322 | 2264.3322 | 2264.3322 | 2264.3322 | 2264.3322 | 2264.3322 | 2264.3322 | 2264.3322 | 2264.3322 | 2264.3322 | 2264.3322 | 2264.3322 | 2264.3322 |  | 43.7436 | 49.4342 | 49.5912 | 49.4219 | 49.4654 | 49.7762 | 50.4059 | 51.515 | 52.0929 | 52.511 | 53.1438 | 53.9516 | 54.9285 | 55.4404 | 55.2744 | 55.4554 | 55.4554 | 55.4554 | 55.4554 | 55.4554 | 55.4554 | 55.4554 | 55.4554 | 55.4554 | 55.4554 | 55.4554 | 55.4554 | 55.4554 | 55.4554 | 55.4554
65% | 1900.1465 | 2285.7258 | 2324.4723 | 2305.4797 | 2323.5388 | 2330.9589 | 2354.74 | 2403.639 | 2444.775 | 2463.7113 | 2446.8335 | 2517.5958 | 2528.8188 | 2515.5371 | 2542.1699 | 2555.8723 | 2555.8723 | 2555.8723 | 2555.8723 | 2555.8723 | 2555.8723 | 2555.8723 | 2555.8723 | 2555.8723 | 2555.8723 | 2555.8723 | 2555.8723 | 2555.8723 | 2555.8723 | 2555.8723 |  | 12.655 | 14.421 | 14.4697 | 14.4172 | 14.4307 | 14.5271 | 14.7226 | 15.0668 | 15.2461 | 15.3759 | 15.5723 | 15.823 | 16.1261 | 16.285 | 16.2335 | 16.2897 | 16.2897 | 16.2897 | 16.2897 | 16.2897 | 16.2897 | 16.2897 | 16.2897 | 16.2897 | 16.2897 | 16.2897 | 16.2897 | 16.2897 | 16.2897 | 16.2897
60% | 2395.395 | 2958.7224 | 3015.3307 | 2987.5827 | 3013.9668 | 3024.8076 | 3059.5514 | 3130.9924 | 3191.0917 | 3218.7573 | 3194.0991 | 3297.482 | 3313.8788 | 3294.4743 | 3333.3846 | 3353.4037 | 3353.4037 | 3353.4037 | 3353.4037 | 3353.4037 | 3353.4037 | 3353.4037 | 3353.4037 | 3353.4037 | 3353.4037 | 3353.4037 | 3353.4037 | 3353.4037 | 3353.4037 | 3353.4037 |  | 69.7368 | 80.3657 | 80.659 | 80.3428 | 80.4241 | 81.0045 | 82.1808 | 84.2523 | 85.3317 | 86.1126 | 87.2945 | 88.8034 | 90.628 | 91.5842 | 91.2742 | 91.6122 | 91.6122 | 91.6122 | 91.6122 | 91.6122 | 91.6122 | 91.6122 | 91.6122 | 91.6122 | 91.6122 | 91.6122 | 91.6122 | 91.6122 | 91.6122 | 91.6122
55% | 2397.9043 | 3091.1628 | 3160.8278 | 3126.6797 | 3159.1493 | 3172.4904 | 3215.248 | 3303.1668 | 3377.1279 | 3411.1746 | 3380.829 | 3508.0571 | 3528.2358 | 3504.3556 | 3552.2406 | 3576.8771 | 3576.8771 | 3576.8771 | 3576.8771 | 3576.8771 | 3576.8771 | 3576.8771 | 3576.8771 | 3576.8771 | 3576.8771 | 3576.8771 | 3576.8771 | 3576.8771 | 3576.8771 | 3576.8771 |  | 281.6802 | 329.8208 | 331.1492 | 329.717 | 330.0853 | 332.7141 | 338.0417 | 347.4243 | 352.3132 | 355.8501 | 361.2031 | 368.0372 | 376.3012 | 380.6321 | 379.2281 | 380.7589 | 380.7589 | 380.7589 | 380.7589 | 380.7589 | 380.7589 | 380.7589 | 380.7589 | 380.7589 | 380.7589 | 380.7589 | 380.7589 | 380.7589 | 380.7589 | 380.7589
50% | 1977.8845 | 2764.4944 | 2843.5402 | 2804.7939 | 2841.6356 | 2856.7733 | 2905.2884 | 3005.046 | 3088.9664 | 3127.5977 | 3093.1659 | 3237.526 | 3260.4218 | 3233.3261 | 3287.6591 | 3315.613 | 3315.613 | 3315.613 | 3315.613 | 3315.613 | 3315.613 | 3315.613 | 3315.613 | 3315.613 | 3315.613 | 3315.613 | 3315.613 | 3315.613 | 3315.613 | 3315.613 |  | 543.2253 | 651.7379 | 654.7323 | 651.5039 | 652.3342 | 658.2598 | 670.2686 | 691.4175 | 702.4375 | 710.41 | 722.476 | 737.8807 | 756.5083 | 766.2706 | 763.1058 | 766.5564 | 766.5564 | 766.5564 | 766.5564 | 766.5564 | 766.5564 | 766.5564 | 766.5564 | 766.5564 | 766.5564 | 766.5564 | 766.5564 | 766.5564 | 766.5564 | 766.5564
45% | 892.7494 | 1543.8389 | 1609.2663 | 1577.1954 | 1607.6899 | 1620.2195 | 1660.3762 | 1742.9472 | 1812.4095 | 1844.3852 | 1815.8854 | 1935.3746 | 1954.3258 | 1931.8982 | 1976.8705 | 2000.0084 | 2000.0084 | 2000.0084 | 2000.0084 | 2000.0084 | 2000.0084 | 2000.0084 | 2000.0084 | 2000.0084 | 2000.0084 | 2000.0084 | 2000.0084 | 2000.0084 | 2000.0084 | 2000.0084 |  | 742.5052 | 928.9193 | 934.0633 | 928.5173 | 929.9435 | 940.1232 | 960.7531 | 997.085 | 1016.0161 | 1029.7122 | 1050.4404 | 1076.9041 | 1108.9046 | 1125.6752 | 1120.2384 | 1126.1661 | 1126.1661 | 1126.1661 | 1126.1661 | 1126.1661 | 1126.1661 | 1126.1661 | 1126.1661 | 1126.1661 | 1126.1661 | 1126.1661 | 1126.1661 | 1126.1661 | 1126.1661 | 1126.1661
40% | 82.6197 | 448.4043 | 495.3965 | 472.3621 | 494.2643 | 503.2635 | 532.1055 | 591.4108 | 641.301 | 664.267 | 643.7975 | 729.6188 | 743.2302 | 727.122 | 759.4226 | 776.041 | 776.041 | 776.041 | 776.041 | 776.041 | 776.041 | 776.041 | 776.041 | 776.041 | 776.041 | 776.041 | 776.041 | 776.041 | 776.041 | 776.041 |  | 686.4025 | 938.8137 | 945.7788 | 938.2693 | 940.2006 | 953.9841 | 981.9179 | 1031.1125 | 1056.7459 | 1075.2908 | 1103.3575 | 1139.1903 | 1182.5201 | 1205.2281 | 1197.8665 | 1205.8928 | 1205.8928 | 1205.8928 | 1205.8928 | 1205.8928 | 1205.8928 | 1205.8928 | 1205.8928 | 1205.8928 | 1205.8928 | 1205.8928 | 1205.8928 | 1205.8928 | 1205.8928 | 1205.8928
35% |  | 1.6148 | 5.4003 | 3.2709 | 5.2834 | 6.2472 | 9.8686 | 19.8299 | 30.7782 | 36.5919 | 31.3867 | 55.7517 | 60.2225 | 54.9494 | 65.7537 | 71.6692 | 71.6692 | 71.6692 | 71.6692 | 71.6692 | 71.6692 | 71.6692 | 71.6692 | 71.6692 | 71.6692 | 71.6692 | 71.6692 | 71.6692 | 71.6692 | 71.6692 |  | 458.782 | 868.8929 | 880.2097 | 868.0084 | 871.1463 | 893.5414 | 938.9274 | 1018.8574 | 1060.506 | 1090.6372 | 1136.2393 | 1194.4595 | 1264.8606 | 1301.7559 | 1289.7949 | 1302.8359 | 1302.8359 | 1302.8359 | 1302.8359 | 1302.8359 | 1302.8359 | 1302.8359 | 1302.8359 | 1302.8359 | 1302.8359 | 1302.8359 | 1302.8359 | 1302.8359 | 1302.8359 | 1302.8359
30% | [31 empty] | 3.5003 | 199.9764 | 209.3483 | 199.2523 | 201.8267 | 220.6429 | 261.1304 | 339.9291 | 384.6819 | 418.6009 | 472.3546 | 545.1319 | 639.1947 | 691.0757 | 674.0645 | 692.6208 | 692.6208 | 692.6208 | 692.6208 | 692.6208 | 692.6208 | 692.6208 | 692.6208 | 692.6208 | 692.6208 | 692.6208 | 692.6208 | 692.6208 | 692.6208 | 692.6208
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 14376.0875 | 18589.8496 | 19027.0063 | 18812.4517 | 19016.448 | 19100.402 | 19369.9964 | 19926.8305 | 20397.8067 | 20615.378 | 20421.4347 | 21237.0849 | 21367.0492 | 21213.2626 | 21521.8675 | 21680.9955 | 21680.9955 | 21680.9955 | 21680.9955 | 21680.9955 | 21680.9955 | 21680.9955 | 21680.9955 | 21680.9955 | 21680.9955 | 21680.9955 | 21680.9955 | 21680.9955 | 21680.9955 | 21680.9955 | E @ R (MWh) | 2899.7446 | 4117.569 | 4155.085 | 4114.6453 | 4125.0234 | 4199.5321 | 4352.8623 | 4630.3154 | 4778.5425 | 4887.3062 | 5054.3091 | 5271.6303 | 5540.4179 | 5683.8418 | 5637.1556 | 5688.0662 | 5688.0662 | 5688.0662 | 5688.0662 | 5688.0662 | 5688.0662 | 5688.0662 | 5688.0662 | 5688.0662 | 5688.0662 | 5688.0662 | 5688.0662 | 5688.0662 | 5688.0662 | 5688.0662
Option 8 Summer POE50 W E @ R (MWh) N 2 | 10063.2613 | 13012.8947 | 13318.9044 | 13168.7162 | 13311.5136 | 13370.2814 | 13558.9975 | 13948.7813 | 14278.4647 | 14430.7646 | 14295.0043 | 14865.9595 | 14956.9344 | 14849.2838 | 15065.3072 | 15176.6968 | 15176.6968 | 15176.6968 | 15176.6968 | 15176.6968 | 15176.6968 | 15176.6968 | 15176.6968 | 15176.6968 | 15176.6968 | 15176.6968 | 15176.6968 | 15176.6968 | 15176.6968 | 15176.6968 | Option 8 Summer POE10 W E @ R (MWh) N 2 | 869.9234 | 1235.2707 | 1246.5255 | 1234.3936 | 1237.507 | 1259.8596 | 1305.8587 | 1389.0946 | 1433.5627 | 1466.1918 | 1516.2927 | 1581.4891 | 1662.1254 | 1705.1525 | 1691.1467 | 1706.4199 | 1706.4199 | 1706.4199 | 1706.4199 | 1706.4199 | 1706.4199 | 1706.4199 | 1706.4199 | 1706.4199 | 1706.4199 | 1706.4199 | 1706.4199 | 1706.4199 | 1706.4199 | 1706.4199

## POF N,N-1 & N-2 Risk
N-2 Method 1
| Asset name | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Tx 1 Pof | DS-WGI-TRNFMR-9000004493 | 2.964% | 2.964% | 3.087% | 3.212% | 3.341% | 3.473% | 3.607% | 3.745% | 3.885% | 4.029% | 4.175% | 4.325% | 4.477% | 4.633% | 4.792% | 4.792% | 4.792% | 4.792% | 4.792% | 4.792% | 4.792% | 4.792% | 4.792% | 4.792% | 4.792% | 4.792% | 4.792% | 4.792% | 4.792% | 4.792%
Tx 2 Pof | DS-WGI-TRNFMR-9000003147 | 1.383% | 1.383% | 1.461% | 1.543% | 1.626% | 1.713% | 1.802% | 1.894% | 1.988% | 2.085% | 2.185% | 2.288% | 2.394% | 2.502% | 2.613% | 2.613% | 2.613% | 2.613% | 2.613% | 2.613% | 2.613% | 2.613% | 2.613% | 2.613% | 2.613% | 2.613% | 2.613% | 2.613% | 2.613% | 2.613%
Tx 3 Pof | DS-WGI-TRNFMR-9000007146 | 1.383% | 1.383% | 1.461% | 1.543% | 1.626% | 1.713% | 1.802% | 1.894% | 1.988% | 2.085% | 2.185% | 2.288% | 2.394% | 2.502% | 2.613% | 2.613% | 2.613% | 2.613% | 2.613% | 2.613% | 2.613% | 2.613% | 2.613% | 2.613% | 2.613% | 2.613% | 2.613% | 2.613% | 2.613% | 2.613%
Tx 4 Pof
Tx 5 Pof
Total Tx Pof |  | 5.73% | 5.73% | 6.009% | 6.297% | 6.594% | 6.898% | 7.211% | 7.532% | 7.861% | 8.199% | 8.546% | 8.901% | 9.265% | 9.637% | 10.02% | 10.02% | 10.02% | 10.02% | 10.02% | 10.02% | 10.02% | 10.02% | 10.02% | 10.02% | 10.02% | 10.02% | 10.02% | 10.02% | 10.02% | 10.02%
N-1 Risk |  | 2.21% | 2.21% | 2.318% | 2.43% | 2.544% | 2.661% | 2.782% | 2.906% | 3.033% | 3.163% | 3.297% | 3.434% | 3.574% | 3.718% | 3.865% | 3.865% | 3.865% | 3.865% | 3.865% | 3.865% | 3.865% | 3.865% | 3.865% | 3.865% | 3.865% | 3.865% | 3.865% | 3.865% | 3.865% | 3.865%
N-2 Risk |  | 0.0237% | 0.0237% | 0.02615% | 0.02881% | 0.03167% | 0.03476% | 0.03808% | 0.04165% | 0.04548% | 0.04958% | 0.05397% | 0.05866% | 0.06368% | 0.06902% | 0.07471% | 0.07471% | 0.07471% | 0.07471% | 0.07471% | 0.07471% | 0.07471% | 0.07471% | 0.07471% | 0.07471% | 0.07471% | 0.07471% | 0.07471% | 0.07471% | 0.07471% | 0.07471%
N Risk |  | 97.77% | 97.77% | 97.66% | 97.54% | 97.42% | 97.3% | 97.18% | 97.05% | 96.92% | 96.79% | 96.65% | 96.51% | 96.36% | 96.21% | 96.06% | 96.06% | 96.06% | 96.06% | 96.06% | 96.06% | 96.06% | 96.06% | 96.06% | 96.06% | 96.06% | 96.06% | 96.06% | 96.06% | 96.06% | 96.06%

## Summary
Involuntary load shedding (NER 5.17.1(c)(4)(ii))
Option 1 - Do Nothing | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Weighted Energy @ Risk (MWh) under N Conditions | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.062696 | 0.0049965 | 0.11828 | 0.35438 | 0.37975 | 0.39514 | 0.39514 | 0.39514 | 0.39514 | 0.39514 | 0.39514 | 0.39514 | 0.39514 | 0.39514 | 0.39514 | 0.39514 | 0.39514 | 0.39514 | 0.39514 | 0.39514
Weighted Energy @ Risk (MWh) under N-1 Conditions | 2.2587 | 10.6047 | 12.6676 | 15.5222 | 17.6112 | 20.4393 | 27.5376 | 53.1609 | 72.9643 | 62.6435 | 114.8665 | 119.9881 | 139.8342 | 184.009 | 195.2376 | 195.8327 | 195.8327 | 195.8327 | 195.8327 | 195.8327 | 195.8327 | 195.8327 | 195.8327 | 195.8327 | 195.8327 | 195.8327 | 195.8327 | 195.8327 | 195.8327 | 195.8327
Weighted Energy @ Risk (MWh) under N-2 Conditions | 7.013 | 9.5557 | 10.8408 | 12.269 | 13.8076 | 15.5249 | 17.9127 | 22.1785 | 25.7354 | 27.063 | 33.0605 | 36.4078 | 40.5703 | 46.349 | 50.5538 | 50.6797 | 50.6797 | 50.6797 | 50.6797 | 50.6797 | 50.6797 | 50.6797 | 50.6797 | 50.6797 | 50.6797 | 50.6797 | 50.6797 | 50.6797 | 50.6797 | 50.6797
Total EUE (MWh) - Option 1 | 9.2716 | 20.1604 | 23.5084 | 27.7911 | 31.4188 | 35.9641 | 45.4503 | 75.3394 | 98.6997 | 89.7066 | 147.9896 | 156.401 | 180.5228 | 230.7123 | 246.1711 | 246.9075 | 246.9075 | 246.9075 | 246.9075 | 246.9075 | 246.9075 | 246.9075 | 246.9075 | 246.9075 | 246.9075 | 246.9075 | 246.9075 | 246.9075 | 246.9075 | 246.9075
Cost of EUE ($) - Option 1 | 394788.2008 | 858434.4176 | 1000994.2857 | 1183354.2871 | 1337823.2762 | 1531362.5145 | 1935286.2231 | 3207972.9402 | 4202660.3292 | 3819730.2991 | 6301440.037 | 6659597.6105 | 7686710.5898 | 9823795.6893 | 10482034.0894 | 10513390.0159 | 10513390.0159 | 10513390.0159 | 10513390.0159 | 10513390.0159 | 10513390.0159 | 10513390.0159 | 10513390.0159 | 10513390.0159 | 10513390.0159 | 10513390.0159 | 10513390.0159 | 10513390.0159 | 10513390.0159 | 10513390.0159
Hours at Risk pA. (Hrs) (N) | 0.2972 | 0.2972 | 0.2972 | 0.2972 | 0.2972 | 0.2972 | 0.2972 | 0.2972 | 0.2972 | 0.2972 | 0.2972 | 0.67536 | 0.67536 | 8.9969 | 1.8642 | 1.8642 | 1.8642 | 1.8642 | 1.8642 | 1.8642 | 1.8642 | 1.8642 | 1.8642 | 1.8642 | 1.8642 | 1.8642 | 1.8642 | 1.8642 | 1.8642 | 1.8642
Option 2 - Replace 3 x 10/13.5 MVA Tx with 3 x 20/33 MVA Tx | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Weighted Energy @ Risk (MWh) under N Conditions | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Weighted Energy @ Risk (MWh) under N-1 Conditions | 2.256 | 10.6047 | 12.6676 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Weighted Energy @ Risk (MWh) under N-2 Conditions | 7.013 | 9.5557 | 10.8408 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total EUE (MWh) - Option 2 | 9.2689 | 20.1604 | 23.5084 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cost of EUE ($) - Option 2 | 394673.8567 | 858434.4176 | 1000994.2857 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 - Replace 1 x 10/13.5 MVA Tx with 1 x 20/33 MVA Tx | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Weighted Energy @ Risk (MWh) under N Conditions | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Weighted Energy @ Risk (MWh) under N-1 Conditions | 2.256 | 10.6047 | 12.6676 | 0.0093251 | 0.0098976 | 0.01138 | 0.014212 | 0.029773 | 0.071739 | 0.038587 | 0.30963 | 0.21635 | 0.41193 | 1.0649 | 1.1427 | 1.1442 | 1.1442 | 1.1442 | 1.1442 | 1.1442 | 1.1442 | 1.1442 | 1.1442 | 1.1442 | 1.1442 | 1.1442 | 1.1442 | 1.1442 | 1.1442 | 1.1442
Weighted Energy @ Risk (MWh) under N-2 Conditions | 7.013 | 9.5557 | 10.8408 | 0.46073 | 0.54435 | 0.65214 | 0.87452 | 1.5522 | 2.1061 | 1.9732 | 3.353 | 3.6769 | 4.367 | 5.7215 | 6.3044 | 6.3235 | 6.3235 | 6.3235 | 6.3235 | 6.3235 | 6.3235 | 6.3235 | 6.3235 | 6.3235 | 6.3235 | 6.3235 | 6.3235 | 6.3235 | 6.3235 | 6.3235
Total EUE (MWh) - Option 3 | 9.2689 | 20.1604 | 23.5084 | 0.47005 | 0.55425 | 0.66352 | 0.88873 | 1.5819 | 2.1778 | 2.0118 | 3.6626 | 3.8932 | 4.779 | 6.7865 | 7.447 | 7.4677 | 7.4677 | 7.4677 | 7.4677 | 7.4677 | 7.4677 | 7.4677 | 7.4677 | 7.4677 | 7.4677 | 7.4677 | 7.4677 | 7.4677 | 7.4677 | 7.4677
Cost of EUE ($) - Option 3 | 394673.8567 | 858434.4176 | 1000994.2857 | 20014.9011 | 23600.1425 | 28252.8547 | 37842.3371 | 67359.3338 | 92731.8727 | 85664.465 | 155954.2553 | 165775.6576 | 203489.9266 | 288969.7633 | 317097.2966 | 317977.1828 | 317977.1828 | 317977.1828 | 317977.1828 | 317977.1828 | 317977.1828 | 317977.1828 | 317977.1828 | 317977.1828 | 317977.1828 | 317977.1828 | 317977.1828 | 317977.1828 | 317977.1828 | 317977.1828
Option 4 - Construct 2x 20/33MVA zone substation in Inverloch | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Weighted Energy @ Risk (MWh) under N Conditions | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Weighted Energy @ Risk (MWh) under N-1 Conditions | 2.256 | 10.6047 | 12.6676 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Weighted Energy @ Risk (MWh) under N-2 Conditions | 7.013 | 9.5557 | 10.8408 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total EUE (MWh) - Option 4 | 9.2689 | 20.1604 | 23.5084 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cost of EUE ($) - Option 4 | 394673.8567 | 858434.4176 | 1000994.2857 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 - Contract network support services to defer network investment | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Weighted Energy @ Risk (MWh) under N Conditions | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Weighted Energy @ Risk (MWh) under N-1 Conditions | 0.1829 | 1.3398 | 1.7319 | 2.5012 | 2.8567 | 3.507 | 5.5581 | 15.5065 | 24.2283 | 18.331 | 45.228 | 45.4965 | 55.6928 | 81.5817 | 87.0399 | 87.2195 | 87.2195 | 87.2195 | 87.2195 | 87.2195 | 87.2195 | 87.2195 | 87.2195 | 87.2195 | 87.2195 | 87.2195 | 87.2195 | 87.2195 | 87.2195 | 87.2195
Weighted Energy @ Risk (MWh) under N-2 Conditions | 4.4688 | 6.5132 | 7.4464 | 8.5059 | 9.6342 | 10.8921 | 12.7227 | 16.2472 | 19.1244 | 19.8717 | 25.0011 | 27.5231 | 30.7756 | 35.5908 | 38.9072 | 39.0213 | 39.0213 | 39.0213 | 39.0213 | 39.0213 | 39.0213 | 39.0213 | 39.0213 | 39.0213 | 39.0213 | 39.0213 | 39.0213 | 39.0213 | 39.0213 | 39.0213
Total EUE (MWh) - Option 5 | 4.6517 | 7.853 | 9.1782 | 11.0071 | 12.4909 | 14.3991 | 18.2808 | 31.7536 | 43.3527 | 38.2027 | 70.2291 | 73.0196 | 86.4684 | 117.1724 | 125.9471 | 126.2407 | 126.2407 | 126.2407 | 126.2407 | 126.2407 | 126.2407 | 126.2407 | 126.2407 | 126.2407 | 126.2407 | 126.2407 | 126.2407 | 126.2407 | 126.2407 | 126.2407
Cost of EUE ($) - Option 5 | 198069.5217 | 334382.9315 | 390811.2305 | 468685.4227 | 531865.8602 | 613118.2122 | 778400.1263 | 1352078.6126 | 1845968.2668 | 1626680.3288 | 2990374.4608 | 3109196.5006 | 3681848.0609 | 4989233.9338 | 5362863.3327 | 5375366.0695 | 5375366.0695 | 5375366.0695 | 5375366.0695 | 5375366.0695 | 5375366.0695 | 5375366.0695 | 5375366.0695 | 5375366.0695 | 5375366.0695 | 5375366.0695 | 5375366.0695 | 5375366.0695 | 5375366.0695 | 5375366.0695
Option 6 - | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Weighted Energy @ Risk (MWh) under N Conditions | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.062696 | 0.0049965 | 0.11828 | 0.35438 | 0.37975 | 0.39514 | 0.39514 | 0.39514 | 0.39514 | 0.39514 | 0.39514 | 0.39514 | 0.39514 | 0.39514 | 0.39514 | 0.39514 | 0.39514 | 0.39514 | 0.39514 | 0.39514
Weighted Energy @ Risk (MWh) under N-1 Conditions | 2.256 | 10.6047 | 12.6676 | 15.5222 | 17.6112 | 20.4393 | 27.5376 | 53.1609 | 72.9643 | 62.6435 | 114.8665 | 119.9881 | 139.8342 | 184.009 | 195.2376 | 195.8327 | 195.8327 | 195.8327 | 195.8327 | 195.8327 | 195.8327 | 195.8327 | 195.8327 | 195.8327 | 195.8327 | 195.8327 | 195.8327 | 195.8327 | 195.8327 | 195.8327
Weighted Energy @ Risk (MWh) under N-2 Conditions | 7.013 | 9.5557 | 10.8408 | 12.269 | 13.8076 | 15.5249 | 17.9127 | 22.1785 | 25.7354 | 27.063 | 33.0605 | 36.4078 | 40.5703 | 46.349 | 50.5538 | 50.6797 | 50.6797 | 50.6797 | 50.6797 | 50.6797 | 50.6797 | 50.6797 | 50.6797 | 50.6797 | 50.6797 | 50.6797 | 50.6797 | 50.6797 | 50.6797 | 50.6797
Total EUE (MWh) - Option 6 | 9.2689 | 20.1604 | 23.5084 | 27.7911 | 31.4188 | 35.9641 | 45.4503 | 75.3394 | 98.6997 | 89.7066 | 147.9896 | 156.401 | 180.5228 | 230.7123 | 246.1711 | 246.9075 | 246.9075 | 246.9075 | 246.9075 | 246.9075 | 246.9075 | 246.9075 | 246.9075 | 246.9075 | 246.9075 | 246.9075 | 246.9075 | 246.9075 | 246.9075 | 246.9075
Cost of EUE ($) - Option 6 | 394673.8567 | 858434.4176 | 1000994.2857 | 1183354.2871 | 1337823.2762 | 1531362.5145 | 1935286.2231 | 3207972.9402 | 4202660.3292 | 3819730.2991 | 6301440.037 | 6659597.6105 | 7686710.5898 | 9823795.6893 | 10482034.0894 | 10513390.0159 | 10513390.0159 | 10513390.0159 | 10513390.0159 | 10513390.0159 | 10513390.0159 | 10513390.0159 | 10513390.0159 | 10513390.0159 | 10513390.0159 | 10513390.0159 | 10513390.0159 | 10513390.0159 | 10513390.0159 | 10513390.0159
Option 7 - | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Weighted Energy @ Risk (MWh) under N Conditions | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.062696 | 0.0049965 | 0.11828 | 0.35438 | 0.37975 | 0.39514 | 0.39514 | 0.39514 | 0.39514 | 0.39514 | 0.39514 | 0.39514 | 0.39514 | 0.39514 | 0.39514 | 0.39514 | 0.39514 | 0.39514 | 0.39514 | 0.39514
Weighted Energy @ Risk (MWh) under N-1 Conditions | 2.256 | 10.6047 | 12.6676 | 15.5222 | 17.6112 | 20.4393 | 27.5376 | 53.1609 | 72.9643 | 62.6435 | 114.8665 | 119.9881 | 139.8342 | 184.009 | 195.2376 | 195.8327 | 195.8327 | 195.8327 | 195.8327 | 195.8327 | 195.8327 | 195.8327 | 195.8327 | 195.8327 | 195.8327 | 195.8327 | 195.8327 | 195.8327 | 195.8327 | 195.8327
Weighted Energy @ Risk (MWh) under N-2 Conditions | 7.013 | 9.5557 | 10.8408 | 12.269 | 13.8076 | 15.5249 | 17.9127 | 22.1785 | 25.7354 | 27.063 | 33.0605 | 36.4078 | 40.5703 | 46.349 | 50.5538 | 50.6797 | 50.6797 | 50.6797 | 50.6797 | 50.6797 | 50.6797 | 50.6797 | 50.6797 | 50.6797 | 50.6797 | 50.6797 | 50.6797 | 50.6797 | 50.6797 | 50.6797
Total EUE (MWh) - Option 7 | 9.2689 | 20.1604 | 23.5084 | 27.7911 | 31.4188 | 35.9641 | 45.4503 | 75.3394 | 98.6997 | 89.7066 | 147.9896 | 156.401 | 180.5228 | 230.7123 | 246.1711 | 246.9075 | 246.9075 | 246.9075 | 246.9075 | 246.9075 | 246.9075 | 246.9075 | 246.9075 | 246.9075 | 246.9075 | 246.9075 | 246.9075 | 246.9075 | 246.9075 | 246.9075
Cost of EUE ($) - Option 7 | 394673.8567 | 858434.4176 | 1000994.2857 | 1183354.2871 | 1337823.2762 | 1531362.5145 | 1935286.2231 | 3207972.9402 | 4202660.3292 | 3819730.2991 | 6301440.037 | 6659597.6105 | 7686710.5898 | 9823795.6893 | 10482034.0894 | 10513390.0159 | 10513390.0159 | 10513390.0159 | 10513390.0159 | 10513390.0159 | 10513390.0159 | 10513390.0159 | 10513390.0159 | 10513390.0159 | 10513390.0159 | 10513390.0159 | 10513390.0159 | 10513390.0159 | 10513390.0159 | 10513390.0159
Option 8 - | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Weighted Energy @ Risk (MWh) under N Conditions | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.062696 | 0.0049965 | 0.11828 | 0.35438 | 0.37975 | 0.39514 | 0.39514 | 0.39514 | 0.39514 | 0.39514 | 0.39514 | 0.39514 | 0.39514 | 0.39514 | 0.39514 | 0.39514 | 0.39514 | 0.39514 | 0.39514 | 0.39514
Weighted Energy @ Risk (MWh) under N-1 Conditions | 2.256 | 10.6047 | 12.6676 | 15.5222 | 17.6112 | 20.4393 | 27.5376 | 53.1609 | 72.9643 | 62.6435 | 114.8665 | 119.9881 | 139.8342 | 184.009 | 195.2376 | 195.8327 | 195.8327 | 195.8327 | 195.8327 | 195.8327 | 195.8327 | 195.8327 | 195.8327 | 195.8327 | 195.8327 | 195.8327 | 195.8327 | 195.8327 | 195.8327 | 195.8327
Weighted Energy @ Risk (MWh) under N-2 Conditions | 7.013 | 9.5557 | 10.8408 | 12.269 | 13.8076 | 15.5249 | 17.9127 | 22.1785 | 25.7354 | 27.063 | 33.0605 | 36.4078 | 40.5703 | 46.349 | 50.5538 | 50.6797 | 50.6797 | 50.6797 | 50.6797 | 50.6797 | 50.6797 | 50.6797 | 50.6797 | 50.6797 | 50.6797 | 50.6797 | 50.6797 | 50.6797 | 50.6797 | 50.6797
Total EUE (MWh) - Option 8 | 9.2689 | 20.1604 | 23.5084 | 27.7911 | 31.4188 | 35.9641 | 45.4503 | 75.3394 | 98.6997 | 89.7066 | 147.9896 | 156.401 | 180.5228 | 230.7123 | 246.1711 | 246.9075 | 246.9075 | 246.9075 | 246.9075 | 246.9075 | 246.9075 | 246.9075 | 246.9075 | 246.9075 | 246.9075 | 246.9075 | 246.9075 | 246.9075 | 246.9075 | 246.9075
Cost of EUE ($) - Option 8 | 394673.8567 | 858434.4176 | 1000994.2857 | 1183354.2871 | 1337823.2762 | 1531362.5145 | 1935286.2231 | 3207972.9402 | 4202660.3292 | 3819730.2991 | 6301440.037 | 6659597.6105 | 7686710.5898 | 9823795.6893 | 10482034.0894 | 10513390.0159 | 10513390.0159 | 10513390.0159 | 10513390.0159 | 10513390.0159 | 10513390.0159 | 10513390.0159 | 10513390.0159 | 10513390.0159 | 10513390.0159 | 10513390.0159 | 10513390.0159 | 10513390.0159 | 10513390.0159 | 10513390.0159