## Info
Document description
This model Energy at Risk model has been developed to calculated Energy at Risk (EaR) in terms of Expected Unsureved Energy (EUE) and the cost of EUE. The modelling inputs, calculation steps and outputs are described in the 'Modelling Steps' tab. Further detail on EaR/EUE calculations can be found in AusNet's Network Planning Policy and Guidelines.
Tab # | Tab Name | Description | Source/ Inputs
0.1 | Modelling Steps | E@R model process flowchart and underlying equations | N/A
0.2 | Modelling Example & QA | Example E@R model calculations and data flow; also used to validate base case | N/A
0.3 | QA | Quality assurance and data validation | Entire workbook
1.1 | Output for AusNet's NPV Model | Aggregates Supply Risk ($M) and EUE (MWh) for input into AusNet’s NPV model | Summary tab
2.1 | Key Model Assumptions & Inputs | E@R model inputs and asset selection | Augmentation plans from RPs/EPCs, Embedded Generation DB, Demand Management DB
2.2 | Tx PoF | Transformer Probabilities of Failure | Provided by Asset Management Team
2.3 | Customer No. and Volume per Feeder | Customer consumption data | Provided by Finance Team
2.4 | AER VCR Rates (2024) | AER 2024 VCR rates | AER VCR Factsheet
2.5 | Forecast - Summer | Summer Forecast Data | Extract from Forecasting Toolbox
2.6 | Forecast- Winter | Winter Forecast Data | Extract from Forecasting Toolbox
2.7 | Ratings | Station Rating Data | AMS 20-101 / Provided by Asset mangement Team
2.8 | FT (Forecast & Transfers) | Forecast, transfer & PF inputs | Forecast Summer , Forecast Winter , NP Transfer Sheet, PF = avg. max demand PF across stations
2.9 | Load Duration Curves | Load duration curve data | LDC Tool; data sourced from PI SCADA Historian and AEMO
3.1 | Capacity N | Option N capacity calculated | FT Sheet, Ratings & Key Model Assumptions
3.2 | Capacity N-1 | Option N-1 capacity calculated | FT Sheet, Ratings & Key Model Assumptions
3.3 | Capacity N-1 | Option N-2 capacity calculated | FT Sheet, Ratings & Key Model Assumptions
3.4 | Demand | Calculates maximum demand | FT Sheet & Key Model Assumptions
3.5 | MD Weighted LDC | Maps maximum demand forecast to load duration curve | Demand Sheet & Load Duration Curve Sheet
3.6 | Locational VCR | Calculates tailored VCR by location using feeder energy mix and AER rates | AER VCR Rates (2024) & Customer No./Volume per Feeder
3.7 | E@R N | Calculates N EUE using capacity and demand inputs | MD Weighted LDC & Capacity N
3.8 | E@R N-1 | Calculates N-1 EUE using capacity and demand inputs | MD Weighted LDC & Capacity N-1
3.9 | E@R N-2 | Calculates N-2 EUE using capacity and demand inputs | MD Weighted LDC & Capacity N-2
4 | POF N,N-1 & N-2 Risk | Calculates Station N , N-1 & N-2 PoF's from Tx PoF Data & MTTR | TX PoF & Key Model Assumptions
4.1 | Summary | Collates weighted EUE and calculates supply risk | E@R & Locational VCR
Revision table
Date | Editted by | Change
2025-10-14 | HT | Draft Version 2.1
2025-10-20 | HT | Version 2.2
2025-11-10 | HT | Version 2.3 Example Page Update and General Refinements

## Modelling Steps
Eq1. Locational VCR |  | Data Inputs |  |  | Calculations |  |  |  |  | Outputs
|  |  | Customer No. and Vol per Feeder |  | Eq1.
Locational VCR
Eq2. Maximum Demand
AER Latetst VCR Rates
Eq3. Options & Do nothing Capacity
Eq6. & Eq7.
Load Forecast
[9 empty] | Summary Sheet | Output for AusNet's NPV Model
Eq4. Help Sheet | Re Name Forecasted LDC add Forecast MD to eq
Transfer Capacity
Eq2.
Eq5. Energy at Risk ( Option/ Do Nothing Capacity) |  |  |  |  | Options & Do Nothing Max Demand
Embeded Generation
Eq6. Weighted Expected Unserved Energy
[6 empty] | Eq.4 | Eq.5
Demand Mangement Capacity
[6 empty] | Forecasted LDC |  | Energy @ Risk Sheet
Eq7. Supply Risk
Load Duration Curves
|  |  | Asset Ratings |  | Eq3.
Options & Do Nothing Capacity
Planned & Proposed Works

## Modelling Steps Example & QA
End of Sheet
Data Inputs |  |  | Calculations | [12 empty] | Outputs
AER VCR Rates(2024 |  |  | Locational (Tailored VCR)
Category | Rate |  | Base case |  | Energy Usage (CY 2024 kWh) | Energy Usage (CY 2024 %) | Tailored VCR
Dec 24 AER VCR ($/kWh) - Res | 49.23 |  | Dec 24 AER VCR ($/kWh) - Res | 49.23 | 88661416.1819 | 59.86% | 29.4686
Dec 24 AER VCR ($/kWh) - Com | 34.39 |  | Dec 24 AER VCR ($/kWh) - Com | 34.39 | 45585213.1364 | 30.78% | 10.584
Dec 24 AER VCR ($/kWh) - Ind | 33.49 |  | Dec 24 AER VCR ($/kWh) - Ind | 33.49 | 5851096.6819 | 3.95% | 1.323
Dec 24 AER VCR ($/kWh) - Agr | 22.25 |  | Dec 24 AER VCR ($/kWh) - Agr | 22.25 | 8019086.0298 | 5.414% | 1.2046
[5 empty] | 148116812.03 |  | 42.5803
Customer No. and Vol per Feeder | [6 empty] | 42580.277 | [8 empty] | Summary |  | Outputs for NPV model
COMMERCIAL | 45585213.1364 | [14 empty] | Year | 2031 | Year | 2031
[16 empty] | E@R MWh | 8.6006 | E@R MWh | 8.6006
RESIDENTL | 88661416.1819 | [14 empty] | cost of EUE ($) | 366215.4289 | cost of EUE ($M) | 0.36622
FARM | 8019086.0298
INDUSTRIAL | 5851096.6819
Forecast (FCT)
Forecast | 2031
Summer POE50 | 40.6454
Summer POE10 | 49.5868
Winter POE50 | 42.4923
Winter POE10 | 45.4922
Transfer Capacity |  |  | Option Max Demand |  |  |  | MD Weighted LDC |  |  | E@R (N) |  | E@R (N-1) |  | E@R (N-2)
Year | 2031 |  | Forecast | 2031 |  |  | % of MD | Summer - AD - Hours | FY31 | % of MD | FY31 | % of MD | FY31 | % of MD | FY31
Capacity | 0 |  | Summer POE50 | 40.5354 |  |  | 100% | 0 | 40.5354 | 100% |  | 100% |  | 100%
|  |  | Summer POE10 | 49.4768 |  |  | 99% | 0.37816 | 40.13 | 99% |  | 99% | 1.9032 | 99% | 8.5778
Embedded Generation |  |  | Winter POE50 | 42.3823 |  |  | 98% | 0.37816 | 39.7246 | 98% |  | 98% | 0 | 98% | 0
|  |  | Winter POE10 | 45.3822 |  |  | 97% | 0.37816 | 39.3193 | 97% |  | 97% | 0 | 97% | 0
Year | 2031 | [5 empty] | 95% | 0.75633 | 38.5086 | 95% |  | 95% | 1.3667 | 95% | 8.0413
Capacity | 0.11 | [5 empty] | 90% | 9.0759 | 36.4818 | 90% |  | 90% | 18.2632 | 90% | 165.1044
[7 empty] | 85% | 40.4636 | 34.455 | 85% |  | 85% | 10.815 | 85% | 559.2785
Demand Mangement | [6 empty] | 80% | 94.5411 | 32.4283 | 80% |  | 80% |  | 80% | 853.9736
[7 empty] | 75% | 197.0236 | 30.4015 | 75% |  | 75% |  | 75% | 1410.6614
Year | 2031 | [5 empty] | 70% | 336.9444 | 28.3747 | 70% |  | 70% |  | 70% | 1642.4083
Capacity | 0 | [5 empty] | 65% | 521.4885 | 26.348 | 65% |  | 65% |  | 65% | 1792.1753
[7 empty] | 60% | 812.675 | 24.3212 | 60% |  | 60% |  | 60% | 2237.6502
LDC | [6 empty] | 55% | 1202.1843 | 22.2944 | 55% |  | 55% |  | 55% | 2203.7758
[7 empty] | 50% | 1686.2345 | 20.2677 | 50% |  | 50% |  | 50% | 1757.6154
% of MD | Summer - AD - Duration % | Summer - AD - Hours |  |  |  |  | 45% | 2129.0649 | 18.2409 | 45% |  | 45% |  | 45% | 710.4292
100% | 0% | 0 |  |  |  |  | 40% | 2484.5393 | 16.2141 | 40% |  | 40% |  | 40% | 30.6206
99% | 0.00861% | 0.37816 |  |  |  |  | 35% | 2808.248 | 14.1874 | 35% |  | 35% |  | 35%
98% | 0.00861% | 0.37816 |  |  |  |  | 30% | 3095.6528 | 12.1606 | 30% |  | 30% |  | 30%
97% | 0.00861% | 0.37816 |  |  |  |  | 25% | 3358.8552 | 10.1338 | 25% |  | 25% |  | 25%
95% | 0.01722% | 0.75633 |  |  |  |  | 20% | 3588.7791 | 8.1071 | 20% |  | 20% |  | 20%
90% | 0.2066% | 9.0759 |  |  |  |  | 15% | 3802.4419 | 6.0803 | 15% |  | 15% |  | 15%
85% | 0.9213% | 40.4636 |  |  |  |  | 10% | 4024.8025 | 4.0535 | 10% |  | 10% |  | 10%
80% | 2.153% | 94.5411 |  |  |  |  | 5% | 4239.978 | 2.0268 | 5% |  | 5% |  | 5%
75% | 4.486% | 197.0236 |  |  |  |  | 9.992e-14% | 4391.6218 | 4.0503e-14 | 9.992e-14% |  | 9.992e-14% |  | 9.992e-14%
70% | 7.672% | 336.9444 | [7 empty] | Total E@R | 0 | Total E@R | 32.0245 | Total E@R | 13246.5087
65% | 11.87% | 521.4885 | [7 empty] | Total WE@R | 0 | Total WE@R | 0.55296 | Total WE@R | 2.0872
60% | 18.5% | 812.675 |  |  |  |  | MD Weighted LDC
55% | 27.37% | 1202.1843
50% | 38.39% | 1686.2345 |  |  |  |  | % of MD | Summer - MD - Hours | FY31
45% | 48.48% | 2129.0649 |  |  |  |  | 100% | 0 | 49.4768 | E@R (N) |  | E@R (N-1) |  | E@R (N-2)
40% | 56.57% | 2484.5393 |  |  |  |  | 99% | 0 | 48.982
35% | 63.94% | 2808.248 |  |  |  |  | 98% | 0 | 48.4873 | % of MD | FY31 | % of MD | FY31 | % of MD | FY31
30% | 70.48% | 3095.6528 |  |  |  |  | 97% | 0.37816 | 47.9925 | 100% |  | 100% |  | 100%
25% | 76.48% | 3358.8552 |  |  |  |  | 95% | 0.37816 | 47.003 | 99% |  | 99% | 0 | 99% | 0
20% | 81.71% | 3588.7791 |  |  |  |  | 90% | 0.75633 | 44.5291 | 98% |  | 98% | 0 | 98% | 0
15% | 86.58% | 3802.4419 |  |  |  |  | 85% | 1.1345 | 42.0553 | 97% |  | 97% | 4.8934 | 97% | 11.568
10% | 91.64% | 4024.8025 |  |  |  |  | 80% | 2.6471 | 39.5815 | 95% |  | 95% | 0 | 95% | 0
5% | 96.54% | 4239.978 |  |  |  |  | 75% | 3.4035 | 37.1076 | 90% |  | 90% | 3.9579 | 90% | 10.6325
9.992e-14% | 99.99% | 4391.6218 |  |  |  |  | 70% | 5.6725 | 34.6338 | 85% |  | 85% | 3.0224 | 85% | 9.697
[7 empty] | 65% | 6.4288 | 32.1599 | 80% |  | 80% | 8.3474 | 80% | 35.0458
[7 empty] | 60% | 11.3449 | 29.6861 | 75% |  | 75% | 2.3027 | 75% | 15.6519
[7 empty] | 55% | 35.5474 | 27.2122 | 70% |  | 70% | 1.4984 | 70% | 41.3425
LDC | [6 empty] | 50% | 95.2974 | 24.7384 | 65% |  | 65% |  | 65% | 11.9098
[7 empty] | 45% | 208.7467 | 22.2646 | 60% |  | 60% |  | 60% | 65.2519
% of MD | Summer - MD - Duration % | Summer - MD - Hours |  |  |  |  | 40% | 380.4333 | 19.7907 | 55% |  | 55% |  | 55% | 261.367
100% | 0% | 0 |  |  |  |  | 35% | 696.5786 | 17.3169 | 50% |  | 50% |  | 50% | 497.438
99% | 0% | 0 |  |  |  |  | 30% | 1260.7997 | 14.843 | 45% |  | 45% |  | 45% | 663.8471
98% | 0% | 0 |  |  |  |  | 25% | 1965.3198 | 12.3692 | 40% |  | 40% |  | 40% | 579.8966
97% | 0.00861% | 0.37816 |  |  |  |  | 20% | 2490.2118 | 9.8954 | 35% |  | 35% |  | 35% | 292.8244
95% | 0.00861% | 0.37816 |  |  |  |  | 15% | 2997.7083 | 7.4215 | 30% |  | 30% |  | 30%
90% | 0.01722% | 0.75633 |  |  |  |  | 10% | 3491.5908 | 4.9477 | 25% |  | 25% |  | 25%
85% | 0.02583% | 1.1345 |  |  |  |  | 5% | 3955.9766 | 2.4738 | 20% |  | 20% |  | 20%
80% | 0.06027% | 2.6471 |  |  |  |  | 9.992e-14% | 4391.6218 | 4.9437e-14 | 15% |  | 15% |  | 15%
75% | 0.07749% | 3.4035 | [7 empty] | 10% |  | 10% |  | 10%
70% | 0.1292% | 5.6725 | [7 empty] | 5% |  | 5% |  | 5%
65% | 0.1464% | 6.4288 | [7 empty] | 9.992e-14% |  | 9.992e-14% |  | 9.992e-14%
60% | 0.2583% | 11.3449 | [7 empty] | Total E@R | 0 | Total E@R | 23.782 | Total E@R | 2471.5078
55% | 0.8094% | 35.5474 |  |  |  |  | MD Weighted LDC |  |  | Total WE@R | 0 | Total WE@R | 0.17599 | Total WE@R | 0.1669
50% | 2.17% | 95.2974
45% | 4.753% | 208.7467 |  |  |  |  | % of MD | Winter - AD - Hours | FY31
40% | 8.662% | 380.4333 |  |  |  |  | 100% | 0 | 42.3823
35% | 15.86% | 696.5786 |  |  |  |  | 99% | 0.2972 | 41.9585 | E@R (N) |  | E@R (N-1) |  | E@R (N-2)
30% | 28.71% | 1260.7997 |  |  |  |  | 98% | 0.2972 | 41.5347
25% | 44.75% | 1965.3198 |  |  |  |  | 97% | 0.2972 | 41.1108 | % of MD | FY31 | % of MD | FY31 | % of MD | FY31
20% | 56.7% | 2490.2118 |  |  |  |  | 95% | 1.486 | 40.2632 | 100% |  | 100% |  | 100%
15% | 68.25% | 2997.7083 |  |  |  |  | 90% | 8.6188 | 38.1441 | 99% |  | 99% | 1.8041 | 99% | 7.1685
10% | 79.5% | 3491.5908 |  |  |  |  | 85% | 40.1218 | 36.025 | 98% |  | 98% | 0 | 98% | 0
5% | 90.07% | 3955.9766 |  |  |  |  | 80% | 93.0231 | 33.9058 | 97% |  | 97% | 0 | 97% | 0
9.992e-14% | 99.99% | 4391.6218 |  |  |  |  | 75% | 197.0426 | 31.7867 | 95% |  | 95% | 5.453 | 95% | 26.9107
[7 empty] | 70% | 378.0365 | 29.6676 | 90% |  | 90% | 22.1375 | 90% | 150.8839
[7 empty] | 65% | 616.0926 | 27.5485 | 85% |  | 85% | 31.0571 | 85% | 599.6452
[7 empty] | 60% | 934.9866 | 25.4294 | 80% |  | 80% |  | 80% | 894.8474
LDC | [6 empty] | 55% | 1310.9428 | 23.3103 | 75% |  | 75% |  | 75% | 1539.1021
[7 empty] | 50% | 1730.2899 | 21.1912 | 70% |  | 70% |  | 70% | 2294.4906
% of MD | Winter - AD (P50) - Duration % | Winter - AD - Hours |  |  |  |  | 45% | 2168.0633 | 19.072 | 65% |  | 65% |  | 65% | 2513.4087
100% | 0% | 0 |  |  |  |  | 40% | 2609.7004 | 16.9529 | 60% |  | 60% |  | 60% | 2691.1276
99% | 0.006767% | 0.2972 |  |  |  |  | 35% | 2998.1389 | 14.8338 | 55% |  | 55% |  | 55% | 2375.977
98% | 0.006767% | 0.2972 |  |  |  |  | 30% | 3309.3057 | 12.7147 | 50% |  | 50% |  | 50% | 1761.5555
97% | 0.006767% | 0.2972 |  |  |  |  | 25% | 3537.8514 | 10.5956 | 45% |  | 45% |  | 45% | 911.2667
95% | 0.03383% | 1.486 |  |  |  |  | 20% | 3731.0305 | 8.4765 | 40% |  | 40% |  | 40% | 108.8464
90% | 0.1962% | 8.6188 |  |  |  |  | 15% | 3910.2412 | 6.3573 | 35% |  | 35% |  | 35%
85% | 0.9135% | 40.1218 |  |  |  |  | 10% | 4075.1864 | 4.2382 | 30% |  | 30% |  | 30%
80% | 2.118% | 93.0231 |  |  |  |  | 5% | 4251.7223 | 2.1191 | 25% |  | 25% |  | 25%
75% | 4.486% | 197.0426 |  |  |  |  | 9.992e-14% | 4391.7028 | 4.2348e-14 | 20% |  | 20% |  | 20%
70% | 8.607% | 378.0365 | [7 empty] | 15% |  | 15% |  | 15%
65% | 14.03% | 616.0926 | [7 empty] | 10% |  | 10% |  | 10%
60% | 21.29% | 934.9866 | [7 empty] | 5% |  | 5% |  | 5%
55% | 29.85% | 1310.9428 | [7 empty] | 9.992e-14% |  | 9.992e-14% |  | 9.992e-14%
50% | 39.4% | 1730.2899 |  |  |  |  | MD Weighted LDC |  |  | Total E@R | 0 | Total E@R | 59.8472 | Total E@R | 15716.478
45% | 49.36% | 2168.0633 | [7 empty] | Total WE@R | 0 | Total WE@R | 0.87797 | Total WE@R | 2.104
40% | 59.42% | 2609.7004 |  |  |  |  | % of MD | Winter - MD - Hours | FY31
35% | 68.26% | 2998.1389 |  |  |  |  | 100% | 0 | 45.3822 | E@R (N) |  | E@R (N-1) |  | E@R (N-2)
30% | 75.35% | 3309.3057 |  |  |  |  | 99% | 0.2972 | 44.9284
25% | 80.55% | 3537.8514 |  |  |  |  | 98% | 0.2972 | 44.4746 | % of MD | FY31 | % of MD | FY31 | % of MD | FY31
20% | 84.95% | 3731.0305 |  |  |  |  | 97% | 0.2972 | 44.0208 | 100% |  | 100% |  | 100%
15% | 89.03% | 3910.2412 |  |  |  |  | 95% | 1.486 | 43.1131 | 99% |  | 99% | 2.6912 | 99% | 8.0557
10% | 92.79% | 4075.1864 |  |  |  |  | 90% | 8.6188 | 40.844 | 98% |  | 98% | 0 | 98% | 0
5% | 96.81% | 4251.7223 |  |  |  |  | 85% | 40.1218 | 38.5749 | 97% |  | 97% | 0 | 97% | 0
9.992e-14% | 99.99% | 4391.7028 |  |  |  |  | 80% | 93.0231 | 36.3058 | 95% |  | 95% | 8.8767 | 95% | 30.3344
[7 empty] | 75% | 197.0426 | 34.0367 | 90% |  | 90% | 41.9304 | 90% | 170.6769
[7 empty] | 70% | 378.0365 | 31.7676 | 85% |  | 85% | 113.7089 | 85% | 682.3388
[7 empty] | 65% | 616.0926 | 29.4985 | 80% |  | 80% | 70.906 | 80% | 1025.7752
LDC | [6 empty] | 60% | 934.9866 | 27.2293 | 75% |  | 75% | 0.97067 | 75% | 1780.9419
[7 empty] | 55% | 1310.9428 | 24.9602 | 70% |  | 70% |  | 70% | 2688.1435
% of MD | Winter - MD (P10) - Duration % | Winter - MD - Hours |  |  |  |  | 50% | 1730.2899 | 22.6911 | 65% |  | 65% |  | 65% | 2995.4612
100% | 0% | 0 |  |  |  |  | 45% | 2168.0633 | 20.422 | 60% |  | 60% |  | 60% | 3289.0403
99% | 0.006767% | 0.2972 |  |  |  |  | 40% | 2609.7004 | 18.1529 | 55% |  | 55% |  | 55% | 3024.4867
98% | 0.006767% | 0.2972 |  |  |  |  | 35% | 2998.1389 | 15.8838 | 50% |  | 50% |  | 50% | 2422.0123
97% | 0.006767% | 0.2972 |  |  |  |  | 30% | 3309.3057 | 13.6147 | 45% |  | 45% |  | 45% | 1535.0798
95% | 0.03383% | 1.486 |  |  |  |  | 25% | 3537.8514 | 11.3456 | 40% |  | 40% |  | 40% | 546.5039
90% | 0.1962% | 8.6188 |  |  |  |  | 20% | 3731.0305 | 9.0764 | 35% |  | 35% |  | 35% | 0.90619
85% | 0.9135% | 40.1218 |  |  |  |  | 15% | 3910.2412 | 6.8073 | 30% |  | 30% |  | 30%
80% | 2.118% | 93.0231 |  |  |  |  | 10% | 4075.1864 | 4.5382 | 25% |  | 25% |  | 25%
75% | 4.486% | 197.0426 |  |  |  |  | 5% | 4251.7223 | 2.2691 | 20% |  | 20% |  | 20%
70% | 8.607% | 378.0365 |  |  |  |  | 9.992e-14% | 4391.7028 | 4.5346e-14 | 15% |  | 15% |  | 15%
65% | 14.03% | 616.0926 | [7 empty] | 10% |  | 10% |  | 10%
60% | 21.29% | 934.9866 | [7 empty] | 5% |  | 5% |  | 5%
55% | 29.85% | 1310.9428 | [7 empty] | 9.992e-14% |  | 9.992e-14% |  | 9.992e-14%
50% | 39.4% | 1730.2899 | [7 empty] | Total E@R | 0 | Total E@R | 236.6931 | Total E@R | 19997.7591
45% | 49.36% | 2168.0633 | [7 empty] | Total WE@R | 0 | Total WE@R | 1.4881 | Total WE@R | 1.1474
40% | 59.42% | 2609.7004
35% | 68.26% | 2998.1389
30% | 75.35% | 3309.3057
25% | 80.55% | 3537.8514
20% | 84.95% | 3731.0305
15% | 89.03% | 3910.2412
10% | 92.79% | 4075.1864
5% | 96.81% | 4251.7223
9.992e-14% | 99.99% | 4391.7028
Ratings (MVA) |  |  |  | Option Capacity
SCR (N) | 55.8 |  |  | Year | 2031
SCR (N-1) | 35.3 |  |  | SCR (N) | 55.8
SCR (N-2) | 17.65 |  |  | SCR (N-1) | 35.3
WCR (N) | 56.8 |  |  | SCR (N-2) | 17.65
WCR (N-1) | 36.1 |  |  | WCR (N) | 56.8
WCR (N-2) | 18.05 |  |  | WCR (N-1) | 36.1
|  |  |  | WCR (N-2) | 18.05
Planned Works
Year | 2031
Capacity (N) | 0
Capacity (N-1) | 0
Capacity (N-2) | 0
Power Factor
Value | 0.99
End of Sheet

## QA
Overall Status
Good
Number | Check Name | Status | Info
1 | Forecast | Good | Confirms POE10 forecast is higher than POE50
2 | Option Maximum Demand | Good | Confirms whether transfers, embedded generation, and demand management contribute to demand reduction when present
3 | EUE Base Case | Good | Confirms Do Nothing/Base Case EUE for FY31 is the same as the example / checks model in Modelling Steps Example Sheet
4 | Feeder Consumption | Good | Confirms if aggregated feeder energy consumption by customer category matches with total feeder energy consumption (excluding uncategorised consumption)

## Output for AusNet's NPV model
Involuntary load shedding (NER 5.17.1(c)(4)(ii))
Base Case
Cost
Option 1 - Do Nothing | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Cost of EUE ($M) | 0.08828 | 0.15484 | 0.18134 | 0.21763 | 0.24652 | 0.28515 | 0.36622 | 0.6538 | 0.89977 | 0.79091 | 1.476 | 1.5408 | 1.8403 | 2.5111 | 2.6912 | 2.6984 | 2.6984 | 2.6984 | 2.6984 | 2.6984 | 2.6984 | 2.6984 | 2.6984 | 2.6984 | 2.6984 | 2.6984 | 2.6984 | 2.6984 | 2.6984 | 2.6984
Total EUE (MWh) | 2.0733 | 3.6364 | 4.2587 | 5.1111 | 5.7895 | 6.6967 | 8.6006 | 15.3544 | 21.1311 | 18.5746 | 34.6642 | 36.1849 | 43.2184 | 58.9741 | 63.2029 | 63.3724 | 63.3724 | 63.3724 | 63.3724 | 63.3724 | 63.3724 | 63.3724 | 63.3724 | 63.3724 | 63.3724 | 63.3724 | 63.3724 | 63.3724 | 63.3724 | 63.3724
Residual Values
Option 2 - Replace 3 x 10/13.5 MVA Tx with 3 x 20/33 MVA Tx | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Cost of Avoided EUE ($M) | 0.088249 | 0.15484 | 0.18134 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total EUE (MWh) | 2.0725 | 3.6364 | 4.2587 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 - Replace 1 x 10/13.5 MVA Tx with 1 x 20/33 MVA Tx | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Cost of Avoided EUE ($M) | 0.088249 | 0.15484 | 0.18134 | 0.0019397 | 0.0023384 | 0.0028923 | 0.0042131 | 0.0092716 | 0.013747 | 0.011967 | 0.024691 | 0.026724 | 0.032923 | 0.046447 | 0.051338 | 0.051505 | 0.051505 | 0.051505 | 0.051505 | 0.051505 | 0.051505 | 0.051505 | 0.051505 | 0.051505 | 0.051505 | 0.051505 | 0.051505 | 0.051505 | 0.051505 | 0.051505
Total EUE (MWh) | 2.0725 | 3.6364 | 4.2587 | 0.045553 | 0.054917 | 0.067927 | 0.098946 | 0.21774 | 0.32284 | 0.28105 | 0.57986 | 0.62762 | 0.77321 | 1.0908 | 1.2057 | 1.2096 | 1.2096 | 1.2096 | 1.2096 | 1.2096 | 1.2096 | 1.2096 | 1.2096 | 1.2096 | 1.2096 | 1.2096 | 1.2096 | 1.2096 | 1.2096 | 1.2096
Option 4 - Construct 2x 20/33MVA zone substation in Inverloch | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Cost of Avoided EUE ($M) | 0.088249 | 0.15484 | 0.18134 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total EUE (MWh) | 2.0725 | 3.6364 | 4.2587 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 - Contract network support services to defer network investment | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Cost of Avoided EUE ($M) | 0.046115 | 0.074785 | 0.086297 | 0.10061 | 0.11436 | 0.13048 | 0.15819 | 0.25036 | 0.33996 | 0.30507 | 0.57822 | 0.59252 | 0.71922 | 1.021 | 1.1055 | 1.1076 | 1.1076 | 1.1076 | 1.1076 | 1.1076 | 1.1076 | 1.1076 | 1.1076 | 1.1076 | 1.1076 | 1.1076 | 1.1076 | 1.1076 | 1.1076 | 1.1076
Total EUE (MWh) | 1.083 | 1.7563 | 2.0267 | 2.3629 | 2.6857 | 3.0642 | 3.7152 | 5.8798 | 7.9839 | 7.1647 | 13.5795 | 13.9153 | 16.8909 | 23.9782 | 25.9627 | 26.0121 | 26.0121 | 26.0121 | 26.0121 | 26.0121 | 26.0121 | 26.0121 | 26.0121 | 26.0121 | 26.0121 | 26.0121 | 26.0121 | 26.0121 | 26.0121 | 26.0121
Option 6 - | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Cost of Avoided EUE ($M) | 0.088249 | 0.15484 | 0.18134 | 0.21763 | 0.24652 | 0.28515 | 0.36622 | 0.6538 | 0.89977 | 0.79091 | 1.476 | 1.5408 | 1.8403 | 2.5111 | 2.6912 | 2.6984 | 2.6984 | 2.6984 | 2.6984 | 2.6984 | 2.6984 | 2.6984 | 2.6984 | 2.6984 | 2.6984 | 2.6984 | 2.6984 | 2.6984 | 2.6984 | 2.6984
Total EUE (MWh) | 2.0725 | 3.6364 | 4.2587 | 5.1111 | 5.7895 | 6.6967 | 8.6006 | 15.3544 | 21.1311 | 18.5746 | 34.6642 | 36.1849 | 43.2184 | 58.9741 | 63.2029 | 63.3724 | 63.3724 | 63.3724 | 63.3724 | 63.3724 | 63.3724 | 63.3724 | 63.3724 | 63.3724 | 63.3724 | 63.3724 | 63.3724 | 63.3724 | 63.3724 | 63.3724
Option 7 - | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Cost of Avoided EUE ($M) | 0.088249 | 0.15484 | 0.18134 | 0.21763 | 0.24652 | 0.28515 | 0.36622 | 0.6538 | 0.89977 | 0.79091 | 1.476 | 1.5408 | 1.8403 | 2.5111 | 2.6912 | 2.6984 | 2.6984 | 2.6984 | 2.6984 | 2.6984 | 2.6984 | 2.6984 | 2.6984 | 2.6984 | 2.6984 | 2.6984 | 2.6984 | 2.6984 | 2.6984 | 2.6984
Total EUE (MWh) | 2.0725 | 3.6364 | 4.2587 | 5.1111 | 5.7895 | 6.6967 | 8.6006 | 15.3544 | 21.1311 | 18.5746 | 34.6642 | 36.1849 | 43.2184 | 58.9741 | 63.2029 | 63.3724 | 63.3724 | 63.3724 | 63.3724 | 63.3724 | 63.3724 | 63.3724 | 63.3724 | 63.3724 | 63.3724 | 63.3724 | 63.3724 | 63.3724 | 63.3724 | 63.3724
Option 8 - | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Cost of Avoided EUE ($M) | 0.088249 | 0.15484 | 0.18134 | 0.21763 | 0.24652 | 0.28515 | 0.36622 | 0.6538 | 0.89977 | 0.79091 | 1.476 | 1.5408 | 1.8403 | 2.5111 | 2.6912 | 2.6984 | 2.6984 | 2.6984 | 2.6984 | 2.6984 | 2.6984 | 2.6984 | 2.6984 | 2.6984 | 2.6984 | 2.6984 | 2.6984 | 2.6984 | 2.6984 | 2.6984
Total EUE (MWh) | 2.0725 | 3.6364 | 4.2587 | 5.1111 | 5.7895 | 6.6967 | 8.6006 | 15.3544 | 21.1311 | 18.5746 | 34.6642 | 36.1849 | 43.2184 | 58.9741 | 63.2029 | 63.3724 | 63.3724 | 63.3724 | 63.3724 | 63.3724 | 63.3724 | 63.3724 | 63.3724 | 63.3724 | 63.3724 | 63.3724 | 63.3724 | 63.3724 | 63.3724 | 63.3724

## Key Model Assumption & Inputs
Select ZSS & Region | WGI | East | MTTR
Probability Weighting for 10% POE MDs | 30% |  |  | Central | North | East | For Analysis
Probability Weighting for 50% POE MDs | 70% |  | N-1 MTTR (years) | 0.3858 | 0.1418 | 0.3858 | 0.3858
First year of analysis | FY25 |  | N-2 MTTR (years) | 0.2344 | 0.049 | 0.2344 | 0.2344
Select Sensitivity Variant | Forecast Sensitivity
Low | 90% |  | PV Factor's |  |  | PoF Sensitvity
Options | Name |  | Summer | 1.33 |  | Varaint
Option 1 - Do Nothing | Do Nothing |  | Winter | 1.13 |  | Base | 100%
Option 2 - Replace 3 x 10/13.5 MVA Tx with 3 x 20/33 MVA Tx | Replace 3 x 10/13.5 MVA Tx with 3 x 20/33 MVA Tx
Option 3 - Replace 1 x 10/13.5 MVA Tx with 1 x 20/33 MVA Tx | Replace 1 x 10/13.5 MVA Tx with 1 x 20/33 MVA Tx |  | Demand Response
Option 4 - Construct 2x 20/33MVA zone substation in Inverloch | Construct 2x 20/33MVA zone substation in Inverloch |  | Average Rate % | 20%
Option 5 - Contract network support services to defer network investment | Contract network support services to defer network investment
Option 6 -
Option 7 -
Option 8 -
Added Capacity (MVA) | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39
Added Capacity (MVA) Option 1 N | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 1 N-1 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 1 N-2 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 2 N |  |  |  | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2
Added Capacity (MVA) Option 2 N-1 |  |  |  | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2
Added Capacity (MVA) Option 2 N-2 |  |  |  | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2
Added Capacity (MVA) Option 3 N |  |  |  | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35
Added Capacity (MVA) Option 3 N-1 |  |  |  | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35
Added Capacity (MVA) Option 3 N-2 |  |  |  | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35
Added Capacity (MVA) Option 4 N | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 4 N-1 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 4 N-2 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 5 N | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 5 N-1 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 5 N-2 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 6 N | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 6 N-1 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 6 N-2 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 7 N | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 7 N-1 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 7 N-2 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 8 N | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 8 N-1 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 8 N-2 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Embedded Generation (MVA) | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39
Avaliable Embedded Generation (MVA) Option 1 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11
Added Embedded Generation (MVA) Option 2 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Embedded Generation (MVA) Option 3 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Embedded Generation (MVA) Option 4 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Embedded Generation (MVA) Option 5 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Embedded Generation (MVA) Option 6 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Embedded Generation (MVA) Option 7 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Embedded Generation (MVA) Option 8 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Demand Management (MVA) | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39
Avaliable Demand Management (MVA) Option 1 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Demand Management (MVA) Option 2 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Demand Management (MVA) Option 3 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Demand Management (MVA) Option 4 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Demand Management (MVA) Option 5 | 4.0981 | 4.3758 | 4.3835 | 4.3752 | 4.3773 | 4.3925 | 4.4232 | 4.4774 | 4.5056 | 4.526 | 4.5569 | 4.5963 | 4.644 | 4.6689 | 4.6608
Added Demand Management (MVA) Option 6 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Demand Management (MVA) Option 7 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Demand Management (MVA) Option 8 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Transfers (MVA) | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39
Planned Transfers (MVA) Option 1 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Transfers (MVA) Option 2 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Transfers (MVA) Option 3 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Transfers (MVA) Option 4 |  |  |  | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66
Added Transfers (MVA) Option 5 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Transfers (MVA) Option 6 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Transfers (MVA) Option 7 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Transfers (MVA) Option 8 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Block Loads Not in Forecast (MVA) | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39
Block Loads (MVA) | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Base | FY25: 100%
High | FY25: 110%
Low | FY25: 90%

## Tx PoF
Transformer Failure Rates for individual Transformers
[5 empty] | 10 | 8 | 10 | 6 | 8 | 6 | 6 | 10 | 6
Zone | arm_asset_id | floc | user_status | Age | Major Winding insulation | Accelerated cellulose Aging | Winding insulating liquid | Hot metal fault covered by paper | Chemical contamination, degradation | Physical & chemical contamination, degradation | Physical contamination | Short Circuit Concern | OLTC | WMA Health Score | WMA CS | WMA effective age | WMA Beta | WMA Eta | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WGI | 30192717 | DS-WGI-TRNFMR-9000004493 |  | 59 | 5 | 3 | 1 | 5 | 2 | 1 | 5 | 5 | 5 | 351.4286 | 4 | 60 | 3.5 | 82 | 1.976% | 1.976% | 2.058% | 2.142% | 2.227% | 2.315% | 2.405% | 2.496% | 2.59% | 2.686% | 2.783% | 2.883% | 2.985% | 3.089% | 3.195% | 3.303% | 3.413% | 3.525% | 3.639% | 3.755% | 3.873% | 3.994% | 4.116% | 4.241% | 4.368% | 4.497% | 4.628% | 4.761% | 4.897% | 5.034%
WGI | 30111322 | DS-WGI-TRNFMR-9000003147 |  | 59 | 5 | 5 | 1 | 3 | 2 | 1 | 4 | 5 | 5 | 348.5714 | 3 | 44 | 3.5 | 82 | 0.9218% | 0.9218% | 0.9742% | 1.028% | 1.084% | 1.142% | 1.201% | 1.262% | 1.325% | 1.39% | 1.457% | 1.525% | 1.596% | 1.668% | 1.742% | 1.818% | 1.896% | 1.976% | 2.058% | 2.142% | 2.227% | 2.315% | 2.405% | 2.496% | 2.59% | 2.686% | 2.783% | 2.883% | 2.985% | 3.089%
EPG | 30026486 | DS-EPG-TRNFMR-9000010175 |  | 45 | 5 | 3 | 2 | 1 | 2 | 1 | 4 | 5 | 5 | 322.8571 | 3 | 44 | 3.5 | 84.05 | 0.8458% | 0.8458% | 0.8939% | 0.9436% | 0.9949% | 1.048% | 1.102% | 1.159% | 1.216% | 1.276% | 1.337% | 1.4% | 1.465% | 1.531% | 1.599% | 1.669% | 1.741% | 1.814% | 1.889% | 1.966% | 2.045% | 2.125% | 2.208% | 2.292% | 2.378% | 2.466% | 2.556% | 2.648% | 2.741% | 2.837%
EPG | 30058367 | DS-EPG-TRNFMR-9000010174 |  | 45 | 5 | 3 | 2 | 1 | 2 | 1 | 4 | 5 | 5 | 322.8571 | 3 | 44 | 3.5 | 84.05 | 0.8458% | 0.8458% | 0.8939% | 0.9436% | 0.9949% | 1.048% | 1.102% | 1.159% | 1.216% | 1.276% | 1.337% | 1.4% | 1.465% | 1.531% | 1.599% | 1.669% | 1.741% | 1.814% | 1.889% | 1.966% | 2.045% | 2.125% | 2.208% | 2.292% | 2.378% | 2.466% | 2.556% | 2.648% | 2.741% | 2.837%
WGI | 30475971 | DS-WGI-TRNFMR-9000007146 |  | 49 | 5 | 5 | 1 | 1 | 1 | 1 | 2 | 5 | 1 | 268.5714 | 3 | 44 | 3.5 | 82 | 0.9218% | 0.9218% | 0.9742% | 1.028% | 1.084% | 1.142% | 1.201% | 1.262% | 1.325% | 1.39% | 1.457% | 1.525% | 1.596% | 1.668% | 1.742% | 1.818% | 1.896% | 1.976% | 2.058% | 2.142% | 2.227% | 2.315% | 2.405% | 2.496% | 2.59% | 2.686% | 2.783% | 2.883% | 2.985% | 3.089%
EPG | 30209984 | DS-EPG-TRNFMR-9000007095 |  | 24 | 3 | 3 | 1 | 3 | 2 | 1 | 4 | 3 | 3 | 251.4286 | 3 | 44 | 3.5 | 84.05 | 0.8458% | 0.8458% | 0.8939% | 0.9436% | 0.9949% | 1.048% | 1.102% | 1.159% | 1.216% | 1.276% | 1.337% | 1.4% | 1.465% | 1.531% | 1.599% | 1.669% | 1.741% | 1.814% | 1.889% | 1.966% | 2.045% | 2.125% | 2.208% | 2.292% | 2.378% | 2.466% | 2.556% | 2.648% | 2.741% | 2.837%
CLN | 30338702 | DS-CLN-TRNFMR-9000006730 |  | 21 | 3 | 2 | 2 | 3 | 1 | 1 | 3 | 3 | 2 | 225.7143 | 2 | 24 | 3.5 | 84.05 | 0.1909% | 0.1909% | 0.211% | 0.2322% | 0.2547% | 0.2785% | 0.3035% | 0.3298% | 0.3575% | 0.3865% | 0.4168% | 0.4486% | 0.4817% | 0.5162% | 0.5522% | 0.5897% | 0.6286% | 0.669% | 0.7109% | 0.7543% | 0.7993% | 0.8458% | 0.8939% | 0.9436% | 0.9949% | 1.048% | 1.102% | 1.159% | 1.216% | 1.276%
CRE | 30165029 | DS-CRE-TRNFMR-9000525811 |  | 13 | 3 | 2 | 1 | 3 | 2 | 1 | 4 | 2 | 2 | 217.1429 | 2 | 24 | 3.5 | 84.05 | 0.1909% | 0.1909% | 0.211% | 0.2322% | 0.2547% | 0.2785% | 0.3035% | 0.3298% | 0.3575% | 0.3865% | 0.4168% | 0.4486% | 0.4817% | 0.5162% | 0.5522% | 0.5897% | 0.6286% | 0.669% | 0.7109% | 0.7543% | 0.7993% | 0.8458% | 0.8939% | 0.9436% | 0.9949% | 1.048% | 1.102% | 1.159% | 1.216% | 1.276%
LLG | 30359074 | DS-LLG-TRNFMR-9000007796 |  | 20 | 1 | 2 | 1 | 2 | 1 | 1 | 5 | 3 | 2 | 191.4286 | 2 | 24 | 3.5 | 84.05 | 0.1909% | 0.1909% | 0.211% | 0.2322% | 0.2547% | 0.2785% | 0.3035% | 0.3298% | 0.3575% | 0.3865% | 0.4168% | 0.4486% | 0.4817% | 0.5162% | 0.5522% | 0.5897% | 0.6286% | 0.669% | 0.7109% | 0.7543% | 0.7993% | 0.8458% | 0.8939% | 0.9436% | 0.9949% | 1.048% | 1.102% | 1.159% | 1.216% | 1.276%
CRE | 30380287 | DS-CRE-TRNFMR-9000525810 |  | 13 | 2 | 2 | 1 | 1 | 2 | 1 | 3 | 2 | 2 | 177.1429 | 2 | 24 | 3.5 | 84.05 | 0.1909% | 0.1909% | 0.211% | 0.2322% | 0.2547% | 0.2785% | 0.3035% | 0.3298% | 0.3575% | 0.3865% | 0.4168% | 0.4486% | 0.4817% | 0.5162% | 0.5522% | 0.5897% | 0.6286% | 0.669% | 0.7109% | 0.7543% | 0.7993% | 0.8458% | 0.8939% | 0.9436% | 0.9949% | 1.048% | 1.102% | 1.159% | 1.216% | 1.276%
CLN | 30000439 | DS-CLN-TRNFMR-9000001306 |  | 19 | 2 | 2 | 1 | 1 | 1 | 1 | 3 | 2 | 2 | 165.7143 | 2 | 24 | 3.5 | 84.05 | 0.1909% | 0.1909% | 0.211% | 0.2322% | 0.2547% | 0.2785% | 0.3035% | 0.3298% | 0.3575% | 0.3865% | 0.4168% | 0.4486% | 0.4817% | 0.5162% | 0.5522% | 0.5897% | 0.6286% | 0.669% | 0.7109% | 0.7543% | 0.7993% | 0.8458% | 0.8939% | 0.9436% | 0.9949% | 1.048% | 1.102% | 1.159% | 1.216% | 1.276%
OFR | 30035965 | DS-OFR-TRNFMR-9000014181 |  | 16 | 2 | 2 | 1 | 1 | 1 | 1 | 3 | 2 | 2 | 165.7143 | 2 | 24 | 3.5 | 84.05 | 0.1909% | 0.1909% | 0.211% | 0.2322% | 0.2547% | 0.2785% | 0.3035% | 0.3298% | 0.3575% | 0.3865% | 0.4168% | 0.4486% | 0.4817% | 0.5162% | 0.5522% | 0.5897% | 0.6286% | 0.669% | 0.7109% | 0.7543% | 0.7993% | 0.8458% | 0.8939% | 0.9436% | 0.9949% | 1.048% | 1.102% | 1.159% | 1.216% | 1.276%
KLO | 30002764 | DS-KLO-TRNFMR-9000412348 |  | 15 | 1 | 2 | 1 | 1 | 1 | 1 | 4 | 2 | 2 | 160 | 2 | 24 | 3.5 | 84.05 | 0.1909% | 0.1909% | 0.211% | 0.2322% | 0.2547% | 0.2785% | 0.3035% | 0.3298% | 0.3575% | 0.3865% | 0.4168% | 0.4486% | 0.4817% | 0.5162% | 0.5522% | 0.5897% | 0.6286% | 0.669% | 0.7109% | 0.7543% | 0.7993% | 0.8458% | 0.8939% | 0.9436% | 0.9949% | 1.048% | 1.102% | 1.159% | 1.216% | 1.276%
OFR | 30221642 | DS-OFR-TRNFMR-9000016122 |  | 16 | 1 | 2 | 1 | 1 | 1 | 1 | 3 | 2 | 2 | 151.4286 | 2 | 24 | 3.5 | 84.05 | 0.1909% | 0.1909% | 0.211% | 0.2322% | 0.2547% | 0.2785% | 0.3035% | 0.3298% | 0.3575% | 0.3865% | 0.4168% | 0.4486% | 0.4817% | 0.5162% | 0.5522% | 0.5897% | 0.6286% | 0.669% | 0.7109% | 0.7543% | 0.7993% | 0.8458% | 0.8939% | 0.9436% | 0.9949% | 1.048% | 1.102% | 1.159% | 1.216% | 1.276%
KLO | 30208816 | DS-KLO-TRNFMR-9000412347 |  | 15 | 1 | 2 | 1 | 1 | 1 | 1 | 3 | 2 | 2 | 151.4286 | 2 | 24 | 3.5 | 84.05 | 0.1909% | 0.1909% | 0.211% | 0.2322% | 0.2547% | 0.2785% | 0.3035% | 0.3298% | 0.3575% | 0.3865% | 0.4168% | 0.4486% | 0.4817% | 0.5162% | 0.5522% | 0.5897% | 0.6286% | 0.669% | 0.7109% | 0.7543% | 0.7993% | 0.8458% | 0.8939% | 0.9436% | 0.9949% | 1.048% | 1.102% | 1.159% | 1.216% | 1.276%
PHM | 32944656 | DS-PHM-TRNFMR-9000004393 |  | 8 | 2 | 2 | 1 | 1 | 1 | 1 | 3 | 1 | 1 | 142.8571 | 1 | 8 | 3.5 | 84.05 | 0.01357% | 0.01357% | 0.01791% | 0.023% | 0.02887% | 0.03555% | 0.04308% | 0.0515% | 0.06084% | 0.07112% | 0.08238% | 0.09465% | 0.1079% | 0.1223% | 0.1378% | 0.1543% | 0.172% | 0.1909% | 0.211% | 0.2322% | 0.2547% | 0.2785% | 0.3035% | 0.3298% | 0.3575% | 0.3865% | 0.4168% | 0.4486% | 0.4817% | 0.5162%
PHM | 32944654 | DS-PHM-TRNFMR-9000007050 |  | 8 | 2 | 2 | 1 | 1 | 1 | 1 | 3 | 1 | 1 | 142.8571 | 1 | 8 | 3.5 | 84.05 | 0.01357% | 0.01357% | 0.01791% | 0.023% | 0.02887% | 0.03555% | 0.04308% | 0.0515% | 0.06084% | 0.07112% | 0.08238% | 0.09465% | 0.1079% | 0.1223% | 0.1378% | 0.1543% | 0.172% | 0.1909% | 0.211% | 0.2322% | 0.2547% | 0.2785% | 0.3035% | 0.3298% | 0.3575% | 0.3865% | 0.4168% | 0.4486% | 0.4817% | 0.5162%

## AER VCR Rates(2024)
Category | Rate | Notes
Dec 24 AER VCR ($/kWh) - Res | 49.23 | Vic Av Res
Dec 24 AER VCR ($/kWh) - Com | 34.39 | Vic Av Com
Dec 24 AER VCR ($/kWh) - Ind | 33.49 | Vic Av Ind
Dec 24 AER VCR ($/kWh) - Agr | 22.25 | Vic Av Agr

## Customer No. and Vol per Feeder
CUSTOMER_CLASS | Feeder | VOL | CUST_NO | ZSS | Customer mix received from AusNet Financial Planning & Strategy on 25/7/2025
COMMERCIAL | bra11 | 9860526.7854 | 168 | bra
COMMERCIAL | bge13 | 654988.62 | 45 | bge
COMMERCIAL | phi11 | 1878610.03 | 37 | phi
NCONUML | moe11 | 47447.48 | 18 | moe
NCONUML | drn13 | 27414.73 | 17 | drn
COMMERCIAL | smg34 | 5224461.8 | 1 | smg
FARM | wgl13 | 901266.5312 | 97 | wgl
FARM | msd2 | 2808295.5668 | 471 | msd
NCONUML | elm34 | 86758.8 | 34 | elm
| rwt36 | 703.54 | 2 | rwt
COMMERCIAL | lga41 | 1099100.22 | 2 | lga
| bdl33 | 4298.82 | 8 | bdl
NCONUML | smr14 | 27225.34 | 18 | smr
COMMERCIAL | cln24 | 4484028.8333 | 290 | cln
RESIDENTL | ofr14 | 13024383.6958 | 3554 | ofr
NCONUML | bdl43 | 100361.9983 | 38 | bdl
| ofr22 | 16469.09 | 22 | ofr
NCONUML | rwn33 | 8721.79 | 7 | rwn
LIGHTING | hpk12 | 342838 | 1 | hpk
COMMERCIAL | bra23 | 6262297.01 | 84 | bra
FARM | tt1 | 1865.76 | 1 | tt
LIGHTING | mfa14 | 787800.53 | 1 | mfa
RESIDENTL | brt22 | 9968534.1043 | 1376 | brt
RESIDENTL | mwl25 | 4092575.372 | 493 | mwl
NCONUML | wgi22 | 83961.44 | 23 | wgi
INDUSTRIAL | ldl22 | 4379901.5885 | 45 | ldl
RESIDENTL | phm22 | 3628742.5283 | 796 | phm
FARM | mfa23 | 2691321.6324 | 201 | mfa
NCONUML | rwn32 | 60415.37 | 23 | rwn
FARM | cre22 | 55644.16 | 17 | cre
RESIDENTL | elm24 | 17367685.5307 | 2999 | elm
COMMERCIAL | tt9 | 7181168.3052 | 213 | tt
COMMERCIAL | kms12 | 15257134.8455 | 395 | kms
NCONUML | cyn31 | 24759.23 | 14 | cyn
| llg12 | 26420.7189 | 15 | llg
LIGHTING | ruba22 | 247422.69 | 1 | ruba
RESIDENTL | wt12 | 10803758.701 | 2579 | wt
COMMERCIAL | bwn14 | 6975240.1 | 156 | bwn
NCONUML | bge12 | 37366.03 | 11 | bge
NCONUML | rwn24 | 30489.76 | 21 | rwn
FARM | sfs1 | 113380.09 | 9 | sfs
| bwr13 | 80076.52 | 46 | bwr
FARM | wt13 | 37228.86 | 3 | wt
FARM | cre23 | 226478.55 | 9 | cre
COMMERCIAL | rwn22 | 1886562.0146 | 72 | rwn
| tgn23 | 13898.1302 | 15 | tgn
FARM | ldl22 | 7887.95 | 1 | ldl
RESIDENTL | fgy21 | 7153989.4877 | 1047 | fgy
FARM | mjg11 | 735019.886 | 74 | mjg
| ldl14 | 17432.2687 | 11 | ldl
INDUSTRIAL | ldl24 | 64751.4 | 12 | ldl
| sle13 | 253.3245 | 2 | sle
FARM | moe21 | 6301170.9744 | 504 | moe
FARM | bge23 | 671977.1074 | 66 | bge
RESIDENTL | elm32 | 19949095.4752 | 2463 | elm
COMMERCIAL | ftr12 | 1975462.7263 | 113 | ftr
RESIDENTL | lyd12 | 6657897.88 | 1592 | lyd
RESIDENTL | epg31 | 11862355.3417 | 3027 | epg
NCONUML | ofr11 | 57102.89 | 18 | ofr
FARM | moe11 | 65350.2807 | 7 | moe
FARM | nla32 | 1181128.1259 | 84 | nla
FARM | smr24 | 4141783.4574 | 392 | smr
RESIDENTL | fgy13 | 7970231.1446 | 1518 | fgy
FARM | bdl41 | 1305847.5951 | 258 | bdl
NCONUML | elm23 | 62172.37 | 40 | elm
| elm22 | 20617.5429 | 26 | elm
NCONUML | cre21 | 58240.1 | 18 | cre
FARM | phm32 | 50851.13 | 8 | phm
INDUSTRIAL | lga21 | 208132.02 | 16 | lga
INDUSTRIAL | nrn13 | 39703.59 | 6 | nrn
RESIDENTL | hpk22 | 18949862.0449 | 4569 | hpk
NCONUML | cyn13 | 17637.49 | 6 | cyn
COMMERCIAL | cre31 | 14851829.6913 | 363 | cre
COMMERCIAL | epg32 | 5001490.9226 | 156 | epg
| phm32 | 41386.12 | 47 | phm
NCONUML | wo33 | 6875.31 | 2 | wo
FARM | wgl21 | 5056187.7677 | 366 | wgl
INDUSTRIAL | cre22 | 240829.25 | 4 | cre
RESIDENTL | wgi34 | 3671110.7601 | 570 | wgi
INDUSTRIAL | ldl12 | 10352583.7 | 7 | ldl
INDUSTRIAL | wyk12 | 149433.7 | 6 | wyk
INDUSTRIAL | cyn14 | 23200.151 | 3 | cyn
| wo11 | 4136.2425 | 3 | wo
| msd4 | 20521.76 | 37 | msd
FARM | mby12 | 52034.88 | 19 | mby
COMMERCIAL | rwt22 | 7145877.6761 | 143 | rwt
COMMERCIAL | wo12 | 23719023.8 | 1 | wo
RESIDENTL | wn2 | 17414453.5902 | 3500 | wn
COMMERCIAL | wots25 | 3483725.2811 | 72 | wots
RESIDENTL | bwr33 | 46024.67 | 2 | bwr
RESIDENTL | wn3 | 12349888.6736 | 2099 | wn
RESIDENTL | bn24 | 2992797.8263 | 559 | bn
| bra21 | 41455.7142 | 65 | bra
INDUSTRIAL | hpk14 | 16381.88 | 4 | hpk
RESIDENTL | epg32 | 14811809.1158 | 3829 | epg
COMMERCIAL | cln14 | 10141314.5039 | 129 | cln
FARM | smg31 | 14995.46 | 5 | smg
INDUSTRIAL | drn22 | 2117102.6666 | 12 | drn
NCONUML | drn12 | 43785.8374 | 16 | drn
INDUSTRIAL | fgy34 | 128392.6893 | 5 | fgy
NCONUML | fgy31 | 6707.46 | 4 | fgy
| wt8 | 7059.0655 | 13 | wt
| bwn12 | 6521.57 | 6 | bwn
COMMERCIAL | myt12 | 10774273.2986 | 307 | myt
COMMERCIAL | ldl21 | 5339830.9491 | 117 | ldl
| cln21 | 32425.72 | 66 | cln
INDUSTRIAL | fgy14 | 162921.94 | 7 | fgy
| tgn12 | 22490.11 | 3 | tgn
COMMERCIAL | epg12 | 8214339.5389 | 163 | epg
NCONUML | moe23 | 69334.91 | 17 | moe
FARM | cyn14 | 7715.15 | 1 | cyn
RESIDENTL | lyd14 | 10580841.4317 | 1203 | lyd
COMMERCIAL | smg23 | 21963007.1063 | 434 | smg
INDUSTRIAL | bra33 | 2076536.62 | 34 | bra
INDUSTRIAL | rwt14 | 2271244.55 | 44 | rwt
COMMERCIAL | lga14 | 2174194.9787 | 115 | lga
INDUSTRIAL | myt22 | 3176.32 | 3 | myt
FARM | cyn21 | 10230.57 | 2 | cyn
| klo24 | 65411.35 | 119 | klo
COMMERCIAL | brt21 | 6571769.7252 | 216 | brt
FARM | kms11 | 665243.0597 | 75 | kms
| elm34 | 25999.6869 | 33 | elm
INDUSTRIAL | mwl11 | 366139.79 | 15 | mwl
INDUSTRIAL | lyd14 | 80895.88 | 12 | lyd
LIGHTING | cpk11 | 1086.88 | 1 | cpk
NCONUML | fgy23 | 34402.31 | 12 | fgy
| bra32 | 15753.982 | 22 | bra
RESIDENTL | epg12 | 26391788.5687 | 6905 | epg
COMMERCIAL | cyn24 | 15647575.1097 | 304 | cyn
INDUSTRIAL | phm21 | 511727.73 | 19 | phm
NCONUML | ftr12 | 5424.58 | 5 | ftr
| bwa23 | 5447.575 | 8 | bwa
NCONUML | llg12 | 4182.92 | 3 | llg
COMMERCIAL | drn13 | 5299129.684 | 96 | drn
INDUSTRIAL | hpk21 | 31624.71 | 8 | hpk
INDUSTRIAL | wyk23 | 1500537.4334 | 28 | wyk
RESIDENTL | lga12 | 4152631.2896 | 644 | lga
RESIDENTL | cyn11 | 6009338.551 | 1440 | cyn
NCONUML | fgy24 | 70027.41 | 43 | fgy
| moe23 | 74726.3012 | 22 | moe
COMMERCIAL | elm24 | 3531802.26 | 46 | elm
LIGHTING | elm33 | 1000.47 | 1 | elm
RESIDENTL | smg23 | 6500499.5996 | 1411 | smg
FARM | msd4 | 1851245.0012 | 252 | msd
COMMERCIAL | lga24 | 21693950.3379 | 92 | lga
COMMERCIAL | ldl11 | 7360578.73 | 74 | ldl
NCONUML | rve13 | 29515.6981 | 24 | rve
COMMERCIAL | trc01 | 365242.5067 | 42 | trc
COMMERCIAL | wt15 | 1164715.6471 | 30 | wt
COMMERCIAL | bra14 | 811059.401 | 59 | bra
| ftr21 | 17034.7542 | 20 | ftr
RESIDENTL | bra23 | 7643359.408 | 1736 | bra
INDUSTRIAL | cpk11 | 59065.36 | 14 | cpk
INDUSTRIAL | hpk12 | 531460.54 | 46 | hpk
FARM | fgy23 | 137430.23 | 3 | fgy
INDUSTRIAL | tt4 | 77015.1997 | 16 | tt
FARM | cpk22 | 45399.86 | 6 | cpk
INDUSTRIAL | yn31 | 1004932.7745 | 6 | yn
FARM | myt22 | 1873055.6433 | 191 | myt
| cpk12 | 20188.43 | 32 | cpk
RESIDENTL | bwa22 | 6606654.3694 | 1106 | bwa
| mfa34 | 1434.55 | 6 | mfa
| nla31 | 4780.58 | 5 | nla
FARM | mdg1 | 36782.2 | 6 | mdg
RESIDENTL | mwl21 | 3605605.4081 | 859 | mwl
COMMERCIAL | phm33 | 14452041.4603 | 180 | phm
INDUSTRIAL | ofr23 | 154535.41 | 17 | ofr
INDUSTRIAL | elm21 | 177435.466 | 7 | elm
INDUSTRIAL | wt5 | 89.11 | 1 | wt
FARM | llg13 | 1917532.2118 | 152 | llg
INDUSTRIAL | klk21 | 41156.68 | 10 | klk
NCONUML | wt9 | 48247.64 | 17 | wt
FARM | mdi1 | 153288.2952 | 21 | mdi
INDUSTRIAL | nrn14 | 19245.31 | 5 | nrn
INDUSTRIAL | wgl12 | 500659.11 | 16 | wgl
FARM | fgy13 | 80534.51 | 6 | fgy
INDUSTRIAL | bwr14 | 1597974.48 | 1 | bwr
LIGHTING | bn11 | 103048.5 | 1 | bn
RESIDENTL | klo14 | 40411755.0117 | 10946 | klo
RESIDENTL | fgy33 | 9101921.8028 | 1763 | fgy
LIGHTING | cre31 | 2308168.51 | 1 | cre
RESIDENTL | wn5 | 8555201.9981 | 1156 | wn
COMMERCIAL | mfa22 | 5299491.9938 | 179 | mfa
COMMERCIAL | lyd11 | 3798691.89 | 62 | lyd
LIGHTING | bn24 | 2014.81 | 1 | bn
COMMERCIAL | cf1 | 9360587.4941 | 189 | cf
FARM | lga11 | 4665290.6529 | 555 | lga
RESIDENTL | lyd13 | 10895753.2364 | 2051 | lyd
NCONUML | cre33 | 35388.67 | 19 | cre
| smg32 | 685.05 | 3 | smg
INDUSTRIAL | cyn11 | 1966971.1028 | 55 | cyn
COMMERCIAL | wn2 | 10157994.9798 | 156 | wn
| phm21 | 32464.7212 | 22 | phm
| sfs1 | 13890.635 | 10 | sfs
NCONUML | tt12 | 15011.94 | 8 | tt
FARM | lga21 | 1065599.6961 | 147 | lga
| ldl12 | 52350.63 | 6 | ldl
INDUSTRIAL | smg31 | 231921 | 9 | smg
LIGHTING | myt12 | 813470.88 | 6 | myt
| smr24 | 66801.9 | 34 | smr
NCONUML | cre32 | 49453.4427 | 23 | cre
INDUSTRIAL | bdl44 | 2337630.2078 | 41 | bdl
| rve11 | 302066.1 | 12 | rve
FARM | wo31 | 3245.01 | 1 | wo
LIGHTING | ofr13 | 171706.2 | 2 | ofr
RESIDENTL | tt9 | 13181645.445 | 3553 | tt
COMMERCIAL | wgl11 | 13522117.9742 | 216 | wgl
COMMERCIAL | hpk24 | 15242696.9791 | 271 | hpk
COMMERCIAL | bwr34 | 12222544.1423 | 437 | bwr
NCONUML | nla34 | 19980.17 | 11 | nla
FARM | bwr24 | 9303.26 | 1 | bwr
| wgi23 | 15962.8799 | 36 | wgi
RESIDENTL | cln13 | 18593732.5659 | 6830 | cln
RESIDENTL | lga13 | 1879247.7046 | 295 | lga
RESIDENTL | cnr3 | 108696.4186 | 22 | cnr
| wgl12 | 112644.3661 | 43 | wgl
COMMERCIAL | cln12 | 8203266.5202 | 86 | cln
NCONUML | ofr21 | 100427.35 | 34 | ofr
RESIDENTL | drn24 | 10021102.8231 | 2473 | drn
COMMERCIAL | cyn31 | 1940881.6507 | 53 | cyn
NCONUML | ldl24 | 34534.3 | 19 | ldl
COMMERCIAL | ofr13 | 9302944.2987 | 197 | ofr
| wots13 | 58538.6484 | 32 | wots
| cpk23 | 23360.0808 | 24 | cpk
NCONUML | cln11 | 4587.8606 | 9 | cln
| wt15 | 51811.4 | 11 | wt
COMMERCIAL | epg24 | 26841528 | 1 | epg
FARM | drn22 | 329138.5031 | 52 | drn
| mfa31 | 16838.31 | 22 | mfa
COMMERCIAL | bra32 | 4055727.3404 | 158 | bra
COMMERCIAL | cpk21 | 14974774.5549 | 258 | cpk
INDUSTRIAL | myt21 | 335981.9667 | 19 | myt
FARM | nrn14 | 139044.47 | 14 | nrn
| wt5 | 22324.85 | 13 | wt
INDUSTRIAL | mfa23 | 139940.33 | 14 | mfa
FARM | wyk12 | 2634438.6357 | 233 | wyk
RESIDENTL | epg23 | 3653084.6682 | 932 | epg
COMMERCIAL | tgn11 | 2525258.71 | 85 | tgn
| wt13 | 22551.0062 | 37 | wt
| cyn13 | 10533.28 | 7 | cyn
INDUSTRIAL | fgy13 | 259435.94 | 2 | fgy
RESIDENTL | cln12 | 23908773.0216 | 6775 | cln
COMMERCIAL | brt22 | 9042592.2197 | 210 | brt
COMMERCIAL | rwt25 | 7526054.6961 | 146 | rwt
FARM | mfa31 | 218040.8355 | 21 | mfa
COMMERCIAL | cln22 | 3248277.4443 | 37 | cln
NCONUML | bdl33 | 22970.8 | 8 | bdl
COMMERCIAL | fgy12 | 74427.591 | 4 | fgy
RESIDENTL | mwl16 | 8188909.2298 | 1700 | mwl
INDUSTRIAL | moe25 | 612177.9824 | 16 | moe
COMMERCIAL | tt7 | 24970154.3491 | 341 | tt
INDUSTRIAL | bwr24 | 4118148.7987 | 125 | bwr
RESIDENTL | moe13 | 2791200.4315 | 357 | moe
FARM | wyk24 | 694188.3378 | 94 | wyk
NCONUML | wo14 | 36996.26 | 12 | wo
RESIDENTL | bra13 | 6470560.8911 | 1572 | bra
RESIDENTL | tt7 | 39398.92 | 9 | tt
FARM | epg34 | 15821.91 | 5 | epg
INDUSTRIAL | yn35 | 6582.38 | 2 | yn
NCONUML | bwa23 | 749.23 | 1 | bwa
FARM | sle13 | 1461316.56 | 213 | sle
COMMERCIAL | cpk13 | 4127340.5971 | 198 | cpk
INDUSTRIAL | ldl14 | 1064067.7426 | 16 | ldl
| rwt14 | 62105.3312 | 18 | rwt
LIGHTING | hpk13 | 14513.85 | 1 | hpk
RESIDENTL | klk22 | 940238.19 | 128 | klk
COMMERCIAL | mwl25 | 259300.06 | 16 | mwl
| mjg11 | 96977.3135 | 7 | mjg
RESIDENTL | hpk24 | 4867180.3451 | 1284 | hpk
FARM | ftr21 | 6703423.0704 | 705 | ftr
FARM | smr12 | 441800.25 | 44 | smr
FARM | bwr13 | 73574.54 | 13 | bwr
| ldl22 | 9241.11 | 9 | ldl
FARM | wo22 | 35676.335 | 7 | wo
NCONUML | moe12 | 9318.9 | 3 | moe
INDUSTRIAL | bdl31 | 1561951.6978 | 44 | bdl
COMMERCIAL | ofr14 | 8393968.2568 | 77 | ofr
NCONUML | tgn23 | 48562.71 | 16 | tgn
NCONUML | cyn21 | 25127.29 | 5 | cyn
FARM | phm34 | 22945.58 | 3 | phm
INDUSTRIAL | cyn33 | 36519.92 | 4 | cyn
LIGHTING | bm8b32 | 1070.04 | 1 | bmb
FARM | llg12 | 5311057.9488 | 488 | llg
NCONUML | rwt32 | 94072.85 | 46 | rwt
COMMERCIAL | myt11 | 912988.53 | 42 | myt
INDUSTRIAL | cpk22 | 129954.91 | 11 | cpk
| cre22 | 20388.051 | 33 | cre
RESIDENTL | ldl21 | 5451727.7741 | 1502 | ldl
FARM | bdl44 | 8189534.7866 | 736 | bdl
INDUSTRIAL | bn11 | 1899511.3657 | 45 | bn
INDUSTRIAL | wgi31 | 152399.6 | 19 | wgi
INDUSTRIAL | mdi1 | 16.0426 | 1 | mdi
| ofr11 | 90492.4817 | 79 | ofr
LIGHTING | kms11 | 547479.19 | 1 | kms
RESIDENTL | phi12 | 18738852.0082 | 4967 | phi
COMMERCIAL | bwr12 | 7897915.6022 | 287 | bwr
FARM | msd1 | 2520603.4144 | 354 | msd
COMMERCIAL | tgn44 | 4662112.18 | 89 | tgn
NCONUML | uwy1 | 29815.85 | 15 | uwy
NCONUML | lga22 | 54192.29 | 17 | lga
NCONUML | lga23 | 17186.13 | 6 | lga
INDUSTRIAL | hpk13 | 1952010.47 | 3 | hpk
FARM | drn23 | 391232.6382 | 58 | drn
FARM | ldl23 | 5910515.5529 | 453 | ldl
FARM | bdl31 | 55336.85 | 12 | bdl
RESIDENTL | bwr34 | 11176240.016 | 2984 | bwr
RESIDENTL | ofr13 | 5689359.8131 | 1445 | ofr
NCONUML | bra21 | 145563.002 | 72 | bra
COMMERCIAL | cf2 | 1114027.3697 | 138 | cf
RESIDENTL | bdl32 | 16368580.902 | 3124 | bdl
COMMERCIAL | smr22 | 10240657.5236 | 95 | smr
NCONUML | rve12 | 34563.18 | 21 | rve
COMMERCIAL | cnr3 | 208527.63 | 11 | cnr
| elm25 | 9741.0155 | 15 | elm
INDUSTRIAL | lyd13 | 30651.21 | 5 | lyd
INDUSTRIAL | mby12 | 279353.09 | 7 | mby
INDUSTRIAL | epg21 | 31298.6803 | 2 | epg
FARM | wgl12 | 7817936.5802 | 624 | wgl
COMMERCIAL | moe13 | 1401894.0174 | 82 | moe
RESIDENTL | lga14 | 7239522.4699 | 1158 | lga
RESIDENTL | epg35 | 308209.78 | 22 | epg
FARM | hpk14 | 29274.39 | 5 | hpk
LIGHTING | bn22 | 341591.58 | 1 | bn
NCONUML | bge11 | 85890.46 | 45 | bge
NCONUML | wt7 | 26985.19 | 18 | wt
| wo31 | 27869.149 | 41 | wo
INDUSTRIAL | elm32 | 759094.4258 | 68 | elm
NCONUML | cre23 | 95638.5 | 25 | cre
RESIDENTL | cln23 | 19292170.1488 | 4992 | cln
| lga21 | 17263.28 | 18 | lga
NCONUML | bwn12 | 35975.24 | 12 | bwn
| fgy31 | 1671.76 | 6 | fgy
NCONUML | ftr23 | 39743.6852 | 30 | ftr
NCONUML | smg21 | 9405.11 | 5 | smg
RESIDENTL | epg13 | 24819451.0174 | 7299 | epg
RESIDENTL | ruba22 | 5955886.59 | 1080 | ruba
INDUSTRIAL | bwr23 | 1917390.4058 | 110 | bwr
COMMERCIAL | bn23 | 4585306.9 | 117 | bn
| fgy24 | 60212.15 | 95 | fgy
LIGHTING | brt21 | 27441.26 | 1 | brt
COMMERCIAL | mby14 | 13812.56 | 3 | mby
RESIDENTL | drn21 | 15235611.8074 | 3585 | drn
RESIDENTL | nrn11 | 3368324.1063 | 703 | nrn
NCONUML | cln21 | 97183.1897 | 28 | cln
NCONUML | tgn12 | 26909.78 | 9 | tgn
FARM | moe22 | 48531.59 | 7 | moe
RESIDENTL | bra14 | 17287022.2386 | 4193 | bra
RESIDENTL | brt21 | 8587133.8204 | 1368 | brt
INDUSTRIAL | ldl23 | 2181365.61 | 45 | ldl
NCONUML | klo24 | 121410.57 | 41 | klo
INDUSTRIAL | wt8 | 22231.36 | 5 | wt
| bdl41 | 27628.4721 | 32 | bdl
COMMERCIAL | sle14 | 13227565.7623 | 343 | sle
| smr14 | 17300.3116 | 19 | smr
INDUSTRIAL | llg11 | 439641.21 | 9 | llg
| wgi22 | 13903.1 | 35 | wgi
NCONUML | moe22 | 34069.45 | 10 | moe
| ftr12 | 15921.46 | 17 | ftr
COMMERCIAL | epg11 | 902129.45 | 16 | epg
RESIDENTL | cpk13 | 21255549.7429 | 4974 | cpk
| fgy23 | 9273.25 | 10 | fgy
FARM | cyn12 | 9105.46 | 2 | cyn
INDUSTRIAL | rwn31 | 527467.66 | 22 | rwn
RESIDENTL | bm8b32 | 357081.227 | 62 | bmb
FARM | ruba22 | 1060033.1321 | 158 | ruba
INDUSTRIAL | cnr1 | 88077.93 | 3 | cnr
FARM | cpk12 | 972803.9358 | 91 | cpk
COMMERCIAL | wo14 | 14658340.7796 | 304 | wo
COMMERCIAL | tt5 | 6134357.4395 | 224 | tt
INDUSTRIAL | wo11 | 18559582.74 | 7 | wo
| wgl23 | 17798.7289 | 12 | wgl
NCONUML | cyn12 | 64730.9 | 21 | cyn
COMMERCIAL | bwr33 | 3515549.759 | 83 | bwr
COMMERCIAL | cyn22 | 10287381.4837 | 183 | cyn
COMMERCIAL | rwt32 | 5482054.6843 | 198 | rwt
INDUSTRIAL | nrn12 | 7260.73 | 2 | nrn
RESIDENTL | cln22 | 8137131.1146 | 3340 | cln
| kms12 | 36774.1343 | 44 | kms
| cyn24 | 12784.0842 | 11 | cyn
| smg33 | 11524.64 | 21 | smg
COMMERCIAL | rve11 | 18192998.0721 | 274 | rve
FARM | wt5 | 8146.48 | 2 | wt
INDUSTRIAL | bge23 | 983662.8538 | 7 | bge
| msd2 | 9983.6 | 13 | msd
| bra12 | 98134.87 | 2 | bra
RESIDENTL | hpk23 | 13762355.5073 | 3377 | hpk
COMMERCIAL | smr13 | 15057236.7589 | 394 | smr
INDUSTRIAL | rwt21 | 372221.49 | 45 | rwt
FARM | rve12 | 22362.86 | 5 | rve
NCONUML | fgy32 | 32042.28 | 18 | fgy
INDUSTRIAL | smr12 | 37387308.69 | 3 | smr
NCONUML | mfa34 | 19451.19 | 8 | mfa
FARM | wots13 | 4844280.0942 | 510 | wots
COMMERCIAL | drn21 | 3220798.94 | 52 | drn
INDUSTRIAL | wo31 | 765.77 | 1 | wo
| fgy32 | 8528.5063 | 10 | fgy
INDUSTRIAL | bwr32 | 3058614 | 72 | bwr
| elm23 | 20831.6 | 30 | elm
INDUSTRIAL | mwl12 | 574569.29 | 12 | mwl
RESIDENTL | cpk21 | 7771248.352 | 1679 | cpk
COMMERCIAL | wots11 | 6621581.9604 | 243 | wots
INDUSTRIAL | ftr21 | 313604.8 | 24 | ftr
NCONUML | lyd11 | 43059.75 | 9 | lyd
FARM | phm21 | 25361.56 | 3 | phm
INDUSTRIAL | wyk13 | 453974.55 | 15 | wyk
INDUSTRIAL | mdg1 | 21781.42 | 1 | mdg
INDUSTRIAL | tt1 | 7434378.9861 | 77 | tt
INDUSTRIAL | wgi34 | 1206209.57 | 8 | wgi
LIGHTING | wgi33 | 1050486.0487 | 2 | wgi
COMMERCIAL | wgl15 | 27996457.3831 | 596 | wgl
RESIDENTL | bge23 | 16900476.9279 | 2094 | bge
INDUSTRIAL | bwr13 | 2417661.2776 | 147 | bwr
NCONUML | epg23 | 28250.73 | 7 | epg
INDUSTRIAL | drn14 | 25996.95 | 2 | drn
RESIDENTL | drn14 | 23831050.9741 | 4399 | drn
RESIDENTL | rwt31 | 5842296.4371 | 1436 | rwt
COMMERCIAL | drn24 | 1717660.9 | 35 | drn
FARM | epg14 | 3614.72 | 1 | epg
RESIDENTL | smr13 | 11225814.5464 | 2447 | smr
COMMERCIAL | wots12 | 14359758.4732 | 371 | wots
COMMERCIAL | klk11 | 3080934.4269 | 114 | klk
NCONUML | mwl14 | 31252.61 | 13 | mwl
INDUSTRIAL | sle11 | 266690.1 | 32 | sle
NCONUML | epg31 | 41319.36 | 24 | epg
RESIDENTL | cf1 | 4176161.3871 | 493 | cf
INDUSTRIAL | phm34 | 816155.12 | 6 | phm
FARM | rwn34 | 20402.21 | 4 | rwn
| mby12 | 1524.95 | 3 | mby
RESIDENTL | wgi31 | 14866992.8529 | 3617 | wgi
RESIDENTL | wots25 | 16858284.9544 | 3532 | wots
RESIDENTL | cre33 | 21876811.5892 | 4235 | cre
RESIDENTL | fgy34 | 4606270.9018 | 975 | fgy
RESIDENTL | cyn32 | 15011504.2579 | 3573 | cyn
RESIDENTL | klk11 | 9194980.7775 | 1227 | klk
INDUSTRIAL | fgy33 | 1452360.19 | 13 | fgy
INDUSTRIAL | wgl13 | 6688610.4344 | 14 | wgl
| tgn41 | 12751.16 | 13 | tgn
COMMERCIAL | klk22 | 85830.78 | 8 | klk
| mby11 | 4292.69 | 12 | mby
FARM | drn12 | 9939.61 | 1 | drn
RESIDENTL | rwn24 | 15617115.6722 | 2794 | rwn
RESIDENTL | cre32 | 8053371.5554 | 2218 | cre
COMMERCIAL | bwn11 | 5920812.2037 | 76 | bwn
NCONUML | smg33 | 19709.42 | 12 | smg
INDUSTRIAL | mby11 | 90387.22 | 16 | mby
COMMERCIAL | tgn41 | 8173213.7745 | 338 | tgn
INDUSTRIAL | wn7 | 3582803.57 | 9 | wn
FARM | bwr23 | 29264.76 | 8 | bwr
RESIDENTL | bwn13 | 8026926.4045 | 1629 | bwn
FARM | wgi24 | 1757204.2906 | 142 | wgi
| rve13 | 21148.03 | 29 | rve
RESIDENTL | wgl21 | 23764201.6622 | 4642 | wgl
COMMERCIAL | wn1 | 22168293.2818 | 620 | wn
INDUSTRIAL | cyn32 | 738566.1077 | 85 | cyn
| hpk21 | 27858.58 | 57 | hpk
COMMERCIAL | klo11 | 2030116.61 | 11 | klo
INDUSTRIAL | bn22 | 260832.7234 | 23 | bn
| ofr24 | 25053.77 | 43 | ofr
| drn12 | 30292.1138 | 29 | drn
COMMERCIAL | smg22 | 18806077.0677 | 136 | smg
COMMERCIAL | bwa22 | 4509592.2057 | 144 | bwa
COMMERCIAL | drn12 | 15118769.4919 | 112 | drn
| ldl23 | 80304.9161 | 48 | ldl
| rwn32 | 14306.27 | 22 | rwn
| drn23 | 12868.4314 | 15 | drn
RESIDENTL | mwl22 | 12904194.2639 | 2809 | mwl
COMMERCIAL | tt6 | 3682930.1298 | 115 | tt
COMMERCIAL | bra24 | 3429037.1414 | 127 | bra
NCONUML | hpk11 | 112614.82 | 31 | hpk
RESIDENTL | mfa21 | 12551518.2306 | 1921 | mfa
RESIDENTL | bge22 | 19945240.9452 | 3164 | bge
| tt4 | 9710.0483 | 41 | tt
NCONUML | phm22 | 22255.8232 | 9 | phm
COMMERCIAL | fgy21 | 1241019.6707 | 34 | fgy
INDUSTRIAL | nla31 | 516137.35 | 16 | nla
FARM | wyk13 | 707273.0378 | 84 | wyk
NCONUML | elm25 | 44655.33 | 20 | elm
| ofr23 | 28214.1089 | 26 | ofr
INDUSTRIAL | ruba22 | 167892.49 | 8 | ruba
FARM | hpk21 | 3124.97 | 1 | hpk
FARM | wn4 | 999664.927 | 129 | wn
COMMERCIAL | wn6 | 8795190.5545 | 246 | wn
| cre23 | 50195.43 | 25 | cre
COMMERCIAL | bwr22 | 15914202.1636 | 269 | bwr
INDUSTRIAL | elm22 | 545216.4127 | 27 | elm
NCONUML | bwr32 | 46210.27 | 31 | bwr
COMMERCIAL | moe12 | 4799517.76 | 51 | moe
| drn22 | 43438.5 | 28 | drn
FARM | bn22 | 13032.09 | 3 | bn
FARM | ldl24 | 222231.4641 | 11 | ldl
| bdl31 | 24144.6762 | 16 | bdl
FARM | cpk11 | 227979.0877 | 18 | cpk
FARM | elm33 | 50441.5205 | 4 | elm
INDUSTRIAL | rve13 | 147824.4003 | 10 | rve
COMMERCIAL | uwy1 | 603856.89 | 33 | uwy
FARM | mfa21 | 13347321.3386 | 701 | mfa
RESIDENTL | wo14 | 1446838.665 | 266 | wo
NCONUML | rwt14 | 102266.96 | 37 | rwt
| kms11 | 9612.23 | 20 | kms
RESIDENTL | phi11 | 5828644.3864 | 1391 | phi
COMMERCIAL | tgn12 | 10174331.2835 | 242 | tgn
LIGHTING | drn21 | 522455.53 | 1 | drn
INDUSTRIAL | smr22 | 2060432.23 | 13 | smr
| moe21 | 19173.8011 | 29 | moe
NCONUML | fgy12 | 1668.8419 | 4 | fgy
COMMERCIAL | elm25 | 2590499.6378 | 73 | elm
| epg34 | 11737.1961 | 27 | epg
COMMERCIAL | cpk23 | 2022573.8223 | 44 | cpk
COMMERCIAL | sle31 | 4198591.4215 | 178 | sle
FARM | nrn13 | 23844.37 | 5 | nrn
FARM | elm26 | 83060.0495 | 12 | elm
INDUSTRIAL | rve12 | 67014.5 | 12 | rve
INDUSTRIAL | moe21 | 304282.5341 | 37 | moe
COMMERCIAL | ofr21 | 9424773.56 | 126 | ofr
FARM | wn3 | 4385381.9629 | 585 | wn
FARM | klk21 | 574949.1868 | 82 | klk
NCONUML | wyk13 | 97422.66 | 49 | wyk
FARM | bwn12 | 14573.05 | 3 | bwn
NCONUML | msd2 | 8161.26 | 6 | msd
COMMERCIAL | elm31 | 474386.1613 | 1 | elm
RESIDENTL | rwt35 | 12065.95 | 2 | rwt
RESIDENTL | wt6 | 15702930.1084 | 3397 | wt
RESIDENTL | cln24 | 3991370.9732 | 1090 | cln
COMMERCIAL | smg21 | 2744632.8687 | 43 | smg
| myt21 | 64545.94 | 22 | myt
RESIDENTL | lga22 | 9862202.3617 | 1608 | lga
INDUSTRIAL | cyn13 | 4447831.06 | 67 | cyn
COMMERCIAL | ruba12 | 6703349.3664 | 290 | ruba
| smr23 | 7378.7014 | 9 | smr
FARM | phi13 | 230339.12 | 15 | phi
RESIDENTL | wt11 | 8665012.8839 | 2213 | wt
RESIDENTL | bge13 | 9255563.8982 | 1458 | bge
COMMERCIAL | bge11 | 11367890.3817 | 330 | bge
COMMERCIAL | wgi23 | 2290528.82 | 95 | wgi
COMMERCIAL | epg35 | 29855241.8371 | 304 | epg
NCONUML | mwl23 | 55631.52 | 20 | mwl
RESIDENTL | tgn11 | 18615536.7391 | 4196 | tgn
RESIDENTL | klo24 | 35150523.3753 | 8219 | klo
| wgi32 | 32777.55 | 36 | wgi
| uwy1 | 1895.86 | 6 | uwy
COMMERCIAL | wots24 | 5008654.6646 | 265 | wots
INDUSTRIAL | phi13 | 601326.64 | 38 | phi
LIGHTING | cf1 | 76883.018 | 3 | cf
RESIDENTL | cre21 | 18876617.5647 | 4715 | cre
INDUSTRIAL | wo32 | 73086.25 | 1 | wo
COMMERCIAL | lga13 | 621321.4861 | 47 | lga
FARM | cnr2 | 245915.51 | 48 | cnr
COMMERCIAL | bge22 | 4521687.9575 | 100 | bge
INDUSTRIAL | cyn12 | 101425.5 | 5 | cyn
FARM | drn11 | 51881.33 | 8 | drn
INDUSTRIAL | wo23 | 212041.78 | 1 | wo
RESIDENTL | lga23 | 5064870.5947 | 821 | lga
RESIDENTL | bn12 | 3438265.7182 | 625 | bn
RESIDENTL | bra21 | 23268334.8963 | 5707 | bra
| bdl42 | 11198.42 | 14 | bdl
FARM | cnr1 | 2440.03 | 2 | cnr
| phm34 | 68320.3174 | 32 | phm
FARM | rwt31 | 12148.87 | 1 | rwt
| smg31 | 8879.89 | 17 | smg
LIGHTING | tgn11 | 1064655.8 | 1 | tgn
FARM | llg14 | 4195351.6172 | 347 | llg
FARM | mwl11 | 2401732.236 | 295 | mwl
INDUSTRIAL | brt22 | 103539.39 | 15 | brt
COMMERCIAL | mwl14 | 15268408.4249 | 139 | mwl
RESIDENTL | wn1 | 4757807.4084 | 1039 | wn
COMMERCIAL | wo33 | 4706642.85 | 27 | wo
| nrn14 | 10562.91 | 10 | nrn
RESIDENTL | wgl15 | 10836827.2608 | 2158 | wgl
RESIDENTL | mfa22 | 4069843.249 | 701 | mfa
NCONUML | wyk24 | 96009.71 | 32 | wyk
NCONUML | rwn34 | 17137.95 | 21 | rwn
NCONUML | rve11 | 32578.28 | 16 | rve
INDUSTRIAL | klk11 | 54511.69 | 7 | klk
RESIDENTL | tt2 | 73044.37 | 7 | tt
COMMERCIAL | rwn32 | 3002784.6794 | 97 | rwn
NCONUML | tt1 | 9612.49 | 4 | tt
NCONUML | bwr23 | 79898.93 | 30 | bwr
NCONUML | epg14 | 19866.64 | 14 | epg
| elm26 | 27328.755 | 32 | elm
INDUSTRIAL | bdl32 | 418697.92 | 34 | bdl
FARM | wt11 | 3746.97 | 1 | wt
NCONUML | ofr23 | 50364.93 | 30 | ofr
INDUSTRIAL | smg23 | 412547.84 | 9 | smg
LIGHTING | klo14 | 3058096.87 | 1 | klo
| nrn13 | 13473.67 | 22 | nrn
FARM | bra12 | 12444.91 | 1 | bra
COMMERCIAL | cre21 | 15222170.3645 | 489 | cre
INDUSTRIAL | wgi32 | 984365.53 | 33 | wgi
NCONUML | rwt25 | 118451.05 | 54 | rwt
INDUSTRIAL | mwe236 | 280541.09 | 16 | mwe
RESIDENTL | epg33 | 183201.2006 | 6 | epg
INDUSTRIAL | elm33 | 243571.284 | 12 | elm
RESIDENTL | ldl11 | 13512975.3636 | 2241 | ldl
| mwl12 | 15850.97 | 9 | mwl
INDUSTRIAL | fgy21 | 6595081.67 | 18 | fgy
LIGHTING | smr24 | 109914.08 | 1 | smr
RESIDENTL | rwt25 | 10768082.8154 | 2324 | rwt
INDUSTRIAL | rwt15 | 3409961.2906 | 83 | rwt
INDUSTRIAL | phi12 | 3418741.3516 | 25 | phi
INDUSTRIAL | bwa22 | 1592049.74 | 9 | bwa
NCONUML | wo22 | 90587.46 | 26 | wo
INDUSTRIAL | ldl21 | 599666.7 | 44 | ldl
INDUSTRIAL | wt6 | 1814.16 | 1 | wt
NCONUML | ofr22 | 9198.59 | 2 | ofr
INDUSTRIAL | bra13 | 1860337.5903 | 47 | bra
COMMERCIAL | fgy24 | 2616699.5517 | 109 | fgy
RESIDENTL | epg11 | 6094828.0666 | 1503 | epg
NCONUML | rwt36 | 1279.88 | 1 | rwt
RESIDENTL | bwn14 | 23184606.5946 | 3016 | bwn
COMMERCIAL | bra31 | 7996775.7312 | 141 | bra
| nla32 | 13550.62 | 15 | nla
FARM | brt11 | 223967.42 | 33 | brt
| hpk12 | 10433.13 | 13 | hpk
INDUSTRIAL | llg13 | 899195.7591 | 21 | llg
INDUSTRIAL | wgl21 | 1687828.17 | 29 | wgl
INDUSTRIAL | cnr2 | 615523.18 | 19 | cnr
INDUSTRIAL | mfa14 | 499885.98 | 5 | mfa
RESIDENTL | drn13 | 15714620.5428 | 2698 | drn
FARM | kms12 | 1180373.8068 | 156 | kms
COMMERCIAL | rwn24 | 15303994.2605 | 63 | rwn
NCONUML | wn4 | 65357.11 | 21 | wn
COMMERCIAL | rwn33 | 562037.42 | 22 | rwn
| moe22 | 3614.75 | 12 | moe
| wgl13 | 39374.2 | 44 | wgl
| moe11 | 8193.3901 | 21 | moe
COMMERCIAL | wt7 | 4475658.5866 | 198 | wt
NCONUML | bwr13 | 106489.72 | 46 | bwr
NCONUML | kms12 | 115620.45 | 45 | kms
NCONUML | cyn24 | 41312.6858 | 21 | cyn
COMMERCIAL | mwl13 | 8520395.3383 | 232 | mwl
COMMERCIAL | cyn32 | 10902527.7138 | 351 | cyn
INDUSTRIAL | tgn31 | 3050316.88 | 29 | tgn
| wo13 | 12961.22 | 9 | wo
NCONUML | bra12 | 30121.15 | 6 | bra
| mwl24 | 4141.68 | 3 | mwl
RESIDENTL | ftr22 | 5196242.6186 | 1010 | ftr
| cyn12 | 33132.831 | 28 | cyn
| mwl11 | 4217.9 | 11 | mwl
NCONUML | sle13 | 9744.3474 | 7 | sle
RESIDENTL | sle14 | 16027394.2978 | 4223 | sle
RESIDENTL | wgl23 | 5362246.1099 | 739 | wgl
COMMERCIAL | cre23 | 25513720.5265 | 132 | cre
RESIDENTL | bdl43 | 5886157.096 | 1122 | bdl
RESIDENTL | bge21 | 100743.92 | 11 | bge
RESIDENTL | smg22 | 10427736.14 | 2476 | smg
FARM | rwn31 | 347566.14 | 21 | rwn
INDUSTRIAL | bn12 | 8173831.79 | 6 | bn
| wgi24 | 27543.5394 | 32 | wgi
| mfa23 | 2828.28 | 3 | mfa
NCONUML | elm22 | 93887.89 | 42 | elm
INDUSTRIAL | wots13 | 2426481.9937 | 28 | wots
RESIDENTL | mwl13 | 9372820.2657 | 1896 | mwl
COMMERCIAL | epg31 | 8736205.1691 | 170 | epg
| bdl44 | 43009.9658 | 33 | bdl
COMMERCIAL | wgl24 | 14484234.4559 | 200 | wgl
INDUSTRIAL | wn3 | 1104797.78 | 30 | wn
| wgi33 | 38017.7186 | 28 | wgi
NCONUML | wo31 | 91536.41 | 24 | wo
FARM | ldl14 | 3990495.203 | 142 | ldl
NCONUML | wyk12 | 43139.17 | 24 | wyk
INDUSTRIAL | mwl15 | 15961047.4 | 1 | mwl
LIGHTING | bdl32 | 23514.52 | 1 | bdl
| rve12 | 15159.19 | 33 | rve
NCONUML | phm34 | 55440.25 | 17 | phm
COMMERCIAL | phm22 | 18761180.3018 | 732 | phm
RESIDENTL | cyn22 | 8715945.6121 | 2142 | cyn
FARM | fgy31 | 3345.68 | 2 | fgy
RESIDENTL | smr22 | 8159798.5324 | 1327 | smr
RESIDENTL | cyn23 | 7298806.6664 | 1621 | cyn
FARM | bdl42 | 2407309.4815 | 483 | bdl
| wyk23 | 31976.68 | 33 | wyk
INDUSTRIAL | rwn26 | 257525.5397 | 10 | rwn
NCONUML | bwn11 | 91006.47 | 23 | bwn
COMMERCIAL | cyn23 | 7883296.3431 | 299 | cyn
| moe15 | 19145.0797 | 16 | moe
| drn11 | 44271.4909 | 65 | drn
INDUSTRIAL | moe22 | 88009.47 | 4 | moe
NCONUML | mdg1 | 4146.1 | 9 | mdg
FARM | bra33 | 5568.67 | 1 | bra
LIGHTING | bwa22 | 75542.46 | 1 | bwa
NCONUML | hpk14 | 64164.68 | 20 | hpk
NCONUML |  | 262.3928 | 5 | #REF!
INDUSTRIAL | cln13 | 2016187.9013 | 2 | cln
FARM | ofr11 | 1184021.9516 | 51 | ofr
FARM | phm31 | 2011038.4476 | 90 | phm
NCONUML | elm21 | 62554.36 | 23 | elm
NCONUML | wt8 | 36862.33 | 14 | wt
NCONUML | cnr1 | 1922.85 | 2 | cnr
INDUSTRIAL | cre31 | 212230.18 | 2 | cre
COMMERCIAL | mfa34 | 8313764.4144 | 170 | mfa
INDUSTRIAL | tt5 | 637183.9506 | 23 | tt
INDUSTRIAL | llg14 | 1201432.9268 | 29 | llg
RESIDENTL | wo23 | 1549813.7708 | 361 | wo
| bwr23 | 25383.1703 | 47 | bwr
| sle11 | 3997.21 | 10 | sle
NCONUML | epg22 | 8538.04 | 7 | epg
NCONUML | bwr24 | 20744.02 | 14 | bwr
INDUSTRIAL | myt12 | 952524.23 | 20 | myt
| ftr23 | 53453.1274 | 33 | ftr
RESIDENTL | bra11 | 9331476.9371 | 2277 | bra
FARM | ldl13 | 3504918.0126 | 302 | ldl
| brt11 | 8693.81 | 14 | brt
INDUSTRIAL | phm31 | 91642.7039 | 2 | phm
COMMERCIAL | bdl43 | 22280533.2345 | 523 | bdl
FARM | moe23 | 4928404.5033 | 365 | moe
| klk21 | 7164.56 | 8 | klk
| wt7 | 8483.27 | 17 | wt
FARM | llg11 | 4501914.1562 | 365 | llg
LIGHTING | cf2 | 13221.322 | 1 | cf
| tgn31 | 23134.1673 | 13 | tgn
RESIDENTL | nla31 | 3471883.5329 | 742 | nla
COMMERCIAL | bdl31 | 6479518.62 | 206 | bdl
COMMERCIAL | smr23 | 799486.21 | 26 | smr
INDUSTRIAL | rve11 | 154936.16 | 21 | rve
RESIDENTL | bm8b33 | 130717.0048 | 17 | bmb
FARM | phi12 | 364625.9 | 40 | phi
INDUSTRIAL | klk22 | 5518.6 | 1 | klk
RESIDENTL | llg12 | 7619865.2998 | 1210 | llg
RESIDENTL | cln21 | 24090170.4832 | 5877 | cln
NCONUML | cpk11 | 17830.25 | 17 | cpk
COMMERCIAL | ruba22 | 3463594.5603 | 120 | ruba
NCONUML | brt22 | 9306.55 | 7 | brt
INDUSTRIAL | epg32 | 7635590.16 | 5 | epg
INDUSTRIAL | cln12 | 360384.55 | 1 | cln
COMMERCIAL | bwr13 | 10101102.0366 | 288 | bwr
COMMERCIAL | wo22 | 9017310.64 | 153 | wo
INDUSTRIAL | hpk24 | 9439809.63 | 31 | hpk
COMMERCIAL | cpk12 | 5057421.24 | 115 | cpk
| lyd14 | 55928.8081 | 17 | lyd
INDUSTRIAL | klo11 | 67703.26 | 1 | klo
RESIDENTL | ldl14 | 11349760.1474 | 1905 | ldl
LIGHTING | myt21 | 2294.9 | 1 | myt
RESIDENTL | rwn22 | 13452598.5118 | 2640 | rwn
COMMERCIAL | bm8b32 | 168652.4116 | 16 | bmb
INDUSTRIAL | bdl34 | 328519.77 | 31 | bdl
| tt12 | 16952.1045 | 5 | tt
RESIDENTL | wots24 | 6979604.5034 | 1172 | wots
INDUSTRIAL | wyk24 | 160679.33 | 16 | wyk
COMMERCIAL | klo12 | 12237846.22 | 9 | klo
RESIDENTL | wo33 | 232024.16 | 58 | wo
COMMERCIAL | bn24 | 3468313.5774 | 163 | bn
COMMERCIAL | lga12 | 9341312.33 | 61 | lga
| msd1 | 16071.3636 | 20 | msd
INDUSTRIAL | ofr24 | 300622.14 | 4 | ofr
INDUSTRIAL | bwn13 | 24333.45 | 4 | bwn
| tt1 | 26786.62 | 3 | tt
INDUSTRIAL | rwt31 | 22449174.23 | 3 | rwt
FARM | mfa14 | 28798.91 | 1 | mfa
| bwr32 | 10607.4826 | 52 | bwr
INDUSTRIAL | wn4 | 1120535.2101 | 54 | wn
RESIDENTL | bwr12 | 975012.274 | 199 | bwr
INDUSTRIAL | wgi24 | 1432383.73 | 33 | wgi
| llg13 | 135285.4952 | 24 | llg
| rwn34 | 10950.9 | 10 | rwn
FARM | elm34 | 16399.68 | 6 | elm
RESIDENTL | ruba12 | 12797333.4035 | 1890 | ruba
COMMERCIAL | hpk22 | 5875279.82 | 181 | hpk
| cln11 | 262675.9461 | 229 | cln
RESIDENTL | cf2 | 494427.3912 | 409 | cf
FARM | elm22 | 15544.2323 | 4 | elm
INDUSTRIAL | smg32 | 67645.78 | 1 | smg
FARM | bwa23 | 3495492.525 | 169 | bwa
NCONUML | phm24 | 66511.6 | 15 | phm
NCONUML | wgi23 | 35701.3 | 15 | wgi
NCONUML | epg35 | 18576.68 | 9 | epg
NCONUML | llg13 | 26801.83 | 12 | llg
LIGHTING | phi13 | 74566.47 | 1 | phi
| ldl24 | 28689.7774 | 48 | ldl
| bge11 | 41147.6131 | 30 | bge
RESIDENTL | ofr21 | 18456788.2346 | 4412 | ofr
INDUSTRIAL | ofr11 | 52339.71 | 6 | ofr
COMMERCIAL | nrn11 | 8254682.48 | 13 | nrn
FARM | moe15 | 1053275.4428 | 126 | moe
INDUSTRIAL | lyd12 | 15947.41 | 3 | lyd
INDUSTRIAL | wt10 | 5540.7 | 1 | wt
RESIDENTL | rwt21 | 965731.93 | 282 | rwt
FARM | wo13 | 51683.13 | 6 | wo
INDUSTRIAL | epg34 | 25722.81 | 2 | epg
COMMERCIAL | lys36 | 31611.41 | 1 | lys
RESIDENTL | wn6 | 17451542.0984 | 3750 | wn
NCONUML | hpk12 | 23613.79 | 7 | hpk
INDUSTRIAL | ruba24 | 189283.4035 | 13 | ruba
| nrn12 | 36108.6 | 9 | nrn
NCONUML | nla32 | 30069.03 | 18 | nla
COMMERCIAL | bm8b31 | 174913.9253 | 14 | bmb
| wo22 | 26321.2427 | 38 | wo
INDUSTRIAL | fgy31 | 4952.61 | 1 | fgy
RESIDENTL | cln14 | 25051991.2109 | 8311 | cln
RESIDENTL | lga24 | 3807672.9803 | 653 | lga
RESIDENTL | bra31 | 2624204.8049 | 649 | bra
COMMERCIAL | cln21 | 7282112.3749 | 104 | cln
COMMERCIAL | ftr23 | 8984637.4811 | 336 | ftr
RESIDENTL | klo13 | 97850.5847 | 89 | klo
INDUSTRIAL | ofr14 | 250.62 | 1 | ofr
FARM | mwl24 | 966080.4815 | 75 | mwl
NCONUML | bdl41 | 86032.0652 | 28 | bdl
INDUSTRIAL | epg13 | 201122.3196 | 20 | epg
COMMERCIAL | tgn23 | 6173474.1124 | 95 | tgn
| moe12 | 11374.0239 | 16 | moe
INDUSTRIAL | drn11 | 8297.91 | 2 | drn
| wn4 | 46461.2191 | 29 | wn
NCONUML | wgl13 | 85005.64 | 23 | wgl
INDUSTRIAL | ftr22 | 264831.3749 | 23 | ftr
NCONUML | mjg11 | 5653.43 | 3 | mjg
RESIDENTL | klo12 | 526.2 | 1 | klo
COMMERCIAL | cln11 | 18408618.7138 | 182 | cln
NCONUML | wo13 | 11132.69 | 4 | wo
COMMERCIAL | yn38 | 28127.08 | 5 | yn
NCONUML | mwl24 | 19701.6 | 5 | mwl
RESIDENTL | wots12 | 7880580.6899 | 1786 | wots
COMMERCIAL | tgn43 | 5598797.62 | 126 | tgn
NCONUML | mfa23 | 6277.17 | 3 | mfa
NCONUML | bra32 | 63005.82 | 38 | bra
FARM | bdl34 | 247623.03 | 51 | bdl
INDUSTRIAL | wn5 | 6299826.69 | 33 | wn
| mby13 | 155.9226 | 1 | mby
FARM | ofr23 | 2419763.5413 | 305 | ofr
NCONUML | cre22 | 86458.6773 | 42 | cre
NCONUML | hpk23 | 84001.53 | 23 | hpk
RESIDENTL | bra24 | 8260262.5707 | 1824 | bra
| cyn14 | 12637.7523 | 26 | cyn
LIGHTING | wgl11 | 2443513.25 | 2 | wgl
NCONUML | wgi24 | 69610.83 | 24 | wgi
COMMERCIAL | klo14 | 11961206.944 | 269 | klo
FARM | drn14 | 379625.3327 | 36 | drn
RESIDENTL | bwr22 | 1941843.629 | 510 | bwr
| llg14 | 42684.6726 | 22 | llg
INDUSTRIAL | drn21 | 709809.96 | 3 | drn
INDUSTRIAL | tgn42 | 199383.97 | 5 | tgn
RESIDENTL | sle32 | 6677118.757 | 1350 | sle
RESIDENTL | myt12 | 14552002.0991 | 2380 | myt
FARM | myt21 | 821475.54 | 124 | myt
| bn11 | 39921.12 | 40 | bn
NCONUML | mby12 | 15769.2 | 4 | mby
NCONUML | bdl44 | 1602.59 | 5 | bdl
COMMERCIAL | tt12 | 10810239.5174 | 467 | tt
NCONUML | wn7 | 7884.6 | 2 | wn
| bdl34 | 14430.17 | 36 | bdl
RESIDENTL | lyd11 | 11014119.7855 | 2574 | lyd
FARM | wyk23 | 2329152.6841 | 202 | wyk
| epg23 | 66262.7623 | 20 | epg
RESIDENTL | rwt32 | 15157646.1346 | 3808 | rwt
RESIDENTL | cre31 | 23125994.5084 | 5990 | cre
FARM | bn11 | 9012293.1298 | 1372 | bn
COMMERCIAL |  | 2470964.7554 | 79 | #REF!
INDUSTRIAL | kms11 | 3849512.37 | 9 | kms
RESIDENTL | sle31 | 15232222.0022 | 4728 | sle
RESIDENTL | myt11 | 3230941.4261 | 365 | myt
| wyk12 | 33744.4845 | 17 | wyk
| lga11 | 13750.1489 | 25 | lga
COMMERCIAL | cre33 | 14716025.8299 | 132 | cre
RESIDENTL | trc01 | 404888.8876 | 85 | trc
| moe25 | 10579.3743 | 23 | moe
NCONUML | msd1 | 8725.66 | 9 | msd
RESIDENTL | mwl14 | 1637810.9082 | 178 | mwl
FARM | wn5 | 10157746.9699 | 1090 | wn
INDUSTRIAL | bwr33 | 13101695.07 | 41 | bwr
NCONUML | ofr24 | 72292.73 | 18 | ofr
| mdg1 | 5594.13 | 4 | mdg
FARM | wgi33 | 86057.74 | 7 | wgi
RESIDENTL | rwt22 | 12512450.4989 | 3066 | rwt
RESIDENTL | cnr2 | 3844076.3719 | 1054 | cnr
| hpk14 | 17565.23 | 35 | hpk
NCONUML | drn23 | 37389.78 | 20 | drn
RESIDENTL | tgn44 | 11943542.7304 | 2804 | tgn
| tgn42 | 0 | 1 | tgn
NCONUML | rwt22 | 27503.296 | 22 | rwt
FARM | mwl16 | 172184.54 | 14 | mwl
COMMERCIAL | nla34 | 1413700.5844 | 93 | nla
| epg22 | 2049.9261 | 2 | epg
FARM | tgn41 | 3728231.4432 | 423 | tgn
COMMERCIAL | lga23 | 3382991.9134 | 119 | lga
NCONUML | sle31 | 61055.23 | 20 | sle
NCONUML | tgn44 | 66469.79 | 20 | tgn
| phm24 | 18272.6834 | 34 | phm
RESIDENTL | hpk11 | 16523367.4098 | 4141 | hpk
| hpk13 | 40054.7485 | 22 | hpk
| bwr24 | 10180.34 | 28 | bwr
COMMERCIAL | bdl33 | 34051046.7333 | 257 | bdl
COMMERCIAL | wt9 | 7035668.1433 | 128 | wt
NCONUML | wt15 | 16005.53 | 14 | wt
FARM | ruba24 | 730484.142 | 55 | ruba
NCONUML | cpk23 | 20021.69 | 18 | cpk
INDUSTRIAL | mwl21 | 320021.87 | 5 | mwl
COMMERCIAL | hpk23 | 12064171.7331 | 206 | hpk
INDUSTRIAL | wt11 | 2563605.84 | 2 | wt
RESIDENTL | wt15 | 8580853.2399 | 1947 | wt
| elm21 | 24345.52 | 16 | elm
INDUSTRIAL | mwl16 | 183545.9668 | 9 | mwl
FARM | rve13 | 9637.99 | 1 | rve
NCONUML | drn22 | 69938.3 | 27 | drn
NCONUML | bdl31 | 70697.58 | 29 | bdl
NCONUML | bwa24 | 1320.25 | 1 | bwa
COMMERCIAL | mwl23 | 10773058.8537 | 154 | mwl
COMMERCIAL | elm23 | 5093994.3825 | 95 | elm
FARM | smr23 | 1078615.6398 | 156 | smr
| cpk11 | 37835.6667 | 47 | cpk
INDUSTRIAL | bra14 | 14750.52 | 4 | bra
RESIDENTL | rwn33 | 5693275.4596 | 1153 | rwn
| bn22 | 41634.09 | 21 | bn
INDUSTRIAL | tt2 | 11531135.8238 | 100 | tt
INDUSTRIAL | wt12 | 3871876.0911 | 67 | wt
INDUSTRIAL | mwl22 | 292678.42 | 8 | mwl
RESIDENTL | bn23 | 8695284.412 | 1665 | bn
COMMERCIAL | cyn11 | 9621618.8569 | 233 | cyn
| cyn21 | 22400.14 | 28 | cyn
INDUSTRIAL | mjg11 | 1321804.29 | 13 | mjg
INDUSTRIAL | cf2 | 1970.494 | 2 | cf
RESIDENTL | tt5 | 6560032.4165 | 1633 | tt
COMMERCIAL | smr14 | 6818307.6657 | 239 | smr
COMMERCIAL | smg33 | 1348313.99 | 14 | smg
RESIDENTL | rwt15 | 11066767.0768 | 2454 | rwt
COMMERCIAL | cre32 | 14440881.1645 | 427 | cre
INDUSTRIAL | smr24 | 4639865.5557 | 45 | smr
COMMERCIAL | fgy23 | 10185283.97 | 98 | fgy
COMMERCIAL | hpk11 | 3476478.711 | 53 | hpk
| cre32 | 19011.64 | 13 | cre
NCONUML | wgl23 | 12760.41 | 6 | wgl
COMMERCIAL | nrn15 | 84419.81 | 3 | nrn
NCONUML | moe15 | 22748.39 | 11 | moe
RESIDENTL | tt12 | 86039.86 | 6 | tt
RESIDENTL | cyn31 | 8632445.7043 | 2077 | cyn
RESIDENTL | wgl24 | 16633542.8094 | 2715 | wgl
COMMERCIAL | wgi22 | 6881286.006 | 159 | wgi
INDUSTRIAL | smr13 | 992080.85 | 26 | smr
NCONUML | cpk12 | 17033.61 | 10 | cpk
NCONUML | ftr21 | 16597.26 | 11 | ftr
FARM | mwl12 | 18529.37 | 2 | mwl
INDUSTRIAL | epg33 | 1129768.4897 | 4 | epg
| wyk13 | 9658.4809 | 15 | wyk
LIGHTING | trc01 | 669938.2281 | 2 | trc
FARM | hpk13 | 2305.94 | 1 | hpk
RESIDENTL | tt6 | 19150788.3328 | 4695 | tt
FARM | tgn31 | 5369095.0164 | 562 | tgn
NCONUML | wgl24 | 11028.97 | 10 | wgl
INDUSTRIAL | brt11 | 82545.9018 | 12 | brt
LIGHTING | mby11 | 10728.24 | 1 | mby
NCONUML | myt21 | 24178.1 | 12 | myt
| wt10 | 6115.9374 | 5 | wt
RESIDENTL | bge12 | 9796026.1467 | 1789 | bge
FARM | myt11 | 2640136.7565 | 257 | myt
NCONUML | cyn11 | 21168.08 | 13 | cyn
INDUSTRIAL |  | 942329979.1078 | 12 | #REF!
INDUSTRIAL | elm34 | 168803.0667 | 15 | elm
| brt22 | 30486.3216 | 18 | brt
INDUSTRIAL | epg11 | 6777.42 | 2 | epg
RESIDENTL | elm34 | 19825611.7814 | 4189 | elm
COMMERCIAL | sle13 | 974523.8832 | 109 | sle
INDUSTRIAL | lga13 | 207007.5439 | 9 | lga
RESIDENTL | mwl23 | 3618535.6291 | 812 | mwl
| fgy14 | 28887.99 | 26 | fgy
COMMERCIAL | mby13 | 2521770.2974 | 71 | mby
| lga12 | 14720.56 | 12 | lga
RESIDENTL | cpk12 | 17343162.547 | 2927 | cpk
COMMERCIAL | wt5 | 19785711.5258 | 118 | wt
INDUSTRIAL | drn24 | 4643890.64 | 3 | drn
FARM | drn21 | 13254.24 | 1 | drn
NCONUML | mwl11 | 360.93 | 3 | mwl
RESIDENTL | epg34 | 15669683.4078 | 3862 | epg
NCONUML | wt10 | 27658.61 | 16 | wt
LIGHTING | rwt14 | 962126.36 | 3 | rwt
COMMERCIAL | drn23 | 5472888.3558 | 161 | drn
LIGHTING | bwn11 | 6340546.01 | 1 | bwn
INDUSTRIAL | sfs1 | 80102.39 | 5 | sfs
COMMERCIAL | phm34 | 4610839.9937 | 66 | phm
COMMERCIAL | mfa31 | 3803351.87 | 100 | mfa
INDUSTRIAL | rwt25 | 2203508.65 | 42 | rwt
| bwa22 | 41045.3074 | 24 | bwa
FARM | smr13 | 139441.5096 | 27 | smr
NCONUML | phi12 | 84007.84 | 24 | phi
| fgy21 | 10377.87 | 9 | fgy
NCONUML | rwt15 | 44056.974 | 28 | rwt
LIGHTING | nla34 | 5187.52 | 1 | nla
RESIDENTL | sfs1 | 6449039.4989 | 958 | sfs
RESIDENTL | msd4 | 16354350.3097 | 2395 | msd
INDUSTRIAL | phm33 | 724516.58 | 21 | phm
COMMERCIAL | wgl14 | 59932538.6 | 1 | wgl
COMMERCIAL | rwt31 | 3904134.109 | 54 | rwt
RESIDENTL | wt5 | 5466545.168 | 1335 | wt
FARM | ftr22 | 3872176.8459 | 271 | ftr
| wn5 | 51237.831 | 23 | wn
INDUSTRIAL | kms12 | 880994.04 | 26 | kms
NCONUML | rwt31 | 27889.28 | 18 | rwt
RESIDENTL | elm22 | 20622579.4478 | 3120 | elm
| bn24 | 7126.586 | 9 | bn
FARM | wots11 | 7572710.4051 | 689 | wots
INDUSTRIAL | myt11 | 122662.09 | 11 | myt
NCONUML | bdl32 | 81716.25 | 38 | bdl
NCONUML | cyn33 | 39860.39 | 20 | cyn
| lga13 | 7900.07 | 12 | lga
COMMERCIAL | wn7 | 705796.26 | 31 | wn
RESIDENTL | tgn23 | 12995258.1614 | 2157 | tgn
RESIDENTL | wgl12 | 18309192.1093 | 3011 | wgl
NCONUML | drn14 | 58816.42 | 20 | drn
INDUSTRIAL | tt9 | 1853761.73 | 4 | tt
RESIDENTL | kms12 | 23913269.0041 | 4277 | kms
COMMERCIAL | wgi33 | 13737748.8552 | 364 | wgi
COMMERCIAL | phm21 | 28428865.0993 | 838 | phm
FARM | sle32 | 5441049.7096 | 310 | sle
NCONUML | cyn32 | 58907.16 | 38 | cyn
INDUSTRIAL | msd2 | 165834.72 | 18 | msd
COMMERCIAL | bwr23 | 26845428.111 | 233 | bwr
RESIDENTL | msd2 | 5810770.2828 | 1153 | msd
FARM | klk11 | 2014936.8264 | 177 | klk
| wots12 | 13459.1171 | 22 | wots
INDUSTRIAL | rwn24 | 4339629.96 | 13 | rwn
INDUSTRIAL | tgn41 | 1853911.3546 | 62 | tgn
COMMERCIAL | smg32 | 6595824.87 | 22 | smg
| wgi34 | 86239.94 | 15 | wgi
RESIDENTL | bn22 | 13286130.4589 | 3118 | bn
RESIDENTL | mfa31 | 9237847.4317 | 2206 | mfa
COMMERCIAL | wgi34 | 9571334.08 | 60 | wgi
RESIDENTL | mdi1 | 176577.17 | 31 | mdi
NCONUML | rwn31 | 16738.19 | 15 | rwn
INDUSTRIAL | drn13 | 239296.9 | 11 | drn
INDUSTRIAL | bdl43 | 306419.52 | 21 | bdl
NCONUML | wo23 | 56204.51 | 16 | wo
COMMERCIAL | ftr21 | 2804675.8206 | 100 | ftr
COMMERCIAL | bwa23 | 206762.2501 | 23 | bwa
NCONUML | mfa21 | 28416.84 | 12 | mfa
| cln23 | 52144.7804 | 85 | cln
RESIDENTL | rve11 | 2276471.0008 | 508 | rve
COMMERCIAL | ofr24 | 6649904.8426 | 113 | ofr
NCONUML | phi13 | 105028.33 | 33 | phi
FARM | smg22 | 25054.15 | 4 | smg
FARM | bwn11 | 18419.1 | 1 | bwn
INDUSTRIAL | epg31 | 360181.3871 | 31 | epg
COMMERCIAL | fgy14 | 7872993.2117 | 231 | fgy
| ldl11 | 24480.7 | 22 | ldl
INDUSTRIAL | wgl24 | 939120.3004 | 39 | wgl
| phm22 | 31542.7748 | 10 | phm
COMMERCIAL | moe15 | 2469270.3666 | 172 | moe
| cnr3 | 100.0469 | 1 | cnr
RESIDENTL | bwn12 | 4456239.3509 | 1013 | bwn
COMMERCIAL | mwl24 | 5791496.4979 | 78 | mwl
COMMERCIAL | wo13 | 2493976.37 | 46 | wo
RESIDENTL | elm25 | 10534980.5572 | 2009 | elm
RESIDENTL | phm32 | 14466986.7977 | 3288 | phm
COMMERCIAL | ofr11 | 14130002.2904 | 224 | ofr
INDUSTRIAL | bge13 | 1057475.88 | 11 | bge
RESIDENTL | ofr22 | 7907197.5875 | 2174 | ofr
INDUSTRIAL | lga22 | 745287.81 | 44 | lga
FARM | hpk22 | 33600.65 | 5 | hpk
COMMERCIAL | epg23 | 63543126.9632 | 711 | epg
NCONUML | epg34 | 29379.47 | 21 | epg
| mwl23 | 14018.9088 | 10 | mwl
FARM | lyd14 | 350081.37 | 31 | lyd
| elm33 | 18371.0537 | 30 | elm
RESIDENTL | bwn11 | 14758921.2622 | 2984 | bwn
| cyn33 | 33636.86 | 37 | cyn
INDUSTRIAL | ldl13 | 1566146.5513 | 31 | ldl
NCONUML | smg32 | 19512.15 | 10 | smg
NCONUML | lga21 | 24931.49 | 9 | lga
RESIDENTL | mfa34 | 6438005.323 | 995 | mfa
COMMERCIAL | lga22 | 10229963.6597 | 340 | lga
COMMERCIAL | wgi31 | 4363035.5887 | 128 | wgi
| wt9 | 17175.83 | 21 | wt
INDUSTRIAL | mfa21 | 1292894.4886 | 57 | mfa
FARM | wgi32 | 343056.5273 | 19 | wgi
COMMERCIAL | bge21 | 44944.8 | 1 | bge
INDUSTRIAL | elm26 | 46289.86 | 5 | elm
NCONUML | msd4 | 12187.83 | 6 | msd
COMMERCIAL | bra21 | 14789918.5926 | 289 | bra
| cpk22 | 7305.07 | 12 | cpk
NCONUML | phm32 | 76324.09 | 20 | phm
NCONUML | sfs1 | 44865.78 | 10 | sfs
COMMERCIAL | lyd13 | 6072257.17 | 42 | lyd
FARM | cyn33 | 36456.98 | 4 | cyn
NCONUML | phm21 | 71428.0533 | 24 | phm
COMMERCIAL | sle32 | 5434267.6149 | 190 | sle
NCONUML | smg31 | 21751.86 | 17 | smg
NCONUML | wots11 | 25057.91 | 11 | wots
RESIDENTL | tgn43 | 15724147.9465 | 3608 | tgn
INDUSTRIAL | cyn21 | 9259443.95 | 23 | cyn
INDUSTRIAL | bn23 | 1923467.13 | 19 | bn
NCONUML | nrn14 | 79150.17 | 17 | nrn
NCONUML | cyn22 | 32483.16 | 10 | cyn
NCONUML | wgl12 | 47271.49 | 20 | wgl
COMMERCIAL | phm24 | 600129.57 | 25 | phm
NCONUML | lga11 | 25837.14 | 8 | lga
NCONUML | tgn41 | 7415.11 | 5 | tgn
RESIDENTL | wgl11 | 17118670.1537 | 3818 | wgl
RESIDENTL | wots11 | 15871220.8415 | 2910 | wots
| rwn31 | 40233.5106 | 27 | rwn
COMMERCIAL | elm32 | 8171019.0636 | 263 | elm
FARM | mby11 | 1335559.7721 | 187 | mby
INDUSTRIAL | mwl25 | 33119.15 | 8 | mwl
FARM | rwn26 | 5055.63 | 2 | rwn
| nla34 | 8234.98 | 10 | nla
RESIDENTL |  | 349105.8277 | 492 | #REF!
FARM | epg13 | 82815.8863 | 12 | epg
| wyk24 | 32167.14 | 30 | wyk
FARM | sle11 | 16862.17 | 6 | sle
COMMERCIAL | bm8b33 | 3349.12 | 2 | bmb
RESIDENTL | smg21 | 17914575.4009 | 3718 | smg
INDUSTRIAL | bdl42 | 622534.62 | 24 | bdl
| yn38 | 7519.7419 | 1 | yn
| phi13 | 28221.5917 | 27 | phi
| epg14 | 9258.9052 | 38 | epg
FARM | nla31 | 1791184.5035 | 140 | nla
INDUSTRIAL | wgi33 | 1188063.8119 | 37 | wgi
LIGHTING | phm33 | 4303153.65 | 2 | phm
RESIDENTL | phm33 | 12878778.4238 | 2134 | phm
COMMERCIAL | wgl23 | 3870974.8784 | 252 | wgl
NCONUML | wt5 | 58508.56 | 14 | wt
NCONUML | bwn14 | 81385.02 | 37 | bwn
NCONUML | mfa31 | 49958.93 | 14 | mfa
COMMERCIAL | bra12 | 23355928.37 | 122 | bra
NCONUML | wt13 | 98966.19 | 41 | wt
COMMERCIAL | klo24 | 13267963.2484 | 244 | klo
COMMERCIAL | bge12 | 6262328.83 | 64 | bge
COMMERCIAL | wn4 | 10511680.2174 | 332 | wn
INDUSTRIAL | tt6 | 2940006.87 | 14 | tt
FARM | cln13 | 4519.0334 | 1 | cln
RESIDENTL | bwa23 | 1839261.5711 | 259 | bwa
RESIDENTL | smr12 | 601661.7559 | 102 | smr
NCONUML | bra31 | 17155.48 | 11 | bra
FARM | cln22 | 84599.56 | 6 | cln
RESIDENTL | moe23 | 10757204.18 | 1872 | moe
FARM | bn23 | 4995698.9571 | 709 | bn
INDUSTRIAL | bwr12 | 7576207.2428 | 317 | bwr
COMMERCIAL | elm33 | 8652520.7547 | 229 | elm
RESIDENTL | tgn12 | 769554.192 | 239 | tgn
NCONUML | bn23 | 5729.17 | 9 | bn
| cyn11 | 35169.6447 | 13 | cyn
INDUSTRIAL | wots12 | 5742170.47 | 22 | wots
INDUSTRIAL | llg12 | 8080777.31 | 18 | llg
NCONUML | ofr14 | 11958.45 | 3 | ofr
RESIDENTL | rwn34 | 11161403.5989 | 1490 | rwn
RESIDENTL | fgy12 | 975691.3435 | 398 | fgy
COMMERCIAL | wyk24 | 11852940.7836 | 290 | wyk
COMMERCIAL | smr12 | 1199230.8 | 20 | smr
INDUSTRIAL | wgl11 | 590499.13 | 17 | wgl
INDUSTRIAL | moe13 | 8896507.14 | 13 | moe
INDUSTRIAL | wots11 | 14616083.73 | 22 | wots
NCONUML | epg13 | 4325.18 | 2 | epg
NCONUML | bn22 | 72789.04 | 38 | bn
RESIDENTL | bwr23 | 15381612.1105 | 3589 | bwr
NCONUML | cln13 | 19538.3161 | 10 | cln
COMMERCIAL | bwa24 | 4350900.07 | 4 | bwa
COMMERCIAL | bwr32 | 11258727.4704 | 251 | bwr
RESIDENTL | bra32 | 8710928.5985 | 2041 | bra
FARM | klo14 | 681766.459 | 92 | klo
INDUSTRIAL | tt7 | 9353368.9205 | 125 | tt
RESIDENTL | wo11 | 815896.564 | 156 | wo
LIGHTING | mwl24 | 803944.3 | 2 | mwl
COMMERCIAL | bwr24 | 7860784.794 | 262 | bwr
COMMERCIAL | drn14 | 5284276.4061 | 147 | drn
NCONUML | hpk24 | 27055.52 | 10 | hpk
| cyn32 | 34865.18 | 48 | cyn
| bra23 | 7974.72 | 25 | bra
RESIDENTL | rve13 | 16767421.4281 | 3587 | rve
COMMERCIAL | bwn13 | 11531398.8601 | 263 | bwn
FARM | cln23 | 76487.94 | 5 | cln
NCONUML | ruba24 | 1482.28 | 4 | ruba
COMMERCIAL | msd1 | 4448954.738 | 126 | msd
| phm31 | 2299.25 | 4 | phm
LIGHTING | wn1 | 677520.74 | 1 | wn
COMMERCIAL | wt8 | 2125517.5597 | 71 | wt
RESIDENTL | bdl33 | 5101200.3632 | 906 | bdl
COMMERCIAL | rwt21 | 33203170.5825 | 281 | rwt
FARM |  | 15223.9488 | 53 | #REF!
| fgy13 | 16173.63 | 19 | fgy
| wt11 | 14907.843 | 20 | wt
RESIDENTL | mwl24 | 4259131.5949 | 729 | mwl
INDUSTRIAL | bwn12 | 375603.57 | 33 | bwn
| lyd12 | 10355.6 | 16 | lyd
| lyd13 | 31235.27 | 24 | lyd
| elm32 | 28931.8643 | 22 | elm
RESIDENTL | ldl13 | 20183081.1078 | 3515 | ldl
COMMERCIAL | epg14 | 4722560.1631 | 66 | epg
FARM | epg32 | 616929.8369 | 16 | epg
| smg23 | 6841.4304 | 12 | smg
NCONUML | mwl16 | 31954.29 | 10 | mwl
COMMERCIAL | ofr22 | 3955299.41 | 63 | ofr
FARM | wgl24 | 9990463.449 | 886 | wgl
COMMERCIAL | llg14 | 8402501.0583 | 280 | llg
COMMERCIAL | wgi24 | 3234685.3433 | 136 | wgi
FARM | cnr3 | 47812.597 | 17 | cnr
| epg33 | 55263.0616 | 6 | epg
INDUSTRIAL | bra24 | 1115020.317 | 14 | bra
NCONUML | wgi33 | 84992.31 | 23 | wgi
FARM | rwt15 | 1849.17 | 1 | rwt
RESIDENTL | ldl12 | 620798.3677 | 119 | ldl
INDUSTRIAL | bwr22 | 8606432.4227 | 334 | bwr
FARM | cf2 | 2033.193 | 1 | cf
NCONUML | klo14 | 36515.49 | 28 | klo
INDUSTRIAL | trc01 | 31629.57 | 2 | trc
RESIDENTL | lga21 | 9412760.8279 | 1623 | lga
RESIDENTL | wt13 | 15834142.0313 | 3223 | wt
RESIDENTL | cyn13 | 3260017.5153 | 858 | cyn
INDUSTRIAL | ofr21 | 138382.59 | 9 | ofr
NCONUML | sle32 | 22407.43 | 13 | sle
COMMERCIAL | lyd12 | 210380 | 9 | lyd
NCONUML | wyk23 | 87622.06 | 45 | wyk
| fgy33 | 11652.67 | 18 | fgy
INDUSTRIAL | hpk22 | 98414.21 | 14 | hpk
NCONUML | sle11 | 59204.61 | 19 | sle
RESIDENTL | bwr13 | 20902397.8318 | 4170 | bwr
COMMERCIAL | rwn34 | 3999387.7688 | 144 | rwn
| hpk22 | 19671.58 | 41 | hpk
FARM | klk22 | 332413.14 | 10 | klk
INDUSTRIAL | wn1 | 2988984.92 | 20 | wn
NCONUML | rwn26 | 27156.61 | 25 | rwn
| bwr33 | 13120.641 | 3 | bwr
NCONUML | mby11 | 20114.34 | 7 | mby
RESIDENTL | smg33 | 11198068.0634 | 2626 | smg
FARM | bn12 | 813334.585 | 146 | bn
FARM | bdl32 | 1026406.0127 | 170 | bdl
FARM | drn24 | 15422429 | 2 | drn
LIGHTING | cre21 | 378603.77 | 3 | cre
RESIDENTL | smg32 | 834640.09 | 219 | smg
| wt12 | 39199.7023 | 19 | wt
FARM | bwn14 | 804408.7 | 76 | bwn
NCONUML | bwr33 | 16865.43 | 3 | bwr
INDUSTRIAL | rwn22 | 12871.85 | 4 | rwn
NCONUML | drn11 | 63307.01 | 20 | drn
INDUSTRIAL | mwl13 | 228128.43 | 11 | mwl
COMMERCIAL | elm22 | 6567142.5918 | 154 | elm
FARM | trc01 | 521142.3328 | 100 | trc
COMMERCIAL | rwt14 | 11855990.576 | 301 | rwt
INDUSTRIAL | sle14 | 1780526.4437 | 64 | sle
RESIDENTL | smr24 | 17064871.7804 | 2952 | smr
FARM | bwa22 | 1586063.9755 | 254 | bwa
NCONUML | tt4 | 37478.54 | 17 | tt
| tt9 | 28146.8116 | 74 | tt
COMMERCIAL | epg34 | 4040655.8363 | 65 | epg
FARM | nrn11 | 7816.07 | 2 | nrn
LIGHTING | cpk23 | 1632459.3 | 1 | cpk
RESIDENTL | fgy31 | 4476808.4262 | 913 | fgy
COMMERCIAL | fgy33 | 6399813.6929 | 132 | fgy
| cnr2 | 20535.9245 | 15 | cnr
INDUSTRIAL | sle32 | 10933678.58 | 25 | sle
| bra13 | 120577.89 | 18 | bra
RESIDENTL | wgi23 | 12118480.0079 | 2685 | wgi
INDUSTRIAL | wn6 | 922850.6842 | 19 | wn
LIGHTING | tgn44 | 752.53 | 1 | tgn
RESIDENTL | wt8 | 8250779.9392 | 1851 | wt
COMMERCIAL | moe25 | 5695010.3572 | 176 | moe
FARM | wgi34 | 4315044.5216 | 374 | wgi
INDUSTRIAL | fgy32 | 667572.7217 | 61 | fgy
NCONUML | wo32 | 55386.46 | 14 | wo
INDUSTRIAL | lys36 | 1267258.48 | 1 | lys
| bn12 | 10728.35 | 13 | bn
NCONUML | brt11 | 10828.27 | 7 | brt
| drn21 | 27694.76 | 39 | drn
| drn24 | 16030.7 | 26 | drn
RESIDENTL | cpk23 | 11646034.7633 | 2466 | cpk
RESIDENTL | wots13 | 7948103.7952 | 1344 | wots
FARM | wgl23 | 3908847.1376 | 390 | wgl
COMMERCIAL | wyk13 | 4417313.7071 | 191 | wyk
NCONUML | klk21 | 10664.54 | 6 | klk
INDUSTRIAL | smg22 | 31514.93 | 2 | smg
RESIDENTL | wgi22 | 12719214.8315 | 3088 | wgi
| cpk13 | 49314.0333 | 41 | cpk
COMMERCIAL | bdl41 | 11311068.2286 | 367 | bdl
NCONUML | nrn12 | 43208.48 | 18 | nrn
RESIDENTL | fgy23 | 5177398.3937 | 1023 | fgy
NCONUML | brt21 | 3240.29 | 5 | brt
NCONUML | tgn31 | 2100.01 | 7 | tgn
RESIDENTL | mjg11 | 6256821.3625 | 1064 | mjg
INDUSTRIAL | lga24 | 175905.212 | 21 | lga
COMMERCIAL | moe21 | 6644337.36 | 291 | moe
INDUSTRIAL | bwn14 | 326743.47 | 17 | bwn
INDUSTRIAL | phm22 | 15545673.5732 | 29 | phm
LIGHTING | klo24 | 2201282.63 | 3 | klo
FARM | epg12 | 13782.33 | 2 | epg
INDUSTRIAL | cln14 | 247.5387 | 1 | cln
FARM | bge13 | 383352.554 | 75 | bge
NCONUML | bra14 | 25509.54 | 26 | bra
RESIDENTL | fgy24 | 17189073.2659 | 3574 | fgy
NCONUML | lyd14 | 37348.84 | 18 | lyd
FARM | fgy21 | 91303 | 9 | fgy
INDUSTRIAL | elm24 | 6476.78 | 2 | elm
FARM | bra24 | 985.88 | 1 | bra
COMMERCIAL | ldl24 | 1420329.0926 | 55 | ldl
INDUSTRIAL | wots24 | 329358.8434 | 32 | wots
| moe13 | 6325.43 | 5 | moe
COMMERCIAL | cyn14 | 5422735.5047 | 221 | cyn
LIGHTING | smg21 | 4640189.26 | 4 | smg
COMMERCIAL | tgn42 | 24454733.755 | 420 | tgn
INDUSTRIAL | lga14 | 502652.15 | 16 | lga
INDUSTRIAL | cre33 | 377497.19 | 17 | cre
FARM | ldl11 | 223383.36 | 16 | ldl
INDUSTRIAL | bn24 | 28582582.13 | 34 | bn
COMMERCIAL | tt1 | 14308038.8686 | 155 | tt
| wn3 | 30735.58 | 33 | wn
NCONUML | ldl21 | 10778.31 | 7 | ldl
NCONUML | wt6 | 188781.23 | 35 | wt
RESIDENTL | elm23 | 20356024.4153 | 3325 | elm
COMMERCIAL | drn11 | 4003224.2127 | 79 | drn
COMMERCIAL | bra34 | 7850026.49 | 9 | bra
FARM | cyn32 | 3133.97 | 2 | cyn
FARM | cpk23 | 18946.87 | 2 | cpk
FARM | wt15 | 5251.96 | 1 | wt
NCONUML | wgi32 | 95036.63 | 31 | wgi
COMMERCIAL | phm32 | 13343791.1884 | 221 | phm
COMMERCIAL | epg22 | 38007492.3668 | 89 | epg
INDUSTRIAL | wgl15 | 1553419.6108 | 26 | wgl
FARM | phm33 | 7138587.5126 | 545 | phm
LIGHTING | bra32 | 1301740.84 | 1 | bra
COMMERCIAL | bra22 | 30448240 | 1 | bra
COMMERCIAL | msd4 | 11090376.2999 | 395 | msd
COMMERCIAL | lyd14 | 7038791.6959 | 51 | lyd
| phi12 | 701365.4285 | 34 | phi
| nrn11 | 5120.38 | 9 | nrn
INDUSTRIAL | smg21 | 777155.28 | 5 | smg
NCONUML | nla31 | 5002.08 | 5 | nla
RESIDENTL | wyk13 | 19583843.7522 | 3346 | wyk
RESIDENTL | tgn41 | 6800482.2089 | 1104 | tgn
COMMERCIAL | fgy34 | 7285642.6158 | 201 | fgy
FARM | wgl11 | 5210774.8775 | 355 | wgl
FARM | tgn11 | 616949.6887 | 82 | tgn
NCONUML | wn5 | 5268.61 | 9 | wn
NCONUML | bdl42 | 6088.6 | 9 | bdl
INDUSTRIAL | hpk23 | 515987.93 | 6 | hpk
FARM | tgn44 | 47621.17 | 6 | tgn
| smr13 | 35140.976 | 19 | smr
| wgi31 | 18377.08 | 37 | wgi
NCONUML | bwr34 | 85519.21 | 30 | bwr
| bdl32 | 24365.9844 | 40 | bdl
COMMERCIAL | fgy13 | 5672167.28 | 57 | fgy
INDUSTRIAL | sle31 | 621920.2305 | 85 | sle
NCONUML | cyn23 | 72679.67 | 24 | cyn
NCONUML | hpk22 | 92149.17 | 38 | hpk
RESIDENTL | cre23 | 13902510.3441 | 3180 | cre
COMMERCIAL | lga21 | 4415159.211 | 179 | lga
| cre33 | 51988.0123 | 70 | cre
INDUSTRIAL | bra32 | 800790.5812 | 33 | bra
| rwn26 | 43959.1499 | 36 | rwn
NCONUML | ftr22 | 27457.1971 | 11 | ftr
FARM | cyn23 | 28738.28 | 3 | cyn
FARM | wn2 | 2722540.844 | 262 | wn
FARM | wots25 | 1192605.1156 | 155 | wots
COMMERCIAL | lga11 | 2601951.4442 | 115 | lga
COMMERCIAL | cnr1 | 836269.15 | 40 | cnr
RESIDENTL | cre22 | 15737441.9951 | 3931 | cre
RESIDENTL | cyn24 | 3227627.7482 | 729 | cyn
| drn14 | 42739.5968 | 43 | drn
NCONUML | wgi34 | 240.62 | 2 | wgi
COMMERCIAL | mdi1 | 200221.43 | 4 | mdi
LIGHTING | lga22 | 290997.27 | 1 | lga
RESIDENTL | sle13 | 2426821.6594 | 1643 | sle
RESIDENTL | mby12 | 3267894.3821 | 609 | mby
FARM | wgi31 | 368672.79 | 43 | wgi
INDUSTRIAL | cyn24 | 15644182.2427 | 207 | cyn
| fgy34 | 3433.61 | 11 | fgy
RESIDENTL | bge11 | 15368827.4604 | 2654 | bge
RESIDENTL | ftr12 | 3825364.7454 | 636 | ftr
| mfa21 | 17049.39 | 26 | mfa
COMMERCIAL | wgi21 | 45541.7604 | 2 | wgi
INDUSTRIAL | wo14 | 2975508 | 24 | wo
COMMERCIAL | wgl12 | 5759083.9004 | 210 | wgl
INDUSTRIAL | moe23 | 765740.5661 | 26 | moe
COMMERCIAL | hpk14 | 5487941.7 | 85 | hpk
NCONUML | tt2 | 10017.24 | 3 | tt
INDUSTRIAL | cpk13 | 1507420.269 | 6 | cpk
INDUSTRIAL | lga41 | 52440142.6 | 1 | lga
NCONUML | elm26 | 60173.53 | 25 | elm
FARM | cf1 | 12492.747 | 1 | cf
RESIDENTL | bwr32 | 11435795.4629 | 2903 | bwr
NCONUML | cln23 | 19017.15 | 5 | cln
RESIDENTL | bdl41 | 18711766.0554 | 3582 | bdl
RESIDENTL | tt4 | 9918702.5206 | 2673 | tt
NCONUML | nrn13 | 44749.68 | 14 | nrn
NCONUML | mwl12 | 43601.75 | 11 | mwl
FARM | cln12 | 30466.72 | 1 | cln
INDUSTRIAL | cpk21 | 122110.94 | 5 | cpk
NCONUML | epg11 | 2275 | 2 | epg
FARM | brt22 | 1064314.9433 | 146 | brt
NCONUML | moe21 | 60919.67 | 15 | moe
RESIDENTL | ldl22 | 4948357.507 | 1104 | ldl
INDUSTRIAL | epg22 | 206880.17 | 13 | epg
NCONUML | cln12 | 55224.6632 | 17 | cln
| wo14 | 16653.0726 | 14 | wo
INDUSTRIAL | wo13 | 14774006.15 | 3 | wo
INDUSTRIAL | wgi22 | 729700.7 | 28 | wgi
COMMERCIAL | msd2 | 2629949.014 | 87 | msd
NCONUML | ldl22 | 11421.24 | 5 | ldl
RESIDENTL | wo22 | 17812297.6729 | 4125 | wo
FARM | mwl25 | 2028215.2676 | 224 | mwl
| cln14 | 46492.03 | 68 | cln
INDUSTRIAL | smr14 | 413387.45 | 34 | smr
FARM | rwn33 | 39914.72 | 5 | rwn
NCONUML | tt7 | 28203.83 | 11 | tt
INDUSTRIAL | lga11 | 317451.8284 | 16 | lga
INDUSTRIAL | tt12 | 6074893.6495 | 86 | tt
INDUSTRIAL | rwn32 | 87972.96 | 1 | rwn
RESIDENTL | myt21 | 10899844.0445 | 1487 | myt
RESIDENTL | cyn14 | 9596207.6734 | 2758 | cyn
RESIDENTL | kms11 | 9874885.3712 | 1972 | kms
COMMERCIAL | wo32 | 9961950.2687 | 147 | wo
NCONUML | hpk21 | 96497.83 | 40 | hpk
FARM | mwl13 | 248036.6173 | 7 | mwl
RESIDENTL | smr23 | 3447913.5369 | 523 | smr
INDUSTRIAL | nla32 | 1443086.18 | 25 | nla
| rwt32 | 35174.87 | 36 | rwt
INDUSTRIAL | moe11 | 65970.59 | 6 | moe
INDUSTRIAL | wo33 | 33298223.9508 | 7 | wo
INDUSTRIAL | bra31 | 2919.84 | 1 | bra
RESIDENTL | moe15 | 9740983.6859 | 1552 | moe
RESIDENTL | moe12 | 4538532.291 | 887 | moe
INDUSTRIAL | bdl41 | 1328921.5447 | 34 | bdl
NCONUML | tt6 | 36560.52 | 20 | tt
RESIDENTL | uwy1 | 6496143.3356 | 1032 | uwy
RESIDENTL | wgi32 | 16438958.2366 | 3917 | wgi
COMMERCIAL | rwn31 | 2125446.8547 | 72 | rwn
| ldl13 | 45979.2126 | 34 | ldl
LIGHTING | hpk23 | 2010173.36 | 1 | hpk
RESIDENTL | fgy14 | 9703108.5669 | 2483 | fgy
FARM | rwn24 | 30208.83 | 4 | rwn
COMMERCIAL | wo23 | 11409957.4027 | 304 | wo
| myt12 | 115131.3847 | 34 | myt
| bge13 | 13458.3255 | 19 | bge
| sle32 | 15918.6359 | 20 | sle
FARM | epg11 | 14625.27 | 2 | epg
NCONUML | mwl21 | 34561.25 | 17 | mwl
COMMERCIAL | nrn12 | 21654160.6835 | 271 | nrn
COMMERCIAL | llg13 | 15983000.2277 | 99 | llg
| lga22 | 14116.8478 | 12 | lga
FARM | hpk11 | 14620.89 | 5 | hpk
RESIDENTL | ofr11 | 25072251.243 | 5672 | ofr
FARM | ftr12 | 9732520.1395 | 879 | ftr
RESIDENTL | epg21 | 580054.4394 | 151 | epg
FARM | bge22 | 343097.1961 | 60 | bge
COMMERCIAL | sfs1 | 1879673.1771 | 124 | sfs
| cln24 | 61460.6675 | 37 | cln
NCONUML | smg22 | 48204.28 | 25 | smg
RESIDENTL | phm34 | 11301839.7716 | 2904 | phm
RESIDENTL | phm31 | 2762476.4376 | 550 | phm
NCONUML | smr13 | 69764.68 | 26 | smr
RESIDENTL | wyk12 | 12357178.5976 | 1789 | wyk
INDUSTRIAL | sle13 | 125251.914 | 47 | sle
FARM | phm24 | 689286.43 | 52 | phm
| cre31 | 63798.4484 | 85 | cre
INDUSTRIAL | bge12 | 121322.77 | 7 | bge
FARM | wots12 | 5076.62 | 1 | wots
NCONUML | cf1 | 1922.85 | 2 | cf
RESIDENTL | wo31 | 20016820.444 | 4554 | wo
FARM | smr22 | 1275801.32 | 154 | smr
FARM | lga22 | 1443457.6222 | 105 | lga
COMMERCIAL | mwl22 | 10003347.9587 | 192 | mwl
FARM | bn24 | 2239563.0749 | 370 | bn
NCONUML | wots25 | 45798.68 | 13 | wots
NCONUML | wgi31 | 79233.36 | 21 | wgi
FARM | epg23 | 30049.96 | 2 | epg
NCONUML | klk11 | 24723.1 | 13 | klk
| mwl14 | 3593.32 | 2 | mwl
RESIDENTL | mdg1 | 4384126.608 | 684 | mdg
RESIDENTL | nrn14 | 9562152.1887 | 1877 | nrn
LIGHTING | msd4 | 139319.89 | 1 | msd
LIGHTING | sfs1 | 1558457.9 | 1 | sfs
| klo14 | 120043.1087 | 185 | klo
RESIDENTL | hpk14 | 17025183.7337 | 3944 | hpk
FARM | lga12 | 4046898.7707 | 351 | lga
COMMERCIAL | ldl14 | 12475957.7156 | 266 | ldl
RESIDENTL | bn11 | 14382992.5485 | 2912 | bn
COMMERCIAL | bdl34 | 6213094.4744 | 204 | bdl
FARM | lyd11 | 23799.7 | 3 | lyd
| mwl22 | 10189.434 | 23 | mwl
NCONUML | cf2 | 120.31 | 1 | cf
| epg32 | 18473.04 | 31 | epg
RESIDENTL | bdl34 | 21922135.2151 | 5106 | bdl
COMMERCIAL | rwn26 | 3719056.4225 | 81 | rwn
INDUSTRIAL | mby13 | 219583.33 | 2 | mby
NCONUML | fgy33 | 40029.49 | 14 | fgy
| ftr22 | 13372.1897 | 14 | ftr
NCONUML | mwl13 | 53127.87 | 17 | mwl
INDUSTRIAL | rwt32 | 132361.99 | 4 | rwt
COMMERCIAL | phm23 | 17053480.4 | 2 | phm
COMMERCIAL | bra13 | 19208526.3529 | 181 | bra
FARM | wn1 | 37241.96 | 7 | wn
FARM | bm8b33 | 1540.9 | 2 | bmb
COMMERCIAL | wt10 | 13883699.3972 | 155 | wt
INDUSTRIAL | uwy1 | 90405.23 | 3 | uwy
RESIDENTL | ldl23 | 26005181.5029 | 4084 | ldl
FARM | klo24 | 194259.84 | 22 | klo
| hpk11 | 33718.6052 | 42 | hpk
NCONUML | phm33 | 47915.862 | 19 | phm
FARM | wn6 | 4543418.3442 | 605 | wn
COMMERCIAL | cyn21 | 3633643.5973 | 195 | cyn
INDUSTRIAL | wo22 | 393144.5 | 11 | wo
RESIDENTL | tgn42 | 795534.2193 | 223 | tgn
INDUSTRIAL | mwl23 | 715134.0252 | 54 | mwl
| rwt22 | 26934.55 | 52 | rwt
COMMERCIAL | phm31 | 4117822.4369 | 32 | phm
RESIDENTL | epg22 | 39578.43 | 14 | epg
RESIDENTL | nla32 | 6559402.1513 | 1220 | nla
RESIDENTL | myt22 | 1017937.6841 | 120 | myt
| wgl15 | 30619.4 | 19 | wgl
LIGHTING | mjg11 | 68938.73 | 1 | mjg
COMMERCIAL | phi12 | 2400712.314 | 73 | phi
COMMERCIAL | rwt36 | 2264519.95 | 43 | rwt
INDUSTRIAL | wgi23 | 157973.74 | 15 | wgi
NCONUML | elm24 | 74942.52 | 25 | elm
RESIDENTL | wt10 | 3332972.5881 | 860 | wt
NCONUML | ruba22 | 360.93 | 3 | ruba
FARM | phi11 | 82538.05 | 19 | phi
| bra11 | 11169.2884 | 32 | bra
INDUSTRIAL | moe15 | 1465208.8927 | 46 | moe
| tt5 | 13084.5535 | 33 | tt
LIGHTING | elm34 | 2971413.79 | 6 | elm
FARM | rwt25 | 33966.32 | 4 | rwt
RESIDENTL | moe11 | 9711471.9521 | 1967 | moe
INDUSTRIAL | rwt22 | 12240.297 | 2 | rwt
FARM | tgn23 | 1979366.6929 | 215 | tgn
COMMERCIAL | elm34 | 4840398.0166 | 153 | elm
NCONUML | phi11 | 19831.48 | 5 | phi
NCONUML | bra13 | 31922.03 | 14 | bra
RESIDENTL | mwl11 | 7113484.1589 | 1047 | mwl
| sle14 | 9929.5555 | 28 | sle
COMMERCIAL | cpk11 | 7316179.79 | 51 | cpk
| cyn31 | 5192.9 | 11 | cyn
NCONUML | epg12 | 1563.57 | 9 | epg
| epg11 | 4794.77 | 9 | epg
INDUSTRIAL | bwa23 | 17470876.21 | 8 | bwa
FARM | cln21 | 792.83 | 1 | cln
COMMERCIAL | wn3 | 8489705.5245 | 275 | wn
COMMERCIAL | bwn12 | 29123057.9665 | 274 | bwn
NCONUML | bra23 | 28962.5293 | 21 | bra
| bge12 | 5967.8256 | 14 | bge
INDUSTRIAL | tgn12 | 464065.58 | 15 | tgn
LIGHTING | fgy31 | 1047083.29 | 1 | fgy
NCONUML | moe25 | 63582.44 | 18 | moe
NCONUML | fgy21 | 30728.13 | 12 | fgy
INDUSTRIAL | lyd11 | 151654.68 | 9 | lyd
FARM | bwn13 | 5960.02 | 1 | bwn
RESIDENTL | lga11 | 6965787.8425 | 1044 | lga
NCONUML | bwr22 | 31744.79 | 14 | bwr
COMMERCIAL | llg12 | 3977405.3306 | 115 | llg
COMMERCIAL | mfa21 | 3716072.0048 | 197 | mfa
INDUSTRIAL | phm32 | 1008.48 | 1 | phm
COMMERCIAL | nrn13 | 3605622.38 | 41 | nrn
FARM | cyn22 | 1131.4275 | 1 | cyn
INDUSTRIAL | ftr23 | 1828762.8842 | 76 | ftr
INDUSTRIAL | mfa31 | 463955.39 | 14 | mfa
INDUSTRIAL | bge11 | 395339.98 | 10 | bge
RESIDENTL | wo13 | 2691801.805 | 586 | wo
RESIDENTL | llg11 | 4969161.4408 | 709 | llg
| cpk21 | 8908.612 | 12 | cpk
INDUSTRIAL | cre23 | 238715.04 | 8 | cre
COMMERCIAL | epg33 | 43303826.6612 | 357 | epg
FARM | ofr21 | 60907.55 | 6 | ofr
COMMERCIAL | cpk22 | 8802072.7366 | 32 | cpk
NCONUML | bra24 | 34184.91 | 27 | bra
NCONUML | wn6 | 84222.69 | 35 | wn
FARM | mfa22 | 15017348.1505 | 702 | mfa
FARM | lga24 | 2675198.7919 | 323 | lga
COMMERCIAL | phi13 | 13565764.588 | 480 | phi
FARM | lga13 | 6142984.8245 | 572 | lga
NCONUML | wn2 | 74469.51 | 25 | wn
COMMERCIAL | wyk23 | 9043742.9219 | 306 | wyk
INDUSTRIAL | cyn31 | 110897.03 | 2 | cyn
RESIDENTL | wt7 | 9398293.9689 | 2293 | wt
COMMERCIAL | rwt15 | 2407529.701 | 118 | rwt
| wots11 | 29868.01 | 43 | wots
COMMERCIAL | wt12 | 9788397.4198 | 246 | wt
FARM | wots24 | 5049980.8194 | 706 | wots
COMMERCIAL | ftr22 | 3919173.7529 | 139 | ftr
INDUSTRIAL | ruba12 | 859698.6565 | 35 | ruba
| wots25 | 37134.4365 | 43 | wots
RESIDENTL | ofr24 | 14317680.0438 | 3420 | ofr
COMMERCIAL | bdl32 | 9327480.3168 | 349 | bdl
NCONUML | trc01 | 2600.11 | 1 | trc
RESIDENTL | wgi33 | 15074294.4922 | 2906 | wgi
RESIDENTL | wyk24 | 16651462.561 | 3130 | wyk
NCONUML | wn1 | 109135.95 | 32 | wn
NCONUML | fgy34 | 69468.4 | 26 | fgy
| tgn43 | 23585.3 | 37 | tgn
| bwn11 | 22540.96 | 33 | bwn
COMMERCIAL | bn11 | 11469939.8143 | 448 | bn
RESIDENTL | wn7 | 334597.06 | 81 | wn
FARM | lga23 | 6580772.0568 | 604 | lga
RESIDENTL | mby13 | 1114988.13 | 129 | mby
INDUSTRIAL | moe12 | 309363.05 | 10 | moe
NCONUML | wgl21 | 72341.71 | 26 | wgl
| rwn22 | 13422.17 | 20 | rwn
FARM | ofr13 | 1726.88 | 2 | ofr
INDUSTRIAL | smg33 | 3791.86 | 1 | smg
COMMERCIAL | cnr2 | 2241662.7301 | 123 | cnr
NCONUML | bwn13 | 114734.08 | 27 | bwn
INDUSTRIAL | tgn43 | 8336.37 | 2 | tgn
NCONUML | bra33 | 54640.5039 | 38 | bra
LIGHTING | drn23 | 137376.82 | 1 | drn
COMMERCIAL | wt11 | 6045415.4763 | 137 | wt
| wo23 | 3425.76 | 13 | wo
RESIDENTL | drn11 | 23689909.4015 | 5897 | drn
RESIDENTL | bra33 | 17227071.6094 | 3920 | bra
FARM | cre21 | 1165190.53 | 9 | cre
| wo32 | 20472.5797 | 26 | wo
NCONUML | mfa22 | 12133.93 | 8 | mfa
COMMERCIAL | fgy32 | 10874129.2215 | 316 | fgy
INDUSTRIAL | bdl33 | 6444229.03 | 34 | bdl
NCONUML | cnr3 | 880.96 | 3 | cnr
COMMERCIAL | bwr14 | 64319.73 | 1 | bwr
NCONUML | ldl11 | 15379.88 | 9 | ldl
FARM | bdl33 | 333127.23 | 48 | bdl
INDUSTRIAL | elm23 | 351538.3612 | 12 | elm
NCONUML | lga14 | 16509.29 | 6 | lga
NCONUML | rwt21 | 45520.76 | 13 | rwt
INDUSTRIAL | mwl24 | 3823292.43 | 15 | mwl
RESIDENTL | epg14 | 8906284.5994 | 2218 | epg
NCONUML | drn21 | 11559.57 | 6 | drn
FARM | ldl21 | 4274.77 | 1 | ldl
| lga14 | 13272.15 | 11 | lga
LIGHTING | wo22 | 1145144.2306 | 3 | wo
LIGHTING | bdl33 | 755365.47 | 1 | bdl
INDUSTRIAL | lga12 | 340570.559 | 7 | lga
RESIDENTL | ofr23 | 20573594.8025 | 3065 | ofr
LIGHTING | tgn12 | 393.8997 | 1 | tgn
RESIDENTL | fgy32 | 4718000.0914 | 1180 | fgy
COMMERCIAL | moe11 | 6876107.6583 | 169 | moe
COMMERCIAL | wgl13 | 16726185.3211 | 289 | wgl
COMMERCIAL | cre22 | 19152716.1468 | 212 | cre
RESIDENTL | drn12 | 16081122.8597 | 3986 | drn
COMMERCIAL | mfa23 | 8005013.26 | 78 | mfa
| cln13 | 39224.5517 | 61 | cln
INDUSTRIAL | mfa22 | 1793714.26 | 36 | mfa
LIGHTING | smr23 | 37560.88 | 1 | smr
RESIDENTL | rwn32 | 6727398.7344 | 1603 | rwn
FARM | lga14 | 4550189.1065 | 436 | lga
| cln12 | 24735.6225 | 51 | cln
COMMERCIAL | kms11 | 4936701.5866 | 120 | kms
RESIDENTL | smr14 | 10997106.9114 | 1697 | smr
| epg13 | 194183.3358 | 102 | epg
| brt21 | 9723.1397 | 7 | brt
INDUSTRIAL | drn12 | 10032.09 | 2 | drn
| tt7 | 34871.95 | 3 | tt
INDUSTRIAL | wots25 | 7153785.931 | 7 | wots
FARM | tgn43 | 14451.81 | 2 | tgn
NCONUML | ldl14 | 38917.21 | 26 | ldl
INDUSTRIAL | brt21 | 238786.6 | 10 | brt
| llg11 | 8477.8 | 10 | llg
RESIDENTL | wgi24 | 12721878.952 | 3596 | wgi
RESIDENTL | cyn21 | 10508542.767 | 2257 | cyn
INDUSTRIAL | bra11 | 3982632.29 | 3 | bra
INDUSTRIAL | phi11 | 184139.3994 | 13 | phi
| hpk24 | 8609.4373 | 14 | hpk
NCONUML | ldl13 | 24965.12 | 22 | ldl
RESIDENTL | hpk21 | 20637351.8958 | 5254 | hpk
RESIDENTL | wgl13 | 19626090.0794 | 4751 | wgl
COMMERCIAL | elm21 | 12124007.57 | 258 | elm
COMMERCIAL | wt13 | 23168272.4303 | 498 | wt
| hpk23 | 55023.71 | 41 | hpk
COMMERCIAL | mdg1 | 1157212.0402 | 52 | mdg
NCONUML | wt11 | 64055.27 | 25 | wt
NCONUML | phm31 | 9383.328 | 4 | phm
COMMERCIAL | bge23 | 4904566.2339 | 176 | bge
NCONUML | smg23 | 17942.69 | 11 | smg
| mwl16 | 4764.4783 | 12 | mwl
COMMERCIAL | hpk12 | 20352329.5415 | 361 | hpk
RESIDENTL | ruba24 | 4395729.6843 | 894 | ruba
COMMERCIAL | nla32 | 3390681.6399 | 175 | nla
NCONUML | lyd12 | 44439.84 | 9 | lyd
| cln22 | 289385.5413 | 85 | cln
NCONUML | cpk21 | 53769.1 | 26 | cpk
| ruba22 | 8482.6526 | 15 | ruba
COMMERCIAL | myt22 | 191990.12 | 18 | myt
RESIDENTL | mby11 | 5261006.6685 | 922 | mby
RESIDENTL | rwn26 | 21195116.3973 | 2454 | rwn
| rwt31 | 14608.62 | 19 | rwt
INDUSTRIAL | epg35 | 1615230.05 | 4 | epg
| bge23 | 30837.693 | 28 | bge
NCONUML | bdl34 | 70291.97 | 25 | bdl
NCONUML | ofr13 | 30258.73 | 11 | ofr
| klk11 | 25230.2094 | 21 | klk
NCONUML | bn12 | 1241.66 | 2 | bn
COMMERCIAL | wgi32 | 5461052.6827 | 195 | wgi
NCONUML | ldl12 | 45990.38 | 14 | ldl
INDUSTRIAL | bra23 | 3394433.4433 | 42 | bra
| wo33 | 4138.8 | 1 | wo
NCONUML | myt12 | 33269.22 | 16 | myt
INDUSTRIAL | ldl11 | 1468879.69 | 10 | ldl
RESIDENTL | msd1 | 8481569.4252 | 1750 | msd
NCONUML | bn11 | 57126.91 | 28 | bn
INDUSTRIAL | ftr12 | 2824402.5 | 31 | ftr
INDUSTRIAL | hpk11 | 29483.41 | 8 | hpk
NCONUML | epg33 | 5589.26 | 2 | epg
COMMERCIAL | wo31 | 10532525.1457 | 139 | wo
| wgl21 | 38182.04 | 53 | wgl
| bge22 | 25062.3495 | 31 | bge
RESIDENTL | tt1 | 171030.69 | 8 | tt
INDUSTRIAL | bwr34 | 134229.36 | 26 | bwr
COMMERCIAL | bra33 | 14409139.6368 | 303 | bra
COMMERCIAL | bdl44 | 4495186.894 | 197 | bdl
| bwn13 | 12482.8878 | 14 | bwn
NCONUML | wn3 | 40552.61 | 16 | wn
NCONUML | smr24 | 41055.27 | 16 | smr
INDUSTRIAL | mwl14 | 4499194.0326 | 50 | mwl
| wots24 | 36833.8626 | 36 | wots
NCONUML | wt12 | 74491.29 | 36 | wt
COMMERCIAL | smg31 | 17181337.4 | 81 | smg
FARM | lyd13 | 146611.14 | 18 | lyd
NCONUML | wots12 | 53576.05 | 15 | wots
INDUSTRIAL | fgy12 | 30820.7097 | 2 | fgy
FARM | myt12 | 4025860.4278 | 600 | myt
INDUSTRIAL | cyn22 | 204983.76 | 12 | cyn
COMMERCIAL | cyn33 | 3196035.4476 | 122 | cyn
COMMERCIAL | mby12 | 1853426.4391 | 89 | mby
NCONUML | tgn43 | 111938.06 | 34 | tgn
NCONUML | wo11 | 17571.55 | 5 | wo
INDUSTRIAL | epg12 | 1405424.52 | 3 | epg
| cf2 | 30699.57 | 2 | cf
COMMERCIAL | llg11 | 3213282.749 | 85 | llg
LIGHTING | rwn24 | 1936572.72 | 3 | rwn
INDUSTRIAL | cln24 | 15633.29 | 3 | cln
FARM | sle31 | 4999785.6618 | 315 | sle
INDUSTRIAL | cf1 | 129164.746 | 4 | cf
| ruba12 | 126134.0367 | 24 | ruba
| bwr12 | 18318.3952 | 15 | bwr
FARM | elm32 | 382389.8968 | 32 | elm
| ofr21 | 113717.1 | 52 | ofr
INDUSTRIAL | wn2 | 282430.54 | 13 | wn
NCONUML | bge22 | 82280.88 | 49 | bge
NCONUML | cnr2 | 33661.17 | 17 | cnr
NCONUML | wots13 | 10386.18 | 6 | wots
FARM | elm24 | 39172.3194 | 4 | elm
COMMERCIAL | nrn14 | 6896476.1265 | 116 | nrn
NCONUML | ruba12 | 27603.68 | 16 | ruba
NCONUML | hpk13 | 50290.3 | 16 | hpk
NCONUML | bra11 | 44798.92 | 35 | bra
| rwt21 | 23376.2409 | 6 | rwt
RESIDENTL | drn23 | 20613814.4846 | 2434 | drn
RESIDENTL | rwt36 | 2676215.9999 | 821 | rwt
RESIDENTL | llg13 | 6857833.0372 | 1230 | llg
COMMERCIAL | wyk12 | 4295149.2844 | 131 | wyk
INDUSTRIAL | ofr13 | 1622296.11 | 21 | ofr
| bra14 | 30334.7783 | 42 | bra
INDUSTRIAL | tgn11 | 3321263.75 | 18 | tgn
LIGHTING | mby13 | 9944.78 | 1 | mby
RESIDENTL | cln11 | 39284605.9906 | 12154 | cln
COMMERCIAL | drn22 | 10741065.2473 | 246 | drn
RESIDENTL | wo32 | 11244170.0715 | 2343 | wo
| bra33 | 27895.4569 | 47 | bra
COMMERCIAL | epg21 | 21867278.1603 | 75 | epg
INDUSTRIAL | cre21 | 293542.6 | 2 | cre
RESIDENTL | bwr24 | 1834966.95 | 415 | bwr
RESIDENTL | hpk13 | 8888406.848 | 2283 | hpk
NCONUML | moe13 | 240.62 | 2 | moe
RESIDENTL | mwl12 | 3605926.3697 | 887 | mwl
| elm24 | 29520.3106 | 27 | elm
COMMERCIAL | tgn31 | 5251765.7474 | 163 | tgn
| rwt25 | 17882.0217 | 23 | rwt
RESIDENTL | moe21 | 9438147.1697 | 1978 | moe
COMMERCIAL | mjg11 | 16973320.0649 | 258 | mjg
COMMERCIAL | moe22 | 1619971.835 | 34 | moe
NCONUML | cpk13 | 44472.2623 | 32 | cpk
| phi11 | 13149.9006 | 9 | phi
FARM | cyn11 | 2814.65 | 1 | cyn
FARM | cyn24 | 25049.8 | 2 | cyn
FARM | drn13 | 379220.8035 | 25 | drn
COMMERCIAL | mwe236 | 663523.2 | 21 | mwe
INDUSTRIAL | phm24 | 35612.08 | 4 | phm
INDUSTRIAL | bge22 | 36211.2493 | 9 | bge
RESIDENTL | cnr1 | 478523.9112 | 104 | cnr
| lga24 | 10918.35 | 11 | lga
NCONUML | sle14 | 98131.7526 | 34 | sle
NCONUML | tt5 | 14462.54 | 12 | tt
| epg12 | 53720.6497 | 70 | epg
NCONUML | kms11 | 42647.24 | 13 | kms
FARM | elm23 | 38507.8 | 8 | elm
COMMERCIAL | cyn12 | 12045879.7132 | 241 | cyn
INDUSTRIAL | fgy23 | 1420677.79 | 11 | fgy
COMMERCIAL | mfa14 | 259168.13 | 17 | mfa
| bra31 | 49797.7422 | 13 | bra
COMMERCIAL | mwl12 | 1780079.4127 | 78 | mwl
| bwr22 | 2405.71 | 25 | bwr
INDUSTRIAL | fgy24 | 415478.9 | 15 | fgy
COMMERCIAL | hpk13 | 9763023.5697 | 134 | hpk
| cyn22 | 22272.33 | 22 | cyn
| ldl21 | 13369.5383 | 42 | ldl
| wt6 | 17591.4373 | 23 | wt
RESIDENTL | wn4 | 11276854.4814 | 2349 | wn
FARM | mwl14 | 451834.7532 | 54 | mwl
RESIDENTL | bm8b31 | 357131.6719 | 111 | bmb
NCONUML | cyn14 | 48577.9677 | 22 | cyn
FARM | cre32 | 5136.47 | 1 | cre
FARM | bwr34 | 4550.33 | 1 | bwr
RESIDENTL | llg14 | 14855712.1657 | 2170 | llg
FARM | smg33 | 29400.19 | 7 | smg
RESIDENTL | drn22 | 21996972.8148 | 3999 | drn
NCONUML | elm32 | 42948.38 | 25 | elm
INDUSTRIAL | klo14 | 587332.99 | 17 | klo
| tgn11 | 22256.53 | 32 | tgn
INDUSTRIAL | tgn44 | 4536032.57 | 9 | tgn
COMMERCIAL | ldl23 | 15994398.5627 | 272 | ldl
| wn6 | 146062.0009 | 59 | wn
COMMERCIAL | tt2 | 18806104.6367 | 399 | tt
COMMERCIAL | brt11 | 4047117.81 | 129 | brt
NCONUML | llg14 | 65195.01 | 40 | llg
FARM | fgy24 | 95940.3 | 9 | fgy
NCONUML | fgy14 | 61562.37 | 33 | fgy
COMMERCIAL | rve12 | 3272242.91 | 54 | rve
INDUSTRIAL | cpk23 | 208291.634 | 5 | cpk
| lga23 | 41697.3391 | 21 | lga
INDUSTRIAL | yn38 | 642769.3081 | 6 | yn
COMMERCIAL | bwa21 | 7920817.52 | 6 | bwa
INDUSTRIAL | elm25 | 2097.04 | 1 | elm
COMMERCIAL | wots13 | 3416108.1488 | 213 | wots
FARM | wgi22 | 191494.2501 | 24 | wgi
NCONUML | fgy13 | 27847.71 | 7 | fgy
| bra24 | 9840.15 | 27 | bra
FARM | ofr14 | 100163.6258 | 21 | ofr
NCONUML | nrn11 | 16820.36 | 5 | nrn
RESIDENTL | smg31 | 12434679.8443 | 2879 | smg
COMMERCIAL | smr24 | 15083854.4686 | 348 | smr
| lyd11 | 12152.66 | 25 | lyd
INDUSTRIAL | bra12 | 1282907.1727 | 55 | bra
FARM | wgl15 | 3297105.6723 | 233 | wgl
INDUSTRIAL | msd1 | 544058.7154 | 15 | msd
| epg31 | 13971.3347 | 31 | epg
INDUSTRIAL | wgl23 | 572354.5027 | 44 | wgl
INDUSTRIAL | cpk12 | 343353.79 | 14 | cpk
INDUSTRIAL | mfa34 | 4790944.63 | 37 | mfa
| wn2 | 65478.1843 | 60 | wn
INDUSTRIAL | drn23 | 222019.33 | 21 | drn
| klo11 | 24997.4 | 1 | klo
COMMERCIAL | cyn13 | 11562540.4133 | 213 | cyn
| tgn44 | 15598.29 | 27 | tgn
| wn1 | 5093 | 9 | wn
NCONUML | wots24 | 22958.48 | 11 | wots
RESIDENTL | ftr21 | 5974099.1685 | 1654 | ftr
NCONUML | wgl11 | 116770.29 | 32 | wgl
FARM | phm22 | 2513172.8482 | 159 | phm
| mfa22 | 25912.0235 | 15 | mfa
| tt2 | 5693.01 | 1 | tt
RESIDENTL | cyn12 | 11384819.6049 | 2642 | cyn
COMMERCIAL | mby11 | 1920906.95 | 83 | mby
RESIDENTL | bdl42 | 7579399.6648 | 1528 | bdl
COMMERCIAL | sle11 | 16789466.3124 | 430 | sle
COMMERCIAL | bdl42 | 3935066.2305 | 228 | bdl
NCONUML | rwn22 | 25304.89 | 19 | rwn
INDUSTRIAL | cre32 | 1414910.91 | 33 | cre
INDUSTRIAL | bwn11 | 121807.37 | 8 | bwn
NCONUML | smr22 | 29006.3 | 13 | smr
RESIDENTL | phm24 | 12991887.5254 | 2975 | phm
RESIDENTL | phm21 | 5600884.0097 | 1319 | phm
NCONUML | ldl23 | 93357.12 | 44 | ldl
RESIDENTL | ldl24 | 19255310.9766 | 3964 | ldl
INDUSTRIAL | bra21 | 9682528.358 | 10 | bra
| sle31 | 21276.5675 | 34 | sle
| myt11 | 11671.01 | 10 | myt
RESIDENTL | elm21 | 10927220.6891 | 2208 | elm
COMMERCIAL | epg13 | 13081700.0195 | 121 | epg
COMMERCIAL | hpk21 | 6771211.022 | 80 | hpk
NCONUML | bwr12 | 55323.1848 | 22 | bwr
| trc01 | 7370.1419 | 1 | trc
| epg35 | 12733.43 | 3 | epg
INDUSTRIAL | bge21 | 30163.23 | 3 | bge
RESIDENTL | tgn31 | 10330935.5842 | 1504 | tgn
COMMERCIAL | moe23 | 8180066.6029 | 204 | moe
FARM | bra21 | 5211.11 | 2 | bra
LIGHTING | llg12 | 9573.66 | 1 | llg
RESIDENTL | bdl31 | 18828777.9984 | 3534 | bdl
COMMERCIAL | nla31 | 1365542.8767 | 73 | nla
INDUSTRIAL | klo24 | 421040.3606 | 14 | klo
FARM | bdl43 | 35833.9 | 4 | bdl
FARM | cyn31 | 3324.08 | 1 | cyn
FARM | sle14 | 508528.62 | 59 | sle
FARM | fgy34 | 3609.3 | 1 | fgy
RESIDENTL | elm26 | 19204314.084 | 3128 | elm
COMMERCIAL | ldl13 | 4974121.0157 | 271 | ldl
NCONUML | tgn42 | 32526.3 | 9 | tgn
RESIDENTL | nrn13 | 11128338.9236 | 2708 | nrn
| drn13 | 33230.29 | 35 | drn
RESIDENTL | mfa14 | 15628.16 | 8 | mfa
RESIDENTL | rwt14 | 5266292.5405 | 1232 | rwt
FARM | ftr23 | 7584335.745 | 587 | ftr
FARM | moe12 | 2890738.1544 | 266 | moe
RESIDENTL | klk21 | 6022162.144 | 692 | klk
COMMERCIAL | bn22 | 11917129.8815 | 407 | bn
COMMERCIAL | cln13 | 10498926.3291 | 102 | cln
INDUSTRIAL | cln11 | 955300.36 | 11 | cln
FARM | bge11 | 1450445.3683 | 132 | bge
| mwl25 | 368.2898 | 2 | mwl
| rwn33 | 13688.96 | 19 | rwn
| bdl43 | 33766.9817 | 15 | bdl
NCONUML | cln14 | 95979.5703 | 31 | cln
NCONUML | lga24 | 7306.35 | 4 | lga
| bn23 | 36133.4118 | 23 | bn
| ofr14 | 18460.3638 | 32 | ofr
FARM | wo14 | 29381.84 | 3 | wo
FARM | cln24 | 15169.45 | 1 | cln
FARM | smg21 | 2813.13 | 1 | smg
FARM | uwy1 | 50419.26 | 6 | uwy
RESIDENTL | cpk11 | 18255270.9798 | 3705 | cpk
INDUSTRIAL | rwn34 | 151721.8975 | 12 | rwn
FARM | mfa34 | 8352796.4311 | 398 | mfa
INDUSTRIAL | cyn23 | 283668.3977 | 39 | cyn
COMMERCIAL | cln23 | 7919442.4187 | 94 | cln
| rwn24 | 145239.1574 | 36 | rwn
INDUSTRIAL | cln21 | 91173.7471 | 8 | cln
INDUSTRIAL | wots23 | 9771996.01 | 2 | wots
COMMERCIAL | ofr23 | 7962081.4442 | 137 | ofr
FARM | cln11 | 5358747.3528 | 175 | cln
INDUSTRIAL | epg23 | 1603069.098 | 49 | epg
NCONUML | elm33 | 106570.09 | 33 | elm
| tt6 | 16214.4725 | 50 | tt
NCONUML | lga12 | 120.31 | 1 | lga
RESIDENTL | moe25 | 15202048.016 | 3044 | moe
RESIDENTL | moe22 | 6183768.6959 | 1343 | moe
RESIDENTL | mfa23 | 1535883.9368 | 206 | mfa
FARM | rwn22 | 76017.25 | 13 | rwn
COMMERCIAL | fgy31 | 26687.08 | 5 | fgy
RESIDENTL | elm33 | 17751529.9107 | 3238 | elm
COMMERCIAL | ldl22 | 7642772.3181 | 272 | ldl
NCONUML | llg11 | 13058.17 | 7 | llg
| ruba24 | 72607.09 | 10 | ruba
FARM | rwt32 | 21924.18 | 3 | rwt
FARM | ruba12 | 5735958.293 | 534 | ruba
FARM | brt21 | 526055.8565 | 65 | brt
| rwt15 | 24735.76 | 50 | rwt
NCONUML | bge13 | 40077 | 45 | bge
COMMERCIAL | klk21 | 1344972.0506 | 75 | klk
INDUSTRIAL | msd4 | 532825.24 | 27 | msd
| mwl21 | 2371.576 | 7 | mwl
RESIDENTL | wt9 | 13126762.7947 | 2901 | wt
FARM | wgi23 | 957555.9102 | 143 | wgi
| wgl24 | 12928.4076 | 27 | wgl
NCONUML | tgn11 | 50804.93 | 14 | tgn
LIGHTING | hpk22 | 402155.12 | 2 | hpk
INDUSTRIAL | wt13 | 198794.34 | 24 | wt
LIGHTING | wots24 | 69082.45 | 1 | wots
| ofr13 | 25120.5182 | 29 | ofr
| cre21 | 98632.2224 | 69 | cre
| smg22 | 13378.71 | 23 | smg
COMMERCIAL | tt4 | 4770691.1401 | 169 | tt
COMMERCIAL | elm26 | 2765254.86 | 47 | elm
NCONUML | bwa22 | 120.31 | 1 | bwa
| cyn23 | 386495.78 | 52 | cyn
INDUSTRIAL | nla34 | 227255.6563 | 13 | nla
FARM | mwl22 | 63.01 | 1 | mwl
| cf1 | 5771.13 | 3 | cf
NCONUML | cpk22 | 15413.02 | 10 | cpk
NCONUML | lyd13 | 28195.47 | 10 | lyd
NCONUML | cre31 | 35482.06 | 18 | cre
COMMERCIAL | wo11 | 6006584.4175 | 54 | wo
INDUSTRIAL | wt7 | 2382042.5333 | 25 | wt
| bwr34 | 19530.96 | 64 | bwr
NCONUML | bge23 | 57838.96 | 34 | bge
INDUSTRIAL | tgn23 | 187420.5 | 24 | tgn
RESIDENTL | cyn33 | 17836008.3498 | 3662 | cyn
RESIDENTL | nla34 | 7124747.0562 | 1408 | nla
| wgl11 | 21820.8596 | 38 | wgl
COMMERCIAL | bn12 | 3658135.6563 | 31 | bn
| mwl13 | 7054.2121 | 17 | mwl
COMMERCIAL | rwt26 | 65754589.65 | 1 | rwt
FARM | wt9 | 2789.4 | 1 | wt
RESIDENTL | bdl44 | 10906570.4152 | 1766 | bdl
FARM | cre33 | 2156267.3416 | 81 | cre
COMMERCIAL | wgl21 | 7364849.9167 | 150 | wgl
COMMERCIAL | wn5 | 3727109.367 | 208 | wn
NCONUML | mwl22 | 81020 | 27 | mwl
NCONUML | bn24 | 14677.57 | 9 | bn
| smr22 | 9887.67 | 15 | smr
|  | 8782.36 | 2 | #REF!
RESIDENTL | sle11 | 5311421.2716 | 1344 | sle
RESIDENTL | nw13 | 126364.0108 | 18 | nw
RESIDENTL | ftr23 | 12909653.9148 | 2620 | ftr
COMMERCIAL | mwl11 | 1278518.3133 | 72 | mwl
LIGHTING | llg13 | 66328.6913 | 1 | llg
NCONUML | klk22 | 2600.11 | 1 | klk
RESIDENTL | wyk23 | 22445865.182 | 3391 | wyk
COMMERCIAL | wt6 | 6354339.6482 | 191 | wt
RESIDENTL | brt11 | 6592458.6386 | 1001 | brt
NCONUML | tt9 | 66916.75 | 41 | tt
FARM | smr14 | 4406259.38 | 487 | smr
NCONUML | epg32 | 55568.91 | 13 | epg
RESIDENTL | rwn31 | 17135173.2235 | 2210 | rwn
| phm33 | 20993.1171 | 27 | phm
NCONUML | myt11 | 6079.5 | 6 | myt
RESIDENTL | nrn12 | 2807836.1314 | 591 | nrn
COMMERCIAL | mwl16 | 411566.3345 | 42 | mwl
INDUSTRIAL | lga23 | 1068068.6578 | 23 | lga
COMMERCIAL | ldl12 | 15390056.6509 | 380 | ldl
FARM | nla34 | 624678.3932 | 78 | nla
COMMERCIAL | rve13 | 1685040.429 | 44 | rve
NCONUML | drn24 | 11009.3526 | 4 | drn
COMMERCIAL | myt21 | 6919383.7104 | 251 | myt
FARM | moe13 | 3478506.4958 | 306 | moe
COMMERCIAL | mwl21 | 9182796.6603 | 240 | mwl
NCONUML | wgl15 | 97647.0301 | 36 | wgl
| bwn14 | 31300.22 | 31 | bwn
RESIDENTL | cpk22 | 8203984.593 | 1482 | cpk
RESIDENTL | rve12 | 17634581.2748 | 3656 | rve
RESIDENTL | phi13 | 17016004.0328 | 4317 | phi
RESIDENTL | hpk12 | 5058413.1519 | 1238 | hpk
COMMERCIAL | ruba24 | 4555190.3466 | 105 | ruba
FARM | cln14 | 51639.06 | 13 | cln
INDUSTRIAL | wt9 | 148098.11 | 5 | wt
| smg21 | 44014.37 | 27 | smg
INDUSTRIAL | smr23 | 883845.12 | 6 | smr

## Forecast - Summer
Forecasting Application - 13/10/2025
asset_type | asset | extremum | scenario | demand_year | season | poe | customer_count | pv_capacity | value | forecast_round | unit | region
zone_sub | cln | maximum |  | 2022 | Summer | 50 | 38619 | 72.2578 | 77.9086 | 202503 | MVA | central
zone_sub | cln | maximum |  | 2022 | Summer | 10 | 38619 | 72.2578 | 91.3183 | 202503 | MVA | central
zone_sub | cln | maximum |  | 2023 | Summer | 10 | 41429 | 81.3604 | 97.5884 | 202503 | MVA | central
zone_sub | cln | maximum |  | 2023 | Summer | 50 | 41429 | 81.3604 | 83.3369 | 202503 | MVA | central
zone_sub | cln | maximum |  | 2024 | Summer | 10 | 44846 | 94.6588 | 104.9463 | 202503 | MVA | central
zone_sub | cln | maximum |  | 2024 | Summer | 50 | 44846 | 94.6588 | 89.7351 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2025 | Summer | 10 |  |  | 119.6766 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2025 | Summer | 50 |  |  | 104.3341 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2026 | Summer | 10 |  |  | 124.2514 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2026 | Summer | 50 |  |  | 108.3435 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2027 | Summer | 10 |  |  | 128.0364 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2027 | Summer | 50 |  |  | 111.4611 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2028 | Summer | 10 |  |  | 131.3686 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2028 | Summer | 50 |  |  | 115.2173 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2029 | Summer | 10 |  |  | 136.7682 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2029 | Summer | 50 |  |  | 119.0984 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2030 | Summer | 10 |  |  | 141.634 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2030 | Summer | 50 |  |  | 123.2461 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2031 | Summer | 10 |  |  | 148.4809 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2031 | Summer | 50 |  |  | 128.0275 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2032 | Summer | 10 |  |  | 155.6302 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2032 | Summer | 50 |  |  | 133.6994 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2033 | Summer | 10 |  |  | 161.4365 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2033 | Summer | 50 |  |  | 139.0092 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2034 | Summer | 10 |  |  | 166.8996 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2034 | Summer | 50 |  |  | 144.6013 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2035 | Summer | 10 |  |  | 175.1342 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2035 | Summer | 50 |  |  | 154.2938 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2036 | Summer | 10 |  |  | 181.0486 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2036 | Summer | 50 |  |  | 157.43 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2037 | Summer | 10 |  |  | 187.0195 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2037 | Summer | 50 |  |  | 163.5566 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2038 | Summer | 10 |  |  | 193.3671 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2038 | Summer | 50 |  |  | 168.1999 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2039 | Summer | 10 |  |  | 192.0421 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2039 | Summer | 50 |  |  | 167.0472 | 202503 | MVA | central
zone_sub | cre | maximum |  | 2022 | Summer | 10 | 24937 | 39.5122 | 71.3044 | 202503 | MVA | central
zone_sub | cre | maximum |  | 2022 | Summer | 50 | 24937 | 39.5122 | 64.1683 | 202503 | MVA | central
zone_sub | cre | maximum |  | 2023 | Summer | 10 | 25835 | 43.8704 | 73.6781 | 202503 | MVA | central
zone_sub | cre | maximum |  | 2023 | Summer | 50 | 25835 | 43.8704 | 65.8328 | 202503 | MVA | central
zone_sub | cre | maximum |  | 2024 | Summer | 10 | 26314 | 48.9572 | 74.7994 | 202503 | MVA | central
zone_sub | cre | maximum |  | 2024 | Summer | 50 | 26314 | 48.9572 | 66.0879 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2025 | Summer | 10 |  |  | 89.8342 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2025 | Summer | 50 |  |  | 80.6612 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2026 | Summer | 10 |  |  | 90.653 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2026 | Summer | 50 |  |  | 81.4056 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2027 | Summer | 10 |  |  | 89.7773 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2027 | Summer | 50 |  |  | 80.6131 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2028 | Summer | 10 |  |  | 94.9573 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2028 | Summer | 50 |  |  | 85.9509 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2029 | Summer | 10 |  |  | 94.8385 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2029 | Summer | 50 |  |  | 85.6114 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2030 | Summer | 10 |  |  | 96.1186 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2030 | Summer | 50 |  |  | 85.7941 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2031 | Summer | 10 |  |  | 97.2062 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2031 | Summer | 50 |  |  | 86.4866 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2032 | Summer | 10 |  |  | 98.0786 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2032 | Summer | 50 |  |  | 87.2925 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2033 | Summer | 10 |  |  | 98.8781 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2033 | Summer | 50 |  |  | 88.2343 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2034 | Summer | 10 |  |  | 99.6475 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2034 | Summer | 50 |  |  | 88.9575 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2035 | Summer | 10 |  |  | 99.2707 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2035 | Summer | 50 |  |  | 89.8044 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2036 | Summer | 10 |  |  | 99.9981 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2036 | Summer | 50 |  |  | 89.5675 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2037 | Summer | 10 |  |  | 101.1509 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2037 | Summer | 50 |  |  | 90.5821 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2038 | Summer | 10 |  |  | 101.3208 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2038 | Summer | 50 |  |  | 90.3196 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2039 | Summer | 10 |  |  | 99.6095 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2039 | Summer | 50 |  |  | 88.5146 | 202503 | MVA | central
zone_sub | epg | maximum |  | 2022 | Summer | 10 | 29371 | 40.0067 | 87.2498 | 202503 | MVA | central
zone_sub | epg | maximum |  | 2022 | Summer | 50 | 29371 | 40.0067 | 72.9666 | 202503 | MVA | central
zone_sub | epg | maximum |  | 2023 | Summer | 10 | 30422 | 45.1511 | 90.3071 | 202503 | MVA | central
zone_sub | epg | maximum |  | 2023 | Summer | 50 | 30422 | 45.1511 | 75.7012 | 202503 | MVA | central
zone_sub | epg | maximum |  | 2024 | Summer | 10 | 32118 | 51.557 | 95.8895 | 202503 | MVA | central
zone_sub | epg | maximum |  | 2024 | Summer | 50 | 32118 | 51.557 | 79.9844 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2025 | Summer | 10 |  |  | 109.0669 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2025 | Summer | 50 |  |  | 92.5622 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2026 | Summer | 10 |  |  | 118.5447 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2026 | Summer | 50 |  |  | 101.6723 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2027 | Summer | 10 |  |  | 121.4869 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2027 | Summer | 50 |  |  | 104.4042 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2028 | Summer | 10 |  |  | 119.8786 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2028 | Summer | 50 |  |  | 102.6031 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2029 | Summer | 10 |  |  | 121.9204 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2029 | Summer | 50 |  |  | 105.5757 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2030 | Summer | 10 |  |  | 124.6444 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2030 | Summer | 50 |  |  | 106.371 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2031 | Summer | 10 |  |  | 127.5507 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2031 | Summer | 50 |  |  | 110.1341 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2032 | Summer | 10 |  |  | 131.8742 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2032 | Summer | 50 |  |  | 112.2581 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2033 | Summer | 10 |  |  | 136.3355 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2033 | Summer | 50 |  |  | 113.9316 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2034 | Summer | 10 |  |  | 140.9437 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2034 | Summer | 50 |  |  | 117.5793 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2035 | Summer | 10 |  |  | 144.5914 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2035 | Summer | 50 |  |  | 120.4726 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2036 | Summer | 50 |  |  | 128.0797 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2036 | Summer | 10 |  |  | 149.6115 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2037 | Summer | 10 |  |  | 152.9797 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2037 | Summer | 50 |  |  | 129.922 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2038 | Summer | 10 |  |  | 155.1715 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2038 | Summer | 50 |  |  | 132.5568 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2039 | Summer | 10 |  |  | 152.1644 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2039 | Summer | 50 |  |  | 125.7761 | 202503 | MVA | central
zone_sub | klo | maximum |  | 2022 | Summer | 10 | 14879 | 23.0226 | 53.5677 | 202503 | MVA | central
zone_sub | klo | maximum |  | 2022 | Summer | 50 | 14879 | 23.0226 | 41.9423 | 202503 | MVA | central
zone_sub | klo | maximum |  | 2023 | Summer | 10 | 17175 | 27.7177 | 61.121 | 202503 | MVA | central
zone_sub | klo | maximum |  | 2023 | Summer | 50 | 17175 | 27.7177 | 48.3019 | 202503 | MVA | central
zone_sub | klo | maximum |  | 2024 | Summer | 10 | 19951 | 34.2052 | 70.1897 | 202503 | MVA | central
zone_sub | klo | maximum |  | 2024 | Summer | 50 | 19951 | 34.2052 | 55.7613 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2025 | Summer | 10 |  |  | 83.6879 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2025 | Summer | 50 |  |  | 68.2523 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2026 | Summer | 10 |  |  | 94.1984 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2026 | Summer | 50 |  |  | 77.9353 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2027 | Summer | 10 |  |  | 102.4436 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2027 | Summer | 50 |  |  | 84.7194 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2028 | Summer | 10 |  |  | 118.3247 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2028 | Summer | 50 |  |  | 99.6669 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2029 | Summer | 10 |  |  | 126.3487 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2029 | Summer | 50 |  |  | 106.8624 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2030 | Summer | 10 |  |  | 135.5692 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2030 | Summer | 50 |  |  | 115.5707 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2031 | Summer | 10 |  |  | 148.561 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2031 | Summer | 50 |  |  | 127.0156 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2032 | Summer | 10 |  |  | 164.8827 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2032 | Summer | 50 |  |  | 137.8179 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2033 | Summer | 10 |  |  | 180.5841 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2033 | Summer | 50 |  |  | 151.2391 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2034 | Summer | 10 |  |  | 196.9964 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2034 | Summer | 50 |  |  | 164.8814 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2035 | Summer | 10 |  |  | 212.9758 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2035 | Summer | 50 |  |  | 181.5355 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2036 | Summer | 10 |  |  | 230.0573 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2036 | Summer | 50 |  |  | 195.8954 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2037 | Summer | 10 |  |  | 248.4456 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2037 | Summer | 50 |  |  | 212.2991 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2038 | Summer | 10 |  |  | 266.5409 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2038 | Summer | 50 |  |  | 225.6959 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2039 | Summer | 10 |  |  | 272.6357 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2039 | Summer | 50 |  |  | 228.9049 | 202503 | MVA | central
zone_sub | ofr | maximum |  | 2022 | Summer | 10 | 23246 | 35.5119 | 59.9776 | 202503 | MVA | central
zone_sub | ofr | maximum |  | 2022 | Summer | 50 | 23246 | 35.5119 | 53.856 | 202503 | MVA | central
zone_sub | ofr | maximum |  | 2023 | Summer | 10 | 24109 | 39.5748 | 62.0639 | 202503 | MVA | central
zone_sub | ofr | maximum |  | 2023 | Summer | 50 | 24109 | 39.5748 | 55.451 | 202503 | MVA | central
zone_sub | ofr | maximum |  | 2024 | Summer | 10 | 24997 | 44.4669 | 64.073 | 202503 | MVA | central
zone_sub | ofr | maximum |  | 2024 | Summer | 50 | 24997 | 44.4669 | 56.9594 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2025 | Summer | 10 |  |  | 69.589 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2025 | Summer | 50 |  |  | 61.9907 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2026 | Summer | 10 |  |  | 76.597 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2026 | Summer | 50 |  |  | 68.9791 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2027 | Summer | 10 |  |  | 81.5678 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2027 | Summer | 50 |  |  | 74.0072 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2028 | Summer | 10 |  |  | 84.5283 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2028 | Summer | 50 |  |  | 76.6284 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2029 | Summer | 10 |  |  | 86.8984 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2029 | Summer | 50 |  |  | 78.9811 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2030 | Summer | 10 |  |  | 88.8048 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2030 | Summer | 50 |  |  | 80.4506 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2031 | Summer | 10 |  |  | 90.6365 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2031 | Summer | 50 |  |  | 82.1352 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2032 | Summer | 10 |  |  | 92.2256 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2032 | Summer | 50 |  |  | 83.4813 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2033 | Summer | 10 |  |  | 92.9929 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2033 | Summer | 50 |  |  | 84.3346 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2034 | Summer | 10 |  |  | 94.1573 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2034 | Summer | 50 |  |  | 86.446 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2035 | Summer | 10 |  |  | 95.4952 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2035 | Summer | 50 |  |  | 87.894 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2036 | Summer | 10 |  |  | 96.8516 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2036 | Summer | 50 |  |  | 88.627 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2037 | Summer | 10 |  |  | 98.5806 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2037 | Summer | 50 |  |  | 90.0391 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2038 | Summer | 10 |  |  | 98.8168 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2038 | Summer | 50 |  |  | 89.5765 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2039 | Summer | 10 |  |  | 97.8239 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2039 | Summer | 50 |  |  | 88.3981 | 202503 | MVA | central
zone_sub | phm | maximum |  | 2022 | Summer | 50 | 16270 | 23.521 | 51.4174 | 202503 | MVA | central
zone_sub | phm | maximum |  | 2022 | Summer | 10 | 16270 | 23.521 | 56.9097 | 202503 | MVA | central
zone_sub | phm | maximum |  | 2023 | Summer | 10 | 16562 | 25.5412 | 57.758 | 202503 | MVA | central
zone_sub | phm | maximum |  | 2023 | Summer | 50 | 16562 | 25.5412 | 52.1386 | 202503 | MVA | central
zone_sub | phm | maximum |  | 2024 | Summer | 10 | 16854 | 27.7496 | 58.7282 | 202503 | MVA | central
zone_sub | phm | maximum |  | 2024 | Summer | 50 | 16854 | 27.7496 | 52.8621 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2025 | Summer | 10 |  |  | 75.5207 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2025 | Summer | 50 |  |  | 69.621 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2026 | Summer | 10 |  |  | 79.8845 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2026 | Summer | 50 |  |  | 74.1527 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2027 | Summer | 10 |  |  | 79.6008 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2027 | Summer | 50 |  |  | 73.9998 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2028 | Summer | 10 |  |  | 79.5894 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2028 | Summer | 50 |  |  | 73.965 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2029 | Summer | 10 |  |  | 80.0199 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2029 | Summer | 50 |  |  | 74.4648 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2030 | Summer | 10 |  |  | 81.1895 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2030 | Summer | 50 |  |  | 75.0153 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2031 | Summer | 10 |  |  | 81.9552 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2031 | Summer | 50 |  |  | 76.1566 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2032 | Summer | 10 |  |  | 82.7146 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2032 | Summer | 50 |  |  | 76.9783 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2033 | Summer | 10 |  |  | 83.6062 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2033 | Summer | 50 |  |  | 77.4148 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2034 | Summer | 10 |  |  | 84.4206 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2034 | Summer | 50 |  |  | 77.8841 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2035 | Summer | 10 |  |  | 85.2206 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2035 | Summer | 50 |  |  | 78.3211 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2036 | Summer | 10 |  |  | 85.2937 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2036 | Summer | 50 |  |  | 79.127 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2037 | Summer | 10 |  |  | 86.2309 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2037 | Summer | 50 |  |  | 80.1321 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2038 | Summer | 10 |  |  | 85.4841 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2038 | Summer | 50 |  |  | 80.0404 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2039 | Summer | 10 |  |  | 79.3417 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2039 | Summer | 50 |  |  | 73.3195 | 202503 | MVA | central
zone_sub | llg | maximum |  | 2022 | Summer | 10 | 7174 | 11.5134 | 25.3928 | 202503 | MVA | central
zone_sub | llg | maximum |  | 2022 | Summer | 50 | 7174 | 11.5134 | 23.4346 | 202503 | MVA | central
zone_sub | llg | maximum |  | 2023 | Summer | 10 | 7235 | 12.7349 | 25.4543 | 202503 | MVA | central
zone_sub | llg | maximum |  | 2023 | Summer | 50 | 7235 | 12.7349 | 23.4406 | 202503 | MVA | central
zone_sub | llg | maximum |  | 2024 | Summer | 10 | 7295 | 13.7538 | 25.544 | 202503 | MVA | central
zone_sub | llg | maximum |  | 2024 | Summer | 50 | 7295 | 13.7538 | 23.5081 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2025 | Summer | 10 |  |  | 28.7312 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2025 | Summer | 50 |  |  | 26.0976 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2026 | Summer | 10 |  |  | 33.0834 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2026 | Summer | 50 |  |  | 30.4575 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2027 | Summer | 10 |  |  | 33.0249 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2027 | Summer | 50 |  |  | 30.4247 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2028 | Summer | 10 |  |  | 33.0633 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2028 | Summer | 50 |  |  | 30.3952 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2029 | Summer | 10 |  |  | 33.1822 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2029 | Summer | 50 |  |  | 30.8677 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2030 | Summer | 10 |  |  | 33.5865 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2030 | Summer | 50 |  |  | 31.5616 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2031 | Summer | 10 |  |  | 33.8573 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2031 | Summer | 50 |  |  | 32.037 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2032 | Summer | 10 |  |  | 34.0794 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2032 | Summer | 50 |  |  | 31.4591 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2033 | Summer | 10 |  |  | 34.1121 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2033 | Summer | 50 |  |  | 31.5166 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2034 | Summer | 10 |  |  | 34.3124 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2034 | Summer | 50 |  |  | 31.792 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2035 | Summer | 10 |  |  | 34.3834 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2035 | Summer | 50 |  |  | 32.8827 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2036 | Summer | 10 |  |  | 34.3832 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2036 | Summer | 50 |  |  | 31.8492 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2037 | Summer | 10 |  |  | 34.3374 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2037 | Summer | 50 |  |  | 31.7885 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2038 | Summer | 10 |  |  | 34.3276 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2038 | Summer | 50 |  |  | 31.7234 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2039 | Summer | 10 |  |  | 32.6827 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2039 | Summer | 50 |  |  | 30.3101 | 202503 | MVA | central
zone_sub | wgi | maximum |  | 2022 | Summer | 10 | 21696 | 27.3902 | 50.299 | 202503 | MVA | east
zone_sub | wgi | maximum |  | 2022 | Summer | 50 | 21696 | 27.3902 | 41.2414 | 202503 | MVA | east
zone_sub | wgi | maximum |  | 2023 | Summer | 10 | 22045 | 30.4273 | 50.6919 | 202503 | MVA | east
zone_sub | wgi | maximum |  | 2023 | Summer | 50 | 22045 | 30.4273 | 41.4384 | 202503 | MVA | east
zone_sub | wgi | maximum |  | 2024 | Summer | 10 | 22388 | 33.5461 | 51.0465 | 202503 | MVA | east
zone_sub | wgi | maximum |  | 2024 | Summer | 50 | 22388 | 33.5461 | 41.5121 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2025 | Summer | 10 |  |  | 54.5057 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2025 | Summer | 50 |  |  | 44.6075 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2026 | Summer | 10 |  |  | 54.6012 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2026 | Summer | 50 |  |  | 44.9185 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2027 | Summer | 10 |  |  | 54.4983 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2027 | Summer | 50 |  |  | 44.7661 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2028 | Summer | 10 |  |  | 54.5247 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2028 | Summer | 50 |  |  | 44.911 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2029 | Summer | 10 |  |  | 54.7136 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2029 | Summer | 50 |  |  | 44.9706 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2030 | Summer | 10 |  |  | 55.0965 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2030 | Summer | 50 |  |  | 45.1615 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2031 | Summer | 10 |  |  | 55.7707 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2031 | Summer | 50 |  |  | 45.5541 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2032 | Summer | 50 |  |  | 45.8843 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2032 | Summer | 10 |  |  | 56.122 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2033 | Summer | 10 |  |  | 56.3761 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2033 | Summer | 50 |  |  | 46.0363 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2034 | Summer | 10 |  |  | 56.7608 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2034 | Summer | 50 |  |  | 45.9008 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2035 | Summer | 10 |  |  | 57.2519 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2035 | Summer | 50 |  |  | 46.4689 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2036 | Summer | 10 |  |  | 57.8457 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2036 | Summer | 50 |  |  | 46.559 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2037 | Summer | 10 |  |  | 58.1569 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2037 | Summer | 50 |  |  | 46.4523 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2038 | Summer | 10 |  |  | 58.056 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2038 | Summer | 50 |  |  | 46.6661 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2039 | Summer | 10 |  |  | 56.811 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2039 | Summer | 50 |  |  | 45.5652 | 202503 | MVA | east

## Forecast- Winter
Forecasting Application - 13/10/2025
asset_type | asset | extremum | scenario | demand_year | season | poe | customer_count | pv_capacity | value | forecast_round | unit | region
zone_sub | cln | maximum |  | 2022 | Winter | 10 | 38619 | 72.2578 | 63.0362 | 202503 | MVA | central
zone_sub | cln | maximum |  | 2022 | Winter | 50 | 38619 | 72.2578 | 58.8161 | 202503 | MVA | central
zone_sub | cln | maximum |  | 2023 | Winter | 10 | 41429 | 81.3604 | 67.9918 | 202503 | MVA | central
zone_sub | cln | maximum |  | 2023 | Winter | 50 | 41429 | 81.3604 | 63.4647 | 202503 | MVA | central
zone_sub | cln | maximum |  | 2024 | Winter | 10 | 44846 | 94.6588 | 74.018 | 202503 | MVA | central
zone_sub | cln | maximum |  | 2024 | Winter | 50 | 44846 | 94.6588 | 69.1182 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2025 | Winter | 10 |  |  | 89.4372 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2025 | Winter | 50 |  |  | 84.5179 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2026 | Winter | 10 |  |  | 93.2911 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2026 | Winter | 50 |  |  | 88.1502 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2027 | Winter | 10 |  |  | 98.0701 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2027 | Winter | 50 |  |  | 92.8679 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2028 | Winter | 10 |  |  | 102.5171 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2028 | Winter | 50 |  |  | 97.437 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2029 | Winter | 10 |  |  | 107.2692 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2029 | Winter | 50 |  |  | 101.4753 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2030 | Winter | 10 |  |  | 112.2902 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2030 | Winter | 50 |  |  | 107.1286 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2031 | Winter | 10 |  |  | 119.5588 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2031 | Winter | 50 |  |  | 113.3315 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2032 | Winter | 10 |  |  | 125.8642 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2032 | Winter | 50 |  |  | 119.6901 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2033 | Winter | 10 |  |  | 131.807 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2033 | Winter | 50 |  |  | 125.9989 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2034 | Winter | 10 |  |  | 137.993 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2034 | Winter | 50 |  |  | 131.579 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2035 | Winter | 10 |  |  | 145.465 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2035 | Winter | 50 |  |  | 137.6925 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2036 | Winter | 10 |  |  | 147.8036 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2036 | Winter | 50 |  |  | 139.8743 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2037 | Winter | 10 |  |  | 155.8793 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2037 | Winter | 50 |  |  | 147.8441 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2038 | Winter | 10 |  |  | 163.4009 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2038 | Winter | 50 |  |  | 156.1056 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2039 | Winter | 10 |  |  | 133.5693 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2039 | Winter | 50 |  |  | 127.2077 | 202503 | MVA | central
zone_sub | cre | maximum |  | 2022 | Winter | 10 | 24937 | 39.5122 | 50.635 | 202503 | MVA | central
zone_sub | cre | maximum |  | 2022 | Winter | 50 | 24937 | 39.5122 | 48.3881 | 202503 | MVA | central
zone_sub | cre | maximum |  | 2023 | Winter | 10 | 25835 | 43.8704 | 52.4586 | 202503 | MVA | central
zone_sub | cre | maximum |  | 2023 | Winter | 50 | 25835 | 43.8704 | 50.1308 | 202503 | MVA | central
zone_sub | cre | maximum |  | 2024 | Winter | 10 | 26314 | 48.9572 | 53.4328 | 202503 | MVA | central
zone_sub | cre | maximum |  | 2024 | Winter | 50 | 26314 | 48.9572 | 51.0617 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2025 | Winter | 10 |  |  | 68.4471 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2025 | Winter | 50 |  |  | 65.7336 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2026 | Winter | 10 |  |  | 69.4459 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2026 | Winter | 50 |  |  | 66.605 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2027 | Winter | 10 |  |  | 69.249 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2027 | Winter | 50 |  |  | 66.728 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2028 | Winter | 10 |  |  | 74.3386 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2028 | Winter | 50 |  |  | 72.0847 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2029 | Winter | 10 |  |  | 74.5773 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2029 | Winter | 50 |  |  | 72.2361 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2030 | Winter | 10 |  |  | 76.3193 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2030 | Winter | 50 |  |  | 74.0669 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2031 | Winter | 10 |  |  | 77.7248 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2031 | Winter | 50 |  |  | 75.6012 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2032 | Winter | 10 |  |  | 79.2116 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2032 | Winter | 50 |  |  | 76.7507 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2033 | Winter | 10 |  |  | 79.7367 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2033 | Winter | 50 |  |  | 77.8762 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2034 | Winter | 10 |  |  | 80.3545 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2034 | Winter | 50 |  |  | 78.6625 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2035 | Winter | 10 |  |  | 81.081 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2035 | Winter | 50 |  |  | 79.0014 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2036 | Winter | 10 |  |  | 80.0375 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2036 | Winter | 50 |  |  | 78.1499 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2037 | Winter | 10 |  |  | 83.4116 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2037 | Winter | 50 |  |  | 80.9567 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2038 | Winter | 10 |  |  | 84.3767 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2038 | Winter | 50 |  |  | 81.4995 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2039 | Winter | 10 |  |  | 72.4681 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2039 | Winter | 50 |  |  | 69.0004 | 202503 | MVA | central
zone_sub | epg | maximum |  | 2022 | Winter | 10 | 29371 | 40.0067 | 65.9271 | 202503 | MVA | central
zone_sub | epg | maximum |  | 2022 | Winter | 50 | 29371 | 40.0067 | 59.4269 | 202503 | MVA | central
zone_sub | epg | maximum |  | 2023 | Winter | 10 | 30422 | 45.1511 | 68.3101 | 202503 | MVA | central
zone_sub | epg | maximum |  | 2023 | Winter | 50 | 30422 | 45.1511 | 61.7598 | 202503 | MVA | central
zone_sub | epg | maximum |  | 2024 | Winter | 50 | 32118 | 51.557 | 65.5719 | 202503 | MVA | central
zone_sub | epg | maximum |  | 2024 | Winter | 10 | 32118 | 51.557 | 72.1952 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2025 | Winter | 10 |  |  | 85.9871 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2025 | Winter | 50 |  |  | 79.3939 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2026 | Winter | 10 |  |  | 95.0802 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2026 | Winter | 50 |  |  | 89.3565 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2027 | Winter | 10 |  |  | 100.5082 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2027 | Winter | 50 |  |  | 92.7492 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2028 | Winter | 10 |  |  | 99.8778 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2028 | Winter | 50 |  |  | 93.3308 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2029 | Winter | 10 |  |  | 103.1049 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2029 | Winter | 50 |  |  | 96.5577 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2030 | Winter | 10 |  |  | 109.1359 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2030 | Winter | 50 |  |  | 102.3455 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2031 | Winter | 10 |  |  | 112.51 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2031 | Winter | 50 |  |  | 104.2867 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2032 | Winter | 10 |  |  | 121.7799 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2032 | Winter | 50 |  |  | 114.0182 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2033 | Winter | 10 |  |  | 127.6696 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2033 | Winter | 50 |  |  | 119.7255 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2034 | Winter | 10 |  |  | 133.3287 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2034 | Winter | 50 |  |  | 125.5482 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2035 | Winter | 10 |  |  | 135.1129 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2035 | Winter | 50 |  |  | 126.6853 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2036 | Winter | 10 |  |  | 142.2751 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2036 | Winter | 50 |  |  | 134.3407 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2037 | Winter | 10 |  |  | 149.629 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2037 | Winter | 50 |  |  | 142.1357 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2038 | Winter | 10 |  |  | 150.109 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2038 | Winter | 50 |  |  | 141.9626 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2039 | Winter | 10 |  |  | 116.0207 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2039 | Winter | 50 |  |  | 101.3122 | 202503 | MVA | central
zone_sub | klo | maximum |  | 2022 | Winter | 10 | 14879 | 23.0226 | 48.7862 | 202503 | MVA | central
zone_sub | klo | maximum |  | 2022 | Winter | 50 | 14879 | 23.0226 | 43.3886 | 202503 | MVA | central
zone_sub | klo | maximum |  | 2023 | Winter | 10 | 17175 | 27.7177 | 56.3067 | 202503 | MVA | central
zone_sub | klo | maximum |  | 2023 | Winter | 50 | 17175 | 27.7177 | 50.077 | 202503 | MVA | central
zone_sub | klo | maximum |  | 2024 | Winter | 10 | 19951 | 34.2052 | 65.4015 | 202503 | MVA | central
zone_sub | klo | maximum |  | 2024 | Winter | 50 | 19951 | 34.2052 | 58.1655 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2025 | Winter | 10 |  |  | 79.8942 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2025 | Winter | 50 |  |  | 72.3119 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2026 | Winter | 10 |  |  | 92.3723 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2026 | Winter | 50 |  |  | 83.7626 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2027 | Winter | 10 |  |  | 102.9502 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2027 | Winter | 50 |  |  | 93.3778 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2028 | Winter | 10 |  |  | 120.3965 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2028 | Winter | 50 |  |  | 109.8362 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2029 | Winter | 10 |  |  | 129.7211 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2029 | Winter | 50 |  |  | 118.6301 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2030 | Winter | 10 |  |  | 142.5707 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2030 | Winter | 50 |  |  | 129.8167 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2031 | Winter | 10 |  |  | 159.4027 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2031 | Winter | 50 |  |  | 143.8497 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2032 | Winter | 10 |  |  | 178.8568 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2032 | Winter | 50 |  |  | 161.743 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2033 | Winter | 10 |  |  | 196.8658 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2033 | Winter | 50 |  |  | 178.8635 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2034 | Winter | 10 |  |  | 214.3536 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2034 | Winter | 50 |  |  | 194.8729 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2035 | Winter | 10 |  |  | 235.0946 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2035 | Winter | 50 |  |  | 213.0243 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2036 | Winter | 10 |  |  | 246.5584 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2036 | Winter | 50 |  |  | 225.0657 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2037 | Winter | 10 |  |  | 273.2503 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2037 | Winter | 50 |  |  | 249.8153 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2038 | Winter | 10 |  |  | 298.8878 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2038 | Winter | 50 |  |  | 271.7276 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2039 | Winter | 10 |  |  | 252.4111 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2039 | Winter | 50 |  |  | 227.0702 | 202503 | MVA | central
zone_sub | llg | maximum |  | 2022 | Winter | 10 | 7174 | 11.5134 | 22.426 | 202503 | MVA | central
zone_sub | llg | maximum |  | 2022 | Winter | 50 | 7174 | 11.5134 | 20.2322 | 202503 | MVA | central
zone_sub | llg | maximum |  | 2023 | Winter | 10 | 7235 | 12.7349 | 22.5982 | 202503 | MVA | central
zone_sub | llg | maximum |  | 2023 | Winter | 50 | 7235 | 12.7349 | 20.4035 | 202503 | MVA | central
zone_sub | llg | maximum |  | 2024 | Winter | 10 | 7295 | 13.7538 | 22.7705 | 202503 | MVA | central
zone_sub | llg | maximum |  | 2024 | Winter | 50 | 7295 | 13.7538 | 20.5738 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2025 | Winter | 10 |  |  | 26.1225 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2025 | Winter | 50 |  |  | 23.9159 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2026 | Winter | 10 |  |  | 30.6829 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2026 | Winter | 50 |  |  | 28.4398 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2027 | Winter | 10 |  |  | 31.049 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2027 | Winter | 50 |  |  | 28.8402 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2028 | Winter | 10 |  |  | 31.3064 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2028 | Winter | 50 |  |  | 29.108 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2029 | Winter | 10 |  |  | 31.5714 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2029 | Winter | 50 |  |  | 29.4846 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2030 | Winter | 10 |  |  | 32.5932 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2030 | Winter | 50 |  |  | 30.3426 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2031 | Winter | 10 |  |  | 33.1905 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2031 | Winter | 50 |  |  | 31.0163 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2032 | Winter | 10 |  |  | 33.8014 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2032 | Winter | 50 |  |  | 31.6154 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2033 | Winter | 10 |  |  | 34.0793 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2033 | Winter | 50 |  |  | 31.8255 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2034 | Winter | 10 |  |  | 34.2253 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2034 | Winter | 50 |  |  | 32.0656 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2035 | Winter | 10 |  |  | 33.7185 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2035 | Winter | 50 |  |  | 31.7299 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2036 | Winter | 10 |  |  | 33.9832 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2036 | Winter | 50 |  |  | 31.9069 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2037 | Winter | 10 |  |  | 34.9987 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2037 | Winter | 50 |  |  | 32.7389 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2038 | Winter | 10 |  |  | 34.5209 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2038 | Winter | 50 |  |  | 32.3709 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2039 | Winter | 10 |  |  | 28.3277 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2039 | Winter | 50 |  |  | 26.2847 | 202503 | MVA | central
zone_sub | ofr | maximum |  | 2022 | Winter | 10 | 23246 | 35.5119 | 49.8939 | 202503 | MVA | central
zone_sub | ofr | maximum |  | 2022 | Winter | 50 | 23246 | 35.5119 | 46.8764 | 202503 | MVA | central
zone_sub | ofr | maximum |  | 2023 | Winter | 10 | 24109 | 39.5748 | 51.7437 | 202503 | MVA | central
zone_sub | ofr | maximum |  | 2023 | Winter | 50 | 24109 | 39.5748 | 48.6149 | 202503 | MVA | central
zone_sub | ofr | maximum |  | 2024 | Winter | 10 | 24997 | 44.4669 | 53.6497 | 202503 | MVA | central
zone_sub | ofr | maximum |  | 2024 | Winter | 50 | 24997 | 44.4669 | 50.4065 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2025 | Winter | 10 |  |  | 59.4536 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2025 | Winter | 50 |  |  | 56.1183 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2026 | Winter | 10 |  |  | 66.5595 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2026 | Winter | 50 |  |  | 63.2802 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2027 | Winter | 10 |  |  | 72.8129 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2027 | Winter | 50 |  |  | 69.3039 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2028 | Winter | 10 |  |  | 76.0509 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2028 | Winter | 50 |  |  | 72.5305 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2029 | Winter | 10 |  |  | 78.6773 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2029 | Winter | 50 |  |  | 74.8582 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2030 | Winter | 10 |  |  | 81.1629 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2030 | Winter | 50 |  |  | 77.5373 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2031 | Winter | 10 |  |  | 83.2732 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2031 | Winter | 50 |  |  | 79.5294 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2032 | Winter | 10 |  |  | 85.4834 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2032 | Winter | 50 |  |  | 81.7407 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2033 | Winter | 10 |  |  | 86.4197 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2033 | Winter | 50 |  |  | 82.8706 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2034 | Winter | 10 |  |  | 87.7259 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2034 | Winter | 50 |  |  | 83.8526 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2035 | Winter | 10 |  |  | 90.1815 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2035 | Winter | 50 |  |  | 86.3425 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2036 | Winter | 10 |  |  | 89.3155 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2036 | Winter | 50 |  |  | 84.7668 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2037 | Winter | 10 |  |  | 92.5351 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2037 | Winter | 50 |  |  | 88.8524 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2038 | Winter | 10 |  |  | 94.3753 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2038 | Winter | 50 |  |  | 94.1939 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2039 | Winter | 10 |  |  | 80.6717 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2039 | Winter | 50 |  |  | 77.1549 | 202503 | MVA | central
zone_sub | phm | maximum |  | 2022 | Winter | 10 | 16270 | 23.521 | 48.1658 | 202503 | MVA | central
zone_sub | phm | maximum |  | 2022 | Winter | 50 | 16270 | 23.521 | 45.1092 | 202503 | MVA | central
zone_sub | phm | maximum |  | 2023 | Winter | 10 | 16562 | 25.5412 | 49.0318 | 202503 | MVA | central
zone_sub | phm | maximum |  | 2023 | Winter | 50 | 16562 | 25.5412 | 45.9202 | 202503 | MVA | central
zone_sub | phm | maximum |  | 2024 | Winter | 10 | 16854 | 27.7496 | 49.8978 | 202503 | MVA | central
zone_sub | phm | maximum |  | 2024 | Winter | 50 | 16854 | 27.7496 | 46.7311 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2025 | Winter | 10 |  |  | 67.0847 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2025 | Winter | 50 |  |  | 64.1376 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2026 | Winter | 10 |  |  | 71.7531 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2026 | Winter | 50 |  |  | 68.6294 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2027 | Winter | 10 |  |  | 72.4584 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2027 | Winter | 50 |  |  | 69.3785 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2028 | Winter | 10 |  |  | 72.887 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2028 | Winter | 50 |  |  | 69.9467 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2029 | Winter | 10 |  |  | 73.8781 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2029 | Winter | 50 |  |  | 70.9603 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2030 | Winter | 10 |  |  | 76.2493 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2030 | Winter | 50 |  |  | 73.2946 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2031 | Winter | 10 |  |  | 77.5227 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2031 | Winter | 50 |  |  | 74.8388 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2032 | Winter | 10 |  |  | 79.9897 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2032 | Winter | 50 |  |  | 76.8149 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2033 | Winter | 10 |  |  | 87.5343 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2033 | Winter | 50 |  |  | 77.8299 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2034 | Winter | 10 |  |  | 81.2629 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2034 | Winter | 50 |  |  | 78.7091 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2035 | Winter | 10 |  |  | 80.0205 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2035 | Winter | 50 |  |  | 77.0055 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2036 | Winter | 10 |  |  | 81.6454 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2036 | Winter | 50 |  |  | 78.9538 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2037 | Winter | 10 |  |  | 85.2253 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2037 | Winter | 50 |  |  | 82.0295 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2038 | Winter | 10 |  |  | 82.7648 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2038 | Winter | 50 |  |  | 79.6564 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2039 | Winter | 10 |  |  | 67.0558 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2039 | Winter | 50 |  |  | 63.9852 | 202503 | MVA | central
zone_sub | wgi | maximum |  | 2022 | Winter | 10 | 21696 | 27.3902 | 41.941 | 202503 | MVA | east
zone_sub | wgi | maximum |  | 2022 | Winter | 50 | 21696 | 27.3902 | 38.234 | 202503 | MVA | east
zone_sub | wgi | maximum |  | 2023 | Winter | 10 | 22045 | 30.4273 | 42.6315 | 202503 | MVA | east
zone_sub | wgi | maximum |  | 2023 | Winter | 50 | 22045 | 30.4273 | 38.883 | 202503 | MVA | east
zone_sub | wgi | maximum |  | 2024 | Winter | 10 | 22388 | 33.5461 | 43.3126 | 202503 | MVA | east
zone_sub | wgi | maximum |  | 2024 | Winter | 50 | 22388 | 33.5461 | 39.5207 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2025 | Winter | 10 |  |  | 47.2482 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2025 | Winter | 50 |  |  | 43.6466 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2026 | Winter | 10 |  |  | 47.6557 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2026 | Winter | 50 |  |  | 44.0841 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2027 | Winter | 10 |  |  | 49.0622 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2027 | Winter | 50 |  |  | 44.625 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2028 | Winter | 10 |  |  | 49.028 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2028 | Winter | 50 |  |  | 45.3431 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2029 | Winter | 10 |  |  | 49.3373 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2029 | Winter | 50 |  |  | 46.0239 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2030 | Winter | 10 |  |  | 50.5469 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2030 | Winter | 50 |  |  | 47.2137 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2031 | Winter | 10 |  |  | 54.0224 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2031 | Winter | 50 |  |  | 50.206 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2032 | Winter | 10 |  |  | 55.4565 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2032 | Winter | 50 |  |  | 51.8155 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2033 | Winter | 10 |  |  | 54.099 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2033 | Winter | 50 |  |  | 50.6413 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2034 | Winter | 10 |  |  | 57.8491 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2034 | Winter | 50 |  |  | 54.2764 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2035 | Winter | 10 |  |  | 56.2746 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2035 | Winter | 50 |  |  | 54.9313 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2036 | Winter | 10 |  |  | 57.6913 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2036 | Winter | 50 |  |  | 55.4021 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2037 | Winter | 10 |  |  | 58.7122 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2037 | Winter | 50 |  |  | 57.6212 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2038 | Winter | 10 |  |  | 58.2928 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2038 | Winter | 50 |  |  | 57.9824 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2039 | Winter | 10 |  |  | 49.2493 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2039 | Winter | 50 |  |  | 45.4578 | 202503 | MVA | east

## Ratings
STATION OUTPUT RATING (TRANSFORMER SUMMATION) SUMMARY
|  |  | Station N Rating |  | Station N-1 Rating |  | Station N-2 Rating
|  |  | SCR | WCR | SCR | WCR | SCR | WCR | Remarks | Remarks | Bus Target | Station Cap Bank
S/S Name | No. TX | Name Plate MVA | MVA | MVA | MVA | MVA | MVA | MVA | For N-1 Ratings | N-2 | Voltage kV | MVAr
CLN_Old | 2 | 66 | 87.3 | 95.3 | 44.6 | 48.9 | 0 | 0 | Loss of T1 |  | 22 | 12
CLN | 3 | 99 | 130.95 | 142.95 | 89.2 | 97.8 | 44.6 | 48.9
CRE | 2 | 66 | 84.3 | 93.8 | 41.1 | 46.3 | 0 | 0 | Loss of T2 or T3 |  | 22 | 12
EPG | 3 | 99 | 123.1 | 139.9 | 87.8 | 98.1 | 43.9 | 49.05 | Loss of T3 | Using Highest value | 22
KLO | 2 | 66 | 97.5 | 97.5 | 49.1 | 49.1 | 0 | 0 | Loss of T1 or T2 |  | 22.44 | 6
LLG | 1 | 33 | 47.4 | 48.3 | 0 | 0 | 0 | 0 | N rating only |  | 22 | 4
OFR | 2 | 66 | 93.2 | 93.2 | 45.2 | 48 | 0 | 0 | Loss of T1 or T2 |  | 22 | 6
PHM | 2 | 66 | 91.9 | 95.7 | 45 | 49.1 | 0 | 0 | Loss of T1 or T2 |  | 22 | 12
WGI | 3 | 40.5 | 55.8 | 56.8 | 35.3 | 36.1 | 17.65 | 18.05

## Power Factor
asset_type | asset | PF
zone_sub | cln | 1
zone_sub | cre | 1
zone_sub | cyn | 1
zone_sub | epg | 1
zone_sub | klo | 0.99
zone_sub | llg | 0.99
zone_sub | ofr | 1
zone_sub | phm | 1
zone_sub | wgi | 0.99

## FT
Forecast tool (MVA) |  | Forecast Capacity & Transfers
ZSS |  | WGI
Summer
[5 empty] | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads
DY (Apr 1 to Mar 30) |  | 2022/23 | 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2028/29 | 2029/30 | 2030/31 | 2031/32 | 2032/33 | 2033/34 | 2034/35 | 2035/36 | 2036/37 | 2037/38 | 2038/39
DY (Apr 1 to Mar 30) |  | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038
FY (Jul 1 to Jun 30) |  | 2022/23 | 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2028/29 | 2029/30 | 2030/31 | 2031/32 | 2032/33 | 2033/34 | 2034/35 | 2035/36 | 2036/37 | 2037/38 | 2038/39
FY (Jul 1 to Jun 30) |  |  |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39
Summer POE50 | 50 |  |  | 41.5121 | 44.6075 | 44.9185 | 44.7661 | 44.911 | 44.9706 | 45.1615 | 45.5541 | 45.8843 | 46.0363 | 45.9008 | 46.4689 | 46.559 | 46.4523 | 46.6661
Summer POE10 | 10 |  |  | 51.0465 | 54.5057 | 54.6012 | 54.4983 | 54.5247 | 54.7136 | 55.0965 | 55.7707 | 56.122 | 56.3761 | 56.7608 | 57.2519 | 57.8457 | 58.1569 | 58.056
Winter
[5 empty] | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads
DM (Apr 1 to Mar 30) |  |  |  | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2028/29 | 2029/30 | 2030/31 | 2031/32 | 2032/33 | 2033/34 | 2034/35 | 2035/36 | 2036/37 | 2037/38 | 2038/39
DY (Apr 1 to Mar 30) |  |  |  | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038
FY (Jul 1 to Jun 30) |  |  |  | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2028/29 | 2029/30 | 2030/31 | 2031/32 | 2032/33 | 2033/34 | 2034/35 | 2035/36 | 2036/37 | 2037/38 | 2038/39
FY (Jul 1 to Jun 30) |  |  |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39
Winter POE50 | 50 |  |  | 39.5207 | 43.6466 | 44.0841 | 44.625 | 45.3431 | 46.0239 | 47.2137 | 50.206 | 51.8155 | 50.6413 | 54.2764 | 54.9313 | 55.4021 | 57.6212 | 57.9824
Winter POE10 | 10 |  |  | 43.3126 | 47.2482 | 47.6557 | 49.0622 | 49.028 | 49.3373 | 50.5469 | 54.0224 | 55.4565 | 54.099 | 57.8491 | 56.2746 | 57.6913 | 58.7122 | 58.2928
Transfers (MVA)
|  | Feeder | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39
|  | WGI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | PowerFactor | 0.99

## Load Duration Curves
Station
WGI
POE10
[6 empty] | Stations | KLO |  | EPG |  | CRE |  | CLN |  | PHM |  | OFR |  | LLG |  | WGI
| % of MD | Winter - MD (P10) - Duration % | Winter - MD - Hours | Summer - MD - Duration % | Summer - MD - Hours | %MD | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration %
| 100% | 0% | 0 | 0% | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| 99% | 0.006767% | 0.2972 | 0% | 0 | 99% | 0.01722% | 0.02707% | 0% | 0.04737% | 0% | 0% | 0.00861% | 0.01353% | 0.03444% | 0.03383% | 0.01722% | 0.0203% | 0.02583% | 0.006767% | 0% | 0.006767%
| 98% | 0.006767% | 0.2972 | 0% | 0 | 98% | 0.01722% | 0.07443% | 0.00861% | 0.08797% | 0.02583% | 0.01353% | 0.02583% | 0.0203% | 0.05166% | 0.07443% | 0.02583% | 0.0812% | 0.04305% | 0.0203% | 0% | 0.006767%
| 97% | 0.006767% | 0.2972 | 0.00861% | 0.37816 | 97% | 0.02583% | 0.09474% | 0.02583% | 0.1421% | 0.04305% | 0.02707% | 0.05166% | 0.03383% | 0.0861% | 0.1556% | 0.04305% | 0.1083% | 0.05166% | 0.04737% | 0.00861% | 0.006767%
| 95% | 0.03383% | 1.486 | 0.00861% | 0.37816 | 95% | 0.05166% | 0.1895% | 0.09471% | 0.3519% | 0.0861% | 0.08797% | 0.1033% | 0.05413% | 0.1378% | 0.3992% | 0.07749% | 0.1759% | 0.09471% | 0.09474% | 0.00861% | 0.03383%
| 90% | 0.1962% | 8.6188 | 0.01722% | 0.75633 | 90% | 0.0861% | 0.9135% | 0.1894% | 1.786% | 0.1894% | 0.7579% | 0.1808% | 0.07443% | 0.3702% | 1.793% | 0.2066% | 0.8932% | 0.353% | 0.2639% | 0.01722% | 0.1962%
| 85% | 0.9135% | 40.1218 | 0.02583% | 1.1345 | 85% | 0.1205% | 2.355% | 0.353% | 4.588% | 0.2669% | 2.761% | 0.3272% | 0.318% | 0.6027% | 5.393% | 0.3702% | 2.68% | 0.7147% | 0.7443% | 0.02583% | 0.9135%
| 80% | 2.118% | 93.0231 | 0.06027% | 2.6471 | 80% | 0.31% | 5.616% | 0.6458% | 8.885% | 0.4219% | 6.787% | 0.4477% | 0.9406% | 0.7749% | 11.33% | 0.5683% | 6.11% | 1.317% | 1.915% | 0.06027% | 2.118%
| 75% | 4.486% | 197.0426 | 0.07749% | 3.4035 | 75% | 0.4822% | 9.995% | 0.9988% | 14.05% | 0.5338% | 11.76% | 0.5855% | 2.876% | 1.102% | 18.3% | 0.7491% | 10.38% | 2.764% | 4.601% | 0.07749% | 4.486%
| 70% | 8.607% | 378.0365 | 0.1292% | 5.6725 | 70% | 0.7491% | 14.12% | 1.498% | 19.88% | 0.8438% | 17.56% | 0.7921% | 7.376% | 1.739% | 26.3% | 0.9557% | 15.73% | 6.225% | 8.837% | 0.1292% | 8.607%
| 65% | 14.03% | 616.0926 | 0.1464% | 6.4288 | 65% | 1.154% | 18.84% | 2.265% | 27.11% | 1.102% | 25.21% | 1.05% | 12.51% | 2.6% | 35.36% | 1.541% | 22.03% | 12.05% | 15.25% | 0.1464% | 14.03%
| 60% | 21.29% | 934.9866 | 0.2583% | 11.3449 | 60% | 1.602% | 25.14% | 3.203% | 35.21% | 1.627% | 33.62% | 1.748% | 18.2% | 4.055% | 46.14% | 2.247% | 29.44% | 20.92% | 25.15% | 0.2583% | 21.29%
| 55% | 29.85% | 1310.9428 | 0.8094% | 35.5474 | 55% | 2.411% | 33.56% | 4.357% | 45.33% | 2.48% | 42.68% | 2.419% | 25.42% | 7.095% | 59.16% | 3.496% | 37.5% | 33.11% | 37.15% | 0.8094% | 29.85%
| 50% | 39.4% | 1730.2899 | 2.17% | 95.2974 | 50% | 4.598% | 44.25% | 6.303% | 58.26% | 3.84% | 54.87% | 4.064% | 34.04% | 14.48% | 73.62% | 5.881% | 47.91% | 47.93% | 51.32% | 2.17% | 39.4%
| 45% | 49.36% | 2168.0633 | 4.753% | 208.7467 | 45% | 9.592% | 58.98% | 10.8% | 69.36% | 6.535% | 71.48% | 8.378% | 45.63% | 26.86% | 85.96% | 11.13% | 62.3% | 62.8% | 65.85% | 4.753% | 49.36%
| 40% | 59.42% | 2609.7004 | 8.662% | 380.4333 | 40% | 19.83% | 71.65% | 21.2% | 75.98% | 14.01% | 84.31% | 16.88% | 65.51% | 41.17% | 92.73% | 21.13% | 79.32% | 76.24% | 79.08% | 8.662% | 59.42%
| 35% | 68.26% | 2998.1389 | 15.86% | 696.5786 | 35% | 37.74% | 78.94% | 37.58% | 85.16% | 27.53% | 88.52% | 26.59% | 78.66% | 63.28% | 95.6% | 34.85% | 87.21% | 86.9% | 88.41% | 15.86% | 68.26%
| 30% | 75.35% | 3309.3057 | 28.71% | 1260.7997 | 30% | 66.82% | 83.24% | 57.09% | 93.38% | 49.73% | 90.98% | 45.59% | 83.41% | 86.84% | 97.25% | 59.02% | 90.02% | 92.6% | 93.97% | 28.71% | 75.35%
| 25% | 80.55% | 3537.8514 | 44.75% | 1965.3198 | 25% | 77.33% | 87.43% | 77.75% | 96.1% | 81.07% | 93.44% | 72.26% | 87.95% | 94.88% | 98.4% | 83.32% | 92.46% | 96.47% | 96.66% | 44.75% | 80.55%
| 20% | 84.95% | 3731.0305 | 56.7% | 2490.2118 | 20% | 85.59% | 92.06% | 96.84% | 97.65% | 89.22% | 95.65% | 79.18% | 93.87% | 97.51% | 99.11% | 91.2% | 94.84% | 98.65% | 98.41% | 56.7% | 84.95%
| 15% | 89.03% | 3910.2412 | 68.25% | 2997.7083 | 15% | 96.14% | 98.9% | 99.64% | 98.65% | 96.11% | 97.43% | 86.26% | 99.55% | 99.38% | 99.49% | 97.48% | 97.23% | 99.31% | 99.14% | 68.25% | 89.03%
| 10% | 92.79% | 4075.1864 | 79.5% | 3491.5908 | 10% | 99.99% | 99.99% | 99.99% | 99.16% | 99.9% | 98.78% | 98.3% | 99.6% | 99.99% | 99.7% | 99.99% | 99.59% | 99.63% | 99.41% | 79.5% | 92.79%
| 5% | 96.81% | 4251.7223 | 90.07% | 3955.9766 | 5% | 99.99% | 99.99% | 99.99% | 99.49% | 99.99% | 99.76% | 99.99% | 99.61% | 99.99% | 99.99% | 99.99% | 99.99% | 99.68% | 99.6% | 90.07% | 96.81%
| 9.992e-14% | 99.99% | 4391.7028 | 99.99% | 4391.6218 | 0% | 99.99% | 99.99% | 99.99% | 99.99% | 99.99% | 99.99% | 99.99% | 99.63% | 99.99% | 99.99% | 99.99% | 99.99% | 99.71% | 99.63% | 99.99% | 99.99%
POE 50
[6 empty] | Stations | KLO |  | EPG |  | CRE |  | CLN |  | PHM |  | OFR |  | LLG |  | WGI
| % of MD | Winter - AD (P50) - Duration % | Winter - AD - Hours | Summer - AD - Duration % | Summer - AD - Hours | %MD | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration %
| 100% | 0% | 0 | 0% | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| 99% | 0.006767% | 0.2972 | 0.00861% | 0.37816 | 99% | 0.03444% | 0.02707% | 0.04305% | 0.04737% | 0% | 0% | 0% | 0.01353% | 0% | 0.03383% | 0% | 0.0203% | 0.00861% | 0.006767% | 0.00861% | 0.006767%
| 98% | 0.006767% | 0.2972 | 0.00861% | 0.37816 | 98% | 0.05166% | 0.07443% | 0.07749% | 0.08797% | 0% | 0.01353% | 0.00861% | 0.0203% | 0% | 0.07443% | 0.00861% | 0.0812% | 0.00861% | 0.0203% | 0.00861% | 0.006767%
| 97% | 0.006767% | 0.2972 | 0.00861% | 0.37816 | 97% | 0.06888% | 0.09474% | 0.07749% | 0.1421% | 0.02583% | 0.02707% | 0.01722% | 0.03383% | 0.00861% | 0.1556% | 0.01722% | 0.1083% | 0.01722% | 0.0406% | 0.00861% | 0.006767%
| 95% | 0.03383% | 1.486 | 0.01722% | 0.75633 | 95% | 0.0861% | 0.1895% | 0.1378% | 0.3519% | 0.04305% | 0.08797% | 0.02583% | 0.05413% | 0.05166% | 0.3992% | 0.04305% | 0.1759% | 0.01722% | 0.1015% | 0.01722% | 0.03383%
| 90% | 0.1962% | 8.6188 | 0.2066% | 9.0759 | 90% | 0.1292% | 0.9135% | 0.2583% | 1.786% | 0.1119% | 0.7579% | 0.1033% | 0.07443% | 0.1292% | 1.793% | 0.1033% | 0.8932% | 0.0861% | 0.3451% | 0.2066% | 0.1962%
| 85% | 0.9135% | 40.1218 | 0.9213% | 40.4636 | 85% | 0.2497% | 2.355% | 0.465% | 4.588% | 0.2755% | 2.761% | 0.1808% | 0.318% | 0.3616% | 5.393% | 0.2066% | 2.68% | 0.31% | 0.9% | 0.9213% | 0.9135%
| 80% | 2.118% | 93.0231 | 2.153% | 94.5411 | 80% | 0.4133% | 5.616% | 0.7835% | 8.885% | 0.6113% | 6.787% | 0.2669% | 0.9406% | 0.706% | 11.33% | 0.6286% | 6.11% | 0.8008% | 2.517% | 2.153% | 2.118%
| 75% | 4.486% | 197.0426 | 4.486% | 197.0236 | 75% | 0.8352% | 9.995% | 1.257% | 14.05% | 0.9902% | 11.76% | 0.4047% | 2.876% | 1.662% | 18.3% | 1.309% | 10.38% | 1.834% | 5.562% | 4.486% | 4.486%
| 70% | 8.607% | 378.0365 | 7.672% | 336.9444 | 70% | 1.619% | 14.12% | 2.101% | 19.88% | 1.911% | 17.56% | 0.8008% | 7.376% | 3.427% | 26.3% | 2.419% | 15.73% | 4.374% | 10.11% | 7.672% | 8.607%
| 65% | 14.03% | 616.0926 | 11.87% | 521.4885 | 65% | 3.057% | 18.84% | 4.288% | 27.11% | 3.504% | 25.21% | 1.352% | 12.51% | 8.188% | 35.36% | 4.598% | 22.03% | 9.179% | 17.54% | 11.87% | 14.03%
| 60% | 21.29% | 934.9866 | 18.5% | 812.675 | 60% | 5.528% | 25.14% | 9.342% | 35.21% | 7.758% | 33.62% | 3.573% | 18.2% | 15.71% | 46.14% | 9.17% | 29.44% | 16.83% | 27.53% | 18.5% | 21.29%
| 55% | 29.85% | 1310.9428 | 27.37% | 1202.1843 | 55% | 11.8% | 33.56% | 17.61% | 45.33% | 16.05% | 42.68% | 8.283% | 25.42% | 24.94% | 59.16% | 14.93% | 37.5% | 27.43% | 40.02% | 27.37% | 29.85%
| 50% | 39.4% | 1730.2899 | 38.39% | 1686.2345 | 50% | 21.47% | 44.25% | 28.46% | 58.26% | 24.85% | 54.87% | 17.57% | 34.04% | 37.94% | 73.62% | 22.35% | 47.91% | 40.6% | 54.15% | 38.39% | 39.4%
| 45% | 49.36% | 2168.0633 | 48.48% | 2129.0649 | 45% | 35.07% | 58.98% | 42.44% | 69.36% | 37.15% | 71.48% | 28.59% | 45.63% | 57.06% | 85.96% | 36.95% | 62.3% | 53.97% | 68.39% | 48.48% | 49.36%
| 40% | 59.42% | 2609.7004 | 56.57% | 2484.5393 | 40% | 60.78% | 71.65% | 63.35% | 75.98% | 61.17% | 84.31% | 46.88% | 65.51% | 72.05% | 92.73% | 55.62% | 79.32% | 65.21% | 80.79% | 56.57% | 59.42%
| 35% | 68.26% | 2998.1389 | 63.94% | 2808.248 | 35% | 70.59% | 78.94% | 76.04% | 85.16% | 71.05% | 88.52% | 69.68% | 78.66% | 80.86% | 95.6% | 68.46% | 87.21% | 75.09% | 89.43% | 63.94% | 68.26%
| 30% | 75.35% | 3309.3057 | 70.48% | 3095.6528 | 30% | 76.73% | 83.24% | 80.97% | 93.38% | 75.06% | 90.98% | 76.64% | 83.41% | 85.59% | 97.25% | 74.6% | 90.02% | 81.51% | 94.17% | 70.48% | 75.35%
| 25% | 80.55% | 3537.8514 | 76.48% | 3358.8552 | 25% | 83.08% | 87.43% | 85.41% | 96.1% | 78.56% | 93.44% | 83.93% | 87.95% | 89.4% | 98.4% | 78.93% | 92.46% | 86.44% | 96.81% | 76.48% | 80.55%
| 20% | 84.95% | 3731.0305 | 81.71% | 3588.7791 | 20% | 91.12% | 92.06% | 89.28% | 97.65% | 81.79% | 95.65% | 91.73% | 93.87% | 92.22% | 99.11% | 84.56% | 94.84% | 90.52% | 98.48% | 81.71% | 84.95%
| 15% | 89.03% | 3910.2412 | 86.58% | 3802.4419 | 15% | 99.18% | 98.9% | 92.61% | 98.65% | 86.18% | 97.43% | 98.93% | 99.55% | 94.55% | 99.49% | 92.06% | 97.23% | 93.75% | 99.28% | 86.58% | 89.03%
| 10% | 92.79% | 4075.1864 | 91.64% | 4024.8025 | 10% | 99.99% | 99.99% | 95.16% | 99.16% | 91.73% | 98.78% | 99.75% | 99.6% | 96.73% | 99.7% | 99.06% | 99.59% | 96.19% | 99.59% | 91.64% | 92.79%
| 5% | 96.81% | 4251.7223 | 96.54% | 4239.978 | 5% | 99.99% | 99.99% | 97.15% | 99.49% | 97.84% | 99.76% | 99.99% | 99.61% | 99.31% | 99.99% | 99.99% | 99.99% | 98.14% | 99.77% | 96.54% | 96.81%
| 9.992e-14% | 99.99% | 4391.7028 | 99.99% | 4391.6218 | 0% | 99.99% | 99.99% | 99.99% | 99.99% | 99.99% | 99.99% | 99.99% | 99.63% | 99.99% | 99.99% | 99.99% | 99.99% | 99.78% | 99.99% | 99.99% | 99.99%
POE10
|  | Summer | Winter
| Year | 2019/2020 | 2023
| Start | 2024-10-01 | 2024-04-01
| End | 2025-04-01 | 2024-10-01
| Days | 183 | 183
| Hours | 4392 | 4392
POE50
|  | Summer | Winter
| Year | 2023/2024 | 2023
| Start | 2023-10-01 | 2024-04-01
| End | 2024-04-01 | 2024-10-01
| Days | 183 | 183
| Hours | 4392 | 4392

## Capacity N
Option 1 - Do Nothing - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N Rating (MVA) - Option 1 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8
SCR N Rating (MVA) - Option 1 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8
Planned Additional Capacity (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2 - Replace 3 x 10/13.5 MVA Tx with 3 x 20/33 MVA Tx - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N Rating (MVA) - Option 2 | 56.8 | 56.8 | 56.8 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
SCR N Rating (MVA) - Option 2 | 55.8 | 55.8 | 55.8 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99
Capacity Added (MVA) | 0 | 0 | 0 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2
Option 3 - Replace 1 x 10/13.5 MVA Tx with 1 x 20/33 MVA Tx - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N Rating (MVA) - Option 3 | 56.8 | 56.8 | 56.8 | 72.15 | 72.15 | 72.15 | 72.15 | 72.15 | 72.15 | 72.15 | 72.15 | 72.15 | 72.15 | 72.15 | 72.15 | 72.15 | 72.15 | 72.15 | 72.15 | 72.15 | 72.15 | 72.15 | 72.15 | 72.15 | 72.15 | 72.15 | 72.15 | 72.15 | 72.15 | 72.15
SCR N Rating (MVA) - Option 3 | 55.8 | 55.8 | 55.8 | 71.15 | 71.15 | 71.15 | 71.15 | 71.15 | 71.15 | 71.15 | 71.15 | 71.15 | 71.15 | 71.15 | 71.15 | 71.15 | 71.15 | 71.15 | 71.15 | 71.15 | 71.15 | 71.15 | 71.15 | 71.15 | 71.15 | 71.15 | 71.15 | 71.15 | 71.15 | 71.15
Capacity Added (MVA) | 0 | 0 | 0 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35
Option 4 - Construct 2x 20/33MVA zone substation in Inverloch - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N Rating (MVA) - Option 4 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8
SCR N Rating (MVA) - Option 4 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 - Contract network support services to defer network investment - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N Rating (MVA) - Option 5 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8
SCR N Rating (MVA) - Option 5 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 6 - - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N Rating (MVA) - Option 6 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8
SCR N Rating (MVA) - Option 6 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 7 - - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N Rating (MVA) - Option 7 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8
SCR N Rating (MVA) - Option 7 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 8 - - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N Rating (MVA) - Option 8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8 | 56.8
SCR N Rating (MVA) - Option 8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Capacity N-1
Option 1 - Do Nothing - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-1 Rating (MVA) - Option 1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1
SCR N-1 Rating (MVA) - Option 1 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3
Planned Additional Capacity (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2 - Replace 3 x 10/13.5 MVA Tx with 3 x 20/33 MVA Tx - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-1 Rating (MVA) - Option 2 | 36.1 | 36.1 | 36.1 | 79.3 | 79.3 | 79.3 | 79.3 | 79.3 | 79.3 | 79.3 | 79.3 | 79.3 | 79.3 | 79.3 | 79.3 | 79.3 | 79.3 | 79.3 | 79.3 | 79.3 | 79.3 | 79.3 | 79.3 | 79.3 | 79.3 | 79.3 | 79.3 | 79.3 | 79.3 | 79.3
SCR N-1 Rating (MVA) - Option 2 | 35.3 | 35.3 | 35.3 | 78.5 | 78.5 | 78.5 | 78.5 | 78.5 | 78.5 | 78.5 | 78.5 | 78.5 | 78.5 | 78.5 | 78.5 | 78.5 | 78.5 | 78.5 | 78.5 | 78.5 | 78.5 | 78.5 | 78.5 | 78.5 | 78.5 | 78.5 | 78.5 | 78.5 | 78.5 | 78.5
Capacity Added (MVA) | 0 | 0 | 0 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2
Option 3 - Replace 1 x 10/13.5 MVA Tx with 1 x 20/33 MVA Tx - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-1 Rating (MVA) - Option 3 | 36.1 | 36.1 | 36.1 | 51.45 | 51.45 | 51.45 | 51.45 | 51.45 | 51.45 | 51.45 | 51.45 | 51.45 | 51.45 | 51.45 | 51.45 | 51.45 | 51.45 | 51.45 | 51.45 | 51.45 | 51.45 | 51.45 | 51.45 | 51.45 | 51.45 | 51.45 | 51.45 | 51.45 | 51.45 | 51.45
SCR N-1 Rating (MVA) - Option 3 | 35.3 | 35.3 | 35.3 | 50.65 | 50.65 | 50.65 | 50.65 | 50.65 | 50.65 | 50.65 | 50.65 | 50.65 | 50.65 | 50.65 | 50.65 | 50.65 | 50.65 | 50.65 | 50.65 | 50.65 | 50.65 | 50.65 | 50.65 | 50.65 | 50.65 | 50.65 | 50.65 | 50.65 | 50.65 | 50.65
Capacity Added (MVA) | 0 | 0 | 0 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35
Option 4 - Construct 2x 20/33MVA zone substation in Inverloch - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-1 Rating (MVA) - Option 4 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1
SCR N-1 Rating (MVA) - Option 4 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 - Contract network support services to defer network investment - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-1 Rating (MVA) - Option 5 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1
SCR N-1 Rating (MVA) - Option 5 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 6 - - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-1 Rating (MVA) - Option 6 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1
SCR N-1 Rating (MVA) - Option 6 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 7 - - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-1 Rating (MVA) - Option 7 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1
SCR N-1 Rating (MVA) - Option 7 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 8 - - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-1 Rating (MVA) - Option 8 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1 | 36.1
SCR N-1 Rating (MVA) - Option 8 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3 | 35.3
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Capacity N-2
Option 1 - Do Nothing - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-2 Rating (MVA) - Option 1 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05
SCR N-2 Rating (MVA) - Option 1 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65
Planned Additional Capacity (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2 - Replace 3 x 10/13.5 MVA Tx with 3 x 20/33 MVA Tx - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-2 Rating (MVA) - Option 2 | 18.05 | 18.05 | 18.05 | 61.25 | 61.25 | 61.25 | 61.25 | 61.25 | 61.25 | 61.25 | 61.25 | 61.25 | 61.25 | 61.25 | 61.25 | 61.25 | 61.25 | 61.25 | 61.25 | 61.25 | 61.25 | 61.25 | 61.25 | 61.25 | 61.25 | 61.25 | 61.25 | 61.25 | 61.25 | 61.25
SCR N-2 Rating (MVA) - Option 2 | 17.65 | 17.65 | 17.65 | 60.85 | 60.85 | 60.85 | 60.85 | 60.85 | 60.85 | 60.85 | 60.85 | 60.85 | 60.85 | 60.85 | 60.85 | 60.85 | 60.85 | 60.85 | 60.85 | 60.85 | 60.85 | 60.85 | 60.85 | 60.85 | 60.85 | 60.85 | 60.85 | 60.85 | 60.85 | 60.85
Capacity Added (MVA) | 0 | 0 | 0 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2
Option 3 - Replace 1 x 10/13.5 MVA Tx with 1 x 20/33 MVA Tx - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-2 Rating (MVA) - Option 3 | 18.05 | 18.05 | 18.05 | 33.4 | 33.4 | 33.4 | 33.4 | 33.4 | 33.4 | 33.4 | 33.4 | 33.4 | 33.4 | 33.4 | 33.4 | 33.4 | 33.4 | 33.4 | 33.4 | 33.4 | 33.4 | 33.4 | 33.4 | 33.4 | 33.4 | 33.4 | 33.4 | 33.4 | 33.4 | 33.4
SCR N-2 Rating (MVA) - Option 3 | 17.65 | 17.65 | 17.65 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33
Capacity Added (MVA) | 0 | 0 | 0 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35
Option 4 - Construct 2x 20/33MVA zone substation in Inverloch - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-2 Rating (MVA) - Option 4 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05
SCR N-2 Rating (MVA) - Option 4 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 - Contract network support services to defer network investment - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-2 Rating (MVA) - Option 5 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05
SCR N-2 Rating (MVA) - Option 5 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 6 - - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-2 Rating (MVA) - Option 6 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05
SCR N-2 Rating (MVA) - Option 6 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 7 - - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-2 Rating (MVA) - Option 7 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05
SCR N-2 Rating (MVA) - Option 7 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 8 - - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-2 Rating (MVA) - Option 8 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05 | 18.05
SCR N-2 Rating (MVA) - Option 8 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65 | 17.65
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Demand
Option 1 - Do Nothing
Winter Season | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Maximum Demand (MVA) - P50 | 35.5686 | 39.2819 | 39.6757 | 40.1625 | 40.8088 | 41.4215 | 42.4923 | 45.1854 | 46.6339 | 45.5772 | 48.8487 | 49.4382 | 49.8619 | 51.8591 | 52.1842 | 52.1842 | 52.1842 | 52.1842 | 52.1842 | 52.1842 | 52.1842 | 52.1842 | 52.1842 | 52.1842 | 52.1842 | 52.1842 | 52.1842 | 52.1842 | 52.1842 | 52.1842
Maximum Demand (MVA) - P10 | 38.9814 | 42.5233 | 42.8901 | 44.156 | 44.1252 | 44.4035 | 45.4922 | 48.6201 | 49.9109 | 48.6891 | 52.0642 | 50.6471 | 51.9222 | 52.841 | 52.4635 | 52.4635 | 52.4635 | 52.4635 | 52.4635 | 52.4635 | 52.4635 | 52.4635 | 52.4635 | 52.4635 | 52.4635 | 52.4635 | 52.4635 | 52.4635 | 52.4635 | 52.4635
Block loads (MVA) not in the forecast | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Available Transfers (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Demand management (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Embedded generation (MVA) | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11
Total Maximum Demand (MVA) - Option 1 Winter POE50 | 35.4586 | 39.1719 | 39.5657 | 40.0525 | 40.6988 | 41.3115 | 42.3823 | 45.0754 | 46.5239 | 45.4672 | 48.7387 | 49.3282 | 49.7519 | 51.7491 | 52.0742 | 52.0742 | 52.0742 | 52.0742 | 52.0742 | 52.0742 | 52.0742 | 52.0742 | 52.0742 | 52.0742 | 52.0742 | 52.0742 | 52.0742 | 52.0742 | 52.0742 | 52.0742
Total Maximum Demand (MVA) - Option 1 Winter POE10 | 38.8714 | 42.4133 | 42.7801 | 44.046 | 44.0152 | 44.2935 | 45.3822 | 48.5101 | 49.8009 | 48.5791 | 51.9542 | 50.5371 | 51.8122 | 52.731 | 52.3535 | 52.3535 | 52.3535 | 52.3535 | 52.3535 | 52.3535 | 52.3535 | 52.3535 | 52.3535 | 52.3535 | 52.3535 | 52.3535 | 52.3535 | 52.3535 | 52.3535 | 52.3535
Summer Season | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Maximum Demand (MVA) - P50 | 37.3609 | 40.1467 | 40.4267 | 40.2894 | 40.4199 | 40.4735 | 40.6454 | 40.9986 | 41.2959 | 41.4327 | 41.3107 | 41.822 | 41.9031 | 41.8071 | 41.9995 | 41.9995 | 41.9995 | 41.9995 | 41.9995 | 41.9995 | 41.9995 | 41.9995 | 41.9995 | 41.9995 | 41.9995 | 41.9995 | 41.9995 | 41.9995 | 41.9995 | 41.9995
Maximum Demand (MVA) - P10 | 45.9418 | 49.0552 | 49.1411 | 49.0484 | 49.0723 | 49.2423 | 49.5868 | 50.1936 | 50.5098 | 50.7385 | 51.0847 | 51.5267 | 52.0611 | 52.3412 | 52.2504 | 52.2504 | 52.2504 | 52.2504 | 52.2504 | 52.2504 | 52.2504 | 52.2504 | 52.2504 | 52.2504 | 52.2504 | 52.2504 | 52.2504 | 52.2504 | 52.2504 | 52.2504
Block loads (MVA) not in the forecast | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Available Transfers (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Demand management (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Embedded generation (MVA) | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Maximum Demand (MVA) - Option 1 Summer POE50 | 37.2509 | 40.0367 | 40.3167 | 40.1794 | 40.3099 | 40.3635 | 40.5354 | 40.8886 | 41.1859 | 41.3227 | 41.2007 | 41.712 | 41.7931 | 41.6971 | 41.8895 | 41.9995 | 41.9995 | 41.9995 | 41.9995 | 41.9995 | 41.9995 | 41.9995 | 41.9995 | 41.9995 | 41.9995 | 41.9995 | 41.9995 | 41.9995 | 41.9995 | 41.9995
Total Maximum Demand (MVA) - Option 1 Summer POE10 | 45.8318 | 48.9452 | 49.0311 | 48.9384 | 48.9623 | 49.1323 | 49.4768 | 50.0836 | 50.3998 | 50.6285 | 50.9747 | 51.4167 | 51.9511 | 52.2312 | 52.1404 | 52.2504 | 52.2504 | 52.2504 | 52.2504 | 52.2504 | 52.2504 | 52.2504 | 52.2504 | 52.2504 | 52.2504 | 52.2504 | 52.2504 | 52.2504 | 52.2504 | 52.2504
Option 2 - Replace 3 x 10/13.5 MVA Tx with 3 x 20/33 MVA Tx
Year | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Added Transfers (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Added Demand management (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Added Embedded generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Maximum Demand (MVA) - Option 2 Winter POE50 | 35.4586 | 39.1719 | 39.5657 | 40.0525 | 40.6988 | 41.3115 | 42.3823 | 45.0754 | 46.5239 | 45.4672 | 48.7387 | 49.3282 | 49.7519 | 51.7491 | 52.0742 | 52.0742 | 52.0742 | 52.0742 | 52.0742 | 52.0742 | 52.0742 | 52.0742 | 52.0742 | 52.0742 | 52.0742 | 52.0742 | 52.0742 | 52.0742 | 52.0742 | 52.0742
Total Maximum Demand (MVA) - Option 2 Winter POE10 | 38.8714 | 42.4133 | 42.7801 | 44.046 | 44.0152 | 44.2935 | 45.3822 | 48.5101 | 49.8009 | 48.5791 | 51.9542 | 50.5371 | 51.8122 | 52.731 | 52.3535 | 52.3535 | 52.3535 | 52.3535 | 52.3535 | 52.3535 | 52.3535 | 52.3535 | 52.3535 | 52.3535 | 52.3535 | 52.3535 | 52.3535 | 52.3535 | 52.3535 | 52.3535
Total Maximum Demand (MVA) - Option 2 Summer POE50 | 37.2509 | 40.0367 | 40.3167 | 40.1794 | 40.3099 | 40.3635 | 40.5354 | 40.8886 | 41.1859 | 41.3227 | 41.2007 | 41.712 | 41.7931 | 41.6971 | 41.8895 | 41.9995 | 41.9995 | 41.9995 | 41.9995 | 41.9995 | 41.9995 | 41.9995 | 41.9995 | 41.9995 | 41.9995 | 41.9995 | 41.9995 | 41.9995 | 41.9995 | 41.9995
Total Maximum Demand (MVA) - Option 2 Summer POE10 | 45.8318 | 48.9452 | 49.0311 | 48.9384 | 48.9623 | 49.1323 | 49.4768 | 50.0836 | 50.3998 | 50.6285 | 50.9747 | 51.4167 | 51.9511 | 52.2312 | 52.1404 | 52.2504 | 52.2504 | 52.2504 | 52.2504 | 52.2504 | 52.2504 | 52.2504 | 52.2504 | 52.2504 | 52.2504 | 52.2504 | 52.2504 | 52.2504 | 52.2504 | 52.2504
Option 3 - Replace 1 x 10/13.5 MVA Tx with 1 x 20/33 MVA Tx
Year | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Added Transfers (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Added Demand management (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Added Embedded generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Maximum Demand (MVA) - Option 3 Winter POE50 | 35.4586 | 39.1719 | 39.5657 | 40.0525 | 40.6988 | 41.3115 | 42.3823 | 45.0754 | 46.5239 | 45.4672 | 48.7387 | 49.3282 | 49.7519 | 51.7491 | 52.0742 | 52.0742 | 52.0742 | 52.0742 | 52.0742 | 52.0742 | 52.0742 | 52.0742 | 52.0742 | 52.0742 | 52.0742 | 52.0742 | 52.0742 | 52.0742 | 52.0742 | 52.0742
Total Maximum Demand (MVA) - Option 3 Winter POE10 | 38.8714 | 42.4133 | 42.7801 | 44.046 | 44.0152 | 44.2935 | 45.3822 | 48.5101 | 49.8009 | 48.5791 | 51.9542 | 50.5371 | 51.8122 | 52.731 | 52.3535 | 52.3535 | 52.3535 | 52.3535 | 52.3535 | 52.3535 | 52.3535 | 52.3535 | 52.3535 | 52.3535 | 52.3535 | 52.3535 | 52.3535 | 52.3535 | 52.3535 | 52.3535
Total Maximum Demand (MVA) - Option 3 Summer POE50 | 37.2509 | 40.0367 | 40.3167 | 40.1794 | 40.3099 | 40.3635 | 40.5354 | 40.8886 | 41.1859 | 41.3227 | 41.2007 | 41.712 | 41.7931 | 41.6971 | 41.8895 | 41.9995 | 41.9995 | 41.9995 | 41.9995 | 41.9995 | 41.9995 | 41.9995 | 41.9995 | 41.9995 | 41.9995 | 41.9995 | 41.9995 | 41.9995 | 41.9995 | 41.9995
Total Maximum Demand (MVA) - Option 3 Summer POE10 | 45.8318 | 48.9452 | 49.0311 | 48.9384 | 48.9623 | 49.1323 | 49.4768 | 50.0836 | 50.3998 | 50.6285 | 50.9747 | 51.4167 | 51.9511 | 52.2312 | 52.1404 | 52.2504 | 52.2504 | 52.2504 | 52.2504 | 52.2504 | 52.2504 | 52.2504 | 52.2504 | 52.2504 | 52.2504 | 52.2504 | 52.2504 | 52.2504 | 52.2504 | 52.2504
Option 4 - Construct 2x 20/33MVA zone substation in Inverloch
Year | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Added Transfers (MVA) | 0 | 0 | 0 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66
Added Demand management (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Added Embedded generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Maximum Demand (MVA) - Option 4 Winter POE50 | 35.4586 | 39.1719 | 39.5657 | -25.9475 | -25.3012 | -24.6885 | -23.6177 | -20.9246 | -19.4761 | -20.5328 | -17.2613 | -16.6718 | -16.2481 | -14.2509 | -13.9258 | -13.9258 | -13.9258 | -13.9258 | -13.9258 | -13.9258 | -13.9258 | -13.9258 | -13.9258 | -13.9258 | -13.9258 | -13.9258 | -13.9258 | -13.9258 | -13.9258 | -13.9258
Total Maximum Demand (MVA) - Option 4 Winter POE10 | 38.8714 | 42.4133 | 42.7801 | -21.954 | -21.9848 | -21.7065 | -20.6178 | -17.4899 | -16.1991 | -17.4209 | -14.0458 | -15.4629 | -14.1878 | -13.269 | -13.6465 | -13.6465 | -13.6465 | -13.6465 | -13.6465 | -13.6465 | -13.6465 | -13.6465 | -13.6465 | -13.6465 | -13.6465 | -13.6465 | -13.6465 | -13.6465 | -13.6465 | -13.6465
Total Maximum Demand (MVA) - Option 4 Summer POE50 | 37.2509 | 40.0367 | 40.3167 | -25.8206 | -25.6901 | -25.6365 | -25.4646 | -25.1114 | -24.8141 | -24.6773 | -24.7993 | -24.288 | -24.2069 | -24.3029 | -24.1105 | -24.0005 | -24.0005 | -24.0005 | -24.0005 | -24.0005 | -24.0005 | -24.0005 | -24.0005 | -24.0005 | -24.0005 | -24.0005 | -24.0005 | -24.0005 | -24.0005 | -24.0005
Total Maximum Demand (MVA) - Option 4 Summer POE10 | 45.8318 | 48.9452 | 49.0311 | -17.0616 | -17.0377 | -16.8677 | -16.5232 | -15.9164 | -15.6002 | -15.3715 | -15.0253 | -14.5833 | -14.0489 | -13.7688 | -13.8596 | -13.7496 | -13.7496 | -13.7496 | -13.7496 | -13.7496 | -13.7496 | -13.7496 | -13.7496 | -13.7496 | -13.7496 | -13.7496 | -13.7496 | -13.7496 | -13.7496 | -13.7496
Option 5 - Contract network support services to defer network investment
Year | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Added Transfers (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Added Demand management (MVA) | 4.0981 | 4.3758 | 4.3835 | 4.3752 | 4.3773 | 4.3925 | 4.4232 | 4.4774 | 4.5056 | 4.526 | 4.5569 | 4.5963 | 4.644 | 4.6689 | 4.6608 | 4.6608 | 4.6608 | 4.6608 | 4.6608 | 4.6608 | 4.6608 | 4.6608 | 4.6608 | 4.6608 | 4.6608 | 4.6608 | 4.6608 | 4.6608 | 4.6608 | 4.6608
Added Embedded generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Maximum Demand (MVA) - Option 5 Winter POE50 | 31.3605 | 34.7961 | 35.1822 | 35.6773 | 36.3215 | 36.919 | 37.9591 | 40.598 | 42.0184 | 40.9412 | 44.1819 | 44.7319 | 45.1079 | 47.0802 | 47.4134 | 47.4134 | 47.4134 | 47.4134 | 47.4134 | 47.4134 | 47.4134 | 47.4134 | 47.4134 | 47.4134 | 47.4134 | 47.4134 | 47.4134 | 47.4134 | 47.4134 | 47.4134
Total Maximum Demand (MVA) - Option 5 Winter POE10 | 34.7733 | 38.0375 | 38.3967 | 39.6708 | 39.6378 | 39.901 | 40.959 | 44.0327 | 45.2953 | 44.0531 | 47.3973 | 45.9408 | 47.1682 | 48.062 | 47.6926 | 47.6926 | 47.6926 | 47.6926 | 47.6926 | 47.6926 | 47.6926 | 47.6926 | 47.6926 | 47.6926 | 47.6926 | 47.6926 | 47.6926 | 47.6926 | 47.6926 | 47.6926
Total Maximum Demand (MVA) - Option 5 Summer POE50 | 33.1528 | 35.6609 | 35.9332 | 35.8042 | 35.9326 | 35.971 | 36.1121 | 36.4113 | 36.6803 | 36.7967 | 36.6439 | 37.1157 | 37.1491 | 37.0282 | 37.2287 | 37.3387 | 37.3387 | 37.3387 | 37.3387 | 37.3387 | 37.3387 | 37.3387 | 37.3387 | 37.3387 | 37.3387 | 37.3387 | 37.3387 | 37.3387 | 37.3387 | 37.3387
Total Maximum Demand (MVA) - Option 5 Summer POE10 | 41.7337 | 44.5693 | 44.6476 | 44.5632 | 44.5849 | 44.7398 | 45.0536 | 45.6062 | 45.8942 | 46.1025 | 46.4178 | 46.8204 | 47.3072 | 47.5623 | 47.4796 | 47.5896 | 47.5896 | 47.5896 | 47.5896 | 47.5896 | 47.5896 | 47.5896 | 47.5896 | 47.5896 | 47.5896 | 47.5896 | 47.5896 | 47.5896 | 47.5896 | 47.5896
Option 6 -
Year | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Added Transfers (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Added Demand management (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Added Embedded generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Maximum Demand (MVA) - Option 6 Winter POE50 | 35.4586 | 39.1719 | 39.5657 | 40.0525 | 40.6988 | 41.3115 | 42.3823 | 45.0754 | 46.5239 | 45.4672 | 48.7387 | 49.3282 | 49.7519 | 51.7491 | 52.0742 | 52.0742 | 52.0742 | 52.0742 | 52.0742 | 52.0742 | 52.0742 | 52.0742 | 52.0742 | 52.0742 | 52.0742 | 52.0742 | 52.0742 | 52.0742 | 52.0742 | 52.0742
Total Maximum Demand (MVA) - Option 6 Winter POE10 | 38.8714 | 42.4133 | 42.7801 | 44.046 | 44.0152 | 44.2935 | 45.3822 | 48.5101 | 49.8009 | 48.5791 | 51.9542 | 50.5371 | 51.8122 | 52.731 | 52.3535 | 52.3535 | 52.3535 | 52.3535 | 52.3535 | 52.3535 | 52.3535 | 52.3535 | 52.3535 | 52.3535 | 52.3535 | 52.3535 | 52.3535 | 52.3535 | 52.3535 | 52.3535
Total Maximum Demand (MVA) - Option 6 Summer POE50 | 37.2509 | 40.0367 | 40.3167 | 40.1794 | 40.3099 | 40.3635 | 40.5354 | 40.8886 | 41.1859 | 41.3227 | 41.2007 | 41.712 | 41.7931 | 41.6971 | 41.8895 | 41.9995 | 41.9995 | 41.9995 | 41.9995 | 41.9995 | 41.9995 | 41.9995 | 41.9995 | 41.9995 | 41.9995 | 41.9995 | 41.9995 | 41.9995 | 41.9995 | 41.9995
Total Maximum Demand (MVA) - Option 6 Summer POE10 | 45.8318 | 48.9452 | 49.0311 | 48.9384 | 48.9623 | 49.1323 | 49.4768 | 50.0836 | 50.3998 | 50.6285 | 50.9747 | 51.4167 | 51.9511 | 52.2312 | 52.1404 | 52.2504 | 52.2504 | 52.2504 | 52.2504 | 52.2504 | 52.2504 | 52.2504 | 52.2504 | 52.2504 | 52.2504 | 52.2504 | 52.2504 | 52.2504 | 52.2504 | 52.2504
Option 7 -
Year | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Added Transfers (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Added Demand management (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Added Embedded generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Maximum Demand (MVA) - Option 7 Winter POE50 | 35.4586 | 39.1719 | 39.5657 | 40.0525 | 40.6988 | 41.3115 | 42.3823 | 45.0754 | 46.5239 | 45.4672 | 48.7387 | 49.3282 | 49.7519 | 51.7491 | 52.0742 | 52.0742 | 52.0742 | 52.0742 | 52.0742 | 52.0742 | 52.0742 | 52.0742 | 52.0742 | 52.0742 | 52.0742 | 52.0742 | 52.0742 | 52.0742 | 52.0742 | 52.0742
Total Maximum Demand (MVA) - Option 7 Winter POE10 | 38.8714 | 42.4133 | 42.7801 | 44.046 | 44.0152 | 44.2935 | 45.3822 | 48.5101 | 49.8009 | 48.5791 | 51.9542 | 50.5371 | 51.8122 | 52.731 | 52.3535 | 52.3535 | 52.3535 | 52.3535 | 52.3535 | 52.3535 | 52.3535 | 52.3535 | 52.3535 | 52.3535 | 52.3535 | 52.3535 | 52.3535 | 52.3535 | 52.3535 | 52.3535
Total Maximum Demand (MVA) - Option 7 Summer POE50 | 37.2509 | 40.0367 | 40.3167 | 40.1794 | 40.3099 | 40.3635 | 40.5354 | 40.8886 | 41.1859 | 41.3227 | 41.2007 | 41.712 | 41.7931 | 41.6971 | 41.8895 | 41.9995 | 41.9995 | 41.9995 | 41.9995 | 41.9995 | 41.9995 | 41.9995 | 41.9995 | 41.9995 | 41.9995 | 41.9995 | 41.9995 | 41.9995 | 41.9995 | 41.9995
Total Maximum Demand (MVA) - Option 7 Summer POE10 | 45.8318 | 48.9452 | 49.0311 | 48.9384 | 48.9623 | 49.1323 | 49.4768 | 50.0836 | 50.3998 | 50.6285 | 50.9747 | 51.4167 | 51.9511 | 52.2312 | 52.1404 | 52.2504 | 52.2504 | 52.2504 | 52.2504 | 52.2504 | 52.2504 | 52.2504 | 52.2504 | 52.2504 | 52.2504 | 52.2504 | 52.2504 | 52.2504 | 52.2504 | 52.2504
Option 8 -
Year | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Added Transfers (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Added Demand management (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Added Embedded generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Maximum Demand (MVA) - Option 8 Winter POE50 | 35.4586 | 39.1719 | 39.5657 | 40.0525 | 40.6988 | 41.3115 | 42.3823 | 45.0754 | 46.5239 | 45.4672 | 48.7387 | 49.3282 | 49.7519 | 51.7491 | 52.0742 | 52.0742 | 52.0742 | 52.0742 | 52.0742 | 52.0742 | 52.0742 | 52.0742 | 52.0742 | 52.0742 | 52.0742 | 52.0742 | 52.0742 | 52.0742 | 52.0742 | 52.0742
Total Maximum Demand (MVA) - Option 8 Winter POE10 | 38.8714 | 42.4133 | 42.7801 | 44.046 | 44.0152 | 44.2935 | 45.3822 | 48.5101 | 49.8009 | 48.5791 | 51.9542 | 50.5371 | 51.8122 | 52.731 | 52.3535 | 52.3535 | 52.3535 | 52.3535 | 52.3535 | 52.3535 | 52.3535 | 52.3535 | 52.3535 | 52.3535 | 52.3535 | 52.3535 | 52.3535 | 52.3535 | 52.3535 | 52.3535
Total Maximum Demand (MVA) - Option 8 Summer POE50 | 37.2509 | 40.0367 | 40.3167 | 40.1794 | 40.3099 | 40.3635 | 40.5354 | 40.8886 | 41.1859 | 41.3227 | 41.2007 | 41.712 | 41.7931 | 41.6971 | 41.8895 | 41.9995 | 41.9995 | 41.9995 | 41.9995 | 41.9995 | 41.9995 | 41.9995 | 41.9995 | 41.9995 | 41.9995 | 41.9995 | 41.9995 | 41.9995 | 41.9995 | 41.9995
Total Maximum Demand (MVA) - Option 8 Summer POE10 | 45.8318 | 48.9452 | 49.0311 | 48.9384 | 48.9623 | 49.1323 | 49.4768 | 50.0836 | 50.3998 | 50.6285 | 50.9747 | 51.4167 | 51.9511 | 52.2312 | 52.1404 | 52.2504 | 52.2504 | 52.2504 | 52.2504 | 52.2504 | 52.2504 | 52.2504 | 52.2504 | 52.2504 | 52.2504 | 52.2504 | 52.2504 | 52.2504 | 52.2504 | 52.2504

## Forecasted LDC
Option 1 - Do Nothing
Winter Season | [31 empty] | Winter Season
P50 | [31 empty] | P10
% of MD | Winter - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Winter - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 35.4586 | 39.1719 | 39.5657 | 40.0525 | 40.6988 | 41.3115 | 42.3823 | 45.0754 | 46.5239 | 45.4672 | 48.7387 | 49.3282 | 49.7519 | 51.7491 | 52.0742 | 52.0742 | 52.0742 | 52.0742 | 52.0742 | 52.0742 | 52.0742 | 52.0742 | 52.0742 | 52.0742 | 52.0742 | 52.0742 | 52.0742 | 52.0742 | 52.0742 | 52.0742 | 100% | 0 | 38.8714 | 42.4133 | 42.7801 | 44.046 | 44.0152 | 44.2935 | 45.3822 | 48.5101 | 49.8009 | 48.5791 | 51.9542 | 50.5371 | 51.8122 | 52.731 | 52.3535 | 52.3535 | 52.3535 | 52.3535 | 52.3535 | 52.3535 | 52.3535 | 52.3535 | 52.3535 | 52.3535 | 52.3535 | 52.3535 | 52.3535 | 52.3535 | 52.3535 | 52.3535
99% | 0.2972 | 35.104 | 38.7802 | 39.17 | 39.652 | 40.2918 | 40.8984 | 41.9585 | 44.6246 | 46.0587 | 45.0125 | 48.2513 | 48.8349 | 49.2544 | 51.2316 | 51.5535 | 51.5535 | 51.5535 | 51.5535 | 51.5535 | 51.5535 | 51.5535 | 51.5535 | 51.5535 | 51.5535 | 51.5535 | 51.5535 | 51.5535 | 51.5535 | 51.5535 | 51.5535 | 99% | 0.2972 | 38.4827 | 41.9892 | 42.3523 | 43.6056 | 43.575 | 43.8506 | 44.9284 | 48.025 | 49.3029 | 48.0933 | 51.4346 | 50.0317 | 51.294 | 52.2037 | 51.83 | 51.83 | 51.83 | 51.83 | 51.83 | 51.83 | 51.83 | 51.83 | 51.83 | 51.83 | 51.83 | 51.83 | 51.83 | 51.83 | 51.83 | 51.83
98% | 0.2972 | 34.7495 | 38.3885 | 38.7744 | 39.2514 | 39.8848 | 40.4853 | 41.5347 | 44.1739 | 45.5935 | 44.5578 | 47.764 | 48.3416 | 48.7568 | 50.7141 | 51.0327 | 51.0327 | 51.0327 | 51.0327 | 51.0327 | 51.0327 | 51.0327 | 51.0327 | 51.0327 | 51.0327 | 51.0327 | 51.0327 | 51.0327 | 51.0327 | 51.0327 | 51.0327 | 98% | 0.2972 | 38.0939 | 41.5651 | 41.9245 | 43.1651 | 43.1349 | 43.4077 | 44.4746 | 47.5399 | 48.8049 | 47.6075 | 50.9151 | 49.5264 | 50.7759 | 51.6764 | 51.3064 | 51.3064 | 51.3064 | 51.3064 | 51.3064 | 51.3064 | 51.3064 | 51.3064 | 51.3064 | 51.3064 | 51.3064 | 51.3064 | 51.3064 | 51.3064 | 51.3064 | 51.3064
97% | 0.2972 | 34.3949 | 37.9968 | 38.3787 | 38.8509 | 39.4778 | 40.0722 | 41.1108 | 43.7231 | 45.1282 | 44.1032 | 47.2766 | 47.8483 | 48.2593 | 50.1966 | 50.512 | 50.512 | 50.512 | 50.512 | 50.512 | 50.512 | 50.512 | 50.512 | 50.512 | 50.512 | 50.512 | 50.512 | 50.512 | 50.512 | 50.512 | 50.512 | 97% | 0.2972 | 37.7052 | 41.1409 | 41.4967 | 42.7246 | 42.6947 | 42.9647 | 44.0208 | 47.0548 | 48.3068 | 47.1217 | 50.3955 | 49.021 | 50.2578 | 51.1491 | 50.7829 | 50.7829 | 50.7829 | 50.7829 | 50.7829 | 50.7829 | 50.7829 | 50.7829 | 50.7829 | 50.7829 | 50.7829 | 50.7829 | 50.7829 | 50.7829 | 50.7829 | 50.7829
95% | 1.486 | 33.6857 | 37.2134 | 37.5874 | 38.0499 | 38.6639 | 39.2459 | 40.2632 | 42.8216 | 44.1977 | 43.1938 | 46.3018 | 46.8618 | 47.2643 | 49.1617 | 49.4705 | 49.4705 | 49.4705 | 49.4705 | 49.4705 | 49.4705 | 49.4705 | 49.4705 | 49.4705 | 49.4705 | 49.4705 | 49.4705 | 49.4705 | 49.4705 | 49.4705 | 49.4705 | 95% | 1.486 | 36.9278 | 40.2927 | 40.6411 | 41.8437 | 41.8144 | 42.0789 | 43.1131 | 46.0846 | 47.3108 | 46.1501 | 49.3565 | 48.0103 | 49.2216 | 50.0944 | 49.7358 | 49.7358 | 49.7358 | 49.7358 | 49.7358 | 49.7358 | 49.7358 | 49.7358 | 49.7358 | 49.7358 | 49.7358 | 49.7358 | 49.7358 | 49.7358 | 49.7358 | 49.7358
90% | 8.6188 | 31.9128 | 35.2548 | 35.6091 | 36.0472 | 36.6289 | 37.1804 | 38.1441 | 40.5679 | 41.8715 | 40.9205 | 43.8649 | 44.3954 | 44.7767 | 46.5742 | 46.8668 | 46.8668 | 46.8668 | 46.8668 | 46.8668 | 46.8668 | 46.8668 | 46.8668 | 46.8668 | 46.8668 | 46.8668 | 46.8668 | 46.8668 | 46.8668 | 46.8668 | 46.8668 | 90% | 8.6188 | 34.9842 | 38.172 | 38.5021 | 39.6414 | 39.6137 | 39.8642 | 40.844 | 43.6591 | 44.8208 | 43.7212 | 46.7587 | 45.4834 | 46.6309 | 47.4579 | 47.1181 | 47.1181 | 47.1181 | 47.1181 | 47.1181 | 47.1181 | 47.1181 | 47.1181 | 47.1181 | 47.1181 | 47.1181 | 47.1181 | 47.1181 | 47.1181 | 47.1181 | 47.1181
85% | 40.1218 | 30.1398 | 33.2962 | 33.6308 | 34.0446 | 34.594 | 35.1148 | 36.025 | 38.3141 | 39.5453 | 38.6471 | 41.4279 | 41.9289 | 42.2891 | 43.9867 | 44.2631 | 44.2631 | 44.2631 | 44.2631 | 44.2631 | 44.2631 | 44.2631 | 44.2631 | 44.2631 | 44.2631 | 44.2631 | 44.2631 | 44.2631 | 44.2631 | 44.2631 | 44.2631 | 85% | 40.1218 | 33.0407 | 36.0513 | 36.3631 | 37.4391 | 37.4129 | 37.6495 | 38.5749 | 41.2336 | 42.3307 | 41.2922 | 44.161 | 42.9565 | 44.0403 | 44.8213 | 44.5005 | 44.5005 | 44.5005 | 44.5005 | 44.5005 | 44.5005 | 44.5005 | 44.5005 | 44.5005 | 44.5005 | 44.5005 | 44.5005 | 44.5005 | 44.5005 | 44.5005 | 44.5005
80% | 93.0231 | 28.3669 | 31.3376 | 31.6526 | 32.042 | 32.559 | 33.0492 | 33.9058 | 36.0603 | 37.2191 | 36.3737 | 38.991 | 39.4625 | 39.8015 | 41.3993 | 41.6594 | 41.6594 | 41.6594 | 41.6594 | 41.6594 | 41.6594 | 41.6594 | 41.6594 | 41.6594 | 41.6594 | 41.6594 | 41.6594 | 41.6594 | 41.6594 | 41.6594 | 41.6594 | 80% | 93.0231 | 31.0971 | 33.9307 | 34.2241 | 35.2368 | 35.2121 | 35.4348 | 36.3058 | 38.8081 | 39.8407 | 38.8633 | 41.5633 | 40.4297 | 41.4497 | 42.1848 | 41.8828 | 41.8828 | 41.8828 | 41.8828 | 41.8828 | 41.8828 | 41.8828 | 41.8828 | 41.8828 | 41.8828 | 41.8828 | 41.8828 | 41.8828 | 41.8828 | 41.8828 | 41.8828
75% | 197.0426 | 26.594 | 29.379 | 29.6743 | 30.0394 | 30.5241 | 30.9836 | 31.7867 | 33.8065 | 34.8929 | 34.1004 | 36.554 | 36.9961 | 37.3139 | 38.8118 | 39.0556 | 39.0556 | 39.0556 | 39.0556 | 39.0556 | 39.0556 | 39.0556 | 39.0556 | 39.0556 | 39.0556 | 39.0556 | 39.0556 | 39.0556 | 39.0556 | 39.0556 | 39.0556 | 75% | 197.0426 | 29.1535 | 31.81 | 32.0851 | 33.0345 | 33.0114 | 33.2201 | 34.0367 | 36.3826 | 37.3507 | 36.4343 | 38.9656 | 37.9028 | 38.8591 | 39.5482 | 39.2651 | 39.2651 | 39.2651 | 39.2651 | 39.2651 | 39.2651 | 39.2651 | 39.2651 | 39.2651 | 39.2651 | 39.2651 | 39.2651 | 39.2651 | 39.2651 | 39.2651 | 39.2651
70% | 378.0365 | 24.821 | 27.4204 | 27.696 | 28.0367 | 28.4892 | 28.9181 | 29.6676 | 31.5528 | 32.5668 | 31.827 | 34.1171 | 34.5297 | 34.8263 | 36.2244 | 36.4519 | 36.4519 | 36.4519 | 36.4519 | 36.4519 | 36.4519 | 36.4519 | 36.4519 | 36.4519 | 36.4519 | 36.4519 | 36.4519 | 36.4519 | 36.4519 | 36.4519 | 36.4519 | 70% | 378.0365 | 27.21 | 29.6893 | 29.9461 | 30.8322 | 30.8106 | 31.0055 | 31.7676 | 33.9571 | 34.8606 | 34.0054 | 36.3679 | 35.376 | 36.2685 | 36.9117 | 36.6474 | 36.6474 | 36.6474 | 36.6474 | 36.6474 | 36.6474 | 36.6474 | 36.6474 | 36.6474 | 36.6474 | 36.6474 | 36.6474 | 36.6474 | 36.6474 | 36.6474 | 36.6474
65% | 616.0926 | 23.0481 | 25.4618 | 25.7177 | 26.0341 | 26.4542 | 26.8525 | 27.5485 | 29.299 | 30.2406 | 29.5537 | 31.6802 | 32.0633 | 32.3387 | 33.6369 | 33.8482 | 33.8482 | 33.8482 | 33.8482 | 33.8482 | 33.8482 | 33.8482 | 33.8482 | 33.8482 | 33.8482 | 33.8482 | 33.8482 | 33.8482 | 33.8482 | 33.8482 | 33.8482 | 65% | 616.0926 | 25.2664 | 27.5687 | 27.8071 | 28.6299 | 28.6099 | 28.7908 | 29.4985 | 31.5316 | 32.3706 | 31.5764 | 33.7702 | 32.8491 | 33.6779 | 34.2751 | 34.0298 | 34.0298 | 34.0298 | 34.0298 | 34.0298 | 34.0298 | 34.0298 | 34.0298 | 34.0298 | 34.0298 | 34.0298 | 34.0298 | 34.0298 | 34.0298 | 34.0298 | 34.0298
60% | 934.9866 | 21.2752 | 23.5032 | 23.7394 | 24.0315 | 24.4193 | 24.7869 | 25.4294 | 27.0452 | 27.9144 | 27.2803 | 29.2432 | 29.5969 | 29.8511 | 31.0495 | 31.2445 | 31.2445 | 31.2445 | 31.2445 | 31.2445 | 31.2445 | 31.2445 | 31.2445 | 31.2445 | 31.2445 | 31.2445 | 31.2445 | 31.2445 | 31.2445 | 31.2445 | 31.2445 | 60% | 934.9866 | 23.3228 | 25.448 | 25.6681 | 26.4276 | 26.4091 | 26.5761 | 27.2293 | 29.1061 | 29.8805 | 29.1474 | 31.1725 | 30.3223 | 31.0873 | 31.6386 | 31.4121 | 31.4121 | 31.4121 | 31.4121 | 31.4121 | 31.4121 | 31.4121 | 31.4121 | 31.4121 | 31.4121 | 31.4121 | 31.4121 | 31.4121 | 31.4121 | 31.4121 | 31.4121
55% | 1310.9428 | 19.5022 | 21.5446 | 21.7611 | 22.0289 | 22.3843 | 22.7213 | 23.3103 | 24.7915 | 25.5882 | 25.0069 | 26.8063 | 27.1305 | 27.3635 | 28.462 | 28.6408 | 28.6408 | 28.6408 | 28.6408 | 28.6408 | 28.6408 | 28.6408 | 28.6408 | 28.6408 | 28.6408 | 28.6408 | 28.6408 | 28.6408 | 28.6408 | 28.6408 | 28.6408 | 55% | 1310.9428 | 21.3793 | 23.3273 | 23.5291 | 24.2253 | 24.2083 | 24.3614 | 24.9602 | 26.6806 | 27.3905 | 26.7185 | 28.5748 | 27.7954 | 28.4967 | 29.002 | 28.7944 | 28.7944 | 28.7944 | 28.7944 | 28.7944 | 28.7944 | 28.7944 | 28.7944 | 28.7944 | 28.7944 | 28.7944 | 28.7944 | 28.7944 | 28.7944 | 28.7944 | 28.7944
50% | 1730.2899 | 17.7293 | 19.586 | 19.7828 | 20.0262 | 20.3494 | 20.6558 | 21.1912 | 22.5377 | 23.262 | 22.7336 | 24.3694 | 24.6641 | 24.8759 | 25.8746 | 26.0371 | 26.0371 | 26.0371 | 26.0371 | 26.0371 | 26.0371 | 26.0371 | 26.0371 | 26.0371 | 26.0371 | 26.0371 | 26.0371 | 26.0371 | 26.0371 | 26.0371 | 26.0371 | 50% | 1730.2899 | 19.4357 | 21.2067 | 21.3901 | 22.023 | 22.0076 | 22.1468 | 22.6911 | 24.2551 | 24.9004 | 24.2895 | 25.9771 | 25.2686 | 25.9061 | 26.3655 | 26.1767 | 26.1767 | 26.1767 | 26.1767 | 26.1767 | 26.1767 | 26.1767 | 26.1767 | 26.1767 | 26.1767 | 26.1767 | 26.1767 | 26.1767 | 26.1767 | 26.1767 | 26.1767
45% | 2168.0633 | 15.9564 | 17.6274 | 17.8046 | 18.0236 | 18.3145 | 18.5902 | 19.072 | 20.2839 | 20.9358 | 20.4602 | 21.9324 | 22.1977 | 22.3883 | 23.2871 | 23.4334 | 23.4334 | 23.4334 | 23.4334 | 23.4334 | 23.4334 | 23.4334 | 23.4334 | 23.4334 | 23.4334 | 23.4334 | 23.4334 | 23.4334 | 23.4334 | 23.4334 | 23.4334 | 45% | 2168.0633 | 17.4921 | 19.086 | 19.2511 | 19.8207 | 19.8068 | 19.9321 | 20.422 | 21.8296 | 22.4104 | 21.8606 | 23.3794 | 22.7417 | 23.3155 | 23.7289 | 23.5591 | 23.5591 | 23.5591 | 23.5591 | 23.5591 | 23.5591 | 23.5591 | 23.5591 | 23.5591 | 23.5591 | 23.5591 | 23.5591 | 23.5591 | 23.5591 | 23.5591 | 23.5591
40% | 2609.7004 | 14.1835 | 15.6688 | 15.8263 | 16.021 | 16.2795 | 16.5246 | 16.9529 | 18.0302 | 18.6096 | 18.1869 | 19.4955 | 19.7313 | 19.9008 | 20.6996 | 20.8297 | 20.8297 | 20.8297 | 20.8297 | 20.8297 | 20.8297 | 20.8297 | 20.8297 | 20.8297 | 20.8297 | 20.8297 | 20.8297 | 20.8297 | 20.8297 | 20.8297 | 20.8297 | 40% | 2609.7004 | 15.5485 | 16.9653 | 17.1121 | 17.6184 | 17.6061 | 17.7174 | 18.1529 | 19.404 | 19.9203 | 19.4316 | 20.7817 | 20.2148 | 20.7249 | 21.0924 | 20.9414 | 20.9414 | 20.9414 | 20.9414 | 20.9414 | 20.9414 | 20.9414 | 20.9414 | 20.9414 | 20.9414 | 20.9414 | 20.9414 | 20.9414 | 20.9414 | 20.9414 | 20.9414
35% | 2998.1389 | 12.4105 | 13.7102 | 13.848 | 14.0184 | 14.2446 | 14.459 | 14.8338 | 15.7764 | 16.2834 | 15.9135 | 17.0586 | 17.2649 | 17.4132 | 18.1122 | 18.226 | 18.226 | 18.226 | 18.226 | 18.226 | 18.226 | 18.226 | 18.226 | 18.226 | 18.226 | 18.226 | 18.226 | 18.226 | 18.226 | 18.226 | 18.226 | 35% | 2998.1389 | 13.605 | 14.8447 | 14.973 | 15.4161 | 15.4053 | 15.5027 | 15.8838 | 16.9785 | 17.4303 | 17.0027 | 18.184 | 17.688 | 18.1343 | 18.4558 | 18.3237 | 18.3237 | 18.3237 | 18.3237 | 18.3237 | 18.3237 | 18.3237 | 18.3237 | 18.3237 | 18.3237 | 18.3237 | 18.3237 | 18.3237 | 18.3237 | 18.3237 | 18.3237
30% | 3309.3057 | 10.6376 | 11.7516 | 11.8697 | 12.0157 | 12.2096 | 12.3935 | 12.7147 | 13.5226 | 13.9572 | 13.6402 | 14.6216 | 14.7985 | 14.9256 | 15.5247 | 15.6223 | 15.6223 | 15.6223 | 15.6223 | 15.6223 | 15.6223 | 15.6223 | 15.6223 | 15.6223 | 15.6223 | 15.6223 | 15.6223 | 15.6223 | 15.6223 | 15.6223 | 15.6223 | 30% | 3309.3057 | 11.6614 | 12.724 | 12.834 | 13.2138 | 13.2046 | 13.2881 | 13.6147 | 14.553 | 14.9403 | 14.5737 | 15.5862 | 15.1611 | 15.5436 | 15.8193 | 15.706 | 15.706 | 15.706 | 15.706 | 15.706 | 15.706 | 15.706 | 15.706 | 15.706 | 15.706 | 15.706 | 15.706 | 15.706 | 15.706 | 15.706 | 15.706
25% | 3537.8514 | 8.8647 | 9.793 | 9.8914 | 10.0131 | 10.1747 | 10.3279 | 10.5956 | 11.2688 | 11.631 | 11.3668 | 12.1847 | 12.332 | 12.438 | 12.9373 | 13.0185 | 13.0185 | 13.0185 | 13.0185 | 13.0185 | 13.0185 | 13.0185 | 13.0185 | 13.0185 | 13.0185 | 13.0185 | 13.0185 | 13.0185 | 13.0185 | 13.0185 | 13.0185 | 25% | 3537.8514 | 9.7178 | 10.6033 | 10.695 | 11.0115 | 11.0038 | 11.0734 | 11.3456 | 12.1275 | 12.4502 | 12.1448 | 12.9885 | 12.6343 | 12.953 | 13.1827 | 13.0884 | 13.0884 | 13.0884 | 13.0884 | 13.0884 | 13.0884 | 13.0884 | 13.0884 | 13.0884 | 13.0884 | 13.0884 | 13.0884 | 13.0884 | 13.0884 | 13.0884 | 13.0884
20% | 3731.0305 | 7.0917 | 7.8344 | 7.9131 | 8.0105 | 8.1398 | 8.2623 | 8.4765 | 9.0151 | 9.3048 | 9.0934 | 9.7477 | 9.8656 | 9.9504 | 10.3498 | 10.4148 | 10.4148 | 10.4148 | 10.4148 | 10.4148 | 10.4148 | 10.4148 | 10.4148 | 10.4148 | 10.4148 | 10.4148 | 10.4148 | 10.4148 | 10.4148 | 10.4148 | 10.4148 | 20% | 3731.0305 | 7.7743 | 8.4827 | 8.556 | 8.8092 | 8.803 | 8.8587 | 9.0764 | 9.702 | 9.9602 | 9.7158 | 10.3908 | 10.1074 | 10.3624 | 10.5462 | 10.4707 | 10.4707 | 10.4707 | 10.4707 | 10.4707 | 10.4707 | 10.4707 | 10.4707 | 10.4707 | 10.4707 | 10.4707 | 10.4707 | 10.4707 | 10.4707 | 10.4707 | 10.4707
15% | 3910.2412 | 5.3188 | 5.8758 | 5.9349 | 6.0079 | 6.1048 | 6.1967 | 6.3573 | 6.7613 | 6.9786 | 6.8201 | 7.3108 | 7.3992 | 7.4628 | 7.7624 | 7.8111 | 7.8111 | 7.8111 | 7.8111 | 7.8111 | 7.8111 | 7.8111 | 7.8111 | 7.8111 | 7.8111 | 7.8111 | 7.8111 | 7.8111 | 7.8111 | 7.8111 | 7.8111 | 15% | 3910.2412 | 5.8307 | 6.362 | 6.417 | 6.6069 | 6.6023 | 6.644 | 6.8073 | 7.2765 | 7.4701 | 7.2869 | 7.7931 | 7.5806 | 7.7718 | 7.9096 | 7.853 | 7.853 | 7.853 | 7.853 | 7.853 | 7.853 | 7.853 | 7.853 | 7.853 | 7.853 | 7.853 | 7.853 | 7.853 | 7.853 | 7.853 | 7.853
10% | 4075.1864 | 3.5459 | 3.9172 | 3.9566 | 4.0052 | 4.0699 | 4.1312 | 4.2382 | 4.5075 | 4.6524 | 4.5467 | 4.8739 | 4.9328 | 4.9752 | 5.1749 | 5.2074 | 5.2074 | 5.2074 | 5.2074 | 5.2074 | 5.2074 | 5.2074 | 5.2074 | 5.2074 | 5.2074 | 5.2074 | 5.2074 | 5.2074 | 5.2074 | 5.2074 | 5.2074 | 10% | 4075.1864 | 3.8871 | 4.2413 | 4.278 | 4.4046 | 4.4015 | 4.4294 | 4.5382 | 4.851 | 4.9801 | 4.8579 | 5.1954 | 5.0537 | 5.1812 | 5.2731 | 5.2353 | 5.2353 | 5.2353 | 5.2353 | 5.2353 | 5.2353 | 5.2353 | 5.2353 | 5.2353 | 5.2353 | 5.2353 | 5.2353 | 5.2353 | 5.2353 | 5.2353 | 5.2353
5% | 4251.7223 | 1.7729 | 1.9586 | 1.9783 | 2.0026 | 2.0349 | 2.0656 | 2.1191 | 2.2538 | 2.3262 | 2.2734 | 2.4369 | 2.4664 | 2.4876 | 2.5875 | 2.6037 | 2.6037 | 2.6037 | 2.6037 | 2.6037 | 2.6037 | 2.6037 | 2.6037 | 2.6037 | 2.6037 | 2.6037 | 2.6037 | 2.6037 | 2.6037 | 2.6037 | 2.6037 | 5% | 4251.7223 | 1.9436 | 2.1207 | 2.139 | 2.2023 | 2.2008 | 2.2147 | 2.2691 | 2.4255 | 2.49 | 2.429 | 2.5977 | 2.5269 | 2.5906 | 2.6365 | 2.6177 | 2.6177 | 2.6177 | 2.6177 | 2.6177 | 2.6177 | 2.6177 | 2.6177 | 2.6177 | 2.6177 | 2.6177 | 2.6177 | 2.6177 | 2.6177 | 2.6177 | 2.6177
9.992e-14% | 4391.7028 | 3.543e-14 | 3.9141e-14 | 3.9534e-14 | 4.002e-14 | 4.0666e-14 | 4.1279e-14 | 4.2348e-14 | 4.5039e-14 | 4.6487e-14 | 4.5431e-14 | 4.87e-14 | 4.9289e-14 | 4.9712e-14 | 5.1708e-14 | 5.2033e-14 | 5.2033e-14 | 5.2033e-14 | 5.2033e-14 | 5.2033e-14 | 5.2033e-14 | 5.2033e-14 | 5.2033e-14 | 5.2033e-14 | 5.2033e-14 | 5.2033e-14 | 5.2033e-14 | 5.2033e-14 | 5.2033e-14 | 5.2033e-14 | 5.2033e-14 | 9.992e-14% | 4391.7028 | 3.884e-14 | 4.2379e-14 | 4.2746e-14 | 4.4011e-14 | 4.398e-14 | 4.4258e-14 | 4.5346e-14 | 4.8471e-14 | 4.9761e-14 | 4.854e-14 | 5.1913e-14 | 5.0497e-14 | 5.1771e-14 | 5.2689e-14 | 5.2312e-14 | 5.2312e-14 | 5.2312e-14 | 5.2312e-14 | 5.2312e-14 | 5.2312e-14 | 5.2312e-14 | 5.2312e-14 | 5.2312e-14 | 5.2312e-14 | 5.2312e-14 | 5.2312e-14 | 5.2312e-14 | 5.2312e-14 | 5.2312e-14 | 5.2312e-14
Summer Season | [31 empty] | Summer Season
P50 | [31 empty] | P10
% of MD | Summer - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Summer - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 37.2509 | 40.0367 | 40.3167 | 40.1794 | 40.3099 | 40.3635 | 40.5354 | 40.8886 | 41.1859 | 41.3227 | 41.2007 | 41.712 | 41.7931 | 41.6971 | 41.8895 | 41.9995 | 41.9995 | 41.9995 | 41.9995 | 41.9995 | 41.9995 | 41.9995 | 41.9995 | 41.9995 | 41.9995 | 41.9995 | 41.9995 | 41.9995 | 41.9995 | 41.9995 | 100% | 0 | 45.8318 | 48.9452 | 49.0311 | 48.9384 | 48.9623 | 49.1323 | 49.4768 | 50.0836 | 50.3998 | 50.6285 | 50.9747 | 51.4167 | 51.9511 | 52.2312 | 52.1404 | 52.2504 | 52.2504 | 52.2504 | 52.2504 | 52.2504 | 52.2504 | 52.2504 | 52.2504 | 52.2504 | 52.2504 | 52.2504 | 52.2504 | 52.2504 | 52.2504 | 52.2504
99% | 0.37816 | 36.8784 | 39.6364 | 39.9135 | 39.7777 | 39.9068 | 39.9599 | 40.13 | 40.4798 | 40.774 | 40.9094 | 40.7887 | 41.2949 | 41.3751 | 41.2801 | 41.4706 | 41.5795 | 41.5795 | 41.5795 | 41.5795 | 41.5795 | 41.5795 | 41.5795 | 41.5795 | 41.5795 | 41.5795 | 41.5795 | 41.5795 | 41.5795 | 41.5795 | 41.5795 | 99% | 0 | 45.3735 | 48.4557 | 48.5408 | 48.4491 | 48.4726 | 48.6409 | 48.982 | 49.5828 | 49.8958 | 50.1222 | 50.465 | 50.9025 | 51.4316 | 51.7089 | 51.619 | 51.7279 | 51.7279 | 51.7279 | 51.7279 | 51.7279 | 51.7279 | 51.7279 | 51.7279 | 51.7279 | 51.7279 | 51.7279 | 51.7279 | 51.7279 | 51.7279 | 51.7279
98% | 0.37816 | 36.5059 | 39.236 | 39.5103 | 39.3759 | 39.5037 | 39.5563 | 39.7246 | 40.0709 | 40.3621 | 40.4962 | 40.3767 | 40.8777 | 40.9572 | 40.8632 | 41.0517 | 41.1595 | 41.1595 | 41.1595 | 41.1595 | 41.1595 | 41.1595 | 41.1595 | 41.1595 | 41.1595 | 41.1595 | 41.1595 | 41.1595 | 41.1595 | 41.1595 | 41.1595 | 98% | 0 | 44.9152 | 47.9662 | 48.0504 | 47.9597 | 47.983 | 48.1496 | 48.4873 | 49.0819 | 49.3918 | 49.6159 | 49.9552 | 50.3883 | 50.9121 | 51.1866 | 51.0976 | 51.2054 | 51.2054 | 51.2054 | 51.2054 | 51.2054 | 51.2054 | 51.2054 | 51.2054 | 51.2054 | 51.2054 | 51.2054 | 51.2054 | 51.2054 | 51.2054 | 51.2054
97% | 0.37816 | 36.1334 | 38.8356 | 39.1072 | 38.9741 | 39.1006 | 39.1526 | 39.3193 | 39.662 | 39.9503 | 40.083 | 39.9647 | 40.4606 | 40.5393 | 40.4462 | 40.6328 | 40.7395 | 40.7395 | 40.7395 | 40.7395 | 40.7395 | 40.7395 | 40.7395 | 40.7395 | 40.7395 | 40.7395 | 40.7395 | 40.7395 | 40.7395 | 40.7395 | 40.7395 | 97% | 0.37816 | 44.4569 | 47.4768 | 47.5601 | 47.4703 | 47.4934 | 47.6583 | 47.9925 | 48.5811 | 48.8878 | 49.1097 | 49.4455 | 49.8742 | 50.3926 | 50.6643 | 50.5762 | 50.6829 | 50.6829 | 50.6829 | 50.6829 | 50.6829 | 50.6829 | 50.6829 | 50.6829 | 50.6829 | 50.6829 | 50.6829 | 50.6829 | 50.6829 | 50.6829 | 50.6829
95% | 0.75633 | 35.3884 | 38.0349 | 38.3008 | 38.1705 | 38.2944 | 38.3454 | 38.5086 | 38.8442 | 39.1266 | 39.2565 | 39.1407 | 39.6264 | 39.7034 | 39.6123 | 39.7951 | 39.8996 | 39.8996 | 39.8996 | 39.8996 | 39.8996 | 39.8996 | 39.8996 | 39.8996 | 39.8996 | 39.8996 | 39.8996 | 39.8996 | 39.8996 | 39.8996 | 39.8996 | 95% | 0.37816 | 43.5402 | 46.4979 | 46.5795 | 46.4915 | 46.5141 | 46.6757 | 47.003 | 47.5794 | 47.8798 | 48.0971 | 48.426 | 48.8458 | 49.3536 | 49.6196 | 49.5334 | 49.6379 | 49.6379 | 49.6379 | 49.6379 | 49.6379 | 49.6379 | 49.6379 | 49.6379 | 49.6379 | 49.6379 | 49.6379 | 49.6379 | 49.6379 | 49.6379 | 49.6379
90% | 9.0759 | 33.5258 | 36.0331 | 36.285 | 36.1615 | 36.2789 | 36.3272 | 36.4818 | 36.7998 | 37.0673 | 37.1904 | 37.0807 | 37.5408 | 37.6138 | 37.5274 | 37.7006 | 37.7996 | 37.7996 | 37.7996 | 37.7996 | 37.7996 | 37.7996 | 37.7996 | 37.7996 | 37.7996 | 37.7996 | 37.7996 | 37.7996 | 37.7996 | 37.7996 | 37.7996 | 90% | 0.75633 | 41.2486 | 44.0506 | 44.128 | 44.0446 | 44.066 | 44.219 | 44.5291 | 45.0752 | 45.3598 | 45.5657 | 45.8772 | 46.275 | 46.756 | 47.0081 | 46.9264 | 47.0254 | 47.0254 | 47.0254 | 47.0254 | 47.0254 | 47.0254 | 47.0254 | 47.0254 | 47.0254 | 47.0254 | 47.0254 | 47.0254 | 47.0254 | 47.0254 | 47.0254
85% | 40.4636 | 31.6633 | 34.0312 | 34.2692 | 34.1525 | 34.2634 | 34.309 | 34.455 | 34.7554 | 35.008 | 35.1243 | 35.0206 | 35.4552 | 35.5241 | 35.4425 | 35.6061 | 35.6996 | 35.6996 | 35.6996 | 35.6996 | 35.6996 | 35.6996 | 35.6996 | 35.6996 | 35.6996 | 35.6996 | 35.6996 | 35.6996 | 35.6996 | 35.6996 | 35.6996 | 85% | 1.1345 | 38.957 | 41.6034 | 41.6764 | 41.5977 | 41.6179 | 41.7624 | 42.0553 | 42.5711 | 42.8398 | 43.0342 | 43.3285 | 43.7042 | 44.1585 | 44.3965 | 44.3193 | 44.4128 | 44.4128 | 44.4128 | 44.4128 | 44.4128 | 44.4128 | 44.4128 | 44.4128 | 44.4128 | 44.4128 | 44.4128 | 44.4128 | 44.4128 | 44.4128 | 44.4128
80% | 94.5411 | 29.8007 | 32.0294 | 32.2533 | 32.1436 | 32.2479 | 32.2908 | 32.4283 | 32.7109 | 32.9487 | 33.0581 | 32.9606 | 33.3696 | 33.4345 | 33.3577 | 33.5116 | 33.5996 | 33.5996 | 33.5996 | 33.5996 | 33.5996 | 33.5996 | 33.5996 | 33.5996 | 33.5996 | 33.5996 | 33.5996 | 33.5996 | 33.5996 | 33.5996 | 33.5996 | 80% | 2.6471 | 36.6655 | 39.1561 | 39.2249 | 39.1508 | 39.1698 | 39.3058 | 39.5815 | 40.0669 | 40.3198 | 40.5028 | 40.7798 | 41.1333 | 41.5609 | 41.785 | 41.7123 | 41.8003 | 41.8003 | 41.8003 | 41.8003 | 41.8003 | 41.8003 | 41.8003 | 41.8003 | 41.8003 | 41.8003 | 41.8003 | 41.8003 | 41.8003 | 41.8003 | 41.8003
75% | 197.0236 | 27.9382 | 30.0275 | 30.2375 | 30.1346 | 30.2324 | 30.2726 | 30.4015 | 30.6665 | 30.8894 | 30.992 | 30.9005 | 31.284 | 31.3448 | 31.2728 | 31.4172 | 31.4997 | 31.4997 | 31.4997 | 31.4997 | 31.4997 | 31.4997 | 31.4997 | 31.4997 | 31.4997 | 31.4997 | 31.4997 | 31.4997 | 31.4997 | 31.4997 | 31.4997 | 75% | 3.4035 | 34.3739 | 36.7089 | 36.7733 | 36.7038 | 36.7217 | 36.8492 | 37.1076 | 37.5627 | 37.7998 | 37.9714 | 38.231 | 38.5625 | 38.9633 | 39.1734 | 39.1053 | 39.1878 | 39.1878 | 39.1878 | 39.1878 | 39.1878 | 39.1878 | 39.1878 | 39.1878 | 39.1878 | 39.1878 | 39.1878 | 39.1878 | 39.1878 | 39.1878 | 39.1878
70% | 336.9444 | 26.0756 | 28.0257 | 28.2217 | 28.1256 | 28.2169 | 28.2545 | 28.3747 | 28.6221 | 28.8301 | 28.9259 | 28.8405 | 29.1984 | 29.2552 | 29.188 | 29.3227 | 29.3997 | 29.3997 | 29.3997 | 29.3997 | 29.3997 | 29.3997 | 29.3997 | 29.3997 | 29.3997 | 29.3997 | 29.3997 | 29.3997 | 29.3997 | 29.3997 | 29.3997 | 70% | 5.6725 | 32.0823 | 34.2616 | 34.3217 | 34.2569 | 34.2736 | 34.3926 | 34.6338 | 35.0585 | 35.2798 | 35.44 | 35.6823 | 35.9917 | 36.3658 | 36.5618 | 36.4983 | 36.5753 | 36.5753 | 36.5753 | 36.5753 | 36.5753 | 36.5753 | 36.5753 | 36.5753 | 36.5753 | 36.5753 | 36.5753 | 36.5753 | 36.5753 | 36.5753 | 36.5753
65% | 521.4885 | 24.2131 | 26.0239 | 26.2058 | 26.1166 | 26.2014 | 26.2363 | 26.348 | 26.5776 | 26.7708 | 26.8597 | 26.7805 | 27.1128 | 27.1655 | 27.1031 | 27.2282 | 27.2997 | 27.2997 | 27.2997 | 27.2997 | 27.2997 | 27.2997 | 27.2997 | 27.2997 | 27.2997 | 27.2997 | 27.2997 | 27.2997 | 27.2997 | 27.2997 | 27.2997 | 65% | 6.4288 | 29.7907 | 31.8143 | 31.8702 | 31.81 | 31.8255 | 31.936 | 32.1599 | 32.5543 | 32.7599 | 32.9085 | 33.1336 | 33.4208 | 33.7682 | 33.9503 | 33.8913 | 33.9628 | 33.9628 | 33.9628 | 33.9628 | 33.9628 | 33.9628 | 33.9628 | 33.9628 | 33.9628 | 33.9628 | 33.9628 | 33.9628 | 33.9628 | 33.9628 | 33.9628
60% | 812.675 | 22.3505 | 24.022 | 24.19 | 24.1077 | 24.186 | 24.2181 | 24.3212 | 24.5332 | 24.7115 | 24.7936 | 24.7204 | 25.0272 | 25.0758 | 25.0183 | 25.1337 | 25.1997 | 25.1997 | 25.1997 | 25.1997 | 25.1997 | 25.1997 | 25.1997 | 25.1997 | 25.1997 | 25.1997 | 25.1997 | 25.1997 | 25.1997 | 25.1997 | 25.1997 | 60% | 11.3449 | 27.4991 | 29.3671 | 29.4186 | 29.3631 | 29.3774 | 29.4794 | 29.6861 | 30.0502 | 30.2399 | 30.3771 | 30.5848 | 30.85 | 31.1707 | 31.3387 | 31.2842 | 31.3502 | 31.3502 | 31.3502 | 31.3502 | 31.3502 | 31.3502 | 31.3502 | 31.3502 | 31.3502 | 31.3502 | 31.3502 | 31.3502 | 31.3502 | 31.3502 | 31.3502
55% | 1202.1843 | 20.488 | 22.0202 | 22.1742 | 22.0987 | 22.1705 | 22.1999 | 22.2944 | 22.4888 | 22.6522 | 22.7275 | 22.6604 | 22.9416 | 22.9862 | 22.9334 | 23.0392 | 23.0997 | 23.0997 | 23.0997 | 23.0997 | 23.0997 | 23.0997 | 23.0997 | 23.0997 | 23.0997 | 23.0997 | 23.0997 | 23.0997 | 23.0997 | 23.0997 | 23.0997 | 55% | 35.5474 | 25.2075 | 26.9198 | 26.9671 | 26.9161 | 26.9292 | 27.0227 | 27.2122 | 27.546 | 27.7199 | 27.8457 | 28.0361 | 28.2792 | 28.5731 | 28.7272 | 28.6772 | 28.7377 | 28.7377 | 28.7377 | 28.7377 | 28.7377 | 28.7377 | 28.7377 | 28.7377 | 28.7377 | 28.7377 | 28.7377 | 28.7377 | 28.7377 | 28.7377 | 28.7377
50% | 1686.2345 | 18.6255 | 20.0184 | 20.1583 | 20.0897 | 20.155 | 20.1818 | 20.2677 | 20.4443 | 20.5929 | 20.6613 | 20.6004 | 20.856 | 20.8965 | 20.8486 | 20.9448 | 20.9998 | 20.9998 | 20.9998 | 20.9998 | 20.9998 | 20.9998 | 20.9998 | 20.9998 | 20.9998 | 20.9998 | 20.9998 | 20.9998 | 20.9998 | 20.9998 | 20.9998 | 50% | 95.2974 | 22.9159 | 24.4726 | 24.5155 | 24.4692 | 24.4811 | 24.5661 | 24.7384 | 25.0418 | 25.1999 | 25.3143 | 25.4873 | 25.7083 | 25.9756 | 26.1156 | 26.0702 | 26.1252 | 26.1252 | 26.1252 | 26.1252 | 26.1252 | 26.1252 | 26.1252 | 26.1252 | 26.1252 | 26.1252 | 26.1252 | 26.1252 | 26.1252 | 26.1252 | 26.1252
45% | 2129.0649 | 16.7629 | 18.0165 | 18.1425 | 18.0808 | 18.1395 | 18.1636 | 18.2409 | 18.3999 | 18.5336 | 18.5952 | 18.5403 | 18.7704 | 18.8069 | 18.7637 | 18.8503 | 18.8998 | 18.8998 | 18.8998 | 18.8998 | 18.8998 | 18.8998 | 18.8998 | 18.8998 | 18.8998 | 18.8998 | 18.8998 | 18.8998 | 18.8998 | 18.8998 | 18.8998 | 45% | 208.7467 | 20.6243 | 22.0253 | 22.064 | 22.0223 | 22.033 | 22.1095 | 22.2646 | 22.5376 | 22.6799 | 22.7828 | 22.9386 | 23.1375 | 23.378 | 23.504 | 23.4632 | 23.5127 | 23.5127 | 23.5127 | 23.5127 | 23.5127 | 23.5127 | 23.5127 | 23.5127 | 23.5127 | 23.5127 | 23.5127 | 23.5127 | 23.5127 | 23.5127 | 23.5127
40% | 2484.5393 | 14.9004 | 16.0147 | 16.1267 | 16.0718 | 16.124 | 16.1454 | 16.2141 | 16.3555 | 16.4743 | 16.5291 | 16.4803 | 16.6848 | 16.7172 | 16.6788 | 16.7558 | 16.7998 | 16.7998 | 16.7998 | 16.7998 | 16.7998 | 16.7998 | 16.7998 | 16.7998 | 16.7998 | 16.7998 | 16.7998 | 16.7998 | 16.7998 | 16.7998 | 16.7998 | 40% | 380.4333 | 18.3327 | 19.5781 | 19.6124 | 19.5754 | 19.5849 | 19.6529 | 19.7907 | 20.0334 | 20.1599 | 20.2514 | 20.3899 | 20.5667 | 20.7804 | 20.8925 | 20.8562 | 20.9002 | 20.9002 | 20.9002 | 20.9002 | 20.9002 | 20.9002 | 20.9002 | 20.9002 | 20.9002 | 20.9002 | 20.9002 | 20.9002 | 20.9002 | 20.9002 | 20.9002
35% | 2808.248 | 13.0378 | 14.0129 | 14.1108 | 14.0628 | 14.1085 | 14.1272 | 14.1874 | 14.311 | 14.415 | 14.4629 | 14.4203 | 14.5992 | 14.6276 | 14.594 | 14.6613 | 14.6998 | 14.6998 | 14.6998 | 14.6998 | 14.6998 | 14.6998 | 14.6998 | 14.6998 | 14.6998 | 14.6998 | 14.6998 | 14.6998 | 14.6998 | 14.6998 | 14.6998 | 35% | 696.5786 | 16.0411 | 17.1308 | 17.1609 | 17.1285 | 17.1368 | 17.1963 | 17.3169 | 17.5293 | 17.6399 | 17.72 | 17.8411 | 17.9958 | 18.1829 | 18.2809 | 18.2491 | 18.2876 | 18.2876 | 18.2876 | 18.2876 | 18.2876 | 18.2876 | 18.2876 | 18.2876 | 18.2876 | 18.2876 | 18.2876 | 18.2876 | 18.2876 | 18.2876 | 18.2876
30% | 3095.6528 | 11.1753 | 12.011 | 12.095 | 12.0538 | 12.093 | 12.1091 | 12.1606 | 12.2666 | 12.3558 | 12.3968 | 12.3602 | 12.5136 | 12.5379 | 12.5091 | 12.5669 | 12.5999 | 12.5999 | 12.5999 | 12.5999 | 12.5999 | 12.5999 | 12.5999 | 12.5999 | 12.5999 | 12.5999 | 12.5999 | 12.5999 | 12.5999 | 12.5999 | 12.5999 | 30% | 1260.7997 | 13.7495 | 14.6835 | 14.7093 | 14.6815 | 14.6887 | 14.7397 | 14.843 | 15.0251 | 15.1199 | 15.1886 | 15.2924 | 15.425 | 15.5853 | 15.6694 | 15.6421 | 15.6751 | 15.6751 | 15.6751 | 15.6751 | 15.6751 | 15.6751 | 15.6751 | 15.6751 | 15.6751 | 15.6751 | 15.6751 | 15.6751 | 15.6751 | 15.6751 | 15.6751
25% | 3358.8552 | 9.3127 | 10.0092 | 10.0792 | 10.0449 | 10.0775 | 10.0909 | 10.1338 | 10.2222 | 10.2965 | 10.3307 | 10.3002 | 10.428 | 10.4483 | 10.4243 | 10.4724 | 10.4999 | 10.4999 | 10.4999 | 10.4999 | 10.4999 | 10.4999 | 10.4999 | 10.4999 | 10.4999 | 10.4999 | 10.4999 | 10.4999 | 10.4999 | 10.4999 | 10.4999 | 25% | 1965.3198 | 11.458 | 12.2363 | 12.2578 | 12.2346 | 12.2406 | 12.2831 | 12.3692 | 12.5209 | 12.5999 | 12.6571 | 12.7437 | 12.8542 | 12.9878 | 13.0578 | 13.0351 | 13.0626 | 13.0626 | 13.0626 | 13.0626 | 13.0626 | 13.0626 | 13.0626 | 13.0626 | 13.0626 | 13.0626 | 13.0626 | 13.0626 | 13.0626 | 13.0626 | 13.0626
20% | 3588.7791 | 7.4502 | 8.0073 | 8.0633 | 8.0359 | 8.062 | 8.0727 | 8.1071 | 8.1777 | 8.2372 | 8.2645 | 8.2401 | 8.3424 | 8.3586 | 8.3394 | 8.3779 | 8.3999 | 8.3999 | 8.3999 | 8.3999 | 8.3999 | 8.3999 | 8.3999 | 8.3999 | 8.3999 | 8.3999 | 8.3999 | 8.3999 | 8.3999 | 8.3999 | 8.3999 | 20% | 2490.2118 | 9.1664 | 9.789 | 9.8062 | 9.7877 | 9.7925 | 9.8265 | 9.8954 | 10.0167 | 10.08 | 10.1257 | 10.1949 | 10.2833 | 10.3902 | 10.4462 | 10.4281 | 10.4501 | 10.4501 | 10.4501 | 10.4501 | 10.4501 | 10.4501 | 10.4501 | 10.4501 | 10.4501 | 10.4501 | 10.4501 | 10.4501 | 10.4501 | 10.4501 | 10.4501
15% | 3802.4419 | 5.5876 | 6.0055 | 6.0475 | 6.0269 | 6.0465 | 6.0545 | 6.0803 | 6.1333 | 6.1779 | 6.1984 | 6.1801 | 6.2568 | 6.269 | 6.2546 | 6.2834 | 6.2999 | 6.2999 | 6.2999 | 6.2999 | 6.2999 | 6.2999 | 6.2999 | 6.2999 | 6.2999 | 6.2999 | 6.2999 | 6.2999 | 6.2999 | 6.2999 | 6.2999 | 15% | 2997.7083 | 6.8748 | 7.3418 | 7.3547 | 7.3408 | 7.3443 | 7.3698 | 7.4215 | 7.5125 | 7.56 | 7.5943 | 7.6462 | 7.7125 | 7.7927 | 7.8347 | 7.8211 | 7.8376 | 7.8376 | 7.8376 | 7.8376 | 7.8376 | 7.8376 | 7.8376 | 7.8376 | 7.8376 | 7.8376 | 7.8376 | 7.8376 | 7.8376 | 7.8376 | 7.8376
10% | 4024.8025 | 3.7251 | 4.0037 | 4.0317 | 4.0179 | 4.031 | 4.0364 | 4.0535 | 4.0889 | 4.1186 | 4.1323 | 4.1201 | 4.1712 | 4.1793 | 4.1697 | 4.189 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 10% | 3491.5908 | 4.5832 | 4.8945 | 4.9031 | 4.8938 | 4.8962 | 4.9132 | 4.9477 | 5.0084 | 5.04 | 5.0629 | 5.0975 | 5.1417 | 5.1951 | 5.2231 | 5.214 | 5.225 | 5.225 | 5.225 | 5.225 | 5.225 | 5.225 | 5.225 | 5.225 | 5.225 | 5.225 | 5.225 | 5.225 | 5.225 | 5.225 | 5.225
5% | 4239.978 | 1.8625 | 2.0018 | 2.0158 | 2.009 | 2.0155 | 2.0182 | 2.0268 | 2.0444 | 2.0593 | 2.0661 | 2.06 | 2.0856 | 2.0897 | 2.0849 | 2.0945 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 5% | 3955.9766 | 2.2916 | 2.4473 | 2.4516 | 2.4469 | 2.4481 | 2.4566 | 2.4738 | 2.5042 | 2.52 | 2.5314 | 2.5487 | 2.5708 | 2.5976 | 2.6116 | 2.607 | 2.6125 | 2.6125 | 2.6125 | 2.6125 | 2.6125 | 2.6125 | 2.6125 | 2.6125 | 2.6125 | 2.6125 | 2.6125 | 2.6125 | 2.6125 | 2.6125 | 2.6125
9.992e-14% | 4391.6218 | 3.7221e-14 | 4.0005e-14 | 4.0284e-14 | 4.0147e-14 | 4.0278e-14 | 4.0331e-14 | 4.0503e-14 | 4.0856e-14 | 4.1153e-14 | 4.129e-14 | 4.1168e-14 | 4.1679e-14 | 4.176e-14 | 4.1664e-14 | 4.1856e-14 | 4.1966e-14 | 4.1966e-14 | 4.1966e-14 | 4.1966e-14 | 4.1966e-14 | 4.1966e-14 | 4.1966e-14 | 4.1966e-14 | 4.1966e-14 | 4.1966e-14 | 4.1966e-14 | 4.1966e-14 | 4.1966e-14 | 4.1966e-14 | 4.1966e-14 | 9.992e-14% | 4391.6218 | 4.5795e-14 | 4.8906e-14 | 4.8992e-14 | 4.8899e-14 | 4.8923e-14 | 4.9093e-14 | 4.9437e-14 | 5.0044e-14 | 5.0359e-14 | 5.0588e-14 | 5.0934e-14 | 5.1376e-14 | 5.191e-14 | 5.2189e-14 | 5.2099e-14 | 5.2209e-14 | 5.2209e-14 | 5.2209e-14 | 5.2209e-14 | 5.2209e-14 | 5.2209e-14 | 5.2209e-14 | 5.2209e-14 | 5.2209e-14 | 5.2209e-14 | 5.2209e-14 | 5.2209e-14 | 5.2209e-14 | 5.2209e-14 | 5.2209e-14
Option 2
Winter Season | [31 empty] | Winter Season
P50 | [31 empty] | P10
% of MD | Winter - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Winter - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 35.4586 | 39.1719 | 39.5657 | 40.0525 | 40.6988 | 41.3115 | 42.3823 | 45.0754 | 46.5239 | 45.4672 | 48.7387 | 49.3282 | 49.7519 | 51.7491 | 52.0742 | 52.0742 | 52.0742 | 52.0742 | 52.0742 | 52.0742 | 52.0742 | 52.0742 | 52.0742 | 52.0742 | 52.0742 | 52.0742 | 52.0742 | 52.0742 | 52.0742 | 52.0742 | 100% | 0 | 38.8714 | 42.4133 | 42.7801 | 44.046 | 44.0152 | 44.2935 | 45.3822 | 48.5101 | 49.8009 | 48.5791 | 51.9542 | 50.5371 | 51.8122 | 52.731 | 52.3535 | 52.3535 | 52.3535 | 52.3535 | 52.3535 | 52.3535 | 52.3535 | 52.3535 | 52.3535 | 52.3535 | 52.3535 | 52.3535 | 52.3535 | 52.3535 | 52.3535 | 52.3535
99% | 0.2972 | 35.104 | 38.7802 | 39.17 | 39.652 | 40.2918 | 40.8984 | 41.9585 | 44.6246 | 46.0587 | 45.0125 | 48.2513 | 48.8349 | 49.2544 | 51.2316 | 51.5535 | 51.5535 | 51.5535 | 51.5535 | 51.5535 | 51.5535 | 51.5535 | 51.5535 | 51.5535 | 51.5535 | 51.5535 | 51.5535 | 51.5535 | 51.5535 | 51.5535 | 51.5535 | 99% | 0.2972 | 38.4827 | 41.9892 | 42.3523 | 43.6056 | 43.575 | 43.8506 | 44.9284 | 48.025 | 49.3029 | 48.0933 | 51.4346 | 50.0317 | 51.294 | 52.2037 | 51.83 | 51.83 | 51.83 | 51.83 | 51.83 | 51.83 | 51.83 | 51.83 | 51.83 | 51.83 | 51.83 | 51.83 | 51.83 | 51.83 | 51.83 | 51.83
98% | 0.2972 | 34.7495 | 38.3885 | 38.7744 | 39.2514 | 39.8848 | 40.4853 | 41.5347 | 44.1739 | 45.5935 | 44.5578 | 47.764 | 48.3416 | 48.7568 | 50.7141 | 51.0327 | 51.0327 | 51.0327 | 51.0327 | 51.0327 | 51.0327 | 51.0327 | 51.0327 | 51.0327 | 51.0327 | 51.0327 | 51.0327 | 51.0327 | 51.0327 | 51.0327 | 51.0327 | 98% | 0.2972 | 38.0939 | 41.5651 | 41.9245 | 43.1651 | 43.1349 | 43.4077 | 44.4746 | 47.5399 | 48.8049 | 47.6075 | 50.9151 | 49.5264 | 50.7759 | 51.6764 | 51.3064 | 51.3064 | 51.3064 | 51.3064 | 51.3064 | 51.3064 | 51.3064 | 51.3064 | 51.3064 | 51.3064 | 51.3064 | 51.3064 | 51.3064 | 51.3064 | 51.3064 | 51.3064
97% | 0.2972 | 34.3949 | 37.9968 | 38.3787 | 38.8509 | 39.4778 | 40.0722 | 41.1108 | 43.7231 | 45.1282 | 44.1032 | 47.2766 | 47.8483 | 48.2593 | 50.1966 | 50.512 | 50.512 | 50.512 | 50.512 | 50.512 | 50.512 | 50.512 | 50.512 | 50.512 | 50.512 | 50.512 | 50.512 | 50.512 | 50.512 | 50.512 | 50.512 | 97% | 0.2972 | 37.7052 | 41.1409 | 41.4967 | 42.7246 | 42.6947 | 42.9647 | 44.0208 | 47.0548 | 48.3068 | 47.1217 | 50.3955 | 49.021 | 50.2578 | 51.1491 | 50.7829 | 50.7829 | 50.7829 | 50.7829 | 50.7829 | 50.7829 | 50.7829 | 50.7829 | 50.7829 | 50.7829 | 50.7829 | 50.7829 | 50.7829 | 50.7829 | 50.7829 | 50.7829
95% | 1.486 | 33.6857 | 37.2134 | 37.5874 | 38.0499 | 38.6639 | 39.2459 | 40.2632 | 42.8216 | 44.1977 | 43.1938 | 46.3018 | 46.8618 | 47.2643 | 49.1617 | 49.4705 | 49.4705 | 49.4705 | 49.4705 | 49.4705 | 49.4705 | 49.4705 | 49.4705 | 49.4705 | 49.4705 | 49.4705 | 49.4705 | 49.4705 | 49.4705 | 49.4705 | 49.4705 | 95% | 1.486 | 36.9278 | 40.2927 | 40.6411 | 41.8437 | 41.8144 | 42.0789 | 43.1131 | 46.0846 | 47.3108 | 46.1501 | 49.3565 | 48.0103 | 49.2216 | 50.0944 | 49.7358 | 49.7358 | 49.7358 | 49.7358 | 49.7358 | 49.7358 | 49.7358 | 49.7358 | 49.7358 | 49.7358 | 49.7358 | 49.7358 | 49.7358 | 49.7358 | 49.7358 | 49.7358
90% | 8.6188 | 31.9128 | 35.2548 | 35.6091 | 36.0472 | 36.6289 | 37.1804 | 38.1441 | 40.5679 | 41.8715 | 40.9205 | 43.8649 | 44.3954 | 44.7767 | 46.5742 | 46.8668 | 46.8668 | 46.8668 | 46.8668 | 46.8668 | 46.8668 | 46.8668 | 46.8668 | 46.8668 | 46.8668 | 46.8668 | 46.8668 | 46.8668 | 46.8668 | 46.8668 | 46.8668 | 90% | 8.6188 | 34.9842 | 38.172 | 38.5021 | 39.6414 | 39.6137 | 39.8642 | 40.844 | 43.6591 | 44.8208 | 43.7212 | 46.7587 | 45.4834 | 46.6309 | 47.4579 | 47.1181 | 47.1181 | 47.1181 | 47.1181 | 47.1181 | 47.1181 | 47.1181 | 47.1181 | 47.1181 | 47.1181 | 47.1181 | 47.1181 | 47.1181 | 47.1181 | 47.1181 | 47.1181
85% | 40.1218 | 30.1398 | 33.2962 | 33.6308 | 34.0446 | 34.594 | 35.1148 | 36.025 | 38.3141 | 39.5453 | 38.6471 | 41.4279 | 41.9289 | 42.2891 | 43.9867 | 44.2631 | 44.2631 | 44.2631 | 44.2631 | 44.2631 | 44.2631 | 44.2631 | 44.2631 | 44.2631 | 44.2631 | 44.2631 | 44.2631 | 44.2631 | 44.2631 | 44.2631 | 44.2631 | 85% | 40.1218 | 33.0407 | 36.0513 | 36.3631 | 37.4391 | 37.4129 | 37.6495 | 38.5749 | 41.2336 | 42.3307 | 41.2922 | 44.161 | 42.9565 | 44.0403 | 44.8213 | 44.5005 | 44.5005 | 44.5005 | 44.5005 | 44.5005 | 44.5005 | 44.5005 | 44.5005 | 44.5005 | 44.5005 | 44.5005 | 44.5005 | 44.5005 | 44.5005 | 44.5005 | 44.5005
80% | 93.0231 | 28.3669 | 31.3376 | 31.6526 | 32.042 | 32.559 | 33.0492 | 33.9058 | 36.0603 | 37.2191 | 36.3737 | 38.991 | 39.4625 | 39.8015 | 41.3993 | 41.6594 | 41.6594 | 41.6594 | 41.6594 | 41.6594 | 41.6594 | 41.6594 | 41.6594 | 41.6594 | 41.6594 | 41.6594 | 41.6594 | 41.6594 | 41.6594 | 41.6594 | 41.6594 | 80% | 93.0231 | 31.0971 | 33.9307 | 34.2241 | 35.2368 | 35.2121 | 35.4348 | 36.3058 | 38.8081 | 39.8407 | 38.8633 | 41.5633 | 40.4297 | 41.4497 | 42.1848 | 41.8828 | 41.8828 | 41.8828 | 41.8828 | 41.8828 | 41.8828 | 41.8828 | 41.8828 | 41.8828 | 41.8828 | 41.8828 | 41.8828 | 41.8828 | 41.8828 | 41.8828 | 41.8828
75% | 197.0426 | 26.594 | 29.379 | 29.6743 | 30.0394 | 30.5241 | 30.9836 | 31.7867 | 33.8065 | 34.8929 | 34.1004 | 36.554 | 36.9961 | 37.3139 | 38.8118 | 39.0556 | 39.0556 | 39.0556 | 39.0556 | 39.0556 | 39.0556 | 39.0556 | 39.0556 | 39.0556 | 39.0556 | 39.0556 | 39.0556 | 39.0556 | 39.0556 | 39.0556 | 39.0556 | 75% | 197.0426 | 29.1535 | 31.81 | 32.0851 | 33.0345 | 33.0114 | 33.2201 | 34.0367 | 36.3826 | 37.3507 | 36.4343 | 38.9656 | 37.9028 | 38.8591 | 39.5482 | 39.2651 | 39.2651 | 39.2651 | 39.2651 | 39.2651 | 39.2651 | 39.2651 | 39.2651 | 39.2651 | 39.2651 | 39.2651 | 39.2651 | 39.2651 | 39.2651 | 39.2651 | 39.2651
70% | 378.0365 | 24.821 | 27.4204 | 27.696 | 28.0367 | 28.4892 | 28.9181 | 29.6676 | 31.5528 | 32.5668 | 31.827 | 34.1171 | 34.5297 | 34.8263 | 36.2244 | 36.4519 | 36.4519 | 36.4519 | 36.4519 | 36.4519 | 36.4519 | 36.4519 | 36.4519 | 36.4519 | 36.4519 | 36.4519 | 36.4519 | 36.4519 | 36.4519 | 36.4519 | 36.4519 | 70% | 378.0365 | 27.21 | 29.6893 | 29.9461 | 30.8322 | 30.8106 | 31.0055 | 31.7676 | 33.9571 | 34.8606 | 34.0054 | 36.3679 | 35.376 | 36.2685 | 36.9117 | 36.6474 | 36.6474 | 36.6474 | 36.6474 | 36.6474 | 36.6474 | 36.6474 | 36.6474 | 36.6474 | 36.6474 | 36.6474 | 36.6474 | 36.6474 | 36.6474 | 36.6474 | 36.6474
65% | 616.0926 | 23.0481 | 25.4618 | 25.7177 | 26.0341 | 26.4542 | 26.8525 | 27.5485 | 29.299 | 30.2406 | 29.5537 | 31.6802 | 32.0633 | 32.3387 | 33.6369 | 33.8482 | 33.8482 | 33.8482 | 33.8482 | 33.8482 | 33.8482 | 33.8482 | 33.8482 | 33.8482 | 33.8482 | 33.8482 | 33.8482 | 33.8482 | 33.8482 | 33.8482 | 33.8482 | 65% | 616.0926 | 25.2664 | 27.5687 | 27.8071 | 28.6299 | 28.6099 | 28.7908 | 29.4985 | 31.5316 | 32.3706 | 31.5764 | 33.7702 | 32.8491 | 33.6779 | 34.2751 | 34.0298 | 34.0298 | 34.0298 | 34.0298 | 34.0298 | 34.0298 | 34.0298 | 34.0298 | 34.0298 | 34.0298 | 34.0298 | 34.0298 | 34.0298 | 34.0298 | 34.0298 | 34.0298
60% | 934.9866 | 21.2752 | 23.5032 | 23.7394 | 24.0315 | 24.4193 | 24.7869 | 25.4294 | 27.0452 | 27.9144 | 27.2803 | 29.2432 | 29.5969 | 29.8511 | 31.0495 | 31.2445 | 31.2445 | 31.2445 | 31.2445 | 31.2445 | 31.2445 | 31.2445 | 31.2445 | 31.2445 | 31.2445 | 31.2445 | 31.2445 | 31.2445 | 31.2445 | 31.2445 | 31.2445 | 60% | 934.9866 | 23.3228 | 25.448 | 25.6681 | 26.4276 | 26.4091 | 26.5761 | 27.2293 | 29.1061 | 29.8805 | 29.1474 | 31.1725 | 30.3223 | 31.0873 | 31.6386 | 31.4121 | 31.4121 | 31.4121 | 31.4121 | 31.4121 | 31.4121 | 31.4121 | 31.4121 | 31.4121 | 31.4121 | 31.4121 | 31.4121 | 31.4121 | 31.4121 | 31.4121 | 31.4121
55% | 1310.9428 | 19.5022 | 21.5446 | 21.7611 | 22.0289 | 22.3843 | 22.7213 | 23.3103 | 24.7915 | 25.5882 | 25.0069 | 26.8063 | 27.1305 | 27.3635 | 28.462 | 28.6408 | 28.6408 | 28.6408 | 28.6408 | 28.6408 | 28.6408 | 28.6408 | 28.6408 | 28.6408 | 28.6408 | 28.6408 | 28.6408 | 28.6408 | 28.6408 | 28.6408 | 28.6408 | 55% | 1310.9428 | 21.3793 | 23.3273 | 23.5291 | 24.2253 | 24.2083 | 24.3614 | 24.9602 | 26.6806 | 27.3905 | 26.7185 | 28.5748 | 27.7954 | 28.4967 | 29.002 | 28.7944 | 28.7944 | 28.7944 | 28.7944 | 28.7944 | 28.7944 | 28.7944 | 28.7944 | 28.7944 | 28.7944 | 28.7944 | 28.7944 | 28.7944 | 28.7944 | 28.7944 | 28.7944
50% | 1730.2899 | 17.7293 | 19.586 | 19.7828 | 20.0262 | 20.3494 | 20.6558 | 21.1912 | 22.5377 | 23.262 | 22.7336 | 24.3694 | 24.6641 | 24.8759 | 25.8746 | 26.0371 | 26.0371 | 26.0371 | 26.0371 | 26.0371 | 26.0371 | 26.0371 | 26.0371 | 26.0371 | 26.0371 | 26.0371 | 26.0371 | 26.0371 | 26.0371 | 26.0371 | 26.0371 | 50% | 1730.2899 | 19.4357 | 21.2067 | 21.3901 | 22.023 | 22.0076 | 22.1468 | 22.6911 | 24.2551 | 24.9004 | 24.2895 | 25.9771 | 25.2686 | 25.9061 | 26.3655 | 26.1767 | 26.1767 | 26.1767 | 26.1767 | 26.1767 | 26.1767 | 26.1767 | 26.1767 | 26.1767 | 26.1767 | 26.1767 | 26.1767 | 26.1767 | 26.1767 | 26.1767 | 26.1767
45% | 2168.0633 | 15.9564 | 17.6274 | 17.8046 | 18.0236 | 18.3145 | 18.5902 | 19.072 | 20.2839 | 20.9358 | 20.4602 | 21.9324 | 22.1977 | 22.3883 | 23.2871 | 23.4334 | 23.4334 | 23.4334 | 23.4334 | 23.4334 | 23.4334 | 23.4334 | 23.4334 | 23.4334 | 23.4334 | 23.4334 | 23.4334 | 23.4334 | 23.4334 | 23.4334 | 23.4334 | 45% | 2168.0633 | 17.4921 | 19.086 | 19.2511 | 19.8207 | 19.8068 | 19.9321 | 20.422 | 21.8296 | 22.4104 | 21.8606 | 23.3794 | 22.7417 | 23.3155 | 23.7289 | 23.5591 | 23.5591 | 23.5591 | 23.5591 | 23.5591 | 23.5591 | 23.5591 | 23.5591 | 23.5591 | 23.5591 | 23.5591 | 23.5591 | 23.5591 | 23.5591 | 23.5591 | 23.5591
40% | 2609.7004 | 14.1835 | 15.6688 | 15.8263 | 16.021 | 16.2795 | 16.5246 | 16.9529 | 18.0302 | 18.6096 | 18.1869 | 19.4955 | 19.7313 | 19.9008 | 20.6996 | 20.8297 | 20.8297 | 20.8297 | 20.8297 | 20.8297 | 20.8297 | 20.8297 | 20.8297 | 20.8297 | 20.8297 | 20.8297 | 20.8297 | 20.8297 | 20.8297 | 20.8297 | 20.8297 | 40% | 2609.7004 | 15.5485 | 16.9653 | 17.1121 | 17.6184 | 17.6061 | 17.7174 | 18.1529 | 19.404 | 19.9203 | 19.4316 | 20.7817 | 20.2148 | 20.7249 | 21.0924 | 20.9414 | 20.9414 | 20.9414 | 20.9414 | 20.9414 | 20.9414 | 20.9414 | 20.9414 | 20.9414 | 20.9414 | 20.9414 | 20.9414 | 20.9414 | 20.9414 | 20.9414 | 20.9414
35% | 2998.1389 | 12.4105 | 13.7102 | 13.848 | 14.0184 | 14.2446 | 14.459 | 14.8338 | 15.7764 | 16.2834 | 15.9135 | 17.0586 | 17.2649 | 17.4132 | 18.1122 | 18.226 | 18.226 | 18.226 | 18.226 | 18.226 | 18.226 | 18.226 | 18.226 | 18.226 | 18.226 | 18.226 | 18.226 | 18.226 | 18.226 | 18.226 | 18.226 | 35% | 2998.1389 | 13.605 | 14.8447 | 14.973 | 15.4161 | 15.4053 | 15.5027 | 15.8838 | 16.9785 | 17.4303 | 17.0027 | 18.184 | 17.688 | 18.1343 | 18.4558 | 18.3237 | 18.3237 | 18.3237 | 18.3237 | 18.3237 | 18.3237 | 18.3237 | 18.3237 | 18.3237 | 18.3237 | 18.3237 | 18.3237 | 18.3237 | 18.3237 | 18.3237 | 18.3237
30% | 3309.3057 | 10.6376 | 11.7516 | 11.8697 | 12.0157 | 12.2096 | 12.3935 | 12.7147 | 13.5226 | 13.9572 | 13.6402 | 14.6216 | 14.7985 | 14.9256 | 15.5247 | 15.6223 | 15.6223 | 15.6223 | 15.6223 | 15.6223 | 15.6223 | 15.6223 | 15.6223 | 15.6223 | 15.6223 | 15.6223 | 15.6223 | 15.6223 | 15.6223 | 15.6223 | 15.6223 | 30% | 3309.3057 | 11.6614 | 12.724 | 12.834 | 13.2138 | 13.2046 | 13.2881 | 13.6147 | 14.553 | 14.9403 | 14.5737 | 15.5862 | 15.1611 | 15.5436 | 15.8193 | 15.706 | 15.706 | 15.706 | 15.706 | 15.706 | 15.706 | 15.706 | 15.706 | 15.706 | 15.706 | 15.706 | 15.706 | 15.706 | 15.706 | 15.706 | 15.706
25% | 3537.8514 | 8.8647 | 9.793 | 9.8914 | 10.0131 | 10.1747 | 10.3279 | 10.5956 | 11.2688 | 11.631 | 11.3668 | 12.1847 | 12.332 | 12.438 | 12.9373 | 13.0185 | 13.0185 | 13.0185 | 13.0185 | 13.0185 | 13.0185 | 13.0185 | 13.0185 | 13.0185 | 13.0185 | 13.0185 | 13.0185 | 13.0185 | 13.0185 | 13.0185 | 13.0185 | 25% | 3537.8514 | 9.7178 | 10.6033 | 10.695 | 11.0115 | 11.0038 | 11.0734 | 11.3456 | 12.1275 | 12.4502 | 12.1448 | 12.9885 | 12.6343 | 12.953 | 13.1827 | 13.0884 | 13.0884 | 13.0884 | 13.0884 | 13.0884 | 13.0884 | 13.0884 | 13.0884 | 13.0884 | 13.0884 | 13.0884 | 13.0884 | 13.0884 | 13.0884 | 13.0884 | 13.0884
20% | 3731.0305 | 7.0917 | 7.8344 | 7.9131 | 8.0105 | 8.1398 | 8.2623 | 8.4765 | 9.0151 | 9.3048 | 9.0934 | 9.7477 | 9.8656 | 9.9504 | 10.3498 | 10.4148 | 10.4148 | 10.4148 | 10.4148 | 10.4148 | 10.4148 | 10.4148 | 10.4148 | 10.4148 | 10.4148 | 10.4148 | 10.4148 | 10.4148 | 10.4148 | 10.4148 | 10.4148 | 20% | 3731.0305 | 7.7743 | 8.4827 | 8.556 | 8.8092 | 8.803 | 8.8587 | 9.0764 | 9.702 | 9.9602 | 9.7158 | 10.3908 | 10.1074 | 10.3624 | 10.5462 | 10.4707 | 10.4707 | 10.4707 | 10.4707 | 10.4707 | 10.4707 | 10.4707 | 10.4707 | 10.4707 | 10.4707 | 10.4707 | 10.4707 | 10.4707 | 10.4707 | 10.4707 | 10.4707
15% | 3910.2412 | 5.3188 | 5.8758 | 5.9349 | 6.0079 | 6.1048 | 6.1967 | 6.3573 | 6.7613 | 6.9786 | 6.8201 | 7.3108 | 7.3992 | 7.4628 | 7.7624 | 7.8111 | 7.8111 | 7.8111 | 7.8111 | 7.8111 | 7.8111 | 7.8111 | 7.8111 | 7.8111 | 7.8111 | 7.8111 | 7.8111 | 7.8111 | 7.8111 | 7.8111 | 7.8111 | 15% | 3910.2412 | 5.8307 | 6.362 | 6.417 | 6.6069 | 6.6023 | 6.644 | 6.8073 | 7.2765 | 7.4701 | 7.2869 | 7.7931 | 7.5806 | 7.7718 | 7.9096 | 7.853 | 7.853 | 7.853 | 7.853 | 7.853 | 7.853 | 7.853 | 7.853 | 7.853 | 7.853 | 7.853 | 7.853 | 7.853 | 7.853 | 7.853 | 7.853
10% | 4075.1864 | 3.5459 | 3.9172 | 3.9566 | 4.0052 | 4.0699 | 4.1312 | 4.2382 | 4.5075 | 4.6524 | 4.5467 | 4.8739 | 4.9328 | 4.9752 | 5.1749 | 5.2074 | 5.2074 | 5.2074 | 5.2074 | 5.2074 | 5.2074 | 5.2074 | 5.2074 | 5.2074 | 5.2074 | 5.2074 | 5.2074 | 5.2074 | 5.2074 | 5.2074 | 5.2074 | 10% | 4075.1864 | 3.8871 | 4.2413 | 4.278 | 4.4046 | 4.4015 | 4.4294 | 4.5382 | 4.851 | 4.9801 | 4.8579 | 5.1954 | 5.0537 | 5.1812 | 5.2731 | 5.2353 | 5.2353 | 5.2353 | 5.2353 | 5.2353 | 5.2353 | 5.2353 | 5.2353 | 5.2353 | 5.2353 | 5.2353 | 5.2353 | 5.2353 | 5.2353 | 5.2353 | 5.2353
5% | 4251.7223 | 1.7729 | 1.9586 | 1.9783 | 2.0026 | 2.0349 | 2.0656 | 2.1191 | 2.2538 | 2.3262 | 2.2734 | 2.4369 | 2.4664 | 2.4876 | 2.5875 | 2.6037 | 2.6037 | 2.6037 | 2.6037 | 2.6037 | 2.6037 | 2.6037 | 2.6037 | 2.6037 | 2.6037 | 2.6037 | 2.6037 | 2.6037 | 2.6037 | 2.6037 | 2.6037 | 5% | 4251.7223 | 1.9436 | 2.1207 | 2.139 | 2.2023 | 2.2008 | 2.2147 | 2.2691 | 2.4255 | 2.49 | 2.429 | 2.5977 | 2.5269 | 2.5906 | 2.6365 | 2.6177 | 2.6177 | 2.6177 | 2.6177 | 2.6177 | 2.6177 | 2.6177 | 2.6177 | 2.6177 | 2.6177 | 2.6177 | 2.6177 | 2.6177 | 2.6177 | 2.6177 | 2.6177
9.992e-14% | 4391.7028 | 3.543e-14 | 3.9141e-14 | 3.9534e-14 | 4.002e-14 | 4.0666e-14 | 4.1279e-14 | 4.2348e-14 | 4.5039e-14 | 4.6487e-14 | 4.5431e-14 | 4.87e-14 | 4.9289e-14 | 4.9712e-14 | 5.1708e-14 | 5.2033e-14 | 5.2033e-14 | 5.2033e-14 | 5.2033e-14 | 5.2033e-14 | 5.2033e-14 | 5.2033e-14 | 5.2033e-14 | 5.2033e-14 | 5.2033e-14 | 5.2033e-14 | 5.2033e-14 | 5.2033e-14 | 5.2033e-14 | 5.2033e-14 | 5.2033e-14 | 9.992e-14% | 4391.7028 | 3.884e-14 | 4.2379e-14 | 4.2746e-14 | 4.4011e-14 | 4.398e-14 | 4.4258e-14 | 4.5346e-14 | 4.8471e-14 | 4.9761e-14 | 4.854e-14 | 5.1913e-14 | 5.0497e-14 | 5.1771e-14 | 5.2689e-14 | 5.2312e-14 | 5.2312e-14 | 5.2312e-14 | 5.2312e-14 | 5.2312e-14 | 5.2312e-14 | 5.2312e-14 | 5.2312e-14 | 5.2312e-14 | 5.2312e-14 | 5.2312e-14 | 5.2312e-14 | 5.2312e-14 | 5.2312e-14 | 5.2312e-14 | 5.2312e-14
Summer Season | [31 empty] | Summer Season
P50 | [31 empty] | P10
% of MD | Summer - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Summer - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 37.2509 | 40.0367 | 40.3167 | 40.1794 | 40.3099 | 40.3635 | 40.5354 | 40.8886 | 41.1859 | 41.3227 | 41.2007 | 41.712 | 41.7931 | 41.6971 | 41.8895 | 41.9995 | 41.9995 | 41.9995 | 41.9995 | 41.9995 | 41.9995 | 41.9995 | 41.9995 | 41.9995 | 41.9995 | 41.9995 | 41.9995 | 41.9995 | 41.9995 | 41.9995 | 100% | 0 | 45.8318 | 48.9452 | 49.0311 | 48.9384 | 48.9623 | 49.1323 | 49.4768 | 50.0836 | 50.3998 | 50.6285 | 50.9747 | 51.4167 | 51.9511 | 52.2312 | 52.1404 | 52.2504 | 52.2504 | 52.2504 | 52.2504 | 52.2504 | 52.2504 | 52.2504 | 52.2504 | 52.2504 | 52.2504 | 52.2504 | 52.2504 | 52.2504 | 52.2504 | 52.2504
99% | 0.37816 | 36.8784 | 39.6364 | 39.9135 | 39.7777 | 39.9068 | 39.9599 | 40.13 | 40.4798 | 40.774 | 40.9094 | 40.7887 | 41.2949 | 41.3751 | 41.2801 | 41.4706 | 41.5795 | 41.5795 | 41.5795 | 41.5795 | 41.5795 | 41.5795 | 41.5795 | 41.5795 | 41.5795 | 41.5795 | 41.5795 | 41.5795 | 41.5795 | 41.5795 | 41.5795 | 99% | 0 | 45.3735 | 48.4557 | 48.5408 | 48.4491 | 48.4726 | 48.6409 | 48.982 | 49.5828 | 49.8958 | 50.1222 | 50.465 | 50.9025 | 51.4316 | 51.7089 | 51.619 | 51.7279 | 51.7279 | 51.7279 | 51.7279 | 51.7279 | 51.7279 | 51.7279 | 51.7279 | 51.7279 | 51.7279 | 51.7279 | 51.7279 | 51.7279 | 51.7279 | 51.7279
98% | 0.37816 | 36.5059 | 39.236 | 39.5103 | 39.3759 | 39.5037 | 39.5563 | 39.7246 | 40.0709 | 40.3621 | 40.4962 | 40.3767 | 40.8777 | 40.9572 | 40.8632 | 41.0517 | 41.1595 | 41.1595 | 41.1595 | 41.1595 | 41.1595 | 41.1595 | 41.1595 | 41.1595 | 41.1595 | 41.1595 | 41.1595 | 41.1595 | 41.1595 | 41.1595 | 41.1595 | 98% | 0 | 44.9152 | 47.9662 | 48.0504 | 47.9597 | 47.983 | 48.1496 | 48.4873 | 49.0819 | 49.3918 | 49.6159 | 49.9552 | 50.3883 | 50.9121 | 51.1866 | 51.0976 | 51.2054 | 51.2054 | 51.2054 | 51.2054 | 51.2054 | 51.2054 | 51.2054 | 51.2054 | 51.2054 | 51.2054 | 51.2054 | 51.2054 | 51.2054 | 51.2054 | 51.2054
97% | 0.37816 | 36.1334 | 38.8356 | 39.1072 | 38.9741 | 39.1006 | 39.1526 | 39.3193 | 39.662 | 39.9503 | 40.083 | 39.9647 | 40.4606 | 40.5393 | 40.4462 | 40.6328 | 40.7395 | 40.7395 | 40.7395 | 40.7395 | 40.7395 | 40.7395 | 40.7395 | 40.7395 | 40.7395 | 40.7395 | 40.7395 | 40.7395 | 40.7395 | 40.7395 | 40.7395 | 97% | 0.37816 | 44.4569 | 47.4768 | 47.5601 | 47.4703 | 47.4934 | 47.6583 | 47.9925 | 48.5811 | 48.8878 | 49.1097 | 49.4455 | 49.8742 | 50.3926 | 50.6643 | 50.5762 | 50.6829 | 50.6829 | 50.6829 | 50.6829 | 50.6829 | 50.6829 | 50.6829 | 50.6829 | 50.6829 | 50.6829 | 50.6829 | 50.6829 | 50.6829 | 50.6829 | 50.6829
95% | 0.75633 | 35.3884 | 38.0349 | 38.3008 | 38.1705 | 38.2944 | 38.3454 | 38.5086 | 38.8442 | 39.1266 | 39.2565 | 39.1407 | 39.6264 | 39.7034 | 39.6123 | 39.7951 | 39.8996 | 39.8996 | 39.8996 | 39.8996 | 39.8996 | 39.8996 | 39.8996 | 39.8996 | 39.8996 | 39.8996 | 39.8996 | 39.8996 | 39.8996 | 39.8996 | 39.8996 | 95% | 0.37816 | 43.5402 | 46.4979 | 46.5795 | 46.4915 | 46.5141 | 46.6757 | 47.003 | 47.5794 | 47.8798 | 48.0971 | 48.426 | 48.8458 | 49.3536 | 49.6196 | 49.5334 | 49.6379 | 49.6379 | 49.6379 | 49.6379 | 49.6379 | 49.6379 | 49.6379 | 49.6379 | 49.6379 | 49.6379 | 49.6379 | 49.6379 | 49.6379 | 49.6379 | 49.6379
90% | 9.0759 | 33.5258 | 36.0331 | 36.285 | 36.1615 | 36.2789 | 36.3272 | 36.4818 | 36.7998 | 37.0673 | 37.1904 | 37.0807 | 37.5408 | 37.6138 | 37.5274 | 37.7006 | 37.7996 | 37.7996 | 37.7996 | 37.7996 | 37.7996 | 37.7996 | 37.7996 | 37.7996 | 37.7996 | 37.7996 | 37.7996 | 37.7996 | 37.7996 | 37.7996 | 37.7996 | 90% | 0.75633 | 41.2486 | 44.0506 | 44.128 | 44.0446 | 44.066 | 44.219 | 44.5291 | 45.0752 | 45.3598 | 45.5657 | 45.8772 | 46.275 | 46.756 | 47.0081 | 46.9264 | 47.0254 | 47.0254 | 47.0254 | 47.0254 | 47.0254 | 47.0254 | 47.0254 | 47.0254 | 47.0254 | 47.0254 | 47.0254 | 47.0254 | 47.0254 | 47.0254 | 47.0254
85% | 40.4636 | 31.6633 | 34.0312 | 34.2692 | 34.1525 | 34.2634 | 34.309 | 34.455 | 34.7554 | 35.008 | 35.1243 | 35.0206 | 35.4552 | 35.5241 | 35.4425 | 35.6061 | 35.6996 | 35.6996 | 35.6996 | 35.6996 | 35.6996 | 35.6996 | 35.6996 | 35.6996 | 35.6996 | 35.6996 | 35.6996 | 35.6996 | 35.6996 | 35.6996 | 35.6996 | 85% | 1.1345 | 38.957 | 41.6034 | 41.6764 | 41.5977 | 41.6179 | 41.7624 | 42.0553 | 42.5711 | 42.8398 | 43.0342 | 43.3285 | 43.7042 | 44.1585 | 44.3965 | 44.3193 | 44.4128 | 44.4128 | 44.4128 | 44.4128 | 44.4128 | 44.4128 | 44.4128 | 44.4128 | 44.4128 | 44.4128 | 44.4128 | 44.4128 | 44.4128 | 44.4128 | 44.4128
80% | 94.5411 | 29.8007 | 32.0294 | 32.2533 | 32.1436 | 32.2479 | 32.2908 | 32.4283 | 32.7109 | 32.9487 | 33.0581 | 32.9606 | 33.3696 | 33.4345 | 33.3577 | 33.5116 | 33.5996 | 33.5996 | 33.5996 | 33.5996 | 33.5996 | 33.5996 | 33.5996 | 33.5996 | 33.5996 | 33.5996 | 33.5996 | 33.5996 | 33.5996 | 33.5996 | 33.5996 | 80% | 2.6471 | 36.6655 | 39.1561 | 39.2249 | 39.1508 | 39.1698 | 39.3058 | 39.5815 | 40.0669 | 40.3198 | 40.5028 | 40.7798 | 41.1333 | 41.5609 | 41.785 | 41.7123 | 41.8003 | 41.8003 | 41.8003 | 41.8003 | 41.8003 | 41.8003 | 41.8003 | 41.8003 | 41.8003 | 41.8003 | 41.8003 | 41.8003 | 41.8003 | 41.8003 | 41.8003
75% | 197.0236 | 27.9382 | 30.0275 | 30.2375 | 30.1346 | 30.2324 | 30.2726 | 30.4015 | 30.6665 | 30.8894 | 30.992 | 30.9005 | 31.284 | 31.3448 | 31.2728 | 31.4172 | 31.4997 | 31.4997 | 31.4997 | 31.4997 | 31.4997 | 31.4997 | 31.4997 | 31.4997 | 31.4997 | 31.4997 | 31.4997 | 31.4997 | 31.4997 | 31.4997 | 31.4997 | 75% | 3.4035 | 34.3739 | 36.7089 | 36.7733 | 36.7038 | 36.7217 | 36.8492 | 37.1076 | 37.5627 | 37.7998 | 37.9714 | 38.231 | 38.5625 | 38.9633 | 39.1734 | 39.1053 | 39.1878 | 39.1878 | 39.1878 | 39.1878 | 39.1878 | 39.1878 | 39.1878 | 39.1878 | 39.1878 | 39.1878 | 39.1878 | 39.1878 | 39.1878 | 39.1878 | 39.1878
70% | 336.9444 | 26.0756 | 28.0257 | 28.2217 | 28.1256 | 28.2169 | 28.2545 | 28.3747 | 28.6221 | 28.8301 | 28.9259 | 28.8405 | 29.1984 | 29.2552 | 29.188 | 29.3227 | 29.3997 | 29.3997 | 29.3997 | 29.3997 | 29.3997 | 29.3997 | 29.3997 | 29.3997 | 29.3997 | 29.3997 | 29.3997 | 29.3997 | 29.3997 | 29.3997 | 29.3997 | 70% | 5.6725 | 32.0823 | 34.2616 | 34.3217 | 34.2569 | 34.2736 | 34.3926 | 34.6338 | 35.0585 | 35.2798 | 35.44 | 35.6823 | 35.9917 | 36.3658 | 36.5618 | 36.4983 | 36.5753 | 36.5753 | 36.5753 | 36.5753 | 36.5753 | 36.5753 | 36.5753 | 36.5753 | 36.5753 | 36.5753 | 36.5753 | 36.5753 | 36.5753 | 36.5753 | 36.5753
65% | 521.4885 | 24.2131 | 26.0239 | 26.2058 | 26.1166 | 26.2014 | 26.2363 | 26.348 | 26.5776 | 26.7708 | 26.8597 | 26.7805 | 27.1128 | 27.1655 | 27.1031 | 27.2282 | 27.2997 | 27.2997 | 27.2997 | 27.2997 | 27.2997 | 27.2997 | 27.2997 | 27.2997 | 27.2997 | 27.2997 | 27.2997 | 27.2997 | 27.2997 | 27.2997 | 27.2997 | 65% | 6.4288 | 29.7907 | 31.8143 | 31.8702 | 31.81 | 31.8255 | 31.936 | 32.1599 | 32.5543 | 32.7599 | 32.9085 | 33.1336 | 33.4208 | 33.7682 | 33.9503 | 33.8913 | 33.9628 | 33.9628 | 33.9628 | 33.9628 | 33.9628 | 33.9628 | 33.9628 | 33.9628 | 33.9628 | 33.9628 | 33.9628 | 33.9628 | 33.9628 | 33.9628 | 33.9628
60% | 812.675 | 22.3505 | 24.022 | 24.19 | 24.1077 | 24.186 | 24.2181 | 24.3212 | 24.5332 | 24.7115 | 24.7936 | 24.7204 | 25.0272 | 25.0758 | 25.0183 | 25.1337 | 25.1997 | 25.1997 | 25.1997 | 25.1997 | 25.1997 | 25.1997 | 25.1997 | 25.1997 | 25.1997 | 25.1997 | 25.1997 | 25.1997 | 25.1997 | 25.1997 | 25.1997 | 60% | 11.3449 | 27.4991 | 29.3671 | 29.4186 | 29.3631 | 29.3774 | 29.4794 | 29.6861 | 30.0502 | 30.2399 | 30.3771 | 30.5848 | 30.85 | 31.1707 | 31.3387 | 31.2842 | 31.3502 | 31.3502 | 31.3502 | 31.3502 | 31.3502 | 31.3502 | 31.3502 | 31.3502 | 31.3502 | 31.3502 | 31.3502 | 31.3502 | 31.3502 | 31.3502 | 31.3502
55% | 1202.1843 | 20.488 | 22.0202 | 22.1742 | 22.0987 | 22.1705 | 22.1999 | 22.2944 | 22.4888 | 22.6522 | 22.7275 | 22.6604 | 22.9416 | 22.9862 | 22.9334 | 23.0392 | 23.0997 | 23.0997 | 23.0997 | 23.0997 | 23.0997 | 23.0997 | 23.0997 | 23.0997 | 23.0997 | 23.0997 | 23.0997 | 23.0997 | 23.0997 | 23.0997 | 23.0997 | 55% | 35.5474 | 25.2075 | 26.9198 | 26.9671 | 26.9161 | 26.9292 | 27.0227 | 27.2122 | 27.546 | 27.7199 | 27.8457 | 28.0361 | 28.2792 | 28.5731 | 28.7272 | 28.6772 | 28.7377 | 28.7377 | 28.7377 | 28.7377 | 28.7377 | 28.7377 | 28.7377 | 28.7377 | 28.7377 | 28.7377 | 28.7377 | 28.7377 | 28.7377 | 28.7377 | 28.7377
50% | 1686.2345 | 18.6255 | 20.0184 | 20.1583 | 20.0897 | 20.155 | 20.1818 | 20.2677 | 20.4443 | 20.5929 | 20.6613 | 20.6004 | 20.856 | 20.8965 | 20.8486 | 20.9448 | 20.9998 | 20.9998 | 20.9998 | 20.9998 | 20.9998 | 20.9998 | 20.9998 | 20.9998 | 20.9998 | 20.9998 | 20.9998 | 20.9998 | 20.9998 | 20.9998 | 20.9998 | 50% | 95.2974 | 22.9159 | 24.4726 | 24.5155 | 24.4692 | 24.4811 | 24.5661 | 24.7384 | 25.0418 | 25.1999 | 25.3143 | 25.4873 | 25.7083 | 25.9756 | 26.1156 | 26.0702 | 26.1252 | 26.1252 | 26.1252 | 26.1252 | 26.1252 | 26.1252 | 26.1252 | 26.1252 | 26.1252 | 26.1252 | 26.1252 | 26.1252 | 26.1252 | 26.1252 | 26.1252
45% | 2129.0649 | 16.7629 | 18.0165 | 18.1425 | 18.0808 | 18.1395 | 18.1636 | 18.2409 | 18.3999 | 18.5336 | 18.5952 | 18.5403 | 18.7704 | 18.8069 | 18.7637 | 18.8503 | 18.8998 | 18.8998 | 18.8998 | 18.8998 | 18.8998 | 18.8998 | 18.8998 | 18.8998 | 18.8998 | 18.8998 | 18.8998 | 18.8998 | 18.8998 | 18.8998 | 18.8998 | 45% | 208.7467 | 20.6243 | 22.0253 | 22.064 | 22.0223 | 22.033 | 22.1095 | 22.2646 | 22.5376 | 22.6799 | 22.7828 | 22.9386 | 23.1375 | 23.378 | 23.504 | 23.4632 | 23.5127 | 23.5127 | 23.5127 | 23.5127 | 23.5127 | 23.5127 | 23.5127 | 23.5127 | 23.5127 | 23.5127 | 23.5127 | 23.5127 | 23.5127 | 23.5127 | 23.5127
40% | 2484.5393 | 14.9004 | 16.0147 | 16.1267 | 16.0718 | 16.124 | 16.1454 | 16.2141 | 16.3555 | 16.4743 | 16.5291 | 16.4803 | 16.6848 | 16.7172 | 16.6788 | 16.7558 | 16.7998 | 16.7998 | 16.7998 | 16.7998 | 16.7998 | 16.7998 | 16.7998 | 16.7998 | 16.7998 | 16.7998 | 16.7998 | 16.7998 | 16.7998 | 16.7998 | 16.7998 | 40% | 380.4333 | 18.3327 | 19.5781 | 19.6124 | 19.5754 | 19.5849 | 19.6529 | 19.7907 | 20.0334 | 20.1599 | 20.2514 | 20.3899 | 20.5667 | 20.7804 | 20.8925 | 20.8562 | 20.9002 | 20.9002 | 20.9002 | 20.9002 | 20.9002 | 20.9002 | 20.9002 | 20.9002 | 20.9002 | 20.9002 | 20.9002 | 20.9002 | 20.9002 | 20.9002 | 20.9002
35% | 2808.248 | 13.0378 | 14.0129 | 14.1108 | 14.0628 | 14.1085 | 14.1272 | 14.1874 | 14.311 | 14.415 | 14.4629 | 14.4203 | 14.5992 | 14.6276 | 14.594 | 14.6613 | 14.6998 | 14.6998 | 14.6998 | 14.6998 | 14.6998 | 14.6998 | 14.6998 | 14.6998 | 14.6998 | 14.6998 | 14.6998 | 14.6998 | 14.6998 | 14.6998 | 14.6998 | 35% | 696.5786 | 16.0411 | 17.1308 | 17.1609 | 17.1285 | 17.1368 | 17.1963 | 17.3169 | 17.5293 | 17.6399 | 17.72 | 17.8411 | 17.9958 | 18.1829 | 18.2809 | 18.2491 | 18.2876 | 18.2876 | 18.2876 | 18.2876 | 18.2876 | 18.2876 | 18.2876 | 18.2876 | 18.2876 | 18.2876 | 18.2876 | 18.2876 | 18.2876 | 18.2876 | 18.2876
30% | 3095.6528 | 11.1753 | 12.011 | 12.095 | 12.0538 | 12.093 | 12.1091 | 12.1606 | 12.2666 | 12.3558 | 12.3968 | 12.3602 | 12.5136 | 12.5379 | 12.5091 | 12.5669 | 12.5999 | 12.5999 | 12.5999 | 12.5999 | 12.5999 | 12.5999 | 12.5999 | 12.5999 | 12.5999 | 12.5999 | 12.5999 | 12.5999 | 12.5999 | 12.5999 | 12.5999 | 30% | 1260.7997 | 13.7495 | 14.6835 | 14.7093 | 14.6815 | 14.6887 | 14.7397 | 14.843 | 15.0251 | 15.1199 | 15.1886 | 15.2924 | 15.425 | 15.5853 | 15.6694 | 15.6421 | 15.6751 | 15.6751 | 15.6751 | 15.6751 | 15.6751 | 15.6751 | 15.6751 | 15.6751 | 15.6751 | 15.6751 | 15.6751 | 15.6751 | 15.6751 | 15.6751 | 15.6751
25% | 3358.8552 | 9.3127 | 10.0092 | 10.0792 | 10.0449 | 10.0775 | 10.0909 | 10.1338 | 10.2222 | 10.2965 | 10.3307 | 10.3002 | 10.428 | 10.4483 | 10.4243 | 10.4724 | 10.4999 | 10.4999 | 10.4999 | 10.4999 | 10.4999 | 10.4999 | 10.4999 | 10.4999 | 10.4999 | 10.4999 | 10.4999 | 10.4999 | 10.4999 | 10.4999 | 10.4999 | 25% | 1965.3198 | 11.458 | 12.2363 | 12.2578 | 12.2346 | 12.2406 | 12.2831 | 12.3692 | 12.5209 | 12.5999 | 12.6571 | 12.7437 | 12.8542 | 12.9878 | 13.0578 | 13.0351 | 13.0626 | 13.0626 | 13.0626 | 13.0626 | 13.0626 | 13.0626 | 13.0626 | 13.0626 | 13.0626 | 13.0626 | 13.0626 | 13.0626 | 13.0626 | 13.0626 | 13.0626
20% | 3588.7791 | 7.4502 | 8.0073 | 8.0633 | 8.0359 | 8.062 | 8.0727 | 8.1071 | 8.1777 | 8.2372 | 8.2645 | 8.2401 | 8.3424 | 8.3586 | 8.3394 | 8.3779 | 8.3999 | 8.3999 | 8.3999 | 8.3999 | 8.3999 | 8.3999 | 8.3999 | 8.3999 | 8.3999 | 8.3999 | 8.3999 | 8.3999 | 8.3999 | 8.3999 | 8.3999 | 20% | 2490.2118 | 9.1664 | 9.789 | 9.8062 | 9.7877 | 9.7925 | 9.8265 | 9.8954 | 10.0167 | 10.08 | 10.1257 | 10.1949 | 10.2833 | 10.3902 | 10.4462 | 10.4281 | 10.4501 | 10.4501 | 10.4501 | 10.4501 | 10.4501 | 10.4501 | 10.4501 | 10.4501 | 10.4501 | 10.4501 | 10.4501 | 10.4501 | 10.4501 | 10.4501 | 10.4501
15% | 3802.4419 | 5.5876 | 6.0055 | 6.0475 | 6.0269 | 6.0465 | 6.0545 | 6.0803 | 6.1333 | 6.1779 | 6.1984 | 6.1801 | 6.2568 | 6.269 | 6.2546 | 6.2834 | 6.2999 | 6.2999 | 6.2999 | 6.2999 | 6.2999 | 6.2999 | 6.2999 | 6.2999 | 6.2999 | 6.2999 | 6.2999 | 6.2999 | 6.2999 | 6.2999 | 6.2999 | 15% | 2997.7083 | 6.8748 | 7.3418 | 7.3547 | 7.3408 | 7.3443 | 7.3698 | 7.4215 | 7.5125 | 7.56 | 7.5943 | 7.6462 | 7.7125 | 7.7927 | 7.8347 | 7.8211 | 7.8376 | 7.8376 | 7.8376 | 7.8376 | 7.8376 | 7.8376 | 7.8376 | 7.8376 | 7.8376 | 7.8376 | 7.8376 | 7.8376 | 7.8376 | 7.8376 | 7.8376
10% | 4024.8025 | 3.7251 | 4.0037 | 4.0317 | 4.0179 | 4.031 | 4.0364 | 4.0535 | 4.0889 | 4.1186 | 4.1323 | 4.1201 | 4.1712 | 4.1793 | 4.1697 | 4.189 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 10% | 3491.5908 | 4.5832 | 4.8945 | 4.9031 | 4.8938 | 4.8962 | 4.9132 | 4.9477 | 5.0084 | 5.04 | 5.0629 | 5.0975 | 5.1417 | 5.1951 | 5.2231 | 5.214 | 5.225 | 5.225 | 5.225 | 5.225 | 5.225 | 5.225 | 5.225 | 5.225 | 5.225 | 5.225 | 5.225 | 5.225 | 5.225 | 5.225 | 5.225
5% | 4239.978 | 1.8625 | 2.0018 | 2.0158 | 2.009 | 2.0155 | 2.0182 | 2.0268 | 2.0444 | 2.0593 | 2.0661 | 2.06 | 2.0856 | 2.0897 | 2.0849 | 2.0945 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 5% | 3955.9766 | 2.2916 | 2.4473 | 2.4516 | 2.4469 | 2.4481 | 2.4566 | 2.4738 | 2.5042 | 2.52 | 2.5314 | 2.5487 | 2.5708 | 2.5976 | 2.6116 | 2.607 | 2.6125 | 2.6125 | 2.6125 | 2.6125 | 2.6125 | 2.6125 | 2.6125 | 2.6125 | 2.6125 | 2.6125 | 2.6125 | 2.6125 | 2.6125 | 2.6125 | 2.6125
9.992e-14% | 4391.6218 | 3.7221e-14 | 4.0005e-14 | 4.0284e-14 | 4.0147e-14 | 4.0278e-14 | 4.0331e-14 | 4.0503e-14 | 4.0856e-14 | 4.1153e-14 | 4.129e-14 | 4.1168e-14 | 4.1679e-14 | 4.176e-14 | 4.1664e-14 | 4.1856e-14 | 4.1966e-14 | 4.1966e-14 | 4.1966e-14 | 4.1966e-14 | 4.1966e-14 | 4.1966e-14 | 4.1966e-14 | 4.1966e-14 | 4.1966e-14 | 4.1966e-14 | 4.1966e-14 | 4.1966e-14 | 4.1966e-14 | 4.1966e-14 | 4.1966e-14 | 9.992e-14% | 4391.6218 | 4.5795e-14 | 4.8906e-14 | 4.8992e-14 | 4.8899e-14 | 4.8923e-14 | 4.9093e-14 | 4.9437e-14 | 5.0044e-14 | 5.0359e-14 | 5.0588e-14 | 5.0934e-14 | 5.1376e-14 | 5.191e-14 | 5.2189e-14 | 5.2099e-14 | 5.2209e-14 | 5.2209e-14 | 5.2209e-14 | 5.2209e-14 | 5.2209e-14 | 5.2209e-14 | 5.2209e-14 | 5.2209e-14 | 5.2209e-14 | 5.2209e-14 | 5.2209e-14 | 5.2209e-14 | 5.2209e-14 | 5.2209e-14 | 5.2209e-14
Option 3
Winter Season | [31 empty] | Winter Season
P50 | [31 empty] | P10
% of MD | Winter - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Winter - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 35.4586 | 39.1719 | 39.5657 | 40.0525 | 40.6988 | 41.3115 | 42.3823 | 45.0754 | 46.5239 | 45.4672 | 48.7387 | 49.3282 | 49.7519 | 51.7491 | 52.0742 | 52.0742 | 52.0742 | 52.0742 | 52.0742 | 52.0742 | 52.0742 | 52.0742 | 52.0742 | 52.0742 | 52.0742 | 52.0742 | 52.0742 | 52.0742 | 52.0742 | 52.0742 | 100% | 0 | 38.8714 | 42.4133 | 42.7801 | 44.046 | 44.0152 | 44.2935 | 45.3822 | 48.5101 | 49.8009 | 48.5791 | 51.9542 | 50.5371 | 51.8122 | 52.731 | 52.3535 | 52.3535 | 52.3535 | 52.3535 | 52.3535 | 52.3535 | 52.3535 | 52.3535 | 52.3535 | 52.3535 | 52.3535 | 52.3535 | 52.3535 | 52.3535 | 52.3535 | 52.3535
99% | 0.2972 | 35.104 | 38.7802 | 39.17 | 39.652 | 40.2918 | 40.8984 | 41.9585 | 44.6246 | 46.0587 | 45.0125 | 48.2513 | 48.8349 | 49.2544 | 51.2316 | 51.5535 | 51.5535 | 51.5535 | 51.5535 | 51.5535 | 51.5535 | 51.5535 | 51.5535 | 51.5535 | 51.5535 | 51.5535 | 51.5535 | 51.5535 | 51.5535 | 51.5535 | 51.5535 | 99% | 0.2972 | 38.4827 | 41.9892 | 42.3523 | 43.6056 | 43.575 | 43.8506 | 44.9284 | 48.025 | 49.3029 | 48.0933 | 51.4346 | 50.0317 | 51.294 | 52.2037 | 51.83 | 51.83 | 51.83 | 51.83 | 51.83 | 51.83 | 51.83 | 51.83 | 51.83 | 51.83 | 51.83 | 51.83 | 51.83 | 51.83 | 51.83 | 51.83
98% | 0.2972 | 34.7495 | 38.3885 | 38.7744 | 39.2514 | 39.8848 | 40.4853 | 41.5347 | 44.1739 | 45.5935 | 44.5578 | 47.764 | 48.3416 | 48.7568 | 50.7141 | 51.0327 | 51.0327 | 51.0327 | 51.0327 | 51.0327 | 51.0327 | 51.0327 | 51.0327 | 51.0327 | 51.0327 | 51.0327 | 51.0327 | 51.0327 | 51.0327 | 51.0327 | 51.0327 | 98% | 0.2972 | 38.0939 | 41.5651 | 41.9245 | 43.1651 | 43.1349 | 43.4077 | 44.4746 | 47.5399 | 48.8049 | 47.6075 | 50.9151 | 49.5264 | 50.7759 | 51.6764 | 51.3064 | 51.3064 | 51.3064 | 51.3064 | 51.3064 | 51.3064 | 51.3064 | 51.3064 | 51.3064 | 51.3064 | 51.3064 | 51.3064 | 51.3064 | 51.3064 | 51.3064 | 51.3064
97% | 0.2972 | 34.3949 | 37.9968 | 38.3787 | 38.8509 | 39.4778 | 40.0722 | 41.1108 | 43.7231 | 45.1282 | 44.1032 | 47.2766 | 47.8483 | 48.2593 | 50.1966 | 50.512 | 50.512 | 50.512 | 50.512 | 50.512 | 50.512 | 50.512 | 50.512 | 50.512 | 50.512 | 50.512 | 50.512 | 50.512 | 50.512 | 50.512 | 50.512 | 97% | 0.2972 | 37.7052 | 41.1409 | 41.4967 | 42.7246 | 42.6947 | 42.9647 | 44.0208 | 47.0548 | 48.3068 | 47.1217 | 50.3955 | 49.021 | 50.2578 | 51.1491 | 50.7829 | 50.7829 | 50.7829 | 50.7829 | 50.7829 | 50.7829 | 50.7829 | 50.7829 | 50.7829 | 50.7829 | 50.7829 | 50.7829 | 50.7829 | 50.7829 | 50.7829 | 50.7829
95% | 1.486 | 33.6857 | 37.2134 | 37.5874 | 38.0499 | 38.6639 | 39.2459 | 40.2632 | 42.8216 | 44.1977 | 43.1938 | 46.3018 | 46.8618 | 47.2643 | 49.1617 | 49.4705 | 49.4705 | 49.4705 | 49.4705 | 49.4705 | 49.4705 | 49.4705 | 49.4705 | 49.4705 | 49.4705 | 49.4705 | 49.4705 | 49.4705 | 49.4705 | 49.4705 | 49.4705 | 95% | 1.486 | 36.9278 | 40.2927 | 40.6411 | 41.8437 | 41.8144 | 42.0789 | 43.1131 | 46.0846 | 47.3108 | 46.1501 | 49.3565 | 48.0103 | 49.2216 | 50.0944 | 49.7358 | 49.7358 | 49.7358 | 49.7358 | 49.7358 | 49.7358 | 49.7358 | 49.7358 | 49.7358 | 49.7358 | 49.7358 | 49.7358 | 49.7358 | 49.7358 | 49.7358 | 49.7358
90% | 8.6188 | 31.9128 | 35.2548 | 35.6091 | 36.0472 | 36.6289 | 37.1804 | 38.1441 | 40.5679 | 41.8715 | 40.9205 | 43.8649 | 44.3954 | 44.7767 | 46.5742 | 46.8668 | 46.8668 | 46.8668 | 46.8668 | 46.8668 | 46.8668 | 46.8668 | 46.8668 | 46.8668 | 46.8668 | 46.8668 | 46.8668 | 46.8668 | 46.8668 | 46.8668 | 46.8668 | 90% | 8.6188 | 34.9842 | 38.172 | 38.5021 | 39.6414 | 39.6137 | 39.8642 | 40.844 | 43.6591 | 44.8208 | 43.7212 | 46.7587 | 45.4834 | 46.6309 | 47.4579 | 47.1181 | 47.1181 | 47.1181 | 47.1181 | 47.1181 | 47.1181 | 47.1181 | 47.1181 | 47.1181 | 47.1181 | 47.1181 | 47.1181 | 47.1181 | 47.1181 | 47.1181 | 47.1181
85% | 40.1218 | 30.1398 | 33.2962 | 33.6308 | 34.0446 | 34.594 | 35.1148 | 36.025 | 38.3141 | 39.5453 | 38.6471 | 41.4279 | 41.9289 | 42.2891 | 43.9867 | 44.2631 | 44.2631 | 44.2631 | 44.2631 | 44.2631 | 44.2631 | 44.2631 | 44.2631 | 44.2631 | 44.2631 | 44.2631 | 44.2631 | 44.2631 | 44.2631 | 44.2631 | 44.2631 | 85% | 40.1218 | 33.0407 | 36.0513 | 36.3631 | 37.4391 | 37.4129 | 37.6495 | 38.5749 | 41.2336 | 42.3307 | 41.2922 | 44.161 | 42.9565 | 44.0403 | 44.8213 | 44.5005 | 44.5005 | 44.5005 | 44.5005 | 44.5005 | 44.5005 | 44.5005 | 44.5005 | 44.5005 | 44.5005 | 44.5005 | 44.5005 | 44.5005 | 44.5005 | 44.5005 | 44.5005
80% | 93.0231 | 28.3669 | 31.3376 | 31.6526 | 32.042 | 32.559 | 33.0492 | 33.9058 | 36.0603 | 37.2191 | 36.3737 | 38.991 | 39.4625 | 39.8015 | 41.3993 | 41.6594 | 41.6594 | 41.6594 | 41.6594 | 41.6594 | 41.6594 | 41.6594 | 41.6594 | 41.6594 | 41.6594 | 41.6594 | 41.6594 | 41.6594 | 41.6594 | 41.6594 | 41.6594 | 80% | 93.0231 | 31.0971 | 33.9307 | 34.2241 | 35.2368 | 35.2121 | 35.4348 | 36.3058 | 38.8081 | 39.8407 | 38.8633 | 41.5633 | 40.4297 | 41.4497 | 42.1848 | 41.8828 | 41.8828 | 41.8828 | 41.8828 | 41.8828 | 41.8828 | 41.8828 | 41.8828 | 41.8828 | 41.8828 | 41.8828 | 41.8828 | 41.8828 | 41.8828 | 41.8828 | 41.8828
75% | 197.0426 | 26.594 | 29.379 | 29.6743 | 30.0394 | 30.5241 | 30.9836 | 31.7867 | 33.8065 | 34.8929 | 34.1004 | 36.554 | 36.9961 | 37.3139 | 38.8118 | 39.0556 | 39.0556 | 39.0556 | 39.0556 | 39.0556 | 39.0556 | 39.0556 | 39.0556 | 39.0556 | 39.0556 | 39.0556 | 39.0556 | 39.0556 | 39.0556 | 39.0556 | 39.0556 | 75% | 197.0426 | 29.1535 | 31.81 | 32.0851 | 33.0345 | 33.0114 | 33.2201 | 34.0367 | 36.3826 | 37.3507 | 36.4343 | 38.9656 | 37.9028 | 38.8591 | 39.5482 | 39.2651 | 39.2651 | 39.2651 | 39.2651 | 39.2651 | 39.2651 | 39.2651 | 39.2651 | 39.2651 | 39.2651 | 39.2651 | 39.2651 | 39.2651 | 39.2651 | 39.2651 | 39.2651
70% | 378.0365 | 24.821 | 27.4204 | 27.696 | 28.0367 | 28.4892 | 28.9181 | 29.6676 | 31.5528 | 32.5668 | 31.827 | 34.1171 | 34.5297 | 34.8263 | 36.2244 | 36.4519 | 36.4519 | 36.4519 | 36.4519 | 36.4519 | 36.4519 | 36.4519 | 36.4519 | 36.4519 | 36.4519 | 36.4519 | 36.4519 | 36.4519 | 36.4519 | 36.4519 | 36.4519 | 70% | 378.0365 | 27.21 | 29.6893 | 29.9461 | 30.8322 | 30.8106 | 31.0055 | 31.7676 | 33.9571 | 34.8606 | 34.0054 | 36.3679 | 35.376 | 36.2685 | 36.9117 | 36.6474 | 36.6474 | 36.6474 | 36.6474 | 36.6474 | 36.6474 | 36.6474 | 36.6474 | 36.6474 | 36.6474 | 36.6474 | 36.6474 | 36.6474 | 36.6474 | 36.6474 | 36.6474
65% | 616.0926 | 23.0481 | 25.4618 | 25.7177 | 26.0341 | 26.4542 | 26.8525 | 27.5485 | 29.299 | 30.2406 | 29.5537 | 31.6802 | 32.0633 | 32.3387 | 33.6369 | 33.8482 | 33.8482 | 33.8482 | 33.8482 | 33.8482 | 33.8482 | 33.8482 | 33.8482 | 33.8482 | 33.8482 | 33.8482 | 33.8482 | 33.8482 | 33.8482 | 33.8482 | 33.8482 | 65% | 616.0926 | 25.2664 | 27.5687 | 27.8071 | 28.6299 | 28.6099 | 28.7908 | 29.4985 | 31.5316 | 32.3706 | 31.5764 | 33.7702 | 32.8491 | 33.6779 | 34.2751 | 34.0298 | 34.0298 | 34.0298 | 34.0298 | 34.0298 | 34.0298 | 34.0298 | 34.0298 | 34.0298 | 34.0298 | 34.0298 | 34.0298 | 34.0298 | 34.0298 | 34.0298 | 34.0298
60% | 934.9866 | 21.2752 | 23.5032 | 23.7394 | 24.0315 | 24.4193 | 24.7869 | 25.4294 | 27.0452 | 27.9144 | 27.2803 | 29.2432 | 29.5969 | 29.8511 | 31.0495 | 31.2445 | 31.2445 | 31.2445 | 31.2445 | 31.2445 | 31.2445 | 31.2445 | 31.2445 | 31.2445 | 31.2445 | 31.2445 | 31.2445 | 31.2445 | 31.2445 | 31.2445 | 31.2445 | 60% | 934.9866 | 23.3228 | 25.448 | 25.6681 | 26.4276 | 26.4091 | 26.5761 | 27.2293 | 29.1061 | 29.8805 | 29.1474 | 31.1725 | 30.3223 | 31.0873 | 31.6386 | 31.4121 | 31.4121 | 31.4121 | 31.4121 | 31.4121 | 31.4121 | 31.4121 | 31.4121 | 31.4121 | 31.4121 | 31.4121 | 31.4121 | 31.4121 | 31.4121 | 31.4121 | 31.4121
55% | 1310.9428 | 19.5022 | 21.5446 | 21.7611 | 22.0289 | 22.3843 | 22.7213 | 23.3103 | 24.7915 | 25.5882 | 25.0069 | 26.8063 | 27.1305 | 27.3635 | 28.462 | 28.6408 | 28.6408 | 28.6408 | 28.6408 | 28.6408 | 28.6408 | 28.6408 | 28.6408 | 28.6408 | 28.6408 | 28.6408 | 28.6408 | 28.6408 | 28.6408 | 28.6408 | 28.6408 | 55% | 1310.9428 | 21.3793 | 23.3273 | 23.5291 | 24.2253 | 24.2083 | 24.3614 | 24.9602 | 26.6806 | 27.3905 | 26.7185 | 28.5748 | 27.7954 | 28.4967 | 29.002 | 28.7944 | 28.7944 | 28.7944 | 28.7944 | 28.7944 | 28.7944 | 28.7944 | 28.7944 | 28.7944 | 28.7944 | 28.7944 | 28.7944 | 28.7944 | 28.7944 | 28.7944 | 28.7944
50% | 1730.2899 | 17.7293 | 19.586 | 19.7828 | 20.0262 | 20.3494 | 20.6558 | 21.1912 | 22.5377 | 23.262 | 22.7336 | 24.3694 | 24.6641 | 24.8759 | 25.8746 | 26.0371 | 26.0371 | 26.0371 | 26.0371 | 26.0371 | 26.0371 | 26.0371 | 26.0371 | 26.0371 | 26.0371 | 26.0371 | 26.0371 | 26.0371 | 26.0371 | 26.0371 | 26.0371 | 50% | 1730.2899 | 19.4357 | 21.2067 | 21.3901 | 22.023 | 22.0076 | 22.1468 | 22.6911 | 24.2551 | 24.9004 | 24.2895 | 25.9771 | 25.2686 | 25.9061 | 26.3655 | 26.1767 | 26.1767 | 26.1767 | 26.1767 | 26.1767 | 26.1767 | 26.1767 | 26.1767 | 26.1767 | 26.1767 | 26.1767 | 26.1767 | 26.1767 | 26.1767 | 26.1767 | 26.1767
45% | 2168.0633 | 15.9564 | 17.6274 | 17.8046 | 18.0236 | 18.3145 | 18.5902 | 19.072 | 20.2839 | 20.9358 | 20.4602 | 21.9324 | 22.1977 | 22.3883 | 23.2871 | 23.4334 | 23.4334 | 23.4334 | 23.4334 | 23.4334 | 23.4334 | 23.4334 | 23.4334 | 23.4334 | 23.4334 | 23.4334 | 23.4334 | 23.4334 | 23.4334 | 23.4334 | 23.4334 | 45% | 2168.0633 | 17.4921 | 19.086 | 19.2511 | 19.8207 | 19.8068 | 19.9321 | 20.422 | 21.8296 | 22.4104 | 21.8606 | 23.3794 | 22.7417 | 23.3155 | 23.7289 | 23.5591 | 23.5591 | 23.5591 | 23.5591 | 23.5591 | 23.5591 | 23.5591 | 23.5591 | 23.5591 | 23.5591 | 23.5591 | 23.5591 | 23.5591 | 23.5591 | 23.5591 | 23.5591
40% | 2609.7004 | 14.1835 | 15.6688 | 15.8263 | 16.021 | 16.2795 | 16.5246 | 16.9529 | 18.0302 | 18.6096 | 18.1869 | 19.4955 | 19.7313 | 19.9008 | 20.6996 | 20.8297 | 20.8297 | 20.8297 | 20.8297 | 20.8297 | 20.8297 | 20.8297 | 20.8297 | 20.8297 | 20.8297 | 20.8297 | 20.8297 | 20.8297 | 20.8297 | 20.8297 | 20.8297 | 40% | 2609.7004 | 15.5485 | 16.9653 | 17.1121 | 17.6184 | 17.6061 | 17.7174 | 18.1529 | 19.404 | 19.9203 | 19.4316 | 20.7817 | 20.2148 | 20.7249 | 21.0924 | 20.9414 | 20.9414 | 20.9414 | 20.9414 | 20.9414 | 20.9414 | 20.9414 | 20.9414 | 20.9414 | 20.9414 | 20.9414 | 20.9414 | 20.9414 | 20.9414 | 20.9414 | 20.9414
35% | 2998.1389 | 12.4105 | 13.7102 | 13.848 | 14.0184 | 14.2446 | 14.459 | 14.8338 | 15.7764 | 16.2834 | 15.9135 | 17.0586 | 17.2649 | 17.4132 | 18.1122 | 18.226 | 18.226 | 18.226 | 18.226 | 18.226 | 18.226 | 18.226 | 18.226 | 18.226 | 18.226 | 18.226 | 18.226 | 18.226 | 18.226 | 18.226 | 18.226 | 35% | 2998.1389 | 13.605 | 14.8447 | 14.973 | 15.4161 | 15.4053 | 15.5027 | 15.8838 | 16.9785 | 17.4303 | 17.0027 | 18.184 | 17.688 | 18.1343 | 18.4558 | 18.3237 | 18.3237 | 18.3237 | 18.3237 | 18.3237 | 18.3237 | 18.3237 | 18.3237 | 18.3237 | 18.3237 | 18.3237 | 18.3237 | 18.3237 | 18.3237 | 18.3237 | 18.3237
30% | 3309.3057 | 10.6376 | 11.7516 | 11.8697 | 12.0157 | 12.2096 | 12.3935 | 12.7147 | 13.5226 | 13.9572 | 13.6402 | 14.6216 | 14.7985 | 14.9256 | 15.5247 | 15.6223 | 15.6223 | 15.6223 | 15.6223 | 15.6223 | 15.6223 | 15.6223 | 15.6223 | 15.6223 | 15.6223 | 15.6223 | 15.6223 | 15.6223 | 15.6223 | 15.6223 | 15.6223 | 30% | 3309.3057 | 11.6614 | 12.724 | 12.834 | 13.2138 | 13.2046 | 13.2881 | 13.6147 | 14.553 | 14.9403 | 14.5737 | 15.5862 | 15.1611 | 15.5436 | 15.8193 | 15.706 | 15.706 | 15.706 | 15.706 | 15.706 | 15.706 | 15.706 | 15.706 | 15.706 | 15.706 | 15.706 | 15.706 | 15.706 | 15.706 | 15.706 | 15.706
25% | 3537.8514 | 8.8647 | 9.793 | 9.8914 | 10.0131 | 10.1747 | 10.3279 | 10.5956 | 11.2688 | 11.631 | 11.3668 | 12.1847 | 12.332 | 12.438 | 12.9373 | 13.0185 | 13.0185 | 13.0185 | 13.0185 | 13.0185 | 13.0185 | 13.0185 | 13.0185 | 13.0185 | 13.0185 | 13.0185 | 13.0185 | 13.0185 | 13.0185 | 13.0185 | 13.0185 | 25% | 3537.8514 | 9.7178 | 10.6033 | 10.695 | 11.0115 | 11.0038 | 11.0734 | 11.3456 | 12.1275 | 12.4502 | 12.1448 | 12.9885 | 12.6343 | 12.953 | 13.1827 | 13.0884 | 13.0884 | 13.0884 | 13.0884 | 13.0884 | 13.0884 | 13.0884 | 13.0884 | 13.0884 | 13.0884 | 13.0884 | 13.0884 | 13.0884 | 13.0884 | 13.0884 | 13.0884
20% | 3731.0305 | 7.0917 | 7.8344 | 7.9131 | 8.0105 | 8.1398 | 8.2623 | 8.4765 | 9.0151 | 9.3048 | 9.0934 | 9.7477 | 9.8656 | 9.9504 | 10.3498 | 10.4148 | 10.4148 | 10.4148 | 10.4148 | 10.4148 | 10.4148 | 10.4148 | 10.4148 | 10.4148 | 10.4148 | 10.4148 | 10.4148 | 10.4148 | 10.4148 | 10.4148 | 10.4148 | 20% | 3731.0305 | 7.7743 | 8.4827 | 8.556 | 8.8092 | 8.803 | 8.8587 | 9.0764 | 9.702 | 9.9602 | 9.7158 | 10.3908 | 10.1074 | 10.3624 | 10.5462 | 10.4707 | 10.4707 | 10.4707 | 10.4707 | 10.4707 | 10.4707 | 10.4707 | 10.4707 | 10.4707 | 10.4707 | 10.4707 | 10.4707 | 10.4707 | 10.4707 | 10.4707 | 10.4707
15% | 3910.2412 | 5.3188 | 5.8758 | 5.9349 | 6.0079 | 6.1048 | 6.1967 | 6.3573 | 6.7613 | 6.9786 | 6.8201 | 7.3108 | 7.3992 | 7.4628 | 7.7624 | 7.8111 | 7.8111 | 7.8111 | 7.8111 | 7.8111 | 7.8111 | 7.8111 | 7.8111 | 7.8111 | 7.8111 | 7.8111 | 7.8111 | 7.8111 | 7.8111 | 7.8111 | 7.8111 | 15% | 3910.2412 | 5.8307 | 6.362 | 6.417 | 6.6069 | 6.6023 | 6.644 | 6.8073 | 7.2765 | 7.4701 | 7.2869 | 7.7931 | 7.5806 | 7.7718 | 7.9096 | 7.853 | 7.853 | 7.853 | 7.853 | 7.853 | 7.853 | 7.853 | 7.853 | 7.853 | 7.853 | 7.853 | 7.853 | 7.853 | 7.853 | 7.853 | 7.853
10% | 4075.1864 | 3.5459 | 3.9172 | 3.9566 | 4.0052 | 4.0699 | 4.1312 | 4.2382 | 4.5075 | 4.6524 | 4.5467 | 4.8739 | 4.9328 | 4.9752 | 5.1749 | 5.2074 | 5.2074 | 5.2074 | 5.2074 | 5.2074 | 5.2074 | 5.2074 | 5.2074 | 5.2074 | 5.2074 | 5.2074 | 5.2074 | 5.2074 | 5.2074 | 5.2074 | 5.2074 | 10% | 4075.1864 | 3.8871 | 4.2413 | 4.278 | 4.4046 | 4.4015 | 4.4294 | 4.5382 | 4.851 | 4.9801 | 4.8579 | 5.1954 | 5.0537 | 5.1812 | 5.2731 | 5.2353 | 5.2353 | 5.2353 | 5.2353 | 5.2353 | 5.2353 | 5.2353 | 5.2353 | 5.2353 | 5.2353 | 5.2353 | 5.2353 | 5.2353 | 5.2353 | 5.2353 | 5.2353
5% | 4251.7223 | 1.7729 | 1.9586 | 1.9783 | 2.0026 | 2.0349 | 2.0656 | 2.1191 | 2.2538 | 2.3262 | 2.2734 | 2.4369 | 2.4664 | 2.4876 | 2.5875 | 2.6037 | 2.6037 | 2.6037 | 2.6037 | 2.6037 | 2.6037 | 2.6037 | 2.6037 | 2.6037 | 2.6037 | 2.6037 | 2.6037 | 2.6037 | 2.6037 | 2.6037 | 2.6037 | 5% | 4251.7223 | 1.9436 | 2.1207 | 2.139 | 2.2023 | 2.2008 | 2.2147 | 2.2691 | 2.4255 | 2.49 | 2.429 | 2.5977 | 2.5269 | 2.5906 | 2.6365 | 2.6177 | 2.6177 | 2.6177 | 2.6177 | 2.6177 | 2.6177 | 2.6177 | 2.6177 | 2.6177 | 2.6177 | 2.6177 | 2.6177 | 2.6177 | 2.6177 | 2.6177 | 2.6177
9.992e-14% | 4391.7028 | 3.543e-14 | 3.9141e-14 | 3.9534e-14 | 4.002e-14 | 4.0666e-14 | 4.1279e-14 | 4.2348e-14 | 4.5039e-14 | 4.6487e-14 | 4.5431e-14 | 4.87e-14 | 4.9289e-14 | 4.9712e-14 | 5.1708e-14 | 5.2033e-14 | 5.2033e-14 | 5.2033e-14 | 5.2033e-14 | 5.2033e-14 | 5.2033e-14 | 5.2033e-14 | 5.2033e-14 | 5.2033e-14 | 5.2033e-14 | 5.2033e-14 | 5.2033e-14 | 5.2033e-14 | 5.2033e-14 | 5.2033e-14 | 5.2033e-14 | 9.992e-14% | 4391.7028 | 3.884e-14 | 4.2379e-14 | 4.2746e-14 | 4.4011e-14 | 4.398e-14 | 4.4258e-14 | 4.5346e-14 | 4.8471e-14 | 4.9761e-14 | 4.854e-14 | 5.1913e-14 | 5.0497e-14 | 5.1771e-14 | 5.2689e-14 | 5.2312e-14 | 5.2312e-14 | 5.2312e-14 | 5.2312e-14 | 5.2312e-14 | 5.2312e-14 | 5.2312e-14 | 5.2312e-14 | 5.2312e-14 | 5.2312e-14 | 5.2312e-14 | 5.2312e-14 | 5.2312e-14 | 5.2312e-14 | 5.2312e-14 | 5.2312e-14
Summer Season | [31 empty] | Summer Season
P50 | [31 empty] | P10
% of MD | Summer - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Summer - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 37.2509 | 40.0367 | 40.3167 | 40.1794 | 40.3099 | 40.3635 | 40.5354 | 40.8886 | 41.1859 | 41.3227 | 41.2007 | 41.712 | 41.7931 | 41.6971 | 41.8895 | 41.9995 | 41.9995 | 41.9995 | 41.9995 | 41.9995 | 41.9995 | 41.9995 | 41.9995 | 41.9995 | 41.9995 | 41.9995 | 41.9995 | 41.9995 | 41.9995 | 41.9995 | 100% | 0 | 45.8318 | 48.9452 | 49.0311 | 48.9384 | 48.9623 | 49.1323 | 49.4768 | 50.0836 | 50.3998 | 50.6285 | 50.9747 | 51.4167 | 51.9511 | 52.2312 | 52.1404 | 52.2504 | 52.2504 | 52.2504 | 52.2504 | 52.2504 | 52.2504 | 52.2504 | 52.2504 | 52.2504 | 52.2504 | 52.2504 | 52.2504 | 52.2504 | 52.2504 | 52.2504
99% | 0.37816 | 36.8784 | 39.6364 | 39.9135 | 39.7777 | 39.9068 | 39.9599 | 40.13 | 40.4798 | 40.774 | 40.9094 | 40.7887 | 41.2949 | 41.3751 | 41.2801 | 41.4706 | 41.5795 | 41.5795 | 41.5795 | 41.5795 | 41.5795 | 41.5795 | 41.5795 | 41.5795 | 41.5795 | 41.5795 | 41.5795 | 41.5795 | 41.5795 | 41.5795 | 41.5795 | 99% | 0 | 45.3735 | 48.4557 | 48.5408 | 48.4491 | 48.4726 | 48.6409 | 48.982 | 49.5828 | 49.8958 | 50.1222 | 50.465 | 50.9025 | 51.4316 | 51.7089 | 51.619 | 51.7279 | 51.7279 | 51.7279 | 51.7279 | 51.7279 | 51.7279 | 51.7279 | 51.7279 | 51.7279 | 51.7279 | 51.7279 | 51.7279 | 51.7279 | 51.7279 | 51.7279
98% | 0.37816 | 36.5059 | 39.236 | 39.5103 | 39.3759 | 39.5037 | 39.5563 | 39.7246 | 40.0709 | 40.3621 | 40.4962 | 40.3767 | 40.8777 | 40.9572 | 40.8632 | 41.0517 | 41.1595 | 41.1595 | 41.1595 | 41.1595 | 41.1595 | 41.1595 | 41.1595 | 41.1595 | 41.1595 | 41.1595 | 41.1595 | 41.1595 | 41.1595 | 41.1595 | 41.1595 | 98% | 0 | 44.9152 | 47.9662 | 48.0504 | 47.9597 | 47.983 | 48.1496 | 48.4873 | 49.0819 | 49.3918 | 49.6159 | 49.9552 | 50.3883 | 50.9121 | 51.1866 | 51.0976 | 51.2054 | 51.2054 | 51.2054 | 51.2054 | 51.2054 | 51.2054 | 51.2054 | 51.2054 | 51.2054 | 51.2054 | 51.2054 | 51.2054 | 51.2054 | 51.2054 | 51.2054
97% | 0.37816 | 36.1334 | 38.8356 | 39.1072 | 38.9741 | 39.1006 | 39.1526 | 39.3193 | 39.662 | 39.9503 | 40.083 | 39.9647 | 40.4606 | 40.5393 | 40.4462 | 40.6328 | 40.7395 | 40.7395 | 40.7395 | 40.7395 | 40.7395 | 40.7395 | 40.7395 | 40.7395 | 40.7395 | 40.7395 | 40.7395 | 40.7395 | 40.7395 | 40.7395 | 40.7395 | 97% | 0.37816 | 44.4569 | 47.4768 | 47.5601 | 47.4703 | 47.4934 | 47.6583 | 47.9925 | 48.5811 | 48.8878 | 49.1097 | 49.4455 | 49.8742 | 50.3926 | 50.6643 | 50.5762 | 50.6829 | 50.6829 | 50.6829 | 50.6829 | 50.6829 | 50.6829 | 50.6829 | 50.6829 | 50.6829 | 50.6829 | 50.6829 | 50.6829 | 50.6829 | 50.6829 | 50.6829
95% | 0.75633 | 35.3884 | 38.0349 | 38.3008 | 38.1705 | 38.2944 | 38.3454 | 38.5086 | 38.8442 | 39.1266 | 39.2565 | 39.1407 | 39.6264 | 39.7034 | 39.6123 | 39.7951 | 39.8996 | 39.8996 | 39.8996 | 39.8996 | 39.8996 | 39.8996 | 39.8996 | 39.8996 | 39.8996 | 39.8996 | 39.8996 | 39.8996 | 39.8996 | 39.8996 | 39.8996 | 95% | 0.37816 | 43.5402 | 46.4979 | 46.5795 | 46.4915 | 46.5141 | 46.6757 | 47.003 | 47.5794 | 47.8798 | 48.0971 | 48.426 | 48.8458 | 49.3536 | 49.6196 | 49.5334 | 49.6379 | 49.6379 | 49.6379 | 49.6379 | 49.6379 | 49.6379 | 49.6379 | 49.6379 | 49.6379 | 49.6379 | 49.6379 | 49.6379 | 49.6379 | 49.6379 | 49.6379
90% | 9.0759 | 33.5258 | 36.0331 | 36.285 | 36.1615 | 36.2789 | 36.3272 | 36.4818 | 36.7998 | 37.0673 | 37.1904 | 37.0807 | 37.5408 | 37.6138 | 37.5274 | 37.7006 | 37.7996 | 37.7996 | 37.7996 | 37.7996 | 37.7996 | 37.7996 | 37.7996 | 37.7996 | 37.7996 | 37.7996 | 37.7996 | 37.7996 | 37.7996 | 37.7996 | 37.7996 | 90% | 0.75633 | 41.2486 | 44.0506 | 44.128 | 44.0446 | 44.066 | 44.219 | 44.5291 | 45.0752 | 45.3598 | 45.5657 | 45.8772 | 46.275 | 46.756 | 47.0081 | 46.9264 | 47.0254 | 47.0254 | 47.0254 | 47.0254 | 47.0254 | 47.0254 | 47.0254 | 47.0254 | 47.0254 | 47.0254 | 47.0254 | 47.0254 | 47.0254 | 47.0254 | 47.0254
85% | 40.4636 | 31.6633 | 34.0312 | 34.2692 | 34.1525 | 34.2634 | 34.309 | 34.455 | 34.7554 | 35.008 | 35.1243 | 35.0206 | 35.4552 | 35.5241 | 35.4425 | 35.6061 | 35.6996 | 35.6996 | 35.6996 | 35.6996 | 35.6996 | 35.6996 | 35.6996 | 35.6996 | 35.6996 | 35.6996 | 35.6996 | 35.6996 | 35.6996 | 35.6996 | 35.6996 | 85% | 1.1345 | 38.957 | 41.6034 | 41.6764 | 41.5977 | 41.6179 | 41.7624 | 42.0553 | 42.5711 | 42.8398 | 43.0342 | 43.3285 | 43.7042 | 44.1585 | 44.3965 | 44.3193 | 44.4128 | 44.4128 | 44.4128 | 44.4128 | 44.4128 | 44.4128 | 44.4128 | 44.4128 | 44.4128 | 44.4128 | 44.4128 | 44.4128 | 44.4128 | 44.4128 | 44.4128
80% | 94.5411 | 29.8007 | 32.0294 | 32.2533 | 32.1436 | 32.2479 | 32.2908 | 32.4283 | 32.7109 | 32.9487 | 33.0581 | 32.9606 | 33.3696 | 33.4345 | 33.3577 | 33.5116 | 33.5996 | 33.5996 | 33.5996 | 33.5996 | 33.5996 | 33.5996 | 33.5996 | 33.5996 | 33.5996 | 33.5996 | 33.5996 | 33.5996 | 33.5996 | 33.5996 | 33.5996 | 80% | 2.6471 | 36.6655 | 39.1561 | 39.2249 | 39.1508 | 39.1698 | 39.3058 | 39.5815 | 40.0669 | 40.3198 | 40.5028 | 40.7798 | 41.1333 | 41.5609 | 41.785 | 41.7123 | 41.8003 | 41.8003 | 41.8003 | 41.8003 | 41.8003 | 41.8003 | 41.8003 | 41.8003 | 41.8003 | 41.8003 | 41.8003 | 41.8003 | 41.8003 | 41.8003 | 41.8003
75% | 197.0236 | 27.9382 | 30.0275 | 30.2375 | 30.1346 | 30.2324 | 30.2726 | 30.4015 | 30.6665 | 30.8894 | 30.992 | 30.9005 | 31.284 | 31.3448 | 31.2728 | 31.4172 | 31.4997 | 31.4997 | 31.4997 | 31.4997 | 31.4997 | 31.4997 | 31.4997 | 31.4997 | 31.4997 | 31.4997 | 31.4997 | 31.4997 | 31.4997 | 31.4997 | 31.4997 | 75% | 3.4035 | 34.3739 | 36.7089 | 36.7733 | 36.7038 | 36.7217 | 36.8492 | 37.1076 | 37.5627 | 37.7998 | 37.9714 | 38.231 | 38.5625 | 38.9633 | 39.1734 | 39.1053 | 39.1878 | 39.1878 | 39.1878 | 39.1878 | 39.1878 | 39.1878 | 39.1878 | 39.1878 | 39.1878 | 39.1878 | 39.1878 | 39.1878 | 39.1878 | 39.1878 | 39.1878
70% | 336.9444 | 26.0756 | 28.0257 | 28.2217 | 28.1256 | 28.2169 | 28.2545 | 28.3747 | 28.6221 | 28.8301 | 28.9259 | 28.8405 | 29.1984 | 29.2552 | 29.188 | 29.3227 | 29.3997 | 29.3997 | 29.3997 | 29.3997 | 29.3997 | 29.3997 | 29.3997 | 29.3997 | 29.3997 | 29.3997 | 29.3997 | 29.3997 | 29.3997 | 29.3997 | 29.3997 | 70% | 5.6725 | 32.0823 | 34.2616 | 34.3217 | 34.2569 | 34.2736 | 34.3926 | 34.6338 | 35.0585 | 35.2798 | 35.44 | 35.6823 | 35.9917 | 36.3658 | 36.5618 | 36.4983 | 36.5753 | 36.5753 | 36.5753 | 36.5753 | 36.5753 | 36.5753 | 36.5753 | 36.5753 | 36.5753 | 36.5753 | 36.5753 | 36.5753 | 36.5753 | 36.5753 | 36.5753
65% | 521.4885 | 24.2131 | 26.0239 | 26.2058 | 26.1166 | 26.2014 | 26.2363 | 26.348 | 26.5776 | 26.7708 | 26.8597 | 26.7805 | 27.1128 | 27.1655 | 27.1031 | 27.2282 | 27.2997 | 27.2997 | 27.2997 | 27.2997 | 27.2997 | 27.2997 | 27.2997 | 27.2997 | 27.2997 | 27.2997 | 27.2997 | 27.2997 | 27.2997 | 27.2997 | 27.2997 | 65% | 6.4288 | 29.7907 | 31.8143 | 31.8702 | 31.81 | 31.8255 | 31.936 | 32.1599 | 32.5543 | 32.7599 | 32.9085 | 33.1336 | 33.4208 | 33.7682 | 33.9503 | 33.8913 | 33.9628 | 33.9628 | 33.9628 | 33.9628 | 33.9628 | 33.9628 | 33.9628 | 33.9628 | 33.9628 | 33.9628 | 33.9628 | 33.9628 | 33.9628 | 33.9628 | 33.9628
60% | 812.675 | 22.3505 | 24.022 | 24.19 | 24.1077 | 24.186 | 24.2181 | 24.3212 | 24.5332 | 24.7115 | 24.7936 | 24.7204 | 25.0272 | 25.0758 | 25.0183 | 25.1337 | 25.1997 | 25.1997 | 25.1997 | 25.1997 | 25.1997 | 25.1997 | 25.1997 | 25.1997 | 25.1997 | 25.1997 | 25.1997 | 25.1997 | 25.1997 | 25.1997 | 25.1997 | 60% | 11.3449 | 27.4991 | 29.3671 | 29.4186 | 29.3631 | 29.3774 | 29.4794 | 29.6861 | 30.0502 | 30.2399 | 30.3771 | 30.5848 | 30.85 | 31.1707 | 31.3387 | 31.2842 | 31.3502 | 31.3502 | 31.3502 | 31.3502 | 31.3502 | 31.3502 | 31.3502 | 31.3502 | 31.3502 | 31.3502 | 31.3502 | 31.3502 | 31.3502 | 31.3502 | 31.3502
55% | 1202.1843 | 20.488 | 22.0202 | 22.1742 | 22.0987 | 22.1705 | 22.1999 | 22.2944 | 22.4888 | 22.6522 | 22.7275 | 22.6604 | 22.9416 | 22.9862 | 22.9334 | 23.0392 | 23.0997 | 23.0997 | 23.0997 | 23.0997 | 23.0997 | 23.0997 | 23.0997 | 23.0997 | 23.0997 | 23.0997 | 23.0997 | 23.0997 | 23.0997 | 23.0997 | 23.0997 | 55% | 35.5474 | 25.2075 | 26.9198 | 26.9671 | 26.9161 | 26.9292 | 27.0227 | 27.2122 | 27.546 | 27.7199 | 27.8457 | 28.0361 | 28.2792 | 28.5731 | 28.7272 | 28.6772 | 28.7377 | 28.7377 | 28.7377 | 28.7377 | 28.7377 | 28.7377 | 28.7377 | 28.7377 | 28.7377 | 28.7377 | 28.7377 | 28.7377 | 28.7377 | 28.7377 | 28.7377
50% | 1686.2345 | 18.6255 | 20.0184 | 20.1583 | 20.0897 | 20.155 | 20.1818 | 20.2677 | 20.4443 | 20.5929 | 20.6613 | 20.6004 | 20.856 | 20.8965 | 20.8486 | 20.9448 | 20.9998 | 20.9998 | 20.9998 | 20.9998 | 20.9998 | 20.9998 | 20.9998 | 20.9998 | 20.9998 | 20.9998 | 20.9998 | 20.9998 | 20.9998 | 20.9998 | 20.9998 | 50% | 95.2974 | 22.9159 | 24.4726 | 24.5155 | 24.4692 | 24.4811 | 24.5661 | 24.7384 | 25.0418 | 25.1999 | 25.3143 | 25.4873 | 25.7083 | 25.9756 | 26.1156 | 26.0702 | 26.1252 | 26.1252 | 26.1252 | 26.1252 | 26.1252 | 26.1252 | 26.1252 | 26.1252 | 26.1252 | 26.1252 | 26.1252 | 26.1252 | 26.1252 | 26.1252 | 26.1252
45% | 2129.0649 | 16.7629 | 18.0165 | 18.1425 | 18.0808 | 18.1395 | 18.1636 | 18.2409 | 18.3999 | 18.5336 | 18.5952 | 18.5403 | 18.7704 | 18.8069 | 18.7637 | 18.8503 | 18.8998 | 18.8998 | 18.8998 | 18.8998 | 18.8998 | 18.8998 | 18.8998 | 18.8998 | 18.8998 | 18.8998 | 18.8998 | 18.8998 | 18.8998 | 18.8998 | 18.8998 | 45% | 208.7467 | 20.6243 | 22.0253 | 22.064 | 22.0223 | 22.033 | 22.1095 | 22.2646 | 22.5376 | 22.6799 | 22.7828 | 22.9386 | 23.1375 | 23.378 | 23.504 | 23.4632 | 23.5127 | 23.5127 | 23.5127 | 23.5127 | 23.5127 | 23.5127 | 23.5127 | 23.5127 | 23.5127 | 23.5127 | 23.5127 | 23.5127 | 23.5127 | 23.5127 | 23.5127
40% | 2484.5393 | 14.9004 | 16.0147 | 16.1267 | 16.0718 | 16.124 | 16.1454 | 16.2141 | 16.3555 | 16.4743 | 16.5291 | 16.4803 | 16.6848 | 16.7172 | 16.6788 | 16.7558 | 16.7998 | 16.7998 | 16.7998 | 16.7998 | 16.7998 | 16.7998 | 16.7998 | 16.7998 | 16.7998 | 16.7998 | 16.7998 | 16.7998 | 16.7998 | 16.7998 | 16.7998 | 40% | 380.4333 | 18.3327 | 19.5781 | 19.6124 | 19.5754 | 19.5849 | 19.6529 | 19.7907 | 20.0334 | 20.1599 | 20.2514 | 20.3899 | 20.5667 | 20.7804 | 20.8925 | 20.8562 | 20.9002 | 20.9002 | 20.9002 | 20.9002 | 20.9002 | 20.9002 | 20.9002 | 20.9002 | 20.9002 | 20.9002 | 20.9002 | 20.9002 | 20.9002 | 20.9002 | 20.9002
35% | 2808.248 | 13.0378 | 14.0129 | 14.1108 | 14.0628 | 14.1085 | 14.1272 | 14.1874 | 14.311 | 14.415 | 14.4629 | 14.4203 | 14.5992 | 14.6276 | 14.594 | 14.6613 | 14.6998 | 14.6998 | 14.6998 | 14.6998 | 14.6998 | 14.6998 | 14.6998 | 14.6998 | 14.6998 | 14.6998 | 14.6998 | 14.6998 | 14.6998 | 14.6998 | 14.6998 | 35% | 696.5786 | 16.0411 | 17.1308 | 17.1609 | 17.1285 | 17.1368 | 17.1963 | 17.3169 | 17.5293 | 17.6399 | 17.72 | 17.8411 | 17.9958 | 18.1829 | 18.2809 | 18.2491 | 18.2876 | 18.2876 | 18.2876 | 18.2876 | 18.2876 | 18.2876 | 18.2876 | 18.2876 | 18.2876 | 18.2876 | 18.2876 | 18.2876 | 18.2876 | 18.2876 | 18.2876
30% | 3095.6528 | 11.1753 | 12.011 | 12.095 | 12.0538 | 12.093 | 12.1091 | 12.1606 | 12.2666 | 12.3558 | 12.3968 | 12.3602 | 12.5136 | 12.5379 | 12.5091 | 12.5669 | 12.5999 | 12.5999 | 12.5999 | 12.5999 | 12.5999 | 12.5999 | 12.5999 | 12.5999 | 12.5999 | 12.5999 | 12.5999 | 12.5999 | 12.5999 | 12.5999 | 12.5999 | 30% | 1260.7997 | 13.7495 | 14.6835 | 14.7093 | 14.6815 | 14.6887 | 14.7397 | 14.843 | 15.0251 | 15.1199 | 15.1886 | 15.2924 | 15.425 | 15.5853 | 15.6694 | 15.6421 | 15.6751 | 15.6751 | 15.6751 | 15.6751 | 15.6751 | 15.6751 | 15.6751 | 15.6751 | 15.6751 | 15.6751 | 15.6751 | 15.6751 | 15.6751 | 15.6751 | 15.6751
25% | 3358.8552 | 9.3127 | 10.0092 | 10.0792 | 10.0449 | 10.0775 | 10.0909 | 10.1338 | 10.2222 | 10.2965 | 10.3307 | 10.3002 | 10.428 | 10.4483 | 10.4243 | 10.4724 | 10.4999 | 10.4999 | 10.4999 | 10.4999 | 10.4999 | 10.4999 | 10.4999 | 10.4999 | 10.4999 | 10.4999 | 10.4999 | 10.4999 | 10.4999 | 10.4999 | 10.4999 | 25% | 1965.3198 | 11.458 | 12.2363 | 12.2578 | 12.2346 | 12.2406 | 12.2831 | 12.3692 | 12.5209 | 12.5999 | 12.6571 | 12.7437 | 12.8542 | 12.9878 | 13.0578 | 13.0351 | 13.0626 | 13.0626 | 13.0626 | 13.0626 | 13.0626 | 13.0626 | 13.0626 | 13.0626 | 13.0626 | 13.0626 | 13.0626 | 13.0626 | 13.0626 | 13.0626 | 13.0626
20% | 3588.7791 | 7.4502 | 8.0073 | 8.0633 | 8.0359 | 8.062 | 8.0727 | 8.1071 | 8.1777 | 8.2372 | 8.2645 | 8.2401 | 8.3424 | 8.3586 | 8.3394 | 8.3779 | 8.3999 | 8.3999 | 8.3999 | 8.3999 | 8.3999 | 8.3999 | 8.3999 | 8.3999 | 8.3999 | 8.3999 | 8.3999 | 8.3999 | 8.3999 | 8.3999 | 8.3999 | 20% | 2490.2118 | 9.1664 | 9.789 | 9.8062 | 9.7877 | 9.7925 | 9.8265 | 9.8954 | 10.0167 | 10.08 | 10.1257 | 10.1949 | 10.2833 | 10.3902 | 10.4462 | 10.4281 | 10.4501 | 10.4501 | 10.4501 | 10.4501 | 10.4501 | 10.4501 | 10.4501 | 10.4501 | 10.4501 | 10.4501 | 10.4501 | 10.4501 | 10.4501 | 10.4501 | 10.4501
15% | 3802.4419 | 5.5876 | 6.0055 | 6.0475 | 6.0269 | 6.0465 | 6.0545 | 6.0803 | 6.1333 | 6.1779 | 6.1984 | 6.1801 | 6.2568 | 6.269 | 6.2546 | 6.2834 | 6.2999 | 6.2999 | 6.2999 | 6.2999 | 6.2999 | 6.2999 | 6.2999 | 6.2999 | 6.2999 | 6.2999 | 6.2999 | 6.2999 | 6.2999 | 6.2999 | 6.2999 | 15% | 2997.7083 | 6.8748 | 7.3418 | 7.3547 | 7.3408 | 7.3443 | 7.3698 | 7.4215 | 7.5125 | 7.56 | 7.5943 | 7.6462 | 7.7125 | 7.7927 | 7.8347 | 7.8211 | 7.8376 | 7.8376 | 7.8376 | 7.8376 | 7.8376 | 7.8376 | 7.8376 | 7.8376 | 7.8376 | 7.8376 | 7.8376 | 7.8376 | 7.8376 | 7.8376 | 7.8376
10% | 4024.8025 | 3.7251 | 4.0037 | 4.0317 | 4.0179 | 4.031 | 4.0364 | 4.0535 | 4.0889 | 4.1186 | 4.1323 | 4.1201 | 4.1712 | 4.1793 | 4.1697 | 4.189 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 10% | 3491.5908 | 4.5832 | 4.8945 | 4.9031 | 4.8938 | 4.8962 | 4.9132 | 4.9477 | 5.0084 | 5.04 | 5.0629 | 5.0975 | 5.1417 | 5.1951 | 5.2231 | 5.214 | 5.225 | 5.225 | 5.225 | 5.225 | 5.225 | 5.225 | 5.225 | 5.225 | 5.225 | 5.225 | 5.225 | 5.225 | 5.225 | 5.225 | 5.225
5% | 4239.978 | 1.8625 | 2.0018 | 2.0158 | 2.009 | 2.0155 | 2.0182 | 2.0268 | 2.0444 | 2.0593 | 2.0661 | 2.06 | 2.0856 | 2.0897 | 2.0849 | 2.0945 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 5% | 3955.9766 | 2.2916 | 2.4473 | 2.4516 | 2.4469 | 2.4481 | 2.4566 | 2.4738 | 2.5042 | 2.52 | 2.5314 | 2.5487 | 2.5708 | 2.5976 | 2.6116 | 2.607 | 2.6125 | 2.6125 | 2.6125 | 2.6125 | 2.6125 | 2.6125 | 2.6125 | 2.6125 | 2.6125 | 2.6125 | 2.6125 | 2.6125 | 2.6125 | 2.6125 | 2.6125
9.992e-14% | 4391.6218 | 3.7221e-14 | 4.0005e-14 | 4.0284e-14 | 4.0147e-14 | 4.0278e-14 | 4.0331e-14 | 4.0503e-14 | 4.0856e-14 | 4.1153e-14 | 4.129e-14 | 4.1168e-14 | 4.1679e-14 | 4.176e-14 | 4.1664e-14 | 4.1856e-14 | 4.1966e-14 | 4.1966e-14 | 4.1966e-14 | 4.1966e-14 | 4.1966e-14 | 4.1966e-14 | 4.1966e-14 | 4.1966e-14 | 4.1966e-14 | 4.1966e-14 | 4.1966e-14 | 4.1966e-14 | 4.1966e-14 | 4.1966e-14 | 4.1966e-14 | 9.992e-14% | 4391.6218 | 4.5795e-14 | 4.8906e-14 | 4.8992e-14 | 4.8899e-14 | 4.8923e-14 | 4.9093e-14 | 4.9437e-14 | 5.0044e-14 | 5.0359e-14 | 5.0588e-14 | 5.0934e-14 | 5.1376e-14 | 5.191e-14 | 5.2189e-14 | 5.2099e-14 | 5.2209e-14 | 5.2209e-14 | 5.2209e-14 | 5.2209e-14 | 5.2209e-14 | 5.2209e-14 | 5.2209e-14 | 5.2209e-14 | 5.2209e-14 | 5.2209e-14 | 5.2209e-14 | 5.2209e-14 | 5.2209e-14 | 5.2209e-14 | 5.2209e-14
Option 4
Winter Season | [31 empty] | Winter Season
P50 | [31 empty] | P10
% of MD | Winter - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Winter - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 35.4586 | 39.1719 | 39.5657 | -25.9475 | -25.3012 | -24.6885 | -23.6177 | -20.9246 | -19.4761 | -20.5328 | -17.2613 | -16.6718 | -16.2481 | -14.2509 | -13.9258 | -13.9258 | -13.9258 | -13.9258 | -13.9258 | -13.9258 | -13.9258 | -13.9258 | -13.9258 | -13.9258 | -13.9258 | -13.9258 | -13.9258 | -13.9258 | -13.9258 | -13.9258 | 100% | 0 | 38.8714 | 42.4133 | 42.7801 | -21.954 | -21.9848 | -21.7065 | -20.6178 | -17.4899 | -16.1991 | -17.4209 | -14.0458 | -15.4629 | -14.1878 | -13.269 | -13.6465 | -13.6465 | -13.6465 | -13.6465 | -13.6465 | -13.6465 | -13.6465 | -13.6465 | -13.6465 | -13.6465 | -13.6465 | -13.6465 | -13.6465 | -13.6465 | -13.6465 | -13.6465
99% | 0.2972 | 35.104 | 38.7802 | 39.17 | -25.688 | -25.0482 | -24.4416 | -23.3815 | -20.7154 | -19.2813 | -20.3275 | -17.0887 | -16.5051 | -16.0856 | -14.1084 | -13.7865 | -13.7865 | -13.7865 | -13.7865 | -13.7865 | -13.7865 | -13.7865 | -13.7865 | -13.7865 | -13.7865 | -13.7865 | -13.7865 | -13.7865 | -13.7865 | -13.7865 | -13.7865 | 99% | 0.2972 | 38.4827 | 41.9892 | 42.3523 | -21.7344 | -21.765 | -21.4894 | -20.4116 | -17.315 | -16.0371 | -17.2467 | -13.9054 | -15.3083 | -14.046 | -13.1363 | -13.51 | -13.51 | -13.51 | -13.51 | -13.51 | -13.51 | -13.51 | -13.51 | -13.51 | -13.51 | -13.51 | -13.51 | -13.51 | -13.51 | -13.51 | -13.51
98% | 0.2972 | 34.7495 | 38.3885 | 38.7744 | -25.4286 | -24.7952 | -24.1947 | -23.1453 | -20.5061 | -19.0865 | -20.1222 | -16.916 | -16.3384 | -15.9232 | -13.9659 | -13.6473 | -13.6473 | -13.6473 | -13.6473 | -13.6473 | -13.6473 | -13.6473 | -13.6473 | -13.6473 | -13.6473 | -13.6473 | -13.6473 | -13.6473 | -13.6473 | -13.6473 | -13.6473 | 98% | 0.2972 | 38.0939 | 41.5651 | 41.9245 | -21.5149 | -21.5451 | -21.2723 | -20.2054 | -17.1401 | -15.8751 | -17.0725 | -13.7649 | -15.1536 | -13.9041 | -13.0036 | -13.3736 | -13.3736 | -13.3736 | -13.3736 | -13.3736 | -13.3736 | -13.3736 | -13.3736 | -13.3736 | -13.3736 | -13.3736 | -13.3736 | -13.3736 | -13.3736 | -13.3736 | -13.3736
97% | 0.2972 | 34.3949 | 37.9968 | 38.3787 | -25.1691 | -24.5422 | -23.9478 | -22.9092 | -20.2969 | -18.8918 | -19.9168 | -16.7434 | -16.1717 | -15.7607 | -13.8234 | -13.508 | -13.508 | -13.508 | -13.508 | -13.508 | -13.508 | -13.508 | -13.508 | -13.508 | -13.508 | -13.508 | -13.508 | -13.508 | -13.508 | -13.508 | -13.508 | 97% | 0.2972 | 37.7052 | 41.1409 | 41.4967 | -21.2954 | -21.3253 | -21.0553 | -19.9992 | -16.9652 | -15.7132 | -16.8983 | -13.6245 | -14.999 | -13.7622 | -12.8709 | -13.2371 | -13.2371 | -13.2371 | -13.2371 | -13.2371 | -13.2371 | -13.2371 | -13.2371 | -13.2371 | -13.2371 | -13.2371 | -13.2371 | -13.2371 | -13.2371 | -13.2371 | -13.2371
95% | 1.486 | 33.6857 | 37.2134 | 37.5874 | -24.6501 | -24.0361 | -23.4541 | -22.4368 | -19.8784 | -18.5023 | -19.5062 | -16.3982 | -15.8382 | -15.4357 | -13.5383 | -13.2295 | -13.2295 | -13.2295 | -13.2295 | -13.2295 | -13.2295 | -13.2295 | -13.2295 | -13.2295 | -13.2295 | -13.2295 | -13.2295 | -13.2295 | -13.2295 | -13.2295 | -13.2295 | 95% | 1.486 | 36.9278 | 40.2927 | 40.6411 | -20.8563 | -20.8856 | -20.6211 | -19.5869 | -16.6154 | -15.3892 | -16.5499 | -13.3435 | -14.6897 | -13.4784 | -12.6056 | -12.9642 | -12.9642 | -12.9642 | -12.9642 | -12.9642 | -12.9642 | -12.9642 | -12.9642 | -12.9642 | -12.9642 | -12.9642 | -12.9642 | -12.9642 | -12.9642 | -12.9642 | -12.9642
90% | 8.6188 | 31.9128 | 35.2548 | 35.6091 | -23.3528 | -22.7711 | -22.2196 | -21.2559 | -18.8321 | -17.5285 | -18.4795 | -15.5351 | -15.0046 | -14.6233 | -12.8258 | -12.5332 | -12.5332 | -12.5332 | -12.5332 | -12.5332 | -12.5332 | -12.5332 | -12.5332 | -12.5332 | -12.5332 | -12.5332 | -12.5332 | -12.5332 | -12.5332 | -12.5332 | -12.5332 | 90% | 8.6188 | 34.9842 | 38.172 | 38.5021 | -19.7586 | -19.7863 | -19.5358 | -18.556 | -15.7409 | -14.5792 | -15.6788 | -12.6413 | -13.9166 | -12.7691 | -11.9421 | -12.2819 | -12.2819 | -12.2819 | -12.2819 | -12.2819 | -12.2819 | -12.2819 | -12.2819 | -12.2819 | -12.2819 | -12.2819 | -12.2819 | -12.2819 | -12.2819 | -12.2819 | -12.2819
85% | 40.1218 | 30.1398 | 33.2962 | 33.6308 | -22.0554 | -21.506 | -20.9852 | -20.075 | -17.7859 | -16.5547 | -17.4529 | -14.6721 | -14.1711 | -13.8109 | -12.1133 | -11.8369 | -11.8369 | -11.8369 | -11.8369 | -11.8369 | -11.8369 | -11.8369 | -11.8369 | -11.8369 | -11.8369 | -11.8369 | -11.8369 | -11.8369 | -11.8369 | -11.8369 | -11.8369 | 85% | 40.1218 | 33.0407 | 36.0513 | 36.3631 | -18.6609 | -18.6871 | -18.4505 | -17.5251 | -14.8664 | -13.7693 | -14.8078 | -11.939 | -13.1435 | -12.0597 | -11.2787 | -11.5995 | -11.5995 | -11.5995 | -11.5995 | -11.5995 | -11.5995 | -11.5995 | -11.5995 | -11.5995 | -11.5995 | -11.5995 | -11.5995 | -11.5995 | -11.5995 | -11.5995 | -11.5995
80% | 93.0231 | 28.3669 | 31.3376 | 31.6526 | -20.758 | -20.241 | -19.7508 | -18.8942 | -16.7397 | -15.5809 | -16.4263 | -13.809 | -13.3375 | -12.9985 | -11.4007 | -11.1406 | -11.1406 | -11.1406 | -11.1406 | -11.1406 | -11.1406 | -11.1406 | -11.1406 | -11.1406 | -11.1406 | -11.1406 | -11.1406 | -11.1406 | -11.1406 | -11.1406 | -11.1406 | 80% | 93.0231 | 31.0971 | 33.9307 | 34.2241 | -17.5632 | -17.5879 | -17.3652 | -16.4942 | -13.9919 | -12.9593 | -13.9367 | -11.2367 | -12.3703 | -11.3503 | -10.6152 | -10.9172 | -10.9172 | -10.9172 | -10.9172 | -10.9172 | -10.9172 | -10.9172 | -10.9172 | -10.9172 | -10.9172 | -10.9172 | -10.9172 | -10.9172 | -10.9172 | -10.9172 | -10.9172
75% | 197.0426 | 26.594 | 29.379 | 29.6743 | -19.4606 | -18.9759 | -18.5164 | -17.7133 | -15.6935 | -14.6071 | -15.3996 | -12.946 | -12.5039 | -12.1861 | -10.6882 | -10.4444 | -10.4444 | -10.4444 | -10.4444 | -10.4444 | -10.4444 | -10.4444 | -10.4444 | -10.4444 | -10.4444 | -10.4444 | -10.4444 | -10.4444 | -10.4444 | -10.4444 | -10.4444 | 75% | 197.0426 | 29.1535 | 31.81 | 32.0851 | -16.4655 | -16.4886 | -16.2799 | -15.4633 | -13.1174 | -12.1493 | -13.0657 | -10.5344 | -11.5972 | -10.6409 | -9.9518 | -10.2349 | -10.2349 | -10.2349 | -10.2349 | -10.2349 | -10.2349 | -10.2349 | -10.2349 | -10.2349 | -10.2349 | -10.2349 | -10.2349 | -10.2349 | -10.2349 | -10.2349 | -10.2349
70% | 378.0365 | 24.821 | 27.4204 | 27.696 | -18.1633 | -17.7108 | -17.2819 | -16.5324 | -14.6472 | -13.6332 | -14.373 | -12.0829 | -11.6703 | -11.3737 | -9.9756 | -9.7481 | -9.7481 | -9.7481 | -9.7481 | -9.7481 | -9.7481 | -9.7481 | -9.7481 | -9.7481 | -9.7481 | -9.7481 | -9.7481 | -9.7481 | -9.7481 | -9.7481 | -9.7481 | 70% | 378.0365 | 27.21 | 29.6893 | 29.9461 | -15.3678 | -15.3894 | -15.1945 | -14.4324 | -12.2429 | -11.3394 | -12.1946 | -9.8321 | -10.824 | -9.9315 | -9.2883 | -9.5526 | -9.5526 | -9.5526 | -9.5526 | -9.5526 | -9.5526 | -9.5526 | -9.5526 | -9.5526 | -9.5526 | -9.5526 | -9.5526 | -9.5526 | -9.5526 | -9.5526 | -9.5526
65% | 616.0926 | 23.0481 | 25.4618 | 25.7177 | -16.8659 | -16.4458 | -16.0475 | -15.3515 | -13.601 | -12.6594 | -13.3463 | -11.2198 | -10.8367 | -10.5613 | -9.2631 | -9.0518 | -9.0518 | -9.0518 | -9.0518 | -9.0518 | -9.0518 | -9.0518 | -9.0518 | -9.0518 | -9.0518 | -9.0518 | -9.0518 | -9.0518 | -9.0518 | -9.0518 | -9.0518 | 65% | 616.0926 | 25.2664 | 27.5687 | 27.8071 | -14.2701 | -14.2901 | -14.1092 | -13.4015 | -11.3684 | -10.5294 | -11.3236 | -9.1298 | -10.0509 | -9.2221 | -8.6249 | -8.8702 | -8.8702 | -8.8702 | -8.8702 | -8.8702 | -8.8702 | -8.8702 | -8.8702 | -8.8702 | -8.8702 | -8.8702 | -8.8702 | -8.8702 | -8.8702 | -8.8702 | -8.8702
60% | 934.9866 | 21.2752 | 23.5032 | 23.7394 | -15.5685 | -15.1807 | -14.8131 | -14.1706 | -12.5548 | -11.6856 | -12.3197 | -10.3568 | -10.0031 | -9.7489 | -8.5505 | -8.3555 | -8.3555 | -8.3555 | -8.3555 | -8.3555 | -8.3555 | -8.3555 | -8.3555 | -8.3555 | -8.3555 | -8.3555 | -8.3555 | -8.3555 | -8.3555 | -8.3555 | -8.3555 | 60% | 934.9866 | 23.3228 | 25.448 | 25.6681 | -13.1724 | -13.1909 | -13.0239 | -12.3707 | -10.4939 | -9.7195 | -10.4526 | -8.4275 | -9.2777 | -8.5127 | -7.9614 | -8.1879 | -8.1879 | -8.1879 | -8.1879 | -8.1879 | -8.1879 | -8.1879 | -8.1879 | -8.1879 | -8.1879 | -8.1879 | -8.1879 | -8.1879 | -8.1879 | -8.1879 | -8.1879
55% | 1310.9428 | 19.5022 | 21.5446 | 21.7611 | -14.2711 | -13.9157 | -13.5787 | -12.9897 | -11.5085 | -10.7118 | -11.2931 | -9.4937 | -9.1695 | -8.9365 | -7.838 | -7.6592 | -7.6592 | -7.6592 | -7.6592 | -7.6592 | -7.6592 | -7.6592 | -7.6592 | -7.6592 | -7.6592 | -7.6592 | -7.6592 | -7.6592 | -7.6592 | -7.6592 | -7.6592 | 55% | 1310.9428 | 21.3793 | 23.3273 | 23.5291 | -12.0747 | -12.0917 | -11.9386 | -11.3398 | -9.6194 | -8.9095 | -9.5815 | -7.7252 | -8.5046 | -7.8033 | -7.298 | -7.5056 | -7.5056 | -7.5056 | -7.5056 | -7.5056 | -7.5056 | -7.5056 | -7.5056 | -7.5056 | -7.5056 | -7.5056 | -7.5056 | -7.5056 | -7.5056 | -7.5056 | -7.5056
50% | 1730.2899 | 17.7293 | 19.586 | 19.7828 | -12.9738 | -12.6506 | -12.3442 | -11.8088 | -10.4623 | -9.738 | -10.2664 | -8.6306 | -8.3359 | -8.1241 | -7.1254 | -6.9629 | -6.9629 | -6.9629 | -6.9629 | -6.9629 | -6.9629 | -6.9629 | -6.9629 | -6.9629 | -6.9629 | -6.9629 | -6.9629 | -6.9629 | -6.9629 | -6.9629 | -6.9629 | 50% | 1730.2899 | 19.4357 | 21.2067 | 21.3901 | -10.977 | -10.9924 | -10.8532 | -10.3089 | -8.7449 | -8.0996 | -8.7105 | -7.0229 | -7.7314 | -7.0939 | -6.6345 | -6.8233 | -6.8233 | -6.8233 | -6.8233 | -6.8233 | -6.8233 | -6.8233 | -6.8233 | -6.8233 | -6.8233 | -6.8233 | -6.8233 | -6.8233 | -6.8233 | -6.8233 | -6.8233
45% | 2168.0633 | 15.9564 | 17.6274 | 17.8046 | -11.6764 | -11.3855 | -11.1098 | -10.628 | -9.4161 | -8.7642 | -9.2398 | -7.7676 | -7.5023 | -7.3117 | -6.4129 | -6.2666 | -6.2666 | -6.2666 | -6.2666 | -6.2666 | -6.2666 | -6.2666 | -6.2666 | -6.2666 | -6.2666 | -6.2666 | -6.2666 | -6.2666 | -6.2666 | -6.2666 | -6.2666 | 45% | 2168.0633 | 17.4921 | 19.086 | 19.2511 | -9.8793 | -9.8932 | -9.7679 | -9.278 | -7.8704 | -7.2896 | -7.8394 | -6.3206 | -6.9583 | -6.3845 | -5.9711 | -6.1409 | -6.1409 | -6.1409 | -6.1409 | -6.1409 | -6.1409 | -6.1409 | -6.1409 | -6.1409 | -6.1409 | -6.1409 | -6.1409 | -6.1409 | -6.1409 | -6.1409 | -6.1409
40% | 2609.7004 | 14.1835 | 15.6688 | 15.8263 | -10.379 | -10.1205 | -9.8754 | -9.4471 | -8.3698 | -7.7904 | -8.2131 | -6.9045 | -6.6687 | -6.4992 | -5.7004 | -5.5703 | -5.5703 | -5.5703 | -5.5703 | -5.5703 | -5.5703 | -5.5703 | -5.5703 | -5.5703 | -5.5703 | -5.5703 | -5.5703 | -5.5703 | -5.5703 | -5.5703 | -5.5703 | 40% | 2609.7004 | 15.5485 | 16.9653 | 17.1121 | -8.7816 | -8.7939 | -8.6826 | -8.2471 | -6.996 | -6.4797 | -6.9684 | -5.6183 | -6.1852 | -5.6751 | -5.3076 | -5.4586 | -5.4586 | -5.4586 | -5.4586 | -5.4586 | -5.4586 | -5.4586 | -5.4586 | -5.4586 | -5.4586 | -5.4586 | -5.4586 | -5.4586 | -5.4586 | -5.4586 | -5.4586
35% | 2998.1389 | 12.4105 | 13.7102 | 13.848 | -9.0816 | -8.8554 | -8.641 | -8.2662 | -7.3236 | -6.8166 | -7.1865 | -6.0414 | -5.8351 | -5.6868 | -4.9878 | -4.874 | -4.874 | -4.874 | -4.874 | -4.874 | -4.874 | -4.874 | -4.874 | -4.874 | -4.874 | -4.874 | -4.874 | -4.874 | -4.874 | -4.874 | -4.874 | 35% | 2998.1389 | 13.605 | 14.8447 | 14.973 | -7.6839 | -7.6947 | -7.5973 | -7.2162 | -6.1215 | -5.6697 | -6.0973 | -4.916 | -5.412 | -4.9657 | -4.6442 | -4.7763 | -4.7763 | -4.7763 | -4.7763 | -4.7763 | -4.7763 | -4.7763 | -4.7763 | -4.7763 | -4.7763 | -4.7763 | -4.7763 | -4.7763 | -4.7763 | -4.7763 | -4.7763
30% | 3309.3057 | 10.6376 | 11.7516 | 11.8697 | -7.7843 | -7.5904 | -7.4065 | -7.0853 | -6.2774 | -5.8428 | -6.1598 | -5.1784 | -5.0015 | -4.8744 | -4.2753 | -4.1777 | -4.1777 | -4.1777 | -4.1777 | -4.1777 | -4.1777 | -4.1777 | -4.1777 | -4.1777 | -4.1777 | -4.1777 | -4.1777 | -4.1777 | -4.1777 | -4.1777 | -4.1777 | 30% | 3309.3057 | 11.6614 | 12.724 | 12.834 | -6.5862 | -6.5954 | -6.5119 | -6.1853 | -5.247 | -4.8597 | -5.2263 | -4.2138 | -4.6389 | -4.2564 | -3.9807 | -4.094 | -4.094 | -4.094 | -4.094 | -4.094 | -4.094 | -4.094 | -4.094 | -4.094 | -4.094 | -4.094 | -4.094 | -4.094 | -4.094 | -4.094 | -4.094
25% | 3537.8514 | 8.8647 | 9.793 | 9.8914 | -6.4869 | -6.3253 | -6.1721 | -5.9044 | -5.2312 | -4.869 | -5.1332 | -4.3153 | -4.168 | -4.062 | -3.5627 | -3.4815 | -3.4815 | -3.4815 | -3.4815 | -3.4815 | -3.4815 | -3.4815 | -3.4815 | -3.4815 | -3.4815 | -3.4815 | -3.4815 | -3.4815 | -3.4815 | -3.4815 | -3.4815 | 25% | 3537.8514 | 9.7178 | 10.6033 | 10.695 | -5.4885 | -5.4962 | -5.4266 | -5.1544 | -4.3725 | -4.0498 | -4.3552 | -3.5115 | -3.8657 | -3.547 | -3.3173 | -3.4116 | -3.4116 | -3.4116 | -3.4116 | -3.4116 | -3.4116 | -3.4116 | -3.4116 | -3.4116 | -3.4116 | -3.4116 | -3.4116 | -3.4116 | -3.4116 | -3.4116 | -3.4116
20% | 3731.0305 | 7.0917 | 7.8344 | 7.9131 | -5.1895 | -5.0602 | -4.9377 | -4.7235 | -4.1849 | -3.8952 | -4.1066 | -3.4523 | -3.3344 | -3.2496 | -2.8502 | -2.7852 | -2.7852 | -2.7852 | -2.7852 | -2.7852 | -2.7852 | -2.7852 | -2.7852 | -2.7852 | -2.7852 | -2.7852 | -2.7852 | -2.7852 | -2.7852 | -2.7852 | -2.7852 | 20% | 3731.0305 | 7.7743 | 8.4827 | 8.556 | -4.3908 | -4.397 | -4.3413 | -4.1236 | -3.498 | -3.2398 | -3.4842 | -2.8092 | -3.0926 | -2.8376 | -2.6538 | -2.7293 | -2.7293 | -2.7293 | -2.7293 | -2.7293 | -2.7293 | -2.7293 | -2.7293 | -2.7293 | -2.7293 | -2.7293 | -2.7293 | -2.7293 | -2.7293 | -2.7293 | -2.7293
15% | 3910.2412 | 5.3188 | 5.8758 | 5.9349 | -3.8921 | -3.7952 | -3.7033 | -3.5427 | -3.1387 | -2.9214 | -3.0799 | -2.5892 | -2.5008 | -2.4372 | -2.1376 | -2.0889 | -2.0889 | -2.0889 | -2.0889 | -2.0889 | -2.0889 | -2.0889 | -2.0889 | -2.0889 | -2.0889 | -2.0889 | -2.0889 | -2.0889 | -2.0889 | -2.0889 | -2.0889 | 15% | 3910.2412 | 5.8307 | 6.362 | 6.417 | -3.2931 | -3.2977 | -3.256 | -3.0927 | -2.6235 | -2.4299 | -2.6131 | -2.1069 | -2.3194 | -2.1282 | -1.9904 | -2.047 | -2.047 | -2.047 | -2.047 | -2.047 | -2.047 | -2.047 | -2.047 | -2.047 | -2.047 | -2.047 | -2.047 | -2.047 | -2.047 | -2.047 | -2.047
10% | 4075.1864 | 3.5459 | 3.9172 | 3.9566 | -2.5948 | -2.5301 | -2.4688 | -2.3618 | -2.0925 | -1.9476 | -2.0533 | -1.7261 | -1.6672 | -1.6248 | -1.4251 | -1.3926 | -1.3926 | -1.3926 | -1.3926 | -1.3926 | -1.3926 | -1.3926 | -1.3926 | -1.3926 | -1.3926 | -1.3926 | -1.3926 | -1.3926 | -1.3926 | -1.3926 | -1.3926 | 10% | 4075.1864 | 3.8871 | 4.2413 | 4.278 | -2.1954 | -2.1985 | -2.1706 | -2.0618 | -1.749 | -1.6199 | -1.7421 | -1.4046 | -1.5463 | -1.4188 | -1.3269 | -1.3647 | -1.3647 | -1.3647 | -1.3647 | -1.3647 | -1.3647 | -1.3647 | -1.3647 | -1.3647 | -1.3647 | -1.3647 | -1.3647 | -1.3647 | -1.3647 | -1.3647 | -1.3647
5% | 4251.7223 | 1.7729 | 1.9586 | 1.9783 | -1.2974 | -1.2651 | -1.2344 | -1.1809 | -1.0462 | -0.9738 | -1.0266 | -0.86306 | -0.83359 | -0.81241 | -0.71254 | -0.69629 | -0.69629 | -0.69629 | -0.69629 | -0.69629 | -0.69629 | -0.69629 | -0.69629 | -0.69629 | -0.69629 | -0.69629 | -0.69629 | -0.69629 | -0.69629 | -0.69629 | -0.69629 | 5% | 4251.7223 | 1.9436 | 2.1207 | 2.139 | -1.0977 | -1.0992 | -1.0853 | -1.0309 | -0.87449 | -0.80996 | -0.87105 | -0.70229 | -0.77314 | -0.70939 | -0.66345 | -0.68233 | -0.68233 | -0.68233 | -0.68233 | -0.68233 | -0.68233 | -0.68233 | -0.68233 | -0.68233 | -0.68233 | -0.68233 | -0.68233 | -0.68233 | -0.68233 | -0.68233 | -0.68233
9.992e-14% | 4391.7028 | 3.543e-14 | 3.9141e-14 | 3.9534e-14 | -2.5927e-14 | -2.5281e-14 | -2.4669e-14 | -2.3599e-14 | -2.0908e-14 | -1.9461e-14 | -2.0516e-14 | -1.7247e-14 | -1.6659e-14 | -1.6235e-14 | -1.424e-14 | -1.3915e-14 | -1.3915e-14 | -1.3915e-14 | -1.3915e-14 | -1.3915e-14 | -1.3915e-14 | -1.3915e-14 | -1.3915e-14 | -1.3915e-14 | -1.3915e-14 | -1.3915e-14 | -1.3915e-14 | -1.3915e-14 | -1.3915e-14 | -1.3915e-14 | -1.3915e-14 | 9.992e-14% | 4391.7028 | 3.884e-14 | 4.2379e-14 | 4.2746e-14 | -2.1936e-14 | -2.1967e-14 | -2.1689e-14 | -2.0601e-14 | -1.7476e-14 | -1.6186e-14 | -1.7407e-14 | -1.4035e-14 | -1.5451e-14 | -1.4176e-14 | -1.3258e-14 | -1.3636e-14 | -1.3636e-14 | -1.3636e-14 | -1.3636e-14 | -1.3636e-14 | -1.3636e-14 | -1.3636e-14 | -1.3636e-14 | -1.3636e-14 | -1.3636e-14 | -1.3636e-14 | -1.3636e-14 | -1.3636e-14 | -1.3636e-14 | -1.3636e-14 | -1.3636e-14
Summer Season | [31 empty] | Summer Season
P50 | [31 empty] | P10
% of MD | Summer - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Summer - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 37.2509 | 40.0367 | 40.3167 | -25.8206 | -25.6901 | -25.6365 | -25.4646 | -25.1114 | -24.8141 | -24.6773 | -24.7993 | -24.288 | -24.2069 | -24.3029 | -24.1105 | -24.0005 | -24.0005 | -24.0005 | -24.0005 | -24.0005 | -24.0005 | -24.0005 | -24.0005 | -24.0005 | -24.0005 | -24.0005 | -24.0005 | -24.0005 | -24.0005 | -24.0005 | 100% | 0 | 45.8318 | 48.9452 | 49.0311 | -17.0616 | -17.0377 | -16.8677 | -16.5232 | -15.9164 | -15.6002 | -15.3715 | -15.0253 | -14.5833 | -14.0489 | -13.7688 | -13.8596 | -13.7496 | -13.7496 | -13.7496 | -13.7496 | -13.7496 | -13.7496 | -13.7496 | -13.7496 | -13.7496 | -13.7496 | -13.7496 | -13.7496 | -13.7496 | -13.7496 | -13.7496
99% | 0.37816 | 36.8784 | 39.6364 | 39.9135 | -25.5623 | -25.4332 | -25.3801 | -25.21 | -24.8602 | -24.566 | -24.4306 | -24.5513 | -24.0451 | -23.9649 | -24.0599 | -23.8694 | -23.7605 | -23.7605 | -23.7605 | -23.7605 | -23.7605 | -23.7605 | -23.7605 | -23.7605 | -23.7605 | -23.7605 | -23.7605 | -23.7605 | -23.7605 | -23.7605 | -23.7605 | 99% | 0 | 45.3735 | 48.4557 | 48.5408 | -16.8909 | -16.8674 | -16.6991 | -16.358 | -15.7572 | -15.4442 | -15.2178 | -14.875 | -14.4375 | -13.9084 | -13.6311 | -13.721 | -13.6121 | -13.6121 | -13.6121 | -13.6121 | -13.6121 | -13.6121 | -13.6121 | -13.6121 | -13.6121 | -13.6121 | -13.6121 | -13.6121 | -13.6121 | -13.6121 | -13.6121
98% | 0.37816 | 36.5059 | 39.236 | 39.5103 | -25.3041 | -25.1763 | -25.1237 | -24.9554 | -24.6091 | -24.3179 | -24.1838 | -24.3033 | -23.8023 | -23.7228 | -23.8168 | -23.6283 | -23.5205 | -23.5205 | -23.5205 | -23.5205 | -23.5205 | -23.5205 | -23.5205 | -23.5205 | -23.5205 | -23.5205 | -23.5205 | -23.5205 | -23.5205 | -23.5205 | -23.5205 | 98% | 0 | 44.9152 | 47.9662 | 48.0504 | -16.7203 | -16.697 | -16.5304 | -16.1927 | -15.5981 | -15.2882 | -15.0641 | -14.7248 | -14.2917 | -13.7679 | -13.4934 | -13.5824 | -13.4746 | -13.4746 | -13.4746 | -13.4746 | -13.4746 | -13.4746 | -13.4746 | -13.4746 | -13.4746 | -13.4746 | -13.4746 | -13.4746 | -13.4746 | -13.4746 | -13.4746
97% | 0.37816 | 36.1334 | 38.8356 | 39.1072 | -25.0459 | -24.9194 | -24.8674 | -24.7007 | -24.358 | -24.0697 | -23.937 | -24.0553 | -23.5594 | -23.4807 | -23.5738 | -23.3872 | -23.2805 | -23.2805 | -23.2805 | -23.2805 | -23.2805 | -23.2805 | -23.2805 | -23.2805 | -23.2805 | -23.2805 | -23.2805 | -23.2805 | -23.2805 | -23.2805 | -23.2805 | 97% | 0.37816 | 44.4569 | 47.4768 | 47.5601 | -16.5497 | -16.5266 | -16.3617 | -16.0275 | -15.4389 | -15.1322 | -14.9103 | -14.5745 | -14.1458 | -13.6274 | -13.3557 | -13.4438 | -13.3371 | -13.3371 | -13.3371 | -13.3371 | -13.3371 | -13.3371 | -13.3371 | -13.3371 | -13.3371 | -13.3371 | -13.3371 | -13.3371 | -13.3371 | -13.3371 | -13.3371
95% | 0.75633 | 35.3884 | 38.0349 | 38.3008 | -24.5295 | -24.4056 | -24.3546 | -24.1914 | -23.8558 | -23.5734 | -23.4435 | -23.5593 | -23.0736 | -22.9966 | -23.0877 | -22.9049 | -22.8004 | -22.8004 | -22.8004 | -22.8004 | -22.8004 | -22.8004 | -22.8004 | -22.8004 | -22.8004 | -22.8004 | -22.8004 | -22.8004 | -22.8004 | -22.8004 | -22.8004 | 95% | 0.37816 | 43.5402 | 46.4979 | 46.5795 | -16.2085 | -16.1859 | -16.0243 | -15.697 | -15.1206 | -14.8202 | -14.6029 | -14.274 | -13.8542 | -13.3464 | -13.0804 | -13.1666 | -13.0621 | -13.0621 | -13.0621 | -13.0621 | -13.0621 | -13.0621 | -13.0621 | -13.0621 | -13.0621 | -13.0621 | -13.0621 | -13.0621 | -13.0621 | -13.0621 | -13.0621
90% | 9.0759 | 33.5258 | 36.0331 | 36.285 | -23.2385 | -23.1211 | -23.0728 | -22.9182 | -22.6002 | -22.3327 | -22.2096 | -22.3193 | -21.8592 | -21.7862 | -21.8726 | -21.6994 | -21.6004 | -21.6004 | -21.6004 | -21.6004 | -21.6004 | -21.6004 | -21.6004 | -21.6004 | -21.6004 | -21.6004 | -21.6004 | -21.6004 | -21.6004 | -21.6004 | -21.6004 | 90% | 0.75633 | 41.2486 | 44.0506 | 44.128 | -15.3554 | -15.334 | -15.181 | -14.8709 | -14.3248 | -14.0402 | -13.8343 | -13.5228 | -13.125 | -12.644 | -12.3919 | -12.4736 | -12.3746 | -12.3746 | -12.3746 | -12.3746 | -12.3746 | -12.3746 | -12.3746 | -12.3746 | -12.3746 | -12.3746 | -12.3746 | -12.3746 | -12.3746 | -12.3746 | -12.3746
85% | 40.4636 | 31.6633 | 34.0312 | 34.2692 | -21.9475 | -21.8366 | -21.791 | -21.645 | -21.3446 | -21.092 | -20.9757 | -21.0794 | -20.6448 | -20.5759 | -20.6575 | -20.4939 | -20.4004 | -20.4004 | -20.4004 | -20.4004 | -20.4004 | -20.4004 | -20.4004 | -20.4004 | -20.4004 | -20.4004 | -20.4004 | -20.4004 | -20.4004 | -20.4004 | -20.4004 | 85% | 1.1345 | 38.957 | 41.6034 | 41.6764 | -14.5023 | -14.4821 | -14.3376 | -14.0447 | -13.5289 | -13.2602 | -13.0658 | -12.7715 | -12.3958 | -11.9415 | -11.7035 | -11.7807 | -11.6872 | -11.6872 | -11.6872 | -11.6872 | -11.6872 | -11.6872 | -11.6872 | -11.6872 | -11.6872 | -11.6872 | -11.6872 | -11.6872 | -11.6872 | -11.6872 | -11.6872
80% | 94.5411 | 29.8007 | 32.0294 | 32.2533 | -20.6564 | -20.5521 | -20.5092 | -20.3717 | -20.0891 | -19.8513 | -19.7419 | -19.8394 | -19.4304 | -19.3655 | -19.4423 | -19.2884 | -19.2004 | -19.2004 | -19.2004 | -19.2004 | -19.2004 | -19.2004 | -19.2004 | -19.2004 | -19.2004 | -19.2004 | -19.2004 | -19.2004 | -19.2004 | -19.2004 | -19.2004 | 80% | 2.6471 | 36.6655 | 39.1561 | 39.2249 | -13.6492 | -13.6302 | -13.4942 | -13.2185 | -12.7331 | -12.4802 | -12.2972 | -12.0202 | -11.6667 | -11.2391 | -11.015 | -11.0877 | -10.9997 | -10.9997 | -10.9997 | -10.9997 | -10.9997 | -10.9997 | -10.9997 | -10.9997 | -10.9997 | -10.9997 | -10.9997 | -10.9997 | -10.9997 | -10.9997 | -10.9997
75% | 197.0236 | 27.9382 | 30.0275 | 30.2375 | -19.3654 | -19.2676 | -19.2274 | -19.0985 | -18.8335 | -18.6106 | -18.508 | -18.5995 | -18.216 | -18.1552 | -18.2272 | -18.0828 | -18.0003 | -18.0003 | -18.0003 | -18.0003 | -18.0003 | -18.0003 | -18.0003 | -18.0003 | -18.0003 | -18.0003 | -18.0003 | -18.0003 | -18.0003 | -18.0003 | -18.0003 | 75% | 3.4035 | 34.3739 | 36.7089 | 36.7733 | -12.7962 | -12.7783 | -12.6508 | -12.3924 | -11.9373 | -11.7002 | -11.5286 | -11.269 | -10.9375 | -10.5367 | -10.3266 | -10.3947 | -10.3122 | -10.3122 | -10.3122 | -10.3122 | -10.3122 | -10.3122 | -10.3122 | -10.3122 | -10.3122 | -10.3122 | -10.3122 | -10.3122 | -10.3122 | -10.3122 | -10.3122
70% | 336.9444 | 26.0756 | 28.0257 | 28.2217 | -18.0744 | -17.9831 | -17.9455 | -17.8253 | -17.5779 | -17.3699 | -17.2741 | -17.3595 | -17.0016 | -16.9448 | -17.012 | -16.8773 | -16.8003 | -16.8003 | -16.8003 | -16.8003 | -16.8003 | -16.8003 | -16.8003 | -16.8003 | -16.8003 | -16.8003 | -16.8003 | -16.8003 | -16.8003 | -16.8003 | -16.8003 | 70% | 5.6725 | 32.0823 | 34.2616 | 34.3217 | -11.9431 | -11.9264 | -11.8074 | -11.5662 | -11.1415 | -10.9202 | -10.76 | -10.5177 | -10.2083 | -9.8342 | -9.6382 | -9.7017 | -9.6247 | -9.6247 | -9.6247 | -9.6247 | -9.6247 | -9.6247 | -9.6247 | -9.6247 | -9.6247 | -9.6247 | -9.6247 | -9.6247 | -9.6247 | -9.6247 | -9.6247
65% | 521.4885 | 24.2131 | 26.0239 | 26.2058 | -16.7834 | -16.6986 | -16.6637 | -16.552 | -16.3224 | -16.1292 | -16.0403 | -16.1195 | -15.7872 | -15.7345 | -15.7969 | -15.6718 | -15.6003 | -15.6003 | -15.6003 | -15.6003 | -15.6003 | -15.6003 | -15.6003 | -15.6003 | -15.6003 | -15.6003 | -15.6003 | -15.6003 | -15.6003 | -15.6003 | -15.6003 | 65% | 6.4288 | 29.7907 | 31.8143 | 31.8702 | -11.09 | -11.0745 | -10.964 | -10.7401 | -10.3457 | -10.1401 | -9.9915 | -9.7664 | -9.4792 | -9.1318 | -8.9497 | -9.0087 | -8.9372 | -8.9372 | -8.9372 | -8.9372 | -8.9372 | -8.9372 | -8.9372 | -8.9372 | -8.9372 | -8.9372 | -8.9372 | -8.9372 | -8.9372 | -8.9372 | -8.9372
60% | 812.675 | 22.3505 | 24.022 | 24.19 | -15.4923 | -15.414 | -15.3819 | -15.2788 | -15.0668 | -14.8885 | -14.8064 | -14.8796 | -14.5728 | -14.5242 | -14.5817 | -14.4663 | -14.4003 | -14.4003 | -14.4003 | -14.4003 | -14.4003 | -14.4003 | -14.4003 | -14.4003 | -14.4003 | -14.4003 | -14.4003 | -14.4003 | -14.4003 | -14.4003 | -14.4003 | 60% | 11.3449 | 27.4991 | 29.3671 | 29.4186 | -10.2369 | -10.2226 | -10.1206 | -9.9139 | -9.5498 | -9.3601 | -9.2229 | -9.0152 | -8.75 | -8.4293 | -8.2613 | -8.3158 | -8.2498 | -8.2498 | -8.2498 | -8.2498 | -8.2498 | -8.2498 | -8.2498 | -8.2498 | -8.2498 | -8.2498 | -8.2498 | -8.2498 | -8.2498 | -8.2498 | -8.2498
55% | 1202.1843 | 20.488 | 22.0202 | 22.1742 | -14.2013 | -14.1295 | -14.1001 | -14.0056 | -13.8112 | -13.6478 | -13.5725 | -13.6396 | -13.3584 | -13.3138 | -13.3666 | -13.2608 | -13.2003 | -13.2003 | -13.2003 | -13.2003 | -13.2003 | -13.2003 | -13.2003 | -13.2003 | -13.2003 | -13.2003 | -13.2003 | -13.2003 | -13.2003 | -13.2003 | -13.2003 | 55% | 35.5474 | 25.2075 | 26.9198 | 26.9671 | -9.3839 | -9.3708 | -9.2773 | -9.0878 | -8.754 | -8.5801 | -8.4543 | -8.2639 | -8.0208 | -7.7269 | -7.5728 | -7.6228 | -7.5623 | -7.5623 | -7.5623 | -7.5623 | -7.5623 | -7.5623 | -7.5623 | -7.5623 | -7.5623 | -7.5623 | -7.5623 | -7.5623 | -7.5623 | -7.5623 | -7.5623
50% | 1686.2345 | 18.6255 | 20.0184 | 20.1583 | -12.9103 | -12.845 | -12.8182 | -12.7323 | -12.5557 | -12.4071 | -12.3387 | -12.3996 | -12.144 | -12.1035 | -12.1514 | -12.0552 | -12.0002 | -12.0002 | -12.0002 | -12.0002 | -12.0002 | -12.0002 | -12.0002 | -12.0002 | -12.0002 | -12.0002 | -12.0002 | -12.0002 | -12.0002 | -12.0002 | -12.0002 | 50% | 95.2974 | 22.9159 | 24.4726 | 24.5155 | -8.5308 | -8.5189 | -8.4339 | -8.2616 | -7.9582 | -7.8001 | -7.6857 | -7.5127 | -7.2917 | -7.0244 | -6.8844 | -6.9298 | -6.8748 | -6.8748 | -6.8748 | -6.8748 | -6.8748 | -6.8748 | -6.8748 | -6.8748 | -6.8748 | -6.8748 | -6.8748 | -6.8748 | -6.8748 | -6.8748 | -6.8748
45% | 2129.0649 | 16.7629 | 18.0165 | 18.1425 | -11.6192 | -11.5605 | -11.5364 | -11.4591 | -11.3001 | -11.1664 | -11.1048 | -11.1597 | -10.9296 | -10.8931 | -10.9363 | -10.8497 | -10.8002 | -10.8002 | -10.8002 | -10.8002 | -10.8002 | -10.8002 | -10.8002 | -10.8002 | -10.8002 | -10.8002 | -10.8002 | -10.8002 | -10.8002 | -10.8002 | -10.8002 | 45% | 208.7467 | 20.6243 | 22.0253 | 22.064 | -7.6777 | -7.667 | -7.5905 | -7.4354 | -7.1624 | -7.0201 | -6.9172 | -6.7614 | -6.5625 | -6.322 | -6.196 | -6.2368 | -6.1873 | -6.1873 | -6.1873 | -6.1873 | -6.1873 | -6.1873 | -6.1873 | -6.1873 | -6.1873 | -6.1873 | -6.1873 | -6.1873 | -6.1873 | -6.1873 | -6.1873
40% | 2484.5393 | 14.9004 | 16.0147 | 16.1267 | -10.3282 | -10.276 | -10.2546 | -10.1859 | -10.0445 | -9.9257 | -9.8709 | -9.9197 | -9.7152 | -9.6828 | -9.7212 | -9.6442 | -9.6002 | -9.6002 | -9.6002 | -9.6002 | -9.6002 | -9.6002 | -9.6002 | -9.6002 | -9.6002 | -9.6002 | -9.6002 | -9.6002 | -9.6002 | -9.6002 | -9.6002 | 40% | 380.4333 | 18.3327 | 19.5781 | 19.6124 | -6.8246 | -6.8151 | -6.7471 | -6.6093 | -6.3666 | -6.2401 | -6.1486 | -6.0101 | -5.8333 | -5.6196 | -5.5075 | -5.5438 | -5.4998 | -5.4998 | -5.4998 | -5.4998 | -5.4998 | -5.4998 | -5.4998 | -5.4998 | -5.4998 | -5.4998 | -5.4998 | -5.4998 | -5.4998 | -5.4998 | -5.4998
35% | 2808.248 | 13.0378 | 14.0129 | 14.1108 | -9.0372 | -8.9915 | -8.9728 | -8.9126 | -8.789 | -8.685 | -8.6371 | -8.6797 | -8.5008 | -8.4724 | -8.506 | -8.4387 | -8.4002 | -8.4002 | -8.4002 | -8.4002 | -8.4002 | -8.4002 | -8.4002 | -8.4002 | -8.4002 | -8.4002 | -8.4002 | -8.4002 | -8.4002 | -8.4002 | -8.4002 | 35% | 696.5786 | 16.0411 | 17.1308 | 17.1609 | -5.9715 | -5.9632 | -5.9037 | -5.7831 | -5.5707 | -5.4601 | -5.38 | -5.2589 | -5.1042 | -4.9171 | -4.8191 | -4.8509 | -4.8124 | -4.8124 | -4.8124 | -4.8124 | -4.8124 | -4.8124 | -4.8124 | -4.8124 | -4.8124 | -4.8124 | -4.8124 | -4.8124 | -4.8124 | -4.8124 | -4.8124
30% | 3095.6528 | 11.1753 | 12.011 | 12.095 | -7.7462 | -7.707 | -7.6909 | -7.6394 | -7.5334 | -7.4442 | -7.4032 | -7.4398 | -7.2864 | -7.2621 | -7.2909 | -7.2331 | -7.2001 | -7.2001 | -7.2001 | -7.2001 | -7.2001 | -7.2001 | -7.2001 | -7.2001 | -7.2001 | -7.2001 | -7.2001 | -7.2001 | -7.2001 | -7.2001 | -7.2001 | 30% | 1260.7997 | 13.7495 | 14.6835 | 14.7093 | -5.1185 | -5.1113 | -5.0603 | -4.957 | -4.7749 | -4.6801 | -4.6114 | -4.5076 | -4.375 | -4.2147 | -4.1306 | -4.1579 | -4.1249 | -4.1249 | -4.1249 | -4.1249 | -4.1249 | -4.1249 | -4.1249 | -4.1249 | -4.1249 | -4.1249 | -4.1249 | -4.1249 | -4.1249 | -4.1249 | -4.1249
25% | 3358.8552 | 9.3127 | 10.0092 | 10.0792 | -6.4551 | -6.4225 | -6.4091 | -6.3662 | -6.2778 | -6.2035 | -6.1693 | -6.1998 | -6.072 | -6.0517 | -6.0757 | -6.0276 | -6.0001 | -6.0001 | -6.0001 | -6.0001 | -6.0001 | -6.0001 | -6.0001 | -6.0001 | -6.0001 | -6.0001 | -6.0001 | -6.0001 | -6.0001 | -6.0001 | -6.0001 | 25% | 1965.3198 | 11.458 | 12.2363 | 12.2578 | -4.2654 | -4.2594 | -4.2169 | -4.1308 | -3.9791 | -3.9001 | -3.8429 | -3.7563 | -3.6458 | -3.5122 | -3.4422 | -3.4649 | -3.4374 | -3.4374 | -3.4374 | -3.4374 | -3.4374 | -3.4374 | -3.4374 | -3.4374 | -3.4374 | -3.4374 | -3.4374 | -3.4374 | -3.4374 | -3.4374 | -3.4374
20% | 3588.7791 | 7.4502 | 8.0073 | 8.0633 | -5.1641 | -5.138 | -5.1273 | -5.0929 | -5.0223 | -4.9628 | -4.9355 | -4.9599 | -4.8576 | -4.8414 | -4.8606 | -4.8221 | -4.8001 | -4.8001 | -4.8001 | -4.8001 | -4.8001 | -4.8001 | -4.8001 | -4.8001 | -4.8001 | -4.8001 | -4.8001 | -4.8001 | -4.8001 | -4.8001 | -4.8001 | 20% | 2490.2118 | 9.1664 | 9.789 | 9.8062 | -3.4123 | -3.4075 | -3.3735 | -3.3046 | -3.1833 | -3.12 | -3.0743 | -3.0051 | -2.9167 | -2.8098 | -2.7538 | -2.7719 | -2.7499 | -2.7499 | -2.7499 | -2.7499 | -2.7499 | -2.7499 | -2.7499 | -2.7499 | -2.7499 | -2.7499 | -2.7499 | -2.7499 | -2.7499 | -2.7499 | -2.7499
15% | 3802.4419 | 5.5876 | 6.0055 | 6.0475 | -3.8731 | -3.8535 | -3.8455 | -3.8197 | -3.7667 | -3.7221 | -3.7016 | -3.7199 | -3.6432 | -3.631 | -3.6454 | -3.6166 | -3.6001 | -3.6001 | -3.6001 | -3.6001 | -3.6001 | -3.6001 | -3.6001 | -3.6001 | -3.6001 | -3.6001 | -3.6001 | -3.6001 | -3.6001 | -3.6001 | -3.6001 | 15% | 2997.7083 | 6.8748 | 7.3418 | 7.3547 | -2.5592 | -2.5557 | -2.5302 | -2.4785 | -2.3875 | -2.34 | -2.3057 | -2.2538 | -2.1875 | -2.1073 | -2.0653 | -2.0789 | -2.0624 | -2.0624 | -2.0624 | -2.0624 | -2.0624 | -2.0624 | -2.0624 | -2.0624 | -2.0624 | -2.0624 | -2.0624 | -2.0624 | -2.0624 | -2.0624 | -2.0624
10% | 4024.8025 | 3.7251 | 4.0037 | 4.0317 | -2.5821 | -2.569 | -2.5636 | -2.5465 | -2.5111 | -2.4814 | -2.4677 | -2.4799 | -2.4288 | -2.4207 | -2.4303 | -2.411 | -2.4 | -2.4 | -2.4 | -2.4 | -2.4 | -2.4 | -2.4 | -2.4 | -2.4 | -2.4 | -2.4 | -2.4 | -2.4 | -2.4 | -2.4 | 10% | 3491.5908 | 4.5832 | 4.8945 | 4.9031 | -1.7062 | -1.7038 | -1.6868 | -1.6523 | -1.5916 | -1.56 | -1.5371 | -1.5025 | -1.4583 | -1.4049 | -1.3769 | -1.386 | -1.375 | -1.375 | -1.375 | -1.375 | -1.375 | -1.375 | -1.375 | -1.375 | -1.375 | -1.375 | -1.375 | -1.375 | -1.375 | -1.375 | -1.375
5% | 4239.978 | 1.8625 | 2.0018 | 2.0158 | -1.291 | -1.2845 | -1.2818 | -1.2732 | -1.2556 | -1.2407 | -1.2339 | -1.24 | -1.2144 | -1.2103 | -1.2151 | -1.2055 | -1.2 | -1.2 | -1.2 | -1.2 | -1.2 | -1.2 | -1.2 | -1.2 | -1.2 | -1.2 | -1.2 | -1.2 | -1.2 | -1.2 | -1.2 | 5% | 3955.9766 | 2.2916 | 2.4473 | 2.4516 | -0.85308 | -0.85189 | -0.84339 | -0.82616 | -0.79582 | -0.78001 | -0.76857 | -0.75127 | -0.72917 | -0.70244 | -0.68844 | -0.69298 | -0.68748 | -0.68748 | -0.68748 | -0.68748 | -0.68748 | -0.68748 | -0.68748 | -0.68748 | -0.68748 | -0.68748 | -0.68748 | -0.68748 | -0.68748 | -0.68748 | -0.68748
9.992e-14% | 4391.6218 | 3.7221e-14 | 4.0005e-14 | 4.0284e-14 | -2.58e-14 | -2.567e-14 | -2.5616e-14 | -2.5444e-14 | -2.5091e-14 | -2.4794e-14 | -2.4658e-14 | -2.4779e-14 | -2.4269e-14 | -2.4188e-14 | -2.4283e-14 | -2.4091e-14 | -2.3981e-14 | -2.3981e-14 | -2.3981e-14 | -2.3981e-14 | -2.3981e-14 | -2.3981e-14 | -2.3981e-14 | -2.3981e-14 | -2.3981e-14 | -2.3981e-14 | -2.3981e-14 | -2.3981e-14 | -2.3981e-14 | -2.3981e-14 | -2.3981e-14 | 9.992e-14% | 4391.6218 | 4.5795e-14 | 4.8906e-14 | 4.8992e-14 | -1.7048e-14 | -1.7024e-14 | -1.6854e-14 | -1.651e-14 | -1.5904e-14 | -1.5588e-14 | -1.5359e-14 | -1.5013e-14 | -1.4572e-14 | -1.4038e-14 | -1.3758e-14 | -1.3849e-14 | -1.3739e-14 | -1.3739e-14 | -1.3739e-14 | -1.3739e-14 | -1.3739e-14 | -1.3739e-14 | -1.3739e-14 | -1.3739e-14 | -1.3739e-14 | -1.3739e-14 | -1.3739e-14 | -1.3739e-14 | -1.3739e-14 | -1.3739e-14 | -1.3739e-14
Option 5
Winter Season | [31 empty] | Winter Season
P50 | [31 empty] | P10
% of MD | Winter - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Winter - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 31.3605 | 34.7961 | 35.1822 | 35.6773 | 36.3215 | 36.919 | 37.9591 | 40.598 | 42.0184 | 40.9412 | 44.1819 | 44.7319 | 45.1079 | 47.0802 | 47.4134 | 47.4134 | 47.4134 | 47.4134 | 47.4134 | 47.4134 | 47.4134 | 47.4134 | 47.4134 | 47.4134 | 47.4134 | 47.4134 | 47.4134 | 47.4134 | 47.4134 | 47.4134 | 100% | 0 | 34.7733 | 38.0375 | 38.3967 | 39.6708 | 39.6378 | 39.901 | 40.959 | 44.0327 | 45.2953 | 44.0531 | 47.3973 | 45.9408 | 47.1682 | 48.062 | 47.6926 | 47.6926 | 47.6926 | 47.6926 | 47.6926 | 47.6926 | 47.6926 | 47.6926 | 47.6926 | 47.6926 | 47.6926 | 47.6926 | 47.6926 | 47.6926 | 47.6926 | 47.6926
99% | 0.2972 | 31.0469 | 34.4482 | 34.8304 | 35.3205 | 35.9582 | 36.5498 | 37.5795 | 40.192 | 41.5982 | 40.5318 | 43.7401 | 44.2846 | 44.6568 | 46.6094 | 46.9392 | 46.9392 | 46.9392 | 46.9392 | 46.9392 | 46.9392 | 46.9392 | 46.9392 | 46.9392 | 46.9392 | 46.9392 | 46.9392 | 46.9392 | 46.9392 | 46.9392 | 46.9392 | 99% | 0.2972 | 34.4255 | 37.6571 | 38.0127 | 39.2741 | 39.2415 | 39.502 | 40.5494 | 43.5924 | 44.8423 | 43.6126 | 46.9233 | 45.4814 | 46.6965 | 47.5814 | 47.2157 | 47.2157 | 47.2157 | 47.2157 | 47.2157 | 47.2157 | 47.2157 | 47.2157 | 47.2157 | 47.2157 | 47.2157 | 47.2157 | 47.2157 | 47.2157 | 47.2157 | 47.2157
98% | 0.2972 | 30.7333 | 34.1002 | 34.4786 | 34.9637 | 35.595 | 36.1806 | 37.1999 | 39.7861 | 41.178 | 40.1224 | 43.2982 | 43.8373 | 44.2058 | 46.1386 | 46.4651 | 46.4651 | 46.4651 | 46.4651 | 46.4651 | 46.4651 | 46.4651 | 46.4651 | 46.4651 | 46.4651 | 46.4651 | 46.4651 | 46.4651 | 46.4651 | 46.4651 | 46.4651 | 98% | 0.2972 | 34.0778 | 37.2768 | 37.6287 | 38.8774 | 38.8451 | 39.103 | 40.1398 | 43.1521 | 44.3894 | 43.172 | 46.4494 | 45.022 | 46.2248 | 47.1008 | 46.7388 | 46.7388 | 46.7388 | 46.7388 | 46.7388 | 46.7388 | 46.7388 | 46.7388 | 46.7388 | 46.7388 | 46.7388 | 46.7388 | 46.7388 | 46.7388 | 46.7388 | 46.7388
97% | 0.2972 | 30.4197 | 33.7522 | 34.1268 | 34.607 | 35.2318 | 35.8114 | 36.8203 | 39.3801 | 40.7578 | 39.713 | 42.8564 | 43.3899 | 43.7547 | 45.6678 | 45.991 | 45.991 | 45.991 | 45.991 | 45.991 | 45.991 | 45.991 | 45.991 | 45.991 | 45.991 | 45.991 | 45.991 | 45.991 | 45.991 | 45.991 | 45.991 | 97% | 0.2972 | 33.7301 | 36.8964 | 37.2448 | 38.4807 | 38.4487 | 38.704 | 39.7302 | 42.7118 | 43.9364 | 42.7315 | 45.9754 | 44.5626 | 45.7532 | 46.6202 | 46.2619 | 46.2619 | 46.2619 | 46.2619 | 46.2619 | 46.2619 | 46.2619 | 46.2619 | 46.2619 | 46.2619 | 46.2619 | 46.2619 | 46.2619 | 46.2619 | 46.2619 | 46.2619
95% | 1.486 | 29.7925 | 33.0563 | 33.4231 | 33.8934 | 34.5054 | 35.0731 | 36.0611 | 38.5681 | 39.9174 | 38.8941 | 41.9728 | 42.4953 | 42.8525 | 44.7262 | 45.0427 | 45.0427 | 45.0427 | 45.0427 | 45.0427 | 45.0427 | 45.0427 | 45.0427 | 45.0427 | 45.0427 | 45.0427 | 45.0427 | 45.0427 | 45.0427 | 45.0427 | 45.0427 | 95% | 1.486 | 33.0346 | 36.1356 | 36.4768 | 37.6873 | 37.6559 | 37.906 | 38.911 | 41.8311 | 43.0305 | 41.8504 | 45.0274 | 43.6438 | 44.8098 | 45.6589 | 45.308 | 45.308 | 45.308 | 45.308 | 45.308 | 45.308 | 45.308 | 45.308 | 45.308 | 45.308 | 45.308 | 45.308 | 45.308 | 45.308 | 45.308 | 45.308
90% | 8.6188 | 28.2245 | 31.3165 | 31.664 | 32.1095 | 32.6893 | 33.2271 | 34.1632 | 36.5382 | 37.8165 | 36.8471 | 39.7637 | 40.2587 | 40.5971 | 42.3722 | 42.672 | 42.672 | 42.672 | 42.672 | 42.672 | 42.672 | 42.672 | 42.672 | 42.672 | 42.672 | 42.672 | 42.672 | 42.672 | 42.672 | 42.672 | 42.672 | 90% | 8.6188 | 31.2959 | 34.2338 | 34.557 | 35.7037 | 35.674 | 35.9109 | 36.8631 | 39.6295 | 40.7658 | 39.6478 | 42.6576 | 41.3468 | 42.4514 | 43.2558 | 42.9234 | 42.9234 | 42.9234 | 42.9234 | 42.9234 | 42.9234 | 42.9234 | 42.9234 | 42.9234 | 42.9234 | 42.9234 | 42.9234 | 42.9234 | 42.9234 | 42.9234 | 42.9234
85% | 40.1218 | 26.6565 | 29.5767 | 29.9049 | 30.3257 | 30.8732 | 31.3812 | 32.2652 | 34.5083 | 35.7156 | 34.8 | 37.5546 | 38.0221 | 38.3417 | 40.0181 | 40.3014 | 40.3014 | 40.3014 | 40.3014 | 40.3014 | 40.3014 | 40.3014 | 40.3014 | 40.3014 | 40.3014 | 40.3014 | 40.3014 | 40.3014 | 40.3014 | 40.3014 | 40.3014 | 85% | 40.1218 | 29.5573 | 32.3319 | 32.6372 | 33.7202 | 33.6922 | 33.9159 | 34.8151 | 37.4278 | 38.501 | 37.4451 | 40.2877 | 39.0497 | 40.093 | 40.8527 | 40.5388 | 40.5388 | 40.5388 | 40.5388 | 40.5388 | 40.5388 | 40.5388 | 40.5388 | 40.5388 | 40.5388 | 40.5388 | 40.5388 | 40.5388 | 40.5388 | 40.5388 | 40.5388
80% | 93.0231 | 25.0884 | 27.8369 | 28.1458 | 28.5418 | 29.0572 | 29.5352 | 30.3673 | 32.4784 | 33.6147 | 32.753 | 35.3455 | 35.7855 | 36.0863 | 37.6641 | 37.9307 | 37.9307 | 37.9307 | 37.9307 | 37.9307 | 37.9307 | 37.9307 | 37.9307 | 37.9307 | 37.9307 | 37.9307 | 37.9307 | 37.9307 | 37.9307 | 37.9307 | 37.9307 | 80% | 93.0231 | 27.8186 | 30.43 | 30.7173 | 31.7366 | 31.7103 | 31.9208 | 32.7672 | 35.2262 | 36.2362 | 35.2425 | 37.9178 | 36.7527 | 37.7346 | 38.4496 | 38.1541 | 38.1541 | 38.1541 | 38.1541 | 38.1541 | 38.1541 | 38.1541 | 38.1541 | 38.1541 | 38.1541 | 38.1541 | 38.1541 | 38.1541 | 38.1541 | 38.1541 | 38.1541
75% | 197.0426 | 23.5204 | 26.0971 | 26.3867 | 26.758 | 27.2411 | 27.6893 | 28.4693 | 30.4485 | 31.5138 | 30.7059 | 33.1364 | 33.5489 | 33.8309 | 35.3101 | 35.56 | 35.56 | 35.56 | 35.56 | 35.56 | 35.56 | 35.56 | 35.56 | 35.56 | 35.56 | 35.56 | 35.56 | 35.56 | 35.56 | 35.56 | 35.56 | 75% | 197.0426 | 26.0799 | 28.5281 | 28.7975 | 29.7531 | 29.7284 | 29.9258 | 30.7192 | 33.0246 | 33.9715 | 33.0398 | 35.548 | 34.4556 | 35.3762 | 36.0465 | 35.7695 | 35.7695 | 35.7695 | 35.7695 | 35.7695 | 35.7695 | 35.7695 | 35.7695 | 35.7695 | 35.7695 | 35.7695 | 35.7695 | 35.7695 | 35.7695 | 35.7695 | 35.7695
70% | 378.0365 | 21.9524 | 24.3573 | 24.6276 | 24.9741 | 25.425 | 25.8433 | 26.5713 | 28.4186 | 29.4129 | 28.6588 | 30.9273 | 31.3123 | 31.5755 | 32.9561 | 33.1893 | 33.1893 | 33.1893 | 33.1893 | 33.1893 | 33.1893 | 33.1893 | 33.1893 | 33.1893 | 33.1893 | 33.1893 | 33.1893 | 33.1893 | 33.1893 | 33.1893 | 33.1893 | 70% | 378.0365 | 24.3413 | 26.6263 | 26.8777 | 27.7696 | 27.7465 | 27.9307 | 28.6713 | 30.8229 | 31.7067 | 30.8372 | 33.1781 | 32.1586 | 33.0177 | 33.6434 | 33.3849 | 33.3849 | 33.3849 | 33.3849 | 33.3849 | 33.3849 | 33.3849 | 33.3849 | 33.3849 | 33.3849 | 33.3849 | 33.3849 | 33.3849 | 33.3849 | 33.3849 | 33.3849
65% | 616.0926 | 20.3843 | 22.6175 | 22.8684 | 23.1902 | 23.6089 | 23.9974 | 24.6734 | 26.3887 | 27.3119 | 26.6118 | 28.7182 | 29.0757 | 29.3201 | 30.6021 | 30.8187 | 30.8187 | 30.8187 | 30.8187 | 30.8187 | 30.8187 | 30.8187 | 30.8187 | 30.8187 | 30.8187 | 30.8187 | 30.8187 | 30.8187 | 30.8187 | 30.8187 | 30.8187 | 65% | 616.0926 | 22.6026 | 24.7244 | 24.9578 | 25.786 | 25.7646 | 25.9357 | 26.6233 | 28.6213 | 29.4419 | 28.6345 | 30.8082 | 29.8615 | 30.6593 | 31.2403 | 31.0002 | 31.0002 | 31.0002 | 31.0002 | 31.0002 | 31.0002 | 31.0002 | 31.0002 | 31.0002 | 31.0002 | 31.0002 | 31.0002 | 31.0002 | 31.0002 | 31.0002 | 31.0002
60% | 934.9866 | 18.8163 | 20.8777 | 21.1093 | 21.4064 | 21.7929 | 22.1514 | 22.7754 | 24.3588 | 25.211 | 24.5647 | 26.5091 | 26.8391 | 27.0648 | 28.2481 | 28.448 | 28.448 | 28.448 | 28.448 | 28.448 | 28.448 | 28.448 | 28.448 | 28.448 | 28.448 | 28.448 | 28.448 | 28.448 | 28.448 | 28.448 | 28.448 | 60% | 934.9866 | 20.864 | 22.8225 | 23.038 | 23.8025 | 23.7827 | 23.9406 | 24.5754 | 26.4196 | 27.1772 | 26.4319 | 28.4384 | 27.5645 | 28.3009 | 28.8372 | 28.6156 | 28.6156 | 28.6156 | 28.6156 | 28.6156 | 28.6156 | 28.6156 | 28.6156 | 28.6156 | 28.6156 | 28.6156 | 28.6156 | 28.6156 | 28.6156 | 28.6156 | 28.6156
55% | 1310.9428 | 17.2483 | 19.1379 | 19.3502 | 19.6225 | 19.9768 | 20.3055 | 20.8775 | 22.3289 | 23.1101 | 22.5177 | 24.3 | 24.6025 | 24.8094 | 25.8941 | 26.0773 | 26.0773 | 26.0773 | 26.0773 | 26.0773 | 26.0773 | 26.0773 | 26.0773 | 26.0773 | 26.0773 | 26.0773 | 26.0773 | 26.0773 | 26.0773 | 26.0773 | 26.0773 | 55% | 1310.9428 | 19.1253 | 20.9206 | 21.1182 | 21.8189 | 21.8008 | 21.9456 | 22.5274 | 24.218 | 24.9124 | 24.2292 | 26.0685 | 25.2675 | 25.9425 | 26.4341 | 26.231 | 26.231 | 26.231 | 26.231 | 26.231 | 26.231 | 26.231 | 26.231 | 26.231 | 26.231 | 26.231 | 26.231 | 26.231 | 26.231 | 26.231 | 26.231
50% | 1730.2899 | 15.6803 | 17.3981 | 17.5911 | 17.8386 | 18.1607 | 18.4595 | 18.9795 | 20.299 | 21.0092 | 20.4706 | 22.0909 | 22.3659 | 22.554 | 23.5401 | 23.7067 | 23.7067 | 23.7067 | 23.7067 | 23.7067 | 23.7067 | 23.7067 | 23.7067 | 23.7067 | 23.7067 | 23.7067 | 23.7067 | 23.7067 | 23.7067 | 23.7067 | 23.7067 | 50% | 1730.2899 | 17.3866 | 19.0188 | 19.1983 | 19.8354 | 19.8189 | 19.9505 | 20.4795 | 22.0164 | 22.6476 | 22.0265 | 23.6987 | 22.9704 | 23.5841 | 24.031 | 23.8463 | 23.8463 | 23.8463 | 23.8463 | 23.8463 | 23.8463 | 23.8463 | 23.8463 | 23.8463 | 23.8463 | 23.8463 | 23.8463 | 23.8463 | 23.8463 | 23.8463 | 23.8463
45% | 2168.0633 | 14.1122 | 15.6583 | 15.832 | 16.0548 | 16.3447 | 16.6136 | 17.0816 | 18.2691 | 18.9083 | 18.4235 | 19.8818 | 20.1293 | 20.2986 | 21.1861 | 21.336 | 21.336 | 21.336 | 21.336 | 21.336 | 21.336 | 21.336 | 21.336 | 21.336 | 21.336 | 21.336 | 21.336 | 21.336 | 21.336 | 21.336 | 21.336 | 45% | 2168.0633 | 15.648 | 17.1169 | 17.2785 | 17.8519 | 17.837 | 17.9555 | 18.4315 | 19.8147 | 20.3829 | 19.8239 | 21.3288 | 20.6734 | 21.2257 | 21.6279 | 21.4617 | 21.4617 | 21.4617 | 21.4617 | 21.4617 | 21.4617 | 21.4617 | 21.4617 | 21.4617 | 21.4617 | 21.4617 | 21.4617 | 21.4617 | 21.4617 | 21.4617 | 21.4617
40% | 2609.7004 | 12.5442 | 13.9185 | 14.0729 | 14.2709 | 14.5286 | 14.7676 | 15.1836 | 16.2392 | 16.8073 | 16.3765 | 17.6728 | 17.8928 | 18.0432 | 18.8321 | 18.9653 | 18.9653 | 18.9653 | 18.9653 | 18.9653 | 18.9653 | 18.9653 | 18.9653 | 18.9653 | 18.9653 | 18.9653 | 18.9653 | 18.9653 | 18.9653 | 18.9653 | 18.9653 | 40% | 2609.7004 | 13.9093 | 15.215 | 15.3587 | 15.8683 | 15.8551 | 15.9604 | 16.3836 | 17.6131 | 18.1181 | 17.6212 | 18.9589 | 18.3763 | 18.8673 | 19.2248 | 19.0771 | 19.0771 | 19.0771 | 19.0771 | 19.0771 | 19.0771 | 19.0771 | 19.0771 | 19.0771 | 19.0771 | 19.0771 | 19.0771 | 19.0771 | 19.0771 | 19.0771 | 19.0771
35% | 2998.1389 | 10.9762 | 12.1786 | 12.3138 | 12.487 | 12.7125 | 12.9217 | 13.2857 | 14.2093 | 14.7064 | 14.3294 | 15.4637 | 15.6562 | 15.7878 | 16.4781 | 16.5947 | 16.5947 | 16.5947 | 16.5947 | 16.5947 | 16.5947 | 16.5947 | 16.5947 | 16.5947 | 16.5947 | 16.5947 | 16.5947 | 16.5947 | 16.5947 | 16.5947 | 16.5947 | 35% | 2998.1389 | 12.1706 | 13.3131 | 13.4388 | 13.8848 | 13.8732 | 13.9654 | 14.3356 | 15.4115 | 15.8534 | 15.4186 | 16.5891 | 16.0793 | 16.5089 | 16.8217 | 16.6924 | 16.6924 | 16.6924 | 16.6924 | 16.6924 | 16.6924 | 16.6924 | 16.6924 | 16.6924 | 16.6924 | 16.6924 | 16.6924 | 16.6924 | 16.6924 | 16.6924 | 16.6924
30% | 3309.3057 | 9.4082 | 10.4388 | 10.5547 | 10.7032 | 10.8964 | 11.0757 | 11.3877 | 12.1794 | 12.6055 | 12.2824 | 13.2546 | 13.4196 | 13.5324 | 14.1241 | 14.224 | 14.224 | 14.224 | 14.224 | 14.224 | 14.224 | 14.224 | 14.224 | 14.224 | 14.224 | 14.224 | 14.224 | 14.224 | 14.224 | 14.224 | 14.224 | 30% | 3309.3057 | 10.432 | 11.4113 | 11.519 | 11.9012 | 11.8913 | 11.9703 | 12.2877 | 13.2098 | 13.5886 | 13.2159 | 14.2192 | 13.7823 | 14.1505 | 14.4186 | 14.3078 | 14.3078 | 14.3078 | 14.3078 | 14.3078 | 14.3078 | 14.3078 | 14.3078 | 14.3078 | 14.3078 | 14.3078 | 14.3078 | 14.3078 | 14.3078 | 14.3078 | 14.3078
25% | 3537.8514 | 7.8401 | 8.699 | 8.7956 | 8.9193 | 9.0804 | 9.2298 | 9.4898 | 10.1495 | 10.5046 | 10.2353 | 11.0455 | 11.183 | 11.277 | 11.77 | 11.8533 | 11.8533 | 11.8533 | 11.8533 | 11.8533 | 11.8533 | 11.8533 | 11.8533 | 11.8533 | 11.8533 | 11.8533 | 11.8533 | 11.8533 | 11.8533 | 11.8533 | 11.8533 | 25% | 3537.8514 | 8.6933 | 9.5094 | 9.5992 | 9.9177 | 9.9095 | 9.9753 | 10.2397 | 11.0082 | 11.3238 | 11.0133 | 11.8493 | 11.4852 | 11.7921 | 12.0155 | 11.9232 | 11.9232 | 11.9232 | 11.9232 | 11.9232 | 11.9232 | 11.9232 | 11.9232 | 11.9232 | 11.9232 | 11.9232 | 11.9232 | 11.9232 | 11.9232 | 11.9232 | 11.9232
20% | 3731.0305 | 6.2721 | 6.9592 | 7.0364 | 7.1355 | 7.2643 | 7.3838 | 7.5918 | 8.1196 | 8.4037 | 8.1882 | 8.8364 | 8.9464 | 9.0216 | 9.416 | 9.4827 | 9.4827 | 9.4827 | 9.4827 | 9.4827 | 9.4827 | 9.4827 | 9.4827 | 9.4827 | 9.4827 | 9.4827 | 9.4827 | 9.4827 | 9.4827 | 9.4827 | 9.4827 | 20% | 3731.0305 | 6.9547 | 7.6075 | 7.6793 | 7.9342 | 7.9276 | 7.9802 | 8.1918 | 8.8065 | 9.0591 | 8.8106 | 9.4795 | 9.1882 | 9.4336 | 9.6124 | 9.5385 | 9.5385 | 9.5385 | 9.5385 | 9.5385 | 9.5385 | 9.5385 | 9.5385 | 9.5385 | 9.5385 | 9.5385 | 9.5385 | 9.5385 | 9.5385 | 9.5385 | 9.5385
15% | 3910.2412 | 4.7041 | 5.2194 | 5.2773 | 5.3516 | 5.4482 | 5.5379 | 5.6939 | 6.0897 | 6.3028 | 6.1412 | 6.6273 | 6.7098 | 6.7662 | 7.062 | 7.112 | 7.112 | 7.112 | 7.112 | 7.112 | 7.112 | 7.112 | 7.112 | 7.112 | 7.112 | 7.112 | 7.112 | 7.112 | 7.112 | 7.112 | 7.112 | 15% | 3910.2412 | 5.216 | 5.7056 | 5.7595 | 5.9506 | 5.9457 | 5.9852 | 6.1438 | 6.6049 | 6.7943 | 6.608 | 7.1096 | 6.8911 | 7.0752 | 7.2093 | 7.1539 | 7.1539 | 7.1539 | 7.1539 | 7.1539 | 7.1539 | 7.1539 | 7.1539 | 7.1539 | 7.1539 | 7.1539 | 7.1539 | 7.1539 | 7.1539 | 7.1539 | 7.1539
10% | 4075.1864 | 3.1361 | 3.4796 | 3.5182 | 3.5677 | 3.6321 | 3.6919 | 3.7959 | 4.0598 | 4.2018 | 4.0941 | 4.4182 | 4.4732 | 4.5108 | 4.708 | 4.7413 | 4.7413 | 4.7413 | 4.7413 | 4.7413 | 4.7413 | 4.7413 | 4.7413 | 4.7413 | 4.7413 | 4.7413 | 4.7413 | 4.7413 | 4.7413 | 4.7413 | 4.7413 | 10% | 4075.1864 | 3.4773 | 3.8038 | 3.8397 | 3.9671 | 3.9638 | 3.9901 | 4.0959 | 4.4033 | 4.5295 | 4.4053 | 4.7397 | 4.5941 | 4.7168 | 4.8062 | 4.7693 | 4.7693 | 4.7693 | 4.7693 | 4.7693 | 4.7693 | 4.7693 | 4.7693 | 4.7693 | 4.7693 | 4.7693 | 4.7693 | 4.7693 | 4.7693 | 4.7693 | 4.7693
5% | 4251.7223 | 1.568 | 1.7398 | 1.7591 | 1.7839 | 1.8161 | 1.846 | 1.898 | 2.0299 | 2.1009 | 2.0471 | 2.2091 | 2.2366 | 2.2554 | 2.354 | 2.3707 | 2.3707 | 2.3707 | 2.3707 | 2.3707 | 2.3707 | 2.3707 | 2.3707 | 2.3707 | 2.3707 | 2.3707 | 2.3707 | 2.3707 | 2.3707 | 2.3707 | 2.3707 | 5% | 4251.7223 | 1.7387 | 1.9019 | 1.9198 | 1.9835 | 1.9819 | 1.9951 | 2.0479 | 2.2016 | 2.2648 | 2.2027 | 2.3699 | 2.297 | 2.3584 | 2.4031 | 2.3846 | 2.3846 | 2.3846 | 2.3846 | 2.3846 | 2.3846 | 2.3846 | 2.3846 | 2.3846 | 2.3846 | 2.3846 | 2.3846 | 2.3846 | 2.3846 | 2.3846 | 2.3846
9.992e-14% | 4391.7028 | 3.1335e-14 | 3.4768e-14 | 3.5154e-14 | 3.5649e-14 | 3.6292e-14 | 3.689e-14 | 3.7929e-14 | 4.0566e-14 | 4.1985e-14 | 4.0908e-14 | 4.4147e-14 | 4.4696e-14 | 4.5072e-14 | 4.7043e-14 | 4.7375e-14 | 4.7375e-14 | 4.7375e-14 | 4.7375e-14 | 4.7375e-14 | 4.7375e-14 | 4.7375e-14 | 4.7375e-14 | 4.7375e-14 | 4.7375e-14 | 4.7375e-14 | 4.7375e-14 | 4.7375e-14 | 4.7375e-14 | 4.7375e-14 | 4.7375e-14 | 9.992e-14% | 4391.7028 | 3.4745e-14 | 3.8007e-14 | 3.8366e-14 | 3.9639e-14 | 3.9606e-14 | 3.9869e-14 | 4.0926e-14 | 4.3998e-14 | 4.5259e-14 | 4.4018e-14 | 4.7359e-14 | 4.5904e-14 | 4.7131e-14 | 4.8024e-14 | 4.7655e-14 | 4.7655e-14 | 4.7655e-14 | 4.7655e-14 | 4.7655e-14 | 4.7655e-14 | 4.7655e-14 | 4.7655e-14 | 4.7655e-14 | 4.7655e-14 | 4.7655e-14 | 4.7655e-14 | 4.7655e-14 | 4.7655e-14 | 4.7655e-14 | 4.7655e-14
Summer Season | [31 empty] | Summer Season
P50 | [31 empty] | P10
% of MD | Summer - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Summer - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 33.1528 | 35.6609 | 35.9332 | 35.8042 | 35.9326 | 35.971 | 36.1121 | 36.4113 | 36.6803 | 36.7967 | 36.6439 | 37.1157 | 37.1491 | 37.0282 | 37.2287 | 37.3387 | 37.3387 | 37.3387 | 37.3387 | 37.3387 | 37.3387 | 37.3387 | 37.3387 | 37.3387 | 37.3387 | 37.3387 | 37.3387 | 37.3387 | 37.3387 | 37.3387 | 100% | 0 | 41.7337 | 44.5693 | 44.6476 | 44.5632 | 44.5849 | 44.7398 | 45.0536 | 45.6062 | 45.8942 | 46.1025 | 46.4178 | 46.8204 | 47.3072 | 47.5623 | 47.4796 | 47.5896 | 47.5896 | 47.5896 | 47.5896 | 47.5896 | 47.5896 | 47.5896 | 47.5896 | 47.5896 | 47.5896 | 47.5896 | 47.5896 | 47.5896 | 47.5896 | 47.5896
99% | 0.37816 | 32.8213 | 35.3043 | 35.5739 | 35.4462 | 35.5733 | 35.6113 | 35.751 | 36.0472 | 36.3135 | 36.4287 | 36.2774 | 36.7445 | 36.7776 | 36.6579 | 36.8564 | 36.9653 | 36.9653 | 36.9653 | 36.9653 | 36.9653 | 36.9653 | 36.9653 | 36.9653 | 36.9653 | 36.9653 | 36.9653 | 36.9653 | 36.9653 | 36.9653 | 36.9653 | 99% | 0 | 41.3164 | 44.1236 | 44.2011 | 44.1176 | 44.1391 | 44.2924 | 44.603 | 45.1502 | 45.4353 | 45.6415 | 45.9537 | 46.3522 | 46.8341 | 47.0866 | 47.0048 | 47.1137 | 47.1137 | 47.1137 | 47.1137 | 47.1137 | 47.1137 | 47.1137 | 47.1137 | 47.1137 | 47.1137 | 47.1137 | 47.1137 | 47.1137 | 47.1137 | 47.1137
98% | 0.37816 | 32.4898 | 34.9477 | 35.2145 | 35.0881 | 35.2139 | 35.2516 | 35.3899 | 35.6831 | 35.9467 | 36.0608 | 35.911 | 36.3734 | 36.4061 | 36.2876 | 36.4841 | 36.5919 | 36.5919 | 36.5919 | 36.5919 | 36.5919 | 36.5919 | 36.5919 | 36.5919 | 36.5919 | 36.5919 | 36.5919 | 36.5919 | 36.5919 | 36.5919 | 36.5919 | 98% | 0 | 40.899 | 43.6779 | 43.7546 | 43.672 | 43.6932 | 43.845 | 44.1525 | 44.6941 | 44.9763 | 45.1805 | 45.4895 | 45.884 | 46.361 | 46.611 | 46.53 | 46.6378 | 46.6378 | 46.6378 | 46.6378 | 46.6378 | 46.6378 | 46.6378 | 46.6378 | 46.6378 | 46.6378 | 46.6378 | 46.6378 | 46.6378 | 46.6378 | 46.6378
97% | 0.37816 | 32.1582 | 34.5911 | 34.8552 | 34.7301 | 34.8546 | 34.8919 | 35.0287 | 35.3189 | 35.5799 | 35.6928 | 35.5446 | 36.0022 | 36.0346 | 35.9173 | 36.1118 | 36.2185 | 36.2185 | 36.2185 | 36.2185 | 36.2185 | 36.2185 | 36.2185 | 36.2185 | 36.2185 | 36.2185 | 36.2185 | 36.2185 | 36.2185 | 36.2185 | 36.2185 | 97% | 0.37816 | 40.4817 | 43.2323 | 43.3082 | 43.2263 | 43.2474 | 43.3976 | 43.702 | 44.238 | 44.5174 | 44.7195 | 45.0253 | 45.4158 | 45.888 | 46.1354 | 46.0552 | 46.1619 | 46.1619 | 46.1619 | 46.1619 | 46.1619 | 46.1619 | 46.1619 | 46.1619 | 46.1619 | 46.1619 | 46.1619 | 46.1619 | 46.1619 | 46.1619 | 46.1619
95% | 0.75633 | 31.4952 | 33.8779 | 34.1365 | 34.014 | 34.136 | 34.1725 | 34.3065 | 34.5907 | 34.8463 | 34.9569 | 34.8117 | 35.2599 | 35.2917 | 35.1768 | 35.3673 | 35.4718 | 35.4718 | 35.4718 | 35.4718 | 35.4718 | 35.4718 | 35.4718 | 35.4718 | 35.4718 | 35.4718 | 35.4718 | 35.4718 | 35.4718 | 35.4718 | 35.4718 | 95% | 0.37816 | 39.647 | 42.3409 | 42.4152 | 42.3351 | 42.3557 | 42.5028 | 42.8009 | 43.3259 | 43.5995 | 43.7974 | 44.097 | 44.4794 | 44.9418 | 45.1842 | 45.1056 | 45.2101 | 45.2101 | 45.2101 | 45.2101 | 45.2101 | 45.2101 | 45.2101 | 45.2101 | 45.2101 | 45.2101 | 45.2101 | 45.2101 | 45.2101 | 45.2101 | 45.2101
90% | 9.0759 | 29.8375 | 32.0948 | 32.3399 | 32.2238 | 32.3393 | 32.3739 | 32.5009 | 32.7702 | 33.0123 | 33.117 | 32.9795 | 33.4041 | 33.4342 | 33.3254 | 33.5058 | 33.6048 | 33.6048 | 33.6048 | 33.6048 | 33.6048 | 33.6048 | 33.6048 | 33.6048 | 33.6048 | 33.6048 | 33.6048 | 33.6048 | 33.6048 | 33.6048 | 33.6048 | 90% | 0.75633 | 37.5603 | 40.1124 | 40.1828 | 40.1069 | 40.1264 | 40.2658 | 40.5482 | 41.0456 | 41.3048 | 41.4923 | 41.7761 | 42.1384 | 42.5764 | 42.806 | 42.7316 | 42.8306 | 42.8306 | 42.8306 | 42.8306 | 42.8306 | 42.8306 | 42.8306 | 42.8306 | 42.8306 | 42.8306 | 42.8306 | 42.8306 | 42.8306 | 42.8306 | 42.8306
85% | 40.4636 | 28.1799 | 30.3118 | 30.5432 | 30.4336 | 30.5427 | 30.5754 | 30.6953 | 30.9496 | 31.1782 | 31.2772 | 31.1473 | 31.5483 | 31.5768 | 31.4739 | 31.6444 | 31.7379 | 31.7379 | 31.7379 | 31.7379 | 31.7379 | 31.7379 | 31.7379 | 31.7379 | 31.7379 | 31.7379 | 31.7379 | 31.7379 | 31.7379 | 31.7379 | 31.7379 | 85% | 1.1345 | 35.4737 | 37.8839 | 37.9504 | 37.8787 | 37.8972 | 38.0288 | 38.2955 | 38.7653 | 39.0101 | 39.1872 | 39.4552 | 39.7973 | 40.2111 | 40.4279 | 40.3576 | 40.4511 | 40.4511 | 40.4511 | 40.4511 | 40.4511 | 40.4511 | 40.4511 | 40.4511 | 40.4511 | 40.4511 | 40.4511 | 40.4511 | 40.4511 | 40.4511 | 40.4511
80% | 94.5411 | 26.5222 | 28.5287 | 28.7466 | 28.6434 | 28.7461 | 28.7768 | 28.8897 | 29.129 | 29.3442 | 29.4374 | 29.3151 | 29.6926 | 29.7193 | 29.6225 | 29.783 | 29.871 | 29.871 | 29.871 | 29.871 | 29.871 | 29.871 | 29.871 | 29.871 | 29.871 | 29.871 | 29.871 | 29.871 | 29.871 | 29.871 | 29.871 | 80% | 2.6471 | 33.387 | 35.6555 | 35.7181 | 35.6506 | 35.6679 | 35.7918 | 36.0429 | 36.485 | 36.7154 | 36.882 | 37.1343 | 37.4563 | 37.8457 | 38.0498 | 37.9837 | 38.0717 | 38.0717 | 38.0717 | 38.0717 | 38.0717 | 38.0717 | 38.0717 | 38.0717 | 38.0717 | 38.0717 | 38.0717 | 38.0717 | 38.0717 | 38.0717 | 38.0717
75% | 197.0236 | 24.8646 | 26.7457 | 26.9499 | 26.8532 | 26.9494 | 26.9783 | 27.0841 | 27.3085 | 27.5102 | 27.5975 | 27.4829 | 27.8368 | 27.8618 | 27.7711 | 27.9215 | 28.004 | 28.004 | 28.004 | 28.004 | 28.004 | 28.004 | 28.004 | 28.004 | 28.004 | 28.004 | 28.004 | 28.004 | 28.004 | 28.004 | 28.004 | 75% | 3.4035 | 31.3003 | 33.427 | 33.4857 | 33.4224 | 33.4387 | 33.5548 | 33.7902 | 34.2047 | 34.4207 | 34.5769 | 34.8134 | 35.1153 | 35.4804 | 35.6717 | 35.6097 | 35.6922 | 35.6922 | 35.6922 | 35.6922 | 35.6922 | 35.6922 | 35.6922 | 35.6922 | 35.6922 | 35.6922 | 35.6922 | 35.6922 | 35.6922 | 35.6922 | 35.6922
70% | 336.9444 | 23.207 | 24.9626 | 25.1532 | 25.063 | 25.1528 | 25.1797 | 25.2785 | 25.4879 | 25.6762 | 25.7577 | 25.6507 | 25.981 | 26.0044 | 25.9197 | 26.0601 | 26.1371 | 26.1371 | 26.1371 | 26.1371 | 26.1371 | 26.1371 | 26.1371 | 26.1371 | 26.1371 | 26.1371 | 26.1371 | 26.1371 | 26.1371 | 26.1371 | 26.1371 | 70% | 5.6725 | 29.2136 | 31.1985 | 31.2533 | 31.1943 | 31.2094 | 31.3178 | 31.5375 | 31.9244 | 32.1259 | 32.2718 | 32.4925 | 32.7743 | 33.115 | 33.2936 | 33.2357 | 33.3127 | 33.3127 | 33.3127 | 33.3127 | 33.3127 | 33.3127 | 33.3127 | 33.3127 | 33.3127 | 33.3127 | 33.3127 | 33.3127 | 33.3127 | 33.3127 | 33.3127
65% | 521.4885 | 21.5493 | 23.1796 | 23.3566 | 23.2727 | 23.3562 | 23.3812 | 23.4729 | 23.6673 | 23.8422 | 23.9179 | 23.8185 | 24.1252 | 24.1469 | 24.0683 | 24.1987 | 24.2702 | 24.2702 | 24.2702 | 24.2702 | 24.2702 | 24.2702 | 24.2702 | 24.2702 | 24.2702 | 24.2702 | 24.2702 | 24.2702 | 24.2702 | 24.2702 | 24.2702 | 65% | 6.4288 | 27.1269 | 28.9701 | 29.0209 | 28.9661 | 28.9802 | 29.0808 | 29.2848 | 29.6441 | 29.8312 | 29.9666 | 30.1716 | 30.4333 | 30.7497 | 30.9155 | 30.8617 | 30.9332 | 30.9332 | 30.9332 | 30.9332 | 30.9332 | 30.9332 | 30.9332 | 30.9332 | 30.9332 | 30.9332 | 30.9332 | 30.9332 | 30.9332 | 30.9332 | 30.9332
60% | 812.675 | 19.8917 | 21.3965 | 21.5599 | 21.4825 | 21.5595 | 21.5826 | 21.6673 | 21.8468 | 22.0082 | 22.078 | 21.9863 | 22.2694 | 22.2895 | 22.2169 | 22.3372 | 22.4032 | 22.4032 | 22.4032 | 22.4032 | 22.4032 | 22.4032 | 22.4032 | 22.4032 | 22.4032 | 22.4032 | 22.4032 | 22.4032 | 22.4032 | 22.4032 | 22.4032 | 60% | 11.3449 | 25.0402 | 26.7416 | 26.7886 | 26.7379 | 26.751 | 26.8439 | 27.0321 | 27.3637 | 27.5365 | 27.6615 | 27.8507 | 28.0922 | 28.3843 | 28.5374 | 28.4877 | 28.5537 | 28.5537 | 28.5537 | 28.5537 | 28.5537 | 28.5537 | 28.5537 | 28.5537 | 28.5537 | 28.5537 | 28.5537 | 28.5537 | 28.5537 | 28.5537 | 28.5537
55% | 1202.1843 | 18.234 | 19.6135 | 19.7633 | 19.6923 | 19.7629 | 19.7841 | 19.8617 | 20.0262 | 20.1742 | 20.2382 | 20.1541 | 20.4136 | 20.432 | 20.3655 | 20.4758 | 20.5363 | 20.5363 | 20.5363 | 20.5363 | 20.5363 | 20.5363 | 20.5363 | 20.5363 | 20.5363 | 20.5363 | 20.5363 | 20.5363 | 20.5363 | 20.5363 | 20.5363 | 55% | 35.5474 | 22.9535 | 24.5131 | 24.5562 | 24.5098 | 24.5217 | 24.6069 | 24.7795 | 25.0834 | 25.2418 | 25.3564 | 25.5298 | 25.7512 | 26.0189 | 26.1592 | 26.1138 | 26.1743 | 26.1743 | 26.1743 | 26.1743 | 26.1743 | 26.1743 | 26.1743 | 26.1743 | 26.1743 | 26.1743 | 26.1743 | 26.1743 | 26.1743 | 26.1743 | 26.1743
50% | 1686.2345 | 16.5764 | 17.8305 | 17.9666 | 17.9021 | 17.9663 | 17.9855 | 18.0561 | 18.2056 | 18.3401 | 18.3983 | 18.3219 | 18.5579 | 18.5746 | 18.5141 | 18.6143 | 18.6693 | 18.6693 | 18.6693 | 18.6693 | 18.6693 | 18.6693 | 18.6693 | 18.6693 | 18.6693 | 18.6693 | 18.6693 | 18.6693 | 18.6693 | 18.6693 | 18.6693 | 50% | 95.2974 | 20.8669 | 22.2847 | 22.3238 | 22.2816 | 22.2925 | 22.3699 | 22.5268 | 22.8031 | 22.9471 | 23.0513 | 23.2089 | 23.4102 | 23.6536 | 23.7811 | 23.7398 | 23.7948 | 23.7948 | 23.7948 | 23.7948 | 23.7948 | 23.7948 | 23.7948 | 23.7948 | 23.7948 | 23.7948 | 23.7948 | 23.7948 | 23.7948 | 23.7948 | 23.7948
45% | 2129.0649 | 14.9188 | 16.0474 | 16.1699 | 16.1119 | 16.1697 | 16.187 | 16.2504 | 16.3851 | 16.5061 | 16.5585 | 16.4897 | 16.7021 | 16.7171 | 16.6627 | 16.7529 | 16.8024 | 16.8024 | 16.8024 | 16.8024 | 16.8024 | 16.8024 | 16.8024 | 16.8024 | 16.8024 | 16.8024 | 16.8024 | 16.8024 | 16.8024 | 16.8024 | 16.8024 | 45% | 208.7467 | 18.7802 | 20.0562 | 20.0914 | 20.0534 | 20.0632 | 20.1329 | 20.2741 | 20.5228 | 20.6524 | 20.7461 | 20.888 | 21.0692 | 21.2882 | 21.403 | 21.3658 | 21.4153 | 21.4153 | 21.4153 | 21.4153 | 21.4153 | 21.4153 | 21.4153 | 21.4153 | 21.4153 | 21.4153 | 21.4153 | 21.4153 | 21.4153 | 21.4153 | 21.4153
40% | 2484.5393 | 13.2611 | 14.2644 | 14.3733 | 14.3217 | 14.373 | 14.3884 | 14.4448 | 14.5645 | 14.6721 | 14.7187 | 14.6575 | 14.8463 | 14.8596 | 14.8113 | 14.8915 | 14.9355 | 14.9355 | 14.9355 | 14.9355 | 14.9355 | 14.9355 | 14.9355 | 14.9355 | 14.9355 | 14.9355 | 14.9355 | 14.9355 | 14.9355 | 14.9355 | 14.9355 | 40% | 380.4333 | 16.6935 | 17.8277 | 17.859 | 17.8253 | 17.834 | 17.8959 | 18.0214 | 18.2425 | 18.3577 | 18.441 | 18.5671 | 18.7282 | 18.9229 | 19.0249 | 18.9918 | 19.0358 | 19.0358 | 19.0358 | 19.0358 | 19.0358 | 19.0358 | 19.0358 | 19.0358 | 19.0358 | 19.0358 | 19.0358 | 19.0358 | 19.0358 | 19.0358 | 19.0358
35% | 2808.248 | 11.6035 | 12.4813 | 12.5766 | 12.5315 | 12.5764 | 12.5899 | 12.6392 | 12.7439 | 12.8381 | 12.8788 | 12.8254 | 12.9905 | 13.0022 | 12.9599 | 13.03 | 13.0685 | 13.0685 | 13.0685 | 13.0685 | 13.0685 | 13.0685 | 13.0685 | 13.0685 | 13.0685 | 13.0685 | 13.0685 | 13.0685 | 13.0685 | 13.0685 | 13.0685 | 35% | 696.5786 | 14.6068 | 15.5993 | 15.6267 | 15.5971 | 15.6047 | 15.6589 | 15.7688 | 15.9622 | 16.063 | 16.1359 | 16.2462 | 16.3871 | 16.5575 | 16.6468 | 16.6178 | 16.6563 | 16.6563 | 16.6563 | 16.6563 | 16.6563 | 16.6563 | 16.6563 | 16.6563 | 16.6563 | 16.6563 | 16.6563 | 16.6563 | 16.6563 | 16.6563 | 16.6563
30% | 3095.6528 | 9.9458 | 10.6983 | 10.78 | 10.7413 | 10.7798 | 10.7913 | 10.8336 | 10.9234 | 11.0041 | 11.039 | 10.9932 | 11.1347 | 11.1447 | 11.1085 | 11.1686 | 11.2016 | 11.2016 | 11.2016 | 11.2016 | 11.2016 | 11.2016 | 11.2016 | 11.2016 | 11.2016 | 11.2016 | 11.2016 | 11.2016 | 11.2016 | 11.2016 | 11.2016 | 30% | 1260.7997 | 12.5201 | 13.3708 | 13.3943 | 13.369 | 13.3755 | 13.4219 | 13.5161 | 13.6819 | 13.7683 | 13.8308 | 13.9254 | 14.0461 | 14.1921 | 14.2687 | 14.2439 | 14.2769 | 14.2769 | 14.2769 | 14.2769 | 14.2769 | 14.2769 | 14.2769 | 14.2769 | 14.2769 | 14.2769 | 14.2769 | 14.2769 | 14.2769 | 14.2769 | 14.2769
25% | 3358.8552 | 8.2882 | 8.9152 | 8.9833 | 8.9511 | 8.9831 | 8.9928 | 9.028 | 9.1028 | 9.1701 | 9.1992 | 9.161 | 9.2789 | 9.2873 | 9.257 | 9.3072 | 9.3347 | 9.3347 | 9.3347 | 9.3347 | 9.3347 | 9.3347 | 9.3347 | 9.3347 | 9.3347 | 9.3347 | 9.3347 | 9.3347 | 9.3347 | 9.3347 | 9.3347 | 25% | 1965.3198 | 10.4334 | 11.1423 | 11.1619 | 11.1408 | 11.1462 | 11.1849 | 11.2634 | 11.4016 | 11.4736 | 11.5256 | 11.6045 | 11.7051 | 11.8268 | 11.8906 | 11.8699 | 11.8974 | 11.8974 | 11.8974 | 11.8974 | 11.8974 | 11.8974 | 11.8974 | 11.8974 | 11.8974 | 11.8974 | 11.8974 | 11.8974 | 11.8974 | 11.8974 | 11.8974
20% | 3588.7791 | 6.6306 | 7.1322 | 7.1866 | 7.1608 | 7.1865 | 7.1942 | 7.2224 | 7.2823 | 7.3361 | 7.3593 | 7.3288 | 7.4231 | 7.4298 | 7.4056 | 7.4457 | 7.4677 | 7.4677 | 7.4677 | 7.4677 | 7.4677 | 7.4677 | 7.4677 | 7.4677 | 7.4677 | 7.4677 | 7.4677 | 7.4677 | 7.4677 | 7.4677 | 7.4677 | 20% | 2490.2118 | 8.3467 | 8.9139 | 8.9295 | 8.9126 | 8.917 | 8.948 | 9.0107 | 9.1212 | 9.1788 | 9.2205 | 9.2836 | 9.3641 | 9.4614 | 9.5125 | 9.4959 | 9.5179 | 9.5179 | 9.5179 | 9.5179 | 9.5179 | 9.5179 | 9.5179 | 9.5179 | 9.5179 | 9.5179 | 9.5179 | 9.5179 | 9.5179 | 9.5179 | 9.5179
15% | 3802.4419 | 4.9729 | 5.3491 | 5.39 | 5.3706 | 5.3899 | 5.3957 | 5.4168 | 5.4617 | 5.502 | 5.5195 | 5.4966 | 5.5674 | 5.5724 | 5.5542 | 5.5843 | 5.6008 | 5.6008 | 5.6008 | 5.6008 | 5.6008 | 5.6008 | 5.6008 | 5.6008 | 5.6008 | 5.6008 | 5.6008 | 5.6008 | 5.6008 | 5.6008 | 5.6008 | 15% | 2997.7083 | 6.2601 | 6.6854 | 6.6971 | 6.6845 | 6.6877 | 6.711 | 6.758 | 6.8409 | 6.8841 | 6.9154 | 6.9627 | 7.0231 | 7.0961 | 7.1343 | 7.1219 | 7.1384 | 7.1384 | 7.1384 | 7.1384 | 7.1384 | 7.1384 | 7.1384 | 7.1384 | 7.1384 | 7.1384 | 7.1384 | 7.1384 | 7.1384 | 7.1384 | 7.1384
10% | 4024.8025 | 3.3153 | 3.5661 | 3.5933 | 3.5804 | 3.5933 | 3.5971 | 3.6112 | 3.6411 | 3.668 | 3.6797 | 3.6644 | 3.7116 | 3.7149 | 3.7028 | 3.7229 | 3.7339 | 3.7339 | 3.7339 | 3.7339 | 3.7339 | 3.7339 | 3.7339 | 3.7339 | 3.7339 | 3.7339 | 3.7339 | 3.7339 | 3.7339 | 3.7339 | 3.7339 | 10% | 3491.5908 | 4.1734 | 4.4569 | 4.4648 | 4.4563 | 4.4585 | 4.474 | 4.5054 | 4.5606 | 4.5894 | 4.6103 | 4.6418 | 4.682 | 4.7307 | 4.7562 | 4.748 | 4.759 | 4.759 | 4.759 | 4.759 | 4.759 | 4.759 | 4.759 | 4.759 | 4.759 | 4.759 | 4.759 | 4.759 | 4.759 | 4.759 | 4.759
5% | 4239.978 | 1.6576 | 1.783 | 1.7967 | 1.7902 | 1.7966 | 1.7986 | 1.8056 | 1.8206 | 1.834 | 1.8398 | 1.8322 | 1.8558 | 1.8575 | 1.8514 | 1.8614 | 1.8669 | 1.8669 | 1.8669 | 1.8669 | 1.8669 | 1.8669 | 1.8669 | 1.8669 | 1.8669 | 1.8669 | 1.8669 | 1.8669 | 1.8669 | 1.8669 | 1.8669 | 5% | 3955.9766 | 2.0867 | 2.2285 | 2.2324 | 2.2282 | 2.2292 | 2.237 | 2.2527 | 2.2803 | 2.2947 | 2.3051 | 2.3209 | 2.341 | 2.3654 | 2.3781 | 2.374 | 2.3795 | 2.3795 | 2.3795 | 2.3795 | 2.3795 | 2.3795 | 2.3795 | 2.3795 | 2.3795 | 2.3795 | 2.3795 | 2.3795 | 2.3795 | 2.3795 | 2.3795
9.992e-14% | 4391.6218 | 3.3126e-14 | 3.5632e-14 | 3.5904e-14 | 3.5776e-14 | 3.5904e-14 | 3.5942e-14 | 3.6083e-14 | 3.6382e-14 | 3.6651e-14 | 3.6767e-14 | 3.6615e-14 | 3.7086e-14 | 3.7119e-14 | 3.6999e-14 | 3.7199e-14 | 3.7309e-14 | 3.7309e-14 | 3.7309e-14 | 3.7309e-14 | 3.7309e-14 | 3.7309e-14 | 3.7309e-14 | 3.7309e-14 | 3.7309e-14 | 3.7309e-14 | 3.7309e-14 | 3.7309e-14 | 3.7309e-14 | 3.7309e-14 | 3.7309e-14 | 9.992e-14% | 4391.6218 | 4.17e-14 | 4.4534e-14 | 4.4612e-14 | 4.4528e-14 | 4.4549e-14 | 4.4704e-14 | 4.5018e-14 | 4.557e-14 | 4.5858e-14 | 4.6066e-14 | 4.6381e-14 | 4.6783e-14 | 4.7269e-14 | 4.7524e-14 | 4.7442e-14 | 4.7552e-14 | 4.7552e-14 | 4.7552e-14 | 4.7552e-14 | 4.7552e-14 | 4.7552e-14 | 4.7552e-14 | 4.7552e-14 | 4.7552e-14 | 4.7552e-14 | 4.7552e-14 | 4.7552e-14 | 4.7552e-14 | 4.7552e-14 | 4.7552e-14
Option 6
Winter Season | [31 empty] | Winter Season
P50 | [31 empty] | P10
% of MD | Winter - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Winter - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 35.4586 | 39.1719 | 39.5657 | 40.0525 | 40.6988 | 41.3115 | 42.3823 | 45.0754 | 46.5239 | 45.4672 | 48.7387 | 49.3282 | 49.7519 | 51.7491 | 52.0742 | 52.0742 | 52.0742 | 52.0742 | 52.0742 | 52.0742 | 52.0742 | 52.0742 | 52.0742 | 52.0742 | 52.0742 | 52.0742 | 52.0742 | 52.0742 | 52.0742 | 52.0742 | 100% | 0 | 38.8714 | 42.4133 | 42.7801 | 44.046 | 44.0152 | 44.2935 | 45.3822 | 48.5101 | 49.8009 | 48.5791 | 51.9542 | 50.5371 | 51.8122 | 52.731 | 52.3535 | 52.3535 | 52.3535 | 52.3535 | 52.3535 | 52.3535 | 52.3535 | 52.3535 | 52.3535 | 52.3535 | 52.3535 | 52.3535 | 52.3535 | 52.3535 | 52.3535 | 52.3535
99% | 0.2972 | 35.104 | 38.7802 | 39.17 | 39.652 | 40.2918 | 40.8984 | 41.9585 | 44.6246 | 46.0587 | 45.0125 | 48.2513 | 48.8349 | 49.2544 | 51.2316 | 51.5535 | 51.5535 | 51.5535 | 51.5535 | 51.5535 | 51.5535 | 51.5535 | 51.5535 | 51.5535 | 51.5535 | 51.5535 | 51.5535 | 51.5535 | 51.5535 | 51.5535 | 51.5535 | 99% | 0.2972 | 38.4827 | 41.9892 | 42.3523 | 43.6056 | 43.575 | 43.8506 | 44.9284 | 48.025 | 49.3029 | 48.0933 | 51.4346 | 50.0317 | 51.294 | 52.2037 | 51.83 | 51.83 | 51.83 | 51.83 | 51.83 | 51.83 | 51.83 | 51.83 | 51.83 | 51.83 | 51.83 | 51.83 | 51.83 | 51.83 | 51.83 | 51.83
98% | 0.2972 | 34.7495 | 38.3885 | 38.7744 | 39.2514 | 39.8848 | 40.4853 | 41.5347 | 44.1739 | 45.5935 | 44.5578 | 47.764 | 48.3416 | 48.7568 | 50.7141 | 51.0327 | 51.0327 | 51.0327 | 51.0327 | 51.0327 | 51.0327 | 51.0327 | 51.0327 | 51.0327 | 51.0327 | 51.0327 | 51.0327 | 51.0327 | 51.0327 | 51.0327 | 51.0327 | 98% | 0.2972 | 38.0939 | 41.5651 | 41.9245 | 43.1651 | 43.1349 | 43.4077 | 44.4746 | 47.5399 | 48.8049 | 47.6075 | 50.9151 | 49.5264 | 50.7759 | 51.6764 | 51.3064 | 51.3064 | 51.3064 | 51.3064 | 51.3064 | 51.3064 | 51.3064 | 51.3064 | 51.3064 | 51.3064 | 51.3064 | 51.3064 | 51.3064 | 51.3064 | 51.3064 | 51.3064
97% | 0.2972 | 34.3949 | 37.9968 | 38.3787 | 38.8509 | 39.4778 | 40.0722 | 41.1108 | 43.7231 | 45.1282 | 44.1032 | 47.2766 | 47.8483 | 48.2593 | 50.1966 | 50.512 | 50.512 | 50.512 | 50.512 | 50.512 | 50.512 | 50.512 | 50.512 | 50.512 | 50.512 | 50.512 | 50.512 | 50.512 | 50.512 | 50.512 | 50.512 | 97% | 0.2972 | 37.7052 | 41.1409 | 41.4967 | 42.7246 | 42.6947 | 42.9647 | 44.0208 | 47.0548 | 48.3068 | 47.1217 | 50.3955 | 49.021 | 50.2578 | 51.1491 | 50.7829 | 50.7829 | 50.7829 | 50.7829 | 50.7829 | 50.7829 | 50.7829 | 50.7829 | 50.7829 | 50.7829 | 50.7829 | 50.7829 | 50.7829 | 50.7829 | 50.7829 | 50.7829
95% | 1.486 | 33.6857 | 37.2134 | 37.5874 | 38.0499 | 38.6639 | 39.2459 | 40.2632 | 42.8216 | 44.1977 | 43.1938 | 46.3018 | 46.8618 | 47.2643 | 49.1617 | 49.4705 | 49.4705 | 49.4705 | 49.4705 | 49.4705 | 49.4705 | 49.4705 | 49.4705 | 49.4705 | 49.4705 | 49.4705 | 49.4705 | 49.4705 | 49.4705 | 49.4705 | 49.4705 | 95% | 1.486 | 36.9278 | 40.2927 | 40.6411 | 41.8437 | 41.8144 | 42.0789 | 43.1131 | 46.0846 | 47.3108 | 46.1501 | 49.3565 | 48.0103 | 49.2216 | 50.0944 | 49.7358 | 49.7358 | 49.7358 | 49.7358 | 49.7358 | 49.7358 | 49.7358 | 49.7358 | 49.7358 | 49.7358 | 49.7358 | 49.7358 | 49.7358 | 49.7358 | 49.7358 | 49.7358
90% | 8.6188 | 31.9128 | 35.2548 | 35.6091 | 36.0472 | 36.6289 | 37.1804 | 38.1441 | 40.5679 | 41.8715 | 40.9205 | 43.8649 | 44.3954 | 44.7767 | 46.5742 | 46.8668 | 46.8668 | 46.8668 | 46.8668 | 46.8668 | 46.8668 | 46.8668 | 46.8668 | 46.8668 | 46.8668 | 46.8668 | 46.8668 | 46.8668 | 46.8668 | 46.8668 | 46.8668 | 90% | 8.6188 | 34.9842 | 38.172 | 38.5021 | 39.6414 | 39.6137 | 39.8642 | 40.844 | 43.6591 | 44.8208 | 43.7212 | 46.7587 | 45.4834 | 46.6309 | 47.4579 | 47.1181 | 47.1181 | 47.1181 | 47.1181 | 47.1181 | 47.1181 | 47.1181 | 47.1181 | 47.1181 | 47.1181 | 47.1181 | 47.1181 | 47.1181 | 47.1181 | 47.1181 | 47.1181
85% | 40.1218 | 30.1398 | 33.2962 | 33.6308 | 34.0446 | 34.594 | 35.1148 | 36.025 | 38.3141 | 39.5453 | 38.6471 | 41.4279 | 41.9289 | 42.2891 | 43.9867 | 44.2631 | 44.2631 | 44.2631 | 44.2631 | 44.2631 | 44.2631 | 44.2631 | 44.2631 | 44.2631 | 44.2631 | 44.2631 | 44.2631 | 44.2631 | 44.2631 | 44.2631 | 44.2631 | 85% | 40.1218 | 33.0407 | 36.0513 | 36.3631 | 37.4391 | 37.4129 | 37.6495 | 38.5749 | 41.2336 | 42.3307 | 41.2922 | 44.161 | 42.9565 | 44.0403 | 44.8213 | 44.5005 | 44.5005 | 44.5005 | 44.5005 | 44.5005 | 44.5005 | 44.5005 | 44.5005 | 44.5005 | 44.5005 | 44.5005 | 44.5005 | 44.5005 | 44.5005 | 44.5005 | 44.5005
80% | 93.0231 | 28.3669 | 31.3376 | 31.6526 | 32.042 | 32.559 | 33.0492 | 33.9058 | 36.0603 | 37.2191 | 36.3737 | 38.991 | 39.4625 | 39.8015 | 41.3993 | 41.6594 | 41.6594 | 41.6594 | 41.6594 | 41.6594 | 41.6594 | 41.6594 | 41.6594 | 41.6594 | 41.6594 | 41.6594 | 41.6594 | 41.6594 | 41.6594 | 41.6594 | 41.6594 | 80% | 93.0231 | 31.0971 | 33.9307 | 34.2241 | 35.2368 | 35.2121 | 35.4348 | 36.3058 | 38.8081 | 39.8407 | 38.8633 | 41.5633 | 40.4297 | 41.4497 | 42.1848 | 41.8828 | 41.8828 | 41.8828 | 41.8828 | 41.8828 | 41.8828 | 41.8828 | 41.8828 | 41.8828 | 41.8828 | 41.8828 | 41.8828 | 41.8828 | 41.8828 | 41.8828 | 41.8828
75% | 197.0426 | 26.594 | 29.379 | 29.6743 | 30.0394 | 30.5241 | 30.9836 | 31.7867 | 33.8065 | 34.8929 | 34.1004 | 36.554 | 36.9961 | 37.3139 | 38.8118 | 39.0556 | 39.0556 | 39.0556 | 39.0556 | 39.0556 | 39.0556 | 39.0556 | 39.0556 | 39.0556 | 39.0556 | 39.0556 | 39.0556 | 39.0556 | 39.0556 | 39.0556 | 39.0556 | 75% | 197.0426 | 29.1535 | 31.81 | 32.0851 | 33.0345 | 33.0114 | 33.2201 | 34.0367 | 36.3826 | 37.3507 | 36.4343 | 38.9656 | 37.9028 | 38.8591 | 39.5482 | 39.2651 | 39.2651 | 39.2651 | 39.2651 | 39.2651 | 39.2651 | 39.2651 | 39.2651 | 39.2651 | 39.2651 | 39.2651 | 39.2651 | 39.2651 | 39.2651 | 39.2651 | 39.2651
70% | 378.0365 | 24.821 | 27.4204 | 27.696 | 28.0367 | 28.4892 | 28.9181 | 29.6676 | 31.5528 | 32.5668 | 31.827 | 34.1171 | 34.5297 | 34.8263 | 36.2244 | 36.4519 | 36.4519 | 36.4519 | 36.4519 | 36.4519 | 36.4519 | 36.4519 | 36.4519 | 36.4519 | 36.4519 | 36.4519 | 36.4519 | 36.4519 | 36.4519 | 36.4519 | 36.4519 | 70% | 378.0365 | 27.21 | 29.6893 | 29.9461 | 30.8322 | 30.8106 | 31.0055 | 31.7676 | 33.9571 | 34.8606 | 34.0054 | 36.3679 | 35.376 | 36.2685 | 36.9117 | 36.6474 | 36.6474 | 36.6474 | 36.6474 | 36.6474 | 36.6474 | 36.6474 | 36.6474 | 36.6474 | 36.6474 | 36.6474 | 36.6474 | 36.6474 | 36.6474 | 36.6474 | 36.6474
65% | 616.0926 | 23.0481 | 25.4618 | 25.7177 | 26.0341 | 26.4542 | 26.8525 | 27.5485 | 29.299 | 30.2406 | 29.5537 | 31.6802 | 32.0633 | 32.3387 | 33.6369 | 33.8482 | 33.8482 | 33.8482 | 33.8482 | 33.8482 | 33.8482 | 33.8482 | 33.8482 | 33.8482 | 33.8482 | 33.8482 | 33.8482 | 33.8482 | 33.8482 | 33.8482 | 33.8482 | 65% | 616.0926 | 25.2664 | 27.5687 | 27.8071 | 28.6299 | 28.6099 | 28.7908 | 29.4985 | 31.5316 | 32.3706 | 31.5764 | 33.7702 | 32.8491 | 33.6779 | 34.2751 | 34.0298 | 34.0298 | 34.0298 | 34.0298 | 34.0298 | 34.0298 | 34.0298 | 34.0298 | 34.0298 | 34.0298 | 34.0298 | 34.0298 | 34.0298 | 34.0298 | 34.0298 | 34.0298
60% | 934.9866 | 21.2752 | 23.5032 | 23.7394 | 24.0315 | 24.4193 | 24.7869 | 25.4294 | 27.0452 | 27.9144 | 27.2803 | 29.2432 | 29.5969 | 29.8511 | 31.0495 | 31.2445 | 31.2445 | 31.2445 | 31.2445 | 31.2445 | 31.2445 | 31.2445 | 31.2445 | 31.2445 | 31.2445 | 31.2445 | 31.2445 | 31.2445 | 31.2445 | 31.2445 | 31.2445 | 60% | 934.9866 | 23.3228 | 25.448 | 25.6681 | 26.4276 | 26.4091 | 26.5761 | 27.2293 | 29.1061 | 29.8805 | 29.1474 | 31.1725 | 30.3223 | 31.0873 | 31.6386 | 31.4121 | 31.4121 | 31.4121 | 31.4121 | 31.4121 | 31.4121 | 31.4121 | 31.4121 | 31.4121 | 31.4121 | 31.4121 | 31.4121 | 31.4121 | 31.4121 | 31.4121 | 31.4121
55% | 1310.9428 | 19.5022 | 21.5446 | 21.7611 | 22.0289 | 22.3843 | 22.7213 | 23.3103 | 24.7915 | 25.5882 | 25.0069 | 26.8063 | 27.1305 | 27.3635 | 28.462 | 28.6408 | 28.6408 | 28.6408 | 28.6408 | 28.6408 | 28.6408 | 28.6408 | 28.6408 | 28.6408 | 28.6408 | 28.6408 | 28.6408 | 28.6408 | 28.6408 | 28.6408 | 28.6408 | 55% | 1310.9428 | 21.3793 | 23.3273 | 23.5291 | 24.2253 | 24.2083 | 24.3614 | 24.9602 | 26.6806 | 27.3905 | 26.7185 | 28.5748 | 27.7954 | 28.4967 | 29.002 | 28.7944 | 28.7944 | 28.7944 | 28.7944 | 28.7944 | 28.7944 | 28.7944 | 28.7944 | 28.7944 | 28.7944 | 28.7944 | 28.7944 | 28.7944 | 28.7944 | 28.7944 | 28.7944
50% | 1730.2899 | 17.7293 | 19.586 | 19.7828 | 20.0262 | 20.3494 | 20.6558 | 21.1912 | 22.5377 | 23.262 | 22.7336 | 24.3694 | 24.6641 | 24.8759 | 25.8746 | 26.0371 | 26.0371 | 26.0371 | 26.0371 | 26.0371 | 26.0371 | 26.0371 | 26.0371 | 26.0371 | 26.0371 | 26.0371 | 26.0371 | 26.0371 | 26.0371 | 26.0371 | 26.0371 | 50% | 1730.2899 | 19.4357 | 21.2067 | 21.3901 | 22.023 | 22.0076 | 22.1468 | 22.6911 | 24.2551 | 24.9004 | 24.2895 | 25.9771 | 25.2686 | 25.9061 | 26.3655 | 26.1767 | 26.1767 | 26.1767 | 26.1767 | 26.1767 | 26.1767 | 26.1767 | 26.1767 | 26.1767 | 26.1767 | 26.1767 | 26.1767 | 26.1767 | 26.1767 | 26.1767 | 26.1767
45% | 2168.0633 | 15.9564 | 17.6274 | 17.8046 | 18.0236 | 18.3145 | 18.5902 | 19.072 | 20.2839 | 20.9358 | 20.4602 | 21.9324 | 22.1977 | 22.3883 | 23.2871 | 23.4334 | 23.4334 | 23.4334 | 23.4334 | 23.4334 | 23.4334 | 23.4334 | 23.4334 | 23.4334 | 23.4334 | 23.4334 | 23.4334 | 23.4334 | 23.4334 | 23.4334 | 23.4334 | 45% | 2168.0633 | 17.4921 | 19.086 | 19.2511 | 19.8207 | 19.8068 | 19.9321 | 20.422 | 21.8296 | 22.4104 | 21.8606 | 23.3794 | 22.7417 | 23.3155 | 23.7289 | 23.5591 | 23.5591 | 23.5591 | 23.5591 | 23.5591 | 23.5591 | 23.5591 | 23.5591 | 23.5591 | 23.5591 | 23.5591 | 23.5591 | 23.5591 | 23.5591 | 23.5591 | 23.5591
40% | 2609.7004 | 14.1835 | 15.6688 | 15.8263 | 16.021 | 16.2795 | 16.5246 | 16.9529 | 18.0302 | 18.6096 | 18.1869 | 19.4955 | 19.7313 | 19.9008 | 20.6996 | 20.8297 | 20.8297 | 20.8297 | 20.8297 | 20.8297 | 20.8297 | 20.8297 | 20.8297 | 20.8297 | 20.8297 | 20.8297 | 20.8297 | 20.8297 | 20.8297 | 20.8297 | 20.8297 | 40% | 2609.7004 | 15.5485 | 16.9653 | 17.1121 | 17.6184 | 17.6061 | 17.7174 | 18.1529 | 19.404 | 19.9203 | 19.4316 | 20.7817 | 20.2148 | 20.7249 | 21.0924 | 20.9414 | 20.9414 | 20.9414 | 20.9414 | 20.9414 | 20.9414 | 20.9414 | 20.9414 | 20.9414 | 20.9414 | 20.9414 | 20.9414 | 20.9414 | 20.9414 | 20.9414 | 20.9414
35% | 2998.1389 | 12.4105 | 13.7102 | 13.848 | 14.0184 | 14.2446 | 14.459 | 14.8338 | 15.7764 | 16.2834 | 15.9135 | 17.0586 | 17.2649 | 17.4132 | 18.1122 | 18.226 | 18.226 | 18.226 | 18.226 | 18.226 | 18.226 | 18.226 | 18.226 | 18.226 | 18.226 | 18.226 | 18.226 | 18.226 | 18.226 | 18.226 | 18.226 | 35% | 2998.1389 | 13.605 | 14.8447 | 14.973 | 15.4161 | 15.4053 | 15.5027 | 15.8838 | 16.9785 | 17.4303 | 17.0027 | 18.184 | 17.688 | 18.1343 | 18.4558 | 18.3237 | 18.3237 | 18.3237 | 18.3237 | 18.3237 | 18.3237 | 18.3237 | 18.3237 | 18.3237 | 18.3237 | 18.3237 | 18.3237 | 18.3237 | 18.3237 | 18.3237 | 18.3237
30% | 3309.3057 | 10.6376 | 11.7516 | 11.8697 | 12.0157 | 12.2096 | 12.3935 | 12.7147 | 13.5226 | 13.9572 | 13.6402 | 14.6216 | 14.7985 | 14.9256 | 15.5247 | 15.6223 | 15.6223 | 15.6223 | 15.6223 | 15.6223 | 15.6223 | 15.6223 | 15.6223 | 15.6223 | 15.6223 | 15.6223 | 15.6223 | 15.6223 | 15.6223 | 15.6223 | 15.6223 | 30% | 3309.3057 | 11.6614 | 12.724 | 12.834 | 13.2138 | 13.2046 | 13.2881 | 13.6147 | 14.553 | 14.9403 | 14.5737 | 15.5862 | 15.1611 | 15.5436 | 15.8193 | 15.706 | 15.706 | 15.706 | 15.706 | 15.706 | 15.706 | 15.706 | 15.706 | 15.706 | 15.706 | 15.706 | 15.706 | 15.706 | 15.706 | 15.706 | 15.706
25% | 3537.8514 | 8.8647 | 9.793 | 9.8914 | 10.0131 | 10.1747 | 10.3279 | 10.5956 | 11.2688 | 11.631 | 11.3668 | 12.1847 | 12.332 | 12.438 | 12.9373 | 13.0185 | 13.0185 | 13.0185 | 13.0185 | 13.0185 | 13.0185 | 13.0185 | 13.0185 | 13.0185 | 13.0185 | 13.0185 | 13.0185 | 13.0185 | 13.0185 | 13.0185 | 13.0185 | 25% | 3537.8514 | 9.7178 | 10.6033 | 10.695 | 11.0115 | 11.0038 | 11.0734 | 11.3456 | 12.1275 | 12.4502 | 12.1448 | 12.9885 | 12.6343 | 12.953 | 13.1827 | 13.0884 | 13.0884 | 13.0884 | 13.0884 | 13.0884 | 13.0884 | 13.0884 | 13.0884 | 13.0884 | 13.0884 | 13.0884 | 13.0884 | 13.0884 | 13.0884 | 13.0884 | 13.0884
20% | 3731.0305 | 7.0917 | 7.8344 | 7.9131 | 8.0105 | 8.1398 | 8.2623 | 8.4765 | 9.0151 | 9.3048 | 9.0934 | 9.7477 | 9.8656 | 9.9504 | 10.3498 | 10.4148 | 10.4148 | 10.4148 | 10.4148 | 10.4148 | 10.4148 | 10.4148 | 10.4148 | 10.4148 | 10.4148 | 10.4148 | 10.4148 | 10.4148 | 10.4148 | 10.4148 | 10.4148 | 20% | 3731.0305 | 7.7743 | 8.4827 | 8.556 | 8.8092 | 8.803 | 8.8587 | 9.0764 | 9.702 | 9.9602 | 9.7158 | 10.3908 | 10.1074 | 10.3624 | 10.5462 | 10.4707 | 10.4707 | 10.4707 | 10.4707 | 10.4707 | 10.4707 | 10.4707 | 10.4707 | 10.4707 | 10.4707 | 10.4707 | 10.4707 | 10.4707 | 10.4707 | 10.4707 | 10.4707
15% | 3910.2412 | 5.3188 | 5.8758 | 5.9349 | 6.0079 | 6.1048 | 6.1967 | 6.3573 | 6.7613 | 6.9786 | 6.8201 | 7.3108 | 7.3992 | 7.4628 | 7.7624 | 7.8111 | 7.8111 | 7.8111 | 7.8111 | 7.8111 | 7.8111 | 7.8111 | 7.8111 | 7.8111 | 7.8111 | 7.8111 | 7.8111 | 7.8111 | 7.8111 | 7.8111 | 7.8111 | 15% | 3910.2412 | 5.8307 | 6.362 | 6.417 | 6.6069 | 6.6023 | 6.644 | 6.8073 | 7.2765 | 7.4701 | 7.2869 | 7.7931 | 7.5806 | 7.7718 | 7.9096 | 7.853 | 7.853 | 7.853 | 7.853 | 7.853 | 7.853 | 7.853 | 7.853 | 7.853 | 7.853 | 7.853 | 7.853 | 7.853 | 7.853 | 7.853 | 7.853
10% | 4075.1864 | 3.5459 | 3.9172 | 3.9566 | 4.0052 | 4.0699 | 4.1312 | 4.2382 | 4.5075 | 4.6524 | 4.5467 | 4.8739 | 4.9328 | 4.9752 | 5.1749 | 5.2074 | 5.2074 | 5.2074 | 5.2074 | 5.2074 | 5.2074 | 5.2074 | 5.2074 | 5.2074 | 5.2074 | 5.2074 | 5.2074 | 5.2074 | 5.2074 | 5.2074 | 5.2074 | 10% | 4075.1864 | 3.8871 | 4.2413 | 4.278 | 4.4046 | 4.4015 | 4.4294 | 4.5382 | 4.851 | 4.9801 | 4.8579 | 5.1954 | 5.0537 | 5.1812 | 5.2731 | 5.2353 | 5.2353 | 5.2353 | 5.2353 | 5.2353 | 5.2353 | 5.2353 | 5.2353 | 5.2353 | 5.2353 | 5.2353 | 5.2353 | 5.2353 | 5.2353 | 5.2353 | 5.2353
5% | 4251.7223 | 1.7729 | 1.9586 | 1.9783 | 2.0026 | 2.0349 | 2.0656 | 2.1191 | 2.2538 | 2.3262 | 2.2734 | 2.4369 | 2.4664 | 2.4876 | 2.5875 | 2.6037 | 2.6037 | 2.6037 | 2.6037 | 2.6037 | 2.6037 | 2.6037 | 2.6037 | 2.6037 | 2.6037 | 2.6037 | 2.6037 | 2.6037 | 2.6037 | 2.6037 | 2.6037 | 5% | 4251.7223 | 1.9436 | 2.1207 | 2.139 | 2.2023 | 2.2008 | 2.2147 | 2.2691 | 2.4255 | 2.49 | 2.429 | 2.5977 | 2.5269 | 2.5906 | 2.6365 | 2.6177 | 2.6177 | 2.6177 | 2.6177 | 2.6177 | 2.6177 | 2.6177 | 2.6177 | 2.6177 | 2.6177 | 2.6177 | 2.6177 | 2.6177 | 2.6177 | 2.6177 | 2.6177
9.992e-14% | 4391.7028 | 3.543e-14 | 3.9141e-14 | 3.9534e-14 | 4.002e-14 | 4.0666e-14 | 4.1279e-14 | 4.2348e-14 | 4.5039e-14 | 4.6487e-14 | 4.5431e-14 | 4.87e-14 | 4.9289e-14 | 4.9712e-14 | 5.1708e-14 | 5.2033e-14 | 5.2033e-14 | 5.2033e-14 | 5.2033e-14 | 5.2033e-14 | 5.2033e-14 | 5.2033e-14 | 5.2033e-14 | 5.2033e-14 | 5.2033e-14 | 5.2033e-14 | 5.2033e-14 | 5.2033e-14 | 5.2033e-14 | 5.2033e-14 | 5.2033e-14 | 9.992e-14% | 4391.7028 | 3.884e-14 | 4.2379e-14 | 4.2746e-14 | 4.4011e-14 | 4.398e-14 | 4.4258e-14 | 4.5346e-14 | 4.8471e-14 | 4.9761e-14 | 4.854e-14 | 5.1913e-14 | 5.0497e-14 | 5.1771e-14 | 5.2689e-14 | 5.2312e-14 | 5.2312e-14 | 5.2312e-14 | 5.2312e-14 | 5.2312e-14 | 5.2312e-14 | 5.2312e-14 | 5.2312e-14 | 5.2312e-14 | 5.2312e-14 | 5.2312e-14 | 5.2312e-14 | 5.2312e-14 | 5.2312e-14 | 5.2312e-14 | 5.2312e-14
Summer Season | [31 empty] | Summer Season
P50 | [31 empty] | P10
% of MD | Summer - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Summer - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 37.2509 | 40.0367 | 40.3167 | 40.1794 | 40.3099 | 40.3635 | 40.5354 | 40.8886 | 41.1859 | 41.3227 | 41.2007 | 41.712 | 41.7931 | 41.6971 | 41.8895 | 41.9995 | 41.9995 | 41.9995 | 41.9995 | 41.9995 | 41.9995 | 41.9995 | 41.9995 | 41.9995 | 41.9995 | 41.9995 | 41.9995 | 41.9995 | 41.9995 | 41.9995 | 100% | 0 | 45.8318 | 48.9452 | 49.0311 | 48.9384 | 48.9623 | 49.1323 | 49.4768 | 50.0836 | 50.3998 | 50.6285 | 50.9747 | 51.4167 | 51.9511 | 52.2312 | 52.1404 | 52.2504 | 52.2504 | 52.2504 | 52.2504 | 52.2504 | 52.2504 | 52.2504 | 52.2504 | 52.2504 | 52.2504 | 52.2504 | 52.2504 | 52.2504 | 52.2504 | 52.2504
99% | 0.37816 | 36.8784 | 39.6364 | 39.9135 | 39.7777 | 39.9068 | 39.9599 | 40.13 | 40.4798 | 40.774 | 40.9094 | 40.7887 | 41.2949 | 41.3751 | 41.2801 | 41.4706 | 41.5795 | 41.5795 | 41.5795 | 41.5795 | 41.5795 | 41.5795 | 41.5795 | 41.5795 | 41.5795 | 41.5795 | 41.5795 | 41.5795 | 41.5795 | 41.5795 | 41.5795 | 99% | 0 | 45.3735 | 48.4557 | 48.5408 | 48.4491 | 48.4726 | 48.6409 | 48.982 | 49.5828 | 49.8958 | 50.1222 | 50.465 | 50.9025 | 51.4316 | 51.7089 | 51.619 | 51.7279 | 51.7279 | 51.7279 | 51.7279 | 51.7279 | 51.7279 | 51.7279 | 51.7279 | 51.7279 | 51.7279 | 51.7279 | 51.7279 | 51.7279 | 51.7279 | 51.7279
98% | 0.37816 | 36.5059 | 39.236 | 39.5103 | 39.3759 | 39.5037 | 39.5563 | 39.7246 | 40.0709 | 40.3621 | 40.4962 | 40.3767 | 40.8777 | 40.9572 | 40.8632 | 41.0517 | 41.1595 | 41.1595 | 41.1595 | 41.1595 | 41.1595 | 41.1595 | 41.1595 | 41.1595 | 41.1595 | 41.1595 | 41.1595 | 41.1595 | 41.1595 | 41.1595 | 41.1595 | 98% | 0 | 44.9152 | 47.9662 | 48.0504 | 47.9597 | 47.983 | 48.1496 | 48.4873 | 49.0819 | 49.3918 | 49.6159 | 49.9552 | 50.3883 | 50.9121 | 51.1866 | 51.0976 | 51.2054 | 51.2054 | 51.2054 | 51.2054 | 51.2054 | 51.2054 | 51.2054 | 51.2054 | 51.2054 | 51.2054 | 51.2054 | 51.2054 | 51.2054 | 51.2054 | 51.2054
97% | 0.37816 | 36.1334 | 38.8356 | 39.1072 | 38.9741 | 39.1006 | 39.1526 | 39.3193 | 39.662 | 39.9503 | 40.083 | 39.9647 | 40.4606 | 40.5393 | 40.4462 | 40.6328 | 40.7395 | 40.7395 | 40.7395 | 40.7395 | 40.7395 | 40.7395 | 40.7395 | 40.7395 | 40.7395 | 40.7395 | 40.7395 | 40.7395 | 40.7395 | 40.7395 | 40.7395 | 97% | 0.37816 | 44.4569 | 47.4768 | 47.5601 | 47.4703 | 47.4934 | 47.6583 | 47.9925 | 48.5811 | 48.8878 | 49.1097 | 49.4455 | 49.8742 | 50.3926 | 50.6643 | 50.5762 | 50.6829 | 50.6829 | 50.6829 | 50.6829 | 50.6829 | 50.6829 | 50.6829 | 50.6829 | 50.6829 | 50.6829 | 50.6829 | 50.6829 | 50.6829 | 50.6829 | 50.6829
95% | 0.75633 | 35.3884 | 38.0349 | 38.3008 | 38.1705 | 38.2944 | 38.3454 | 38.5086 | 38.8442 | 39.1266 | 39.2565 | 39.1407 | 39.6264 | 39.7034 | 39.6123 | 39.7951 | 39.8996 | 39.8996 | 39.8996 | 39.8996 | 39.8996 | 39.8996 | 39.8996 | 39.8996 | 39.8996 | 39.8996 | 39.8996 | 39.8996 | 39.8996 | 39.8996 | 39.8996 | 95% | 0.37816 | 43.5402 | 46.4979 | 46.5795 | 46.4915 | 46.5141 | 46.6757 | 47.003 | 47.5794 | 47.8798 | 48.0971 | 48.426 | 48.8458 | 49.3536 | 49.6196 | 49.5334 | 49.6379 | 49.6379 | 49.6379 | 49.6379 | 49.6379 | 49.6379 | 49.6379 | 49.6379 | 49.6379 | 49.6379 | 49.6379 | 49.6379 | 49.6379 | 49.6379 | 49.6379
90% | 9.0759 | 33.5258 | 36.0331 | 36.285 | 36.1615 | 36.2789 | 36.3272 | 36.4818 | 36.7998 | 37.0673 | 37.1904 | 37.0807 | 37.5408 | 37.6138 | 37.5274 | 37.7006 | 37.7996 | 37.7996 | 37.7996 | 37.7996 | 37.7996 | 37.7996 | 37.7996 | 37.7996 | 37.7996 | 37.7996 | 37.7996 | 37.7996 | 37.7996 | 37.7996 | 37.7996 | 90% | 0.75633 | 41.2486 | 44.0506 | 44.128 | 44.0446 | 44.066 | 44.219 | 44.5291 | 45.0752 | 45.3598 | 45.5657 | 45.8772 | 46.275 | 46.756 | 47.0081 | 46.9264 | 47.0254 | 47.0254 | 47.0254 | 47.0254 | 47.0254 | 47.0254 | 47.0254 | 47.0254 | 47.0254 | 47.0254 | 47.0254 | 47.0254 | 47.0254 | 47.0254 | 47.0254
85% | 40.4636 | 31.6633 | 34.0312 | 34.2692 | 34.1525 | 34.2634 | 34.309 | 34.455 | 34.7554 | 35.008 | 35.1243 | 35.0206 | 35.4552 | 35.5241 | 35.4425 | 35.6061 | 35.6996 | 35.6996 | 35.6996 | 35.6996 | 35.6996 | 35.6996 | 35.6996 | 35.6996 | 35.6996 | 35.6996 | 35.6996 | 35.6996 | 35.6996 | 35.6996 | 35.6996 | 85% | 1.1345 | 38.957 | 41.6034 | 41.6764 | 41.5977 | 41.6179 | 41.7624 | 42.0553 | 42.5711 | 42.8398 | 43.0342 | 43.3285 | 43.7042 | 44.1585 | 44.3965 | 44.3193 | 44.4128 | 44.4128 | 44.4128 | 44.4128 | 44.4128 | 44.4128 | 44.4128 | 44.4128 | 44.4128 | 44.4128 | 44.4128 | 44.4128 | 44.4128 | 44.4128 | 44.4128
80% | 94.5411 | 29.8007 | 32.0294 | 32.2533 | 32.1436 | 32.2479 | 32.2908 | 32.4283 | 32.7109 | 32.9487 | 33.0581 | 32.9606 | 33.3696 | 33.4345 | 33.3577 | 33.5116 | 33.5996 | 33.5996 | 33.5996 | 33.5996 | 33.5996 | 33.5996 | 33.5996 | 33.5996 | 33.5996 | 33.5996 | 33.5996 | 33.5996 | 33.5996 | 33.5996 | 33.5996 | 80% | 2.6471 | 36.6655 | 39.1561 | 39.2249 | 39.1508 | 39.1698 | 39.3058 | 39.5815 | 40.0669 | 40.3198 | 40.5028 | 40.7798 | 41.1333 | 41.5609 | 41.785 | 41.7123 | 41.8003 | 41.8003 | 41.8003 | 41.8003 | 41.8003 | 41.8003 | 41.8003 | 41.8003 | 41.8003 | 41.8003 | 41.8003 | 41.8003 | 41.8003 | 41.8003 | 41.8003
75% | 197.0236 | 27.9382 | 30.0275 | 30.2375 | 30.1346 | 30.2324 | 30.2726 | 30.4015 | 30.6665 | 30.8894 | 30.992 | 30.9005 | 31.284 | 31.3448 | 31.2728 | 31.4172 | 31.4997 | 31.4997 | 31.4997 | 31.4997 | 31.4997 | 31.4997 | 31.4997 | 31.4997 | 31.4997 | 31.4997 | 31.4997 | 31.4997 | 31.4997 | 31.4997 | 31.4997 | 75% | 3.4035 | 34.3739 | 36.7089 | 36.7733 | 36.7038 | 36.7217 | 36.8492 | 37.1076 | 37.5627 | 37.7998 | 37.9714 | 38.231 | 38.5625 | 38.9633 | 39.1734 | 39.1053 | 39.1878 | 39.1878 | 39.1878 | 39.1878 | 39.1878 | 39.1878 | 39.1878 | 39.1878 | 39.1878 | 39.1878 | 39.1878 | 39.1878 | 39.1878 | 39.1878 | 39.1878
70% | 336.9444 | 26.0756 | 28.0257 | 28.2217 | 28.1256 | 28.2169 | 28.2545 | 28.3747 | 28.6221 | 28.8301 | 28.9259 | 28.8405 | 29.1984 | 29.2552 | 29.188 | 29.3227 | 29.3997 | 29.3997 | 29.3997 | 29.3997 | 29.3997 | 29.3997 | 29.3997 | 29.3997 | 29.3997 | 29.3997 | 29.3997 | 29.3997 | 29.3997 | 29.3997 | 29.3997 | 70% | 5.6725 | 32.0823 | 34.2616 | 34.3217 | 34.2569 | 34.2736 | 34.3926 | 34.6338 | 35.0585 | 35.2798 | 35.44 | 35.6823 | 35.9917 | 36.3658 | 36.5618 | 36.4983 | 36.5753 | 36.5753 | 36.5753 | 36.5753 | 36.5753 | 36.5753 | 36.5753 | 36.5753 | 36.5753 | 36.5753 | 36.5753 | 36.5753 | 36.5753 | 36.5753 | 36.5753
65% | 521.4885 | 24.2131 | 26.0239 | 26.2058 | 26.1166 | 26.2014 | 26.2363 | 26.348 | 26.5776 | 26.7708 | 26.8597 | 26.7805 | 27.1128 | 27.1655 | 27.1031 | 27.2282 | 27.2997 | 27.2997 | 27.2997 | 27.2997 | 27.2997 | 27.2997 | 27.2997 | 27.2997 | 27.2997 | 27.2997 | 27.2997 | 27.2997 | 27.2997 | 27.2997 | 27.2997 | 65% | 6.4288 | 29.7907 | 31.8143 | 31.8702 | 31.81 | 31.8255 | 31.936 | 32.1599 | 32.5543 | 32.7599 | 32.9085 | 33.1336 | 33.4208 | 33.7682 | 33.9503 | 33.8913 | 33.9628 | 33.9628 | 33.9628 | 33.9628 | 33.9628 | 33.9628 | 33.9628 | 33.9628 | 33.9628 | 33.9628 | 33.9628 | 33.9628 | 33.9628 | 33.9628 | 33.9628
60% | 812.675 | 22.3505 | 24.022 | 24.19 | 24.1077 | 24.186 | 24.2181 | 24.3212 | 24.5332 | 24.7115 | 24.7936 | 24.7204 | 25.0272 | 25.0758 | 25.0183 | 25.1337 | 25.1997 | 25.1997 | 25.1997 | 25.1997 | 25.1997 | 25.1997 | 25.1997 | 25.1997 | 25.1997 | 25.1997 | 25.1997 | 25.1997 | 25.1997 | 25.1997 | 25.1997 | 60% | 11.3449 | 27.4991 | 29.3671 | 29.4186 | 29.3631 | 29.3774 | 29.4794 | 29.6861 | 30.0502 | 30.2399 | 30.3771 | 30.5848 | 30.85 | 31.1707 | 31.3387 | 31.2842 | 31.3502 | 31.3502 | 31.3502 | 31.3502 | 31.3502 | 31.3502 | 31.3502 | 31.3502 | 31.3502 | 31.3502 | 31.3502 | 31.3502 | 31.3502 | 31.3502 | 31.3502
55% | 1202.1843 | 20.488 | 22.0202 | 22.1742 | 22.0987 | 22.1705 | 22.1999 | 22.2944 | 22.4888 | 22.6522 | 22.7275 | 22.6604 | 22.9416 | 22.9862 | 22.9334 | 23.0392 | 23.0997 | 23.0997 | 23.0997 | 23.0997 | 23.0997 | 23.0997 | 23.0997 | 23.0997 | 23.0997 | 23.0997 | 23.0997 | 23.0997 | 23.0997 | 23.0997 | 23.0997 | 55% | 35.5474 | 25.2075 | 26.9198 | 26.9671 | 26.9161 | 26.9292 | 27.0227 | 27.2122 | 27.546 | 27.7199 | 27.8457 | 28.0361 | 28.2792 | 28.5731 | 28.7272 | 28.6772 | 28.7377 | 28.7377 | 28.7377 | 28.7377 | 28.7377 | 28.7377 | 28.7377 | 28.7377 | 28.7377 | 28.7377 | 28.7377 | 28.7377 | 28.7377 | 28.7377 | 28.7377
50% | 1686.2345 | 18.6255 | 20.0184 | 20.1583 | 20.0897 | 20.155 | 20.1818 | 20.2677 | 20.4443 | 20.5929 | 20.6613 | 20.6004 | 20.856 | 20.8965 | 20.8486 | 20.9448 | 20.9998 | 20.9998 | 20.9998 | 20.9998 | 20.9998 | 20.9998 | 20.9998 | 20.9998 | 20.9998 | 20.9998 | 20.9998 | 20.9998 | 20.9998 | 20.9998 | 20.9998 | 50% | 95.2974 | 22.9159 | 24.4726 | 24.5155 | 24.4692 | 24.4811 | 24.5661 | 24.7384 | 25.0418 | 25.1999 | 25.3143 | 25.4873 | 25.7083 | 25.9756 | 26.1156 | 26.0702 | 26.1252 | 26.1252 | 26.1252 | 26.1252 | 26.1252 | 26.1252 | 26.1252 | 26.1252 | 26.1252 | 26.1252 | 26.1252 | 26.1252 | 26.1252 | 26.1252 | 26.1252
45% | 2129.0649 | 16.7629 | 18.0165 | 18.1425 | 18.0808 | 18.1395 | 18.1636 | 18.2409 | 18.3999 | 18.5336 | 18.5952 | 18.5403 | 18.7704 | 18.8069 | 18.7637 | 18.8503 | 18.8998 | 18.8998 | 18.8998 | 18.8998 | 18.8998 | 18.8998 | 18.8998 | 18.8998 | 18.8998 | 18.8998 | 18.8998 | 18.8998 | 18.8998 | 18.8998 | 18.8998 | 45% | 208.7467 | 20.6243 | 22.0253 | 22.064 | 22.0223 | 22.033 | 22.1095 | 22.2646 | 22.5376 | 22.6799 | 22.7828 | 22.9386 | 23.1375 | 23.378 | 23.504 | 23.4632 | 23.5127 | 23.5127 | 23.5127 | 23.5127 | 23.5127 | 23.5127 | 23.5127 | 23.5127 | 23.5127 | 23.5127 | 23.5127 | 23.5127 | 23.5127 | 23.5127 | 23.5127
40% | 2484.5393 | 14.9004 | 16.0147 | 16.1267 | 16.0718 | 16.124 | 16.1454 | 16.2141 | 16.3555 | 16.4743 | 16.5291 | 16.4803 | 16.6848 | 16.7172 | 16.6788 | 16.7558 | 16.7998 | 16.7998 | 16.7998 | 16.7998 | 16.7998 | 16.7998 | 16.7998 | 16.7998 | 16.7998 | 16.7998 | 16.7998 | 16.7998 | 16.7998 | 16.7998 | 16.7998 | 40% | 380.4333 | 18.3327 | 19.5781 | 19.6124 | 19.5754 | 19.5849 | 19.6529 | 19.7907 | 20.0334 | 20.1599 | 20.2514 | 20.3899 | 20.5667 | 20.7804 | 20.8925 | 20.8562 | 20.9002 | 20.9002 | 20.9002 | 20.9002 | 20.9002 | 20.9002 | 20.9002 | 20.9002 | 20.9002 | 20.9002 | 20.9002 | 20.9002 | 20.9002 | 20.9002 | 20.9002
35% | 2808.248 | 13.0378 | 14.0129 | 14.1108 | 14.0628 | 14.1085 | 14.1272 | 14.1874 | 14.311 | 14.415 | 14.4629 | 14.4203 | 14.5992 | 14.6276 | 14.594 | 14.6613 | 14.6998 | 14.6998 | 14.6998 | 14.6998 | 14.6998 | 14.6998 | 14.6998 | 14.6998 | 14.6998 | 14.6998 | 14.6998 | 14.6998 | 14.6998 | 14.6998 | 14.6998 | 35% | 696.5786 | 16.0411 | 17.1308 | 17.1609 | 17.1285 | 17.1368 | 17.1963 | 17.3169 | 17.5293 | 17.6399 | 17.72 | 17.8411 | 17.9958 | 18.1829 | 18.2809 | 18.2491 | 18.2876 | 18.2876 | 18.2876 | 18.2876 | 18.2876 | 18.2876 | 18.2876 | 18.2876 | 18.2876 | 18.2876 | 18.2876 | 18.2876 | 18.2876 | 18.2876 | 18.2876
30% | 3095.6528 | 11.1753 | 12.011 | 12.095 | 12.0538 | 12.093 | 12.1091 | 12.1606 | 12.2666 | 12.3558 | 12.3968 | 12.3602 | 12.5136 | 12.5379 | 12.5091 | 12.5669 | 12.5999 | 12.5999 | 12.5999 | 12.5999 | 12.5999 | 12.5999 | 12.5999 | 12.5999 | 12.5999 | 12.5999 | 12.5999 | 12.5999 | 12.5999 | 12.5999 | 12.5999 | 30% | 1260.7997 | 13.7495 | 14.6835 | 14.7093 | 14.6815 | 14.6887 | 14.7397 | 14.843 | 15.0251 | 15.1199 | 15.1886 | 15.2924 | 15.425 | 15.5853 | 15.6694 | 15.6421 | 15.6751 | 15.6751 | 15.6751 | 15.6751 | 15.6751 | 15.6751 | 15.6751 | 15.6751 | 15.6751 | 15.6751 | 15.6751 | 15.6751 | 15.6751 | 15.6751 | 15.6751
25% | 3358.8552 | 9.3127 | 10.0092 | 10.0792 | 10.0449 | 10.0775 | 10.0909 | 10.1338 | 10.2222 | 10.2965 | 10.3307 | 10.3002 | 10.428 | 10.4483 | 10.4243 | 10.4724 | 10.4999 | 10.4999 | 10.4999 | 10.4999 | 10.4999 | 10.4999 | 10.4999 | 10.4999 | 10.4999 | 10.4999 | 10.4999 | 10.4999 | 10.4999 | 10.4999 | 10.4999 | 25% | 1965.3198 | 11.458 | 12.2363 | 12.2578 | 12.2346 | 12.2406 | 12.2831 | 12.3692 | 12.5209 | 12.5999 | 12.6571 | 12.7437 | 12.8542 | 12.9878 | 13.0578 | 13.0351 | 13.0626 | 13.0626 | 13.0626 | 13.0626 | 13.0626 | 13.0626 | 13.0626 | 13.0626 | 13.0626 | 13.0626 | 13.0626 | 13.0626 | 13.0626 | 13.0626 | 13.0626
20% | 3588.7791 | 7.4502 | 8.0073 | 8.0633 | 8.0359 | 8.062 | 8.0727 | 8.1071 | 8.1777 | 8.2372 | 8.2645 | 8.2401 | 8.3424 | 8.3586 | 8.3394 | 8.3779 | 8.3999 | 8.3999 | 8.3999 | 8.3999 | 8.3999 | 8.3999 | 8.3999 | 8.3999 | 8.3999 | 8.3999 | 8.3999 | 8.3999 | 8.3999 | 8.3999 | 8.3999 | 20% | 2490.2118 | 9.1664 | 9.789 | 9.8062 | 9.7877 | 9.7925 | 9.8265 | 9.8954 | 10.0167 | 10.08 | 10.1257 | 10.1949 | 10.2833 | 10.3902 | 10.4462 | 10.4281 | 10.4501 | 10.4501 | 10.4501 | 10.4501 | 10.4501 | 10.4501 | 10.4501 | 10.4501 | 10.4501 | 10.4501 | 10.4501 | 10.4501 | 10.4501 | 10.4501 | 10.4501
15% | 3802.4419 | 5.5876 | 6.0055 | 6.0475 | 6.0269 | 6.0465 | 6.0545 | 6.0803 | 6.1333 | 6.1779 | 6.1984 | 6.1801 | 6.2568 | 6.269 | 6.2546 | 6.2834 | 6.2999 | 6.2999 | 6.2999 | 6.2999 | 6.2999 | 6.2999 | 6.2999 | 6.2999 | 6.2999 | 6.2999 | 6.2999 | 6.2999 | 6.2999 | 6.2999 | 6.2999 | 15% | 2997.7083 | 6.8748 | 7.3418 | 7.3547 | 7.3408 | 7.3443 | 7.3698 | 7.4215 | 7.5125 | 7.56 | 7.5943 | 7.6462 | 7.7125 | 7.7927 | 7.8347 | 7.8211 | 7.8376 | 7.8376 | 7.8376 | 7.8376 | 7.8376 | 7.8376 | 7.8376 | 7.8376 | 7.8376 | 7.8376 | 7.8376 | 7.8376 | 7.8376 | 7.8376 | 7.8376
10% | 4024.8025 | 3.7251 | 4.0037 | 4.0317 | 4.0179 | 4.031 | 4.0364 | 4.0535 | 4.0889 | 4.1186 | 4.1323 | 4.1201 | 4.1712 | 4.1793 | 4.1697 | 4.189 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 10% | 3491.5908 | 4.5832 | 4.8945 | 4.9031 | 4.8938 | 4.8962 | 4.9132 | 4.9477 | 5.0084 | 5.04 | 5.0629 | 5.0975 | 5.1417 | 5.1951 | 5.2231 | 5.214 | 5.225 | 5.225 | 5.225 | 5.225 | 5.225 | 5.225 | 5.225 | 5.225 | 5.225 | 5.225 | 5.225 | 5.225 | 5.225 | 5.225 | 5.225
5% | 4239.978 | 1.8625 | 2.0018 | 2.0158 | 2.009 | 2.0155 | 2.0182 | 2.0268 | 2.0444 | 2.0593 | 2.0661 | 2.06 | 2.0856 | 2.0897 | 2.0849 | 2.0945 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 5% | 3955.9766 | 2.2916 | 2.4473 | 2.4516 | 2.4469 | 2.4481 | 2.4566 | 2.4738 | 2.5042 | 2.52 | 2.5314 | 2.5487 | 2.5708 | 2.5976 | 2.6116 | 2.607 | 2.6125 | 2.6125 | 2.6125 | 2.6125 | 2.6125 | 2.6125 | 2.6125 | 2.6125 | 2.6125 | 2.6125 | 2.6125 | 2.6125 | 2.6125 | 2.6125 | 2.6125
9.992e-14% | 4391.6218 | 3.7221e-14 | 4.0005e-14 | 4.0284e-14 | 4.0147e-14 | 4.0278e-14 | 4.0331e-14 | 4.0503e-14 | 4.0856e-14 | 4.1153e-14 | 4.129e-14 | 4.1168e-14 | 4.1679e-14 | 4.176e-14 | 4.1664e-14 | 4.1856e-14 | 4.1966e-14 | 4.1966e-14 | 4.1966e-14 | 4.1966e-14 | 4.1966e-14 | 4.1966e-14 | 4.1966e-14 | 4.1966e-14 | 4.1966e-14 | 4.1966e-14 | 4.1966e-14 | 4.1966e-14 | 4.1966e-14 | 4.1966e-14 | 4.1966e-14 | 9.992e-14% | 4391.6218 | 4.5795e-14 | 4.8906e-14 | 4.8992e-14 | 4.8899e-14 | 4.8923e-14 | 4.9093e-14 | 4.9437e-14 | 5.0044e-14 | 5.0359e-14 | 5.0588e-14 | 5.0934e-14 | 5.1376e-14 | 5.191e-14 | 5.2189e-14 | 5.2099e-14 | 5.2209e-14 | 5.2209e-14 | 5.2209e-14 | 5.2209e-14 | 5.2209e-14 | 5.2209e-14 | 5.2209e-14 | 5.2209e-14 | 5.2209e-14 | 5.2209e-14 | 5.2209e-14 | 5.2209e-14 | 5.2209e-14 | 5.2209e-14 | 5.2209e-14
Option 7
Winter Season | [31 empty] | Winter Season
P50 | [31 empty] | P10
% of MD | Winter - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Winter - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 35.4586 | 39.1719 | 39.5657 | 40.0525 | 40.6988 | 41.3115 | 42.3823 | 45.0754 | 46.5239 | 45.4672 | 48.7387 | 49.3282 | 49.7519 | 51.7491 | 52.0742 | 52.0742 | 52.0742 | 52.0742 | 52.0742 | 52.0742 | 52.0742 | 52.0742 | 52.0742 | 52.0742 | 52.0742 | 52.0742 | 52.0742 | 52.0742 | 52.0742 | 52.0742 | 100% | 0 | 38.8714 | 42.4133 | 42.7801 | 44.046 | 44.0152 | 44.2935 | 45.3822 | 48.5101 | 49.8009 | 48.5791 | 51.9542 | 50.5371 | 51.8122 | 52.731 | 52.3535 | 52.3535 | 52.3535 | 52.3535 | 52.3535 | 52.3535 | 52.3535 | 52.3535 | 52.3535 | 52.3535 | 52.3535 | 52.3535 | 52.3535 | 52.3535 | 52.3535 | 52.3535
99% | 0.2972 | 35.104 | 38.7802 | 39.17 | 39.652 | 40.2918 | 40.8984 | 41.9585 | 44.6246 | 46.0587 | 45.0125 | 48.2513 | 48.8349 | 49.2544 | 51.2316 | 51.5535 | 51.5535 | 51.5535 | 51.5535 | 51.5535 | 51.5535 | 51.5535 | 51.5535 | 51.5535 | 51.5535 | 51.5535 | 51.5535 | 51.5535 | 51.5535 | 51.5535 | 51.5535 | 99% | 0.2972 | 38.4827 | 41.9892 | 42.3523 | 43.6056 | 43.575 | 43.8506 | 44.9284 | 48.025 | 49.3029 | 48.0933 | 51.4346 | 50.0317 | 51.294 | 52.2037 | 51.83 | 51.83 | 51.83 | 51.83 | 51.83 | 51.83 | 51.83 | 51.83 | 51.83 | 51.83 | 51.83 | 51.83 | 51.83 | 51.83 | 51.83 | 51.83
98% | 0.2972 | 34.7495 | 38.3885 | 38.7744 | 39.2514 | 39.8848 | 40.4853 | 41.5347 | 44.1739 | 45.5935 | 44.5578 | 47.764 | 48.3416 | 48.7568 | 50.7141 | 51.0327 | 51.0327 | 51.0327 | 51.0327 | 51.0327 | 51.0327 | 51.0327 | 51.0327 | 51.0327 | 51.0327 | 51.0327 | 51.0327 | 51.0327 | 51.0327 | 51.0327 | 51.0327 | 98% | 0.2972 | 38.0939 | 41.5651 | 41.9245 | 43.1651 | 43.1349 | 43.4077 | 44.4746 | 47.5399 | 48.8049 | 47.6075 | 50.9151 | 49.5264 | 50.7759 | 51.6764 | 51.3064 | 51.3064 | 51.3064 | 51.3064 | 51.3064 | 51.3064 | 51.3064 | 51.3064 | 51.3064 | 51.3064 | 51.3064 | 51.3064 | 51.3064 | 51.3064 | 51.3064 | 51.3064
97% | 0.2972 | 34.3949 | 37.9968 | 38.3787 | 38.8509 | 39.4778 | 40.0722 | 41.1108 | 43.7231 | 45.1282 | 44.1032 | 47.2766 | 47.8483 | 48.2593 | 50.1966 | 50.512 | 50.512 | 50.512 | 50.512 | 50.512 | 50.512 | 50.512 | 50.512 | 50.512 | 50.512 | 50.512 | 50.512 | 50.512 | 50.512 | 50.512 | 50.512 | 97% | 0.2972 | 37.7052 | 41.1409 | 41.4967 | 42.7246 | 42.6947 | 42.9647 | 44.0208 | 47.0548 | 48.3068 | 47.1217 | 50.3955 | 49.021 | 50.2578 | 51.1491 | 50.7829 | 50.7829 | 50.7829 | 50.7829 | 50.7829 | 50.7829 | 50.7829 | 50.7829 | 50.7829 | 50.7829 | 50.7829 | 50.7829 | 50.7829 | 50.7829 | 50.7829 | 50.7829
95% | 1.486 | 33.6857 | 37.2134 | 37.5874 | 38.0499 | 38.6639 | 39.2459 | 40.2632 | 42.8216 | 44.1977 | 43.1938 | 46.3018 | 46.8618 | 47.2643 | 49.1617 | 49.4705 | 49.4705 | 49.4705 | 49.4705 | 49.4705 | 49.4705 | 49.4705 | 49.4705 | 49.4705 | 49.4705 | 49.4705 | 49.4705 | 49.4705 | 49.4705 | 49.4705 | 49.4705 | 95% | 1.486 | 36.9278 | 40.2927 | 40.6411 | 41.8437 | 41.8144 | 42.0789 | 43.1131 | 46.0846 | 47.3108 | 46.1501 | 49.3565 | 48.0103 | 49.2216 | 50.0944 | 49.7358 | 49.7358 | 49.7358 | 49.7358 | 49.7358 | 49.7358 | 49.7358 | 49.7358 | 49.7358 | 49.7358 | 49.7358 | 49.7358 | 49.7358 | 49.7358 | 49.7358 | 49.7358
90% | 8.6188 | 31.9128 | 35.2548 | 35.6091 | 36.0472 | 36.6289 | 37.1804 | 38.1441 | 40.5679 | 41.8715 | 40.9205 | 43.8649 | 44.3954 | 44.7767 | 46.5742 | 46.8668 | 46.8668 | 46.8668 | 46.8668 | 46.8668 | 46.8668 | 46.8668 | 46.8668 | 46.8668 | 46.8668 | 46.8668 | 46.8668 | 46.8668 | 46.8668 | 46.8668 | 46.8668 | 90% | 8.6188 | 34.9842 | 38.172 | 38.5021 | 39.6414 | 39.6137 | 39.8642 | 40.844 | 43.6591 | 44.8208 | 43.7212 | 46.7587 | 45.4834 | 46.6309 | 47.4579 | 47.1181 | 47.1181 | 47.1181 | 47.1181 | 47.1181 | 47.1181 | 47.1181 | 47.1181 | 47.1181 | 47.1181 | 47.1181 | 47.1181 | 47.1181 | 47.1181 | 47.1181 | 47.1181
85% | 40.1218 | 30.1398 | 33.2962 | 33.6308 | 34.0446 | 34.594 | 35.1148 | 36.025 | 38.3141 | 39.5453 | 38.6471 | 41.4279 | 41.9289 | 42.2891 | 43.9867 | 44.2631 | 44.2631 | 44.2631 | 44.2631 | 44.2631 | 44.2631 | 44.2631 | 44.2631 | 44.2631 | 44.2631 | 44.2631 | 44.2631 | 44.2631 | 44.2631 | 44.2631 | 44.2631 | 85% | 40.1218 | 33.0407 | 36.0513 | 36.3631 | 37.4391 | 37.4129 | 37.6495 | 38.5749 | 41.2336 | 42.3307 | 41.2922 | 44.161 | 42.9565 | 44.0403 | 44.8213 | 44.5005 | 44.5005 | 44.5005 | 44.5005 | 44.5005 | 44.5005 | 44.5005 | 44.5005 | 44.5005 | 44.5005 | 44.5005 | 44.5005 | 44.5005 | 44.5005 | 44.5005 | 44.5005
80% | 93.0231 | 28.3669 | 31.3376 | 31.6526 | 32.042 | 32.559 | 33.0492 | 33.9058 | 36.0603 | 37.2191 | 36.3737 | 38.991 | 39.4625 | 39.8015 | 41.3993 | 41.6594 | 41.6594 | 41.6594 | 41.6594 | 41.6594 | 41.6594 | 41.6594 | 41.6594 | 41.6594 | 41.6594 | 41.6594 | 41.6594 | 41.6594 | 41.6594 | 41.6594 | 41.6594 | 80% | 93.0231 | 31.0971 | 33.9307 | 34.2241 | 35.2368 | 35.2121 | 35.4348 | 36.3058 | 38.8081 | 39.8407 | 38.8633 | 41.5633 | 40.4297 | 41.4497 | 42.1848 | 41.8828 | 41.8828 | 41.8828 | 41.8828 | 41.8828 | 41.8828 | 41.8828 | 41.8828 | 41.8828 | 41.8828 | 41.8828 | 41.8828 | 41.8828 | 41.8828 | 41.8828 | 41.8828
75% | 197.0426 | 26.594 | 29.379 | 29.6743 | 30.0394 | 30.5241 | 30.9836 | 31.7867 | 33.8065 | 34.8929 | 34.1004 | 36.554 | 36.9961 | 37.3139 | 38.8118 | 39.0556 | 39.0556 | 39.0556 | 39.0556 | 39.0556 | 39.0556 | 39.0556 | 39.0556 | 39.0556 | 39.0556 | 39.0556 | 39.0556 | 39.0556 | 39.0556 | 39.0556 | 39.0556 | 75% | 197.0426 | 29.1535 | 31.81 | 32.0851 | 33.0345 | 33.0114 | 33.2201 | 34.0367 | 36.3826 | 37.3507 | 36.4343 | 38.9656 | 37.9028 | 38.8591 | 39.5482 | 39.2651 | 39.2651 | 39.2651 | 39.2651 | 39.2651 | 39.2651 | 39.2651 | 39.2651 | 39.2651 | 39.2651 | 39.2651 | 39.2651 | 39.2651 | 39.2651 | 39.2651 | 39.2651
70% | 378.0365 | 24.821 | 27.4204 | 27.696 | 28.0367 | 28.4892 | 28.9181 | 29.6676 | 31.5528 | 32.5668 | 31.827 | 34.1171 | 34.5297 | 34.8263 | 36.2244 | 36.4519 | 36.4519 | 36.4519 | 36.4519 | 36.4519 | 36.4519 | 36.4519 | 36.4519 | 36.4519 | 36.4519 | 36.4519 | 36.4519 | 36.4519 | 36.4519 | 36.4519 | 36.4519 | 70% | 378.0365 | 27.21 | 29.6893 | 29.9461 | 30.8322 | 30.8106 | 31.0055 | 31.7676 | 33.9571 | 34.8606 | 34.0054 | 36.3679 | 35.376 | 36.2685 | 36.9117 | 36.6474 | 36.6474 | 36.6474 | 36.6474 | 36.6474 | 36.6474 | 36.6474 | 36.6474 | 36.6474 | 36.6474 | 36.6474 | 36.6474 | 36.6474 | 36.6474 | 36.6474 | 36.6474
65% | 616.0926 | 23.0481 | 25.4618 | 25.7177 | 26.0341 | 26.4542 | 26.8525 | 27.5485 | 29.299 | 30.2406 | 29.5537 | 31.6802 | 32.0633 | 32.3387 | 33.6369 | 33.8482 | 33.8482 | 33.8482 | 33.8482 | 33.8482 | 33.8482 | 33.8482 | 33.8482 | 33.8482 | 33.8482 | 33.8482 | 33.8482 | 33.8482 | 33.8482 | 33.8482 | 33.8482 | 65% | 616.0926 | 25.2664 | 27.5687 | 27.8071 | 28.6299 | 28.6099 | 28.7908 | 29.4985 | 31.5316 | 32.3706 | 31.5764 | 33.7702 | 32.8491 | 33.6779 | 34.2751 | 34.0298 | 34.0298 | 34.0298 | 34.0298 | 34.0298 | 34.0298 | 34.0298 | 34.0298 | 34.0298 | 34.0298 | 34.0298 | 34.0298 | 34.0298 | 34.0298 | 34.0298 | 34.0298
60% | 934.9866 | 21.2752 | 23.5032 | 23.7394 | 24.0315 | 24.4193 | 24.7869 | 25.4294 | 27.0452 | 27.9144 | 27.2803 | 29.2432 | 29.5969 | 29.8511 | 31.0495 | 31.2445 | 31.2445 | 31.2445 | 31.2445 | 31.2445 | 31.2445 | 31.2445 | 31.2445 | 31.2445 | 31.2445 | 31.2445 | 31.2445 | 31.2445 | 31.2445 | 31.2445 | 31.2445 | 60% | 934.9866 | 23.3228 | 25.448 | 25.6681 | 26.4276 | 26.4091 | 26.5761 | 27.2293 | 29.1061 | 29.8805 | 29.1474 | 31.1725 | 30.3223 | 31.0873 | 31.6386 | 31.4121 | 31.4121 | 31.4121 | 31.4121 | 31.4121 | 31.4121 | 31.4121 | 31.4121 | 31.4121 | 31.4121 | 31.4121 | 31.4121 | 31.4121 | 31.4121 | 31.4121 | 31.4121
55% | 1310.9428 | 19.5022 | 21.5446 | 21.7611 | 22.0289 | 22.3843 | 22.7213 | 23.3103 | 24.7915 | 25.5882 | 25.0069 | 26.8063 | 27.1305 | 27.3635 | 28.462 | 28.6408 | 28.6408 | 28.6408 | 28.6408 | 28.6408 | 28.6408 | 28.6408 | 28.6408 | 28.6408 | 28.6408 | 28.6408 | 28.6408 | 28.6408 | 28.6408 | 28.6408 | 28.6408 | 55% | 1310.9428 | 21.3793 | 23.3273 | 23.5291 | 24.2253 | 24.2083 | 24.3614 | 24.9602 | 26.6806 | 27.3905 | 26.7185 | 28.5748 | 27.7954 | 28.4967 | 29.002 | 28.7944 | 28.7944 | 28.7944 | 28.7944 | 28.7944 | 28.7944 | 28.7944 | 28.7944 | 28.7944 | 28.7944 | 28.7944 | 28.7944 | 28.7944 | 28.7944 | 28.7944 | 28.7944
50% | 1730.2899 | 17.7293 | 19.586 | 19.7828 | 20.0262 | 20.3494 | 20.6558 | 21.1912 | 22.5377 | 23.262 | 22.7336 | 24.3694 | 24.6641 | 24.8759 | 25.8746 | 26.0371 | 26.0371 | 26.0371 | 26.0371 | 26.0371 | 26.0371 | 26.0371 | 26.0371 | 26.0371 | 26.0371 | 26.0371 | 26.0371 | 26.0371 | 26.0371 | 26.0371 | 26.0371 | 50% | 1730.2899 | 19.4357 | 21.2067 | 21.3901 | 22.023 | 22.0076 | 22.1468 | 22.6911 | 24.2551 | 24.9004 | 24.2895 | 25.9771 | 25.2686 | 25.9061 | 26.3655 | 26.1767 | 26.1767 | 26.1767 | 26.1767 | 26.1767 | 26.1767 | 26.1767 | 26.1767 | 26.1767 | 26.1767 | 26.1767 | 26.1767 | 26.1767 | 26.1767 | 26.1767 | 26.1767
45% | 2168.0633 | 15.9564 | 17.6274 | 17.8046 | 18.0236 | 18.3145 | 18.5902 | 19.072 | 20.2839 | 20.9358 | 20.4602 | 21.9324 | 22.1977 | 22.3883 | 23.2871 | 23.4334 | 23.4334 | 23.4334 | 23.4334 | 23.4334 | 23.4334 | 23.4334 | 23.4334 | 23.4334 | 23.4334 | 23.4334 | 23.4334 | 23.4334 | 23.4334 | 23.4334 | 23.4334 | 45% | 2168.0633 | 17.4921 | 19.086 | 19.2511 | 19.8207 | 19.8068 | 19.9321 | 20.422 | 21.8296 | 22.4104 | 21.8606 | 23.3794 | 22.7417 | 23.3155 | 23.7289 | 23.5591 | 23.5591 | 23.5591 | 23.5591 | 23.5591 | 23.5591 | 23.5591 | 23.5591 | 23.5591 | 23.5591 | 23.5591 | 23.5591 | 23.5591 | 23.5591 | 23.5591 | 23.5591
40% | 2609.7004 | 14.1835 | 15.6688 | 15.8263 | 16.021 | 16.2795 | 16.5246 | 16.9529 | 18.0302 | 18.6096 | 18.1869 | 19.4955 | 19.7313 | 19.9008 | 20.6996 | 20.8297 | 20.8297 | 20.8297 | 20.8297 | 20.8297 | 20.8297 | 20.8297 | 20.8297 | 20.8297 | 20.8297 | 20.8297 | 20.8297 | 20.8297 | 20.8297 | 20.8297 | 20.8297 | 40% | 2609.7004 | 15.5485 | 16.9653 | 17.1121 | 17.6184 | 17.6061 | 17.7174 | 18.1529 | 19.404 | 19.9203 | 19.4316 | 20.7817 | 20.2148 | 20.7249 | 21.0924 | 20.9414 | 20.9414 | 20.9414 | 20.9414 | 20.9414 | 20.9414 | 20.9414 | 20.9414 | 20.9414 | 20.9414 | 20.9414 | 20.9414 | 20.9414 | 20.9414 | 20.9414 | 20.9414
35% | 2998.1389 | 12.4105 | 13.7102 | 13.848 | 14.0184 | 14.2446 | 14.459 | 14.8338 | 15.7764 | 16.2834 | 15.9135 | 17.0586 | 17.2649 | 17.4132 | 18.1122 | 18.226 | 18.226 | 18.226 | 18.226 | 18.226 | 18.226 | 18.226 | 18.226 | 18.226 | 18.226 | 18.226 | 18.226 | 18.226 | 18.226 | 18.226 | 18.226 | 35% | 2998.1389 | 13.605 | 14.8447 | 14.973 | 15.4161 | 15.4053 | 15.5027 | 15.8838 | 16.9785 | 17.4303 | 17.0027 | 18.184 | 17.688 | 18.1343 | 18.4558 | 18.3237 | 18.3237 | 18.3237 | 18.3237 | 18.3237 | 18.3237 | 18.3237 | 18.3237 | 18.3237 | 18.3237 | 18.3237 | 18.3237 | 18.3237 | 18.3237 | 18.3237 | 18.3237
30% | 3309.3057 | 10.6376 | 11.7516 | 11.8697 | 12.0157 | 12.2096 | 12.3935 | 12.7147 | 13.5226 | 13.9572 | 13.6402 | 14.6216 | 14.7985 | 14.9256 | 15.5247 | 15.6223 | 15.6223 | 15.6223 | 15.6223 | 15.6223 | 15.6223 | 15.6223 | 15.6223 | 15.6223 | 15.6223 | 15.6223 | 15.6223 | 15.6223 | 15.6223 | 15.6223 | 15.6223 | 30% | 3309.3057 | 11.6614 | 12.724 | 12.834 | 13.2138 | 13.2046 | 13.2881 | 13.6147 | 14.553 | 14.9403 | 14.5737 | 15.5862 | 15.1611 | 15.5436 | 15.8193 | 15.706 | 15.706 | 15.706 | 15.706 | 15.706 | 15.706 | 15.706 | 15.706 | 15.706 | 15.706 | 15.706 | 15.706 | 15.706 | 15.706 | 15.706 | 15.706
25% | 3537.8514 | 8.8647 | 9.793 | 9.8914 | 10.0131 | 10.1747 | 10.3279 | 10.5956 | 11.2688 | 11.631 | 11.3668 | 12.1847 | 12.332 | 12.438 | 12.9373 | 13.0185 | 13.0185 | 13.0185 | 13.0185 | 13.0185 | 13.0185 | 13.0185 | 13.0185 | 13.0185 | 13.0185 | 13.0185 | 13.0185 | 13.0185 | 13.0185 | 13.0185 | 13.0185 | 25% | 3537.8514 | 9.7178 | 10.6033 | 10.695 | 11.0115 | 11.0038 | 11.0734 | 11.3456 | 12.1275 | 12.4502 | 12.1448 | 12.9885 | 12.6343 | 12.953 | 13.1827 | 13.0884 | 13.0884 | 13.0884 | 13.0884 | 13.0884 | 13.0884 | 13.0884 | 13.0884 | 13.0884 | 13.0884 | 13.0884 | 13.0884 | 13.0884 | 13.0884 | 13.0884 | 13.0884
20% | 3731.0305 | 7.0917 | 7.8344 | 7.9131 | 8.0105 | 8.1398 | 8.2623 | 8.4765 | 9.0151 | 9.3048 | 9.0934 | 9.7477 | 9.8656 | 9.9504 | 10.3498 | 10.4148 | 10.4148 | 10.4148 | 10.4148 | 10.4148 | 10.4148 | 10.4148 | 10.4148 | 10.4148 | 10.4148 | 10.4148 | 10.4148 | 10.4148 | 10.4148 | 10.4148 | 10.4148 | 20% | 3731.0305 | 7.7743 | 8.4827 | 8.556 | 8.8092 | 8.803 | 8.8587 | 9.0764 | 9.702 | 9.9602 | 9.7158 | 10.3908 | 10.1074 | 10.3624 | 10.5462 | 10.4707 | 10.4707 | 10.4707 | 10.4707 | 10.4707 | 10.4707 | 10.4707 | 10.4707 | 10.4707 | 10.4707 | 10.4707 | 10.4707 | 10.4707 | 10.4707 | 10.4707 | 10.4707
15% | 3910.2412 | 5.3188 | 5.8758 | 5.9349 | 6.0079 | 6.1048 | 6.1967 | 6.3573 | 6.7613 | 6.9786 | 6.8201 | 7.3108 | 7.3992 | 7.4628 | 7.7624 | 7.8111 | 7.8111 | 7.8111 | 7.8111 | 7.8111 | 7.8111 | 7.8111 | 7.8111 | 7.8111 | 7.8111 | 7.8111 | 7.8111 | 7.8111 | 7.8111 | 7.8111 | 7.8111 | 15% | 3910.2412 | 5.8307 | 6.362 | 6.417 | 6.6069 | 6.6023 | 6.644 | 6.8073 | 7.2765 | 7.4701 | 7.2869 | 7.7931 | 7.5806 | 7.7718 | 7.9096 | 7.853 | 7.853 | 7.853 | 7.853 | 7.853 | 7.853 | 7.853 | 7.853 | 7.853 | 7.853 | 7.853 | 7.853 | 7.853 | 7.853 | 7.853 | 7.853
10% | 4075.1864 | 3.5459 | 3.9172 | 3.9566 | 4.0052 | 4.0699 | 4.1312 | 4.2382 | 4.5075 | 4.6524 | 4.5467 | 4.8739 | 4.9328 | 4.9752 | 5.1749 | 5.2074 | 5.2074 | 5.2074 | 5.2074 | 5.2074 | 5.2074 | 5.2074 | 5.2074 | 5.2074 | 5.2074 | 5.2074 | 5.2074 | 5.2074 | 5.2074 | 5.2074 | 5.2074 | 10% | 4075.1864 | 3.8871 | 4.2413 | 4.278 | 4.4046 | 4.4015 | 4.4294 | 4.5382 | 4.851 | 4.9801 | 4.8579 | 5.1954 | 5.0537 | 5.1812 | 5.2731 | 5.2353 | 5.2353 | 5.2353 | 5.2353 | 5.2353 | 5.2353 | 5.2353 | 5.2353 | 5.2353 | 5.2353 | 5.2353 | 5.2353 | 5.2353 | 5.2353 | 5.2353 | 5.2353
5% | 4251.7223 | 1.7729 | 1.9586 | 1.9783 | 2.0026 | 2.0349 | 2.0656 | 2.1191 | 2.2538 | 2.3262 | 2.2734 | 2.4369 | 2.4664 | 2.4876 | 2.5875 | 2.6037 | 2.6037 | 2.6037 | 2.6037 | 2.6037 | 2.6037 | 2.6037 | 2.6037 | 2.6037 | 2.6037 | 2.6037 | 2.6037 | 2.6037 | 2.6037 | 2.6037 | 2.6037 | 5% | 4251.7223 | 1.9436 | 2.1207 | 2.139 | 2.2023 | 2.2008 | 2.2147 | 2.2691 | 2.4255 | 2.49 | 2.429 | 2.5977 | 2.5269 | 2.5906 | 2.6365 | 2.6177 | 2.6177 | 2.6177 | 2.6177 | 2.6177 | 2.6177 | 2.6177 | 2.6177 | 2.6177 | 2.6177 | 2.6177 | 2.6177 | 2.6177 | 2.6177 | 2.6177 | 2.6177
9.992e-14% | 4391.7028 | 3.543e-14 | 3.9141e-14 | 3.9534e-14 | 4.002e-14 | 4.0666e-14 | 4.1279e-14 | 4.2348e-14 | 4.5039e-14 | 4.6487e-14 | 4.5431e-14 | 4.87e-14 | 4.9289e-14 | 4.9712e-14 | 5.1708e-14 | 5.2033e-14 | 5.2033e-14 | 5.2033e-14 | 5.2033e-14 | 5.2033e-14 | 5.2033e-14 | 5.2033e-14 | 5.2033e-14 | 5.2033e-14 | 5.2033e-14 | 5.2033e-14 | 5.2033e-14 | 5.2033e-14 | 5.2033e-14 | 5.2033e-14 | 5.2033e-14 | 9.992e-14% | 4391.7028 | 3.884e-14 | 4.2379e-14 | 4.2746e-14 | 4.4011e-14 | 4.398e-14 | 4.4258e-14 | 4.5346e-14 | 4.8471e-14 | 4.9761e-14 | 4.854e-14 | 5.1913e-14 | 5.0497e-14 | 5.1771e-14 | 5.2689e-14 | 5.2312e-14 | 5.2312e-14 | 5.2312e-14 | 5.2312e-14 | 5.2312e-14 | 5.2312e-14 | 5.2312e-14 | 5.2312e-14 | 5.2312e-14 | 5.2312e-14 | 5.2312e-14 | 5.2312e-14 | 5.2312e-14 | 5.2312e-14 | 5.2312e-14 | 5.2312e-14
Summer Season | [31 empty] | Summer Season
P50 | [31 empty] | P10
% of MD | Summer - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Summer - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 37.2509 | 40.0367 | 40.3167 | 40.1794 | 40.3099 | 40.3635 | 40.5354 | 40.8886 | 41.1859 | 41.3227 | 41.2007 | 41.712 | 41.7931 | 41.6971 | 41.8895 | 41.9995 | 41.9995 | 41.9995 | 41.9995 | 41.9995 | 41.9995 | 41.9995 | 41.9995 | 41.9995 | 41.9995 | 41.9995 | 41.9995 | 41.9995 | 41.9995 | 41.9995 | 100% | 0 | 45.8318 | 48.9452 | 49.0311 | 48.9384 | 48.9623 | 49.1323 | 49.4768 | 50.0836 | 50.3998 | 50.6285 | 50.9747 | 51.4167 | 51.9511 | 52.2312 | 52.1404 | 52.2504 | 52.2504 | 52.2504 | 52.2504 | 52.2504 | 52.2504 | 52.2504 | 52.2504 | 52.2504 | 52.2504 | 52.2504 | 52.2504 | 52.2504 | 52.2504 | 52.2504
99% | 0.37816 | 36.8784 | 39.6364 | 39.9135 | 39.7777 | 39.9068 | 39.9599 | 40.13 | 40.4798 | 40.774 | 40.9094 | 40.7887 | 41.2949 | 41.3751 | 41.2801 | 41.4706 | 41.5795 | 41.5795 | 41.5795 | 41.5795 | 41.5795 | 41.5795 | 41.5795 | 41.5795 | 41.5795 | 41.5795 | 41.5795 | 41.5795 | 41.5795 | 41.5795 | 41.5795 | 99% | 0 | 45.3735 | 48.4557 | 48.5408 | 48.4491 | 48.4726 | 48.6409 | 48.982 | 49.5828 | 49.8958 | 50.1222 | 50.465 | 50.9025 | 51.4316 | 51.7089 | 51.619 | 51.7279 | 51.7279 | 51.7279 | 51.7279 | 51.7279 | 51.7279 | 51.7279 | 51.7279 | 51.7279 | 51.7279 | 51.7279 | 51.7279 | 51.7279 | 51.7279 | 51.7279
98% | 0.37816 | 36.5059 | 39.236 | 39.5103 | 39.3759 | 39.5037 | 39.5563 | 39.7246 | 40.0709 | 40.3621 | 40.4962 | 40.3767 | 40.8777 | 40.9572 | 40.8632 | 41.0517 | 41.1595 | 41.1595 | 41.1595 | 41.1595 | 41.1595 | 41.1595 | 41.1595 | 41.1595 | 41.1595 | 41.1595 | 41.1595 | 41.1595 | 41.1595 | 41.1595 | 41.1595 | 98% | 0 | 44.9152 | 47.9662 | 48.0504 | 47.9597 | 47.983 | 48.1496 | 48.4873 | 49.0819 | 49.3918 | 49.6159 | 49.9552 | 50.3883 | 50.9121 | 51.1866 | 51.0976 | 51.2054 | 51.2054 | 51.2054 | 51.2054 | 51.2054 | 51.2054 | 51.2054 | 51.2054 | 51.2054 | 51.2054 | 51.2054 | 51.2054 | 51.2054 | 51.2054 | 51.2054
97% | 0.37816 | 36.1334 | 38.8356 | 39.1072 | 38.9741 | 39.1006 | 39.1526 | 39.3193 | 39.662 | 39.9503 | 40.083 | 39.9647 | 40.4606 | 40.5393 | 40.4462 | 40.6328 | 40.7395 | 40.7395 | 40.7395 | 40.7395 | 40.7395 | 40.7395 | 40.7395 | 40.7395 | 40.7395 | 40.7395 | 40.7395 | 40.7395 | 40.7395 | 40.7395 | 40.7395 | 97% | 0.37816 | 44.4569 | 47.4768 | 47.5601 | 47.4703 | 47.4934 | 47.6583 | 47.9925 | 48.5811 | 48.8878 | 49.1097 | 49.4455 | 49.8742 | 50.3926 | 50.6643 | 50.5762 | 50.6829 | 50.6829 | 50.6829 | 50.6829 | 50.6829 | 50.6829 | 50.6829 | 50.6829 | 50.6829 | 50.6829 | 50.6829 | 50.6829 | 50.6829 | 50.6829 | 50.6829
95% | 0.75633 | 35.3884 | 38.0349 | 38.3008 | 38.1705 | 38.2944 | 38.3454 | 38.5086 | 38.8442 | 39.1266 | 39.2565 | 39.1407 | 39.6264 | 39.7034 | 39.6123 | 39.7951 | 39.8996 | 39.8996 | 39.8996 | 39.8996 | 39.8996 | 39.8996 | 39.8996 | 39.8996 | 39.8996 | 39.8996 | 39.8996 | 39.8996 | 39.8996 | 39.8996 | 39.8996 | 95% | 0.37816 | 43.5402 | 46.4979 | 46.5795 | 46.4915 | 46.5141 | 46.6757 | 47.003 | 47.5794 | 47.8798 | 48.0971 | 48.426 | 48.8458 | 49.3536 | 49.6196 | 49.5334 | 49.6379 | 49.6379 | 49.6379 | 49.6379 | 49.6379 | 49.6379 | 49.6379 | 49.6379 | 49.6379 | 49.6379 | 49.6379 | 49.6379 | 49.6379 | 49.6379 | 49.6379
90% | 9.0759 | 33.5258 | 36.0331 | 36.285 | 36.1615 | 36.2789 | 36.3272 | 36.4818 | 36.7998 | 37.0673 | 37.1904 | 37.0807 | 37.5408 | 37.6138 | 37.5274 | 37.7006 | 37.7996 | 37.7996 | 37.7996 | 37.7996 | 37.7996 | 37.7996 | 37.7996 | 37.7996 | 37.7996 | 37.7996 | 37.7996 | 37.7996 | 37.7996 | 37.7996 | 37.7996 | 90% | 0.75633 | 41.2486 | 44.0506 | 44.128 | 44.0446 | 44.066 | 44.219 | 44.5291 | 45.0752 | 45.3598 | 45.5657 | 45.8772 | 46.275 | 46.756 | 47.0081 | 46.9264 | 47.0254 | 47.0254 | 47.0254 | 47.0254 | 47.0254 | 47.0254 | 47.0254 | 47.0254 | 47.0254 | 47.0254 | 47.0254 | 47.0254 | 47.0254 | 47.0254 | 47.0254
85% | 40.4636 | 31.6633 | 34.0312 | 34.2692 | 34.1525 | 34.2634 | 34.309 | 34.455 | 34.7554 | 35.008 | 35.1243 | 35.0206 | 35.4552 | 35.5241 | 35.4425 | 35.6061 | 35.6996 | 35.6996 | 35.6996 | 35.6996 | 35.6996 | 35.6996 | 35.6996 | 35.6996 | 35.6996 | 35.6996 | 35.6996 | 35.6996 | 35.6996 | 35.6996 | 35.6996 | 85% | 1.1345 | 38.957 | 41.6034 | 41.6764 | 41.5977 | 41.6179 | 41.7624 | 42.0553 | 42.5711 | 42.8398 | 43.0342 | 43.3285 | 43.7042 | 44.1585 | 44.3965 | 44.3193 | 44.4128 | 44.4128 | 44.4128 | 44.4128 | 44.4128 | 44.4128 | 44.4128 | 44.4128 | 44.4128 | 44.4128 | 44.4128 | 44.4128 | 44.4128 | 44.4128 | 44.4128
80% | 94.5411 | 29.8007 | 32.0294 | 32.2533 | 32.1436 | 32.2479 | 32.2908 | 32.4283 | 32.7109 | 32.9487 | 33.0581 | 32.9606 | 33.3696 | 33.4345 | 33.3577 | 33.5116 | 33.5996 | 33.5996 | 33.5996 | 33.5996 | 33.5996 | 33.5996 | 33.5996 | 33.5996 | 33.5996 | 33.5996 | 33.5996 | 33.5996 | 33.5996 | 33.5996 | 33.5996 | 80% | 2.6471 | 36.6655 | 39.1561 | 39.2249 | 39.1508 | 39.1698 | 39.3058 | 39.5815 | 40.0669 | 40.3198 | 40.5028 | 40.7798 | 41.1333 | 41.5609 | 41.785 | 41.7123 | 41.8003 | 41.8003 | 41.8003 | 41.8003 | 41.8003 | 41.8003 | 41.8003 | 41.8003 | 41.8003 | 41.8003 | 41.8003 | 41.8003 | 41.8003 | 41.8003 | 41.8003
75% | 197.0236 | 27.9382 | 30.0275 | 30.2375 | 30.1346 | 30.2324 | 30.2726 | 30.4015 | 30.6665 | 30.8894 | 30.992 | 30.9005 | 31.284 | 31.3448 | 31.2728 | 31.4172 | 31.4997 | 31.4997 | 31.4997 | 31.4997 | 31.4997 | 31.4997 | 31.4997 | 31.4997 | 31.4997 | 31.4997 | 31.4997 | 31.4997 | 31.4997 | 31.4997 | 31.4997 | 75% | 3.4035 | 34.3739 | 36.7089 | 36.7733 | 36.7038 | 36.7217 | 36.8492 | 37.1076 | 37.5627 | 37.7998 | 37.9714 | 38.231 | 38.5625 | 38.9633 | 39.1734 | 39.1053 | 39.1878 | 39.1878 | 39.1878 | 39.1878 | 39.1878 | 39.1878 | 39.1878 | 39.1878 | 39.1878 | 39.1878 | 39.1878 | 39.1878 | 39.1878 | 39.1878 | 39.1878
70% | 336.9444 | 26.0756 | 28.0257 | 28.2217 | 28.1256 | 28.2169 | 28.2545 | 28.3747 | 28.6221 | 28.8301 | 28.9259 | 28.8405 | 29.1984 | 29.2552 | 29.188 | 29.3227 | 29.3997 | 29.3997 | 29.3997 | 29.3997 | 29.3997 | 29.3997 | 29.3997 | 29.3997 | 29.3997 | 29.3997 | 29.3997 | 29.3997 | 29.3997 | 29.3997 | 29.3997 | 70% | 5.6725 | 32.0823 | 34.2616 | 34.3217 | 34.2569 | 34.2736 | 34.3926 | 34.6338 | 35.0585 | 35.2798 | 35.44 | 35.6823 | 35.9917 | 36.3658 | 36.5618 | 36.4983 | 36.5753 | 36.5753 | 36.5753 | 36.5753 | 36.5753 | 36.5753 | 36.5753 | 36.5753 | 36.5753 | 36.5753 | 36.5753 | 36.5753 | 36.5753 | 36.5753 | 36.5753
65% | 521.4885 | 24.2131 | 26.0239 | 26.2058 | 26.1166 | 26.2014 | 26.2363 | 26.348 | 26.5776 | 26.7708 | 26.8597 | 26.7805 | 27.1128 | 27.1655 | 27.1031 | 27.2282 | 27.2997 | 27.2997 | 27.2997 | 27.2997 | 27.2997 | 27.2997 | 27.2997 | 27.2997 | 27.2997 | 27.2997 | 27.2997 | 27.2997 | 27.2997 | 27.2997 | 27.2997 | 65% | 6.4288 | 29.7907 | 31.8143 | 31.8702 | 31.81 | 31.8255 | 31.936 | 32.1599 | 32.5543 | 32.7599 | 32.9085 | 33.1336 | 33.4208 | 33.7682 | 33.9503 | 33.8913 | 33.9628 | 33.9628 | 33.9628 | 33.9628 | 33.9628 | 33.9628 | 33.9628 | 33.9628 | 33.9628 | 33.9628 | 33.9628 | 33.9628 | 33.9628 | 33.9628 | 33.9628
60% | 812.675 | 22.3505 | 24.022 | 24.19 | 24.1077 | 24.186 | 24.2181 | 24.3212 | 24.5332 | 24.7115 | 24.7936 | 24.7204 | 25.0272 | 25.0758 | 25.0183 | 25.1337 | 25.1997 | 25.1997 | 25.1997 | 25.1997 | 25.1997 | 25.1997 | 25.1997 | 25.1997 | 25.1997 | 25.1997 | 25.1997 | 25.1997 | 25.1997 | 25.1997 | 25.1997 | 60% | 11.3449 | 27.4991 | 29.3671 | 29.4186 | 29.3631 | 29.3774 | 29.4794 | 29.6861 | 30.0502 | 30.2399 | 30.3771 | 30.5848 | 30.85 | 31.1707 | 31.3387 | 31.2842 | 31.3502 | 31.3502 | 31.3502 | 31.3502 | 31.3502 | 31.3502 | 31.3502 | 31.3502 | 31.3502 | 31.3502 | 31.3502 | 31.3502 | 31.3502 | 31.3502 | 31.3502
55% | 1202.1843 | 20.488 | 22.0202 | 22.1742 | 22.0987 | 22.1705 | 22.1999 | 22.2944 | 22.4888 | 22.6522 | 22.7275 | 22.6604 | 22.9416 | 22.9862 | 22.9334 | 23.0392 | 23.0997 | 23.0997 | 23.0997 | 23.0997 | 23.0997 | 23.0997 | 23.0997 | 23.0997 | 23.0997 | 23.0997 | 23.0997 | 23.0997 | 23.0997 | 23.0997 | 23.0997 | 55% | 35.5474 | 25.2075 | 26.9198 | 26.9671 | 26.9161 | 26.9292 | 27.0227 | 27.2122 | 27.546 | 27.7199 | 27.8457 | 28.0361 | 28.2792 | 28.5731 | 28.7272 | 28.6772 | 28.7377 | 28.7377 | 28.7377 | 28.7377 | 28.7377 | 28.7377 | 28.7377 | 28.7377 | 28.7377 | 28.7377 | 28.7377 | 28.7377 | 28.7377 | 28.7377 | 28.7377
50% | 1686.2345 | 18.6255 | 20.0184 | 20.1583 | 20.0897 | 20.155 | 20.1818 | 20.2677 | 20.4443 | 20.5929 | 20.6613 | 20.6004 | 20.856 | 20.8965 | 20.8486 | 20.9448 | 20.9998 | 20.9998 | 20.9998 | 20.9998 | 20.9998 | 20.9998 | 20.9998 | 20.9998 | 20.9998 | 20.9998 | 20.9998 | 20.9998 | 20.9998 | 20.9998 | 20.9998 | 50% | 95.2974 | 22.9159 | 24.4726 | 24.5155 | 24.4692 | 24.4811 | 24.5661 | 24.7384 | 25.0418 | 25.1999 | 25.3143 | 25.4873 | 25.7083 | 25.9756 | 26.1156 | 26.0702 | 26.1252 | 26.1252 | 26.1252 | 26.1252 | 26.1252 | 26.1252 | 26.1252 | 26.1252 | 26.1252 | 26.1252 | 26.1252 | 26.1252 | 26.1252 | 26.1252 | 26.1252
45% | 2129.0649 | 16.7629 | 18.0165 | 18.1425 | 18.0808 | 18.1395 | 18.1636 | 18.2409 | 18.3999 | 18.5336 | 18.5952 | 18.5403 | 18.7704 | 18.8069 | 18.7637 | 18.8503 | 18.8998 | 18.8998 | 18.8998 | 18.8998 | 18.8998 | 18.8998 | 18.8998 | 18.8998 | 18.8998 | 18.8998 | 18.8998 | 18.8998 | 18.8998 | 18.8998 | 18.8998 | 45% | 208.7467 | 20.6243 | 22.0253 | 22.064 | 22.0223 | 22.033 | 22.1095 | 22.2646 | 22.5376 | 22.6799 | 22.7828 | 22.9386 | 23.1375 | 23.378 | 23.504 | 23.4632 | 23.5127 | 23.5127 | 23.5127 | 23.5127 | 23.5127 | 23.5127 | 23.5127 | 23.5127 | 23.5127 | 23.5127 | 23.5127 | 23.5127 | 23.5127 | 23.5127 | 23.5127
40% | 2484.5393 | 14.9004 | 16.0147 | 16.1267 | 16.0718 | 16.124 | 16.1454 | 16.2141 | 16.3555 | 16.4743 | 16.5291 | 16.4803 | 16.6848 | 16.7172 | 16.6788 | 16.7558 | 16.7998 | 16.7998 | 16.7998 | 16.7998 | 16.7998 | 16.7998 | 16.7998 | 16.7998 | 16.7998 | 16.7998 | 16.7998 | 16.7998 | 16.7998 | 16.7998 | 16.7998 | 40% | 380.4333 | 18.3327 | 19.5781 | 19.6124 | 19.5754 | 19.5849 | 19.6529 | 19.7907 | 20.0334 | 20.1599 | 20.2514 | 20.3899 | 20.5667 | 20.7804 | 20.8925 | 20.8562 | 20.9002 | 20.9002 | 20.9002 | 20.9002 | 20.9002 | 20.9002 | 20.9002 | 20.9002 | 20.9002 | 20.9002 | 20.9002 | 20.9002 | 20.9002 | 20.9002 | 20.9002
35% | 2808.248 | 13.0378 | 14.0129 | 14.1108 | 14.0628 | 14.1085 | 14.1272 | 14.1874 | 14.311 | 14.415 | 14.4629 | 14.4203 | 14.5992 | 14.6276 | 14.594 | 14.6613 | 14.6998 | 14.6998 | 14.6998 | 14.6998 | 14.6998 | 14.6998 | 14.6998 | 14.6998 | 14.6998 | 14.6998 | 14.6998 | 14.6998 | 14.6998 | 14.6998 | 14.6998 | 35% | 696.5786 | 16.0411 | 17.1308 | 17.1609 | 17.1285 | 17.1368 | 17.1963 | 17.3169 | 17.5293 | 17.6399 | 17.72 | 17.8411 | 17.9958 | 18.1829 | 18.2809 | 18.2491 | 18.2876 | 18.2876 | 18.2876 | 18.2876 | 18.2876 | 18.2876 | 18.2876 | 18.2876 | 18.2876 | 18.2876 | 18.2876 | 18.2876 | 18.2876 | 18.2876 | 18.2876
30% | 3095.6528 | 11.1753 | 12.011 | 12.095 | 12.0538 | 12.093 | 12.1091 | 12.1606 | 12.2666 | 12.3558 | 12.3968 | 12.3602 | 12.5136 | 12.5379 | 12.5091 | 12.5669 | 12.5999 | 12.5999 | 12.5999 | 12.5999 | 12.5999 | 12.5999 | 12.5999 | 12.5999 | 12.5999 | 12.5999 | 12.5999 | 12.5999 | 12.5999 | 12.5999 | 12.5999 | 30% | 1260.7997 | 13.7495 | 14.6835 | 14.7093 | 14.6815 | 14.6887 | 14.7397 | 14.843 | 15.0251 | 15.1199 | 15.1886 | 15.2924 | 15.425 | 15.5853 | 15.6694 | 15.6421 | 15.6751 | 15.6751 | 15.6751 | 15.6751 | 15.6751 | 15.6751 | 15.6751 | 15.6751 | 15.6751 | 15.6751 | 15.6751 | 15.6751 | 15.6751 | 15.6751 | 15.6751
25% | 3358.8552 | 9.3127 | 10.0092 | 10.0792 | 10.0449 | 10.0775 | 10.0909 | 10.1338 | 10.2222 | 10.2965 | 10.3307 | 10.3002 | 10.428 | 10.4483 | 10.4243 | 10.4724 | 10.4999 | 10.4999 | 10.4999 | 10.4999 | 10.4999 | 10.4999 | 10.4999 | 10.4999 | 10.4999 | 10.4999 | 10.4999 | 10.4999 | 10.4999 | 10.4999 | 10.4999 | 25% | 1965.3198 | 11.458 | 12.2363 | 12.2578 | 12.2346 | 12.2406 | 12.2831 | 12.3692 | 12.5209 | 12.5999 | 12.6571 | 12.7437 | 12.8542 | 12.9878 | 13.0578 | 13.0351 | 13.0626 | 13.0626 | 13.0626 | 13.0626 | 13.0626 | 13.0626 | 13.0626 | 13.0626 | 13.0626 | 13.0626 | 13.0626 | 13.0626 | 13.0626 | 13.0626 | 13.0626
20% | 3588.7791 | 7.4502 | 8.0073 | 8.0633 | 8.0359 | 8.062 | 8.0727 | 8.1071 | 8.1777 | 8.2372 | 8.2645 | 8.2401 | 8.3424 | 8.3586 | 8.3394 | 8.3779 | 8.3999 | 8.3999 | 8.3999 | 8.3999 | 8.3999 | 8.3999 | 8.3999 | 8.3999 | 8.3999 | 8.3999 | 8.3999 | 8.3999 | 8.3999 | 8.3999 | 8.3999 | 20% | 2490.2118 | 9.1664 | 9.789 | 9.8062 | 9.7877 | 9.7925 | 9.8265 | 9.8954 | 10.0167 | 10.08 | 10.1257 | 10.1949 | 10.2833 | 10.3902 | 10.4462 | 10.4281 | 10.4501 | 10.4501 | 10.4501 | 10.4501 | 10.4501 | 10.4501 | 10.4501 | 10.4501 | 10.4501 | 10.4501 | 10.4501 | 10.4501 | 10.4501 | 10.4501 | 10.4501
15% | 3802.4419 | 5.5876 | 6.0055 | 6.0475 | 6.0269 | 6.0465 | 6.0545 | 6.0803 | 6.1333 | 6.1779 | 6.1984 | 6.1801 | 6.2568 | 6.269 | 6.2546 | 6.2834 | 6.2999 | 6.2999 | 6.2999 | 6.2999 | 6.2999 | 6.2999 | 6.2999 | 6.2999 | 6.2999 | 6.2999 | 6.2999 | 6.2999 | 6.2999 | 6.2999 | 6.2999 | 15% | 2997.7083 | 6.8748 | 7.3418 | 7.3547 | 7.3408 | 7.3443 | 7.3698 | 7.4215 | 7.5125 | 7.56 | 7.5943 | 7.6462 | 7.7125 | 7.7927 | 7.8347 | 7.8211 | 7.8376 | 7.8376 | 7.8376 | 7.8376 | 7.8376 | 7.8376 | 7.8376 | 7.8376 | 7.8376 | 7.8376 | 7.8376 | 7.8376 | 7.8376 | 7.8376 | 7.8376
10% | 4024.8025 | 3.7251 | 4.0037 | 4.0317 | 4.0179 | 4.031 | 4.0364 | 4.0535 | 4.0889 | 4.1186 | 4.1323 | 4.1201 | 4.1712 | 4.1793 | 4.1697 | 4.189 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 10% | 3491.5908 | 4.5832 | 4.8945 | 4.9031 | 4.8938 | 4.8962 | 4.9132 | 4.9477 | 5.0084 | 5.04 | 5.0629 | 5.0975 | 5.1417 | 5.1951 | 5.2231 | 5.214 | 5.225 | 5.225 | 5.225 | 5.225 | 5.225 | 5.225 | 5.225 | 5.225 | 5.225 | 5.225 | 5.225 | 5.225 | 5.225 | 5.225 | 5.225
5% | 4239.978 | 1.8625 | 2.0018 | 2.0158 | 2.009 | 2.0155 | 2.0182 | 2.0268 | 2.0444 | 2.0593 | 2.0661 | 2.06 | 2.0856 | 2.0897 | 2.0849 | 2.0945 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 5% | 3955.9766 | 2.2916 | 2.4473 | 2.4516 | 2.4469 | 2.4481 | 2.4566 | 2.4738 | 2.5042 | 2.52 | 2.5314 | 2.5487 | 2.5708 | 2.5976 | 2.6116 | 2.607 | 2.6125 | 2.6125 | 2.6125 | 2.6125 | 2.6125 | 2.6125 | 2.6125 | 2.6125 | 2.6125 | 2.6125 | 2.6125 | 2.6125 | 2.6125 | 2.6125 | 2.6125
9.992e-14% | 4391.6218 | 3.7221e-14 | 4.0005e-14 | 4.0284e-14 | 4.0147e-14 | 4.0278e-14 | 4.0331e-14 | 4.0503e-14 | 4.0856e-14 | 4.1153e-14 | 4.129e-14 | 4.1168e-14 | 4.1679e-14 | 4.176e-14 | 4.1664e-14 | 4.1856e-14 | 4.1966e-14 | 4.1966e-14 | 4.1966e-14 | 4.1966e-14 | 4.1966e-14 | 4.1966e-14 | 4.1966e-14 | 4.1966e-14 | 4.1966e-14 | 4.1966e-14 | 4.1966e-14 | 4.1966e-14 | 4.1966e-14 | 4.1966e-14 | 4.1966e-14 | 9.992e-14% | 4391.6218 | 4.5795e-14 | 4.8906e-14 | 4.8992e-14 | 4.8899e-14 | 4.8923e-14 | 4.9093e-14 | 4.9437e-14 | 5.0044e-14 | 5.0359e-14 | 5.0588e-14 | 5.0934e-14 | 5.1376e-14 | 5.191e-14 | 5.2189e-14 | 5.2099e-14 | 5.2209e-14 | 5.2209e-14 | 5.2209e-14 | 5.2209e-14 | 5.2209e-14 | 5.2209e-14 | 5.2209e-14 | 5.2209e-14 | 5.2209e-14 | 5.2209e-14 | 5.2209e-14 | 5.2209e-14 | 5.2209e-14 | 5.2209e-14 | 5.2209e-14
Option 8
Winter Season | [31 empty] | Winter Season
P50 | [31 empty] | P10
% of MD | Winter - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Winter - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 35.4586 | 39.1719 | 39.5657 | 40.0525 | 40.6988 | 41.3115 | 42.3823 | 45.0754 | 46.5239 | 45.4672 | 48.7387 | 49.3282 | 49.7519 | 51.7491 | 52.0742 | 52.0742 | 52.0742 | 52.0742 | 52.0742 | 52.0742 | 52.0742 | 52.0742 | 52.0742 | 52.0742 | 52.0742 | 52.0742 | 52.0742 | 52.0742 | 52.0742 | 52.0742 | 100% | 0 | 38.8714 | 42.4133 | 42.7801 | 44.046 | 44.0152 | 44.2935 | 45.3822 | 48.5101 | 49.8009 | 48.5791 | 51.9542 | 50.5371 | 51.8122 | 52.731 | 52.3535 | 52.3535 | 52.3535 | 52.3535 | 52.3535 | 52.3535 | 52.3535 | 52.3535 | 52.3535 | 52.3535 | 52.3535 | 52.3535 | 52.3535 | 52.3535 | 52.3535 | 52.3535
99% | 0.2972 | 35.104 | 38.7802 | 39.17 | 39.652 | 40.2918 | 40.8984 | 41.9585 | 44.6246 | 46.0587 | 45.0125 | 48.2513 | 48.8349 | 49.2544 | 51.2316 | 51.5535 | 51.5535 | 51.5535 | 51.5535 | 51.5535 | 51.5535 | 51.5535 | 51.5535 | 51.5535 | 51.5535 | 51.5535 | 51.5535 | 51.5535 | 51.5535 | 51.5535 | 51.5535 | 99% | 0.2972 | 38.4827 | 41.9892 | 42.3523 | 43.6056 | 43.575 | 43.8506 | 44.9284 | 48.025 | 49.3029 | 48.0933 | 51.4346 | 50.0317 | 51.294 | 52.2037 | 51.83 | 51.83 | 51.83 | 51.83 | 51.83 | 51.83 | 51.83 | 51.83 | 51.83 | 51.83 | 51.83 | 51.83 | 51.83 | 51.83 | 51.83 | 51.83
98% | 0.2972 | 34.7495 | 38.3885 | 38.7744 | 39.2514 | 39.8848 | 40.4853 | 41.5347 | 44.1739 | 45.5935 | 44.5578 | 47.764 | 48.3416 | 48.7568 | 50.7141 | 51.0327 | 51.0327 | 51.0327 | 51.0327 | 51.0327 | 51.0327 | 51.0327 | 51.0327 | 51.0327 | 51.0327 | 51.0327 | 51.0327 | 51.0327 | 51.0327 | 51.0327 | 51.0327 | 98% | 0.2972 | 38.0939 | 41.5651 | 41.9245 | 43.1651 | 43.1349 | 43.4077 | 44.4746 | 47.5399 | 48.8049 | 47.6075 | 50.9151 | 49.5264 | 50.7759 | 51.6764 | 51.3064 | 51.3064 | 51.3064 | 51.3064 | 51.3064 | 51.3064 | 51.3064 | 51.3064 | 51.3064 | 51.3064 | 51.3064 | 51.3064 | 51.3064 | 51.3064 | 51.3064 | 51.3064
97% | 0.2972 | 34.3949 | 37.9968 | 38.3787 | 38.8509 | 39.4778 | 40.0722 | 41.1108 | 43.7231 | 45.1282 | 44.1032 | 47.2766 | 47.8483 | 48.2593 | 50.1966 | 50.512 | 50.512 | 50.512 | 50.512 | 50.512 | 50.512 | 50.512 | 50.512 | 50.512 | 50.512 | 50.512 | 50.512 | 50.512 | 50.512 | 50.512 | 50.512 | 97% | 0.2972 | 37.7052 | 41.1409 | 41.4967 | 42.7246 | 42.6947 | 42.9647 | 44.0208 | 47.0548 | 48.3068 | 47.1217 | 50.3955 | 49.021 | 50.2578 | 51.1491 | 50.7829 | 50.7829 | 50.7829 | 50.7829 | 50.7829 | 50.7829 | 50.7829 | 50.7829 | 50.7829 | 50.7829 | 50.7829 | 50.7829 | 50.7829 | 50.7829 | 50.7829 | 50.7829
95% | 1.486 | 33.6857 | 37.2134 | 37.5874 | 38.0499 | 38.6639 | 39.2459 | 40.2632 | 42.8216 | 44.1977 | 43.1938 | 46.3018 | 46.8618 | 47.2643 | 49.1617 | 49.4705 | 49.4705 | 49.4705 | 49.4705 | 49.4705 | 49.4705 | 49.4705 | 49.4705 | 49.4705 | 49.4705 | 49.4705 | 49.4705 | 49.4705 | 49.4705 | 49.4705 | 49.4705 | 95% | 1.486 | 36.9278 | 40.2927 | 40.6411 | 41.8437 | 41.8144 | 42.0789 | 43.1131 | 46.0846 | 47.3108 | 46.1501 | 49.3565 | 48.0103 | 49.2216 | 50.0944 | 49.7358 | 49.7358 | 49.7358 | 49.7358 | 49.7358 | 49.7358 | 49.7358 | 49.7358 | 49.7358 | 49.7358 | 49.7358 | 49.7358 | 49.7358 | 49.7358 | 49.7358 | 49.7358
90% | 8.6188 | 31.9128 | 35.2548 | 35.6091 | 36.0472 | 36.6289 | 37.1804 | 38.1441 | 40.5679 | 41.8715 | 40.9205 | 43.8649 | 44.3954 | 44.7767 | 46.5742 | 46.8668 | 46.8668 | 46.8668 | 46.8668 | 46.8668 | 46.8668 | 46.8668 | 46.8668 | 46.8668 | 46.8668 | 46.8668 | 46.8668 | 46.8668 | 46.8668 | 46.8668 | 46.8668 | 90% | 8.6188 | 34.9842 | 38.172 | 38.5021 | 39.6414 | 39.6137 | 39.8642 | 40.844 | 43.6591 | 44.8208 | 43.7212 | 46.7587 | 45.4834 | 46.6309 | 47.4579 | 47.1181 | 47.1181 | 47.1181 | 47.1181 | 47.1181 | 47.1181 | 47.1181 | 47.1181 | 47.1181 | 47.1181 | 47.1181 | 47.1181 | 47.1181 | 47.1181 | 47.1181 | 47.1181
85% | 40.1218 | 30.1398 | 33.2962 | 33.6308 | 34.0446 | 34.594 | 35.1148 | 36.025 | 38.3141 | 39.5453 | 38.6471 | 41.4279 | 41.9289 | 42.2891 | 43.9867 | 44.2631 | 44.2631 | 44.2631 | 44.2631 | 44.2631 | 44.2631 | 44.2631 | 44.2631 | 44.2631 | 44.2631 | 44.2631 | 44.2631 | 44.2631 | 44.2631 | 44.2631 | 44.2631 | 85% | 40.1218 | 33.0407 | 36.0513 | 36.3631 | 37.4391 | 37.4129 | 37.6495 | 38.5749 | 41.2336 | 42.3307 | 41.2922 | 44.161 | 42.9565 | 44.0403 | 44.8213 | 44.5005 | 44.5005 | 44.5005 | 44.5005 | 44.5005 | 44.5005 | 44.5005 | 44.5005 | 44.5005 | 44.5005 | 44.5005 | 44.5005 | 44.5005 | 44.5005 | 44.5005 | 44.5005
80% | 93.0231 | 28.3669 | 31.3376 | 31.6526 | 32.042 | 32.559 | 33.0492 | 33.9058 | 36.0603 | 37.2191 | 36.3737 | 38.991 | 39.4625 | 39.8015 | 41.3993 | 41.6594 | 41.6594 | 41.6594 | 41.6594 | 41.6594 | 41.6594 | 41.6594 | 41.6594 | 41.6594 | 41.6594 | 41.6594 | 41.6594 | 41.6594 | 41.6594 | 41.6594 | 41.6594 | 80% | 93.0231 | 31.0971 | 33.9307 | 34.2241 | 35.2368 | 35.2121 | 35.4348 | 36.3058 | 38.8081 | 39.8407 | 38.8633 | 41.5633 | 40.4297 | 41.4497 | 42.1848 | 41.8828 | 41.8828 | 41.8828 | 41.8828 | 41.8828 | 41.8828 | 41.8828 | 41.8828 | 41.8828 | 41.8828 | 41.8828 | 41.8828 | 41.8828 | 41.8828 | 41.8828 | 41.8828
75% | 197.0426 | 26.594 | 29.379 | 29.6743 | 30.0394 | 30.5241 | 30.9836 | 31.7867 | 33.8065 | 34.8929 | 34.1004 | 36.554 | 36.9961 | 37.3139 | 38.8118 | 39.0556 | 39.0556 | 39.0556 | 39.0556 | 39.0556 | 39.0556 | 39.0556 | 39.0556 | 39.0556 | 39.0556 | 39.0556 | 39.0556 | 39.0556 | 39.0556 | 39.0556 | 39.0556 | 75% | 197.0426 | 29.1535 | 31.81 | 32.0851 | 33.0345 | 33.0114 | 33.2201 | 34.0367 | 36.3826 | 37.3507 | 36.4343 | 38.9656 | 37.9028 | 38.8591 | 39.5482 | 39.2651 | 39.2651 | 39.2651 | 39.2651 | 39.2651 | 39.2651 | 39.2651 | 39.2651 | 39.2651 | 39.2651 | 39.2651 | 39.2651 | 39.2651 | 39.2651 | 39.2651 | 39.2651
70% | 378.0365 | 24.821 | 27.4204 | 27.696 | 28.0367 | 28.4892 | 28.9181 | 29.6676 | 31.5528 | 32.5668 | 31.827 | 34.1171 | 34.5297 | 34.8263 | 36.2244 | 36.4519 | 36.4519 | 36.4519 | 36.4519 | 36.4519 | 36.4519 | 36.4519 | 36.4519 | 36.4519 | 36.4519 | 36.4519 | 36.4519 | 36.4519 | 36.4519 | 36.4519 | 36.4519 | 70% | 378.0365 | 27.21 | 29.6893 | 29.9461 | 30.8322 | 30.8106 | 31.0055 | 31.7676 | 33.9571 | 34.8606 | 34.0054 | 36.3679 | 35.376 | 36.2685 | 36.9117 | 36.6474 | 36.6474 | 36.6474 | 36.6474 | 36.6474 | 36.6474 | 36.6474 | 36.6474 | 36.6474 | 36.6474 | 36.6474 | 36.6474 | 36.6474 | 36.6474 | 36.6474 | 36.6474
65% | 616.0926 | 23.0481 | 25.4618 | 25.7177 | 26.0341 | 26.4542 | 26.8525 | 27.5485 | 29.299 | 30.2406 | 29.5537 | 31.6802 | 32.0633 | 32.3387 | 33.6369 | 33.8482 | 33.8482 | 33.8482 | 33.8482 | 33.8482 | 33.8482 | 33.8482 | 33.8482 | 33.8482 | 33.8482 | 33.8482 | 33.8482 | 33.8482 | 33.8482 | 33.8482 | 33.8482 | 65% | 616.0926 | 25.2664 | 27.5687 | 27.8071 | 28.6299 | 28.6099 | 28.7908 | 29.4985 | 31.5316 | 32.3706 | 31.5764 | 33.7702 | 32.8491 | 33.6779 | 34.2751 | 34.0298 | 34.0298 | 34.0298 | 34.0298 | 34.0298 | 34.0298 | 34.0298 | 34.0298 | 34.0298 | 34.0298 | 34.0298 | 34.0298 | 34.0298 | 34.0298 | 34.0298 | 34.0298
60% | 934.9866 | 21.2752 | 23.5032 | 23.7394 | 24.0315 | 24.4193 | 24.7869 | 25.4294 | 27.0452 | 27.9144 | 27.2803 | 29.2432 | 29.5969 | 29.8511 | 31.0495 | 31.2445 | 31.2445 | 31.2445 | 31.2445 | 31.2445 | 31.2445 | 31.2445 | 31.2445 | 31.2445 | 31.2445 | 31.2445 | 31.2445 | 31.2445 | 31.2445 | 31.2445 | 31.2445 | 60% | 934.9866 | 23.3228 | 25.448 | 25.6681 | 26.4276 | 26.4091 | 26.5761 | 27.2293 | 29.1061 | 29.8805 | 29.1474 | 31.1725 | 30.3223 | 31.0873 | 31.6386 | 31.4121 | 31.4121 | 31.4121 | 31.4121 | 31.4121 | 31.4121 | 31.4121 | 31.4121 | 31.4121 | 31.4121 | 31.4121 | 31.4121 | 31.4121 | 31.4121 | 31.4121 | 31.4121
55% | 1310.9428 | 19.5022 | 21.5446 | 21.7611 | 22.0289 | 22.3843 | 22.7213 | 23.3103 | 24.7915 | 25.5882 | 25.0069 | 26.8063 | 27.1305 | 27.3635 | 28.462 | 28.6408 | 28.6408 | 28.6408 | 28.6408 | 28.6408 | 28.6408 | 28.6408 | 28.6408 | 28.6408 | 28.6408 | 28.6408 | 28.6408 | 28.6408 | 28.6408 | 28.6408 | 28.6408 | 55% | 1310.9428 | 21.3793 | 23.3273 | 23.5291 | 24.2253 | 24.2083 | 24.3614 | 24.9602 | 26.6806 | 27.3905 | 26.7185 | 28.5748 | 27.7954 | 28.4967 | 29.002 | 28.7944 | 28.7944 | 28.7944 | 28.7944 | 28.7944 | 28.7944 | 28.7944 | 28.7944 | 28.7944 | 28.7944 | 28.7944 | 28.7944 | 28.7944 | 28.7944 | 28.7944 | 28.7944
50% | 1730.2899 | 17.7293 | 19.586 | 19.7828 | 20.0262 | 20.3494 | 20.6558 | 21.1912 | 22.5377 | 23.262 | 22.7336 | 24.3694 | 24.6641 | 24.8759 | 25.8746 | 26.0371 | 26.0371 | 26.0371 | 26.0371 | 26.0371 | 26.0371 | 26.0371 | 26.0371 | 26.0371 | 26.0371 | 26.0371 | 26.0371 | 26.0371 | 26.0371 | 26.0371 | 26.0371 | 50% | 1730.2899 | 19.4357 | 21.2067 | 21.3901 | 22.023 | 22.0076 | 22.1468 | 22.6911 | 24.2551 | 24.9004 | 24.2895 | 25.9771 | 25.2686 | 25.9061 | 26.3655 | 26.1767 | 26.1767 | 26.1767 | 26.1767 | 26.1767 | 26.1767 | 26.1767 | 26.1767 | 26.1767 | 26.1767 | 26.1767 | 26.1767 | 26.1767 | 26.1767 | 26.1767 | 26.1767
45% | 2168.0633 | 15.9564 | 17.6274 | 17.8046 | 18.0236 | 18.3145 | 18.5902 | 19.072 | 20.2839 | 20.9358 | 20.4602 | 21.9324 | 22.1977 | 22.3883 | 23.2871 | 23.4334 | 23.4334 | 23.4334 | 23.4334 | 23.4334 | 23.4334 | 23.4334 | 23.4334 | 23.4334 | 23.4334 | 23.4334 | 23.4334 | 23.4334 | 23.4334 | 23.4334 | 23.4334 | 45% | 2168.0633 | 17.4921 | 19.086 | 19.2511 | 19.8207 | 19.8068 | 19.9321 | 20.422 | 21.8296 | 22.4104 | 21.8606 | 23.3794 | 22.7417 | 23.3155 | 23.7289 | 23.5591 | 23.5591 | 23.5591 | 23.5591 | 23.5591 | 23.5591 | 23.5591 | 23.5591 | 23.5591 | 23.5591 | 23.5591 | 23.5591 | 23.5591 | 23.5591 | 23.5591 | 23.5591
40% | 2609.7004 | 14.1835 | 15.6688 | 15.8263 | 16.021 | 16.2795 | 16.5246 | 16.9529 | 18.0302 | 18.6096 | 18.1869 | 19.4955 | 19.7313 | 19.9008 | 20.6996 | 20.8297 | 20.8297 | 20.8297 | 20.8297 | 20.8297 | 20.8297 | 20.8297 | 20.8297 | 20.8297 | 20.8297 | 20.8297 | 20.8297 | 20.8297 | 20.8297 | 20.8297 | 20.8297 | 40% | 2609.7004 | 15.5485 | 16.9653 | 17.1121 | 17.6184 | 17.6061 | 17.7174 | 18.1529 | 19.404 | 19.9203 | 19.4316 | 20.7817 | 20.2148 | 20.7249 | 21.0924 | 20.9414 | 20.9414 | 20.9414 | 20.9414 | 20.9414 | 20.9414 | 20.9414 | 20.9414 | 20.9414 | 20.9414 | 20.9414 | 20.9414 | 20.9414 | 20.9414 | 20.9414 | 20.9414
35% | 2998.1389 | 12.4105 | 13.7102 | 13.848 | 14.0184 | 14.2446 | 14.459 | 14.8338 | 15.7764 | 16.2834 | 15.9135 | 17.0586 | 17.2649 | 17.4132 | 18.1122 | 18.226 | 18.226 | 18.226 | 18.226 | 18.226 | 18.226 | 18.226 | 18.226 | 18.226 | 18.226 | 18.226 | 18.226 | 18.226 | 18.226 | 18.226 | 18.226 | 35% | 2998.1389 | 13.605 | 14.8447 | 14.973 | 15.4161 | 15.4053 | 15.5027 | 15.8838 | 16.9785 | 17.4303 | 17.0027 | 18.184 | 17.688 | 18.1343 | 18.4558 | 18.3237 | 18.3237 | 18.3237 | 18.3237 | 18.3237 | 18.3237 | 18.3237 | 18.3237 | 18.3237 | 18.3237 | 18.3237 | 18.3237 | 18.3237 | 18.3237 | 18.3237 | 18.3237
30% | 3309.3057 | 10.6376 | 11.7516 | 11.8697 | 12.0157 | 12.2096 | 12.3935 | 12.7147 | 13.5226 | 13.9572 | 13.6402 | 14.6216 | 14.7985 | 14.9256 | 15.5247 | 15.6223 | 15.6223 | 15.6223 | 15.6223 | 15.6223 | 15.6223 | 15.6223 | 15.6223 | 15.6223 | 15.6223 | 15.6223 | 15.6223 | 15.6223 | 15.6223 | 15.6223 | 15.6223 | 30% | 3309.3057 | 11.6614 | 12.724 | 12.834 | 13.2138 | 13.2046 | 13.2881 | 13.6147 | 14.553 | 14.9403 | 14.5737 | 15.5862 | 15.1611 | 15.5436 | 15.8193 | 15.706 | 15.706 | 15.706 | 15.706 | 15.706 | 15.706 | 15.706 | 15.706 | 15.706 | 15.706 | 15.706 | 15.706 | 15.706 | 15.706 | 15.706 | 15.706
25% | 3537.8514 | 8.8647 | 9.793 | 9.8914 | 10.0131 | 10.1747 | 10.3279 | 10.5956 | 11.2688 | 11.631 | 11.3668 | 12.1847 | 12.332 | 12.438 | 12.9373 | 13.0185 | 13.0185 | 13.0185 | 13.0185 | 13.0185 | 13.0185 | 13.0185 | 13.0185 | 13.0185 | 13.0185 | 13.0185 | 13.0185 | 13.0185 | 13.0185 | 13.0185 | 13.0185 | 25% | 3537.8514 | 9.7178 | 10.6033 | 10.695 | 11.0115 | 11.0038 | 11.0734 | 11.3456 | 12.1275 | 12.4502 | 12.1448 | 12.9885 | 12.6343 | 12.953 | 13.1827 | 13.0884 | 13.0884 | 13.0884 | 13.0884 | 13.0884 | 13.0884 | 13.0884 | 13.0884 | 13.0884 | 13.0884 | 13.0884 | 13.0884 | 13.0884 | 13.0884 | 13.0884 | 13.0884
20% | 3731.0305 | 7.0917 | 7.8344 | 7.9131 | 8.0105 | 8.1398 | 8.2623 | 8.4765 | 9.0151 | 9.3048 | 9.0934 | 9.7477 | 9.8656 | 9.9504 | 10.3498 | 10.4148 | 10.4148 | 10.4148 | 10.4148 | 10.4148 | 10.4148 | 10.4148 | 10.4148 | 10.4148 | 10.4148 | 10.4148 | 10.4148 | 10.4148 | 10.4148 | 10.4148 | 10.4148 | 20% | 3731.0305 | 7.7743 | 8.4827 | 8.556 | 8.8092 | 8.803 | 8.8587 | 9.0764 | 9.702 | 9.9602 | 9.7158 | 10.3908 | 10.1074 | 10.3624 | 10.5462 | 10.4707 | 10.4707 | 10.4707 | 10.4707 | 10.4707 | 10.4707 | 10.4707 | 10.4707 | 10.4707 | 10.4707 | 10.4707 | 10.4707 | 10.4707 | 10.4707 | 10.4707 | 10.4707
15% | 3910.2412 | 5.3188 | 5.8758 | 5.9349 | 6.0079 | 6.1048 | 6.1967 | 6.3573 | 6.7613 | 6.9786 | 6.8201 | 7.3108 | 7.3992 | 7.4628 | 7.7624 | 7.8111 | 7.8111 | 7.8111 | 7.8111 | 7.8111 | 7.8111 | 7.8111 | 7.8111 | 7.8111 | 7.8111 | 7.8111 | 7.8111 | 7.8111 | 7.8111 | 7.8111 | 7.8111 | 15% | 3910.2412 | 5.8307 | 6.362 | 6.417 | 6.6069 | 6.6023 | 6.644 | 6.8073 | 7.2765 | 7.4701 | 7.2869 | 7.7931 | 7.5806 | 7.7718 | 7.9096 | 7.853 | 7.853 | 7.853 | 7.853 | 7.853 | 7.853 | 7.853 | 7.853 | 7.853 | 7.853 | 7.853 | 7.853 | 7.853 | 7.853 | 7.853 | 7.853
10% | 4075.1864 | 3.5459 | 3.9172 | 3.9566 | 4.0052 | 4.0699 | 4.1312 | 4.2382 | 4.5075 | 4.6524 | 4.5467 | 4.8739 | 4.9328 | 4.9752 | 5.1749 | 5.2074 | 5.2074 | 5.2074 | 5.2074 | 5.2074 | 5.2074 | 5.2074 | 5.2074 | 5.2074 | 5.2074 | 5.2074 | 5.2074 | 5.2074 | 5.2074 | 5.2074 | 5.2074 | 10% | 4075.1864 | 3.8871 | 4.2413 | 4.278 | 4.4046 | 4.4015 | 4.4294 | 4.5382 | 4.851 | 4.9801 | 4.8579 | 5.1954 | 5.0537 | 5.1812 | 5.2731 | 5.2353 | 5.2353 | 5.2353 | 5.2353 | 5.2353 | 5.2353 | 5.2353 | 5.2353 | 5.2353 | 5.2353 | 5.2353 | 5.2353 | 5.2353 | 5.2353 | 5.2353 | 5.2353
5% | 4251.7223 | 1.7729 | 1.9586 | 1.9783 | 2.0026 | 2.0349 | 2.0656 | 2.1191 | 2.2538 | 2.3262 | 2.2734 | 2.4369 | 2.4664 | 2.4876 | 2.5875 | 2.6037 | 2.6037 | 2.6037 | 2.6037 | 2.6037 | 2.6037 | 2.6037 | 2.6037 | 2.6037 | 2.6037 | 2.6037 | 2.6037 | 2.6037 | 2.6037 | 2.6037 | 2.6037 | 5% | 4251.7223 | 1.9436 | 2.1207 | 2.139 | 2.2023 | 2.2008 | 2.2147 | 2.2691 | 2.4255 | 2.49 | 2.429 | 2.5977 | 2.5269 | 2.5906 | 2.6365 | 2.6177 | 2.6177 | 2.6177 | 2.6177 | 2.6177 | 2.6177 | 2.6177 | 2.6177 | 2.6177 | 2.6177 | 2.6177 | 2.6177 | 2.6177 | 2.6177 | 2.6177 | 2.6177
9.992e-14% | 4391.7028 | 3.543e-14 | 3.9141e-14 | 3.9534e-14 | 4.002e-14 | 4.0666e-14 | 4.1279e-14 | 4.2348e-14 | 4.5039e-14 | 4.6487e-14 | 4.5431e-14 | 4.87e-14 | 4.9289e-14 | 4.9712e-14 | 5.1708e-14 | 5.2033e-14 | 5.2033e-14 | 5.2033e-14 | 5.2033e-14 | 5.2033e-14 | 5.2033e-14 | 5.2033e-14 | 5.2033e-14 | 5.2033e-14 | 5.2033e-14 | 5.2033e-14 | 5.2033e-14 | 5.2033e-14 | 5.2033e-14 | 5.2033e-14 | 5.2033e-14 | 9.992e-14% | 4391.7028 | 3.884e-14 | 4.2379e-14 | 4.2746e-14 | 4.4011e-14 | 4.398e-14 | 4.4258e-14 | 4.5346e-14 | 4.8471e-14 | 4.9761e-14 | 4.854e-14 | 5.1913e-14 | 5.0497e-14 | 5.1771e-14 | 5.2689e-14 | 5.2312e-14 | 5.2312e-14 | 5.2312e-14 | 5.2312e-14 | 5.2312e-14 | 5.2312e-14 | 5.2312e-14 | 5.2312e-14 | 5.2312e-14 | 5.2312e-14 | 5.2312e-14 | 5.2312e-14 | 5.2312e-14 | 5.2312e-14 | 5.2312e-14 | 5.2312e-14
Summer Season | [31 empty] | Summer Season
P50 | [31 empty] | P10
% of MD | Summer - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Summer - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 37.2509 | 40.0367 | 40.3167 | 40.1794 | 40.3099 | 40.3635 | 40.5354 | 40.8886 | 41.1859 | 41.3227 | 41.2007 | 41.712 | 41.7931 | 41.6971 | 41.8895 | 41.9995 | 41.9995 | 41.9995 | 41.9995 | 41.9995 | 41.9995 | 41.9995 | 41.9995 | 41.9995 | 41.9995 | 41.9995 | 41.9995 | 41.9995 | 41.9995 | 41.9995 | 100% | 0 | 45.8318 | 48.9452 | 49.0311 | 48.9384 | 48.9623 | 49.1323 | 49.4768 | 50.0836 | 50.3998 | 50.6285 | 50.9747 | 51.4167 | 51.9511 | 52.2312 | 52.1404 | 52.2504 | 52.2504 | 52.2504 | 52.2504 | 52.2504 | 52.2504 | 52.2504 | 52.2504 | 52.2504 | 52.2504 | 52.2504 | 52.2504 | 52.2504 | 52.2504 | 52.2504
99% | 0.37816 | 36.8784 | 39.6364 | 39.9135 | 39.7777 | 39.9068 | 39.9599 | 40.13 | 40.4798 | 40.774 | 40.9094 | 40.7887 | 41.2949 | 41.3751 | 41.2801 | 41.4706 | 41.5795 | 41.5795 | 41.5795 | 41.5795 | 41.5795 | 41.5795 | 41.5795 | 41.5795 | 41.5795 | 41.5795 | 41.5795 | 41.5795 | 41.5795 | 41.5795 | 41.5795 | 99% | 0 | 45.3735 | 48.4557 | 48.5408 | 48.4491 | 48.4726 | 48.6409 | 48.982 | 49.5828 | 49.8958 | 50.1222 | 50.465 | 50.9025 | 51.4316 | 51.7089 | 51.619 | 51.7279 | 51.7279 | 51.7279 | 51.7279 | 51.7279 | 51.7279 | 51.7279 | 51.7279 | 51.7279 | 51.7279 | 51.7279 | 51.7279 | 51.7279 | 51.7279 | 51.7279
98% | 0.37816 | 36.5059 | 39.236 | 39.5103 | 39.3759 | 39.5037 | 39.5563 | 39.7246 | 40.0709 | 40.3621 | 40.4962 | 40.3767 | 40.8777 | 40.9572 | 40.8632 | 41.0517 | 41.1595 | 41.1595 | 41.1595 | 41.1595 | 41.1595 | 41.1595 | 41.1595 | 41.1595 | 41.1595 | 41.1595 | 41.1595 | 41.1595 | 41.1595 | 41.1595 | 41.1595 | 98% | 0 | 44.9152 | 47.9662 | 48.0504 | 47.9597 | 47.983 | 48.1496 | 48.4873 | 49.0819 | 49.3918 | 49.6159 | 49.9552 | 50.3883 | 50.9121 | 51.1866 | 51.0976 | 51.2054 | 51.2054 | 51.2054 | 51.2054 | 51.2054 | 51.2054 | 51.2054 | 51.2054 | 51.2054 | 51.2054 | 51.2054 | 51.2054 | 51.2054 | 51.2054 | 51.2054
97% | 0.37816 | 36.1334 | 38.8356 | 39.1072 | 38.9741 | 39.1006 | 39.1526 | 39.3193 | 39.662 | 39.9503 | 40.083 | 39.9647 | 40.4606 | 40.5393 | 40.4462 | 40.6328 | 40.7395 | 40.7395 | 40.7395 | 40.7395 | 40.7395 | 40.7395 | 40.7395 | 40.7395 | 40.7395 | 40.7395 | 40.7395 | 40.7395 | 40.7395 | 40.7395 | 40.7395 | 97% | 0.37816 | 44.4569 | 47.4768 | 47.5601 | 47.4703 | 47.4934 | 47.6583 | 47.9925 | 48.5811 | 48.8878 | 49.1097 | 49.4455 | 49.8742 | 50.3926 | 50.6643 | 50.5762 | 50.6829 | 50.6829 | 50.6829 | 50.6829 | 50.6829 | 50.6829 | 50.6829 | 50.6829 | 50.6829 | 50.6829 | 50.6829 | 50.6829 | 50.6829 | 50.6829 | 50.6829
95% | 0.75633 | 35.3884 | 38.0349 | 38.3008 | 38.1705 | 38.2944 | 38.3454 | 38.5086 | 38.8442 | 39.1266 | 39.2565 | 39.1407 | 39.6264 | 39.7034 | 39.6123 | 39.7951 | 39.8996 | 39.8996 | 39.8996 | 39.8996 | 39.8996 | 39.8996 | 39.8996 | 39.8996 | 39.8996 | 39.8996 | 39.8996 | 39.8996 | 39.8996 | 39.8996 | 39.8996 | 95% | 0.37816 | 43.5402 | 46.4979 | 46.5795 | 46.4915 | 46.5141 | 46.6757 | 47.003 | 47.5794 | 47.8798 | 48.0971 | 48.426 | 48.8458 | 49.3536 | 49.6196 | 49.5334 | 49.6379 | 49.6379 | 49.6379 | 49.6379 | 49.6379 | 49.6379 | 49.6379 | 49.6379 | 49.6379 | 49.6379 | 49.6379 | 49.6379 | 49.6379 | 49.6379 | 49.6379
90% | 9.0759 | 33.5258 | 36.0331 | 36.285 | 36.1615 | 36.2789 | 36.3272 | 36.4818 | 36.7998 | 37.0673 | 37.1904 | 37.0807 | 37.5408 | 37.6138 | 37.5274 | 37.7006 | 37.7996 | 37.7996 | 37.7996 | 37.7996 | 37.7996 | 37.7996 | 37.7996 | 37.7996 | 37.7996 | 37.7996 | 37.7996 | 37.7996 | 37.7996 | 37.7996 | 37.7996 | 90% | 0.75633 | 41.2486 | 44.0506 | 44.128 | 44.0446 | 44.066 | 44.219 | 44.5291 | 45.0752 | 45.3598 | 45.5657 | 45.8772 | 46.275 | 46.756 | 47.0081 | 46.9264 | 47.0254 | 47.0254 | 47.0254 | 47.0254 | 47.0254 | 47.0254 | 47.0254 | 47.0254 | 47.0254 | 47.0254 | 47.0254 | 47.0254 | 47.0254 | 47.0254 | 47.0254
85% | 40.4636 | 31.6633 | 34.0312 | 34.2692 | 34.1525 | 34.2634 | 34.309 | 34.455 | 34.7554 | 35.008 | 35.1243 | 35.0206 | 35.4552 | 35.5241 | 35.4425 | 35.6061 | 35.6996 | 35.6996 | 35.6996 | 35.6996 | 35.6996 | 35.6996 | 35.6996 | 35.6996 | 35.6996 | 35.6996 | 35.6996 | 35.6996 | 35.6996 | 35.6996 | 35.6996 | 85% | 1.1345 | 38.957 | 41.6034 | 41.6764 | 41.5977 | 41.6179 | 41.7624 | 42.0553 | 42.5711 | 42.8398 | 43.0342 | 43.3285 | 43.7042 | 44.1585 | 44.3965 | 44.3193 | 44.4128 | 44.4128 | 44.4128 | 44.4128 | 44.4128 | 44.4128 | 44.4128 | 44.4128 | 44.4128 | 44.4128 | 44.4128 | 44.4128 | 44.4128 | 44.4128 | 44.4128
80% | 94.5411 | 29.8007 | 32.0294 | 32.2533 | 32.1436 | 32.2479 | 32.2908 | 32.4283 | 32.7109 | 32.9487 | 33.0581 | 32.9606 | 33.3696 | 33.4345 | 33.3577 | 33.5116 | 33.5996 | 33.5996 | 33.5996 | 33.5996 | 33.5996 | 33.5996 | 33.5996 | 33.5996 | 33.5996 | 33.5996 | 33.5996 | 33.5996 | 33.5996 | 33.5996 | 33.5996 | 80% | 2.6471 | 36.6655 | 39.1561 | 39.2249 | 39.1508 | 39.1698 | 39.3058 | 39.5815 | 40.0669 | 40.3198 | 40.5028 | 40.7798 | 41.1333 | 41.5609 | 41.785 | 41.7123 | 41.8003 | 41.8003 | 41.8003 | 41.8003 | 41.8003 | 41.8003 | 41.8003 | 41.8003 | 41.8003 | 41.8003 | 41.8003 | 41.8003 | 41.8003 | 41.8003 | 41.8003
75% | 197.0236 | 27.9382 | 30.0275 | 30.2375 | 30.1346 | 30.2324 | 30.2726 | 30.4015 | 30.6665 | 30.8894 | 30.992 | 30.9005 | 31.284 | 31.3448 | 31.2728 | 31.4172 | 31.4997 | 31.4997 | 31.4997 | 31.4997 | 31.4997 | 31.4997 | 31.4997 | 31.4997 | 31.4997 | 31.4997 | 31.4997 | 31.4997 | 31.4997 | 31.4997 | 31.4997 | 75% | 3.4035 | 34.3739 | 36.7089 | 36.7733 | 36.7038 | 36.7217 | 36.8492 | 37.1076 | 37.5627 | 37.7998 | 37.9714 | 38.231 | 38.5625 | 38.9633 | 39.1734 | 39.1053 | 39.1878 | 39.1878 | 39.1878 | 39.1878 | 39.1878 | 39.1878 | 39.1878 | 39.1878 | 39.1878 | 39.1878 | 39.1878 | 39.1878 | 39.1878 | 39.1878 | 39.1878
70% | 336.9444 | 26.0756 | 28.0257 | 28.2217 | 28.1256 | 28.2169 | 28.2545 | 28.3747 | 28.6221 | 28.8301 | 28.9259 | 28.8405 | 29.1984 | 29.2552 | 29.188 | 29.3227 | 29.3997 | 29.3997 | 29.3997 | 29.3997 | 29.3997 | 29.3997 | 29.3997 | 29.3997 | 29.3997 | 29.3997 | 29.3997 | 29.3997 | 29.3997 | 29.3997 | 29.3997 | 70% | 5.6725 | 32.0823 | 34.2616 | 34.3217 | 34.2569 | 34.2736 | 34.3926 | 34.6338 | 35.0585 | 35.2798 | 35.44 | 35.6823 | 35.9917 | 36.3658 | 36.5618 | 36.4983 | 36.5753 | 36.5753 | 36.5753 | 36.5753 | 36.5753 | 36.5753 | 36.5753 | 36.5753 | 36.5753 | 36.5753 | 36.5753 | 36.5753 | 36.5753 | 36.5753 | 36.5753
65% | 521.4885 | 24.2131 | 26.0239 | 26.2058 | 26.1166 | 26.2014 | 26.2363 | 26.348 | 26.5776 | 26.7708 | 26.8597 | 26.7805 | 27.1128 | 27.1655 | 27.1031 | 27.2282 | 27.2997 | 27.2997 | 27.2997 | 27.2997 | 27.2997 | 27.2997 | 27.2997 | 27.2997 | 27.2997 | 27.2997 | 27.2997 | 27.2997 | 27.2997 | 27.2997 | 27.2997 | 65% | 6.4288 | 29.7907 | 31.8143 | 31.8702 | 31.81 | 31.8255 | 31.936 | 32.1599 | 32.5543 | 32.7599 | 32.9085 | 33.1336 | 33.4208 | 33.7682 | 33.9503 | 33.8913 | 33.9628 | 33.9628 | 33.9628 | 33.9628 | 33.9628 | 33.9628 | 33.9628 | 33.9628 | 33.9628 | 33.9628 | 33.9628 | 33.9628 | 33.9628 | 33.9628 | 33.9628
60% | 812.675 | 22.3505 | 24.022 | 24.19 | 24.1077 | 24.186 | 24.2181 | 24.3212 | 24.5332 | 24.7115 | 24.7936 | 24.7204 | 25.0272 | 25.0758 | 25.0183 | 25.1337 | 25.1997 | 25.1997 | 25.1997 | 25.1997 | 25.1997 | 25.1997 | 25.1997 | 25.1997 | 25.1997 | 25.1997 | 25.1997 | 25.1997 | 25.1997 | 25.1997 | 25.1997 | 60% | 11.3449 | 27.4991 | 29.3671 | 29.4186 | 29.3631 | 29.3774 | 29.4794 | 29.6861 | 30.0502 | 30.2399 | 30.3771 | 30.5848 | 30.85 | 31.1707 | 31.3387 | 31.2842 | 31.3502 | 31.3502 | 31.3502 | 31.3502 | 31.3502 | 31.3502 | 31.3502 | 31.3502 | 31.3502 | 31.3502 | 31.3502 | 31.3502 | 31.3502 | 31.3502 | 31.3502
55% | 1202.1843 | 20.488 | 22.0202 | 22.1742 | 22.0987 | 22.1705 | 22.1999 | 22.2944 | 22.4888 | 22.6522 | 22.7275 | 22.6604 | 22.9416 | 22.9862 | 22.9334 | 23.0392 | 23.0997 | 23.0997 | 23.0997 | 23.0997 | 23.0997 | 23.0997 | 23.0997 | 23.0997 | 23.0997 | 23.0997 | 23.0997 | 23.0997 | 23.0997 | 23.0997 | 23.0997 | 55% | 35.5474 | 25.2075 | 26.9198 | 26.9671 | 26.9161 | 26.9292 | 27.0227 | 27.2122 | 27.546 | 27.7199 | 27.8457 | 28.0361 | 28.2792 | 28.5731 | 28.7272 | 28.6772 | 28.7377 | 28.7377 | 28.7377 | 28.7377 | 28.7377 | 28.7377 | 28.7377 | 28.7377 | 28.7377 | 28.7377 | 28.7377 | 28.7377 | 28.7377 | 28.7377 | 28.7377
50% | 1686.2345 | 18.6255 | 20.0184 | 20.1583 | 20.0897 | 20.155 | 20.1818 | 20.2677 | 20.4443 | 20.5929 | 20.6613 | 20.6004 | 20.856 | 20.8965 | 20.8486 | 20.9448 | 20.9998 | 20.9998 | 20.9998 | 20.9998 | 20.9998 | 20.9998 | 20.9998 | 20.9998 | 20.9998 | 20.9998 | 20.9998 | 20.9998 | 20.9998 | 20.9998 | 20.9998 | 50% | 95.2974 | 22.9159 | 24.4726 | 24.5155 | 24.4692 | 24.4811 | 24.5661 | 24.7384 | 25.0418 | 25.1999 | 25.3143 | 25.4873 | 25.7083 | 25.9756 | 26.1156 | 26.0702 | 26.1252 | 26.1252 | 26.1252 | 26.1252 | 26.1252 | 26.1252 | 26.1252 | 26.1252 | 26.1252 | 26.1252 | 26.1252 | 26.1252 | 26.1252 | 26.1252 | 26.1252
45% | 2129.0649 | 16.7629 | 18.0165 | 18.1425 | 18.0808 | 18.1395 | 18.1636 | 18.2409 | 18.3999 | 18.5336 | 18.5952 | 18.5403 | 18.7704 | 18.8069 | 18.7637 | 18.8503 | 18.8998 | 18.8998 | 18.8998 | 18.8998 | 18.8998 | 18.8998 | 18.8998 | 18.8998 | 18.8998 | 18.8998 | 18.8998 | 18.8998 | 18.8998 | 18.8998 | 18.8998 | 45% | 208.7467 | 20.6243 | 22.0253 | 22.064 | 22.0223 | 22.033 | 22.1095 | 22.2646 | 22.5376 | 22.6799 | 22.7828 | 22.9386 | 23.1375 | 23.378 | 23.504 | 23.4632 | 23.5127 | 23.5127 | 23.5127 | 23.5127 | 23.5127 | 23.5127 | 23.5127 | 23.5127 | 23.5127 | 23.5127 | 23.5127 | 23.5127 | 23.5127 | 23.5127 | 23.5127
40% | 2484.5393 | 14.9004 | 16.0147 | 16.1267 | 16.0718 | 16.124 | 16.1454 | 16.2141 | 16.3555 | 16.4743 | 16.5291 | 16.4803 | 16.6848 | 16.7172 | 16.6788 | 16.7558 | 16.7998 | 16.7998 | 16.7998 | 16.7998 | 16.7998 | 16.7998 | 16.7998 | 16.7998 | 16.7998 | 16.7998 | 16.7998 | 16.7998 | 16.7998 | 16.7998 | 16.7998 | 40% | 380.4333 | 18.3327 | 19.5781 | 19.6124 | 19.5754 | 19.5849 | 19.6529 | 19.7907 | 20.0334 | 20.1599 | 20.2514 | 20.3899 | 20.5667 | 20.7804 | 20.8925 | 20.8562 | 20.9002 | 20.9002 | 20.9002 | 20.9002 | 20.9002 | 20.9002 | 20.9002 | 20.9002 | 20.9002 | 20.9002 | 20.9002 | 20.9002 | 20.9002 | 20.9002 | 20.9002
35% | 2808.248 | 13.0378 | 14.0129 | 14.1108 | 14.0628 | 14.1085 | 14.1272 | 14.1874 | 14.311 | 14.415 | 14.4629 | 14.4203 | 14.5992 | 14.6276 | 14.594 | 14.6613 | 14.6998 | 14.6998 | 14.6998 | 14.6998 | 14.6998 | 14.6998 | 14.6998 | 14.6998 | 14.6998 | 14.6998 | 14.6998 | 14.6998 | 14.6998 | 14.6998 | 14.6998 | 35% | 696.5786 | 16.0411 | 17.1308 | 17.1609 | 17.1285 | 17.1368 | 17.1963 | 17.3169 | 17.5293 | 17.6399 | 17.72 | 17.8411 | 17.9958 | 18.1829 | 18.2809 | 18.2491 | 18.2876 | 18.2876 | 18.2876 | 18.2876 | 18.2876 | 18.2876 | 18.2876 | 18.2876 | 18.2876 | 18.2876 | 18.2876 | 18.2876 | 18.2876 | 18.2876 | 18.2876
30% | 3095.6528 | 11.1753 | 12.011 | 12.095 | 12.0538 | 12.093 | 12.1091 | 12.1606 | 12.2666 | 12.3558 | 12.3968 | 12.3602 | 12.5136 | 12.5379 | 12.5091 | 12.5669 | 12.5999 | 12.5999 | 12.5999 | 12.5999 | 12.5999 | 12.5999 | 12.5999 | 12.5999 | 12.5999 | 12.5999 | 12.5999 | 12.5999 | 12.5999 | 12.5999 | 12.5999 | 30% | 1260.7997 | 13.7495 | 14.6835 | 14.7093 | 14.6815 | 14.6887 | 14.7397 | 14.843 | 15.0251 | 15.1199 | 15.1886 | 15.2924 | 15.425 | 15.5853 | 15.6694 | 15.6421 | 15.6751 | 15.6751 | 15.6751 | 15.6751 | 15.6751 | 15.6751 | 15.6751 | 15.6751 | 15.6751 | 15.6751 | 15.6751 | 15.6751 | 15.6751 | 15.6751 | 15.6751
25% | 3358.8552 | 9.3127 | 10.0092 | 10.0792 | 10.0449 | 10.0775 | 10.0909 | 10.1338 | 10.2222 | 10.2965 | 10.3307 | 10.3002 | 10.428 | 10.4483 | 10.4243 | 10.4724 | 10.4999 | 10.4999 | 10.4999 | 10.4999 | 10.4999 | 10.4999 | 10.4999 | 10.4999 | 10.4999 | 10.4999 | 10.4999 | 10.4999 | 10.4999 | 10.4999 | 10.4999 | 25% | 1965.3198 | 11.458 | 12.2363 | 12.2578 | 12.2346 | 12.2406 | 12.2831 | 12.3692 | 12.5209 | 12.5999 | 12.6571 | 12.7437 | 12.8542 | 12.9878 | 13.0578 | 13.0351 | 13.0626 | 13.0626 | 13.0626 | 13.0626 | 13.0626 | 13.0626 | 13.0626 | 13.0626 | 13.0626 | 13.0626 | 13.0626 | 13.0626 | 13.0626 | 13.0626 | 13.0626
20% | 3588.7791 | 7.4502 | 8.0073 | 8.0633 | 8.0359 | 8.062 | 8.0727 | 8.1071 | 8.1777 | 8.2372 | 8.2645 | 8.2401 | 8.3424 | 8.3586 | 8.3394 | 8.3779 | 8.3999 | 8.3999 | 8.3999 | 8.3999 | 8.3999 | 8.3999 | 8.3999 | 8.3999 | 8.3999 | 8.3999 | 8.3999 | 8.3999 | 8.3999 | 8.3999 | 8.3999 | 20% | 2490.2118 | 9.1664 | 9.789 | 9.8062 | 9.7877 | 9.7925 | 9.8265 | 9.8954 | 10.0167 | 10.08 | 10.1257 | 10.1949 | 10.2833 | 10.3902 | 10.4462 | 10.4281 | 10.4501 | 10.4501 | 10.4501 | 10.4501 | 10.4501 | 10.4501 | 10.4501 | 10.4501 | 10.4501 | 10.4501 | 10.4501 | 10.4501 | 10.4501 | 10.4501 | 10.4501
15% | 3802.4419 | 5.5876 | 6.0055 | 6.0475 | 6.0269 | 6.0465 | 6.0545 | 6.0803 | 6.1333 | 6.1779 | 6.1984 | 6.1801 | 6.2568 | 6.269 | 6.2546 | 6.2834 | 6.2999 | 6.2999 | 6.2999 | 6.2999 | 6.2999 | 6.2999 | 6.2999 | 6.2999 | 6.2999 | 6.2999 | 6.2999 | 6.2999 | 6.2999 | 6.2999 | 6.2999 | 15% | 2997.7083 | 6.8748 | 7.3418 | 7.3547 | 7.3408 | 7.3443 | 7.3698 | 7.4215 | 7.5125 | 7.56 | 7.5943 | 7.6462 | 7.7125 | 7.7927 | 7.8347 | 7.8211 | 7.8376 | 7.8376 | 7.8376 | 7.8376 | 7.8376 | 7.8376 | 7.8376 | 7.8376 | 7.8376 | 7.8376 | 7.8376 | 7.8376 | 7.8376 | 7.8376 | 7.8376
10% | 4024.8025 | 3.7251 | 4.0037 | 4.0317 | 4.0179 | 4.031 | 4.0364 | 4.0535 | 4.0889 | 4.1186 | 4.1323 | 4.1201 | 4.1712 | 4.1793 | 4.1697 | 4.189 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 10% | 3491.5908 | 4.5832 | 4.8945 | 4.9031 | 4.8938 | 4.8962 | 4.9132 | 4.9477 | 5.0084 | 5.04 | 5.0629 | 5.0975 | 5.1417 | 5.1951 | 5.2231 | 5.214 | 5.225 | 5.225 | 5.225 | 5.225 | 5.225 | 5.225 | 5.225 | 5.225 | 5.225 | 5.225 | 5.225 | 5.225 | 5.225 | 5.225 | 5.225
5% | 4239.978 | 1.8625 | 2.0018 | 2.0158 | 2.009 | 2.0155 | 2.0182 | 2.0268 | 2.0444 | 2.0593 | 2.0661 | 2.06 | 2.0856 | 2.0897 | 2.0849 | 2.0945 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 5% | 3955.9766 | 2.2916 | 2.4473 | 2.4516 | 2.4469 | 2.4481 | 2.4566 | 2.4738 | 2.5042 | 2.52 | 2.5314 | 2.5487 | 2.5708 | 2.5976 | 2.6116 | 2.607 | 2.6125 | 2.6125 | 2.6125 | 2.6125 | 2.6125 | 2.6125 | 2.6125 | 2.6125 | 2.6125 | 2.6125 | 2.6125 | 2.6125 | 2.6125 | 2.6125 | 2.6125
9.992e-14% | 4391.6218 | 3.7221e-14 | 4.0005e-14 | 4.0284e-14 | 4.0147e-14 | 4.0278e-14 | 4.0331e-14 | 4.0503e-14 | 4.0856e-14 | 4.1153e-14 | 4.129e-14 | 4.1168e-14 | 4.1679e-14 | 4.176e-14 | 4.1664e-14 | 4.1856e-14 | 4.1966e-14 | 4.1966e-14 | 4.1966e-14 | 4.1966e-14 | 4.1966e-14 | 4.1966e-14 | 4.1966e-14 | 4.1966e-14 | 4.1966e-14 | 4.1966e-14 | 4.1966e-14 | 4.1966e-14 | 4.1966e-14 | 4.1966e-14 | 4.1966e-14 | 9.992e-14% | 4391.6218 | 4.5795e-14 | 4.8906e-14 | 4.8992e-14 | 4.8899e-14 | 4.8923e-14 | 4.9093e-14 | 4.9437e-14 | 5.0044e-14 | 5.0359e-14 | 5.0588e-14 | 5.0934e-14 | 5.1376e-14 | 5.191e-14 | 5.2189e-14 | 5.2099e-14 | 5.2209e-14 | 5.2209e-14 | 5.2209e-14 | 5.2209e-14 | 5.2209e-14 | 5.2209e-14 | 5.2209e-14 | 5.2209e-14 | 5.2209e-14 | 5.2209e-14 | 5.2209e-14 | 5.2209e-14 | 5.2209e-14 | 5.2209e-14 | 5.2209e-14

## Locational VCR
Base case |  | Energy Usage (CY 2024 kWh) | Energy Usage (CY 2024 %) | Tailored VCR
Dec 24 AER VCR ($/kWh) - Res | 49.23 | 88661416.1819 | 59.86% | 29.4686
Dec 24 AER VCR ($/kWh) - Com | 34.39 | 45585213.1364 | 30.78% | 10.584
Dec 24 AER VCR ($/kWh) - Ind | 33.49 | 5851096.6819 | 3.95% | 1.323
Dec 24 AER VCR ($/kWh) - Agr | 22.25 | 8019086.0298 | 5.414% | 1.2046
|  | 148116812.03 |  | 42.5803 | KW/h
|  |  |  | 42580.277 | MW/h

## E@R N
Option 1 - Do Nothing
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99%
98%
97%
95%
90%
85%
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1 Winter POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 1 Winter POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99
98%
97%
95%
90%
85%
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1 Summer POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 1 Summer POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2 - Replace 3 x 10/13.5 MVA Tx with 3 x 20/33 MVA Tx
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99%
98%
97%
95%
90%
85%
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2 Winter POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 2 Winter POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99
98%
97%
95%
90%
85%
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2 Summer POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 2 Summer POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 - Replace 1 x 10/13.5 MVA Tx with 1 x 20/33 MVA Tx
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99%
98%
97%
95%
90%
85%
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 Winter POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 3 Winter POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99
98%
97%
95%
90%
85%
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 Summer POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 3 Summer POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 - Construct 2x 20/33MVA zone substation in Inverloch
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99%
98%
97%
95%
90%
85%
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 Winter POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 4 Winter POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99
98%
97%
95%
90%
85%
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 Summer POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 4 Summer POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 - Contract network support services to defer network investment
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99%
98%
97%
95%
90%
85%
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 Winter POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 5 Winter POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99
98%
97%
95%
90%
85%
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 Summer POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 5 Summer POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 6 -
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99%
98%
97%
95%
90%
85%
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 6 Winter POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 6 Winter POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99
98%
97%
95%
90%
85%
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 6 Summer POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 6 Summer POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 7 -
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99%
98%
97%
95%
90%
85%
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 7 Winter POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 7 Winter POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99
98%
97%
95%
90%
85%
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 7 Summer POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 7 Summer POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 8 -
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99%
98%
97%
95%
90%
85%
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 8 Winter POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 8 Winter POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99
98%
97%
95%
90%
85%
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 8 Summer POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 8 Summer POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## E@R N-1
Option 1 - Do Nothing
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% |  | 0.85477 | 0.97121 | 1.1152 | 1.3063 | 1.4875 | 1.8041 | 2.6005 | 3.0288 | 2.7163 | 3.6838 | 3.8581 | 3.9834 | 4.574 | 4.6701 | 4.6701 | 4.6701 | 4.6701 | 4.6701 | 4.6701 | 4.6701 | 4.6701 | 4.6701 | 4.6701 | 4.6701 | 4.6701 | 4.6701 | 4.6701 | 4.6701 | 4.6701 |  | 0.76588 | 1.8133 | 1.9218 | 2.2961 | 2.287 | 2.3693 | 2.6912 | 3.6162 | 3.9979 | 3.6366 | 4.6346 | 4.2156 | 4.5926 | 4.8643 | 4.7527 | 4.7527 | 4.7527 | 4.7527 | 4.7527 | 4.7527 | 4.7527 | 4.7527 | 4.7527 | 4.7527 | 4.7527 | 4.7527 | 4.7527 | 4.7527 | 4.7527 | 4.7527
98% |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
97% |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
95% |  | 1.7892 | 2.2386 | 2.7941 | 3.5317 | 4.231 | 5.453 | 8.5265 | 10.1796 | 8.9736 | 12.7072 | 13.3799 | 13.8635 | 16.1428 | 16.5138 | 16.5138 | 16.5138 | 16.5138 | 16.5138 | 16.5138 | 16.5138 | 16.5138 | 16.5138 | 16.5138 | 16.5138 | 16.5138 | 16.5138 | 16.5138 | 16.5138 | 16.5138 |  | 1.4462 | 5.4884 | 5.907 | 7.3517 | 7.3165 | 7.6342 | 8.8767 | 12.4463 | 13.9194 | 12.525 | 16.3768 | 14.7596 | 16.2148 | 17.2634 | 16.8326 | 16.8326 | 16.8326 | 16.8326 | 16.8326 | 16.8326 | 16.8326 | 16.8326 | 16.8326 | 16.8326 | 16.8326 | 16.8326 | 16.8326 | 16.8326 | 16.8326 | 16.8326
90% |  | 2.2571 | 3.9884 | 6.7708 | 11.03 | 15.0726 | 22.1375 | 39.906 | 49.4631 | 42.4909 | 64.076 | 67.965 | 70.7605 | 83.9378 | 86.0827 | 86.0827 | 86.0827 | 86.0827 | 86.0827 | 86.0827 | 86.0827 | 86.0827 | 86.0827 | 86.0827 | 86.0827 | 86.0827 | 86.0827 | 86.0827 | 86.0827 | 86.0827 |  | 1.2574 | 22.3422 | 24.7623 | 33.1144 | 32.9108 | 34.7474 | 41.9304 | 62.5676 | 71.0837 | 63.0226 | 85.2907 | 75.9414 | 84.3539 | 90.4161 | 87.9254 | 87.9254 | 87.9254 | 87.9254 | 87.9254 | 87.9254 | 87.9254 | 87.9254 | 87.9254 | 87.9254 | 87.9254 | 87.9254 | 87.9254 | 87.9254 | 87.9254 | 87.9254
85% |  |  |  |  | 2.1655 | 8.9007 | 31.0571 | 105.2507 | 145.1799 | 116.0504 | 206.2313 | 222.4792 | 234.1587 | 289.2127 | 298.1738 | 298.1738 | 298.1738 | 298.1738 | 298.1738 | 298.1738 | 298.1738 | 298.1738 | 298.1738 | 298.1738 | 298.1738 | 298.1738 | 298.1738 | 298.1738 | 298.1738 | 298.1738 |  |  | 31.8883 | 41.9816 | 76.8759 | 76.0255 | 83.6985 | 113.7089 | 199.9294 | 235.5092 | 201.8302 | 294.8651 | 255.804 | 290.9508 | 316.2783 | 305.8726 | 305.8726 | 305.8726 | 305.8726 | 305.8726 | 305.8726 | 305.8726 | 305.8726 | 305.8726 | 305.8726 | 305.8726 | 305.8726 | 305.8726 | 305.8726 | 305.8726 | 305.8726
80% | [7 empty] | 57.5329 | 120.7337 | 74.6133 | 217.3957 | 243.1208 | 261.6129 | 348.7792 | 362.9672 | 362.9672 | 362.9672 | 362.9672 | 362.9672 | 362.9672 | 362.9672 | 362.9672 | 362.9672 | 362.9672 | 362.9672 | 362.9672 | 362.9672 | 362.9672 | 362.9672 | 362.9672 |  |  |  | 0.8561 | 21.5377 | 20.7169 | 28.6755 | 70.906 | 207.4181 | 263.7511 | 210.4275 | 357.7285 | 295.8836 | 351.5311 | 391.6319 | 375.1566 | 375.1566 | 375.1566 | 375.1566 | 375.1566 | 375.1566 | 375.1566 | 375.1566 | 375.1566 | 375.1566 | 375.1566 | 375.1566 | 375.1566 | 375.1566 | 375.1566 | 375.1566
75% | [8 empty] | 28.0034 | 1.7144 | 173.9745 | 221.4919 | 255.6491 | 416.656 | 442.8629 | 442.8629 | 442.8629 | 442.8629 | 442.8629 | 442.8629 | 442.8629 | 442.8629 | 442.8629 | 442.8629 | 442.8629 | 442.8629 | 442.8629 | 442.8629 | 442.8629 | 442.8629 | [7 empty] | 0.97067 | 155.5446 | 259.5988 | 161.1034 | 433.1866 | 318.9513 | 421.7392 | 495.8103 | 465.3784 | 465.3784 | 465.3784 | 465.3784 | 465.3784 | 465.3784 | 465.3784 | 465.3784 | 465.3784 | 465.3784 | 465.3784 | 465.3784 | 465.3784 | 465.3784 | 465.3784 | 465.3784
70% | [10 empty] | 7.6559 | 29.4651 | 53.6075 | 256.6677 | 299.3259 | 299.3259 | 299.3259 | 299.3259 | 299.3259 | 299.3259 | 299.3259 | 299.3259 | 299.3259 | 299.3259 | 299.3259 | 299.3259 | 299.3259 | 299.3259 | 299.3259 | 299.3259 | [8 empty] | 2.9795 | 56.8461 | 4.1639 | 283.5753 | 116.4036 | 264.9419 | 385.5105 | 335.9752 | 335.9752 | 335.9752 | 335.9752 | 335.9752 | 335.9752 | 335.9752 | 335.9752 | 335.9752 | 335.9752 | 335.9752 | 335.9752 | 335.9752 | 335.9752 | 335.9752 | 335.9752
65% | FY38: 0.7116; FY39: 5.6622; FY40: 5.6622; FY41: 5.6622; FY42: 5.6622; FY43: 5.6622; FY44: 5.6622; FY45: 5.6622; FY46: 5.6622; FY47: 5.6622; FY48: 5.6622; FY49: 5.6622; FY50: 5.6622; FY51: 5.6622; FY52: 5.6622; FY53: 5.6622; FY54: 5.6622 | [11 empty] | 3.2889 |  | 1.3047 | 29.7436 | 13.6273 | 13.6273 | 13.6273 | 13.6273 | 13.6273 | 13.6273 | 13.6273 | 13.6273 | 13.6273 | 13.6273 | 13.6273 | 13.6273 | 13.6273 | 13.6273 | 13.6273 | 13.6273
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 4.8521 | 7.1262 | 10.5732 | 17.8532 | 29.3949 | 59.8472 | 211.6784 | 353.0228 | 244.0934 | 678.8671 | 793.7423 | 884.6991 | 1402.5149 | 1501.096 | 1501.096 | 1501.096 | 1501.096 | 1501.096 | 1501.096 | 1501.096 | 1501.096 | 1501.096 | 1501.096 | 1501.096 | 1501.096 | 1501.096 | 1501.096 | 1501.096 | 1501.096 | E @ R (MWh) | 3.4348 | 60.9169 | 74.6745 | 139.764 | 137.8641 | 155.5536 | 236.6931 | 638.0567 | 895.6592 | 650.1421 | 1464.157 | 1071.1395 | 1421.2727 | 1714.2032 | 1589.4656 | 1589.4656 | 1589.4656 | 1589.4656 | 1589.4656 | 1589.4656 | 1589.4656 | 1589.4656 | 1589.4656 | 1589.4656 | 1589.4656 | 1589.4656 | 1589.4656 | 1589.4656 | 1589.4656 | 1589.4656
Option 1 Winter POE50 W E @ R (MWh) N 1 | 0 | 3.3964 | 4.9884 | 7.4013 | 12.4972 | 20.5764 | 41.893 | 148.1749 | 247.1159 | 170.8654 | 475.207 | 555.6196 | 619.2894 | 981.7605 | 1050.7672 | 1050.7672 | 1050.7672 | 1050.7672 | 1050.7672 | 1050.7672 | 1050.7672 | 1050.7672 | 1050.7672 | 1050.7672 | 1050.7672 | 1050.7672 | 1050.7672 | 1050.7672 | 1050.7672 | 1050.7672 | Option 1 Winter POE10 W E @ R (MWh) N 1 | 1.0304 | 18.2751 | 22.4024 | 41.9292 | 41.3592 | 46.6661 | 71.0079 | 191.417 | 268.6977 | 195.0426 | 439.2471 | 321.3418 | 426.3818 | 514.261 | 476.8397 | 476.8397 | 476.8397 | 476.8397 | 476.8397 | 476.8397 | 476.8397 | 476.8397 | 476.8397 | 476.8397 | 476.8397 | 476.8397 | 476.8397 | 476.8397 | 476.8397 | 476.8397
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | 0.66733 | 1.7156 | 1.8209 | 1.7693 | 1.8184 | 1.8385 | 1.9032 | 2.0361 | 2.1479 | 2.1994 | 2.1535 | 2.3459 | 2.3764 | 2.3403 | 2.4127 | 2.4541 | 2.4541 | 2.4541 | 2.4541 | 2.4541 | 2.4541 | 2.4541 | 2.4541 | 2.4541 | 2.4541 | 2.4541 | 2.4541 | 2.4541 | 2.4541 | 2.4541 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
98% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
97% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 3.5495 | 4.6974 | 4.7291 | 4.6949 | 4.7037 | 4.7664 | 4.8934 | 5.1171 | 5.2337 | 5.318 | 5.4457 | 5.6087 | 5.8057 | 5.909 | 5.8755 | 5.9161 | 5.9161 | 5.9161 | 5.9161 | 5.9161 | 5.9161 | 5.9161 | 5.9161 | 5.9161 | 5.9161 | 5.9161 | 5.9161 | 5.9161 | 5.9161 | 5.9161
95% | 0.17429 | 1.1856 | 1.2873 | 1.2375 | 1.2848 | 1.3043 | 1.3667 | 1.4949 | 1.6028 | 1.6525 | 1.6082 | 1.7938 | 1.8233 | 1.7884 | 1.8583 | 1.8982 | 1.8982 | 1.8982 | 1.8982 | 1.8982 | 1.8982 | 1.8982 | 1.8982 | 1.8982 | 1.8982 | 1.8982 | 1.8982 | 1.8982 | 1.8982 | 1.8982 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
90% | 0.017439 | 14.426 | 16.5803 | 15.5243 | 16.5284 | 16.941 | 18.2632 | 20.9821 | 23.2693 | 24.3221 | 23.3837 | 27.3182 | 27.9422 | 27.2037 | 28.6845 | 29.531 | 29.531 | 29.531 | 29.531 | 29.531 | 29.531 | 29.531 | 29.531 | 29.531 | 29.531 | 29.531 | 29.531 | 29.531 | 29.531 | 29.531 |  | 2.6829 | 3.7719 | 3.802 | 3.7696 | 3.7779 | 3.8374 | 3.9579 | 4.1701 | 4.2807 | 4.3608 | 4.4819 | 4.6365 | 4.8234 | 4.9214 | 4.8896 | 4.9281 | 4.9281 | 4.9281 | 4.9281 | 4.9281 | 4.9281 | 4.9281 | 4.9281 | 4.9281 | 4.9281 | 4.9281 | 4.9281 | 4.9281 | 4.9281 | 4.9281
85% |  | 4.2128 | 7.5535 | 5.7978 | 7.4619 | 8.2047 | 10.815 | 17.2668 | 23.8022 | 27.1443 | 24.1554 | 37.602 | 39.829 | 37.1935 | 42.4782 | 45.4993 | 45.4993 | 45.4993 | 45.4993 | 45.4993 | 45.4993 | 45.4993 | 45.4993 | 45.4993 | 45.4993 | 45.4993 | 45.4993 | 45.4993 | 45.4993 | 45.4993 |  | 1.8163 | 2.8464 | 2.8749 | 2.8442 | 2.8521 | 2.9084 | 3.0224 | 3.2232 | 3.3278 | 3.4035 | 3.518 | 3.6643 | 3.8411 | 3.9338 | 3.9037 | 3.9401 | 3.9401 | 3.9401 | 3.9401 | 3.9401 | 3.9401 | 3.9401 | 3.9401 | 3.9401 | 3.9401 | 3.9401 | 3.9401 | 3.9401 | 3.9401 | 3.9401
80% | [11 empty] | 0.31223 | 0.64989 | 0.26352 | 1.2096 | 2.056 | 2.056 | 2.056 | 2.056 | 2.056 | 2.056 | 2.056 | 2.056 | 2.056 | 2.056 | 2.056 | 2.056 | 2.056 | 2.056 | 2.056 |  | 3.7987 | 7.6839 | 7.7911 | 7.6755 | 7.7053 | 7.9174 | 8.3474 | 9.1046 | 9.4992 | 9.7847 | 10.2167 | 10.7682 | 11.4352 | 11.7847 | 11.6714 | 11.8087 | 11.8087 | 11.8087 | 11.8087 | 11.8087 | 11.8087 | 11.8087 | 11.8087 | 11.8087 | 11.8087 | 11.8087 | 11.8087 | 11.8087 | 11.8087 | 11.8087
75% | [31 empty] | 0.30768 | 1.991 | 2.0414 | 1.9871 | 2.0011 | 2.1007 | 2.3027 | 2.6583 | 2.8437 | 2.9777 | 3.1807 | 3.4397 | 3.753 | 3.9172 | 3.8639 | 3.9284 | 3.9284 | 3.9284 | 3.9284 | 3.9284 | 3.9284 | 3.9284 | 3.9284 | 3.9284 | 3.9284 | 3.9284 | 3.9284 | 3.9284 | 3.9284 | 3.9284
70% | [32 empty] | 0.92015 | 1.0045 | 0.91371 | 0.93666 | 1.1084 | 1.4984 | 2.3195 | 2.8134 | 3.1894 | 3.7589 | 4.486 | 5.3652 | 5.8259 | 5.6765 | 5.8575 | 5.8575 | 5.8575 | 5.8575 | 5.8575 | 5.8575 | 5.8575 | 5.8575 | 5.8575 | 5.8575 | 5.8575 | 5.8575 | 5.8575 | 5.8575 | 5.8575
65% | [40 empty] | 0.0029263 | 0.021684 | 0.070373 | 0.16537 | 0.23056 | 0.20828 | 0.23542 | 0.23542 | 0.23542 | 0.23542 | 0.23542 | 0.23542 | 0.23542 | 0.23542 | 0.23542 | 0.23542 | 0.23542 | 0.23542 | 0.23542 | 0.23542 | 0.23542
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0.85046 | 21.3245 | 26.9695 | 24.0856 | 26.8226 | 28.0056 | 32.0245 | 41.3621 | 50.314 | 54.7652 | 50.7878 | 68.6784 | 71.8945 | 68.1016 | 75.8769 | 80.6243 | 80.6243 | 80.6243 | 80.6243 | 80.6243 | 80.6243 | 80.6243 | 80.6243 | 80.6243 | 80.6243 | 80.6243 | 80.6243 | 80.6243 | 80.6243 | 80.6243 | E @ R (MWh) | 12.1549 | 21.6917 | 22.0205 | 21.6662 | 21.7569 | 22.4122 | 23.782 | 26.327 | 27.7185 | 28.7467 | 30.3173 | 32.3469 | 34.837 | 36.1573 | 35.7281 | 36.2482 | 36.2482 | 36.2482 | 36.2482 | 36.2482 | 36.2482 | 36.2482 | 36.2482 | 36.2482 | 36.2482 | 36.2482 | 36.2482 | 36.2482 | 36.2482 | 36.2482
Option 1 Summer POE50 W E @ R (MWh) N 1 | 0.59532 | 14.9272 | 18.8787 | 16.8599 | 18.7758 | 19.6039 | 22.4172 | 28.9535 | 35.2198 | 38.3356 | 35.5515 | 48.0749 | 50.3262 | 47.6711 | 53.1139 | 56.437 | 56.437 | 56.437 | 56.437 | 56.437 | 56.437 | 56.437 | 56.437 | 56.437 | 56.437 | 56.437 | 56.437 | 56.437 | 56.437 | 56.437 | Option 1 Summer POE10 W E @ R (MWh) N 1 | 3.6465 | 6.5075 | 6.6061 | 6.4999 | 6.5271 | 6.7237 | 7.1346 | 7.8981 | 8.3155 | 8.624 | 9.0952 | 9.7041 | 10.4511 | 10.8472 | 10.7184 | 10.8744 | 10.8744 | 10.8744 | 10.8744 | 10.8744 | 10.8744 | 10.8744 | 10.8744 | 10.8744 | 10.8744 | 10.8744 | 10.8744 | 10.8744 | 10.8744 | 10.8744
Option 2 - Replace 3 x 10/13.5 MVA Tx with 3 x 20/33 MVA Tx
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | FY26: 0.85477; FY27: 0.97121 |  | 0.76588 | 1.8133 | 1.9218
98% | FY26: 0; FY27: 0 |  | 0 | 0 | 0
97% | FY26: 0; FY27: 0 |  | 0 | 0 | 0
95% | FY26: 1.7892; FY27: 2.2386 |  | 1.4462 | 5.4884 | 5.907
90% | FY26: 2.2571; FY27: 3.9884 |  | 1.2574 | 22.3422 | 24.7623
85% | [32 empty] | 31.8883 | 41.9816
80% | [33 empty] | 0.8561
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 4.8521 | 7.1262 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 3.4348 | 60.9169 | 74.6745 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2 Winter POE50 W E @ R (MWh) N 1 | 0 | 3.3964 | 4.9884 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 2 Winter POE10 W E @ R (MWh) N 1 | 1.0304 | 18.2751 | 22.4024 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | FY25: 0.66733; FY26: 1.7156; FY27: 1.8209 |  | 0 | 0 | 0
98% | FY25: 0; FY26: 0; FY27: 0 |  | 0 | 0 | 0
97% | FY25: 0; FY26: 0; FY27: 0 |  | 3.5495 | 4.6974 | 4.7291
95% | FY25: 0.17429; FY26: 1.1856; FY27: 1.2873 |  | 0 | 0 | 0
90% | FY25: 0.017439; FY26: 14.426; FY27: 16.5803 |  | 2.6829 | 3.7719 | 3.802
85% | FY26: 4.2128; FY27: 7.5535 |  | 1.8163 | 2.8464 | 2.8749
80% | [31 empty] | 3.7987 | 7.6839 | 7.7911
75% | [31 empty] | 0.30768 | 1.991 | 2.0414
70% | [32 empty] | 0.92015 | 1.0045
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0.85046 | 21.3245 | 26.9695 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 12.0334 | 21.6917 | 22.0205 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2 Summer POE50 W E @ R (MWh) N 1 | 0.59532 | 14.9272 | 18.8787 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 2 Summer POE10 W E @ R (MWh) N 1 | 3.61 | 6.5075 | 6.6061 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 - Replace 1 x 10/13.5 MVA Tx with 1 x 20/33 MVA Tx
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% |  | 0.85477 | 0.97121 | [10 empty] | 0.02569 | 0.10813 | 0.10813 | 0.10813 | 0.10813 | 0.10813 | 0.10813 | 0.10813 | 0.10813 | 0.10813 | 0.10813 | 0.10813 | 0.10813 | 0.10813 | 0.10813 | 0.10813 | 0.10813 |  | 0.76588 | 1.8133 | 1.9218 | [7 empty] | 0.0727 |  | 0.037617 | 0.30235 | 0.19072 | 0.19072 | 0.19072 | 0.19072 | 0.19072 | 0.19072 | 0.19072 | 0.19072 | 0.19072 | 0.19072 | 0.19072 | 0.19072 | 0.19072 | 0.19072 | 0.19072 | 0.19072
98% |  | 0 | 0 | [11 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
97% | FY26: 0; FY27: 0 |  | 0 | 0 | 0 | [10 empty] | 0
95% | FY26: 1.7892; FY27: 2.2386 |  | 1.4462 | 5.4884 | 5.907
90% | FY26: 2.2571; FY27: 3.9884 |  | 1.2574 | 22.3422 | 24.7623
85% | [32 empty] | 31.8883 | 41.9816
80% | [33 empty] | 0.8561
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 4.8521 | 7.1262 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.025433 | 0.10705 | 0.10705 | 0.10705 | 0.10705 | 0.10705 | 0.10705 | 0.10705 | 0.10705 | 0.10705 | 0.10705 | 0.10705 | 0.10705 | 0.10705 | 0.10705 | 0.10705 | 0.10705 | E @ R (MWh) | 3.4348 | 60.9169 | 74.6745 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.071973 | 0 | 0.037241 | 0.29933 | 0.18881 | 0.18881 | 0.18881 | 0.18881 | 0.18881 | 0.18881 | 0.18881 | 0.18881 | 0.18881 | 0.18881 | 0.18881 | 0.18881 | 0.18881 | 0.18881 | 0.18881 | 0.18881
Option 3 Winter POE50 W E @ R (MWh) N 1 | 0 | 3.3964 | 4.9884 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.017803 | 0.074932 | 0.074932 | 0.074932 | 0.074932 | 0.074932 | 0.074932 | 0.074932 | 0.074932 | 0.074932 | 0.074932 | 0.074932 | 0.074932 | 0.074932 | 0.074932 | 0.074932 | 0.074932 | Option 3 Winter POE10 W E @ R (MWh) N 1 | 1.0304 | 18.2751 | 22.4024 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.021592 | 0 | 0.011172 | 0.089798 | 0.056643 | 0.056643 | 0.056643 | 0.056643 | 0.056643 | 0.056643 | 0.056643 | 0.056643 | 0.056643 | 0.056643 | 0.056643 | 0.056643 | 0.056643 | 0.056643 | 0.056643 | 0.056643
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | FY25: 0.66733; FY26: 1.7156; FY27: 1.8209 |  | 0 | 0 | 0 | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
98% | FY25: 0; FY26: 0; FY27: 0 |  | 0 | 0 | 0 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
97% | FY25: 0; FY26: 0; FY27: 0 |  | 3.5495 | 4.6974 | 4.7291 | [9 empty] | 0.025002 | 0.10416 | 0.072653 | 0.11124 | 0.11124 | 0.11124 | 0.11124 | 0.11124 | 0.11124 | 0.11124 | 0.11124 | 0.11124 | 0.11124 | 0.11124 | 0.11124 | 0.11124 | 0.11124 | 0.11124
95% | FY25: 0.17429; FY26: 1.1856; FY27: 1.2873 |  | 0 | 0 | 0 | [10 empty] | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
90% | FY25: 0.017439; FY26: 14.426; FY27: 16.5803 |  | 2.6829 | 3.7719 | 3.802
85% | FY26: 4.2128; FY27: 7.5535 |  | 1.8163 | 2.8464 | 2.8749
80% | [31 empty] | 3.7987 | 7.6839 | 7.7911
75% | [31 empty] | 0.30768 | 1.991 | 2.0414
70% | [32 empty] | 0.92015 | 1.0045
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0.85046 | 21.3245 | 26.9695 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 12.0334 | 21.6917 | 22.0205 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.024752 | 0.10312 | 0.071927 | 0.11012 | 0.11012 | 0.11012 | 0.11012 | 0.11012 | 0.11012 | 0.11012 | 0.11012 | 0.11012 | 0.11012 | 0.11012 | 0.11012 | 0.11012 | 0.11012 | 0.11012
Option 3 Summer POE50 W E @ R (MWh) N 1 | 0.59532 | 14.9272 | 18.8787 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 3 Summer POE10 W E @ R (MWh) N 1 | 3.61 | 6.5075 | 6.6061 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0074257 | 0.030935 | 0.021578 | 0.033037 | 0.033037 | 0.033037 | 0.033037 | 0.033037 | 0.033037 | 0.033037 | 0.033037 | 0.033037 | 0.033037 | 0.033037 | 0.033037 | 0.033037 | 0.033037 | 0.033037
Option 4 - Construct 2x 20/33MVA zone substation in Inverloch
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | FY26: 0.85477; FY27: 0.97121 |  | 0.76588 | 1.8133 | 1.9218
98% | FY26: 0; FY27: 0 |  | 0 | 0 | 0
97% | FY26: 0; FY27: 0 |  | 0 | 0 | 0
95% | FY26: 1.7892; FY27: 2.2386 |  | 1.4462 | 5.4884 | 5.907
90% | FY26: 2.2571; FY27: 3.9884 |  | 1.2574 | 22.3422 | 24.7623
85% | [32 empty] | 31.8883 | 41.9816
80% | [33 empty] | 0.8561
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 4.8521 | 7.1262 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 3.4348 | 60.9169 | 74.6745 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 Winter POE50 W E @ R (MWh) N 1 | 0 | 3.3964 | 4.9884 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 4 Winter POE10 W E @ R (MWh) N 1 | 1.0304 | 18.2751 | 22.4024 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | FY25: 0.66733; FY26: 1.7156; FY27: 1.8209 |  | 0 | 0 | 0
98% | FY25: 0; FY26: 0; FY27: 0 |  | 0 | 0 | 0
97% | FY25: 0; FY26: 0; FY27: 0 |  | 3.5495 | 4.6974 | 4.7291
95% | FY25: 0.17429; FY26: 1.1856; FY27: 1.2873 |  | 0 | 0 | 0
90% | FY25: 0.017439; FY26: 14.426; FY27: 16.5803 |  | 2.6829 | 3.7719 | 3.802
85% | FY26: 4.2128; FY27: 7.5535 |  | 1.8163 | 2.8464 | 2.8749
80% | [31 empty] | 3.7987 | 7.6839 | 7.7911
75% | [31 empty] | 0.30768 | 1.991 | 2.0414
70% | [32 empty] | 0.92015 | 1.0045
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0.85046 | 21.3245 | 26.9695 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 12.0334 | 21.6917 | 22.0205 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 Summer POE50 W E @ R (MWh) N 1 | 0.59532 | 14.9272 | 18.8787 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 4 Summer POE10 W E @ R (MWh) N 1 | 3.61 | 6.5075 | 6.6061 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 - Contract network support services to defer network investment
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% |  |  |  |  | 0.020065 | 0.18855 | 0.4961 | 1.2765 | 1.6965 | 1.378 | 2.3363 | 2.4989 | 2.6101 | 3.1933 | 3.2919 | 3.2919 | 3.2919 | 3.2919 | 3.2919 | 3.2919 | 3.2919 | 3.2919 | 3.2919 | 3.2919 | 3.2919 | 3.2919 | 3.2919 | 3.2919 | 3.2919 | 3.2919 |  |  | 0.5193 | 0.62551 | 1.0023 | 0.99254 | 1.0704 | 1.3832 | 2.2922 | 2.6655 | 2.2982 | 3.2871 | 2.8564 | 3.2194 | 3.4837 | 3.3744 | 3.3744 | 3.3744 | 3.3744 | 3.3744 | 3.3744 | 3.3744 | 3.3744 | 3.3744 | 3.3744 | 3.3744 | 3.3744 | 3.3744 | 3.3744 | 3.3744 | 3.3744
98% | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
97% | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
95% | [6 empty] | 0.40621 | 3.4167 | 5.0377 | 3.8084 | 7.5068 | 8.1345 | 8.5636 | 10.8144 | 11.1947 | 11.1947 | 11.1947 | 11.1947 | 11.1947 | 11.1947 | 11.1947 | 11.1947 | 11.1947 | 11.1947 | 11.1947 | 11.1947 | 11.1947 | 11.1947 | 11.1947 | 11.1947 |  |  | 0.49456 | 0.90443 | 2.3585 | 2.3209 | 2.6213 | 3.8287 | 7.3366 | 8.7774 | 7.3598 | 11.1763 | 9.5142 | 10.9149 | 11.935 | 11.5134 | 11.5134 | 11.5134 | 11.5134 | 11.5134 | 11.5134 | 11.5134 | 11.5134 | 11.5134 | 11.5134 | 11.5134 | 11.5134 | 11.5134 | 11.5134 | 11.5134 | 11.5134
90% | [7 empty] | 10.3652 | 19.7362 | 12.6294 | 34.0107 | 37.6396 | 40.1206 | 53.1331 | 55.3314 | 55.3314 | 55.3314 | 55.3314 | 55.3314 | 55.3314 | 55.3314 | 55.3314 | 55.3314 | 55.3314 | 55.3314 | 55.3314 | 55.3314 | 55.3314 | 55.3314 | 55.3314 |  |  | 0.0023825 | 0.26378 | 4.5299 | 4.3564 | 5.8304 | 12.7468 | 33.0268 | 41.3569 | 33.161 | 55.2255 | 45.616 | 53.7139 | 59.6113 | 57.1741 | 57.1741 | 57.1741 | 57.1741 | 57.1741 | 57.1741 | 57.1741 | 57.1741 | 57.1741 | 57.1741 | 57.1741 | 57.1741 | 57.1741 | 57.1741 | 57.1741 | 57.1741
85% | [7 empty] | 1.4902 | 22.0909 | 4.2947 | 80.6208 | 95.7819 | 106.1474 | 160.5126 | 169.697 | 169.697 | 169.697 | 169.697 | 169.697 | 169.697 | 169.697 | 169.697 | 169.697 | 169.697 | 169.697 | 169.697 | 169.697 | 169.697 | 169.697 | 169.697 | [7 empty] | 4.4788 | 76.5101 | 111.3124 | 77.0709 | 169.2546 | 129.1068 | 162.9395 | 187.5783 | 177.3958 | 177.3958 | 177.3958 | 177.3958 | 177.3958 | 177.3958 | 177.3958 | 177.3958 | 177.3958 | 177.3958 | 177.3958 | 177.3958 | 177.3958 | 177.3958 | 177.3958 | 177.3958
80% | [10 empty] | 25.3342 | 43.6922 | 58.9362 | 145.0099 | 159.5514 | 159.5514 | 159.5514 | 159.5514 | 159.5514 | 159.5514 | 159.5514 | 159.5514 | 159.5514 | 159.5514 | 159.5514 | 159.5514 | 159.5514 | 159.5514 | 159.5514 | 159.5514 | [8 empty] | 21.1827 | 67.1118 | 21.728 | 158.8509 | 95.2853 | 148.8522 | 187.8626 | 171.7408 | 171.7408 | 171.7408 | 171.7408 | 171.7408 | 171.7408 | 171.7408 | 171.7408 | 171.7408 | 171.7408 | 171.7408 | 171.7408 | 171.7408 | 171.7408 | 171.7408 | 171.7408
75% | FY38: 54.0536; FY39: 73.5259; FY40: 73.5259; FY41: 73.5259; FY42: 73.5259; FY43: 73.5259; FY44: 73.5259; FY45: 73.5259; FY46: 73.5259; FY47: 73.5259; FY48: 73.5259; FY49: 73.5259; FY50: 73.5259; FY51: 73.5259; FY52: 73.5259; FY53: 73.5259; FY54: 73.5259 | [9 empty] | 0.42625 |  | 72.5228 | 9.645 | 58.921 | 119.4852 | 92.0269 | 92.0269 | 92.0269 | 92.0269 | 92.0269 | 92.0269 | 92.0269 | 92.0269 | 92.0269 | 92.0269 | 92.0269 | 92.0269 | 92.0269 | 92.0269 | 92.0269 | 92.0269
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0.019864 | 0.18666 | 0.89329 | 16.3831 | 48.0757 | 21.8893 | 148.3107 | 185.8696 | 214.214 | 422.4497 | 467.8662 | 467.8662 | 467.8662 | 467.8662 | 467.8662 | 467.8662 | 467.8662 | 467.8662 | 467.8662 | 467.8662 | 467.8662 | 467.8662 | 467.8662 | 467.8662 | 467.8662 | 467.8662 | E @ R (MWh) | 0 | 1.0061 | 1.7758 | 7.8118 | 7.5932 | 9.4268 | 22.2131 | 138.9448 | 229.3338 | 140.2018 | 465.6141 | 289.1034 | 434.1753 | 564.2565 | 508.0932 | 508.0932 | 508.0932 | 508.0932 | 508.0932 | 508.0932 | 508.0932 | 508.0932 | 508.0932 | 508.0932 | 508.0932 | 508.0932 | 508.0932 | 508.0932 | 508.0932 | 508.0932
Option 5 Winter POE50 W E @ R (MWh) N 1 | 0 | 0 | 0 | 0 | 0.013905 | 0.13066 | 0.6253 | 11.4681 | 33.653 | 15.3225 | 103.8175 | 130.1087 | 149.9498 | 295.7148 | 327.5064 | 327.5064 | 327.5064 | 327.5064 | 327.5064 | 327.5064 | 327.5064 | 327.5064 | 327.5064 | 327.5064 | 327.5064 | 327.5064 | 327.5064 | 327.5064 | 327.5064 | 327.5064 | Option 5 Winter POE10 W E @ R (MWh) N 1 | 0 | 0.30183 | 0.53273 | 2.3435 | 2.278 | 2.828 | 6.6639 | 41.6834 | 68.8001 | 42.0606 | 139.6842 | 86.731 | 130.2526 | 169.2769 | 152.428 | 152.428 | 152.428 | 152.428 | 152.428 | 152.428 | 152.428 | 152.428 | 152.428 | 152.428 | 152.428 | 152.428 | 152.428 | 152.428 | 152.428 | 152.428
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 |  | 0.069054 | 0.17151 | 0.12298 | 0.17128 | 0.18574 | 0.23883 | 0.3514 | 0.45262 | 0.49642 | 0.43892 | 0.61646 | 0.62903 | 0.58352 | 0.65897 | 0.70036 | 0.70036 | 0.70036 | 0.70036 | 0.70036 | 0.70036 | 0.70036 | 0.70036 | 0.70036 | 0.70036 | 0.70036 | 0.70036 | 0.70036 | 0.70036 | 0.70036 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
98% |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
97% | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2.0384 | 3.084 | 3.1128 | 3.0817 | 3.0897 | 3.1468 | 3.2625 | 3.4663 | 3.5725 | 3.6493 | 3.7655 | 3.914 | 4.0934 | 4.1875 | 4.157 | 4.1976 | 4.1976 | 4.1976 | 4.1976 | 4.1976 | 4.1976 | 4.1976 | 4.1976 | 4.1976 | 4.1976 | 4.1976 | 4.1976 | 4.1976 | 4.1976 | 4.1976
95% | [7 empty] | 9.3155e-05 | 0.020189 | 0.039641 | 0.01543 | 0.12561 | 0.13735 | 0.097302 | 0.16622 | 0.20616 | 0.20616 | 0.20616 | 0.20616 | 0.20616 | 0.20616 | 0.20616 | 0.20616 | 0.20616 | 0.20616 | 0.20616 | 0.20616 | 0.20616 | 0.20616 | 0.20616 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
90% | FY39: 0.01011; FY40: 0.065734; FY41: 0.065734; FY42: 0.065734; FY43: 0.065734; FY44: 0.065734; FY45: 0.065734; FY46: 0.065734; FY47: 0.065734; FY48: 0.065734; FY49: 0.065734; FY50: 0.065734; FY51: 0.065734; FY52: 0.065734; FY53: 0.065734; FY54: 0.065734 |  | 1.2493 | 2.2412 | 2.2686 | 2.2391 | 2.2467 | 2.3009 | 2.4106 | 2.604 | 2.7047 | 2.7776 | 2.8879 | 3.0287 | 3.1989 | 3.2882 | 3.2592 | 3.2977 | 3.2977 | 3.2977 | 3.2977 | 3.2977 | 3.2977 | 3.2977 | 3.2977 | 3.2977 | 3.2977 | 3.2977 | 3.2977 | 3.2977 | 3.2977 | 3.2977
85% | [31 empty] | 0.46023 | 1.3985 | 1.4244 | 1.3965 | 1.4037 | 1.4549 | 1.5587 | 1.7416 | 1.8369 | 1.9058 | 2.0102 | 2.1434 | 2.3044 | 2.3889 | 2.3615 | 2.3979 | 2.3979 | 2.3979 | 2.3979 | 2.3979 | 2.3979 | 2.3979 | 2.3979 | 2.3979 | 2.3979 | 2.3979 | 2.3979 | 2.3979 | 2.3979 | 2.3979
80% | [31 empty] | 0.010931 | 2.2232 | 2.3208 | 2.2155 | 2.2426 | 2.4358 | 2.8275 | 3.5171 | 3.8765 | 4.1365 | 4.53 | 5.0323 | 5.6398 | 5.9582 | 5.855 | 5.9922 | 5.9922 | 5.9922 | 5.9922 | 5.9922 | 5.9922 | 5.9922 | 5.9922 | 5.9922 | 5.9922 | 5.9922 | 5.9922 | 5.9922 | 5.9922 | 5.9922
75% | [32 empty] | 0.021443 | 0.029608 | 0.020859 | 0.022965 | 0.04089 | 0.092639 | 0.23287 | 0.33013 | 0.4106 | 0.54822 | 0.7511 | 1.0309 | 1.1804 | 1.132 | 1.1964 | 1.1964 | 1.1964 | 1.1964 | 1.1964 | 1.1964 | 1.1964 | 1.1964 | 1.1964 | 1.1964 | 1.1964 | 1.1964 | 1.1964 | 1.1964 | 1.1964
70% | [43 empty] | 0.015605 | 0.065911 | 0.045829 | 0.07333 | 0.07333 | 0.07333 | 0.07333 | 0.07333 | 0.07333 | 0.07333 | 0.07333 | 0.07333 | 0.07333 | 0.07333 | 0.07333 | 0.07333 | 0.07333 | 0.07333
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0.068363 | 0.16979 | 0.12175 | 0.16956 | 0.18389 | 0.23644 | 0.34798 | 0.46808 | 0.5307 | 0.4498 | 0.73465 | 0.75871 | 0.67401 | 0.82695 | 0.96253 | 0.96253 | 0.96253 | 0.96253 | 0.96253 | 0.96253 | 0.96253 | 0.96253 | 0.96253 | 0.96253 | 0.96253 | 0.96253 | 0.96253 | 0.96253 | 0.96253 | E @ R (MWh) | 3.7214 | 8.8786 | 9.0647 | 8.8642 | 8.9156 | 9.2855 | 10.0505 | 11.4462 | 12.1975 | 12.751 | 13.6043 | 14.7208 | 16.1203 | 16.8984 | 16.6424 | 16.9836 | 16.9836 | 16.9836 | 16.9836 | 16.9836 | 16.9836 | 16.9836 | 16.9836 | 16.9836 | 16.9836 | 16.9836 | 16.9836 | 16.9836 | 16.9836 | 16.9836
Option 5 Summer POE50 W E @ R (MWh) N 1 | 0 | 0.047854 | 0.11885 | 0.085226 | 0.1187 | 0.12872 | 0.16551 | 0.24358 | 0.32766 | 0.37149 | 0.31486 | 0.51425 | 0.5311 | 0.47181 | 0.57886 | 0.67377 | 0.67377 | 0.67377 | 0.67377 | 0.67377 | 0.67377 | 0.67377 | 0.67377 | 0.67377 | 0.67377 | 0.67377 | 0.67377 | 0.67377 | 0.67377 | 0.67377 | Option 5 Summer POE10 W E @ R (MWh) N 1 | 1.1164 | 2.6636 | 2.7194 | 2.6592 | 2.6747 | 2.7857 | 3.0151 | 3.4339 | 3.6592 | 3.8253 | 4.0813 | 4.4162 | 4.8361 | 5.0695 | 4.9927 | 5.0951 | 5.0951 | 5.0951 | 5.0951 | 5.0951 | 5.0951 | 5.0951 | 5.0951 | 5.0951 | 5.0951 | 5.0951 | 5.0951 | 5.0951 | 5.0951 | 5.0951
Option 6 -
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% |  | 0.85477 | 0.97121 | 1.1152 | 1.3063 | 1.4875 | 1.8041 | 2.6005 | 3.0288 | 2.7163 | 3.6838 | 3.8581 | 3.9834 | 4.574 | 4.6701 | 4.6701 | 4.6701 | 4.6701 | 4.6701 | 4.6701 | 4.6701 | 4.6701 | 4.6701 | 4.6701 | 4.6701 | 4.6701 | 4.6701 | 4.6701 | 4.6701 | 4.6701 |  | 0.76588 | 1.8133 | 1.9218 | 2.2961 | 2.287 | 2.3693 | 2.6912 | 3.6162 | 3.9979 | 3.6366 | 4.6346 | 4.2156 | 4.5926 | 4.8643 | 4.7527 | 4.7527 | 4.7527 | 4.7527 | 4.7527 | 4.7527 | 4.7527 | 4.7527 | 4.7527 | 4.7527 | 4.7527 | 4.7527 | 4.7527 | 4.7527 | 4.7527 | 4.7527
98% |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
97% |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
95% |  | 1.7892 | 2.2386 | 2.7941 | 3.5317 | 4.231 | 5.453 | 8.5265 | 10.1796 | 8.9736 | 12.7072 | 13.3799 | 13.8635 | 16.1428 | 16.5138 | 16.5138 | 16.5138 | 16.5138 | 16.5138 | 16.5138 | 16.5138 | 16.5138 | 16.5138 | 16.5138 | 16.5138 | 16.5138 | 16.5138 | 16.5138 | 16.5138 | 16.5138 |  | 1.4462 | 5.4884 | 5.907 | 7.3517 | 7.3165 | 7.6342 | 8.8767 | 12.4463 | 13.9194 | 12.525 | 16.3768 | 14.7596 | 16.2148 | 17.2634 | 16.8326 | 16.8326 | 16.8326 | 16.8326 | 16.8326 | 16.8326 | 16.8326 | 16.8326 | 16.8326 | 16.8326 | 16.8326 | 16.8326 | 16.8326 | 16.8326 | 16.8326 | 16.8326
90% |  | 2.2571 | 3.9884 | 6.7708 | 11.03 | 15.0726 | 22.1375 | 39.906 | 49.4631 | 42.4909 | 64.076 | 67.965 | 70.7605 | 83.9378 | 86.0827 | 86.0827 | 86.0827 | 86.0827 | 86.0827 | 86.0827 | 86.0827 | 86.0827 | 86.0827 | 86.0827 | 86.0827 | 86.0827 | 86.0827 | 86.0827 | 86.0827 | 86.0827 |  | 1.2574 | 22.3422 | 24.7623 | 33.1144 | 32.9108 | 34.7474 | 41.9304 | 62.5676 | 71.0837 | 63.0226 | 85.2907 | 75.9414 | 84.3539 | 90.4161 | 87.9254 | 87.9254 | 87.9254 | 87.9254 | 87.9254 | 87.9254 | 87.9254 | 87.9254 | 87.9254 | 87.9254 | 87.9254 | 87.9254 | 87.9254 | 87.9254 | 87.9254 | 87.9254
85% |  |  |  |  | 2.1655 | 8.9007 | 31.0571 | 105.2507 | 145.1799 | 116.0504 | 206.2313 | 222.4792 | 234.1587 | 289.2127 | 298.1738 | 298.1738 | 298.1738 | 298.1738 | 298.1738 | 298.1738 | 298.1738 | 298.1738 | 298.1738 | 298.1738 | 298.1738 | 298.1738 | 298.1738 | 298.1738 | 298.1738 | 298.1738 |  |  | 31.8883 | 41.9816 | 76.8759 | 76.0255 | 83.6985 | 113.7089 | 199.9294 | 235.5092 | 201.8302 | 294.8651 | 255.804 | 290.9508 | 316.2783 | 305.8726 | 305.8726 | 305.8726 | 305.8726 | 305.8726 | 305.8726 | 305.8726 | 305.8726 | 305.8726 | 305.8726 | 305.8726 | 305.8726 | 305.8726 | 305.8726 | 305.8726 | 305.8726
80% | [7 empty] | 57.5329 | 120.7337 | 74.6133 | 217.3957 | 243.1208 | 261.6129 | 348.7792 | 362.9672 | 362.9672 | 362.9672 | 362.9672 | 362.9672 | 362.9672 | 362.9672 | 362.9672 | 362.9672 | 362.9672 | 362.9672 | 362.9672 | 362.9672 | 362.9672 | 362.9672 | 362.9672 |  |  |  | 0.8561 | 21.5377 | 20.7169 | 28.6755 | 70.906 | 207.4181 | 263.7511 | 210.4275 | 357.7285 | 295.8836 | 351.5311 | 391.6319 | 375.1566 | 375.1566 | 375.1566 | 375.1566 | 375.1566 | 375.1566 | 375.1566 | 375.1566 | 375.1566 | 375.1566 | 375.1566 | 375.1566 | 375.1566 | 375.1566 | 375.1566 | 375.1566
75% | [8 empty] | 28.0034 | 1.7144 | 173.9745 | 221.4919 | 255.6491 | 416.656 | 442.8629 | 442.8629 | 442.8629 | 442.8629 | 442.8629 | 442.8629 | 442.8629 | 442.8629 | 442.8629 | 442.8629 | 442.8629 | 442.8629 | 442.8629 | 442.8629 | 442.8629 | 442.8629 | [7 empty] | 0.97067 | 155.5446 | 259.5988 | 161.1034 | 433.1866 | 318.9513 | 421.7392 | 495.8103 | 465.3784 | 465.3784 | 465.3784 | 465.3784 | 465.3784 | 465.3784 | 465.3784 | 465.3784 | 465.3784 | 465.3784 | 465.3784 | 465.3784 | 465.3784 | 465.3784 | 465.3784 | 465.3784
70% | [10 empty] | 7.6559 | 29.4651 | 53.6075 | 256.6677 | 299.3259 | 299.3259 | 299.3259 | 299.3259 | 299.3259 | 299.3259 | 299.3259 | 299.3259 | 299.3259 | 299.3259 | 299.3259 | 299.3259 | 299.3259 | 299.3259 | 299.3259 | 299.3259 | [8 empty] | 2.9795 | 56.8461 | 4.1639 | 283.5753 | 116.4036 | 264.9419 | 385.5105 | 335.9752 | 335.9752 | 335.9752 | 335.9752 | 335.9752 | 335.9752 | 335.9752 | 335.9752 | 335.9752 | 335.9752 | 335.9752 | 335.9752 | 335.9752 | 335.9752 | 335.9752 | 335.9752
65% | FY38: 0.7116; FY39: 5.6622; FY40: 5.6622; FY41: 5.6622; FY42: 5.6622; FY43: 5.6622; FY44: 5.6622; FY45: 5.6622; FY46: 5.6622; FY47: 5.6622; FY48: 5.6622; FY49: 5.6622; FY50: 5.6622; FY51: 5.6622; FY52: 5.6622; FY53: 5.6622; FY54: 5.6622 | [11 empty] | 3.2889 |  | 1.3047 | 29.7436 | 13.6273 | 13.6273 | 13.6273 | 13.6273 | 13.6273 | 13.6273 | 13.6273 | 13.6273 | 13.6273 | 13.6273 | 13.6273 | 13.6273 | 13.6273 | 13.6273 | 13.6273 | 13.6273
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 4.8521 | 7.1262 | 10.5732 | 17.8532 | 29.3949 | 59.8472 | 211.6784 | 353.0228 | 244.0934 | 678.8671 | 793.7423 | 884.6991 | 1402.5149 | 1501.096 | 1501.096 | 1501.096 | 1501.096 | 1501.096 | 1501.096 | 1501.096 | 1501.096 | 1501.096 | 1501.096 | 1501.096 | 1501.096 | 1501.096 | 1501.096 | 1501.096 | 1501.096 | E @ R (MWh) | 3.4348 | 60.9169 | 74.6745 | 139.764 | 137.8641 | 155.5536 | 236.6931 | 638.0567 | 895.6592 | 650.1421 | 1464.157 | 1071.1395 | 1421.2727 | 1714.2032 | 1589.4656 | 1589.4656 | 1589.4656 | 1589.4656 | 1589.4656 | 1589.4656 | 1589.4656 | 1589.4656 | 1589.4656 | 1589.4656 | 1589.4656 | 1589.4656 | 1589.4656 | 1589.4656 | 1589.4656 | 1589.4656
Option 6 Winter POE50 W E @ R (MWh) N 1 | 0 | 3.3964 | 4.9884 | 7.4013 | 12.4972 | 20.5764 | 41.893 | 148.1749 | 247.1159 | 170.8654 | 475.207 | 555.6196 | 619.2894 | 981.7605 | 1050.7672 | 1050.7672 | 1050.7672 | 1050.7672 | 1050.7672 | 1050.7672 | 1050.7672 | 1050.7672 | 1050.7672 | 1050.7672 | 1050.7672 | 1050.7672 | 1050.7672 | 1050.7672 | 1050.7672 | 1050.7672 | Option 6 Winter POE10 W E @ R (MWh) N 1 | 1.0304 | 18.2751 | 22.4024 | 41.9292 | 41.3592 | 46.6661 | 71.0079 | 191.417 | 268.6977 | 195.0426 | 439.2471 | 321.3418 | 426.3818 | 514.261 | 476.8397 | 476.8397 | 476.8397 | 476.8397 | 476.8397 | 476.8397 | 476.8397 | 476.8397 | 476.8397 | 476.8397 | 476.8397 | 476.8397 | 476.8397 | 476.8397 | 476.8397 | 476.8397
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | 0.66733 | 1.7156 | 1.8209 | 1.7693 | 1.8184 | 1.8385 | 1.9032 | 2.0361 | 2.1479 | 2.1994 | 2.1535 | 2.3459 | 2.3764 | 2.3403 | 2.4127 | 2.4541 | 2.4541 | 2.4541 | 2.4541 | 2.4541 | 2.4541 | 2.4541 | 2.4541 | 2.4541 | 2.4541 | 2.4541 | 2.4541 | 2.4541 | 2.4541 | 2.4541 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
98% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
97% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 3.5495 | 4.6974 | 4.7291 | 4.6949 | 4.7037 | 4.7664 | 4.8934 | 5.1171 | 5.2337 | 5.318 | 5.4457 | 5.6087 | 5.8057 | 5.909 | 5.8755 | 5.9161 | 5.9161 | 5.9161 | 5.9161 | 5.9161 | 5.9161 | 5.9161 | 5.9161 | 5.9161 | 5.9161 | 5.9161 | 5.9161 | 5.9161 | 5.9161 | 5.9161
95% | 0.17429 | 1.1856 | 1.2873 | 1.2375 | 1.2848 | 1.3043 | 1.3667 | 1.4949 | 1.6028 | 1.6525 | 1.6082 | 1.7938 | 1.8233 | 1.7884 | 1.8583 | 1.8982 | 1.8982 | 1.8982 | 1.8982 | 1.8982 | 1.8982 | 1.8982 | 1.8982 | 1.8982 | 1.8982 | 1.8982 | 1.8982 | 1.8982 | 1.8982 | 1.8982 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
90% | 0.017439 | 14.426 | 16.5803 | 15.5243 | 16.5284 | 16.941 | 18.2632 | 20.9821 | 23.2693 | 24.3221 | 23.3837 | 27.3182 | 27.9422 | 27.2037 | 28.6845 | 29.531 | 29.531 | 29.531 | 29.531 | 29.531 | 29.531 | 29.531 | 29.531 | 29.531 | 29.531 | 29.531 | 29.531 | 29.531 | 29.531 | 29.531 |  | 2.6829 | 3.7719 | 3.802 | 3.7696 | 3.7779 | 3.8374 | 3.9579 | 4.1701 | 4.2807 | 4.3608 | 4.4819 | 4.6365 | 4.8234 | 4.9214 | 4.8896 | 4.9281 | 4.9281 | 4.9281 | 4.9281 | 4.9281 | 4.9281 | 4.9281 | 4.9281 | 4.9281 | 4.9281 | 4.9281 | 4.9281 | 4.9281 | 4.9281 | 4.9281
85% |  | 4.2128 | 7.5535 | 5.7978 | 7.4619 | 8.2047 | 10.815 | 17.2668 | 23.8022 | 27.1443 | 24.1554 | 37.602 | 39.829 | 37.1935 | 42.4782 | 45.4993 | 45.4993 | 45.4993 | 45.4993 | 45.4993 | 45.4993 | 45.4993 | 45.4993 | 45.4993 | 45.4993 | 45.4993 | 45.4993 | 45.4993 | 45.4993 | 45.4993 |  | 1.8163 | 2.8464 | 2.8749 | 2.8442 | 2.8521 | 2.9084 | 3.0224 | 3.2232 | 3.3278 | 3.4035 | 3.518 | 3.6643 | 3.8411 | 3.9338 | 3.9037 | 3.9401 | 3.9401 | 3.9401 | 3.9401 | 3.9401 | 3.9401 | 3.9401 | 3.9401 | 3.9401 | 3.9401 | 3.9401 | 3.9401 | 3.9401 | 3.9401 | 3.9401
80% | [11 empty] | 0.31223 | 0.64989 | 0.26352 | 1.2096 | 2.056 | 2.056 | 2.056 | 2.056 | 2.056 | 2.056 | 2.056 | 2.056 | 2.056 | 2.056 | 2.056 | 2.056 | 2.056 | 2.056 | 2.056 |  | 3.7987 | 7.6839 | 7.7911 | 7.6755 | 7.7053 | 7.9174 | 8.3474 | 9.1046 | 9.4992 | 9.7847 | 10.2167 | 10.7682 | 11.4352 | 11.7847 | 11.6714 | 11.8087 | 11.8087 | 11.8087 | 11.8087 | 11.8087 | 11.8087 | 11.8087 | 11.8087 | 11.8087 | 11.8087 | 11.8087 | 11.8087 | 11.8087 | 11.8087 | 11.8087
75% | [31 empty] | 0.30768 | 1.991 | 2.0414 | 1.9871 | 2.0011 | 2.1007 | 2.3027 | 2.6583 | 2.8437 | 2.9777 | 3.1807 | 3.4397 | 3.753 | 3.9172 | 3.8639 | 3.9284 | 3.9284 | 3.9284 | 3.9284 | 3.9284 | 3.9284 | 3.9284 | 3.9284 | 3.9284 | 3.9284 | 3.9284 | 3.9284 | 3.9284 | 3.9284 | 3.9284
70% | [32 empty] | 0.92015 | 1.0045 | 0.91371 | 0.93666 | 1.1084 | 1.4984 | 2.3195 | 2.8134 | 3.1894 | 3.7589 | 4.486 | 5.3652 | 5.8259 | 5.6765 | 5.8575 | 5.8575 | 5.8575 | 5.8575 | 5.8575 | 5.8575 | 5.8575 | 5.8575 | 5.8575 | 5.8575 | 5.8575 | 5.8575 | 5.8575 | 5.8575 | 5.8575
65% | [40 empty] | 0.0029263 | 0.021684 | 0.070373 | 0.16537 | 0.23056 | 0.20828 | 0.23542 | 0.23542 | 0.23542 | 0.23542 | 0.23542 | 0.23542 | 0.23542 | 0.23542 | 0.23542 | 0.23542 | 0.23542 | 0.23542 | 0.23542 | 0.23542 | 0.23542
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0.85046 | 21.3245 | 26.9695 | 24.0856 | 26.8226 | 28.0056 | 32.0245 | 41.3621 | 50.314 | 54.7652 | 50.7878 | 68.6784 | 71.8945 | 68.1016 | 75.8769 | 80.6243 | 80.6243 | 80.6243 | 80.6243 | 80.6243 | 80.6243 | 80.6243 | 80.6243 | 80.6243 | 80.6243 | 80.6243 | 80.6243 | 80.6243 | 80.6243 | 80.6243 | E @ R (MWh) | 12.0334 | 21.6917 | 22.0205 | 21.6662 | 21.7569 | 22.4122 | 23.782 | 26.327 | 27.7185 | 28.7467 | 30.3173 | 32.3469 | 34.837 | 36.1573 | 35.7281 | 36.2482 | 36.2482 | 36.2482 | 36.2482 | 36.2482 | 36.2482 | 36.2482 | 36.2482 | 36.2482 | 36.2482 | 36.2482 | 36.2482 | 36.2482 | 36.2482 | 36.2482
Option 6 Summer POE50 W E @ R (MWh) N 1 | 0.59532 | 14.9272 | 18.8787 | 16.8599 | 18.7758 | 19.6039 | 22.4172 | 28.9535 | 35.2198 | 38.3356 | 35.5515 | 48.0749 | 50.3262 | 47.6711 | 53.1139 | 56.437 | 56.437 | 56.437 | 56.437 | 56.437 | 56.437 | 56.437 | 56.437 | 56.437 | 56.437 | 56.437 | 56.437 | 56.437 | 56.437 | 56.437 | Option 6 Summer POE10 W E @ R (MWh) N 1 | 3.61 | 6.5075 | 6.6061 | 6.4999 | 6.5271 | 6.7237 | 7.1346 | 7.8981 | 8.3155 | 8.624 | 9.0952 | 9.7041 | 10.4511 | 10.8472 | 10.7184 | 10.8744 | 10.8744 | 10.8744 | 10.8744 | 10.8744 | 10.8744 | 10.8744 | 10.8744 | 10.8744 | 10.8744 | 10.8744 | 10.8744 | 10.8744 | 10.8744 | 10.8744
Option 7 -
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% |  | 0.85477 | 0.97121 | 1.1152 | 1.3063 | 1.4875 | 1.8041 | 2.6005 | 3.0288 | 2.7163 | 3.6838 | 3.8581 | 3.9834 | 4.574 | 4.6701 | 4.6701 | 4.6701 | 4.6701 | 4.6701 | 4.6701 | 4.6701 | 4.6701 | 4.6701 | 4.6701 | 4.6701 | 4.6701 | 4.6701 | 4.6701 | 4.6701 | 4.6701 |  | 0.76588 | 1.8133 | 1.9218 | 2.2961 | 2.287 | 2.3693 | 2.6912 | 3.6162 | 3.9979 | 3.6366 | 4.6346 | 4.2156 | 4.5926 | 4.8643 | 4.7527 | 4.7527 | 4.7527 | 4.7527 | 4.7527 | 4.7527 | 4.7527 | 4.7527 | 4.7527 | 4.7527 | 4.7527 | 4.7527 | 4.7527 | 4.7527 | 4.7527 | 4.7527
98% |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
97% |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
95% |  | 1.7892 | 2.2386 | 2.7941 | 3.5317 | 4.231 | 5.453 | 8.5265 | 10.1796 | 8.9736 | 12.7072 | 13.3799 | 13.8635 | 16.1428 | 16.5138 | 16.5138 | 16.5138 | 16.5138 | 16.5138 | 16.5138 | 16.5138 | 16.5138 | 16.5138 | 16.5138 | 16.5138 | 16.5138 | 16.5138 | 16.5138 | 16.5138 | 16.5138 |  | 1.4462 | 5.4884 | 5.907 | 7.3517 | 7.3165 | 7.6342 | 8.8767 | 12.4463 | 13.9194 | 12.525 | 16.3768 | 14.7596 | 16.2148 | 17.2634 | 16.8326 | 16.8326 | 16.8326 | 16.8326 | 16.8326 | 16.8326 | 16.8326 | 16.8326 | 16.8326 | 16.8326 | 16.8326 | 16.8326 | 16.8326 | 16.8326 | 16.8326 | 16.8326
90% |  | 2.2571 | 3.9884 | 6.7708 | 11.03 | 15.0726 | 22.1375 | 39.906 | 49.4631 | 42.4909 | 64.076 | 67.965 | 70.7605 | 83.9378 | 86.0827 | 86.0827 | 86.0827 | 86.0827 | 86.0827 | 86.0827 | 86.0827 | 86.0827 | 86.0827 | 86.0827 | 86.0827 | 86.0827 | 86.0827 | 86.0827 | 86.0827 | 86.0827 |  | 1.2574 | 22.3422 | 24.7623 | 33.1144 | 32.9108 | 34.7474 | 41.9304 | 62.5676 | 71.0837 | 63.0226 | 85.2907 | 75.9414 | 84.3539 | 90.4161 | 87.9254 | 87.9254 | 87.9254 | 87.9254 | 87.9254 | 87.9254 | 87.9254 | 87.9254 | 87.9254 | 87.9254 | 87.9254 | 87.9254 | 87.9254 | 87.9254 | 87.9254 | 87.9254
85% |  |  |  |  | 2.1655 | 8.9007 | 31.0571 | 105.2507 | 145.1799 | 116.0504 | 206.2313 | 222.4792 | 234.1587 | 289.2127 | 298.1738 | 298.1738 | 298.1738 | 298.1738 | 298.1738 | 298.1738 | 298.1738 | 298.1738 | 298.1738 | 298.1738 | 298.1738 | 298.1738 | 298.1738 | 298.1738 | 298.1738 | 298.1738 |  |  | 31.8883 | 41.9816 | 76.8759 | 76.0255 | 83.6985 | 113.7089 | 199.9294 | 235.5092 | 201.8302 | 294.8651 | 255.804 | 290.9508 | 316.2783 | 305.8726 | 305.8726 | 305.8726 | 305.8726 | 305.8726 | 305.8726 | 305.8726 | 305.8726 | 305.8726 | 305.8726 | 305.8726 | 305.8726 | 305.8726 | 305.8726 | 305.8726 | 305.8726
80% | [7 empty] | 57.5329 | 120.7337 | 74.6133 | 217.3957 | 243.1208 | 261.6129 | 348.7792 | 362.9672 | 362.9672 | 362.9672 | 362.9672 | 362.9672 | 362.9672 | 362.9672 | 362.9672 | 362.9672 | 362.9672 | 362.9672 | 362.9672 | 362.9672 | 362.9672 | 362.9672 | 362.9672 |  |  |  | 0.8561 | 21.5377 | 20.7169 | 28.6755 | 70.906 | 207.4181 | 263.7511 | 210.4275 | 357.7285 | 295.8836 | 351.5311 | 391.6319 | 375.1566 | 375.1566 | 375.1566 | 375.1566 | 375.1566 | 375.1566 | 375.1566 | 375.1566 | 375.1566 | 375.1566 | 375.1566 | 375.1566 | 375.1566 | 375.1566 | 375.1566 | 375.1566
75% | [8 empty] | 28.0034 | 1.7144 | 173.9745 | 221.4919 | 255.6491 | 416.656 | 442.8629 | 442.8629 | 442.8629 | 442.8629 | 442.8629 | 442.8629 | 442.8629 | 442.8629 | 442.8629 | 442.8629 | 442.8629 | 442.8629 | 442.8629 | 442.8629 | 442.8629 | 442.8629 | [7 empty] | 0.97067 | 155.5446 | 259.5988 | 161.1034 | 433.1866 | 318.9513 | 421.7392 | 495.8103 | 465.3784 | 465.3784 | 465.3784 | 465.3784 | 465.3784 | 465.3784 | 465.3784 | 465.3784 | 465.3784 | 465.3784 | 465.3784 | 465.3784 | 465.3784 | 465.3784 | 465.3784 | 465.3784
70% | [10 empty] | 7.6559 | 29.4651 | 53.6075 | 256.6677 | 299.3259 | 299.3259 | 299.3259 | 299.3259 | 299.3259 | 299.3259 | 299.3259 | 299.3259 | 299.3259 | 299.3259 | 299.3259 | 299.3259 | 299.3259 | 299.3259 | 299.3259 | 299.3259 | [8 empty] | 2.9795 | 56.8461 | 4.1639 | 283.5753 | 116.4036 | 264.9419 | 385.5105 | 335.9752 | 335.9752 | 335.9752 | 335.9752 | 335.9752 | 335.9752 | 335.9752 | 335.9752 | 335.9752 | 335.9752 | 335.9752 | 335.9752 | 335.9752 | 335.9752 | 335.9752 | 335.9752
65% | FY38: 0.7116; FY39: 5.6622; FY40: 5.6622; FY41: 5.6622; FY42: 5.6622; FY43: 5.6622; FY44: 5.6622; FY45: 5.6622; FY46: 5.6622; FY47: 5.6622; FY48: 5.6622; FY49: 5.6622; FY50: 5.6622; FY51: 5.6622; FY52: 5.6622; FY53: 5.6622; FY54: 5.6622 | [11 empty] | 3.2889 |  | 1.3047 | 29.7436 | 13.6273 | 13.6273 | 13.6273 | 13.6273 | 13.6273 | 13.6273 | 13.6273 | 13.6273 | 13.6273 | 13.6273 | 13.6273 | 13.6273 | 13.6273 | 13.6273 | 13.6273 | 13.6273
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 4.8521 | 7.1262 | 10.5732 | 17.8532 | 29.3949 | 59.8472 | 211.6784 | 353.0228 | 244.0934 | 678.8671 | 793.7423 | 884.6991 | 1402.5149 | 1501.096 | 1501.096 | 1501.096 | 1501.096 | 1501.096 | 1501.096 | 1501.096 | 1501.096 | 1501.096 | 1501.096 | 1501.096 | 1501.096 | 1501.096 | 1501.096 | 1501.096 | 1501.096 | E @ R (MWh) | 3.4348 | 60.9169 | 74.6745 | 139.764 | 137.8641 | 155.5536 | 236.6931 | 638.0567 | 895.6592 | 650.1421 | 1464.157 | 1071.1395 | 1421.2727 | 1714.2032 | 1589.4656 | 1589.4656 | 1589.4656 | 1589.4656 | 1589.4656 | 1589.4656 | 1589.4656 | 1589.4656 | 1589.4656 | 1589.4656 | 1589.4656 | 1589.4656 | 1589.4656 | 1589.4656 | 1589.4656 | 1589.4656
Option 7 Winter POE50 W E @ R (MWh) N 1 | 0 | 3.3964 | 4.9884 | 7.4013 | 12.4972 | 20.5764 | 41.893 | 148.1749 | 247.1159 | 170.8654 | 475.207 | 555.6196 | 619.2894 | 981.7605 | 1050.7672 | 1050.7672 | 1050.7672 | 1050.7672 | 1050.7672 | 1050.7672 | 1050.7672 | 1050.7672 | 1050.7672 | 1050.7672 | 1050.7672 | 1050.7672 | 1050.7672 | 1050.7672 | 1050.7672 | 1050.7672 | Option 7 Winter POE10 W E @ R (MWh) N 1 | 1.0304 | 18.2751 | 22.4024 | 41.9292 | 41.3592 | 46.6661 | 71.0079 | 191.417 | 268.6977 | 195.0426 | 439.2471 | 321.3418 | 426.3818 | 514.261 | 476.8397 | 476.8397 | 476.8397 | 476.8397 | 476.8397 | 476.8397 | 476.8397 | 476.8397 | 476.8397 | 476.8397 | 476.8397 | 476.8397 | 476.8397 | 476.8397 | 476.8397 | 476.8397
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | 0.66733 | 1.7156 | 1.8209 | 1.7693 | 1.8184 | 1.8385 | 1.9032 | 2.0361 | 2.1479 | 2.1994 | 2.1535 | 2.3459 | 2.3764 | 2.3403 | 2.4127 | 2.4541 | 2.4541 | 2.4541 | 2.4541 | 2.4541 | 2.4541 | 2.4541 | 2.4541 | 2.4541 | 2.4541 | 2.4541 | 2.4541 | 2.4541 | 2.4541 | 2.4541 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
98% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
97% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 3.5495 | 4.6974 | 4.7291 | 4.6949 | 4.7037 | 4.7664 | 4.8934 | 5.1171 | 5.2337 | 5.318 | 5.4457 | 5.6087 | 5.8057 | 5.909 | 5.8755 | 5.9161 | 5.9161 | 5.9161 | 5.9161 | 5.9161 | 5.9161 | 5.9161 | 5.9161 | 5.9161 | 5.9161 | 5.9161 | 5.9161 | 5.9161 | 5.9161 | 5.9161
95% | 0.17429 | 1.1856 | 1.2873 | 1.2375 | 1.2848 | 1.3043 | 1.3667 | 1.4949 | 1.6028 | 1.6525 | 1.6082 | 1.7938 | 1.8233 | 1.7884 | 1.8583 | 1.8982 | 1.8982 | 1.8982 | 1.8982 | 1.8982 | 1.8982 | 1.8982 | 1.8982 | 1.8982 | 1.8982 | 1.8982 | 1.8982 | 1.8982 | 1.8982 | 1.8982 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
90% | 0.017439 | 14.426 | 16.5803 | 15.5243 | 16.5284 | 16.941 | 18.2632 | 20.9821 | 23.2693 | 24.3221 | 23.3837 | 27.3182 | 27.9422 | 27.2037 | 28.6845 | 29.531 | 29.531 | 29.531 | 29.531 | 29.531 | 29.531 | 29.531 | 29.531 | 29.531 | 29.531 | 29.531 | 29.531 | 29.531 | 29.531 | 29.531 |  | 2.6829 | 3.7719 | 3.802 | 3.7696 | 3.7779 | 3.8374 | 3.9579 | 4.1701 | 4.2807 | 4.3608 | 4.4819 | 4.6365 | 4.8234 | 4.9214 | 4.8896 | 4.9281 | 4.9281 | 4.9281 | 4.9281 | 4.9281 | 4.9281 | 4.9281 | 4.9281 | 4.9281 | 4.9281 | 4.9281 | 4.9281 | 4.9281 | 4.9281 | 4.9281
85% |  | 4.2128 | 7.5535 | 5.7978 | 7.4619 | 8.2047 | 10.815 | 17.2668 | 23.8022 | 27.1443 | 24.1554 | 37.602 | 39.829 | 37.1935 | 42.4782 | 45.4993 | 45.4993 | 45.4993 | 45.4993 | 45.4993 | 45.4993 | 45.4993 | 45.4993 | 45.4993 | 45.4993 | 45.4993 | 45.4993 | 45.4993 | 45.4993 | 45.4993 |  | 1.8163 | 2.8464 | 2.8749 | 2.8442 | 2.8521 | 2.9084 | 3.0224 | 3.2232 | 3.3278 | 3.4035 | 3.518 | 3.6643 | 3.8411 | 3.9338 | 3.9037 | 3.9401 | 3.9401 | 3.9401 | 3.9401 | 3.9401 | 3.9401 | 3.9401 | 3.9401 | 3.9401 | 3.9401 | 3.9401 | 3.9401 | 3.9401 | 3.9401 | 3.9401
80% | [11 empty] | 0.31223 | 0.64989 | 0.26352 | 1.2096 | 2.056 | 2.056 | 2.056 | 2.056 | 2.056 | 2.056 | 2.056 | 2.056 | 2.056 | 2.056 | 2.056 | 2.056 | 2.056 | 2.056 | 2.056 |  | 3.7987 | 7.6839 | 7.7911 | 7.6755 | 7.7053 | 7.9174 | 8.3474 | 9.1046 | 9.4992 | 9.7847 | 10.2167 | 10.7682 | 11.4352 | 11.7847 | 11.6714 | 11.8087 | 11.8087 | 11.8087 | 11.8087 | 11.8087 | 11.8087 | 11.8087 | 11.8087 | 11.8087 | 11.8087 | 11.8087 | 11.8087 | 11.8087 | 11.8087 | 11.8087
75% | [31 empty] | 0.30768 | 1.991 | 2.0414 | 1.9871 | 2.0011 | 2.1007 | 2.3027 | 2.6583 | 2.8437 | 2.9777 | 3.1807 | 3.4397 | 3.753 | 3.9172 | 3.8639 | 3.9284 | 3.9284 | 3.9284 | 3.9284 | 3.9284 | 3.9284 | 3.9284 | 3.9284 | 3.9284 | 3.9284 | 3.9284 | 3.9284 | 3.9284 | 3.9284 | 3.9284
70% | [32 empty] | 0.92015 | 1.0045 | 0.91371 | 0.93666 | 1.1084 | 1.4984 | 2.3195 | 2.8134 | 3.1894 | 3.7589 | 4.486 | 5.3652 | 5.8259 | 5.6765 | 5.8575 | 5.8575 | 5.8575 | 5.8575 | 5.8575 | 5.8575 | 5.8575 | 5.8575 | 5.8575 | 5.8575 | 5.8575 | 5.8575 | 5.8575 | 5.8575 | 5.8575
65% | [40 empty] | 0.0029263 | 0.021684 | 0.070373 | 0.16537 | 0.23056 | 0.20828 | 0.23542 | 0.23542 | 0.23542 | 0.23542 | 0.23542 | 0.23542 | 0.23542 | 0.23542 | 0.23542 | 0.23542 | 0.23542 | 0.23542 | 0.23542 | 0.23542 | 0.23542
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0.85046 | 21.3245 | 26.9695 | 24.0856 | 26.8226 | 28.0056 | 32.0245 | 41.3621 | 50.314 | 54.7652 | 50.7878 | 68.6784 | 71.8945 | 68.1016 | 75.8769 | 80.6243 | 80.6243 | 80.6243 | 80.6243 | 80.6243 | 80.6243 | 80.6243 | 80.6243 | 80.6243 | 80.6243 | 80.6243 | 80.6243 | 80.6243 | 80.6243 | 80.6243 | E @ R (MWh) | 12.0334 | 21.6917 | 22.0205 | 21.6662 | 21.7569 | 22.4122 | 23.782 | 26.327 | 27.7185 | 28.7467 | 30.3173 | 32.3469 | 34.837 | 36.1573 | 35.7281 | 36.2482 | 36.2482 | 36.2482 | 36.2482 | 36.2482 | 36.2482 | 36.2482 | 36.2482 | 36.2482 | 36.2482 | 36.2482 | 36.2482 | 36.2482 | 36.2482 | 36.2482
Option 7 Summer POE50 W E @ R (MWh) N 1 | 0.59532 | 14.9272 | 18.8787 | 16.8599 | 18.7758 | 19.6039 | 22.4172 | 28.9535 | 35.2198 | 38.3356 | 35.5515 | 48.0749 | 50.3262 | 47.6711 | 53.1139 | 56.437 | 56.437 | 56.437 | 56.437 | 56.437 | 56.437 | 56.437 | 56.437 | 56.437 | 56.437 | 56.437 | 56.437 | 56.437 | 56.437 | 56.437 | Option 7 Summer POE10 W E @ R (MWh) N 1 | 3.61 | 6.5075 | 6.6061 | 6.4999 | 6.5271 | 6.7237 | 7.1346 | 7.8981 | 8.3155 | 8.624 | 9.0952 | 9.7041 | 10.4511 | 10.8472 | 10.7184 | 10.8744 | 10.8744 | 10.8744 | 10.8744 | 10.8744 | 10.8744 | 10.8744 | 10.8744 | 10.8744 | 10.8744 | 10.8744 | 10.8744 | 10.8744 | 10.8744 | 10.8744
Option 8 -
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% |  | 0.85477 | 0.97121 | 1.1152 | 1.3063 | 1.4875 | 1.8041 | 2.6005 | 3.0288 | 2.7163 | 3.6838 | 3.8581 | 3.9834 | 4.574 | 4.6701 | 4.6701 | 4.6701 | 4.6701 | 4.6701 | 4.6701 | 4.6701 | 4.6701 | 4.6701 | 4.6701 | 4.6701 | 4.6701 | 4.6701 | 4.6701 | 4.6701 | 4.6701 |  | 0.76588 | 1.8133 | 1.9218 | 2.2961 | 2.287 | 2.3693 | 2.6912 | 3.6162 | 3.9979 | 3.6366 | 4.6346 | 4.2156 | 4.5926 | 4.8643 | 4.7527 | 4.7527 | 4.7527 | 4.7527 | 4.7527 | 4.7527 | 4.7527 | 4.7527 | 4.7527 | 4.7527 | 4.7527 | 4.7527 | 4.7527 | 4.7527 | 4.7527 | 4.7527
98% |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
97% |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
95% |  | 1.7892 | 2.2386 | 2.7941 | 3.5317 | 4.231 | 5.453 | 8.5265 | 10.1796 | 8.9736 | 12.7072 | 13.3799 | 13.8635 | 16.1428 | 16.5138 | 16.5138 | 16.5138 | 16.5138 | 16.5138 | 16.5138 | 16.5138 | 16.5138 | 16.5138 | 16.5138 | 16.5138 | 16.5138 | 16.5138 | 16.5138 | 16.5138 | 16.5138 |  | 1.4462 | 5.4884 | 5.907 | 7.3517 | 7.3165 | 7.6342 | 8.8767 | 12.4463 | 13.9194 | 12.525 | 16.3768 | 14.7596 | 16.2148 | 17.2634 | 16.8326 | 16.8326 | 16.8326 | 16.8326 | 16.8326 | 16.8326 | 16.8326 | 16.8326 | 16.8326 | 16.8326 | 16.8326 | 16.8326 | 16.8326 | 16.8326 | 16.8326 | 16.8326
90% |  | 2.2571 | 3.9884 | 6.7708 | 11.03 | 15.0726 | 22.1375 | 39.906 | 49.4631 | 42.4909 | 64.076 | 67.965 | 70.7605 | 83.9378 | 86.0827 | 86.0827 | 86.0827 | 86.0827 | 86.0827 | 86.0827 | 86.0827 | 86.0827 | 86.0827 | 86.0827 | 86.0827 | 86.0827 | 86.0827 | 86.0827 | 86.0827 | 86.0827 |  | 1.2574 | 22.3422 | 24.7623 | 33.1144 | 32.9108 | 34.7474 | 41.9304 | 62.5676 | 71.0837 | 63.0226 | 85.2907 | 75.9414 | 84.3539 | 90.4161 | 87.9254 | 87.9254 | 87.9254 | 87.9254 | 87.9254 | 87.9254 | 87.9254 | 87.9254 | 87.9254 | 87.9254 | 87.9254 | 87.9254 | 87.9254 | 87.9254 | 87.9254 | 87.9254
85% |  |  |  |  | 2.1655 | 8.9007 | 31.0571 | 105.2507 | 145.1799 | 116.0504 | 206.2313 | 222.4792 | 234.1587 | 289.2127 | 298.1738 | 298.1738 | 298.1738 | 298.1738 | 298.1738 | 298.1738 | 298.1738 | 298.1738 | 298.1738 | 298.1738 | 298.1738 | 298.1738 | 298.1738 | 298.1738 | 298.1738 | 298.1738 |  |  | 31.8883 | 41.9816 | 76.8759 | 76.0255 | 83.6985 | 113.7089 | 199.9294 | 235.5092 | 201.8302 | 294.8651 | 255.804 | 290.9508 | 316.2783 | 305.8726 | 305.8726 | 305.8726 | 305.8726 | 305.8726 | 305.8726 | 305.8726 | 305.8726 | 305.8726 | 305.8726 | 305.8726 | 305.8726 | 305.8726 | 305.8726 | 305.8726 | 305.8726
80% | [7 empty] | 57.5329 | 120.7337 | 74.6133 | 217.3957 | 243.1208 | 261.6129 | 348.7792 | 362.9672 | 362.9672 | 362.9672 | 362.9672 | 362.9672 | 362.9672 | 362.9672 | 362.9672 | 362.9672 | 362.9672 | 362.9672 | 362.9672 | 362.9672 | 362.9672 | 362.9672 | 362.9672 |  |  |  | 0.8561 | 21.5377 | 20.7169 | 28.6755 | 70.906 | 207.4181 | 263.7511 | 210.4275 | 357.7285 | 295.8836 | 351.5311 | 391.6319 | 375.1566 | 375.1566 | 375.1566 | 375.1566 | 375.1566 | 375.1566 | 375.1566 | 375.1566 | 375.1566 | 375.1566 | 375.1566 | 375.1566 | 375.1566 | 375.1566 | 375.1566 | 375.1566
75% | [8 empty] | 28.0034 | 1.7144 | 173.9745 | 221.4919 | 255.6491 | 416.656 | 442.8629 | 442.8629 | 442.8629 | 442.8629 | 442.8629 | 442.8629 | 442.8629 | 442.8629 | 442.8629 | 442.8629 | 442.8629 | 442.8629 | 442.8629 | 442.8629 | 442.8629 | 442.8629 | [7 empty] | 0.97067 | 155.5446 | 259.5988 | 161.1034 | 433.1866 | 318.9513 | 421.7392 | 495.8103 | 465.3784 | 465.3784 | 465.3784 | 465.3784 | 465.3784 | 465.3784 | 465.3784 | 465.3784 | 465.3784 | 465.3784 | 465.3784 | 465.3784 | 465.3784 | 465.3784 | 465.3784 | 465.3784
70% | [10 empty] | 7.6559 | 29.4651 | 53.6075 | 256.6677 | 299.3259 | 299.3259 | 299.3259 | 299.3259 | 299.3259 | 299.3259 | 299.3259 | 299.3259 | 299.3259 | 299.3259 | 299.3259 | 299.3259 | 299.3259 | 299.3259 | 299.3259 | 299.3259 | [8 empty] | 2.9795 | 56.8461 | 4.1639 | 283.5753 | 116.4036 | 264.9419 | 385.5105 | 335.9752 | 335.9752 | 335.9752 | 335.9752 | 335.9752 | 335.9752 | 335.9752 | 335.9752 | 335.9752 | 335.9752 | 335.9752 | 335.9752 | 335.9752 | 335.9752 | 335.9752 | 335.9752
65% | FY38: 0.7116; FY39: 5.6622; FY40: 5.6622; FY41: 5.6622; FY42: 5.6622; FY43: 5.6622; FY44: 5.6622; FY45: 5.6622; FY46: 5.6622; FY47: 5.6622; FY48: 5.6622; FY49: 5.6622; FY50: 5.6622; FY51: 5.6622; FY52: 5.6622; FY53: 5.6622; FY54: 5.6622 | [11 empty] | 3.2889 |  | 1.3047 | 29.7436 | 13.6273 | 13.6273 | 13.6273 | 13.6273 | 13.6273 | 13.6273 | 13.6273 | 13.6273 | 13.6273 | 13.6273 | 13.6273 | 13.6273 | 13.6273 | 13.6273 | 13.6273 | 13.6273
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 4.8521 | 7.1262 | 10.5732 | 17.8532 | 29.3949 | 59.8472 | 211.6784 | 353.0228 | 244.0934 | 678.8671 | 793.7423 | 884.6991 | 1402.5149 | 1501.096 | 1501.096 | 1501.096 | 1501.096 | 1501.096 | 1501.096 | 1501.096 | 1501.096 | 1501.096 | 1501.096 | 1501.096 | 1501.096 | 1501.096 | 1501.096 | 1501.096 | 1501.096 | E @ R (MWh) | 3.4348 | 60.9169 | 74.6745 | 139.764 | 137.8641 | 155.5536 | 236.6931 | 638.0567 | 895.6592 | 650.1421 | 1464.157 | 1071.1395 | 1421.2727 | 1714.2032 | 1589.4656 | 1589.4656 | 1589.4656 | 1589.4656 | 1589.4656 | 1589.4656 | 1589.4656 | 1589.4656 | 1589.4656 | 1589.4656 | 1589.4656 | 1589.4656 | 1589.4656 | 1589.4656 | 1589.4656 | 1589.4656
Option 8 Winter POE50 W E @ R (MWh) N 1 | 0 | 3.3964 | 4.9884 | 7.4013 | 12.4972 | 20.5764 | 41.893 | 148.1749 | 247.1159 | 170.8654 | 475.207 | 555.6196 | 619.2894 | 981.7605 | 1050.7672 | 1050.7672 | 1050.7672 | 1050.7672 | 1050.7672 | 1050.7672 | 1050.7672 | 1050.7672 | 1050.7672 | 1050.7672 | 1050.7672 | 1050.7672 | 1050.7672 | 1050.7672 | 1050.7672 | 1050.7672 | Option 8 Winter POE10 W E @ R (MWh) N 1 | 1.0304 | 18.2751 | 22.4024 | 41.9292 | 41.3592 | 46.6661 | 71.0079 | 191.417 | 268.6977 | 195.0426 | 439.2471 | 321.3418 | 426.3818 | 514.261 | 476.8397 | 476.8397 | 476.8397 | 476.8397 | 476.8397 | 476.8397 | 476.8397 | 476.8397 | 476.8397 | 476.8397 | 476.8397 | 476.8397 | 476.8397 | 476.8397 | 476.8397 | 476.8397
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | 0.66733 | 1.7156 | 1.8209 | 1.7693 | 1.8184 | 1.8385 | 1.9032 | 2.0361 | 2.1479 | 2.1994 | 2.1535 | 2.3459 | 2.3764 | 2.3403 | 2.4127 | 2.4541 | 2.4541 | 2.4541 | 2.4541 | 2.4541 | 2.4541 | 2.4541 | 2.4541 | 2.4541 | 2.4541 | 2.4541 | 2.4541 | 2.4541 | 2.4541 | 2.4541 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
98% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
97% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 3.5495 | 4.6974 | 4.7291 | 4.6949 | 4.7037 | 4.7664 | 4.8934 | 5.1171 | 5.2337 | 5.318 | 5.4457 | 5.6087 | 5.8057 | 5.909 | 5.8755 | 5.9161 | 5.9161 | 5.9161 | 5.9161 | 5.9161 | 5.9161 | 5.9161 | 5.9161 | 5.9161 | 5.9161 | 5.9161 | 5.9161 | 5.9161 | 5.9161 | 5.9161
95% | 0.17429 | 1.1856 | 1.2873 | 1.2375 | 1.2848 | 1.3043 | 1.3667 | 1.4949 | 1.6028 | 1.6525 | 1.6082 | 1.7938 | 1.8233 | 1.7884 | 1.8583 | 1.8982 | 1.8982 | 1.8982 | 1.8982 | 1.8982 | 1.8982 | 1.8982 | 1.8982 | 1.8982 | 1.8982 | 1.8982 | 1.8982 | 1.8982 | 1.8982 | 1.8982 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
90% | 0.017439 | 14.426 | 16.5803 | 15.5243 | 16.5284 | 16.941 | 18.2632 | 20.9821 | 23.2693 | 24.3221 | 23.3837 | 27.3182 | 27.9422 | 27.2037 | 28.6845 | 29.531 | 29.531 | 29.531 | 29.531 | 29.531 | 29.531 | 29.531 | 29.531 | 29.531 | 29.531 | 29.531 | 29.531 | 29.531 | 29.531 | 29.531 |  | 2.6829 | 3.7719 | 3.802 | 3.7696 | 3.7779 | 3.8374 | 3.9579 | 4.1701 | 4.2807 | 4.3608 | 4.4819 | 4.6365 | 4.8234 | 4.9214 | 4.8896 | 4.9281 | 4.9281 | 4.9281 | 4.9281 | 4.9281 | 4.9281 | 4.9281 | 4.9281 | 4.9281 | 4.9281 | 4.9281 | 4.9281 | 4.9281 | 4.9281 | 4.9281
85% |  | 4.2128 | 7.5535 | 5.7978 | 7.4619 | 8.2047 | 10.815 | 17.2668 | 23.8022 | 27.1443 | 24.1554 | 37.602 | 39.829 | 37.1935 | 42.4782 | 45.4993 | 45.4993 | 45.4993 | 45.4993 | 45.4993 | 45.4993 | 45.4993 | 45.4993 | 45.4993 | 45.4993 | 45.4993 | 45.4993 | 45.4993 | 45.4993 | 45.4993 |  | 1.8163 | 2.8464 | 2.8749 | 2.8442 | 2.8521 | 2.9084 | 3.0224 | 3.2232 | 3.3278 | 3.4035 | 3.518 | 3.6643 | 3.8411 | 3.9338 | 3.9037 | 3.9401 | 3.9401 | 3.9401 | 3.9401 | 3.9401 | 3.9401 | 3.9401 | 3.9401 | 3.9401 | 3.9401 | 3.9401 | 3.9401 | 3.9401 | 3.9401 | 3.9401
80% | [11 empty] | 0.31223 | 0.64989 | 0.26352 | 1.2096 | 2.056 | 2.056 | 2.056 | 2.056 | 2.056 | 2.056 | 2.056 | 2.056 | 2.056 | 2.056 | 2.056 | 2.056 | 2.056 | 2.056 | 2.056 |  | 3.7987 | 7.6839 | 7.7911 | 7.6755 | 7.7053 | 7.9174 | 8.3474 | 9.1046 | 9.4992 | 9.7847 | 10.2167 | 10.7682 | 11.4352 | 11.7847 | 11.6714 | 11.8087 | 11.8087 | 11.8087 | 11.8087 | 11.8087 | 11.8087 | 11.8087 | 11.8087 | 11.8087 | 11.8087 | 11.8087 | 11.8087 | 11.8087 | 11.8087 | 11.8087
75% | [31 empty] | 0.30768 | 1.991 | 2.0414 | 1.9871 | 2.0011 | 2.1007 | 2.3027 | 2.6583 | 2.8437 | 2.9777 | 3.1807 | 3.4397 | 3.753 | 3.9172 | 3.8639 | 3.9284 | 3.9284 | 3.9284 | 3.9284 | 3.9284 | 3.9284 | 3.9284 | 3.9284 | 3.9284 | 3.9284 | 3.9284 | 3.9284 | 3.9284 | 3.9284 | 3.9284
70% | [32 empty] | 0.92015 | 1.0045 | 0.91371 | 0.93666 | 1.1084 | 1.4984 | 2.3195 | 2.8134 | 3.1894 | 3.7589 | 4.486 | 5.3652 | 5.8259 | 5.6765 | 5.8575 | 5.8575 | 5.8575 | 5.8575 | 5.8575 | 5.8575 | 5.8575 | 5.8575 | 5.8575 | 5.8575 | 5.8575 | 5.8575 | 5.8575 | 5.8575 | 5.8575
65% | [40 empty] | 0.0029263 | 0.021684 | 0.070373 | 0.16537 | 0.23056 | 0.20828 | 0.23542 | 0.23542 | 0.23542 | 0.23542 | 0.23542 | 0.23542 | 0.23542 | 0.23542 | 0.23542 | 0.23542 | 0.23542 | 0.23542 | 0.23542 | 0.23542 | 0.23542
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0.85046 | 21.3245 | 26.9695 | 24.0856 | 26.8226 | 28.0056 | 32.0245 | 41.3621 | 50.314 | 54.7652 | 50.7878 | 68.6784 | 71.8945 | 68.1016 | 75.8769 | 80.6243 | 80.6243 | 80.6243 | 80.6243 | 80.6243 | 80.6243 | 80.6243 | 80.6243 | 80.6243 | 80.6243 | 80.6243 | 80.6243 | 80.6243 | 80.6243 | 80.6243 | E @ R (MWh) | 12.0334 | 21.6917 | 22.0205 | 21.6662 | 21.7569 | 22.4122 | 23.782 | 26.327 | 27.7185 | 28.7467 | 30.3173 | 32.3469 | 34.837 | 36.1573 | 35.7281 | 36.2482 | 36.2482 | 36.2482 | 36.2482 | 36.2482 | 36.2482 | 36.2482 | 36.2482 | 36.2482 | 36.2482 | 36.2482 | 36.2482 | 36.2482 | 36.2482 | 36.2482
Option 8 Summer POE50 W E @ R (MWh) N 1 | 0.59532 | 14.9272 | 18.8787 | 16.8599 | 18.7758 | 19.6039 | 22.4172 | 28.9535 | 35.2198 | 38.3356 | 35.5515 | 48.0749 | 50.3262 | 47.6711 | 53.1139 | 56.437 | 56.437 | 56.437 | 56.437 | 56.437 | 56.437 | 56.437 | 56.437 | 56.437 | 56.437 | 56.437 | 56.437 | 56.437 | 56.437 | 56.437 | Option 8 Summer POE10 W E @ R (MWh) N 1 | 3.61 | 6.5075 | 6.6061 | 6.4999 | 6.5271 | 6.7237 | 7.1346 | 7.8981 | 8.3155 | 8.624 | 9.0952 | 9.7041 | 10.4511 | 10.8472 | 10.7184 | 10.8744 | 10.8744 | 10.8744 | 10.8744 | 10.8744 | 10.8744 | 10.8744 | 10.8744 | 10.8744 | 10.8744 | 10.8744 | 10.8744 | 10.8744 | 10.8744 | 10.8744

## E@R N-2
Option 1 - Do Nothing
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | 5.1211 | 6.2192 | 6.3356 | 6.4796 | 6.6707 | 6.8519 | 7.1685 | 7.9649 | 8.3933 | 8.0808 | 9.0482 | 9.2225 | 9.3478 | 9.9384 | 10.0346 | 10.0346 | 10.0346 | 10.0346 | 10.0346 | 10.0346 | 10.0346 | 10.0346 | 10.0346 | 10.0346 | 10.0346 | 10.0346 | 10.0346 | 10.0346 | 10.0346 | 10.0346 |  | 6.1303 | 7.1777 | 7.2862 | 7.6605 | 7.6514 | 7.7337 | 8.0557 | 8.9806 | 9.3623 | 9.001 | 9.9991 | 9.58 | 9.9571 | 10.2288 | 10.1171 | 10.1171 | 10.1171 | 10.1171 | 10.1171 | 10.1171 | 10.1171 | 10.1171 | 10.1171 | 10.1171 | 10.1171 | 10.1171 | 10.1171 | 10.1171 | 10.1171 | 10.1171
98% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
97% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
95% | 19.0092 | 23.247 | 23.6963 | 24.2519 | 24.9895 | 25.6887 | 26.9107 | 29.9842 | 31.6373 | 30.4313 | 34.165 | 34.8377 | 35.3212 | 37.6005 | 37.9715 | 37.9715 | 37.9715 | 37.9715 | 37.9715 | 37.9715 | 37.9715 | 37.9715 | 37.9715 | 37.9715 | 37.9715 | 37.9715 | 37.9715 | 37.9715 | 37.9715 | 37.9715 |  | 22.9039 | 26.9462 | 27.3648 | 28.8095 | 28.7742 | 29.0919 | 30.3344 | 33.9041 | 35.3771 | 33.9828 | 37.8346 | 36.2174 | 37.6725 | 38.7211 | 38.2903 | 38.2903 | 38.2903 | 38.2903 | 38.2903 | 38.2903 | 38.2903 | 38.2903 | 38.2903 | 38.2903 | 38.2903 | 38.2903 | 38.2903 | 38.2903 | 38.2903 | 38.2903
90% | 105.2028 | 129.7026 | 132.3005 | 135.5122 | 139.7764 | 143.8191 | 150.8839 | 168.6524 | 178.2095 | 171.2373 | 192.8224 | 196.7114 | 199.5069 | 212.6842 | 214.8291 | 214.8291 | 214.8291 | 214.8291 | 214.8291 | 214.8291 | 214.8291 | 214.8291 | 214.8291 | 214.8291 | 214.8291 | 214.8291 | 214.8291 | 214.8291 | 214.8291 | 214.8291 |  | 127.7194 | 151.0886 | 153.5087 | 161.8608 | 161.6572 | 163.4938 | 170.6769 | 191.314 | 199.8301 | 191.769 | 214.0372 | 204.6878 | 213.1003 | 219.1625 | 216.6718 | 216.6718 | 216.6718 | 216.6718 | 216.6718 | 216.6718 | 216.6718 | 216.6718 | 216.6718 | 216.6718 | 216.6718 | 216.6718 | 216.6718 | 216.6718 | 216.6718 | 216.6718
85% | 408.7931 | 511.1512 | 522.005 | 535.4235 | 553.2391 | 570.1289 | 599.6452 | 673.8807 | 713.8099 | 684.6804 | 774.8612 | 791.1091 | 802.7887 | 857.8426 | 866.8037 | 866.8037 | 866.8037 | 866.8037 | 866.8037 | 866.8037 | 866.8037 | 866.8037 | 866.8037 | 866.8037 | 866.8037 | 866.8037 | 866.8037 | 866.8037 | 866.8037 | 866.8037 |  | 502.8656 | 600.5006 | 610.6116 | 645.5059 | 644.6555 | 652.3285 | 682.3388 | 768.5594 | 804.1392 | 770.4602 | 863.495 | 824.4339 | 859.5808 | 884.9083 | 874.5026 | 874.5026 | 874.5026 | 874.5026 | 874.5026 | 874.5026 | 874.5026 | 874.5026 | 874.5026 | 874.5026 | 874.5026 | 874.5026 | 874.5026 | 874.5026 | 874.5026 | 874.5026
80% | 592.6734 | 754.7359 | 771.9205 | 793.1658 | 821.3732 | 848.1145 | 894.8474 | 1012.3836 | 1075.6029 | 1029.4825 | 1172.2649 | 1197.99 | 1216.482 | 1303.6484 | 1317.8363 | 1317.8363 | 1317.8363 | 1317.8363 | 1317.8363 | 1317.8363 | 1317.8363 | 1317.8363 | 1317.8363 | 1317.8363 | 1317.8363 | 1317.8363 | 1317.8363 | 1317.8363 | 1317.8363 | 1317.8363 |  | 741.6174 | 896.2017 | 912.2103 | 967.4581 | 966.1116 | 978.2602 | 1025.7752 | 1162.2872 | 1218.6203 | 1165.2967 | 1312.5977 | 1250.7528 | 1306.4003 | 1346.5011 | 1330.0258 | 1330.0258 | 1330.0258 | 1330.0258 | 1330.0258 | 1330.0258 | 1330.0258 | 1330.0258 | 1330.0258 | 1330.0258 | 1330.0258 | 1330.0258 | 1330.0258 | 1330.0258 | 1330.0258 | 1330.0258
75% | 980.9496 | 1280.2989 | 1312.0411 | 1351.2837 | 1403.3862 | 1452.7807 | 1539.1021 | 1756.2058 | 1872.9798 | 1787.7897 | 2051.5263 | 2099.0437 | 2133.2008 | 2294.2077 | 2320.4147 | 2320.4147 | 2320.4147 | 2320.4147 | 2320.4147 | 2320.4147 | 2320.4147 | 2320.4147 | 2320.4147 | 2320.4147 | 2320.4147 | 2320.4147 | 2320.4147 | 2320.4147 | 2320.4147 | 2320.4147 |  | 1256.0675 | 1541.6038 | 1571.1735 | 1673.2229 | 1670.7358 | 1693.1758 | 1780.9419 | 2033.0964 | 2137.1505 | 2038.6552 | 2310.7383 | 2196.5031 | 2299.291 | 2373.362 | 2342.9301 | 2342.9301 | 2342.9301 | 2342.9301 | 2342.9301 | 2342.9301 | 2342.9301 | 2342.9301 | 2342.9301 | 2342.9301 | 2342.9301 | 2342.9301 | 2342.9301 | 2342.9301 | 2342.9301 | 2342.9301
70% | 1385.9626 | 1873.2259 | 1924.894 | 1988.7709 | 2073.5802 | 2153.9818 | 2294.4906 | 2647.8796 | 2837.9574 | 2699.29 | 3128.585 | 3205.9311 | 3261.5301 | 3523.6078 | 3566.266 | 3566.266 | 3566.266 | 3566.266 | 3566.266 | 3566.266 | 3566.266 | 3566.266 | 3566.266 | 3566.266 | 3566.266 | 3566.266 | 3566.266 | 3566.266 | 3566.266 | 3566.266 |  | 1833.7834 | 2298.5628 | 2346.6947 | 2512.8048 | 2508.7564 | 2545.283 | 2688.1435 | 3098.5859 | 3267.9592 | 3107.6342 | 3550.5153 | 3364.5698 | 3531.882 | 3652.4506 | 3602.9153 | 3602.9153 | 3602.9153 | 3602.9153 | 3602.9153 | 3602.9153 | 3602.9153 | 3602.9153 | 3602.9153 | 3602.9153 | 3602.9153 | 3602.9153 | 3602.9153 | 3602.9153 | 3602.9153 | 3602.9153
65% | 1400.8592 | 1997.5436 | 2060.8145 | 2139.0357 | 2242.8901 | 2341.3468 | 2513.4087 | 2946.1556 | 3178.9178 | 3009.1109 | 3534.8094 | 3629.5246 | 3697.6091 | 4018.5396 | 4070.7772 | 4070.7772 | 4070.7772 | 4070.7772 | 4070.7772 | 4070.7772 | 4070.7772 | 4070.7772 | 4070.7772 | 4070.7772 | 4070.7772 | 4070.7772 | 4070.7772 | 4070.7772 | 4070.7772 | 4070.7772 |  | 1949.2438 | 2518.3953 | 2577.3359 | 2780.7481 | 2775.7906 | 2820.5196 | 2995.4612 | 3498.0737 | 3705.4819 | 3509.1539 | 4051.4896 | 3823.7877 | 4028.6719 | 4176.3156 | 4115.6566 | 4115.6566 | 4115.6566 | 4115.6566 | 4115.6566 | 4115.6566 | 4115.6566 | 4115.6566 | 4115.6566 | 4115.6566 | 4115.6566 | 4115.6566 | 4115.6566 | 4115.6566 | 4115.6566 | 4115.6566
60% | 1311.1794 | 2051.2755 | 2129.7534 | 2226.7749 | 2355.5904 | 2477.711 | 2691.1276 | 3227.8842 | 3516.5903 | 3305.9706 | 3958.0197 | 4075.4994 | 4159.9479 | 4558.0133 | 4622.8061 | 4622.8061 | 4622.8061 | 4622.8061 | 4622.8061 | 4622.8061 | 4622.8061 | 4622.8061 | 4622.8061 | 4622.8061 | 4622.8061 | 4622.8061 | 4622.8061 | 4622.8061 | 4622.8061 | 4622.8061 |  | 1991.367 | 2697.3127 | 2770.4195 | 3022.7214 | 3016.5724 | 3072.052 | 3289.0403 | 3912.4546 | 4169.7129 | 3926.1979 | 4598.8827 | 4316.4532 | 4570.5808 | 4753.7104 | 4678.4721 | 4678.4721 | 4678.4721 | 4678.4721 | 4678.4721 | 4678.4721 | 4678.4721 | 4678.4721 | 4678.4721 | 4678.4721 | 4678.4721 | 4678.4721 | 4678.4721 | 4678.4721 | 4678.4721 | 4678.4721
55% | 879.254 | 1681.979 | 1767.0979 | 1872.3296 | 2012.0458 | 2144.5006 | 2375.977 | 2958.1553 | 3271.2924 | 3042.8496 | 3750.0767 | 3877.4979 | 3969.0926 | 4400.8433 | 4471.1191 | 4471.1191 | 4471.1191 | 4471.1191 | 4471.1191 | 4471.1191 | 4471.1191 | 4471.1191 | 4471.1191 | 4471.1191 | 4471.1191 | 4471.1191 | 4471.1191 | 4471.1191 | 4471.1191 | 4471.1191 |  | 1617.0008 | 2382.6855 | 2461.9788 | 2735.6311 | 2728.9617 | 2789.1362 | 3024.4867 | 3700.6558 | 3979.6839 | 3715.5621 | 4445.1712 | 4138.8418 | 4414.4743 | 4613.1009 | 4531.4957 | 4531.4957 | 4531.4957 | 4531.4957 | 4531.4957 | 4531.4957 | 4531.4957 | 4531.4957 | 4531.4957 | 4531.4957 | 4531.4957 | 4531.4957 | 4531.4957 | 4531.4957 | 4531.4957 | 4531.4957
50% | 249.4213 | 1054.7724 | 1141.4594 | 1248.6298 | 1390.9199 | 1525.8148 | 1761.5555 | 2354.459 | 2673.3649 | 2440.7136 | 3160.9695 | 3290.738 | 3384.0202 | 3823.7248 | 3895.2952 | 3895.2952 | 3895.2952 | 3895.2952 | 3895.2952 | 3895.2952 | 3895.2952 | 3895.2952 | 3895.2952 | 3895.2952 | 3895.2952 | 3895.2952 | 3895.2952 | 3895.2952 | 3895.2952 | 3895.2952 |  | 988.5972 | 1768.3876 | 1849.1417 | 2127.8353 | 2121.0431 | 2182.3261 | 2422.0123 | 3110.6381 | 3394.8066 | 3125.819 | 3868.8693 | 3556.8965 | 3837.6069 | 4039.8926 | 3956.7841 | 3956.7841 | 3956.7841 | 3956.7841 | 3956.7841 | 3956.7841 | 3956.7841 | 3956.7841 | 3956.7841 | 3956.7841 | 3956.7841 | 3956.7841 | 3956.7841 | 3956.7841 | 3956.7841 | 3956.7841
45% |  | 263.6586 | 332.2401 | 426.8754 | 561.1949 | 688.6055 | 911.2667 | 1471.2745 | 1772.4867 | 1552.7434 | 2233.0378 | 2355.6065 | 2443.7131 | 2859.0218 | 2926.6213 | 2926.6213 | 2926.6213 | 2926.6213 | 2926.6213 | 2926.6213 | 2926.6213 | 2926.6213 | 2926.6213 | 2926.6213 | 2926.6213 | 2926.6213 | 2926.6213 | 2926.6213 | 2926.6213 | 2926.6213 |  | 216.2457 | 917.7197 | 993.9934 | 1257.2244 | 1250.8091 | 1308.6919 | 1535.0798 | 2185.4989 | 2453.9011 | 2199.8376 | 2901.6616 | 2606.9978 | 2872.1337 | 3063.1961 | 2984.6986 | 2984.6986 | 2984.6986 | 2984.6986 | 2984.6986 | 2984.6986 | 2984.6986 | 2984.6986 | 2984.6986 | 2984.6986 | 2984.6986 | 2984.6986 | 2984.6986 | 2984.6986 | 2984.6986 | 2984.6986
40% |  |  |  |  | 7.5893 | 31.1945 | 108.8464 | 488.9496 | 760.7952 | 562.4477 | 1176.5041 | 1287.1386 | 1366.6666 | 1741.5381 | 1802.5557 | 1802.5557 | 1802.5557 | 1802.5557 | 1802.5557 | 1802.5557 | 1802.5557 | 1802.5557 | 1802.5557 | 1802.5557 | 1802.5557 | 1802.5557 | 1802.5557 | 1802.5557 | 1802.5557 | 1802.5557 |  |  | 111.7593 | 148.9205 | 314.3792 | 309.6857 | 353.1877 | 546.5039 | 1133.5939 | 1375.8626 | 1146.5364 | 1780.0262 | 1514.0529 | 1753.3734 | 1925.8327 | 1854.9782 | 1854.9782 | 1854.9782 | 1854.9782 | 1854.9782 | 1854.9782 | 1854.9782 | 1854.9782 | 1854.9782 | 1854.9782 | 1854.9782 | 1854.9782 | 1854.9782 | 1854.9782 | 1854.9782 | 1854.9782
35% | [8 empty] | 26.1432 | 1.6005 | 166.5253 | 222.5876 | 267.429 | 526.6894 | 574.0431 | 574.0431 | 574.0431 | 574.0431 | 574.0431 | 574.0431 | 574.0431 | 574.0431 | 574.0431 | 574.0431 | 574.0431 | 574.0431 | 574.0431 | 574.0431 | 574.0431 | 574.0431 | [7 empty] | 0.90619 | 146.8106 | 272.8539 | 152.6356 | 556.5587 | 360.2185 | 535.8744 | 669.7143 | 614.7265 | 614.7265 | 614.7265 | 614.7265 | 614.7265 | 614.7265 | 614.7265 | 614.7265 | 614.7265 | 614.7265 | 614.7265 | 614.7265 | 614.7265 | 614.7265 | 614.7265 | 614.7265
30% | FY38: 0.23254; FY39: 1.8503; FY40: 1.8503; FY41: 1.8503; FY42: 1.8503; FY43: 1.8503; FY44: 1.8503; FY45: 1.8503; FY46: 1.8503; FY47: 1.8503; FY48: 1.8503; FY49: 1.8503; FY50: 1.8503; FY51: 1.8503; FY52: 1.8503; FY53: 1.8503; FY54: 1.8503 | [11 empty] | 1.0747 |  | 0.42635 | 9.7196 | 4.4531 | 4.4531 | 4.4531 | 4.4531 | 4.4531 | 4.4531 | 4.4531 | 4.4531 | 4.4531 | 4.4531 | 4.4531 | 4.4531 | 4.4531 | 4.4531 | 4.4531 | 4.4531
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 7265.0415 | 11511.5317 | 12003.3126 | 12621.0477 | 13457.3132 | 14266.4334 | 15716.478 | 19546.391 | 21698.9988 | 20123.164 | 25089.7832 | 26010.7036 | 26677.1895 | 29866.4513 | 30392.2317 | 30392.2317 | 30392.2317 | 30392.2317 | 30392.2317 | 30392.2317 | 30392.2317 | 30392.2317 | 30392.2317 | 30392.2317 | 30392.2317 | 30392.2317 | 30392.2317 | 30392.2317 | 30392.2317 | 30392.2317 | E @ R (MWh) | 11141.0066 | 15759.1581 | 16266.3334 | 18053.5033 | 18009.2926 | 18409.3276 | 19997.7591 | 24734.6086 | 26754.4944 | 24841.616 | 30197.9216 | 27921.9531 | 29968.3153 | 31459.0485 | 30845.1507 | 30845.1507 | 30845.1507 | 30845.1507 | 30845.1507 | 30845.1507 | 30845.1507 | 30845.1507 | 30845.1507 | 30845.1507 | 30845.1507 | 30845.1507 | 30845.1507 | 30845.1507 | 30845.1507 | 30845.1507
Option 1 Winter POE50 W E @ R (MWh) N 2 | 5085.529 | 8058.0722 | 8402.3188 | 8834.7334 | 9420.1193 | 9986.5034 | 11001.5346 | 13682.4737 | 15189.2992 | 14086.2148 | 17562.8482 | 18207.4925 | 18674.0327 | 20906.5159 | 21274.5622 | 21274.5622 | 21274.5622 | 21274.5622 | 21274.5622 | 21274.5622 | 21274.5622 | 21274.5622 | 21274.5622 | 21274.5622 | 21274.5622 | 21274.5622 | 21274.5622 | 21274.5622 | 21274.5622 | 21274.5622 | Option 1 Winter POE10 W E @ R (MWh) N 2 | 3342.302 | 4727.7474 | 4879.9 | 5416.051 | 5402.7878 | 5522.7983 | 5999.3277 | 7420.3826 | 8026.3483 | 7452.4848 | 9059.3765 | 8376.5859 | 8990.4946 | 9437.7145 | 9253.5452 | 9253.5452 | 9253.5452 | 9253.5452 | 9253.5452 | 9253.5452 | 9253.5452 | 9253.5452 | 9253.5452 | 9253.5452 | 9253.5452 | 9253.5452 | 9253.5452 | 9253.5452 | 9253.5452 | 9253.5452
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | 7.3419 | 8.3902 | 8.4955 | 8.4439 | 8.493 | 8.5131 | 8.5778 | 8.7107 | 8.8225 | 8.874 | 8.8281 | 9.0205 | 9.051 | 9.0149 | 9.0873 | 9.1287 | 9.1287 | 9.1287 | 9.1287 | 9.1287 | 9.1287 | 9.1287 | 9.1287 | 9.1287 | 9.1287 | 9.1287 | 9.1287 | 9.1287 | 9.1287 | 9.1287 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
98% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
97% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 10.2241 | 11.372 | 11.4037 | 11.3695 | 11.3783 | 11.441 | 11.568 | 11.7917 | 11.9083 | 11.9926 | 12.1203 | 12.2833 | 12.4803 | 12.5836 | 12.5501 | 12.5907 | 12.5907 | 12.5907 | 12.5907 | 12.5907 | 12.5907 | 12.5907 | 12.5907 | 12.5907 | 12.5907 | 12.5907 | 12.5907 | 12.5907 | 12.5907 | 12.5907
95% | 6.8489 | 7.8602 | 7.9619 | 7.9121 | 7.9594 | 7.9789 | 8.0413 | 8.1695 | 8.2774 | 8.3271 | 8.2828 | 8.4684 | 8.4979 | 8.463 | 8.5329 | 8.5728 | 8.5728 | 8.5728 | 8.5728 | 8.5728 | 8.5728 | 8.5728 | 8.5728 | 8.5728 | 8.5728 | 8.5728 | 8.5728 | 8.5728 | 8.5728 | 8.5728 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
90% | 139.8285 | 161.2671 | 163.4215 | 162.3655 | 163.3696 | 163.7822 | 165.1044 | 167.8232 | 170.1105 | 171.1633 | 170.2249 | 174.1594 | 174.7834 | 174.0449 | 175.5257 | 176.3722 | 176.3722 | 176.3722 | 176.3722 | 176.3722 | 176.3722 | 176.3722 | 176.3722 | 176.3722 | 176.3722 | 176.3722 | 176.3722 | 176.3722 | 176.3722 | 176.3722 |  | 9.3575 | 10.4465 | 10.4766 | 10.4442 | 10.4525 | 10.512 | 10.6325 | 10.8447 | 10.9553 | 11.0354 | 11.1564 | 11.3111 | 11.498 | 11.596 | 11.5642 | 11.6027 | 11.6027 | 11.6027 | 11.6027 | 11.6027 | 11.6027 | 11.6027 | 11.6027 | 11.6027 | 11.6027 | 11.6027 | 11.6027 | 11.6027 | 11.6027 | 11.6027
85% | 469.0739 | 545.5841 | 553.2725 | 549.5038 | 553.0872 | 554.5596 | 559.2785 | 568.9815 | 577.144 | 580.9015 | 577.5525 | 591.5938 | 593.8207 | 591.1853 | 596.47 | 599.4911 | 599.4911 | 599.4911 | 599.4911 | 599.4911 | 599.4911 | 599.4911 | 599.4911 | 599.4911 | 599.4911 | 599.4911 | 599.4911 | 599.4911 | 599.4911 | 599.4911 |  | 8.4909 | 9.521 | 9.5495 | 9.5188 | 9.5267 | 9.583 | 9.697 | 9.8978 | 10.0024 | 10.0781 | 10.1926 | 10.3389 | 10.5157 | 10.6084 | 10.5783 | 10.6147 | 10.6147 | 10.6147 | 10.6147 | 10.6147 | 10.6147 | 10.6147 | 10.6147 | 10.6147 | 10.6147 | 10.6147 | 10.6147 | 10.6147 | 10.6147 | 10.6147
80% | 707.4418 | 831.7279 | 844.2173 | 838.0953 | 843.9164 | 846.3082 | 853.9736 | 869.7356 | 882.9952 | 889.099 | 883.6587 | 906.4679 | 910.0855 | 905.8043 | 914.3891 | 919.2966 | 919.2966 | 919.2966 | 919.2966 | 919.2966 | 919.2966 | 919.2966 | 919.2966 | 919.2966 | 919.2966 | 919.2966 | 919.2966 | 919.2966 | 919.2966 | 919.2966 |  | 30.4971 | 34.3823 | 34.4895 | 34.3739 | 34.4037 | 34.6158 | 35.0458 | 35.803 | 36.1976 | 36.4831 | 36.9151 | 37.4666 | 38.1336 | 38.4831 | 38.3698 | 38.5071 | 38.5071 | 38.5071 | 38.5071 | 38.5071 | 38.5071 | 38.5071 | 38.5071 | 38.5071 | 38.5071 | 38.5071 | 38.5071 | 38.5071 | 38.5071 | 38.5071
75% | 1149.798 | 1371.0584 | 1393.2926 | 1382.3939 | 1392.7569 | 1397.0149 | 1410.6614 | 1438.7215 | 1462.327 | 1473.1933 | 1463.5082 | 1504.1143 | 1510.5546 | 1502.933 | 1518.216 | 1526.9526 | 1526.9526 | 1526.9526 | 1526.9526 | 1526.9526 | 1526.9526 | 1526.9526 | 1526.9526 | 1526.9526 | 1526.9526 | 1526.9526 | 1526.9526 | 1526.9526 | 1526.9526 | 1526.9526 |  | 13.5153 | 15.3402 | 15.3906 | 15.3363 | 15.3503 | 15.4499 | 15.6519 | 16.0075 | 16.1929 | 16.3269 | 16.5299 | 16.7889 | 17.1022 | 17.2664 | 17.2131 | 17.2776 | 17.2776 | 17.2776 | 17.2776 | 17.2776 | 17.2776 | 17.2776 | 17.2776 | 17.2776 | 17.2776 | 17.2776 | 17.2776 | 17.2776 | 17.2776 | 17.2776
70% | 1309.2261 | 1591.8262 | 1620.2245 | 1606.3043 | 1619.5402 | 1624.9786 | 1642.4083 | 1678.2476 | 1708.3971 | 1722.2759 | 1709.9059 | 1761.7692 | 1769.9948 | 1760.2603 | 1779.7801 | 1790.9388 | 1790.9388 | 1790.9388 | 1790.9388 | 1790.9388 | 1790.9388 | 1790.9388 | 1790.9388 | 1790.9388 | 1790.9388 | 1790.9388 | 1790.9388 | 1790.9388 | 1790.9388 | 1790.9388 |  | 35.3464 | 40.4679 | 40.6092 | 40.4568 | 40.496 | 40.7757 | 41.3425 | 42.3407 | 42.8608 | 43.237 | 43.8065 | 44.5336 | 45.4128 | 45.8735 | 45.7241 | 45.9051 | 45.9051 | 45.9051 | 45.9051 | 45.9051 | 45.9051 | 45.9051 | 45.9051 | 45.9051 | 45.9051 | 45.9051 | 45.9051 | 45.9051 | 45.9051 | 45.9051
65% | 1383.0411 | 1730.0625 | 1764.9344 | 1747.8411 | 1764.0942 | 1770.7723 | 1792.1753 | 1836.1844 | 1873.2068 | 1890.2494 | 1875.0595 | 1938.7455 | 1948.8462 | 1936.8927 | 1960.8622 | 1974.5646 | 1974.5646 | 1974.5646 | 1974.5646 | 1974.5646 | 1974.5646 | 1974.5646 | 1974.5646 | 1974.5646 | 1974.5646 | 1974.5646 | 1974.5646 | 1974.5646 | 1974.5646 | 1974.5646 |  | 10.0489 | 11.6384 | 11.6822 | 11.6349 | 11.6471 | 11.7339 | 11.9098 | 12.2196 | 12.381 | 12.4978 | 12.6745 | 12.9001 | 13.173 | 13.316 | 13.2696 | 13.3258 | 13.3258 | 13.3258 | 13.3258 | 13.3258 | 13.3258 | 13.3258 | 13.3258 | 13.3258 | 13.3258 | 13.3258 | 13.3258 | 13.3258 | 13.3258 | 13.3258
60% | 1639.9094 | 2146.9041 | 2197.8516 | 2172.8784 | 2196.624 | 2206.3807 | 2237.6502 | 2301.9471 | 2356.0365 | 2380.9355 | 2358.7431 | 2451.7877 | 2466.5448 | 2449.0808 | 2484.1001 | 2504.1192 | 2504.1192 | 2504.1192 | 2504.1192 | 2504.1192 | 2504.1192 | 2504.1192 | 2504.1192 | 2504.1192 | 2504.1192 | 2504.1192 | 2504.1192 | 2504.1192 | 2504.1192 | 2504.1192 |  | 54.0524 | 63.6183 | 63.8823 | 63.5977 | 63.6709 | 64.1933 | 65.2519 | 67.1163 | 68.0878 | 68.7906 | 69.8543 | 71.2123 | 72.8544 | 73.715 | 73.436 | 73.774 | 73.774 | 73.774 | 73.774 | 73.774 | 73.774 | 73.774 | 73.774 | 73.774 | 73.774 | 73.774 | 73.774 | 73.774 | 73.774 | 73.774
55% | 1468.1665 | 2092.0991 | 2154.7976 | 2124.0644 | 2153.2869 | 2165.294 | 2203.7758 | 2282.9027 | 2349.4677 | 2380.1097 | 2352.7987 | 2467.304 | 2485.4648 | 2463.9727 | 2507.0692 | 2531.7056 | 2531.7056 | 2531.7056 | 2531.7056 | 2531.7056 | 2531.7056 | 2531.7056 | 2531.7056 | 2531.7056 | 2531.7056 | 2531.7056 | 2531.7056 | 2531.7056 | 2531.7056 | 2531.7056 |  | 210.6416 | 253.9682 | 255.1638 | 253.8747 | 254.2062 | 256.5722 | 261.367 | 269.8113 | 274.2113 | 277.3946 | 282.2122 | 288.363 | 295.8006 | 299.6984 | 298.4348 | 299.9656 | 299.9656 | 299.9656 | 299.9656 | 299.9656 | 299.9656 | 299.9656 | 299.9656 | 299.9656 | 299.9656 | 299.9656 | 299.9656 | 299.9656 | 299.9656 | 299.9656
50% | 922.9519 | 1630.9008 | 1702.042 | 1667.1704 | 1700.3279 | 1713.9518 | 1757.6154 | 1847.3972 | 1922.9257 | 1957.6938 | 1926.7051 | 2056.6293 | 2077.2355 | 2052.8494 | 2101.749 | 2129.7029 | 2129.7029 | 2129.7029 | 2129.7029 | 2129.7029 | 2129.7029 | 2129.7029 | 2129.7029 | 2129.7029 | 2129.7029 | 2129.7029 | 2129.7029 | 2129.7029 | 2129.7029 | 2129.7029 |  | 383.0991 | 480.7604 | 483.4553 | 480.5498 | 481.297 | 486.6301 | 497.438 | 516.4721 | 526.39 | 533.5653 | 544.4247 | 558.2889 | 575.0538 | 583.8398 | 580.9915 | 584.442 | 584.442 | 584.442 | 584.442 | 584.442 | 584.442 | 584.442 | 584.442 | 584.442 | 584.442 | 584.442 | 584.442 | 584.442 | 584.442 | 584.442
45% | 113.1135 | 605.5456 | 664.4302 | 635.5664 | 663.0115 | 674.2882 | 710.4292 | 784.743 | 847.2591 | 876.0372 | 850.3875 | 957.9277 | 974.9838 | 954.799 | 995.274 | 1018.4119 | 1018.4119 | 1018.4119 | 1018.4119 | 1018.4119 | 1018.4119 | 1018.4119 | 1018.4119 | 1018.4119 | 1018.4119 | 1018.4119 | 1018.4119 | 1018.4119 | 1018.4119 | 1018.4119 |  | 467.4239 | 635.1966 | 639.8262 | 634.8348 | 636.1184 | 645.2801 | 663.8471 | 696.5457 | 713.5838 | 725.9102 | 744.5656 | 768.3829 | 797.1834 | 812.2769 | 807.3838 | 813.3115 | 813.3115 | 813.3115 | 813.3115 | 813.3115 | 813.3115 | 813.3115 | 813.3115 | 813.3115 | 813.3115 | 813.3115 | 813.3115 | 813.3115 | 813.3115 | 813.3115
40% |  | 11.9277 | 21.3864 | 16.4156 | 21.1271 | 23.2302 | 30.6206 | 48.888 | 67.3917 | 76.8544 | 68.3917 | 106.9766 | 113.8368 | 105.7399 | 122.2575 | 132.2021 | 132.2021 | 132.2021 | 132.2021 | 132.2021 | 132.2021 | 132.2021 | 132.2021 | 132.2021 | 132.2021 | 132.2021 | 132.2021 | 132.2021 | 132.2021 | 132.2021 |  | 313.9328 | 541.1029 | 547.3715 | 540.613 | 542.3511 | 554.7563 | 579.8966 | 624.1718 | 647.2418 | 663.9323 | 689.1923 | 721.4418 | 760.4386 | 780.8759 | 774.2504 | 782.2767 | 782.2767 | 782.2767 | 782.2767 | 782.2767 | 782.2767 | 782.2767 | 782.2767 | 782.2767 | 782.2767 | 782.2767 | 782.2767 | 782.2767 | 782.2767 | 782.2767
35% | [31 empty] | 32.1525 | 240.1146 | 248.3143 | 239.479 | 241.7375 | 258.1321 | 292.8244 | 358.5913 | 395.1611 | 422.2729 | 463.3148 | 515.7129 | 579.0739 | 612.2797 | 601.5148 | 614.5558 | 614.5558 | 614.5558 | 614.5558 | 614.5558 | 614.5558 | 614.5558 | 614.5558 | 614.5558 | 614.5558 | 614.5558 | 614.5558 | 614.5558 | 614.5558 | 614.5558
30% | [40 empty] | 0.54575 | 4.0441 | 13.1246 | 30.8413 | 43.0003 | 38.845 | 43.905 | 43.905 | 43.905 | 43.905 | 43.905 | 43.905 | 43.905 | 43.905 | 43.905 | 43.905 | 43.905 | 43.905 | 43.905 | 43.905 | 43.905
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 9223.5741 | 12607.8025 | 12965.3646 | 12789.7654 | 12956.7185 | 13025.4821 | 13246.5087 | 13704.0276 | 14092.0177 | 14271.5572 | 14111.5063 | 14785.6146 | 14893.2628 | 14765.8898 | 15021.58 | 15168.2446 | 15168.2446 | 15168.2446 | 15168.2446 | 15168.2446 | 15168.2446 | 15168.2446 | 15168.2446 | 15168.2446 | 15168.2446 | 15168.2446 | 15168.2446 | 15168.2446 | 15168.2446 | 15168.2446 | E @ R (MWh) | 1562.9946 | 2324.4501 | 2347.8985 | 2322.6227 | 2329.1093 | 2375.6785 | 2471.5078 | 2644.8974 | 2737.5223 | 2805.7218 | 2911.5932 | 3051.3274 | 3226.9658 | 3321.8588 | 3290.8844 | 3328.4339 | 3328.4339 | 3328.4339 | 3328.4339 | 3328.4339 | 3328.4339 | 3328.4339 | 3328.4339 | 3328.4339 | 3328.4339 | 3328.4339 | 3328.4339 | 3328.4339 | 3328.4339 | 3328.4339
Option 1 Summer POE50 W E @ R (MWh) N 2 | 6456.5019 | 8825.4618 | 9075.7552 | 8952.8358 | 9069.703 | 9117.8375 | 9272.5561 | 9592.8193 | 9864.4124 | 9990.0901 | 9878.0544 | 10349.9302 | 10425.2839 | 10336.1228 | 10515.106 | 10617.7712 | 10617.7712 | 10617.7712 | 10617.7712 | 10617.7712 | 10617.7712 | 10617.7712 | 10617.7712 | 10617.7712 | 10617.7712 | 10617.7712 | 10617.7712 | 10617.7712 | 10617.7712 | 10617.7712 | Option 1 Summer POE10 W E @ R (MWh) N 2 | 468.8984 | 697.335 | 704.3695 | 696.7868 | 698.7328 | 712.7036 | 741.4523 | 793.4692 | 821.2567 | 841.7165 | 873.478 | 915.3982 | 968.0898 | 996.5577 | 987.2653 | 998.5302 | 998.5302 | 998.5302 | 998.5302 | 998.5302 | 998.5302 | 998.5302 | 998.5302 | 998.5302 | 998.5302 | 998.5302 | 998.5302 | 998.5302 | 998.5302 | 998.5302
Option 2 - Replace 3 x 10/13.5 MVA Tx with 3 x 20/33 MVA Tx
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | FY25: 5.1211; FY26: 6.2192; FY27: 6.3356 |  | 6.1303 | 7.1777 | 7.2862
98% | FY25: 0; FY26: 0; FY27: 0 |  | 0 | 0 | 0
97% | FY25: 0; FY26: 0; FY27: 0 |  | 0 | 0 | 0
95% | FY25: 19.0092; FY26: 23.247; FY27: 23.6963 |  | 22.9039 | 26.9462 | 27.3648
90% | FY25: 105.2028; FY26: 129.7026; FY27: 132.3005 |  | 127.7194 | 151.0886 | 153.5087
85% | FY25: 408.7931; FY26: 511.1512; FY27: 522.005 |  | 502.8656 | 600.5006 | 610.6116
80% | FY25: 592.6734; FY26: 754.7359; FY27: 771.9205 |  | 741.6174 | 896.2017 | 912.2103
75% | FY25: 980.9496; FY26: 1280.2989; FY27: 1312.0411 |  | 1256.0675 | 1541.6038 | 1571.1735
70% | FY25: 1385.9626; FY26: 1873.2259; FY27: 1924.894 |  | 1833.7834 | 2298.5628 | 2346.6947
65% | FY25: 1400.8592; FY26: 1997.5436; FY27: 2060.8145 |  | 1949.2438 | 2518.3953 | 2577.3359
60% | FY25: 1311.1794; FY26: 2051.2755; FY27: 2129.7534 |  | 1991.367 | 2697.3127 | 2770.4195
55% | FY25: 879.254; FY26: 1681.979; FY27: 1767.0979 |  | 1617.0008 | 2382.6855 | 2461.9788
50% | FY25: 249.4213; FY26: 1054.7724; FY27: 1141.4594 |  | 988.5972 | 1768.3876 | 1849.1417
45% | FY26: 263.6586; FY27: 332.2401 |  | 216.2457 | 917.7197 | 993.9934
40% | [32 empty] | 111.7593 | 148.9205
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 7265.0415 | 11511.5317 | 12003.3126 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 11141.0066 | 15759.1581 | 16266.3334 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2 Winter POE50 W E @ R (MWh) N 2 | 5085.529 | 8058.0722 | 8402.3188 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 2 Winter POE10 W E @ R (MWh) N 2 | 3342.302 | 4727.7474 | 4879.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | FY25: 7.3419; FY26: 8.3902; FY27: 8.4955 |  | 0 | 0 | 0
98% | FY25: 0; FY26: 0; FY27: 0 |  | 0 | 0 | 0
97% | FY25: 0; FY26: 0; FY27: 0 |  | 10.2241 | 11.372 | 11.4037
95% | FY25: 6.8489; FY26: 7.8602; FY27: 7.9619 |  | 0 | 0 | 0
90% | FY25: 139.8285; FY26: 161.2671; FY27: 163.4215 |  | 9.3575 | 10.4465 | 10.4766
85% | FY25: 469.0739; FY26: 545.5841; FY27: 553.2725 |  | 8.4909 | 9.521 | 9.5495
80% | FY25: 707.4418; FY26: 831.7279; FY27: 844.2173 |  | 30.4971 | 34.3823 | 34.4895
75% | FY25: 1149.798; FY26: 1371.0584; FY27: 1393.2926 |  | 13.5153 | 15.3402 | 15.3906
70% | FY25: 1309.2261; FY26: 1591.8262; FY27: 1620.2245 |  | 35.3464 | 40.4679 | 40.6092
65% | FY25: 1383.0411; FY26: 1730.0625; FY27: 1764.9344 |  | 10.0489 | 11.6384 | 11.6822
60% | FY25: 1639.9094; FY26: 2146.9041; FY27: 2197.8516 |  | 54.0524 | 63.6183 | 63.8823
55% | FY25: 1468.1665; FY26: 2092.0991; FY27: 2154.7976 |  | 210.6416 | 253.9682 | 255.1638
50% | FY25: 922.9519; FY26: 1630.9008; FY27: 1702.042 |  | 383.0991 | 480.7604 | 483.4553
45% | FY25: 113.1135; FY26: 605.5456; FY27: 664.4302 |  | 467.4239 | 635.1966 | 639.8262
40% | FY26: 11.9277; FY27: 21.3864 |  | 313.9328 | 541.1029 | 547.3715
35% | [31 empty] | 32.1525 | 240.1146 | 248.3143
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 9223.5741 | 12607.8025 | 12965.3646 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 1562.9946 | 2324.4501 | 2347.8985 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2 Summer POE50 W E @ R (MWh) N 2 | 6456.5019 | 8825.4618 | 9075.7552 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 2 Summer POE10 W E @ R (MWh) N 2 | 468.8984 | 697.335 | 704.3695 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 - Replace 1 x 10/13.5 MVA Tx with 1 x 20/33 MVA Tx
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | 5.1211 | 6.2192 | 6.3356 | 1.9176 | 2.1087 | 2.2899 | 2.6065 | 3.4029 | 3.8313 | 3.5188 | 4.4862 | 4.6605 | 4.7858 | 5.3764 | 5.4726 | 5.4726 | 5.4726 | 5.4726 | 5.4726 | 5.4726 | 5.4726 | 5.4726 | 5.4726 | 5.4726 | 5.4726 | 5.4726 | 5.4726 | 5.4726 | 5.4726 | 5.4726 |  | 6.1303 | 7.1777 | 7.2862 | 3.0985 | 3.0894 | 3.1717 | 3.4937 | 4.4186 | 4.8003 | 4.439 | 5.4371 | 5.018 | 5.3951 | 5.6668 | 5.5552 | 5.5552 | 5.5552 | 5.5552 | 5.5552 | 5.5552 | 5.5552 | 5.5552 | 5.5552 | 5.5552 | 5.5552 | 5.5552 | 5.5552 | 5.5552 | 5.5552 | 5.5552
98% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
97% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
95% | 19.0092 | 23.247 | 23.6963 | 6.0039 | 6.7415 | 7.4407 | 8.6628 | 11.7362 | 13.3894 | 12.1833 | 15.917 | 16.5897 | 17.0732 | 19.3525 | 19.7236 | 19.7236 | 19.7236 | 19.7236 | 19.7236 | 19.7236 | 19.7236 | 19.7236 | 19.7236 | 19.7236 | 19.7236 | 19.7236 | 19.7236 | 19.7236 | 19.7236 | 19.7236 |  | 22.9039 | 26.9462 | 27.3648 | 10.5615 | 10.5263 | 10.8439 | 12.0864 | 15.6561 | 17.1291 | 15.7348 | 19.5866 | 17.9694 | 19.4245 | 20.4731 | 20.0423 | 20.0423 | 20.0423 | 20.0423 | 20.0423 | 20.0423 | 20.0423 | 20.0423 | 20.0423 | 20.0423 | 20.0423 | 20.0423 | 20.0423 | 20.0423 | 20.0423 | 20.0423
90% | 105.2028 | 129.7026 | 132.3005 | 26.0243 | 30.2885 | 34.3311 | 41.3959 | 59.1644 | 68.7216 | 61.7494 | 83.3344 | 87.2234 | 90.019 | 103.1963 | 105.3412 | 105.3412 | 105.3412 | 105.3412 | 105.3412 | 105.3412 | 105.3412 | 105.3412 | 105.3412 | 105.3412 | 105.3412 | 105.3412 | 105.3412 | 105.3412 | 105.3412 | 105.3412 |  | 127.7194 | 151.0886 | 153.5087 | 52.3728 | 52.1693 | 54.0058 | 61.1889 | 81.8261 | 90.3422 | 82.281 | 104.5492 | 95.1998 | 103.6123 | 109.6745 | 107.1839 | 107.1839 | 107.1839 | 107.1839 | 107.1839 | 107.1839 | 107.1839 | 107.1839 | 107.1839 | 107.1839 | 107.1839 | 107.1839 | 107.1839 | 107.1839 | 107.1839 | 107.1839
85% | 408.7931 | 511.1512 | 522.005 | 51.8517 | 69.6674 | 86.5571 | 116.0735 | 190.309 | 230.2381 | 201.1086 | 291.2895 | 307.5374 | 319.2169 | 374.2709 | 383.232 | 383.232 | 383.232 | 383.232 | 383.232 | 383.232 | 383.232 | 383.232 | 383.232 | 383.232 | 383.232 | 383.232 | 383.232 | 383.232 | 383.232 | 383.232 |  | 502.8656 | 600.5006 | 610.6116 | 161.9342 | 161.0837 | 168.7568 | 198.7671 | 284.9877 | 320.5675 | 286.8884 | 379.9233 | 340.8622 | 376.009 | 401.3366 | 390.9308 | 390.9308 | 390.9308 | 390.9308 | 390.9308 | 390.9308 | 390.9308 | 390.9308 | 390.9308 | 390.9308 | 390.9308 | 390.9308 | 390.9308 | 390.9308 | 390.9308 | 390.9308
80% | 592.6734 | 754.7359 | 771.9205 | 5.4883 | 18.5302 | 37.6546 | 82.8118 | 200.348 | 263.5674 | 217.447 | 360.2293 | 385.9544 | 404.4465 | 491.6128 | 505.8008 | 505.8008 | 505.8008 | 505.8008 | 505.8008 | 505.8008 | 505.8008 | 505.8008 | 505.8008 | 505.8008 | 505.8008 | 505.8008 | 505.8008 | 505.8008 | 505.8008 | 505.8008 |  | 741.6174 | 896.2017 | 912.2103 | 155.4225 | 154.076 | 166.2246 | 213.7396 | 350.2517 | 406.5848 | 353.2611 | 500.5622 | 438.7172 | 494.3648 | 534.4655 | 517.9902 | 517.9902 | 517.9902 | 517.9902 | 517.9902 | 517.9902 | 517.9902 | 517.9902 | 517.9902 | 517.9902 | 517.9902 | 517.9902 | 517.9902 | 517.9902 | 517.9902 | 517.9902
75% | 980.9496 | 1280.2989 | 1312.0411 |  |  |  | 6.28 | 159.5067 | 276.2806 | 191.0906 | 454.8271 | 502.3445 | 536.5017 | 697.5086 | 723.7156 | 723.7156 | 723.7156 | 723.7156 | 723.7156 | 723.7156 | 723.7156 | 723.7156 | 723.7156 | 723.7156 | 723.7156 | 723.7156 | 723.7156 | 723.7156 | 723.7156 | 723.7156 |  | 1256.0675 | 1541.6038 | 1571.1735 | 79.6784 | 77.6058 | 97.2363 | 184.2427 | 436.3972 | 540.4514 | 441.956 | 714.0392 | 599.8039 | 702.5918 | 776.6629 | 746.231 | 746.231 | 746.231 | 746.231 | 746.231 | 746.231 | 746.231 | 746.231 | 746.231 | 746.231 | 746.231 | 746.231 | 746.231 | 746.231 | 746.231 | 746.231
70% | 1385.9626 | 1873.2259 | 1924.894 |  |  |  |  | 6.6366 | 86.7116 | 19.5272 | 350.3285 | 427.6746 | 483.2736 | 745.3513 | 788.0095 | 788.0095 | 788.0095 | 788.0095 | 788.0095 | 788.0095 | 788.0095 | 788.0095 | 788.0095 | 788.0095 | 788.0095 | 788.0095 | 788.0095 | 788.0095 | 788.0095 | 788.0095 |  | 1833.7834 | 2298.5628 | 2346.6947 |  |  |  | 16.1665 | 320.3294 | 489.7027 | 329.3777 | 772.2588 | 586.3133 | 753.6255 | 874.1941 | 824.6588 | 824.6588 | 824.6588 | 824.6588 | 824.6588 | 824.6588 | 824.6588 | 824.6588 | 824.6588 | 824.6588 | 824.6588 | 824.6588 | 824.6588 | 824.6588 | 824.6588 | 824.6588
65% | 1400.8592 | 1997.5436 | 2060.8145 | [7 empty] | 25.1177 | 61.592 | 97.3418 | 364.3796 | 416.6172 | 416.6172 | 416.6172 | 416.6172 | 416.6172 | 416.6172 | 416.6172 | 416.6172 | 416.6172 | 416.6172 | 416.6172 | 416.6172 | 416.6172 | 416.6172 | 416.6172 | 416.6172 |  | 1949.2438 | 2518.3953 | 2577.3359 |  |  |  |  | 15.2295 | 101.9789 | 17.9574 | 397.3295 | 183.9223 | 374.5118 | 522.1556 | 461.4965 | 461.4965 | 461.4965 | 461.4965 | 461.4965 | 461.4965 | 461.4965 | 461.4965 | 461.4965 | 461.4965 | 461.4965 | 461.4965 | 461.4965 | 461.4965 | 461.4965 | 461.4965
60% | 1311.1794 | 2051.2755 | 2129.7534 | [10 empty] | 3.4589 | 12.3032 | 12.3032 | 12.3032 | 12.3032 | 12.3032 | 12.3032 | 12.3032 | 12.3032 | 12.3032 | 12.3032 | 12.3032 | 12.3032 | 12.3032 | 12.3032 | 12.3032 | 12.3032 |  | 1991.367 | 2697.3127 | 2770.4195 | [7 empty] | 8.4122 |  | 4.7534 | 46.3165 | 24.158 | 24.158 | 24.158 | 24.158 | 24.158 | 24.158 | 24.158 | 24.158 | 24.158 | 24.158 | 24.158 | 24.158 | 24.158 | 24.158 | 24.158 | 24.158
55% | FY25: 879.254; FY26: 1681.979; FY27: 1767.0979 |  | 1617.0008 | 2382.6855 | 2461.9788
50% | FY25: 249.4213; FY26: 1054.7724; FY27: 1141.4594 |  | 988.5972 | 1768.3876 | 1849.1417
45% | FY26: 263.6586; FY27: 332.2401 |  | 216.2457 | 917.7197 | 993.9934
40% | [32 empty] | 111.7593 | 148.9205
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 7265.0415 | 11511.5317 | 12003.3126 | 90.3729 | 126.0629 | 166.5908 | 255.2522 | 624.7928 | 933.3126 | 699.5586 | 1569.6744 | 1775.6407 | 1933.132 | 2776.4622 | 2930.6133 | 2930.6133 | 2930.6133 | 2930.6133 | 2930.6133 | 2930.6133 | 2930.6133 | 2930.6133 | 2930.6133 | 2930.6133 | 2930.6133 | 2930.6133 | 2930.6133 | 2930.6133 | 2930.6133 | 2930.6133 | E @ R (MWh) | 11141.0066 | 15759.1581 | 16266.3334 | 458.4372 | 453.965 | 495.2369 | 682.7881 | 1494.0052 | 1951.8413 | 1516.5765 | 2873.077 | 2245.1281 | 2805.9453 | 3258.0361 | 3067.2642 | 3067.2642 | 3067.2642 | 3067.2642 | 3067.2642 | 3067.2642 | 3067.2642 | 3067.2642 | 3067.2642 | 3067.2642 | 3067.2642 | 3067.2642 | 3067.2642 | 3067.2642 | 3067.2642 | 3067.2642
Option 3 Winter POE50 W E @ R (MWh) N 2 | 5085.529 | 8058.0722 | 8402.3188 | 63.261 | 88.244 | 116.6136 | 178.6766 | 437.3549 | 653.3188 | 489.691 | 1098.7721 | 1242.9485 | 1353.1924 | 1943.5236 | 2051.4293 | 2051.4293 | 2051.4293 | 2051.4293 | 2051.4293 | 2051.4293 | 2051.4293 | 2051.4293 | 2051.4293 | 2051.4293 | 2051.4293 | 2051.4293 | 2051.4293 | 2051.4293 | 2051.4293 | 2051.4293 | Option 3 Winter POE10 W E @ R (MWh) N 2 | 3342.302 | 4727.7474 | 4879.9 | 137.5311 | 136.1895 | 148.5711 | 204.8364 | 448.2016 | 585.5524 | 454.973 | 861.9231 | 673.5384 | 841.7836 | 977.4108 | 920.1793 | 920.1793 | 920.1793 | 920.1793 | 920.1793 | 920.1793 | 920.1793 | 920.1793 | 920.1793 | 920.1793 | 920.1793 | 920.1793 | 920.1793 | 920.1793 | 920.1793 | 920.1793
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | 7.3419 | 8.3902 | 8.4955 | 2.639 | 2.6881 | 2.7083 | 2.773 | 2.9059 | 3.0177 | 3.0692 | 3.0233 | 3.2157 | 3.2462 | 3.2101 | 3.2825 | 3.3239 | 3.3239 | 3.3239 | 3.3239 | 3.3239 | 3.3239 | 3.3239 | 3.3239 | 3.3239 | 3.3239 | 3.3239 | 3.3239 | 3.3239 | 3.3239 | 3.3239 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
98% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
97% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 10.2241 | 11.372 | 11.4037 | 5.5647 | 5.5735 | 5.6361 | 5.7632 | 5.9869 | 6.1035 | 6.1878 | 6.3155 | 6.4784 | 6.6755 | 6.7788 | 6.7453 | 6.7858 | 6.7858 | 6.7858 | 6.7858 | 6.7858 | 6.7858 | 6.7858 | 6.7858 | 6.7858 | 6.7858 | 6.7858 | 6.7858 | 6.7858 | 6.7858 | 6.7858
95% | 6.8489 | 7.8602 | 7.9619 | 2.1072 | 2.1546 | 2.1741 | 2.2364 | 2.3647 | 2.4726 | 2.5223 | 2.478 | 2.6636 | 2.693 | 2.6582 | 2.7281 | 2.768 | 2.768 | 2.768 | 2.768 | 2.768 | 2.768 | 2.768 | 2.768 | 2.768 | 2.768 | 2.768 | 2.768 | 2.768 | 2.768 | 2.768 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
90% | 139.8285 | 161.2671 | 163.4215 | 34.6594 | 35.6635 | 36.0761 | 37.3983 | 40.1172 | 42.4044 | 43.4573 | 42.5188 | 46.4533 | 47.0773 | 46.3388 | 47.8196 | 48.6662 | 48.6662 | 48.6662 | 48.6662 | 48.6662 | 48.6662 | 48.6662 | 48.6662 | 48.6662 | 48.6662 | 48.6662 | 48.6662 | 48.6662 | 48.6662 | 48.6662 |  | 9.3575 | 10.4465 | 10.4766 | 4.6393 | 4.6477 | 4.7071 | 4.8277 | 5.0399 | 5.1505 | 5.2305 | 5.3516 | 5.5062 | 5.6932 | 5.7912 | 5.7594 | 5.7979 | 5.7979 | 5.7979 | 5.7979 | 5.7979 | 5.7979 | 5.7979 | 5.7979 | 5.7979 | 5.7979 | 5.7979 | 5.7979 | 5.7979 | 5.7979 | 5.7979
85% | 469.0739 | 545.5841 | 553.2725 | 67.7036 | 71.287 | 72.7594 | 77.4783 | 87.1812 | 95.3438 | 99.1013 | 95.7523 | 109.7936 | 112.0205 | 109.3851 | 114.6698 | 117.6908 | 117.6908 | 117.6908 | 117.6908 | 117.6908 | 117.6908 | 117.6908 | 117.6908 | 117.6908 | 117.6908 | 117.6908 | 117.6908 | 117.6908 | 117.6908 | 117.6908 |  | 8.4909 | 9.521 | 9.5495 | 3.714 | 3.7219 | 3.7781 | 3.8921 | 4.0929 | 4.1975 | 4.2732 | 4.3878 | 4.534 | 4.7109 | 4.8036 | 4.7735 | 4.8099 | 4.8099 | 4.8099 | 4.8099 | 4.8099 | 4.8099 | 4.8099 | 4.8099 | 4.8099 | 4.8099 | 4.8099 | 4.8099 | 4.8099 | 4.8099 | 4.8099
80% | 707.4418 | 831.7279 | 844.2173 | 17.8779 | 21.4146 | 22.9567 | 28.2447 | 40.7513 | 52.9403 | 59.0095 | 53.5896 | 76.3784 | 79.996 | 75.7148 | 84.2996 | 89.2071 | 89.2071 | 89.2071 | 89.2071 | 89.2071 | 89.2071 | 89.2071 | 89.2071 | 89.2071 | 89.2071 | 89.2071 | 89.2071 | 89.2071 | 89.2071 | 89.2071 |  | 30.4971 | 34.3823 | 34.4895 | 11.1547 | 11.1844 | 11.3965 | 11.8265 | 12.5837 | 12.9783 | 13.2638 | 13.6958 | 14.2473 | 14.9143 | 15.2638 | 15.1505 | 15.2878 | 15.2878 | 15.2878 | 15.2878 | 15.2878 | 15.2878 | 15.2878 | 15.2878 | 15.2878 | 15.2878 | 15.2878 | 15.2878 | 15.2878 | 15.2878 | 15.2878
75% | 1149.798 | 1371.0584 | 1393.2926 | [6 empty] | 0.08382 |  | 3.356 | 4.6285 | 3.1445 | 6.404 | 8.7734 | 8.7734 | 8.7734 | 8.7734 | 8.7734 | 8.7734 | 8.7734 | 8.7734 | 8.7734 | 8.7734 | 8.7734 | 8.7734 | 8.7734 | 8.7734 | 8.7734 |  | 13.5153 | 15.3402 | 15.3906 | 3.7266 | 3.7406 | 3.8403 | 4.0422 | 4.3979 | 4.5832 | 4.7173 | 4.9202 | 5.1793 | 5.4925 | 5.6567 | 5.6035 | 5.668 | 5.668 | 5.668 | 5.668 | 5.668 | 5.668 | 5.668 | 5.668 | 5.668 | 5.668 | 5.668 | 5.668 | 5.668 | 5.668 | 5.668
70% | FY25: 1309.2261; FY26: 1591.8262; FY27: 1620.2245 |  | 35.3464 | 40.4679 | 40.6092 | 5.6279 | 5.6671 | 5.9468 | 6.5136 | 7.5117 | 8.0318 | 8.4081 | 8.9776 | 9.7047 | 10.5838 | 11.0446 | 10.8952 | 11.0762 | 11.0762 | 11.0762 | 11.0762 | 11.0762 | 11.0762 | 11.0762 | 11.0762 | 11.0762 | 11.0762 | 11.0762 | 11.0762 | 11.0762 | 11.0762 | 11.0762
65% | FY25: 1383.0411; FY26: 1730.0625; FY27: 1764.9344 |  | 10.0489 | 11.6384 | 11.6822 | 0.24416 | 0.25055 | 0.29853 | 0.40803 | 0.63992 | 0.77999 | 0.88937 | 1.0649 | 1.2905 | 1.5633 | 1.7063 | 1.66 | 1.7161 | 1.7161 | 1.7161 | 1.7161 | 1.7161 | 1.7161 | 1.7161 | 1.7161 | 1.7161 | 1.7161 | 1.7161 | 1.7161 | 1.7161 | 1.7161 | 1.7161
60% | FY25: 1639.9094; FY26: 2146.9041; FY27: 2197.8516 |  | 54.0524 | 63.6183 | 63.8823 | [7 empty] | 0.017202 | 0.16934 | 0.55848 | 0.84997 | 0.74897 | 0.87212 | 0.87212 | 0.87212 | 0.87212 | 0.87212 | 0.87212 | 0.87212 | 0.87212 | 0.87212 | 0.87212 | 0.87212 | 0.87212 | 0.87212 | 0.87212 | 0.87212
55% | FY25: 1468.1665; FY26: 2092.0991; FY27: 2154.7976 |  | 210.6416 | 253.9682 | 255.1638
50% | FY25: 922.9519; FY26: 1630.9008; FY27: 1702.042 |  | 383.0991 | 480.7604 | 483.4553
45% | FY25: 113.1135; FY26: 605.5456; FY27: 664.4302 |  | 467.4239 | 635.1966 | 639.8262
40% | FY26: 11.9277; FY27: 21.3864 |  | 313.9328 | 541.1029 | 547.3715
35% | [31 empty] | 32.1525 | 240.1146 | 248.3143
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 9223.5741 | 12607.8025 | 12965.3646 | 123.7373 | 131.8758 | 135.3078 | 146.6494 | 171.5871 | 194.217 | 205.1709 | 195.3884 | 239.442 | 247.165 | 238.047 | 256.6115 | 267.7251 | 267.7251 | 267.7251 | 267.7251 | 267.7251 | 267.7251 | 267.7251 | 267.7251 | 267.7251 | 267.7251 | 267.7251 | 267.7251 | 267.7251 | 267.7251 | 267.7251 | E @ R (MWh) | 1562.9946 | 2324.4501 | 2347.8985 | 34.3247 | 34.4378 | 35.2475 | 36.9006 | 39.8505 | 41.4067 | 42.5404 | 44.2832 | 46.6387 | 49.6901 | 51.376 | 50.823 | 51.4937 | 51.4937 | 51.4937 | 51.4937 | 51.4937 | 51.4937 | 51.4937 | 51.4937 | 51.4937 | 51.4937 | 51.4937 | 51.4937 | 51.4937 | 51.4937 | 51.4937
Option 3 Summer POE50 W E @ R (MWh) N 2 | 6456.5019 | 8825.4618 | 9075.7552 | 86.6161 | 92.3131 | 94.7154 | 102.6546 | 120.111 | 135.9519 | 143.6196 | 136.7719 | 167.6094 | 173.0155 | 166.6329 | 179.6281 | 187.4076 | 187.4076 | 187.4076 | 187.4076 | 187.4076 | 187.4076 | 187.4076 | 187.4076 | 187.4076 | 187.4076 | 187.4076 | 187.4076 | 187.4076 | 187.4076 | 187.4076 | Option 3 Summer POE10 W E @ R (MWh) N 2 | 468.8984 | 697.335 | 704.3695 | 10.2974 | 10.3313 | 10.5743 | 11.0702 | 11.9552 | 12.422 | 12.7621 | 13.285 | 13.9916 | 14.907 | 15.4128 | 15.2469 | 15.4481 | 15.4481 | 15.4481 | 15.4481 | 15.4481 | 15.4481 | 15.4481 | 15.4481 | 15.4481 | 15.4481 | 15.4481 | 15.4481 | 15.4481 | 15.4481 | 15.4481
Option 4 - Construct 2x 20/33MVA zone substation in Inverloch
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | FY25: 5.1211; FY26: 6.2192; FY27: 6.3356 |  | 6.1303 | 7.1777 | 7.2862
98% | FY25: 0; FY26: 0; FY27: 0 |  | 0 | 0 | 0
97% | FY25: 0; FY26: 0; FY27: 0 |  | 0 | 0 | 0
95% | FY25: 19.0092; FY26: 23.247; FY27: 23.6963 |  | 22.9039 | 26.9462 | 27.3648
90% | FY25: 105.2028; FY26: 129.7026; FY27: 132.3005 |  | 127.7194 | 151.0886 | 153.5087
85% | FY25: 408.7931; FY26: 511.1512; FY27: 522.005 |  | 502.8656 | 600.5006 | 610.6116
80% | FY25: 592.6734; FY26: 754.7359; FY27: 771.9205 |  | 741.6174 | 896.2017 | 912.2103
75% | FY25: 980.9496; FY26: 1280.2989; FY27: 1312.0411 |  | 1256.0675 | 1541.6038 | 1571.1735
70% | FY25: 1385.9626; FY26: 1873.2259; FY27: 1924.894 |  | 1833.7834 | 2298.5628 | 2346.6947
65% | FY25: 1400.8592; FY26: 1997.5436; FY27: 2060.8145 |  | 1949.2438 | 2518.3953 | 2577.3359
60% | FY25: 1311.1794; FY26: 2051.2755; FY27: 2129.7534 |  | 1991.367 | 2697.3127 | 2770.4195
55% | FY25: 879.254; FY26: 1681.979; FY27: 1767.0979 |  | 1617.0008 | 2382.6855 | 2461.9788
50% | FY25: 249.4213; FY26: 1054.7724; FY27: 1141.4594 |  | 988.5972 | 1768.3876 | 1849.1417
45% | FY26: 263.6586; FY27: 332.2401 |  | 216.2457 | 917.7197 | 993.9934
40% | [32 empty] | 111.7593 | 148.9205
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 7265.0415 | 11511.5317 | 12003.3126 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 11141.0066 | 15759.1581 | 16266.3334 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 Winter POE50 W E @ R (MWh) N 2 | 5085.529 | 8058.0722 | 8402.3188 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 4 Winter POE10 W E @ R (MWh) N 2 | 3342.302 | 4727.7474 | 4879.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | FY25: 7.3419; FY26: 8.3902; FY27: 8.4955 |  | 0 | 0 | 0
98% | FY25: 0; FY26: 0; FY27: 0 |  | 0 | 0 | 0
97% | FY25: 0; FY26: 0; FY27: 0 |  | 10.2241 | 11.372 | 11.4037
95% | FY25: 6.8489; FY26: 7.8602; FY27: 7.9619 |  | 0 | 0 | 0
90% | FY25: 139.8285; FY26: 161.2671; FY27: 163.4215 |  | 9.3575 | 10.4465 | 10.4766
85% | FY25: 469.0739; FY26: 545.5841; FY27: 553.2725 |  | 8.4909 | 9.521 | 9.5495
80% | FY25: 707.4418; FY26: 831.7279; FY27: 844.2173 |  | 30.4971 | 34.3823 | 34.4895
75% | FY25: 1149.798; FY26: 1371.0584; FY27: 1393.2926 |  | 13.5153 | 15.3402 | 15.3906
70% | FY25: 1309.2261; FY26: 1591.8262; FY27: 1620.2245 |  | 35.3464 | 40.4679 | 40.6092
65% | FY25: 1383.0411; FY26: 1730.0625; FY27: 1764.9344 |  | 10.0489 | 11.6384 | 11.6822
60% | FY25: 1639.9094; FY26: 2146.9041; FY27: 2197.8516 |  | 54.0524 | 63.6183 | 63.8823
55% | FY25: 1468.1665; FY26: 2092.0991; FY27: 2154.7976 |  | 210.6416 | 253.9682 | 255.1638
50% | FY25: 922.9519; FY26: 1630.9008; FY27: 1702.042 |  | 383.0991 | 480.7604 | 483.4553
45% | FY25: 113.1135; FY26: 605.5456; FY27: 664.4302 |  | 467.4239 | 635.1966 | 639.8262
40% | FY26: 11.9277; FY27: 21.3864 |  | 313.9328 | 541.1029 | 547.3715
35% | [31 empty] | 32.1525 | 240.1146 | 248.3143
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 9223.5741 | 12607.8025 | 12965.3646 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 1562.9946 | 2324.4501 | 2347.8985 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 Summer POE50 W E @ R (MWh) N 2 | 6456.5019 | 8825.4618 | 9075.7552 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 4 Summer POE10 W E @ R (MWh) N 2 | 468.8984 | 697.335 | 704.3695 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 - Contract network support services to defer network investment
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | 3.9093 | 4.9252 | 5.0394 | 5.1858 | 5.3763 | 5.553 | 5.8605 | 6.6409 | 7.0609 | 6.7424 | 7.7007 | 7.8633 | 7.9745 | 8.5578 | 8.6563 | 8.6563 | 8.6563 | 8.6563 | 8.6563 | 8.6563 | 8.6563 | 8.6563 | 8.6563 | 8.6563 | 8.6563 | 8.6563 | 8.6563 | 8.6563 | 8.6563 | 8.6563 |  | 4.9185 | 5.8837 | 5.9899 | 6.3667 | 6.357 | 6.4348 | 6.7477 | 7.6566 | 8.03 | 7.6626 | 8.6515 | 8.2208 | 8.5838 | 8.8481 | 8.7389 | 8.7389 | 8.7389 | 8.7389 | 8.7389 | 8.7389 | 8.7389 | 8.7389 | 8.7389 | 8.7389 | 8.7389 | 8.7389 | 8.7389 | 8.7389 | 8.7389 | 8.7389
98% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
97% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
95% | 14.3322 | 18.2531 | 18.6937 | 19.2587 | 19.9939 | 20.6758 | 21.8628 | 24.8745 | 26.4954 | 25.2661 | 28.9645 | 29.5922 | 30.0213 | 32.2721 | 32.6524 | 32.6524 | 32.6524 | 32.6524 | 32.6524 | 32.6524 | 32.6524 | 32.6524 | 32.6524 | 32.6524 | 32.6524 | 32.6524 | 32.6524 | 32.6524 | 32.6524 | 32.6524 |  | 18.227 | 21.9523 | 22.3622 | 23.8163 | 23.7786 | 24.079 | 25.2864 | 28.7943 | 30.2352 | 28.8175 | 32.6341 | 30.9719 | 32.3726 | 33.3927 | 32.9711 | 32.9711 | 32.9711 | 32.9711 | 32.9711 | 32.9711 | 32.9711 | 32.9711 | 32.9711 | 32.9711 | 32.9711 | 32.9711 | 32.9711 | 32.9711 | 32.9711 | 32.9711
90% | 78.1644 | 100.8318 | 103.3791 | 106.6454 | 110.8956 | 114.8381 | 121.7002 | 139.1116 | 148.4827 | 141.3758 | 162.7571 | 166.386 | 168.867 | 181.8795 | 184.0778 | 184.0778 | 184.0778 | 184.0778 | 184.0778 | 184.0778 | 184.0778 | 184.0778 | 184.0778 | 184.0778 | 184.0778 | 184.0778 | 184.0778 | 184.0778 | 184.0778 | 184.0778 |  | 100.6809 | 122.2178 | 124.5874 | 132.9939 | 132.7764 | 134.5129 | 141.4932 | 161.7732 | 170.1033 | 161.9075 | 183.9719 | 174.3624 | 182.4603 | 188.3577 | 185.9205 | 185.9205 | 185.9205 | 185.9205 | 185.9205 | 185.9205 | 185.9205 | 185.9205 | 185.9205 | 185.9205 | 185.9205 | 185.9205 | 185.9205 | 185.9205 | 185.9205 | 185.9205
85% | 295.8283 | 390.5311 | 401.1737 | 414.8199 | 432.577 | 449.0487 | 477.7178 | 550.4613 | 589.6131 | 559.9211 | 649.2508 | 664.4119 | 674.7773 | 729.1426 | 738.3269 | 738.3269 | 738.3269 | 738.3269 | 738.3269 | 738.3269 | 738.3269 | 738.3269 | 738.3269 | 738.3269 | 738.3269 | 738.3269 | 738.3269 | 738.3269 | 738.3269 | 738.3269 |  | 389.9008 | 479.8806 | 489.7803 | 524.9023 | 523.9933 | 531.2483 | 560.4115 | 645.14 | 679.9424 | 645.7009 | 737.8846 | 697.7367 | 731.5694 | 756.2082 | 746.0258 | 746.0258 | 746.0258 | 746.0258 | 746.0258 | 746.0258 | 746.0258 | 746.0258 | 746.0258 | 746.0258 | 746.0258 | 746.0258 | 746.0258 | 746.0258 | 746.0258 | 746.0258
80% | 413.8176 | 563.7595 | 580.6097 | 602.2156 | 630.3302 | 656.4097 | 701.8012 | 816.9751 | 878.9636 | 831.9527 | 973.3873 | 997.3917 | 1013.8032 | 1099.879 | 1114.4205 | 1114.4205 | 1114.4205 | 1114.4205 | 1114.4205 | 1114.4205 | 1114.4205 | 1114.4205 | 1114.4205 | 1114.4205 | 1114.4205 | 1114.4205 | 1114.4205 | 1114.4205 | 1114.4205 | 1114.4205 |  | 562.7615 | 705.2254 | 720.8995 | 776.5078 | 775.0686 | 786.5554 | 832.729 | 966.8788 | 1021.981 | 967.7668 | 1113.7201 | 1050.1545 | 1103.7214 | 1142.7318 | 1126.61 | 1126.61 | 1126.61 | 1126.61 | 1126.61 | 1126.61 | 1126.61 | 1126.61 | 1126.61 | 1126.61 | 1126.61 | 1126.61 | 1126.61 | 1126.61 | 1126.61 | 1126.61
75% | 650.5809 | 927.542 | 958.6665 | 998.5752 | 1050.5063 | 1098.6783 | 1182.522 | 1395.2624 | 1509.7627 | 1422.9278 | 1684.1749 | 1728.5141 | 1758.828 | 1917.8208 | 1944.6807 | 1944.6807 | 1944.6807 | 1944.6807 | 1944.6807 | 1944.6807 | 1944.6807 | 1944.6807 | 1944.6807 | 1944.6807 | 1944.6807 | 1944.6807 | 1944.6807 | 1944.6807 | 1944.6807 | 1944.6807 |  | 925.6987 | 1188.8469 | 1217.7989 | 1320.5144 | 1317.856 | 1339.0734 | 1424.3618 | 1672.1529 | 1773.9335 | 1673.7933 | 1943.387 | 1825.9735 | 1924.9181 | 1996.9751 | 1967.1961 | 1967.1961 | 1967.1961 | 1967.1961 | 1967.1961 | 1967.1961 | 1967.1961 | 1967.1961 | 1967.1961 | 1967.1961 | 1967.1961 | 1967.1961 | 1967.1961 | 1967.1961 | 1967.1961 | 1967.1961
70% | 848.2074 | 1299.0288 | 1349.6913 | 1414.6524 | 1499.1829 | 1577.5944 | 1714.0703 | 2060.3568 | 2246.7338 | 2105.3889 | 2530.6318 | 2602.8045 | 2652.1478 | 2910.947 | 2954.668 | 2954.668 | 2954.668 | 2954.668 | 2954.668 | 2954.668 | 2954.668 | 2954.668 | 2954.668 | 2954.668 | 2954.668 | 2954.668 | 2954.668 | 2954.668 | 2954.668 | 2954.668 |  | 1296.0282 | 1724.3656 | 1771.492 | 1938.6863 | 1934.3591 | 1968.8956 | 2107.7232 | 2511.0631 | 2676.7356 | 2513.7331 | 2952.5621 | 2761.4432 | 2922.4996 | 3039.7897 | 2991.3173 | 2991.3173 | 2991.3173 | 2991.3173 | 2991.3173 | 2991.3173 | 2991.3173 | 2991.3173 | 2991.3173 | 2991.3173 | 2991.3173 | 2991.3173 | 2991.3173 | 2991.3173 | 2991.3173 | 2991.3173
65% | 742.3444 | 1294.4033 | 1356.4427 | 1435.9917 | 1539.5046 | 1635.5244 | 1802.6477 | 2226.6971 | 2454.9274 | 2281.8418 | 2802.5783 | 2890.9583 | 2951.3823 | 3268.2981 | 3321.8372 | 3321.8372 | 3321.8372 | 3321.8372 | 3321.8372 | 3321.8372 | 3321.8372 | 3321.8372 | 3321.8372 | 3321.8372 | 3321.8372 | 3321.8372 | 3321.8372 | 3321.8372 | 3321.8372 | 3321.8372 |  | 1290.729 | 1815.255 | 1872.9642 | 2077.704 | 2072.4051 | 2114.6972 | 2284.7002 | 2778.6152 | 2981.4915 | 2781.8849 | 3319.2584 | 3085.2214 | 3282.445 | 3426.0741 | 3366.7165 | 3366.7165 | 3366.7165 | 3366.7165 | 3366.7165 | 3366.7165 | 3366.7165 | 3366.7165 | 3366.7165 | 3366.7165 | 3366.7165 | 3366.7165 | 3366.7165 | 3366.7165 | 3366.7165 | 3366.7165
60% | 494.392 | 1179.1371 | 1256.0875 | 1354.7558 | 1483.1478 | 1602.2459 | 1809.5368 | 2335.5056 | 2618.5905 | 2403.9041 | 3049.7984 | 3159.4204 | 3234.3671 | 3627.4529 | 3693.86 | 3693.86 | 3693.86 | 3693.86 | 3693.86 | 3693.86 | 3693.86 | 3693.86 | 3693.86 | 3693.86 | 3693.86 | 3693.86 | 3693.86 | 3693.86 | 3693.86 | 3693.86 |  | 1174.5796 | 1825.1742 | 1896.7537 | 2150.7023 | 2144.1298 | 2196.5868 | 2407.4496 | 3020.0759 | 3271.7131 | 3024.1314 | 3690.6615 | 3400.3742 | 3645 | 3823.15 | 3749.526 | 3749.526 | 3749.526 | 3749.526 | 3749.526 | 3749.526 | 3749.526 | 3749.526 | 3749.526 | 3749.526 | 3749.526 | 3749.526 | 3749.526 | 3749.526 | 3749.526 | 3749.526
55% | 70.4002 | 736.038 | 819.5002 | 926.5181 | 1065.7749 | 1194.9513 | 1419.7838 | 1990.2613 | 2297.3016 | 2064.448 | 2764.9995 | 2883.8979 | 2965.1868 | 3391.5365 | 3463.5632 | 3463.5632 | 3463.5632 | 3463.5632 | 3463.5632 | 3463.5632 | 3463.5632 | 3463.5632 | 3463.5632 | 3463.5632 | 3463.5632 | 3463.5632 | 3463.5632 | 3463.5632 | 3463.5632 | 3463.5632 |  | 731.0949 | 1436.7444 | 1514.3811 | 1789.8195 | 1782.6908 | 1839.5869 | 2068.2934 | 2732.7618 | 3005.6931 | 2737.1604 | 3460.094 | 3145.2418 | 3410.5686 | 3603.7941 | 3523.9398 | 3523.9398 | 3523.9398 | 3523.9398 | 3523.9398 | 3523.9398 | 3523.9398 | 3523.9398 | 3523.9398 | 3523.9398 | 3523.9398 | 3523.9398 | 3523.9398 | 3523.9398 | 3523.9398 | 3523.9398
50% |  | 142.6261 | 201.5044 | 290.6451 | 427.2164 | 558.7725 | 787.7469 | 1368.734 | 1681.4308 | 1444.2874 | 2157.7448 | 2278.8336 | 2361.62 | 2795.8241 | 2869.1777 | 2869.1777 | 2869.1777 | 2869.1777 | 2869.1777 | 2869.1777 | 2869.1777 | 2869.1777 | 2869.1777 | 2869.1777 | 2869.1777 | 2869.1777 | 2869.1777 | 2869.1777 | 2869.1777 | 2869.1777 |  | 139.4391 | 805.02 | 884.087 | 1164.5996 | 1157.3396 | 1215.2838 | 1448.2037 | 2124.9132 | 2402.8725 | 2129.3928 | 2865.6446 | 2544.9921 | 2815.2068 | 3011.992 | 2930.6666 | 2930.6666 | 2930.6666 | 2930.6666 | 2930.6666 | 2930.6666 | 2930.6666 | 2930.6666 | 2930.6666 | 2930.6666 | 2930.6666 | 2930.6666 | 2930.6666 | 2930.6666 | 2930.6666 | 2930.6666
45% |  |  |  |  | 1.4778 | 19.8848 | 99.6465 | 540.2399 | 835.5875 | 611.6014 | 1285.4744 | 1399.845 | 1478.0382 | 1888.1516 | 1957.4354 | 1957.4354 | 1957.4354 | 1957.4354 | 1957.4354 | 1957.4354 | 1957.4354 | 1957.4354 | 1957.4354 | 1957.4354 | 1957.4354 | 1957.4354 | 1957.4354 | 1957.4354 | 1957.4354 | 1957.4354 |  |  | 108.0115 | 150.3451 | 351.7636 | 345.5838 | 396.2841 | 615.3004 | 1254.4644 | 1517.0019 | 1258.6955 | 1954.0982 | 1651.2363 | 1906.4589 | 2092.3259 | 2015.5127 | 2015.5127 | 2015.5127 | 2015.5127 | 2015.5127 | 2015.5127 | 2015.5127 | 2015.5127 | 2015.5127 | 2015.5127 | 2015.5127 | 2015.5127 | 2015.5127 | 2015.5127 | 2015.5127 | 2015.5127
40% | [7 empty] | 5.2227 | 77.4224 | 15.0517 | 335.4276 | 426.8776 | 495.0208 | 865.1983 | 927.7361 | 927.7361 | 927.7361 | 927.7361 | 927.7361 | 927.7361 | 927.7361 | 927.7361 | 927.7361 | 927.7361 | 927.7361 | 927.7361 | 927.7361 | 927.7361 | 927.7361 | 927.7361 | [7 empty] | 15.6969 | 312.356 | 530.1862 | 315.46 | 924.7239 | 651.3506 | 881.723 | 1049.4928 | 980.1586 | 980.1586 | 980.1586 | 980.1586 | 980.1586 | 980.1586 | 980.1586 | 980.1586 | 980.1586 | 980.1586 | 980.1586 | 980.1586 | 980.1586 | 980.1586 | 980.1586 | 980.1586
35% | FY38: 50.4629; FY39: 68.6417; FY40: 68.6417; FY41: 68.6417; FY42: 68.6417; FY43: 68.6417; FY44: 68.6417; FY45: 68.6417; FY46: 68.6417; FY47: 68.6417; FY48: 68.6417; FY49: 68.6417; FY50: 68.6417; FY51: 68.6417; FY52: 68.6417; FY53: 68.6417; FY54: 68.6417 | [9 empty] | 0.39794 |  | 67.7052 | 9.0043 | 55.007 | 111.5479 | 85.9137 | 85.9137 | 85.9137 | 85.9137 | 85.9137 | 85.9137 | 85.9137 | 85.9137 | 85.9137 | 85.9137 | 85.9137 | 85.9137 | 85.9137 | 85.9137 | 85.9137 | 85.9137
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 3575.8569 | 6590.5052 | 6980.2802 | 7493.5709 | 8183.3237 | 8844.8352 | 10043.4475 | 13325.7398 | 15218.6486 | 13775.5622 | 18248.5611 | 19044.4285 | 19594.1141 | 22539.7489 | 23046.9367 | 23046.9367 | 23046.9367 | 23046.9367 | 23046.9367 | 23046.9367 | 23046.9367 | 23046.9367 | 23046.9367 | 23046.9367 | 23046.9367 | 23046.9367 | 23046.9367 | 23046.9367 | 23046.9367 | 23046.9367 | E @ R (MWh) | 6567.7177 | 10136.1917 | 10564.7268 | 12135.7929 | 12094.1745 | 12427.7058 | 13799.013 | 18034.479 | 19869.614 | 18063.6457 | 23022.447 | 20825.921 | 22673.5093 | 24041.8335 | 23474.1016 | 23474.1016 | 23474.1016 | 23474.1016 | 23474.1016 | 23474.1016 | 23474.1016 | 23474.1016 | 23474.1016 | 23474.1016 | 23474.1016 | 23474.1016 | 23474.1016 | 23474.1016 | 23474.1016 | 23474.1016
Option 5 Winter POE50 W E @ R (MWh) N 2 | 2503.0998 | 4613.3536 | 4886.1961 | 5245.4996 | 5728.3266 | 6191.3846 | 7030.4133 | 9328.0178 | 10653.054 | 9642.8935 | 12773.9928 | 13331.1 | 13715.8799 | 15777.8242 | 16132.8557 | 16132.8557 | 16132.8557 | 16132.8557 | 16132.8557 | 16132.8557 | 16132.8557 | 16132.8557 | 16132.8557 | 16132.8557 | 16132.8557 | 16132.8557 | 16132.8557 | 16132.8557 | 16132.8557 | 16132.8557 | Option 5 Winter POE10 W E @ R (MWh) N 2 | 1970.3153 | 3040.8575 | 3169.418 | 3640.7379 | 3628.2524 | 3728.3118 | 4139.7039 | 5410.3437 | 5960.8842 | 5419.0937 | 6906.7341 | 6247.7763 | 6802.0528 | 7212.5501 | 7042.2305 | 7042.2305 | 7042.2305 | 7042.2305 | 7042.2305 | 7042.2305 | 7042.2305 | 7042.2305 | 7042.2305 | 7042.2305 | 7042.2305 | 7042.2305 | 7042.2305 | 7042.2305 | 7042.2305 | 7042.2305
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | 5.7999 | 6.7437 | 6.8461 | 6.7976 | 6.8459 | 6.8603 | 6.9134 | 7.026 | 7.1272 | 7.171 | 7.1135 | 7.2911 | 7.3036 | 7.2581 | 7.3336 | 7.375 | 7.375 | 7.375 | 7.375 | 7.375 | 7.375 | 7.375 | 7.375 | 7.375 | 7.375 | 7.375 | 7.375 | 7.375 | 7.375 | 7.375 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
98% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
97% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 8.713 | 9.7586 | 9.7874 | 9.7563 | 9.7643 | 9.8214 | 9.9371 | 10.1409 | 10.2471 | 10.3239 | 10.4401 | 10.5886 | 10.768 | 10.8621 | 10.8316 | 10.8722 | 10.8722 | 10.8722 | 10.8722 | 10.8722 | 10.8722 | 10.8722 | 10.8722 | 10.8722 | 10.8722 | 10.8722 | 10.8722 | 10.8722 | 10.8722 | 10.8722
95% | 5.3611 | 6.2717 | 6.3705 | 6.3237 | 6.3703 | 6.3842 | 6.4355 | 6.5441 | 6.6417 | 6.684 | 6.6285 | 6.7998 | 6.8119 | 6.768 | 6.8408 | 6.8808 | 6.8808 | 6.8808 | 6.8808 | 6.8808 | 6.8808 | 6.8808 | 6.8808 | 6.8808 | 6.8808 | 6.8808 | 6.8808 | 6.8808 | 6.8808 | 6.8808 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
90% | 108.291 | 127.5924 | 129.6878 | 128.6954 | 129.6831 | 129.979 | 131.0647 | 133.367 | 135.4372 | 136.333 | 135.157 | 138.788 | 139.0452 | 138.1144 | 139.6576 | 140.5041 | 140.5041 | 140.5041 | 140.5041 | 140.5041 | 140.5041 | 140.5041 | 140.5041 | 140.5041 | 140.5041 | 140.5041 | 140.5041 | 140.5041 | 140.5041 | 140.5041 |  | 7.9239 | 8.9158 | 8.9432 | 8.9137 | 8.9213 | 8.9755 | 9.0852 | 9.2786 | 9.3793 | 9.4522 | 9.5625 | 9.7033 | 9.8735 | 9.9628 | 9.9338 | 9.9723 | 9.9723 | 9.9723 | 9.9723 | 9.9723 | 9.9723 | 9.9723 | 9.9723 | 9.9723 | 9.9723 | 9.9723 | 9.9723 | 9.9723 | 9.9723 | 9.9723
85% | 356.523 | 425.4059 | 432.8838 | 429.3421 | 432.8671 | 433.923 | 437.7978 | 446.0142 | 453.4022 | 456.5993 | 452.4022 | 465.3607 | 466.2784 | 462.9567 | 468.4639 | 471.4849 | 471.4849 | 471.4849 | 471.4849 | 471.4849 | 471.4849 | 471.4849 | 471.4849 | 471.4849 | 471.4849 | 471.4849 | 471.4849 | 471.4849 | 471.4849 | 471.4849 |  | 7.1348 | 8.0731 | 8.099 | 8.0711 | 8.0783 | 8.1295 | 8.2333 | 8.4162 | 8.5115 | 8.5804 | 8.6848 | 8.818 | 8.979 | 9.0635 | 9.0361 | 9.0725 | 9.0725 | 9.0725 | 9.0725 | 9.0725 | 9.0725 | 9.0725 | 9.0725 | 9.0725 | 9.0725 | 9.0725 | 9.0725 | 9.0725 | 9.0725 | 9.0725
80% | 524.6094 | 636.5055 | 648.653 | 642.8997 | 648.6259 | 650.3411 | 656.6355 | 669.9826 | 681.984 | 687.1775 | 680.3595 | 701.4098 | 702.9005 | 697.5046 | 706.4507 | 711.3583 | 711.3583 | 711.3583 | 711.3583 | 711.3583 | 711.3583 | 711.3583 | 711.3583 | 711.3583 | 711.3583 | 711.3583 | 711.3583 | 711.3583 | 711.3583 | 711.3583 |  | 25.3829 | 28.9216 | 29.0192 | 28.9139 | 28.941 | 29.1342 | 29.5259 | 30.2155 | 30.5749 | 30.8349 | 31.2284 | 31.7307 | 32.3382 | 32.6566 | 32.5534 | 32.6906 | 32.6906 | 32.6906 | 32.6906 | 32.6906 | 32.6906 | 32.6906 | 32.6906 | 32.6906 | 32.6906 | 32.6906 | 32.6906 | 32.6906 | 32.6906 | 32.6906
75% | 824.3107 | 1023.5138 | 1045.1394 | 1034.8969 | 1045.0911 | 1048.1446 | 1059.3501 | 1083.1113 | 1104.4767 | 1113.7225 | 1101.5848 | 1139.0596 | 1141.7134 | 1132.1074 | 1148.0337 | 1156.7703 | 1156.7703 | 1156.7703 | 1156.7703 | 1156.7703 | 1156.7703 | 1156.7703 | 1156.7703 | 1156.7703 | 1156.7703 | 1156.7703 | 1156.7703 | 1156.7703 | 1156.7703 | 1156.7703 |  | 11.1132 | 12.7753 | 12.8212 | 12.7717 | 12.7845 | 12.8752 | 13.0592 | 13.3831 | 13.5519 | 13.674 | 13.8588 | 14.0948 | 14.3801 | 14.5296 | 14.4812 | 14.5456 | 14.5456 | 14.5456 | 14.5456 | 14.5456 | 14.5456 | 14.5456 | 14.5456 | 14.5456 | 14.5456 | 14.5456 | 14.5456 | 14.5456 | 14.5456 | 14.5456
70% | 893.5042 | 1147.9322 | 1175.5531 | 1162.4711 | 1175.4915 | 1179.3914 | 1193.7034 | 1224.0519 | 1251.3405 | 1263.1494 | 1247.6467 | 1295.5107 | 1298.9002 | 1286.6312 | 1306.9727 | 1318.1314 | 1318.1314 | 1318.1314 | 1318.1314 | 1318.1314 | 1318.1314 | 1318.1314 | 1318.1314 | 1318.1314 | 1318.1314 | 1318.1314 | 1318.1314 | 1318.1314 | 1318.1314 | 1318.1314 |  | 28.605 | 33.2696 | 33.3983 | 33.2596 | 33.2952 | 33.55 | 34.0662 | 34.9753 | 35.449 | 35.7918 | 36.3104 | 36.9726 | 37.7734 | 38.193 | 38.057 | 38.2379 | 38.2379 | 38.2379 | 38.2379 | 38.2379 | 38.2379 | 38.2379 | 38.2379 | 38.2379 | 38.2379 | 38.2379 | 38.2379 | 38.2379 | 38.2379 | 38.2379
65% | 872.5518 | 1184.9789 | 1218.8962 | 1202.832 | 1218.8205 | 1223.6095 | 1241.184 | 1278.4508 | 1311.96 | 1326.4609 | 1307.4242 | 1366.1992 | 1370.3613 | 1355.2955 | 1380.274 | 1393.9764 | 1393.9764 | 1393.9764 | 1393.9764 | 1393.9764 | 1393.9764 | 1393.9764 | 1393.9764 | 1393.9764 | 1393.9764 | 1393.9764 | 1393.9764 | 1393.9764 | 1393.9764 | 1393.9764 |  | 7.9568 | 9.4044 | 9.4444 | 9.4013 | 9.4124 | 9.4914 | 9.6516 | 9.9338 | 10.0808 | 10.1872 | 10.3481 | 10.5536 | 10.8021 | 10.9324 | 10.8902 | 10.9463 | 10.9463 | 10.9463 | 10.9463 | 10.9463 | 10.9463 | 10.9463 | 10.9463 | 10.9463 | 10.9463 | 10.9463 | 10.9463 | 10.9463 | 10.9463 | 10.9463
60% | 894.0897 | 1350.5426 | 1400.0953 | 1376.6258 | 1399.9848 | 1406.9815 | 1432.6576 | 1487.104 | 1536.0606 | 1557.2463 | 1529.4339 | 1615.3035 | 1621.3844 | 1599.3734 | 1635.8667 | 1655.8858 | 1655.8858 | 1655.8858 | 1655.8858 | 1655.8858 | 1655.8858 | 1655.8858 | 1655.8858 | 1655.8858 | 1655.8858 | 1655.8858 | 1655.8858 | 1655.8858 | 1655.8858 | 1655.8858 |  | 41.4606 | 50.1733 | 50.4137 | 50.1545 | 50.2211 | 50.6969 | 51.6611 | 53.3592 | 54.244 | 54.8842 | 55.853 | 57.0898 | 58.5855 | 59.3693 | 59.1152 | 59.4532 | 59.4532 | 59.4532 | 59.4532 | 59.4532 | 59.4532 | 59.4532 | 59.4532 | 59.4532 | 59.4532 | 59.4532 | 59.4532 | 59.4532 | 59.4532 | 59.4532
55% | 550.324 | 1112.0573 | 1173.0394 | 1144.1567 | 1172.9034 | 1181.5138 | 1213.1122 | 1280.1165 | 1340.365 | 1366.4371 | 1332.2099 | 1437.8852 | 1445.3686 | 1418.2808 | 1463.1913 | 1487.8278 | 1487.8278 | 1487.8278 | 1487.8278 | 1487.8278 | 1487.8278 | 1487.8278 | 1487.8278 | 1487.8278 | 1487.8278 | 1487.8278 | 1487.8278 | 1487.8278 | 1487.8278 | 1487.8278 |  | 153.6106 | 193.0724 | 194.1613 | 192.9873 | 193.2892 | 195.4441 | 199.8112 | 207.5023 | 211.5098 | 214.4091 | 218.797 | 224.3991 | 231.1732 | 234.7234 | 233.5725 | 235.1033 | 235.1033 | 235.1033 | 235.1033 | 235.1033 | 235.1033 | 235.1033 | 235.1033 | 235.1033 | 235.1033 | 235.1033 | 235.1033 | 235.1033 | 235.1033 | 235.1033
50% | 49.8038 | 518.8905 | 588.0842 | 555.3122 | 587.9298 | 597.6998 | 633.553 | 709.5799 | 777.9412 | 807.5241 | 768.6879 | 888.5931 | 897.0842 | 866.3488 | 917.3068 | 945.2607 | 945.2607 | 945.2607 | 945.2607 | 945.2607 | 945.2607 | 945.2607 | 945.2607 | 945.2607 | 945.2607 | 945.2607 | 945.2607 | 945.2607 | 945.2607 | 945.2607 |  | 254.5469 | 343.4966 | 345.9512 | 343.3048 | 343.9854 | 348.8427 | 358.6866 | 376.0227 | 385.056 | 391.5912 | 401.4819 | 414.1094 | 429.3788 | 437.3811 | 434.7869 | 438.2375 | 438.2375 | 438.2375 | 438.2375 | 438.2375 | 438.2375 | 438.2375 | 438.2375 | 438.2375 | 438.2375 | 438.2375 | 438.2375 | 438.2375 | 438.2375 | 438.2375
45% |  | 4.0437 | 12.3523 | 7.8614 | 12.3288 | 13.8581 | 20.2188 | 37.5481 | 57.5019 | 67.3962 | 54.5623 | 98.3355 | 101.8963 | 89.2935 | 110.6183 | 123.2319 | 123.2319 | 123.2319 | 123.2319 | 123.2319 | 123.2319 | 123.2319 | 123.2319 | 123.2319 | 123.2319 | 123.2319 | 123.2319 | 123.2319 | 123.2319 | 123.2319 |  | 246.5838 | 399.3908 | 403.6075 | 399.0613 | 400.2304 | 408.5749 | 425.4856 | 455.2675 | 470.7857 | 482.0126 | 499.0039 | 520.6967 | 546.9281 | 560.6753 | 556.2186 | 562.1463 | 562.1463 | 562.1463 | 562.1463 | 562.1463 | 562.1463 | 562.1463 | 562.1463 | 562.1463 | 562.1463 | 562.1463 | 562.1463 | 562.1463 | 562.1463 | 562.1463
40% | [31 empty] | 52.5459 | 221.8136 | 227.523 | 221.3674 | 222.9505 | 234.2491 | 257.1469 | 297.4726 | 318.4848 | 333.6864 | 356.6932 | 386.066 | 421.5842 | 440.1984 | 434.1639 | 442.1902 | 442.1902 | 442.1902 | 442.1902 | 442.1902 | 442.1902 | 442.1902 | 442.1902 | 442.1902 | 442.1902 | 442.1902 | 442.1902 | 442.1902 | 442.1902 | 442.1902
35% | [32 empty] | 2.2408 | 3.094 | 2.1798 | 2.3998 | 4.273 | 9.6808 | 24.3349 | 34.4988 | 42.9073 | 57.2889 | 78.4903 | 108.2743 | 125.6526 | 119.8874 | 127.5832 | 127.5832 | 127.5832 | 127.5832 | 127.5832 | 127.5832 | 127.5832 | 127.5832 | 127.5832 | 127.5832 | 127.5832 | 127.5832 | 127.5832 | 127.5832 | 127.5832
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 5034.3169 | 7469.0333 | 7759.2251 | 7621.2324 | 7758.5728 | 7799.8996 | 7952.2997 | 8279.2674 | 8577.5958 | 8707.9423 | 8536.9782 | 9068.9308 | 9107.0574 | 8969.3332 | 9198.1001 | 9324.5005 | 9324.5005 | 9324.5005 | 9324.5005 | 9324.5005 | 9324.5005 | 9324.5005 | 9324.5005 | 9324.5005 | 9324.5005 | 9324.5005 | 9324.5005 | 9324.5005 | 9324.5005 | 9324.5005 | E @ R (MWh) | 837.1218 | 1308.0928 | 1322.9007 | 1306.9412 | 1311.0306 | 1340.5173 | 1401.8704 | 1514.9996 | 1576.4498 | 1621.9517 | 1692.4555 | 1785.2798 | 1901.6302 | 1964.358 | 1943.8924 | 1971.1407 | 1971.1407 | 1971.1407 | 1971.1407 | 1971.1407 | 1971.1407 | 1971.1407 | 1971.1407 | 1971.1407 | 1971.1407 | 1971.1407 | 1971.1407 | 1971.1407 | 1971.1407 | 1971.1407
Option 5 Summer POE50 W E @ R (MWh) N 2 | 3524.0218 | 5228.3233 | 5431.4576 | 5334.8627 | 5431.001 | 5459.9297 | 5566.6098 | 5795.4872 | 6004.317 | 6095.5596 | 5975.8848 | 6348.2515 | 6374.9402 | 6278.5332 | 6438.6701 | 6527.1503 | 6527.1503 | 6527.1503 | 6527.1503 | 6527.1503 | 6527.1503 | 6527.1503 | 6527.1503 | 6527.1503 | 6527.1503 | 6527.1503 | 6527.1503 | 6527.1503 | 6527.1503 | 6527.1503 | Option 5 Summer POE10 W E @ R (MWh) N 2 | 251.1365 | 392.4278 | 396.8702 | 392.0824 | 393.3092 | 402.1552 | 420.5611 | 454.4999 | 472.9349 | 486.5855 | 507.7367 | 535.5839 | 570.4891 | 589.3074 | 583.1677 | 591.3422 | 591.3422 | 591.3422 | 591.3422 | 591.3422 | 591.3422 | 591.3422 | 591.3422 | 591.3422 | 591.3422 | 591.3422 | 591.3422 | 591.3422 | 591.3422 | 591.3422
Option 6 -
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | 5.1211 | 6.2192 | 6.3356 | 6.4796 | 6.6707 | 6.8519 | 7.1685 | 7.9649 | 8.3933 | 8.0808 | 9.0482 | 9.2225 | 9.3478 | 9.9384 | 10.0346 | 10.0346 | 10.0346 | 10.0346 | 10.0346 | 10.0346 | 10.0346 | 10.0346 | 10.0346 | 10.0346 | 10.0346 | 10.0346 | 10.0346 | 10.0346 | 10.0346 | 10.0346 |  | 6.1303 | 7.1777 | 7.2862 | 7.6605 | 7.6514 | 7.7337 | 8.0557 | 8.9806 | 9.3623 | 9.001 | 9.9991 | 9.58 | 9.9571 | 10.2288 | 10.1171 | 10.1171 | 10.1171 | 10.1171 | 10.1171 | 10.1171 | 10.1171 | 10.1171 | 10.1171 | 10.1171 | 10.1171 | 10.1171 | 10.1171 | 10.1171 | 10.1171 | 10.1171
98% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
97% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
95% | 19.0092 | 23.247 | 23.6963 | 24.2519 | 24.9895 | 25.6887 | 26.9107 | 29.9842 | 31.6373 | 30.4313 | 34.165 | 34.8377 | 35.3212 | 37.6005 | 37.9715 | 37.9715 | 37.9715 | 37.9715 | 37.9715 | 37.9715 | 37.9715 | 37.9715 | 37.9715 | 37.9715 | 37.9715 | 37.9715 | 37.9715 | 37.9715 | 37.9715 | 37.9715 |  | 22.9039 | 26.9462 | 27.3648 | 28.8095 | 28.7742 | 29.0919 | 30.3344 | 33.9041 | 35.3771 | 33.9828 | 37.8346 | 36.2174 | 37.6725 | 38.7211 | 38.2903 | 38.2903 | 38.2903 | 38.2903 | 38.2903 | 38.2903 | 38.2903 | 38.2903 | 38.2903 | 38.2903 | 38.2903 | 38.2903 | 38.2903 | 38.2903 | 38.2903 | 38.2903
90% | 105.2028 | 129.7026 | 132.3005 | 135.5122 | 139.7764 | 143.8191 | 150.8839 | 168.6524 | 178.2095 | 171.2373 | 192.8224 | 196.7114 | 199.5069 | 212.6842 | 214.8291 | 214.8291 | 214.8291 | 214.8291 | 214.8291 | 214.8291 | 214.8291 | 214.8291 | 214.8291 | 214.8291 | 214.8291 | 214.8291 | 214.8291 | 214.8291 | 214.8291 | 214.8291 |  | 127.7194 | 151.0886 | 153.5087 | 161.8608 | 161.6572 | 163.4938 | 170.6769 | 191.314 | 199.8301 | 191.769 | 214.0372 | 204.6878 | 213.1003 | 219.1625 | 216.6718 | 216.6718 | 216.6718 | 216.6718 | 216.6718 | 216.6718 | 216.6718 | 216.6718 | 216.6718 | 216.6718 | 216.6718 | 216.6718 | 216.6718 | 216.6718 | 216.6718 | 216.6718
85% | 408.7931 | 511.1512 | 522.005 | 535.4235 | 553.2391 | 570.1289 | 599.6452 | 673.8807 | 713.8099 | 684.6804 | 774.8612 | 791.1091 | 802.7887 | 857.8426 | 866.8037 | 866.8037 | 866.8037 | 866.8037 | 866.8037 | 866.8037 | 866.8037 | 866.8037 | 866.8037 | 866.8037 | 866.8037 | 866.8037 | 866.8037 | 866.8037 | 866.8037 | 866.8037 |  | 502.8656 | 600.5006 | 610.6116 | 645.5059 | 644.6555 | 652.3285 | 682.3388 | 768.5594 | 804.1392 | 770.4602 | 863.495 | 824.4339 | 859.5808 | 884.9083 | 874.5026 | 874.5026 | 874.5026 | 874.5026 | 874.5026 | 874.5026 | 874.5026 | 874.5026 | 874.5026 | 874.5026 | 874.5026 | 874.5026 | 874.5026 | 874.5026 | 874.5026 | 874.5026
80% | 592.6734 | 754.7359 | 771.9205 | 793.1658 | 821.3732 | 848.1145 | 894.8474 | 1012.3836 | 1075.6029 | 1029.4825 | 1172.2649 | 1197.99 | 1216.482 | 1303.6484 | 1317.8363 | 1317.8363 | 1317.8363 | 1317.8363 | 1317.8363 | 1317.8363 | 1317.8363 | 1317.8363 | 1317.8363 | 1317.8363 | 1317.8363 | 1317.8363 | 1317.8363 | 1317.8363 | 1317.8363 | 1317.8363 |  | 741.6174 | 896.2017 | 912.2103 | 967.4581 | 966.1116 | 978.2602 | 1025.7752 | 1162.2872 | 1218.6203 | 1165.2967 | 1312.5977 | 1250.7528 | 1306.4003 | 1346.5011 | 1330.0258 | 1330.0258 | 1330.0258 | 1330.0258 | 1330.0258 | 1330.0258 | 1330.0258 | 1330.0258 | 1330.0258 | 1330.0258 | 1330.0258 | 1330.0258 | 1330.0258 | 1330.0258 | 1330.0258 | 1330.0258
75% | 980.9496 | 1280.2989 | 1312.0411 | 1351.2837 | 1403.3862 | 1452.7807 | 1539.1021 | 1756.2058 | 1872.9798 | 1787.7897 | 2051.5263 | 2099.0437 | 2133.2008 | 2294.2077 | 2320.4147 | 2320.4147 | 2320.4147 | 2320.4147 | 2320.4147 | 2320.4147 | 2320.4147 | 2320.4147 | 2320.4147 | 2320.4147 | 2320.4147 | 2320.4147 | 2320.4147 | 2320.4147 | 2320.4147 | 2320.4147 |  | 1256.0675 | 1541.6038 | 1571.1735 | 1673.2229 | 1670.7358 | 1693.1758 | 1780.9419 | 2033.0964 | 2137.1505 | 2038.6552 | 2310.7383 | 2196.5031 | 2299.291 | 2373.362 | 2342.9301 | 2342.9301 | 2342.9301 | 2342.9301 | 2342.9301 | 2342.9301 | 2342.9301 | 2342.9301 | 2342.9301 | 2342.9301 | 2342.9301 | 2342.9301 | 2342.9301 | 2342.9301 | 2342.9301 | 2342.9301
70% | 1385.9626 | 1873.2259 | 1924.894 | 1988.7709 | 2073.5802 | 2153.9818 | 2294.4906 | 2647.8796 | 2837.9574 | 2699.29 | 3128.585 | 3205.9311 | 3261.5301 | 3523.6078 | 3566.266 | 3566.266 | 3566.266 | 3566.266 | 3566.266 | 3566.266 | 3566.266 | 3566.266 | 3566.266 | 3566.266 | 3566.266 | 3566.266 | 3566.266 | 3566.266 | 3566.266 | 3566.266 |  | 1833.7834 | 2298.5628 | 2346.6947 | 2512.8048 | 2508.7564 | 2545.283 | 2688.1435 | 3098.5859 | 3267.9592 | 3107.6342 | 3550.5153 | 3364.5698 | 3531.882 | 3652.4506 | 3602.9153 | 3602.9153 | 3602.9153 | 3602.9153 | 3602.9153 | 3602.9153 | 3602.9153 | 3602.9153 | 3602.9153 | 3602.9153 | 3602.9153 | 3602.9153 | 3602.9153 | 3602.9153 | 3602.9153 | 3602.9153
65% | 1400.8592 | 1997.5436 | 2060.8145 | 2139.0357 | 2242.8901 | 2341.3468 | 2513.4087 | 2946.1556 | 3178.9178 | 3009.1109 | 3534.8094 | 3629.5246 | 3697.6091 | 4018.5396 | 4070.7772 | 4070.7772 | 4070.7772 | 4070.7772 | 4070.7772 | 4070.7772 | 4070.7772 | 4070.7772 | 4070.7772 | 4070.7772 | 4070.7772 | 4070.7772 | 4070.7772 | 4070.7772 | 4070.7772 | 4070.7772 |  | 1949.2438 | 2518.3953 | 2577.3359 | 2780.7481 | 2775.7906 | 2820.5196 | 2995.4612 | 3498.0737 | 3705.4819 | 3509.1539 | 4051.4896 | 3823.7877 | 4028.6719 | 4176.3156 | 4115.6566 | 4115.6566 | 4115.6566 | 4115.6566 | 4115.6566 | 4115.6566 | 4115.6566 | 4115.6566 | 4115.6566 | 4115.6566 | 4115.6566 | 4115.6566 | 4115.6566 | 4115.6566 | 4115.6566 | 4115.6566
60% | 1311.1794 | 2051.2755 | 2129.7534 | 2226.7749 | 2355.5904 | 2477.711 | 2691.1276 | 3227.8842 | 3516.5903 | 3305.9706 | 3958.0197 | 4075.4994 | 4159.9479 | 4558.0133 | 4622.8061 | 4622.8061 | 4622.8061 | 4622.8061 | 4622.8061 | 4622.8061 | 4622.8061 | 4622.8061 | 4622.8061 | 4622.8061 | 4622.8061 | 4622.8061 | 4622.8061 | 4622.8061 | 4622.8061 | 4622.8061 |  | 1991.367 | 2697.3127 | 2770.4195 | 3022.7214 | 3016.5724 | 3072.052 | 3289.0403 | 3912.4546 | 4169.7129 | 3926.1979 | 4598.8827 | 4316.4532 | 4570.5808 | 4753.7104 | 4678.4721 | 4678.4721 | 4678.4721 | 4678.4721 | 4678.4721 | 4678.4721 | 4678.4721 | 4678.4721 | 4678.4721 | 4678.4721 | 4678.4721 | 4678.4721 | 4678.4721 | 4678.4721 | 4678.4721 | 4678.4721
55% | 879.254 | 1681.979 | 1767.0979 | 1872.3296 | 2012.0458 | 2144.5006 | 2375.977 | 2958.1553 | 3271.2924 | 3042.8496 | 3750.0767 | 3877.4979 | 3969.0926 | 4400.8433 | 4471.1191 | 4471.1191 | 4471.1191 | 4471.1191 | 4471.1191 | 4471.1191 | 4471.1191 | 4471.1191 | 4471.1191 | 4471.1191 | 4471.1191 | 4471.1191 | 4471.1191 | 4471.1191 | 4471.1191 | 4471.1191 |  | 1617.0008 | 2382.6855 | 2461.9788 | 2735.6311 | 2728.9617 | 2789.1362 | 3024.4867 | 3700.6558 | 3979.6839 | 3715.5621 | 4445.1712 | 4138.8418 | 4414.4743 | 4613.1009 | 4531.4957 | 4531.4957 | 4531.4957 | 4531.4957 | 4531.4957 | 4531.4957 | 4531.4957 | 4531.4957 | 4531.4957 | 4531.4957 | 4531.4957 | 4531.4957 | 4531.4957 | 4531.4957 | 4531.4957 | 4531.4957
50% | 249.4213 | 1054.7724 | 1141.4594 | 1248.6298 | 1390.9199 | 1525.8148 | 1761.5555 | 2354.459 | 2673.3649 | 2440.7136 | 3160.9695 | 3290.738 | 3384.0202 | 3823.7248 | 3895.2952 | 3895.2952 | 3895.2952 | 3895.2952 | 3895.2952 | 3895.2952 | 3895.2952 | 3895.2952 | 3895.2952 | 3895.2952 | 3895.2952 | 3895.2952 | 3895.2952 | 3895.2952 | 3895.2952 | 3895.2952 |  | 988.5972 | 1768.3876 | 1849.1417 | 2127.8353 | 2121.0431 | 2182.3261 | 2422.0123 | 3110.6381 | 3394.8066 | 3125.819 | 3868.8693 | 3556.8965 | 3837.6069 | 4039.8926 | 3956.7841 | 3956.7841 | 3956.7841 | 3956.7841 | 3956.7841 | 3956.7841 | 3956.7841 | 3956.7841 | 3956.7841 | 3956.7841 | 3956.7841 | 3956.7841 | 3956.7841 | 3956.7841 | 3956.7841 | 3956.7841
45% |  | 263.6586 | 332.2401 | 426.8754 | 561.1949 | 688.6055 | 911.2667 | 1471.2745 | 1772.4867 | 1552.7434 | 2233.0378 | 2355.6065 | 2443.7131 | 2859.0218 | 2926.6213 | 2926.6213 | 2926.6213 | 2926.6213 | 2926.6213 | 2926.6213 | 2926.6213 | 2926.6213 | 2926.6213 | 2926.6213 | 2926.6213 | 2926.6213 | 2926.6213 | 2926.6213 | 2926.6213 | 2926.6213 |  | 216.2457 | 917.7197 | 993.9934 | 1257.2244 | 1250.8091 | 1308.6919 | 1535.0798 | 2185.4989 | 2453.9011 | 2199.8376 | 2901.6616 | 2606.9978 | 2872.1337 | 3063.1961 | 2984.6986 | 2984.6986 | 2984.6986 | 2984.6986 | 2984.6986 | 2984.6986 | 2984.6986 | 2984.6986 | 2984.6986 | 2984.6986 | 2984.6986 | 2984.6986 | 2984.6986 | 2984.6986 | 2984.6986 | 2984.6986
40% |  |  |  |  | 7.5893 | 31.1945 | 108.8464 | 488.9496 | 760.7952 | 562.4477 | 1176.5041 | 1287.1386 | 1366.6666 | 1741.5381 | 1802.5557 | 1802.5557 | 1802.5557 | 1802.5557 | 1802.5557 | 1802.5557 | 1802.5557 | 1802.5557 | 1802.5557 | 1802.5557 | 1802.5557 | 1802.5557 | 1802.5557 | 1802.5557 | 1802.5557 | 1802.5557 |  |  | 111.7593 | 148.9205 | 314.3792 | 309.6857 | 353.1877 | 546.5039 | 1133.5939 | 1375.8626 | 1146.5364 | 1780.0262 | 1514.0529 | 1753.3734 | 1925.8327 | 1854.9782 | 1854.9782 | 1854.9782 | 1854.9782 | 1854.9782 | 1854.9782 | 1854.9782 | 1854.9782 | 1854.9782 | 1854.9782 | 1854.9782 | 1854.9782 | 1854.9782 | 1854.9782 | 1854.9782 | 1854.9782
35% | [8 empty] | 26.1432 | 1.6005 | 166.5253 | 222.5876 | 267.429 | 526.6894 | 574.0431 | 574.0431 | 574.0431 | 574.0431 | 574.0431 | 574.0431 | 574.0431 | 574.0431 | 574.0431 | 574.0431 | 574.0431 | 574.0431 | 574.0431 | 574.0431 | 574.0431 | 574.0431 | [7 empty] | 0.90619 | 146.8106 | 272.8539 | 152.6356 | 556.5587 | 360.2185 | 535.8744 | 669.7143 | 614.7265 | 614.7265 | 614.7265 | 614.7265 | 614.7265 | 614.7265 | 614.7265 | 614.7265 | 614.7265 | 614.7265 | 614.7265 | 614.7265 | 614.7265 | 614.7265 | 614.7265 | 614.7265
30% | FY38: 0.23254; FY39: 1.8503; FY40: 1.8503; FY41: 1.8503; FY42: 1.8503; FY43: 1.8503; FY44: 1.8503; FY45: 1.8503; FY46: 1.8503; FY47: 1.8503; FY48: 1.8503; FY49: 1.8503; FY50: 1.8503; FY51: 1.8503; FY52: 1.8503; FY53: 1.8503; FY54: 1.8503 | [11 empty] | 1.0747 |  | 0.42635 | 9.7196 | 4.4531 | 4.4531 | 4.4531 | 4.4531 | 4.4531 | 4.4531 | 4.4531 | 4.4531 | 4.4531 | 4.4531 | 4.4531 | 4.4531 | 4.4531 | 4.4531 | 4.4531 | 4.4531
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 7265.0415 | 11511.5317 | 12003.3126 | 12621.0477 | 13457.3132 | 14266.4334 | 15716.478 | 19546.391 | 21698.9988 | 20123.164 | 25089.7832 | 26010.7036 | 26677.1895 | 29866.4513 | 30392.2317 | 30392.2317 | 30392.2317 | 30392.2317 | 30392.2317 | 30392.2317 | 30392.2317 | 30392.2317 | 30392.2317 | 30392.2317 | 30392.2317 | 30392.2317 | 30392.2317 | 30392.2317 | 30392.2317 | 30392.2317 | E @ R (MWh) | 11141.0066 | 15759.1581 | 16266.3334 | 18053.5033 | 18009.2926 | 18409.3276 | 19997.7591 | 24734.6086 | 26754.4944 | 24841.616 | 30197.9216 | 27921.9531 | 29968.3153 | 31459.0485 | 30845.1507 | 30845.1507 | 30845.1507 | 30845.1507 | 30845.1507 | 30845.1507 | 30845.1507 | 30845.1507 | 30845.1507 | 30845.1507 | 30845.1507 | 30845.1507 | 30845.1507 | 30845.1507 | 30845.1507 | 30845.1507
Option 6 Winter POE50 W E @ R (MWh) N 2 | 5085.529 | 8058.0722 | 8402.3188 | 8834.7334 | 9420.1193 | 9986.5034 | 11001.5346 | 13682.4737 | 15189.2992 | 14086.2148 | 17562.8482 | 18207.4925 | 18674.0327 | 20906.5159 | 21274.5622 | 21274.5622 | 21274.5622 | 21274.5622 | 21274.5622 | 21274.5622 | 21274.5622 | 21274.5622 | 21274.5622 | 21274.5622 | 21274.5622 | 21274.5622 | 21274.5622 | 21274.5622 | 21274.5622 | 21274.5622 | Option 6 Winter POE10 W E @ R (MWh) N 2 | 3342.302 | 4727.7474 | 4879.9 | 5416.051 | 5402.7878 | 5522.7983 | 5999.3277 | 7420.3826 | 8026.3483 | 7452.4848 | 9059.3765 | 8376.5859 | 8990.4946 | 9437.7145 | 9253.5452 | 9253.5452 | 9253.5452 | 9253.5452 | 9253.5452 | 9253.5452 | 9253.5452 | 9253.5452 | 9253.5452 | 9253.5452 | 9253.5452 | 9253.5452 | 9253.5452 | 9253.5452 | 9253.5452 | 9253.5452
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | 7.3419 | 8.3902 | 8.4955 | 8.4439 | 8.493 | 8.5131 | 8.5778 | 8.7107 | 8.8225 | 8.874 | 8.8281 | 9.0205 | 9.051 | 9.0149 | 9.0873 | 9.1287 | 9.1287 | 9.1287 | 9.1287 | 9.1287 | 9.1287 | 9.1287 | 9.1287 | 9.1287 | 9.1287 | 9.1287 | 9.1287 | 9.1287 | 9.1287 | 9.1287 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
98% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
97% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 10.2241 | 11.372 | 11.4037 | 11.3695 | 11.3783 | 11.441 | 11.568 | 11.7917 | 11.9083 | 11.9926 | 12.1203 | 12.2833 | 12.4803 | 12.5836 | 12.5501 | 12.5907 | 12.5907 | 12.5907 | 12.5907 | 12.5907 | 12.5907 | 12.5907 | 12.5907 | 12.5907 | 12.5907 | 12.5907 | 12.5907 | 12.5907 | 12.5907 | 12.5907
95% | 6.8489 | 7.8602 | 7.9619 | 7.9121 | 7.9594 | 7.9789 | 8.0413 | 8.1695 | 8.2774 | 8.3271 | 8.2828 | 8.4684 | 8.4979 | 8.463 | 8.5329 | 8.5728 | 8.5728 | 8.5728 | 8.5728 | 8.5728 | 8.5728 | 8.5728 | 8.5728 | 8.5728 | 8.5728 | 8.5728 | 8.5728 | 8.5728 | 8.5728 | 8.5728 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
90% | 139.8285 | 161.2671 | 163.4215 | 162.3655 | 163.3696 | 163.7822 | 165.1044 | 167.8232 | 170.1105 | 171.1633 | 170.2249 | 174.1594 | 174.7834 | 174.0449 | 175.5257 | 176.3722 | 176.3722 | 176.3722 | 176.3722 | 176.3722 | 176.3722 | 176.3722 | 176.3722 | 176.3722 | 176.3722 | 176.3722 | 176.3722 | 176.3722 | 176.3722 | 176.3722 |  | 9.3575 | 10.4465 | 10.4766 | 10.4442 | 10.4525 | 10.512 | 10.6325 | 10.8447 | 10.9553 | 11.0354 | 11.1564 | 11.3111 | 11.498 | 11.596 | 11.5642 | 11.6027 | 11.6027 | 11.6027 | 11.6027 | 11.6027 | 11.6027 | 11.6027 | 11.6027 | 11.6027 | 11.6027 | 11.6027 | 11.6027 | 11.6027 | 11.6027 | 11.6027
85% | 469.0739 | 545.5841 | 553.2725 | 549.5038 | 553.0872 | 554.5596 | 559.2785 | 568.9815 | 577.144 | 580.9015 | 577.5525 | 591.5938 | 593.8207 | 591.1853 | 596.47 | 599.4911 | 599.4911 | 599.4911 | 599.4911 | 599.4911 | 599.4911 | 599.4911 | 599.4911 | 599.4911 | 599.4911 | 599.4911 | 599.4911 | 599.4911 | 599.4911 | 599.4911 |  | 8.4909 | 9.521 | 9.5495 | 9.5188 | 9.5267 | 9.583 | 9.697 | 9.8978 | 10.0024 | 10.0781 | 10.1926 | 10.3389 | 10.5157 | 10.6084 | 10.5783 | 10.6147 | 10.6147 | 10.6147 | 10.6147 | 10.6147 | 10.6147 | 10.6147 | 10.6147 | 10.6147 | 10.6147 | 10.6147 | 10.6147 | 10.6147 | 10.6147 | 10.6147
80% | 707.4418 | 831.7279 | 844.2173 | 838.0953 | 843.9164 | 846.3082 | 853.9736 | 869.7356 | 882.9952 | 889.099 | 883.6587 | 906.4679 | 910.0855 | 905.8043 | 914.3891 | 919.2966 | 919.2966 | 919.2966 | 919.2966 | 919.2966 | 919.2966 | 919.2966 | 919.2966 | 919.2966 | 919.2966 | 919.2966 | 919.2966 | 919.2966 | 919.2966 | 919.2966 |  | 30.4971 | 34.3823 | 34.4895 | 34.3739 | 34.4037 | 34.6158 | 35.0458 | 35.803 | 36.1976 | 36.4831 | 36.9151 | 37.4666 | 38.1336 | 38.4831 | 38.3698 | 38.5071 | 38.5071 | 38.5071 | 38.5071 | 38.5071 | 38.5071 | 38.5071 | 38.5071 | 38.5071 | 38.5071 | 38.5071 | 38.5071 | 38.5071 | 38.5071 | 38.5071
75% | 1149.798 | 1371.0584 | 1393.2926 | 1382.3939 | 1392.7569 | 1397.0149 | 1410.6614 | 1438.7215 | 1462.327 | 1473.1933 | 1463.5082 | 1504.1143 | 1510.5546 | 1502.933 | 1518.216 | 1526.9526 | 1526.9526 | 1526.9526 | 1526.9526 | 1526.9526 | 1526.9526 | 1526.9526 | 1526.9526 | 1526.9526 | 1526.9526 | 1526.9526 | 1526.9526 | 1526.9526 | 1526.9526 | 1526.9526 |  | 13.5153 | 15.3402 | 15.3906 | 15.3363 | 15.3503 | 15.4499 | 15.6519 | 16.0075 | 16.1929 | 16.3269 | 16.5299 | 16.7889 | 17.1022 | 17.2664 | 17.2131 | 17.2776 | 17.2776 | 17.2776 | 17.2776 | 17.2776 | 17.2776 | 17.2776 | 17.2776 | 17.2776 | 17.2776 | 17.2776 | 17.2776 | 17.2776 | 17.2776 | 17.2776
70% | 1309.2261 | 1591.8262 | 1620.2245 | 1606.3043 | 1619.5402 | 1624.9786 | 1642.4083 | 1678.2476 | 1708.3971 | 1722.2759 | 1709.9059 | 1761.7692 | 1769.9948 | 1760.2603 | 1779.7801 | 1790.9388 | 1790.9388 | 1790.9388 | 1790.9388 | 1790.9388 | 1790.9388 | 1790.9388 | 1790.9388 | 1790.9388 | 1790.9388 | 1790.9388 | 1790.9388 | 1790.9388 | 1790.9388 | 1790.9388 |  | 35.3464 | 40.4679 | 40.6092 | 40.4568 | 40.496 | 40.7757 | 41.3425 | 42.3407 | 42.8608 | 43.237 | 43.8065 | 44.5336 | 45.4128 | 45.8735 | 45.7241 | 45.9051 | 45.9051 | 45.9051 | 45.9051 | 45.9051 | 45.9051 | 45.9051 | 45.9051 | 45.9051 | 45.9051 | 45.9051 | 45.9051 | 45.9051 | 45.9051 | 45.9051
65% | 1383.0411 | 1730.0625 | 1764.9344 | 1747.8411 | 1764.0942 | 1770.7723 | 1792.1753 | 1836.1844 | 1873.2068 | 1890.2494 | 1875.0595 | 1938.7455 | 1948.8462 | 1936.8927 | 1960.8622 | 1974.5646 | 1974.5646 | 1974.5646 | 1974.5646 | 1974.5646 | 1974.5646 | 1974.5646 | 1974.5646 | 1974.5646 | 1974.5646 | 1974.5646 | 1974.5646 | 1974.5646 | 1974.5646 | 1974.5646 |  | 10.0489 | 11.6384 | 11.6822 | 11.6349 | 11.6471 | 11.7339 | 11.9098 | 12.2196 | 12.381 | 12.4978 | 12.6745 | 12.9001 | 13.173 | 13.316 | 13.2696 | 13.3258 | 13.3258 | 13.3258 | 13.3258 | 13.3258 | 13.3258 | 13.3258 | 13.3258 | 13.3258 | 13.3258 | 13.3258 | 13.3258 | 13.3258 | 13.3258 | 13.3258
60% | 1639.9094 | 2146.9041 | 2197.8516 | 2172.8784 | 2196.624 | 2206.3807 | 2237.6502 | 2301.9471 | 2356.0365 | 2380.9355 | 2358.7431 | 2451.7877 | 2466.5448 | 2449.0808 | 2484.1001 | 2504.1192 | 2504.1192 | 2504.1192 | 2504.1192 | 2504.1192 | 2504.1192 | 2504.1192 | 2504.1192 | 2504.1192 | 2504.1192 | 2504.1192 | 2504.1192 | 2504.1192 | 2504.1192 | 2504.1192 |  | 54.0524 | 63.6183 | 63.8823 | 63.5977 | 63.6709 | 64.1933 | 65.2519 | 67.1163 | 68.0878 | 68.7906 | 69.8543 | 71.2123 | 72.8544 | 73.715 | 73.436 | 73.774 | 73.774 | 73.774 | 73.774 | 73.774 | 73.774 | 73.774 | 73.774 | 73.774 | 73.774 | 73.774 | 73.774 | 73.774 | 73.774 | 73.774
55% | 1468.1665 | 2092.0991 | 2154.7976 | 2124.0644 | 2153.2869 | 2165.294 | 2203.7758 | 2282.9027 | 2349.4677 | 2380.1097 | 2352.7987 | 2467.304 | 2485.4648 | 2463.9727 | 2507.0692 | 2531.7056 | 2531.7056 | 2531.7056 | 2531.7056 | 2531.7056 | 2531.7056 | 2531.7056 | 2531.7056 | 2531.7056 | 2531.7056 | 2531.7056 | 2531.7056 | 2531.7056 | 2531.7056 | 2531.7056 |  | 210.6416 | 253.9682 | 255.1638 | 253.8747 | 254.2062 | 256.5722 | 261.367 | 269.8113 | 274.2113 | 277.3946 | 282.2122 | 288.363 | 295.8006 | 299.6984 | 298.4348 | 299.9656 | 299.9656 | 299.9656 | 299.9656 | 299.9656 | 299.9656 | 299.9656 | 299.9656 | 299.9656 | 299.9656 | 299.9656 | 299.9656 | 299.9656 | 299.9656 | 299.9656
50% | 922.9519 | 1630.9008 | 1702.042 | 1667.1704 | 1700.3279 | 1713.9518 | 1757.6154 | 1847.3972 | 1922.9257 | 1957.6938 | 1926.7051 | 2056.6293 | 2077.2355 | 2052.8494 | 2101.749 | 2129.7029 | 2129.7029 | 2129.7029 | 2129.7029 | 2129.7029 | 2129.7029 | 2129.7029 | 2129.7029 | 2129.7029 | 2129.7029 | 2129.7029 | 2129.7029 | 2129.7029 | 2129.7029 | 2129.7029 |  | 383.0991 | 480.7604 | 483.4553 | 480.5498 | 481.297 | 486.6301 | 497.438 | 516.4721 | 526.39 | 533.5653 | 544.4247 | 558.2889 | 575.0538 | 583.8398 | 580.9915 | 584.442 | 584.442 | 584.442 | 584.442 | 584.442 | 584.442 | 584.442 | 584.442 | 584.442 | 584.442 | 584.442 | 584.442 | 584.442 | 584.442 | 584.442
45% | 113.1135 | 605.5456 | 664.4302 | 635.5664 | 663.0115 | 674.2882 | 710.4292 | 784.743 | 847.2591 | 876.0372 | 850.3875 | 957.9277 | 974.9838 | 954.799 | 995.274 | 1018.4119 | 1018.4119 | 1018.4119 | 1018.4119 | 1018.4119 | 1018.4119 | 1018.4119 | 1018.4119 | 1018.4119 | 1018.4119 | 1018.4119 | 1018.4119 | 1018.4119 | 1018.4119 | 1018.4119 |  | 467.4239 | 635.1966 | 639.8262 | 634.8348 | 636.1184 | 645.2801 | 663.8471 | 696.5457 | 713.5838 | 725.9102 | 744.5656 | 768.3829 | 797.1834 | 812.2769 | 807.3838 | 813.3115 | 813.3115 | 813.3115 | 813.3115 | 813.3115 | 813.3115 | 813.3115 | 813.3115 | 813.3115 | 813.3115 | 813.3115 | 813.3115 | 813.3115 | 813.3115 | 813.3115
40% |  | 11.9277 | 21.3864 | 16.4156 | 21.1271 | 23.2302 | 30.6206 | 48.888 | 67.3917 | 76.8544 | 68.3917 | 106.9766 | 113.8368 | 105.7399 | 122.2575 | 132.2021 | 132.2021 | 132.2021 | 132.2021 | 132.2021 | 132.2021 | 132.2021 | 132.2021 | 132.2021 | 132.2021 | 132.2021 | 132.2021 | 132.2021 | 132.2021 | 132.2021 |  | 313.9328 | 541.1029 | 547.3715 | 540.613 | 542.3511 | 554.7563 | 579.8966 | 624.1718 | 647.2418 | 663.9323 | 689.1923 | 721.4418 | 760.4386 | 780.8759 | 774.2504 | 782.2767 | 782.2767 | 782.2767 | 782.2767 | 782.2767 | 782.2767 | 782.2767 | 782.2767 | 782.2767 | 782.2767 | 782.2767 | 782.2767 | 782.2767 | 782.2767 | 782.2767
35% | [31 empty] | 32.1525 | 240.1146 | 248.3143 | 239.479 | 241.7375 | 258.1321 | 292.8244 | 358.5913 | 395.1611 | 422.2729 | 463.3148 | 515.7129 | 579.0739 | 612.2797 | 601.5148 | 614.5558 | 614.5558 | 614.5558 | 614.5558 | 614.5558 | 614.5558 | 614.5558 | 614.5558 | 614.5558 | 614.5558 | 614.5558 | 614.5558 | 614.5558 | 614.5558 | 614.5558
30% | [40 empty] | 0.54575 | 4.0441 | 13.1246 | 30.8413 | 43.0003 | 38.845 | 43.905 | 43.905 | 43.905 | 43.905 | 43.905 | 43.905 | 43.905 | 43.905 | 43.905 | 43.905 | 43.905 | 43.905 | 43.905 | 43.905 | 43.905
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 9223.5741 | 12607.8025 | 12965.3646 | 12789.7654 | 12956.7185 | 13025.4821 | 13246.5087 | 13704.0276 | 14092.0177 | 14271.5572 | 14111.5063 | 14785.6146 | 14893.2628 | 14765.8898 | 15021.58 | 15168.2446 | 15168.2446 | 15168.2446 | 15168.2446 | 15168.2446 | 15168.2446 | 15168.2446 | 15168.2446 | 15168.2446 | 15168.2446 | 15168.2446 | 15168.2446 | 15168.2446 | 15168.2446 | 15168.2446 | E @ R (MWh) | 1562.9946 | 2324.4501 | 2347.8985 | 2322.6227 | 2329.1093 | 2375.6785 | 2471.5078 | 2644.8974 | 2737.5223 | 2805.7218 | 2911.5932 | 3051.3274 | 3226.9658 | 3321.8588 | 3290.8844 | 3328.4339 | 3328.4339 | 3328.4339 | 3328.4339 | 3328.4339 | 3328.4339 | 3328.4339 | 3328.4339 | 3328.4339 | 3328.4339 | 3328.4339 | 3328.4339 | 3328.4339 | 3328.4339 | 3328.4339
Option 6 Summer POE50 W E @ R (MWh) N 2 | 6456.5019 | 8825.4618 | 9075.7552 | 8952.8358 | 9069.703 | 9117.8375 | 9272.5561 | 9592.8193 | 9864.4124 | 9990.0901 | 9878.0544 | 10349.9302 | 10425.2839 | 10336.1228 | 10515.106 | 10617.7712 | 10617.7712 | 10617.7712 | 10617.7712 | 10617.7712 | 10617.7712 | 10617.7712 | 10617.7712 | 10617.7712 | 10617.7712 | 10617.7712 | 10617.7712 | 10617.7712 | 10617.7712 | 10617.7712 | Option 6 Summer POE10 W E @ R (MWh) N 2 | 468.8984 | 697.335 | 704.3695 | 696.7868 | 698.7328 | 712.7036 | 741.4523 | 793.4692 | 821.2567 | 841.7165 | 873.478 | 915.3982 | 968.0898 | 996.5577 | 987.2653 | 998.5302 | 998.5302 | 998.5302 | 998.5302 | 998.5302 | 998.5302 | 998.5302 | 998.5302 | 998.5302 | 998.5302 | 998.5302 | 998.5302 | 998.5302 | 998.5302 | 998.5302
Option 7 -
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | 5.1211 | 6.2192 | 6.3356 | 6.4796 | 6.6707 | 6.8519 | 7.1685 | 7.9649 | 8.3933 | 8.0808 | 9.0482 | 9.2225 | 9.3478 | 9.9384 | 10.0346 | 10.0346 | 10.0346 | 10.0346 | 10.0346 | 10.0346 | 10.0346 | 10.0346 | 10.0346 | 10.0346 | 10.0346 | 10.0346 | 10.0346 | 10.0346 | 10.0346 | 10.0346 |  | 6.1303 | 7.1777 | 7.2862 | 7.6605 | 7.6514 | 7.7337 | 8.0557 | 8.9806 | 9.3623 | 9.001 | 9.9991 | 9.58 | 9.9571 | 10.2288 | 10.1171 | 10.1171 | 10.1171 | 10.1171 | 10.1171 | 10.1171 | 10.1171 | 10.1171 | 10.1171 | 10.1171 | 10.1171 | 10.1171 | 10.1171 | 10.1171 | 10.1171 | 10.1171
98% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
97% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
95% | 19.0092 | 23.247 | 23.6963 | 24.2519 | 24.9895 | 25.6887 | 26.9107 | 29.9842 | 31.6373 | 30.4313 | 34.165 | 34.8377 | 35.3212 | 37.6005 | 37.9715 | 37.9715 | 37.9715 | 37.9715 | 37.9715 | 37.9715 | 37.9715 | 37.9715 | 37.9715 | 37.9715 | 37.9715 | 37.9715 | 37.9715 | 37.9715 | 37.9715 | 37.9715 |  | 22.9039 | 26.9462 | 27.3648 | 28.8095 | 28.7742 | 29.0919 | 30.3344 | 33.9041 | 35.3771 | 33.9828 | 37.8346 | 36.2174 | 37.6725 | 38.7211 | 38.2903 | 38.2903 | 38.2903 | 38.2903 | 38.2903 | 38.2903 | 38.2903 | 38.2903 | 38.2903 | 38.2903 | 38.2903 | 38.2903 | 38.2903 | 38.2903 | 38.2903 | 38.2903
90% | 105.2028 | 129.7026 | 132.3005 | 135.5122 | 139.7764 | 143.8191 | 150.8839 | 168.6524 | 178.2095 | 171.2373 | 192.8224 | 196.7114 | 199.5069 | 212.6842 | 214.8291 | 214.8291 | 214.8291 | 214.8291 | 214.8291 | 214.8291 | 214.8291 | 214.8291 | 214.8291 | 214.8291 | 214.8291 | 214.8291 | 214.8291 | 214.8291 | 214.8291 | 214.8291 |  | 127.7194 | 151.0886 | 153.5087 | 161.8608 | 161.6572 | 163.4938 | 170.6769 | 191.314 | 199.8301 | 191.769 | 214.0372 | 204.6878 | 213.1003 | 219.1625 | 216.6718 | 216.6718 | 216.6718 | 216.6718 | 216.6718 | 216.6718 | 216.6718 | 216.6718 | 216.6718 | 216.6718 | 216.6718 | 216.6718 | 216.6718 | 216.6718 | 216.6718 | 216.6718
85% | 408.7931 | 511.1512 | 522.005 | 535.4235 | 553.2391 | 570.1289 | 599.6452 | 673.8807 | 713.8099 | 684.6804 | 774.8612 | 791.1091 | 802.7887 | 857.8426 | 866.8037 | 866.8037 | 866.8037 | 866.8037 | 866.8037 | 866.8037 | 866.8037 | 866.8037 | 866.8037 | 866.8037 | 866.8037 | 866.8037 | 866.8037 | 866.8037 | 866.8037 | 866.8037 |  | 502.8656 | 600.5006 | 610.6116 | 645.5059 | 644.6555 | 652.3285 | 682.3388 | 768.5594 | 804.1392 | 770.4602 | 863.495 | 824.4339 | 859.5808 | 884.9083 | 874.5026 | 874.5026 | 874.5026 | 874.5026 | 874.5026 | 874.5026 | 874.5026 | 874.5026 | 874.5026 | 874.5026 | 874.5026 | 874.5026 | 874.5026 | 874.5026 | 874.5026 | 874.5026
80% | 592.6734 | 754.7359 | 771.9205 | 793.1658 | 821.3732 | 848.1145 | 894.8474 | 1012.3836 | 1075.6029 | 1029.4825 | 1172.2649 | 1197.99 | 1216.482 | 1303.6484 | 1317.8363 | 1317.8363 | 1317.8363 | 1317.8363 | 1317.8363 | 1317.8363 | 1317.8363 | 1317.8363 | 1317.8363 | 1317.8363 | 1317.8363 | 1317.8363 | 1317.8363 | 1317.8363 | 1317.8363 | 1317.8363 |  | 741.6174 | 896.2017 | 912.2103 | 967.4581 | 966.1116 | 978.2602 | 1025.7752 | 1162.2872 | 1218.6203 | 1165.2967 | 1312.5977 | 1250.7528 | 1306.4003 | 1346.5011 | 1330.0258 | 1330.0258 | 1330.0258 | 1330.0258 | 1330.0258 | 1330.0258 | 1330.0258 | 1330.0258 | 1330.0258 | 1330.0258 | 1330.0258 | 1330.0258 | 1330.0258 | 1330.0258 | 1330.0258 | 1330.0258
75% | 980.9496 | 1280.2989 | 1312.0411 | 1351.2837 | 1403.3862 | 1452.7807 | 1539.1021 | 1756.2058 | 1872.9798 | 1787.7897 | 2051.5263 | 2099.0437 | 2133.2008 | 2294.2077 | 2320.4147 | 2320.4147 | 2320.4147 | 2320.4147 | 2320.4147 | 2320.4147 | 2320.4147 | 2320.4147 | 2320.4147 | 2320.4147 | 2320.4147 | 2320.4147 | 2320.4147 | 2320.4147 | 2320.4147 | 2320.4147 |  | 1256.0675 | 1541.6038 | 1571.1735 | 1673.2229 | 1670.7358 | 1693.1758 | 1780.9419 | 2033.0964 | 2137.1505 | 2038.6552 | 2310.7383 | 2196.5031 | 2299.291 | 2373.362 | 2342.9301 | 2342.9301 | 2342.9301 | 2342.9301 | 2342.9301 | 2342.9301 | 2342.9301 | 2342.9301 | 2342.9301 | 2342.9301 | 2342.9301 | 2342.9301 | 2342.9301 | 2342.9301 | 2342.9301 | 2342.9301
70% | 1385.9626 | 1873.2259 | 1924.894 | 1988.7709 | 2073.5802 | 2153.9818 | 2294.4906 | 2647.8796 | 2837.9574 | 2699.29 | 3128.585 | 3205.9311 | 3261.5301 | 3523.6078 | 3566.266 | 3566.266 | 3566.266 | 3566.266 | 3566.266 | 3566.266 | 3566.266 | 3566.266 | 3566.266 | 3566.266 | 3566.266 | 3566.266 | 3566.266 | 3566.266 | 3566.266 | 3566.266 |  | 1833.7834 | 2298.5628 | 2346.6947 | 2512.8048 | 2508.7564 | 2545.283 | 2688.1435 | 3098.5859 | 3267.9592 | 3107.6342 | 3550.5153 | 3364.5698 | 3531.882 | 3652.4506 | 3602.9153 | 3602.9153 | 3602.9153 | 3602.9153 | 3602.9153 | 3602.9153 | 3602.9153 | 3602.9153 | 3602.9153 | 3602.9153 | 3602.9153 | 3602.9153 | 3602.9153 | 3602.9153 | 3602.9153 | 3602.9153
65% | 1400.8592 | 1997.5436 | 2060.8145 | 2139.0357 | 2242.8901 | 2341.3468 | 2513.4087 | 2946.1556 | 3178.9178 | 3009.1109 | 3534.8094 | 3629.5246 | 3697.6091 | 4018.5396 | 4070.7772 | 4070.7772 | 4070.7772 | 4070.7772 | 4070.7772 | 4070.7772 | 4070.7772 | 4070.7772 | 4070.7772 | 4070.7772 | 4070.7772 | 4070.7772 | 4070.7772 | 4070.7772 | 4070.7772 | 4070.7772 |  | 1949.2438 | 2518.3953 | 2577.3359 | 2780.7481 | 2775.7906 | 2820.5196 | 2995.4612 | 3498.0737 | 3705.4819 | 3509.1539 | 4051.4896 | 3823.7877 | 4028.6719 | 4176.3156 | 4115.6566 | 4115.6566 | 4115.6566 | 4115.6566 | 4115.6566 | 4115.6566 | 4115.6566 | 4115.6566 | 4115.6566 | 4115.6566 | 4115.6566 | 4115.6566 | 4115.6566 | 4115.6566 | 4115.6566 | 4115.6566
60% | 1311.1794 | 2051.2755 | 2129.7534 | 2226.7749 | 2355.5904 | 2477.711 | 2691.1276 | 3227.8842 | 3516.5903 | 3305.9706 | 3958.0197 | 4075.4994 | 4159.9479 | 4558.0133 | 4622.8061 | 4622.8061 | 4622.8061 | 4622.8061 | 4622.8061 | 4622.8061 | 4622.8061 | 4622.8061 | 4622.8061 | 4622.8061 | 4622.8061 | 4622.8061 | 4622.8061 | 4622.8061 | 4622.8061 | 4622.8061 |  | 1991.367 | 2697.3127 | 2770.4195 | 3022.7214 | 3016.5724 | 3072.052 | 3289.0403 | 3912.4546 | 4169.7129 | 3926.1979 | 4598.8827 | 4316.4532 | 4570.5808 | 4753.7104 | 4678.4721 | 4678.4721 | 4678.4721 | 4678.4721 | 4678.4721 | 4678.4721 | 4678.4721 | 4678.4721 | 4678.4721 | 4678.4721 | 4678.4721 | 4678.4721 | 4678.4721 | 4678.4721 | 4678.4721 | 4678.4721
55% | 879.254 | 1681.979 | 1767.0979 | 1872.3296 | 2012.0458 | 2144.5006 | 2375.977 | 2958.1553 | 3271.2924 | 3042.8496 | 3750.0767 | 3877.4979 | 3969.0926 | 4400.8433 | 4471.1191 | 4471.1191 | 4471.1191 | 4471.1191 | 4471.1191 | 4471.1191 | 4471.1191 | 4471.1191 | 4471.1191 | 4471.1191 | 4471.1191 | 4471.1191 | 4471.1191 | 4471.1191 | 4471.1191 | 4471.1191 |  | 1617.0008 | 2382.6855 | 2461.9788 | 2735.6311 | 2728.9617 | 2789.1362 | 3024.4867 | 3700.6558 | 3979.6839 | 3715.5621 | 4445.1712 | 4138.8418 | 4414.4743 | 4613.1009 | 4531.4957 | 4531.4957 | 4531.4957 | 4531.4957 | 4531.4957 | 4531.4957 | 4531.4957 | 4531.4957 | 4531.4957 | 4531.4957 | 4531.4957 | 4531.4957 | 4531.4957 | 4531.4957 | 4531.4957 | 4531.4957
50% | 249.4213 | 1054.7724 | 1141.4594 | 1248.6298 | 1390.9199 | 1525.8148 | 1761.5555 | 2354.459 | 2673.3649 | 2440.7136 | 3160.9695 | 3290.738 | 3384.0202 | 3823.7248 | 3895.2952 | 3895.2952 | 3895.2952 | 3895.2952 | 3895.2952 | 3895.2952 | 3895.2952 | 3895.2952 | 3895.2952 | 3895.2952 | 3895.2952 | 3895.2952 | 3895.2952 | 3895.2952 | 3895.2952 | 3895.2952 |  | 988.5972 | 1768.3876 | 1849.1417 | 2127.8353 | 2121.0431 | 2182.3261 | 2422.0123 | 3110.6381 | 3394.8066 | 3125.819 | 3868.8693 | 3556.8965 | 3837.6069 | 4039.8926 | 3956.7841 | 3956.7841 | 3956.7841 | 3956.7841 | 3956.7841 | 3956.7841 | 3956.7841 | 3956.7841 | 3956.7841 | 3956.7841 | 3956.7841 | 3956.7841 | 3956.7841 | 3956.7841 | 3956.7841 | 3956.7841
45% |  | 263.6586 | 332.2401 | 426.8754 | 561.1949 | 688.6055 | 911.2667 | 1471.2745 | 1772.4867 | 1552.7434 | 2233.0378 | 2355.6065 | 2443.7131 | 2859.0218 | 2926.6213 | 2926.6213 | 2926.6213 | 2926.6213 | 2926.6213 | 2926.6213 | 2926.6213 | 2926.6213 | 2926.6213 | 2926.6213 | 2926.6213 | 2926.6213 | 2926.6213 | 2926.6213 | 2926.6213 | 2926.6213 |  | 216.2457 | 917.7197 | 993.9934 | 1257.2244 | 1250.8091 | 1308.6919 | 1535.0798 | 2185.4989 | 2453.9011 | 2199.8376 | 2901.6616 | 2606.9978 | 2872.1337 | 3063.1961 | 2984.6986 | 2984.6986 | 2984.6986 | 2984.6986 | 2984.6986 | 2984.6986 | 2984.6986 | 2984.6986 | 2984.6986 | 2984.6986 | 2984.6986 | 2984.6986 | 2984.6986 | 2984.6986 | 2984.6986 | 2984.6986
40% |  |  |  |  | 7.5893 | 31.1945 | 108.8464 | 488.9496 | 760.7952 | 562.4477 | 1176.5041 | 1287.1386 | 1366.6666 | 1741.5381 | 1802.5557 | 1802.5557 | 1802.5557 | 1802.5557 | 1802.5557 | 1802.5557 | 1802.5557 | 1802.5557 | 1802.5557 | 1802.5557 | 1802.5557 | 1802.5557 | 1802.5557 | 1802.5557 | 1802.5557 | 1802.5557 |  |  | 111.7593 | 148.9205 | 314.3792 | 309.6857 | 353.1877 | 546.5039 | 1133.5939 | 1375.8626 | 1146.5364 | 1780.0262 | 1514.0529 | 1753.3734 | 1925.8327 | 1854.9782 | 1854.9782 | 1854.9782 | 1854.9782 | 1854.9782 | 1854.9782 | 1854.9782 | 1854.9782 | 1854.9782 | 1854.9782 | 1854.9782 | 1854.9782 | 1854.9782 | 1854.9782 | 1854.9782 | 1854.9782
35% | [8 empty] | 26.1432 | 1.6005 | 166.5253 | 222.5876 | 267.429 | 526.6894 | 574.0431 | 574.0431 | 574.0431 | 574.0431 | 574.0431 | 574.0431 | 574.0431 | 574.0431 | 574.0431 | 574.0431 | 574.0431 | 574.0431 | 574.0431 | 574.0431 | 574.0431 | 574.0431 | [7 empty] | 0.90619 | 146.8106 | 272.8539 | 152.6356 | 556.5587 | 360.2185 | 535.8744 | 669.7143 | 614.7265 | 614.7265 | 614.7265 | 614.7265 | 614.7265 | 614.7265 | 614.7265 | 614.7265 | 614.7265 | 614.7265 | 614.7265 | 614.7265 | 614.7265 | 614.7265 | 614.7265 | 614.7265
30% | FY38: 0.23254; FY39: 1.8503; FY40: 1.8503; FY41: 1.8503; FY42: 1.8503; FY43: 1.8503; FY44: 1.8503; FY45: 1.8503; FY46: 1.8503; FY47: 1.8503; FY48: 1.8503; FY49: 1.8503; FY50: 1.8503; FY51: 1.8503; FY52: 1.8503; FY53: 1.8503; FY54: 1.8503 | [11 empty] | 1.0747 |  | 0.42635 | 9.7196 | 4.4531 | 4.4531 | 4.4531 | 4.4531 | 4.4531 | 4.4531 | 4.4531 | 4.4531 | 4.4531 | 4.4531 | 4.4531 | 4.4531 | 4.4531 | 4.4531 | 4.4531 | 4.4531
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 7265.0415 | 11511.5317 | 12003.3126 | 12621.0477 | 13457.3132 | 14266.4334 | 15716.478 | 19546.391 | 21698.9988 | 20123.164 | 25089.7832 | 26010.7036 | 26677.1895 | 29866.4513 | 30392.2317 | 30392.2317 | 30392.2317 | 30392.2317 | 30392.2317 | 30392.2317 | 30392.2317 | 30392.2317 | 30392.2317 | 30392.2317 | 30392.2317 | 30392.2317 | 30392.2317 | 30392.2317 | 30392.2317 | 30392.2317 | E @ R (MWh) | 11141.0066 | 15759.1581 | 16266.3334 | 18053.5033 | 18009.2926 | 18409.3276 | 19997.7591 | 24734.6086 | 26754.4944 | 24841.616 | 30197.9216 | 27921.9531 | 29968.3153 | 31459.0485 | 30845.1507 | 30845.1507 | 30845.1507 | 30845.1507 | 30845.1507 | 30845.1507 | 30845.1507 | 30845.1507 | 30845.1507 | 30845.1507 | 30845.1507 | 30845.1507 | 30845.1507 | 30845.1507 | 30845.1507 | 30845.1507
Option 7 Winter POE50 W E @ R (MWh) N 2 | 5085.529 | 8058.0722 | 8402.3188 | 8834.7334 | 9420.1193 | 9986.5034 | 11001.5346 | 13682.4737 | 15189.2992 | 14086.2148 | 17562.8482 | 18207.4925 | 18674.0327 | 20906.5159 | 21274.5622 | 21274.5622 | 21274.5622 | 21274.5622 | 21274.5622 | 21274.5622 | 21274.5622 | 21274.5622 | 21274.5622 | 21274.5622 | 21274.5622 | 21274.5622 | 21274.5622 | 21274.5622 | 21274.5622 | 21274.5622 | Option 7 Winter POE10 W E @ R (MWh) N 2 | 3342.302 | 4727.7474 | 4879.9 | 5416.051 | 5402.7878 | 5522.7983 | 5999.3277 | 7420.3826 | 8026.3483 | 7452.4848 | 9059.3765 | 8376.5859 | 8990.4946 | 9437.7145 | 9253.5452 | 9253.5452 | 9253.5452 | 9253.5452 | 9253.5452 | 9253.5452 | 9253.5452 | 9253.5452 | 9253.5452 | 9253.5452 | 9253.5452 | 9253.5452 | 9253.5452 | 9253.5452 | 9253.5452 | 9253.5452
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | 7.3419 | 8.3902 | 8.4955 | 8.4439 | 8.493 | 8.5131 | 8.5778 | 8.7107 | 8.8225 | 8.874 | 8.8281 | 9.0205 | 9.051 | 9.0149 | 9.0873 | 9.1287 | 9.1287 | 9.1287 | 9.1287 | 9.1287 | 9.1287 | 9.1287 | 9.1287 | 9.1287 | 9.1287 | 9.1287 | 9.1287 | 9.1287 | 9.1287 | 9.1287 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
98% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
97% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 10.2241 | 11.372 | 11.4037 | 11.3695 | 11.3783 | 11.441 | 11.568 | 11.7917 | 11.9083 | 11.9926 | 12.1203 | 12.2833 | 12.4803 | 12.5836 | 12.5501 | 12.5907 | 12.5907 | 12.5907 | 12.5907 | 12.5907 | 12.5907 | 12.5907 | 12.5907 | 12.5907 | 12.5907 | 12.5907 | 12.5907 | 12.5907 | 12.5907 | 12.5907
95% | 6.8489 | 7.8602 | 7.9619 | 7.9121 | 7.9594 | 7.9789 | 8.0413 | 8.1695 | 8.2774 | 8.3271 | 8.2828 | 8.4684 | 8.4979 | 8.463 | 8.5329 | 8.5728 | 8.5728 | 8.5728 | 8.5728 | 8.5728 | 8.5728 | 8.5728 | 8.5728 | 8.5728 | 8.5728 | 8.5728 | 8.5728 | 8.5728 | 8.5728 | 8.5728 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
90% | 139.8285 | 161.2671 | 163.4215 | 162.3655 | 163.3696 | 163.7822 | 165.1044 | 167.8232 | 170.1105 | 171.1633 | 170.2249 | 174.1594 | 174.7834 | 174.0449 | 175.5257 | 176.3722 | 176.3722 | 176.3722 | 176.3722 | 176.3722 | 176.3722 | 176.3722 | 176.3722 | 176.3722 | 176.3722 | 176.3722 | 176.3722 | 176.3722 | 176.3722 | 176.3722 |  | 9.3575 | 10.4465 | 10.4766 | 10.4442 | 10.4525 | 10.512 | 10.6325 | 10.8447 | 10.9553 | 11.0354 | 11.1564 | 11.3111 | 11.498 | 11.596 | 11.5642 | 11.6027 | 11.6027 | 11.6027 | 11.6027 | 11.6027 | 11.6027 | 11.6027 | 11.6027 | 11.6027 | 11.6027 | 11.6027 | 11.6027 | 11.6027 | 11.6027 | 11.6027
85% | 469.0739 | 545.5841 | 553.2725 | 549.5038 | 553.0872 | 554.5596 | 559.2785 | 568.9815 | 577.144 | 580.9015 | 577.5525 | 591.5938 | 593.8207 | 591.1853 | 596.47 | 599.4911 | 599.4911 | 599.4911 | 599.4911 | 599.4911 | 599.4911 | 599.4911 | 599.4911 | 599.4911 | 599.4911 | 599.4911 | 599.4911 | 599.4911 | 599.4911 | 599.4911 |  | 8.4909 | 9.521 | 9.5495 | 9.5188 | 9.5267 | 9.583 | 9.697 | 9.8978 | 10.0024 | 10.0781 | 10.1926 | 10.3389 | 10.5157 | 10.6084 | 10.5783 | 10.6147 | 10.6147 | 10.6147 | 10.6147 | 10.6147 | 10.6147 | 10.6147 | 10.6147 | 10.6147 | 10.6147 | 10.6147 | 10.6147 | 10.6147 | 10.6147 | 10.6147
80% | 707.4418 | 831.7279 | 844.2173 | 838.0953 | 843.9164 | 846.3082 | 853.9736 | 869.7356 | 882.9952 | 889.099 | 883.6587 | 906.4679 | 910.0855 | 905.8043 | 914.3891 | 919.2966 | 919.2966 | 919.2966 | 919.2966 | 919.2966 | 919.2966 | 919.2966 | 919.2966 | 919.2966 | 919.2966 | 919.2966 | 919.2966 | 919.2966 | 919.2966 | 919.2966 |  | 30.4971 | 34.3823 | 34.4895 | 34.3739 | 34.4037 | 34.6158 | 35.0458 | 35.803 | 36.1976 | 36.4831 | 36.9151 | 37.4666 | 38.1336 | 38.4831 | 38.3698 | 38.5071 | 38.5071 | 38.5071 | 38.5071 | 38.5071 | 38.5071 | 38.5071 | 38.5071 | 38.5071 | 38.5071 | 38.5071 | 38.5071 | 38.5071 | 38.5071 | 38.5071
75% | 1149.798 | 1371.0584 | 1393.2926 | 1382.3939 | 1392.7569 | 1397.0149 | 1410.6614 | 1438.7215 | 1462.327 | 1473.1933 | 1463.5082 | 1504.1143 | 1510.5546 | 1502.933 | 1518.216 | 1526.9526 | 1526.9526 | 1526.9526 | 1526.9526 | 1526.9526 | 1526.9526 | 1526.9526 | 1526.9526 | 1526.9526 | 1526.9526 | 1526.9526 | 1526.9526 | 1526.9526 | 1526.9526 | 1526.9526 |  | 13.5153 | 15.3402 | 15.3906 | 15.3363 | 15.3503 | 15.4499 | 15.6519 | 16.0075 | 16.1929 | 16.3269 | 16.5299 | 16.7889 | 17.1022 | 17.2664 | 17.2131 | 17.2776 | 17.2776 | 17.2776 | 17.2776 | 17.2776 | 17.2776 | 17.2776 | 17.2776 | 17.2776 | 17.2776 | 17.2776 | 17.2776 | 17.2776 | 17.2776 | 17.2776
70% | 1309.2261 | 1591.8262 | 1620.2245 | 1606.3043 | 1619.5402 | 1624.9786 | 1642.4083 | 1678.2476 | 1708.3971 | 1722.2759 | 1709.9059 | 1761.7692 | 1769.9948 | 1760.2603 | 1779.7801 | 1790.9388 | 1790.9388 | 1790.9388 | 1790.9388 | 1790.9388 | 1790.9388 | 1790.9388 | 1790.9388 | 1790.9388 | 1790.9388 | 1790.9388 | 1790.9388 | 1790.9388 | 1790.9388 | 1790.9388 |  | 35.3464 | 40.4679 | 40.6092 | 40.4568 | 40.496 | 40.7757 | 41.3425 | 42.3407 | 42.8608 | 43.237 | 43.8065 | 44.5336 | 45.4128 | 45.8735 | 45.7241 | 45.9051 | 45.9051 | 45.9051 | 45.9051 | 45.9051 | 45.9051 | 45.9051 | 45.9051 | 45.9051 | 45.9051 | 45.9051 | 45.9051 | 45.9051 | 45.9051 | 45.9051
65% | 1383.0411 | 1730.0625 | 1764.9344 | 1747.8411 | 1764.0942 | 1770.7723 | 1792.1753 | 1836.1844 | 1873.2068 | 1890.2494 | 1875.0595 | 1938.7455 | 1948.8462 | 1936.8927 | 1960.8622 | 1974.5646 | 1974.5646 | 1974.5646 | 1974.5646 | 1974.5646 | 1974.5646 | 1974.5646 | 1974.5646 | 1974.5646 | 1974.5646 | 1974.5646 | 1974.5646 | 1974.5646 | 1974.5646 | 1974.5646 |  | 10.0489 | 11.6384 | 11.6822 | 11.6349 | 11.6471 | 11.7339 | 11.9098 | 12.2196 | 12.381 | 12.4978 | 12.6745 | 12.9001 | 13.173 | 13.316 | 13.2696 | 13.3258 | 13.3258 | 13.3258 | 13.3258 | 13.3258 | 13.3258 | 13.3258 | 13.3258 | 13.3258 | 13.3258 | 13.3258 | 13.3258 | 13.3258 | 13.3258 | 13.3258
60% | 1639.9094 | 2146.9041 | 2197.8516 | 2172.8784 | 2196.624 | 2206.3807 | 2237.6502 | 2301.9471 | 2356.0365 | 2380.9355 | 2358.7431 | 2451.7877 | 2466.5448 | 2449.0808 | 2484.1001 | 2504.1192 | 2504.1192 | 2504.1192 | 2504.1192 | 2504.1192 | 2504.1192 | 2504.1192 | 2504.1192 | 2504.1192 | 2504.1192 | 2504.1192 | 2504.1192 | 2504.1192 | 2504.1192 | 2504.1192 |  | 54.0524 | 63.6183 | 63.8823 | 63.5977 | 63.6709 | 64.1933 | 65.2519 | 67.1163 | 68.0878 | 68.7906 | 69.8543 | 71.2123 | 72.8544 | 73.715 | 73.436 | 73.774 | 73.774 | 73.774 | 73.774 | 73.774 | 73.774 | 73.774 | 73.774 | 73.774 | 73.774 | 73.774 | 73.774 | 73.774 | 73.774 | 73.774
55% | 1468.1665 | 2092.0991 | 2154.7976 | 2124.0644 | 2153.2869 | 2165.294 | 2203.7758 | 2282.9027 | 2349.4677 | 2380.1097 | 2352.7987 | 2467.304 | 2485.4648 | 2463.9727 | 2507.0692 | 2531.7056 | 2531.7056 | 2531.7056 | 2531.7056 | 2531.7056 | 2531.7056 | 2531.7056 | 2531.7056 | 2531.7056 | 2531.7056 | 2531.7056 | 2531.7056 | 2531.7056 | 2531.7056 | 2531.7056 |  | 210.6416 | 253.9682 | 255.1638 | 253.8747 | 254.2062 | 256.5722 | 261.367 | 269.8113 | 274.2113 | 277.3946 | 282.2122 | 288.363 | 295.8006 | 299.6984 | 298.4348 | 299.9656 | 299.9656 | 299.9656 | 299.9656 | 299.9656 | 299.9656 | 299.9656 | 299.9656 | 299.9656 | 299.9656 | 299.9656 | 299.9656 | 299.9656 | 299.9656 | 299.9656
50% | 922.9519 | 1630.9008 | 1702.042 | 1667.1704 | 1700.3279 | 1713.9518 | 1757.6154 | 1847.3972 | 1922.9257 | 1957.6938 | 1926.7051 | 2056.6293 | 2077.2355 | 2052.8494 | 2101.749 | 2129.7029 | 2129.7029 | 2129.7029 | 2129.7029 | 2129.7029 | 2129.7029 | 2129.7029 | 2129.7029 | 2129.7029 | 2129.7029 | 2129.7029 | 2129.7029 | 2129.7029 | 2129.7029 | 2129.7029 |  | 383.0991 | 480.7604 | 483.4553 | 480.5498 | 481.297 | 486.6301 | 497.438 | 516.4721 | 526.39 | 533.5653 | 544.4247 | 558.2889 | 575.0538 | 583.8398 | 580.9915 | 584.442 | 584.442 | 584.442 | 584.442 | 584.442 | 584.442 | 584.442 | 584.442 | 584.442 | 584.442 | 584.442 | 584.442 | 584.442 | 584.442 | 584.442
45% | 113.1135 | 605.5456 | 664.4302 | 635.5664 | 663.0115 | 674.2882 | 710.4292 | 784.743 | 847.2591 | 876.0372 | 850.3875 | 957.9277 | 974.9838 | 954.799 | 995.274 | 1018.4119 | 1018.4119 | 1018.4119 | 1018.4119 | 1018.4119 | 1018.4119 | 1018.4119 | 1018.4119 | 1018.4119 | 1018.4119 | 1018.4119 | 1018.4119 | 1018.4119 | 1018.4119 | 1018.4119 |  | 467.4239 | 635.1966 | 639.8262 | 634.8348 | 636.1184 | 645.2801 | 663.8471 | 696.5457 | 713.5838 | 725.9102 | 744.5656 | 768.3829 | 797.1834 | 812.2769 | 807.3838 | 813.3115 | 813.3115 | 813.3115 | 813.3115 | 813.3115 | 813.3115 | 813.3115 | 813.3115 | 813.3115 | 813.3115 | 813.3115 | 813.3115 | 813.3115 | 813.3115 | 813.3115
40% |  | 11.9277 | 21.3864 | 16.4156 | 21.1271 | 23.2302 | 30.6206 | 48.888 | 67.3917 | 76.8544 | 68.3917 | 106.9766 | 113.8368 | 105.7399 | 122.2575 | 132.2021 | 132.2021 | 132.2021 | 132.2021 | 132.2021 | 132.2021 | 132.2021 | 132.2021 | 132.2021 | 132.2021 | 132.2021 | 132.2021 | 132.2021 | 132.2021 | 132.2021 |  | 313.9328 | 541.1029 | 547.3715 | 540.613 | 542.3511 | 554.7563 | 579.8966 | 624.1718 | 647.2418 | 663.9323 | 689.1923 | 721.4418 | 760.4386 | 780.8759 | 774.2504 | 782.2767 | 782.2767 | 782.2767 | 782.2767 | 782.2767 | 782.2767 | 782.2767 | 782.2767 | 782.2767 | 782.2767 | 782.2767 | 782.2767 | 782.2767 | 782.2767 | 782.2767
35% | [31 empty] | 32.1525 | 240.1146 | 248.3143 | 239.479 | 241.7375 | 258.1321 | 292.8244 | 358.5913 | 395.1611 | 422.2729 | 463.3148 | 515.7129 | 579.0739 | 612.2797 | 601.5148 | 614.5558 | 614.5558 | 614.5558 | 614.5558 | 614.5558 | 614.5558 | 614.5558 | 614.5558 | 614.5558 | 614.5558 | 614.5558 | 614.5558 | 614.5558 | 614.5558 | 614.5558
30% | [40 empty] | 0.54575 | 4.0441 | 13.1246 | 30.8413 | 43.0003 | 38.845 | 43.905 | 43.905 | 43.905 | 43.905 | 43.905 | 43.905 | 43.905 | 43.905 | 43.905 | 43.905 | 43.905 | 43.905 | 43.905 | 43.905 | 43.905
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 9223.5741 | 12607.8025 | 12965.3646 | 12789.7654 | 12956.7185 | 13025.4821 | 13246.5087 | 13704.0276 | 14092.0177 | 14271.5572 | 14111.5063 | 14785.6146 | 14893.2628 | 14765.8898 | 15021.58 | 15168.2446 | 15168.2446 | 15168.2446 | 15168.2446 | 15168.2446 | 15168.2446 | 15168.2446 | 15168.2446 | 15168.2446 | 15168.2446 | 15168.2446 | 15168.2446 | 15168.2446 | 15168.2446 | 15168.2446 | E @ R (MWh) | 1562.9946 | 2324.4501 | 2347.8985 | 2322.6227 | 2329.1093 | 2375.6785 | 2471.5078 | 2644.8974 | 2737.5223 | 2805.7218 | 2911.5932 | 3051.3274 | 3226.9658 | 3321.8588 | 3290.8844 | 3328.4339 | 3328.4339 | 3328.4339 | 3328.4339 | 3328.4339 | 3328.4339 | 3328.4339 | 3328.4339 | 3328.4339 | 3328.4339 | 3328.4339 | 3328.4339 | 3328.4339 | 3328.4339 | 3328.4339
Option 7 Summer POE50 W E @ R (MWh) N 2 | 6456.5019 | 8825.4618 | 9075.7552 | 8952.8358 | 9069.703 | 9117.8375 | 9272.5561 | 9592.8193 | 9864.4124 | 9990.0901 | 9878.0544 | 10349.9302 | 10425.2839 | 10336.1228 | 10515.106 | 10617.7712 | 10617.7712 | 10617.7712 | 10617.7712 | 10617.7712 | 10617.7712 | 10617.7712 | 10617.7712 | 10617.7712 | 10617.7712 | 10617.7712 | 10617.7712 | 10617.7712 | 10617.7712 | 10617.7712 | Option 7 Summer POE10 W E @ R (MWh) N 2 | 468.8984 | 697.335 | 704.3695 | 696.7868 | 698.7328 | 712.7036 | 741.4523 | 793.4692 | 821.2567 | 841.7165 | 873.478 | 915.3982 | 968.0898 | 996.5577 | 987.2653 | 998.5302 | 998.5302 | 998.5302 | 998.5302 | 998.5302 | 998.5302 | 998.5302 | 998.5302 | 998.5302 | 998.5302 | 998.5302 | 998.5302 | 998.5302 | 998.5302 | 998.5302
Option 8 -
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | 5.1211 | 6.2192 | 6.3356 | 6.4796 | 6.6707 | 6.8519 | 7.1685 | 7.9649 | 8.3933 | 8.0808 | 9.0482 | 9.2225 | 9.3478 | 9.9384 | 10.0346 | 10.0346 | 10.0346 | 10.0346 | 10.0346 | 10.0346 | 10.0346 | 10.0346 | 10.0346 | 10.0346 | 10.0346 | 10.0346 | 10.0346 | 10.0346 | 10.0346 | 10.0346 |  | 6.1303 | 7.1777 | 7.2862 | 7.6605 | 7.6514 | 7.7337 | 8.0557 | 8.9806 | 9.3623 | 9.001 | 9.9991 | 9.58 | 9.9571 | 10.2288 | 10.1171 | 10.1171 | 10.1171 | 10.1171 | 10.1171 | 10.1171 | 10.1171 | 10.1171 | 10.1171 | 10.1171 | 10.1171 | 10.1171 | 10.1171 | 10.1171 | 10.1171 | 10.1171
98% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
97% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
95% | 19.0092 | 23.247 | 23.6963 | 24.2519 | 24.9895 | 25.6887 | 26.9107 | 29.9842 | 31.6373 | 30.4313 | 34.165 | 34.8377 | 35.3212 | 37.6005 | 37.9715 | 37.9715 | 37.9715 | 37.9715 | 37.9715 | 37.9715 | 37.9715 | 37.9715 | 37.9715 | 37.9715 | 37.9715 | 37.9715 | 37.9715 | 37.9715 | 37.9715 | 37.9715 |  | 22.9039 | 26.9462 | 27.3648 | 28.8095 | 28.7742 | 29.0919 | 30.3344 | 33.9041 | 35.3771 | 33.9828 | 37.8346 | 36.2174 | 37.6725 | 38.7211 | 38.2903 | 38.2903 | 38.2903 | 38.2903 | 38.2903 | 38.2903 | 38.2903 | 38.2903 | 38.2903 | 38.2903 | 38.2903 | 38.2903 | 38.2903 | 38.2903 | 38.2903 | 38.2903
90% | 105.2028 | 129.7026 | 132.3005 | 135.5122 | 139.7764 | 143.8191 | 150.8839 | 168.6524 | 178.2095 | 171.2373 | 192.8224 | 196.7114 | 199.5069 | 212.6842 | 214.8291 | 214.8291 | 214.8291 | 214.8291 | 214.8291 | 214.8291 | 214.8291 | 214.8291 | 214.8291 | 214.8291 | 214.8291 | 214.8291 | 214.8291 | 214.8291 | 214.8291 | 214.8291 |  | 127.7194 | 151.0886 | 153.5087 | 161.8608 | 161.6572 | 163.4938 | 170.6769 | 191.314 | 199.8301 | 191.769 | 214.0372 | 204.6878 | 213.1003 | 219.1625 | 216.6718 | 216.6718 | 216.6718 | 216.6718 | 216.6718 | 216.6718 | 216.6718 | 216.6718 | 216.6718 | 216.6718 | 216.6718 | 216.6718 | 216.6718 | 216.6718 | 216.6718 | 216.6718
85% | 408.7931 | 511.1512 | 522.005 | 535.4235 | 553.2391 | 570.1289 | 599.6452 | 673.8807 | 713.8099 | 684.6804 | 774.8612 | 791.1091 | 802.7887 | 857.8426 | 866.8037 | 866.8037 | 866.8037 | 866.8037 | 866.8037 | 866.8037 | 866.8037 | 866.8037 | 866.8037 | 866.8037 | 866.8037 | 866.8037 | 866.8037 | 866.8037 | 866.8037 | 866.8037 |  | 502.8656 | 600.5006 | 610.6116 | 645.5059 | 644.6555 | 652.3285 | 682.3388 | 768.5594 | 804.1392 | 770.4602 | 863.495 | 824.4339 | 859.5808 | 884.9083 | 874.5026 | 874.5026 | 874.5026 | 874.5026 | 874.5026 | 874.5026 | 874.5026 | 874.5026 | 874.5026 | 874.5026 | 874.5026 | 874.5026 | 874.5026 | 874.5026 | 874.5026 | 874.5026
80% | 592.6734 | 754.7359 | 771.9205 | 793.1658 | 821.3732 | 848.1145 | 894.8474 | 1012.3836 | 1075.6029 | 1029.4825 | 1172.2649 | 1197.99 | 1216.482 | 1303.6484 | 1317.8363 | 1317.8363 | 1317.8363 | 1317.8363 | 1317.8363 | 1317.8363 | 1317.8363 | 1317.8363 | 1317.8363 | 1317.8363 | 1317.8363 | 1317.8363 | 1317.8363 | 1317.8363 | 1317.8363 | 1317.8363 |  | 741.6174 | 896.2017 | 912.2103 | 967.4581 | 966.1116 | 978.2602 | 1025.7752 | 1162.2872 | 1218.6203 | 1165.2967 | 1312.5977 | 1250.7528 | 1306.4003 | 1346.5011 | 1330.0258 | 1330.0258 | 1330.0258 | 1330.0258 | 1330.0258 | 1330.0258 | 1330.0258 | 1330.0258 | 1330.0258 | 1330.0258 | 1330.0258 | 1330.0258 | 1330.0258 | 1330.0258 | 1330.0258 | 1330.0258
75% | 980.9496 | 1280.2989 | 1312.0411 | 1351.2837 | 1403.3862 | 1452.7807 | 1539.1021 | 1756.2058 | 1872.9798 | 1787.7897 | 2051.5263 | 2099.0437 | 2133.2008 | 2294.2077 | 2320.4147 | 2320.4147 | 2320.4147 | 2320.4147 | 2320.4147 | 2320.4147 | 2320.4147 | 2320.4147 | 2320.4147 | 2320.4147 | 2320.4147 | 2320.4147 | 2320.4147 | 2320.4147 | 2320.4147 | 2320.4147 |  | 1256.0675 | 1541.6038 | 1571.1735 | 1673.2229 | 1670.7358 | 1693.1758 | 1780.9419 | 2033.0964 | 2137.1505 | 2038.6552 | 2310.7383 | 2196.5031 | 2299.291 | 2373.362 | 2342.9301 | 2342.9301 | 2342.9301 | 2342.9301 | 2342.9301 | 2342.9301 | 2342.9301 | 2342.9301 | 2342.9301 | 2342.9301 | 2342.9301 | 2342.9301 | 2342.9301 | 2342.9301 | 2342.9301 | 2342.9301
70% | 1385.9626 | 1873.2259 | 1924.894 | 1988.7709 | 2073.5802 | 2153.9818 | 2294.4906 | 2647.8796 | 2837.9574 | 2699.29 | 3128.585 | 3205.9311 | 3261.5301 | 3523.6078 | 3566.266 | 3566.266 | 3566.266 | 3566.266 | 3566.266 | 3566.266 | 3566.266 | 3566.266 | 3566.266 | 3566.266 | 3566.266 | 3566.266 | 3566.266 | 3566.266 | 3566.266 | 3566.266 |  | 1833.7834 | 2298.5628 | 2346.6947 | 2512.8048 | 2508.7564 | 2545.283 | 2688.1435 | 3098.5859 | 3267.9592 | 3107.6342 | 3550.5153 | 3364.5698 | 3531.882 | 3652.4506 | 3602.9153 | 3602.9153 | 3602.9153 | 3602.9153 | 3602.9153 | 3602.9153 | 3602.9153 | 3602.9153 | 3602.9153 | 3602.9153 | 3602.9153 | 3602.9153 | 3602.9153 | 3602.9153 | 3602.9153 | 3602.9153
65% | 1400.8592 | 1997.5436 | 2060.8145 | 2139.0357 | 2242.8901 | 2341.3468 | 2513.4087 | 2946.1556 | 3178.9178 | 3009.1109 | 3534.8094 | 3629.5246 | 3697.6091 | 4018.5396 | 4070.7772 | 4070.7772 | 4070.7772 | 4070.7772 | 4070.7772 | 4070.7772 | 4070.7772 | 4070.7772 | 4070.7772 | 4070.7772 | 4070.7772 | 4070.7772 | 4070.7772 | 4070.7772 | 4070.7772 | 4070.7772 |  | 1949.2438 | 2518.3953 | 2577.3359 | 2780.7481 | 2775.7906 | 2820.5196 | 2995.4612 | 3498.0737 | 3705.4819 | 3509.1539 | 4051.4896 | 3823.7877 | 4028.6719 | 4176.3156 | 4115.6566 | 4115.6566 | 4115.6566 | 4115.6566 | 4115.6566 | 4115.6566 | 4115.6566 | 4115.6566 | 4115.6566 | 4115.6566 | 4115.6566 | 4115.6566 | 4115.6566 | 4115.6566 | 4115.6566 | 4115.6566
60% | 1311.1794 | 2051.2755 | 2129.7534 | 2226.7749 | 2355.5904 | 2477.711 | 2691.1276 | 3227.8842 | 3516.5903 | 3305.9706 | 3958.0197 | 4075.4994 | 4159.9479 | 4558.0133 | 4622.8061 | 4622.8061 | 4622.8061 | 4622.8061 | 4622.8061 | 4622.8061 | 4622.8061 | 4622.8061 | 4622.8061 | 4622.8061 | 4622.8061 | 4622.8061 | 4622.8061 | 4622.8061 | 4622.8061 | 4622.8061 |  | 1991.367 | 2697.3127 | 2770.4195 | 3022.7214 | 3016.5724 | 3072.052 | 3289.0403 | 3912.4546 | 4169.7129 | 3926.1979 | 4598.8827 | 4316.4532 | 4570.5808 | 4753.7104 | 4678.4721 | 4678.4721 | 4678.4721 | 4678.4721 | 4678.4721 | 4678.4721 | 4678.4721 | 4678.4721 | 4678.4721 | 4678.4721 | 4678.4721 | 4678.4721 | 4678.4721 | 4678.4721 | 4678.4721 | 4678.4721
55% | 879.254 | 1681.979 | 1767.0979 | 1872.3296 | 2012.0458 | 2144.5006 | 2375.977 | 2958.1553 | 3271.2924 | 3042.8496 | 3750.0767 | 3877.4979 | 3969.0926 | 4400.8433 | 4471.1191 | 4471.1191 | 4471.1191 | 4471.1191 | 4471.1191 | 4471.1191 | 4471.1191 | 4471.1191 | 4471.1191 | 4471.1191 | 4471.1191 | 4471.1191 | 4471.1191 | 4471.1191 | 4471.1191 | 4471.1191 |  | 1617.0008 | 2382.6855 | 2461.9788 | 2735.6311 | 2728.9617 | 2789.1362 | 3024.4867 | 3700.6558 | 3979.6839 | 3715.5621 | 4445.1712 | 4138.8418 | 4414.4743 | 4613.1009 | 4531.4957 | 4531.4957 | 4531.4957 | 4531.4957 | 4531.4957 | 4531.4957 | 4531.4957 | 4531.4957 | 4531.4957 | 4531.4957 | 4531.4957 | 4531.4957 | 4531.4957 | 4531.4957 | 4531.4957 | 4531.4957
50% | 249.4213 | 1054.7724 | 1141.4594 | 1248.6298 | 1390.9199 | 1525.8148 | 1761.5555 | 2354.459 | 2673.3649 | 2440.7136 | 3160.9695 | 3290.738 | 3384.0202 | 3823.7248 | 3895.2952 | 3895.2952 | 3895.2952 | 3895.2952 | 3895.2952 | 3895.2952 | 3895.2952 | 3895.2952 | 3895.2952 | 3895.2952 | 3895.2952 | 3895.2952 | 3895.2952 | 3895.2952 | 3895.2952 | 3895.2952 |  | 988.5972 | 1768.3876 | 1849.1417 | 2127.8353 | 2121.0431 | 2182.3261 | 2422.0123 | 3110.6381 | 3394.8066 | 3125.819 | 3868.8693 | 3556.8965 | 3837.6069 | 4039.8926 | 3956.7841 | 3956.7841 | 3956.7841 | 3956.7841 | 3956.7841 | 3956.7841 | 3956.7841 | 3956.7841 | 3956.7841 | 3956.7841 | 3956.7841 | 3956.7841 | 3956.7841 | 3956.7841 | 3956.7841 | 3956.7841
45% |  | 263.6586 | 332.2401 | 426.8754 | 561.1949 | 688.6055 | 911.2667 | 1471.2745 | 1772.4867 | 1552.7434 | 2233.0378 | 2355.6065 | 2443.7131 | 2859.0218 | 2926.6213 | 2926.6213 | 2926.6213 | 2926.6213 | 2926.6213 | 2926.6213 | 2926.6213 | 2926.6213 | 2926.6213 | 2926.6213 | 2926.6213 | 2926.6213 | 2926.6213 | 2926.6213 | 2926.6213 | 2926.6213 |  | 216.2457 | 917.7197 | 993.9934 | 1257.2244 | 1250.8091 | 1308.6919 | 1535.0798 | 2185.4989 | 2453.9011 | 2199.8376 | 2901.6616 | 2606.9978 | 2872.1337 | 3063.1961 | 2984.6986 | 2984.6986 | 2984.6986 | 2984.6986 | 2984.6986 | 2984.6986 | 2984.6986 | 2984.6986 | 2984.6986 | 2984.6986 | 2984.6986 | 2984.6986 | 2984.6986 | 2984.6986 | 2984.6986 | 2984.6986
40% |  |  |  |  | 7.5893 | 31.1945 | 108.8464 | 488.9496 | 760.7952 | 562.4477 | 1176.5041 | 1287.1386 | 1366.6666 | 1741.5381 | 1802.5557 | 1802.5557 | 1802.5557 | 1802.5557 | 1802.5557 | 1802.5557 | 1802.5557 | 1802.5557 | 1802.5557 | 1802.5557 | 1802.5557 | 1802.5557 | 1802.5557 | 1802.5557 | 1802.5557 | 1802.5557 |  |  | 111.7593 | 148.9205 | 314.3792 | 309.6857 | 353.1877 | 546.5039 | 1133.5939 | 1375.8626 | 1146.5364 | 1780.0262 | 1514.0529 | 1753.3734 | 1925.8327 | 1854.9782 | 1854.9782 | 1854.9782 | 1854.9782 | 1854.9782 | 1854.9782 | 1854.9782 | 1854.9782 | 1854.9782 | 1854.9782 | 1854.9782 | 1854.9782 | 1854.9782 | 1854.9782 | 1854.9782 | 1854.9782
35% | [8 empty] | 26.1432 | 1.6005 | 166.5253 | 222.5876 | 267.429 | 526.6894 | 574.0431 | 574.0431 | 574.0431 | 574.0431 | 574.0431 | 574.0431 | 574.0431 | 574.0431 | 574.0431 | 574.0431 | 574.0431 | 574.0431 | 574.0431 | 574.0431 | 574.0431 | 574.0431 | [7 empty] | 0.90619 | 146.8106 | 272.8539 | 152.6356 | 556.5587 | 360.2185 | 535.8744 | 669.7143 | 614.7265 | 614.7265 | 614.7265 | 614.7265 | 614.7265 | 614.7265 | 614.7265 | 614.7265 | 614.7265 | 614.7265 | 614.7265 | 614.7265 | 614.7265 | 614.7265 | 614.7265 | 614.7265
30% | FY38: 0.23254; FY39: 1.8503; FY40: 1.8503; FY41: 1.8503; FY42: 1.8503; FY43: 1.8503; FY44: 1.8503; FY45: 1.8503; FY46: 1.8503; FY47: 1.8503; FY48: 1.8503; FY49: 1.8503; FY50: 1.8503; FY51: 1.8503; FY52: 1.8503; FY53: 1.8503; FY54: 1.8503 | [11 empty] | 1.0747 |  | 0.42635 | 9.7196 | 4.4531 | 4.4531 | 4.4531 | 4.4531 | 4.4531 | 4.4531 | 4.4531 | 4.4531 | 4.4531 | 4.4531 | 4.4531 | 4.4531 | 4.4531 | 4.4531 | 4.4531 | 4.4531
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 7265.0415 | 11511.5317 | 12003.3126 | 12621.0477 | 13457.3132 | 14266.4334 | 15716.478 | 19546.391 | 21698.9988 | 20123.164 | 25089.7832 | 26010.7036 | 26677.1895 | 29866.4513 | 30392.2317 | 30392.2317 | 30392.2317 | 30392.2317 | 30392.2317 | 30392.2317 | 30392.2317 | 30392.2317 | 30392.2317 | 30392.2317 | 30392.2317 | 30392.2317 | 30392.2317 | 30392.2317 | 30392.2317 | 30392.2317 | E @ R (MWh) | 11141.0066 | 15759.1581 | 16266.3334 | 18053.5033 | 18009.2926 | 18409.3276 | 19997.7591 | 24734.6086 | 26754.4944 | 24841.616 | 30197.9216 | 27921.9531 | 29968.3153 | 31459.0485 | 30845.1507 | 30845.1507 | 30845.1507 | 30845.1507 | 30845.1507 | 30845.1507 | 30845.1507 | 30845.1507 | 30845.1507 | 30845.1507 | 30845.1507 | 30845.1507 | 30845.1507 | 30845.1507 | 30845.1507 | 30845.1507
Option 8 Winter POE50 W E @ R (MWh) N 2 | 5085.529 | 8058.0722 | 8402.3188 | 8834.7334 | 9420.1193 | 9986.5034 | 11001.5346 | 13682.4737 | 15189.2992 | 14086.2148 | 17562.8482 | 18207.4925 | 18674.0327 | 20906.5159 | 21274.5622 | 21274.5622 | 21274.5622 | 21274.5622 | 21274.5622 | 21274.5622 | 21274.5622 | 21274.5622 | 21274.5622 | 21274.5622 | 21274.5622 | 21274.5622 | 21274.5622 | 21274.5622 | 21274.5622 | 21274.5622 | Option 8 Winter POE10 W E @ R (MWh) N 2 | 3342.302 | 4727.7474 | 4879.9 | 5416.051 | 5402.7878 | 5522.7983 | 5999.3277 | 7420.3826 | 8026.3483 | 7452.4848 | 9059.3765 | 8376.5859 | 8990.4946 | 9437.7145 | 9253.5452 | 9253.5452 | 9253.5452 | 9253.5452 | 9253.5452 | 9253.5452 | 9253.5452 | 9253.5452 | 9253.5452 | 9253.5452 | 9253.5452 | 9253.5452 | 9253.5452 | 9253.5452 | 9253.5452 | 9253.5452
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | 7.3419 | 8.3902 | 8.4955 | 8.4439 | 8.493 | 8.5131 | 8.5778 | 8.7107 | 8.8225 | 8.874 | 8.8281 | 9.0205 | 9.051 | 9.0149 | 9.0873 | 9.1287 | 9.1287 | 9.1287 | 9.1287 | 9.1287 | 9.1287 | 9.1287 | 9.1287 | 9.1287 | 9.1287 | 9.1287 | 9.1287 | 9.1287 | 9.1287 | 9.1287 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
98% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
97% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 10.2241 | 11.372 | 11.4037 | 11.3695 | 11.3783 | 11.441 | 11.568 | 11.7917 | 11.9083 | 11.9926 | 12.1203 | 12.2833 | 12.4803 | 12.5836 | 12.5501 | 12.5907 | 12.5907 | 12.5907 | 12.5907 | 12.5907 | 12.5907 | 12.5907 | 12.5907 | 12.5907 | 12.5907 | 12.5907 | 12.5907 | 12.5907 | 12.5907 | 12.5907
95% | 6.8489 | 7.8602 | 7.9619 | 7.9121 | 7.9594 | 7.9789 | 8.0413 | 8.1695 | 8.2774 | 8.3271 | 8.2828 | 8.4684 | 8.4979 | 8.463 | 8.5329 | 8.5728 | 8.5728 | 8.5728 | 8.5728 | 8.5728 | 8.5728 | 8.5728 | 8.5728 | 8.5728 | 8.5728 | 8.5728 | 8.5728 | 8.5728 | 8.5728 | 8.5728 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
90% | 139.8285 | 161.2671 | 163.4215 | 162.3655 | 163.3696 | 163.7822 | 165.1044 | 167.8232 | 170.1105 | 171.1633 | 170.2249 | 174.1594 | 174.7834 | 174.0449 | 175.5257 | 176.3722 | 176.3722 | 176.3722 | 176.3722 | 176.3722 | 176.3722 | 176.3722 | 176.3722 | 176.3722 | 176.3722 | 176.3722 | 176.3722 | 176.3722 | 176.3722 | 176.3722 |  | 9.3575 | 10.4465 | 10.4766 | 10.4442 | 10.4525 | 10.512 | 10.6325 | 10.8447 | 10.9553 | 11.0354 | 11.1564 | 11.3111 | 11.498 | 11.596 | 11.5642 | 11.6027 | 11.6027 | 11.6027 | 11.6027 | 11.6027 | 11.6027 | 11.6027 | 11.6027 | 11.6027 | 11.6027 | 11.6027 | 11.6027 | 11.6027 | 11.6027 | 11.6027
85% | 469.0739 | 545.5841 | 553.2725 | 549.5038 | 553.0872 | 554.5596 | 559.2785 | 568.9815 | 577.144 | 580.9015 | 577.5525 | 591.5938 | 593.8207 | 591.1853 | 596.47 | 599.4911 | 599.4911 | 599.4911 | 599.4911 | 599.4911 | 599.4911 | 599.4911 | 599.4911 | 599.4911 | 599.4911 | 599.4911 | 599.4911 | 599.4911 | 599.4911 | 599.4911 |  | 8.4909 | 9.521 | 9.5495 | 9.5188 | 9.5267 | 9.583 | 9.697 | 9.8978 | 10.0024 | 10.0781 | 10.1926 | 10.3389 | 10.5157 | 10.6084 | 10.5783 | 10.6147 | 10.6147 | 10.6147 | 10.6147 | 10.6147 | 10.6147 | 10.6147 | 10.6147 | 10.6147 | 10.6147 | 10.6147 | 10.6147 | 10.6147 | 10.6147 | 10.6147
80% | 707.4418 | 831.7279 | 844.2173 | 838.0953 | 843.9164 | 846.3082 | 853.9736 | 869.7356 | 882.9952 | 889.099 | 883.6587 | 906.4679 | 910.0855 | 905.8043 | 914.3891 | 919.2966 | 919.2966 | 919.2966 | 919.2966 | 919.2966 | 919.2966 | 919.2966 | 919.2966 | 919.2966 | 919.2966 | 919.2966 | 919.2966 | 919.2966 | 919.2966 | 919.2966 |  | 30.4971 | 34.3823 | 34.4895 | 34.3739 | 34.4037 | 34.6158 | 35.0458 | 35.803 | 36.1976 | 36.4831 | 36.9151 | 37.4666 | 38.1336 | 38.4831 | 38.3698 | 38.5071 | 38.5071 | 38.5071 | 38.5071 | 38.5071 | 38.5071 | 38.5071 | 38.5071 | 38.5071 | 38.5071 | 38.5071 | 38.5071 | 38.5071 | 38.5071 | 38.5071
75% | 1149.798 | 1371.0584 | 1393.2926 | 1382.3939 | 1392.7569 | 1397.0149 | 1410.6614 | 1438.7215 | 1462.327 | 1473.1933 | 1463.5082 | 1504.1143 | 1510.5546 | 1502.933 | 1518.216 | 1526.9526 | 1526.9526 | 1526.9526 | 1526.9526 | 1526.9526 | 1526.9526 | 1526.9526 | 1526.9526 | 1526.9526 | 1526.9526 | 1526.9526 | 1526.9526 | 1526.9526 | 1526.9526 | 1526.9526 |  | 13.5153 | 15.3402 | 15.3906 | 15.3363 | 15.3503 | 15.4499 | 15.6519 | 16.0075 | 16.1929 | 16.3269 | 16.5299 | 16.7889 | 17.1022 | 17.2664 | 17.2131 | 17.2776 | 17.2776 | 17.2776 | 17.2776 | 17.2776 | 17.2776 | 17.2776 | 17.2776 | 17.2776 | 17.2776 | 17.2776 | 17.2776 | 17.2776 | 17.2776 | 17.2776
70% | 1309.2261 | 1591.8262 | 1620.2245 | 1606.3043 | 1619.5402 | 1624.9786 | 1642.4083 | 1678.2476 | 1708.3971 | 1722.2759 | 1709.9059 | 1761.7692 | 1769.9948 | 1760.2603 | 1779.7801 | 1790.9388 | 1790.9388 | 1790.9388 | 1790.9388 | 1790.9388 | 1790.9388 | 1790.9388 | 1790.9388 | 1790.9388 | 1790.9388 | 1790.9388 | 1790.9388 | 1790.9388 | 1790.9388 | 1790.9388 |  | 35.3464 | 40.4679 | 40.6092 | 40.4568 | 40.496 | 40.7757 | 41.3425 | 42.3407 | 42.8608 | 43.237 | 43.8065 | 44.5336 | 45.4128 | 45.8735 | 45.7241 | 45.9051 | 45.9051 | 45.9051 | 45.9051 | 45.9051 | 45.9051 | 45.9051 | 45.9051 | 45.9051 | 45.9051 | 45.9051 | 45.9051 | 45.9051 | 45.9051 | 45.9051
65% | 1383.0411 | 1730.0625 | 1764.9344 | 1747.8411 | 1764.0942 | 1770.7723 | 1792.1753 | 1836.1844 | 1873.2068 | 1890.2494 | 1875.0595 | 1938.7455 | 1948.8462 | 1936.8927 | 1960.8622 | 1974.5646 | 1974.5646 | 1974.5646 | 1974.5646 | 1974.5646 | 1974.5646 | 1974.5646 | 1974.5646 | 1974.5646 | 1974.5646 | 1974.5646 | 1974.5646 | 1974.5646 | 1974.5646 | 1974.5646 |  | 10.0489 | 11.6384 | 11.6822 | 11.6349 | 11.6471 | 11.7339 | 11.9098 | 12.2196 | 12.381 | 12.4978 | 12.6745 | 12.9001 | 13.173 | 13.316 | 13.2696 | 13.3258 | 13.3258 | 13.3258 | 13.3258 | 13.3258 | 13.3258 | 13.3258 | 13.3258 | 13.3258 | 13.3258 | 13.3258 | 13.3258 | 13.3258 | 13.3258 | 13.3258
60% | 1639.9094 | 2146.9041 | 2197.8516 | 2172.8784 | 2196.624 | 2206.3807 | 2237.6502 | 2301.9471 | 2356.0365 | 2380.9355 | 2358.7431 | 2451.7877 | 2466.5448 | 2449.0808 | 2484.1001 | 2504.1192 | 2504.1192 | 2504.1192 | 2504.1192 | 2504.1192 | 2504.1192 | 2504.1192 | 2504.1192 | 2504.1192 | 2504.1192 | 2504.1192 | 2504.1192 | 2504.1192 | 2504.1192 | 2504.1192 |  | 54.0524 | 63.6183 | 63.8823 | 63.5977 | 63.6709 | 64.1933 | 65.2519 | 67.1163 | 68.0878 | 68.7906 | 69.8543 | 71.2123 | 72.8544 | 73.715 | 73.436 | 73.774 | 73.774 | 73.774 | 73.774 | 73.774 | 73.774 | 73.774 | 73.774 | 73.774 | 73.774 | 73.774 | 73.774 | 73.774 | 73.774 | 73.774
55% | 1468.1665 | 2092.0991 | 2154.7976 | 2124.0644 | 2153.2869 | 2165.294 | 2203.7758 | 2282.9027 | 2349.4677 | 2380.1097 | 2352.7987 | 2467.304 | 2485.4648 | 2463.9727 | 2507.0692 | 2531.7056 | 2531.7056 | 2531.7056 | 2531.7056 | 2531.7056 | 2531.7056 | 2531.7056 | 2531.7056 | 2531.7056 | 2531.7056 | 2531.7056 | 2531.7056 | 2531.7056 | 2531.7056 | 2531.7056 |  | 210.6416 | 253.9682 | 255.1638 | 253.8747 | 254.2062 | 256.5722 | 261.367 | 269.8113 | 274.2113 | 277.3946 | 282.2122 | 288.363 | 295.8006 | 299.6984 | 298.4348 | 299.9656 | 299.9656 | 299.9656 | 299.9656 | 299.9656 | 299.9656 | 299.9656 | 299.9656 | 299.9656 | 299.9656 | 299.9656 | 299.9656 | 299.9656 | 299.9656 | 299.9656
50% | 922.9519 | 1630.9008 | 1702.042 | 1667.1704 | 1700.3279 | 1713.9518 | 1757.6154 | 1847.3972 | 1922.9257 | 1957.6938 | 1926.7051 | 2056.6293 | 2077.2355 | 2052.8494 | 2101.749 | 2129.7029 | 2129.7029 | 2129.7029 | 2129.7029 | 2129.7029 | 2129.7029 | 2129.7029 | 2129.7029 | 2129.7029 | 2129.7029 | 2129.7029 | 2129.7029 | 2129.7029 | 2129.7029 | 2129.7029 |  | 383.0991 | 480.7604 | 483.4553 | 480.5498 | 481.297 | 486.6301 | 497.438 | 516.4721 | 526.39 | 533.5653 | 544.4247 | 558.2889 | 575.0538 | 583.8398 | 580.9915 | 584.442 | 584.442 | 584.442 | 584.442 | 584.442 | 584.442 | 584.442 | 584.442 | 584.442 | 584.442 | 584.442 | 584.442 | 584.442 | 584.442 | 584.442
45% | 113.1135 | 605.5456 | 664.4302 | 635.5664 | 663.0115 | 674.2882 | 710.4292 | 784.743 | 847.2591 | 876.0372 | 850.3875 | 957.9277 | 974.9838 | 954.799 | 995.274 | 1018.4119 | 1018.4119 | 1018.4119 | 1018.4119 | 1018.4119 | 1018.4119 | 1018.4119 | 1018.4119 | 1018.4119 | 1018.4119 | 1018.4119 | 1018.4119 | 1018.4119 | 1018.4119 | 1018.4119 |  | 467.4239 | 635.1966 | 639.8262 | 634.8348 | 636.1184 | 645.2801 | 663.8471 | 696.5457 | 713.5838 | 725.9102 | 744.5656 | 768.3829 | 797.1834 | 812.2769 | 807.3838 | 813.3115 | 813.3115 | 813.3115 | 813.3115 | 813.3115 | 813.3115 | 813.3115 | 813.3115 | 813.3115 | 813.3115 | 813.3115 | 813.3115 | 813.3115 | 813.3115 | 813.3115
40% |  | 11.9277 | 21.3864 | 16.4156 | 21.1271 | 23.2302 | 30.6206 | 48.888 | 67.3917 | 76.8544 | 68.3917 | 106.9766 | 113.8368 | 105.7399 | 122.2575 | 132.2021 | 132.2021 | 132.2021 | 132.2021 | 132.2021 | 132.2021 | 132.2021 | 132.2021 | 132.2021 | 132.2021 | 132.2021 | 132.2021 | 132.2021 | 132.2021 | 132.2021 |  | 313.9328 | 541.1029 | 547.3715 | 540.613 | 542.3511 | 554.7563 | 579.8966 | 624.1718 | 647.2418 | 663.9323 | 689.1923 | 721.4418 | 760.4386 | 780.8759 | 774.2504 | 782.2767 | 782.2767 | 782.2767 | 782.2767 | 782.2767 | 782.2767 | 782.2767 | 782.2767 | 782.2767 | 782.2767 | 782.2767 | 782.2767 | 782.2767 | 782.2767 | 782.2767
35% | [31 empty] | 32.1525 | 240.1146 | 248.3143 | 239.479 | 241.7375 | 258.1321 | 292.8244 | 358.5913 | 395.1611 | 422.2729 | 463.3148 | 515.7129 | 579.0739 | 612.2797 | 601.5148 | 614.5558 | 614.5558 | 614.5558 | 614.5558 | 614.5558 | 614.5558 | 614.5558 | 614.5558 | 614.5558 | 614.5558 | 614.5558 | 614.5558 | 614.5558 | 614.5558 | 614.5558
30% | [40 empty] | 0.54575 | 4.0441 | 13.1246 | 30.8413 | 43.0003 | 38.845 | 43.905 | 43.905 | 43.905 | 43.905 | 43.905 | 43.905 | 43.905 | 43.905 | 43.905 | 43.905 | 43.905 | 43.905 | 43.905 | 43.905 | 43.905
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 9223.5741 | 12607.8025 | 12965.3646 | 12789.7654 | 12956.7185 | 13025.4821 | 13246.5087 | 13704.0276 | 14092.0177 | 14271.5572 | 14111.5063 | 14785.6146 | 14893.2628 | 14765.8898 | 15021.58 | 15168.2446 | 15168.2446 | 15168.2446 | 15168.2446 | 15168.2446 | 15168.2446 | 15168.2446 | 15168.2446 | 15168.2446 | 15168.2446 | 15168.2446 | 15168.2446 | 15168.2446 | 15168.2446 | 15168.2446 | E @ R (MWh) | 1562.9946 | 2324.4501 | 2347.8985 | 2322.6227 | 2329.1093 | 2375.6785 | 2471.5078 | 2644.8974 | 2737.5223 | 2805.7218 | 2911.5932 | 3051.3274 | 3226.9658 | 3321.8588 | 3290.8844 | 3328.4339 | 3328.4339 | 3328.4339 | 3328.4339 | 3328.4339 | 3328.4339 | 3328.4339 | 3328.4339 | 3328.4339 | 3328.4339 | 3328.4339 | 3328.4339 | 3328.4339 | 3328.4339 | 3328.4339
Option 8 Summer POE50 W E @ R (MWh) N 2 | 6456.5019 | 8825.4618 | 9075.7552 | 8952.8358 | 9069.703 | 9117.8375 | 9272.5561 | 9592.8193 | 9864.4124 | 9990.0901 | 9878.0544 | 10349.9302 | 10425.2839 | 10336.1228 | 10515.106 | 10617.7712 | 10617.7712 | 10617.7712 | 10617.7712 | 10617.7712 | 10617.7712 | 10617.7712 | 10617.7712 | 10617.7712 | 10617.7712 | 10617.7712 | 10617.7712 | 10617.7712 | 10617.7712 | 10617.7712 | Option 8 Summer POE10 W E @ R (MWh) N 2 | 468.8984 | 697.335 | 704.3695 | 696.7868 | 698.7328 | 712.7036 | 741.4523 | 793.4692 | 821.2567 | 841.7165 | 873.478 | 915.3982 | 968.0898 | 996.5577 | 987.2653 | 998.5302 | 998.5302 | 998.5302 | 998.5302 | 998.5302 | 998.5302 | 998.5302 | 998.5302 | 998.5302 | 998.5302 | 998.5302 | 998.5302 | 998.5302 | 998.5302 | 998.5302

## POF N,N-1 & N-2 Risk
N-2 Method 1
| Asset name | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Tx 1 Pof | DS-WGI-TRNFMR-9000004493 | 1.976% | 1.976% | 2.058% | 2.142% | 2.227% | 2.315% | 2.405% | 2.496% | 2.59% | 2.686% | 2.783% | 2.883% | 2.985% | 3.089% | 3.195% | 3.195% | 3.195% | 3.195% | 3.195% | 3.195% | 3.195% | 3.195% | 3.195% | 3.195% | 3.195% | 3.195% | 3.195% | 3.195% | 3.195% | 3.195%
Tx 2 Pof | DS-WGI-TRNFMR-9000003147 | 0.9218% | 0.9218% | 0.9742% | 1.028% | 1.084% | 1.142% | 1.201% | 1.262% | 1.325% | 1.39% | 1.457% | 1.525% | 1.596% | 1.668% | 1.742% | 1.742% | 1.742% | 1.742% | 1.742% | 1.742% | 1.742% | 1.742% | 1.742% | 1.742% | 1.742% | 1.742% | 1.742% | 1.742% | 1.742% | 1.742%
Tx 3 Pof | DS-WGI-TRNFMR-9000007146 | 0.9218% | 0.9218% | 0.9742% | 1.028% | 1.084% | 1.142% | 1.201% | 1.262% | 1.325% | 1.39% | 1.457% | 1.525% | 1.596% | 1.668% | 1.742% | 1.742% | 1.742% | 1.742% | 1.742% | 1.742% | 1.742% | 1.742% | 1.742% | 1.742% | 1.742% | 1.742% | 1.742% | 1.742% | 1.742% | 1.742%
Tx 4 Pof
Tx 5 Pof
Total Tx Pof |  | 3.82% | 3.82% | 4.006% | 4.198% | 4.396% | 4.599% | 4.807% | 5.021% | 5.241% | 5.466% | 5.697% | 5.934% | 6.177% | 6.425% | 6.679% | 6.679% | 6.679% | 6.679% | 6.679% | 6.679% | 6.679% | 6.679% | 6.679% | 6.679% | 6.679% | 6.679% | 6.679% | 6.679% | 6.679% | 6.679%
N-1 Risk |  | 1.474% | 1.474% | 1.546% | 1.62% | 1.696% | 1.774% | 1.855% | 1.937% | 2.022% | 2.109% | 2.198% | 2.289% | 2.383% | 2.479% | 2.577% | 2.577% | 2.577% | 2.577% | 2.577% | 2.577% | 2.577% | 2.577% | 2.577% | 2.577% | 2.577% | 2.577% | 2.577% | 2.577% | 2.577% | 2.577%
N-2 Risk |  | 0.01053% | 0.01053% | 0.01162% | 0.0128% | 0.01408% | 0.01545% | 0.01692% | 0.01851% | 0.02021% | 0.02204% | 0.02399% | 0.02607% | 0.0283% | 0.03068% | 0.03321% | 0.03321% | 0.03321% | 0.03321% | 0.03321% | 0.03321% | 0.03321% | 0.03321% | 0.03321% | 0.03321% | 0.03321% | 0.03321% | 0.03321% | 0.03321% | 0.03321% | 0.03321%
N Risk |  | 98.52% | 98.52% | 98.44% | 98.37% | 98.29% | 98.21% | 98.13% | 98.04% | 97.96% | 97.87% | 97.78% | 97.68% | 97.59% | 97.49% | 97.39% | 97.39% | 97.39% | 97.39% | 97.39% | 97.39% | 97.39% | 97.39% | 97.39% | 97.39% | 97.39% | 97.39% | 97.39% | 97.39% | 97.39% | 97.39%

## Summary
Involuntary load shedding (NER 5.17.1(c)(4)(ii))
Option 1 - Do Nothing | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Weighted Energy @ Risk (MWh) under N Conditions | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Weighted Energy @ Risk (MWh) under N-1 Conditions | 0.1003 | 0.78098 | 1.0023 | 1.4061 | 1.6028 | 1.9694 | 3.0951 | 8.3833 | 12.9562 | 10.037 | 24.0182 | 24.4461 | 30.0831 | 43.8321 | 46.6677 | 46.7869 | 46.7869 | 46.7869 | 46.7869 | 46.7869 | 46.7869 | 46.7869 | 46.7869 | 46.7869 | 46.7869 | 46.7869 | 46.7869 | 46.7869 | 46.7869 | 46.7869
Weighted Energy @ Risk (MWh) under N-2 Conditions | 1.973 | 2.8554 | 3.2564 | 3.705 | 4.1867 | 4.7273 | 5.5055 | 6.9711 | 8.1749 | 8.5377 | 10.646 | 11.7388 | 13.1353 | 15.142 | 16.5352 | 16.5855 | 16.5855 | 16.5855 | 16.5855 | 16.5855 | 16.5855 | 16.5855 | 16.5855 | 16.5855 | 16.5855 | 16.5855 | 16.5855 | 16.5855 | 16.5855 | 16.5855
Total EUE (MWh) - Option 1 | 2.0733 | 3.6364 | 4.2587 | 5.1111 | 5.7895 | 6.6967 | 8.6006 | 15.3544 | 21.1311 | 18.5746 | 34.6642 | 36.1849 | 43.2184 | 58.9741 | 63.2029 | 63.3724 | 63.3724 | 63.3724 | 63.3724 | 63.3724 | 63.3724 | 63.3724 | 63.3724 | 63.3724 | 63.3724 | 63.3724 | 63.3724 | 63.3724 | 63.3724 | 63.3724
Cost of EUE ($) - Option 1 | 88279.6477 | 154837.3319 | 181337.4266 | 217630.6447 | 246518.0678 | 285145.927 | 366215.4289 | 653795.436 | 899769.3066 | 790911.764 | 1476011.1922 | 1540765.1766 | 1840251.2779 | 2511133.3647 | 2691195.0652 | 2698414.6144 | 2698414.6144 | 2698414.6144 | 2698414.6144 | 2698414.6144 | 2698414.6144 | 2698414.6144 | 2698414.6144 | 2698414.6144 | 2698414.6144 | 2698414.6144 | 2698414.6144 | 2698414.6144 | 2698414.6144 | 2698414.6144
Hours at Risk pA. (Hrs) (N) | 0.2972 | 0.2972 | 0.2972 | 0.2972 | 0.2972 | 0.2972 | 0.2972 | 0.2972 | 0.2972 | 0.2972 | 0.2972 | 0.2972 | 0.2972 | 0.2972 | 0.2972 | 0.2972 | 0.2972 | 0.2972 | 0.2972 | 0.2972 | 0.2972 | 0.2972 | 0.2972 | 0.2972 | 0.2972 | 0.2972 | 0.2972 | 0.2972 | 0.2972 | 0.2972
Option 2 - Replace 3 x 10/13.5 MVA Tx with 3 x 20/33 MVA Tx | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Weighted Energy @ Risk (MWh) under N Conditions | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Weighted Energy @ Risk (MWh) under N-1 Conditions | 0.099581 | 0.78098 | 1.0023 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Weighted Energy @ Risk (MWh) under N-2 Conditions | 1.973 | 2.8554 | 3.2564 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total EUE (MWh) - Option 2 | 2.0725 | 3.6364 | 4.2587 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cost of EUE ($) - Option 2 | 88249.2162 | 154837.3319 | 181337.4266 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 - Replace 1 x 10/13.5 MVA Tx with 1 x 20/33 MVA Tx | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Weighted Energy @ Risk (MWh) under N Conditions | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Weighted Energy @ Risk (MWh) under N-1 Conditions | 0.099581 | 0.78098 | 1.0023 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00053629 | 0 | 0.00053618 | 0.0040337 | 0.0045707 | 0.0049634 | 0.0049634 | 0.0049634 | 0.0049634 | 0.0049634 | 0.0049634 | 0.0049634 | 0.0049634 | 0.0049634 | 0.0049634 | 0.0049634 | 0.0049634 | 0.0049634 | 0.0049634 | 0.0049634
Weighted Energy @ Risk (MWh) under N-2 Conditions | 1.973 | 2.8554 | 3.2564 | 0.045553 | 0.054917 | 0.067927 | 0.098946 | 0.21774 | 0.32284 | 0.28105 | 0.57932 | 0.62762 | 0.77267 | 1.0868 | 1.2011 | 1.2046 | 1.2046 | 1.2046 | 1.2046 | 1.2046 | 1.2046 | 1.2046 | 1.2046 | 1.2046 | 1.2046 | 1.2046 | 1.2046 | 1.2046 | 1.2046 | 1.2046
Total EUE (MWh) - Option 3 | 2.0725 | 3.6364 | 4.2587 | 0.045553 | 0.054917 | 0.067927 | 0.098946 | 0.21774 | 0.32284 | 0.28105 | 0.57986 | 0.62762 | 0.77321 | 1.0908 | 1.2057 | 1.2096 | 1.2096 | 1.2096 | 1.2096 | 1.2096 | 1.2096 | 1.2096 | 1.2096 | 1.2096 | 1.2096 | 1.2096 | 1.2096 | 1.2096 | 1.2096 | 1.2096
Cost of EUE ($) - Option 3 | 88249.2162 | 154837.3319 | 181337.4266 | 1939.6653 | 2338.385 | 2892.3429 | 4213.1393 | 9271.623 | 13746.6287 | 11967.3261 | 24690.5829 | 26724.1736 | 32923.4344 | 46446.9692 | 51338.4515 | 51505.2543 | 51505.2543 | 51505.2543 | 51505.2543 | 51505.2543 | 51505.2543 | 51505.2543 | 51505.2543 | 51505.2543 | 51505.2543 | 51505.2543 | 51505.2543 | 51505.2543 | 51505.2543 | 51505.2543
Option 4 - Construct 2x 20/33MVA zone substation in Inverloch | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Weighted Energy @ Risk (MWh) under N Conditions | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Weighted Energy @ Risk (MWh) under N-1 Conditions | 0.099581 | 0.78098 | 1.0023 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Weighted Energy @ Risk (MWh) under N-2 Conditions | 1.973 | 2.8554 | 3.2564 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total EUE (MWh) - Option 4 | 2.0725 | 3.6364 | 4.2587 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cost of EUE ($) - Option 4 | 88249.2162 | 154837.3319 | 181337.4266 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 - Contract network support services to defer network investment | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Weighted Energy @ Risk (MWh) under N Conditions | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Weighted Energy @ Risk (MWh) under N-1 Conditions | 0.021881 | 0.058169 | 0.06765 | 0.10202 | 0.10693 | 0.12809 | 0.23122 | 1.2583 | 2.4481 | 1.4852 | 6.1765 | 5.7597 | 7.7151 | 13.2069 | 14.1654 | 14.1722 | 14.1722 | 14.1722 | 14.1722 | 14.1722 | 14.1722 | 14.1722 | 14.1722 | 14.1722 | 14.1722 | 14.1722 | 14.1722 | 14.1722 | 14.1722 | 14.1722
Weighted Energy @ Risk (MWh) under N-2 Conditions | 1.0611 | 1.6982 | 1.959 | 2.2609 | 2.5788 | 2.9361 | 3.484 | 4.6215 | 5.5358 | 5.6795 | 7.403 | 8.1555 | 9.1757 | 10.7713 | 11.7973 | 11.84 | 11.84 | 11.84 | 11.84 | 11.84 | 11.84 | 11.84 | 11.84 | 11.84 | 11.84 | 11.84 | 11.84 | 11.84 | 11.84 | 11.84
Total EUE (MWh) - Option 5 | 1.083 | 1.7563 | 2.0267 | 2.3629 | 2.6857 | 3.0642 | 3.7152 | 5.8798 | 7.9839 | 7.1647 | 13.5795 | 13.9153 | 16.8909 | 23.9782 | 25.9627 | 26.0121 | 26.0121 | 26.0121 | 26.0121 | 26.0121 | 26.0121 | 26.0121 | 26.0121 | 26.0121 | 26.0121 | 26.0121 | 26.0121 | 26.0121 | 26.0121 | 26.0121
Cost of EUE ($) - Option 5 | 46114.6679 | 74784.7836 | 86297.3602 | 100611.7197 | 114356.9506 | 130475.9144 | 158194.1132 | 250362.0944 | 339956.1078 | 305073.8819 | 578218.9727 | 592516.0602 | 719217.1674 | 1020998.4402 | 1105498.4791 | 1107603.9982 | 1107603.9982 | 1107603.9982 | 1107603.9982 | 1107603.9982 | 1107603.9982 | 1107603.9982 | 1107603.9982 | 1107603.9982 | 1107603.9982 | 1107603.9982 | 1107603.9982 | 1107603.9982 | 1107603.9982 | 1107603.9982
Option 6 - | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Weighted Energy @ Risk (MWh) under N Conditions | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Weighted Energy @ Risk (MWh) under N-1 Conditions | 0.099581 | 0.78098 | 1.0023 | 1.4061 | 1.6028 | 1.9694 | 3.0951 | 8.3833 | 12.9562 | 10.037 | 24.0182 | 24.4461 | 30.0831 | 43.8321 | 46.6677 | 46.7869 | 46.7869 | 46.7869 | 46.7869 | 46.7869 | 46.7869 | 46.7869 | 46.7869 | 46.7869 | 46.7869 | 46.7869 | 46.7869 | 46.7869 | 46.7869 | 46.7869
Weighted Energy @ Risk (MWh) under N-2 Conditions | 1.973 | 2.8554 | 3.2564 | 3.705 | 4.1867 | 4.7273 | 5.5055 | 6.9711 | 8.1749 | 8.5377 | 10.646 | 11.7388 | 13.1353 | 15.142 | 16.5352 | 16.5855 | 16.5855 | 16.5855 | 16.5855 | 16.5855 | 16.5855 | 16.5855 | 16.5855 | 16.5855 | 16.5855 | 16.5855 | 16.5855 | 16.5855 | 16.5855 | 16.5855
Total EUE (MWh) - Option 6 | 2.0725 | 3.6364 | 4.2587 | 5.1111 | 5.7895 | 6.6967 | 8.6006 | 15.3544 | 21.1311 | 18.5746 | 34.6642 | 36.1849 | 43.2184 | 58.9741 | 63.2029 | 63.3724 | 63.3724 | 63.3724 | 63.3724 | 63.3724 | 63.3724 | 63.3724 | 63.3724 | 63.3724 | 63.3724 | 63.3724 | 63.3724 | 63.3724 | 63.3724 | 63.3724
Cost of EUE ($) - Option 6 | 88249.2162 | 154837.3319 | 181337.4266 | 217630.6447 | 246518.0678 | 285145.927 | 366215.4289 | 653795.436 | 899769.3066 | 790911.764 | 1476011.1922 | 1540765.1766 | 1840251.2779 | 2511133.3647 | 2691195.0652 | 2698414.6144 | 2698414.6144 | 2698414.6144 | 2698414.6144 | 2698414.6144 | 2698414.6144 | 2698414.6144 | 2698414.6144 | 2698414.6144 | 2698414.6144 | 2698414.6144 | 2698414.6144 | 2698414.6144 | 2698414.6144 | 2698414.6144
Option 7 - | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Weighted Energy @ Risk (MWh) under N Conditions | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Weighted Energy @ Risk (MWh) under N-1 Conditions | 0.099581 | 0.78098 | 1.0023 | 1.4061 | 1.6028 | 1.9694 | 3.0951 | 8.3833 | 12.9562 | 10.037 | 24.0182 | 24.4461 | 30.0831 | 43.8321 | 46.6677 | 46.7869 | 46.7869 | 46.7869 | 46.7869 | 46.7869 | 46.7869 | 46.7869 | 46.7869 | 46.7869 | 46.7869 | 46.7869 | 46.7869 | 46.7869 | 46.7869 | 46.7869
Weighted Energy @ Risk (MWh) under N-2 Conditions | 1.973 | 2.8554 | 3.2564 | 3.705 | 4.1867 | 4.7273 | 5.5055 | 6.9711 | 8.1749 | 8.5377 | 10.646 | 11.7388 | 13.1353 | 15.142 | 16.5352 | 16.5855 | 16.5855 | 16.5855 | 16.5855 | 16.5855 | 16.5855 | 16.5855 | 16.5855 | 16.5855 | 16.5855 | 16.5855 | 16.5855 | 16.5855 | 16.5855 | 16.5855
Total EUE (MWh) - Option 7 | 2.0725 | 3.6364 | 4.2587 | 5.1111 | 5.7895 | 6.6967 | 8.6006 | 15.3544 | 21.1311 | 18.5746 | 34.6642 | 36.1849 | 43.2184 | 58.9741 | 63.2029 | 63.3724 | 63.3724 | 63.3724 | 63.3724 | 63.3724 | 63.3724 | 63.3724 | 63.3724 | 63.3724 | 63.3724 | 63.3724 | 63.3724 | 63.3724 | 63.3724 | 63.3724
Cost of EUE ($) - Option 7 | 88249.2162 | 154837.3319 | 181337.4266 | 217630.6447 | 246518.0678 | 285145.927 | 366215.4289 | 653795.436 | 899769.3066 | 790911.764 | 1476011.1922 | 1540765.1766 | 1840251.2779 | 2511133.3647 | 2691195.0652 | 2698414.6144 | 2698414.6144 | 2698414.6144 | 2698414.6144 | 2698414.6144 | 2698414.6144 | 2698414.6144 | 2698414.6144 | 2698414.6144 | 2698414.6144 | 2698414.6144 | 2698414.6144 | 2698414.6144 | 2698414.6144 | 2698414.6144
Option 8 - | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Weighted Energy @ Risk (MWh) under N Conditions | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Weighted Energy @ Risk (MWh) under N-1 Conditions | 0.099581 | 0.78098 | 1.0023 | 1.4061 | 1.6028 | 1.9694 | 3.0951 | 8.3833 | 12.9562 | 10.037 | 24.0182 | 24.4461 | 30.0831 | 43.8321 | 46.6677 | 46.7869 | 46.7869 | 46.7869 | 46.7869 | 46.7869 | 46.7869 | 46.7869 | 46.7869 | 46.7869 | 46.7869 | 46.7869 | 46.7869 | 46.7869 | 46.7869 | 46.7869
Weighted Energy @ Risk (MWh) under N-2 Conditions | 1.973 | 2.8554 | 3.2564 | 3.705 | 4.1867 | 4.7273 | 5.5055 | 6.9711 | 8.1749 | 8.5377 | 10.646 | 11.7388 | 13.1353 | 15.142 | 16.5352 | 16.5855 | 16.5855 | 16.5855 | 16.5855 | 16.5855 | 16.5855 | 16.5855 | 16.5855 | 16.5855 | 16.5855 | 16.5855 | 16.5855 | 16.5855 | 16.5855 | 16.5855
Total EUE (MWh) - Option 8 | 2.0725 | 3.6364 | 4.2587 | 5.1111 | 5.7895 | 6.6967 | 8.6006 | 15.3544 | 21.1311 | 18.5746 | 34.6642 | 36.1849 | 43.2184 | 58.9741 | 63.2029 | 63.3724 | 63.3724 | 63.3724 | 63.3724 | 63.3724 | 63.3724 | 63.3724 | 63.3724 | 63.3724 | 63.3724 | 63.3724 | 63.3724 | 63.3724 | 63.3724 | 63.3724
Cost of EUE ($) - Option 8 | 88249.2162 | 154837.3319 | 181337.4266 | 217630.6447 | 246518.0678 | 285145.927 | 366215.4289 | 653795.436 | 899769.3066 | 790911.764 | 1476011.1922 | 1540765.1766 | 1840251.2779 | 2511133.3647 | 2691195.0652 | 2698414.6144 | 2698414.6144 | 2698414.6144 | 2698414.6144 | 2698414.6144 | 2698414.6144 | 2698414.6144 | 2698414.6144 | 2698414.6144 | 2698414.6144 | 2698414.6144 | 2698414.6144 | 2698414.6144 | 2698414.6144 | 2698414.6144