## Lists
yes/No List
Yes
No

## Intro
Navigation Dashboard
| Model Overview |  | Description
|  | 0.1 Model Steps | Overview of the NPV modelling process.
|  | 0.2 QA | Automated quality assurance checks.
Output
|  | 1.1 BC Summary | Business Case summary of NPV analysis, including the ranking of assessed options and optimal commissioning timing based on NPV.
Inputs
|  | 2.1 KMA | Key model inputs and assumptions.
|  | 2.2.1 Supply Risk $ Base Demand | Collects the Supply Risk or Value of EUE (in $) calculated in linked Energy at Risk calculators.
|  | 2.2.2 Supply Risk $ Low Demand | Collects the Supply Risk or Value of EUE (in $) calculated in linked Energy at Risk calculators for the Low Demand sensitivity.
|  | 2.2.3 Supply Risk $ High Demand | Collects the Supply Risk or Value of EUE (in $) calculated in linked Energy at Risk calculators for the High Demand sensitivity.
|  | 2.2.4 Supply Risk $ Low PoF | Collects the Supply Risk or Value of EUE (in $) calculated in linked Energy at Risk calculators for the Low Transformer Probability of Failure sensitivity.
|  | 2.2.5 Supply Risk $ High PoF | Collects the Supply Risk or Value of EUE (in $) calculated in linked Energy at Risk calculators for the High Transformer Probability of Failure sensitivity.
|  | 2.3.1 Cost Summary | Collects costs from cost sheets and converts estimates to $2024.
|  | 2.3.2 Option 2 Cost | Cost estimate of Option 2.
|  | 2.3.3 Option 3 Cost | Cost estimate of Option 3.
|  | 2.3.4 Option 4 Cost | Cost estimate of Option 4.
|  | 2.3.5 Option 5 Cost | Cost estimate of Option 5.
|  | 2.3.6 Option 6 Cost | Cost estimate of Option 6.
|  | 2.3.7 Option 7 Cost | Cost estimate of Option 7.
|  | 2.3.8 Option 8 Cost | Cost estimate of Option 8.
|  | 2.3.9 Option 9 Cost | Cost estimate of Option 9.
|  | 2.3.10 Option 10 Cost | Cost estimate of Option 10.
Analysis & NPV Calculations
|  | 3.1 NPV | NPV calculator using central/base case assumptions.
|  | 3.2.1 NPV (LoDiscount) | NPV calculator using a lower discount rate.
|  | 3.2.2 NPV (HiDiscount) | NPV calculator using a higher discount rate.
|  | 3.2.3 NPV (LoCost) | NPV calculator using lower capital cost.
|  | 3.2.4 NPV (HiCost) | NPV calculator using higher capital cost.
|  | 3.2.5 NPV (Low Demand) | NPV calculator using a lower demand forecast
|  | 3.2.6 NPV (High Demand) | NPV calculator using a higher demand forecast
|  | 3.2.7 NPV (Low VCR) | NPV calculator using a lower VCR.
|  | 3.2.8 NPV (High VCR) | NPV calculator using a higher VCR.
|  | 3.2.9 NPV (Low PoF's) | NPV calculator using a lower PoF.
|  | 3.2.10 NPV (High PoF's) | NPV calculator using a higher PoF.
|  | 3.3 Adjustments | Post modelling adjustments
Glossary
| Term | Full Form | Description | Where Used in Model
| NPV | Net Present Value | A financial metric that calculates the present value of future cash flows minus initial investment. | 3.x NPV sheets, 1.1 BC Summary
| VCR | Value of Customer Reliability | Represents the cost of electricity outages per customer, used to quantify reliability benefits. | 2.1 KMA, 3.2.x Sensitivity tabs
| PoF | Probability of Failure | Likelihood that an asset will fail within a given time period. | 2.1 KMA, 3.2.x Sensitivity tabs
| EaR | Energy at Risk | Expected unserved energy due to network constraints or asset failure. | 2.2.x Supply Risk tabs
| WACC | Weighted Average Cost of Capital | The average rate of return a company is expected to pay its investors; used as discount rate. | 2.1 KMA
| Capex | Capital Expenditure | Funds used by a company to acquire or upgrade physical assets such as equipment or infrastructure. | 2.3.x Cost Summary, 3.x NPV sheets
| Opex | Operational Expenditure | Ongoing costs for running a product, business, or system. | 2.3.x Cost Summary, 3.x NPV sheets
| Sensitivity Analysis | Sensitivity Analysis | Technique used to determine how different values of an input affect a particular output under a given set of assumptions. | 3.2.x Sensitivity tabs
| Discount Rate (WACC) | Discount Rate | Rate used to discount future cash flows to their present value. | 2.1 KMA, 3.x NPV sheets
| Business Case | Business Case | A justification for a proposed project or investment, including benefits, costs, and risks. | Info tab, 1.1 BC Summary
| Optimal Timing | Optimal Timing | Optimal timing of the preferred project option, which is the year the annual benefits exceed the annual costs. | 1.1 BC Summary
External Links
Main External Files
EaR_Augment East Gippsland 66kV Loop (MWTS-TGN-MFA lines)_summary.xlsx
Variants for Sensitivities
Other External Reference
CSIRO GenCost 2024-25 PDF (linked in Inputs tab for cost assumptions).

## Change Log
Revision Table
Date | Editted by | Comment
2025-09-03 | BO | Draft version for circulation
2025-09-23 | HT | Added additional options
2025-09-30 | HT | Added Demand Sensitivities
2025-10-09 | BO / HT | Updated info page; added modelling process diagram and QA checks
2025-10-28 | HT | Updated Info page , Added VCR & Pof Sensitivities

## 0.1 Model Steps
|  |  | Asset EaR Inputs | Data Inputs |  | Calculations |  |  |  | Outputs
Eq1. Annual Risk Reducion Benefit
MWTS East 66kV Loop (W Fulham BESS)
Eq2. Annulised CAPEX |  |  | N/A
[5 empty] | BAU / Do Nothing Supply Risk $M |  | Eq1.
| Using the PMT function in excel |  | N/A
Annual Risk Reduction Benfit $M
Eq3. Opex
|  |  | N/A | [5 empty] | Eq5. & Eq6.
Option Supply Risk $M (after augmentation)
Eq4. Annual Total Cost | [8 empty] | Net Present Value & Optimal Timing | Outputs / BC Summaries
N/A
Eq3.
Eq5. Net Present Value Benefits & Optimal Timing = (Annual risk reduction benfit > annual cost) |  |  | N/A
Opex
Eq6. NPV calculated with Capex one year before optimal timing; Benefits and Opex start one year after. |  |  | N/A |  |  |  |  | Eq4.
|  | Using the NPV formula in excel |  |  | Option Cost Estimates |  |  | Annualised Total Cost
N/A
Eq2.
|  |  | N/A |  |  |  | Annualised Capex
WACC
N/A

## 0.2 QA
Overall Status
Good
Number | Check Name | Status | Info |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1 | Benefits start | Good | Confirm benefits only start after the Capex investment is completed and commissioned | Input costs check | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2 | Opex start | Good | Confirm Opex only starts after the Capex investment is completed and commissioned | Benfits checks | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | Risk assessment period | Good | Confirm BAU / Do Nothing Supply Risk or Option Risk Reduction Benefit is capped at 15 years

## 1.1 BC Summary
Outputs for executive summary
Include in Assesment | Option | Description | PV benefits | PV costs | NPV | Rank Input | Optimal year | [26 empty] | Yes
No
Yes | 1 | Do Nothing | 0 | 0 | 0 | 5
Yes | 2 | Augment MWTS-TGN with 19/4.75 AAC + Augment TGN-MFA with 19/4.75 AAC | 281.4667 | 36.9045 | 244.5622 | 1 | FY30
Yes | 3 | Augment MWTS-TGN with 19/4.75 AAC + New TGN-SLE 66kV line with 19/4.75 AAC | 276.2428 | 56.785 | 219.4578 | 3 | FY31
Yes | 4 | Augment MWTS-TGN with 19/4.75 AAC + New Switching Station at Winnindoo (WISS) + Augment TGN-WISS wit | 280.8724 | 50.3756 | 230.4968 | 2 | FY31
Yes | 5 | Augment MWTS-TGN with 19/4.75 AAC + construct 30MW/150MWh BESS at BDSS | 301.4266 | 83.9403 | 217.4863 | 4 | FY33
No | 6 | [5 empty] | -
0 | 7 | [5 empty] | -
0 | 8 | [5 empty] | -
0 | 9 | [5 empty] | -
0 | 10 | [5 empty] | -
Optimal Timing
| Option 1 | Do Nothing
|  |  |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
|  | Undiscounted | EUE Value ($m, real $2024) | 1.1137 | 2.6361 | 4.8351 | 2.3613 | 2.5897 | 2.9899 | 4.739 | 7.1467 | 11.4165 | 12.1547 | 21.27 | 23.3412 | 28.4421 | 53.1535 | 43.3219 | 43.3219 | 43.3219 | 43.3219 | 43.3219 | 43.3219 | 43.3219 | 43.3219 | 43.3219 | 43.3219 | 43.3219 | 43.3219 | 43.3219 | 43.3219 | 43.3219 | 43.3219
| Option 2 | Augment MWTS-TGN with 19/4.75 AAC + Augment TGN-MFA with 19/4.75 AAC
|  |  |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
|  | Undiscounted | EUE Value ($m, real $2024) | 1.1137 | 2.6361 | 4.8351 | 0.037438 | 0.05616 | 0.087536 | 0.15929 | 0.24956 | 0.53594 | 0.61292 | 1.6853 | 1.3511 | 2.5671 | 7.3917 | 5.0403 | 5.0403 | 5.0403 | 5.0403 | 5.0403 | 5.0403 | 5.0403 | 5.0403 | 5.0403 | 5.0403 | 5.0403 | 5.0403 | 5.0403 | 5.0403 | 5.0403 | 5.0403
|  |  | $m, real $2024 | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
|  | Undiscounted | Capex | 0 | 0 | 40.4306 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Undiscounted | Opex | 0 | 0 | 0 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431
|  | Undiscounted | Total costs | 0 | 0 | 40.4306 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431
|  |  | $m, real $2024 | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
|  | Undiscounted | Benefits (reduction in EUE relative to Option 0) | 0 | 0 | 0 | 2.3239 | 2.5336 | 2.9024 | 4.5797 | 6.8971 | 10.8805 | 11.5418 | 19.5847 | 21.9902 | 25.875 | 45.7618 | 38.2817 | 38.2817 | 38.2817 | 38.2817 | 38.2817 | 38.2817 | 38.2817 | 38.2817 | 38.2817 | 38.2817 | 38.2817 | 38.2817 | 38.2817 | 38.2817 | 38.2817 | 38.2817
|  |  | Optimal Timing | FY25: FY30
FY31
FY31
|  |  | Option 2 | FY25: FY31
| Option 3 | Augment MWTS-TGN with 19/4.75 AAC + New TGN-SLE 66kV line with 19/4.75 AAC
|  |  |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
|  | Undiscounted | EUE Value ($m, real $2024) | 1.1137 | 2.6361 | 4.8351 | 0.0060347 | 0.0079976 | 0.013061 | 0.030296 | 0.09615 | 0.43224 | 0.53044 | 1.7172 | 1.3408 | 2.9132 | 7.8574 | 5.603 | 5.603 | 5.603 | 5.603 | 5.603 | 5.603 | 5.603 | 5.603 | 5.603 | 5.603 | 5.603 | 5.603 | 5.603 | 5.603 | 5.603 | 5.603
|  |  | $m, real $2024 | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
|  | Undiscounted | Capex | 0 | 0 | 65.8197 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Undiscounted | Opex | 0 | 0 | 0 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582
|  | Undiscounted | Total costs | 0 | 0 | 65.8197 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582
|  |  | $m, real $2024 | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
|  | Undiscounted | Benefits (reduction in EUE relative to Option 0) | 0 | 0 | 0 | 2.3553 | 2.5817 | 2.9769 | 4.7087 | 7.0505 | 10.9843 | 11.6243 | 19.5528 | 22.0004 | 25.5289 | 45.2961 | 37.7189 | 37.7189 | 37.7189 | 37.7189 | 37.7189 | 37.7189 | 37.7189 | 37.7189 | 37.7189 | 37.7189 | 37.7189 | 37.7189 | 37.7189 | 37.7189 | 37.7189 | 37.7189
|  |  | Optimal Timing | FY25: FY31
FY30
FY30
|  |  | Option 3 | FY25: FY30
| Option 4 | Augment MWTS-TGN with 19/4.75 AAC + New Switching Station at Winnindoo (WISS) + Augment TGN-WISS wit
|  |  |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
|  | Undiscounted | EUE Value ($m, real $2024) | 1.1137 | 2.6361 | 4.8351 | 0.011211 | 0.013463 | 0.019408 | 0.039024 | 0.092869 | 0.36202 | 0.4436 | 1.4872 | 1.1652 | 2.4614 | 7.0261 | 4.8938 | 4.8938 | 4.8938 | 4.8938 | 4.8938 | 4.8938 | 4.8938 | 4.8938 | 4.8938 | 4.8938 | 4.8938 | 4.8938 | 4.8938 | 4.8938 | 4.8938 | 4.8938
|  |  | $m, real $2024 | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
|  | Undiscounted | Capex | 0 | 0 | 58.3905 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Undiscounted | Opex | 0 | 0 | 0 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839
|  | Undiscounted | Total costs | 0 | 0 | 58.3905 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839
|  |  | $m, real $2024 | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
|  | Undiscounted | Benefits (reduction in EUE relative to Option 0) | 0 | 0 | 0 | 2.3501 | 2.5763 | 2.9705 | 4.6999 | 7.0538 | 11.0545 | 11.7111 | 19.7828 | 22.176 | 25.9808 | 46.1274 | 38.4281 | 38.4281 | 38.4281 | 38.4281 | 38.4281 | 38.4281 | 38.4281 | 38.4281 | 38.4281 | 38.4281 | 38.4281 | 38.4281 | 38.4281 | 38.4281 | 38.4281 | 38.4281
|  |  | Optimal Timing | FY25: FY31
FY33
FY33
|  |  | Option 4 | FY25: FY33
| Option 5 | Augment MWTS-TGN with 19/4.75 AAC + construct 30MW/150MWh BESS at BDSS
|  |  |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
|  | Undiscounted | EUE Value ($m, real $2024) | 1.1137 | 2.6361 | 4.8351 | 0.01758 | 0.022594 | 0.033687 | 0.065859 | 0.10345 | 0.16921 | 0.18013 | 0.24965 | 0.24546 | 0.31 | 0.50155 | 0.44973 | 0.44973 | 0.44973 | 0.44973 | 0.44973 | 0.44973 | 0.44973 | 0.44973 | 0.44973 | 0.44973 | 0.44973 | 0.44973 | 0.44973 | 0.44973 | 0.44973 | 0.44973
|  |  | $m, real $2024 | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
|  | Undiscounted | Capex | 0 | 0 | 78.12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78.12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Undiscounted | Opex | 0 | 0 | 0 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812
|  | Undiscounted | Total costs | 0 | 0 | 78.12 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 78.9012 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812
|  |  | $m, real $2024 | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
|  | Undiscounted | Benefits (reduction in EUE relative to Option 0) | 0 | 0 | 0 | 2.3437 | 2.5671 | 2.9562 | 4.6731 | 7.0432 | 11.2473 | 11.9746 | 21.0204 | 23.0958 | 28.1321 | 52.6519 | 42.8722 | 42.8722 | 42.8722 | 42.8722 | 42.8722 | 42.8722 | 42.8722 | 42.8722 | 42.8722 | 42.8722 | 42.8722 | 42.8722 | 42.8722 | 42.8722 | 42.8722 | 42.8722
|  |  | Optimal Timing | FY25: FY33
-
-
Option 5 | bar: FY25
Option 6
|  |  |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
|  | Undiscounted | EUE Value ($m, real $2024) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | $m, real $2024 | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
|  | Undiscounted | Capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Undiscounted | Opex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Undiscounted | Total costs | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | $m, real $2024 | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
|  | Undiscounted | Benefits (reduction in EUE relative to Option 0) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Optimal Timing | bar: FY25
FY33
FY33
|  |  | Option 6 | FY25: FY33
Option 7
|  |  |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
|  | Undiscounted | EUE Value ($m, real $2024) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | $m, real $2024 | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
|  | Undiscounted | Capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Undiscounted | Opex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Undiscounted | Total costs | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | $m, real $2024 | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
|  | Undiscounted | Benefits (reduction in EUE relative to Option 0) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Optimal Timing | bar: FY25
-
-
Option 7 | bar: FY25
Option 8
|  |  |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
|  | Undiscounted | EUE Value ($m, real $2024) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | $m, real $2024 | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
|  | Undiscounted | Capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Undiscounted | Opex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Undiscounted | Total costs | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | $m, real $2024 | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
|  | Undiscounted | Benefits (reduction in EUE relative to Option 0) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Optimal Timing | bar: FY25
-
-
Option 8 | bar: FY25
Option 9
|  |  |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
|  | Undiscounted | EUE Value ($m, real $2024) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | $m, real $2024 | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
|  | Undiscounted | Capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Undiscounted | Opex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Undiscounted | Total costs | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | $m, real $2024 | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
|  | Undiscounted | Benefits (reduction in EUE relative to Option 0) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Optimal Timing | bar: FY25
-
-
Option 9 | bar: FY25
Option 10
|  |  |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
|  | Undiscounted | EUE Value ($m, real $2024) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | $m, real $2024 | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
|  | Undiscounted | Capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Undiscounted | Opex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Undiscounted | Total costs | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | $m, real $2024 | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
|  | Undiscounted | Benefits (reduction in EUE relative to Option 0) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Optimal Timing | bar: FY25
-
-
Option 10 | bar: FY25
NPV Analysis
| Option 1 | Do Nothing
|  |  |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
|  | Undiscounted | EUE Value ($m, real $2024) | 1.1137 | 2.6361 | 4.8351 | 2.3613 | 2.5897 | 2.9899 | 4.739 | 7.1467 | 11.4165 | 12.1547 | 21.27 | 23.3412 | 28.4421 | 53.1535 | 43.3219 | 43.3219 | 43.3219 | 43.3219 | 43.3219 | 43.3219 | 43.3219 | 43.3219 | 43.3219 | 43.3219 | 43.3219 | 43.3219 | 43.3219 | 43.3219 | 43.3219 | 43.3219
| Option 2 | Augment MWTS-TGN with 19/4.75 AAC + Augment TGN-MFA with 19/4.75 AAC
|  |  | $m, real $2024 | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
|  | Undiscounted | Capex | 0 | 0 | 0 | 0 | 40.4306 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Undiscounted | Opex | 0 | 0 | 0 | 0 | 0 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431
|  | Undiscounted | Total costs | 0 | 0 | 0 | 0 | 40.4306 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431
|  |  | $m, real $2024 | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
|  | Undiscounted | Benefits (reduction in EUE relative to Option 0) | 0 | 0 | 0 | 0 | 0 | 2.9024 | 4.5797 | 6.8971 | 10.8805 | 11.5418 | 19.5847 | 21.9902 | 25.875 | 45.7618 | 38.2817 | 38.2817 | 38.2817 | 38.2817 | 38.2817 | 38.2817 | 38.2817 | 38.2817 | 38.2817 | 38.2817 | 38.2817 | 38.2817 | 38.2817 | 38.2817 | 38.2817 | 38.2817
|  |  | ($m, real $2024) | FY25: Undiscounted; FY28: Discounted
|  |  |  | Benefits | Costs | Net benefits | PV benefits | PV costs | NPV
|  |  | Option 2 | FY25: 762.5197; FY26: 50.5382; FY27: 711.9815; FY28: 281.4667; FY29: 36.9045; FY30: 244.5622
| Option 3 | Augment MWTS-TGN with 19/4.75 AAC + New TGN-SLE 66kV line with 19/4.75 AAC
|  |  | $m, real $2024 | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
|  | Undiscounted | Capex | 0 | 0 | 0 | 0 | 0 | 65.8197 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Undiscounted | Opex | 0 | 0 | 0 | 0 | 0 | 0 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582
|  | Undiscounted | Total costs | 0 | 0 | 0 | 0 | 0 | 65.8197 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582
|  |  | $m, real $2024 | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
|  | Undiscounted | Benefits (reduction in EUE relative to Option 0) | 0 | 0 | 0 | 0 | 0 | 0 | 4.7087 | 7.0505 | 10.9843 | 11.6243 | 19.5528 | 22.0004 | 25.5289 | 45.2961 | 37.7189 | 37.7189 | 37.7189 | 37.7189 | 37.7189 | 37.7189 | 37.7189 | 37.7189 | 37.7189 | 37.7189 | 37.7189 | 37.7189 | 37.7189 | 37.7189 | 37.7189 | 37.7189
|  |  | ($m, real $2024) | FY25: Undiscounted; FY28: Discounted
|  |  |  | Benefits | Costs | Net benefits | PV benefits | PV costs | NPV
|  |  | Option 3 | FY25: 750.2485; FY26: 81.6164; FY27: 668.6321; FY28: 276.2428; FY29: 56.785; FY30: 219.4578
| Option 4 | Augment MWTS-TGN with 19/4.75 AAC + New Switching Station at Winnindoo (WISS) + Augment TGN-WISS wit
|  |  | $m, real $2024 | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
|  | Undiscounted | Capex | 0 | 0 | 0 | 0 | 0 | 58.3905 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Undiscounted | Opex | 0 | 0 | 0 | 0 | 0 | 0 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839
|  | Undiscounted | Total costs | 0 | 0 | 0 | 0 | 0 | 58.3905 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839
|  |  | $m, real $2024 | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
|  | Undiscounted | Benefits (reduction in EUE relative to Option 0) | 0 | 0 | 0 | 0 | 0 | 0 | 4.6999 | 7.0538 | 11.0545 | 11.7111 | 19.7828 | 22.176 | 25.9808 | 46.1274 | 38.4281 | 38.4281 | 38.4281 | 38.4281 | 38.4281 | 38.4281 | 38.4281 | 38.4281 | 38.4281 | 38.4281 | 38.4281 | 38.4281 | 38.4281 | 38.4281 | 38.4281 | 38.4281
|  |  | ($m, real $2024) | FY25: Undiscounted; FY28: Discounted
|  |  |  | Benefits | Costs | Net benefits | PV benefits | PV costs | NPV
|  |  | Option 4 | FY25: 763.4361; FY26: 72.4042; FY27: 691.0319; FY28: 280.8724; FY29: 50.3756; FY30: 230.4968
| Option 5 | Augment MWTS-TGN with 19/4.75 AAC + construct 30MW/150MWh BESS at BDSS
|  |  | $m, real $2024 | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
|  | Undiscounted | Capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78.12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78.12 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Undiscounted | Opex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812
|  | Undiscounted | Total costs | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78.12 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 78.9012 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812
|  |  | $m, real $2024 | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
|  | Undiscounted | Benefits (reduction in EUE relative to Option 0) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11.2473 | 11.9746 | 21.0204 | 23.0958 | 28.1321 | 52.6519 | 42.8722 | 42.8722 | 42.8722 | 42.8722 | 42.8722 | 42.8722 | 42.8722 | 42.8722 | 42.8722 | 42.8722 | 42.8722 | 42.8722 | 42.8722 | 42.8722 | 42.8722 | 42.8722
|  |  | ($m, real $2024) | FY25: Undiscounted; FY28: Discounted
|  |  |  | Benefits | Costs | Net benefits | PV benefits | PV costs | NPV
|  |  | Option 5 | FY25: 834.0772; FY26: 173.4265; FY27: 660.6507; FY28: 301.4266; FY29: 83.9403; FY30: 217.4863
Option 6
|  |  | $m, real $2024 | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
|  | Undiscounted | Capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Undiscounted | Opex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Undiscounted | Total costs | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | $m, real $2024 | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
|  | Undiscounted | Benefits (reduction in EUE relative to Option 0) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | ($m, real $2024) | FY25: Undiscounted; FY28: Discounted
|  |  |  | Benefits | Costs | Net benefits | PV benefits | PV costs | NPV
|  |  | Option 6 | FY25: 0; FY26: 0; FY27: 0
Option 7
|  |  | $m, real $2024 | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
|  | Undiscounted | Capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Undiscounted | Opex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Undiscounted | Total costs | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | $m, real $2024 | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
|  | Undiscounted | Benefits (reduction in EUE relative to Option 0) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | ($m, real $2024) | FY25: Undiscounted; FY28: Discounted
|  |  |  | Benefits | Costs | Net benefits | PV benefits | PV costs | NPV
|  |  | Option 7 | FY25: 0; FY26: 0; FY27: 0
Option 8
|  |  | $m, real $2024 | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
|  | Undiscounted | Capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Undiscounted | Opex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Undiscounted | Total costs | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | $m, real $2024 | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
|  | Undiscounted | Benefits (reduction in EUE relative to Option 0) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | ($m, real $2024) | FY25: Undiscounted; FY28: Discounted
|  |  |  | Benefits | Costs | Net benefits | PV benefits | PV costs | NPV
|  |  | Option 8 | FY25: 0; FY26: 0; FY27: 0
Option 9
|  |  | $m, real $2024 | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
|  | Undiscounted | Capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Undiscounted | Opex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Undiscounted | Total costs | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | $m, real $2024 | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
|  | Undiscounted | Benefits (reduction in EUE relative to Option 0) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | ($m, real $2024) | FY25: Undiscounted; FY28: Discounted
|  |  |  | Benefits | Costs | Net benefits | PV benefits | PV costs | NPV
|  |  | Option 9 | FY25: 0; FY26: 0; FY27: 0
Option 10
|  |  | $m, real $2024 | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
|  | Undiscounted | Capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Undiscounted | Opex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Undiscounted | Total costs | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | $m, real $2024 | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
|  | Undiscounted | Benefits (reduction in EUE relative to Option 0) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | ($m, real $2024) | FY25: Undiscounted; FY28: Discounted
|  |  |  | Benefits | Costs | Net benefits | PV benefits | PV costs | NPV
|  |  | Option 10 | FY25: 0; FY26: 0; FY27: 0
Sensitivity analysis
| Option | Description | PV benefits | FY25: PV Cost; FY26: NPV; FY27: Rank; FY28: Optimal timing
Central | 1 | Do Nothing | 0 | FY25: 0; FY26: 0; FY27: 5
| 2 | Augment MWTS-TGN with 19/4.75 AAC + Augment TGN-MFA with 19/4.75 AAC | 281.4667 | FY25: 36.9045; FY26: 244.5622; FY27: 1; FY28: FY30
| 3 | Augment MWTS-TGN with 19/4.75 AAC + New TGN-SLE 66kV line with 19/4.75 AAC | 276.2428 | FY25: 56.785; FY26: 219.4578; FY27: 3; FY28: FY31
| 4 | Augment MWTS-TGN with 19/4.75 AAC + New Switching Station at Winnindoo (WISS) + Augment TGN-WISS wit | 280.8724 | FY25: 50.3756; FY26: 230.4968; FY27: 2; FY28: FY31
| 5 | Augment MWTS-TGN with 19/4.75 AAC + construct 30MW/150MWh BESS at BDSS | 301.4266 | FY25: 83.9403; FY26: 217.4863; FY27: 4; FY28: FY33
| 6 |  | 0 | FY25: 0; FY26: 0; FY27: 5; FY28: -
| 7 |  | 0 | FY25: 0; FY26: 0; FY27: 5; FY28: -
| 8 |  | 0 | FY25: 0; FY26: 0; FY27: 5; FY28: -
| 9 |  | 0 | FY25: 0; FY26: 0; FY27: 5; FY28: -
| 10 |  | 0 | FY25: 0; FY26: 0; FY27: 5; FY28: -
Lower discount rate | 1 | Do Nothing | 0 | FY25: 0; FY26: 0; FY27: 5
| 2 | Augment MWTS-TGN with 19/4.75 AAC + Augment TGN-MFA with 19/4.75 AAC | 359.4744 | FY25: 39.7287; FY26: 319.7457; FY27: 1; FY28: FY30
| 3 | Augment MWTS-TGN with 19/4.75 AAC + New TGN-SLE 66kV line with 19/4.75 AAC | 353.0938 | FY25: 61.9271; FY26: 291.1667; FY27: 3; FY28: FY31
| 4 | Augment MWTS-TGN with 19/4.75 AAC + New Switching Station at Winnindoo (WISS) + Augment TGN-WISS wit | 359.0941 | FY25: 54.9373; FY26: 304.1568; FY27: 2; FY28: FY31
| 5 | Augment MWTS-TGN with 19/4.75 AAC + construct 30MW/150MWh BESS at BDSS | 379.2941 | FY25: 95.3956; FY26: 283.8985; FY27: 4; FY28: FY34
| 6 |  | 0 | FY25: 0; FY26: 0; FY27: 5; FY28: -
| 7 |  | 0 | FY25: 0; FY26: 0; FY27: 5; FY28: -
| 8 |  | 0 | FY25: 0; FY26: 0; FY27: 5; FY28: -
| 9 |  | 0 | FY25: 0; FY26: 0; FY27: 5; FY28: -
| 10 |  | 0 | FY25: 0; FY26: 0; FY27: 5; FY28: -
Higher discount rate | 1 | Do Nothing | 0 | FY25: 0; FY26: 0; FY27: 5
| 2 | Augment MWTS-TGN with 19/4.75 AAC + Augment TGN-MFA with 19/4.75 AAC | 222.9733 | FY25: 34.4388; FY26: 188.5345; FY27: 1; FY28: FY30
| 3 | Augment MWTS-TGN with 19/4.75 AAC + New TGN-SLE 66kV line with 19/4.75 AAC | 218.6264 | FY25: 52.3109; FY26: 166.3154; FY27: 3; FY28: FY31
| 4 | Augment MWTS-TGN with 19/4.75 AAC + New Switching Station at Winnindoo (WISS) + Augment TGN-WISS wit | 222.2367 | FY25: 46.4065; FY26: 175.8302; FY27: 2; FY28: FY31
| 5 | Augment MWTS-TGN with 19/4.75 AAC + construct 30MW/150MWh BESS at BDSS | 237.1174 | FY25: 71.6632; FY26: 165.4543; FY27: 4; FY28: FY33
| 6 |  | 0 | FY25: 0; FY26: 0; FY27: 5; FY28: -
| 7 |  | 0 | FY25: 0; FY26: 0; FY27: 5; FY28: -
| 8 |  | 0 | FY25: 0; FY26: 0; FY27: 5; FY28: -
| 9 |  | 0 | FY25: 0; FY26: 0; FY27: 5; FY28: -
| 10 |  | 0 | FY25: 0; FY26: 0; FY27: 5; FY28: -
Lower cost | 1 | Do Nothing | 0 | FY25: 0; FY26: 0; FY27: 5
| 2 | Augment MWTS-TGN with 19/4.75 AAC + Augment TGN-MFA with 19/4.75 AAC | 285.4829 | FY25: 33.0363; FY26: 252.4466; FY27: 1; FY28: FY28
| 3 | Augment MWTS-TGN with 19/4.75 AAC + New TGN-SLE 66kV line with 19/4.75 AAC | 276.2428 | FY25: 45.428; FY26: 230.8148; FY27: 4; FY28: FY31
| 4 | Augment MWTS-TGN with 19/4.75 AAC + New Switching Station at Winnindoo (WISS) + Augment TGN-WISS wit | 280.8724 | FY25: 40.3005; FY26: 240.572; FY27: 2; FY28: FY31
| 5 | Augment MWTS-TGN with 19/4.75 AAC + construct 30MW/150MWh BESS at BDSS | 301.4266 | FY25: 67.1522; FY26: 234.2743; FY27: 3; FY28: FY33
| 6 |  | 0 | FY25: 0; FY26: 0; FY27: 5; FY28: -
| 7 |  | 0 | FY25: 0; FY26: 0; FY27: 5; FY28: -
| 8 |  | 0 | FY25: 0; FY26: 0; FY27: 5; FY28: -
| 9 |  | 0 | FY25: 0; FY26: 0; FY27: 5; FY28: -
| 10 |  | 0 | FY25: 0; FY26: 0; FY27: 5; FY28: -
Higher cost | 1 | Do Nothing | 0 | FY25: 0; FY26: 0; FY27: 5
| 2 | Augment MWTS-TGN with 19/4.75 AAC + Augment TGN-MFA with 19/4.75 AAC | 279.2523 | FY25: 41.8571; FY26: 237.3952; FY27: 1; FY28: FY31
| 3 | Augment MWTS-TGN with 19/4.75 AAC + New TGN-SLE 66kV line with 19/4.75 AAC | 272.8395 | FY25: 64.3971; FY26: 208.4424; FY27: 3; FY28: FY32
| 4 | Augment MWTS-TGN with 19/4.75 AAC + New Switching Station at Winnindoo (WISS) + Augment TGN-WISS wit | 280.8724 | FY25: 60.4507; FY26: 220.4217; FY27: 2; FY28: FY31
| 5 | Augment MWTS-TGN with 19/4.75 AAC + construct 30MW/150MWh BESS at BDSS | 286.773 | FY25: 90.0367; FY26: 196.7363; FY27: 4; FY28: FY35
| 6 |  | 0 | FY25: 0; FY26: 0; FY27: 5; FY28: -
| 7 |  | 0 | FY25: 0; FY26: 0; FY27: 5; FY28: -
| 8 |  | 0 | FY25: 0; FY26: 0; FY27: 5; FY28: -
| 9 |  | 0 | FY25: 0; FY26: 0; FY27: 5; FY28: -
| 10 |  | 0 | FY25: 0; FY26: 0; FY27: 5; FY28: -
Low Demand | 1 | Do Nothing | 0 | FY25: 0; FY26: 0; FY27: 2
| 2 | Augment MWTS-TGN with 19/4.75 AAC + Augment TGN-MFA with 19/4.75 AAC | 27.1175 | FY25: 26.2539; FY26: 0.86355; FY27: 1; FY28: FY36
| 3 | Augment MWTS-TGN with 19/4.75 AAC + New TGN-SLE 66kV line with 19/4.75 AAC | 24.9857 | FY25: 38.1039; FY26: -13.1182; FY27: 10; FY28: FY38
| 4 | Augment MWTS-TGN with 19/4.75 AAC + New Switching Station at Winnindoo (WISS) + Augment TGN-WISS wit | 25.0289 | FY25: 33.803; FY26: -8.7741; FY27: 9; FY28: FY38
| 5 | Augment MWTS-TGN with 19/4.75 AAC + construct 30MW/150MWh BESS at BDSS | 9.6837 | FY25: 9.6837; FY26: 0; FY27: 2; FY28: -
| 6 |  | 0 | FY25: 0; FY26: 0; FY27: 2; FY28: -
| 7 |  | 0 | FY25: 0; FY26: 0; FY27: 2; FY28: -
| 8 |  | 0 | FY25: 0; FY26: 0; FY27: 2; FY28: -
| 9 |  | 0 | FY25: 0; FY26: 0; FY27: 2; FY28: -
| 10 |  | 0 | FY25: 0; FY26: 0; FY27: 2; FY28: -
High Demand | 1 | Do Nothing | 0 | FY25: 0; FY26: 0; FY27: 5
| 2 | Augment MWTS-TGN with 19/4.75 AAC + Augment TGN-MFA with 19/4.75 AAC | 1320.3215 | FY25: 41.2954; FY26: 1279.026; FY27: 3; FY28: FY28
| 3 | Augment MWTS-TGN with 19/4.75 AAC + New TGN-SLE 66kV line with 19/4.75 AAC | 1317.9689 | FY25: 67.2276; FY26: 1250.7413; FY27: 4; FY28: FY28
| 4 | Augment MWTS-TGN with 19/4.75 AAC + New Switching Station at Winnindoo (WISS) + Augment TGN-WISS wit | 1345.5329 | FY25: 59.6395; FY26: 1285.8934; FY27: 2; FY28: FY28
| 5 | Augment MWTS-TGN with 19/4.75 AAC + construct 30MW/150MWh BESS at BDSS | 1701.9549 | FY25: 110.9278; FY26: 1591.0271; FY27: 1; FY28: FY28
| 6 |  | 0 | FY25: 0; FY26: 0; FY27: 5; FY28: -
| 7 |  | 0 | FY25: 0; FY26: 0; FY27: 5; FY28: -
| 8 |  | 0 | FY25: 0; FY26: 0; FY27: 5; FY28: -
| 9 |  | 0 | FY25: 0; FY26: 0; FY27: 5; FY28: -
| 10 |  | 0 | FY25: 0; FY26: 0; FY27: 5; FY28: -
Low VCR | 1 | Do Nothing | 0 | FY25: 0; FY26: 0; FY27: 5
| 2 | Augment MWTS-TGN with 19/4.75 AAC + Augment TGN-MFA with 19/4.75 AAC | 223.4019 | FY25: 34.8809; FY26: 188.5209; FY27: 1; FY28: FY31
| 3 | Augment MWTS-TGN with 19/4.75 AAC + New TGN-SLE 66kV line with 19/4.75 AAC | 218.2716 | FY25: 53.6643; FY26: 164.6073; FY27: 3; FY28: FY32
| 4 | Augment MWTS-TGN with 19/4.75 AAC + New Switching Station at Winnindoo (WISS) + Augment TGN-WISS wit | 221.9803 | FY25: 47.6071; FY26: 174.3733; FY27: 2; FY28: FY32
| 5 | Augment MWTS-TGN with 19/4.75 AAC + construct 30MW/150MWh BESS at BDSS | 229.4184 | FY25: 75.0306; FY26: 154.3879; FY27: 4; FY28: FY35
| 6 |  | 0 | FY25: 0; FY26: 0; FY27: 5; FY28: -
| 7 |  | 0 | FY25: 0; FY26: 0; FY27: 5; FY28: -
| 8 |  | 0 | FY25: 0; FY26: 0; FY27: 5; FY28: -
| 9 |  | 0 | FY25: 0; FY26: 0; FY27: 5; FY28: -
| 10 |  | 0 | FY25: 0; FY26: 0; FY27: 5; FY28: -
High VCR | 1 | Do Nothing | 0 | FY25: 0; FY26: 0; FY27: 5
| 2 | Augment MWTS-TGN with 19/4.75 AAC + Augment TGN-MFA with 19/4.75 AAC | 342.5795 | FY25: 41.2954; FY26: 301.2841; FY27: 1; FY28: FY28
| 3 | Augment MWTS-TGN with 19/4.75 AAC + New TGN-SLE 66kV line with 19/4.75 AAC | 331.4914 | FY25: 56.785; FY26: 274.7063; FY27: 4; FY28: FY31
| 4 | Augment MWTS-TGN with 19/4.75 AAC + New Switching Station at Winnindoo (WISS) + Augment TGN-WISS wit | 337.0469 | FY25: 50.3756; FY26: 286.6713; FY27: 2; FY28: FY31
| 5 | Augment MWTS-TGN with 19/4.75 AAC + construct 30MW/150MWh BESS at BDSS | 361.7119 | FY25: 83.9403; FY26: 277.7716; FY27: 3; FY28: FY33
| 6 |  | 0 | FY25: 0; FY26: 0; FY27: 5; FY28: -
| 7 |  | 0 | FY25: 0; FY26: 0; FY27: 5; FY28: -
| 8 |  | 0 | FY25: 0; FY26: 0; FY27: 5; FY28: -
| 9 |  | 0 | FY25: 0; FY26: 0; FY27: 5; FY28: -
| 10 |  | 0 | FY25: 0; FY26: 0; FY27: 5; FY28: -
Low Tx PoF | 1 | Do Nothing | 0 | FY25: 0; FY26: 0; FY27: 5
| 2 | Augment MWTS-TGN with 19/4.75 AAC + Augment TGN-MFA with 19/4.75 AAC | 269.4659 | FY25: 34.8809; FY26: 234.585; FY27: 1; FY28: FY31
| 3 | Augment MWTS-TGN with 19/4.75 AAC + New TGN-SLE 66kV line with 19/4.75 AAC | 261.803 | FY25: 53.6643; FY26: 208.1387; FY27: 3; FY28: FY32
| 4 | Augment MWTS-TGN with 19/4.75 AAC + New Switching Station at Winnindoo (WISS) + Augment TGN-WISS wit | 269.5373 | FY25: 50.3756; FY26: 219.1617; FY27: 2; FY28: FY31
| 5 | Augment MWTS-TGN with 19/4.75 AAC + construct 30MW/150MWh BESS at BDSS | 284.6018 | FY25: 79.3649; FY26: 205.2369; FY27: 4; FY28: FY34
| 6 |  | 0 | FY25: 0; FY26: 0; FY27: 5; FY28: -
| 7 |  | 0 | FY25: 0; FY26: 0; FY27: 5; FY28: -
| 8 |  | 0 | FY25: 0; FY26: 0; FY27: 5; FY28: -
| 9 |  | 0 | FY25: 0; FY26: 0; FY27: 5; FY28: -
| 10 |  | 0 | FY25: 0; FY26: 0; FY27: 5; FY28: -
High Tx PoF | 1 | Do Nothing | 0 | FY25: 0; FY26: 0; FY27: 5
| 2 | Augment MWTS-TGN with 19/4.75 AAC + Augment TGN-MFA with 19/4.75 AAC | 293.8109 | FY25: 39.0406; FY26: 254.7703; FY27: 1; FY28: FY29
| 3 | Augment MWTS-TGN with 19/4.75 AAC + New TGN-SLE 66kV line with 19/4.75 AAC | 287.6941 | FY25: 56.785; FY26: 230.909; FY27: 3; FY28: FY31
| 4 | Augment MWTS-TGN with 19/4.75 AAC + New Switching Station at Winnindoo (WISS) + Augment TGN-WISS wit | 292.2076 | FY25: 50.3756; FY26: 241.832; FY27: 2; FY28: FY31
| 5 | Augment MWTS-TGN with 19/4.75 AAC + construct 30MW/150MWh BESS at BDSS | 311.5194 | FY25: 83.9403; FY26: 227.5791; FY27: 4; FY28: FY33
| 6 |  | 0 | FY25: 0; FY26: 0; FY27: 5; FY28: -
| 7 |  | 0 | FY25: 0; FY26: 0; FY27: 5; FY28: -
| 8 |  | 0 | FY25: 0; FY26: 0; FY27: 5; FY28: -
| 9 |  | 0 | FY25: 0; FY26: 0; FY27: 5; FY28: -
| 10 |  | 0 | FY25: 0; FY26: 0; FY27: 5; FY28: -

## 2.1 KMA
Asset and Option Inputs |  |  |  |  | Modelling Inputs
Assets at Risk | Name |  |  |  | Input | Value
Asset 1 | MWTS East 66kV Loop (W Fulham BESS) |  |  |  | Discount Rate | 5.56%
Asset 2 |  |  |  |  | Discount Rate Lower Bound | 4.11%
Asset 3 |  |  |  |  | Discount Rate Upper Bound | 7%
Asset 4 |  |  |  |  | Cost Central | 100%
Asset 5 |  |  |  |  | Cost Upper Bound | 120%
Asset 6 |  |  |  |  | Cost Lower Bound | 80%
Asset 7 |  |  |  |  | Real $2025 to real $2024 conversion factor | 95.36%
Asset 8 |  |  |  |  | Start Financial Year (in FY format 2024-25 = FY25) | FY25
Asset 9 |  |  |  |  | Opex | 1%
Asset 10 |  |  |  |  | VCR Upper Bound | 120%
Options | Name | Asset Life (Years) | Replacement Material Reduction P.A % | Used In Analysis | VCR Central | 100%
Option 1 - Do Nothing | Do Nothing | 45 | N/A | Yes | VCR Lower Bound | 80%
Option 2 - Augment MWTS-TGN with 19/4.75 AAC + Augment TGN-MFA with 19/4.75 AAC | Augment MWTS-TGN with 19/4.75 AAC + Augment TGN-MFA with 19/4.75 AAC | 45 | N/A | Yes
Option 3 - Augment MWTS-TGN with 19/4.75 AAC + New TGN-SLE 66kV line with 19/4.75 AAC | Augment MWTS-TGN with 19/4.75 AAC + New TGN-SLE 66kV line with 19/4.75 AAC | 45 | N/A | Yes
Option 4 - Augment MWTS-TGN with 19/4.75 AAC + New Switching Station at Winnindoo (WISS) + Augment TGN-WISS wit | Augment MWTS-TGN with 19/4.75 AAC + New Switching Station at Winnindoo (WISS) + Augment TGN-WISS wit | 45 | N/A | Yes
Option 5 - Augment MWTS-TGN with 19/4.75 AAC + construct 30MW/150MWh BESS at BDSS | Augment MWTS-TGN with 19/4.75 AAC + construct 30MW/150MWh BESS at BDSS | 15 | 1.619% | Yes
Option 6 - |  | 45 | N/A | No
Auto-populated
Inputs
Sources
Item | Link / Reference | Comments
BESS Replacement P.A reduction | https://www.csiro.au/-/media/Energy/GenCost/GenCost-2024-25-Final_20250728.pdf | Average linear reduction from 2024 to 2054, based on Appendix Table B.4 – Battery Storage (4 & 8-hour durations).

## 2.2.1 SupplyRisk$ BaseD
Option 1 - Do Nothing | [11 empty] | Option 2 - Augment MWTS-TGN with 19/4.75 AAC + Augment TGN-MFA with 19/4.75 AAC | [11 empty] | Option 3 - Augment MWTS-TGN with 19/4.75 AAC + New TGN-SLE 66kV line with 19/4.75 AAC | [11 empty] | Option 4 - Augment MWTS-TGN with 19/4.75 AAC + New Switching Station at Winnindoo (WISS) + Augment TGN-WISS wit | [11 empty] | Option 5 - Augment MWTS-TGN with 19/4.75 AAC + construct 30MW/150MWh BESS at BDSS | [11 empty] | Option 6 - | [11 empty] | Option 7 - | [11 empty] | Option 8 - | [11 empty] | Option 9 - | [11 empty] | Option 10 -
| Total Supply Risk $M by Asset and Year | [11 empty] | Total Supply Risk $M by Asset and Year | [11 empty] | Total Supply Risk $M by Asset and Year | [11 empty] | Total Supply Risk $M by Asset and Year | [11 empty] | Total Supply Risk $M by Asset and Year | [11 empty] | Total Supply Risk $M by Asset and Year | [11 empty] | Total Supply Risk $M by Asset and Year | [11 empty] | Total Supply Risk $M by Asset and Year | [11 empty] | Total Supply Risk $M by Asset and Year | [11 empty] | Total Supply Risk $M by Asset and Year
Source: | EaR_Augment East Gippsland 66kV Loop (MWTS-TGN-MFA lines)_summary.xlsx¦Output for AusNet NPV Model'!C4 | [11 empty] | EaR_Augment East Gippsland 66kV Loop (MWTS-TGN-MFA lines)_summary.xlsx¦Output for AusNet NPV Model'!D4 | [11 empty] | EaR_Augment East Gippsland 66kV Loop (MWTS-TGN-MFA lines)_summary.xlsx¦Output for AusNet NPV Model'!E4 | [11 empty] | EaR_Augment East Gippsland 66kV Loop (MWTS-TGN-MFA lines)_summary.xlsx¦Output for AusNet NPV Model'!F4 | [11 empty] | EaR_Augment East Gippsland 66kV Loop (MWTS-TGN-MFA lines)_summary.xlsx¦Output for AusNet NPV Model'!G4
Year | MWTS East 66kV Loop (W Fulham BESS) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Opt 1 Total | Year | MWTS East 66kV Loop (W Fulham BESS) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Opt 2 Total | Year | MWTS East 66kV Loop (W Fulham BESS) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Opt 3 Total | Year | MWTS East 66kV Loop (W Fulham BESS) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Opt 4 Total | Year | MWTS East 66kV Loop (W Fulham BESS) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Opt 5 Total | Year | MWTS East 66kV Loop (W Fulham BESS) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Opt 6 Total | Year | MWTS East 66kV Loop (W Fulham BESS) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Opt 7 Total | Year | MWTS East 66kV Loop (W Fulham BESS) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Opt 8 Total | Year | MWTS East 66kV Loop (W Fulham BESS) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Opt 9 Total | Year | MWTS East 66kV Loop (W Fulham BESS) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Opt 10 Total
FY25 | 1.1137 | [9 empty] | 1.1137 | FY25 | 1.1137 | [9 empty] | 1.1137 | FY25 | 1.1137 | [9 empty] | 1.1137 | FY25 | 1.1137 | [9 empty] | 1.1137 | FY25 | 1.1137 | [9 empty] | 1.1137 | FY25 | [10 empty] | 0
FY26 | 2.6361 | [9 empty] | 2.6361 | FY26 | 2.6361 | [9 empty] | 2.6361 | FY26 | 2.6361 | [9 empty] | 2.6361 | FY26 | 2.6361 | [9 empty] | 2.6361 | FY26 | 2.6361 | [9 empty] | 2.6361 | FY26
FY27 | 4.8351 | [9 empty] | 4.8351 | FY27 | 4.8351 | [9 empty] | 4.8351 | FY27 | 4.8351 | [9 empty] | 4.8351 | FY27 | 4.8351 | [9 empty] | 4.8351 | FY27 | 4.8351 | [9 empty] | 4.8351 | FY27
FY28 | 2.3613 | [9 empty] | 2.3613 | FY28 | 0.037438 | [9 empty] | 0.037438 | FY28 | 0.0060347 | [9 empty] | 0.0060347 | FY28 | 0.011211 | [9 empty] | 0.011211 | FY28 | 0.01758 | [9 empty] | 0.01758 | FY28
FY29 | 2.5897 | [9 empty] | 2.5897 | FY29 | 0.05616 | [9 empty] | 0.05616 | FY29 | 0.0079976 | [9 empty] | 0.0079976 | FY29 | 0.013463 | [9 empty] | 0.013463 | FY29 | 0.022594 | [9 empty] | 0.022594 | FY29
FY30 | 2.9899 | [9 empty] | 2.9899 | FY30 | 0.087536 | [9 empty] | 0.087536 | FY30 | 0.013061 | [9 empty] | 0.013061 | FY30 | 0.019408 | [9 empty] | 0.019408 | FY30 | 0.033687 | [9 empty] | 0.033687 | FY30
FY31 | 4.739 | [9 empty] | 4.739 | FY31 | 0.15929 | [9 empty] | 0.15929 | FY31 | 0.030296 | [9 empty] | 0.030296 | FY31 | 0.039024 | [9 empty] | 0.039024 | FY31 | 0.065859 | [9 empty] | 0.065859 | FY31
FY32 | 7.1467 | [9 empty] | 7.1467 | FY32 | 0.24956 | [9 empty] | 0.24956 | FY32 | 0.09615 | [9 empty] | 0.09615 | FY32 | 0.092869 | [9 empty] | 0.092869 | FY32 | 0.10345 | [9 empty] | 0.10345 | FY32
FY33 | 11.4165 | [9 empty] | 11.4165 | FY33 | 0.53594 | [9 empty] | 0.53594 | FY33 | 0.43224 | [9 empty] | 0.43224 | FY33 | 0.36202 | [9 empty] | 0.36202 | FY33 | 0.16921 | [9 empty] | 0.16921 | FY33
FY34 | 12.1547 | [9 empty] | 12.1547 | FY34 | 0.61292 | [9 empty] | 0.61292 | FY34 | 0.53044 | [9 empty] | 0.53044 | FY34 | 0.4436 | [9 empty] | 0.4436 | FY34 | 0.18013 | [9 empty] | 0.18013 | FY34
FY35 | 21.27 | [9 empty] | 21.27 | FY35 | 1.6853 | [9 empty] | 1.6853 | FY35 | 1.7172 | [9 empty] | 1.7172 | FY35 | 1.4872 | [9 empty] | 1.4872 | FY35 | 0.24965 | [9 empty] | 0.24965 | FY35
FY36 | 23.3412 | [9 empty] | 23.3412 | FY36 | 1.3511 | [9 empty] | 1.3511 | FY36 | 1.3408 | [9 empty] | 1.3408 | FY36 | 1.1652 | [9 empty] | 1.1652 | FY36 | 0.24546 | [9 empty] | 0.24546 | FY36
FY37 | 28.4421 | [9 empty] | 28.4421 | FY37 | 2.5671 | [9 empty] | 2.5671 | FY37 | 2.9132 | [9 empty] | 2.9132 | FY37 | 2.4614 | [9 empty] | 2.4614 | FY37 | 0.31 | [9 empty] | 0.31 | FY37
FY38 | 53.1535 | [9 empty] | 53.1535 | FY38 | 7.3917 | [9 empty] | 7.3917 | FY38 | 7.8574 | [9 empty] | 7.8574 | FY38 | 7.0261 | [9 empty] | 7.0261 | FY38 | 0.50155 | [9 empty] | 0.50155 | FY38
FY39 | 43.3219 | [9 empty] | 43.3219 | FY39 | 5.0403 | [9 empty] | 5.0403 | FY39 | 5.603 | [9 empty] | 5.603 | FY39 | 4.8938 | [9 empty] | 4.8938 | FY39 | 0.44973 | [9 empty] | 0.44973 | FY39
FY40 | [10 empty] | 43.3219 | FY40 | [10 empty] | 5.0403 | FY40 | [10 empty] | 5.603 | FY40 | [10 empty] | 4.8938 | FY40 | [10 empty] | 0.44973 | FY40 | [10 empty] | 0 | [11 empty] | 0 | [11 empty] | 0 | [11 empty] | 0 | [11 empty] | 0
FY41 | [10 empty] | 43.3219 | FY41 | [10 empty] | 5.0403 | FY41 | [10 empty] | 5.603 | FY41 | [10 empty] | 4.8938 | FY41 | [10 empty] | 0.44973 | FY41 | [10 empty] | 0 | [11 empty] | 0 | [11 empty] | 0 | [11 empty] | 0 | [11 empty] | 0
FY42 | [10 empty] | 43.3219 | FY42 | [10 empty] | 5.0403 | FY42 | [10 empty] | 5.603 | FY42 | [10 empty] | 4.8938 | FY42 | [10 empty] | 0.44973 | FY42 | [10 empty] | 0 | [11 empty] | 0 | [11 empty] | 0 | [11 empty] | 0 | [11 empty] | 0
FY43 | [10 empty] | 43.3219 | FY43 | [10 empty] | 5.0403 | FY43 | [10 empty] | 5.603 | FY43 | [10 empty] | 4.8938 | FY43 | [10 empty] | 0.44973 | FY43 | [10 empty] | 0 | [11 empty] | 0 | [11 empty] | 0 | [11 empty] | 0 | [11 empty] | 0
FY44 | [10 empty] | 43.3219 | FY44 | [10 empty] | 5.0403 | FY44 | [10 empty] | 5.603 | FY44 | [10 empty] | 4.8938 | FY44 | [10 empty] | 0.44973 | FY44 | [10 empty] | 0 | [11 empty] | 0 | [11 empty] | 0 | [11 empty] | 0 | [11 empty] | 0
FY45 | [10 empty] | 43.3219 | FY45 | [10 empty] | 5.0403 | FY45 | [10 empty] | 5.603 | FY45 | [10 empty] | 4.8938 | FY45 | [10 empty] | 0.44973 | FY45 | [10 empty] | 0 | [11 empty] | 0 | [11 empty] | 0 | [11 empty] | 0 | [11 empty] | 0
FY46 | [10 empty] | 43.3219 | FY46 | [10 empty] | 5.0403 | FY46 | [10 empty] | 5.603 | FY46 | [10 empty] | 4.8938 | FY46 | [10 empty] | 0.44973 | FY46 | [10 empty] | 0 | [11 empty] | 0 | [11 empty] | 0 | [11 empty] | 0 | [11 empty] | 0
FY47 | [10 empty] | 43.3219 | FY47 | [10 empty] | 5.0403 | FY47 | [10 empty] | 5.603 | FY47 | [10 empty] | 4.8938 | FY47 | [10 empty] | 0.44973 | FY47 | [10 empty] | 0 | [11 empty] | 0 | [11 empty] | 0 | [11 empty] | 0 | [11 empty] | 0
FY48 | [10 empty] | 43.3219 | FY48 | [10 empty] | 5.0403 | FY48 | [10 empty] | 5.603 | FY48 | [10 empty] | 4.8938 | FY48 | [10 empty] | 0.44973 | FY48 | [10 empty] | 0 | [11 empty] | 0 | [11 empty] | 0 | [11 empty] | 0 | [11 empty] | 0
FY49 | [10 empty] | 43.3219 | FY49 | [10 empty] | 5.0403 | FY49 | [10 empty] | 5.603 | FY49 | [10 empty] | 4.8938 | FY49 | [10 empty] | 0.44973 | FY49 | [10 empty] | 0 | [11 empty] | 0 | [11 empty] | 0 | [11 empty] | 0 | [11 empty] | 0
FY50 | [10 empty] | 43.3219 | FY50 | [10 empty] | 5.0403 | FY50 | [10 empty] | 5.603 | FY50 | [10 empty] | 4.8938 | FY50 | [10 empty] | 0.44973 | FY50 | [10 empty] | 0 | [11 empty] | 0 | [11 empty] | 0 | [11 empty] | 0 | [11 empty] | 0
FY51 | [10 empty] | 43.3219 | FY51 | [10 empty] | 5.0403 | FY51 | [10 empty] | 5.603 | FY51 | [10 empty] | 4.8938 | FY51 | [10 empty] | 0.44973 | FY51 | [10 empty] | 0 | [11 empty] | 0 | [11 empty] | 0 | [11 empty] | 0 | [11 empty] | 0
FY52 | [10 empty] | 43.3219 | FY52 | [10 empty] | 5.0403 | FY52 | [10 empty] | 5.603 | FY52 | [10 empty] | 4.8938 | FY52 | [10 empty] | 0.44973 | FY52 | [10 empty] | 0 | [11 empty] | 0 | [11 empty] | 0 | [11 empty] | 0 | [11 empty] | 0
FY53 | [10 empty] | 43.3219 | FY53 | [10 empty] | 5.0403 | FY53 | [10 empty] | 5.603 | FY53 | [10 empty] | 4.8938 | FY53 | [10 empty] | 0.44973 | FY53 | [10 empty] | 0 | [11 empty] | 0 | [11 empty] | 0 | [11 empty] | 0 | [11 empty] | 0
FY54 | [10 empty] | 43.3219 | FY54 | [10 empty] | 5.0403 | FY54 | [10 empty] | 5.603 | FY54 | [10 empty] | 4.8938 | FY54 | [10 empty] | 0.44973 | FY54 | [10 empty] | 0 | [11 empty] | 0 | [11 empty] | 0 | [11 empty] | 0 | [11 empty] | 0

## 2.2.2 SupplyRisk$ LowD
Option 1 - Do Nothing | [11 empty] | Option 2 - Augment MWTS-TGN with 19/4.75 AAC + Augment TGN-MFA with 19/4.75 AAC | [11 empty] | Option 3 - Augment MWTS-TGN with 19/4.75 AAC + New TGN-SLE 66kV line with 19/4.75 AAC | [11 empty] | Option 4 - Augment MWTS-TGN with 19/4.75 AAC + New Switching Station at Winnindoo (WISS) + Augment TGN-WISS wit | [11 empty] | Option 5 - Augment MWTS-TGN with 19/4.75 AAC + construct 30MW/150MWh BESS at BDSS | [11 empty] | Option 6 - | [11 empty] | Option 7 - | [11 empty] | Option 8 - | [11 empty] | Option 9 - | [11 empty] | Option 10 -
| Total Supply Risk $M by Asset and Year | [11 empty] | Total Supply Risk $M by Asset and Year | [11 empty] | Total Supply Risk $M by Asset and Year | [11 empty] | Total Supply Risk $M by Asset and Year | [11 empty] | Total Supply Risk $M by Asset and Year | [11 empty] | Total Supply Risk $M by Asset and Year | [11 empty] | Total Supply Risk $M by Asset and Year | [11 empty] | Total Supply Risk $M by Asset and Year | [11 empty] | Total Supply Risk $M by Asset and Year | [11 empty] | Total Supply Risk $M by Asset and Year
Source: | EaR_Augment East Gippsland 66kV Loop (MWTS-TGN-MFA lines)_summary.xlsx¦Output for AusNet NPV Model'!C23 | [11 empty] | EaR_Augment East Gippsland 66kV Loop (MWTS-TGN-MFA lines)_summary.xlsx¦Output for AusNet NPV Model'!D23 | [11 empty] | EaR_Augment East Gippsland 66kV Loop (MWTS-TGN-MFA lines)_summary.xlsx¦Output for AusNet NPV Model'!E23 | [11 empty] | EaR_Augment East Gippsland 66kV Loop (MWTS-TGN-MFA lines)_summary.xlsx¦Output for AusNet NPV Model'!F23 | [11 empty] | EaR_Augment East Gippsland 66kV Loop (MWTS-TGN-MFA lines)_summary.xlsx¦Output for AusNet NPV Model'!G23
Year | MWTS East 66kV Loop (W Fulham BESS) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Opt 1 Total | Year | MWTS East 66kV Loop (W Fulham BESS) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Opt 2 Total | Year | MWTS East 66kV Loop (W Fulham BESS) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Opt 3 Total | Year | MWTS East 66kV Loop (W Fulham BESS) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Opt 4 Total | Year | MWTS East 66kV Loop (W Fulham BESS) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Opt 5 Total | Year | MWTS East 66kV Loop (W Fulham BESS) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Opt 6 Total | Year | MWTS East 66kV Loop (W Fulham BESS) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Opt 7 Total | Year | MWTS East 66kV Loop (W Fulham BESS) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Opt 8 Total | Year | MWTS East 66kV Loop (W Fulham BESS) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Opt 9 Total | Year | MWTS East 66kV Loop (W Fulham BESS) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Opt 10 Total
FY25 | 0.035548 | [9 empty] | 0.035548 | FY25 | 0.035548 | [9 empty] | 0.035548 | FY25 | 0.035548 | [9 empty] | 0.035548 | FY25 | 0.035548 | [9 empty] | 0.035548 | FY25 | 0.035548 | [9 empty] | 0.035548 | FY25 | [10 empty] | 0
FY26 | 0.26077 | [9 empty] | 0.26077 | FY26 | 0.26077 | [9 empty] | 0.26077 | FY26 | 0.26077 | [9 empty] | 0.26077 | FY26 | 0.26077 | [9 empty] | 0.26077 | FY26 | 0.26077 | [9 empty] | 0.26077 | FY26
FY27 | 0.65041 | [9 empty] | 0.65041 | FY27 | 0.65041 | [9 empty] | 0.65041 | FY27 | 0.65041 | [9 empty] | 0.65041 | FY27 | 0.65041 | [9 empty] | 0.65041 | FY27 | 0.65041 | [9 empty] | 0.65041 | FY27
FY28 | 0.24823 | [9 empty] | 0.24823 | FY28 | 0.0053674 | [9 empty] | 0.0053674 | FY28 | 0.00067765 | [9 empty] | 0.00067765 | FY28 | 0.0023404 | [9 empty] | 0.0023404 | FY28 | 0.0038113 | [9 empty] | 0.0038113 | FY28
FY29 | 0.31943 | [9 empty] | 0.31943 | FY29 | 0.0085961 | [9 empty] | 0.0085961 | FY29 | 0.00076837 | [9 empty] | 0.00076837 | FY29 | 0.0024977 | [9 empty] | 0.0024977 | FY29 | 0.0041704 | [9 empty] | 0.0041704 | FY29
FY30 | 0.43666 | [9 empty] | 0.43666 | FY30 | 0.015415 | [9 empty] | 0.015415 | FY30 | 0.0010647 | [9 empty] | 0.0010647 | FY30 | 0.003048 | [9 empty] | 0.003048 | FY30 | 0.00544 | [9 empty] | 0.00544 | FY30
FY31 | 0.78759 | [9 empty] | 0.78759 | FY31 | 0.035401 | [9 empty] | 0.035401 | FY31 | 0.0026152 | [9 empty] | 0.0026152 | FY31 | 0.005606 | [9 empty] | 0.005606 | FY31 | 0.010746 | [9 empty] | 0.010746 | FY31
FY32 | 1.1507 | [9 empty] | 1.1507 | FY32 | 0.059663 | [9 empty] | 0.059663 | FY32 | 0.0054919 | [9 empty] | 0.0054919 | FY32 | 0.009606 | [9 empty] | 0.009606 | FY32 | 0.018623 | [9 empty] | 0.018623 | FY32
FY33 | 1.7022 | [9 empty] | 1.7022 | FY33 | 0.10327 | [9 empty] | 0.10327 | FY33 | 0.013141 | [9 empty] | 0.013141 | FY33 | 0.018085 | [9 empty] | 0.018085 | FY33 | 0.034773 | [9 empty] | 0.034773 | FY33
FY34 | 1.6556 | [9 empty] | 1.6556 | FY34 | 0.11059 | [9 empty] | 0.11059 | FY34 | 0.014399 | [9 empty] | 0.014399 | FY34 | 0.019704 | [9 empty] | 0.019704 | FY34 | 0.037739 | [9 empty] | 0.037739 | FY34
FY35 | 2.3474 | [9 empty] | 2.3474 | FY35 | 0.15638 | [9 empty] | 0.15638 | FY35 | 0.02983 | [9 empty] | 0.02983 | FY35 | 0.034607 | [9 empty] | 0.034607 | FY35 | 0.059864 | [9 empty] | 0.059864 | FY35
FY36 | 2.8002 | [9 empty] | 2.8002 | FY36 | 0.15174 | [9 empty] | 0.15174 | FY36 | 0.026036 | [9 empty] | 0.026036 | FY36 | 0.034027 | [9 empty] | 0.034027 | FY36 | 0.059666 | [9 empty] | 0.059666 | FY36
FY37 | 3.1587 | [9 empty] | 3.1587 | FY37 | 0.19725 | [9 empty] | 0.19725 | FY37 | 0.04812 | [9 empty] | 0.04812 | FY37 | 0.050465 | [9 empty] | 0.050465 | FY37 | 0.078054 | [9 empty] | 0.078054 | FY37
FY38 | 5.2105 | [9 empty] | 5.2105 | FY38 | 0.35444 | [9 empty] | 0.35444 | FY38 | 0.20199 | [9 empty] | 0.20199 | FY38 | 0.18266 | [9 empty] | 0.18266 | FY38 | 0.11978 | [9 empty] | 0.11978 | FY38
FY39 | 4.4838 | [9 empty] | 4.4838 | FY39 | 0.27377 | [9 empty] | 0.27377 | FY39 | 0.11855 | [9 empty] | 0.11855 | FY39 | 0.11202 | [9 empty] | 0.11202 | FY39 | 0.10317 | [9 empty] | 0.10317 | FY39
FY40 | [10 empty] | 4.4838 | FY40 | [10 empty] | 0.27377 | FY40 | [10 empty] | 0.11855 | FY40 | [10 empty] | 0.11202 | FY40 | [10 empty] | 0.10317 | FY40 | [10 empty] | 0 | [11 empty] | 0 | [11 empty] | 0 | [11 empty] | 0 | [11 empty] | 0
FY41 | [10 empty] | 4.4838 | FY41 | [10 empty] | 0.27377 | FY41 | [10 empty] | 0.11855 | FY41 | [10 empty] | 0.11202 | FY41 | [10 empty] | 0.10317 | FY41 | [10 empty] | 0 | [11 empty] | 0 | [11 empty] | 0 | [11 empty] | 0 | [11 empty] | 0
FY42 | [10 empty] | 4.4838 | FY42 | [10 empty] | 0.27377 | FY42 | [10 empty] | 0.11855 | FY42 | [10 empty] | 0.11202 | FY42 | [10 empty] | 0.10317 | FY42 | [10 empty] | 0 | [11 empty] | 0 | [11 empty] | 0 | [11 empty] | 0 | [11 empty] | 0
FY43 | [10 empty] | 4.4838 | FY43 | [10 empty] | 0.27377 | FY43 | [10 empty] | 0.11855 | FY43 | [10 empty] | 0.11202 | FY43 | [10 empty] | 0.10317 | FY43 | [10 empty] | 0 | [11 empty] | 0 | [11 empty] | 0 | [11 empty] | 0 | [11 empty] | 0
FY44 | [10 empty] | 4.4838 | FY44 | [10 empty] | 0.27377 | FY44 | [10 empty] | 0.11855 | FY44 | [10 empty] | 0.11202 | FY44 | [10 empty] | 0.10317 | FY44 | [10 empty] | 0 | [11 empty] | 0 | [11 empty] | 0 | [11 empty] | 0 | [11 empty] | 0
FY45 | [10 empty] | 4.4838 | FY45 | [10 empty] | 0.27377 | FY45 | [10 empty] | 0.11855 | FY45 | [10 empty] | 0.11202 | FY45 | [10 empty] | 0.10317 | FY45 | [10 empty] | 0 | [11 empty] | 0 | [11 empty] | 0 | [11 empty] | 0 | [11 empty] | 0
FY46 | [10 empty] | 4.4838 | FY46 | [10 empty] | 0.27377 | FY46 | [10 empty] | 0.11855 | FY46 | [10 empty] | 0.11202 | FY46 | [10 empty] | 0.10317 | FY46 | [10 empty] | 0 | [11 empty] | 0 | [11 empty] | 0 | [11 empty] | 0 | [11 empty] | 0
FY47 | [10 empty] | 4.4838 | FY47 | [10 empty] | 0.27377 | FY47 | [10 empty] | 0.11855 | FY47 | [10 empty] | 0.11202 | FY47 | [10 empty] | 0.10317 | FY47 | [10 empty] | 0 | [11 empty] | 0 | [11 empty] | 0 | [11 empty] | 0 | [11 empty] | 0
FY48 | [10 empty] | 4.4838 | FY48 | [10 empty] | 0.27377 | FY48 | [10 empty] | 0.11855 | FY48 | [10 empty] | 0.11202 | FY48 | [10 empty] | 0.10317 | FY48 | [10 empty] | 0 | [11 empty] | 0 | [11 empty] | 0 | [11 empty] | 0 | [11 empty] | 0
FY49 | [10 empty] | 4.4838 | FY49 | [10 empty] | 0.27377 | FY49 | [10 empty] | 0.11855 | FY49 | [10 empty] | 0.11202 | FY49 | [10 empty] | 0.10317 | FY49 | [10 empty] | 0 | [11 empty] | 0 | [11 empty] | 0 | [11 empty] | 0 | [11 empty] | 0
FY50 | [10 empty] | 4.4838 | FY50 | [10 empty] | 0.27377 | FY50 | [10 empty] | 0.11855 | FY50 | [10 empty] | 0.11202 | FY50 | [10 empty] | 0.10317 | FY50 | [10 empty] | 0 | [11 empty] | 0 | [11 empty] | 0 | [11 empty] | 0 | [11 empty] | 0
FY51 | [10 empty] | 4.4838 | FY51 | [10 empty] | 0.27377 | FY51 | [10 empty] | 0.11855 | FY51 | [10 empty] | 0.11202 | FY51 | [10 empty] | 0.10317 | FY51 | [10 empty] | 0 | [11 empty] | 0 | [11 empty] | 0 | [11 empty] | 0 | [11 empty] | 0
FY52 | [10 empty] | 4.4838 | FY52 | [10 empty] | 0.27377 | FY52 | [10 empty] | 0.11855 | FY52 | [10 empty] | 0.11202 | FY52 | [10 empty] | 0.10317 | FY52 | [10 empty] | 0 | [11 empty] | 0 | [11 empty] | 0 | [11 empty] | 0 | [11 empty] | 0
FY53 | [10 empty] | 4.4838 | FY53 | [10 empty] | 0.27377 | FY53 | [10 empty] | 0.11855 | FY53 | [10 empty] | 0.11202 | FY53 | [10 empty] | 0.10317 | FY53 | [10 empty] | 0 | [11 empty] | 0 | [11 empty] | 0 | [11 empty] | 0 | [11 empty] | 0
FY54 | [10 empty] | 4.4838 | FY54 | [10 empty] | 0.27377 | FY54 | [10 empty] | 0.11855 | FY54 | [10 empty] | 0.11202 | FY54 | [10 empty] | 0.10317 | FY54 | [10 empty] | 0 | [11 empty] | 0 | [11 empty] | 0 | [11 empty] | 0 | [11 empty] | 0

## 2.2.3 SupplyRisk$ HighD
Option 1 - Do Nothing | [11 empty] | Option 2 - Augment MWTS-TGN with 19/4.75 AAC + Augment TGN-MFA with 19/4.75 AAC | [11 empty] | Option 3 - Augment MWTS-TGN with 19/4.75 AAC + New TGN-SLE 66kV line with 19/4.75 AAC | [11 empty] | Option 4 - Augment MWTS-TGN with 19/4.75 AAC + New Switching Station at Winnindoo (WISS) + Augment TGN-WISS wit | [11 empty] | Option 5 - Augment MWTS-TGN with 19/4.75 AAC + construct 30MW/150MWh BESS at BDSS | [11 empty] | Option 6 - | [11 empty] | Option 7 - | [11 empty] | Option 8 - | [11 empty] | Option 9 - | [11 empty] | Option 10 -
| Total Supply Risk $M by Asset and Year | [11 empty] | Total Supply Risk $M by Asset and Year | [11 empty] | Total Supply Risk $M by Asset and Year | [11 empty] | Total Supply Risk $M by Asset and Year | [11 empty] | Total Supply Risk $M by Asset and Year | [11 empty] | Total Supply Risk $M by Asset and Year | [11 empty] | Total Supply Risk $M by Asset and Year | [11 empty] | Total Supply Risk $M by Asset and Year | [11 empty] | Total Supply Risk $M by Asset and Year | [11 empty] | Total Supply Risk $M by Asset and Year
Source: | EaR_Augment East Gippsland 66kV Loop (MWTS-TGN-MFA lines)_summary.xlsx¦Output for AusNet NPV Model'!C42 | [11 empty] | EaR_Augment East Gippsland 66kV Loop (MWTS-TGN-MFA lines)_summary.xlsx¦Output for AusNet NPV Model'!D42 | [11 empty] | EaR_Augment East Gippsland 66kV Loop (MWTS-TGN-MFA lines)_summary.xlsx¦Output for AusNet NPV Model'!E42 | [11 empty] | EaR_Augment East Gippsland 66kV Loop (MWTS-TGN-MFA lines)_summary.xlsx¦Output for AusNet NPV Model'!F42 | [11 empty] | EaR_Augment East Gippsland 66kV Loop (MWTS-TGN-MFA lines)_summary.xlsx¦Output for AusNet NPV Model'!G42
Year | MWTS East 66kV Loop (W Fulham BESS) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Opt 1 Total | Year | MWTS East 66kV Loop (W Fulham BESS) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Opt 2 Total | Year | MWTS East 66kV Loop (W Fulham BESS) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Opt 3 Total | Year | MWTS East 66kV Loop (W Fulham BESS) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Opt 4 Total | Year | MWTS East 66kV Loop (W Fulham BESS) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Opt 5 Total | Year | MWTS East 66kV Loop (W Fulham BESS) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Opt 6 Total | Year | MWTS East 66kV Loop (W Fulham BESS) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Opt 7 Total | Year | MWTS East 66kV Loop (W Fulham BESS) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Opt 8 Total | Year | MWTS East 66kV Loop (W Fulham BESS) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Opt 9 Total | Year | MWTS East 66kV Loop (W Fulham BESS) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Opt 10 Total
FY25 | 5.8608 | [9 empty] | 5.8608 | FY25 | 5.8608 | [9 empty] | 5.8608 | FY25 | 5.8608 | [9 empty] | 5.8608 | FY25 | 5.8608 | [9 empty] | 5.8608 | FY25 | 5.8608 | [9 empty] | 5.8608 | FY25 | [10 empty] | 0
FY26 | 13.0978 | [9 empty] | 13.0978 | FY26 | 13.0978 | [9 empty] | 13.0978 | FY26 | 13.0978 | [9 empty] | 13.0978 | FY26 | 13.0978 | [9 empty] | 13.0978 | FY26 | 13.0978 | [9 empty] | 13.0978 | FY26
FY27 | 21.8339 | [9 empty] | 21.8339 | FY27 | 21.8339 | [9 empty] | 21.8339 | FY27 | 21.8339 | [9 empty] | 21.8339 | FY27 | 21.8339 | [9 empty] | 21.8339 | FY27 | 21.8339 | [9 empty] | 21.8339 | FY27
FY28 | 11.2255 | [9 empty] | 11.2255 | FY28 | 0.1463 | [9 empty] | 0.1463 | FY28 | 0.10202 | [9 empty] | 0.10202 | FY28 | 0.082816 | [9 empty] | 0.082816 | FY28 | 0.072356 | [9 empty] | 0.072356 | FY28
FY29 | 12.0422 | [9 empty] | 12.0422 | FY29 | 0.20804 | [9 empty] | 0.20804 | FY29 | 0.14566 | [9 empty] | 0.14566 | FY29 | 0.12033 | [9 empty] | 0.12033 | FY29 | 0.10331 | [9 empty] | 0.10331 | FY29
FY30 | 14.598 | [9 empty] | 14.598 | FY30 | 0.36802 | [9 empty] | 0.36802 | FY30 | 0.30173 | [9 empty] | 0.30173 | FY30 | 0.25955 | [9 empty] | 0.25955 | FY30 | 0.16568 | [9 empty] | 0.16568 | FY30
FY31 | 25.0662 | [9 empty] | 25.0662 | FY31 | 1.2411 | [9 empty] | 1.2411 | FY31 | 1.368 | [9 empty] | 1.368 | FY31 | 1.1697 | [9 empty] | 1.1697 | FY31 | 0.39463 | [9 empty] | 0.39463 | FY31
FY32 | 40.4461 | [9 empty] | 40.4461 | FY32 | 3.2549 | [9 empty] | 3.2549 | FY32 | 3.8397 | [9 empty] | 3.8397 | FY32 | 3.2945 | [9 empty] | 3.2945 | FY32 | 0.66972 | [9 empty] | 0.66972 | FY32
FY33 | 73.085 | [9 empty] | 73.085 | FY33 | 10.2324 | [9 empty] | 10.2324 | FY33 | 11.3575 | [9 empty] | 11.3575 | FY33 | 10.1335 | [9 empty] | 10.1335 | FY33 | 1.1925 | [9 empty] | 1.1925 | FY33
FY34 | 79.2349 | [9 empty] | 79.2349 | FY34 | 11.5757 | [9 empty] | 11.5757 | FY34 | 12.7949 | [9 empty] | 12.7949 | FY34 | 11.4052 | [9 empty] | 11.4052 | FY34 | 1.1551 | [9 empty] | 1.1551 | FY34
FY35 | 130.2164 | [9 empty] | 130.2164 | FY35 | 26.7759 | [9 empty] | 26.7759 | FY35 | 27.7689 | [9 empty] | 27.7689 | FY35 | 25.4558 | [9 empty] | 25.4558 | FY35 | 2.2125 | [9 empty] | 2.2125 | FY35
FY36 | 129.9448 | [9 empty] | 129.9448 | FY36 | 23.2252 | [9 empty] | 23.2252 | FY36 | 24.8881 | [9 empty] | 24.8881 | FY36 | 22.6298 | [9 empty] | 22.6298 | FY36 | 2.2736 | [9 empty] | 2.2736 | FY36
FY37 | 171.1314 | [9 empty] | 171.1314 | FY37 | 39.6929 | [9 empty] | 39.6929 | FY37 | 40.5508 | [9 empty] | 40.5508 | FY37 | 37.5908 | [9 empty] | 37.5908 | FY37 | 3.248 | [9 empty] | 3.248 | FY37
FY38 | 273.2963 | [9 empty] | 273.2963 | FY38 | 78.1336 | [9 empty] | 78.1336 | FY38 | 76.3955 | [9 empty] | 76.3955 | FY38 | 72.152 | [9 empty] | 72.152 | FY38 | 6.8496 | [9 empty] | 6.8496 | FY38
FY39 | 231.7687 | [9 empty] | 231.7687 | FY39 | 60.865 | [9 empty] | 60.865 | FY39 | 60.7558 | [9 empty] | 60.7558 | FY39 | 57.0528 | [9 empty] | 57.0528 | FY39 | 5.2956 | [9 empty] | 5.2956 | FY39
FY40 | [10 empty] | 231.7687 | FY40 | [10 empty] | 60.865 | FY40 | [10 empty] | 60.7558 | FY40 | [10 empty] | 57.0528 | FY40 | [10 empty] | 5.2956 | FY40 | [10 empty] | 0 | [11 empty] | 0 | [11 empty] | 0 | [11 empty] | 0 | [11 empty] | 0
FY41 | [10 empty] | 231.7687 | FY41 | [10 empty] | 60.865 | FY41 | [10 empty] | 60.7558 | FY41 | [10 empty] | 57.0528 | FY41 | [10 empty] | 5.2956 | FY41 | [10 empty] | 0 | [11 empty] | 0 | [11 empty] | 0 | [11 empty] | 0 | [11 empty] | 0
FY42 | [10 empty] | 231.7687 | FY42 | [10 empty] | 60.865 | FY42 | [10 empty] | 60.7558 | FY42 | [10 empty] | 57.0528 | FY42 | [10 empty] | 5.2956 | FY42 | [10 empty] | 0 | [11 empty] | 0 | [11 empty] | 0 | [11 empty] | 0 | [11 empty] | 0
FY43 | [10 empty] | 231.7687 | FY43 | [10 empty] | 60.865 | FY43 | [10 empty] | 60.7558 | FY43 | [10 empty] | 57.0528 | FY43 | [10 empty] | 5.2956 | FY43 | [10 empty] | 0 | [11 empty] | 0 | [11 empty] | 0 | [11 empty] | 0 | [11 empty] | 0
FY44 | [10 empty] | 231.7687 | FY44 | [10 empty] | 60.865 | FY44 | [10 empty] | 60.7558 | FY44 | [10 empty] | 57.0528 | FY44 | [10 empty] | 5.2956 | FY44 | [10 empty] | 0 | [11 empty] | 0 | [11 empty] | 0 | [11 empty] | 0 | [11 empty] | 0
FY45 | [10 empty] | 231.7687 | FY45 | [10 empty] | 60.865 | FY45 | [10 empty] | 60.7558 | FY45 | [10 empty] | 57.0528 | FY45 | [10 empty] | 5.2956 | FY45 | [10 empty] | 0 | [11 empty] | 0 | [11 empty] | 0 | [11 empty] | 0 | [11 empty] | 0
FY46 | [10 empty] | 231.7687 | FY46 | [10 empty] | 60.865 | FY46 | [10 empty] | 60.7558 | FY46 | [10 empty] | 57.0528 | FY46 | [10 empty] | 5.2956 | FY46 | [10 empty] | 0 | [11 empty] | 0 | [11 empty] | 0 | [11 empty] | 0 | [11 empty] | 0
FY47 | [10 empty] | 231.7687 | FY47 | [10 empty] | 60.865 | FY47 | [10 empty] | 60.7558 | FY47 | [10 empty] | 57.0528 | FY47 | [10 empty] | 5.2956 | FY47 | [10 empty] | 0 | [11 empty] | 0 | [11 empty] | 0 | [11 empty] | 0 | [11 empty] | 0
FY48 | [10 empty] | 231.7687 | FY48 | [10 empty] | 60.865 | FY48 | [10 empty] | 60.7558 | FY48 | [10 empty] | 57.0528 | FY48 | [10 empty] | 5.2956 | FY48 | [10 empty] | 0 | [11 empty] | 0 | [11 empty] | 0 | [11 empty] | 0 | [11 empty] | 0
FY49 | [10 empty] | 231.7687 | FY49 | [10 empty] | 60.865 | FY49 | [10 empty] | 60.7558 | FY49 | [10 empty] | 57.0528 | FY49 | [10 empty] | 5.2956 | FY49 | [10 empty] | 0 | [11 empty] | 0 | [11 empty] | 0 | [11 empty] | 0 | [11 empty] | 0
FY50 | [10 empty] | 231.7687 | FY50 | [10 empty] | 60.865 | FY50 | [10 empty] | 60.7558 | FY50 | [10 empty] | 57.0528 | FY50 | [10 empty] | 5.2956 | FY50 | [10 empty] | 0 | [11 empty] | 0 | [11 empty] | 0 | [11 empty] | 0 | [11 empty] | 0
FY51 | [10 empty] | 231.7687 | FY51 | [10 empty] | 60.865 | FY51 | [10 empty] | 60.7558 | FY51 | [10 empty] | 57.0528 | FY51 | [10 empty] | 5.2956 | FY51 | [10 empty] | 0 | [11 empty] | 0 | [11 empty] | 0 | [11 empty] | 0 | [11 empty] | 0
FY52 | [10 empty] | 231.7687 | FY52 | [10 empty] | 60.865 | FY52 | [10 empty] | 60.7558 | FY52 | [10 empty] | 57.0528 | FY52 | [10 empty] | 5.2956 | FY52 | [10 empty] | 0 | [11 empty] | 0 | [11 empty] | 0 | [11 empty] | 0 | [11 empty] | 0
FY53 | [10 empty] | 231.7687 | FY53 | [10 empty] | 60.865 | FY53 | [10 empty] | 60.7558 | FY53 | [10 empty] | 57.0528 | FY53 | [10 empty] | 5.2956 | FY53 | [10 empty] | 0 | [11 empty] | 0 | [11 empty] | 0 | [11 empty] | 0 | [11 empty] | 0
FY54 | [10 empty] | 231.7687 | FY54 | [10 empty] | 60.865 | FY54 | [10 empty] | 60.7558 | FY54 | [10 empty] | 57.0528 | FY54 | [10 empty] | 5.2956 | FY54 | [10 empty] | 0 | [11 empty] | 0 | [11 empty] | 0 | [11 empty] | 0 | [11 empty] | 0

## 2.2.4 SupplyRisk$ Low PoF
Option 1 - Do Nothing | [11 empty] | Option 2 - Augment MWTS-TGN with 19/4.75 AAC + Augment TGN-MFA with 19/4.75 AAC | [11 empty] | Option 3 - Augment MWTS-TGN with 19/4.75 AAC + New TGN-SLE 66kV line with 19/4.75 AAC | [11 empty] | Option 4 - Augment MWTS-TGN with 19/4.75 AAC + New Switching Station at Winnindoo (WISS) + Augment TGN-WISS wit | [11 empty] | Option 5 - Augment MWTS-TGN with 19/4.75 AAC + construct 30MW/150MWh BESS at BDSS | [11 empty] | Option 6 - | [11 empty] | Option 7 - | [11 empty] | Option 8 - | [11 empty] | Option 9 - | [11 empty] | Option 10 -
| Total Supply Risk $M by Asset and Year | [11 empty] | Total Supply Risk $M by Asset and Year | [11 empty] | Total Supply Risk $M by Asset and Year | [11 empty] | Total Supply Risk $M by Asset and Year | [11 empty] | Total Supply Risk $M by Asset and Year | [11 empty] | Total Supply Risk $M by Asset and Year | [11 empty] | Total Supply Risk $M by Asset and Year | [11 empty] | Total Supply Risk $M by Asset and Year | [11 empty] | Total Supply Risk $M by Asset and Year | [11 empty] | Total Supply Risk $M by Asset and Year
Source: | EaR_Augment East Gippsland 66kV Loop (MWTS-TGN-MFA lines)_summary.xlsx¦Output for AusNet NPV Model_PoF'!C23 | [11 empty] | EaR_Augment East Gippsland 66kV Loop (MWTS-TGN-MFA lines)_summary.xlsx¦Output for AusNet NPV Model_PoF'!D23 | [11 empty] | EaR_Augment East Gippsland 66kV Loop (MWTS-TGN-MFA lines)_summary.xlsx¦Output for AusNet NPV Model_PoF'!E23 | [11 empty] | EaR_Augment East Gippsland 66kV Loop (MWTS-TGN-MFA lines)_summary.xlsx¦Output for AusNet NPV Model_PoF'!F23 | [11 empty] | EaR_Augment East Gippsland 66kV Loop (MWTS-TGN-MFA lines)_summary.xlsx¦Output for AusNet NPV Model_PoF'!G23
Year | MWTS East 66kV Loop (W Fulham BESS) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Opt 1 Total | Year | MWTS East 66kV Loop (W Fulham BESS) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Opt 2 Total | Year | MWTS East 66kV Loop (W Fulham BESS) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Opt 3 Total | Year | MWTS East 66kV Loop (W Fulham BESS) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Opt 4 Total | Year | MWTS East 66kV Loop (W Fulham BESS) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Opt 5 Total | Year | MWTS East 66kV Loop (W Fulham BESS) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Opt 6 Total | Year | MWTS East 66kV Loop (W Fulham BESS) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Opt 7 Total | Year | MWTS East 66kV Loop (W Fulham BESS) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Opt 8 Total | Year | MWTS East 66kV Loop (W Fulham BESS) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Opt 9 Total | Year | MWTS East 66kV Loop (W Fulham BESS) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Opt 10 Total
FY25 | 1.0585 | [9 empty] | 1.0585 | FY25 | 1.0585 | [9 empty] | 1.0585 | FY25 | 1.0585 | [9 empty] | 1.0585 | FY25 | 1.0585 | [9 empty] | 1.0585 | FY25 | 1.0585 | [9 empty] | 1.0585 | FY25 | [10 empty] | 0
FY26 | 2.5254 | [9 empty] | 2.5254 | FY26 | 2.5254 | [9 empty] | 2.5254 | FY26 | 2.5254 | [9 empty] | 2.5254 | FY26 | 2.5254 | [9 empty] | 2.5254 | FY26 | 2.5254 | [9 empty] | 2.5254 | FY26
FY27 | 4.6632 | [9 empty] | 4.6632 | FY27 | 4.6632 | [9 empty] | 4.6632 | FY27 | 4.6632 | [9 empty] | 4.6632 | FY27 | 4.6632 | [9 empty] | 4.6632 | FY27 | 4.6632 | [9 empty] | 4.6632 | FY27
FY28 | 2.1035 | [9 empty] | 2.1035 | FY28 | 0.018719 | [9 empty] | 0.018719 | FY28 | 0.0030174 | [9 empty] | 0.0030174 | FY28 | 0.0056057 | [9 empty] | 0.0056057 | FY28 | 0.0087898 | [9 empty] | 0.0087898 | FY28
FY29 | 2.2678 | [9 empty] | 2.2678 | FY29 | 0.02808 | [9 empty] | 0.02808 | FY29 | 0.0039988 | [9 empty] | 0.0039988 | FY29 | 0.0067313 | [9 empty] | 0.0067313 | FY29 | 0.011297 | [9 empty] | 0.011297 | FY29
FY30 | 2.5783 | [9 empty] | 2.5783 | FY30 | 0.043768 | [9 empty] | 0.043768 | FY30 | 0.0065305 | [9 empty] | 0.0065305 | FY30 | 0.009704 | [9 empty] | 0.009704 | FY30 | 0.016843 | [9 empty] | 0.016843 | FY30
FY31 | 4.15 | [9 empty] | 4.15 | FY31 | 0.079645 | [9 empty] | 0.079645 | FY31 | 0.015152 | [9 empty] | 0.015152 | FY31 | 0.019512 | [9 empty] | 0.019512 | FY31 | 0.032929 | [9 empty] | 0.032929 | FY31
FY32 | 6.4045 | [9 empty] | 6.4045 | FY32 | 0.13384 | [9 empty] | 0.13384 | FY32 | 0.069306 | [9 empty] | 0.069306 | FY32 | 0.060825 | [9 empty] | 0.060825 | FY32 | 0.051726 | [9 empty] | 0.051726 | FY32
FY33 | 10.4631 | [9 empty] | 10.4631 | FY33 | 0.36189 | [9 empty] | 0.36189 | FY33 | 0.38325 | [9 empty] | 0.38325 | FY33 | 0.3058 | [9 empty] | 0.3058 | FY33 | 0.084606 | [9 empty] | 0.084606 | FY33
FY34 | 11.1717 | [9 empty] | 11.1717 | FY34 | 0.42975 | [9 empty] | 0.42975 | FY34 | 0.47757 | [9 empty] | 0.47757 | FY34 | 0.38324 | [9 empty] | 0.38324 | FY34 | 0.090066 | [9 empty] | 0.090066 | FY34
FY35 | 20.1112 | [9 empty] | 20.1112 | FY35 | 1.4493 | [9 empty] | 1.4493 | FY35 | 1.6379 | [9 empty] | 1.6379 | FY35 | 1.3978 | [9 empty] | 1.3978 | FY35 | 0.12482 | [9 empty] | 0.12482 | FY35
FY36 | 22.1651 | [9 empty] | 22.1651 | FY36 | 1.1202 | [9 empty] | 1.1202 | FY36 | 1.2632 | [9 empty] | 1.2632 | FY36 | 1.0777 | [9 empty] | 1.0777 | FY36 | 0.12273 | [9 empty] | 0.12273 | FY36
FY37 | 27.141 | [9 empty] | 27.141 | FY37 | 2.2857 | [9 empty] | 2.2857 | FY37 | 2.8116 | [9 empty] | 2.8116 | FY37 | 2.3475 | [9 empty] | 2.3475 | FY37 | 0.15589 | [9 empty] | 0.15589 | FY37
FY38 | 51.6182 | [9 empty] | 51.6182 | FY38 | 7.0335 | [9 empty] | 7.0335 | FY38 | 7.7083 | [9 empty] | 7.7083 | FY38 | 6.8612 | [9 empty] | 6.8612 | FY38 | 0.29192 | [9 empty] | 0.29192 | FY38
FY39 | 41.8648 | [9 empty] | 41.8648 | FY39 | 4.7117 | [9 empty] | 4.7117 | FY39 | 5.4729 | [9 empty] | 5.4729 | FY39 | 4.7492 | [9 empty] | 4.7492 | FY39 | 0.26155 | [9 empty] | 0.26155 | FY39
FY40 | [10 empty] | 41.8648 | FY40 | [10 empty] | 4.7117 | FY40 | [10 empty] | 5.4729 | FY40 | [10 empty] | 4.7492 | FY40 | [10 empty] | 0.26155 | FY40 | [10 empty] | 0 | [11 empty] | 0 | [11 empty] | 0 | [11 empty] | 0 | [11 empty] | 0
FY41 | [10 empty] | 41.8648 | FY41 | [10 empty] | 4.7117 | FY41 | [10 empty] | 5.4729 | FY41 | [10 empty] | 4.7492 | FY41 | [10 empty] | 0.26155 | FY41 | [10 empty] | 0 | [11 empty] | 0 | [11 empty] | 0 | [11 empty] | 0 | [11 empty] | 0
FY42 | [10 empty] | 41.8648 | FY42 | [10 empty] | 4.7117 | FY42 | [10 empty] | 5.4729 | FY42 | [10 empty] | 4.7492 | FY42 | [10 empty] | 0.26155 | FY42 | [10 empty] | 0 | [11 empty] | 0 | [11 empty] | 0 | [11 empty] | 0 | [11 empty] | 0
FY43 | [10 empty] | 41.8648 | FY43 | [10 empty] | 4.7117 | FY43 | [10 empty] | 5.4729 | FY43 | [10 empty] | 4.7492 | FY43 | [10 empty] | 0.26155 | FY43 | [10 empty] | 0 | [11 empty] | 0 | [11 empty] | 0 | [11 empty] | 0 | [11 empty] | 0
FY44 | [10 empty] | 41.8648 | FY44 | [10 empty] | 4.7117 | FY44 | [10 empty] | 5.4729 | FY44 | [10 empty] | 4.7492 | FY44 | [10 empty] | 0.26155 | FY44 | [10 empty] | 0 | [11 empty] | 0 | [11 empty] | 0 | [11 empty] | 0 | [11 empty] | 0
FY45 | [10 empty] | 41.8648 | FY45 | [10 empty] | 4.7117 | FY45 | [10 empty] | 5.4729 | FY45 | [10 empty] | 4.7492 | FY45 | [10 empty] | 0.26155 | FY45 | [10 empty] | 0 | [11 empty] | 0 | [11 empty] | 0 | [11 empty] | 0 | [11 empty] | 0
FY46 | [10 empty] | 41.8648 | FY46 | [10 empty] | 4.7117 | FY46 | [10 empty] | 5.4729 | FY46 | [10 empty] | 4.7492 | FY46 | [10 empty] | 0.26155 | FY46 | [10 empty] | 0 | [11 empty] | 0 | [11 empty] | 0 | [11 empty] | 0 | [11 empty] | 0
FY47 | [10 empty] | 41.8648 | FY47 | [10 empty] | 4.7117 | FY47 | [10 empty] | 5.4729 | FY47 | [10 empty] | 4.7492 | FY47 | [10 empty] | 0.26155 | FY47 | [10 empty] | 0 | [11 empty] | 0 | [11 empty] | 0 | [11 empty] | 0 | [11 empty] | 0
FY48 | [10 empty] | 41.8648 | FY48 | [10 empty] | 4.7117 | FY48 | [10 empty] | 5.4729 | FY48 | [10 empty] | 4.7492 | FY48 | [10 empty] | 0.26155 | FY48 | [10 empty] | 0 | [11 empty] | 0 | [11 empty] | 0 | [11 empty] | 0 | [11 empty] | 0
FY49 | [10 empty] | 41.8648 | FY49 | [10 empty] | 4.7117 | FY49 | [10 empty] | 5.4729 | FY49 | [10 empty] | 4.7492 | FY49 | [10 empty] | 0.26155 | FY49 | [10 empty] | 0 | [11 empty] | 0 | [11 empty] | 0 | [11 empty] | 0 | [11 empty] | 0
FY50 | [10 empty] | 41.8648 | FY50 | [10 empty] | 4.7117 | FY50 | [10 empty] | 5.4729 | FY50 | [10 empty] | 4.7492 | FY50 | [10 empty] | 0.26155 | FY50 | [10 empty] | 0 | [11 empty] | 0 | [11 empty] | 0 | [11 empty] | 0 | [11 empty] | 0
FY51 | [10 empty] | 41.8648 | FY51 | [10 empty] | 4.7117 | FY51 | [10 empty] | 5.4729 | FY51 | [10 empty] | 4.7492 | FY51 | [10 empty] | 0.26155 | FY51 | [10 empty] | 0 | [11 empty] | 0 | [11 empty] | 0 | [11 empty] | 0 | [11 empty] | 0
FY52 | [10 empty] | 41.8648 | FY52 | [10 empty] | 4.7117 | FY52 | [10 empty] | 5.4729 | FY52 | [10 empty] | 4.7492 | FY52 | [10 empty] | 0.26155 | FY52 | [10 empty] | 0 | [11 empty] | 0 | [11 empty] | 0 | [11 empty] | 0 | [11 empty] | 0
FY53 | [10 empty] | 41.8648 | FY53 | [10 empty] | 4.7117 | FY53 | [10 empty] | 5.4729 | FY53 | [10 empty] | 4.7492 | FY53 | [10 empty] | 0.26155 | FY53 | [10 empty] | 0 | [11 empty] | 0 | [11 empty] | 0 | [11 empty] | 0 | [11 empty] | 0
FY54 | [10 empty] | 41.8648 | FY54 | [10 empty] | 4.7117 | FY54 | [10 empty] | 5.4729 | FY54 | [10 empty] | 4.7492 | FY54 | [10 empty] | 0.26155 | FY54 | [10 empty] | 0 | [11 empty] | 0 | [11 empty] | 0 | [11 empty] | 0 | [11 empty] | 0

## 2.2.5 SupplyRisk$ High PoF
Option 1 - Do Nothing | [11 empty] | Option 2 - Augment MWTS-TGN with 19/4.75 AAC + Augment TGN-MFA with 19/4.75 AAC | [11 empty] | Option 3 - Augment MWTS-TGN with 19/4.75 AAC + New TGN-SLE 66kV line with 19/4.75 AAC | [11 empty] | Option 4 - Augment MWTS-TGN with 19/4.75 AAC + New Switching Station at Winnindoo (WISS) + Augment TGN-WISS wit | [11 empty] | Option 5 - Augment MWTS-TGN with 19/4.75 AAC + construct 30MW/150MWh BESS at BDSS | [11 empty] | Option 6 - | [11 empty] | Option 7 - | [11 empty] | Option 8 - | [11 empty] | Option 9 - | [11 empty] | Option 10 -
| Total Supply Risk $M by Asset and Year | [11 empty] | Total Supply Risk $M by Asset and Year | [11 empty] | Total Supply Risk $M by Asset and Year | [11 empty] | Total Supply Risk $M by Asset and Year | [11 empty] | Total Supply Risk $M by Asset and Year | [11 empty] | Total Supply Risk $M by Asset and Year | [11 empty] | Total Supply Risk $M by Asset and Year | [11 empty] | Total Supply Risk $M by Asset and Year | [11 empty] | Total Supply Risk $M by Asset and Year | [11 empty] | Total Supply Risk $M by Asset and Year
Source: | EaR_Augment East Gippsland 66kV Loop (MWTS-TGN-MFA lines)_summary.xlsx¦Output for AusNet NPV Model_PoF'!C42 | [11 empty] | EaR_Augment East Gippsland 66kV Loop (MWTS-TGN-MFA lines)_summary.xlsx¦Output for AusNet NPV Model_PoF'!D42 | [11 empty] | EaR_Augment East Gippsland 66kV Loop (MWTS-TGN-MFA lines)_summary.xlsx¦Output for AusNet NPV Model_PoF'!E42 | [11 empty] | EaR_Augment East Gippsland 66kV Loop (MWTS-TGN-MFA lines)_summary.xlsx¦Output for AusNet NPV Model_PoF'!F42 | [11 empty] | EaR_Augment East Gippsland 66kV Loop (MWTS-TGN-MFA lines)_summary.xlsx¦Output for AusNet NPV Model_PoF'!G42
Year | MWTS East 66kV Loop (W Fulham BESS) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Opt 1 Total | Year | MWTS East 66kV Loop (W Fulham BESS) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Opt 2 Total | Year | MWTS East 66kV Loop (W Fulham BESS) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Opt 3 Total | Year | MWTS East 66kV Loop (W Fulham BESS) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Opt 4 Total | Year | MWTS East 66kV Loop (W Fulham BESS) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Opt 5 Total | Year | MWTS East 66kV Loop (W Fulham BESS) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Opt 6 Total | Year | MWTS East 66kV Loop (W Fulham BESS) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Opt 7 Total | Year | MWTS East 66kV Loop (W Fulham BESS) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Opt 8 Total | Year | MWTS East 66kV Loop (W Fulham BESS) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Opt 9 Total | Year | MWTS East 66kV Loop (W Fulham BESS) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Opt 10 Total
FY25 | 1.1689 | [9 empty] | 1.1689 | FY25 | 1.1689 | [9 empty] | 1.1689 | FY25 | 1.1689 | [9 empty] | 1.1689 | FY25 | 1.1689 | [9 empty] | 1.1689 | FY25 | 1.1689 | [9 empty] | 1.1689 | FY25 | [10 empty] | 0
FY26 | 2.7468 | [9 empty] | 2.7468 | FY26 | 2.7468 | [9 empty] | 2.7468 | FY26 | 2.7468 | [9 empty] | 2.7468 | FY26 | 2.7468 | [9 empty] | 2.7468 | FY26 | 2.7468 | [9 empty] | 2.7468 | FY26
FY27 | 5.0069 | [9 empty] | 5.0069 | FY27 | 5.0069 | [9 empty] | 5.0069 | FY27 | 5.0069 | [9 empty] | 5.0069 | FY27 | 5.0069 | [9 empty] | 5.0069 | FY27 | 5.0069 | [9 empty] | 5.0069 | FY27
FY28 | 2.6191 | [9 empty] | 2.6191 | FY28 | 0.056157 | [9 empty] | 0.056157 | FY28 | 0.0090521 | [9 empty] | 0.0090521 | FY28 | 0.016817 | [9 empty] | 0.016817 | FY28 | 0.02637 | [9 empty] | 0.02637 | FY28
FY29 | 2.9116 | [9 empty] | 2.9116 | FY29 | 0.08424 | [9 empty] | 0.08424 | FY29 | 0.011996 | [9 empty] | 0.011996 | FY29 | 0.020194 | [9 empty] | 0.020194 | FY29 | 0.033891 | [9 empty] | 0.033891 | FY29
FY30 | 3.4015 | [9 empty] | 3.4015 | FY30 | 0.1313 | [9 empty] | 0.1313 | FY30 | 0.019592 | [9 empty] | 0.019592 | FY30 | 0.029112 | [9 empty] | 0.029112 | FY30 | 0.05053 | [9 empty] | 0.05053 | FY30
FY31 | 5.328 | [9 empty] | 5.328 | FY31 | 0.23894 | [9 empty] | 0.23894 | FY31 | 0.04544 | [9 empty] | 0.04544 | FY31 | 0.058536 | [9 empty] | 0.058536 | FY31 | 0.098788 | [9 empty] | 0.098788 | FY31
FY32 | 7.8888 | [9 empty] | 7.8888 | FY32 | 0.36529 | [9 empty] | 0.36529 | FY32 | 0.12299 | [9 empty] | 0.12299 | FY32 | 0.12491 | [9 empty] | 0.12491 | FY32 | 0.15518 | [9 empty] | 0.15518 | FY32
FY33 | 12.3699 | [9 empty] | 12.3699 | FY33 | 0.71 | [9 empty] | 0.71 | FY33 | 0.48123 | [9 empty] | 0.48123 | FY33 | 0.41824 | [9 empty] | 0.41824 | FY33 | 0.25382 | [9 empty] | 0.25382 | FY33
FY34 | 13.1377 | [9 empty] | 13.1377 | FY34 | 0.79608 | [9 empty] | 0.79608 | FY34 | 0.58331 | [9 empty] | 0.58331 | FY34 | 0.50396 | [9 empty] | 0.50396 | FY34 | 0.2702 | [9 empty] | 0.2702 | FY34
FY35 | 22.4288 | [9 empty] | 22.4288 | FY35 | 1.9212 | [9 empty] | 1.9212 | FY35 | 1.7965 | [9 empty] | 1.7965 | FY35 | 1.5766 | [9 empty] | 1.5766 | FY35 | 0.37447 | [9 empty] | 0.37447 | FY35
FY36 | 24.5174 | [9 empty] | 24.5174 | FY36 | 1.5819 | [9 empty] | 1.5819 | FY36 | 1.4184 | [9 empty] | 1.4184 | FY36 | 1.2528 | [9 empty] | 1.2528 | FY36 | 0.36819 | [9 empty] | 0.36819 | FY36
FY37 | 29.7433 | [9 empty] | 29.7433 | FY37 | 2.8485 | [9 empty] | 2.8485 | FY37 | 3.0149 | [9 empty] | 3.0149 | FY37 | 2.5753 | [9 empty] | 2.5753 | FY37 | 0.46411 | [9 empty] | 0.46411 | FY37
FY38 | 54.6888 | [9 empty] | 54.6888 | FY38 | 7.7498 | [9 empty] | 7.7498 | FY38 | 8.0065 | [9 empty] | 8.0065 | FY38 | 7.1909 | [9 empty] | 7.1909 | FY38 | 0.71118 | [9 empty] | 0.71118 | FY38
FY39 | 44.779 | [9 empty] | 44.779 | FY39 | 5.3689 | [9 empty] | 5.3689 | FY39 | 5.7332 | [9 empty] | 5.7332 | FY39 | 5.0384 | [9 empty] | 5.0384 | FY39 | 0.63791 | [9 empty] | 0.63791 | FY39
FY40 | [10 empty] | 44.779 | FY40 | [10 empty] | 5.3689 | FY40 | [10 empty] | 5.7332 | FY40 | [10 empty] | 5.0384 | FY40 | [10 empty] | 0.63791 | FY40 | [10 empty] | 0 | [11 empty] | 0 | [11 empty] | 0 | [11 empty] | 0 | [11 empty] | 0
FY41 | [10 empty] | 44.779 | FY41 | [10 empty] | 5.3689 | FY41 | [10 empty] | 5.7332 | FY41 | [10 empty] | 5.0384 | FY41 | [10 empty] | 0.63791 | FY41 | [10 empty] | 0 | [11 empty] | 0 | [11 empty] | 0 | [11 empty] | 0 | [11 empty] | 0
FY42 | [10 empty] | 44.779 | FY42 | [10 empty] | 5.3689 | FY42 | [10 empty] | 5.7332 | FY42 | [10 empty] | 5.0384 | FY42 | [10 empty] | 0.63791 | FY42 | [10 empty] | 0 | [11 empty] | 0 | [11 empty] | 0 | [11 empty] | 0 | [11 empty] | 0
FY43 | [10 empty] | 44.779 | FY43 | [10 empty] | 5.3689 | FY43 | [10 empty] | 5.7332 | FY43 | [10 empty] | 5.0384 | FY43 | [10 empty] | 0.63791 | FY43 | [10 empty] | 0 | [11 empty] | 0 | [11 empty] | 0 | [11 empty] | 0 | [11 empty] | 0
FY44 | [10 empty] | 44.779 | FY44 | [10 empty] | 5.3689 | FY44 | [10 empty] | 5.7332 | FY44 | [10 empty] | 5.0384 | FY44 | [10 empty] | 0.63791 | FY44 | [10 empty] | 0 | [11 empty] | 0 | [11 empty] | 0 | [11 empty] | 0 | [11 empty] | 0
FY45 | [10 empty] | 44.779 | FY45 | [10 empty] | 5.3689 | FY45 | [10 empty] | 5.7332 | FY45 | [10 empty] | 5.0384 | FY45 | [10 empty] | 0.63791 | FY45 | [10 empty] | 0 | [11 empty] | 0 | [11 empty] | 0 | [11 empty] | 0 | [11 empty] | 0
FY46 | [10 empty] | 44.779 | FY46 | [10 empty] | 5.3689 | FY46 | [10 empty] | 5.7332 | FY46 | [10 empty] | 5.0384 | FY46 | [10 empty] | 0.63791 | FY46 | [10 empty] | 0 | [11 empty] | 0 | [11 empty] | 0 | [11 empty] | 0 | [11 empty] | 0
FY47 | [10 empty] | 44.779 | FY47 | [10 empty] | 5.3689 | FY47 | [10 empty] | 5.7332 | FY47 | [10 empty] | 5.0384 | FY47 | [10 empty] | 0.63791 | FY47 | [10 empty] | 0 | [11 empty] | 0 | [11 empty] | 0 | [11 empty] | 0 | [11 empty] | 0
FY48 | [10 empty] | 44.779 | FY48 | [10 empty] | 5.3689 | FY48 | [10 empty] | 5.7332 | FY48 | [10 empty] | 5.0384 | FY48 | [10 empty] | 0.63791 | FY48 | [10 empty] | 0 | [11 empty] | 0 | [11 empty] | 0 | [11 empty] | 0 | [11 empty] | 0
FY49 | [10 empty] | 44.779 | FY49 | [10 empty] | 5.3689 | FY49 | [10 empty] | 5.7332 | FY49 | [10 empty] | 5.0384 | FY49 | [10 empty] | 0.63791 | FY49 | [10 empty] | 0 | [11 empty] | 0 | [11 empty] | 0 | [11 empty] | 0 | [11 empty] | 0
FY50 | [10 empty] | 44.779 | FY50 | [10 empty] | 5.3689 | FY50 | [10 empty] | 5.7332 | FY50 | [10 empty] | 5.0384 | FY50 | [10 empty] | 0.63791 | FY50 | [10 empty] | 0 | [11 empty] | 0 | [11 empty] | 0 | [11 empty] | 0 | [11 empty] | 0
FY51 | [10 empty] | 44.779 | FY51 | [10 empty] | 5.3689 | FY51 | [10 empty] | 5.7332 | FY51 | [10 empty] | 5.0384 | FY51 | [10 empty] | 0.63791 | FY51 | [10 empty] | 0 | [11 empty] | 0 | [11 empty] | 0 | [11 empty] | 0 | [11 empty] | 0
FY52 | [10 empty] | 44.779 | FY52 | [10 empty] | 5.3689 | FY52 | [10 empty] | 5.7332 | FY52 | [10 empty] | 5.0384 | FY52 | [10 empty] | 0.63791 | FY52 | [10 empty] | 0 | [11 empty] | 0 | [11 empty] | 0 | [11 empty] | 0 | [11 empty] | 0
FY53 | [10 empty] | 44.779 | FY53 | [10 empty] | 5.3689 | FY53 | [10 empty] | 5.7332 | FY53 | [10 empty] | 5.0384 | FY53 | [10 empty] | 0.63791 | FY53 | [10 empty] | 0 | [11 empty] | 0 | [11 empty] | 0 | [11 empty] | 0 | [11 empty] | 0
FY54 | [10 empty] | 44.779 | FY54 | [10 empty] | 5.3689 | FY54 | [10 empty] | 5.7332 | FY54 | [10 empty] | 5.0384 | FY54 | [10 empty] | 0.63791 | FY54 | [10 empty] | 0 | [11 empty] | 0 | [11 empty] | 0 | [11 empty] | 0 | [11 empty] | 0

## 2.3.1 Cost_Sum
$millions (real $2024) |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30
Real $2025 to real $2024 conversion factor |  | 95.36% |  |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Option 1 | bar: 3 FY27 to 4 FY28; 7 FY31
Build up
| Capex |  |  |  | 3 FY27: 0; 4 FY28: 0; 5 FY29: 0; 6 FY30: 0; 7 FY31: 0
| Opex |  |  |  | 3 FY27: 0; 4 FY28: 0; 5 FY29: 0; 6 FY30: 0; 7 FY31: 0
Summary
| Capex total |  |  |  | 3 FY27: 0; 4 FY28: 0; 5 FY29: 0; 6 FY30: 0; 7 FY31: 0
Opex total | bar: 3 FY27 to 7 FY31
Option 2 | bar: 3 FY27 to 4 FY28; 7 FY31
Capex build up
|  | Incl in capex forecast | Incl in economic analysis | Inc in Lifecycle Replacment | bar: 3 FY27 to 7 FY31
| Design | 1 | 1 | 0 | 3 FY27: C-I-C; 4 FY28: C-I-C; 5 FY29: C-I-C; 6 FY30: C-I-C; 7 FY31: C-I-C
| Internal labour | 1 | 1 | 1 | 3 FY27: C-I-C; 4 FY28: C-I-C; 5 FY29: C-I-C; 6 FY30: C-I-C; 7 FY31: C-I-C
| Materials | 1 | 1 | 0 | 3 FY27: C-I-C; 4 FY28: C-I-C; 5 FY29: C-I-C; 6 FY30: C-I-C; 7 FY31: C-I-C
| Contract costs | 1 | 1 | 1 | 3 FY27: C-I-C; 4 FY28: C-I-C; 5 FY29: C-I-C; 6 FY30: C-I-C; 7 FY31: C-I-C
| P(50) risk allowance | 1 | 1 | 1 | 3 FY27: C-I-C; 4 FY28: C-I-C; 5 FY29: C-I-C; 6 FY30: C-I-C; 7 FY31: C-I-C
| Overheads | 0 | 1 | 1 | 3 FY27: C-I-C; 4 FY28: C-I-C; 5 FY29: C-I-C; 6 FY30: C-I-C; 7 FY31: C-I-C
| Finance charges | 0 | 1 | 1 | 3 FY27: C-I-C; 4 FY28: C-I-C; 5 FY29: C-I-C; 6 FY30: C-I-C; 7 FY31: C-I-C
Capex Timing
[7 empty] | 1 | 0 | 0 | 0 | 0
Estimated Lifecycle Replacment Cost
[12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Opex build up
| Item 1 | [5 empty] | 0 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431
Item 2 | bar: 3 FY27 to 7 FY31
Item 3 | bar: 3 FY27 to 7 FY31
Summary
| Capex total |  |  |  | 0 | 0 | 40.4306 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Opex total |  |  |  | 0 | 0 | 0 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431
Option 3 | bar: 3 FY27 to 4 FY28; 7 FY31
Capex build up
|  | Incl in capex forecast | Incl in economic analysis | Inc in Lifecycle Replacment | bar: 3 FY27 to 7 FY31
| Design | 1 | 1 | 0 | 3 FY27: C-I-C; 4 FY28: C-I-C; 5 FY29: C-I-C; 6 FY30: C-I-C; 7 FY31: C-I-C
| Internal labour | 1 | 1 | 1 | 3 FY27: C-I-C; 4 FY28: C-I-C; 5 FY29: C-I-C; 6 FY30: C-I-C; 7 FY31: C-I-C
| Materials | 1 | 1 | 0 | 3 FY27: C-I-C; 4 FY28: C-I-C; 5 FY29: C-I-C; 6 FY30: C-I-C; 7 FY31: C-I-C
| Contract costs | 1 | 1 | 1 | 3 FY27: C-I-C; 4 FY28: C-I-C; 5 FY29: C-I-C; 6 FY30: C-I-C; 7 FY31: C-I-C
| P(50) risk allowance | 1 | 1 | 1 | 3 FY27: C-I-C; 4 FY28: C-I-C; 5 FY29: C-I-C; 6 FY30: C-I-C; 7 FY31: C-I-C
| Overheads | 0 | 1 | 1 | 3 FY27: C-I-C; 4 FY28: C-I-C; 5 FY29: C-I-C; 6 FY30: C-I-C; 7 FY31: C-I-C
| Finance charges | 0 | 1 | 1 | 3 FY27: C-I-C; 4 FY28: C-I-C; 5 FY29: C-I-C; 6 FY30: C-I-C; 7 FY31: C-I-C
Capex Timing
[7 empty] | 1 | 0 | 0 | 0 | 0
Estimated Lifecycle Replacment Cost
[12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Opex build up
| Item 1 | [5 empty] | 0 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582
Item 2 | bar: 3 FY27 to 7 FY31
Item 3 | bar: 3 FY27 to 7 FY31
Summary
| Capex total |  |  |  | 0 | 0 | 65.8197 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Opex total |  |  |  | 0 | 0 | 0 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582
Option 4 | bar: 3 FY27 to 4 FY28; 7 FY31
Capex build up
|  | Incl in capex forecast | Incl in economic analysis | Inc in Lifecycle Replacment | bar: 3 FY27 to 7 FY31
| Design | 1 | 1 | 0 | 3 FY27: C-I-C; 4 FY28: C-I-C; 5 FY29: C-I-C; 6 FY30: C-I-C; 7 FY31: C-I-C
| Internal labour | 1 | 1 | 1 | 3 FY27: C-I-C; 4 FY28: C-I-C; 5 FY29: C-I-C; 6 FY30: C-I-C; 7 FY31: C-I-C
| Materials | 1 | 1 | 0 | 3 FY27: C-I-C; 4 FY28: C-I-C; 5 FY29: C-I-C; 6 FY30: C-I-C; 7 FY31: C-I-C
| Contract costs | 1 | 1 | 1 | 3 FY27: C-I-C; 4 FY28: C-I-C; 5 FY29: C-I-C; 6 FY30: C-I-C; 7 FY31: C-I-C
| P(50) risk allowance | 1 | 1 | 1 | 3 FY27: C-I-C; 4 FY28: C-I-C; 5 FY29: C-I-C; 6 FY30: C-I-C; 7 FY31: C-I-C
| Overheads | 0 | 1 | 1 | 3 FY27: C-I-C; 4 FY28: C-I-C; 5 FY29: C-I-C; 6 FY30: C-I-C; 7 FY31: C-I-C
| Finance charges | 0 | 1 | 1 | 3 FY27: C-I-C; 4 FY28: C-I-C; 5 FY29: C-I-C; 6 FY30: C-I-C; 7 FY31: C-I-C
Capex Timing
[7 empty] | 1 | 0 | 0 | 0 | 0
Estimated Lifecycle Replacment Cost
[12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Opex build up
| Item 1 | [5 empty] | 0 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839
Item 2 | bar: 3 FY27 to 7 FY31
Item 3 | bar: 3 FY27 to 7 FY31
Summary
| Capex total |  |  |  | 0 | 0 | 58.3905 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Opex total |  |  |  | 0 | 0 | 0 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839
Option 5 | bar: 3 FY27 to 4 FY28; 7 FY31
Capex build up
|  | Incl in capex forecast | Incl in economic analysis | Inc in Lifecycle Replacment | bar: 3 FY27 to 7 FY31
| Design | 1 | 1 | 0 | 3 FY27: C-I-C; 4 FY28: C-I-C; 5 FY29: C-I-C; 6 FY30: C-I-C; 7 FY31: C-I-C
| Internal labour | 1 | 1 | 1 | 3 FY27: C-I-C; 4 FY28: C-I-C; 5 FY29: C-I-C; 6 FY30: C-I-C; 7 FY31: C-I-C
| Materials | 1 | 1 | 0.78286 | 3 FY27: C-I-C; 4 FY28: C-I-C; 5 FY29: C-I-C; 6 FY30: C-I-C; 7 FY31: C-I-C
| Contract costs | 1 | 1 | 1 | 3 FY27: C-I-C; 4 FY28: C-I-C; 5 FY29: C-I-C; 6 FY30: C-I-C; 7 FY31: C-I-C
| P(50) risk allowance | 1 | 1 | 1 | 3 FY27: C-I-C; 4 FY28: C-I-C; 5 FY29: C-I-C; 6 FY30: C-I-C; 7 FY31: C-I-C
| Overheads | 0 | 1 | 1 | 3 FY27: C-I-C; 4 FY28: C-I-C; 5 FY29: C-I-C; 6 FY30: C-I-C; 7 FY31: C-I-C
| Finance charges | 0 | 1 | 1 | 3 FY27: C-I-C; 4 FY28: C-I-C; 5 FY29: C-I-C; 6 FY30: C-I-C; 7 FY31: C-I-C
Capex Timing
[7 empty] | 1 | 0 | 0 | 0 | 0
Estimated Lifecycle Replacment Cost
[12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Opex build up
| Item 1 | [5 empty] | 0 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812
Item 2 | bar: 3 FY27 to 7 FY31
Item 3 | bar: 3 FY27 to 7 FY31
Summary
| Capex total |  |  |  | 0 | 0 | 78.12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78.12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Opex total |  |  |  | 0 | 0 | 0 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812
Option 6 | bar: 3 FY27 to 4 FY28; 7 FY31
Capex build up
|  | Incl in capex forecast | Incl in economic analysis | Inc in Lifecycle Replacment | bar: 3 FY27 to 7 FY31
| Design | 1 | 1 | 0 | 3 FY27: C-I-C; 4 FY28: C-I-C; 5 FY29: C-I-C; 6 FY30: C-I-C; 7 FY31: C-I-C
| Internal labour | 1 | 1 | 1 | 3 FY27: C-I-C; 4 FY28: C-I-C; 5 FY29: C-I-C; 6 FY30: C-I-C; 7 FY31: C-I-C
| Materials | 1 | 1 | 0 | 3 FY27: C-I-C; 4 FY28: C-I-C; 5 FY29: C-I-C; 6 FY30: C-I-C; 7 FY31: C-I-C
| Contract costs | 1 | 1 | 1 | 3 FY27: C-I-C; 4 FY28: C-I-C; 5 FY29: C-I-C; 6 FY30: C-I-C; 7 FY31: C-I-C
| P(50) risk allowance | 1 | 1 | 1 | 3 FY27: C-I-C; 4 FY28: C-I-C; 5 FY29: C-I-C; 6 FY30: C-I-C; 7 FY31: C-I-C
| Overheads | 0 | 1 | 1 | 3 FY27: C-I-C; 4 FY28: C-I-C; 5 FY29: C-I-C; 6 FY30: C-I-C; 7 FY31: C-I-C
| Finance charges | 0 | 1 | 1 | 3 FY27: C-I-C; 4 FY28: C-I-C; 5 FY29: C-I-C; 6 FY30: C-I-C; 7 FY31: C-I-C
Capex Timing
[7 empty] | 1 | 0 | 0 | 0 | 0
Estimated Lifecycle Replacment Cost
[12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Opex build up
| Item 1 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Item 2 | bar: 3 FY27 to 7 FY31
Item 3 | bar: 3 FY27 to 7 FY31
Summary
| Capex total |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Opex total |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 7
Capex build up
|  | Incl in capex forecast | Incl in economic analysis | Inc in Lifecycle Replacment | bar: 3 FY27 to 7 FY31
| Design | 1 | 1 | 0 | 3 FY27: C-I-C; 4 FY28: C-I-C; 5 FY29: C-I-C; 6 FY30: C-I-C; 7 FY31: C-I-C
| Internal labour | 1 | 1 | 1 | 3 FY27: C-I-C; 4 FY28: C-I-C; 5 FY29: C-I-C; 6 FY30: C-I-C; 7 FY31: C-I-C
| Materials | 1 | 1 | 0 | 3 FY27: C-I-C; 4 FY28: C-I-C; 5 FY29: C-I-C; 6 FY30: C-I-C; 7 FY31: C-I-C
| Contract costs | 1 | 1 | 1 | 3 FY27: C-I-C; 4 FY28: C-I-C; 5 FY29: C-I-C; 6 FY30: C-I-C; 7 FY31: C-I-C
| P(50) risk allowance | 1 | 1 | 1 | 3 FY27: C-I-C; 4 FY28: C-I-C; 5 FY29: C-I-C; 6 FY30: C-I-C; 7 FY31: C-I-C
| Overheads | 0 | 1 | 1 | 3 FY27: C-I-C; 4 FY28: C-I-C; 5 FY29: C-I-C; 6 FY30: C-I-C; 7 FY31: C-I-C
| Finance charges | 0 | 1 | 1 | 3 FY27: C-I-C; 4 FY28: C-I-C; 5 FY29: C-I-C; 6 FY30: C-I-C; 7 FY31: C-I-C
Capex Timing
[7 empty] | 1 | 0 | 0 | 0 | 0
Estimated Lifecycle Replacment Cost
[12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Opex build up
| Item 1 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Item 2 | bar: 3 FY27 to 7 FY31
Item 3 | bar: 3 FY27 to 7 FY31
Summary
| Capex total |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Opex total |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 8
Capex build up
|  | Incl in capex forecast | Incl in economic analysis | Inc in Lifecycle Replacment | bar: 3 FY27 to 7 FY31
| Design | 1 | 1 | 0 | 3 FY27: C-I-C; 4 FY28: C-I-C; 5 FY29: C-I-C; 6 FY30: C-I-C; 7 FY31: C-I-C
| Internal labour | 1 | 1 | 1 | 3 FY27: C-I-C; 4 FY28: C-I-C; 5 FY29: C-I-C; 6 FY30: C-I-C; 7 FY31: C-I-C
| Materials | 1 | 1 | 0 | 3 FY27: C-I-C; 4 FY28: C-I-C; 5 FY29: C-I-C; 6 FY30: C-I-C; 7 FY31: C-I-C
| Contract costs | 1 | 1 | 1 | 3 FY27: C-I-C; 4 FY28: C-I-C; 5 FY29: C-I-C; 6 FY30: C-I-C; 7 FY31: C-I-C
| P(50) risk allowance | 1 | 1 | 1 | 3 FY27: C-I-C; 4 FY28: C-I-C; 5 FY29: C-I-C; 6 FY30: C-I-C; 7 FY31: C-I-C
| Overheads | 0 | 1 | 1 | 3 FY27: C-I-C; 4 FY28: C-I-C; 5 FY29: C-I-C; 6 FY30: C-I-C; 7 FY31: C-I-C
| Finance charges | 0 | 1 | 1 | 3 FY27: C-I-C; 4 FY28: C-I-C; 5 FY29: C-I-C; 6 FY30: C-I-C; 7 FY31: C-I-C
Capex Timing
[7 empty] | 1 | 0 | 0 | 0 | 0
Estimated Lifecycle Replacment Cost
[12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Opex build up
| Item 1 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Item 2 | bar: 3 FY27 to 7 FY31
Item 3 | bar: 3 FY27 to 7 FY31
Summary
| Capex total |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Opex total |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 9
Capex build up
|  | Incl in capex forecast | Incl in economic analysis | Inc in Lifecycle Replacment | bar: 3 FY27 to 7 FY31
| Design | 1 | 1 | 0 | 3 FY27: C-I-C; 4 FY28: C-I-C; 5 FY29: C-I-C; 6 FY30: C-I-C; 7 FY31: C-I-C
| Internal labour | 1 | 1 | 1 | 3 FY27: C-I-C; 4 FY28: C-I-C; 5 FY29: C-I-C; 6 FY30: C-I-C; 7 FY31: C-I-C
| Materials | 1 | 1 | 0 | 3 FY27: C-I-C; 4 FY28: C-I-C; 5 FY29: C-I-C; 6 FY30: C-I-C; 7 FY31: C-I-C
| Contract costs | 1 | 1 | 1 | 3 FY27: C-I-C; 4 FY28: C-I-C; 5 FY29: C-I-C; 6 FY30: C-I-C; 7 FY31: C-I-C
| P(50) risk allowance | 1 | 1 | 1 | 3 FY27: C-I-C; 4 FY28: C-I-C; 5 FY29: C-I-C; 6 FY30: C-I-C; 7 FY31: C-I-C
| Overheads | 0 | 1 | 1 | 3 FY27: C-I-C; 4 FY28: C-I-C; 5 FY29: C-I-C; 6 FY30: C-I-C; 7 FY31: C-I-C
| Finance charges | 0 | 1 | 1 | 3 FY27: C-I-C; 4 FY28: C-I-C; 5 FY29: C-I-C; 6 FY30: C-I-C; 7 FY31: C-I-C
Capex Timing
[7 empty] | 1 | 0 | 0 | 0 | 0
Estimated Lifecycle Replacment Cost
[12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Opex build up
| Item 1 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Item 2 | bar: 3 FY27 to 7 FY31
Item 3 | bar: 3 FY27 to 7 FY31
Summary
| Capex total |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Opex total |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 10
Capex build up
|  | Incl in capex forecast | Incl in economic analysis | Inc in Lifecycle Replacment | bar: 3 FY27 to 7 FY31
| Design | 1 | 1 | 0 | 3 FY27: C-I-C; 4 FY28: C-I-C; 5 FY29: C-I-C; 6 FY30: C-I-C; 7 FY31: C-I-C
| Internal labour | 1 | 1 | 1 | 3 FY27: C-I-C; 4 FY28: C-I-C; 5 FY29: C-I-C; 6 FY30: C-I-C; 7 FY31: C-I-C
| Materials | 1 | 1 | 0 | 3 FY27: C-I-C; 4 FY28: C-I-C; 5 FY29: C-I-C; 6 FY30: C-I-C; 7 FY31: C-I-C
| Contract costs | 1 | 1 | 1 | 3 FY27: C-I-C; 4 FY28: C-I-C; 5 FY29: C-I-C; 6 FY30: C-I-C; 7 FY31: C-I-C
| P(50) risk allowance | 1 | 1 | 1 | 3 FY27: C-I-C; 4 FY28: C-I-C; 5 FY29: C-I-C; 6 FY30: C-I-C; 7 FY31: C-I-C
| Overheads | 0 | 1 | 1 | 3 FY27: C-I-C; 4 FY28: C-I-C; 5 FY29: C-I-C; 6 FY30: C-I-C; 7 FY31: C-I-C
| Finance charges | 0 | 1 | 1 | 3 FY27: C-I-C; 4 FY28: C-I-C; 5 FY29: C-I-C; 6 FY30: C-I-C; 7 FY31: C-I-C
Capex Timing
[7 empty] | 1 | 0 | 0 | 0 | 0
Estimated Lifecycle Replacment Cost
[12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Opex build up
| Item 1 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Item 2 | bar: 3 FY27 to 7 FY31
Item 3 | bar: 3 FY27 to 7 FY31
Summary
| Capex total |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Opex total |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## 2.3.2 Option2 Cost
Dollar Basis
Option 2 - Augment MWTS-TGN with 19/4.75 AAC + Augment TGN-MFA with 19/4.75 AAC | Real $2025
PROJECT EXPENDITURE FORECASTS | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | TOTAL | Design | 1 | 1 | C-I-C
DESIGN | 0 | 0 | 0 | 0 | 0 | 0 | C-I-C | Internal labour | 1 | 1 | C-I-C
INTERNAL LABOUR | 0 | 0 | 0 | 0 | 0 | 0 | C-I-C | Materials | 1 | 1 | C-I-C
MATERIALS | 0 | 0 | 0 | 0 | 0 | 0 | C-I-C | Contract costs | 1 | 1 | C-I-C
CONTRACT COSTS | 0 | 0 | 0 | 0 | 0 | 0 | C-I-C | P(50) risk allowance | 1 | 1 | C-I-C
PROJECT DIRECT EXPENDITURE | 0 | 0 | 0 | 0 | 0 | 0 | C-I-C | Overheads | 1 | 1 | C-I-C
P50 RISK | 0 | 0 | 0 | 0 | 0 | 0 | C-I-C | Finance charges | 0 | 0 | C-I-C
DIRECT + P50 RISK | 0 | 0 | 0 | 0 | 0 | 0 | C-I-C
OVERHEADS | 0 | 0 | 0 | 0 | 0 | 0 | C-I-C
FINANCE CHARGES | 0 | 0 | 0 | 0 | 0 | 0 | C-I-C
Direct + P50 RISK + INDIRECTS | 0 | 0 | 0 | 0 | 0 | 0 | C-I-C
P90-P50 RISK | 0 | 0 | 0 | 0 | 0 | 0 | C-I-C
DIRECT + P90 RISK + INDIRECTS | 0 | 0 | 0 | 0 | 0 | 0 | C-I-C

## 2.3.3 Option3 Cost
Dollar Basis
Option 3 - Augment MWTS-TGN with 19/4.75 AAC + New TGN-SLE 66kV line with 19/4.75 AAC | Real $2025
PROJECT EXPENDITURE FORECASTS | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | TOTAL | Design | 1 | 1 | C-I-C
DESIGN | 0 | 0 | 0 | 0 | 0 | 0 | C-I-C | Internal labour | 1 | 1 | C-I-C
INTERNAL LABOUR | 0 | 0 | 0 | 0 | 0 | 0 | C-I-C | Materials | 1 | 1 | C-I-C
MATERIALS | 0 | 0 | 0 | 0 | 0 | 0 | C-I-C | Contract costs | 1 | 1 | C-I-C
CONTRACT COSTS | 0 | 0 | 0 | 0 | 0 | 0 | C-I-C | P(50) risk allowance | 1 | 1 | C-I-C
PROJECT DIRECT EXPENDITURE | 0 | 0 | 0 | 0 | 0 | 0 | C-I-C | Overheads | 1 | 1 | C-I-C
P50 RISK | 0 | 0 | 0 | 0 | 0 | 0 | C-I-C | Finance charges | 0 | 0 | C-I-C
DIRECT + P50 RISK | 0 | 0 | 0 | 0 | 0 | 0 | C-I-C
OVERHEADS | 0 | 0 | 0 | 0 | 0 | 0 | C-I-C
FINANCE CHARGES | 0 | 0 | 0 | 0 | 0 | 0 | C-I-C
Direct + P50 RISK + INDIRECTS | 0 | 0 | 0 | 0 | 0 | 0 | C-I-C
P90-P50 RISK | 0 | 0 | 0 | 0 | 0 | 0 | C-I-C
DIRECT + P90 RISK + INDIRECTS | 0 | 0 | 0 | 0 | 0 | 0 | C-I-C

## 2.3.4 Option4 Cost
Dollar Basis
Option 4 - Augment MWTS-TGN with 19/4.75 AAC + New Switching Station at Winnindoo (WISS) + Augment TGN-WISS wit | Real $2025
PROJECT EXPENDITURE FORECASTS | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | TOTAL | Design | 1 | 1 | C-I-C
DESIGN | 0 | 0 | 0 | 0 | 0 | 0 | C-I-C | Internal labour | 1 | 1 | C-I-C
INTERNAL LABOUR | 0 | 0 | 0 | 0 | 0 | 0 | C-I-C | Materials | 1 | 1 | C-I-C
MATERIALS | 0 | 0 | 0 | 0 | 0 | 0 | C-I-C | Contract costs | 1 | 1 | C-I-C
CONTRACT COSTS | 0 | 0 | 0 | 0 | 0 | 0 | C-I-C | P(50) risk allowance | 1 | 1 | C-I-C
PROJECT DIRECT EXPENDITURE | 0 | 0 | 0 | 0 | 0 | 0 | C-I-C | Overheads | 1 | 1 | C-I-C
P50 RISK | 0 | 0 | 0 | 0 | 0 | 0 | C-I-C | Finance charges | 0 | 0 | C-I-C
DIRECT + P50 RISK | 0 | 0 | 0 | 0 | 0 | 0 | C-I-C
OVERHEADS | 0 | 0 | 0 | 0 | 0 | 0 | C-I-C
FINANCE CHARGES | 0 | 0 | 0 | 0 | 0 | 0 | C-I-C
Direct + P50 RISK + INDIRECTS | 0 | 0 | 0 | 0 | 0 | 0 | C-I-C
P90-P50 RISK | 0 | 0 | 0 | 0 | 0 | 0 | C-I-C
DIRECT + P90 RISK + INDIRECTS | 0 | 0 | 0 | 0 | 0 | 0 | C-I-C

## 2.3.5 Option5 Cost
Dollar Basis
Option 5 - Augment MWTS-TGN with 19/4.75 AAC + construct 30MW/150MWh BESS at BDSS | Real $2025
PROJECT EXPENDITURE FORECASTS | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | TOTAL | Design | 1 | 1 | C-I-C
DESIGN | 0 | 0 | 0 | 0 | 0 | 0 | C-I-C | Internal labour | 1 | 1 | C-I-C
INTERNAL LABOUR | 0 | 0 | 0 | 0 | 0 | 0 | C-I-C | Materials | 1 | 1 | C-I-C
MATERIALS | 0 | 0 | 0 | 0 | 0 | 0 | C-I-C | Contract costs | 1 | 1 | C-I-C
CONTRACT COSTS | 0 | 0 | 0 | 0 | 0 | 0 | C-I-C | P(50) risk allowance | 1 | 1 | C-I-C
PROJECT DIRECT EXPENDITURE | 0 | 0 | 0 | 0 | 0 | 0 | C-I-C | Overheads | 1 | 1 | C-I-C
P50 RISK | 0 | 0 | 0 | 0 | 0 | 0 | C-I-C | Finance charges | 0 | 0 | C-I-C
DIRECT + P50 RISK | 0 | 0 | 0 | 0 | 0 | 0 | C-I-C
OVERHEADS | 0 | 0 | 0 | 0 | 0 | 0 | C-I-C
FINANCE CHARGES | 0 | 0 | 0 | 0 | 0 | 0 | C-I-C
Direct + P50 RISK + INDIRECTS | 0 | 0 | 0 | 0 | 0 | 0 | C-I-C
P90-P50 RISK | 0 | 0 | 0 | 0 | 0 | 0 | C-I-C
DIRECT + P90 RISK + INDIRECTS | 0 | 0 | 0 | 0 | 0 | 0 | C-I-C

## 2.3.6 Option6 Cost (hidden)
Dollar Basis
Not Used | Real $2025
PROJECT EXPENDITURE FORECASTS | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | TOTAL | Design | 1 | 1 | 0
DESIGN | 0 | 0 | 0 | 0 | 0 | 0 |  | Internal labour | 1 | 1 | 0
INTERNAL LABOUR | 0 | 0 | 0 | 0 | 0 | 0 |  | Materials | 1 | 1 | 0
MATERIALS | 0 | 0 | 0 | 0 | 0 | 0 |  | Contract costs | 1 | 1 | 0
CONTRACT COSTS | 0 | 0 | 0 | 0 | 0 | 0 |  | P(50) risk allowance | 1 | 1 | 0
PROJECT DIRECT EXPENDITURE | 0 | 0 | 0 | 0 | 0 | 0 |  | Overheads | 1 | 1 | 0
P50 RISK | 0 | 0 | 0 | 0 | 0 | 0 |  | Finance charges | 0 | 0 | 0
DIRECT + P50 RISK | 0 | 0 | 0 | 0 | 0 | 0
OVERHEADS | 0 | 0 | 0 | 0 | 0 | 0
FINANCE CHARGES | 0 | 0 | 0 | 0 | 0 | 0
Direct + P50 RISK + INDIRECTS | 0 | 0 | 0 | 0 | 0 | 0
P90-P50 RISK | 0 | 0 | 0 | 0 | 0 | 0
DIRECT + P90 RISK + INDIRECTS | 0 | 0 | 0 | 0 | 0 | 0

## 2.3.7 Option7 Cost (hidden)
Dollar Basis
Not Used | Real $2025
PROJECT EXPENDITURE FORECASTS | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | TOTAL | Design | 1 | 1 | 0
DESIGN | 0 | 0 | 0 | 0 | 0 | 0 |  | Internal labour | 1 | 1 | 0
INTERNAL LABOUR | 0 | 0 | 0 | 0 | 0 | 0 |  | Materials | 1 | 1 | 0
MATERIALS | 0 | 0 | 0 | 0 | 0 | 0 |  | Contract costs | 1 | 1 | 0
CONTRACT COSTS | 0 | 0 | 0 | 0 | 0 | 0 |  | P(50) risk allowance | 1 | 1 | 0
PROJECT DIRECT EXPENDITURE | 0 | 0 | 0 | 0 | 0 | 0 |  | Overheads | 1 | 1 | 0
P50 RISK | 0 | 0 | 0 | 0 | 0 | 0 |  | Finance charges | 0 | 0 | 0
DIRECT + P50 RISK | 0 | 0 | 0 | 0 | 0 | 0
OVERHEADS | 0 | 0 | 0 | 0 | 0 | 0
FINANCE CHARGES | 0 | 0 | 0 | 0 | 0 | 0
Direct + P50 RISK + INDIRECTS | 0 | 0 | 0 | 0 | 0 | 0
P90-P50 RISK | 0 | 0 | 0 | 0 | 0 | 0
DIRECT + P90 RISK + INDIRECTS | 0 | 0 | 0 | 0 | 0 | 0

## 2.3.8 Option8 Cost (hidden)
Dollar Basis
Not Used | Real $2025
PROJECT EXPENDITURE FORECASTS | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | TOTAL | Design | 1 | 1 | 0
DESIGN | 0 | 0 | 0 | 0 | 0 | 0 |  | Internal labour | 1 | 1 | 0
INTERNAL LABOUR | 0 | 0 | 0 | 0 | 0 | 0 |  | Materials | 1 | 1 | 0
MATERIALS | 0 | 0 | 0 | 0 | 0 | 0 |  | Contract costs | 1 | 1 | 0
CONTRACT COSTS | 0 | 0 | 0 | 0 | 0 | 0 |  | P(50) risk allowance | 1 | 1 | 0
PROJECT DIRECT EXPENDITURE | 0 | 0 | 0 | 0 | 0 | 0 |  | Overheads | 1 | 1 | 0
P50 RISK | 0 | 0 | 0 | 0 | 0 | 0 |  | Finance charges | 0 | 0 | 0
DIRECT + P50 RISK | 0 | 0 | 0 | 0 | 0 | 0
OVERHEADS | 0 | 0 | 0 | 0 | 0 | 0
FINANCE CHARGES | 0 | 0 | 0 | 0 | 0 | 0
Direct + P50 RISK + INDIRECTS | 0 | 0 | 0 | 0 | 0 | 0
P90-P50 RISK | 0 | 0 | 0 | 0 | 0 | 0
DIRECT + P90 RISK + INDIRECTS | 0 | 0 | 0 | 0 | 0 | 0

## 2.3.9 Option9 Cost (hidden)
Dollar Basis
Not Used | Real $2025
PROJECT EXPENDITURE FORECASTS | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | TOTAL | Design | 1 | 1 | 0
DESIGN | 0 | 0 | 0 | 0 | 0 | 0 |  | Internal labour | 1 | 1 | 0
INTERNAL LABOUR | 0 | 0 | 0 | 0 | 0 | 0 |  | Materials | 1 | 1 | 0
MATERIALS | 0 | 0 | 0 | 0 | 0 | 0 |  | Contract costs | 1 | 1 | 0
CONTRACT COSTS | 0 | 0 | 0 | 0 | 0 | 0 |  | P(50) risk allowance | 1 | 1 | 0
PROJECT DIRECT EXPENDITURE | 0 | 0 | 0 | 0 | 0 | 0 |  | Overheads | 1 | 1 | 0
P50 RISK | 0 | 0 | 0 | 0 | 0 | 0 |  | Finance charges | 0 | 0 | 0
DIRECT + P50 RISK | 0 | 0 | 0 | 0 | 0 | 0
OVERHEADS | 0 | 0 | 0 | 0 | 0 | 0
FINANCE CHARGES | 0 | 0 | 0 | 0 | 0 | 0
Direct + P50 RISK + INDIRECTS | 0 | 0 | 0 | 0 | 0 | 0
P90-P50 RISK | 0 | 0 | 0 | 0 | 0 | 0
DIRECT + P90 RISK + INDIRECTS | 0 | 0 | 0 | 0 | 0 | 0

## 2.3.10 Option10 Cost (hidden)
Dollar Basis
Not Used | Real $2025
PROJECT EXPENDITURE FORECASTS | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | TOTAL | Design | 1 | 1 | 0
DESIGN | 0 | 0 | 0 | 0 | 0 | 0 |  | Internal labour | 1 | 1 | 0
INTERNAL LABOUR | 0 | 0 | 0 | 0 | 0 | 0 |  | Materials | 1 | 1 | 0
MATERIALS | 0 | 0 | 0 | 0 | 0 | 0 |  | Contract costs | 1 | 1 | 0
CONTRACT COSTS | 0 | 0 | 0 | 0 | 0 | 0 |  | P(50) risk allowance | 1 | 1 | 0
PROJECT DIRECT EXPENDITURE | 0 | 0 | 0 | 0 | 0 | 0 |  | Overheads | 1 | 1 | 0
P50 RISK | 0 | 0 | 0 | 0 | 0 | 0 |  | Finance charges | 0 | 0 | 0
DIRECT + P50 RISK | 0 | 0 | 0 | 0 | 0 | 0
OVERHEADS | 0 | 0 | 0 | 0 | 0 | 0
FINANCE CHARGES | 0 | 0 | 0 | 0 | 0 | 0
Direct + P50 RISK + INDIRECTS | 0 | 0 | 0 | 0 | 0 | 0
P90-P50 RISK | 0 | 0 | 0 | 0 | 0 | 0
DIRECT + P90 RISK + INDIRECTS | 0 | 0 | 0 | 0 | 0 | 0

## 3.1 NPV
Economic inputs and assumptions
Scenario | Discount rate | Central
| Cost | Central
| VCR | Central
|  | Central | Lower bound | Upper bound
| Discount rate | 5.56% | 4.11% | 7%
| Cost | 100% | 80% | 120%
| VCR | 100% | 80% | 120%
Asset life for calculating annualised capex (years) | Option 1 | 45
| Option 2 | 45
| Option 3 | 45
| Option 4 | 45
| Option 5 | 15
| Option 6 | 45
| Option 7 | 0
| Option 8 | 0
| Option 9 | 0
| Option 10 | 0
|  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30
|  |  |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Outputs | bar: 3 FY27; 7 FY31
Option 1
| Discounted | Undiscounted
| 0 | 0 | Capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Opex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Reduction in unserved energy | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Net benefit | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | EUE Value ($m, real $2024) | 1.1137 | 2.6361 | 4.8351 | 2.3613 | 2.5897 | 2.9899 | 4.739 | 7.1467 | 11.4165 | 12.1547 | 21.27 | 23.3412 | 28.4421 | 53.1535 | 43.3219 | 43.3219 | 43.3219 | 43.3219 | 43.3219 | 43.3219 | 43.3219 | 43.3219 | 43.3219 | 43.3219 | 43.3219 | 43.3219 | 43.3219 | 43.3219 | 43.3219 | 43.3219
Option 2
Determining Optimal Timing: | Discounted | Undiscounted
| 36.2837 | 40.4306 | Capex | 0 | 0 | 40.4306 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 5.0117 | 10.9163 | Opex | 0 | 0 | 0 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431
| 285.4829 | 767.3772 | Reduction in unserved energy | 0 | 0 | 0 | 2.3239 | 2.5336 | 2.9024 | 4.5797 | 6.8971 | 10.8805 | 11.5418 | 19.5847 | 21.9902 | 25.875 | 45.7618 | 38.2817 | 38.2817 | 38.2817 | 38.2817 | 38.2817 | 38.2817 | 38.2817 | 38.2817 | 38.2817 | 38.2817 | 38.2817 | 38.2817 | 38.2817 | 38.2817 | 38.2817 | 38.2817
| 244.1875 | 716.0304 | Net benefit | 0 | 0 | -40.4306 | 1.9196 | 2.1293 | 2.4981 | 4.1754 | 6.4928 | 10.4762 | 11.1375 | 19.1804 | 21.5859 | 25.4707 | 45.3575 | 37.8774 | 37.8774 | 37.8774 | 37.8774 | 37.8774 | 37.8774 | 37.8774 | 37.8774 | 37.8774 | 37.8774 | 37.8774 | 37.8774 | 37.8774 | 37.8774 | 37.8774 | 37.8774
|  |  | EUE Value ($m, real $2024) | 1.1137 | 2.6361 | 4.8351 | 0.037438 | 0.05616 | 0.087536 | 0.15929 | 0.24956 | 0.53594 | 0.61292 | 1.6853 | 1.3511 | 2.5671 | 7.3917 | 5.0403 | 5.0403 | 5.0403 | 5.0403 | 5.0403 | 5.0403 | 5.0403 | 5.0403 | 5.0403 | 5.0403 | 5.0403 | 5.0403 | 5.0403 | 5.0403 | 5.0403 | 5.0403
|  |  | Annualised capex | 0 | 0 | 2.2111 | 2.2111 | 2.2111 | 2.2111 | 2.2111 | 2.2111 | 2.2111 | 2.2111 | 2.2111 | 2.2111 | 2.2111 | 2.2111 | 2.2111 | 2.2111 | 2.2111 | 2.2111 | 2.2111 | 2.2111 | 2.2111 | 2.2111 | 2.2111 | 2.2111 | 2.2111 | 2.2111 | 2.2111 | 2.2111 | 2.2111 | 2.2111
|  |  | Annualised cost (capex+opex) | 0 | 0 | 2.2111 | 2.6154 | 2.6154 | 2.6154 | 2.6154 | 2.6154 | 2.6154 | 2.6154 | 2.6154 | 2.6154 | 2.6154 | 2.6154 | 2.6154 | 2.6154 | 2.6154 | 2.6154 | 2.6154 | 2.6154 | 2.6154 | 2.6154 | 2.6154 | 2.6154 | 2.6154 | 2.6154 | 2.6154 | 2.6154 | 2.6154 | 2.6154
|  |  | Optimal timing (interim calc) | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  |  | Optimal timing | - | - | - | - | - | Yes | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Adjusted For Optimal Timing: | 32.5621 | 40.4306 | Capex | 0 | 0 | 0 | 0 | 40.4306 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 4.3424 | 10.1076 | Opex | 0 | 0 | 0 | 0 | 0 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431
| 281.4667 | 762.5197 | Reduction in unserved energy | 0 | 0 | 0 | 0 | 0 | 2.9024 | 4.5797 | 6.8971 | 10.8805 | 11.5418 | 19.5847 | 21.9902 | 25.875 | 45.7618 | 38.2817 | 38.2817 | 38.2817 | 38.2817 | 38.2817 | 38.2817 | 38.2817 | 38.2817 | 38.2817 | 38.2817 | 38.2817 | 38.2817 | 38.2817 | 38.2817 | 38.2817 | 38.2817
| 244.5622 | 711.9815 | Net benefit | 0 | 0 | 0 | 0 | -40.4306 | 2.4981 | 4.1754 | 6.4928 | 10.4762 | 11.1375 | 19.1804 | 21.5859 | 25.4707 | 45.3575 | 37.8774 | 37.8774 | 37.8774 | 37.8774 | 37.8774 | 37.8774 | 37.8774 | 37.8774 | 37.8774 | 37.8774 | 37.8774 | 37.8774 | 37.8774 | 37.8774 | 37.8774 | 37.8774
Option 3
Determining Optimal Timing: | Discounted | Undiscounted
| 59.0686 | 65.8197 | Capex | 0 | 0 | 65.8197 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 8.159 | 17.7713 | Opex | 0 | 0 | 0 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582
| 282.5957 | 758.1624 | Reduction in unserved energy | 0 | 0 | 0 | 2.3553 | 2.5817 | 2.9769 | 4.7087 | 7.0505 | 10.9843 | 11.6243 | 19.5528 | 22.0004 | 25.5289 | 45.2961 | 37.7189 | 37.7189 | 37.7189 | 37.7189 | 37.7189 | 37.7189 | 37.7189 | 37.7189 | 37.7189 | 37.7189 | 37.7189 | 37.7189 | 37.7189 | 37.7189 | 37.7189 | 37.7189
| 215.3681 | 674.5714 | Net benefit | 0 | 0 | -65.8197 | 1.6971 | 1.9235 | 2.3187 | 4.0505 | 6.3923 | 10.3261 | 10.9661 | 18.8946 | 21.3422 | 24.8707 | 44.6379 | 37.0607 | 37.0607 | 37.0607 | 37.0607 | 37.0607 | 37.0607 | 37.0607 | 37.0607 | 37.0607 | 37.0607 | 37.0607 | 37.0607 | 37.0607 | 37.0607 | 37.0607 | 37.0607
|  |  | EUE Value ($m, real $2024) | 1.1137 | 2.6361 | 4.8351 | 0.0060347 | 0.0079976 | 0.013061 | 0.030296 | 0.09615 | 0.43224 | 0.53044 | 1.7172 | 1.3408 | 2.9132 | 7.8574 | 5.603 | 5.603 | 5.603 | 5.603 | 5.603 | 5.603 | 5.603 | 5.603 | 5.603 | 5.603 | 5.603 | 5.603 | 5.603 | 5.603 | 5.603 | 5.603
|  |  | Annualised capex | 0 | 0 | 3.5996 | 3.5996 | 3.5996 | 3.5996 | 3.5996 | 3.5996 | 3.5996 | 3.5996 | 3.5996 | 3.5996 | 3.5996 | 3.5996 | 3.5996 | 3.5996 | 3.5996 | 3.5996 | 3.5996 | 3.5996 | 3.5996 | 3.5996 | 3.5996 | 3.5996 | 3.5996 | 3.5996 | 3.5996 | 3.5996 | 3.5996 | 3.5996
|  |  | Annualised cost (capex+opex) | 0 | 0 | 3.5996 | 4.2578 | 4.2578 | 4.2578 | 4.2578 | 4.2578 | 4.2578 | 4.2578 | 4.2578 | 4.2578 | 4.2578 | 4.2578 | 4.2578 | 4.2578 | 4.2578 | 4.2578 | 4.2578 | 4.2578 | 4.2578 | 4.2578 | 4.2578 | 4.2578 | 4.2578 | 4.2578 | 4.2578 | 4.2578 | 4.2578 | 4.2578
|  |  | Optimal timing (interim calc) | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  |  | Optimal timing | - | - | - | - | - | - | Yes | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Adjusted For Optimal Timing: | 50.2179 | 65.8197 | Capex | 0 | 0 | 0 | 0 | 0 | 65.8197 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 6.5671 | 15.7967 | Opex | 0 | 0 | 0 | 0 | 0 | 0 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582
| 276.2428 | 750.2485 | Reduction in unserved energy | 0 | 0 | 0 | 0 | 0 | 0 | 4.7087 | 7.0505 | 10.9843 | 11.6243 | 19.5528 | 22.0004 | 25.5289 | 45.2961 | 37.7189 | 37.7189 | 37.7189 | 37.7189 | 37.7189 | 37.7189 | 37.7189 | 37.7189 | 37.7189 | 37.7189 | 37.7189 | 37.7189 | 37.7189 | 37.7189 | 37.7189 | 37.7189
| 219.4578 | 668.6321 | Net benefit | 0 | 0 | 0 | 0 | 0 | -65.8197 | 4.0505 | 6.3923 | 10.3261 | 10.9661 | 18.8946 | 21.3422 | 24.8707 | 44.6379 | 37.0607 | 37.0607 | 37.0607 | 37.0607 | 37.0607 | 37.0607 | 37.0607 | 37.0607 | 37.0607 | 37.0607 | 37.0607 | 37.0607 | 37.0607 | 37.0607 | 37.0607 | 37.0607
Option 4
Determining Optimal Timing: | Discounted | Undiscounted
| 52.4015 | 58.3905 | Capex | 0 | 0 | 58.3905 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 7.238 | 15.7654 | Opex | 0 | 0 | 0 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839
| 287.2117 | 771.333 | Reduction in unserved energy | 0 | 0 | 0 | 2.3501 | 2.5763 | 2.9705 | 4.6999 | 7.0538 | 11.0545 | 11.7111 | 19.7828 | 22.176 | 25.9808 | 46.1274 | 38.4281 | 38.4281 | 38.4281 | 38.4281 | 38.4281 | 38.4281 | 38.4281 | 38.4281 | 38.4281 | 38.4281 | 38.4281 | 38.4281 | 38.4281 | 38.4281 | 38.4281 | 38.4281
| 227.5722 | 697.1771 | Net benefit | 0 | 0 | -58.3905 | 1.7662 | 1.9924 | 2.3866 | 4.116 | 6.4699 | 10.4706 | 11.1272 | 19.1989 | 21.5921 | 25.3969 | 45.5435 | 37.8442 | 37.8442 | 37.8442 | 37.8442 | 37.8442 | 37.8442 | 37.8442 | 37.8442 | 37.8442 | 37.8442 | 37.8442 | 37.8442 | 37.8442 | 37.8442 | 37.8442 | 37.8442
|  |  | EUE Value ($m, real $2024) | 1.1137 | 2.6361 | 4.8351 | 0.011211 | 0.013463 | 0.019408 | 0.039024 | 0.092869 | 0.36202 | 0.4436 | 1.4872 | 1.1652 | 2.4614 | 7.0261 | 4.8938 | 4.8938 | 4.8938 | 4.8938 | 4.8938 | 4.8938 | 4.8938 | 4.8938 | 4.8938 | 4.8938 | 4.8938 | 4.8938 | 4.8938 | 4.8938 | 4.8938 | 4.8938
|  |  | Annualised capex | 0 | 0 | 3.1933 | 3.1933 | 3.1933 | 3.1933 | 3.1933 | 3.1933 | 3.1933 | 3.1933 | 3.1933 | 3.1933 | 3.1933 | 3.1933 | 3.1933 | 3.1933 | 3.1933 | 3.1933 | 3.1933 | 3.1933 | 3.1933 | 3.1933 | 3.1933 | 3.1933 | 3.1933 | 3.1933 | 3.1933 | 3.1933 | 3.1933 | 3.1933
|  |  | Annualised cost (capex+opex) | 0 | 0 | 3.1933 | 3.7772 | 3.7772 | 3.7772 | 3.7772 | 3.7772 | 3.7772 | 3.7772 | 3.7772 | 3.7772 | 3.7772 | 3.7772 | 3.7772 | 3.7772 | 3.7772 | 3.7772 | 3.7772 | 3.7772 | 3.7772 | 3.7772 | 3.7772 | 3.7772 | 3.7772 | 3.7772 | 3.7772 | 3.7772 | 3.7772 | 3.7772
|  |  | Optimal timing (interim calc) | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  |  | Optimal timing | - | - | - | - | - | - | Yes | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
[11 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19
Adjusted For Optimal Timing: | 44.5497 | 58.3905 | Capex | 0 | 0 | 0 | 0 | 0 | 58.3905 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 5.8259 | 14.0137 | Opex | 0 | 0 | 0 | 0 | 0 | 0 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839
| 280.8724 | 763.4361 | Reduction in unserved energy | 0 | 0 | 0 | 0 | 0 | 0 | 4.6999 | 7.0538 | 11.0545 | 11.7111 | 19.7828 | 22.176 | 25.9808 | 46.1274 | 38.4281 | 38.4281 | 38.4281 | 38.4281 | 38.4281 | 38.4281 | 38.4281 | 38.4281 | 38.4281 | 38.4281 | 38.4281 | 38.4281 | 38.4281 | 38.4281 | 38.4281 | 38.4281
| 230.4968 | 691.0319 | Net benefit | 0 | 0 | 0 | 0 | 0 | -58.3905 | 4.116 | 6.4699 | 10.4706 | 11.1272 | 19.1989 | 21.5921 | 25.3969 | 45.5435 | 37.8442 | 37.8442 | 37.8442 | 37.8442 | 37.8442 | 37.8442 | 37.8442 | 37.8442 | 37.8442 | 37.8442 | 37.8442 | 37.8442 | 37.8442 | 37.8442 | 37.8442 | 37.8442
Option 5
Determining Optimal Timing: | Discounted | Undiscounted
| 101.2441 | 156.2401 | Capex | 0 | 0 | 78.12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78.12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 9.6837 | 21.0924 | Opex | 0 | 0 | 0 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812
| 315.9423 | 853.6606 | Reduction in unserved energy | 0 | 0 | 0 | 2.3437 | 2.5671 | 2.9562 | 4.6731 | 7.0432 | 11.2473 | 11.9746 | 21.0204 | 23.0958 | 28.1321 | 52.6519 | 42.8722 | 42.8722 | 42.8722 | 42.8722 | 42.8722 | 42.8722 | 42.8722 | 42.8722 | 42.8722 | 42.8722 | 42.8722 | 42.8722 | 42.8722 | 42.8722 | 42.8722 | 42.8722
| 205.0145 | 676.3282 | Net benefit | 0 | 0 | -78.12 | 1.5625 | 1.7859 | 2.175 | 3.8919 | 6.262 | 10.4661 | 11.1934 | 20.2392 | 22.3146 | 27.3509 | 51.8707 | 42.091 | 42.091 | 42.091 | -36.029 | 42.091 | 42.091 | 42.091 | 42.091 | 42.091 | 42.091 | 42.091 | 42.091 | 42.091 | 42.091 | 42.091 | 42.091
|  |  | EUE Value ($m, real $2024) | 1.1137 | 2.6361 | 4.8351 | 0.01758 | 0.022594 | 0.033687 | 0.065859 | 0.10345 | 0.16921 | 0.18013 | 0.24965 | 0.24546 | 0.31 | 0.50155 | 0.44973 | 0.44973 | 0.44973 | 0.44973 | 0.44973 | 0.44973 | 0.44973 | 0.44973 | 0.44973 | 0.44973 | 0.44973 | 0.44973 | 0.44973 | 0.44973 | 0.44973 | 0.44973
|  |  | Annualised capex | 0 | 0 | 10.1268 | 10.1268 | 10.1268 | 10.1268 | 10.1268 | 10.1268 | 10.1268 | 10.1268 | 10.1268 | 10.1268 | 10.1268 | 10.1268 | 10.1268 | 10.1268 | 10.1268 | 10.1268 | 10.1268 | 10.1268 | 10.1268 | 10.1268 | 10.1268 | 10.1268 | 10.1268 | 10.1268 | 10.1268 | 10.1268 | 10.1268 | 10.1268
|  |  | Annualised cost (capex+opex) | 0 | 0 | 10.1268 | 10.908 | 10.908 | 10.908 | 10.908 | 10.908 | 10.908 | 10.908 | 10.908 | 10.908 | 10.908 | 10.908 | 10.908 | 10.908 | 10.908 | 10.908 | 10.908 | 10.908 | 10.908 | 10.908 | 10.908 | 10.908 | 10.908 | 10.908 | 10.908 | 10.908 | 10.908 | 10.908
|  |  | Optimal timing (interim calc) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  |  | Optimal timing | - | - | - | - | - | - | - | - | Yes | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Adjusted For Optimal Timing: | 77.2454 | 156.2401 | Capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78.12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78.12 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 6.6948 | 17.1864 | Opex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812
| 301.4266 | 834.0772 | Reduction in unserved energy | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11.2473 | 11.9746 | 21.0204 | 23.0958 | 28.1321 | 52.6519 | 42.8722 | 42.8722 | 42.8722 | 42.8722 | 42.8722 | 42.8722 | 42.8722 | 42.8722 | 42.8722 | 42.8722 | 42.8722 | 42.8722 | 42.8722 | 42.8722 | 42.8722 | 42.8722
| 217.4863 | 660.6507 | Net benefit | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -78.12 | 10.4661 | 11.1934 | 20.2392 | 22.3146 | 27.3509 | 51.8707 | 42.091 | 42.091 | 42.091 | 42.091 | 42.091 | 42.091 | 42.091 | 42.091 | -36.029 | 42.091 | 42.091 | 42.091 | 42.091 | 42.091 | 42.091 | 42.091
Option 6
Determining Optimal Timing: | Discounted | Undiscounted
| 0 | 0 | Capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Opex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Reduction in unserved energy | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Net benefit | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | EUE Value ($m, real $2024) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Annualised capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Annualised cost (capex+opex) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Optimal timing (interim calc) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Optimal timing | - | - | - | - | - | - | - | [19 empty] | - | - | - | - | bar: 1 to 19
Adjusted For Optimal Timing: | 0 | 0 | Capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Opex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Reduction in unserved energy | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Net benefit | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 7
Determining Optimal Timing: | Discounted | Undiscounted
| 0 | 0 | Capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Opex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Reduction in unserved energy | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Net benefit | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | EUE Value ($m, real $2024) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Annualised capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Annualised cost (capex+opex) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Optimal timing (interim calc) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Optimal timing | - | - | - | - | - | - | - | [19 empty] | - | - | - | - | bar: 1 to 19
Adjusted For Optimal Timing: | 0 | 0 | Capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Opex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Reduction in unserved energy | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Net benefit | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 8
Determining Optimal Timing: | Discounted | Undiscounted
| 0 | 0 | Capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Opex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Reduction in unserved energy | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Net benefit | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | EUE Value ($m, real $2024) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Annualised capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Annualised cost (capex+opex) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Optimal timing (interim calc) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Optimal timing | - | - | - | - | - | - | - | [19 empty] | - | - | - | - | bar: 1 to 19
Adjusted For Optimal Timing: | 0 | 0 | Capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Opex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Reduction in unserved energy | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Net benefit | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 9
Determining Optimal Timing: | Discounted | Undiscounted
| 0 | 0 | Capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Opex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Reduction in unserved energy | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Net benefit | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | EUE Value ($m, real $2024) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Annualised capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Annualised cost (capex+opex) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Optimal timing (interim calc) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Optimal timing | - | - | - | - | - | - | - | [19 empty] | - | - | - | - | bar: 1 to 19
Adjusted For Optimal Timing: | 0 | 0 | Capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Opex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Reduction in unserved energy | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Net benefit | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 10
Determining Optimal Timing: | Discounted | Undiscounted
| 0 | 0 | Capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Opex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Reduction in unserved energy | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Net benefit | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | EUE Value ($m, real $2024) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Annualised capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Annualised cost (capex+opex) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Optimal timing (interim calc) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Optimal timing | - | - | - | - | - | - | - | [19 empty] | - | - | - | - | bar: 1 to 19
Adjusted For Optimal Timing: | 0 | 0 | Capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Opex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Reduction in unserved energy | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Net benefit | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## 3.2.1 NPV (LoDiscount)
Economic inputs and assumptions
Scenario | Discount rate | Lower bound
| Cost | Central
| VCR | Central
|  | Central | Lower bound | Upper bound
| Discount rate | 5.56% | 4.11% | 7%
| Cost | 100% | 80% | 120%
| VCR | 100% | 80% | 120%
Asset life for calculating annualised capex (years) | Option 1 | 45
| Option 2 | 45
| Option 3 | 45
| Option 4 | 45
| Option 5 | 15
| Option 6 | 45
| Option 7 | 0
| Option 8 | 0
| Option 9 | 0
| Option 10 | 0
|  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30
|  |  |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Outputs | bar: 3 FY27; 7 FY31
Option 1
| Discounted | Undiscounted
| 0 | 0 | Capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Opex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Reduction in unserved energy | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Net benefit | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | EUE Value ($m, real $2024) | 1.1137 | 2.6361 | 4.8351 | 2.3613 | 2.5897 | 2.9899 | 4.739 | 7.1467 | 11.4165 | 12.1547 | 21.27 | 23.3412 | 28.4421 | 53.1535 | 43.3219 | 43.3219 | 43.3219 | 43.3219 | 43.3219 | 43.3219 | 43.3219 | 43.3219 | 43.3219 | 43.3219 | 43.3219 | 43.3219 | 43.3219 | 43.3219 | 43.3219 | 43.3219
Option 2
Determining Optimal Timing: | Discounted | Undiscounted
| 37.3014 | 40.4306 | Capex | 0 | 0 | 40.4306 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 6.0167 | 10.9163 | Opex | 0 | 0 | 0 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431
| 363.6903 | 767.3772 | Reduction in unserved energy | 0 | 0 | 0 | 2.3239 | 2.5336 | 2.9024 | 4.5797 | 6.8971 | 10.8805 | 11.5418 | 19.5847 | 21.9902 | 25.875 | 45.7618 | 38.2817 | 38.2817 | 38.2817 | 38.2817 | 38.2817 | 38.2817 | 38.2817 | 38.2817 | 38.2817 | 38.2817 | 38.2817 | 38.2817 | 38.2817 | 38.2817 | 38.2817 | 38.2817
| 320.3722 | 716.0304 | Net benefit | 0 | 0 | -40.4306 | 1.9196 | 2.1293 | 2.4981 | 4.1754 | 6.4928 | 10.4762 | 11.1375 | 19.1804 | 21.5859 | 25.4707 | 45.3575 | 37.8774 | 37.8774 | 37.8774 | 37.8774 | 37.8774 | 37.8774 | 37.8774 | 37.8774 | 37.8774 | 37.8774 | 37.8774 | 37.8774 | 37.8774 | 37.8774 | 37.8774 | 37.8774
|  |  | EUE Value ($m, real $2024) | 1.1137 | 2.6361 | 4.8351 | 0.037438 | 0.05616 | 0.087536 | 0.15929 | 0.24956 | 0.53594 | 0.61292 | 1.6853 | 1.3511 | 2.5671 | 7.3917 | 5.0403 | 5.0403 | 5.0403 | 5.0403 | 5.0403 | 5.0403 | 5.0403 | 5.0403 | 5.0403 | 5.0403 | 5.0403 | 5.0403 | 5.0403 | 5.0403 | 5.0403 | 5.0403
|  |  | Annualised capex | 0 | 0 | 2.2731 | 2.2731 | 2.2731 | 2.2731 | 2.2731 | 2.2731 | 2.2731 | 2.2731 | 2.2731 | 2.2731 | 2.2731 | 2.2731 | 2.2731 | 2.2731 | 2.2731 | 2.2731 | 2.2731 | 2.2731 | 2.2731 | 2.2731 | 2.2731 | 2.2731 | 2.2731 | 2.2731 | 2.2731 | 2.2731 | 2.2731 | 2.2731
|  |  | Annualised cost (capex+opex) | 0 | 0 | 2.2731 | 2.6774 | 2.6774 | 2.6774 | 2.6774 | 2.6774 | 2.6774 | 2.6774 | 2.6774 | 2.6774 | 2.6774 | 2.6774 | 2.6774 | 2.6774 | 2.6774 | 2.6774 | 2.6774 | 2.6774 | 2.6774 | 2.6774 | 2.6774 | 2.6774 | 2.6774 | 2.6774 | 2.6774 | 2.6774 | 2.6774 | 2.6774
|  |  | Optimal timing (interim calc) | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  |  | Optimal timing | - | - | - | - | - | Yes | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Adjusted For Optimal Timing: | 34.4144 | 40.4306 | Capex | 0 | 0 | 0 | 0 | 40.4306 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 5.3143 | 10.1076 | Opex | 0 | 0 | 0 | 0 | 0 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431
| 359.4744 | 762.5197 | Reduction in unserved energy | 0 | 0 | 0 | 0 | 0 | 2.9024 | 4.5797 | 6.8971 | 10.8805 | 11.5418 | 19.5847 | 21.9902 | 25.875 | 45.7618 | 38.2817 | 38.2817 | 38.2817 | 38.2817 | 38.2817 | 38.2817 | 38.2817 | 38.2817 | 38.2817 | 38.2817 | 38.2817 | 38.2817 | 38.2817 | 38.2817 | 38.2817 | 38.2817
| 319.7457 | 711.9815 | Net benefit | 0 | 0 | 0 | 0 | -40.4306 | 2.4981 | 4.1754 | 6.4928 | 10.4762 | 11.1375 | 19.1804 | 21.5859 | 25.4707 | 45.3575 | 37.8774 | 37.8774 | 37.8774 | 37.8774 | 37.8774 | 37.8774 | 37.8774 | 37.8774 | 37.8774 | 37.8774 | 37.8774 | 37.8774 | 37.8774 | 37.8774 | 37.8774 | 37.8774
Option 3
Determining Optimal Timing: | Discounted | Undiscounted
| 60.7255 | 65.8197 | Capex | 0 | 0 | 65.8197 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 9.795 | 17.7713 | Opex | 0 | 0 | 0 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582
| 359.8124 | 758.1624 | Reduction in unserved energy | 0 | 0 | 0 | 2.3553 | 2.5817 | 2.9769 | 4.7087 | 7.0505 | 10.9843 | 11.6243 | 19.5528 | 22.0004 | 25.5289 | 45.2961 | 37.7189 | 37.7189 | 37.7189 | 37.7189 | 37.7189 | 37.7189 | 37.7189 | 37.7189 | 37.7189 | 37.7189 | 37.7189 | 37.7189 | 37.7189 | 37.7189 | 37.7189 | 37.7189
| 289.2919 | 674.5714 | Net benefit | 0 | 0 | -65.8197 | 1.6971 | 1.9235 | 2.3187 | 4.0505 | 6.3923 | 10.3261 | 10.9661 | 18.8946 | 21.3422 | 24.8707 | 44.6379 | 37.0607 | 37.0607 | 37.0607 | 37.0607 | 37.0607 | 37.0607 | 37.0607 | 37.0607 | 37.0607 | 37.0607 | 37.0607 | 37.0607 | 37.0607 | 37.0607 | 37.0607 | 37.0607
|  |  | EUE Value ($m, real $2024) | 1.1137 | 2.6361 | 4.8351 | 0.0060347 | 0.0079976 | 0.013061 | 0.030296 | 0.09615 | 0.43224 | 0.53044 | 1.7172 | 1.3408 | 2.9132 | 7.8574 | 5.603 | 5.603 | 5.603 | 5.603 | 5.603 | 5.603 | 5.603 | 5.603 | 5.603 | 5.603 | 5.603 | 5.603 | 5.603 | 5.603 | 5.603 | 5.603
|  |  | Annualised capex | 0 | 0 | 3.7005 | 3.7005 | 3.7005 | 3.7005 | 3.7005 | 3.7005 | 3.7005 | 3.7005 | 3.7005 | 3.7005 | 3.7005 | 3.7005 | 3.7005 | 3.7005 | 3.7005 | 3.7005 | 3.7005 | 3.7005 | 3.7005 | 3.7005 | 3.7005 | 3.7005 | 3.7005 | 3.7005 | 3.7005 | 3.7005 | 3.7005 | 3.7005
|  |  | Annualised cost (capex+opex) | 0 | 0 | 3.7005 | 4.3587 | 4.3587 | 4.3587 | 4.3587 | 4.3587 | 4.3587 | 4.3587 | 4.3587 | 4.3587 | 4.3587 | 4.3587 | 4.3587 | 4.3587 | 4.3587 | 4.3587 | 4.3587 | 4.3587 | 4.3587 | 4.3587 | 4.3587 | 4.3587 | 4.3587 | 4.3587 | 4.3587 | 4.3587 | 4.3587 | 4.3587
|  |  | Optimal timing (interim calc) | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  |  | Optimal timing | - | - | - | - | - | - | Yes | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Adjusted For Optimal Timing: | 53.8138 | 65.8197 | Capex | 0 | 0 | 0 | 0 | 0 | 65.8197 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 8.1133 | 15.7967 | Opex | 0 | 0 | 0 | 0 | 0 | 0 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582
| 353.0938 | 750.2485 | Reduction in unserved energy | 0 | 0 | 0 | 0 | 0 | 0 | 4.7087 | 7.0505 | 10.9843 | 11.6243 | 19.5528 | 22.0004 | 25.5289 | 45.2961 | 37.7189 | 37.7189 | 37.7189 | 37.7189 | 37.7189 | 37.7189 | 37.7189 | 37.7189 | 37.7189 | 37.7189 | 37.7189 | 37.7189 | 37.7189 | 37.7189 | 37.7189 | 37.7189
| 291.1667 | 668.6321 | Net benefit | 0 | 0 | 0 | 0 | 0 | -65.8197 | 4.0505 | 6.3923 | 10.3261 | 10.9661 | 18.8946 | 21.3422 | 24.8707 | 44.6379 | 37.0607 | 37.0607 | 37.0607 | 37.0607 | 37.0607 | 37.0607 | 37.0607 | 37.0607 | 37.0607 | 37.0607 | 37.0607 | 37.0607 | 37.0607 | 37.0607 | 37.0607 | 37.0607
Option 4
Determining Optimal Timing: | Discounted | Undiscounted
| 53.8713 | 58.3905 | Capex | 0 | 0 | 58.3905 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 8.6894 | 15.7654 | Opex | 0 | 0 | 0 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839
| 365.7983 | 771.333 | Reduction in unserved energy | 0 | 0 | 0 | 2.3501 | 2.5763 | 2.9705 | 4.6999 | 7.0538 | 11.0545 | 11.7111 | 19.7828 | 22.176 | 25.9808 | 46.1274 | 38.4281 | 38.4281 | 38.4281 | 38.4281 | 38.4281 | 38.4281 | 38.4281 | 38.4281 | 38.4281 | 38.4281 | 38.4281 | 38.4281 | 38.4281 | 38.4281 | 38.4281 | 38.4281
| 303.2376 | 697.1771 | Net benefit | 0 | 0 | -58.3905 | 1.7662 | 1.9924 | 2.3866 | 4.116 | 6.4699 | 10.4706 | 11.1272 | 19.1989 | 21.5921 | 25.3969 | 45.5435 | 37.8442 | 37.8442 | 37.8442 | 37.8442 | 37.8442 | 37.8442 | 37.8442 | 37.8442 | 37.8442 | 37.8442 | 37.8442 | 37.8442 | 37.8442 | 37.8442 | 37.8442 | 37.8442
|  |  | EUE Value ($m, real $2024) | 1.1137 | 2.6361 | 4.8351 | 0.011211 | 0.013463 | 0.019408 | 0.039024 | 0.092869 | 0.36202 | 0.4436 | 1.4872 | 1.1652 | 2.4614 | 7.0261 | 4.8938 | 4.8938 | 4.8938 | 4.8938 | 4.8938 | 4.8938 | 4.8938 | 4.8938 | 4.8938 | 4.8938 | 4.8938 | 4.8938 | 4.8938 | 4.8938 | 4.8938 | 4.8938
|  |  | Annualised capex | 0 | 0 | 3.2828 | 3.2828 | 3.2828 | 3.2828 | 3.2828 | 3.2828 | 3.2828 | 3.2828 | 3.2828 | 3.2828 | 3.2828 | 3.2828 | 3.2828 | 3.2828 | 3.2828 | 3.2828 | 3.2828 | 3.2828 | 3.2828 | 3.2828 | 3.2828 | 3.2828 | 3.2828 | 3.2828 | 3.2828 | 3.2828 | 3.2828 | 3.2828
|  |  | Annualised cost (capex+opex) | 0 | 0 | 3.2828 | 3.8667 | 3.8667 | 3.8667 | 3.8667 | 3.8667 | 3.8667 | 3.8667 | 3.8667 | 3.8667 | 3.8667 | 3.8667 | 3.8667 | 3.8667 | 3.8667 | 3.8667 | 3.8667 | 3.8667 | 3.8667 | 3.8667 | 3.8667 | 3.8667 | 3.8667 | 3.8667 | 3.8667 | 3.8667 | 3.8667 | 3.8667
|  |  | Optimal timing (interim calc) | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  |  | Optimal timing | - | - | - | - | - | - | Yes | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
[11 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19
Adjusted For Optimal Timing: | 47.7397 | 58.3905 | Capex | 0 | 0 | 0 | 0 | 0 | 58.3905 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 7.1976 | 14.0137 | Opex | 0 | 0 | 0 | 0 | 0 | 0 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839
| 359.0941 | 763.4361 | Reduction in unserved energy | 0 | 0 | 0 | 0 | 0 | 0 | 4.6999 | 7.0538 | 11.0545 | 11.7111 | 19.7828 | 22.176 | 25.9808 | 46.1274 | 38.4281 | 38.4281 | 38.4281 | 38.4281 | 38.4281 | 38.4281 | 38.4281 | 38.4281 | 38.4281 | 38.4281 | 38.4281 | 38.4281 | 38.4281 | 38.4281 | 38.4281 | 38.4281
| 304.1568 | 691.0319 | Net benefit | 0 | 0 | 0 | 0 | 0 | -58.3905 | 4.116 | 6.4699 | 10.4706 | 11.1272 | 19.1989 | 21.5921 | 25.3969 | 45.5435 | 37.8442 | 37.8442 | 37.8442 | 37.8442 | 37.8442 | 37.8442 | 37.8442 | 37.8442 | 37.8442 | 37.8442 | 37.8442 | 37.8442 | 37.8442 | 37.8442 | 37.8442 | 37.8442
Option 5
Determining Optimal Timing: | Discounted | Undiscounted
| 111.4643 | 156.2401 | Capex | 0 | 0 | 78.12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78.12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 11.6255 | 21.0924 | Opex | 0 | 0 | 0 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812
| 403.1049 | 853.6606 | Reduction in unserved energy | 0 | 0 | 0 | 2.3437 | 2.5671 | 2.9562 | 4.6731 | 7.0432 | 11.2473 | 11.9746 | 21.0204 | 23.0958 | 28.1321 | 52.6519 | 42.8722 | 42.8722 | 42.8722 | 42.8722 | 42.8722 | 42.8722 | 42.8722 | 42.8722 | 42.8722 | 42.8722 | 42.8722 | 42.8722 | 42.8722 | 42.8722 | 42.8722 | 42.8722
| 280.0152 | 676.3282 | Net benefit | 0 | 0 | -78.12 | 1.5625 | 1.7859 | 2.175 | 3.8919 | 6.262 | 10.4661 | 11.1934 | 20.2392 | 22.3146 | 27.3509 | 51.8707 | 42.091 | 42.091 | 42.091 | -36.029 | 42.091 | 42.091 | 42.091 | 42.091 | 42.091 | 42.091 | 42.091 | 42.091 | 42.091 | 42.091 | 42.091 | 42.091
|  |  | EUE Value ($m, real $2024) | 1.1137 | 2.6361 | 4.8351 | 0.01758 | 0.022594 | 0.033687 | 0.065859 | 0.10345 | 0.16921 | 0.18013 | 0.24965 | 0.24546 | 0.31 | 0.50155 | 0.44973 | 0.44973 | 0.44973 | 0.44973 | 0.44973 | 0.44973 | 0.44973 | 0.44973 | 0.44973 | 0.44973 | 0.44973 | 0.44973 | 0.44973 | 0.44973 | 0.44973 | 0.44973
|  |  | Annualised capex | 0 | 0 | 11.149 | 11.149 | 11.149 | 11.149 | 11.149 | 11.149 | 11.149 | 11.149 | 11.149 | 11.149 | 11.149 | 11.149 | 11.149 | 11.149 | 11.149 | 11.149 | 11.149 | 11.149 | 11.149 | 11.149 | 11.149 | 11.149 | 11.149 | 11.149 | 11.149 | 11.149 | 11.149 | 11.149
|  |  | Annualised cost (capex+opex) | 0 | 0 | 11.149 | 11.9302 | 11.9302 | 11.9302 | 11.9302 | 11.9302 | 11.9302 | 11.9302 | 11.9302 | 11.9302 | 11.9302 | 11.9302 | 11.9302 | 11.9302 | 11.9302 | 11.9302 | 11.9302 | 11.9302 | 11.9302 | 11.9302 | 11.9302 | 11.9302 | 11.9302 | 11.9302 | 11.9302 | 11.9302 | 11.9302 | 11.9302
|  |  | Optimal timing (interim calc) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  |  | Optimal timing | - | - | - | - | - | - | - | - | - | Yes | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Adjusted For Optimal Timing: | 87.5348 | 156.2401 | Capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78.12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78.12 | 0 | 0 | 0 | 0 | 0 | 0
| 7.8608 | 16.4052 | Opex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812
| 379.2941 | 822.8299 | Reduction in unserved energy | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11.9746 | 21.0204 | 23.0958 | 28.1321 | 52.6519 | 42.8722 | 42.8722 | 42.8722 | 42.8722 | 42.8722 | 42.8722 | 42.8722 | 42.8722 | 42.8722 | 42.8722 | 42.8722 | 42.8722 | 42.8722 | 42.8722 | 42.8722 | 42.8722
| 283.8985 | 650.1847 | Net benefit | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -78.12 | 11.1934 | 20.2392 | 22.3146 | 27.3509 | 51.8707 | 42.091 | 42.091 | 42.091 | 42.091 | 42.091 | 42.091 | 42.091 | 42.091 | 42.091 | -36.029 | 42.091 | 42.091 | 42.091 | 42.091 | 42.091 | 42.091
Option 6
Determining Optimal Timing: | Discounted | Undiscounted
| 0 | 0 | Capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Opex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Reduction in unserved energy | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Net benefit | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | EUE Value ($m, real $2024) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Annualised capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Annualised cost (capex+opex) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Optimal timing (interim calc) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Optimal timing | - | - | - | - | - | - | - | [19 empty] | - | - | - | - | bar: 1 to 19
Adjusted For Optimal Timing: | 0 | 0 | Capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Opex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Reduction in unserved energy | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Net benefit | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 7
Determining Optimal Timing: | Discounted | Undiscounted
| 0 | 0 | Capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Opex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Reduction in unserved energy | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Net benefit | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | EUE Value ($m, real $2024) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Annualised capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Annualised cost (capex+opex) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Optimal timing (interim calc) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Optimal timing | - | - | - | - | - | - | - | [19 empty] | - | - | - | - | bar: 1 to 19
Adjusted For Optimal Timing: | 0 | 0 | Capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Opex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Reduction in unserved energy | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Net benefit | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 8
Determining Optimal Timing: | Discounted | Undiscounted
| 0 | 0 | Capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Opex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Reduction in unserved energy | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Net benefit | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | EUE Value ($m, real $2024) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Annualised capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Annualised cost (capex+opex) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Optimal timing (interim calc) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Optimal timing | - | - | - | - | - | - | - | [19 empty] | - | - | - | - | bar: 1 to 19
Adjusted For Optimal Timing: | 0 | 0 | Capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Opex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Reduction in unserved energy | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Net benefit | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 9
Determining Optimal Timing: | Discounted | Undiscounted
| 0 | 0 | Capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Opex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Reduction in unserved energy | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Net benefit | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | EUE Value ($m, real $2024) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Annualised capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Annualised cost (capex+opex) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Optimal timing (interim calc) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Optimal timing | - | - | - | - | - | - | - | [19 empty] | - | - | - | - | bar: 1 to 19
Adjusted For Optimal Timing: | 0 | 0 | Capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Opex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Reduction in unserved energy | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Net benefit | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 10
Determining Optimal Timing: | Discounted | Undiscounted
| 0 | 0 | Capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Opex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Reduction in unserved energy | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Net benefit | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | EUE Value ($m, real $2024) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Annualised capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Annualised cost (capex+opex) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Optimal timing (interim calc) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Optimal timing | - | - | - | - | - | - | - | [19 empty] | - | - | - | - | bar: 1 to 19
Adjusted For Optimal Timing: | 0 | 0 | Capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Opex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Reduction in unserved energy | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Net benefit | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## 3.2.2 NPV (HiDiscount)
Economic inputs and assumptions
Scenario | Discount rate | Upper bound
| Cost | Central
| VCR | Central
|  | Central | Lower bound | Upper bound
| Discount rate | 5.56% | 4.11% | 7%
| Cost | 100% | 80% | 120%
| VCR | 100% | 80% | 120%
Asset life for calculating annualised capex (years) | Option 1 | 45
| Option 2 | 45
| Option 3 | 45
| Option 4 | 45
| Option 5 | 15
| Option 6 | 45
| Option 7 | 0
| Option 8 | 0
| Option 9 | 0
| Option 10 | 0
|  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30
|  |  |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Outputs | bar: 3 FY27; 7 FY31
Option 1
| Discounted | Undiscounted
| 0 | 0 | Capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Opex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Reduction in unserved energy | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Net benefit | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | EUE Value ($m, real $2024) | 1.1137 | 2.6361 | 4.8351 | 2.3613 | 2.5897 | 2.9899 | 4.739 | 7.1467 | 11.4165 | 12.1547 | 21.27 | 23.3412 | 28.4421 | 53.1535 | 43.3219 | 43.3219 | 43.3219 | 43.3219 | 43.3219 | 43.3219 | 43.3219 | 43.3219 | 43.3219 | 43.3219 | 43.3219 | 43.3219 | 43.3219 | 43.3219 | 43.3219 | 43.3219
Option 2
Determining Optimal Timing: | Discounted | Undiscounted
| 35.3136 | 40.4306 | Capex | 0 | 0 | 40.4306 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 4.2329 | 10.9163 | Opex | 0 | 0 | 0 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431
| 226.8031 | 767.3772 | Reduction in unserved energy | 0 | 0 | 0 | 2.3239 | 2.5336 | 2.9024 | 4.5797 | 6.8971 | 10.8805 | 11.5418 | 19.5847 | 21.9902 | 25.875 | 45.7618 | 38.2817 | 38.2817 | 38.2817 | 38.2817 | 38.2817 | 38.2817 | 38.2817 | 38.2817 | 38.2817 | 38.2817 | 38.2817 | 38.2817 | 38.2817 | 38.2817 | 38.2817 | 38.2817
| 187.2565 | 716.0304 | Net benefit | 0 | 0 | -40.4306 | 1.9196 | 2.1293 | 2.4981 | 4.1754 | 6.4928 | 10.4762 | 11.1375 | 19.1804 | 21.5859 | 25.4707 | 45.3575 | 37.8774 | 37.8774 | 37.8774 | 37.8774 | 37.8774 | 37.8774 | 37.8774 | 37.8774 | 37.8774 | 37.8774 | 37.8774 | 37.8774 | 37.8774 | 37.8774 | 37.8774 | 37.8774
|  |  | EUE Value ($m, real $2024) | 1.1137 | 2.6361 | 4.8351 | 0.037438 | 0.05616 | 0.087536 | 0.15929 | 0.24956 | 0.53594 | 0.61292 | 1.6853 | 1.3511 | 2.5671 | 7.3917 | 5.0403 | 5.0403 | 5.0403 | 5.0403 | 5.0403 | 5.0403 | 5.0403 | 5.0403 | 5.0403 | 5.0403 | 5.0403 | 5.0403 | 5.0403 | 5.0403 | 5.0403 | 5.0403
|  |  | Annualised capex | 0 | 0 | 2.152 | 2.152 | 2.152 | 2.152 | 2.152 | 2.152 | 2.152 | 2.152 | 2.152 | 2.152 | 2.152 | 2.152 | 2.152 | 2.152 | 2.152 | 2.152 | 2.152 | 2.152 | 2.152 | 2.152 | 2.152 | 2.152 | 2.152 | 2.152 | 2.152 | 2.152 | 2.152 | 2.152
|  |  | Annualised cost (capex+opex) | 0 | 0 | 2.152 | 2.5563 | 2.5563 | 2.5563 | 2.5563 | 2.5563 | 2.5563 | 2.5563 | 2.5563 | 2.5563 | 2.5563 | 2.5563 | 2.5563 | 2.5563 | 2.5563 | 2.5563 | 2.5563 | 2.5563 | 2.5563 | 2.5563 | 2.5563 | 2.5563 | 2.5563 | 2.5563 | 2.5563 | 2.5563 | 2.5563 | 2.5563
|  |  | Optimal timing (interim calc) | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  |  | Optimal timing | - | - | - | - | - | Yes | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Adjusted For Optimal Timing: | 30.8443 | 40.4306 | Capex | 0 | 0 | 0 | 0 | 40.4306 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 3.5945 | 10.1076 | Opex | 0 | 0 | 0 | 0 | 0 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431
| 222.9733 | 762.5197 | Reduction in unserved energy | 0 | 0 | 0 | 0 | 0 | 2.9024 | 4.5797 | 6.8971 | 10.8805 | 11.5418 | 19.5847 | 21.9902 | 25.875 | 45.7618 | 38.2817 | 38.2817 | 38.2817 | 38.2817 | 38.2817 | 38.2817 | 38.2817 | 38.2817 | 38.2817 | 38.2817 | 38.2817 | 38.2817 | 38.2817 | 38.2817 | 38.2817 | 38.2817
| 188.5345 | 711.9815 | Net benefit | 0 | 0 | 0 | 0 | -40.4306 | 2.4981 | 4.1754 | 6.4928 | 10.4762 | 11.1375 | 19.1804 | 21.5859 | 25.4707 | 45.3575 | 37.8774 | 37.8774 | 37.8774 | 37.8774 | 37.8774 | 37.8774 | 37.8774 | 37.8774 | 37.8774 | 37.8774 | 37.8774 | 37.8774 | 37.8774 | 37.8774 | 37.8774 | 37.8774
Option 3
Determining Optimal Timing: | Discounted | Undiscounted
| 57.4895 | 65.8197 | Capex | 0 | 0 | 65.8197 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 6.8911 | 17.7713 | Opex | 0 | 0 | 0 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582
| 224.641 | 758.1624 | Reduction in unserved energy | 0 | 0 | 0 | 2.3553 | 2.5817 | 2.9769 | 4.7087 | 7.0505 | 10.9843 | 11.6243 | 19.5528 | 22.0004 | 25.5289 | 45.2961 | 37.7189 | 37.7189 | 37.7189 | 37.7189 | 37.7189 | 37.7189 | 37.7189 | 37.7189 | 37.7189 | 37.7189 | 37.7189 | 37.7189 | 37.7189 | 37.7189 | 37.7189 | 37.7189
| 160.2605 | 674.5714 | Net benefit | 0 | 0 | -65.8197 | 1.6971 | 1.9235 | 2.3187 | 4.0505 | 6.3923 | 10.3261 | 10.9661 | 18.8946 | 21.3422 | 24.8707 | 44.6379 | 37.0607 | 37.0607 | 37.0607 | 37.0607 | 37.0607 | 37.0607 | 37.0607 | 37.0607 | 37.0607 | 37.0607 | 37.0607 | 37.0607 | 37.0607 | 37.0607 | 37.0607 | 37.0607
|  |  | EUE Value ($m, real $2024) | 1.1137 | 2.6361 | 4.8351 | 0.0060347 | 0.0079976 | 0.013061 | 0.030296 | 0.09615 | 0.43224 | 0.53044 | 1.7172 | 1.3408 | 2.9132 | 7.8574 | 5.603 | 5.603 | 5.603 | 5.603 | 5.603 | 5.603 | 5.603 | 5.603 | 5.603 | 5.603 | 5.603 | 5.603 | 5.603 | 5.603 | 5.603 | 5.603
|  |  | Annualised capex | 0 | 0 | 3.5033 | 3.5033 | 3.5033 | 3.5033 | 3.5033 | 3.5033 | 3.5033 | 3.5033 | 3.5033 | 3.5033 | 3.5033 | 3.5033 | 3.5033 | 3.5033 | 3.5033 | 3.5033 | 3.5033 | 3.5033 | 3.5033 | 3.5033 | 3.5033 | 3.5033 | 3.5033 | 3.5033 | 3.5033 | 3.5033 | 3.5033 | 3.5033
|  |  | Annualised cost (capex+opex) | 0 | 0 | 3.5033 | 4.1615 | 4.1615 | 4.1615 | 4.1615 | 4.1615 | 4.1615 | 4.1615 | 4.1615 | 4.1615 | 4.1615 | 4.1615 | 4.1615 | 4.1615 | 4.1615 | 4.1615 | 4.1615 | 4.1615 | 4.1615 | 4.1615 | 4.1615 | 4.1615 | 4.1615 | 4.1615 | 4.1615 | 4.1615 | 4.1615 | 4.1615
|  |  | Optimal timing (interim calc) | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  |  | Optimal timing | - | - | - | - | - | - | Yes | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Adjusted For Optimal Timing: | 46.9285 | 65.8197 | Capex | 0 | 0 | 0 | 0 | 0 | 65.8197 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 5.3824 | 15.7967 | Opex | 0 | 0 | 0 | 0 | 0 | 0 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582
| 218.6264 | 750.2485 | Reduction in unserved energy | 0 | 0 | 0 | 0 | 0 | 0 | 4.7087 | 7.0505 | 10.9843 | 11.6243 | 19.5528 | 22.0004 | 25.5289 | 45.2961 | 37.7189 | 37.7189 | 37.7189 | 37.7189 | 37.7189 | 37.7189 | 37.7189 | 37.7189 | 37.7189 | 37.7189 | 37.7189 | 37.7189 | 37.7189 | 37.7189 | 37.7189 | 37.7189
| 166.3154 | 668.6321 | Net benefit | 0 | 0 | 0 | 0 | 0 | -65.8197 | 4.0505 | 6.3923 | 10.3261 | 10.9661 | 18.8946 | 21.3422 | 24.8707 | 44.6379 | 37.0607 | 37.0607 | 37.0607 | 37.0607 | 37.0607 | 37.0607 | 37.0607 | 37.0607 | 37.0607 | 37.0607 | 37.0607 | 37.0607 | 37.0607 | 37.0607 | 37.0607 | 37.0607
Option 4
Determining Optimal Timing: | Discounted | Undiscounted
| 51.0005 | 58.3905 | Capex | 0 | 0 | 58.3905 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 6.1133 | 15.7654 | Opex | 0 | 0 | 0 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839
| 228.2385 | 771.333 | Reduction in unserved energy | 0 | 0 | 0 | 2.3501 | 2.5763 | 2.9705 | 4.6999 | 7.0538 | 11.0545 | 11.7111 | 19.7828 | 22.176 | 25.9808 | 46.1274 | 38.4281 | 38.4281 | 38.4281 | 38.4281 | 38.4281 | 38.4281 | 38.4281 | 38.4281 | 38.4281 | 38.4281 | 38.4281 | 38.4281 | 38.4281 | 38.4281 | 38.4281 | 38.4281
| 171.1247 | 697.1771 | Net benefit | 0 | 0 | -58.3905 | 1.7662 | 1.9924 | 2.3866 | 4.116 | 6.4699 | 10.4706 | 11.1272 | 19.1989 | 21.5921 | 25.3969 | 45.5435 | 37.8442 | 37.8442 | 37.8442 | 37.8442 | 37.8442 | 37.8442 | 37.8442 | 37.8442 | 37.8442 | 37.8442 | 37.8442 | 37.8442 | 37.8442 | 37.8442 | 37.8442 | 37.8442
|  |  | EUE Value ($m, real $2024) | 1.1137 | 2.6361 | 4.8351 | 0.011211 | 0.013463 | 0.019408 | 0.039024 | 0.092869 | 0.36202 | 0.4436 | 1.4872 | 1.1652 | 2.4614 | 7.0261 | 4.8938 | 4.8938 | 4.8938 | 4.8938 | 4.8938 | 4.8938 | 4.8938 | 4.8938 | 4.8938 | 4.8938 | 4.8938 | 4.8938 | 4.8938 | 4.8938 | 4.8938 | 4.8938
|  |  | Annualised capex | 0 | 0 | 3.1079 | 3.1079 | 3.1079 | 3.1079 | 3.1079 | 3.1079 | 3.1079 | 3.1079 | 3.1079 | 3.1079 | 3.1079 | 3.1079 | 3.1079 | 3.1079 | 3.1079 | 3.1079 | 3.1079 | 3.1079 | 3.1079 | 3.1079 | 3.1079 | 3.1079 | 3.1079 | 3.1079 | 3.1079 | 3.1079 | 3.1079 | 3.1079
|  |  | Annualised cost (capex+opex) | 0 | 0 | 3.1079 | 3.6918 | 3.6918 | 3.6918 | 3.6918 | 3.6918 | 3.6918 | 3.6918 | 3.6918 | 3.6918 | 3.6918 | 3.6918 | 3.6918 | 3.6918 | 3.6918 | 3.6918 | 3.6918 | 3.6918 | 3.6918 | 3.6918 | 3.6918 | 3.6918 | 3.6918 | 3.6918 | 3.6918 | 3.6918 | 3.6918 | 3.6918
|  |  | Optimal timing (interim calc) | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  |  | Optimal timing | - | - | - | - | - | - | Yes | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
[11 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19
Adjusted For Optimal Timing: | 41.6316 | 58.3905 | Capex | 0 | 0 | 0 | 0 | 0 | 58.3905 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 4.7749 | 14.0137 | Opex | 0 | 0 | 0 | 0 | 0 | 0 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839
| 222.2367 | 763.4361 | Reduction in unserved energy | 0 | 0 | 0 | 0 | 0 | 0 | 4.6999 | 7.0538 | 11.0545 | 11.7111 | 19.7828 | 22.176 | 25.9808 | 46.1274 | 38.4281 | 38.4281 | 38.4281 | 38.4281 | 38.4281 | 38.4281 | 38.4281 | 38.4281 | 38.4281 | 38.4281 | 38.4281 | 38.4281 | 38.4281 | 38.4281 | 38.4281 | 38.4281
| 175.8302 | 691.0319 | Net benefit | 0 | 0 | 0 | 0 | 0 | -58.3905 | 4.116 | 6.4699 | 10.4706 | 11.1272 | 19.1989 | 21.5921 | 25.3969 | 45.5435 | 37.8442 | 37.8442 | 37.8442 | 37.8442 | 37.8442 | 37.8442 | 37.8442 | 37.8442 | 37.8442 | 37.8442 | 37.8442 | 37.8442 | 37.8442 | 37.8442 | 37.8442 | 37.8442
Option 5
Determining Optimal Timing: | Discounted | Undiscounted
| 92.9639 | 156.2401 | Capex | 0 | 0 | 78.12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78.12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 8.1789 | 21.0924 | Opex | 0 | 0 | 0 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812
| 250.5969 | 853.6606 | Reduction in unserved energy | 0 | 0 | 0 | 2.3437 | 2.5671 | 2.9562 | 4.6731 | 7.0432 | 11.2473 | 11.9746 | 21.0204 | 23.0958 | 28.1321 | 52.6519 | 42.8722 | 42.8722 | 42.8722 | 42.8722 | 42.8722 | 42.8722 | 42.8722 | 42.8722 | 42.8722 | 42.8722 | 42.8722 | 42.8722 | 42.8722 | 42.8722 | 42.8722 | 42.8722
| 149.4541 | 676.3282 | Net benefit | 0 | 0 | -78.12 | 1.5625 | 1.7859 | 2.175 | 3.8919 | 6.262 | 10.4661 | 11.1934 | 20.2392 | 22.3146 | 27.3509 | 51.8707 | 42.091 | 42.091 | 42.091 | -36.029 | 42.091 | 42.091 | 42.091 | 42.091 | 42.091 | 42.091 | 42.091 | 42.091 | 42.091 | 42.091 | 42.091 | 42.091
|  |  | EUE Value ($m, real $2024) | 1.1137 | 2.6361 | 4.8351 | 0.01758 | 0.022594 | 0.033687 | 0.065859 | 0.10345 | 0.16921 | 0.18013 | 0.24965 | 0.24546 | 0.31 | 0.50155 | 0.44973 | 0.44973 | 0.44973 | 0.44973 | 0.44973 | 0.44973 | 0.44973 | 0.44973 | 0.44973 | 0.44973 | 0.44973 | 0.44973 | 0.44973 | 0.44973 | 0.44973 | 0.44973
|  |  | Annualised capex | 0 | 0 | 9.2985 | 9.2985 | 9.2985 | 9.2985 | 9.2985 | 9.2985 | 9.2985 | 9.2985 | 9.2985 | 9.2985 | 9.2985 | 9.2985 | 9.2985 | 9.2985 | 9.2985 | 9.2985 | 9.2985 | 9.2985 | 9.2985 | 9.2985 | 9.2985 | 9.2985 | 9.2985 | 9.2985 | 9.2985 | 9.2985 | 9.2985 | 9.2985
|  |  | Annualised cost (capex+opex) | 0 | 0 | 9.2985 | 10.0797 | 10.0797 | 10.0797 | 10.0797 | 10.0797 | 10.0797 | 10.0797 | 10.0797 | 10.0797 | 10.0797 | 10.0797 | 10.0797 | 10.0797 | 10.0797 | 10.0797 | 10.0797 | 10.0797 | 10.0797 | 10.0797 | 10.0797 | 10.0797 | 10.0797 | 10.0797 | 10.0797 | 10.0797 | 10.0797 | 10.0797
|  |  | Optimal timing (interim calc) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  |  | Optimal timing | - | - | - | - | - | - | - | - | Yes | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Adjusted For Optimal Timing: | 66.282 | 156.2401 | Capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78.12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78.12 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 5.3812 | 17.1864 | Opex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812
| 237.1174 | 834.0772 | Reduction in unserved energy | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11.2473 | 11.9746 | 21.0204 | 23.0958 | 28.1321 | 52.6519 | 42.8722 | 42.8722 | 42.8722 | 42.8722 | 42.8722 | 42.8722 | 42.8722 | 42.8722 | 42.8722 | 42.8722 | 42.8722 | 42.8722 | 42.8722 | 42.8722 | 42.8722 | 42.8722
| 165.4543 | 660.6507 | Net benefit | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -78.12 | 10.4661 | 11.1934 | 20.2392 | 22.3146 | 27.3509 | 51.8707 | 42.091 | 42.091 | 42.091 | 42.091 | 42.091 | 42.091 | 42.091 | 42.091 | -36.029 | 42.091 | 42.091 | 42.091 | 42.091 | 42.091 | 42.091 | 42.091
Option 6
Determining Optimal Timing: | Discounted | Undiscounted
| 0 | 0 | Capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Opex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Reduction in unserved energy | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Net benefit | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | EUE Value ($m, real $2024) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Annualised capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Annualised cost (capex+opex) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Optimal timing (interim calc) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Optimal timing | - | - | - | - | - | - | - | [19 empty] | - | - | - | - | bar: 1 to 19
Adjusted For Optimal Timing: | 0 | 0 | Capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Opex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Reduction in unserved energy | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Net benefit | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 7
Determining Optimal Timing: | Discounted | Undiscounted
| 0 | 0 | Capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Opex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Reduction in unserved energy | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Net benefit | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | EUE Value ($m, real $2024) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Annualised capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Annualised cost (capex+opex) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Optimal timing (interim calc) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Optimal timing | - | - | - | - | - | - | - | [19 empty] | - | - | - | - | bar: 1 to 19
Adjusted For Optimal Timing: | 0 | 0 | Capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Opex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Reduction in unserved energy | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Net benefit | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 8
Determining Optimal Timing: | Discounted | Undiscounted
| 0 | 0 | Capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Opex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Reduction in unserved energy | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Net benefit | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | EUE Value ($m, real $2024) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Annualised capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Annualised cost (capex+opex) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Optimal timing (interim calc) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Optimal timing | - | - | - | - | - | - | - | [19 empty] | - | - | - | - | bar: 1 to 19
Adjusted For Optimal Timing: | 0 | 0 | Capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Opex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Reduction in unserved energy | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Net benefit | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 9
Determining Optimal Timing: | Discounted | Undiscounted
| 0 | 0 | Capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Opex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Reduction in unserved energy | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Net benefit | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | EUE Value ($m, real $2024) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Annualised capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Annualised cost (capex+opex) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Optimal timing (interim calc) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Optimal timing | - | - | - | - | - | - | - | [19 empty] | - | - | - | - | bar: 1 to 19
Adjusted For Optimal Timing: | 0 | 0 | Capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Opex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Reduction in unserved energy | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Net benefit | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 10
Determining Optimal Timing: | Discounted | Undiscounted
| 0 | 0 | Capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Opex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Reduction in unserved energy | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Net benefit | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | EUE Value ($m, real $2024) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Annualised capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Annualised cost (capex+opex) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Optimal timing (interim calc) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Optimal timing | - | - | - | - | - | - | - | [19 empty] | - | - | - | - | bar: 1 to 19
Adjusted For Optimal Timing: | 0 | 0 | Capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Opex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Reduction in unserved energy | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Net benefit | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## 3.2.3 NPV (LoCost)
Economic inputs and assumptions
Scenario | Discount rate | Central
| Cost | Lower bound
| VCR | Central
|  | Central | Lower bound | Upper bound
| Discount rate | 5.56% | 4.11% | 7%
| Cost | 100% | 80% | 120%
| VCR | 100% | 80% | 120%
Asset life for calculating annualised capex (years) | Option 1 | 45
| Option 2 | 45
| Option 3 | 45
| Option 4 | 45
| Option 5 | 15
| Option 6 | 45
| Option 7 | 0
| Option 8 | 0
| Option 9 | 0
| Option 10 | 0
|  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30
|  |  |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Outputs | bar: 3 FY27; 7 FY31
Option 1
| Discounted | Undiscounted
| 0 | 0 | Capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Opex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Reduction in unserved energy | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Net benefit | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | EUE Value ($m, real $2024) | 1.1137 | 2.6361 | 4.8351 | 2.3613 | 2.5897 | 2.9899 | 4.739 | 7.1467 | 11.4165 | 12.1547 | 21.27 | 23.3412 | 28.4421 | 53.1535 | 43.3219 | 43.3219 | 43.3219 | 43.3219 | 43.3219 | 43.3219 | 43.3219 | 43.3219 | 43.3219 | 43.3219 | 43.3219 | 43.3219 | 43.3219 | 43.3219 | 43.3219 | 43.3219
Option 2
Determining Optimal Timing: | Discounted | Undiscounted
| 29.0269 | 32.3445 | Capex | 0 | 0 | 32.3445 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 4.0094 | 8.733 | Opex | 0 | 0 | 0 | 0.32344 | 0.32344 | 0.32344 | 0.32344 | 0.32344 | 0.32344 | 0.32344 | 0.32344 | 0.32344 | 0.32344 | 0.32344 | 0.32344 | 0.32344 | 0.32344 | 0.32344 | 0.32344 | 0.32344 | 0.32344 | 0.32344 | 0.32344 | 0.32344 | 0.32344 | 0.32344 | 0.32344 | 0.32344 | 0.32344 | 0.32344
| 285.4829 | 767.3772 | Reduction in unserved energy | 0 | 0 | 0 | 2.3239 | 2.5336 | 2.9024 | 4.5797 | 6.8971 | 10.8805 | 11.5418 | 19.5847 | 21.9902 | 25.875 | 45.7618 | 38.2817 | 38.2817 | 38.2817 | 38.2817 | 38.2817 | 38.2817 | 38.2817 | 38.2817 | 38.2817 | 38.2817 | 38.2817 | 38.2817 | 38.2817 | 38.2817 | 38.2817 | 38.2817
| 252.4466 | 726.2997 | Net benefit | 0 | 0 | -32.3445 | 2.0004 | 2.2101 | 2.5789 | 4.2562 | 6.5736 | 10.5571 | 11.2183 | 19.2613 | 21.6667 | 25.5516 | 45.4384 | 37.9582 | 37.9582 | 37.9582 | 37.9582 | 37.9582 | 37.9582 | 37.9582 | 37.9582 | 37.9582 | 37.9582 | 37.9582 | 37.9582 | 37.9582 | 37.9582 | 37.9582 | 37.9582
|  |  | EUE Value ($m, real $2024) | 1.1137 | 2.6361 | 4.8351 | 0.037438 | 0.05616 | 0.087536 | 0.15929 | 0.24956 | 0.53594 | 0.61292 | 1.6853 | 1.3511 | 2.5671 | 7.3917 | 5.0403 | 5.0403 | 5.0403 | 5.0403 | 5.0403 | 5.0403 | 5.0403 | 5.0403 | 5.0403 | 5.0403 | 5.0403 | 5.0403 | 5.0403 | 5.0403 | 5.0403 | 5.0403
|  |  | Annualised capex | 0 | 0 | 1.7689 | 1.7689 | 1.7689 | 1.7689 | 1.7689 | 1.7689 | 1.7689 | 1.7689 | 1.7689 | 1.7689 | 1.7689 | 1.7689 | 1.7689 | 1.7689 | 1.7689 | 1.7689 | 1.7689 | 1.7689 | 1.7689 | 1.7689 | 1.7689 | 1.7689 | 1.7689 | 1.7689 | 1.7689 | 1.7689 | 1.7689 | 1.7689
|  |  | Annualised cost (capex+opex) | 0 | 0 | 1.7689 | 2.0923 | 2.0923 | 2.0923 | 2.0923 | 2.0923 | 2.0923 | 2.0923 | 2.0923 | 2.0923 | 2.0923 | 2.0923 | 2.0923 | 2.0923 | 2.0923 | 2.0923 | 2.0923 | 2.0923 | 2.0923 | 2.0923 | 2.0923 | 2.0923 | 2.0923 | 2.0923 | 2.0923 | 2.0923 | 2.0923 | 2.0923
|  |  | Optimal timing (interim calc) | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  |  | Optimal timing | - | - | - | Yes | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Adjusted For Optimal Timing: | 29.0269 | 32.3445 | Capex | 0 | 0 | 32.3445 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 4.0094 | 8.733 | Opex | 0 | 0 | 0 | 0.32344 | 0.32344 | 0.32344 | 0.32344 | 0.32344 | 0.32344 | 0.32344 | 0.32344 | 0.32344 | 0.32344 | 0.32344 | 0.32344 | 0.32344 | 0.32344 | 0.32344 | 0.32344 | 0.32344 | 0.32344 | 0.32344 | 0.32344 | 0.32344 | 0.32344 | 0.32344 | 0.32344 | 0.32344 | 0.32344 | 0.32344
| 285.4829 | 767.3772 | Reduction in unserved energy | 0 | 0 | 0 | 2.3239 | 2.5336 | 2.9024 | 4.5797 | 6.8971 | 10.8805 | 11.5418 | 19.5847 | 21.9902 | 25.875 | 45.7618 | 38.2817 | 38.2817 | 38.2817 | 38.2817 | 38.2817 | 38.2817 | 38.2817 | 38.2817 | 38.2817 | 38.2817 | 38.2817 | 38.2817 | 38.2817 | 38.2817 | 38.2817 | 38.2817
| 252.4466 | 726.2997 | Net benefit | 0 | 0 | -32.3445 | 2.0004 | 2.2101 | 2.5789 | 4.2562 | 6.5736 | 10.5571 | 11.2183 | 19.2613 | 21.6667 | 25.5516 | 45.4384 | 37.9582 | 37.9582 | 37.9582 | 37.9582 | 37.9582 | 37.9582 | 37.9582 | 37.9582 | 37.9582 | 37.9582 | 37.9582 | 37.9582 | 37.9582 | 37.9582 | 37.9582 | 37.9582
Option 3
Determining Optimal Timing: | Discounted | Undiscounted
| 47.2549 | 52.6557 | Capex | 0 | 0 | 52.6557 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 6.5272 | 14.2171 | Opex | 0 | 0 | 0 | 0.52656 | 0.52656 | 0.52656 | 0.52656 | 0.52656 | 0.52656 | 0.52656 | 0.52656 | 0.52656 | 0.52656 | 0.52656 | 0.52656 | 0.52656 | 0.52656 | 0.52656 | 0.52656 | 0.52656 | 0.52656 | 0.52656 | 0.52656 | 0.52656 | 0.52656 | 0.52656 | 0.52656 | 0.52656 | 0.52656 | 0.52656
| 282.5957 | 758.1624 | Reduction in unserved energy | 0 | 0 | 0 | 2.3553 | 2.5817 | 2.9769 | 4.7087 | 7.0505 | 10.9843 | 11.6243 | 19.5528 | 22.0004 | 25.5289 | 45.2961 | 37.7189 | 37.7189 | 37.7189 | 37.7189 | 37.7189 | 37.7189 | 37.7189 | 37.7189 | 37.7189 | 37.7189 | 37.7189 | 37.7189 | 37.7189 | 37.7189 | 37.7189 | 37.7189
| 228.8136 | 691.2896 | Net benefit | 0 | 0 | -52.6557 | 1.8287 | 2.0552 | 2.4503 | 4.1821 | 6.5239 | 10.4577 | 11.0977 | 19.0262 | 21.4739 | 25.0024 | 44.7695 | 37.1924 | 37.1924 | 37.1924 | 37.1924 | 37.1924 | 37.1924 | 37.1924 | 37.1924 | 37.1924 | 37.1924 | 37.1924 | 37.1924 | 37.1924 | 37.1924 | 37.1924 | 37.1924
|  |  | EUE Value ($m, real $2024) | 1.1137 | 2.6361 | 4.8351 | 0.0060347 | 0.0079976 | 0.013061 | 0.030296 | 0.09615 | 0.43224 | 0.53044 | 1.7172 | 1.3408 | 2.9132 | 7.8574 | 5.603 | 5.603 | 5.603 | 5.603 | 5.603 | 5.603 | 5.603 | 5.603 | 5.603 | 5.603 | 5.603 | 5.603 | 5.603 | 5.603 | 5.603 | 5.603
|  |  | Annualised capex | 0 | 0 | 2.8796 | 2.8796 | 2.8796 | 2.8796 | 2.8796 | 2.8796 | 2.8796 | 2.8796 | 2.8796 | 2.8796 | 2.8796 | 2.8796 | 2.8796 | 2.8796 | 2.8796 | 2.8796 | 2.8796 | 2.8796 | 2.8796 | 2.8796 | 2.8796 | 2.8796 | 2.8796 | 2.8796 | 2.8796 | 2.8796 | 2.8796 | 2.8796
|  |  | Annualised cost (capex+opex) | 0 | 0 | 2.8796 | 3.4062 | 3.4062 | 3.4062 | 3.4062 | 3.4062 | 3.4062 | 3.4062 | 3.4062 | 3.4062 | 3.4062 | 3.4062 | 3.4062 | 3.4062 | 3.4062 | 3.4062 | 3.4062 | 3.4062 | 3.4062 | 3.4062 | 3.4062 | 3.4062 | 3.4062 | 3.4062 | 3.4062 | 3.4062 | 3.4062 | 3.4062
|  |  | Optimal timing (interim calc) | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  |  | Optimal timing | - | - | - | - | - | - | Yes | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Adjusted For Optimal Timing: | 40.1743 | 52.6557 | Capex | 0 | 0 | 0 | 0 | 0 | 52.6557 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 5.2537 | 12.6374 | Opex | 0 | 0 | 0 | 0 | 0 | 0 | 0.52656 | 0.52656 | 0.52656 | 0.52656 | 0.52656 | 0.52656 | 0.52656 | 0.52656 | 0.52656 | 0.52656 | 0.52656 | 0.52656 | 0.52656 | 0.52656 | 0.52656 | 0.52656 | 0.52656 | 0.52656 | 0.52656 | 0.52656 | 0.52656 | 0.52656 | 0.52656 | 0.52656
| 276.2428 | 750.2485 | Reduction in unserved energy | 0 | 0 | 0 | 0 | 0 | 0 | 4.7087 | 7.0505 | 10.9843 | 11.6243 | 19.5528 | 22.0004 | 25.5289 | 45.2961 | 37.7189 | 37.7189 | 37.7189 | 37.7189 | 37.7189 | 37.7189 | 37.7189 | 37.7189 | 37.7189 | 37.7189 | 37.7189 | 37.7189 | 37.7189 | 37.7189 | 37.7189 | 37.7189
| 230.8148 | 684.9554 | Net benefit | 0 | 0 | 0 | 0 | 0 | -52.6557 | 4.1821 | 6.5239 | 10.4577 | 11.0977 | 19.0262 | 21.4739 | 25.0024 | 44.7695 | 37.1924 | 37.1924 | 37.1924 | 37.1924 | 37.1924 | 37.1924 | 37.1924 | 37.1924 | 37.1924 | 37.1924 | 37.1924 | 37.1924 | 37.1924 | 37.1924 | 37.1924 | 37.1924
Option 4
Determining Optimal Timing: | Discounted | Undiscounted
| 41.9212 | 46.7124 | Capex | 0 | 0 | 46.7124 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 5.7904 | 12.6123 | Opex | 0 | 0 | 0 | 0.46712 | 0.46712 | 0.46712 | 0.46712 | 0.46712 | 0.46712 | 0.46712 | 0.46712 | 0.46712 | 0.46712 | 0.46712 | 0.46712 | 0.46712 | 0.46712 | 0.46712 | 0.46712 | 0.46712 | 0.46712 | 0.46712 | 0.46712 | 0.46712 | 0.46712 | 0.46712 | 0.46712 | 0.46712 | 0.46712 | 0.46712
| 287.2117 | 771.333 | Reduction in unserved energy | 0 | 0 | 0 | 2.3501 | 2.5763 | 2.9705 | 4.6999 | 7.0538 | 11.0545 | 11.7111 | 19.7828 | 22.176 | 25.9808 | 46.1274 | 38.4281 | 38.4281 | 38.4281 | 38.4281 | 38.4281 | 38.4281 | 38.4281 | 38.4281 | 38.4281 | 38.4281 | 38.4281 | 38.4281 | 38.4281 | 38.4281 | 38.4281 | 38.4281
| 239.5001 | 712.0083 | Net benefit | 0 | 0 | -46.7124 | 1.883 | 2.1091 | 2.5034 | 4.2328 | 6.5867 | 10.5873 | 11.244 | 19.3157 | 21.7089 | 25.5136 | 45.6603 | 37.961 | 37.961 | 37.961 | 37.961 | 37.961 | 37.961 | 37.961 | 37.961 | 37.961 | 37.961 | 37.961 | 37.961 | 37.961 | 37.961 | 37.961 | 37.961
|  |  | EUE Value ($m, real $2024) | 1.1137 | 2.6361 | 4.8351 | 0.011211 | 0.013463 | 0.019408 | 0.039024 | 0.092869 | 0.36202 | 0.4436 | 1.4872 | 1.1652 | 2.4614 | 7.0261 | 4.8938 | 4.8938 | 4.8938 | 4.8938 | 4.8938 | 4.8938 | 4.8938 | 4.8938 | 4.8938 | 4.8938 | 4.8938 | 4.8938 | 4.8938 | 4.8938 | 4.8938 | 4.8938
|  |  | Annualised capex | 0 | 0 | 2.5546 | 2.5546 | 2.5546 | 2.5546 | 2.5546 | 2.5546 | 2.5546 | 2.5546 | 2.5546 | 2.5546 | 2.5546 | 2.5546 | 2.5546 | 2.5546 | 2.5546 | 2.5546 | 2.5546 | 2.5546 | 2.5546 | 2.5546 | 2.5546 | 2.5546 | 2.5546 | 2.5546 | 2.5546 | 2.5546 | 2.5546 | 2.5546
|  |  | Annualised cost (capex+opex) | 0 | 0 | 2.5546 | 3.0217 | 3.0217 | 3.0217 | 3.0217 | 3.0217 | 3.0217 | 3.0217 | 3.0217 | 3.0217 | 3.0217 | 3.0217 | 3.0217 | 3.0217 | 3.0217 | 3.0217 | 3.0217 | 3.0217 | 3.0217 | 3.0217 | 3.0217 | 3.0217 | 3.0217 | 3.0217 | 3.0217 | 3.0217 | 3.0217 | 3.0217
|  |  | Optimal timing (interim calc) | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  |  | Optimal timing | - | - | - | - | - | - | Yes | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
[11 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19
Adjusted For Optimal Timing: | 35.6398 | 46.7124 | Capex | 0 | 0 | 0 | 0 | 0 | 46.7124 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 4.6607 | 11.211 | Opex | 0 | 0 | 0 | 0 | 0 | 0 | 0.46712 | 0.46712 | 0.46712 | 0.46712 | 0.46712 | 0.46712 | 0.46712 | 0.46712 | 0.46712 | 0.46712 | 0.46712 | 0.46712 | 0.46712 | 0.46712 | 0.46712 | 0.46712 | 0.46712 | 0.46712 | 0.46712 | 0.46712 | 0.46712 | 0.46712 | 0.46712 | 0.46712
| 280.8724 | 763.4361 | Reduction in unserved energy | 0 | 0 | 0 | 0 | 0 | 0 | 4.6999 | 7.0538 | 11.0545 | 11.7111 | 19.7828 | 22.176 | 25.9808 | 46.1274 | 38.4281 | 38.4281 | 38.4281 | 38.4281 | 38.4281 | 38.4281 | 38.4281 | 38.4281 | 38.4281 | 38.4281 | 38.4281 | 38.4281 | 38.4281 | 38.4281 | 38.4281 | 38.4281
| 240.572 | 705.5127 | Net benefit | 0 | 0 | 0 | 0 | 0 | -46.7124 | 4.2328 | 6.5867 | 10.5873 | 11.244 | 19.3157 | 21.7089 | 25.5136 | 45.6603 | 37.961 | 37.961 | 37.961 | 37.961 | 37.961 | 37.961 | 37.961 | 37.961 | 37.961 | 37.961 | 37.961 | 37.961 | 37.961 | 37.961 | 37.961 | 37.961
Option 5
Determining Optimal Timing: | Discounted | Undiscounted
| 80.9953 | 124.9921 | Capex | 0 | 0 | 62.496 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62.496 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 7.747 | 16.8739 | Opex | 0 | 0 | 0 | 0.62496 | 0.62496 | 0.62496 | 0.62496 | 0.62496 | 0.62496 | 0.62496 | 0.62496 | 0.62496 | 0.62496 | 0.62496 | 0.62496 | 0.62496 | 0.62496 | 0.62496 | 0.62496 | 0.62496 | 0.62496 | 0.62496 | 0.62496 | 0.62496 | 0.62496 | 0.62496 | 0.62496 | 0.62496 | 0.62496 | 0.62496
| 315.9423 | 853.6606 | Reduction in unserved energy | 0 | 0 | 0 | 2.3437 | 2.5671 | 2.9562 | 4.6731 | 7.0432 | 11.2473 | 11.9746 | 21.0204 | 23.0958 | 28.1321 | 52.6519 | 42.8722 | 42.8722 | 42.8722 | 42.8722 | 42.8722 | 42.8722 | 42.8722 | 42.8722 | 42.8722 | 42.8722 | 42.8722 | 42.8722 | 42.8722 | 42.8722 | 42.8722 | 42.8722
| 227.2 | 711.7947 | Net benefit | 0 | 0 | -62.496 | 1.7188 | 1.9422 | 2.3313 | 4.0481 | 6.4182 | 10.6223 | 11.3496 | 20.3954 | 22.4708 | 27.5072 | 52.027 | 42.2472 | 42.2472 | 42.2472 | -20.2488 | 42.2472 | 42.2472 | 42.2472 | 42.2472 | 42.2472 | 42.2472 | 42.2472 | 42.2472 | 42.2472 | 42.2472 | 42.2472 | 42.2472
|  |  | EUE Value ($m, real $2024) | 1.1137 | 2.6361 | 4.8351 | 0.01758 | 0.022594 | 0.033687 | 0.065859 | 0.10345 | 0.16921 | 0.18013 | 0.24965 | 0.24546 | 0.31 | 0.50155 | 0.44973 | 0.44973 | 0.44973 | 0.44973 | 0.44973 | 0.44973 | 0.44973 | 0.44973 | 0.44973 | 0.44973 | 0.44973 | 0.44973 | 0.44973 | 0.44973 | 0.44973 | 0.44973
|  |  | Annualised capex | 0 | 0 | 8.1014 | 8.1014 | 8.1014 | 8.1014 | 8.1014 | 8.1014 | 8.1014 | 8.1014 | 8.1014 | 8.1014 | 8.1014 | 8.1014 | 8.1014 | 8.1014 | 8.1014 | 8.1014 | 8.1014 | 8.1014 | 8.1014 | 8.1014 | 8.1014 | 8.1014 | 8.1014 | 8.1014 | 8.1014 | 8.1014 | 8.1014 | 8.1014
|  |  | Annualised cost (capex+opex) | 0 | 0 | 8.1014 | 8.7264 | 8.7264 | 8.7264 | 8.7264 | 8.7264 | 8.7264 | 8.7264 | 8.7264 | 8.7264 | 8.7264 | 8.7264 | 8.7264 | 8.7264 | 8.7264 | 8.7264 | 8.7264 | 8.7264 | 8.7264 | 8.7264 | 8.7264 | 8.7264 | 8.7264 | 8.7264 | 8.7264 | 8.7264 | 8.7264 | 8.7264
|  |  | Optimal timing (interim calc) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  |  | Optimal timing | - | - | - | - | - | - | - | - | Yes | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Adjusted For Optimal Timing: | 61.7963 | 124.9921 | Capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62.496 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62.496 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 5.3559 | 13.7491 | Opex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.62496 | 0.62496 | 0.62496 | 0.62496 | 0.62496 | 0.62496 | 0.62496 | 0.62496 | 0.62496 | 0.62496 | 0.62496 | 0.62496 | 0.62496 | 0.62496 | 0.62496 | 0.62496 | 0.62496 | 0.62496 | 0.62496 | 0.62496 | 0.62496 | 0.62496
| 301.4266 | 834.0772 | Reduction in unserved energy | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11.2473 | 11.9746 | 21.0204 | 23.0958 | 28.1321 | 52.6519 | 42.8722 | 42.8722 | 42.8722 | 42.8722 | 42.8722 | 42.8722 | 42.8722 | 42.8722 | 42.8722 | 42.8722 | 42.8722 | 42.8722 | 42.8722 | 42.8722 | 42.8722 | 42.8722
| 234.2743 | 695.336 | Net benefit | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -62.496 | 10.6223 | 11.3496 | 20.3954 | 22.4708 | 27.5072 | 52.027 | 42.2472 | 42.2472 | 42.2472 | 42.2472 | 42.2472 | 42.2472 | 42.2472 | 42.2472 | -20.2488 | 42.2472 | 42.2472 | 42.2472 | 42.2472 | 42.2472 | 42.2472 | 42.2472
Option 6
Determining Optimal Timing: | Discounted | Undiscounted
| 0 | 0 | Capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Opex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Reduction in unserved energy | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Net benefit | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | EUE Value ($m, real $2024) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Annualised capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Annualised cost (capex+opex) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Optimal timing (interim calc) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Optimal timing | - | - | - | - | - | - | - | [19 empty] | - | - | - | - | bar: 1 to 19
Adjusted For Optimal Timing: | 0 | 0 | Capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Opex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Reduction in unserved energy | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Net benefit | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 7
Determining Optimal Timing: | Discounted | Undiscounted
| 0 | 0 | Capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Opex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Reduction in unserved energy | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Net benefit | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | EUE Value ($m, real $2024) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Annualised capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Annualised cost (capex+opex) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Optimal timing (interim calc) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Optimal timing | - | - | - | - | - | - | - | [19 empty] | - | - | - | - | bar: 1 to 19
Adjusted For Optimal Timing: | 0 | 0 | Capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Opex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Reduction in unserved energy | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Net benefit | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 8
Determining Optimal Timing: | Discounted | Undiscounted
| 0 | 0 | Capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Opex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Reduction in unserved energy | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Net benefit | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | EUE Value ($m, real $2024) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Annualised capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Annualised cost (capex+opex) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Optimal timing (interim calc) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Optimal timing | - | - | - | - | - | - | - | [19 empty] | - | - | - | - | bar: 1 to 19
Adjusted For Optimal Timing: | 0 | 0 | Capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Opex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Reduction in unserved energy | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Net benefit | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 9
Determining Optimal Timing: | Discounted | Undiscounted
| 0 | 0 | Capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Opex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Reduction in unserved energy | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Net benefit | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | EUE Value ($m, real $2024) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Annualised capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Annualised cost (capex+opex) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Optimal timing (interim calc) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Optimal timing | - | - | - | - | - | - | - | [19 empty] | - | - | - | - | bar: 1 to 19
Adjusted For Optimal Timing: | 0 | 0 | Capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Opex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Reduction in unserved energy | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Net benefit | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 10
Determining Optimal Timing: | Discounted | Undiscounted
| 0 | 0 | Capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Opex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Reduction in unserved energy | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Net benefit | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | EUE Value ($m, real $2024) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Annualised capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Annualised cost (capex+opex) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Optimal timing (interim calc) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Optimal timing | - | - | - | - | - | - | - | [19 empty] | - | - | - | - | bar: 1 to 19
Adjusted For Optimal Timing: | 0 | 0 | Capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Opex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Reduction in unserved energy | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Net benefit | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## 3.2.4 NPV (HiCost)
Economic inputs and assumptions
Scenario | Discount rate | Central
| Cost | Upper bound
| VCR | Central
|  | Central | Lower bound | Upper bound
| Discount rate | 5.56% | 4.11% | 7%
| Cost | 100% | 80% | 120%
| VCR | 100% | 80% | 120%
Asset life for calculating annualised capex (years) | Option 1 | 45
| Option 2 | 45
| Option 3 | 45
| Option 4 | 45
| Option 5 | 15
| Option 6 | 45
| Option 7 | 0
| Option 8 | 0
| Option 9 | 0
| Option 10 | 0
|  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30
|  |  |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Outputs | bar: 3 FY27; 7 FY31
Option 1
| Discounted | Undiscounted
| 0 | 0 | Capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Opex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Reduction in unserved energy | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Net benefit | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | EUE Value ($m, real $2024) | 1.1137 | 2.6361 | 4.8351 | 2.3613 | 2.5897 | 2.9899 | 4.739 | 7.1467 | 11.4165 | 12.1547 | 21.27 | 23.3412 | 28.4421 | 53.1535 | 43.3219 | 43.3219 | 43.3219 | 43.3219 | 43.3219 | 43.3219 | 43.3219 | 43.3219 | 43.3219 | 43.3219 | 43.3219 | 43.3219 | 43.3219 | 43.3219 | 43.3219 | 43.3219
Option 2
Determining Optimal Timing: | Discounted | Undiscounted
| 43.5404 | 48.5167 | Capex | 0 | 0 | 48.5167 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 6.0141 | 13.0995 | Opex | 0 | 0 | 0 | 0.48517 | 0.48517 | 0.48517 | 0.48517 | 0.48517 | 0.48517 | 0.48517 | 0.48517 | 0.48517 | 0.48517 | 0.48517 | 0.48517 | 0.48517 | 0.48517 | 0.48517 | 0.48517 | 0.48517 | 0.48517 | 0.48517 | 0.48517 | 0.48517 | 0.48517 | 0.48517 | 0.48517 | 0.48517 | 0.48517 | 0.48517
| 285.4829 | 767.3772 | Reduction in unserved energy | 0 | 0 | 0 | 2.3239 | 2.5336 | 2.9024 | 4.5797 | 6.8971 | 10.8805 | 11.5418 | 19.5847 | 21.9902 | 25.875 | 45.7618 | 38.2817 | 38.2817 | 38.2817 | 38.2817 | 38.2817 | 38.2817 | 38.2817 | 38.2817 | 38.2817 | 38.2817 | 38.2817 | 38.2817 | 38.2817 | 38.2817 | 38.2817 | 38.2817
| 235.9284 | 705.761 | Net benefit | 0 | 0 | -48.5167 | 1.8387 | 2.0484 | 2.4172 | 4.0945 | 6.4119 | 10.3954 | 11.0566 | 19.0996 | 21.505 | 25.3899 | 45.2767 | 37.7965 | 37.7965 | 37.7965 | 37.7965 | 37.7965 | 37.7965 | 37.7965 | 37.7965 | 37.7965 | 37.7965 | 37.7965 | 37.7965 | 37.7965 | 37.7965 | 37.7965 | 37.7965
|  |  | EUE Value ($m, real $2024) | 1.1137 | 2.6361 | 4.8351 | 0.037438 | 0.05616 | 0.087536 | 0.15929 | 0.24956 | 0.53594 | 0.61292 | 1.6853 | 1.3511 | 2.5671 | 7.3917 | 5.0403 | 5.0403 | 5.0403 | 5.0403 | 5.0403 | 5.0403 | 5.0403 | 5.0403 | 5.0403 | 5.0403 | 5.0403 | 5.0403 | 5.0403 | 5.0403 | 5.0403 | 5.0403
|  |  | Annualised capex | 0 | 0 | 2.6533 | 2.6533 | 2.6533 | 2.6533 | 2.6533 | 2.6533 | 2.6533 | 2.6533 | 2.6533 | 2.6533 | 2.6533 | 2.6533 | 2.6533 | 2.6533 | 2.6533 | 2.6533 | 2.6533 | 2.6533 | 2.6533 | 2.6533 | 2.6533 | 2.6533 | 2.6533 | 2.6533 | 2.6533 | 2.6533 | 2.6533 | 2.6533
|  |  | Annualised cost (capex+opex) | 0 | 0 | 2.6533 | 3.1385 | 3.1385 | 3.1385 | 3.1385 | 3.1385 | 3.1385 | 3.1385 | 3.1385 | 3.1385 | 3.1385 | 3.1385 | 3.1385 | 3.1385 | 3.1385 | 3.1385 | 3.1385 | 3.1385 | 3.1385 | 3.1385 | 3.1385 | 3.1385 | 3.1385 | 3.1385 | 3.1385 | 3.1385 | 3.1385 | 3.1385
|  |  | Optimal timing (interim calc) | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  |  | Optimal timing | - | - | - | - | - | - | Yes | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Adjusted For Optimal Timing: | 37.0164 | 48.5167 | Capex | 0 | 0 | 0 | 0 | 0 | 48.5167 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 4.8407 | 11.644 | Opex | 0 | 0 | 0 | 0 | 0 | 0 | 0.48517 | 0.48517 | 0.48517 | 0.48517 | 0.48517 | 0.48517 | 0.48517 | 0.48517 | 0.48517 | 0.48517 | 0.48517 | 0.48517 | 0.48517 | 0.48517 | 0.48517 | 0.48517 | 0.48517 | 0.48517 | 0.48517 | 0.48517 | 0.48517 | 0.48517 | 0.48517 | 0.48517
| 279.2523 | 759.6174 | Reduction in unserved energy | 0 | 0 | 0 | 0 | 0 | 0 | 4.5797 | 6.8971 | 10.8805 | 11.5418 | 19.5847 | 21.9902 | 25.875 | 45.7618 | 38.2817 | 38.2817 | 38.2817 | 38.2817 | 38.2817 | 38.2817 | 38.2817 | 38.2817 | 38.2817 | 38.2817 | 38.2817 | 38.2817 | 38.2817 | 38.2817 | 38.2817 | 38.2817
| 237.3952 | 699.4567 | Net benefit | 0 | 0 | 0 | 0 | 0 | -48.5167 | 4.0945 | 6.4119 | 10.3954 | 11.0566 | 19.0996 | 21.505 | 25.3899 | 45.2767 | 37.7965 | 37.7965 | 37.7965 | 37.7965 | 37.7965 | 37.7965 | 37.7965 | 37.7965 | 37.7965 | 37.7965 | 37.7965 | 37.7965 | 37.7965 | 37.7965 | 37.7965 | 37.7965
Option 3
Determining Optimal Timing: | Discounted | Undiscounted
| 70.8824 | 78.9836 | Capex | 0 | 0 | 78.9836 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 9.7908 | 21.3256 | Opex | 0 | 0 | 0 | 0.78984 | 0.78984 | 0.78984 | 0.78984 | 0.78984 | 0.78984 | 0.78984 | 0.78984 | 0.78984 | 0.78984 | 0.78984 | 0.78984 | 0.78984 | 0.78984 | 0.78984 | 0.78984 | 0.78984 | 0.78984 | 0.78984 | 0.78984 | 0.78984 | 0.78984 | 0.78984 | 0.78984 | 0.78984 | 0.78984 | 0.78984
| 282.5957 | 758.1624 | Reduction in unserved energy | 0 | 0 | 0 | 2.3553 | 2.5817 | 2.9769 | 4.7087 | 7.0505 | 10.9843 | 11.6243 | 19.5528 | 22.0004 | 25.5289 | 45.2961 | 37.7189 | 37.7189 | 37.7189 | 37.7189 | 37.7189 | 37.7189 | 37.7189 | 37.7189 | 37.7189 | 37.7189 | 37.7189 | 37.7189 | 37.7189 | 37.7189 | 37.7189 | 37.7189
| 201.9226 | 657.8532 | Net benefit | 0 | 0 | -78.9836 | 1.5655 | 1.7919 | 2.187 | 3.9188 | 6.2607 | 10.1944 | 10.8344 | 18.7629 | 21.2106 | 24.7391 | 44.5063 | 36.9291 | 36.9291 | 36.9291 | 36.9291 | 36.9291 | 36.9291 | 36.9291 | 36.9291 | 36.9291 | 36.9291 | 36.9291 | 36.9291 | 36.9291 | 36.9291 | 36.9291 | 36.9291
|  |  | EUE Value ($m, real $2024) | 1.1137 | 2.6361 | 4.8351 | 0.0060347 | 0.0079976 | 0.013061 | 0.030296 | 0.09615 | 0.43224 | 0.53044 | 1.7172 | 1.3408 | 2.9132 | 7.8574 | 5.603 | 5.603 | 5.603 | 5.603 | 5.603 | 5.603 | 5.603 | 5.603 | 5.603 | 5.603 | 5.603 | 5.603 | 5.603 | 5.603 | 5.603 | 5.603
|  |  | Annualised capex | 0 | 0 | 4.3195 | 4.3195 | 4.3195 | 4.3195 | 4.3195 | 4.3195 | 4.3195 | 4.3195 | 4.3195 | 4.3195 | 4.3195 | 4.3195 | 4.3195 | 4.3195 | 4.3195 | 4.3195 | 4.3195 | 4.3195 | 4.3195 | 4.3195 | 4.3195 | 4.3195 | 4.3195 | 4.3195 | 4.3195 | 4.3195 | 4.3195 | 4.3195
|  |  | Annualised cost (capex+opex) | 0 | 0 | 4.3195 | 5.1093 | 5.1093 | 5.1093 | 5.1093 | 5.1093 | 5.1093 | 5.1093 | 5.1093 | 5.1093 | 5.1093 | 5.1093 | 5.1093 | 5.1093 | 5.1093 | 5.1093 | 5.1093 | 5.1093 | 5.1093 | 5.1093 | 5.1093 | 5.1093 | 5.1093 | 5.1093 | 5.1093 | 5.1093 | 5.1093 | 5.1093
|  |  | Optimal timing (interim calc) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  |  | Optimal timing | - | - | - | - | - | - | - | Yes | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Adjusted For Optimal Timing: | 57.0875 | 78.9836 | Capex | 0 | 0 | 0 | 0 | 0 | 0 | 78.9836 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 7.3097 | 18.1662 | Opex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.78984 | 0.78984 | 0.78984 | 0.78984 | 0.78984 | 0.78984 | 0.78984 | 0.78984 | 0.78984 | 0.78984 | 0.78984 | 0.78984 | 0.78984 | 0.78984 | 0.78984 | 0.78984 | 0.78984 | 0.78984 | 0.78984 | 0.78984 | 0.78984 | 0.78984 | 0.78984
| 272.8395 | 745.5398 | Reduction in unserved energy | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.0505 | 10.9843 | 11.6243 | 19.5528 | 22.0004 | 25.5289 | 45.2961 | 37.7189 | 37.7189 | 37.7189 | 37.7189 | 37.7189 | 37.7189 | 37.7189 | 37.7189 | 37.7189 | 37.7189 | 37.7189 | 37.7189 | 37.7189 | 37.7189 | 37.7189 | 37.7189
| 208.4424 | 648.39 | Net benefit | 0 | 0 | 0 | 0 | 0 | 0 | -78.9836 | 6.2607 | 10.1944 | 10.8344 | 18.7629 | 21.2106 | 24.7391 | 44.5063 | 36.9291 | 36.9291 | 36.9291 | 36.9291 | 36.9291 | 36.9291 | 36.9291 | 36.9291 | 36.9291 | 36.9291 | 36.9291 | 36.9291 | 36.9291 | 36.9291 | 36.9291 | 36.9291
Option 4
Determining Optimal Timing: | Discounted | Undiscounted
| 62.8817 | 70.0686 | Capex | 0 | 0 | 70.0686 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 8.6857 | 18.9185 | Opex | 0 | 0 | 0 | 0.70069 | 0.70069 | 0.70069 | 0.70069 | 0.70069 | 0.70069 | 0.70069 | 0.70069 | 0.70069 | 0.70069 | 0.70069 | 0.70069 | 0.70069 | 0.70069 | 0.70069 | 0.70069 | 0.70069 | 0.70069 | 0.70069 | 0.70069 | 0.70069 | 0.70069 | 0.70069 | 0.70069 | 0.70069 | 0.70069 | 0.70069
| 287.2117 | 771.333 | Reduction in unserved energy | 0 | 0 | 0 | 2.3501 | 2.5763 | 2.9705 | 4.6999 | 7.0538 | 11.0545 | 11.7111 | 19.7828 | 22.176 | 25.9808 | 46.1274 | 38.4281 | 38.4281 | 38.4281 | 38.4281 | 38.4281 | 38.4281 | 38.4281 | 38.4281 | 38.4281 | 38.4281 | 38.4281 | 38.4281 | 38.4281 | 38.4281 | 38.4281 | 38.4281
| 215.6443 | 682.3459 | Net benefit | 0 | 0 | -70.0686 | 1.6494 | 1.8756 | 2.2698 | 3.9993 | 6.3531 | 10.3538 | 11.0104 | 19.0821 | 21.4753 | 25.2801 | 45.4267 | 37.7274 | 37.7274 | 37.7274 | 37.7274 | 37.7274 | 37.7274 | 37.7274 | 37.7274 | 37.7274 | 37.7274 | 37.7274 | 37.7274 | 37.7274 | 37.7274 | 37.7274 | 37.7274
|  |  | EUE Value ($m, real $2024) | 1.1137 | 2.6361 | 4.8351 | 0.011211 | 0.013463 | 0.019408 | 0.039024 | 0.092869 | 0.36202 | 0.4436 | 1.4872 | 1.1652 | 2.4614 | 7.0261 | 4.8938 | 4.8938 | 4.8938 | 4.8938 | 4.8938 | 4.8938 | 4.8938 | 4.8938 | 4.8938 | 4.8938 | 4.8938 | 4.8938 | 4.8938 | 4.8938 | 4.8938 | 4.8938
|  |  | Annualised capex | 0 | 0 | 3.8319 | 3.8319 | 3.8319 | 3.8319 | 3.8319 | 3.8319 | 3.8319 | 3.8319 | 3.8319 | 3.8319 | 3.8319 | 3.8319 | 3.8319 | 3.8319 | 3.8319 | 3.8319 | 3.8319 | 3.8319 | 3.8319 | 3.8319 | 3.8319 | 3.8319 | 3.8319 | 3.8319 | 3.8319 | 3.8319 | 3.8319 | 3.8319
|  |  | Annualised cost (capex+opex) | 0 | 0 | 3.8319 | 4.5326 | 4.5326 | 4.5326 | 4.5326 | 4.5326 | 4.5326 | 4.5326 | 4.5326 | 4.5326 | 4.5326 | 4.5326 | 4.5326 | 4.5326 | 4.5326 | 4.5326 | 4.5326 | 4.5326 | 4.5326 | 4.5326 | 4.5326 | 4.5326 | 4.5326 | 4.5326 | 4.5326 | 4.5326 | 4.5326 | 4.5326
|  |  | Optimal timing (interim calc) | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  |  | Optimal timing | - | - | - | - | - | - | Yes | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
[11 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19
Adjusted For Optimal Timing: | 53.4597 | 70.0686 | Capex | 0 | 0 | 0 | 0 | 0 | 70.0686 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 6.991 | 16.8165 | Opex | 0 | 0 | 0 | 0 | 0 | 0 | 0.70069 | 0.70069 | 0.70069 | 0.70069 | 0.70069 | 0.70069 | 0.70069 | 0.70069 | 0.70069 | 0.70069 | 0.70069 | 0.70069 | 0.70069 | 0.70069 | 0.70069 | 0.70069 | 0.70069 | 0.70069 | 0.70069 | 0.70069 | 0.70069 | 0.70069 | 0.70069 | 0.70069
| 280.8724 | 763.4361 | Reduction in unserved energy | 0 | 0 | 0 | 0 | 0 | 0 | 4.6999 | 7.0538 | 11.0545 | 11.7111 | 19.7828 | 22.176 | 25.9808 | 46.1274 | 38.4281 | 38.4281 | 38.4281 | 38.4281 | 38.4281 | 38.4281 | 38.4281 | 38.4281 | 38.4281 | 38.4281 | 38.4281 | 38.4281 | 38.4281 | 38.4281 | 38.4281 | 38.4281
| 220.4217 | 676.5511 | Net benefit | 0 | 0 | 0 | 0 | 0 | -70.0686 | 3.9993 | 6.3531 | 10.3538 | 11.0104 | 19.0821 | 21.4753 | 25.2801 | 45.4267 | 37.7274 | 37.7274 | 37.7274 | 37.7274 | 37.7274 | 37.7274 | 37.7274 | 37.7274 | 37.7274 | 37.7274 | 37.7274 | 37.7274 | 37.7274 | 37.7274 | 37.7274 | 37.7274
Option 5
Determining Optimal Timing: | Discounted | Undiscounted
| 121.4929 | 187.4881 | Capex | 0 | 0 | 93.744 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93.744 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 11.6204 | 25.3109 | Opex | 0 | 0 | 0 | 0.93744 | 0.93744 | 0.93744 | 0.93744 | 0.93744 | 0.93744 | 0.93744 | 0.93744 | 0.93744 | 0.93744 | 0.93744 | 0.93744 | 0.93744 | 0.93744 | 0.93744 | 0.93744 | 0.93744 | 0.93744 | 0.93744 | 0.93744 | 0.93744 | 0.93744 | 0.93744 | 0.93744 | 0.93744 | 0.93744 | 0.93744
| 315.9423 | 853.6606 | Reduction in unserved energy | 0 | 0 | 0 | 2.3437 | 2.5671 | 2.9562 | 4.6731 | 7.0432 | 11.2473 | 11.9746 | 21.0204 | 23.0958 | 28.1321 | 52.6519 | 42.8722 | 42.8722 | 42.8722 | 42.8722 | 42.8722 | 42.8722 | 42.8722 | 42.8722 | 42.8722 | 42.8722 | 42.8722 | 42.8722 | 42.8722 | 42.8722 | 42.8722 | 42.8722
| 182.8289 | 640.8617 | Net benefit | 0 | 0 | -93.744 | 1.4063 | 1.6297 | 2.0188 | 3.7357 | 6.1058 | 10.3098 | 11.0371 | 20.0829 | 22.1584 | 27.1947 | 51.7145 | 41.9348 | 41.9348 | 41.9348 | -51.8093 | 41.9348 | 41.9348 | 41.9348 | 41.9348 | 41.9348 | 41.9348 | 41.9348 | 41.9348 | 41.9348 | 41.9348 | 41.9348 | 41.9348
|  |  | EUE Value ($m, real $2024) | 1.1137 | 2.6361 | 4.8351 | 0.01758 | 0.022594 | 0.033687 | 0.065859 | 0.10345 | 0.16921 | 0.18013 | 0.24965 | 0.24546 | 0.31 | 0.50155 | 0.44973 | 0.44973 | 0.44973 | 0.44973 | 0.44973 | 0.44973 | 0.44973 | 0.44973 | 0.44973 | 0.44973 | 0.44973 | 0.44973 | 0.44973 | 0.44973 | 0.44973 | 0.44973
|  |  | Annualised capex | 0 | 0 | 12.1521 | 12.1521 | 12.1521 | 12.1521 | 12.1521 | 12.1521 | 12.1521 | 12.1521 | 12.1521 | 12.1521 | 12.1521 | 12.1521 | 12.1521 | 12.1521 | 12.1521 | 12.1521 | 12.1521 | 12.1521 | 12.1521 | 12.1521 | 12.1521 | 12.1521 | 12.1521 | 12.1521 | 12.1521 | 12.1521 | 12.1521 | 12.1521
|  |  | Annualised cost (capex+opex) | 0 | 0 | 12.1521 | 13.0896 | 13.0896 | 13.0896 | 13.0896 | 13.0896 | 13.0896 | 13.0896 | 13.0896 | 13.0896 | 13.0896 | 13.0896 | 13.0896 | 13.0896 | 13.0896 | 13.0896 | 13.0896 | 13.0896 | 13.0896 | 13.0896 | 13.0896 | 13.0896 | 13.0896 | 13.0896 | 13.0896 | 13.0896 | 13.0896 | 13.0896
|  |  | Optimal timing (interim calc) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  |  | Optimal timing | - | - | - | - | - | - | - | - | - | - | Yes | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Adjusted For Optimal Timing: | 83.187 | 187.4881 | Capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93.744 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93.744 | 0 | 0 | 0 | 0 | 0
| 6.8497 | 18.7488 | Opex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.93744 | 0.93744 | 0.93744 | 0.93744 | 0.93744 | 0.93744 | 0.93744 | 0.93744 | 0.93744 | 0.93744 | 0.93744 | 0.93744 | 0.93744 | 0.93744 | 0.93744 | 0.93744 | 0.93744 | 0.93744 | 0.93744 | 0.93744
| 286.773 | 810.8554 | Reduction in unserved energy | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21.0204 | 23.0958 | 28.1321 | 52.6519 | 42.8722 | 42.8722 | 42.8722 | 42.8722 | 42.8722 | 42.8722 | 42.8722 | 42.8722 | 42.8722 | 42.8722 | 42.8722 | 42.8722 | 42.8722 | 42.8722 | 42.8722 | 42.8722
| 196.7363 | 604.6185 | Net benefit | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -93.744 | 20.0829 | 22.1584 | 27.1947 | 51.7145 | 41.9348 | 41.9348 | 41.9348 | 41.9348 | 41.9348 | 41.9348 | 41.9348 | 41.9348 | 41.9348 | 41.9348 | -51.8093 | 41.9348 | 41.9348 | 41.9348 | 41.9348 | 41.9348
Option 6
Determining Optimal Timing: | Discounted | Undiscounted
| 0 | 0 | Capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Opex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Reduction in unserved energy | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Net benefit | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | EUE Value ($m, real $2024) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Annualised capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Annualised cost (capex+opex) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Optimal timing (interim calc) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Optimal timing | - | - | - | - | - | - | - | [19 empty] | - | - | - | - | bar: 1 to 19
Adjusted For Optimal Timing: | 0 | 0 | Capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Opex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Reduction in unserved energy | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Net benefit | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 7
Determining Optimal Timing: | Discounted | Undiscounted
| 0 | 0 | Capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Opex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Reduction in unserved energy | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Net benefit | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | EUE Value ($m, real $2024) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Annualised capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Annualised cost (capex+opex) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Optimal timing (interim calc) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Optimal timing | - | - | - | - | - | - | - | [19 empty] | - | - | - | - | bar: 1 to 19
Adjusted For Optimal Timing: | 0 | 0 | Capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Opex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Reduction in unserved energy | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Net benefit | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 8
Determining Optimal Timing: | Discounted | Undiscounted
| 0 | 0 | Capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Opex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Reduction in unserved energy | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Net benefit | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | EUE Value ($m, real $2024) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Annualised capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Annualised cost (capex+opex) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Optimal timing (interim calc) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Optimal timing | - | - | - | - | - | - | - | [19 empty] | - | - | - | - | bar: 1 to 19
Adjusted For Optimal Timing: | 0 | 0 | Capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Opex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Reduction in unserved energy | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Net benefit | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 9
Determining Optimal Timing: | Discounted | Undiscounted
| 0 | 0 | Capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Opex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Reduction in unserved energy | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Net benefit | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | EUE Value ($m, real $2024) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Annualised capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Annualised cost (capex+opex) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Optimal timing (interim calc) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Optimal timing | - | - | - | - | - | - | - | [19 empty] | - | - | - | - | bar: 1 to 19
Adjusted For Optimal Timing: | 0 | 0 | Capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Opex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Reduction in unserved energy | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Net benefit | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 10
Determining Optimal Timing: | Discounted | Undiscounted
| 0 | 0 | Capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Opex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Reduction in unserved energy | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Net benefit | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | EUE Value ($m, real $2024) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Annualised capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Annualised cost (capex+opex) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Optimal timing (interim calc) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Optimal timing | - | - | - | - | - | - | - | [19 empty] | - | - | - | - | bar: 1 to 19
Adjusted For Optimal Timing: | 0 | 0 | Capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Opex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Reduction in unserved energy | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Net benefit | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## 3.2.5 NPV (Low Demand)
Economic inputs and assumptions
Scenario | Discount rate | Central
| Cost | Central
| VCR | Central
|  | Central | Lower bound | Upper bound
| Discount rate | 5.56% | 4.11% | 7%
| Cost | 100% | 80% | 120%
| VCR | 100% | 80% | 120%
Asset life for calculating annualised capex (years) | Option 1 | 45
| Option 2 | 45
| Option 3 | 45
| Option 4 | 45
| Option 5 | 15
| Option 6 | 45
| Option 7 | 0
| Option 8 | 0
| Option 9 | 0
| Option 10 | 0
|  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30
|  |  |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Outputs | bar: 3 FY27; 7 FY31
Option 1
| Discounted | Undiscounted
| 0 | 0 | Capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Opex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Reduction in unserved energy | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Net benefit | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | EUE Value ($m, real $2024) | 0.035548 | 0.26077 | 0.65041 | 0.24823 | 0.31943 | 0.43666 | 0.78759 | 1.1507 | 1.7022 | 1.6556 | 2.3474 | 2.8002 | 3.1587 | 5.2105 | 4.4838 | 4.4838 | 4.4838 | 4.4838 | 4.4838 | 4.4838 | 4.4838 | 4.4838 | 4.4838 | 4.4838 | 4.4838 | 4.4838 | 4.4838 | 4.4838 | 4.4838 | 4.4838
Option 2
Determining Optimal Timing: | Discounted | Undiscounted
| 36.2837 | 40.4306 | Capex | 0 | 0 | 40.4306 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 5.0117 | 10.9163 | Opex | 0 | 0 | 0 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431
| 32.4483 | 85.9794 | Reduction in unserved energy | 0 | 0 | 0 | 0.24287 | 0.31084 | 0.42124 | 0.75219 | 1.091 | 1.599 | 1.545 | 2.191 | 2.6485 | 2.9615 | 4.8561 | 4.21 | 4.21 | 4.21 | 4.21 | 4.21 | 4.21 | 4.21 | 4.21 | 4.21 | 4.21 | 4.21 | 4.21 | 4.21 | 4.21 | 4.21 | 4.21
| -8.8471 | 34.6326 | Net benefit | 0 | 0 | -40.4306 | -0.16144 | -0.09347 | 0.016937 | 0.34788 | 0.68672 | 1.1947 | 1.1407 | 1.7867 | 2.2442 | 2.5572 | 4.4518 | 3.8057 | 3.8057 | 3.8057 | 3.8057 | 3.8057 | 3.8057 | 3.8057 | 3.8057 | 3.8057 | 3.8057 | 3.8057 | 3.8057 | 3.8057 | 3.8057 | 3.8057 | 3.8057
|  |  | EUE Value ($m, real $2024) | 0.035548 | 0.26077 | 0.65041 | 0.0053674 | 0.0085961 | 0.015415 | 0.035401 | 0.059663 | 0.10327 | 0.11059 | 0.15638 | 0.15174 | 0.19725 | 0.35444 | 0.27377 | 0.27377 | 0.27377 | 0.27377 | 0.27377 | 0.27377 | 0.27377 | 0.27377 | 0.27377 | 0.27377 | 0.27377 | 0.27377 | 0.27377 | 0.27377 | 0.27377 | 0.27377
|  |  | Annualised capex | 0 | 0 | 2.2111 | 2.2111 | 2.2111 | 2.2111 | 2.2111 | 2.2111 | 2.2111 | 2.2111 | 2.2111 | 2.2111 | 2.2111 | 2.2111 | 2.2111 | 2.2111 | 2.2111 | 2.2111 | 2.2111 | 2.2111 | 2.2111 | 2.2111 | 2.2111 | 2.2111 | 2.2111 | 2.2111 | 2.2111 | 2.2111 | 2.2111 | 2.2111
|  |  | Annualised cost (capex+opex) | 0 | 0 | 2.2111 | 2.6154 | 2.6154 | 2.6154 | 2.6154 | 2.6154 | 2.6154 | 2.6154 | 2.6154 | 2.6154 | 2.6154 | 2.6154 | 2.6154 | 2.6154 | 2.6154 | 2.6154 | 2.6154 | 2.6154 | 2.6154 | 2.6154 | 2.6154 | 2.6154 | 2.6154 | 2.6154 | 2.6154 | 2.6154 | 2.6154 | 2.6154
|  |  | Optimal timing (interim calc) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  |  | Optimal timing | - | - | - | - | - | - | - | - | - | - | - | Yes | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Adjusted For Optimal Timing: | 23.5351 | 40.4306 | Capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40.4306 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2.7188 | 7.6818 | Opex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431
| 27.1175 | 77.8263 | Reduction in unserved energy | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6485 | 2.9615 | 4.8561 | 4.21 | 4.21 | 4.21 | 4.21 | 4.21 | 4.21 | 4.21 | 4.21 | 4.21 | 4.21 | 4.21 | 4.21 | 4.21 | 4.21 | 4.21 | 4.21
| 0.86355 | 29.7139 | Net benefit | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -40.4306 | 2.2442 | 2.5572 | 4.4518 | 3.8057 | 3.8057 | 3.8057 | 3.8057 | 3.8057 | 3.8057 | 3.8057 | 3.8057 | 3.8057 | 3.8057 | 3.8057 | 3.8057 | 3.8057 | 3.8057 | 3.8057 | 3.8057
Option 3
Determining Optimal Timing: | Discounted | Undiscounted
| 59.0686 | 65.8197 | Capex | 0 | 0 | 65.8197 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 8.159 | 17.7713 | Opex | 0 | 0 | 0 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582
| 33.7446 | 89.3171 | Reduction in unserved energy | 0 | 0 | 0 | 0.24756 | 0.31866 | 0.43559 | 0.78497 | 1.1452 | 1.6891 | 1.6412 | 2.3176 | 2.7742 | 3.1106 | 5.0085 | 4.3652 | 4.3652 | 4.3652 | 4.3652 | 4.3652 | 4.3652 | 4.3652 | 4.3652 | 4.3652 | 4.3652 | 4.3652 | 4.3652 | 4.3652 | 4.3652 | 4.3652 | 4.3652
| -33.483 | 5.7261 | Net benefit | 0 | 0 | -65.8197 | -0.41064 | -0.33953 | -0.2226 | 0.12678 | 0.487 | 1.0309 | 0.983 | 1.6594 | 2.116 | 2.4524 | 4.3503 | 3.707 | 3.707 | 3.707 | 3.707 | 3.707 | 3.707 | 3.707 | 3.707 | 3.707 | 3.707 | 3.707 | 3.707 | 3.707 | 3.707 | 3.707 | 3.707
|  |  | EUE Value ($m, real $2024) | 0.035548 | 0.26077 | 0.65041 | 0.00067765 | 0.00076837 | 0.0010647 | 0.0026152 | 0.0054919 | 0.013141 | 0.014399 | 0.02983 | 0.026036 | 0.04812 | 0.20199 | 0.11855 | 0.11855 | 0.11855 | 0.11855 | 0.11855 | 0.11855 | 0.11855 | 0.11855 | 0.11855 | 0.11855 | 0.11855 | 0.11855 | 0.11855 | 0.11855 | 0.11855 | 0.11855
|  |  | Annualised capex | 0 | 0 | 3.5996 | 3.5996 | 3.5996 | 3.5996 | 3.5996 | 3.5996 | 3.5996 | 3.5996 | 3.5996 | 3.5996 | 3.5996 | 3.5996 | 3.5996 | 3.5996 | 3.5996 | 3.5996 | 3.5996 | 3.5996 | 3.5996 | 3.5996 | 3.5996 | 3.5996 | 3.5996 | 3.5996 | 3.5996 | 3.5996 | 3.5996 | 3.5996
|  |  | Annualised cost (capex+opex) | 0 | 0 | 3.5996 | 4.2578 | 4.2578 | 4.2578 | 4.2578 | 4.2578 | 4.2578 | 4.2578 | 4.2578 | 4.2578 | 4.2578 | 4.2578 | 4.2578 | 4.2578 | 4.2578 | 4.2578 | 4.2578 | 4.2578 | 4.2578 | 4.2578 | 4.2578 | 4.2578 | 4.2578 | 4.2578 | 4.2578 | 4.2578 | 4.2578 | 4.2578
|  |  | Optimal timing (interim calc) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  |  | Optimal timing | - | - | - | - | - | - | - | - | - | - | - | - | - | Yes | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Adjusted For Optimal Timing: | 34.3845 | 65.8197 | Capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65.8197 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 3.7194 | 11.1893 | Opex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582
| 24.9857 | 74.8524 | Reduction in unserved energy | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.0085 | 4.3652 | 4.3652 | 4.3652 | 4.3652 | 4.3652 | 4.3652 | 4.3652 | 4.3652 | 4.3652 | 4.3652 | 4.3652 | 4.3652 | 4.3652 | 4.3652 | 4.3652 | 4.3652
| -13.1182 | -2.1566 | Net benefit | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -65.8197 | 4.3503 | 3.707 | 3.707 | 3.707 | 3.707 | 3.707 | 3.707 | 3.707 | 3.707 | 3.707 | 3.707 | 3.707 | 3.707 | 3.707 | 3.707 | 3.707 | 3.707
Option 4
Determining Optimal Timing: | Discounted | Undiscounted
| 52.4015 | 58.3905 | Capex | 0 | 0 | 58.3905 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 7.238 | 15.7654 | Opex | 0 | 0 | 0 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839
| 33.7637 | 89.403 | Reduction in unserved energy | 0 | 0 | 0 | 0.24589 | 0.31693 | 0.43361 | 0.78198 | 1.1411 | 1.6842 | 1.6359 | 2.3128 | 2.7662 | 3.1083 | 5.0279 | 4.3718 | 4.3718 | 4.3718 | 4.3718 | 4.3718 | 4.3718 | 4.3718 | 4.3718 | 4.3718 | 4.3718 | 4.3718 | 4.3718 | 4.3718 | 4.3718 | 4.3718 | 4.3718
| -25.8758 | 15.2471 | Net benefit | 0 | 0 | -58.3905 | -0.33801 | -0.26697 | -0.1503 | 0.19808 | 0.55718 | 1.1003 | 1.052 | 1.7289 | 2.1823 | 2.5244 | 4.444 | 3.7879 | 3.7879 | 3.7879 | 3.7879 | 3.7879 | 3.7879 | 3.7879 | 3.7879 | 3.7879 | 3.7879 | 3.7879 | 3.7879 | 3.7879 | 3.7879 | 3.7879 | 3.7879
|  |  | EUE Value ($m, real $2024) | 0.035548 | 0.26077 | 0.65041 | 0.0023404 | 0.0024977 | 0.003048 | 0.005606 | 0.009606 | 0.018085 | 0.019704 | 0.034607 | 0.034027 | 0.050465 | 0.18266 | 0.11202 | 0.11202 | 0.11202 | 0.11202 | 0.11202 | 0.11202 | 0.11202 | 0.11202 | 0.11202 | 0.11202 | 0.11202 | 0.11202 | 0.11202 | 0.11202 | 0.11202 | 0.11202
|  |  | Annualised capex | 0 | 0 | 3.1933 | 3.1933 | 3.1933 | 3.1933 | 3.1933 | 3.1933 | 3.1933 | 3.1933 | 3.1933 | 3.1933 | 3.1933 | 3.1933 | 3.1933 | 3.1933 | 3.1933 | 3.1933 | 3.1933 | 3.1933 | 3.1933 | 3.1933 | 3.1933 | 3.1933 | 3.1933 | 3.1933 | 3.1933 | 3.1933 | 3.1933 | 3.1933
|  |  | Annualised cost (capex+opex) | 0 | 0 | 3.1933 | 3.7772 | 3.7772 | 3.7772 | 3.7772 | 3.7772 | 3.7772 | 3.7772 | 3.7772 | 3.7772 | 3.7772 | 3.7772 | 3.7772 | 3.7772 | 3.7772 | 3.7772 | 3.7772 | 3.7772 | 3.7772 | 3.7772 | 3.7772 | 3.7772 | 3.7772 | 3.7772 | 3.7772 | 3.7772 | 3.7772 | 3.7772
|  |  | Optimal timing (interim calc) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  |  | Optimal timing | - | - | - | - | - | - | - | - | - | - | - | - | - | Yes | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
[11 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19
Adjusted For Optimal Timing: | 30.5035 | 58.3905 | Capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 58.3905 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 3.2996 | 9.9264 | Opex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839
| 25.0289 | 74.9762 | Reduction in unserved energy | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.0279 | 4.3718 | 4.3718 | 4.3718 | 4.3718 | 4.3718 | 4.3718 | 4.3718 | 4.3718 | 4.3718 | 4.3718 | 4.3718 | 4.3718 | 4.3718 | 4.3718 | 4.3718 | 4.3718
| -8.7741 | 6.6593 | Net benefit | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -58.3905 | 4.444 | 3.7879 | 3.7879 | 3.7879 | 3.7879 | 3.7879 | 3.7879 | 3.7879 | 3.7879 | 3.7879 | 3.7879 | 3.7879 | 3.7879 | 3.7879 | 3.7879 | 3.7879 | 3.7879
Option 5
Determining Optimal Timing: | Discounted | Undiscounted
| 101.2441 | 156.2401 | Capex | 0 | 0 | 78.12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78.12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 9.6837 | 21.0924 | Opex | 0 | 0 | 0 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812
| 33.761 | 89.4746 | Reduction in unserved energy | 0 | 0 | 0 | 0.24442 | 0.31526 | 0.43122 | 0.77684 | 1.1321 | 1.6675 | 1.6179 | 2.2875 | 2.7406 | 3.0807 | 5.0907 | 4.3806 | 4.3806 | 4.3806 | 4.3806 | 4.3806 | 4.3806 | 4.3806 | 4.3806 | 4.3806 | 4.3806 | 4.3806 | 4.3806 | 4.3806 | 4.3806 | 4.3806 | 4.3806
| -77.1668 | -87.8579 | Net benefit | 0 | 0 | -78.12 | -0.53678 | -0.46594 | -0.34998 | -0.0043566 | 0.35087 | 0.88627 | 0.83665 | 1.5063 | 1.9594 | 2.2995 | 4.3095 | 3.5994 | 3.5994 | 3.5994 | -74.5206 | 3.5994 | 3.5994 | 3.5994 | 3.5994 | 3.5994 | 3.5994 | 3.5994 | 3.5994 | 3.5994 | 3.5994 | 3.5994 | 3.5994
|  |  | EUE Value ($m, real $2024) | 0.035548 | 0.26077 | 0.65041 | 0.0038113 | 0.0041704 | 0.00544 | 0.010746 | 0.018623 | 0.034773 | 0.037739 | 0.059864 | 0.059666 | 0.078054 | 0.11978 | 0.10317 | 0.10317 | 0.10317 | 0.10317 | 0.10317 | 0.10317 | 0.10317 | 0.10317 | 0.10317 | 0.10317 | 0.10317 | 0.10317 | 0.10317 | 0.10317 | 0.10317 | 0.10317
|  |  | Annualised capex | 0 | 0 | 10.1268 | 10.1268 | 10.1268 | 10.1268 | 10.1268 | 10.1268 | 10.1268 | 10.1268 | 10.1268 | 10.1268 | 10.1268 | 10.1268 | 10.1268 | 10.1268 | 10.1268 | 10.1268 | 10.1268 | 10.1268 | 10.1268 | 10.1268 | 10.1268 | 10.1268 | 10.1268 | 10.1268 | 10.1268 | 10.1268 | 10.1268 | 10.1268
|  |  | Annualised cost (capex+opex) | 0 | 0 | 10.1268 | 10.908 | 10.908 | 10.908 | 10.908 | 10.908 | 10.908 | 10.908 | 10.908 | 10.908 | 10.908 | 10.908 | 10.908 | 10.908 | 10.908 | 10.908 | 10.908 | 10.908 | 10.908 | 10.908 | 10.908 | 10.908 | 10.908 | 10.908 | 10.908 | 10.908 | 10.908 | 10.908
|  |  | Optimal timing (interim calc) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Optimal timing | - | - | - | - | - | - | - | [19 empty] | - | - | - | - | bar: 1 to 19
Adjusted For Optimal Timing: | 0 | 0 | Capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 9.6837 | 21.0924 | Opex | 0 | 0 | 0 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812
| 9.6837 | 21.0924 | Reduction in unserved energy | 0 | 0 | 0 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812
| 0 | 0 | Net benefit | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 6
Determining Optimal Timing: | Discounted | Undiscounted
| 0 | 0 | Capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Opex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Reduction in unserved energy | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Net benefit | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | EUE Value ($m, real $2024) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Annualised capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Annualised cost (capex+opex) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Optimal timing (interim calc) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Optimal timing | - | - | - | - | - | - | - | [19 empty] | - | - | - | - | bar: 1 to 19
Adjusted For Optimal Timing: | 0 | 0 | Capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Opex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Reduction in unserved energy | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Net benefit | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 7
Determining Optimal Timing: | Discounted | Undiscounted
| 0 | 0 | Capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Opex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Reduction in unserved energy | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Net benefit | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | EUE Value ($m, real $2024) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Annualised capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Annualised cost (capex+opex) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Optimal timing (interim calc) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Optimal timing | - | - | - | - | - | - | - | [19 empty] | - | - | - | - | bar: 1 to 19
Adjusted For Optimal Timing: | 0 | 0 | Capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Opex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Reduction in unserved energy | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Net benefit | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 8
Determining Optimal Timing: | Discounted | Undiscounted
| 0 | 0 | Capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Opex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Reduction in unserved energy | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Net benefit | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | EUE Value ($m, real $2024) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Annualised capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Annualised cost (capex+opex) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Optimal timing (interim calc) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Optimal timing | - | - | - | - | - | - | - | [19 empty] | - | - | - | - | bar: 1 to 19
Adjusted For Optimal Timing: | 0 | 0 | Capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Opex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Reduction in unserved energy | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Net benefit | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 9
Determining Optimal Timing: | Discounted | Undiscounted
| 0 | 0 | Capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Opex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Reduction in unserved energy | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Net benefit | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | EUE Value ($m, real $2024) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Annualised capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Annualised cost (capex+opex) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Optimal timing (interim calc) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Optimal timing | - | - | - | - | - | - | - | [19 empty] | - | - | - | - | bar: 1 to 19
Adjusted For Optimal Timing: | 0 | 0 | Capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Opex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Reduction in unserved energy | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Net benefit | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 10
Determining Optimal Timing: | Discounted | Undiscounted
| 0 | 0 | Capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Opex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Reduction in unserved energy | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Net benefit | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | EUE Value ($m, real $2024) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Annualised capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Annualised cost (capex+opex) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Optimal timing (interim calc) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Optimal timing | - | - | - | - | - | - | - | [19 empty] | - | - | - | - | bar: 1 to 19
Adjusted For Optimal Timing: | 0 | 0 | Capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Opex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Reduction in unserved energy | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Net benefit | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## 3.2.6 NPV (High Demand)
Economic inputs and assumptions
Scenario | Discount rate | Central
| Cost | Central
| VCR | Central
|  | Central | Lower bound | Upper bound
| Discount rate | 5.56% | 4.11% | 7%
| Cost | 100% | 80% | 120%
| VCR | 100% | 80% | 120%
Asset life for calculating annualised capex (years) | Option 1 | 45
| Option 2 | 45
| Option 3 | 45
| Option 4 | 45
| Option 5 | 15
| Option 6 | 45
| Option 7 | 0
| Option 8 | 0
| Option 9 | 0
| Option 10 | 0
|  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30
|  |  |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Outputs | bar: 3 FY27; 7 FY31
Option 1
| Discounted | Undiscounted
| 0 | 0 | Capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Opex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Reduction in unserved energy | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Net benefit | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | EUE Value ($m, real $2024) | 5.8608 | 13.0978 | 21.8339 | 11.2255 | 12.0422 | 14.598 | 25.0662 | 40.4461 | 73.085 | 79.2349 | 130.2164 | 129.9448 | 171.1314 | 273.2963 | 231.7687 | 231.7687 | 231.7687 | 231.7687 | 231.7687 | 231.7687 | 231.7687 | 231.7687 | 231.7687 | 231.7687 | 231.7687 | 231.7687 | 231.7687 | 231.7687 | 231.7687 | 231.7687
Option 2
Determining Optimal Timing: | Discounted | Undiscounted
| 36.2837 | 40.4306 | Capex | 0 | 0 | 40.4306 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 5.0117 | 10.9163 | Opex | 0 | 0 | 0 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431
| 1320.3215 | 3499.8915 | Reduction in unserved energy | 0 | 0 | 0 | 11.0792 | 11.8342 | 14.23 | 23.8251 | 37.1912 | 62.8526 | 67.6592 | 103.4404 | 106.7196 | 131.4385 | 195.1627 | 170.9037 | 170.9037 | 170.9037 | 170.9037 | 170.9037 | 170.9037 | 170.9037 | 170.9037 | 170.9037 | 170.9037 | 170.9037 | 170.9037 | 170.9037 | 170.9037 | 170.9037 | 170.9037
| 1279.026 | 3448.5447 | Net benefit | 0 | 0 | -40.4306 | 10.6749 | 11.4299 | 13.8257 | 23.4207 | 36.7869 | 62.4483 | 67.2549 | 103.0361 | 106.3153 | 131.0342 | 194.7584 | 170.4994 | 170.4994 | 170.4994 | 170.4994 | 170.4994 | 170.4994 | 170.4994 | 170.4994 | 170.4994 | 170.4994 | 170.4994 | 170.4994 | 170.4994 | 170.4994 | 170.4994 | 170.4994
|  |  | EUE Value ($m, real $2024) | 5.8608 | 13.0978 | 21.8339 | 0.1463 | 0.20804 | 0.36802 | 1.2411 | 3.2549 | 10.2324 | 11.5757 | 26.7759 | 23.2252 | 39.6929 | 78.1336 | 60.865 | 60.865 | 60.865 | 60.865 | 60.865 | 60.865 | 60.865 | 60.865 | 60.865 | 60.865 | 60.865 | 60.865 | 60.865 | 60.865 | 60.865 | 60.865
|  |  | Annualised capex | 0 | 0 | 2.2111 | 2.2111 | 2.2111 | 2.2111 | 2.2111 | 2.2111 | 2.2111 | 2.2111 | 2.2111 | 2.2111 | 2.2111 | 2.2111 | 2.2111 | 2.2111 | 2.2111 | 2.2111 | 2.2111 | 2.2111 | 2.2111 | 2.2111 | 2.2111 | 2.2111 | 2.2111 | 2.2111 | 2.2111 | 2.2111 | 2.2111 | 2.2111
|  |  | Annualised cost (capex+opex) | 0 | 0 | 2.2111 | 2.6154 | 2.6154 | 2.6154 | 2.6154 | 2.6154 | 2.6154 | 2.6154 | 2.6154 | 2.6154 | 2.6154 | 2.6154 | 2.6154 | 2.6154 | 2.6154 | 2.6154 | 2.6154 | 2.6154 | 2.6154 | 2.6154 | 2.6154 | 2.6154 | 2.6154 | 2.6154 | 2.6154 | 2.6154 | 2.6154 | 2.6154
|  |  | Optimal timing (interim calc) | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  |  | Optimal timing | - | - | - | Yes | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Adjusted For Optimal Timing: | 36.2837 | 40.4306 | Capex | 0 | 0 | 40.4306 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 5.0117 | 10.9163 | Opex | 0 | 0 | 0 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431
| 1320.3215 | 3499.8915 | Reduction in unserved energy | 0 | 0 | 0 | 11.0792 | 11.8342 | 14.23 | 23.8251 | 37.1912 | 62.8526 | 67.6592 | 103.4404 | 106.7196 | 131.4385 | 195.1627 | 170.9037 | 170.9037 | 170.9037 | 170.9037 | 170.9037 | 170.9037 | 170.9037 | 170.9037 | 170.9037 | 170.9037 | 170.9037 | 170.9037 | 170.9037 | 170.9037 | 170.9037 | 170.9037
| 1279.026 | 3448.5447 | Net benefit | 0 | 0 | -40.4306 | 10.6749 | 11.4299 | 13.8257 | 23.4207 | 36.7869 | 62.4483 | 67.2549 | 103.0361 | 106.3153 | 131.0342 | 194.7584 | 170.4994 | 170.4994 | 170.4994 | 170.4994 | 170.4994 | 170.4994 | 170.4994 | 170.4994 | 170.4994 | 170.4994 | 170.4994 | 170.4994 | 170.4994 | 170.4994 | 170.4994 | 170.4994
Option 3
Determining Optimal Timing: | Discounted | Undiscounted
| 59.0686 | 65.8197 | Capex | 0 | 0 | 65.8197 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 8.159 | 17.7713 | Opex | 0 | 0 | 0 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582
| 1317.9689 | 3496.9802 | Reduction in unserved energy | 0 | 0 | 0 | 11.1235 | 11.8966 | 14.2963 | 23.6981 | 36.6064 | 61.7275 | 66.44 | 102.4475 | 105.0566 | 130.5806 | 196.9007 | 171.0129 | 171.0129 | 171.0129 | 171.0129 | 171.0129 | 171.0129 | 171.0129 | 171.0129 | 171.0129 | 171.0129 | 171.0129 | 171.0129 | 171.0129 | 171.0129 | 171.0129 | 171.0129
| 1250.7413 | 3413.3892 | Net benefit | 0 | 0 | -65.8197 | 10.4653 | 11.2384 | 13.6381 | 23.0399 | 35.9482 | 61.0693 | 65.7818 | 101.7893 | 104.3985 | 129.9224 | 196.2426 | 170.3547 | 170.3547 | 170.3547 | 170.3547 | 170.3547 | 170.3547 | 170.3547 | 170.3547 | 170.3547 | 170.3547 | 170.3547 | 170.3547 | 170.3547 | 170.3547 | 170.3547 | 170.3547
|  |  | EUE Value ($m, real $2024) | 5.8608 | 13.0978 | 21.8339 | 0.10202 | 0.14566 | 0.30173 | 1.368 | 3.8397 | 11.3575 | 12.7949 | 27.7689 | 24.8881 | 40.5508 | 76.3955 | 60.7558 | 60.7558 | 60.7558 | 60.7558 | 60.7558 | 60.7558 | 60.7558 | 60.7558 | 60.7558 | 60.7558 | 60.7558 | 60.7558 | 60.7558 | 60.7558 | 60.7558 | 60.7558
|  |  | Annualised capex | 0 | 0 | 3.5996 | 3.5996 | 3.5996 | 3.5996 | 3.5996 | 3.5996 | 3.5996 | 3.5996 | 3.5996 | 3.5996 | 3.5996 | 3.5996 | 3.5996 | 3.5996 | 3.5996 | 3.5996 | 3.5996 | 3.5996 | 3.5996 | 3.5996 | 3.5996 | 3.5996 | 3.5996 | 3.5996 | 3.5996 | 3.5996 | 3.5996 | 3.5996
|  |  | Annualised cost (capex+opex) | 0 | 0 | 3.5996 | 4.2578 | 4.2578 | 4.2578 | 4.2578 | 4.2578 | 4.2578 | 4.2578 | 4.2578 | 4.2578 | 4.2578 | 4.2578 | 4.2578 | 4.2578 | 4.2578 | 4.2578 | 4.2578 | 4.2578 | 4.2578 | 4.2578 | 4.2578 | 4.2578 | 4.2578 | 4.2578 | 4.2578 | 4.2578 | 4.2578 | 4.2578
|  |  | Optimal timing (interim calc) | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  |  | Optimal timing | - | - | - | Yes | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Adjusted For Optimal Timing: | 59.0686 | 65.8197 | Capex | 0 | 0 | 65.8197 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 8.159 | 17.7713 | Opex | 0 | 0 | 0 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582
| 1317.9689 | 3496.9802 | Reduction in unserved energy | 0 | 0 | 0 | 11.1235 | 11.8966 | 14.2963 | 23.6981 | 36.6064 | 61.7275 | 66.44 | 102.4475 | 105.0566 | 130.5806 | 196.9007 | 171.0129 | 171.0129 | 171.0129 | 171.0129 | 171.0129 | 171.0129 | 171.0129 | 171.0129 | 171.0129 | 171.0129 | 171.0129 | 171.0129 | 171.0129 | 171.0129 | 171.0129 | 171.0129
| 1250.7413 | 3413.3892 | Net benefit | 0 | 0 | -65.8197 | 10.4653 | 11.2384 | 13.6381 | 23.0399 | 35.9482 | 61.0693 | 65.7818 | 101.7893 | 104.3985 | 129.9224 | 196.2426 | 170.3547 | 170.3547 | 170.3547 | 170.3547 | 170.3547 | 170.3547 | 170.3547 | 170.3547 | 170.3547 | 170.3547 | 170.3547 | 170.3547 | 170.3547 | 170.3547 | 170.3547 | 170.3547
Option 4
Determining Optimal Timing: | Discounted | Undiscounted
| 52.4015 | 58.3905 | Capex | 0 | 0 | 58.3905 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 7.238 | 15.7654 | Opex | 0 | 0 | 0 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839
| 1345.5329 | 3571.4467 | Reduction in unserved energy | 0 | 0 | 0 | 11.1427 | 11.9219 | 14.3385 | 23.8965 | 37.1516 | 62.9515 | 67.8297 | 104.7605 | 107.315 | 133.5406 | 201.1443 | 174.7159 | 174.7159 | 174.7159 | 174.7159 | 174.7159 | 174.7159 | 174.7159 | 174.7159 | 174.7159 | 174.7159 | 174.7159 | 174.7159 | 174.7159 | 174.7159 | 174.7159 | 174.7159
| 1285.8934 | 3497.2908 | Net benefit | 0 | 0 | -58.3905 | 10.5588 | 11.338 | 13.7546 | 23.3126 | 36.5677 | 62.3676 | 67.2458 | 104.1766 | 106.7311 | 132.9566 | 200.5604 | 174.132 | 174.132 | 174.132 | 174.132 | 174.132 | 174.132 | 174.132 | 174.132 | 174.132 | 174.132 | 174.132 | 174.132 | 174.132 | 174.132 | 174.132 | 174.132
|  |  | EUE Value ($m, real $2024) | 5.8608 | 13.0978 | 21.8339 | 0.082816 | 0.12033 | 0.25955 | 1.1697 | 3.2945 | 10.1335 | 11.4052 | 25.4558 | 22.6298 | 37.5908 | 72.152 | 57.0528 | 57.0528 | 57.0528 | 57.0528 | 57.0528 | 57.0528 | 57.0528 | 57.0528 | 57.0528 | 57.0528 | 57.0528 | 57.0528 | 57.0528 | 57.0528 | 57.0528 | 57.0528
|  |  | Annualised capex | 0 | 0 | 3.1933 | 3.1933 | 3.1933 | 3.1933 | 3.1933 | 3.1933 | 3.1933 | 3.1933 | 3.1933 | 3.1933 | 3.1933 | 3.1933 | 3.1933 | 3.1933 | 3.1933 | 3.1933 | 3.1933 | 3.1933 | 3.1933 | 3.1933 | 3.1933 | 3.1933 | 3.1933 | 3.1933 | 3.1933 | 3.1933 | 3.1933 | 3.1933
|  |  | Annualised cost (capex+opex) | 0 | 0 | 3.1933 | 3.7772 | 3.7772 | 3.7772 | 3.7772 | 3.7772 | 3.7772 | 3.7772 | 3.7772 | 3.7772 | 3.7772 | 3.7772 | 3.7772 | 3.7772 | 3.7772 | 3.7772 | 3.7772 | 3.7772 | 3.7772 | 3.7772 | 3.7772 | 3.7772 | 3.7772 | 3.7772 | 3.7772 | 3.7772 | 3.7772 | 3.7772
|  |  | Optimal timing (interim calc) | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  |  | Optimal timing | - | - | - | Yes | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
[11 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19
Adjusted For Optimal Timing: | 52.4015 | 58.3905 | Capex | 0 | 0 | 58.3905 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 7.238 | 15.7654 | Opex | 0 | 0 | 0 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839
| 1345.5329 | 3571.4467 | Reduction in unserved energy | 0 | 0 | 0 | 11.1427 | 11.9219 | 14.3385 | 23.8965 | 37.1516 | 62.9515 | 67.8297 | 104.7605 | 107.315 | 133.5406 | 201.1443 | 174.7159 | 174.7159 | 174.7159 | 174.7159 | 174.7159 | 174.7159 | 174.7159 | 174.7159 | 174.7159 | 174.7159 | 174.7159 | 174.7159 | 174.7159 | 174.7159 | 174.7159 | 174.7159
| 1285.8934 | 3497.2908 | Net benefit | 0 | 0 | -58.3905 | 10.5588 | 11.338 | 13.7546 | 23.3126 | 36.5677 | 62.3676 | 67.2458 | 104.1766 | 106.7311 | 132.9566 | 200.5604 | 174.132 | 174.132 | 174.132 | 174.132 | 174.132 | 174.132 | 174.132 | 174.132 | 174.132 | 174.132 | 174.132 | 174.132 | 174.132 | 174.132 | 174.132 | 174.132
Option 5
Determining Optimal Timing: | Discounted | Undiscounted
| 101.2441 | 156.2401 | Capex | 0 | 0 | 78.12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78.12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 9.6837 | 21.0924 | Opex | 0 | 0 | 0 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812
| 1701.9549 | 4565.5199 | Reduction in unserved energy | 0 | 0 | 0 | 11.1532 | 11.9389 | 14.4323 | 24.6715 | 39.7764 | 71.8925 | 78.0798 | 128.0039 | 127.6712 | 167.8834 | 266.4467 | 226.4731 | 226.4731 | 226.4731 | 226.4731 | 226.4731 | 226.4731 | 226.4731 | 226.4731 | 226.4731 | 226.4731 | 226.4731 | 226.4731 | 226.4731 | 226.4731 | 226.4731 | 226.4731
| 1591.0271 | 4388.1874 | Net benefit | 0 | 0 | -78.12 | 10.372 | 11.1577 | 13.6511 | 23.8903 | 38.9952 | 71.1113 | 77.2986 | 127.2227 | 126.89 | 167.1022 | 265.6655 | 225.6919 | 225.6919 | 225.6919 | 147.5719 | 225.6919 | 225.6919 | 225.6919 | 225.6919 | 225.6919 | 225.6919 | 225.6919 | 225.6919 | 225.6919 | 225.6919 | 225.6919 | 225.6919
|  |  | EUE Value ($m, real $2024) | 5.8608 | 13.0978 | 21.8339 | 0.072356 | 0.10331 | 0.16568 | 0.39463 | 0.66972 | 1.1925 | 1.1551 | 2.2125 | 2.2736 | 3.248 | 6.8496 | 5.2956 | 5.2956 | 5.2956 | 5.2956 | 5.2956 | 5.2956 | 5.2956 | 5.2956 | 5.2956 | 5.2956 | 5.2956 | 5.2956 | 5.2956 | 5.2956 | 5.2956 | 5.2956
|  |  | Annualised capex | 0 | 0 | 10.1268 | 10.1268 | 10.1268 | 10.1268 | 10.1268 | 10.1268 | 10.1268 | 10.1268 | 10.1268 | 10.1268 | 10.1268 | 10.1268 | 10.1268 | 10.1268 | 10.1268 | 10.1268 | 10.1268 | 10.1268 | 10.1268 | 10.1268 | 10.1268 | 10.1268 | 10.1268 | 10.1268 | 10.1268 | 10.1268 | 10.1268 | 10.1268
|  |  | Annualised cost (capex+opex) | 0 | 0 | 10.1268 | 10.908 | 10.908 | 10.908 | 10.908 | 10.908 | 10.908 | 10.908 | 10.908 | 10.908 | 10.908 | 10.908 | 10.908 | 10.908 | 10.908 | 10.908 | 10.908 | 10.908 | 10.908 | 10.908 | 10.908 | 10.908 | 10.908 | 10.908 | 10.908 | 10.908 | 10.908 | 10.908
|  |  | Optimal timing (interim calc) | 0 | 0 | 0 | 1 | 1 | 1 | 1 | [19 empty] | 1 | 1 | 1 | 1 | bar: 1 to 19
|  |  | Optimal timing | - | - | - | Yes | - | - | - | [19 empty] | - | - | - | - | bar: 1 to 19
Adjusted For Optimal Timing: | 101.2441 | 156.2401 | Capex | 0 | 0 | 78.12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78.12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 9.6837 | 21.0924 | Opex | 0 | 0 | 0 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812
| 1701.9549 | 4565.5199 | Reduction in unserved energy | 0 | 0 | 0 | 11.1532 | 11.9389 | 14.4323 | 24.6715 | 39.7764 | 71.8925 | 78.0798 | 128.0039 | 127.6712 | 167.8834 | 266.4467 | 226.4731 | 226.4731 | 226.4731 | 226.4731 | 226.4731 | 226.4731 | 226.4731 | 226.4731 | 226.4731 | 226.4731 | 226.4731 | 226.4731 | 226.4731 | 226.4731 | 226.4731 | 226.4731
| 1591.0271 | 4388.1874 | Net benefit | 0 | 0 | -78.12 | 10.372 | 11.1577 | 13.6511 | 23.8903 | 38.9952 | 71.1113 | 77.2986 | 127.2227 | 126.89 | 167.1022 | 265.6655 | 225.6919 | 225.6919 | 225.6919 | 147.5719 | 225.6919 | 225.6919 | 225.6919 | 225.6919 | 225.6919 | 225.6919 | 225.6919 | 225.6919 | 225.6919 | 225.6919 | 225.6919 | 225.6919
Option 6
Determining Optimal Timing: | Discounted | Undiscounted
| 0 | 0 | Capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Opex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Reduction in unserved energy | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Net benefit | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | EUE Value ($m, real $2024) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Annualised capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Annualised cost (capex+opex) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Optimal timing (interim calc) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Optimal timing | - | - | - | - | - | - | - | [19 empty] | - | - | - | - | bar: 1 to 19
Adjusted For Optimal Timing: | 0 | 0 | Capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Opex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Reduction in unserved energy | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Net benefit | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 7
Determining Optimal Timing: | Discounted | Undiscounted
| 0 | 0 | Capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Opex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Reduction in unserved energy | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Net benefit | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | EUE Value ($m, real $2024) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Annualised capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Annualised cost (capex+opex) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Optimal timing (interim calc) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Optimal timing | - | - | - | - | - | - | - | [19 empty] | - | - | - | - | bar: 1 to 19
Adjusted For Optimal Timing: | 0 | 0 | Capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Opex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Reduction in unserved energy | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Net benefit | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 8
Determining Optimal Timing: | Discounted | Undiscounted
| 0 | 0 | Capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Opex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Reduction in unserved energy | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Net benefit | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | EUE Value ($m, real $2024) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Annualised capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Annualised cost (capex+opex) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Optimal timing (interim calc) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Optimal timing | - | - | - | - | - | - | - | [19 empty] | - | - | - | - | bar: 1 to 19
Adjusted For Optimal Timing: | 0 | 0 | Capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Opex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Reduction in unserved energy | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Net benefit | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 9
Determining Optimal Timing: | Discounted | Undiscounted
| 0 | 0 | Capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Opex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Reduction in unserved energy | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Net benefit | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | EUE Value ($m, real $2024) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Annualised capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Annualised cost (capex+opex) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Optimal timing (interim calc) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Optimal timing | - | - | - | - | - | - | - | [19 empty] | - | - | - | - | bar: 1 to 19
Adjusted For Optimal Timing: | 0 | 0 | Capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Opex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Reduction in unserved energy | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Net benefit | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 10
Determining Optimal Timing: | Discounted | Undiscounted
| 0 | 0 | Capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Opex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Reduction in unserved energy | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Net benefit | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | EUE Value ($m, real $2024) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Annualised capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Annualised cost (capex+opex) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Optimal timing (interim calc) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Optimal timing | - | - | - | - | - | - | - | [19 empty] | - | - | - | - | bar: 1 to 19
Adjusted For Optimal Timing: | 0 | 0 | Capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Opex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Reduction in unserved energy | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Net benefit | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## 3.2.7 NPV (Low VCR)
Economic inputs and assumptions
Scenario | Discount rate | Central
| Cost | Central
| VCR | Lower bound
|  | Central | Lower bound | Upper bound
| Discount rate | 5.56% | 4.11% | 7%
| Cost | 100% | 80% | 120%
| VCR | 100% | 80% | 120%
Asset life for calculating annualised capex (years) | Option 1 | 45
| Option 2 | 45
| Option 3 | 45
| Option 4 | 45
| Option 5 | 15
| Option 6 | 45
| Option 7 | 0
| Option 8 | 0
| Option 9 | 0
| Option 10 | 0
|  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30
|  |  |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Outputs | bar: 3 FY27; 7 FY31
Option 1
| Discounted | Undiscounted
| 0 | 0 | Capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Opex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Reduction in unserved energy | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Net benefit | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | EUE Value ($m, real $2024) | 0.89097 | 2.1089 | 3.868 | 1.8891 | 2.0718 | 2.3919 | 3.7912 | 5.7173 | 9.1332 | 9.7238 | 17.016 | 18.673 | 22.7537 | 42.5228 | 34.6575 | 34.6575 | 34.6575 | 34.6575 | 34.6575 | 34.6575 | 34.6575 | 34.6575 | 34.6575 | 34.6575 | 34.6575 | 34.6575 | 34.6575 | 34.6575 | 34.6575 | 34.6575
Option 2
Determining Optimal Timing: | Discounted | Undiscounted
| 36.2837 | 40.4306 | Capex | 0 | 0 | 40.4306 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 5.0117 | 10.9163 | Opex | 0 | 0 | 0 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431
| 228.3863 | 613.9018 | Reduction in unserved energy | 0 | 0 | 0 | 1.8591 | 2.0269 | 2.3219 | 3.6637 | 5.5177 | 8.7044 | 9.2334 | 15.6678 | 17.5921 | 20.7 | 36.6095 | 30.6253 | 30.6253 | 30.6253 | 30.6253 | 30.6253 | 30.6253 | 30.6253 | 30.6253 | 30.6253 | 30.6253 | 30.6253 | 30.6253 | 30.6253 | 30.6253 | 30.6253 | 30.6253
| 187.0909 | 562.5549 | Net benefit | 0 | 0 | -40.4306 | 1.4548 | 1.6225 | 1.9176 | 3.2594 | 5.1134 | 8.3001 | 8.8291 | 15.2635 | 17.1878 | 20.2957 | 36.2052 | 30.221 | 30.221 | 30.221 | 30.221 | 30.221 | 30.221 | 30.221 | 30.221 | 30.221 | 30.221 | 30.221 | 30.221 | 30.221 | 30.221 | 30.221 | 30.221
|  |  | EUE Value ($m, real $2024) | 0.89097 | 2.1089 | 3.868 | 0.02995 | 0.044928 | 0.070029 | 0.12743 | 0.19965 | 0.42875 | 0.49033 | 1.3482 | 1.0809 | 2.0537 | 5.9133 | 4.0322 | 4.0322 | 4.0322 | 4.0322 | 4.0322 | 4.0322 | 4.0322 | 4.0322 | 4.0322 | 4.0322 | 4.0322 | 4.0322 | 4.0322 | 4.0322 | 4.0322 | 4.0322
|  |  | Annualised capex | 0 | 0 | 2.2111 | 2.2111 | 2.2111 | 2.2111 | 2.2111 | 2.2111 | 2.2111 | 2.2111 | 2.2111 | 2.2111 | 2.2111 | 2.2111 | 2.2111 | 2.2111 | 2.2111 | 2.2111 | 2.2111 | 2.2111 | 2.2111 | 2.2111 | 2.2111 | 2.2111 | 2.2111 | 2.2111 | 2.2111 | 2.2111 | 2.2111 | 2.2111
|  |  | Annualised cost (capex+opex) | 0 | 0 | 2.2111 | 2.6154 | 2.6154 | 2.6154 | 2.6154 | 2.6154 | 2.6154 | 2.6154 | 2.6154 | 2.6154 | 2.6154 | 2.6154 | 2.6154 | 2.6154 | 2.6154 | 2.6154 | 2.6154 | 2.6154 | 2.6154 | 2.6154 | 2.6154 | 2.6154 | 2.6154 | 2.6154 | 2.6154 | 2.6154 | 2.6154 | 2.6154
|  |  | Optimal timing (interim calc) | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  |  | Optimal timing | - | - | - | - | - | - | Yes | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Adjusted For Optimal Timing: | 30.847 | 40.4306 | Capex | 0 | 0 | 0 | 0 | 0 | 40.4306 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 4.0339 | 9.7033 | Opex | 0 | 0 | 0 | 0 | 0 | 0 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431
| 223.4019 | 607.6939 | Reduction in unserved energy | 0 | 0 | 0 | 0 | 0 | 0 | 3.6637 | 5.5177 | 8.7044 | 9.2334 | 15.6678 | 17.5921 | 20.7 | 36.6095 | 30.6253 | 30.6253 | 30.6253 | 30.6253 | 30.6253 | 30.6253 | 30.6253 | 30.6253 | 30.6253 | 30.6253 | 30.6253 | 30.6253 | 30.6253 | 30.6253 | 30.6253 | 30.6253
| 188.5209 | 557.56 | Net benefit | 0 | 0 | 0 | 0 | 0 | -40.4306 | 3.2594 | 5.1134 | 8.3001 | 8.8291 | 15.2635 | 17.1878 | 20.2957 | 36.2052 | 30.221 | 30.221 | 30.221 | 30.221 | 30.221 | 30.221 | 30.221 | 30.221 | 30.221 | 30.221 | 30.221 | 30.221 | 30.221 | 30.221 | 30.221 | 30.221
Option 3
Determining Optimal Timing: | Discounted | Undiscounted
| 59.0686 | 65.8197 | Capex | 0 | 0 | 65.8197 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 8.159 | 17.7713 | Opex | 0 | 0 | 0 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582
| 226.0765 | 606.5299 | Reduction in unserved energy | 0 | 0 | 0 | 1.8842 | 2.0654 | 2.3815 | 3.7669 | 5.6404 | 8.7874 | 9.2994 | 15.6422 | 17.6004 | 20.4231 | 36.2369 | 30.1751 | 30.1751 | 30.1751 | 30.1751 | 30.1751 | 30.1751 | 30.1751 | 30.1751 | 30.1751 | 30.1751 | 30.1751 | 30.1751 | 30.1751 | 30.1751 | 30.1751 | 30.1751
| 158.8489 | 522.9389 | Net benefit | 0 | 0 | -65.8197 | 1.226 | 1.4072 | 1.7233 | 3.1087 | 4.9822 | 8.1292 | 8.6412 | 14.984 | 16.9422 | 19.7649 | 35.5787 | 29.5169 | 29.5169 | 29.5169 | 29.5169 | 29.5169 | 29.5169 | 29.5169 | 29.5169 | 29.5169 | 29.5169 | 29.5169 | 29.5169 | 29.5169 | 29.5169 | 29.5169 | 29.5169
|  |  | EUE Value ($m, real $2024) | 0.89097 | 2.1089 | 3.868 | 0.0048278 | 0.0063981 | 0.010449 | 0.024237 | 0.07692 | 0.34579 | 0.42435 | 1.3738 | 1.0726 | 2.3306 | 6.2859 | 4.4824 | 4.4824 | 4.4824 | 4.4824 | 4.4824 | 4.4824 | 4.4824 | 4.4824 | 4.4824 | 4.4824 | 4.4824 | 4.4824 | 4.4824 | 4.4824 | 4.4824 | 4.4824
|  |  | Annualised capex | 0 | 0 | 3.5996 | 3.5996 | 3.5996 | 3.5996 | 3.5996 | 3.5996 | 3.5996 | 3.5996 | 3.5996 | 3.5996 | 3.5996 | 3.5996 | 3.5996 | 3.5996 | 3.5996 | 3.5996 | 3.5996 | 3.5996 | 3.5996 | 3.5996 | 3.5996 | 3.5996 | 3.5996 | 3.5996 | 3.5996 | 3.5996 | 3.5996 | 3.5996
|  |  | Annualised cost (capex+opex) | 0 | 0 | 3.5996 | 4.2578 | 4.2578 | 4.2578 | 4.2578 | 4.2578 | 4.2578 | 4.2578 | 4.2578 | 4.2578 | 4.2578 | 4.2578 | 4.2578 | 4.2578 | 4.2578 | 4.2578 | 4.2578 | 4.2578 | 4.2578 | 4.2578 | 4.2578 | 4.2578 | 4.2578 | 4.2578 | 4.2578 | 4.2578 | 4.2578 | 4.2578
|  |  | Optimal timing (interim calc) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  |  | Optimal timing | - | - | - | - | - | - | - | Yes | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Adjusted For Optimal Timing: | 47.5729 | 65.8197 | Capex | 0 | 0 | 0 | 0 | 0 | 0 | 65.8197 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 6.0914 | 15.1385 | Opex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582
| 218.2716 | 596.4318 | Reduction in unserved energy | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.6404 | 8.7874 | 9.2994 | 15.6422 | 17.6004 | 20.4231 | 36.2369 | 30.1751 | 30.1751 | 30.1751 | 30.1751 | 30.1751 | 30.1751 | 30.1751 | 30.1751 | 30.1751 | 30.1751 | 30.1751 | 30.1751 | 30.1751 | 30.1751 | 30.1751 | 30.1751
| 164.6073 | 515.4736 | Net benefit | 0 | 0 | 0 | 0 | 0 | 0 | -65.8197 | 4.9822 | 8.1292 | 8.6412 | 14.984 | 16.9422 | 19.7649 | 35.5787 | 29.5169 | 29.5169 | 29.5169 | 29.5169 | 29.5169 | 29.5169 | 29.5169 | 29.5169 | 29.5169 | 29.5169 | 29.5169 | 29.5169 | 29.5169 | 29.5169 | 29.5169 | 29.5169
Option 4
Determining Optimal Timing: | Discounted | Undiscounted
| 52.4015 | 58.3905 | Capex | 0 | 0 | 58.3905 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 7.238 | 15.7654 | Opex | 0 | 0 | 0 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839
| 229.7693 | 617.0664 | Reduction in unserved energy | 0 | 0 | 0 | 1.8801 | 2.061 | 2.3764 | 3.76 | 5.643 | 8.8436 | 9.3689 | 15.8262 | 17.7408 | 20.7846 | 36.9019 | 30.7425 | 30.7425 | 30.7425 | 30.7425 | 30.7425 | 30.7425 | 30.7425 | 30.7425 | 30.7425 | 30.7425 | 30.7425 | 30.7425 | 30.7425 | 30.7425 | 30.7425 | 30.7425
| 170.1299 | 542.9105 | Net benefit | 0 | 0 | -58.3905 | 1.2962 | 1.4771 | 1.7925 | 3.176 | 5.0591 | 8.2597 | 8.785 | 15.2423 | 17.1569 | 20.2007 | 36.318 | 30.1586 | 30.1586 | 30.1586 | 30.1586 | 30.1586 | 30.1586 | 30.1586 | 30.1586 | 30.1586 | 30.1586 | 30.1586 | 30.1586 | 30.1586 | 30.1586 | 30.1586 | 30.1586
|  |  | EUE Value ($m, real $2024) | 0.89097 | 2.1089 | 3.868 | 0.0089691 | 0.01077 | 0.015526 | 0.031219 | 0.074295 | 0.28962 | 0.35488 | 1.1898 | 0.93219 | 1.9691 | 5.6209 | 3.915 | 3.915 | 3.915 | 3.915 | 3.915 | 3.915 | 3.915 | 3.915 | 3.915 | 3.915 | 3.915 | 3.915 | 3.915 | 3.915 | 3.915 | 3.915
|  |  | Annualised capex | 0 | 0 | 3.1933 | 3.1933 | 3.1933 | 3.1933 | 3.1933 | 3.1933 | 3.1933 | 3.1933 | 3.1933 | 3.1933 | 3.1933 | 3.1933 | 3.1933 | 3.1933 | 3.1933 | 3.1933 | 3.1933 | 3.1933 | 3.1933 | 3.1933 | 3.1933 | 3.1933 | 3.1933 | 3.1933 | 3.1933 | 3.1933 | 3.1933 | 3.1933
|  |  | Annualised cost (capex+opex) | 0 | 0 | 3.1933 | 3.7772 | 3.7772 | 3.7772 | 3.7772 | 3.7772 | 3.7772 | 3.7772 | 3.7772 | 3.7772 | 3.7772 | 3.7772 | 3.7772 | 3.7772 | 3.7772 | 3.7772 | 3.7772 | 3.7772 | 3.7772 | 3.7772 | 3.7772 | 3.7772 | 3.7772 | 3.7772 | 3.7772 | 3.7772 | 3.7772 | 3.7772
|  |  | Optimal timing (interim calc) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  |  | Optimal timing | - | - | - | - | - | - | - | Yes | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
[11 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19
Adjusted For Optimal Timing: | 42.2032 | 58.3905 | Capex | 0 | 0 | 0 | 0 | 0 | 0 | 58.3905 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 5.4038 | 13.4298 | Opex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839
| 221.9803 | 606.9889 | Reduction in unserved energy | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.643 | 8.8436 | 9.3689 | 15.8262 | 17.7408 | 20.7846 | 36.9019 | 30.7425 | 30.7425 | 30.7425 | 30.7425 | 30.7425 | 30.7425 | 30.7425 | 30.7425 | 30.7425 | 30.7425 | 30.7425 | 30.7425 | 30.7425 | 30.7425 | 30.7425 | 30.7425
| 174.3733 | 535.1686 | Net benefit | 0 | 0 | 0 | 0 | 0 | 0 | -58.3905 | 5.0591 | 8.2597 | 8.785 | 15.2423 | 17.1569 | 20.2007 | 36.318 | 30.1586 | 30.1586 | 30.1586 | 30.1586 | 30.1586 | 30.1586 | 30.1586 | 30.1586 | 30.1586 | 30.1586 | 30.1586 | 30.1586 | 30.1586 | 30.1586 | 30.1586 | 30.1586
Option 5
Determining Optimal Timing: | Discounted | Undiscounted
| 101.2441 | 156.2401 | Capex | 0 | 0 | 78.12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78.12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 9.6837 | 21.0924 | Opex | 0 | 0 | 0 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812
| 252.7538 | 682.9285 | Reduction in unserved energy | 0 | 0 | 0 | 1.875 | 2.0537 | 2.365 | 3.7385 | 5.6346 | 8.9978 | 9.5797 | 16.8163 | 18.4766 | 22.5057 | 42.1215 | 34.2978 | 34.2978 | 34.2978 | 34.2978 | 34.2978 | 34.2978 | 34.2978 | 34.2978 | 34.2978 | 34.2978 | 34.2978 | 34.2978 | 34.2978 | 34.2978 | 34.2978 | 34.2978
| 141.826 | 505.596 | Net benefit | 0 | 0 | -78.12 | 1.0938 | 1.2725 | 1.5838 | 2.9573 | 4.8534 | 8.2166 | 8.7985 | 16.0351 | 17.6954 | 21.7245 | 41.3403 | 33.5166 | 33.5166 | 33.5166 | -44.6035 | 33.5166 | 33.5166 | 33.5166 | 33.5166 | 33.5166 | 33.5166 | 33.5166 | 33.5166 | 33.5166 | 33.5166 | 33.5166 | 33.5166
|  |  | EUE Value ($m, real $2024) | 0.89097 | 2.1089 | 3.868 | 0.014064 | 0.018075 | 0.026949 | 0.052687 | 0.082761 | 0.13537 | 0.14411 | 0.19972 | 0.19637 | 0.248 | 0.40124 | 0.35978 | 0.35978 | 0.35978 | 0.35978 | 0.35978 | 0.35978 | 0.35978 | 0.35978 | 0.35978 | 0.35978 | 0.35978 | 0.35978 | 0.35978 | 0.35978 | 0.35978 | 0.35978
|  |  | Annualised capex | 0 | 0 | 10.1268 | 10.1268 | 10.1268 | 10.1268 | 10.1268 | 10.1268 | 10.1268 | 10.1268 | 10.1268 | 10.1268 | 10.1268 | 10.1268 | 10.1268 | 10.1268 | 10.1268 | 10.1268 | 10.1268 | 10.1268 | 10.1268 | 10.1268 | 10.1268 | 10.1268 | 10.1268 | 10.1268 | 10.1268 | 10.1268 | 10.1268 | 10.1268
|  |  | Annualised cost (capex+opex) | 0 | 0 | 10.1268 | 10.908 | 10.908 | 10.908 | 10.908 | 10.908 | 10.908 | 10.908 | 10.908 | 10.908 | 10.908 | 10.908 | 10.908 | 10.908 | 10.908 | 10.908 | 10.908 | 10.908 | 10.908 | 10.908 | 10.908 | 10.908 | 10.908 | 10.908 | 10.908 | 10.908 | 10.908 | 10.908
|  |  | Optimal timing (interim calc) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  |  | Optimal timing | - | - | - | - | - | - | - | - | - | - | Yes | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Adjusted For Optimal Timing: | 69.3225 | 156.2401 | Capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78.12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78.12 | 0 | 0 | 0 | 0 | 0
| 5.7081 | 15.624 | Opex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812
| 229.4184 | 648.6843 | Reduction in unserved energy | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.8163 | 18.4766 | 22.5057 | 42.1215 | 34.2978 | 34.2978 | 34.2978 | 34.2978 | 34.2978 | 34.2978 | 34.2978 | 34.2978 | 34.2978 | 34.2978 | 34.2978 | 34.2978 | 34.2978 | 34.2978 | 34.2978 | 34.2978
| 154.3879 | 476.8202 | Net benefit | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -78.12 | 16.0351 | 17.6954 | 21.7245 | 41.3403 | 33.5166 | 33.5166 | 33.5166 | 33.5166 | 33.5166 | 33.5166 | 33.5166 | 33.5166 | 33.5166 | 33.5166 | -44.6035 | 33.5166 | 33.5166 | 33.5166 | 33.5166 | 33.5166
Option 6
Determining Optimal Timing: | Discounted | Undiscounted
| 0 | 0 | Capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Opex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Reduction in unserved energy | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Net benefit | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | EUE Value ($m, real $2024) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Annualised capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Annualised cost (capex+opex) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Optimal timing (interim calc) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Optimal timing | - | - | - | - | - | - | - | [19 empty] | - | - | - | - | bar: 1 to 19
Adjusted For Optimal Timing: | 0 | 0 | Capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Opex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Reduction in unserved energy | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Net benefit | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 7
Determining Optimal Timing: | Discounted | Undiscounted
| 0 | 0 | Capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Opex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Reduction in unserved energy | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Net benefit | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | EUE Value ($m, real $2024) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Annualised capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Annualised cost (capex+opex) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Optimal timing (interim calc) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Optimal timing | - | - | - | - | - | - | - | [19 empty] | - | - | - | - | bar: 1 to 19
Adjusted For Optimal Timing: | 0 | 0 | Capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Opex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Reduction in unserved energy | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Net benefit | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 8
Determining Optimal Timing: | Discounted | Undiscounted
| 0 | 0 | Capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Opex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Reduction in unserved energy | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Net benefit | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | EUE Value ($m, real $2024) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Annualised capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Annualised cost (capex+opex) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Optimal timing (interim calc) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Optimal timing | - | - | - | - | - | - | - | [19 empty] | - | - | - | - | bar: 1 to 19
Adjusted For Optimal Timing: | 0 | 0 | Capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Opex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Reduction in unserved energy | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Net benefit | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 9
Determining Optimal Timing: | Discounted | Undiscounted
| 0 | 0 | Capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Opex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Reduction in unserved energy | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Net benefit | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | EUE Value ($m, real $2024) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Annualised capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Annualised cost (capex+opex) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Optimal timing (interim calc) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Optimal timing | - | - | - | - | - | - | - | [19 empty] | - | - | - | - | bar: 1 to 19
Adjusted For Optimal Timing: | 0 | 0 | Capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Opex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Reduction in unserved energy | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Net benefit | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 10
Determining Optimal Timing: | Discounted | Undiscounted
| 0 | 0 | Capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Opex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Reduction in unserved energy | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Net benefit | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | EUE Value ($m, real $2024) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Annualised capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Annualised cost (capex+opex) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Optimal timing (interim calc) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Optimal timing | - | - | - | - | - | - | - | [19 empty] | - | - | - | - | bar: 1 to 19
Adjusted For Optimal Timing: | 0 | 0 | Capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Opex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Reduction in unserved energy | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Net benefit | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## 3.2.8 NPV (High VCR)
Economic inputs and assumptions
Scenario | Discount rate | Central
| Cost | Central
| VCR | Upper bound
|  | Central | Lower bound | Upper bound
| Discount rate | 5.56% | 4.11% | 7%
| Cost | 100% | 80% | 120%
| VCR | 100% | 80% | 120%
Asset life for calculating annualised capex (years) | Option 1 | 45
| Option 2 | 45
| Option 3 | 45
| Option 4 | 45
| Option 5 | 15
| Option 6 | 45
| Option 7 | 0
| Option 8 | 0
| Option 9 | 0
| Option 10 | 0
|  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30
|  |  |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Outputs | bar: 3 FY27; 7 FY31
Option 1
| Discounted | Undiscounted
| 0 | 0 | Capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Opex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Reduction in unserved energy | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Net benefit | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | EUE Value ($m, real $2024) | 1.3365 | 3.1633 | 5.8021 | 2.8336 | 3.1077 | 3.5879 | 5.6868 | 8.576 | 13.6998 | 14.5856 | 25.524 | 28.0095 | 34.1306 | 63.7842 | 51.9863 | 51.9863 | 51.9863 | 51.9863 | 51.9863 | 51.9863 | 51.9863 | 51.9863 | 51.9863 | 51.9863 | 51.9863 | 51.9863 | 51.9863 | 51.9863 | 51.9863 | 51.9863
Option 2
Determining Optimal Timing: | Discounted | Undiscounted
| 36.2837 | 40.4306 | Capex | 0 | 0 | 40.4306 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 5.0117 | 10.9163 | Opex | 0 | 0 | 0 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431
| 342.5795 | 920.8526 | Reduction in unserved energy | 0 | 0 | 0 | 2.7887 | 3.0403 | 3.4829 | 5.4956 | 8.2765 | 13.0567 | 13.8501 | 23.5017 | 26.3882 | 31.05 | 54.9142 | 45.938 | 45.938 | 45.938 | 45.938 | 45.938 | 45.938 | 45.938 | 45.938 | 45.938 | 45.938 | 45.938 | 45.938 | 45.938 | 45.938 | 45.938 | 45.938
| 301.2841 | 869.5058 | Net benefit | 0 | 0 | -40.4306 | 2.3844 | 2.636 | 3.0786 | 5.0913 | 7.8722 | 12.6524 | 13.4458 | 23.0974 | 25.9839 | 30.6457 | 54.5099 | 45.5337 | 45.5337 | 45.5337 | 45.5337 | 45.5337 | 45.5337 | 45.5337 | 45.5337 | 45.5337 | 45.5337 | 45.5337 | 45.5337 | 45.5337 | 45.5337 | 45.5337 | 45.5337
|  |  | EUE Value ($m, real $2024) | 1.3365 | 3.1633 | 5.8021 | 0.044925 | 0.067392 | 0.10504 | 0.19115 | 0.29948 | 0.64313 | 0.7355 | 2.0223 | 1.6213 | 3.0805 | 8.87 | 6.0483 | 6.0483 | 6.0483 | 6.0483 | 6.0483 | 6.0483 | 6.0483 | 6.0483 | 6.0483 | 6.0483 | 6.0483 | 6.0483 | 6.0483 | 6.0483 | 6.0483 | 6.0483
|  |  | Annualised capex | 0 | 0 | 2.2111 | 2.2111 | 2.2111 | 2.2111 | 2.2111 | 2.2111 | 2.2111 | 2.2111 | 2.2111 | 2.2111 | 2.2111 | 2.2111 | 2.2111 | 2.2111 | 2.2111 | 2.2111 | 2.2111 | 2.2111 | 2.2111 | 2.2111 | 2.2111 | 2.2111 | 2.2111 | 2.2111 | 2.2111 | 2.2111 | 2.2111 | 2.2111
|  |  | Annualised cost (capex+opex) | 0 | 0 | 2.2111 | 2.6154 | 2.6154 | 2.6154 | 2.6154 | 2.6154 | 2.6154 | 2.6154 | 2.6154 | 2.6154 | 2.6154 | 2.6154 | 2.6154 | 2.6154 | 2.6154 | 2.6154 | 2.6154 | 2.6154 | 2.6154 | 2.6154 | 2.6154 | 2.6154 | 2.6154 | 2.6154 | 2.6154 | 2.6154 | 2.6154 | 2.6154
|  |  | Optimal timing (interim calc) | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  |  | Optimal timing | - | - | - | Yes | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Adjusted For Optimal Timing: | 36.2837 | 40.4306 | Capex | 0 | 0 | 40.4306 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 5.0117 | 10.9163 | Opex | 0 | 0 | 0 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431
| 342.5795 | 920.8526 | Reduction in unserved energy | 0 | 0 | 0 | 2.7887 | 3.0403 | 3.4829 | 5.4956 | 8.2765 | 13.0567 | 13.8501 | 23.5017 | 26.3882 | 31.05 | 54.9142 | 45.938 | 45.938 | 45.938 | 45.938 | 45.938 | 45.938 | 45.938 | 45.938 | 45.938 | 45.938 | 45.938 | 45.938 | 45.938 | 45.938 | 45.938 | 45.938
| 301.2841 | 869.5058 | Net benefit | 0 | 0 | -40.4306 | 2.3844 | 2.636 | 3.0786 | 5.0913 | 7.8722 | 12.6524 | 13.4458 | 23.0974 | 25.9839 | 30.6457 | 54.5099 | 45.5337 | 45.5337 | 45.5337 | 45.5337 | 45.5337 | 45.5337 | 45.5337 | 45.5337 | 45.5337 | 45.5337 | 45.5337 | 45.5337 | 45.5337 | 45.5337 | 45.5337 | 45.5337
Option 3
Determining Optimal Timing: | Discounted | Undiscounted
| 59.0686 | 65.8197 | Capex | 0 | 0 | 65.8197 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 8.159 | 17.7713 | Opex | 0 | 0 | 0 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582
| 339.1148 | 909.7948 | Reduction in unserved energy | 0 | 0 | 0 | 2.8264 | 3.0981 | 3.5722 | 5.6504 | 8.4606 | 13.1811 | 13.9491 | 23.4633 | 26.4005 | 30.6347 | 54.3553 | 45.2627 | 45.2627 | 45.2627 | 45.2627 | 45.2627 | 45.2627 | 45.2627 | 45.2627 | 45.2627 | 45.2627 | 45.2627 | 45.2627 | 45.2627 | 45.2627 | 45.2627 | 45.2627
| 271.8872 | 826.2038 | Net benefit | 0 | 0 | -65.8197 | 2.1682 | 2.4399 | 2.914 | 4.9922 | 7.8024 | 12.5229 | 13.2909 | 22.8051 | 25.7423 | 29.9765 | 53.6971 | 44.6045 | 44.6045 | 44.6045 | 44.6045 | 44.6045 | 44.6045 | 44.6045 | 44.6045 | 44.6045 | 44.6045 | 44.6045 | 44.6045 | 44.6045 | 44.6045 | 44.6045 | 44.6045
|  |  | EUE Value ($m, real $2024) | 1.3365 | 3.1633 | 5.8021 | 0.0072417 | 0.0095971 | 0.015673 | 0.036355 | 0.11538 | 0.51869 | 0.63653 | 2.0607 | 1.609 | 3.4959 | 9.4289 | 6.7236 | 6.7236 | 6.7236 | 6.7236 | 6.7236 | 6.7236 | 6.7236 | 6.7236 | 6.7236 | 6.7236 | 6.7236 | 6.7236 | 6.7236 | 6.7236 | 6.7236 | 6.7236
|  |  | Annualised capex | 0 | 0 | 3.5996 | 3.5996 | 3.5996 | 3.5996 | 3.5996 | 3.5996 | 3.5996 | 3.5996 | 3.5996 | 3.5996 | 3.5996 | 3.5996 | 3.5996 | 3.5996 | 3.5996 | 3.5996 | 3.5996 | 3.5996 | 3.5996 | 3.5996 | 3.5996 | 3.5996 | 3.5996 | 3.5996 | 3.5996 | 3.5996 | 3.5996 | 3.5996
|  |  | Annualised cost (capex+opex) | 0 | 0 | 3.5996 | 4.2578 | 4.2578 | 4.2578 | 4.2578 | 4.2578 | 4.2578 | 4.2578 | 4.2578 | 4.2578 | 4.2578 | 4.2578 | 4.2578 | 4.2578 | 4.2578 | 4.2578 | 4.2578 | 4.2578 | 4.2578 | 4.2578 | 4.2578 | 4.2578 | 4.2578 | 4.2578 | 4.2578 | 4.2578 | 4.2578 | 4.2578
|  |  | Optimal timing (interim calc) | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  |  | Optimal timing | - | - | - | - | - | - | Yes | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Adjusted For Optimal Timing: | 50.2179 | 65.8197 | Capex | 0 | 0 | 0 | 0 | 0 | 65.8197 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 6.5671 | 15.7967 | Opex | 0 | 0 | 0 | 0 | 0 | 0 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582
| 331.4914 | 900.2982 | Reduction in unserved energy | 0 | 0 | 0 | 0 | 0 | 0 | 5.6504 | 8.4606 | 13.1811 | 13.9491 | 23.4633 | 26.4005 | 30.6347 | 54.3553 | 45.2627 | 45.2627 | 45.2627 | 45.2627 | 45.2627 | 45.2627 | 45.2627 | 45.2627 | 45.2627 | 45.2627 | 45.2627 | 45.2627 | 45.2627 | 45.2627 | 45.2627 | 45.2627
| 274.7063 | 818.6818 | Net benefit | 0 | 0 | 0 | 0 | 0 | -65.8197 | 4.9922 | 7.8024 | 12.5229 | 13.2909 | 22.8051 | 25.7423 | 29.9765 | 53.6971 | 44.6045 | 44.6045 | 44.6045 | 44.6045 | 44.6045 | 44.6045 | 44.6045 | 44.6045 | 44.6045 | 44.6045 | 44.6045 | 44.6045 | 44.6045 | 44.6045 | 44.6045 | 44.6045
Option 4
Determining Optimal Timing: | Discounted | Undiscounted
| 52.4015 | 58.3905 | Capex | 0 | 0 | 58.3905 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 7.238 | 15.7654 | Opex | 0 | 0 | 0 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839
| 344.654 | 925.5996 | Reduction in unserved energy | 0 | 0 | 0 | 2.8201 | 3.0915 | 3.5646 | 5.6399 | 8.4645 | 13.2654 | 14.0533 | 23.7393 | 26.6112 | 31.1769 | 55.3529 | 46.1137 | 46.1137 | 46.1137 | 46.1137 | 46.1137 | 46.1137 | 46.1137 | 46.1137 | 46.1137 | 46.1137 | 46.1137 | 46.1137 | 46.1137 | 46.1137 | 46.1137 | 46.1137
| 285.0145 | 851.4437 | Net benefit | 0 | 0 | -58.3905 | 2.2362 | 2.5076 | 2.9807 | 5.056 | 7.8806 | 12.6815 | 13.4694 | 23.1554 | 26.0273 | 30.593 | 54.769 | 45.5298 | 45.5298 | 45.5298 | 45.5298 | 45.5298 | 45.5298 | 45.5298 | 45.5298 | 45.5298 | 45.5298 | 45.5298 | 45.5298 | 45.5298 | 45.5298 | 45.5298 | 45.5298
|  |  | EUE Value ($m, real $2024) | 1.3365 | 3.1633 | 5.8021 | 0.013454 | 0.016155 | 0.023289 | 0.046829 | 0.11144 | 0.43443 | 0.53232 | 1.7847 | 1.3983 | 2.9536 | 8.4313 | 5.8726 | 5.8726 | 5.8726 | 5.8726 | 5.8726 | 5.8726 | 5.8726 | 5.8726 | 5.8726 | 5.8726 | 5.8726 | 5.8726 | 5.8726 | 5.8726 | 5.8726 | 5.8726
|  |  | Annualised capex | 0 | 0 | 3.1933 | 3.1933 | 3.1933 | 3.1933 | 3.1933 | 3.1933 | 3.1933 | 3.1933 | 3.1933 | 3.1933 | 3.1933 | 3.1933 | 3.1933 | 3.1933 | 3.1933 | 3.1933 | 3.1933 | 3.1933 | 3.1933 | 3.1933 | 3.1933 | 3.1933 | 3.1933 | 3.1933 | 3.1933 | 3.1933 | 3.1933 | 3.1933
|  |  | Annualised cost (capex+opex) | 0 | 0 | 3.1933 | 3.7772 | 3.7772 | 3.7772 | 3.7772 | 3.7772 | 3.7772 | 3.7772 | 3.7772 | 3.7772 | 3.7772 | 3.7772 | 3.7772 | 3.7772 | 3.7772 | 3.7772 | 3.7772 | 3.7772 | 3.7772 | 3.7772 | 3.7772 | 3.7772 | 3.7772 | 3.7772 | 3.7772 | 3.7772 | 3.7772 | 3.7772
|  |  | Optimal timing (interim calc) | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  |  | Optimal timing | - | - | - | - | - | - | Yes | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
[11 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19
Adjusted For Optimal Timing: | 44.5497 | 58.3905 | Capex | 0 | 0 | 0 | 0 | 0 | 58.3905 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 5.8259 | 14.0137 | Opex | 0 | 0 | 0 | 0 | 0 | 0 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839
| 337.0469 | 916.1233 | Reduction in unserved energy | 0 | 0 | 0 | 0 | 0 | 0 | 5.6399 | 8.4645 | 13.2654 | 14.0533 | 23.7393 | 26.6112 | 31.1769 | 55.3529 | 46.1137 | 46.1137 | 46.1137 | 46.1137 | 46.1137 | 46.1137 | 46.1137 | 46.1137 | 46.1137 | 46.1137 | 46.1137 | 46.1137 | 46.1137 | 46.1137 | 46.1137 | 46.1137
| 286.6713 | 843.7191 | Net benefit | 0 | 0 | 0 | 0 | 0 | -58.3905 | 5.056 | 7.8806 | 12.6815 | 13.4694 | 23.1554 | 26.0273 | 30.593 | 54.769 | 45.5298 | 45.5298 | 45.5298 | 45.5298 | 45.5298 | 45.5298 | 45.5298 | 45.5298 | 45.5298 | 45.5298 | 45.5298 | 45.5298 | 45.5298 | 45.5298 | 45.5298 | 45.5298
Option 5
Determining Optimal Timing: | Discounted | Undiscounted
| 101.2441 | 156.2401 | Capex | 0 | 0 | 78.12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78.12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 9.6837 | 21.0924 | Opex | 0 | 0 | 0 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812
| 379.1307 | 1024.3928 | Reduction in unserved energy | 0 | 0 | 0 | 2.8125 | 3.0806 | 3.5475 | 5.6077 | 8.4518 | 13.4967 | 14.3695 | 25.2244 | 27.715 | 33.7586 | 63.1823 | 51.4466 | 51.4466 | 51.4466 | 51.4466 | 51.4466 | 51.4466 | 51.4466 | 51.4466 | 51.4466 | 51.4466 | 51.4466 | 51.4466 | 51.4466 | 51.4466 | 51.4466 | 51.4466
| 268.2029 | 847.0603 | Net benefit | 0 | 0 | -78.12 | 2.0313 | 2.2994 | 2.7663 | 4.8265 | 7.6706 | 12.7155 | 13.5883 | 24.4432 | 26.9338 | 32.9774 | 62.4011 | 50.6654 | 50.6654 | 50.6654 | -27.4546 | 50.6654 | 50.6654 | 50.6654 | 50.6654 | 50.6654 | 50.6654 | 50.6654 | 50.6654 | 50.6654 | 50.6654 | 50.6654 | 50.6654
|  |  | EUE Value ($m, real $2024) | 1.3365 | 3.1633 | 5.8021 | 0.021096 | 0.027113 | 0.040424 | 0.07903 | 0.12414 | 0.20306 | 0.21616 | 0.29958 | 0.29455 | 0.372 | 0.60186 | 0.53967 | 0.53967 | 0.53967 | 0.53967 | 0.53967 | 0.53967 | 0.53967 | 0.53967 | 0.53967 | 0.53967 | 0.53967 | 0.53967 | 0.53967 | 0.53967 | 0.53967 | 0.53967
|  |  | Annualised capex | 0 | 0 | 10.1268 | 10.1268 | 10.1268 | 10.1268 | 10.1268 | 10.1268 | 10.1268 | 10.1268 | 10.1268 | 10.1268 | 10.1268 | 10.1268 | 10.1268 | 10.1268 | 10.1268 | 10.1268 | 10.1268 | 10.1268 | 10.1268 | 10.1268 | 10.1268 | 10.1268 | 10.1268 | 10.1268 | 10.1268 | 10.1268 | 10.1268 | 10.1268
|  |  | Annualised cost (capex+opex) | 0 | 0 | 10.1268 | 10.908 | 10.908 | 10.908 | 10.908 | 10.908 | 10.908 | 10.908 | 10.908 | 10.908 | 10.908 | 10.908 | 10.908 | 10.908 | 10.908 | 10.908 | 10.908 | 10.908 | 10.908 | 10.908 | 10.908 | 10.908 | 10.908 | 10.908 | 10.908 | 10.908 | 10.908 | 10.908
|  |  | Optimal timing (interim calc) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  |  | Optimal timing | - | - | - | - | - | - | - | - | Yes | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Adjusted For Optimal Timing: | 77.2454 | 156.2401 | Capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78.12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78.12 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 6.6948 | 17.1864 | Opex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812
| 361.7119 | 1000.8927 | Reduction in unserved energy | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13.4967 | 14.3695 | 25.2244 | 27.715 | 33.7586 | 63.1823 | 51.4466 | 51.4466 | 51.4466 | 51.4466 | 51.4466 | 51.4466 | 51.4466 | 51.4466 | 51.4466 | 51.4466 | 51.4466 | 51.4466 | 51.4466 | 51.4466 | 51.4466 | 51.4466
| 277.7716 | 827.4662 | Net benefit | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -78.12 | 12.7155 | 13.5883 | 24.4432 | 26.9338 | 32.9774 | 62.4011 | 50.6654 | 50.6654 | 50.6654 | 50.6654 | 50.6654 | 50.6654 | 50.6654 | 50.6654 | -27.4546 | 50.6654 | 50.6654 | 50.6654 | 50.6654 | 50.6654 | 50.6654 | 50.6654
Option 6
Determining Optimal Timing: | Discounted | Undiscounted
| 0 | 0 | Capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Opex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Reduction in unserved energy | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Net benefit | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | EUE Value ($m, real $2024) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Annualised capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Annualised cost (capex+opex) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Optimal timing (interim calc) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Optimal timing | - | - | - | - | - | - | - | [19 empty] | - | - | - | - | bar: 1 to 19
Adjusted For Optimal Timing: | 0 | 0 | Capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Opex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Reduction in unserved energy | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Net benefit | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 7
Determining Optimal Timing: | Discounted | Undiscounted
| 0 | 0 | Capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Opex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Reduction in unserved energy | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Net benefit | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | EUE Value ($m, real $2024) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Annualised capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Annualised cost (capex+opex) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Optimal timing (interim calc) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Optimal timing | - | - | - | - | - | - | - | [19 empty] | - | - | - | - | bar: 1 to 19
Adjusted For Optimal Timing: | 0 | 0 | Capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Opex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Reduction in unserved energy | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Net benefit | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 8
Determining Optimal Timing: | Discounted | Undiscounted
| 0 | 0 | Capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Opex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Reduction in unserved energy | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Net benefit | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | EUE Value ($m, real $2024) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Annualised capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Annualised cost (capex+opex) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Optimal timing (interim calc) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Optimal timing | - | - | - | - | - | - | - | [19 empty] | - | - | - | - | bar: 1 to 19
Adjusted For Optimal Timing: | 0 | 0 | Capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Opex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Reduction in unserved energy | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Net benefit | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 9
Determining Optimal Timing: | Discounted | Undiscounted
| 0 | 0 | Capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Opex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Reduction in unserved energy | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Net benefit | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | EUE Value ($m, real $2024) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Annualised capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Annualised cost (capex+opex) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Optimal timing (interim calc) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Optimal timing | - | - | - | - | - | - | - | [19 empty] | - | - | - | - | bar: 1 to 19
Adjusted For Optimal Timing: | 0 | 0 | Capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Opex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Reduction in unserved energy | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Net benefit | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 10
Determining Optimal Timing: | Discounted | Undiscounted
| 0 | 0 | Capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Opex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Reduction in unserved energy | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Net benefit | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | EUE Value ($m, real $2024) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Annualised capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Annualised cost (capex+opex) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Optimal timing (interim calc) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Optimal timing | - | - | - | - | - | - | - | [19 empty] | - | - | - | - | bar: 1 to 19
Adjusted For Optimal Timing: | 0 | 0 | Capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Opex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Reduction in unserved energy | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Net benefit | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## 3.2.9 NPV (Low PoF)
Economic inputs and assumptions
Scenario | Discount rate | Central
| Cost | Central
| VCR | Central
|  | Central | Lower bound | Upper bound
| Discount rate | 5.56% | 4.11% | 7%
| Cost | 100% | 80% | 120%
| VCR | 100% | 80% | 120%
Asset life for calculating annualised capex (years) | Option 1 | 45
| Option 2 | 45
| Option 3 | 45
| Option 4 | 45
| Option 5 | 15
| Option 6 | 45
| Option 7 | 0
| Option 8 | 0
| Option 9 | 0
| Option 10 | 0
|  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30
|  |  |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Outputs | bar: 3 FY27; 7 FY31
Option 1
| Discounted | Undiscounted
| 0 | 0 | Capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Opex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Reduction in unserved energy | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Net benefit | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | EUE Value ($m, real $2024) | 1.0585 | 2.5254 | 4.6632 | 2.1035 | 2.2678 | 2.5783 | 4.15 | 6.4045 | 10.4631 | 11.1717 | 20.1112 | 22.1651 | 27.141 | 51.6182 | 41.8648 | 41.8648 | 41.8648 | 41.8648 | 41.8648 | 41.8648 | 41.8648 | 41.8648 | 41.8648 | 41.8648 | 41.8648 | 41.8648 | 41.8648 | 41.8648 | 41.8648 | 41.8648
Option 2
Determining Optimal Timing: | Discounted | Undiscounted
| 36.2837 | 40.4306 | Capex | 0 | 0 | 40.4306 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 5.0117 | 10.9163 | Opex | 0 | 0 | 0 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431
| 274.976 | 741.6402 | Reduction in unserved energy | 0 | 0 | 0 | 2.0848 | 2.2398 | 2.5346 | 4.0703 | 6.2707 | 10.1012 | 10.742 | 18.6619 | 21.0449 | 24.8553 | 44.5846 | 37.1531 | 37.1531 | 37.1531 | 37.1531 | 37.1531 | 37.1531 | 37.1531 | 37.1531 | 37.1531 | 37.1531 | 37.1531 | 37.1531 | 37.1531 | 37.1531 | 37.1531 | 37.1531
| 233.6805 | 690.2934 | Net benefit | 0 | 0 | -40.4306 | 1.6805 | 1.8354 | 2.1303 | 3.666 | 5.8664 | 9.6969 | 10.3377 | 18.2576 | 20.6406 | 24.451 | 44.1803 | 36.7488 | 36.7488 | 36.7488 | 36.7488 | 36.7488 | 36.7488 | 36.7488 | 36.7488 | 36.7488 | 36.7488 | 36.7488 | 36.7488 | 36.7488 | 36.7488 | 36.7488 | 36.7488
|  |  | EUE Value ($m, real $2024) | 1.0585 | 2.5254 | 4.6632 | 0.018719 | 0.02808 | 0.043768 | 0.079645 | 0.13384 | 0.36189 | 0.42975 | 1.4493 | 1.1202 | 2.2857 | 7.0335 | 4.7117 | 4.7117 | 4.7117 | 4.7117 | 4.7117 | 4.7117 | 4.7117 | 4.7117 | 4.7117 | 4.7117 | 4.7117 | 4.7117 | 4.7117 | 4.7117 | 4.7117 | 4.7117
|  |  | Annualised capex | 0 | 0 | 2.2111 | 2.2111 | 2.2111 | 2.2111 | 2.2111 | 2.2111 | 2.2111 | 2.2111 | 2.2111 | 2.2111 | 2.2111 | 2.2111 | 2.2111 | 2.2111 | 2.2111 | 2.2111 | 2.2111 | 2.2111 | 2.2111 | 2.2111 | 2.2111 | 2.2111 | 2.2111 | 2.2111 | 2.2111 | 2.2111 | 2.2111 | 2.2111
|  |  | Annualised cost (capex+opex) | 0 | 0 | 2.2111 | 2.6154 | 2.6154 | 2.6154 | 2.6154 | 2.6154 | 2.6154 | 2.6154 | 2.6154 | 2.6154 | 2.6154 | 2.6154 | 2.6154 | 2.6154 | 2.6154 | 2.6154 | 2.6154 | 2.6154 | 2.6154 | 2.6154 | 2.6154 | 2.6154 | 2.6154 | 2.6154 | 2.6154 | 2.6154 | 2.6154 | 2.6154
|  |  | Optimal timing (interim calc) | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  |  | Optimal timing | - | - | - | - | - | - | Yes | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Adjusted For Optimal Timing: | 30.847 | 40.4306 | Capex | 0 | 0 | 0 | 0 | 0 | 40.4306 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 4.0339 | 9.7033 | Opex | 0 | 0 | 0 | 0 | 0 | 0 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431
| 269.4659 | 734.7811 | Reduction in unserved energy | 0 | 0 | 0 | 0 | 0 | 0 | 4.0703 | 6.2707 | 10.1012 | 10.742 | 18.6619 | 21.0449 | 24.8553 | 44.5846 | 37.1531 | 37.1531 | 37.1531 | 37.1531 | 37.1531 | 37.1531 | 37.1531 | 37.1531 | 37.1531 | 37.1531 | 37.1531 | 37.1531 | 37.1531 | 37.1531 | 37.1531 | 37.1531
| 234.585 | 684.6472 | Net benefit | 0 | 0 | 0 | 0 | 0 | -40.4306 | 3.666 | 5.8664 | 9.6969 | 10.3377 | 18.2576 | 20.6406 | 24.451 | 44.1803 | 36.7488 | 36.7488 | 36.7488 | 36.7488 | 36.7488 | 36.7488 | 36.7488 | 36.7488 | 36.7488 | 36.7488 | 36.7488 | 36.7488 | 36.7488 | 36.7488 | 36.7488 | 36.7488
Option 3
Determining Optimal Timing: | Discounted | Undiscounted
| 59.0686 | 65.8197 | Capex | 0 | 0 | 65.8197 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 8.159 | 17.7713 | Opex | 0 | 0 | 0 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582
| 270.3627 | 728.0658 | Reduction in unserved energy | 0 | 0 | 0 | 2.1005 | 2.2638 | 2.5718 | 4.1348 | 6.3352 | 10.0799 | 10.6941 | 18.4733 | 20.9018 | 24.3294 | 43.9099 | 36.392 | 36.392 | 36.392 | 36.392 | 36.392 | 36.392 | 36.392 | 36.392 | 36.392 | 36.392 | 36.392 | 36.392 | 36.392 | 36.392 | 36.392 | 36.392
| 203.1351 | 644.4749 | Net benefit | 0 | 0 | -65.8197 | 1.4423 | 1.6056 | 1.9136 | 3.4766 | 5.677 | 9.4217 | 10.0359 | 17.8151 | 20.2436 | 23.6712 | 43.2517 | 35.7338 | 35.7338 | 35.7338 | 35.7338 | 35.7338 | 35.7338 | 35.7338 | 35.7338 | 35.7338 | 35.7338 | 35.7338 | 35.7338 | 35.7338 | 35.7338 | 35.7338 | 35.7338
|  |  | EUE Value ($m, real $2024) | 1.0585 | 2.5254 | 4.6632 | 0.0030174 | 0.0039988 | 0.0065305 | 0.015152 | 0.069306 | 0.38325 | 0.47757 | 1.6379 | 1.2632 | 2.8116 | 7.7083 | 5.4729 | 5.4729 | 5.4729 | 5.4729 | 5.4729 | 5.4729 | 5.4729 | 5.4729 | 5.4729 | 5.4729 | 5.4729 | 5.4729 | 5.4729 | 5.4729 | 5.4729 | 5.4729
|  |  | Annualised capex | 0 | 0 | 3.5996 | 3.5996 | 3.5996 | 3.5996 | 3.5996 | 3.5996 | 3.5996 | 3.5996 | 3.5996 | 3.5996 | 3.5996 | 3.5996 | 3.5996 | 3.5996 | 3.5996 | 3.5996 | 3.5996 | 3.5996 | 3.5996 | 3.5996 | 3.5996 | 3.5996 | 3.5996 | 3.5996 | 3.5996 | 3.5996 | 3.5996 | 3.5996
|  |  | Annualised cost (capex+opex) | 0 | 0 | 3.5996 | 4.2578 | 4.2578 | 4.2578 | 4.2578 | 4.2578 | 4.2578 | 4.2578 | 4.2578 | 4.2578 | 4.2578 | 4.2578 | 4.2578 | 4.2578 | 4.2578 | 4.2578 | 4.2578 | 4.2578 | 4.2578 | 4.2578 | 4.2578 | 4.2578 | 4.2578 | 4.2578 | 4.2578 | 4.2578 | 4.2578 | 4.2578
|  |  | Optimal timing (interim calc) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  |  | Optimal timing | - | - | - | - | - | - | - | Yes | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Adjusted For Optimal Timing: | 47.5729 | 65.8197 | Capex | 0 | 0 | 0 | 0 | 0 | 0 | 65.8197 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 6.0914 | 15.1385 | Opex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582
| 261.803 | 716.9949 | Reduction in unserved energy | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.3352 | 10.0799 | 10.6941 | 18.4733 | 20.9018 | 24.3294 | 43.9099 | 36.392 | 36.392 | 36.392 | 36.392 | 36.392 | 36.392 | 36.392 | 36.392 | 36.392 | 36.392 | 36.392 | 36.392 | 36.392 | 36.392 | 36.392 | 36.392
| 208.1387 | 636.0367 | Net benefit | 0 | 0 | 0 | 0 | 0 | 0 | -65.8197 | 5.677 | 9.4217 | 10.0359 | 17.8151 | 20.2436 | 23.6712 | 43.2517 | 35.7338 | 35.7338 | 35.7338 | 35.7338 | 35.7338 | 35.7338 | 35.7338 | 35.7338 | 35.7338 | 35.7338 | 35.7338 | 35.7338 | 35.7338 | 35.7338 | 35.7338 | 35.7338
Option 4
Determining Optimal Timing: | Discounted | Undiscounted
| 52.4015 | 58.3905 | Capex | 0 | 0 | 58.3905 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 7.238 | 15.7654 | Opex | 0 | 0 | 0 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839
| 275.1017 | 741.5487 | Reduction in unserved energy | 0 | 0 | 0 | 2.0979 | 2.2611 | 2.5686 | 4.1305 | 6.3437 | 10.1573 | 10.7885 | 18.7134 | 21.0874 | 24.7935 | 44.7569 | 37.1156 | 37.1156 | 37.1156 | 37.1156 | 37.1156 | 37.1156 | 37.1156 | 37.1156 | 37.1156 | 37.1156 | 37.1156 | 37.1156 | 37.1156 | 37.1156 | 37.1156 | 37.1156
| 215.4622 | 667.3928 | Net benefit | 0 | 0 | -58.3905 | 1.514 | 1.6772 | 1.9847 | 3.5466 | 5.7598 | 9.5734 | 10.2046 | 18.1295 | 20.5035 | 24.2096 | 44.173 | 36.5317 | 36.5317 | 36.5317 | 36.5317 | 36.5317 | 36.5317 | 36.5317 | 36.5317 | 36.5317 | 36.5317 | 36.5317 | 36.5317 | 36.5317 | 36.5317 | 36.5317 | 36.5317
|  |  | EUE Value ($m, real $2024) | 1.0585 | 2.5254 | 4.6632 | 0.0056057 | 0.0067313 | 0.009704 | 0.019512 | 0.060825 | 0.3058 | 0.38324 | 1.3978 | 1.0777 | 2.3475 | 6.8612 | 4.7492 | 4.7492 | 4.7492 | 4.7492 | 4.7492 | 4.7492 | 4.7492 | 4.7492 | 4.7492 | 4.7492 | 4.7492 | 4.7492 | 4.7492 | 4.7492 | 4.7492 | 4.7492
|  |  | Annualised capex | 0 | 0 | 3.1933 | 3.1933 | 3.1933 | 3.1933 | 3.1933 | 3.1933 | 3.1933 | 3.1933 | 3.1933 | 3.1933 | 3.1933 | 3.1933 | 3.1933 | 3.1933 | 3.1933 | 3.1933 | 3.1933 | 3.1933 | 3.1933 | 3.1933 | 3.1933 | 3.1933 | 3.1933 | 3.1933 | 3.1933 | 3.1933 | 3.1933 | 3.1933
|  |  | Annualised cost (capex+opex) | 0 | 0 | 3.1933 | 3.7772 | 3.7772 | 3.7772 | 3.7772 | 3.7772 | 3.7772 | 3.7772 | 3.7772 | 3.7772 | 3.7772 | 3.7772 | 3.7772 | 3.7772 | 3.7772 | 3.7772 | 3.7772 | 3.7772 | 3.7772 | 3.7772 | 3.7772 | 3.7772 | 3.7772 | 3.7772 | 3.7772 | 3.7772 | 3.7772 | 3.7772
|  |  | Optimal timing (interim calc) | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  |  | Optimal timing | - | - | - | - | - | - | Yes | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
[11 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19
Adjusted For Optimal Timing: | 44.5497 | 58.3905 | Capex | 0 | 0 | 0 | 0 | 0 | 58.3905 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 5.8259 | 14.0137 | Opex | 0 | 0 | 0 | 0 | 0 | 0 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839
| 269.5373 | 734.6211 | Reduction in unserved energy | 0 | 0 | 0 | 0 | 0 | 0 | 4.1305 | 6.3437 | 10.1573 | 10.7885 | 18.7134 | 21.0874 | 24.7935 | 44.7569 | 37.1156 | 37.1156 | 37.1156 | 37.1156 | 37.1156 | 37.1156 | 37.1156 | 37.1156 | 37.1156 | 37.1156 | 37.1156 | 37.1156 | 37.1156 | 37.1156 | 37.1156 | 37.1156
| 219.1617 | 662.2169 | Net benefit | 0 | 0 | 0 | 0 | 0 | -58.3905 | 3.5466 | 5.7598 | 9.5734 | 10.2046 | 18.1295 | 20.5035 | 24.2096 | 44.173 | 36.5317 | 36.5317 | 36.5317 | 36.5317 | 36.5317 | 36.5317 | 36.5317 | 36.5317 | 36.5317 | 36.5317 | 36.5317 | 36.5317 | 36.5317 | 36.5317 | 36.5317 | 36.5317
Option 5
Determining Optimal Timing: | Discounted | Undiscounted
| 101.2441 | 156.2401 | Capex | 0 | 0 | 78.12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78.12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 9.6837 | 21.0924 | Opex | 0 | 0 | 0 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812
| 304.2118 | 824.8351 | Reduction in unserved energy | 0 | 0 | 0 | 2.0947 | 2.2565 | 2.5615 | 4.117 | 6.3528 | 10.3785 | 11.0816 | 19.9864 | 22.0423 | 26.9851 | 51.3263 | 41.6033 | 41.6033 | 41.6033 | 41.6033 | 41.6033 | 41.6033 | 41.6033 | 41.6033 | 41.6033 | 41.6033 | 41.6033 | 41.6033 | 41.6033 | 41.6033 | 41.6033 | 41.6033
| 193.284 | 647.5026 | Net benefit | 0 | 0 | -78.12 | 1.3135 | 1.4753 | 1.7803 | 3.3358 | 5.5716 | 9.5973 | 10.3004 | 19.2052 | 21.2611 | 26.2039 | 50.5451 | 40.8221 | 40.8221 | 40.8221 | -37.298 | 40.8221 | 40.8221 | 40.8221 | 40.8221 | 40.8221 | 40.8221 | 40.8221 | 40.8221 | 40.8221 | 40.8221 | 40.8221 | 40.8221
|  |  | EUE Value ($m, real $2024) | 1.0585 | 2.5254 | 4.6632 | 0.0087898 | 0.011297 | 0.016843 | 0.032929 | 0.051726 | 0.084606 | 0.090066 | 0.12482 | 0.12273 | 0.15589 | 0.29192 | 0.26155 | 0.26155 | 0.26155 | 0.26155 | 0.26155 | 0.26155 | 0.26155 | 0.26155 | 0.26155 | 0.26155 | 0.26155 | 0.26155 | 0.26155 | 0.26155 | 0.26155 | 0.26155
|  |  | Annualised capex | 0 | 0 | 10.1268 | 10.1268 | 10.1268 | 10.1268 | 10.1268 | 10.1268 | 10.1268 | 10.1268 | 10.1268 | 10.1268 | 10.1268 | 10.1268 | 10.1268 | 10.1268 | 10.1268 | 10.1268 | 10.1268 | 10.1268 | 10.1268 | 10.1268 | 10.1268 | 10.1268 | 10.1268 | 10.1268 | 10.1268 | 10.1268 | 10.1268 | 10.1268
|  |  | Annualised cost (capex+opex) | 0 | 0 | 10.1268 | 10.908 | 10.908 | 10.908 | 10.908 | 10.908 | 10.908 | 10.908 | 10.908 | 10.908 | 10.908 | 10.908 | 10.908 | 10.908 | 10.908 | 10.908 | 10.908 | 10.908 | 10.908 | 10.908 | 10.908 | 10.908 | 10.908 | 10.908 | 10.908 | 10.908 | 10.908 | 10.908
|  |  | Optimal timing (interim calc) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  |  | Optimal timing | - | - | - | - | - | - | - | - | - | Yes | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Adjusted For Optimal Timing: | 73.1768 | 156.2401 | Capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78.12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78.12 | 0 | 0 | 0 | 0 | 0 | 0
| 6.1881 | 16.4052 | Opex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812
| 284.6018 | 797.074 | Reduction in unserved energy | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11.0816 | 19.9864 | 22.0423 | 26.9851 | 51.3263 | 41.6033 | 41.6033 | 41.6033 | 41.6033 | 41.6033 | 41.6033 | 41.6033 | 41.6033 | 41.6033 | 41.6033 | 41.6033 | 41.6033 | 41.6033 | 41.6033 | 41.6033 | 41.6033
| 205.2369 | 624.4287 | Net benefit | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -78.12 | 10.3004 | 19.2052 | 21.2611 | 26.2039 | 50.5451 | 40.8221 | 40.8221 | 40.8221 | 40.8221 | 40.8221 | 40.8221 | 40.8221 | 40.8221 | 40.8221 | -37.298 | 40.8221 | 40.8221 | 40.8221 | 40.8221 | 40.8221 | 40.8221
Option 6
Determining Optimal Timing: | Discounted | Undiscounted
| 0 | 0 | Capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Opex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Reduction in unserved energy | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Net benefit | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | EUE Value ($m, real $2024) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Annualised capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Annualised cost (capex+opex) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Optimal timing (interim calc) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Optimal timing | - | - | - | - | - | - | - | [19 empty] | - | - | - | - | bar: 1 to 19
Adjusted For Optimal Timing: | 0 | 0 | Capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Opex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Reduction in unserved energy | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Net benefit | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 7
Determining Optimal Timing: | Discounted | Undiscounted
| 0 | 0 | Capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Opex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Reduction in unserved energy | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Net benefit | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | EUE Value ($m, real $2024) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Annualised capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Annualised cost (capex+opex) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Optimal timing (interim calc) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Optimal timing | - | - | - | - | - | - | - | [19 empty] | - | - | - | - | bar: 1 to 19
Adjusted For Optimal Timing: | 0 | 0 | Capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Opex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Reduction in unserved energy | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Net benefit | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 8
Determining Optimal Timing: | Discounted | Undiscounted
| 0 | 0 | Capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Opex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Reduction in unserved energy | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Net benefit | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | EUE Value ($m, real $2024) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Annualised capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Annualised cost (capex+opex) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Optimal timing (interim calc) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Optimal timing | - | - | - | - | - | - | - | [19 empty] | - | - | - | - | bar: 1 to 19
Adjusted For Optimal Timing: | 0 | 0 | Capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Opex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Reduction in unserved energy | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Net benefit | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 9
Determining Optimal Timing: | Discounted | Undiscounted
| 0 | 0 | Capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Opex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Reduction in unserved energy | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Net benefit | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | EUE Value ($m, real $2024) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Annualised capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Annualised cost (capex+opex) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Optimal timing (interim calc) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Optimal timing | - | - | - | - | - | - | - | [19 empty] | - | - | - | - | bar: 1 to 19
Adjusted For Optimal Timing: | 0 | 0 | Capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Opex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Reduction in unserved energy | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Net benefit | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 10
Determining Optimal Timing: | Discounted | Undiscounted
| 0 | 0 | Capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Opex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Reduction in unserved energy | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Net benefit | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | EUE Value ($m, real $2024) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Annualised capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Annualised cost (capex+opex) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Optimal timing (interim calc) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Optimal timing | - | - | - | - | - | - | - | [19 empty] | - | - | - | - | bar: 1 to 19
Adjusted For Optimal Timing: | 0 | 0 | Capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Opex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Reduction in unserved energy | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Net benefit | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## 3.2.10 NPV (High PoF)
Economic inputs and assumptions
Scenario | Discount rate | Central
| Cost | Central
| VCR | Central
|  | Central | Lower bound | Upper bound
| Discount rate | 5.56% | 4.11% | 7%
| Cost | 100% | 80% | 120%
| VCR | 100% | 80% | 120%
Asset life for calculating annualised capex (years) | Option 1 | 45
| Option 2 | 45
| Option 3 | 45
| Option 4 | 45
| Option 5 | 15
| Option 6 | 45
| Option 7 | 0
| Option 8 | 0
| Option 9 | 0
| Option 10 | 0
|  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30
|  |  |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Outputs | bar: 3 FY27; 7 FY31
Option 1
| Discounted | Undiscounted
| 0 | 0 | Capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Opex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Reduction in unserved energy | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Net benefit | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | EUE Value ($m, real $2024) | 1.1689 | 2.7468 | 5.0069 | 2.6191 | 2.9116 | 3.4015 | 5.328 | 7.8888 | 12.3699 | 13.1377 | 22.4288 | 24.5174 | 29.7433 | 54.6888 | 44.779 | 44.779 | 44.779 | 44.779 | 44.779 | 44.779 | 44.779 | 44.779 | 44.779 | 44.779 | 44.779 | 44.779 | 44.779 | 44.779 | 44.779 | 44.779
Option 2
Determining Optimal Timing: | Discounted | Undiscounted
| 36.2837 | 40.4306 | Capex | 0 | 0 | 40.4306 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 5.0117 | 10.9163 | Opex | 0 | 0 | 0 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431
| 295.9898 | 793.1142 | Reduction in unserved energy | 0 | 0 | 0 | 2.563 | 2.8274 | 3.2702 | 5.089 | 7.5235 | 11.6599 | 12.3416 | 20.5076 | 22.9355 | 26.8948 | 46.939 | 39.4102 | 39.4102 | 39.4102 | 39.4102 | 39.4102 | 39.4102 | 39.4102 | 39.4102 | 39.4102 | 39.4102 | 39.4102 | 39.4102 | 39.4102 | 39.4102 | 39.4102 | 39.4102
| 254.6944 | 741.7674 | Net benefit | 0 | 0 | -40.4306 | 2.1587 | 2.4231 | 2.8659 | 4.6847 | 7.1192 | 11.2555 | 11.9373 | 20.1032 | 22.5312 | 26.4905 | 46.5347 | 39.0059 | 39.0059 | 39.0059 | 39.0059 | 39.0059 | 39.0059 | 39.0059 | 39.0059 | 39.0059 | 39.0059 | 39.0059 | 39.0059 | 39.0059 | 39.0059 | 39.0059 | 39.0059
|  |  | EUE Value ($m, real $2024) | 1.1689 | 2.7468 | 5.0069 | 0.056157 | 0.08424 | 0.1313 | 0.23894 | 0.36529 | 0.71 | 0.79608 | 1.9212 | 1.5819 | 2.8485 | 7.7498 | 5.3689 | 5.3689 | 5.3689 | 5.3689 | 5.3689 | 5.3689 | 5.3689 | 5.3689 | 5.3689 | 5.3689 | 5.3689 | 5.3689 | 5.3689 | 5.3689 | 5.3689 | 5.3689
|  |  | Annualised capex | 0 | 0 | 2.2111 | 2.2111 | 2.2111 | 2.2111 | 2.2111 | 2.2111 | 2.2111 | 2.2111 | 2.2111 | 2.2111 | 2.2111 | 2.2111 | 2.2111 | 2.2111 | 2.2111 | 2.2111 | 2.2111 | 2.2111 | 2.2111 | 2.2111 | 2.2111 | 2.2111 | 2.2111 | 2.2111 | 2.2111 | 2.2111 | 2.2111 | 2.2111
|  |  | Annualised cost (capex+opex) | 0 | 0 | 2.2111 | 2.6154 | 2.6154 | 2.6154 | 2.6154 | 2.6154 | 2.6154 | 2.6154 | 2.6154 | 2.6154 | 2.6154 | 2.6154 | 2.6154 | 2.6154 | 2.6154 | 2.6154 | 2.6154 | 2.6154 | 2.6154 | 2.6154 | 2.6154 | 2.6154 | 2.6154 | 2.6154 | 2.6154 | 2.6154 | 2.6154 | 2.6154
|  |  | Optimal timing (interim calc) | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  |  | Optimal timing | - | - | - | - | Yes | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Adjusted For Optimal Timing: | 34.3726 | 40.4306 | Capex | 0 | 0 | 0 | 40.4306 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 4.668 | 10.512 | Opex | 0 | 0 | 0 | 0 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431 | 0.40431
| 293.8109 | 790.5512 | Reduction in unserved energy | 0 | 0 | 0 | 0 | 2.8274 | 3.2702 | 5.089 | 7.5235 | 11.6599 | 12.3416 | 20.5076 | 22.9355 | 26.8948 | 46.939 | 39.4102 | 39.4102 | 39.4102 | 39.4102 | 39.4102 | 39.4102 | 39.4102 | 39.4102 | 39.4102 | 39.4102 | 39.4102 | 39.4102 | 39.4102 | 39.4102 | 39.4102 | 39.4102
| 254.7703 | 739.6087 | Net benefit | 0 | 0 | 0 | -40.4306 | 2.4231 | 2.8659 | 4.6847 | 7.1192 | 11.2555 | 11.9373 | 20.1032 | 22.5312 | 26.4905 | 46.5347 | 39.0059 | 39.0059 | 39.0059 | 39.0059 | 39.0059 | 39.0059 | 39.0059 | 39.0059 | 39.0059 | 39.0059 | 39.0059 | 39.0059 | 39.0059 | 39.0059 | 39.0059 | 39.0059
Option 3
Determining Optimal Timing: | Discounted | Undiscounted
| 59.0686 | 65.8197 | Capex | 0 | 0 | 65.8197 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 8.159 | 17.7713 | Opex | 0 | 0 | 0 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582
| 294.8287 | 788.2589 | Reduction in unserved energy | 0 | 0 | 0 | 2.6101 | 2.8996 | 3.3819 | 5.2825 | 7.7658 | 11.8886 | 12.5544 | 20.6322 | 23.0991 | 26.7284 | 46.6823 | 39.0459 | 39.0459 | 39.0459 | 39.0459 | 39.0459 | 39.0459 | 39.0459 | 39.0459 | 39.0459 | 39.0459 | 39.0459 | 39.0459 | 39.0459 | 39.0459 | 39.0459 | 39.0459
| 227.6011 | 704.6679 | Net benefit | 0 | 0 | -65.8197 | 1.9519 | 2.2414 | 2.7237 | 4.6243 | 7.1076 | 11.2304 | 11.8962 | 19.974 | 22.4409 | 26.0702 | 46.0241 | 38.3877 | 38.3877 | 38.3877 | 38.3877 | 38.3877 | 38.3877 | 38.3877 | 38.3877 | 38.3877 | 38.3877 | 38.3877 | 38.3877 | 38.3877 | 38.3877 | 38.3877 | 38.3877
|  |  | EUE Value ($m, real $2024) | 1.1689 | 2.7468 | 5.0069 | 0.0090521 | 0.011996 | 0.019592 | 0.04544 | 0.12299 | 0.48123 | 0.58331 | 1.7965 | 1.4184 | 3.0149 | 8.0065 | 5.7332 | 5.7332 | 5.7332 | 5.7332 | 5.7332 | 5.7332 | 5.7332 | 5.7332 | 5.7332 | 5.7332 | 5.7332 | 5.7332 | 5.7332 | 5.7332 | 5.7332 | 5.7332
|  |  | Annualised capex | 0 | 0 | 3.5996 | 3.5996 | 3.5996 | 3.5996 | 3.5996 | 3.5996 | 3.5996 | 3.5996 | 3.5996 | 3.5996 | 3.5996 | 3.5996 | 3.5996 | 3.5996 | 3.5996 | 3.5996 | 3.5996 | 3.5996 | 3.5996 | 3.5996 | 3.5996 | 3.5996 | 3.5996 | 3.5996 | 3.5996 | 3.5996 | 3.5996 | 3.5996
|  |  | Annualised cost (capex+opex) | 0 | 0 | 3.5996 | 4.2578 | 4.2578 | 4.2578 | 4.2578 | 4.2578 | 4.2578 | 4.2578 | 4.2578 | 4.2578 | 4.2578 | 4.2578 | 4.2578 | 4.2578 | 4.2578 | 4.2578 | 4.2578 | 4.2578 | 4.2578 | 4.2578 | 4.2578 | 4.2578 | 4.2578 | 4.2578 | 4.2578 | 4.2578 | 4.2578 | 4.2578
|  |  | Optimal timing (interim calc) | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  |  | Optimal timing | - | - | - | - | - | - | Yes | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Adjusted For Optimal Timing: | 50.2179 | 65.8197 | Capex | 0 | 0 | 0 | 0 | 0 | 65.8197 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 6.5671 | 15.7967 | Opex | 0 | 0 | 0 | 0 | 0 | 0 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582 | 0.6582
| 287.6941 | 779.3672 | Reduction in unserved energy | 0 | 0 | 0 | 0 | 0 | 0 | 5.2825 | 7.7658 | 11.8886 | 12.5544 | 20.6322 | 23.0991 | 26.7284 | 46.6823 | 39.0459 | 39.0459 | 39.0459 | 39.0459 | 39.0459 | 39.0459 | 39.0459 | 39.0459 | 39.0459 | 39.0459 | 39.0459 | 39.0459 | 39.0459 | 39.0459 | 39.0459 | 39.0459
| 230.909 | 697.7508 | Net benefit | 0 | 0 | 0 | 0 | 0 | -65.8197 | 4.6243 | 7.1076 | 11.2304 | 11.8962 | 19.974 | 22.4409 | 26.0702 | 46.0241 | 38.3877 | 38.3877 | 38.3877 | 38.3877 | 38.3877 | 38.3877 | 38.3877 | 38.3877 | 38.3877 | 38.3877 | 38.3877 | 38.3877 | 38.3877 | 38.3877 | 38.3877 | 38.3877
Option 4
Determining Optimal Timing: | Discounted | Undiscounted
| 52.4015 | 58.3905 | Capex | 0 | 0 | 58.3905 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 7.238 | 15.7654 | Opex | 0 | 0 | 0 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839
| 299.3217 | 801.1173 | Reduction in unserved energy | 0 | 0 | 0 | 2.6023 | 2.8914 | 3.3724 | 5.2694 | 7.7639 | 11.9516 | 12.6337 | 20.8522 | 23.2646 | 27.168 | 47.4979 | 39.7406 | 39.7406 | 39.7406 | 39.7406 | 39.7406 | 39.7406 | 39.7406 | 39.7406 | 39.7406 | 39.7406 | 39.7406 | 39.7406 | 39.7406 | 39.7406 | 39.7406 | 39.7406
| 239.6822 | 726.9614 | Net benefit | 0 | 0 | -58.3905 | 2.0184 | 2.3075 | 2.7885 | 4.6855 | 7.18 | 11.3677 | 12.0498 | 20.2683 | 22.6807 | 26.5841 | 46.914 | 39.1567 | 39.1567 | 39.1567 | 39.1567 | 39.1567 | 39.1567 | 39.1567 | 39.1567 | 39.1567 | 39.1567 | 39.1567 | 39.1567 | 39.1567 | 39.1567 | 39.1567 | 39.1567
|  |  | EUE Value ($m, real $2024) | 1.1689 | 2.7468 | 5.0069 | 0.016817 | 0.020194 | 0.029112 | 0.058536 | 0.12491 | 0.41824 | 0.50396 | 1.5766 | 1.2528 | 2.5753 | 7.1909 | 5.0384 | 5.0384 | 5.0384 | 5.0384 | 5.0384 | 5.0384 | 5.0384 | 5.0384 | 5.0384 | 5.0384 | 5.0384 | 5.0384 | 5.0384 | 5.0384 | 5.0384 | 5.0384
|  |  | Annualised capex | 0 | 0 | 3.1933 | 3.1933 | 3.1933 | 3.1933 | 3.1933 | 3.1933 | 3.1933 | 3.1933 | 3.1933 | 3.1933 | 3.1933 | 3.1933 | 3.1933 | 3.1933 | 3.1933 | 3.1933 | 3.1933 | 3.1933 | 3.1933 | 3.1933 | 3.1933 | 3.1933 | 3.1933 | 3.1933 | 3.1933 | 3.1933 | 3.1933 | 3.1933
|  |  | Annualised cost (capex+opex) | 0 | 0 | 3.1933 | 3.7772 | 3.7772 | 3.7772 | 3.7772 | 3.7772 | 3.7772 | 3.7772 | 3.7772 | 3.7772 | 3.7772 | 3.7772 | 3.7772 | 3.7772 | 3.7772 | 3.7772 | 3.7772 | 3.7772 | 3.7772 | 3.7772 | 3.7772 | 3.7772 | 3.7772 | 3.7772 | 3.7772 | 3.7772 | 3.7772 | 3.7772
|  |  | Optimal timing (interim calc) | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  |  | Optimal timing | - | - | - | - | - | - | Yes | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
[11 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19
Adjusted For Optimal Timing: | 44.5497 | 58.3905 | Capex | 0 | 0 | 0 | 0 | 0 | 58.3905 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 5.8259 | 14.0137 | Opex | 0 | 0 | 0 | 0 | 0 | 0 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839 | 0.5839
| 292.2076 | 792.2511 | Reduction in unserved energy | 0 | 0 | 0 | 0 | 0 | 0 | 5.2694 | 7.7639 | 11.9516 | 12.6337 | 20.8522 | 23.2646 | 27.168 | 47.4979 | 39.7406 | 39.7406 | 39.7406 | 39.7406 | 39.7406 | 39.7406 | 39.7406 | 39.7406 | 39.7406 | 39.7406 | 39.7406 | 39.7406 | 39.7406 | 39.7406 | 39.7406 | 39.7406
| 241.832 | 719.8469 | Net benefit | 0 | 0 | 0 | 0 | 0 | -58.3905 | 4.6855 | 7.18 | 11.3677 | 12.0498 | 20.2683 | 22.6807 | 26.5841 | 46.914 | 39.1567 | 39.1567 | 39.1567 | 39.1567 | 39.1567 | 39.1567 | 39.1567 | 39.1567 | 39.1567 | 39.1567 | 39.1567 | 39.1567 | 39.1567 | 39.1567 | 39.1567 | 39.1567
Option 5
Determining Optimal Timing: | Discounted | Undiscounted
| 101.2441 | 156.2401 | Capex | 0 | 0 | 78.12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78.12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 9.6837 | 21.0924 | Opex | 0 | 0 | 0 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812
| 327.6728 | 882.4862 | Reduction in unserved energy | 0 | 0 | 0 | 2.5928 | 2.8777 | 3.351 | 5.2292 | 7.7336 | 12.116 | 12.8675 | 22.0543 | 24.1492 | 29.2792 | 53.9776 | 44.1411 | 44.1411 | 44.1411 | 44.1411 | 44.1411 | 44.1411 | 44.1411 | 44.1411 | 44.1411 | 44.1411 | 44.1411 | 44.1411 | 44.1411 | 44.1411 | 44.1411 | 44.1411
| 216.745 | 705.1537 | Net benefit | 0 | 0 | -78.12 | 1.8116 | 2.0965 | 2.5698 | 4.448 | 6.9524 | 11.3348 | 12.0863 | 21.2731 | 23.368 | 28.498 | 53.1964 | 43.3599 | 43.3599 | 43.3599 | -34.7601 | 43.3599 | 43.3599 | 43.3599 | 43.3599 | 43.3599 | 43.3599 | 43.3599 | 43.3599 | 43.3599 | 43.3599 | 43.3599 | 43.3599
|  |  | EUE Value ($m, real $2024) | 1.1689 | 2.7468 | 5.0069 | 0.02637 | 0.033891 | 0.05053 | 0.098788 | 0.15518 | 0.25382 | 0.2702 | 0.37447 | 0.36819 | 0.46411 | 0.71118 | 0.63791 | 0.63791 | 0.63791 | 0.63791 | 0.63791 | 0.63791 | 0.63791 | 0.63791 | 0.63791 | 0.63791 | 0.63791 | 0.63791 | 0.63791 | 0.63791 | 0.63791 | 0.63791
|  |  | Annualised capex | 0 | 0 | 10.1268 | 10.1268 | 10.1268 | 10.1268 | 10.1268 | 10.1268 | 10.1268 | 10.1268 | 10.1268 | 10.1268 | 10.1268 | 10.1268 | 10.1268 | 10.1268 | 10.1268 | 10.1268 | 10.1268 | 10.1268 | 10.1268 | 10.1268 | 10.1268 | 10.1268 | 10.1268 | 10.1268 | 10.1268 | 10.1268 | 10.1268 | 10.1268
|  |  | Annualised cost (capex+opex) | 0 | 0 | 10.1268 | 10.908 | 10.908 | 10.908 | 10.908 | 10.908 | 10.908 | 10.908 | 10.908 | 10.908 | 10.908 | 10.908 | 10.908 | 10.908 | 10.908 | 10.908 | 10.908 | 10.908 | 10.908 | 10.908 | 10.908 | 10.908 | 10.908 | 10.908 | 10.908 | 10.908 | 10.908 | 10.908
|  |  | Optimal timing (interim calc) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  |  | Optimal timing | - | - | - | - | - | - | - | - | Yes | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Adjusted For Optimal Timing: | 77.2454 | 156.2401 | Capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78.12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78.12 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 6.6948 | 17.1864 | Opex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812 | 0.7812
| 311.5194 | 860.7019 | Reduction in unserved energy | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12.116 | 12.8675 | 22.0543 | 24.1492 | 29.2792 | 53.9776 | 44.1411 | 44.1411 | 44.1411 | 44.1411 | 44.1411 | 44.1411 | 44.1411 | 44.1411 | 44.1411 | 44.1411 | 44.1411 | 44.1411 | 44.1411 | 44.1411 | 44.1411 | 44.1411
| 227.5791 | 687.2754 | Net benefit | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -78.12 | 11.3348 | 12.0863 | 21.2731 | 23.368 | 28.498 | 53.1964 | 43.3599 | 43.3599 | 43.3599 | 43.3599 | 43.3599 | 43.3599 | 43.3599 | 43.3599 | -34.7601 | 43.3599 | 43.3599 | 43.3599 | 43.3599 | 43.3599 | 43.3599 | 43.3599
Option 6
Determining Optimal Timing: | Discounted | Undiscounted
| 0 | 0 | Capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Opex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Reduction in unserved energy | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Net benefit | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | EUE Value ($m, real $2024) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Annualised capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Annualised cost (capex+opex) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Optimal timing (interim calc) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Optimal timing | - | - | - | - | - | - | - | [19 empty] | - | - | - | - | bar: 1 to 19
Adjusted For Optimal Timing: | 0 | 0 | Capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Opex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Reduction in unserved energy | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Net benefit | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 7
Determining Optimal Timing: | Discounted | Undiscounted
| 0 | 0 | Capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Opex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Reduction in unserved energy | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Net benefit | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | EUE Value ($m, real $2024) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Annualised capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Annualised cost (capex+opex) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Optimal timing (interim calc) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Optimal timing | - | - | - | - | - | - | - | [19 empty] | - | - | - | - | bar: 1 to 19
Adjusted For Optimal Timing: | 0 | 0 | Capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Opex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Reduction in unserved energy | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Net benefit | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 8
Determining Optimal Timing: | Discounted | Undiscounted
| 0 | 0 | Capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Opex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Reduction in unserved energy | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Net benefit | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | EUE Value ($m, real $2024) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Annualised capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Annualised cost (capex+opex) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Optimal timing (interim calc) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Optimal timing | - | - | - | - | - | - | - | [19 empty] | - | - | - | - | bar: 1 to 19
Adjusted For Optimal Timing: | 0 | 0 | Capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Opex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Reduction in unserved energy | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Net benefit | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 9
Determining Optimal Timing: | Discounted | Undiscounted
| 0 | 0 | Capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Opex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Reduction in unserved energy | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Net benefit | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | EUE Value ($m, real $2024) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Annualised capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Annualised cost (capex+opex) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Optimal timing (interim calc) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Optimal timing | - | - | - | - | - | - | - | [19 empty] | - | - | - | - | bar: 1 to 19
Adjusted For Optimal Timing: | 0 | 0 | Capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Opex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Reduction in unserved energy | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Net benefit | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 10
Determining Optimal Timing: | Discounted | Undiscounted
| 0 | 0 | Capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Opex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Reduction in unserved energy | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Net benefit | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | EUE Value ($m, real $2024) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Annualised capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Annualised cost (capex+opex) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Optimal timing (interim calc) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Optimal timing | - | - | - | - | - | - | - | [19 empty] | - | - | - | - | bar: 1 to 19
Adjusted For Optimal Timing: | 0 | 0 | Capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Opex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Reduction in unserved energy | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Net benefit | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## 3.3 Adjustments
PREFERRED OPTION
$real $2024 (thousands)
|  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | Total
| Input capex (excl mgmt reserve and indirect) | 0 | 0 | 33565.7447 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33565.7447
| Post modelling adjustment | 0 | 0 | -25549.1644 | 9907.8774 | 11826.4062 | 3814.8808 | 0 | 0 | 0 | 0 | 0 | 0 | 3.1832e-12
| Revised reg proposal capex | 0 | 0 | 8016.5803 | 9907.8774 | 11826.4062 | 3814.8808 | 0 | 0 | 0 | 0 | 0 | 0 | 33565.7447