## Lists
yes/No List
Yes
No

## Intro
Navigation Dashboard
| Model Overview |  | Description
|  | 0.1 Model Steps | Overview of the NPV modelling process.
|  | 0.2 QA | Automated quality assurance checks.
Output
|  | 1.1 BC Summary | Business Case summary of NPV analysis, including the ranking of assessed options and optimal commissioning timing based on NPV.
Inputs
|  | 2.1 KMA | Key model inputs and assumptions.
|  | 2.2.1 Supply Risk $ Base Demand | Collects the Supply Risk or Value of EUE (in $) calculated in linked Energy at Risk calculators.
|  | 2.2.2 Supply Risk $ Low Demand | Collects the Supply Risk or Value of EUE (in $) calculated in linked Energy at Risk calculators for the Low Demand sensitivity.
|  | 2.2.3 Supply Risk $ High Demand | Collects the Supply Risk or Value of EUE (in $) calculated in linked Energy at Risk calculators for the High Demand sensitivity.
|  | 2.2.4 Supply Risk $ Low PoF | Collects the Supply Risk or Value of EUE (in $) calculated in linked Energy at Risk calculators for the Low Transformer Probability of Failure sensitivity.
|  | 2.2.5 Supply Risk $ High PoF | Collects the Supply Risk or Value of EUE (in $) calculated in linked Energy at Risk calculators for the High Transformer Probability of Failure sensitivity.
|  | 2.3.1 Cost Summary | Collects costs from cost sheets and converts estimates to $2024.
|  | 2.3.2 Option 2 Cost | Cost estimate of Option 2.
|  | 2.3.3 Option 3 Cost | Cost estimate of Option 3.
|  | 2.3.4 Option 4 Cost | Cost estimate of Option 4.
|  | 2.3.5 Option 5 Cost | Cost estimate of Option 5.
|  | 2.3.6 Option 6 Cost | Cost estimate of Option 6.
|  | 2.3.7 Option 7 Cost | Cost estimate of Option 7.
|  | 2.3.8 Option 8 Cost | Cost estimate of Option 8.
|  | 2.3.9 Option 9 Cost | Cost estimate of Option 9.
|  | 2.3.10 Option 10 Cost | Cost estimate of Option 10.
Analysis & NPV Calculations
|  | 3.1 NPV | NPV calculator using central/base case assumptions.
|  | 3.2.1 NPV (LoDiscount) | NPV calculator using a lower discount rate.
|  | 3.2.2 NPV (HiDiscount) | NPV calculator using a higher discount rate.
|  | 3.2.3 NPV (LoCost) | NPV calculator using lower capital cost.
|  | 3.2.4 NPV (HiCost) | NPV calculator using higher capital cost.
|  | 3.2.5 NPV (Low Demand) | NPV calculator using a lower demand forecast
|  | 3.2.6 NPV (High Demand) | NPV calculator using a higher demand forecast
|  | 3.2.7 NPV (Low VCR) | NPV calculator using a lower VCR.
|  | 3.2.8 NPV (High VCR) | NPV calculator using a higher VCR.
|  | 3.2.9 NPV (Low Tx PoF's) | NPV calculator using a lower Transformer PoF.
|  | 3.2.10 NPV (High Tx PoF's) | NPV calculator using a Higher Transformer Po.
|  | 3.3 Adjustments | Post modelling adjustments
Glossary
| Term | Full Form | Description | Where Used in Model
| NPV | Net Present Value | A financial metric that calculates the present value of future cash flows minus initial investment. | 3.x NPV sheets, 1.1 BC Summary
| VCR | Value of Customer Reliability | Represents the cost of electricity outages per customer, used to quantify reliability benefits. | 2.1 KMA, 3.2.x Sensitivity tabs
| PoF | Probability of Failure | Likelihood that an asset will fail within a given time period. | 2.1 KMA, 3.2.x Sensitivity tabs
| EaR | Energy at Risk | Expected unserved energy due to network constraints or asset failure. | 2.2.x Supply Risk tabs
| WACC | Weighted Average Cost of Capital | The average rate of return a company is expected to pay its investors; used as discount rate. | 2.1 KMA
| Capex | Capital Expenditure | Funds used by a company to acquire or upgrade physical assets such as equipment or infrastructure. | 2.3.x Cost Summary, 3.x NPV sheets
| Opex | Operational Expenditure | Ongoing costs for running a product, business, or system. | 2.3.x Cost Summary, 3.x NPV sheets
| Sensitivity Analysis | Sensitivity Analysis | Technique used to determine how different values of an input affect a particular output under a given set of assumptions. | 3.2.x Sensitivity tabs
| Discount Rate (WACC) | Discount Rate | Rate used to discount future cash flows to their present value. | 2.1 KMA, 3.x NPV sheets
| Business Case | Business Case | A justification for a proposed project or investment, including benefits, costs, and risks. | Info tab, 1.1 BC Summary
| Optimal Timing | Optimal Timing | Optimal timing of the preferred project option, which is the year the annual benefits exceed the annual costs. | 1.1 BC Summary
External Links
Main External Files
E@R CLN22 Feeder V2.7 POE10.xlsx
E@R CLN23 Feeder V2.7 POE10.xlsx
E@R OFR21 Feeder V2.7 POE10.xlsx
E@R PHM21 Feeder V2.7 POE10.xlsx
E@R PHM22 Feeder V2.7 POE10.xlsx
E@R OFR14 Feeder V2.7 POE10.xlsx
ZSS EaR PHM V2.3 POE10.xlsx
ZSS EaR OFR V2.3 POE10.xlsx
ZSS EaR CLN V2.3 POE10.xlsx
ZSS EaR LLG V2.3 POE10.xlsx
Variants for Sensitivities
POE50 versions of all above
Low Demand / High Demand versions
Low PoF / High PoF versions
Other External Reference
CSIRO GenCost 2024-25 PDF (linked in Inputs tab for cost assumptions).

## Change Log
Revision Table
Date | Editted by | Comment
2025-09-03 | BO | Draft version for circulation
2025-09-23 | HT | Added additional options
2025-09-30 | HT | Added Demand Sensitivities
2025-10-09 | BO / HT | Updated info page; added modelling process diagram and QA checks
2025-10-28 | HT | Updated Info page , Added VCR & Pof Sensitivities

## 0.1 Model Steps
|  |  | Asset EaR Inputs | Data Inputs |  | Calculations |  |  |  | Outputs
Eq1. Annual Risk Reducion Benefit
CLN22
Eq2. Annulised CAPEX |  |  | CLN23
[5 empty] | BAU / Do Nothing Supply Risk $M |  | Eq1.
| Using the PMT function in excel |  | OFR21
Annual Risk Reduction Benfit $M
Eq3. Opex
|  |  | PHM21 | [5 empty] | Eq5. & Eq6.
Option Supply Risk $M (after augmentation)
Eq4. Annual Total Cost | [8 empty] | Net Present Value & Optimal Timing | Outputs / BC Summaries
PHM22
Eq3.
Eq5. Net Present Value Benefits & Optimal Timing = (Annual risk reduction benfit > annual cost) |  |  | OFR14
Opex
Eq6. NPV calculated with Capex one year before optimal timing; Benefits and Opex start one year after. |  |  | PHM |  |  |  |  | Eq4.
|  | Using the NPV formula in excel |  |  | Option Cost Estimates |  |  | Annualised Total Cost
OFR
Eq2.
|  |  | CLN |  |  |  | Annualised Capex
WACC
LLG

## 0.2 QA
Overall Status
Good
Number | Check Name | Status | Info |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1 | Benefits start | Good | Confirm benefits only start after the Capex investment is completed and commissioned | Input costs check | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2 | Opex start | Good | Confirm Opex only starts after the Capex investment is completed and commissioned | Benfits checks | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | Risk assessment period | Good | Confirm BAU / Do Nothing Supply Risk or Option Risk Reduction Benefit is capped at 15 years

## 1.1 BC Summary
Outputs for executive summary
Include in Assesment | Option | Description | PV benefits | PV costs | NPV | Rank Input | Optimal year | [26 empty] | Yes
No
Yes | 1 | Do Nothing / Base Case | 0 | 0 | 0 | 9
Yes | 2 | 1A New PHS ZSS + Four new feeders | 9984.918 | 73.6471 | 9911.2708 | 1 | FY28
Yes | 3 | 2A PHM 3rd Tx + Switchroom + Three new feeders + OFR12 New Feeder | 8234.1231 | 44.4559 | 8189.6672 | 5 | FY28
Yes | 4 | 3A OFR 3rd Tx + Switchroom + Three new feeders + OFR12 New Feeder | 3990.3839 | 60.8184 | 3929.5655 | 7 | FY28
Yes | 5 | 4A LLG 2nd Tx + Switchroom + Three new feeders + OFR12 New Feeder | 8365.665 | 56.8962 | 8308.7689 | 3 | FY28
Yes | 6 | 1B New PHS ZSS + Three new feeders | 9884.1595 | 69.644 | 9814.5155 | 2 | FY28
Yes | 7 | 2B PHM 3rd Tx + Switchroom + Two new feeders + OFR12 New Feeder | 8185.5885 | 37.8143 | 8147.7742 | 6 | FY28
Yes | 8 | 3B OFR 3rd Tx + Switchroom + Two new feeders + OFR12 New Feeder | 3926.1287 | 54.1768 | 3871.9518 | 8 | FY28
Yes | 9 | 4B LLG 2nd Tx + Switchroom + Two new feeders + OFR12 New Feeder | 8317.247 | 50.2546 | 8266.9925 | 4 | FY28
Yes | 10 | 5 Non-Network | 6375.8942 | 6375.8942 | 0 | 9 | -
Optimal Timing
| Option 1 | Do Nothing / Base Case
|  |  |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
|  | Undiscounted | EUE Value ($m, real $2024) | 3.3134 | 65.4291 | 247.1322 | 283.0814 | 362.0029 | 439.1049 | 581.3072 | 639.5522 | 702.7745 | 733.9632 | 767.342 | 854.8903 | 782.2544 | 955.1709 | 1138.8523 | 1138.8523 | 1138.8523 | 1138.8523 | 1138.8523 | 1138.8523 | 1138.8523 | 1138.8523 | 1138.8523 | 1138.8523 | 1138.8523 | 1138.8523 | 1138.8523 | 1138.8523 | 1138.8523 | 1138.8523
| Option 2 | 1A New PHS ZSS + Four new feeders
|  |  |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
|  | Undiscounted | EUE Value ($m, real $2024) | 3.3072 | 65.4291 | 247.1322 | 37.5886 | 63.683 | 6.9509 | 8.0097 | 9.1665 | 10.6245 | 12.1107 | 13.9883 | 17.1561 | 17.3946 | 25.5446 | 31.8652 | 31.8652 | 31.8652 | 31.8652 | 31.8652 | 31.8652 | 31.8652 | 31.8652 | 31.8652 | 31.8652 | 31.8652 | 31.8652 | 31.8652 | 31.8652 | 31.8652 | 31.8652
|  |  | $m, real $2024 | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
|  | Undiscounted | Capex | 0 | 0 | 72.1048 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Undiscounted | Opex | 0 | 0 | 0 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105
|  | Undiscounted | Total costs | 0 | 0 | 72.1048 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105
|  |  | $m, real $2024 | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
|  | Undiscounted | Benefits (reduction in EUE relative to Option 0) | 0 | 0 | 0 | 245.4928 | 298.3199 | 432.154 | 573.2974 | 630.3857 | 692.15 | 721.8524 | 753.3537 | 837.7342 | 764.8598 | 929.6264 | 1106.9871 | 1106.9871 | 1106.9871 | 1106.9871 | 1106.9871 | 1106.9871 | 1106.9871 | 1106.9871 | 1106.9871 | 1106.9871 | 1106.9871 | 1106.9871 | 1106.9871 | 1106.9871 | 1106.9871 | 1106.9871
|  |  | Optimal Timing | FY25: FY28
FY31
FY31
|  |  | Option 2 | FY25: FY31
| Option 3 | 2A PHM 3rd Tx + Switchroom + Three new feeders + OFR12 New Feeder
|  |  |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
|  | Undiscounted | EUE Value ($m, real $2024) | 3.3072 | 65.4291 | 247.1322 | 39.3292 | 67.7408 | 15.4464 | 24.3047 | 35.8409 | 52.1247 | 71.9859 | 94.7882 | 141.3396 | 142.0518 | 217.3789 | 297.6234 | 297.6234 | 297.6234 | 297.6234 | 297.6234 | 297.6234 | 297.6234 | 297.6234 | 297.6234 | 297.6234 | 297.6234 | 297.6234 | 297.6234 | 297.6234 | 297.6234 | 297.6234
|  |  | $m, real $2024 | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
|  | Undiscounted | Capex | 0 | 0 | 43.5248 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Undiscounted | Opex | 0 | 0 | 0 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525
|  | Undiscounted | Total costs | 0 | 0 | 43.5248 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525
|  |  | $m, real $2024 | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
|  | Undiscounted | Benefits (reduction in EUE relative to Option 0) | 0 | 0 | 0 | 243.7522 | 294.2621 | 423.6585 | 557.0025 | 603.7113 | 650.6498 | 661.9773 | 672.5539 | 713.5507 | 640.2026 | 737.792 | 841.229 | 841.229 | 841.229 | 841.229 | 841.229 | 841.229 | 841.229 | 841.229 | 841.229 | 841.229 | 841.229 | 841.229 | 841.229 | 841.229 | 841.229 | 841.229
|  |  | Optimal Timing | FY25: FY28
FY30
FY30
|  |  | Option 3 | FY25: FY30
| Option 4 | 3A OFR 3rd Tx + Switchroom + Three new feeders + OFR12 New Feeder
|  |  |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
|  | Undiscounted | EUE Value ($m, real $2024) | 3.3072 | 65.4291 | 247.1322 | 275.4284 | 343.9248 | 341.1361 | 465.1614 | 503.9879 | 542.9852 | 549.0842 | 550.7987 | 562.0687 | 503.7408 | 546.9214 | 583.0902 | 583.0902 | 583.0902 | 583.0902 | 583.0902 | 583.0902 | 583.0902 | 583.0902 | 583.0902 | 583.0902 | 583.0902 | 583.0902 | 583.0902 | 583.0902 | 583.0902 | 583.0902
|  |  | $m, real $2024 | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
|  | Undiscounted | Capex | 0 | 0 | 59.5447 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Undiscounted | Opex | 0 | 0 | 0 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545
|  | Undiscounted | Total costs | 0 | 0 | 59.5447 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545
|  |  | $m, real $2024 | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
|  | Undiscounted | Benefits (reduction in EUE relative to Option 0) | 0 | 0 | 0 | 7.653 | 18.0781 | 97.9688 | 116.1458 | 135.5643 | 159.7892 | 184.879 | 216.5434 | 292.8216 | 278.5136 | 408.2495 | 555.7622 | 555.7622 | 555.7622 | 555.7622 | 555.7622 | 555.7622 | 555.7622 | 555.7622 | 555.7622 | 555.7622 | 555.7622 | 555.7622 | 555.7622 | 555.7622 | 555.7622 | 555.7622
|  |  | Optimal Timing | FY25: FY28
FY33
FY33
|  |  | Option 4 | FY25: FY33
| Option 5 | 4A LLG 2nd Tx + Switchroom + Three new feeders + OFR12 New Feeder
|  |  |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
|  | Undiscounted | EUE Value ($m, real $2024) | 3.3072 | 65.4291 | 247.1322 | 33.9969 | 61.868 | 8.9521 | 17.0549 | 27.8311 | 43.4088 | 62.5269 | 84.5102 | 130.2111 | 130.197 | 204.5204 | 283.9581 | 283.9581 | 283.9581 | 283.9581 | 283.9581 | 283.9581 | 283.9581 | 283.9581 | 283.9581 | 283.9581 | 283.9581 | 283.9581 | 283.9581 | 283.9581 | 283.9581 | 283.9581
|  |  | $m, real $2024 | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
|  | Undiscounted | Capex | 0 | 0 | 55.7046 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Undiscounted | Opex | 0 | 0 | 0 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705
|  | Undiscounted | Total costs | 0 | 0 | 55.7046 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705
|  |  | $m, real $2024 | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
|  | Undiscounted | Benefits (reduction in EUE relative to Option 0) | 0 | 0 | 0 | 249.0844 | 300.1349 | 430.1528 | 564.2523 | 611.7211 | 659.3657 | 671.4363 | 682.8319 | 724.6792 | 652.0574 | 750.6505 | 854.8942 | 854.8942 | 854.8942 | 854.8942 | 854.8942 | 854.8942 | 854.8942 | 854.8942 | 854.8942 | 854.8942 | 854.8942 | 854.8942 | 854.8942 | 854.8942 | 854.8942 | 854.8942
|  |  | Optimal Timing | FY25: FY28
-
-
Option 5 | bar: FY25
| Option 6 | 1B New PHS ZSS + Three new feeders
|  |  |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
|  | Undiscounted | EUE Value ($m, real $2024) | 3.3072 | 65.4291 | 247.1322 | 37.6134 | 6.2242 | 7.0478 | 8.1309 | 9.3539 | 10.9432 | 12.7515 | 15.5559 | 21.5268 | 21.7209 | 36.3614 | 58.0848 | 58.0848 | 58.0848 | 58.0848 | 58.0848 | 58.0848 | 58.0848 | 58.0848 | 58.0848 | 58.0848 | 58.0848 | 58.0848 | 58.0848 | 58.0848 | 58.0848 | 58.0848
|  |  | $m, real $2024 | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
|  | Undiscounted | Capex | 0 | 0 | 68.1854 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Undiscounted | Opex | 0 | 0 | 0 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185
|  | Undiscounted | Total costs | 0 | 0 | 68.1854 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185
|  |  | $m, real $2024 | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
|  | Undiscounted | Benefits (reduction in EUE relative to Option 0) | 0 | 0 | 0 | 245.468 | 355.7787 | 432.0571 | 573.1763 | 630.1983 | 691.8313 | 721.2116 | 751.7861 | 833.3634 | 760.5335 | 918.8095 | 1080.7675 | 1080.7675 | 1080.7675 | 1080.7675 | 1080.7675 | 1080.7675 | 1080.7675 | 1080.7675 | 1080.7675 | 1080.7675 | 1080.7675 | 1080.7675 | 1080.7675 | 1080.7675 | 1080.7675 | 1080.7675
|  |  | Optimal Timing | FY25: FY28
FY33
FY33
|  |  | Option 6 | FY25: FY33
| Option 7 | 2B PHM 3rd Tx + Switchroom + Two new feeders + OFR12 New Feeder
|  |  |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
|  | Undiscounted | EUE Value ($m, real $2024) | 3.3072 | 65.4291 | 247.1322 | 39.5345 | 11.0771 | 15.7599 | 24.6551 | 36.2495 | 52.6223 | 72.5919 | 95.6496 | 143.0216 | 143.9711 | 223.1711 | 314.5418 | 314.5418 | 314.5418 | 314.5418 | 314.5418 | 314.5418 | 314.5418 | 314.5418 | 314.5418 | 314.5418 | 314.5418 | 314.5418 | 314.5418 | 314.5418 | 314.5418 | 314.5418
|  |  | $m, real $2024 | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
|  | Undiscounted | Capex | 0 | 0 | 37.0224 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Undiscounted | Opex | 0 | 0 | 0 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022
|  | Undiscounted | Total costs | 0 | 0 | 37.0224 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022
|  |  | $m, real $2024 | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
|  | Undiscounted | Benefits (reduction in EUE relative to Option 0) | 0 | 0 | 0 | 243.5469 | 350.9258 | 423.345 | 556.6521 | 603.3027 | 650.1521 | 661.3713 | 671.6924 | 711.8687 | 638.2834 | 731.9998 | 824.3106 | 824.3106 | 824.3106 | 824.3106 | 824.3106 | 824.3106 | 824.3106 | 824.3106 | 824.3106 | 824.3106 | 824.3106 | 824.3106 | 824.3106 | 824.3106 | 824.3106 | 824.3106
|  |  | Optimal Timing | FY25: FY28
-
-
Option 7 | bar: FY25
| Option 8 | 3B OFR 3rd Tx + Switchroom + Two new feeders + OFR12 New Feeder
|  |  |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
|  | Undiscounted | EUE Value ($m, real $2024) | 3.3072 | 65.4291 | 247.1322 | 275.5596 | 287.3594 | 341.504 | 465.5892 | 504.4896 | 543.5884 | 549.8429 | 551.8732 | 564.4318 | 506.8434 | 554.5494 | 602.5987 | 602.5987 | 602.5987 | 602.5987 | 602.5987 | 602.5987 | 602.5987 | 602.5987 | 602.5987 | 602.5987 | 602.5987 | 602.5987 | 602.5987 | 602.5987 | 602.5987 | 602.5987
|  |  | $m, real $2024 | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
|  | Undiscounted | Capex | 0 | 0 | 53.0422 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Undiscounted | Opex | 0 | 0 | 0 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042
|  | Undiscounted | Total costs | 0 | 0 | 53.0422 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042
|  |  | $m, real $2024 | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
|  | Undiscounted | Benefits (reduction in EUE relative to Option 0) | 0 | 0 | 0 | 7.5218 | 74.6435 | 97.6009 | 115.718 | 135.0626 | 159.1861 | 184.1202 | 215.4688 | 290.4585 | 275.411 | 400.6215 | 536.2536 | 536.2536 | 536.2536 | 536.2536 | 536.2536 | 536.2536 | 536.2536 | 536.2536 | 536.2536 | 536.2536 | 536.2536 | 536.2536 | 536.2536 | 536.2536 | 536.2536 | 536.2536
|  |  | Optimal Timing | FY25: FY28
-
-
Option 8 | bar: FY25
| Option 9 | 4B LLG 2nd Tx + Switchroom + Two new feeders + OFR12 New Feeder
|  |  |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
|  | Undiscounted | EUE Value ($m, real $2024) | 3.3072 | 65.4291 | 247.1322 | 34.2028 | 5.2049 | 9.2665 | 17.4069 | 28.2418 | 43.9089 | 63.1444 | 85.3132 | 131.8371 | 132.1341 | 210.3483 | 300.8588 | 300.8588 | 300.8588 | 300.8588 | 300.8588 | 300.8588 | 300.8588 | 300.8588 | 300.8588 | 300.8588 | 300.8588 | 300.8588 | 300.8588 | 300.8588 | 300.8588 | 300.8588
|  |  | $m, real $2024 | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
|  | Undiscounted | Capex | 0 | 0 | 49.2021 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Undiscounted | Opex | 0 | 0 | 0 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202
|  | Undiscounted | Total costs | 0 | 0 | 49.2021 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202
|  |  | $m, real $2024 | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
|  | Undiscounted | Benefits (reduction in EUE relative to Option 0) | 0 | 0 | 0 | 248.8786 | 356.798 | 429.8384 | 563.9003 | 611.3104 | 658.8656 | 670.8188 | 682.0288 | 723.0532 | 650.1203 | 744.8226 | 837.9936 | 837.9936 | 837.9936 | 837.9936 | 837.9936 | 837.9936 | 837.9936 | 837.9936 | 837.9936 | 837.9936 | 837.9936 | 837.9936 | 837.9936 | 837.9936 | 837.9936 | 837.9936
|  |  | Optimal Timing | FY25: FY28
-
-
Option 9 | bar: FY25
| Option 10 | 5 Non-Network
|  |  |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
|  | Undiscounted | EUE Value ($m, real $2024) | 2.8305 | 7.6008 | 57.6455 | 75.397 | 116.5181 | 159.884 | 241.6832 | 255.0898 | 275.9942 | 288.7753 | 297.7206 | 352.2877 | 295.989 | 381.8026 | 476.3468 | 476.3468 | 476.3468 | 476.3468 | 476.3468 | 476.3468 | 476.3468 | 476.3468 | 476.3468 | 476.3468 | 476.3468 | 476.3468 | 476.3468 | 476.3468 | 476.3468 | 476.3468
|  |  | $m, real $2024 | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
|  | Undiscounted | Capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Undiscounted | Opex | 0 | 0 | 0 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202
|  | Undiscounted | Total costs | 0 | 0 | 0 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202
|  |  | $m, real $2024 | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
|  | Undiscounted | Benefits (reduction in EUE relative to Option 0) | 0.48285 | 57.8283 | 189.4866 | 207.6844 | 245.4848 | 279.2209 | 339.624 | 384.4625 | 426.7802 | 445.1879 | 469.6214 | 502.6026 | 486.2654 | 573.3683 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055
Optimal Timing | bar: FY25
-
-
Option 10 | bar: FY25
NPV Analysis
| Option 1 | Do Nothing / Base Case
|  |  |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
|  | Undiscounted | EUE Value ($m, real $2024) | 3.3134 | 65.4291 | 247.1322 | 283.0814 | 362.0029 | 439.1049 | 581.3072 | 639.5522 | 702.7745 | 733.9632 | 767.342 | 854.8903 | 782.2544 | 955.1709 | 1138.8523 | 1138.8523 | 1138.8523 | 1138.8523 | 1138.8523 | 1138.8523 | 1138.8523 | 1138.8523 | 1138.8523 | 1138.8523 | 1138.8523 | 1138.8523 | 1138.8523 | 1138.8523 | 1138.8523 | 1138.8523
| Option 2 | 1A New PHS ZSS + Four new feeders
|  |  | $m, real $2024 | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
|  | Undiscounted | Capex | 0 | 0 | 72.1048 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Undiscounted | Opex | 0 | 0 | 0 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105
|  | Undiscounted | Total costs | 0 | 0 | 72.1048 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105
|  |  | $m, real $2024 | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
|  | Undiscounted | Benefits (reduction in EUE relative to Option 0) | 0 | 0 | 0 | 245.4928 | 298.3199 | 432.154 | 573.2974 | 630.3857 | 692.15 | 721.8524 | 753.3537 | 837.7342 | 764.8598 | 929.6264 | 1106.9871 | 1106.9871 | 1106.9871 | 1106.9871 | 1106.9871 | 1106.9871 | 1106.9871 | 1106.9871 | 1106.9871 | 1106.9871 | 1106.9871 | 1106.9871 | 1106.9871 | 1106.9871 | 1106.9871 | 1106.9871
|  |  | ($m, real $2024) | FY25: Undiscounted; FY28: Discounted
|  |  |  | Benefits | Costs | Net benefits | PV benefits | PV costs | NPV
|  |  | Option 2 | FY25: 24591.0207; FY26: 91.5731; FY27: 24499.4476; FY28: 9984.918; FY29: 73.6471; FY30: 9911.2708
| Option 3 | 2A PHM 3rd Tx + Switchroom + Three new feeders + OFR12 New Feeder
|  |  | $m, real $2024 | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
|  | Undiscounted | Capex | 0 | 0 | 43.5248 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Undiscounted | Opex | 0 | 0 | 0 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525
|  | Undiscounted | Total costs | 0 | 0 | 43.5248 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525
|  |  | $m, real $2024 | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
|  | Undiscounted | Benefits (reduction in EUE relative to Option 0) | 0 | 0 | 0 | 243.7522 | 294.2621 | 423.6585 | 557.0025 | 603.7113 | 650.6498 | 661.9773 | 672.5539 | 713.5507 | 640.2026 | 737.792 | 841.229 | 841.229 | 841.229 | 841.229 | 841.229 | 841.229 | 841.229 | 841.229 | 841.229 | 841.229 | 841.229 | 841.229 | 841.229 | 841.229 | 841.229 | 841.229
|  |  | ($m, real $2024) | FY25: Undiscounted; FY28: Discounted
|  |  |  | Benefits | Costs | Net benefits | PV benefits | PV costs | NPV
|  |  | Option 3 | FY25: 19658.7761; FY26: 55.2765; FY27: 19603.4996; FY28: 8234.1231; FY29: 44.4559; FY30: 8189.6672
| Option 4 | 3A OFR 3rd Tx + Switchroom + Three new feeders + OFR12 New Feeder
|  |  | $m, real $2024 | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
|  | Undiscounted | Capex | 0 | 0 | 59.5447 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Undiscounted | Opex | 0 | 0 | 0 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545
|  | Undiscounted | Total costs | 0 | 0 | 59.5447 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545
|  |  | $m, real $2024 | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
|  | Undiscounted | Benefits (reduction in EUE relative to Option 0) | 0 | 0 | 0 | 7.653 | 18.0781 | 97.9688 | 116.1458 | 135.5643 | 159.7892 | 184.879 | 216.5434 | 292.8216 | 278.5136 | 408.2495 | 555.7622 | 555.7622 | 555.7622 | 555.7622 | 555.7622 | 555.7622 | 555.7622 | 555.7622 | 555.7622 | 555.7622 | 555.7622 | 555.7622 | 555.7622 | 555.7622 | 555.7622 | 555.7622
|  |  | ($m, real $2024) | FY25: Undiscounted; FY28: Discounted
|  |  |  | Benefits | Costs | Net benefits | PV benefits | PV costs | NPV
|  |  | Option 4 | FY25: 10808.4009; FY26: 75.6218; FY27: 10732.7791; FY28: 3990.3839; FY29: 60.8184; FY30: 3929.5655
| Option 5 | 4A LLG 2nd Tx + Switchroom + Three new feeders + OFR12 New Feeder
|  |  | $m, real $2024 | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
|  | Undiscounted | Capex | 0 | 0 | 55.7046 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Undiscounted | Opex | 0 | 0 | 0 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705
|  | Undiscounted | Total costs | 0 | 0 | 55.7046 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705
|  |  | $m, real $2024 | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
|  | Undiscounted | Benefits (reduction in EUE relative to Option 0) | 0 | 0 | 0 | 249.0844 | 300.1349 | 430.1528 | 564.2523 | 611.7211 | 659.3657 | 671.4363 | 682.8319 | 724.6792 | 652.0574 | 750.6505 | 854.8942 | 854.8942 | 854.8942 | 854.8942 | 854.8942 | 854.8942 | 854.8942 | 854.8942 | 854.8942 | 854.8942 | 854.8942 | 854.8942 | 854.8942 | 854.8942 | 854.8942 | 854.8942
|  |  | ($m, real $2024) | FY25: Undiscounted; FY28: Discounted
|  |  |  | Benefits | Costs | Net benefits | PV benefits | PV costs | NPV
|  |  | Option 5 | FY25: 19974.6734; FY26: 70.7448; FY27: 19903.9285; FY28: 8365.665; FY29: 56.8962; FY30: 8308.7689
| Option 6 | 1B New PHS ZSS + Three new feeders
|  |  | $m, real $2024 | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
|  | Undiscounted | Capex | 0 | 0 | 68.1854 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Undiscounted | Opex | 0 | 0 | 0 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185
|  | Undiscounted | Total costs | 0 | 0 | 68.1854 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185
|  |  | $m, real $2024 | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
|  | Undiscounted | Benefits (reduction in EUE relative to Option 0) | 0 | 0 | 0 | 245.468 | 355.7787 | 432.0571 | 573.1763 | 630.1983 | 691.8313 | 721.2116 | 751.7861 | 833.3634 | 760.5335 | 918.8095 | 1080.7675 | 1080.7675 | 1080.7675 | 1080.7675 | 1080.7675 | 1080.7675 | 1080.7675 | 1080.7675 | 1080.7675 | 1080.7675 | 1080.7675 | 1080.7675 | 1080.7675 | 1080.7675 | 1080.7675 | 1080.7675
|  |  | ($m, real $2024) | FY25: Undiscounted; FY28: Discounted
|  |  |  | Benefits | Costs | Net benefits | PV benefits | PV costs | NPV
|  |  | Option 6 | FY25: 24206.4938; FY26: 86.5955; FY27: 24119.8983; FY28: 9884.1595; FY29: 69.644; FY30: 9814.5155
| Option 7 | 2B PHM 3rd Tx + Switchroom + Two new feeders + OFR12 New Feeder
|  |  | $m, real $2024 | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
|  | Undiscounted | Capex | 0 | 0 | 37.0224 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Undiscounted | Opex | 0 | 0 | 0 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022
|  | Undiscounted | Total costs | 0 | 0 | 37.0224 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022
|  |  | $m, real $2024 | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
|  | Undiscounted | Benefits (reduction in EUE relative to Option 0) | 0 | 0 | 0 | 243.5469 | 350.9258 | 423.345 | 556.6521 | 603.3027 | 650.1521 | 661.3713 | 671.6924 | 711.8687 | 638.2834 | 731.9998 | 824.3106 | 824.3106 | 824.3106 | 824.3106 | 824.3106 | 824.3106 | 824.3106 | 824.3106 | 824.3106 | 824.3106 | 824.3106 | 824.3106 | 824.3106 | 824.3106 | 824.3106 | 824.3106
|  |  | ($m, real $2024) | FY25: Undiscounted; FY28: Discounted
|  |  |  | Benefits | Costs | Net benefits | PV benefits | PV costs | NPV
|  |  | Option 7 | FY25: 19432.1091; FY26: 47.0184; FY27: 19385.0907; FY28: 8185.5885; FY29: 37.8143; FY30: 8147.7742
| Option 8 | 3B OFR 3rd Tx + Switchroom + Two new feeders + OFR12 New Feeder
|  |  | $m, real $2024 | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
|  | Undiscounted | Capex | 0 | 0 | 53.0422 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Undiscounted | Opex | 0 | 0 | 0 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042
|  | Undiscounted | Total costs | 0 | 0 | 53.0422 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042
|  |  | $m, real $2024 | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
|  | Undiscounted | Benefits (reduction in EUE relative to Option 0) | 0 | 0 | 0 | 7.5218 | 74.6435 | 97.6009 | 115.718 | 135.0626 | 159.1861 | 184.1202 | 215.4688 | 290.4585 | 275.411 | 400.6215 | 536.2536 | 536.2536 | 536.2536 | 536.2536 | 536.2536 | 536.2536 | 536.2536 | 536.2536 | 536.2536 | 536.2536 | 536.2536 | 536.2536 | 536.2536 | 536.2536 | 536.2536 | 536.2536
|  |  | ($m, real $2024) | FY25: Undiscounted; FY28: Discounted
|  |  |  | Benefits | Costs | Net benefits | PV benefits | PV costs | NPV
|  |  | Option 8 | FY25: 10535.8711; FY26: 67.3636; FY27: 10468.5075; FY28: 3926.1287; FY29: 54.1768; FY30: 3871.9518
| Option 9 | 4B LLG 2nd Tx + Switchroom + Two new feeders + OFR12 New Feeder
|  |  | $m, real $2024 | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
|  | Undiscounted | Capex | 0 | 0 | 49.2021 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Undiscounted | Opex | 0 | 0 | 0 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202
|  | Undiscounted | Total costs | 0 | 0 | 49.2021 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202
|  |  | $m, real $2024 | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
|  | Undiscounted | Benefits (reduction in EUE relative to Option 0) | 0 | 0 | 0 | 248.8786 | 356.798 | 429.8384 | 563.9003 | 611.3104 | 658.8656 | 670.8188 | 682.0288 | 723.0532 | 650.1203 | 744.8226 | 837.9936 | 837.9936 | 837.9936 | 837.9936 | 837.9936 | 837.9936 | 837.9936 | 837.9936 | 837.9936 | 837.9936 | 837.9936 | 837.9936 | 837.9936 | 837.9936 | 837.9936 | 837.9936
|  |  | ($m, real $2024) | FY25: Undiscounted; FY28: Discounted
|  |  |  | Benefits | Costs | Net benefits | PV benefits | PV costs | NPV
|  |  | Option 9 | FY25: 19748.3321; FY26: 62.4867; FY27: 19685.8454; FY28: 8317.247; FY29: 50.2546; FY30: 8266.9925
| Option 10 | 5 Non-Network
|  |  | $m, real $2024 | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
|  | Undiscounted | Capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Undiscounted | Opex | 0.48285 | 57.8283 | 189.4866 | 207.6844 | 245.4848 | 279.2209 | 339.624 | 384.4625 | 426.7802 | 445.1879 | 469.6214 | 502.6026 | 486.2654 | 573.3683 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055
|  | Undiscounted | Total costs | 0.48285 | 57.8283 | 189.4866 | 207.6844 | 245.4848 | 279.2209 | 339.624 | 384.4625 | 426.7802 | 445.1879 | 469.6214 | 502.6026 | 486.2654 | 573.3683 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055
|  |  | $m, real $2024 | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
|  | Undiscounted | Benefits (reduction in EUE relative to Option 0) | 0.48285 | 57.8283 | 189.4866 | 207.6844 | 245.4848 | 279.2209 | 339.624 | 384.4625 | 426.7802 | 445.1879 | 469.6214 | 502.6026 | 486.2654 | 573.3683 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055
|  |  | ($m, real $2024) | FY25: Undiscounted; FY28: Discounted
|  |  |  | Benefits | Costs | Net benefits | PV benefits | PV costs | NPV
|  |  | Option 10 | FY25: 15208.189; FY26: 15208.189; FY27: 0; FY28: 6375.8942; FY29: 6375.8942; FY30: 0
Sensitivity analysis
| Option | Description | PV benefits | FY25: PV Cost; FY26: NPV; FY27: Rank; FY28: Optimal timing
Central | 1 | Do Nothing / Base Case | 0 | FY25: 0; FY26: 0; FY27: 9
| 2 | 1A New PHS ZSS + Four new feeders | 9984.918 | FY25: 73.6471; FY26: 9911.2708; FY27: 1; FY28: FY28
| 3 | 2A PHM 3rd Tx + Switchroom + Three new feeders + OFR12 New Feeder | 8234.1231 | FY25: 44.4559; FY26: 8189.6672; FY27: 5; FY28: FY28
| 4 | 3A OFR 3rd Tx + Switchroom + Three new feeders + OFR12 New Feeder | 3990.3839 | FY25: 60.8184; FY26: 3929.5655; FY27: 7; FY28: FY28
| 5 | 4A LLG 2nd Tx + Switchroom + Three new feeders + OFR12 New Feeder | 8365.665 | FY25: 56.8962; FY26: 8308.7689; FY27: 3; FY28: FY28
| 6 | 1B New PHS ZSS + Three new feeders | 9884.1595 | FY25: 69.644; FY26: 9814.5155; FY27: 2; FY28: FY28
| 7 | 2B PHM 3rd Tx + Switchroom + Two new feeders + OFR12 New Feeder | 8185.5885 | FY25: 37.8143; FY26: 8147.7742; FY27: 6; FY28: FY28
| 8 | 3B OFR 3rd Tx + Switchroom + Two new feeders + OFR12 New Feeder | 3926.1287 | FY25: 54.1768; FY26: 3871.9518; FY27: 8; FY28: FY28
| 9 | 4B LLG 2nd Tx + Switchroom + Two new feeders + OFR12 New Feeder | 8317.247 | FY25: 50.2546; FY26: 8266.9925; FY27: 4; FY28: FY28
| 10 | 5 Non-Network | 6375.8942 | FY25: 6375.8942; FY26: 0; FY27: 9; FY28: -
Lower discount rate | 1 | Do Nothing / Base Case | 0 | FY25: 0; FY26: 0; FY27: 9
| 2 | 1A New PHS ZSS + Four new feeders | 12397.6588 | FY25: 77.2545; FY26: 12320.4043; FY27: 1; FY28: FY28
| 3 | 2A PHM 3rd Tx + Switchroom + Three new feeders + OFR12 New Feeder | 10137.1844 | FY25: 46.6334; FY26: 10090.551; FY27: 5; FY28: FY28
| 4 | 3A OFR 3rd Tx + Switchroom + Three new feeders + OFR12 New Feeder | 5091.7761 | FY25: 63.7973; FY26: 5027.9788; FY27: 7; FY28: FY28
| 5 | 4A LLG 2nd Tx + Switchroom + Three new feeders + OFR12 New Feeder | 10299.3596 | FY25: 59.683; FY26: 10239.6766; FY27: 3; FY28: FY28
| 6 | 1B New PHS ZSS + Three new feeders | 12253.1003 | FY25: 73.0552; FY26: 12180.0451; FY27: 2; FY28: FY28
| 7 | 2B PHM 3rd Tx + Switchroom + Two new feeders + OFR12 New Feeder | 10061.5037 | FY25: 39.6665; FY26: 10021.8372; FY27: 6; FY28: FY28
| 8 | 3B OFR 3rd Tx + Switchroom + Two new feeders + OFR12 New Feeder | 4995.5878 | FY25: 56.8304; FY26: 4938.7573; FY27: 8; FY28: FY28
| 9 | 4B LLG 2nd Tx + Switchroom + Two new feeders + OFR12 New Feeder | 10223.8291 | FY25: 52.7161; FY26: 10171.113; FY27: 4; FY28: FY28
| 10 | 5 Non-Network | 7840.1635 | FY25: 7840.1635; FY26: 0; FY27: 9; FY28: -
Higher discount rate | 1 | Do Nothing / Base Case | 0 | FY25: 0; FY26: 0; FY27: 9
| 2 | 1A New PHS ZSS + Four new feeders | 8151.9167 | FY25: 70.5282; FY26: 8081.3885; FY27: 1; FY28: FY28
| 3 | 2A PHM 3rd Tx + Switchroom + Three new feeders + OFR12 New Feeder | 6780.3466 | FY25: 42.5732; FY26: 6737.7734; FY27: 5; FY28: FY28
| 4 | 3A OFR 3rd Tx + Switchroom + Three new feeders + OFR12 New Feeder | 3166.1355 | FY25: 58.2428; FY26: 3107.8928; FY27: 7; FY28: FY28
| 5 | 4A LLG 2nd Tx + Switchroom + Three new feeders + OFR12 New Feeder | 6888.5262 | FY25: 54.4866; FY26: 6834.0396; FY27: 3; FY28: FY28
| 6 | 1B New PHS ZSS + Three new feeders | 8082.8664 | FY25: 66.6946; FY26: 8016.1718; FY27: 2; FY28: FY28
| 7 | 2B PHM 3rd Tx + Switchroom + Two new feeders + OFR12 New Feeder | 6751.2636 | FY25: 36.2129; FY26: 6715.0507; FY27: 6; FY28: FY28
| 8 | 3B OFR 3rd Tx + Switchroom + Two new feeders + OFR12 New Feeder | 3124.8726 | FY25: 51.8825; FY26: 3072.9902; FY27: 8; FY28: FY28
| 9 | 4B LLG 2nd Tx + Switchroom + Two new feeders + OFR12 New Feeder | 6859.5347 | FY25: 48.1263; FY26: 6811.4084; FY27: 4; FY28: FY28
| 10 | 5 Non-Network | 5260.5844 | FY25: 5260.5844; FY26: 0; FY27: 9; FY28: -
Lower cost | 1 | Do Nothing / Base Case | 0 | FY25: 0; FY26: 0; FY27: 10
| 2 | 1A New PHS ZSS + Four new feeders | 9984.918 | FY25: 58.9177; FY26: 9926.0002; FY27: 1; FY28: FY28
| 3 | 2A PHM 3rd Tx + Switchroom + Three new feeders + OFR12 New Feeder | 8234.1231 | FY25: 35.5647; FY26: 8198.5584; FY27: 5; FY28: FY28
| 4 | 3A OFR 3rd Tx + Switchroom + Three new feeders + OFR12 New Feeder | 3990.3839 | FY25: 48.6547; FY26: 3941.7292; FY27: 7; FY28: FY28
| 5 | 4A LLG 2nd Tx + Switchroom + Three new feeders + OFR12 New Feeder | 8365.665 | FY25: 45.5169; FY26: 8320.1481; FY27: 3; FY28: FY28
| 6 | 1B New PHS ZSS + Three new feeders | 9884.1595 | FY25: 55.7152; FY26: 9828.4443; FY27: 2; FY28: FY28
| 7 | 2B PHM 3rd Tx + Switchroom + Two new feeders + OFR12 New Feeder | 8185.5885 | FY25: 30.2514; FY26: 8155.3371; FY27: 6; FY28: FY28
| 8 | 3B OFR 3rd Tx + Switchroom + Two new feeders + OFR12 New Feeder | 3926.1287 | FY25: 43.3415; FY26: 3882.7872; FY27: 8; FY28: FY28
| 9 | 4B LLG 2nd Tx + Switchroom + Two new feeders + OFR12 New Feeder | 8317.247 | FY25: 40.2037; FY26: 8277.0434; FY27: 4; FY28: FY28
| 10 | 5 Non-Network | 6375.8942 | FY25: 5100.7154; FY26: 1275.1788; FY27: 9; FY28: FY25
Higher cost | 1 | Do Nothing / Base Case | 0 | FY25: 0; FY26: 0; FY27: 9
| 2 | 1A New PHS ZSS + Four new feeders | 9984.918 | FY25: 88.3766; FY26: 9896.5414; FY27: 1; FY28: FY28
| 3 | 2A PHM 3rd Tx + Switchroom + Three new feeders + OFR12 New Feeder | 8234.1231 | FY25: 53.347; FY26: 8180.776; FY27: 5; FY28: FY28
| 4 | 3A OFR 3rd Tx + Switchroom + Three new feeders + OFR12 New Feeder | 3990.3839 | FY25: 72.9821; FY26: 3917.4019; FY27: 7; FY28: FY28
| 5 | 4A LLG 2nd Tx + Switchroom + Three new feeders + OFR12 New Feeder | 8365.665 | FY25: 68.2754; FY26: 8297.3897; FY27: 3; FY28: FY28
| 6 | 1B New PHS ZSS + Three new feeders | 9884.1595 | FY25: 83.5728; FY26: 9800.5867; FY27: 2; FY28: FY28
| 7 | 2B PHM 3rd Tx + Switchroom + Two new feeders + OFR12 New Feeder | 8185.5885 | FY25: 45.3771; FY26: 8140.2113; FY27: 6; FY28: FY28
| 8 | 3B OFR 3rd Tx + Switchroom + Two new feeders + OFR12 New Feeder | 3926.1287 | FY25: 65.0122; FY26: 3861.1165; FY27: 8; FY28: FY28
| 9 | 4B LLG 2nd Tx + Switchroom + Two new feeders + OFR12 New Feeder | 8317.247 | FY25: 60.3055; FY26: 8256.9415; FY27: 4; FY28: FY28
| 10 | 5 Non-Network | 7651.0731 | FY25: 7651.0731; FY26: 0; FY27: 9; FY28: -
Low Demand | 1 | Do Nothing / Base Case | 0 | FY25: 0; FY26: 0; FY27: 9
| 2 | 1A New PHS ZSS + Four new feeders | 5173.1818 | FY25: 73.6471; FY26: 5099.5347; FY27: 2; FY28: FY28
| 3 | 2A PHM 3rd Tx + Switchroom + Three new feeders + OFR12 New Feeder | 4499.9352 | FY25: 44.4559; FY26: 4455.4794; FY27: 6; FY28: FY28
| 4 | 3A OFR 3rd Tx + Switchroom + Three new feeders + OFR12 New Feeder | 1628.9256 | FY25: 54.3516; FY26: 1574.574; FY27: 8; FY28: FY30
| 5 | 4A LLG 2nd Tx + Switchroom + Three new feeders + OFR12 New Feeder | 4618.3464 | FY25: 56.8962; FY26: 4561.4502; FY27: 4; FY28: FY28
| 6 | 1B New PHS ZSS + Three new feeders | 5178.1506 | FY25: 69.644; FY26: 5108.5067; FY27: 1; FY28: FY28
| 7 | 2B PHM 3rd Tx + Switchroom + Two new feeders + OFR12 New Feeder | 4509.9613 | FY25: 37.8143; FY26: 4472.147; FY27: 5; FY28: FY28
| 8 | 3B OFR 3rd Tx + Switchroom + Two new feeders + OFR12 New Feeder | 1636.8362 | FY25: 51.2186; FY26: 1585.6176; FY27: 7; FY28: FY29
| 9 | 4B LLG 2nd Tx + Switchroom + Two new feeders + OFR12 New Feeder | 4628.3505 | FY25: 50.2546; FY26: 4578.0959; FY27: 3; FY28: FY28
| 10 | 5 Non-Network | 6375.8942 | FY25: 6375.8942; FY26: 0; FY27: 9; FY28: -
High Demand | 1 | Do Nothing / Base Case | 0 | FY25: 0; FY26: 0; FY27: 10
| 2 | 1A New PHS ZSS + Four new feeders | 16890.9885 | FY25: 73.6471; FY26: 16817.3413; FY27: 1; FY28: FY28
| 3 | 2A PHM 3rd Tx + Switchroom + Three new feeders + OFR12 New Feeder | 13428.0105 | FY25: 44.4559; FY26: 13383.5546; FY27: 4; FY28: FY28
| 4 | 3A OFR 3rd Tx + Switchroom + Three new feeders + OFR12 New Feeder | 8074.6727 | FY25: 60.8184; FY26: 8013.8543; FY27: 7; FY28: FY28
| 5 | 4A LLG 2nd Tx + Switchroom + Three new feeders + OFR12 New Feeder | 13572.3606 | FY25: 56.8962; FY26: 13515.4644; FY27: 3; FY28: FY28
| 6 | 1B New PHS ZSS + Three new feeders | 16314.0822 | FY25: 69.644; FY26: 16244.4383; FY27: 2; FY28: FY28
| 7 | 2B PHM 3rd Tx + Switchroom + Two new feeders + OFR12 New Feeder | 13092.5648 | FY25: 37.8143; FY26: 13054.7505; FY27: 6; FY28: FY28
| 8 | 3B OFR 3rd Tx + Switchroom + Two new feeders + OFR12 New Feeder | 7646.6019 | FY25: 54.1768; FY26: 7592.425; FY27: 8; FY28: FY28
| 9 | 4B LLG 2nd Tx + Switchroom + Two new feeders + OFR12 New Feeder | 13276.6125 | FY25: 50.2546; FY26: 13226.3579; FY27: 5; FY28: FY28
| 10 | 5 Non-Network | 9382.3494 | FY25: 6375.8942; FY26: 3006.4552; FY27: 9; FY28: FY25
Low VCR | 1 | Do Nothing / Base Case | 0 | FY25: 0; FY26: 0; FY27: 9
| 2 | 1A New PHS ZSS + Four new feeders | 7987.9344 | FY25: 73.6471; FY26: 7914.2872; FY27: 1; FY28: FY28
| 3 | 2A PHM 3rd Tx + Switchroom + Three new feeders + OFR12 New Feeder | 6587.2985 | FY25: 44.4559; FY26: 6542.8426; FY27: 5; FY28: FY28
| 4 | 3A OFR 3rd Tx + Switchroom + Three new feeders + OFR12 New Feeder | 3192.3071 | FY25: 60.8184; FY26: 3131.4888; FY27: 7; FY28: FY28
| 5 | 4A LLG 2nd Tx + Switchroom + Three new feeders + OFR12 New Feeder | 6692.532 | FY25: 56.8962; FY26: 6635.6359; FY27: 3; FY28: FY28
| 6 | 1B New PHS ZSS + Three new feeders | 7907.3276 | FY25: 69.644; FY26: 7837.6836; FY27: 2; FY28: FY28
| 7 | 2B PHM 3rd Tx + Switchroom + Two new feeders + OFR12 New Feeder | 6548.4708 | FY25: 37.8143; FY26: 6510.6565; FY27: 6; FY28: FY28
| 8 | 3B OFR 3rd Tx + Switchroom + Two new feeders + OFR12 New Feeder | 3140.9029 | FY25: 54.1768; FY26: 3086.7261; FY27: 8; FY28: FY28
| 9 | 4B LLG 2nd Tx + Switchroom + Two new feeders + OFR12 New Feeder | 6653.7976 | FY25: 50.2546; FY26: 6603.5431; FY27: 4; FY28: FY28
| 10 | 5 Non-Network | 6375.8942 | FY25: 6375.8942; FY26: 0; FY27: 9; FY28: -
High VCR | 1 | Do Nothing / Base Case | 0 | FY25: 0; FY26: 0; FY27: 10
| 2 | 1A New PHS ZSS + Four new feeders | 11981.9016 | FY25: 73.6471; FY26: 11908.2544; FY27: 1; FY28: FY28
| 3 | 2A PHM 3rd Tx + Switchroom + Three new feeders + OFR12 New Feeder | 9880.9477 | FY25: 44.4559; FY26: 9836.4918; FY27: 5; FY28: FY28
| 4 | 3A OFR 3rd Tx + Switchroom + Three new feeders + OFR12 New Feeder | 4788.4607 | FY25: 60.8184; FY26: 4727.6423; FY27: 7; FY28: FY28
| 5 | 4A LLG 2nd Tx + Switchroom + Three new feeders + OFR12 New Feeder | 10038.7981 | FY25: 56.8962; FY26: 9981.9019; FY27: 3; FY28: FY28
| 6 | 1B New PHS ZSS + Three new feeders | 11860.9914 | FY25: 69.644; FY26: 11791.3474; FY27: 2; FY28: FY28
| 7 | 2B PHM 3rd Tx + Switchroom + Two new feeders + OFR12 New Feeder | 9822.7062 | FY25: 37.8143; FY26: 9784.8919; FY27: 6; FY28: FY28
| 8 | 3B OFR 3rd Tx + Switchroom + Two new feeders + OFR12 New Feeder | 4711.3544 | FY25: 54.1768; FY26: 4657.1776; FY27: 8; FY28: FY28
| 9 | 4B LLG 2nd Tx + Switchroom + Two new feeders + OFR12 New Feeder | 9980.6965 | FY25: 50.2546; FY26: 9930.4419; FY27: 4; FY28: FY28
| 10 | 5 Non-Network | 7651.0731 | FY25: 6375.8942; FY26: 1275.1788; FY27: 9; FY28: FY25
Low Tx PoF | 1 | Do Nothing / Base Case | 0 | FY25: 0; FY26: 0; FY27: 10
| 2 | 1A New PHS ZSS + Four new feeders | 9961.0239 | FY25: 73.6471; FY26: 9887.3767; FY27: 1; FY28: FY28
| 3 | 2A PHM 3rd Tx + Switchroom + Three new feeders + OFR12 New Feeder | 8205.3402 | FY25: 44.4559; FY26: 8160.8843; FY27: 5; FY28: FY28
| 4 | 3A OFR 3rd Tx + Switchroom + Three new feeders + OFR12 New Feeder | 3957.5188 | FY25: 60.8184; FY26: 3896.7004; FY27: 8; FY28: FY28
| 5 | 4A LLG 2nd Tx + Switchroom + Three new feeders + OFR12 New Feeder | 8271.1183 | FY25: 56.8962; FY26: 8214.2222; FY27: 3; FY28: FY28
| 6 | 1B New PHS ZSS + Three new feeders | 9860.9128 | FY25: 69.644; FY26: 9791.2688; FY27: 2; FY28: FY28
| 7 | 2B PHM 3rd Tx + Switchroom + Two new feeders + OFR12 New Feeder | 8159.407 | FY25: 37.8143; FY26: 8121.5928; FY27: 6; FY28: FY28
| 8 | 3B OFR 3rd Tx + Switchroom + Two new feeders + OFR12 New Feeder | 3895.9086 | FY25: 54.1768; FY26: 3841.7318; FY27: 9; FY28: FY28
| 9 | 4B LLG 2nd Tx + Switchroom + Two new feeders + OFR12 New Feeder | 8225.4387 | FY25: 50.2546; FY26: 8175.1841; FY27: 4; FY28: FY28
| 10 | 5 Non-Network | 10484.0735 | FY25: 6375.8942; FY26: 4108.1793; FY27: 7; FY28: FY25
High Tx PoF | 1 | Do Nothing / Base Case | 0 | FY25: 0; FY26: 0; FY27: 10
| 2 | 1A New PHS ZSS + Four new feeders | 10008.9983 | FY25: 73.6471; FY26: 9935.3512; FY27: 1; FY28: FY28
| 3 | 2A PHM 3rd Tx + Switchroom + Three new feeders + OFR12 New Feeder | 8263.1018 | FY25: 44.4559; FY26: 8218.6459; FY27: 5; FY28: FY28
| 4 | 3A OFR 3rd Tx + Switchroom + Three new feeders + OFR12 New Feeder | 4023.8558 | FY25: 60.8184; FY26: 3963.0374; FY27: 7; FY28: FY28
| 5 | 4A LLG 2nd Tx + Switchroom + Three new feeders + OFR12 New Feeder | 8460.3933 | FY25: 56.8962; FY26: 8403.4971; FY27: 3; FY28: FY28
| 6 | 1B New PHS ZSS + Three new feeders | 9907.5616 | FY25: 69.644; FY26: 9837.9176; FY27: 2; FY28: FY28
| 7 | 2B PHM 3rd Tx + Switchroom + Two new feeders + OFR12 New Feeder | 8211.9237 | FY25: 37.8143; FY26: 8174.1094; FY27: 6; FY28: FY28
| 8 | 3B OFR 3rd Tx + Switchroom + Two new feeders + OFR12 New Feeder | 3956.9241 | FY25: 54.1768; FY26: 3902.7473; FY27: 8; FY28: FY28
| 9 | 4B LLG 2nd Tx + Switchroom + Two new feeders + OFR12 New Feeder | 8409.1924 | FY25: 50.2546; FY26: 8358.9379; FY27: 4; FY28: FY28
| 10 | 5 Non-Network | 6401.4119 | FY25: 6375.8942; FY26: 25.5177; FY27: 9; FY28: FY25

## 2.1 KMA
Asset and Option Inputs |  |  |  |  | Modelling Inputs
Assets at Risk | Name |  |  |  | Input | Value
Asset 1 | CLN22 |  |  |  | Discount Rate | 5.56%
Asset 2 | CLN23 |  |  |  | Discount Rate Lower Bound | 4.11%
Asset 3 | OFR21 |  |  |  | Discount Rate Upper Bound | 7%
Asset 4 | PHM21 |  |  |  | Cost Central | 100%
Asset 5 | PHM22 |  |  |  | Cost Upper Bound | 120%
Asset 6 | OFR14 |  |  |  | Cost Lower Bound | 80%
Asset 7 | PHM |  |  |  | Real $2025 to real $2024 conversion factor | 95.36%
Asset 8 | OFR |  |  |  | Start Financial Year (in FY format 2024-25 = FY25) | FY25
Asset 9 | CLN |  |  |  | Opex | 1%
Asset 10 | LLG |  |  |  | VCR Upper Bound | 120%
Options | Name | Asset Life (Years) | Replacement Material Reduction P.A % | Used In Analysis | VCR Central | 100%
Option 1 - Do Nothing / Base Case | Do Nothing / Base Case | 45 | N/A | Yes | VCR Lower Bound | 80%
Option 2 - 1A New PHS ZSS + Four new feeders | 1A New PHS ZSS + Four new feeders | 45 | N/A | Yes
Option 3 - 2A PHM 3rd Tx + Switchroom + Three new feeders + OFR12 New Feeder | 2A PHM 3rd Tx + Switchroom + Three new feeders + OFR12 New Feeder | 45 | N/A | Yes
Option 4 - 3A OFR 3rd Tx + Switchroom + Three new feeders + OFR12 New Feeder | 3A OFR 3rd Tx + Switchroom + Three new feeders + OFR12 New Feeder | 45 | N/A | Yes
Option 5 - 4A LLG 2nd Tx + Switchroom + Three new feeders + OFR12 New Feeder | 4A LLG 2nd Tx + Switchroom + Three new feeders + OFR12 New Feeder | 45 | N/A | Yes
Option 6 - 1B New PHS ZSS + Three new feeders | 1B New PHS ZSS + Three new feeders | 45 | N/A | Yes
Option 7 - 2B PHM 3rd Tx + Switchroom + Two new feeders + OFR12 New Feeder | 2B PHM 3rd Tx + Switchroom + Two new feeders + OFR12 New Feeder | 45 | N/A | Yes
Option 8 - 3B OFR 3rd Tx + Switchroom + Two new feeders + OFR12 New Feeder | 3B OFR 3rd Tx + Switchroom + Two new feeders + OFR12 New Feeder | 45 | N/A | Yes
Option 9 - 4B LLG 2nd Tx + Switchroom + Two new feeders + OFR12 New Feeder | 4B LLG 2nd Tx + Switchroom + Two new feeders + OFR12 New Feeder | 45 | N/A | Yes
Option 10 - 5 Non-Network | 5 Non-Network | 45 | N/A | Yes
Auto-populated
Inputs
Sources
Item | Link / Reference | Comments
BESS Replacement P.A reduction | https://www.csiro.au/-/media/Energy/GenCost/GenCost-2024-25-Final_20250728.pdf | Average linear reduction from 2024 to 2054, based on Appendix Table B.4 – Battery Storage (2-hour duration).

## 2.2.1 SupplyRisk$ BaseD
Option 1 - Do Nothing / Base Case | [11 empty] | Option 2 - 1A New PHS ZSS + Four new feeders | [11 empty] | Option 3 - 2A PHM 3rd Tx + Switchroom + Three new feeders + OFR12 New Feeder | [11 empty] | Option 4 - 3A OFR 3rd Tx + Switchroom + Three new feeders + OFR12 New Feeder | [11 empty] | Option 5 - 4A LLG 2nd Tx + Switchroom + Three new feeders + OFR12 New Feeder | [11 empty] | Option 6 - 1B New PHS ZSS + Three new feeders | [11 empty] | Option 7 - 2B PHM 3rd Tx + Switchroom + Two new feeders + OFR12 New Feeder | [11 empty] | Option 8 - 3B OFR 3rd Tx + Switchroom + Two new feeders + OFR12 New Feeder | [11 empty] | Option 9 - 4B LLG 2nd Tx + Switchroom + Two new feeders + OFR12 New Feeder | [11 empty] | Option 10 - 5 Non-Network
| Total Supply Risk $M by Asset and Year | [11 empty] | Total Supply Risk $M by Asset and Year | [11 empty] | Total Supply Risk $M by Asset and Year | [11 empty] | Total Supply Risk $M by Asset and Year | [11 empty] | Total Supply Risk $M by Asset and Year | [11 empty] | Total Supply Risk $M by Asset and Year | [11 empty] | Total Supply Risk $M by Asset and Year | [11 empty] | Total Supply Risk $M by Asset and Year | [11 empty] | Total Supply Risk $M by Asset and Year | [11 empty] | Total Supply Risk $M by Asset and Year
Source: | E@R CLN22 Feeder V2.7 POE10.xlsx¦Output for AusNet''s NPV model'!$B$5:$P$5 | E@R CLN23 Feeder V2.7 POE10.xlsx¦Output for AusNet''s NPV model'!$B$5:$P$5 | E@R OFR21 Feeder V2.7 POE10.xlsx¦Output for AusNet''s NPV model'!$B$5:$P$5 | E@R PHM21 Feeder V2.7 POE10.xlsx¦Output for AusNet''s NPV model'!$B$5:$P$5 | E@R PHM22 Feeder V2.7 POE10.xlsx¦Output for AusNet''s NPV model'!$B$5:$P$5 | E@R OFR14 Feeder V2.7 POE10.xlsx¦Output for AusNet''s NPV model'!$B$5:$P$5 | ZSS EaR PHM V2.3 POE10.xlsx¦Output for AusNet''s NPV model'!$B$5:$P$5 | ZSS EaR OFR V2.3 POE10.xlsx¦Output for AusNet''s NPV model'!$B$5:$P$5 | ZSS EaR CLN V2.3 POE10.xlsx¦Output for AusNet''s NPV model'!$B$5:$P$5 | ZSS EaR LLG V2.3 POE10.xlsx¦Output for AusNet''s NPV model'!$B$5:$P$5 |  |  | E@R CLN22 Feeder V2.7 POE10.xlsx¦Output for AusNet''s NPV model'!$B$10:$P$10 | E@R CLN23 Feeder V2.7 POE10.xlsx¦Output for AusNet''s NPV model'!$B$10:$P$10 | E@R OFR21 Feeder V2.7 POE10.xlsx¦Output for AusNet''s NPV model'!$B$10:$P$10 | E@R PHM21 Feeder V2.7 POE10.xlsx¦Output for AusNet''s NPV model'!$B$10:$P$10 | E@R PHM22 Feeder V2.7 POE10.xlsx¦Output for AusNet''s NPV model'!$B$10:$P$10 | E@R OFR14 Feeder V2.7 POE10.xlsx¦Output for AusNet''s NPV model'!$B$10:$P$10 | ZSS EaR PHM V2.3 POE10.xlsx¦Output for AusNet''s NPV model'!$B$10:$P$10 | ZSS EaR OFR V2.3 POE10.xlsx¦Output for AusNet''s NPV model'!$B$10:$P$10 | ZSS EaR CLN V2.3 POE10.xlsx¦Output for AusNet''s NPV model'!$B$10:$P$10 | ZSS EaR LLG V2.3 POE10.xlsx¦Output for AusNet''s NPV model'!$B$10:$P$10 |  |  | E@R CLN22 Feeder V2.7 POE10.xlsx¦Output for AusNet''s NPV model'!$B$13:$P$13 | E@R CLN23 Feeder V2.7 POE10.xlsx¦Output for AusNet''s NPV model'!$B$13:$P$13 | E@R OFR21 Feeder V2.7 POE10.xlsx¦Output for AusNet''s NPV model'!$B$13:$P$13 | E@R PHM21 Feeder V2.7 POE10.xlsx¦Output for AusNet''s NPV model'!$B$13:$P$13 | E@R PHM22 Feeder V2.7 POE10.xlsx¦Output for AusNet''s NPV model'!$B$13:$P$13 | E@R OFR14 Feeder V2.7 POE10.xlsx¦Output for AusNet''s NPV model'!$B$13:$P$13 | ZSS EaR PHM V2.3 POE10.xlsx¦Output for AusNet''s NPV model'!$B$13:$P$13 | ZSS EaR OFR V2.3 POE10.xlsx¦Output for AusNet''s NPV model'!B$13:$P$13 | ZSS EaR CLN V2.3 POE10.xlsx¦Output for AusNet''s NPV model'!B$13:$P$13 | ZSS EaR LLG V2.3 POE10.xlsx¦Output for AusNet''s NPV model'!B$13:$P$13 |  |  | E@R CLN22 Feeder V2.7 POE10.xlsx¦Output for AusNet''s NPV model'!$B$16:$P$16 | E@R CLN23 Feeder V2.7 POE10.xlsx¦Output for AusNet''s NPV model'!$B$16:$P$16 | E@R OFR21 Feeder V2.7 POE10.xlsx¦Output for AusNet''s NPV model'!$B$16:$P$16 | E@R PHM21 Feeder V2.7 POE10.xlsx¦Output for AusNet''s NPV model'!$B$16:$P$16 | E@R PHM22 Feeder V2.7 POE10.xlsx¦Output for AusNet''s NPV model'!$B$16:$P$16 | E@R OFR14 Feeder V2.7 POE10.xlsx¦Output for AusNet''s NPV model'!$B$16:$P$16 | ZSS EaR PHM V2.3 POE10.xlsx¦Output for AusNet''s NPV model'!$B$16:$P$16 | ZSS EaR OFR V2.3 POE10.xlsx¦Output for AusNet''s NPV model'!$B$16:$P$16 | ZSS EaR CLN V2.3 POE10.xlsx¦Output for AusNet''s NPV model'!$B$16:$P$16 | ZSS EaR LLG V2.3 POE10.xlsx¦Output for AusNet''s NPV model'!$B$16:$P$16 |  |  | E@R CLN22 Feeder V2.7 POE10.xlsx¦Output for AusNet''s NPV model'!$B$19:$P$19 | E@R CLN23 Feeder V2.7 POE10.xlsx¦Output for AusNet''s NPV model'!$B$19:$P$19 | E@R OFR21 Feeder V2.7 POE10.xlsx¦Output for AusNet''s NPV model'!$B$19:$P$19 | E@R PHM21 Feeder V2.7 POE10.xlsx¦Output for AusNet''s NPV model'!$B$19:$P$19 | E@R PHM22 Feeder V2.7 POE10.xlsx¦Output for AusNet''s NPV model'!$B$19:$P$19 | E@R OFR14 Feeder V2.7 POE10.xlsx¦Output for AusNet''s NPV model'!$B$19:$P$19 | ZSS EaR PHM V2.3 POE10.xlsx¦Output for AusNet''s NPV model'!$B$19:$P$19 | ZSS EaR OFR V2.3 POE10.xlsx¦Output for AusNet''s NPV model'!$B$19:$P$19 | ZSS EaR CLN V2.3 POE10.xlsx¦Output for AusNet''s NPV model'!$B$19:$P$19 | ZSS EaR LLG V2.3 POE10.xlsx¦Output for AusNet''s NPV model'!$B$19:$P$19 |  |  | E@R CLN22 Feeder V2.7 POE50.xlsx¦Output for AusNet''s NPV model'!$B$10:$P$10 | E@R CLN23 Feeder V2.7 POE50.xlsx¦Output for AusNet''s NPV model'!$B$10:$P$10 | E@R OFR21 Feeder V2.7 POE50.xlsx¦Output for AusNet''s NPV model'!$B$10:$P$10 | E@R PHM21 Feeder V2.7 POE50.xlsx¦Output for AusNet''s NPV model'!$B$10:$P$10 | E@R PHM22 Feeder V2.7 POE50.xlsx¦Output for AusNet''s NPV model'!$B$10:$P$10 | E@R OFR14 Feeder V2.7 POE50.xlsx¦Output for AusNet''s NPV model'!$B$10:$P$10 | ZSS EaR PHM V2.3 POE50.xlsx¦Output for AusNet''s NPV model'!$B$10:$P$10 | ZSS EaR OFR V2.3 POE50.xlsx¦Output for AusNet''s NPV model'!$B$10:$P$10 | ZSS EaR CLN V2.3 POE50.xlsx¦Output for AusNet''s NPV model'!$B$10:$P$10 | ZSS EaR LLG V2.3 POE50.xlsx¦Output for AusNet''s NPV model'!$B$10:$P$10 |  |  | E@R CLN22 Feeder V2.7 POE50.xlsx¦Output for AusNet''s NPV model'!$B$13:$P$13 | E@R CLN23 Feeder V2.7 POE50.xlsx¦Output for AusNet''s NPV model'!$B$13:$P$13 | E@R OFR21 Feeder V2.7 POE50.xlsx¦Output for AusNet''s NPV model'!$B$13:$P$13 | E@R PHM21 Feeder V2.7 POE50.xlsx¦Output for AusNet''s NPV model'!$B$13:$P$13 | E@R PHM22 Feeder V2.7 POE50.xlsx¦Output for AusNet''s NPV model'!$B$13:$P$13 | E@R OFR14 Feeder V2.7 POE50.xlsx¦Output for AusNet''s NPV model'!$B$13:$P$13 | ZSS EaR PHM V2.3 POE50.xlsx¦Output for AusNet''s NPV model'!$B$13:$P$13 | ZSS EaR OFR V2.3 POE50.xlsx¦Output for AusNet''s NPV model'!$B$13:$P$13 | ZSS EaR CLN V2.3 POE50.xlsx¦Output for AusNet''s NPV model'!$B$13:$P$13 | ZSS EaR LLG V2.3 POE50.xlsx¦Output for AusNet''s NPV model'!$B$13:$P$13 |  |  | E@R CLN22 Feeder V2.7 POE50.xlsx¦Output for AusNet''s NPV model'!$B$16:$P$16 | E@R CLN23 Feeder V2.7 POE50.xlsx¦Output for AusNet''s NPV model'!$B$16:$P$16 | E@R OFR21 Feeder V2.7 POE50.xlsx¦Output for AusNet''s NPV model'!$B$16:$P$16 | E@R PHM21 Feeder V2.7 POE50.xlsx¦Output for AusNet''s NPV model'!$B$16:$P$16 | E@R PHM22 Feeder V2.7 POE50.xlsx¦Output for AusNet''s NPV model'!$B$16:$P$16 | E@R OFR14 Feeder V2.7 POE50.xlsx¦Output for AusNet''s NPV model'!$B$16:$P$16 | ZSS EaR PHM V2.3 POE50.xlsx¦Output for AusNet''s NPV model'!$B$16:$P$16 | ZSS EaR OFR V2.3 POE50.xlsx¦Output for AusNet''s NPV model'!$B$16:$P$16 | ZSS EaR CLN V2.3 POE50.xlsx¦Output for AusNet''s NPV model'!$B$16:$P$16 | ZSS EaR LLG V2.3 POE10.xlsx¦Output for AusNet''s NPV model'!$B$16:$P$16 |  |  | E@R CLN22 Feeder V2.7 POE50.xlsx¦Output for AusNet''s NPV model'!$B$19:$P$19 | E@R CLN23 Feeder V2.7 POE50.xlsx¦Output for AusNet''s NPV model'!$B$19:$P$19 | E@R OFR21 Feeder V2.7 POE50.xlsx¦Output for AusNet''s NPV model'!$B$19:$P$19 | E@R PHM21 Feeder V2.7 POE50.xlsx¦Output for AusNet''s NPV model'!$B$19:$P$19 | E@R PHM22 Feeder V2.7 POE50.xlsx¦Output for AusNet''s NPV model'!$B$19:$P$19 | E@R OFR14 Feeder V2.7 POE50.xlsx¦Output for AusNet''s NPV model'!$B$19:$P$19 | ZSS EaR PHM V2.3 POE50.xlsx¦Output for AusNet''s NPV model'!$B$19:$P$19 | ZSS EaR OFR V2.3 POE50.xlsx¦Output for AusNet''s NPV model'!$B$19:$P$19 | ZSS EaR CLN V2.3 POE50.xlsx¦Output for AusNet''s NPV model'!$B$19:$P$19 | ZSS EaR LLG V2.3 POE10.xlsx¦Output for AusNet''s NPV model'!$B$19:$P$19 |  |  | E@R CLN22 Feeder V2.7 POE10.xlsx¦Output for AusNet''s NPV model'!$B$22:$P$22 | E@R CLN23 Feeder V2.7 POE10.xlsx¦Output for AusNet''s NPV model'!$B$22:$P$22 | E@R OFR21 Feeder V2.7 POE10.xlsx¦Output for AusNet''s NPV model'!$B$22:$P$22 | E@R PHM21 Feeder V2.7 POE10.xlsx¦Output for AusNet''s NPV model'!$B$22:$P$22 | E@R PHM22 Feeder V2.7 POE10.xlsx¦Output for AusNet''s NPV model'!$B$22:$P$22 | E@R OFR14 Feeder V2.7 POE10.xlsx¦Output for AusNet''s NPV model'!$B$22:$P$22 | ZSS EaR PHM V2.3 POE10.xlsx¦Output for AusNet''s NPV model'!$B$22:$P$22 | ZSS EaR OFR V2.3 POE10.xlsx¦Output for AusNet''s NPV model'!$B$22:$P$22 | ZSS EaR CLN V2.3 POE10.xlsx¦Output for AusNet''s NPV model'!$B$22:$P$22 | ZSS EaR LLG V2.3 POE10.xlsx¦Output for AusNet''s NPV model'!$B$22:$P$22
Year | CLN22 | CLN23 | OFR21 | PHM21 | PHM22 | OFR14 | PHM | OFR | CLN | LLG | Opt 1 Total | Year | CLN22 | CLN23 | OFR21 | PHM21 | PHM22 | OFR14 | PHM | OFR | CLN | LLG | Opt 2 Total | Year | CLN22 | CLN23 | OFR21 | PHM21 | PHM22 | OFR14 | PHM | OFR | CLN | LLG | Opt 3 Total | Year | CLN22 | CLN23 | OFR21 | PHM21 | PHM22 | OFR14 | PHM | OFR | CLN | LLG | Opt 4 Total | Year | CLN22 | CLN23 | OFR21 | PHM21 | PHM22 | OFR14 | PHM | OFR | CLN | LLG | Opt 5 Total | Year | CLN22 | CLN23 | OFR21 | PHM21 | PHM22 | OFR14 | PHM | OFR | CLN | LLG | Opt 6 Total | Year | CLN22 | CLN23 | OFR21 | PHM21 | PHM22 | OFR14 | PHM | OFR | CLN | LLG | Opt 7 Total | Year | CLN22 | CLN23 | OFR21 | PHM21 | PHM22 | OFR14 | PHM | OFR | CLN | LLG | Opt 8 Total | Year | CLN22 | CLN23 | OFR21 | PHM21 | PHM22 | OFR14 | PHM | OFR | CLN | LLG | Opt 9 Total | Year | CLN22 | CLN23 | OFR21 | PHM21 | PHM22 | OFR14 | PHM | OFR | CLN | LLG | Opt 10 Total
FY25 | 0 | 0 | 9.261e-05 | 0 | 0 | 0 | 0.00045823 | 0.025861 | 0.0030674 | 3.2839 | 3.3134 | FY25 | 0 | 0 | 9.261e-05 | 0 | 0 | 0 | 0.00045823 | 0.025861 | 0.0030674 | 3.2778 | 3.3072 | FY25 | 0 | 0 | 9.261e-05 | 0 | 0 | 0 | 0.00045823 | 0.025861 | 0.0030674 | 3.2778 | 3.3072 | FY25 | 0 | 0 | 9.261e-05 | 0 | 0 | 0 | 0.00045823 | 0.025861 | 0.0030674 | 3.2778 | 3.3072 | FY25 | 0 | 0 | 9.261e-05 | 0 | 0 | 0 | 0.00045823 | 0.025861 | 0.0030674 | 3.2778 | 3.3072 | FY25 | 0 | 0 | 9.261e-05 | 0 | 0 | 0 | 0.00045823 | 0.025861 | 0.0030674 | 3.2778 | 3.3072 | FY25 | 0 | 0 | 9.261e-05 | 0 | 0 | 0 | 0.00045823 | 0.025861 | 0.0030674 | 3.2778 | 3.3072 | FY25 | 0 | 0 | 9.261e-05 | 0 | 0 | 0 | 0.00045823 | 0.025861 | 0.0030674 | 3.2778 | 3.3072 | FY25 | 0 | 0 | 9.261e-05 | 0 | 0 | 0 | 0.00045823 | 0.025861 | 0.0030674 | 3.2778 | 3.3072 | FY25 | 0 | 0 | 0 | 0 | 0 | 0 | 7.9225e-05 | 0.014534 | 0.0010425 | 2.8149 | 2.8305
FY26 | 0.33417 | 0 | 0.016561 | 61.2197 | 0.0049505 | 0.076122 | 0.01979 | 0.037878 | 0.0015058 | 3.7184 | 65.4291 | FY26 | 0.33417 | 0 | 0.016561 | 61.2197 | 0.0049505 | 0.076122 | 0.01979 | 0.037878 | 0.0015058 | 3.7184 | 65.4291 | FY26 | 0.33417 | 0 | 0.016561 | 61.2197 | 0.0049505 | 0.076122 | 0.01979 | 0.037878 | 0.0015058 | 3.7184 | 65.4291 | FY26 | 0.33417 | 0 | 0.016561 | 61.2197 | 0.0049505 | 0.076122 | 0.01979 | 0.037878 | 0.0015058 | 3.7184 | 65.4291 | FY26 | 0.33417 | 0 | 0.016561 | 61.2197 | 0.0049505 | 0.076122 | 0.01979 | 0.037878 | 0.0015058 | 3.7184 | 65.4291 | FY26 | 0.33417 | 0 | 0.016561 | 61.2197 | 0.0049505 | 0.076122 | 0.01979 | 0.037878 | 0.0015058 | 3.7184 | 65.4291 | FY26 | 0.33417 | 0 | 0.016561 | 61.2197 | 0.0049505 | 0.076122 | 0.01979 | 0.037878 | 0.0015058 | 3.7184 | 65.4291 | FY26 | 0.33417 | 0 | 0.016561 | 61.2197 | 0.0049505 | 0.076122 | 0.01979 | 0.037878 | 0.0015058 | 3.7184 | 65.4291 | FY26 | 0.33417 | 0 | 0.016561 | 61.2197 | 0.0049505 | 0.076122 | 0.01979 | 0.037878 | 0.0015058 | 3.7184 | 65.4291 | FY26 | 0.047751 | 0 | 0 | 4.3361 | 0 | 0 | 0.0019563 | 0.016953 | 0.00016937 | 3.1978 | 7.6008
FY27 | 1.0189 | 0 | 0.095278 | 228.821 | 1.406 | 10.7476 | 0.052811 | 0.16999 | 0.0034545 | 4.8172 | 247.1322 | FY27 | 1.0189 | 0 | 0.095278 | 228.821 | 1.406 | 10.7476 | 0.052811 | 0.16999 | 0.0034545 | 4.8172 | 247.1322 | FY27 | 1.0189 | 0 | 0.095278 | 228.821 | 1.406 | 10.7476 | 0.052811 | 0.16999 | 0.0034545 | 4.8172 | 247.1322 | FY27 | 1.0189 | 0 | 0.095278 | 228.821 | 1.406 | 10.7476 | 0.052811 | 0.16999 | 0.0034545 | 4.8172 | 247.1322 | FY27 | 1.0189 | 0 | 0.095278 | 228.821 | 1.406 | 10.7476 | 0.052811 | 0.16999 | 0.0034545 | 4.8172 | 247.1322 | FY27 | 1.0189 | 0 | 0.095278 | 228.821 | 1.406 | 10.7476 | 0.052811 | 0.16999 | 0.0034545 | 4.8172 | 247.1322 | FY27 | 1.0189 | 0 | 0.095278 | 228.821 | 1.406 | 10.7476 | 0.052811 | 0.16999 | 0.0034545 | 4.8172 | 247.1322 | FY27 | 1.0189 | 0 | 0.095278 | 228.821 | 1.406 | 10.7476 | 0.052811 | 0.16999 | 0.0034545 | 4.8172 | 247.1322 | FY27 | 1.0189 | 0 | 0.095278 | 228.821 | 1.406 | 10.7476 | 0.052811 | 0.16999 | 0.0034545 | 4.8172 | 247.1322 | FY27 | 0.1413 | 0 | 0.0056705 | 49.59 | 0.010662 | 3.6807 | 0.0073495 | 0.054322 | 0.00089479 | 4.1547 | 57.6455
FY28 | 2.2918 | 0 | 0.13664 | 238.429 | 4.6943 | 31.6628 | 0.072204 | 0.4561 | 0.0062069 | 5.3324 | 283.0814 | FY28 | 0 | 0 | 0.13664 | 0 | 0 | 31.6628 | 0.00016975 | 0.4561 | 0.00054316 | 5.3324 | 37.5886 | FY28 | 2.2918 | 0 | 0 | 0 | 0 | 31.6628 | 7.8568e-06 | 0.036021 | 0.0062069 | 5.3324 | 39.3292 | FY28 | 0 | 0 | 0 | 238.429 | 0 | 31.6628 | 0.0037215 | 0.00043472 | 0.00010071 | 5.3324 | 275.4284 | FY28 | 2.2918 | 0 | 0 | 0 | 0 | 31.6628 | 0.00016975 | 0.036021 | 0.0062069 | 0 | 33.9969 | FY28 | 0 | 0 | 0.13664 | 0 | 0.022623 | 31.6628 | 0.0011617 | 0.4561 | 0.0016711 | 5.3324 | 37.6134 | FY28 | 2.2918 | 0 | 0 | 0 | 0.094159 | 31.6628 | 7.8568e-06 | 0.14714 | 0.0062069 | 5.3324 | 39.5345 | FY28 | 0 | 0 | 0 | 238.429 | 0.094159 | 31.6628 | 0.040315 | 0.00043472 | 0.00054316 | 5.3324 | 275.5596 | FY28 | 2.2918 | 0 | 0 | 0 | 0.094159 | 31.6628 | 0.00072934 | 0.14714 | 0.0062069 | 0 | 34.2028 | FY28 | 0.40168 | 0 | 0.0088494 | 54.0823 | 0.15497 | 15.9563 | 0.010742 | 0.17556 | 0.00207 | 4.6044 | 75.397
FY29 | 4.9069 | 0.00048597 | 0.19953 | 281.1681 | 12.1407 | 56.8773 | 0.095266 | 0.73128 | 0.010193 | 5.8731 | 362.0029 | FY29 | 0 | 0 | 0.19953 | 0 | 0 | 56.8773 | 0.00025066 | 0.73128 | 0.0015229 | 5.8731 | 63.683 | FY29 | 4.9069 | 0.00048597 | 0 | 0 | 0 | 56.8773 | 1.2928e-05 | 0.072786 | 0.010193 | 5.8731 | 67.7408 | FY29 | 0 | 0 | 0 | 281.1681 | 0 | 56.8773 | 0.0051594 | 0.00073654 | 0.00040923 | 5.8731 | 343.9248 | FY29 | 4.9069 | 0.00048597 | 0 | 0 | 0 | 56.8773 | 0.00025066 | 0.072786 | 0.010193 | 0 | 61.868 | FY29 | 0 | 0 | 0.19953 | 0 | 0.073892 | 0 | 0.0015289 | 0.072786 | 0.003366 | 5.8731 | 6.2242 | FY29 | 4.9069 | 0.00048597 | 0 | 0 | 0.26192 | 0 | 1.2928e-05 | 0.024417 | 0.010193 | 5.8731 | 11.0771 | FY29 | 0 | 0 | 0 | 281.1681 | 0.26192 | 0 | 0.054047 | 0.00073654 | 0.0015229 | 5.8731 | 287.3594 | FY29 | 4.9069 | 0.00048597 | 0 | 0 | 0.26192 | 0 | 0.00096076 | 0.024417 | 0.010193 | 0 | 5.2049 | FY29 | 0.99581 | 0 | 0.015334 | 77.3143 | 0.28503 | 32.501 | 0.014875 | 0.31419 | 0.0038914 | 5.0737 | 116.5181
FY30 | 8.7974 | 0.11571 | 0.31946 | 334.6302 | 13.2836 | 74.2782 | 0.13073 | 1.0366 | 0.018205 | 6.4947 | 439.1049 | FY30 | 0 | 0 | 0.31946 | 0 | 0 | 0 | 0.00038797 | 0.13221 | 0.0041453 | 6.4947 | 6.9509 | FY30 | 8.7974 | 0.11571 | 0 | 0 | 0 | 0 | 2.1466e-05 | 0.020355 | 0.018205 | 6.4947 | 15.4464 | FY30 | 0 | 0 | 0 | 334.6302 | 0 | 0 | 0.0080748 | 0.0011113 | 0.0019467 | 6.4947 | 341.1361 | FY30 | 8.7974 | 0.11571 | 0 | 0 | 0 | 0 | 0.00038797 | 0.020355 | 0.018205 | 0 | 8.9521 | FY30 | 0 | 0 | 0.31946 | 0 | 0.091808 | 0 | 0.0022328 | 0.13221 | 0.0073412 | 6.4947 | 7.0478 | FY30 | 8.7974 | 0.11571 | 0 | 0 | 0.29729 | 0 | 2.1466e-05 | 0.036486 | 0.018205 | 6.4947 | 15.7599 | FY30 | 0 | 0 | 0 | 334.6302 | 0.29729 | 0 | 0.076462 | 0.0011113 | 0.0041453 | 6.4947 | 341.504 | FY30 | 8.7974 | 0.11571 | 0 | 0 | 0.29729 | 0 | 0.0013596 | 0.036486 | 0.018205 | 0 | 9.2665 | FY30 | 1.9456 | 0.013516 | 0.03491 | 107.1324 | 0.31588 | 44.3161 | 0.022396 | 0.47774 | 0.0078938 | 5.6176 | 159.884
FY31 | 16.6417 | 0.35615 | 0.52199 | 457.8876 | 14.1055 | 82.9038 | 0.19623 | 1.4142 | 0.029597 | 7.2504 | 581.3072 | FY31 | 0 | 0 | 0.52199 | 5.3527e-05 | 0 | 0 | 0.0006489 | 0.22823 | 0.0084063 | 7.2504 | 8.0097 | FY31 | 16.6417 | 0.35615 | 0 | 5.3527e-05 | 0 | 0 | 3.7893e-05 | 0.0268 | 0.029597 | 7.2504 | 24.3047 | FY31 | 0 | 0 | 0 | 457.8876 | 0 | 0 | 0.016946 | 0.0016218 | 0.0047989 | 7.2504 | 465.1614 | FY31 | 16.6417 | 0.35615 | 0 | 5.3527e-05 | 0 | 0 | 0.0006489 | 0.0268 | 0.029597 | 0 | 17.0549 | FY31 | 0.0091261 | 0 | 0.52199 | 5.3527e-05 | 0.10353 | 0 | 0.0042278 | 0.22823 | 0.01335 | 7.2504 | 8.1309 | FY31 | 16.6417 | 0.35615 | 0 | 5.3527e-05 | 0.31926 | 0 | 3.7893e-05 | 0.057954 | 0.029597 | 7.2504 | 24.6551 | FY31 | 0 | 0 | 0 | 457.8876 | 0.31926 | 0 | 0.1219 | 0.0016218 | 0.0084063 | 7.2504 | 465.5892 | FY31 | 16.6417 | 0.35615 | 0 | 0 | 0.31926 | 0 | 0.0022467 | 0.057954 | 0.029597 | 0 | 17.4069 | FY31 | 4.5985 | 0.14312 | 0.065291 | 178.9722 | 0.34228 | 50.5281 | 0.040869 | 0.69625 | 0.013814 | 6.2828 | 241.6832
FY32 | 26.7865 | 0.95811 | 0.78643 | 495.9347 | 15.1327 | 89.796 | 0.2708 | 1.8266 | 0.049583 | 8.0108 | 639.5522 | FY32 | 0 | 0 | 0.78643 | 0.00056072 | 0 | 0 | 0.00098042 | 0.35039 | 0.017337 | 8.0108 | 9.1665 | FY32 | 26.7865 | 0.95811 | 0 | 0.00056072 | 0 | 0 | 6.1087e-05 | 0.035383 | 0.049583 | 8.0108 | 35.8409 | FY32 | 0 | 0 | 0 | 495.9347 | 0 | 0 | 0.028736 | 0.0022398 | 0.011404 | 8.0108 | 503.9879 | FY32 | 26.7865 | 0.95811 | 0 | 0.00056072 | 0 | 0 | 0.00098042 | 0.035383 | 0.049583 | 0 | 27.8311 | FY32 | 0.052233 | 0 | 0.78643 | 0.00056072 | 0.12035 | 0 | 0.0076019 | 0.35039 | 0.02557 | 8.0108 | 9.3539 | FY32 | 26.7865 | 0.95811 | 0 | 0.00056072 | 0.35052 | 0 | 6.1087e-05 | 0.09344 | 0.049583 | 8.0108 | 36.2495 | FY32 | 0 | 0 | 0 | 495.9347 | 0.35052 | 0 | 0.174 | 0.0022398 | 0.017337 | 8.0108 | 504.4896 | FY32 | 26.7865 | 0.95811 | 0 | 0 | 0.35052 | 0 | 0.0037364 | 0.09344 | 0.049583 | 0 | 28.2418 | FY32 | 8.8963 | 0.38212 | 0.1097 | 181.9963 | 0.37379 | 55.3522 | 0.062858 | 0.94034 | 0.025425 | 6.9507 | 255.0898
FY33 | 40.0426 | 3.0094 | 1.3478 | 534.1892 | 16.4822 | 95.9772 | 0.37961 | 2.3255 | 0.30377 | 8.7172 | 702.7745 | FY33 | 0 | 0 | 1.3478 | 0.0038838 | 0 | 0 | 0.0014386 | 0.52122 | 0.032901 | 8.7172 | 10.6245 | FY33 | 40.0426 | 3.0094 | 0 | 0.0038838 | 0 | 0 | 9.8849e-05 | 0.047728 | 0.30377 | 8.7172 | 52.1247 | FY33 | 0 | 0 | 0 | 534.1892 | 0 | 0 | 0.052919 | 0.0030489 | 0.022861 | 8.7172 | 542.9852 | FY33 | 40.0426 | 3.0094 | 0 | 0.0038838 | 0 | 0 | 0.0014386 | 0.047728 | 0.30377 | 0 | 43.4088 | FY33 | 0.14846 | 0.00026684 | 1.3478 | 0.0038838 | 0.14268 | 0 | 0.015938 | 0.52122 | 0.045673 | 8.7172 | 10.9432 | FY33 | 40.0426 | 3.0094 | 0 | 0.0038838 | 0.39173 | 0 | 9.8849e-05 | 0.15364 | 0.30377 | 8.7172 | 52.6223 | FY33 | 0 | 0 | 0 | 534.1892 | 0.39173 | 0 | 0.25429 | 0.0030489 | 0.032901 | 8.7172 | 543.5884 | FY33 | 40.0426 | 3.0094 | 0 | 0 | 0.39173 | 0 | 0.0077891 | 0.15364 | 0.30377 | 0 | 43.9089 | FY33 | 14.8607 | 0.9701 | 0.20617 | 190.9768 | 0.41318 | 59.6092 | 0.10185 | 1.2513 | 0.044104 | 7.5608 | 275.9942
FY34 | 54.1546 | 7.3453 | 1.9107 | 539.4631 | 18.3115 | 99.0912 | 0.55275 | 2.723 | 0.94674 | 9.4643 | 733.9632 | FY34 | 0.0066067 | 0 | 1.9107 | 0.014518 | 0 | 0 | 0.0054495 | 0.6553 | 0.053874 | 9.4643 | 12.1107 | FY34 | 54.1546 | 7.3453 | 0 | 0.014518 | 0 | 0 | 0.0001636 | 0.060274 | 0.94674 | 9.4643 | 71.9859 | FY34 | 0 | 0 | 0 | 539.4631 | 0 | 0 | 0.11375 | 0.0038303 | 0.039199 | 9.4643 | 549.0842 | FY34 | 54.1546 | 7.3453 | 0 | 0.014518 | 0 | 0 | 0.0054495 | 0.060274 | 0.94674 | 0 | 62.5269 | FY34 | 0.29405 | 0.072968 | 1.9107 | 0.014518 | 0.18278 | 0 | 0.050479 | 0.6553 | 0.10646 | 9.4643 | 12.7515 | FY34 | 54.1546 | 7.3453 | 0 | 0.014518 | 0.46006 | 0 | 0.0001636 | 0.20621 | 0.94674 | 9.4643 | 72.5919 | FY34 | 0.0066067 | 0 | 0 | 539.4631 | 0.46006 | 0 | 0.39116 | 0.0038303 | 0.053874 | 9.4643 | 549.8429 | FY34 | 54.1546 | 7.3453 | 0 | 0 | 0.46006 | 0 | 0.031497 | 0.20621 | 0.94674 | 0 | 63.1444 | FY34 | 21.8914 | 2.5268 | 0.27527 | 191.8255 | 0.48679 | 61.794 | 0.18289 | 1.4964 | 0.083329 | 8.2129 | 288.7753
FY35 | 66.3986 | 16.096 | 2.6181 | 540.3509 | 23.4625 | 102.4399 | 0.59054 | 3.2464 | 1.8583 | 10.2807 | 767.342 | FY35 | 0.025596 | 0 | 2.6181 | 0.072888 | 0 | 0 | 0.0029133 | 0.84099 | 0.1471 | 10.2807 | 13.9883 | FY35 | 66.3986 | 16.096 | 0 | 0.072888 | 0 | 0 | 0.00020419 | 0.081359 | 1.8583 | 10.2807 | 94.7882 | FY35 | 0 | 0 | 0 | 540.3509 | 0 | 0 | 0.099208 | 0.0048892 | 0.062971 | 10.2807 | 550.7987 | FY35 | 66.3986 | 16.096 | 0 | 0.072888 | 0 | 0 | 0.0029133 | 0.081359 | 1.8583 | 0 | 84.5102 | FY35 | 0.67279 | 0.22555 | 2.6181 | 0.072888 | 0.30197 | 0 | 0.03416 | 0.84099 | 0.50876 | 10.2807 | 15.5559 | FY35 | 66.3986 | 16.096 | 0 | 0.072888 | 0.65653 | 0 | 0.00020419 | 0.2863 | 1.8583 | 10.2807 | 95.6496 | FY35 | 0.025596 | 0 | 0 | 540.3509 | 0.65653 | 0 | 0.40749 | 0.0048892 | 0.1471 | 10.2807 | 551.8732 | FY35 | 66.3986 | 16.096 | 0 | 0 | 0.65653 | 0 | 0.01739 | 0.2863 | 1.8583 | 0 | 85.3132 | FY35 | 29.1184 | 6.6675 | 0.39705 | 185.5354 | 0.6886 | 64.008 | 0.17152 | 1.8223 | 0.38873 | 8.9231 | 297.7206
FY36 | 97.2424 | 28.7239 | 3.6767 | 550.4303 | 37.7816 | 117.1795 | 0.62519 | 4.0535 | 4.0451 | 11.1321 | 854.8903 | FY36 | 0.10888 | 0.045221 | 3.6767 | 0.067816 | 0 | 0 | 0.003838 | 1.1884 | 0.93316 | 11.1321 | 17.1561 | FY36 | 97.2424 | 28.7239 | 0 | 0.067816 | 0 | 0 | 0.00024947 | 0.12799 | 4.0451 | 11.1321 | 141.3396 | FY36 | 0 | 0 | 0 | 550.4303 | 0 | 0 | 0.091675 | 0.0065816 | 0.40812 | 11.1321 | 562.0687 | FY36 | 97.2424 | 28.7239 | 0 | 0.067816 | 0 | 0 | 0.003838 | 0.12799 | 4.0451 | 0 | 130.2111 | FY36 | 2.5253 | 0.5777 | 3.6767 | 0.067816 | 0.67397 | 0 | 0.029709 | 1.1884 | 1.6552 | 11.1321 | 21.5268 | FY36 | 97.2424 | 28.7239 | 0 | 0.067816 | 1.3534 | 0 | 0.00024947 | 0.45661 | 4.0451 | 11.1321 | 143.0216 | FY36 | 0.10888 | 0.045221 | 0 | 550.4303 | 1.3534 | 0 | 0.42217 | 0.0065816 | 0.93316 | 11.1321 | 564.4318 | FY36 | 97.2424 | 28.7239 | 0 | 0 | 1.3534 | 0 | 0.015594 | 0.45661 | 4.0451 | 0 | 131.8371 | FY36 | 48.5365 | 12.3589 | 0.69885 | 199.7997 | 1.3474 | 75.9949 | 0.16348 | 2.3682 | 1.3517 | 9.6681 | 352.2877
FY37 | 82.1864 | 41.7144 | 2.1769 | 490.6258 | 43.9889 | 98.5408 | 0.81423 | 4.1917 | 6.1557 | 11.8595 | 782.2544 | FY37 | 0.11653 | 0.16036 | 2.1769 | 0.0042064 | 0 | 0 | 0.0050196 | 1.1763 | 1.8958 | 11.8595 | 17.3946 | FY37 | 82.1864 | 41.7144 | 0 | 0.0042064 | 0 | 0 | 0.00036477 | 0.13124 | 6.1557 | 11.8595 | 142.0518 | FY37 | 0 | 0 | 0 | 490.6258 | 0 | 0 | 0.14236 | 0.0074581 | 1.1057 | 11.8595 | 503.7408 | FY37 | 82.1864 | 41.7144 | 0 | 0.0042064 | 0 | 0 | 0.0050196 | 0.13124 | 6.1557 | 0 | 130.197 | FY37 | 1.6056 | 1.0671 | 2.1769 | 0.0042064 | 0.81064 | 0 | 0.051319 | 1.1763 | 2.9694 | 11.8595 | 21.7209 | FY37 | 82.1864 | 41.7144 | 0 | 0.0042064 | 1.6121 | 0 | 0.00036477 | 0.4384 | 6.1557 | 11.8595 | 143.9711 | FY37 | 0.11653 | 0.16036 | 0 | 490.6258 | 1.6121 | 0 | 0.56588 | 0.0074581 | 1.8958 | 11.8595 | 506.8434 | FY37 | 82.1864 | 41.7144 | 0 | 0 | 1.6121 | 0 | 0.027093 | 0.4384 | 6.1557 | 0 | 132.1341 | FY37 | 37.7559 | 18.6773 | 0.3583 | 162.0496 | 1.484 | 60.3094 | 0.23845 | 2.3845 | 2.4443 | 10.2873 | 295.989
FY38 | 118.6467 | 76.0622 | 6.8409 | 531.5785 | 79.0503 | 113.9545 | 1.1351 | 5.4972 | 9.5383 | 12.8673 | 955.1709 | FY38 | 0.26609 | 0.38516 | 6.8409 | 0.021929 | 0 | 0 | 0.009261 | 1.7955 | 3.3584 | 12.8673 | 25.5446 | FY38 | 118.6467 | 76.0622 | 0 | 0.021929 | 0 | 0 | 0.00056323 | 0.24202 | 9.5383 | 12.8673 | 217.3789 | FY38 | 0.0041476 | 0.0053447 | 0 | 531.5785 | 0 | 0 | 0.25667 | 0.010612 | 2.1989 | 12.8673 | 546.9214 | FY38 | 118.6467 | 76.0622 | 0 | 0.021929 | 0 | 0 | 0.009261 | 0.24202 | 9.5383 | 0 | 204.5204 | FY38 | 4.008 | 3.382 | 6.8409 | 0.021929 | 2.4551 | 0 | 0.11366 | 1.7955 | 4.8769 | 12.8673 | 36.3614 | FY38 | 118.6467 | 76.0622 | 0 | 0.021929 | 5.2611 | 0 | 0.00056323 | 0.77307 | 9.5383 | 12.8673 | 223.1711 | FY38 | 0.26609 | 0.38516 | 0 | 531.5785 | 5.2611 | 0 | 0.82225 | 0.010612 | 3.3584 | 12.8673 | 554.5494 | FY38 | 118.6467 | 76.0622 | 0 | 0 | 5.2611 | 0 | 0.066939 | 0.77307 | 9.5383 | 0 | 210.3483 | FY38 | 60.1181 | 38.1473 | 1.4575 | 186.3699 | 4.1807 | 72.6711 | 0.38706 | 3.2799 | 4.0064 | 11.1846 | 381.8026
FY39 | 162.1544 | 107.3756 | 8.7415 | 565.2239 | 130.1437 | 129.5956 | 1.1175 | 6.94 | 13.8874 | 13.6727 | 1138.8523 | FY39 | 0.48954 | 0.8118 | 8.7415 | 0.054965 | 0 | 0 | 0.0081004 | 2.601 | 5.4855 | 13.6727 | 31.8652 | FY39 | 162.1544 | 107.3756 | 0 | 0.054965 | 0 | 0 | 0.00063171 | 0.47766 | 13.8874 | 13.6727 | 297.6234 | FY39 | 0.026201 | 0.073592 | 0 | 565.2239 | 0 | 0 | 0.21208 | 0.014153 | 3.8676 | 13.6727 | 583.0902 | FY39 | 162.1544 | 107.3756 | 0 | 0.054965 | 0 | 0 | 0.0081004 | 0.47766 | 13.8874 | 0 | 283.9581 | FY39 | 9.1344 | 7.7605 | 8.7415 | 0.054965 | 8.4248 | 0 | 0.082146 | 2.601 | 7.6128 | 13.6727 | 58.0848 | FY39 | 162.1544 | 107.3756 | 0 | 0.054965 | 16.1138 | 0 | 0.00063171 | 1.2823 | 13.8874 | 13.6727 | 314.5418 | FY39 | 0.48954 | 0.8118 | 0 | 565.2239 | 16.1138 | 0 | 0.78734 | 0.014153 | 5.4855 | 13.6727 | 602.5987 | FY39 | 162.1544 | 107.3756 | 0 | 0 | 16.1138 | 0 | 0.04526 | 1.2823 | 13.8874 | 0 | 300.8588 | FY39 | 88.8491 | 58.303 | 2.1669 | 207.1544 | 11.7284 | 85.3484 | 0.3441 | 4.374 | 6.2052 | 11.8732 | 476.3468
FY40 | [10 empty] | 1138.8523 | FY40 | [10 empty] | 31.8652 | FY40 | [10 empty] | 297.6234 | FY40 | [10 empty] | 583.0902 | FY40 | [10 empty] | 283.9581 | FY40 | [10 empty] | 58.0848 | FY40 | [10 empty] | 314.5418 | FY40 | [10 empty] | 602.5987 | FY40 | [10 empty] | 300.8588 | FY40 | [10 empty] | 476.3468
FY41 | [10 empty] | 1138.8523 | FY41 | [10 empty] | 31.8652 | FY41 | [10 empty] | 297.6234 | FY41 | [10 empty] | 583.0902 | FY41 | [10 empty] | 283.9581 | FY41 | [10 empty] | 58.0848 | FY41 | [10 empty] | 314.5418 | FY41 | [10 empty] | 602.5987 | FY41 | [10 empty] | 300.8588 | FY41 | [10 empty] | 476.3468
FY42 | [10 empty] | 1138.8523 | FY42 | [10 empty] | 31.8652 | FY42 | [10 empty] | 297.6234 | FY42 | [10 empty] | 583.0902 | FY42 | [10 empty] | 283.9581 | FY42 | [10 empty] | 58.0848 | FY42 | [10 empty] | 314.5418 | FY42 | [10 empty] | 602.5987 | FY42 | [10 empty] | 300.8588 | FY42 | [10 empty] | 476.3468
FY43 | [10 empty] | 1138.8523 | FY43 | [10 empty] | 31.8652 | FY43 | [10 empty] | 297.6234 | FY43 | [10 empty] | 583.0902 | FY43 | [10 empty] | 283.9581 | FY43 | [10 empty] | 58.0848 | FY43 | [10 empty] | 314.5418 | FY43 | [10 empty] | 602.5987 | FY43 | [10 empty] | 300.8588 | FY43 | [10 empty] | 476.3468
FY44 | [10 empty] | 1138.8523 | FY44 | [10 empty] | 31.8652 | FY44 | [10 empty] | 297.6234 | FY44 | [10 empty] | 583.0902 | FY44 | [10 empty] | 283.9581 | FY44 | [10 empty] | 58.0848 | FY44 | [10 empty] | 314.5418 | FY44 | [10 empty] | 602.5987 | FY44 | [10 empty] | 300.8588 | FY44 | [10 empty] | 476.3468
FY45 | [10 empty] | 1138.8523 | FY45 | [10 empty] | 31.8652 | FY45 | [10 empty] | 297.6234 | FY45 | [10 empty] | 583.0902 | FY45 | [10 empty] | 283.9581 | FY45 | [10 empty] | 58.0848 | FY45 | [10 empty] | 314.5418 | FY45 | [10 empty] | 602.5987 | FY45 | [10 empty] | 300.8588 | FY45 | [10 empty] | 476.3468
FY46 | [10 empty] | 1138.8523 | FY46 | [10 empty] | 31.8652 | FY46 | [10 empty] | 297.6234 | FY46 | [10 empty] | 583.0902 | FY46 | [10 empty] | 283.9581 | FY46 | [10 empty] | 58.0848 | FY46 | [10 empty] | 314.5418 | FY46 | [10 empty] | 602.5987 | FY46 | [10 empty] | 300.8588 | FY46 | [10 empty] | 476.3468
FY47 | [10 empty] | 1138.8523 | FY47 | [10 empty] | 31.8652 | FY47 | [10 empty] | 297.6234 | FY47 | [10 empty] | 583.0902 | FY47 | [10 empty] | 283.9581 | FY47 | [10 empty] | 58.0848 | FY47 | [10 empty] | 314.5418 | FY47 | [10 empty] | 602.5987 | FY47 | [10 empty] | 300.8588 | FY47 | [10 empty] | 476.3468
FY48 | [10 empty] | 1138.8523 | FY48 | [10 empty] | 31.8652 | FY48 | [10 empty] | 297.6234 | FY48 | [10 empty] | 583.0902 | FY48 | [10 empty] | 283.9581 | FY48 | [10 empty] | 58.0848 | FY48 | [10 empty] | 314.5418 | FY48 | [10 empty] | 602.5987 | FY48 | [10 empty] | 300.8588 | FY48 | [10 empty] | 476.3468
FY49 | [10 empty] | 1138.8523 | FY49 | [10 empty] | 31.8652 | FY49 | [10 empty] | 297.6234 | FY49 | [10 empty] | 583.0902 | FY49 | [10 empty] | 283.9581 | FY49 | [10 empty] | 58.0848 | FY49 | [10 empty] | 314.5418 | FY49 | [10 empty] | 602.5987 | FY49 | [10 empty] | 300.8588 | FY49 | [10 empty] | 476.3468
FY50 | [10 empty] | 1138.8523 | FY50 | [10 empty] | 31.8652 | FY50 | [10 empty] | 297.6234 | FY50 | [10 empty] | 583.0902 | FY50 | [10 empty] | 283.9581 | FY50 | [10 empty] | 58.0848 | FY50 | [10 empty] | 314.5418 | FY50 | [10 empty] | 602.5987 | FY50 | [10 empty] | 300.8588 | FY50 | [10 empty] | 476.3468
FY51 | [10 empty] | 1138.8523 | FY51 | [10 empty] | 31.8652 | FY51 | [10 empty] | 297.6234 | FY51 | [10 empty] | 583.0902 | FY51 | [10 empty] | 283.9581 | FY51 | [10 empty] | 58.0848 | FY51 | [10 empty] | 314.5418 | FY51 | [10 empty] | 602.5987 | FY51 | [10 empty] | 300.8588 | FY51 | [10 empty] | 476.3468
FY52 | [10 empty] | 1138.8523 | FY52 | [10 empty] | 31.8652 | FY52 | [10 empty] | 297.6234 | FY52 | [10 empty] | 583.0902 | FY52 | [10 empty] | 283.9581 | FY52 | [10 empty] | 58.0848 | FY52 | [10 empty] | 314.5418 | FY52 | [10 empty] | 602.5987 | FY52 | [10 empty] | 300.8588 | FY52 | [10 empty] | 476.3468
FY53 | [10 empty] | 1138.8523 | FY53 | [10 empty] | 31.8652 | FY53 | [10 empty] | 297.6234 | FY53 | [10 empty] | 583.0902 | FY53 | [10 empty] | 283.9581 | FY53 | [10 empty] | 58.0848 | FY53 | [10 empty] | 314.5418 | FY53 | [10 empty] | 602.5987 | FY53 | [10 empty] | 300.8588 | FY53 | [10 empty] | 476.3468
FY54 | [10 empty] | 1138.8523 | FY54 | [10 empty] | 31.8652 | FY54 | [10 empty] | 297.6234 | FY54 | [10 empty] | 583.0902 | FY54 | [10 empty] | 283.9581 | FY54 | [10 empty] | 58.0848 | FY54 | [10 empty] | 314.5418 | FY54 | [10 empty] | 602.5987 | FY54 | [10 empty] | 300.8588 | FY54 | [10 empty] | 476.3468

## 2.2.2 SupplyRisk$ LowD
Option 1 - Do Nothing / Base Case | [11 empty] | Option 2 - 1A New PHS ZSS + Four new feeders | [11 empty] | Option 3 - 2A PHM 3rd Tx + Switchroom + Three new feeders + OFR12 New Feeder | [11 empty] | Option 4 - 3A OFR 3rd Tx + Switchroom + Three new feeders + OFR12 New Feeder | [11 empty] | Option 5 - 4A LLG 2nd Tx + Switchroom + Three new feeders + OFR12 New Feeder | [11 empty] | Option 6 - 1B New PHS ZSS + Three new feeders | [11 empty] | Option 7 - 2B PHM 3rd Tx + Switchroom + Two new feeders + OFR12 New Feeder | [11 empty] | Option 8 - 3B OFR 3rd Tx + Switchroom + Two new feeders + OFR12 New Feeder | [11 empty] | Option 9 - 4B LLG 2nd Tx + Switchroom + Two new feeders + OFR12 New Feeder | [11 empty] | Option 10 - 5 Non-Network
| Total Supply Risk $M by Asset and Year | [11 empty] | Total Supply Risk $M by Asset and Year | [11 empty] | Total Supply Risk $M by Asset and Year | [11 empty] | Total Supply Risk $M by Asset and Year | [11 empty] | Total Supply Risk $M by Asset and Year | [11 empty] | Total Supply Risk $M by Asset and Year | [11 empty] | Total Supply Risk $M by Asset and Year | [11 empty] | Total Supply Risk $M by Asset and Year | [11 empty] | Total Supply Risk $M by Asset and Year | [11 empty] | Total Supply Risk $M by Asset and Year
Source: | E@R CLN22 Feeder V2.7 POE10 Low Demand.xlsx¦Output for AusNet''s NPV model'!$B$5:$P$5 | E@R CLN23 Feeder V2.7 POE10 Low Demand.xlsx¦Output for AusNet''s NPV model'!$B$5:$P$5 | E@R OFR21 Feeder V2.7 POE10 Low Demand.xlsx¦Output for AusNet''s NPV model'!$B$5:$P$5 | E@R PHM21 Feeder V2.7 POE10 Low Demand.xlsx¦Output for AusNet''s NPV model'!$B$5:$P$5 | E@R PHM22 Feeder V2.7 POE10 Low Demand.xlsx¦Output for AusNet''s NPV model'!$B$5:$P$5 | E@R OFR14 Feeder V2.7 POE10 Low Demand.xlsx¦Output for AusNet''s NPV model'!$B$5:$P$5 | ZSS EaR PHM V2.3 POE10 Low Demand.xlsx¦Output for AusNet''s NPV model'!$B$5:$P$5 | ZSS EaR OFR V2.3 POE10 Low Demand.xlsx¦Output for AusNet''s NPV model'!$B$5:$P$5 | ZSS EaR CLN V2.3 POE10 Low Demand.xlsx¦Output for AusNet''s NPV model'!$B$5:$P$5 | ZSS EaR LLG V2.3 POE10 Low Demand.xlsx¦Output for AusNet''s NPV model'!$B$5:$P$5 |  |  | E@R CLN22 Feeder V2.7 POE10 Low Demand.xlsx¦Output for AusNet''s NPV model'!$B$10:$P$10 | E@R CLN23 Feeder V2.7 POE10 Low Demand.xlsx¦Output for AusNet''s NPV model'!$B$10:$P$10 | E@R OFR21 Feeder V2.7 POE10 Low Demand.xlsx¦Output for AusNet''s NPV model'!$B$10:$P$10 | E@R PHM21 Feeder V2.7 POE10 Low Demand.xlsx¦Output for AusNet''s NPV model'!$B$10:$P$10 | E@R PHM22 Feeder V2.7 POE10 Low Demand.xlsx¦Output for AusNet''s NPV model'!$B$10:$P$10 | E@R OFR14 Feeder V2.7 POE10 Low Demand.xlsx¦Output for AusNet''s NPV model'!$B$10:$P$10 | ZSS EaR PHM V2.3 POE10 Low Demand.xlsx¦Output for AusNet''s NPV model'!$B$10:$P$10 | ZSS EaR OFR V2.3 POE10 Low Demand.xlsx¦Output for AusNet''s NPV model'!$B$10:$P$10 | ZSS EaR CLN V2.3 POE10 Low Demand.xlsx¦Output for AusNet''s NPV model'!$B$10:$P$10 | ZSS EaR LLG V2.3 POE10 Low Demand.xlsx¦Output for AusNet''s NPV model'!$B$10:$P$10 |  |  | E@R CLN22 Feeder V2.7 POE10 Low Demand.xlsx¦Output for AusNet''s NPV model'!$B$13:$P$13 | E@R CLN23 Feeder V2.7 POE10 Low Demand.xlsx¦Output for AusNet''s NPV model'!$B$13:$P$13 | E@R OFR21 Feeder V2.7 POE10 Low Demand.xlsx¦Output for AusNet''s NPV model'!$B$13:$P$13 | E@R PHM21 Feeder V2.7 POE10 Low Demand.xlsx¦Output for AusNet''s NPV model'!$B$13:$P$13 | E@R PHM22 Feeder V2.7 POE10 Low Demand.xlsx¦Output for AusNet''s NPV model'!$B$13:$P$13 | E@R OFR14 Feeder V2.7 POE10 Low Demand.xlsx¦Output for AusNet''s NPV model'!$B$13:$P$13 | ZSS EaR PHM V2.3 POE10 Low Demand.xlsx¦Output for AusNet''s NPV model'!$B$13:$P$13 | ZSS EaR OFR V2.3 POE10 Low Demand.xlsx¦Output for AusNet''s NPV model'!B$13:$P$13 | ZSS EaR CLN V2.3 POE10 Low Demand.xlsx¦Output for AusNet''s NPV model'!B$13:$P$13 | ZSS EaR LLG V2.3 POE10 Low Demand.xlsx¦Output for AusNet''s NPV model'!B$13:$P$13 |  |  | E@R CLN22 Feeder V2.7 POE10 Low Demand.xlsx¦Output for AusNet''s NPV model'!$B$16:$P$16 | E@R CLN23 Feeder V2.7 POE10 Low Demand.xlsx¦Output for AusNet''s NPV model'!$B$16:$P$16 | E@R OFR21 Feeder V2.7 POE10 Low Demand.xlsx¦Output for AusNet''s NPV model'!$B$16:$P$16 | E@R PHM21 Feeder V2.7 POE10 Low Demand.xlsx¦Output for AusNet''s NPV model'!$B$16:$P$16 | E@R PHM22 Feeder V2.7 POE10 Low Demand.xlsx¦Output for AusNet''s NPV model'!$B$16:$P$16 | E@R OFR14 Feeder V2.7 POE10 Low Demand.xlsx¦Output for AusNet''s NPV model'!$B$16:$P$16 | ZSS EaR PHM V2.3 POE10 Low Demand.xlsx¦Output for AusNet''s NPV model'!$B$16:$P$16 | ZSS EaR OFR V2.3 POE10 Low Demand.xlsx¦Output for AusNet''s NPV model'!$B$16:$P$16 | ZSS EaR CLN V2.3 POE10 Low Demand.xlsx¦Output for AusNet''s NPV model'!$B$16:$P$16 | ZSS EaR LLG V2.3 POE10 Low Demand.xlsx¦Output for AusNet''s NPV model'!$B$16:$P$16 |  |  | E@R CLN22 Feeder V2.7 POE10 Low Demand.xlsx¦Output for AusNet''s NPV model'!$B$19:$P$19 | E@R CLN23 Feeder V2.7 POE10 Low Demand.xlsx¦Output for AusNet''s NPV model'!$B$19:$P$19 | E@R OFR21 Feeder V2.7 POE10 Low Demand.xlsx¦Output for AusNet''s NPV model'!$B$19:$P$19 | E@R PHM21 Feeder V2.7 POE10 Low Demand.xlsx¦Output for AusNet''s NPV model'!$B$19:$P$19 | E@R PHM22 Feeder V2.7 POE10 Low Demand.xlsx¦Output for AusNet''s NPV model'!$B$19:$P$19 | E@R OFR14 Feeder V2.7 POE10 Low Demand.xlsx¦Output for AusNet''s NPV model'!$B$19:$P$19 | ZSS EaR PHM V2.3 POE10 Low Demand.xlsx¦Output for AusNet''s NPV model'!$B$19:$P$19 | ZSS EaR OFR V2.3 POE10 Low Demand.xlsx¦Output for AusNet''s NPV model'!$B$19:$P$19 | ZSS EaR CLN V2.3 POE10 Low Demand.xlsx¦Output for AusNet''s NPV model'!$B$19:$P$19 | ZSS EaR LLG V2.3 POE10 Low Demand.xlsx¦Output for AusNet''s NPV model'!$B$19:$P$19 |  |  | E@R CLN22 Feeder V2.7 POE50 Low Demand.xlsx¦Output for AusNet''s NPV model'!$B$10:$P$10 | E@R CLN23 Feeder V2.7 POE50 Low Demand.xlsx¦Output for AusNet''s NPV model'!$B$10:$P$10 | E@R OFR21 Feeder V2.7 POE50 Low Demand.xlsx¦Output for AusNet''s NPV model'!$B$10:$P$10 | E@R PHM21 Feeder V2.7 POE50 Low Demand.xlsx¦Output for AusNet''s NPV model'!$B$10:$P$10 | E@R PHM22 Feeder V2.7 POE50 Low Demand.xlsx¦Output for AusNet''s NPV model'!$B$10:$P$10 | E@R OFR14 Feeder V2.7 POE50 Low Demand.xlsx¦Output for AusNet''s NPV model'!$B$10:$P$10 | ZSS EaR PHM V2.3 POE50 Low Demand.xlsx¦Output for AusNet''s NPV model'!$B$10:$P$10 | ZSS EaR OFR V2.3 POE50 Low Demand.xlsx¦Output for AusNet''s NPV model'!$B$10:$P$10 | ZSS EaR CLN V2.3 POE50 Low Demand.xlsx¦Output for AusNet''s NPV model'!$B$10:$P$10 | ZSS EaR LLG V2.3 POE50 Low Demand.xlsx¦Output for AusNet''s NPV model'!$B$10:$P$10 |  |  | E@R CLN22 Feeder V2.7 POE50 Low Demand.xlsx¦Output for AusNet''s NPV model'!$B$13:$P$13 | E@R CLN23 Feeder V2.7 POE50 Low Demand.xlsx¦Output for AusNet''s NPV model'!$B$13:$P$13 | E@R OFR21 Feeder V2.7 POE50 Low Demand.xlsx¦Output for AusNet''s NPV model'!$B$13:$P$13 | E@R PHM21 Feeder V2.7 POE50 Low Demand.xlsx¦Output for AusNet''s NPV model'!$B$13:$P$13 | E@R PHM22 Feeder V2.7 POE50 Low Demand.xlsx¦Output for AusNet''s NPV model'!$B$13:$P$13 | E@R OFR14 Feeder V2.7 POE50 Low Demand.xlsx¦Output for AusNet''s NPV model'!$B$13:$P$13 | ZSS EaR PHM V2.3 POE50 Low Demand.xlsx¦Output for AusNet''s NPV model'!$B$13:$P$13 | ZSS EaR OFR V2.3 POE50 Low Demand.xlsx¦Output for AusNet''s NPV model'!$B$13:$P$13 | ZSS EaR CLN V2.3 POE50 Low Demand.xlsx¦Output for AusNet''s NPV model'!$B$13:$P$13 | ZSS EaR LLG V2.3 POE50 Low Demand.xlsx¦Output for AusNet''s NPV model'!$B$13:$P$13 |  |  | E@R CLN22 Feeder V2.7 POE50 Low Demand.xlsx¦Output for AusNet''s NPV model'!$B$16:$P$16 | E@R CLN23 Feeder V2.7 POE50 Low Demand.xlsx¦Output for AusNet''s NPV model'!$B$16:$P$16 | E@R OFR21 Feeder V2.7 POE50 Low Demand.xlsx¦Output for AusNet''s NPV model'!$B$16:$P$16 | E@R PHM21 Feeder V2.7 POE50 Low Demand.xlsx¦Output for AusNet''s NPV model'!$B$16:$P$16 | E@R PHM22 Feeder V2.7 POE50 Low Demand.xlsx¦Output for AusNet''s NPV model'!$B$16:$P$16 | E@R OFR14 Feeder V2.7 POE50 Low Demand.xlsx¦Output for AusNet''s NPV model'!$B$16:$P$16 | ZSS EaR PHM V2.3 POE50 Low Demand.xlsx¦Output for AusNet''s NPV model'!$B$16:$P$16 | ZSS EaR OFR V2.3 POE50 Low Demand.xlsx¦Output for AusNet''s NPV model'!$B$16:$P$16 | ZSS EaR CLN V2.3 POE50 Low Demand.xlsx¦Output for AusNet''s NPV model'!$B$16:$P$16 | ZSS EaR LLG V2.3 POE10 Low Demand.xlsx¦Output for AusNet''s NPV model'!$B$16:$P$16 |  |  | E@R CLN22 Feeder V2.7 POE50 Low Demand.xlsx¦Output for AusNet''s NPV model'!$B$19:$P$19 | E@R CLN23 Feeder V2.7 POE50 Low Demand.xlsx¦Output for AusNet''s NPV model'!$B$19:$P$19 | E@R OFR21 Feeder V2.7 POE50 Low Demand.xlsx¦Output for AusNet''s NPV model'!$B$19:$P$19 | E@R PHM21 Feeder V2.7 POE50 Low Demand.xlsx¦Output for AusNet''s NPV model'!$B$19:$P$19 | E@R PHM22 Feeder V2.7 POE50 Low Demand.xlsx¦Output for AusNet''s NPV model'!$B$19:$P$19 | E@R OFR14 Feeder V2.7 POE50 Low Demand.xlsx¦Output for AusNet''s NPV model'!$B$19:$P$19 | ZSS EaR PHM V2.3 POE50 Low Demand.xlsx¦Output for AusNet''s NPV model'!$B$19:$P$19 | ZSS EaR OFR V2.3 POE50 Low Demand.xlsx¦Output for AusNet''s NPV model'!$B$19:$P$19 | ZSS EaR CLN V2.3 POE50 Low Demand.xlsx¦Output for AusNet''s NPV model'!$B$19:$P$19 | ZSS EaR LLG V2.3 POE10 Low Demand.xlsx¦Output for AusNet''s NPV model'!$B$19:$P$19 |  |  | E@R CLN22 Feeder V2.7 POE10 Low Demand.xlsx¦Output for AusNet''s NPV model'!$B$22:$P$22 | E@R CLN23 Feeder V2.7 POE10 Low Demand.xlsx¦Output for AusNet''s NPV model'!$B$22:$P$22 | E@R OFR21 Feeder V2.7 POE10 Low Demand.xlsx¦Output for AusNet''s NPV model'!$B$22:$P$22 | E@R PHM21 Feeder V2.7 POE10 Low Demand.xlsx¦Output for AusNet''s NPV model'!$B$22:$P$22 | E@R PHM22 Feeder V2.7 POE10 Low Demand.xlsx¦Output for AusNet''s NPV model'!$B$22:$P$22 | E@R OFR14 Feeder V2.7 POE10 Low Demand.xlsx¦Output for AusNet''s NPV model'!$B$22:$P$22 | ZSS EaR PHM V2.3 POE10 Low Demand.xlsx¦Output for AusNet''s NPV model'!$B$22:$P$22 | ZSS EaR OFR V2.3 POE10 Low Demand.xlsx¦Output for AusNet''s NPV model'!$B$22:$P$22 | ZSS EaR CLN V2.3 POE10 Low Demand.xlsx¦Output for AusNet''s NPV model'!$B$22:$P$22 | ZSS EaR LLG V2.3 POE10 Low Demand.xlsx¦Output for AusNet''s NPV model'!$B$22:$P$22
Year | CLN22 | CLN23 | OFR21 | PHM21 | PHM22 | OFR14 | PHM | OFR | CLN | LLG | Opt 1 Total | Year | CLN22 | CLN23 | OFR21 | PHM21 | PHM22 | OFR14 | PHM | OFR | CLN | LLG | Opt 2 Total | Year | CLN22 | CLN23 | OFR21 | PHM21 | PHM22 | OFR14 | PHM | OFR | CLN | LLG | Opt 3 Total | Year | CLN22 | CLN23 | OFR21 | PHM21 | PHM22 | OFR14 | PHM | OFR | CLN | LLG | Opt 4 Total | Year | CLN22 | CLN23 | OFR21 | PHM21 | PHM22 | OFR14 | PHM | OFR | CLN | LLG | Opt 5 Total | Year | CLN22 | CLN23 | OFR21 | PHM21 | PHM22 | OFR14 | PHM | OFR | CLN | LLG | Opt 6 Total | Year | CLN22 | CLN23 | OFR21 | PHM21 | PHM22 | OFR14 | PHM | OFR | CLN | LLG | Opt 7 Total | Year | CLN22 | CLN23 | OFR21 | PHM21 | PHM22 | OFR14 | PHM | OFR | CLN | LLG | Opt 8 Total | Year | CLN22 | CLN23 | OFR21 | PHM21 | PHM22 | OFR14 | PHM | OFR | CLN | LLG | Opt 9 Total | Year | CLN22 | CLN23 | OFR21 | PHM21 | PHM22 | OFR14 | PHM | OFR | CLN | LLG | Opt 10 Total
FY25 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00013013 | 0.013196 | 0.00044013 | 2.9555 | 2.9693 | FY25 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00013013 | 0.013196 | 0.00044013 | 2.95 | 2.9638 | FY25 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00013013 | 0.013196 | 0.00044013 | 2.95 | 2.9638 | FY25 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00013013 | 0.013196 | 0.00044013 | 2.95 | 2.9638 | FY25 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00013013 | 0.013196 | 0.00044013 | 2.95 | 2.9638 | FY25 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00013013 | 0.013196 | 0.00044013 | 2.95 | 2.9638 | FY25 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00013013 | 0.013196 | 0.00044013 | 2.95 | 2.9638 | FY25 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00013013 | 0.013196 | 0.00044013 | 2.95 | 2.9638 | FY25 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00013013 | 0.013196 | 0.00044013 | 2.95 | 2.9638 | FY25 | 0 | 0 | 0 | 0 | 0 | 0 | 3.3419e-05 | 0.0090373 | 6.1484e-05 | 2.4871 | 2.4962
FY26 | 0.0081584 | 0 | 0 | 18.4042 | 0 | 0 | 0.0045354 | 0.015196 | 6.714e-05 | 3.3466 | 21.7788 | FY26 | 0.0081584 | 0 | 0 | 18.4042 | 0 | 0 | 0.0045354 | 0.015196 | 6.714e-05 | 3.3466 | 21.7788 | FY26 | 0.0081584 | 0 | 0 | 18.4042 | 0 | 0 | 0.0045354 | 0.015196 | 6.714e-05 | 3.3466 | 21.7788 | FY26 | 0.0081584 | 0 | 0 | 18.4042 | 0 | 0 | 0.0045354 | 0.015196 | 6.714e-05 | 3.3466 | 21.7788 | FY26 | 0.0081584 | 0 | 0 | 18.4042 | 0 | 0 | 0.0045354 | 0.015196 | 6.714e-05 | 3.3466 | 21.7788 | FY26 | 0.0081584 | 0 | 0 | 18.4042 | 0 | 0 | 0.0045354 | 0.015196 | 6.714e-05 | 3.3466 | 21.7788 | FY26 | 0.0081584 | 0 | 0 | 18.4042 | 0 | 0 | 0.0045354 | 0.015196 | 6.714e-05 | 3.3466 | 21.7788 | FY26 | 0.0081584 | 0 | 0 | 18.4042 | 0 | 0 | 0.0045354 | 0.015196 | 6.714e-05 | 3.3466 | 21.7788 | FY26 | 0.0081584 | 0 | 0 | 18.4042 | 0 | 0 | 0.0045354 | 0.015196 | 6.714e-05 | 3.3466 | 21.7788 | FY26 | 0 | 0 | 0 | 0.19876 | 0 | 0 | 0.00041611 | 0.0097726 | 3.1045e-05 | 2.826 | 3.0349
FY27 | 0.046019 | 0 | 0 | 107.0715 | 0.23962 | 2.4238 | 0.015907 | 0.045845 | 0.00024045 | 4.3354 | 114.1785 | FY27 | 0.046019 | 0 | 0 | 107.0715 | 0.23962 | 2.4238 | 0.015907 | 0.045845 | 0.00024045 | 4.3354 | 114.1785 | FY27 | 0.046019 | 0 | 0 | 107.0715 | 0.23962 | 2.4238 | 0.015907 | 0.045845 | 0.00024045 | 4.3354 | 114.1785 | FY27 | 0.046019 | 0 | 0 | 107.0715 | 0.23962 | 2.4238 | 0.015907 | 0.045845 | 0.00024045 | 4.3354 | 114.1785 | FY27 | 0.046019 | 0 | 0 | 107.0715 | 0.23962 | 2.4238 | 0.015907 | 0.045845 | 0.00024045 | 4.3354 | 114.1785 | FY27 | 0.046019 | 0 | 0 | 107.0715 | 0.23962 | 2.4238 | 0.015907 | 0.045845 | 0.00024045 | 4.3354 | 114.1785 | FY27 | 0.046019 | 0 | 0 | 107.0715 | 0.23962 | 2.4238 | 0.015907 | 0.045845 | 0.00024045 | 4.3354 | 114.1785 | FY27 | 0.046019 | 0 | 0 | 107.0715 | 0.23962 | 2.4238 | 0.015907 | 0.045845 | 0.00024045 | 4.3354 | 114.1785 | FY27 | 0.046019 | 0 | 0 | 107.0715 | 0.23962 | 2.4238 | 0.015907 | 0.045845 | 0.00024045 | 4.3354 | 114.1785 | FY27 | 0.0028403 | 0 | 0 | 9.5572 | 0 | 0.29805 | 0.0011432 | 0.018618 | 5.4934e-05 | 3.673 | 13.5509
FY28 | 0.10044 | 0 | 0 | 113.6398 | 0.70419 | 12.3653 | 0.02253 | 0.14835 | 0.00092528 | 4.7992 | 131.7807 | FY28 | 0 | 0 | 0 | 0 | 0 | 12.3653 | 9.2025e-05 | 0.14835 | 5.2033e-05 | 4.7992 | 17.313 | FY28 | 0.10044 | 0 | 0 | 0 | 0 | 12.3653 | 3.1666e-06 | 0.015898 | 0.00092528 | 4.7992 | 17.2818 | FY28 | 0 | 0 | 0 | 113.6398 | 0 | 12.3653 | 0.00066466 | 0.00015592 | 3.3211e-05 | 4.7992 | 130.8052 | FY28 | 0.10044 | 0 | 0 | 0 | 0 | 12.3653 | 9.2025e-05 | 0.015898 | 0.00092528 | 0 | 12.4827 | FY28 | 0 | 0 | 0 | 0 | 0 | 12.3653 | 0.00024453 | 0.14835 | 8.2414e-05 | 4.7992 | 17.3132 | FY28 | 0.10044 | 0 | 0 | 0 | 0 | 12.3653 | 3.1666e-06 | 0.035184 | 0.00092528 | 4.7992 | 17.3011 | FY28 | 0 | 0 | 0 | 113.6398 | 0 | 12.3653 | 0.0089534 | 0.00015592 | 5.2033e-05 | 4.7992 | 130.8135 | FY28 | 0.10044 | 0 | 0 | 0 | 0 | 12.3653 | 0.00014933 | 0.035184 | 0.00092528 | 0 | 12.502 | FY28 | 0.010985 | 0 | 0 | 11.257 | 0.00057093 | 3.9063 | 0.0015396 | 0.042001 | 9.415e-05 | 4.0712 | 19.2897
FY29 | 0.32314 | 0 | 0.00045452 | 142.5358 | 1.6543 | 26.6512 | 0.030537 | 0.26925 | 0.0020517 | 5.2858 | 176.7525 | FY29 | 0 | 0 | 0.00045452 | 0 | 0 | 26.6512 | 0.00014609 | 0.26925 | 8.9245e-05 | 5.2858 | 32.2069 | FY29 | 0.32314 | 0 | 0 | 0 | 0 | 26.6512 | 5.3194e-06 | 0.022909 | 0.0020517 | 5.2858 | 32.2851 | FY29 | 0 | 0 | 0 | 142.5358 | 0 | 26.6512 | 0.00087957 | 0.00029885 | 5.6734e-05 | 5.2858 | 174.474 | FY29 | 0.32314 | 0 | 0 | 0 | 0 | 26.6512 | 0.00014609 | 0.022909 | 0.0020517 | 0 | 26.9994 | FY29 | 0 | 0 | 0.00045452 | 0 | 0 | 0 | 0.00034686 | 0.022909 | 0.00015266 | 5.2858 | 5.3097 | FY29 | 0.32314 | 0 | 0 | 0 | 0.00095603 | 0 | 5.3194e-06 | 0.014573 | 0.0020517 | 5.2858 | 5.6265 | FY29 | 0 | 0 | 0 | 142.5358 | 0.00095603 | 0 | 0.012376 | 0.00029885 | 8.9245e-05 | 5.2858 | 147.8353 | FY29 | 0.32314 | 0 | 0 | 0 | 0.00095603 | 0 | 0.00022476 | 0.014573 | 0.0020517 | 0 | 0.34095 | FY29 | 0.037319 | 0 | 0 | 20.3936 | 0.0013668 | 11.6388 | 0.0020656 | 0.079303 | 0.00019217 | 4.4864 | 36.639
FY30 | 0.80817 | 0 | 0.0072246 | 179.7209 | 1.8459 | 37.0639 | 0.04405 | 0.41424 | 0.0048215 | 5.8452 | 225.7545 | FY30 | 0 | 0 | 0.0072246 | 0 | 0 | 0 | 0.00022602 | 0.033138 | 0.000177 | 5.8452 | 5.886 | FY30 | 0.80817 | 0 | 0 | 0 | 0 | 0 | 9.1408e-06 | 0.014375 | 0.0048215 | 5.8452 | 6.6726 | FY30 | 0 | 0 | 0 | 179.7209 | 0 | 0 | 0.0012416 | 0.00048523 | 0.00010376 | 5.8452 | 185.568 | FY30 | 0.80817 | 0 | 0 | 0 | 0 | 0 | 0.00022602 | 0.014375 | 0.0048215 | 0 | 0.82759 | FY30 | 0 | 0 | 0.0072246 | 0 | 0 | 0 | 0.00051617 | 0.033138 | 0.00084409 | 5.8452 | 5.887 | FY30 | 0.80817 | 0 | 0 | 0 | 0.0022423 | 0 | 9.1408e-06 | 0.019194 | 0.0048215 | 5.8452 | 6.6797 | FY30 | 0 | 0 | 0 | 179.7209 | 0.0022423 | 0 | 0.018712 | 0.00048523 | 0.000177 | 5.8452 | 185.5878 | FY30 | 0.80817 | 0 | 0 | 0 | 0.0022423 | 0 | 0.00034878 | 0.019194 | 0.0048215 | 0 | 0.83478 | FY30 | 0.096799 | 0 | 0 | 33.9365 | 0.0028472 | 17.8355 | 0.0030427 | 0.13299 | 0.0010191 | 4.9681 | 56.9767
FY31 | 1.9876 | 0.047401 | 0.017273 | 269.1186 | 1.9781 | 42.4798 | 0.073277 | 0.60707 | 0.0091391 | 6.5254 | 322.8437 | FY31 | 0 | 0 | 0.017273 | 0 | 0 | 0 | 0.00034547 | 0.050148 | 0.0009004 | 6.5254 | 6.594 | FY31 | 1.9876 | 0.047401 | 0 | 0 | 0 | 0 | 1.7313e-05 | 0.018125 | 0.0091391 | 6.5254 | 8.5877 | FY31 | 0 | 0 | 0 | 269.1186 | 0 | 0 | 0.0019956 | 0.00075478 | 0.00020143 | 6.5254 | 275.6469 | FY31 | 1.9876 | 0.047401 | 0 | 0 | 0 | 0 | 0.00034547 | 0.018125 | 0.0091391 | 0 | 2.0626 | FY31 | 0 | 0 | 0.017273 | 0 | 0 | 0 | 0.00082746 | 0.050148 | 0.002561 | 6.5254 | 6.5962 | FY31 | 1.9876 | 0.047401 | 0 | 0 | 0.0025538 | 0 | 1.7313e-05 | 0.024844 | 0.0091391 | 6.5254 | 8.5969 | FY31 | 0 | 0 | 0 | 269.1186 | 0.0025538 | 0 | 0.034724 | 0.00075478 | 0.0009004 | 6.5254 | 275.6828 | FY31 | 1.9876 | 0.047401 | 0 | 0 | 0.0025538 | 0 | 0.00057544 | 0.024844 | 0.0091391 | 0 | 2.0721 | FY31 | 0.26553 | 0 | 0 | 71.4701 | 0.0034434 | 21.3007 | 0.0057947 | 0.21569 | 0.0027267 | 5.5577 | 98.8217
FY32 | 4.3106 | 0.20527 | 0.032628 | 291.2066 | 2.148 | 46.7403 | 0.10689 | 0.82412 | 0.017951 | 7.2097 | 352.8021 | FY32 | 0 | 0 | 0.032628 | 0 | 0 | 0 | 0.00050919 | 0.077189 | 0.0036212 | 7.2097 | 7.3236 | FY32 | 4.3106 | 0.20527 | 0 | 0 | 0 | 0 | 2.8909e-05 | 0.022726 | 0.017951 | 7.2097 | 11.7663 | FY32 | 0 | 0 | 0 | 291.2066 | 0 | 0 | 0.0032437 | 0.0010878 | 0.0014822 | 7.2097 | 298.4222 | FY32 | 4.3106 | 0.20527 | 0 | 0 | 0 | 0 | 0.00050919 | 0.022726 | 0.017951 | 0 | 4.5571 | FY32 | 0 | 0 | 0.032628 | 0 | 0 | 0 | 0.001234 | 0.077189 | 0.0070066 | 7.2097 | 7.3278 | FY32 | 4.3106 | 0.20527 | 0 | 0 | 0.0037839 | 0 | 2.8909e-05 | 0.032161 | 0.017951 | 7.2097 | 11.7795 | FY32 | 0 | 0 | 0 | 291.2066 | 0.0037839 | 0 | 0.053964 | 0.0010878 | 0.0036212 | 7.2097 | 298.4788 | FY32 | 4.3106 | 0.20527 | 0 | 0 | 0.0037839 | 0 | 0.00086882 | 0.032161 | 0.017951 | 0 | 4.5706 | FY32 | 0.74829 | 0.046271 | 0 | 69.8514 | 0.0049308 | 24.022 | 0.0097087 | 0.31603 | 0.0069457 | 6.1496 | 101.1552
FY33 | 8.2511 | 0.52252 | 0.065776 | 314.1402 | 2.3777 | 50.5591 | 0.16079 | 1.1004 | 0.032753 | 7.8455 | 385.056 | FY33 | 0 | 0 | 0.065776 | 0 | 0 | 0 | 0.0007361 | 0.12283 | 0.0094098 | 7.8455 | 8.0442 | FY33 | 8.2511 | 0.52252 | 0 | 0 | 0 | 0 | 4.9015e-05 | 0.028297 | 0.032753 | 7.8455 | 16.6803 | FY33 | 0 | 0 | 0 | 314.1402 | 0 | 0 | 0.0063526 | 0.0015432 | 0.0051975 | 7.8455 | 321.9988 | FY33 | 8.2511 | 0.52252 | 0 | 0 | 0 | 0 | 0.0007361 | 0.028297 | 0.032753 | 0 | 8.8355 | FY33 | 4.6555e-05 | 0 | 0.065776 | 0 | 0 | 0 | 0.0018393 | 0.12283 | 0.014906 | 7.8455 | 8.0509 | FY33 | 8.2511 | 0.52252 | 0 | 0 | 0.0058701 | 0 | 4.9015e-05 | 0.041788 | 0.032753 | 7.8455 | 16.6996 | FY33 | 0 | 0 | 0 | 314.1402 | 0.0058701 | 0 | 0.087903 | 0.0015432 | 0.0094098 | 7.8455 | 322.0905 | FY33 | 8.2511 | 0.52252 | 0 | 0 | 0.0058701 | 0 | 0.0012729 | 0.041788 | 0.032753 | 0 | 8.8554 | FY33 | 1.586 | 0.18958 | 0 | 71.2289 | 0.007229 | 26.4289 | 0.018798 | 0.45403 | 0.014198 | 6.689 | 106.6167
FY34 | 13.3228 | 1.2877 | 0.093371 | 317.3026 | 2.65 | 52.4822 | 0.25784 | 1.3183 | 0.052215 | 8.5179 | 397.2848 | FY34 | 0 | 0 | 0.093371 | 0 | 0 | 0 | 0.0010487 | 0.16254 | 0.017407 | 8.5179 | 8.7922 | FY34 | 13.3228 | 1.2877 | 0 | 0 | 0 | 0 | 8.6489e-05 | 0.034043 | 0.052215 | 8.5179 | 23.2147 | FY34 | 0 | 0 | 0 | 317.3026 | 0 | 0 | 0.024285 | 0.0019756 | 0.011145 | 8.5179 | 325.8579 | FY34 | 13.3228 | 1.2877 | 0 | 0 | 0 | 0 | 0.0010487 | 0.034043 | 0.052215 | 0 | 14.6977 | FY34 | 0.011101 | 0 | 0.093371 | 0 | 0 | 0 | 0.0072018 | 0.16254 | 0.025984 | 8.5179 | 8.8181 | FY34 | 13.3228 | 1.2877 | 0 | 0 | 0.013137 | 0 | 8.6489e-05 | 0.051736 | 0.052215 | 8.5179 | 23.2455 | FY34 | 0 | 0 | 0 | 317.3026 | 0.013137 | 0 | 0.15807 | 0.0019756 | 0.017407 | 8.5179 | 326.0111 | FY34 | 13.3228 | 1.2877 | 0 | 0 | 0.013137 | 0 | 0.0035813 | 0.051736 | 0.052215 | 0 | 14.7311 | FY34 | 2.7914 | 0.40313 | 0.00017452 | 71.104 | 0.015376 | 27.6712 | 0.050181 | 0.56279 | 0.024113 | 7.2664 | 109.8889
FY35 | 18.527 | 3.7369 | 0.14503 | 318.022 | 3.5527 | 54.5112 | 0.26283 | 1.6088 | 0.089097 | 9.2526 | 409.7082 | FY35 | 0 | 0 | 0.14503 | 0 | 0 | 0 | 0.0013994 | 0.2236 | 0.029619 | 9.2526 | 9.6523 | FY35 | 18.527 | 3.7369 | 0 | 0 | 0 | 0 | 0.00010449 | 0.041361 | 0.089097 | 9.2526 | 31.6471 | FY35 | 0 | 0 | 0 | 318.022 | 0 | 0 | 0.013867 | 0.0025584 | 0.019888 | 9.2526 | 327.3109 | FY35 | 18.527 | 3.7369 | 0 | 0 | 0 | 0 | 0.0013994 | 0.041361 | 0.089097 | 0 | 22.3957 | FY35 | 0.03562 | 0 | 0.14503 | 0 | 0.0056133 | 0 | 0.0036935 | 0.2236 | 0.042646 | 9.2526 | 9.7088 | FY35 | 18.527 | 3.7369 | 0 | 0 | 0.044769 | 0 | 0.00010449 | 0.066886 | 0.089097 | 9.2526 | 31.7174 | FY35 | 0 | 0 | 0 | 318.022 | 0.044769 | 0 | 0.15169 | 0.0025584 | 0.029619 | 9.2526 | 327.5033 | FY35 | 18.527 | 3.7369 | 0 | 0 | 0.044769 | 0 | 0.0025385 | 0.066886 | 0.089097 | 0 | 22.4672 | FY35 | 4.7383 | 0.98963 | 0.0024811 | 67.2434 | 0.049991 | 28.9037 | 0.036071 | 0.7089 | 0.038863 | 7.895 | 110.6063
FY36 | 33.1072 | 7.6973 | 0.26475 | 329.8286 | 6.8995 | 64.6641 | 0.26751 | 2.092 | 0.59529 | 10.0189 | 455.4351 | FY36 | 0 | 0 | 0.26475 | 0 | 0 | 0 | 0.0018424 | 0.353 | 0.058541 | 10.0189 | 10.697 | FY36 | 33.1072 | 7.6973 | 0 | 0 | 0 | 0 | 0.00012388 | 0.050884 | 0.59529 | 10.0189 | 51.4697 | FY36 | 0 | 0 | 0 | 329.8286 | 0 | 0 | 0.012853 | 0.0035244 | 0.041622 | 10.0189 | 339.9055 | FY36 | 33.1072 | 7.6973 | 0 | 0 | 0 | 0 | 0.0018424 | 0.050884 | 0.59529 | 0 | 41.4525 | FY36 | 0.11655 | 0.065587 | 0.26475 | 0 | 0.059546 | 0 | 0.0045711 | 0.353 | 0.079319 | 10.0189 | 10.9622 | FY36 | 33.1072 | 7.6973 | 0 | 0 | 0.17316 | 0 | 0.00012388 | 0.097534 | 0.59529 | 10.0189 | 51.6895 | FY36 | 0 | 0 | 0 | 329.8286 | 0.17316 | 0 | 0.14809 | 0.0035244 | 0.058541 | 10.0189 | 340.2308 | FY36 | 33.1072 | 7.6973 | 0 | 0 | 0.17316 | 0 | 0.0033876 | 0.097534 | 0.59529 | 0 | 41.6739 | FY36 | 11.3357 | 2.3111 | 0.0041033 | 77.7553 | 0.1722 | 36.4162 | 0.031333 | 0.98276 | 0.071021 | 8.5548 | 137.6346
FY37 | 25.3546 | 12.2128 | 0.13909 | 282.0988 | 8.5357 | 51.4543 | 0.36579 | 2.1294 | 1.2957 | 10.6735 | 394.2596 | FY37 | 0 | 0 | 0.13909 | 0 | 0 | 0 | 0.0024646 | 0.34207 | 0.084673 | 10.6735 | 11.2418 | FY37 | 25.3546 | 12.2128 | 0 | 0 | 0 | 0 | 0.00018723 | 0.059638 | 1.2957 | 10.6735 | 49.5964 | FY37 | 0 | 0 | 0 | 282.0988 | 0 | 0 | 0.021613 | 0.003837 | 0.062035 | 10.6735 | 292.8598 | FY37 | 25.3546 | 12.2128 | 0 | 0 | 0 | 0 | 0.0024646 | 0.059638 | 1.2957 | 0 | 38.9251 | FY37 | 0.12521 | 0.18063 | 0.13909 | 0 | 0.070662 | 0 | 0.0062434 | 0.34207 | 0.23898 | 10.6735 | 11.7764 | FY37 | 25.3546 | 12.2128 | 0 | 0 | 0.20765 | 0 | 0.00018723 | 0.10417 | 1.2957 | 10.6735 | 49.8486 | FY37 | 0 | 0 | 0 | 282.0988 | 0.20765 | 0 | 0.21353 | 0.003837 | 0.084673 | 10.6735 | 293.282 | FY37 | 25.3546 | 12.2128 | 0 | 0 | 0.20765 | 0 | 0.0043851 | 0.10417 | 1.2957 | 0 | 39.1792 | FY37 | 7.6015 | 4.038 | 0.0014824 | 55.7643 | 0.18794 | 26.4665 | 0.052033 | 0.96047 | 0.13217 | 9.1014 | 104.3058
FY38 | 42.5544 | 26.6244 | 0.60108 | 312.8422 | 20.3165 | 62.1179 | 0.54793 | 2.9276 | 2.3673 | 11.5805 | 482.4799 | FY38 | 0.0036852 | 0.0063269 | 0.60108 | 0 | 0 | 0 | 0.0033655 | 0.59791 | 0.305 | 11.5805 | 13.0979 | FY38 | 42.5544 | 26.6244 | 0 | 0 | 0 | 0 | 0.00030398 | 0.075499 | 2.3673 | 11.5805 | 83.2025 | FY38 | 0 | 0 | 0 | 312.8422 | 0 | 0 | 0.051345 | 0.0055628 | 0.10207 | 11.5805 | 324.5817 | FY38 | 42.5544 | 26.6244 | 0 | 0 | 0 | 0 | 0.0033655 | 0.075499 | 2.3673 | 0 | 71.625 | FY38 | 0.27024 | 0.40581 | 0.60108 | 0 | 0.29438 | 0 | 0.013102 | 0.59791 | 0.77812 | 11.5805 | 14.5412 | FY38 | 42.5544 | 26.6244 | 0 | 0 | 0.61993 | 0 | 0.00030398 | 0.17521 | 2.3673 | 11.5805 | 83.9221 | FY38 | 0.0036852 | 0.0063269 | 0 | 312.8422 | 0.61993 | 0 | 0.3459 | 0.0055628 | 0.305 | 11.5805 | 325.7091 | FY38 | 42.5544 | 26.6244 | 0 | 0 | 0.61993 | 0 | 0.0071215 | 0.17521 | 2.3673 | 0 | 72.3484 | FY38 | 14.8336 | 10.007 | 0.02337 | 68.6239 | 0.49754 | 34.132 | 0.10587 | 1.4383 | 0.49951 | 9.8979 | 140.059
FY39 | 65.9097 | 42.3255 | 0.98089 | 338.7464 | 42.3963 | 73.0812 | 0.51363 | 3.8799 | 3.9733 | 12.3054 | 584.1122 | FY39 | 0.020492 | 0.067332 | 0.98089 | 0 | 0 | 0 | 0.0040864 | 0.99358 | 0.92418 | 12.3054 | 15.296 | FY39 | 65.9097 | 42.3255 | 0 | 0 | 0 | 0 | 0.00032875 | 0.10083 | 3.9733 | 12.3054 | 124.6151 | FY39 | 0 | 0 | 0 | 338.7464 | 0 | 0 | 0.035669 | 0.007798 | 0.40482 | 12.3054 | 351.5002 | FY39 | 65.9097 | 42.3255 | 0 | 0 | 0 | 0 | 0.0040864 | 0.10083 | 3.9733 | 0 | 112.3134 | FY39 | 0.61055 | 0.87808 | 0.98089 | 0 | 0.88026 | 0 | 0.010328 | 0.99358 | 1.6423 | 12.3054 | 18.3014 | FY39 | 65.9097 | 42.3255 | 0 | 0 | 1.8511 | 0 | 0.00032875 | 0.32992 | 3.9733 | 12.3054 | 126.6952 | FY39 | 0.020492 | 0.067332 | 0 | 338.7464 | 1.8511 | 0 | 0.30738 | 0.007798 | 0.92418 | 12.3054 | 354.2301 | FY39 | 65.9097 | 42.3255 | 0 | 0 | 1.8511 | 0 | 0.0070071 | 0.32992 | 3.9733 | 0 | 114.3965 | FY39 | 25.8709 | 17.7969 | 0.067182 | 80.4657 | 1.2556 | 42.3514 | 0.081225 | 2.0877 | 1.1666 | 10.506 | 181.6492
FY40 | [10 empty] | 584.1122 | FY40 | [10 empty] | 15.296 | FY40 | [10 empty] | 124.6151 | FY40 | [10 empty] | 351.5002 | FY40 | [10 empty] | 112.3134 | FY40 | [10 empty] | 18.3014 | FY40 | [10 empty] | 126.6952 | FY40 | [10 empty] | 354.2301 | FY40 | [10 empty] | 114.3965 | FY40 | [10 empty] | 181.6492
FY41 | [10 empty] | 584.1122 | FY41 | [10 empty] | 15.296 | FY41 | [10 empty] | 124.6151 | FY41 | [10 empty] | 351.5002 | FY41 | [10 empty] | 112.3134 | FY41 | [10 empty] | 18.3014 | FY41 | [10 empty] | 126.6952 | FY41 | [10 empty] | 354.2301 | FY41 | [10 empty] | 114.3965 | FY41 | [10 empty] | 181.6492
FY42 | [10 empty] | 584.1122 | FY42 | [10 empty] | 15.296 | FY42 | [10 empty] | 124.6151 | FY42 | [10 empty] | 351.5002 | FY42 | [10 empty] | 112.3134 | FY42 | [10 empty] | 18.3014 | FY42 | [10 empty] | 126.6952 | FY42 | [10 empty] | 354.2301 | FY42 | [10 empty] | 114.3965 | FY42 | [10 empty] | 181.6492
FY43 | [10 empty] | 584.1122 | FY43 | [10 empty] | 15.296 | FY43 | [10 empty] | 124.6151 | FY43 | [10 empty] | 351.5002 | FY43 | [10 empty] | 112.3134 | FY43 | [10 empty] | 18.3014 | FY43 | [10 empty] | 126.6952 | FY43 | [10 empty] | 354.2301 | FY43 | [10 empty] | 114.3965 | FY43 | [10 empty] | 181.6492
FY44 | [10 empty] | 584.1122 | FY44 | [10 empty] | 15.296 | FY44 | [10 empty] | 124.6151 | FY44 | [10 empty] | 351.5002 | FY44 | [10 empty] | 112.3134 | FY44 | [10 empty] | 18.3014 | FY44 | [10 empty] | 126.6952 | FY44 | [10 empty] | 354.2301 | FY44 | [10 empty] | 114.3965 | FY44 | [10 empty] | 181.6492
FY45 | [10 empty] | 584.1122 | FY45 | [10 empty] | 15.296 | FY45 | [10 empty] | 124.6151 | FY45 | [10 empty] | 351.5002 | FY45 | [10 empty] | 112.3134 | FY45 | [10 empty] | 18.3014 | FY45 | [10 empty] | 126.6952 | FY45 | [10 empty] | 354.2301 | FY45 | [10 empty] | 114.3965 | FY45 | [10 empty] | 181.6492
FY46 | [10 empty] | 584.1122 | FY46 | [10 empty] | 15.296 | FY46 | [10 empty] | 124.6151 | FY46 | [10 empty] | 351.5002 | FY46 | [10 empty] | 112.3134 | FY46 | [10 empty] | 18.3014 | FY46 | [10 empty] | 126.6952 | FY46 | [10 empty] | 354.2301 | FY46 | [10 empty] | 114.3965 | FY46 | [10 empty] | 181.6492
FY47 | [10 empty] | 584.1122 | FY47 | [10 empty] | 15.296 | FY47 | [10 empty] | 124.6151 | FY47 | [10 empty] | 351.5002 | FY47 | [10 empty] | 112.3134 | FY47 | [10 empty] | 18.3014 | FY47 | [10 empty] | 126.6952 | FY47 | [10 empty] | 354.2301 | FY47 | [10 empty] | 114.3965 | FY47 | [10 empty] | 181.6492
FY48 | [10 empty] | 584.1122 | FY48 | [10 empty] | 15.296 | FY48 | [10 empty] | 124.6151 | FY48 | [10 empty] | 351.5002 | FY48 | [10 empty] | 112.3134 | FY48 | [10 empty] | 18.3014 | FY48 | [10 empty] | 126.6952 | FY48 | [10 empty] | 354.2301 | FY48 | [10 empty] | 114.3965 | FY48 | [10 empty] | 181.6492
FY49 | [10 empty] | 584.1122 | FY49 | [10 empty] | 15.296 | FY49 | [10 empty] | 124.6151 | FY49 | [10 empty] | 351.5002 | FY49 | [10 empty] | 112.3134 | FY49 | [10 empty] | 18.3014 | FY49 | [10 empty] | 126.6952 | FY49 | [10 empty] | 354.2301 | FY49 | [10 empty] | 114.3965 | FY49 | [10 empty] | 181.6492
FY50 | [10 empty] | 584.1122 | FY50 | [10 empty] | 15.296 | FY50 | [10 empty] | 124.6151 | FY50 | [10 empty] | 351.5002 | FY50 | [10 empty] | 112.3134 | FY50 | [10 empty] | 18.3014 | FY50 | [10 empty] | 126.6952 | FY50 | [10 empty] | 354.2301 | FY50 | [10 empty] | 114.3965 | FY50 | [10 empty] | 181.6492
FY51 | [10 empty] | 584.1122 | FY51 | [10 empty] | 15.296 | FY51 | [10 empty] | 124.6151 | FY51 | [10 empty] | 351.5002 | FY51 | [10 empty] | 112.3134 | FY51 | [10 empty] | 18.3014 | FY51 | [10 empty] | 126.6952 | FY51 | [10 empty] | 354.2301 | FY51 | [10 empty] | 114.3965 | FY51 | [10 empty] | 181.6492
FY52 | [10 empty] | 584.1122 | FY52 | [10 empty] | 15.296 | FY52 | [10 empty] | 124.6151 | FY52 | [10 empty] | 351.5002 | FY52 | [10 empty] | 112.3134 | FY52 | [10 empty] | 18.3014 | FY52 | [10 empty] | 126.6952 | FY52 | [10 empty] | 354.2301 | FY52 | [10 empty] | 114.3965 | FY52 | [10 empty] | 181.6492
FY53 | [10 empty] | 584.1122 | FY53 | [10 empty] | 15.296 | FY53 | [10 empty] | 124.6151 | FY53 | [10 empty] | 351.5002 | FY53 | [10 empty] | 112.3134 | FY53 | [10 empty] | 18.3014 | FY53 | [10 empty] | 126.6952 | FY53 | [10 empty] | 354.2301 | FY53 | [10 empty] | 114.3965 | FY53 | [10 empty] | 181.6492
FY54 | [10 empty] | 584.1122 | FY54 | [10 empty] | 15.296 | FY54 | [10 empty] | 124.6151 | FY54 | [10 empty] | 351.5002 | FY54 | [10 empty] | 112.3134 | FY54 | [10 empty] | 18.3014 | FY54 | [10 empty] | 126.6952 | FY54 | [10 empty] | 354.2301 | FY54 | [10 empty] | 114.3965 | FY54 | [10 empty] | 181.6492

## 2.2.3 SupplyRisk$ HighD
Option 1 - Do Nothing / Base Case | [11 empty] | Option 2 - 1A New PHS ZSS + Four new feeders | [11 empty] | Option 3 - 2A PHM 3rd Tx + Switchroom + Three new feeders + OFR12 New Feeder | [11 empty] | Option 4 - 3A OFR 3rd Tx + Switchroom + Three new feeders + OFR12 New Feeder | [11 empty] | Option 5 - 4A LLG 2nd Tx + Switchroom + Three new feeders + OFR12 New Feeder | [11 empty] | Option 6 - 1B New PHS ZSS + Three new feeders | [11 empty] | Option 7 - 2B PHM 3rd Tx + Switchroom + Two new feeders + OFR12 New Feeder | [11 empty] | Option 8 - 3B OFR 3rd Tx + Switchroom + Two new feeders + OFR12 New Feeder | [11 empty] | Option 9 - 4B LLG 2nd Tx + Switchroom + Two new feeders + OFR12 New Feeder | [11 empty] | Option 10 - 5 Non-Network
| Total Supply Risk $M by Asset and Year | [11 empty] | Total Supply Risk $M by Asset and Year | [11 empty] | Total Supply Risk $M by Asset and Year | [11 empty] | Total Supply Risk $M by Asset and Year | [11 empty] | Total Supply Risk $M by Asset and Year | [11 empty] | Total Supply Risk $M by Asset and Year | [11 empty] | Total Supply Risk $M by Asset and Year | [11 empty] | Total Supply Risk $M by Asset and Year | [11 empty] | Total Supply Risk $M by Asset and Year | [11 empty] | Total Supply Risk $M by Asset and Year
Source: | E@R CLN22 Feeder V2.7 POE10 High Demand.xlsx¦Output for AusNet''s NPV model'!$B$5:$P$5 | E@R CLN23 Feeder V2.7 POE10 High Demand.xlsx¦Output for AusNet''s NPV model'!$B$5:$P$5 | E@R OFR21 Feeder V2.7 POE10 High Demand.xlsx¦Output for AusNet''s NPV model'!$B$5:$P$5 | E@R PHM21 Feeder V2.7 POE10 High Demand.xlsx¦Output for AusNet''s NPV model'!$B$5:$P$5 | E@R PHM22 Feeder V2.7 POE10 High Demand.xlsx¦Output for AusNet''s NPV model'!$B$5:$P$5 | E@R OFR14 Feeder V2.7 POE10 High Demand.xlsx¦Output for AusNet''s NPV model'!$B$5:$P$5 | ZSS EaR PHM V2.3 POE10 High Demand.xlsx¦Output for AusNet''s NPV model'!$B$5:$P$5 | ZSS EaR OFR V2.3 POE10 High Demand.xlsx¦Output for AusNet''s NPV model'!$B$5:$P$5 | ZSS EaR CLN V2.3 POE10 High Demand.xlsx¦Output for AusNet''s NPV model'!$B$5:$P$5 | ZSS EaR LLG V2.3 POE10 High Demand.xlsx¦Output for AusNet''s NPV model'!$B$5:$P$5 |  |  | E@R CLN22 Feeder V2.7 POE10 High Demand.xlsx¦Output for AusNet''s NPV model'!$B$10:$P$10 | E@R CLN23 Feeder V2.7 POE10 High Demand.xlsx¦Output for AusNet''s NPV model'!$B$10:$P$10 | E@R OFR21 Feeder V2.7 POE10 High Demand.xlsx¦Output for AusNet''s NPV model'!$B$10:$P$10 | E@R PHM21 Feeder V2.7 POE10 High Demand.xlsx¦Output for AusNet''s NPV model'!$B$10:$P$10 | E@R PHM22 Feeder V2.7 POE10 High Demand.xlsx¦Output for AusNet''s NPV model'!$B$10:$P$10 | E@R OFR14 Feeder V2.7 POE10 High Demand.xlsx¦Output for AusNet''s NPV model'!$B$10:$P$10 | ZSS EaR PHM V2.3 POE10 High Demand.xlsx¦Output for AusNet''s NPV model'!$B$10:$P$10 | ZSS EaR OFR V2.3 POE10 High Demand.xlsx¦Output for AusNet''s NPV model'!$B$10:$P$10 | ZSS EaR CLN V2.3 POE10 High Demand.xlsx¦Output for AusNet''s NPV model'!$B$10:$P$10 | ZSS EaR LLG V2.3 POE10 High Demand.xlsx¦Output for AusNet''s NPV model'!$B$10:$P$10 |  |  | E@R CLN22 Feeder V2.7 POE10 High Demand.xlsx¦Output for AusNet''s NPV model'!$B$13:$P$13 | E@R CLN23 Feeder V2.7 POE10 High Demand.xlsx¦Output for AusNet''s NPV model'!$B$13:$P$13 | E@R OFR21 Feeder V2.7 POE10 High Demand.xlsx¦Output for AusNet''s NPV model'!$B$13:$P$13 | E@R PHM21 Feeder V2.7 POE10 High Demand.xlsx¦Output for AusNet''s NPV model'!$B$13:$P$13 | E@R PHM22 Feeder V2.7 POE10 High Demand.xlsx¦Output for AusNet''s NPV model'!$B$13:$P$13 | E@R OFR14 Feeder V2.7 POE10 High Demand.xlsx¦Output for AusNet''s NPV model'!$B$13:$P$13 | ZSS EaR PHM V2.3 POE10 High Demand.xlsx¦Output for AusNet''s NPV model'!$B$13:$P$13 | ZSS EaR OFR V2.3 POE10 High Demand.xlsx¦Output for AusNet''s NPV model'!B$13:$P$13 | ZSS EaR CLN V2.3 POE10 High Demand.xlsx¦Output for AusNet''s NPV model'!B$13:$P$13 | ZSS EaR LLG V2.3 POE10 High Demand.xlsx¦Output for AusNet''s NPV model'!B$13:$P$13 |  |  | E@R CLN22 Feeder V2.7 POE10 High Demand.xlsx¦Output for AusNet''s NPV model'!$B$16:$P$16 | E@R CLN23 Feeder V2.7 POE10 High Demand.xlsx¦Output for AusNet''s NPV model'!$B$16:$P$16 | E@R OFR21 Feeder V2.7 POE10 High Demand.xlsx¦Output for AusNet''s NPV model'!$B$16:$P$16 | E@R PHM21 Feeder V2.7 POE10 High Demand.xlsx¦Output for AusNet''s NPV model'!$B$16:$P$16 | E@R PHM22 Feeder V2.7 POE10 High Demand.xlsx¦Output for AusNet''s NPV model'!$B$16:$P$16 | E@R OFR14 Feeder V2.7 POE10 High Demand.xlsx¦Output for AusNet''s NPV model'!$B$16:$P$16 | ZSS EaR PHM V2.3 POE10 High Demand.xlsx¦Output for AusNet''s NPV model'!$B$16:$P$16 | ZSS EaR OFR V2.3 POE10 High Demand.xlsx¦Output for AusNet''s NPV model'!$B$16:$P$16 | ZSS EaR CLN V2.3 POE10 High Demand.xlsx¦Output for AusNet''s NPV model'!$B$16:$P$16 | ZSS EaR LLG V2.3 POE10 High Demand.xlsx¦Output for AusNet''s NPV model'!$B$16:$P$16 |  |  | E@R CLN22 Feeder V2.7 POE10 High Demand.xlsx¦Output for AusNet''s NPV model'!$B$19:$P$19 | E@R CLN23 Feeder V2.7 POE10 High Demand.xlsx¦Output for AusNet''s NPV model'!$B$19:$P$19 | E@R OFR21 Feeder V2.7 POE10 High Demand.xlsx¦Output for AusNet''s NPV model'!$B$19:$P$19 | E@R PHM21 Feeder V2.7 POE10 High Demand.xlsx¦Output for AusNet''s NPV model'!$B$19:$P$19 | E@R PHM22 Feeder V2.7 POE10 High Demand.xlsx¦Output for AusNet''s NPV model'!$B$19:$P$19 | E@R OFR14 Feeder V2.7 POE10 High Demand.xlsx¦Output for AusNet''s NPV model'!$B$19:$P$19 | ZSS EaR PHM V2.3 POE10 High Demand.xlsx¦Output for AusNet''s NPV model'!$B$19:$P$19 | ZSS EaR OFR V2.3 POE10 High Demand.xlsx¦Output for AusNet''s NPV model'!$B$19:$P$19 | ZSS EaR CLN V2.3 POE10 High Demand.xlsx¦Output for AusNet''s NPV model'!$B$19:$P$19 | ZSS EaR LLG V2.3 POE10 High Demand.xlsx¦Output for AusNet''s NPV model'!$B$19:$P$19 |  |  | E@R CLN22 Feeder V2.7 POE50 High Demand.xlsx¦Output for AusNet''s NPV model'!$B$10:$P$10 | E@R CLN23 Feeder V2.7 POE50 High Demand.xlsx¦Output for AusNet''s NPV model'!$B$10:$P$10 | E@R OFR21 Feeder V2.7 POE50 High Demand.xlsx¦Output for AusNet''s NPV model'!$B$10:$P$10 | E@R PHM21 Feeder V2.7 POE50 High Demand.xlsx¦Output for AusNet''s NPV model'!$B$10:$P$10 | E@R PHM22 Feeder V2.7 POE50 High Demand.xlsx¦Output for AusNet''s NPV model'!$B$10:$P$10 | E@R OFR14 Feeder V2.7 POE50 High Demand.xlsx¦Output for AusNet''s NPV model'!$B$10:$P$10 | ZSS EaR PHM V2.3 POE50 High Demand.xlsx¦Output for AusNet''s NPV model'!$B$10:$P$10 | ZSS EaR OFR V2.3 POE50 High Demand.xlsx¦Output for AusNet''s NPV model'!$B$10:$P$10 | ZSS EaR CLN V2.3 POE50 High Demand.xlsx¦Output for AusNet''s NPV model'!$B$10:$P$10 | ZSS EaR LLG V2.3 POE50 High Demand.xlsx¦Output for AusNet''s NPV model'!$B$10:$P$10 |  |  | E@R CLN22 Feeder V2.7 POE50 High Demand.xlsx¦Output for AusNet''s NPV model'!$B$13:$P$13 | E@R CLN23 Feeder V2.7 POE50 High Demand.xlsx¦Output for AusNet''s NPV model'!$B$13:$P$13 | E@R OFR21 Feeder V2.7 POE50 High Demand.xlsx¦Output for AusNet''s NPV model'!$B$13:$P$13 | E@R PHM21 Feeder V2.7 POE50 High Demand.xlsx¦Output for AusNet''s NPV model'!$B$13:$P$13 | E@R PHM22 Feeder V2.7 POE50 High Demand.xlsx¦Output for AusNet''s NPV model'!$B$13:$P$13 | E@R OFR14 Feeder V2.7 POE50 High Demand.xlsx¦Output for AusNet''s NPV model'!$B$13:$P$13 | ZSS EaR PHM V2.3 POE50 High Demand.xlsx¦Output for AusNet''s NPV model'!$B$13:$P$13 | ZSS EaR OFR V2.3 POE50 High Demand.xlsx¦Output for AusNet''s NPV model'!$B$13:$P$13 | ZSS EaR CLN V2.3 POE50 High Demand.xlsx¦Output for AusNet''s NPV model'!$B$13:$P$13 | ZSS EaR LLG V2.3 POE50 High Demand.xlsx¦Output for AusNet''s NPV model'!$B$13:$P$13 |  |  | E@R CLN22 Feeder V2.7 POE50 High Demand.xlsx¦Output for AusNet''s NPV model'!$B$16:$P$16 | E@R CLN23 Feeder V2.7 POE50 High Demand.xlsx¦Output for AusNet''s NPV model'!$B$16:$P$16 | E@R OFR21 Feeder V2.7 POE50 High Demand.xlsx¦Output for AusNet''s NPV model'!$B$16:$P$16 | E@R PHM21 Feeder V2.7 POE50 High Demand.xlsx¦Output for AusNet''s NPV model'!$B$16:$P$16 | E@R PHM22 Feeder V2.7 POE50 High Demand.xlsx¦Output for AusNet''s NPV model'!$B$16:$P$16 | E@R OFR14 Feeder V2.7 POE50 High Demand.xlsx¦Output for AusNet''s NPV model'!$B$16:$P$16 | ZSS EaR PHM V2.3 POE50 High Demand.xlsx¦Output for AusNet''s NPV model'!$B$16:$P$16 | ZSS EaR OFR V2.3 POE50 High Demand.xlsx¦Output for AusNet''s NPV model'!$B$16:$P$16 | ZSS EaR CLN V2.3 POE50 High Demand.xlsx¦Output for AusNet''s NPV model'!$B$16:$P$16 | ZSS EaR LLG V2.3 POE10 High Demand.xlsx¦Output for AusNet''s NPV model'!$B$16:$P$16 |  |  | E@R CLN22 Feeder V2.7 POE50 High Demand.xlsx¦Output for AusNet''s NPV model'!$B$19:$P$19 | E@R CLN23 Feeder V2.7 POE50 High Demand.xlsx¦Output for AusNet''s NPV model'!$B$19:$P$19 | E@R OFR21 Feeder V2.7 POE50 High Demand.xlsx¦Output for AusNet''s NPV model'!$B$19:$P$19 | E@R PHM21 Feeder V2.7 POE50 High Demand.xlsx¦Output for AusNet''s NPV model'!$B$19:$P$19 | E@R PHM22 Feeder V2.7 POE50 High Demand.xlsx¦Output for AusNet''s NPV model'!$B$19:$P$19 | E@R OFR14 Feeder V2.7 POE50 High Demand.xlsx¦Output for AusNet''s NPV model'!$B$19:$P$19 | ZSS EaR PHM V2.3 POE50 High Demand.xlsx¦Output for AusNet''s NPV model'!$B$19:$P$19 | ZSS EaR OFR V2.3 POE50 High Demand.xlsx¦Output for AusNet''s NPV model'!$B$19:$P$19 | ZSS EaR CLN V2.3 POE50 High Demand.xlsx¦Output for AusNet''s NPV model'!$B$19:$P$19 | ZSS EaR LLG V2.3 POE10 High Demand.xlsx¦Output for AusNet''s NPV model'!$B$19:$P$19 |  |  | E@R CLN22 Feeder V2.7 POE10 High Demand.xlsx¦Output for AusNet''s NPV model'!$B$22:$P$22 | E@R CLN23 Feeder V2.7 POE10 High Demand.xlsx¦Output for AusNet''s NPV model'!$B$22:$P$22 | E@R OFR21 Feeder V2.7 POE10 High Demand.xlsx¦Output for AusNet''s NPV model'!$B$22:$P$22 | E@R PHM21 Feeder V2.7 POE10 High Demand.xlsx¦Output for AusNet''s NPV model'!$B$22:$P$22 | E@R PHM22 Feeder V2.7 POE10 High Demand.xlsx¦Output for AusNet''s NPV model'!$B$22:$P$22 | E@R OFR14 Feeder V2.7 POE10 High Demand.xlsx¦Output for AusNet''s NPV model'!$B$22:$P$22 | ZSS EaR PHM V2.3 POE10 High Demand.xlsx¦Output for AusNet''s NPV model'!$B$22:$P$22 | ZSS EaR OFR V2.3 POE10 High Demand.xlsx¦Output for AusNet''s NPV model'!$B$22:$P$22 | ZSS EaR CLN V2.3 POE10 High Demand.xlsx¦Output for AusNet''s NPV model'!$B$22:$P$22 | ZSS EaR LLG V2.3 POE10 High Demand.xlsx¦Output for AusNet''s NPV model'!$B$22:$P$22
Year | CLN22 | CLN23 | OFR21 | PHM21 | PHM22 | OFR14 | PHM | OFR | CLN | LLG | Opt 1 Total | Year | CLN22 | CLN23 | OFR21 | PHM21 | PHM22 | OFR14 | PHM | OFR | CLN | LLG | Opt 2 Total | Year | CLN22 | CLN23 | OFR21 | PHM21 | PHM22 | OFR14 | PHM | OFR | CLN | LLG | Opt 3 Total | Year | CLN22 | CLN23 | OFR21 | PHM21 | PHM22 | OFR14 | PHM | OFR | CLN | LLG | Opt 4 Total | Year | CLN22 | CLN23 | OFR21 | PHM21 | PHM22 | OFR14 | PHM | OFR | CLN | LLG | Opt 5 Total | Year | CLN22 | CLN23 | OFR21 | PHM21 | PHM22 | OFR14 | PHM | OFR | CLN | LLG | Opt 6 Total | Year | CLN22 | CLN23 | OFR21 | PHM21 | PHM22 | OFR14 | PHM | OFR | CLN | LLG | Opt 7 Total | Year | CLN22 | CLN23 | OFR21 | PHM21 | PHM22 | OFR14 | PHM | OFR | CLN | LLG | Opt 8 Total | Year | CLN22 | CLN23 | OFR21 | PHM21 | PHM22 | OFR14 | PHM | OFR | CLN | LLG | Opt 9 Total | Year | CLN22 | CLN23 | OFR21 | PHM21 | PHM22 | OFR14 | PHM | OFR | CLN | LLG | Opt 10 Total
FY25 | 0 | 0 | 0.090384 | 0 | 0 | 0 | 0.0013201 | 0.072084 | 0.0091026 | 3.6123 | 3.7852 | FY25 | 0 | 0 | 0.090384 | 0 | 0 | 0 | 0.0013201 | 0.072084 | 0.0091026 | 3.6055 | 3.7784 | FY25 | 0 | 0 | 0.090384 | 0 | 0 | 0 | 0.0013201 | 0.072084 | 0.0091026 | 3.6055 | 3.7784 | FY25 | 0 | 0 | 0.090384 | 0 | 0 | 0 | 0.0013201 | 0.072084 | 0.0091026 | 3.6055 | 3.7784 | FY25 | 0 | 0 | 0.090384 | 0 | 0 | 0 | 0.0013201 | 0.072084 | 0.0091026 | 3.6055 | 3.7784 | FY25 | 0 | 0 | 0.090384 | 0 | 0 | 0 | 0.0013201 | 0.072084 | 0.0091026 | 3.6055 | 3.7784 | FY25 | 0 | 0 | 0.090384 | 0 | 0 | 0 | 0.0013201 | 0.072084 | 0.0091026 | 3.6055 | 3.7784 | FY25 | 0 | 0 | 0.090384 | 0 | 0 | 0 | 0.0013201 | 0.072084 | 0.0091026 | 3.6055 | 3.7784 | FY25 | 0 | 0 | 0.090384 | 0 | 0 | 0 | 0.0013201 | 0.072084 | 0.0091026 | 3.6055 | 3.7784 | FY25 | 0 | 0 | 0.0099054 | 0 | 0 | 0 | 0.00030971 | 0.029117 | 0.0045662 | 3.1427 | 3.1866
FY26 | 4.0801 | 0 | 0.27305 | 138.5595 | 0.1965 | 1.2525 | 0.05225 | 0.12257 | 0.0065832 | 4.0903 | 148.6333 | FY26 | 4.0801 | 0 | 0.27305 | 138.5595 | 0.1965 | 1.2525 | 0.05225 | 0.12257 | 0.0065832 | 4.0903 | 148.6333 | FY26 | 4.0801 | 0 | 0.27305 | 138.5595 | 0.1965 | 1.2525 | 0.05225 | 0.12257 | 0.0065832 | 4.0903 | 148.6333 | FY26 | 4.0801 | 0 | 0.27305 | 138.5595 | 0.1965 | 1.2525 | 0.05225 | 0.12257 | 0.0065832 | 4.0903 | 148.6333 | FY26 | 4.0801 | 0 | 0.27305 | 138.5595 | 0.1965 | 1.2525 | 0.05225 | 0.12257 | 0.0065832 | 4.0903 | 148.6333 | FY26 | 4.0801 | 0 | 0.27305 | 138.5595 | 0.1965 | 1.2525 | 0.05225 | 0.12257 | 0.0065832 | 4.0903 | 148.6333 | FY26 | 4.0801 | 0 | 0.27305 | 138.5595 | 0.1965 | 1.2525 | 0.05225 | 0.12257 | 0.0065832 | 4.0903 | 148.6333 | FY26 | 4.0801 | 0 | 0.27305 | 138.5595 | 0.1965 | 1.2525 | 0.05225 | 0.12257 | 0.0065832 | 4.0903 | 148.6333 | FY26 | 4.0801 | 0 | 0.27305 | 138.5595 | 0.1965 | 1.2525 | 0.05225 | 0.12257 | 0.0065832 | 4.0903 | 148.6333 | FY26 | 0.9248 | 0 | 0.048979 | 26.0362 | 0 | 0.18091 | 0.010386 | 0.043551 | 0.0027415 | 3.5697 | 30.8172
FY27 | 9.231 | 0 | 0.99211 | 396.2977 | 9.0877 | 26.3914 | 0.11664 | 0.45496 | 0.011955 | 5.2989 | 447.8825 | FY27 | 9.231 | 0 | 0.99211 | 396.2977 | 9.0877 | 26.3914 | 0.11664 | 0.45496 | 0.011955 | 5.2989 | 447.8825 | FY27 | 9.231 | 0 | 0.99211 | 396.2977 | 9.0877 | 26.3914 | 0.11664 | 0.45496 | 0.011955 | 5.2989 | 447.8825 | FY27 | 9.231 | 0 | 0.99211 | 396.2977 | 9.0877 | 26.3914 | 0.11664 | 0.45496 | 0.011955 | 5.2989 | 447.8825 | FY27 | 9.231 | 0 | 0.99211 | 396.2977 | 9.0877 | 26.3914 | 0.11664 | 0.45496 | 0.011955 | 5.2989 | 447.8825 | FY27 | 9.231 | 0 | 0.99211 | 396.2977 | 9.0877 | 26.3914 | 0.11664 | 0.45496 | 0.011955 | 5.2989 | 447.8825 | FY27 | 9.231 | 0 | 0.99211 | 396.2977 | 9.0877 | 26.3914 | 0.11664 | 0.45496 | 0.011955 | 5.2989 | 447.8825 | FY27 | 9.231 | 0 | 0.99211 | 396.2977 | 9.0877 | 26.3914 | 0.11664 | 0.45496 | 0.011955 | 5.2989 | 447.8825 | FY27 | 9.231 | 0 | 0.99211 | 396.2977 | 9.0877 | 26.3914 | 0.11664 | 0.45496 | 0.011955 | 5.2989 | 447.8825 | FY27 | 2.307 | 0 | 0.21366 | 134.6606 | 0.34498 | 13.6493 | 0.031925 | 0.19278 | 0.0054826 | 4.6364 | 156.0422
FY28 | 15.8795 | 0.018585 | 1.4908 | 408.4558 | 25.5244 | 61.2491 | 0.15651 | 1.0065 | 0.018873 | 5.8657 | 519.6658 | FY28 | 0 | 0 | 1.4908 | 0 | 0 | 61.2491 | 0.00079776 | 1.0065 | 0.0050107 | 5.8657 | 69.6179 | FY28 | 15.8795 | 0.018585 | 0 | 0 | 0 | 61.2491 | 1.4963e-05 | 0.14625 | 0.018873 | 5.8657 | 83.178 | FY28 | 0 | 0 | 0 | 408.4558 | 0 | 61.2491 | 0.021895 | 0.00088763 | 0.0026922 | 5.8657 | 475.596 | FY28 | 15.8795 | 0.018585 | 0 | 0 | 0 | 61.2491 | 0.00079776 | 0.14625 | 0.018873 | 0 | 77.3131 | FY28 | 0.0066959 | 0 | 1.4908 | 0 | 0.36004 | 61.2491 | 0.0071337 | 1.0065 | 0.0081684 | 5.8657 | 69.9941 | FY28 | 15.8795 | 0.018585 | 0 | 0 | 0.74311 | 61.2491 | 1.4963e-05 | 0.45217 | 0.018873 | 5.8657 | 84.227 | FY28 | 0 | 0 | 0 | 408.4558 | 0.74311 | 61.2491 | 0.10529 | 0.00088763 | 0.0050107 | 5.8657 | 476.4249 | FY28 | 15.8795 | 0.018585 | 0 | 0 | 0.74311 | 61.2491 | 0.0037995 | 0.45217 | 0.018873 | 0 | 78.3652 | FY28 | 4.8763 | 0 | 0.30625 | 142.5222 | 1.0525 | 37.4464 | 0.044942 | 0.51157 | 0.0091917 | 5.1377 | 191.907
FY29 | 25.9198 | 0.15835 | 2.0537 | 464.1572 | 49.8394 | 100.4966 | 0.20359 | 1.488 | 0.02847 | 6.4604 | 650.8055 | FY29 | 0 | 0 | 2.0537 | 0 | 0 | 100.4966 | 0.0010467 | 1.488 | 0.0084908 | 6.4604 | 110.5081 | FY29 | 25.9198 | 0.15835 | 0 | 0 | 0 | 100.4966 | 2.4358e-05 | 0.29101 | 0.02847 | 6.4604 | 133.3547 | FY29 | 0 | 0 | 0 | 464.1572 | 0 | 100.4966 | 0.030054 | 0.0014027 | 0.005107 | 6.4604 | 571.1507 | FY29 | 25.9198 | 0.15835 | 0 | 0 | 0 | 100.4966 | 0.0010467 | 0.29101 | 0.02847 | 0 | 126.8953 | FY29 | 0.034265 | 0 | 2.0537 | 0 | 0.88769 | 0 | 0.0099778 | 0.29101 | 0.013343 | 6.4604 | 9.7504 | FY29 | 25.9198 | 0.15835 | 0 | 0 | 2.0264 | 0 | 2.4358e-05 | 0.077946 | 0.02847 | 6.4604 | 34.6715 | FY29 | 0 | 0 | 0 | 464.1572 | 2.0264 | 0 | 0.13815 | 0.0014027 | 0.0084908 | 6.4604 | 472.792 | FY29 | 25.9198 | 0.15835 | 0 | 0 | 2.0264 | 0 | 0.0052739 | 0.077946 | 0.02847 | 0 | 28.2163 | FY29 | 9.4287 | 0.038991 | 0.41817 | 182.8713 | 2.174 | 65.4627 | 0.060361 | 0.81343 | 0.01464 | 5.661 | 266.9433
FY30 | 37.4427 | 0.47389 | 2.8372 | 534.3445 | 52.4414 | 127.1474 | 0.27196 | 2.0019 | 0.046528 | 7.1442 | 764.1517 | FY30 | 0 | 0 | 2.8372 | 0.0061919 | 0 | 0 | 0.0014866 | 0.47278 | 0.015956 | 7.1442 | 10.4779 | FY30 | 37.4427 | 0.47389 | 0 | 0.0061919 | 0 | 0 | 3.9698e-05 | 0.040412 | 0.046528 | 7.1442 | 45.1539 | FY30 | 0 | 0 | 0 | 534.3445 | 0 | 0 | 0.04472 | 0.0020812 | 0.010453 | 7.1442 | 541.546 | FY30 | 37.4427 | 0.47389 | 0 | 0.0061919 | 0 | 0 | 0.0014866 | 0.040412 | 0.046528 | 0 | 38.0112 | FY30 | 0.10951 | 0 | 2.8372 | 0.0061919 | 1.0004 | 0 | 0.015796 | 0.47278 | 0.023488 | 7.1442 | 11.6096 | FY30 | 37.4427 | 0.47389 | 0 | 0 | 2.2668 | 0 | 3.9698e-05 | 0.14654 | 0.046528 | 7.1442 | 47.5206 | FY30 | 0 | 0 | 0 | 534.3445 | 2.2668 | 0 | 0.18777 | 0.0020812 | 0.015956 | 7.1442 | 543.9613 | FY30 | 37.4427 | 0.47389 | 0 | 0 | 2.2668 | 0 | 0.0083624 | 0.14654 | 0.046528 | 0 | 40.3847 | FY30 | 15.0106 | 0.23635 | 0.62041 | 231.2268 | 2.3875 | 84.4574 | 0.085155 | 1.1471 | 0.024739 | 6.2671 | 341.463
FY31 | 57.4035 | 1.366 | 4.3315 | 694.6812 | 54.6329 | 140.0695 | 0.38749 | 2.6233 | 0.26511 | 7.9754 | 963.7359 | FY31 | 0.0020893 | 0 | 4.3315 | 2.1852 | 0 | 0 | 0.002524 | 0.72119 | 0.0271 | 7.9754 | 15.245 | FY31 | 57.4035 | 1.366 | 0 | 2.1852 | 0 | 0 | 6.7481e-05 | 0.067126 | 0.26511 | 7.9754 | 69.2624 | FY31 | 0 | 0 | 0 | 694.6812 | 0 | 0 | 0.078826 | 0.0030868 | 0.018597 | 7.9754 | 702.7571 | FY31 | 57.4035 | 1.366 | 0 | 2.1852 | 0 | 0 | 0.002524 | 0.067126 | 0.26511 | 0 | 61.2894 | FY31 | 0.25214 | 0 | 4.3315 | 2.1852 | 1.0658 | 0 | 0.032163 | 0.72119 | 0.037822 | 7.9754 | 16.6012 | FY31 | 57.4035 | 1.366 | 0 | 2.1852 | 2.4176 | 0 | 6.7481e-05 | 0.25888 | 0.26511 | 7.9754 | 71.8718 | FY31 | 0.0020893 | 0 | 0 | 694.6812 | 2.4176 | 0 | 0.27663 | 0.0030868 | 0.0271 | 7.9754 | 705.3831 | FY31 | 57.4035 | 1.366 | 0 | 0 | 2.4176 | 0 | 0.018169 | 0.25888 | 0.26511 | 0 | 61.7293 | FY31 | 26.2516 | 0.5882 | 1.0547 | 337.2819 | 2.5745 | 94.0687 | 0.1346 | 1.56 | 0.038744 | 7.0078 | 470.5607
FY32 | 78.3359 | 4.6683 | 5.8823 | 749.9579 | 57.1476 | 150.6513 | 0.51872 | 3.3328 | 1.1074 | 8.8119 | 1060.4142 | FY32 | 0.024845 | 0 | 5.8823 | 2.8528 | 0 | 0 | 0.0042842 | 1.0067 | 0.047528 | 8.8119 | 18.6303 | FY32 | 78.3359 | 4.6683 | 0 | 2.8528 | 0 | 0 | 0.00010654 | 0.11327 | 1.1074 | 8.8119 | 95.8896 | FY32 | 0 | 0 | 0 | 749.9579 | 0 | 0 | 0.11879 | 0.0044382 | 0.03486 | 8.8119 | 758.9278 | FY32 | 78.3359 | 4.6683 | 0 | 2.8528 | 0 | 0 | 0.0042842 | 0.11327 | 1.1074 | 0 | 87.082 | FY32 | 0.85098 | 0.04031 | 5.8823 | 2.8528 | 1.1669 | 0 | 0.052943 | 1.0067 | 0.14941 | 8.8119 | 20.8143 | FY32 | 78.3359 | 4.6683 | 0 | 2.8528 | 2.6375 | 0 | 0.00010654 | 0.40336 | 1.1074 | 8.8119 | 98.8172 | FY32 | 0.024845 | 0 | 0 | 749.9579 | 2.6375 | 0 | 0.37794 | 0.0044382 | 0.047528 | 8.8119 | 761.862 | FY32 | 78.3359 | 4.6683 | 0 | 0 | 2.6375 | 0 | 0.031477 | 0.40336 | 1.1074 | 0 | 87.184 | FY32 | 39.7131 | 1.6861 | 1.5344 | 350.9966 | 2.804 | 101.703 | 0.19149 | 2.0077 | 0.14572 | 7.7518 | 508.5339
FY33 | 102.8222 | 12.1224 | 8.5097 | 804.2913 | 60.4094 | 160.1517 | 0.70091 | 4.1934 | 2.6178 | 9.5889 | 1165.4077 | FY33 | 0.11148 | 0 | 8.5097 | 3.4042 | 0 | 0 | 0.0094572 | 1.3739 | 0.38877 | 9.5889 | 23.3865 | FY33 | 102.8222 | 12.1224 | 0 | 3.4042 | 0 | 0 | 0.00016781 | 0.19136 | 2.6178 | 9.5889 | 130.747 | FY33 | 0 | 0 | 0 | 804.2913 | 0 | 0 | 0.18509 | 0.00624 | 0.091804 | 9.5889 | 814.1633 | FY33 | 102.8222 | 12.1224 | 0 | 3.4042 | 0 | 0 | 0.0094572 | 0.19136 | 2.6178 | 0 | 121.1674 | FY33 | 2.1007 | 0.22868 | 8.5097 | 3.4042 | 1.3106 | 0 | 0.092078 | 1.3739 | 0.90922 | 9.5889 | 27.518 | FY33 | 102.8222 | 12.1224 | 0 | 3.4042 | 2.9598 | 0 | 0.00016781 | 0.60636 | 2.6178 | 9.5889 | 134.1218 | FY33 | 0.11148 | 0 | 0 | 804.2913 | 2.9598 | 0 | 0.52316 | 0.00624 | 0.38877 | 9.5889 | 817.8697 | FY33 | 102.8222 | 12.1224 | 0 | 3.5099e-06 | 2.9598 | 0 | 0.059364 | 0.60636 | 2.6178 | 0 | 121.1879 | FY33 | 55.8144 | 5.1131 | 2.4574 | 372.7399 | 3.1232 | 108.4178 | 0.27952 | 2.5505 | 0.84206 | 8.4325 | 559.7704
FY34 | 128.561 | 24.0326 | 11.5599 | 811.4391 | 65.578 | 164.9534 | 0.97181 | 4.8807 | 4.4532 | 10.4107 | 1226.8406 | FY34 | 0.24279 | 0.032951 | 11.5599 | 3.306 | 0 | 0 | 0.039838 | 1.6601 | 1.1562 | 10.4107 | 28.4085 | FY34 | 128.561 | 24.0326 | 0 | 3.306 | 0 | 0 | 0.00027133 | 0.25861 | 4.4532 | 10.4107 | 171.0225 | FY34 | 0.0034747 | 0 | 0 | 811.4391 | 0 | 0 | 0.30953 | 0.007893 | 0.56921 | 10.4107 | 822.74 | FY34 | 128.561 | 24.0326 | 0 | 3.306 | 0 | 0 | 0.039838 | 0.25861 | 4.4532 | 0 | 160.6513 | FY34 | 4.1473 | 0.51186 | 11.5599 | 3.306 | 1.4927 | 0 | 0.17967 | 1.6601 | 1.974 | 10.4107 | 35.2423 | FY34 | 128.561 | 24.0326 | 0 | 3.306 | 3.3409 | 0 | 0.00027133 | 0.76544 | 4.4532 | 10.4107 | 174.8703 | FY34 | 0.24279 | 0.032951 | 0 | 811.4391 | 3.3409 | 0 | 0.74854 | 0.007893 | 1.1562 | 10.4107 | 827.3791 | FY34 | 128.561 | 24.0326 | 0 | 0.00047702 | 3.3409 | 0 | 0.1307 | 0.76544 | 4.4532 | 0 | 161.2844 | FY34 | 72.4351 | 11.3272 | 3.4857 | 375.4457 | 3.5519 | 111.8572 | 0.43075 | 2.984 | 1.7952 | 9.1593 | 592.4721
FY35 | 152.1207 | 44.9832 | 14.3969 | 812.1113 | 79.0726 | 170.2421 | 1.0624 | 5.8172 | 6.9476 | 11.3088 | 1298.0628 | FY35 | 0.39122 | 0.16867 | 14.3969 | 3.3241 | 0 | 0 | 0.021712 | 2.0516 | 2.2863 | 11.3088 | 33.9493 | FY35 | 152.1207 | 44.9832 | 0 | 3.3241 | 0 | 0 | 0.00035474 | 0.36065 | 6.9476 | 11.3088 | 219.0454 | FY35 | 0.017592 | 0 | 0 | 812.1113 | 0 | 0 | 0.30957 | 0.010271 | 1.3794 | 11.3088 | 825.1369 | FY35 | 152.1207 | 44.9832 | 0 | 3.3241 | 0 | 0 | 0.021712 | 0.36065 | 6.9476 | 0 | 207.758 | FY35 | 7.5917 | 1.3845 | 14.3969 | 3.3241 | 2.1118 | 0 | 0.16553 | 2.0516 | 3.4636 | 11.3088 | 45.7986 | FY35 | 152.1207 | 44.9832 | 0 | 3.3241 | 4.7734 | 0 | 0.00035474 | 0.98732 | 6.9476 | 11.3088 | 224.4455 | FY35 | 0.39122 | 0.16867 | 0 | 812.1113 | 4.7734 | 0 | 0.80691 | 0.010271 | 2.2863 | 11.3088 | 831.8568 | FY35 | 152.1207 | 44.9832 | 0 | 0.028981 | 4.7734 | 0 | 0.11267 | 0.98732 | 6.9476 | 0 | 209.9539 | FY35 | 87.2318 | 22.9906 | 4.6463 | 367.6189 | 5.042 | 115.4315 | 0.44146 | 3.5556 | 3.1278 | 9.9511 | 620.0372
FY36 | 208.9329 | 73.9475 | 17.4175 | 820.9535 | 110.279 | 190.3546 | 1.1495 | 7.3061 | 12.9693 | 12.2453 | 1455.5553 | FY36 | 1.7662 | 0.48153 | 17.4175 | 5.4326 | 0 | 0.032776 | 0.018765 | 2.707 | 4.936 | 12.2453 | 45.0377 | FY36 | 208.9329 | 73.9475 | 0 | 5.4326 | 0 | 0.032776 | 0.00046329 | 0.57837 | 12.9693 | 12.2453 | 314.1393 | FY36 | 0.10143 | 0.028146 | 0 | 820.9535 | 0 | 0.032776 | 0.31075 | 0.014294 | 3.3924 | 12.2453 | 837.0786 | FY36 | 208.9329 | 73.9475 | 0 | 5.4326 | 0 | 0.032776 | 0.018765 | 0.57837 | 12.9693 | 0 | 301.9123 | FY36 | 18.4554 | 3.6505 | 17.4175 | 5.4326 | 5.0589 | 0.032776 | 0.15711 | 2.707 | 6.9917 | 12.2453 | 72.1488 | FY36 | 208.9329 | 73.9475 | 0 | 5.4326 | 10.6109 | 0.032776 | 0.00046329 | 1.4046 | 12.9693 | 12.2453 | 325.5765 | FY36 | 1.7662 | 0.48153 | 0 | 820.9535 | 10.6109 | 0.032776 | 0.86113 | 0.014294 | 4.936 | 12.2453 | 851.9017 | FY36 | 208.9329 | 73.9475 | 0 | 0.026879 | 10.6109 | 0.032776 | 0.1031 | 1.4046 | 12.9693 | 0 | 308.0281 | FY36 | 125.5559 | 39.1433 | 6.2971 | 381.5097 | 10.5656 | 132.2956 | 0.45001 | 4.457 | 6.1406 | 10.7813 | 717.1962
FY37 | 184.379 | 99.5823 | 12.2169 | 746.8801 | 122.5923 | 166.0235 | 1.4581 | 7.7481 | 17.3791 | 13.0454 | 1371.3047 | FY37 | 1.101 | 0.87608 | 12.2169 | 1.3826 | 0 | 0 | 0.033762 | 2.7478 | 7.4932 | 13.0454 | 38.8967 | FY37 | 184.379 | 99.5823 | 0 | 1.3826 | 0 | 0 | 0.00065563 | 0.55263 | 17.3791 | 13.0454 | 316.3216 | FY37 | 0.10962 | 0.14119 | 0 | 746.8801 | 0 | 0 | 0.43445 | 0.016874 | 5.4629 | 13.0454 | 766.0905 | FY37 | 184.379 | 99.5823 | 0 | 1.3826 | 0 | 0 | 0.033762 | 0.55263 | 17.3791 | 0 | 303.3093 | FY37 | 12.8905 | 6.6667 | 12.2169 | 1.3826 | 6.2758 | 0 | 0.23555 | 2.7478 | 10.1552 | 13.0454 | 65.6165 | FY37 | 184.379 | 99.5823 | 0 | 1.3826 | 13.133 | 0 | 0.00065563 | 1.3897 | 17.3791 | 13.0454 | 330.2916 | FY37 | 1.101 | 0.87608 | 0 | 746.8801 | 13.133 | 0 | 1.1105 | 0.016874 | 7.4932 | 13.0454 | 783.6561 | FY37 | 184.379 | 99.5823 | 0 | 0 | 13.133 | 0 | 0.16205 | 1.3897 | 17.3791 | 0 | 316.025 | FY37 | 106.1937 | 55.0849 | 3.8257 | 331.1975 | 12.1895 | 110.8559 | 0.60828 | 4.6033 | 8.8608 | 11.4733 | 644.8928
FY38 | 251.2654 | 157.0521 | 27.4287 | 799.0235 | 189.6297 | 186.8114 | 1.9768 | 10.3894 | 24.7523 | 14.154 | 1662.4831 | FY38 | 3.0675 | 2.708 | 27.4287 | 2.7348 | 0 | 0.01004 | 0.085667 | 3.8345 | 11.59 | 14.154 | 65.6131 | FY38 | 251.2654 | 157.0521 | 0 | 2.7348 | 0 | 0.01004 | 0.0010211 | 0.97862 | 24.7523 | 14.154 | 450.9482 | FY38 | 0.26522 | 0.37632 | 0 | 799.0235 | 0 | 0.01004 | 0.67076 | 0.025283 | 8.6248 | 14.154 | 823.1498 | FY38 | 251.2654 | 157.0521 | 0 | 2.7348 | 0 | 0.01004 | 0.085667 | 0.97862 | 24.7523 | 0 | 436.8788 | FY38 | 25.2538 | 16.9784 | 27.4287 | 2.7348 | 19.1175 | 0.01004 | 0.40207 | 3.8345 | 15.2148 | 14.154 | 125.1286 | FY38 | 251.2654 | 157.0521 | 0 | 2.7348 | 33.3953 | 0.01004 | 0.0010211 | 2.1327 | 24.7523 | 14.154 | 485.4976 | FY38 | 3.0675 | 2.708 | 0 | 799.0235 | 33.3953 | 0.01004 | 1.526 | 0.025283 | 11.59 | 14.154 | 865.4995 | FY38 | 251.2654 | 157.0521 | 0 | 0.0017809 | 33.3953 | 0.01004 | 0.29635 | 2.1327 | 24.7523 | 0 | 468.9059 | FY38 | 151.443 | 96.5059 | 11.0575 | 366.4882 | 28.5508 | 128.1747 | 0.88648 | 6.0753 | 13.1724 | 12.4713 | 814.8256
FY39 | 324.0806 | 205.871 | 31.9243 | 841.4929 | 277.1931 | 207.9116 | 1.9779 | 15.0407 | 34.0318 | 15.04 | 1954.5638 | FY39 | 7.1833 | 6.8137 | 31.9243 | 5.1177 | 0.0004284 | 0.18743 | 0.056752 | 5.1197 | 16.9014 | 15.04 | 88.3447 | FY39 | 324.0806 | 205.871 | 0 | 5.1177 | 0.0004284 | 0.18743 | 0.0011164 | 1.6154 | 34.0318 | 15.04 | 585.9454 | FY39 | 0.4267 | 0.76079 | 0 | 841.4929 | 0.0004284 | 0.18743 | 0.61667 | 0.042069 | 12.9566 | 15.04 | 871.5235 | FY39 | 324.0806 | 205.871 | 0 | 5.1177 | 0.0004284 | 0.18743 | 0.056752 | 1.6154 | 34.0318 | 0 | 570.9611 | FY39 | 45.1863 | 30.2895 | 31.9243 | 5.1177 | 46.4183 | 0.18743 | 0.34511 | 5.1197 | 21.6452 | 15.04 | 201.2736 | FY39 | 324.0806 | 205.871 | 0 | 5.1177 | 70.2748 | 0.18743 | 0.0011164 | 3.0901 | 34.0318 | 15.04 | 657.6945 | FY39 | 7.1833 | 6.8137 | 0 | 841.4929 | 70.2748 | 0.18743 | 1.5167 | 0.042069 | 16.9014 | 15.04 | 959.4523 | FY39 | 324.0806 | 205.871 | 0 | 0.01497 | 70.2748 | 0.18743 | 0.24252 | 3.0901 | 34.0318 | 0 | 637.7932 | FY39 | 202.9605 | 133.0295 | 13.7463 | 395.1176 | 57.6627 | 145.7804 | 0.84828 | 7.6999 | 18.5819 | 13.2405 | 988.6676
FY40 | [10 empty] | 1954.5638 | FY40 | [10 empty] | 88.3447 | FY40 | [10 empty] | 585.9454 | FY40 | [10 empty] | 871.5235 | FY40 | [10 empty] | 570.9611 | FY40 | [10 empty] | 201.2736 | FY40 | [10 empty] | 657.6945 | FY40 | [10 empty] | 959.4523 | FY40 | [10 empty] | 637.7932 | FY40 | [10 empty] | 988.6676
FY41 | [10 empty] | 1954.5638 | FY41 | [10 empty] | 88.3447 | FY41 | [10 empty] | 585.9454 | FY41 | [10 empty] | 871.5235 | FY41 | [10 empty] | 570.9611 | FY41 | [10 empty] | 201.2736 | FY41 | [10 empty] | 657.6945 | FY41 | [10 empty] | 959.4523 | FY41 | [10 empty] | 637.7932 | FY41 | [10 empty] | 988.6676
FY42 | [10 empty] | 1954.5638 | FY42 | [10 empty] | 88.3447 | FY42 | [10 empty] | 585.9454 | FY42 | [10 empty] | 871.5235 | FY42 | [10 empty] | 570.9611 | FY42 | [10 empty] | 201.2736 | FY42 | [10 empty] | 657.6945 | FY42 | [10 empty] | 959.4523 | FY42 | [10 empty] | 637.7932 | FY42 | [10 empty] | 988.6676
FY43 | [10 empty] | 1954.5638 | FY43 | [10 empty] | 88.3447 | FY43 | [10 empty] | 585.9454 | FY43 | [10 empty] | 871.5235 | FY43 | [10 empty] | 570.9611 | FY43 | [10 empty] | 201.2736 | FY43 | [10 empty] | 657.6945 | FY43 | [10 empty] | 959.4523 | FY43 | [10 empty] | 637.7932 | FY43 | [10 empty] | 988.6676
FY44 | [10 empty] | 1954.5638 | FY44 | [10 empty] | 88.3447 | FY44 | [10 empty] | 585.9454 | FY44 | [10 empty] | 871.5235 | FY44 | [10 empty] | 570.9611 | FY44 | [10 empty] | 201.2736 | FY44 | [10 empty] | 657.6945 | FY44 | [10 empty] | 959.4523 | FY44 | [10 empty] | 637.7932 | FY44 | [10 empty] | 988.6676
FY45 | [10 empty] | 1954.5638 | FY45 | [10 empty] | 88.3447 | FY45 | [10 empty] | 585.9454 | FY45 | [10 empty] | 871.5235 | FY45 | [10 empty] | 570.9611 | FY45 | [10 empty] | 201.2736 | FY45 | [10 empty] | 657.6945 | FY45 | [10 empty] | 959.4523 | FY45 | [10 empty] | 637.7932 | FY45 | [10 empty] | 988.6676
FY46 | [10 empty] | 1954.5638 | FY46 | [10 empty] | 88.3447 | FY46 | [10 empty] | 585.9454 | FY46 | [10 empty] | 871.5235 | FY46 | [10 empty] | 570.9611 | FY46 | [10 empty] | 201.2736 | FY46 | [10 empty] | 657.6945 | FY46 | [10 empty] | 959.4523 | FY46 | [10 empty] | 637.7932 | FY46 | [10 empty] | 988.6676
FY47 | [10 empty] | 1954.5638 | FY47 | [10 empty] | 88.3447 | FY47 | [10 empty] | 585.9454 | FY47 | [10 empty] | 871.5235 | FY47 | [10 empty] | 570.9611 | FY47 | [10 empty] | 201.2736 | FY47 | [10 empty] | 657.6945 | FY47 | [10 empty] | 959.4523 | FY47 | [10 empty] | 637.7932 | FY47 | [10 empty] | 988.6676
FY48 | [10 empty] | 1954.5638 | FY48 | [10 empty] | 88.3447 | FY48 | [10 empty] | 585.9454 | FY48 | [10 empty] | 871.5235 | FY48 | [10 empty] | 570.9611 | FY48 | [10 empty] | 201.2736 | FY48 | [10 empty] | 657.6945 | FY48 | [10 empty] | 959.4523 | FY48 | [10 empty] | 637.7932 | FY48 | [10 empty] | 988.6676
FY49 | [10 empty] | 1954.5638 | FY49 | [10 empty] | 88.3447 | FY49 | [10 empty] | 585.9454 | FY49 | [10 empty] | 871.5235 | FY49 | [10 empty] | 570.9611 | FY49 | [10 empty] | 201.2736 | FY49 | [10 empty] | 657.6945 | FY49 | [10 empty] | 959.4523 | FY49 | [10 empty] | 637.7932 | FY49 | [10 empty] | 988.6676
FY50 | [10 empty] | 1954.5638 | FY50 | [10 empty] | 88.3447 | FY50 | [10 empty] | 585.9454 | FY50 | [10 empty] | 871.5235 | FY50 | [10 empty] | 570.9611 | FY50 | [10 empty] | 201.2736 | FY50 | [10 empty] | 657.6945 | FY50 | [10 empty] | 959.4523 | FY50 | [10 empty] | 637.7932 | FY50 | [10 empty] | 988.6676
FY51 | [10 empty] | 1954.5638 | FY51 | [10 empty] | 88.3447 | FY51 | [10 empty] | 585.9454 | FY51 | [10 empty] | 871.5235 | FY51 | [10 empty] | 570.9611 | FY51 | [10 empty] | 201.2736 | FY51 | [10 empty] | 657.6945 | FY51 | [10 empty] | 959.4523 | FY51 | [10 empty] | 637.7932 | FY51 | [10 empty] | 988.6676
FY52 | [10 empty] | 1954.5638 | FY52 | [10 empty] | 88.3447 | FY52 | [10 empty] | 585.9454 | FY52 | [10 empty] | 871.5235 | FY52 | [10 empty] | 570.9611 | FY52 | [10 empty] | 201.2736 | FY52 | [10 empty] | 657.6945 | FY52 | [10 empty] | 959.4523 | FY52 | [10 empty] | 637.7932 | FY52 | [10 empty] | 988.6676
FY53 | [10 empty] | 1954.5638 | FY53 | [10 empty] | 88.3447 | FY53 | [10 empty] | 585.9454 | FY53 | [10 empty] | 871.5235 | FY53 | [10 empty] | 570.9611 | FY53 | [10 empty] | 201.2736 | FY53 | [10 empty] | 657.6945 | FY53 | [10 empty] | 959.4523 | FY53 | [10 empty] | 637.7932 | FY53 | [10 empty] | 988.6676
FY54 | [10 empty] | 1954.5638 | FY54 | [10 empty] | 88.3447 | FY54 | [10 empty] | 585.9454 | FY54 | [10 empty] | 871.5235 | FY54 | [10 empty] | 570.9611 | FY54 | [10 empty] | 201.2736 | FY54 | [10 empty] | 657.6945 | FY54 | [10 empty] | 959.4523 | FY54 | [10 empty] | 637.7932 | FY54 | [10 empty] | 988.6676

## 2.2.4 SupplyRisk$ Low PoF
Option 1 - Do Nothing / Base Case | [11 empty] | Option 2 - 1A New PHS ZSS + Four new feeders | [11 empty] | Option 3 - 2A PHM 3rd Tx + Switchroom + Three new feeders + OFR12 New Feeder | [11 empty] | Option 4 - 3A OFR 3rd Tx + Switchroom + Three new feeders + OFR12 New Feeder | [11 empty] | Option 5 - 4A LLG 2nd Tx + Switchroom + Three new feeders + OFR12 New Feeder | [11 empty] | Option 6 - 1B New PHS ZSS + Three new feeders | [11 empty] | Option 7 - 2B PHM 3rd Tx + Switchroom + Two new feeders + OFR12 New Feeder | [11 empty] | Option 8 - 3B OFR 3rd Tx + Switchroom + Two new feeders + OFR12 New Feeder | [11 empty] | Option 9 - 4B LLG 2nd Tx + Switchroom + Two new feeders + OFR12 New Feeder | [11 empty] | Option 10 - 5 Non-Network
| Total Supply Risk $M by Asset and Year | [11 empty] | Total Supply Risk $M by Asset and Year | [11 empty] | Total Supply Risk $M by Asset and Year | [11 empty] | Total Supply Risk $M by Asset and Year | [11 empty] | Total Supply Risk $M by Asset and Year | [11 empty] | Total Supply Risk $M by Asset and Year | [11 empty] | Total Supply Risk $M by Asset and Year | [11 empty] | Total Supply Risk $M by Asset and Year | [11 empty] | Total Supply Risk $M by Asset and Year | [11 empty] | Total Supply Risk $M by Asset and Year
Source: | E@R CLN22 Feeder V2.7 POE10.xlsx¦Output for AusNet''s NPV model'!$B$5:$P$5 | E@R CLN23 Feeder V2.7 POE10.xlsx¦Output for AusNet''s NPV model'!$B$5:$P$5 | E@R OFR21 Feeder V2.7 POE10.xlsx¦Output for AusNet''s NPV model'!$B$5:$P$5 | E@R PHM21 Feeder V2.7 POE10.xlsx¦Output for AusNet''s NPV model'!$B$5:$P$5 | E@R PHM22 Feeder V2.7 POE10.xlsx¦Output for AusNet''s NPV model'!$B$5:$P$5 | E@R OFR14 Feeder V2.7 POE10.xlsx¦Output for AusNet''s NPV model'!$B$5:$P$5 | ZSS EaR PHM V2.3 POE10 Low PoF.xlsx¦Output for AusNet''s NPV model'!$B$5:$P$5 | ZSS EaR OFR V2.3 POE10 Low PoF.xlsx¦Output for AusNet''s NPV model'!$B$5:$P$5 | ZSS EaR CLN V2.3 POE10 Low PoF.xlsx¦Output for AusNet''s NPV model'!$B$5:$P$5 | ZSS EaR LLG V2.3 POE10 Low PoF.xlsx¦Output for AusNet''s NPV model'!$B$5:$P$5 |  |  | E@R CLN22 Feeder V2.7 POE10.xlsx¦Output for AusNet''s NPV model'!$B$10:$P$10 | E@R CLN23 Feeder V2.7 POE10.xlsx¦Output for AusNet''s NPV model'!$B$10:$P$10 | E@R OFR21 Feeder V2.7 POE10.xlsx¦Output for AusNet''s NPV model'!$B$10:$P$10 | E@R PHM21 Feeder V2.7 POE10.xlsx¦Output for AusNet''s NPV model'!$B$10:$P$10 | E@R PHM22 Feeder V2.7 POE10.xlsx¦Output for AusNet''s NPV model'!$B$10:$P$10 | E@R OFR14 Feeder V2.7 POE10.xlsx¦Output for AusNet''s NPV model'!$B$10:$P$10 | ZSS EaR PHM V2.3 POE10 Low PoF.xlsx¦Output for AusNet''s NPV model'!$B$10:$P$10 | ZSS EaR OFR V2.3 POE10 Low PoF.xlsx¦Output for AusNet''s NPV model'!$B$10:$P$10 | ZSS EaR CLN V2.3 POE10 Low PoF.xlsx¦Output for AusNet''s NPV model'!$B$10:$P$10 | ZSS EaR LLG V2.3 POE10 Low PoF.xlsx¦Output for AusNet''s NPV model'!$B$10:$P$10 |  |  | E@R CLN22 Feeder V2.7 POE10.xlsx¦Output for AusNet''s NPV model'!$B$13:$P$13 | E@R CLN23 Feeder V2.7 POE10.xlsx¦Output for AusNet''s NPV model'!$B$13:$P$13 | E@R OFR21 Feeder V2.7 POE10.xlsx¦Output for AusNet''s NPV model'!$B$13:$P$13 | E@R PHM21 Feeder V2.7 POE10.xlsx¦Output for AusNet''s NPV model'!$B$13:$P$13 | E@R PHM22 Feeder V2.7 POE10.xlsx¦Output for AusNet''s NPV model'!$B$13:$P$13 | E@R OFR14 Feeder V2.7 POE10.xlsx¦Output for AusNet''s NPV model'!$B$13:$P$13 | ZSS EaR PHM V2.3 POE10 Low PoF.xlsx¦Output for AusNet''s NPV model'!$B$13:$P$13 | ZSS EaR OFR V2.3 POE10 Low PoF.xlsx¦Output for AusNet''s NPV model'!B$13:$P$13 | ZSS EaR CLN V2.3 POE10 Low PoF.xlsx¦Output for AusNet''s NPV model'!B$13:$P$13 | ZSS EaR LLG V2.3 POE10 Low PoF.xlsx¦Output for AusNet''s NPV model'!B$13:$P$13 |  |  | E@R CLN22 Feeder V2.7 POE10.xlsx¦Output for AusNet''s NPV model'!$B$16:$P$16 | E@R CLN23 Feeder V2.7 POE10.xlsx¦Output for AusNet''s NPV model'!$B$16:$P$16 | E@R OFR21 Feeder V2.7 POE10.xlsx¦Output for AusNet''s NPV model'!$B$16:$P$16 | E@R PHM21 Feeder V2.7 POE10.xlsx¦Output for AusNet''s NPV model'!$B$16:$P$16 | E@R PHM22 Feeder V2.7 POE10.xlsx¦Output for AusNet''s NPV model'!$B$16:$P$16 | E@R OFR14 Feeder V2.7 POE10.xlsx¦Output for AusNet''s NPV model'!$B$16:$P$16 | ZSS EaR PHM V2.3 POE10 Low PoF.xlsx¦Output for AusNet''s NPV model'!$B$16:$P$16 | ZSS EaR OFR V2.3 POE10 Low PoF.xlsx¦Output for AusNet''s NPV model'!$B$16:$P$16 | ZSS EaR CLN V2.3 POE10 Low PoF.xlsx¦Output for AusNet''s NPV model'!$B$16:$P$16 | ZSS EaR LLG V2.3 POE10 Low PoF.xlsx¦Output for AusNet''s NPV model'!$B$16:$P$16 |  |  | E@R CLN22 Feeder V2.7 POE10.xlsx¦Output for AusNet''s NPV model'!$B$19:$P$19 | E@R CLN23 Feeder V2.7 POE10.xlsx¦Output for AusNet''s NPV model'!$B$19:$P$19 | E@R OFR21 Feeder V2.7 POE10.xlsx¦Output for AusNet''s NPV model'!$B$19:$P$19 | E@R PHM21 Feeder V2.7 POE10.xlsx¦Output for AusNet''s NPV model'!$B$19:$P$19 | E@R PHM22 Feeder V2.7 POE10.xlsx¦Output for AusNet''s NPV model'!$B$19:$P$19 | E@R OFR14 Feeder V2.7 POE10.xlsx¦Output for AusNet''s NPV model'!$B$19:$P$19 | ZSS EaR PHM V2.3 POE10 Low PoF.xlsx¦Output for AusNet''s NPV model'!$B$19:$P$19 | ZSS EaR OFR V2.3 POE10 Low PoF.xlsx¦Output for AusNet''s NPV model'!$B$19:$P$19 | ZSS EaR CLN V2.3 POE10 Low PoF.xlsx¦Output for AusNet''s NPV model'!$B$19:$P$19 | ZSS EaR LLG V2.3 POE10 Low PoF.xlsx¦Output for AusNet''s NPV model'!$B$19:$P$19 |  |  | E@R CLN22 Feeder V2.7 POE50.xlsx¦Output for AusNet''s NPV model'!$B$10:$P$10 | E@R CLN23 Feeder V2.7 POE50.xlsx¦Output for AusNet''s NPV model'!$B$10:$P$10 | E@R OFR21 Feeder V2.7 POE50.xlsx¦Output for AusNet''s NPV model'!$B$10:$P$10 | E@R PHM21 Feeder V2.7 POE50.xlsx¦Output for AusNet''s NPV model'!$B$10:$P$10 | E@R PHM22 Feeder V2.7 POE50.xlsx¦Output for AusNet''s NPV model'!$B$10:$P$10 | E@R OFR14 Feeder V2.7 POE50.xlsx¦Output for AusNet''s NPV model'!$B$10:$P$10 | ZSS EaR PHM V2.3 POE50 Low PoF.xlsx¦Output for AusNet''s NPV model'!$B$10:$P$10 | ZSS EaR OFR V2.3 POE50 Low PoF.xlsx¦Output for AusNet''s NPV model'!$B$10:$P$10 | ZSS EaR CLN V2.3 POE50 Low PoF.xlsx¦Output for AusNet''s NPV model'!$B$10:$P$10 | ZSS EaR LLG V2.3 POE50 Low PoF.xlsx¦Output for AusNet''s NPV model'!$B$10:$P$10 |  |  | E@R CLN22 Feeder V2.7 POE50.xlsx¦Output for AusNet''s NPV model'!$B$13:$P$13 | E@R CLN23 Feeder V2.7 POE50.xlsx¦Output for AusNet''s NPV model'!$B$13:$P$13 | E@R OFR21 Feeder V2.7 POE50.xlsx¦Output for AusNet''s NPV model'!$B$13:$P$13 | E@R PHM21 Feeder V2.7 POE50.xlsx¦Output for AusNet''s NPV model'!$B$13:$P$13 | E@R PHM22 Feeder V2.7 POE50.xlsx¦Output for AusNet''s NPV model'!$B$13:$P$13 | E@R OFR14 Feeder V2.7 POE50.xlsx¦Output for AusNet''s NPV model'!$B$13:$P$13 | ZSS EaR PHM V2.3 POE50 Low PoF.xlsx¦Output for AusNet''s NPV model'!$B$13:$P$13 | ZSS EaR OFR V2.3 POE50 Low PoF.xlsx¦Output for AusNet''s NPV model'!$B$13:$P$13 | ZSS EaR CLN V2.3 POE50 Low PoF.xlsx¦Output for AusNet''s NPV model'!$B$13:$P$13 | ZSS EaR LLG V2.3 POE50 Low PoF.xlsx¦Output for AusNet''s NPV model'!$B$13:$P$13 |  |  | E@R CLN22 Feeder V2.7 POE50.xlsx¦Output for AusNet''s NPV model'!$B$16:$P$16 | E@R CLN23 Feeder V2.7 POE50.xlsx¦Output for AusNet''s NPV model'!$B$16:$P$16 | E@R OFR21 Feeder V2.7 POE50.xlsx¦Output for AusNet''s NPV model'!$B$16:$P$16 | E@R PHM21 Feeder V2.7 POE50.xlsx¦Output for AusNet''s NPV model'!$B$16:$P$16 | E@R PHM22 Feeder V2.7 POE50.xlsx¦Output for AusNet''s NPV model'!$B$16:$P$16 | E@R OFR14 Feeder V2.7 POE50.xlsx¦Output for AusNet''s NPV model'!$B$16:$P$16 | ZSS EaR PHM V2.3 POE50 Low PoF.xlsx¦Output for AusNet''s NPV model'!$B$16:$P$16 | ZSS EaR OFR V2.3 POE50 Low PoF.xlsx¦Output for AusNet''s NPV model'!$B$16:$P$16 | ZSS EaR CLN V2.3 POE50 Low PoF.xlsx¦Output for AusNet''s NPV model'!$B$16:$P$16 | ZSS EaR LLG V2.3 POE10 Low PoF.xlsx¦Output for AusNet''s NPV model'!$B$16:$P$16 |  |  | E@R CLN22 Feeder V2.7 POE50.xlsx¦Output for AusNet''s NPV model'!$B$19:$P$19 | E@R CLN23 Feeder V2.7 POE50.xlsx¦Output for AusNet''s NPV model'!$B$19:$P$19 | E@R OFR21 Feeder V2.7 POE50.xlsx¦Output for AusNet''s NPV model'!$B$19:$P$19 | E@R PHM21 Feeder V2.7 POE50.xlsx¦Output for AusNet''s NPV model'!$B$19:$P$19 | E@R PHM22 Feeder V2.7 POE50.xlsx¦Output for AusNet''s NPV model'!$B$19:$P$19 | E@R OFR14 Feeder V2.7 POE50.xlsx¦Output for AusNet''s NPV model'!$B$19:$P$19 | ZSS EaR PHM V2.3 POE50 Low PoF.xlsx¦Output for AusNet''s NPV model'!$B$19:$P$19 | ZSS EaR OFR V2.3 POE50 Low PoF.xlsx¦Output for AusNet''s NPV model'!$B$19:$P$19 | ZSS EaR CLN V2.3 POE50 Low PoF.xlsx¦Output for AusNet''s NPV model'!$B$19:$P$19 | ZSS EaR LLG V2.3 POE10 Low PoF.xlsx¦Output for AusNet''s NPV model'!$B$19:$P$19 |  |  | E@R CLN22 Feeder V2.7 POE10.xlsx¦Output for AusNet''s NPV model'!$B$22:$P$22 | E@R CLN23 Feeder V2.7 POE10.xlsx¦Output for AusNet''s NPV model'!$B$22:$P$22 | E@R OFR21 Feeder V2.7 POE10.xlsx¦Output for AusNet''s NPV model'!$B$22:$P$22 | E@R PHM21 Feeder V2.7 POE10.xlsx¦Output for AusNet''s NPV model'!$B$22:$P$22 | E@R PHM22 Feeder V2.7 POE10.xlsx¦Output for AusNet''s NPV model'!$B$22:$P$22 | E@R OFR14 Feeder V2.7 POE10.xlsx¦Output for AusNet''s NPV model'!$B$22:$P$22 | ZSS EaR PHM V2.3 POE10 Low PoF.xlsx¦Output for AusNet''s NPV model'!$B$22:$P$22 | ZSS EaR OFR V2.3 POE10 Low PoF.xlsx¦Output for AusNet''s NPV model'!$B$22:$P$22 | ZSS EaR CLN V2.3 POE10 Low PoF.xlsx¦Output for AusNet''s NPV model'!$B$22:$P$22 | ZSS EaR LLG V2.3 POE10 Low PoF.xlsx¦Output for AusNet''s NPV model'!$B$22:$P$22
Year | CLN22 | CLN23 | OFR21 | PHM21 | PHM22 | OFR14 | PHM | OFR | CLN | LLG | Opt 1 Total | Year | CLN22 | CLN23 | OFR21 | PHM21 | PHM22 | OFR14 | PHM | OFR | CLN | LLG | Opt 2 Total | Year | CLN22 | CLN23 | OFR21 | PHM21 | PHM22 | OFR14 | PHM | OFR | CLN | LLG | Opt 3 Total | Year | CLN22 | CLN23 | OFR21 | PHM21 | PHM22 | OFR14 | PHM | OFR | CLN | LLG | Opt 4 Total | Year | CLN22 | CLN23 | OFR21 | PHM21 | PHM22 | OFR14 | PHM | OFR | CLN | LLG | Opt 5 Total | Year | CLN22 | CLN23 | OFR21 | PHM21 | PHM22 | OFR14 | PHM | OFR | CLN | LLG | Opt 6 Total | Year | CLN22 | CLN23 | OFR21 | PHM21 | PHM22 | OFR14 | PHM | OFR | CLN | LLG | Opt 7 Total | Year | CLN22 | CLN23 | OFR21 | PHM21 | PHM22 | OFR14 | PHM | OFR | CLN | LLG | Opt 8 Total | Year | CLN22 | CLN23 | OFR21 | PHM21 | PHM22 | OFR14 | PHM | OFR | CLN | LLG | Opt 9 Total | Year | CLN22 | CLN23 | OFR21 | PHM21 | PHM22 | OFR14 | PHM | OFR | CLN | LLG | Opt 10 Total
FY25 | 0 | 0 | 9.261e-05 | 0 | 0 | 0 | 0.00021781 | 0.010523 | 0.0014458 | 1.6419 | 1.6542 | FY25 | 0 | 0 | 9.261e-05 | 0 | 0 | 0 | 0.00021781 | 0.010523 | 0.0014458 | 1.6389 | 1.6512 | FY25 | 0 | 0 | 9.261e-05 | 0 | 0 | 0 | 0.00021781 | 0.010523 | 0.0014458 | 1.6389 | 1.6512 | FY25 | 0 | 0 | 9.261e-05 | 0 | 0 | 0 | 0.00021781 | 0.010523 | 0.0014458 | 1.6389 | 1.6512 | FY25 | 0 | 0 | 9.261e-05 | 0 | 0 | 0 | 0.00021781 | 0.010523 | 0.0014458 | 1.6389 | 1.6512 | FY25 | 0 | 0 | 9.261e-05 | 0 | 0 | 0 | 0.00021781 | 0.010523 | 0.0014458 | 1.6389 | 1.6512 | FY25 | 0 | 0 | 9.261e-05 | 0 | 0 | 0 | 0.00021781 | 0.010523 | 0.0014458 | 1.6389 | 1.6512 | FY25 | 0 | 0 | 9.261e-05 | 0 | 0 | 0 | 0.00021781 | 0.010523 | 0.0014458 | 1.6389 | 1.6512 | FY25 | 0 | 0 | 9.261e-05 | 0 | 0 | 0 | 0.00021781 | 0.010523 | 0.0014458 | 1.6389 | 1.6512 | FY25 | 0 | 0 | 0 | 0 | 0 | 0 | 3.0088e-05 | 0.005076 | 0.0004797 | 1.4074 | 0
FY26 | 0.33417 | 0 | 0.016561 | 61.2197 | 0.0049505 | 0.076122 | 0.0098795 | 0.016436 | 0.00069843 | 1.8592 | 63.5377 | FY26 | 0.33417 | 0 | 0.016561 | 61.2197 | 0.0049505 | 0.076122 | 0.0098795 | 0.016436 | 0.00069843 | 1.8592 | 63.5377 | FY26 | 0.33417 | 0 | 0.016561 | 61.2197 | 0.0049505 | 0.076122 | 0.0098795 | 0.016436 | 0.00069843 | 1.8592 | 63.5377 | FY26 | 0.33417 | 0 | 0.016561 | 61.2197 | 0.0049505 | 0.076122 | 0.0098795 | 0.016436 | 0.00069843 | 1.8592 | 63.5377 | FY26 | 0.33417 | 0 | 0.016561 | 61.2197 | 0.0049505 | 0.076122 | 0.0098795 | 0.016436 | 0.00069843 | 1.8592 | 63.5377 | FY26 | 0.33417 | 0 | 0.016561 | 61.2197 | 0.0049505 | 0.076122 | 0.0098795 | 0.016436 | 0.00069843 | 1.8592 | 63.5377 | FY26 | 0.33417 | 0 | 0.016561 | 61.2197 | 0.0049505 | 0.076122 | 0.0098795 | 0.016436 | 0.00069843 | 1.8592 | 63.5377 | FY26 | 0.33417 | 0 | 0.016561 | 61.2197 | 0.0049505 | 0.076122 | 0.0098795 | 0.016436 | 0.00069843 | 1.8592 | 63.5377 | FY26 | 0.33417 | 0 | 0.016561 | 61.2197 | 0.0049505 | 0.076122 | 0.0098795 | 0.016436 | 0.00069843 | 1.8592 | 63.5377 | FY26 | 0.047751 | 0 | 0 | 4.3361 | 0 | 0 | 0.00096519 | 0.0062087 | 6.2021e-05 | 1.5989
FY27 | 1.0189 | 0 | 0.095278 | 228.821 | 1.406 | 10.7476 | 0.026377 | 0.081556 | 0.0016186 | 2.4086 | 244.6069 | FY27 | 1.0189 | 0 | 0.095278 | 228.821 | 1.406 | 10.7476 | 0.026377 | 0.081556 | 0.0016186 | 2.4086 | 244.6069 | FY27 | 1.0189 | 0 | 0.095278 | 228.821 | 1.406 | 10.7476 | 0.026377 | 0.081556 | 0.0016186 | 2.4086 | 244.6069 | FY27 | 1.0189 | 0 | 0.095278 | 228.821 | 1.406 | 10.7476 | 0.026377 | 0.081556 | 0.0016186 | 2.4086 | 244.6069 | FY27 | 1.0189 | 0 | 0.095278 | 228.821 | 1.406 | 10.7476 | 0.026377 | 0.081556 | 0.0016186 | 2.4086 | 244.6069 | FY27 | 1.0189 | 0 | 0.095278 | 228.821 | 1.406 | 10.7476 | 0.026377 | 0.081556 | 0.0016186 | 2.4086 | 244.6069 | FY27 | 1.0189 | 0 | 0.095278 | 228.821 | 1.406 | 10.7476 | 0.026377 | 0.081556 | 0.0016186 | 2.4086 | 244.6069 | FY27 | 1.0189 | 0 | 0.095278 | 228.821 | 1.406 | 10.7476 | 0.026377 | 0.081556 | 0.0016186 | 2.4086 | 244.6069 | FY27 | 1.0189 | 0 | 0.095278 | 228.821 | 1.406 | 10.7476 | 0.026377 | 0.081556 | 0.0016186 | 2.4086 | 244.6069 | FY27 | 0.1413 | 0 | 0.0056705 | 49.59 | 0.010662 | 3.6807 | 0.0036506 | 0.024039 | 0.00040294 | 2.0773
FY28 | 2.2918 | 0 | 0.13664 | 238.429 | 4.6943 | 31.6628 | 0.036055 | 0.22352 | 0.0029014 | 2.6662 | 280.1431 | FY28 | 0 | 0 | 0.13664 | 0 | 0 | 31.6628 | 5.7063e-05 | 0.22352 | 0.00022975 | 2.6662 | 34.6894 | FY28 | 2.2918 | 0 | 0 | 0 | 0 | 31.6628 | 1.9642e-06 | 0.014419 | 0.0029014 | 2.6662 | 36.6381 | FY28 | 0 | 0 | 0 | 238.429 | 0 | 31.6628 | 0.0018233 | 0.00010868 | 2.5427e-05 | 2.6662 | 272.7599 | FY28 | 2.2918 | 0 | 0 | 0 | 0 | 31.6628 | 5.7063e-05 | 0.014419 | 0.0029014 | 0 | 33.9719 | FY28 | 0 | 0 | 0.13664 | 0 | 0.022623 | 31.6628 | 0.00054664 | 0.22352 | 0.00076325 | 2.6662 | 34.7131 | FY28 | 2.2918 | 0 | 0 | 0 | 0.094159 | 31.6628 | 1.9642e-06 | 0.069509 | 0.0029014 | 2.6662 | 36.7873 | FY28 | 0 | 0 | 0 | 238.429 | 0.094159 | 31.6628 | 0.020113 | 0.00010868 | 0.00022975 | 2.6662 | 272.8726 | FY28 | 2.2918 | 0 | 0 | 0 | 0.094159 | 31.6628 | 0.00033206 | 0.069509 | 0.0029014 | 0 | 34.1215 | FY28 | 0.40168 | 0 | 0.0088494 | 54.0823 | 0.15497 | 15.9563 | 0.0053312 | 0.083654 | 0.00095146 | 2.3022
FY29 | 4.9069 | 0.00048597 | 0.19953 | 281.1681 | 12.1407 | 56.8773 | 0.047559 | 0.35995 | 0.004738 | 2.9366 | 358.6419 | FY29 | 0 | 0 | 0.19953 | 0 | 0 | 56.8773 | 8.1208e-05 | 0.35995 | 0.00067885 | 2.9366 | 60.3741 | FY29 | 4.9069 | 0.00048597 | 0 | 0 | 0 | 56.8773 | 3.2321e-06 | 0.031835 | 0.004738 | 2.9366 | 64.7579 | FY29 | 0 | 0 | 0 | 281.1681 | 0 | 56.8773 | 0.0025205 | 0.00018413 | 0.00015746 | 2.9366 | 340.9848 | FY29 | 4.9069 | 0.00048597 | 0 | 0 | 0 | 56.8773 | 8.1208e-05 | 0.031835 | 0.004738 | 0 | 61.8214 | FY29 | 0 | 0 | 0.19953 | 0 | 0.073892 | 0 | 0.00071026 | 0.031835 | 0.0015388 | 2.9366 | 3.2441 | FY29 | 4.9069 | 0.00048597 | 0 | 0 | 0.26192 | 0 | 3.2321e-06 | 0.0082169 | 0.004738 | 2.9366 | 8.1188 | FY29 | 0 | 0 | 0 | 281.1681 | 0.26192 | 0 | 0.026954 | 0.00018413 | 0.00067885 | 2.9366 | 284.3944 | FY29 | 4.9069 | 0.00048597 | 0 | 0 | 0.26192 | 0 | 0.00042871 | 0.0082169 | 0.004738 | 0 | 5.1827 | FY29 | 0.99581 | 0 | 0.015334 | 77.3143 | 0.28503 | 32.501 | 0.0073742 | 0.15191 | 0.0017839 | 2.5368
FY30 | 8.7974 | 0.11571 | 0.31946 | 334.6302 | 13.2836 | 74.2782 | 0.065252 | 0.51128 | 0.0084958 | 3.2474 | 435.257 | FY30 | 0 | 0 | 0.31946 | 0 | 0 | 0 | 0.00012583 | 0.06043 | 0.0019019 | 3.2474 | 3.6293 | FY30 | 8.7974 | 0.11571 | 0 | 0 | 0 | 0 | 5.3666e-06 | 0.0058571 | 0.0084958 | 3.2474 | 12.1748 | FY30 | 0 | 0 | 0 | 334.6302 | 0 | 0 | 0.0039464 | 0.00027782 | 0.00087514 | 3.2474 | 337.8827 | FY30 | 8.7974 | 0.11571 | 0 | 0 | 0 | 0 | 0.00012583 | 0.0058571 | 0.0084958 | 0 | 8.9276 | FY30 | 0 | 0 | 0.31946 | 0 | 0.091808 | 0 | 0.001033 | 0.06043 | 0.0033894 | 3.2474 | 3.7235 | FY30 | 8.7974 | 0.11571 | 0 | 0 | 0.29729 | 0 | 5.3666e-06 | 0.013245 | 0.0084958 | 3.2474 | 12.4795 | FY30 | 0 | 0 | 0 | 334.6302 | 0.29729 | 0 | 0.038124 | 0.00027782 | 0.0019019 | 3.2474 | 338.2152 | FY30 | 8.7974 | 0.11571 | 0 | 0 | 0.29729 | 0 | 0.00060022 | 0.013245 | 0.0084958 | 0 | 9.2328 | FY30 | 1.9456 | 0.013516 | 0.03491 | 107.1324 | 0.31588 | 44.3161 | 0.0111 | 0.23246 | 0.0036468 | 2.8088
FY31 | 16.6417 | 0.35615 | 0.52199 | 457.8876 | 14.1055 | 82.9038 | 0.097943 | 0.69852 | 0.013786 | 3.6252 | 576.8522 | FY31 | 0 | 0 | 0.52199 | 5.3527e-05 | 0 | 0 | 0.0002206 | 0.10713 | 0.0038545 | 3.6252 | 4.2585 | FY31 | 16.6417 | 0.35615 | 0 | 5.3527e-05 | 0 | 0 | 9.4732e-06 | 0.008025 | 0.013786 | 3.6252 | 20.6449 | FY31 | 0 | 0 | 0 | 457.8876 | 0 | 0 | 0.0083354 | 0.00040545 | 0.002188 | 3.6252 | 461.5237 | FY31 | 16.6417 | 0.35615 | 0 | 5.3527e-05 | 0 | 0 | 0.0002206 | 0.008025 | 0.013786 | 0 | 17.0199 | FY31 | 0.0091261 | 0 | 0.52199 | 5.3527e-05 | 0.10353 | 0 | 0.0019876 | 0.10713 | 0.006146 | 3.6252 | 4.3752 | FY31 | 16.6417 | 0.35615 | 0 | 5.3527e-05 | 0.31926 | 0 | 9.4732e-06 | 0.022797 | 0.013786 | 3.6252 | 20.9789 | FY31 | 0 | 0 | 0 | 457.8876 | 0.31926 | 0 | 0.060787 | 0.00040545 | 0.0038545 | 3.6252 | 461.8971 | FY31 | 16.6417 | 0.35615 | 0 | 0 | 0.31926 | 0 | 0.0010027 | 0.022797 | 0.013786 | 0 | 17.3546 | FY31 | 4.5985 | 0.14312 | 0.065291 | 178.9722 | 0.34228 | 50.5281 | 0.020288 | 0.34029 | 0.0063621 | 3.1414
FY32 | 26.7865 | 0.95811 | 0.78643 | 495.9347 | 15.1327 | 89.796 | 0.13515 | 0.90291 | 0.023099 | 4.0054 | 634.461 | FY32 | 0 | 0 | 0.78643 | 0.00056072 | 0 | 0 | 0.00033752 | 0.16669 | 0.0079634 | 4.0054 | 4.9674 | FY32 | 26.7865 | 0.95811 | 0 | 0.00056072 | 0 | 0 | 1.5272e-05 | 0.01109 | 0.023099 | 4.0054 | 31.7847 | FY32 | 0 | 0 | 0 | 495.9347 | 0 | 0 | 0.014167 | 0.00055995 | 0.0052276 | 4.0054 | 499.9601 | FY32 | 26.7865 | 0.95811 | 0 | 0.00056072 | 0 | 0 | 0.00033752 | 0.01109 | 0.023099 | 0 | 27.7797 | FY32 | 0.052233 | 0 | 0.78643 | 0.00056072 | 0.12035 | 0 | 0.0036162 | 0.16669 | 0.011802 | 4.0054 | 5.1471 | FY32 | 26.7865 | 0.95811 | 0 | 0.00056072 | 0.35052 | 0 | 1.5272e-05 | 0.039168 | 0.023099 | 4.0054 | 32.1633 | FY32 | 0 | 0 | 0 | 495.9347 | 0.35052 | 0 | 0.086767 | 0.00055995 | 0.0079634 | 4.0054 | 500.3859 | FY32 | 26.7865 | 0.95811 | 0 | 0 | 0.35052 | 0 | 0.0016915 | 0.039168 | 0.023099 | 0 | 28.159 | FY32 | 8.8963 | 0.38212 | 0.1097 | 181.9963 | 0.37379 | 55.3522 | 0.031216 | 0.46068 | 0.011734 | 3.4754
FY33 | 40.0426 | 3.0094 | 1.3478 | 534.1892 | 16.4822 | 95.9772 | 0.18945 | 1.1502 | 0.26109 | 4.3586 | 697.0077 | FY33 | 0 | 0 | 1.3478 | 0.0038838 | 0 | 0 | 0.00049913 | 0.25033 | 0.015149 | 4.3586 | 5.9763 | FY33 | 40.0426 | 3.0094 | 0 | 0.0038838 | 0 | 0 | 2.4712e-05 | 0.01582 | 0.26109 | 4.3586 | 47.6914 | FY33 | 0 | 0 | 0 | 534.1892 | 0 | 0 | 0.026172 | 0.00076223 | 0.010481 | 4.3586 | 538.5852 | FY33 | 40.0426 | 3.0094 | 0 | 0.0038838 | 0 | 0 | 0.00049913 | 0.01582 | 0.26109 | 0 | 43.3333 | FY33 | 0.14846 | 0.00026684 | 1.3478 | 0.0038838 | 0.14268 | 0 | 0.0077041 | 0.25033 | 0.02112 | 4.3586 | 6.2809 | FY33 | 40.0426 | 3.0094 | 0 | 0.0038838 | 0.39173 | 0 | 2.4712e-05 | 0.067659 | 0.26109 | 4.3586 | 48.135 | FY33 | 0 | 0 | 0 | 534.1892 | 0.39173 | 0 | 0.12681 | 0.00076223 | 0.015149 | 4.3586 | 539.0823 | FY33 | 40.0426 | 3.0094 | 0 | 0 | 0.39173 | 0 | 0.0036408 | 0.067659 | 0.26109 | 0 | 43.7761 | FY33 | 14.8607 | 0.9701 | 0.20617 | 190.9768 | 0.41318 | 59.6092 | 0.050619 | 0.61425 | 0.020385 | 3.7804
FY34 | 54.1546 | 7.3453 | 1.9107 | 539.4631 | 18.3115 | 99.0912 | 0.27588 | 1.3467 | 0.88242 | 4.7322 | 727.5135 | FY34 | 0.0066067 | 0 | 1.9107 | 0.014518 | 0 | 0 | 0.002412 | 0.31546 | 0.024757 | 4.7322 | 7.0066 | FY34 | 54.1546 | 7.3453 | 0 | 0.014518 | 0 | 0 | 4.09e-05 | 0.020553 | 0.88242 | 4.7322 | 67.1496 | FY34 | 0 | 0 | 0 | 539.4631 | 0 | 0 | 0.056469 | 0.00095757 | 0.017931 | 4.7322 | 544.2706 | FY34 | 54.1546 | 7.3453 | 0 | 0.014518 | 0 | 0 | 0.002412 | 0.020553 | 0.88242 | 0 | 62.4198 | FY34 | 0.29405 | 0.072968 | 1.9107 | 0.014518 | 0.18278 | 0 | 0.024866 | 0.31546 | 0.06781 | 4.7322 | 7.6153 | FY34 | 54.1546 | 7.3453 | 0 | 0.014518 | 0.46006 | 0 | 4.09e-05 | 0.092216 | 0.88242 | 4.7322 | 67.6813 | FY34 | 0.0066067 | 0 | 0 | 539.4631 | 0.46006 | 0 | 0.19511 | 0.00095757 | 0.024757 | 4.7322 | 544.8827 | FY34 | 54.1546 | 7.3453 | 0 | 0 | 0.46006 | 0 | 0.01539 | 0.092216 | 0.88242 | 0 | 62.95 | FY34 | 21.8914 | 2.5268 | 0.27527 | 191.8255 | 0.48679 | 61.794 | 0.091018 | 0.73471 | 0.046618 | 4.1064
FY35 | 66.3986 | 16.096 | 2.6181 | 540.3509 | 23.4625 | 102.4399 | 0.29461 | 1.6057 | 1.7598 | 5.1403 | 760.1665 | FY35 | 0.025596 | 0 | 2.6181 | 0.072888 | 0 | 0 | 0.0010403 | 0.406 | 0.10198 | 5.1403 | 8.3659 | FY35 | 66.3986 | 16.096 | 0 | 0.072888 | 0 | 0 | 5.1049e-05 | 0.029221 | 1.7598 | 5.1403 | 89.497 | FY35 | 0 | 0 | 0 | 540.3509 | 0 | 0 | 0.049065 | 0.0012267 | 0.028754 | 5.1403 | 545.5703 | FY35 | 66.3986 | 16.096 | 0 | 0.072888 | 0 | 0 | 0.0010403 | 0.029221 | 1.7598 | 0 | 84.3576 | FY35 | 0.67279 | 0.22555 | 2.6181 | 0.072888 | 0.30197 | 0 | 0.016582 | 0.406 | 0.45056 | 5.1403 | 9.9048 | FY35 | 66.3986 | 16.096 | 0 | 0.072888 | 0.65653 | 0 | 5.1049e-05 | 0.13017 | 1.7598 | 5.1403 | 90.2545 | FY35 | 0.025596 | 0 | 0 | 540.3509 | 0.65653 | 0 | 0.20312 | 0.0012267 | 0.10198 | 5.1403 | 546.4797 | FY35 | 66.3986 | 16.096 | 0 | 0 | 0.65653 | 0 | 0.0082173 | 0.13017 | 1.7598 | 0 | 85.0494 | FY35 | 29.1184 | 6.6675 | 0.39705 | 185.5354 | 0.6886 | 64.008 | 0.085193 | 0.89516 | 0.3343 | 4.4615
FY36 | 97.2424 | 28.7239 | 3.6767 | 550.4303 | 37.7816 | 117.1795 | 0.31173 | 2.006 | 3.8671 | 5.566 | 846.7852 | FY36 | 0.10888 | 0.045221 | 3.6767 | 0.067816 | 0 | 0 | 0.0013759 | 0.5769 | 0.85406 | 5.566 | 10.897 | FY36 | 97.2424 | 28.7239 | 0 | 0.067816 | 0 | 0 | 6.2368e-05 | 0.050233 | 3.8671 | 5.566 | 135.5176 | FY36 | 0 | 0 | 0 | 550.4303 | 0 | 0 | 0.045132 | 0.0016715 | 0.34665 | 5.566 | 556.3898 | FY36 | 97.2424 | 28.7239 | 0 | 0.067816 | 0 | 0 | 0.0013759 | 0.050233 | 3.8671 | 0 | 129.9529 | FY36 | 2.5253 | 0.5777 | 3.6767 | 0.067816 | 0.67397 | 0 | 0.014203 | 0.5769 | 1.5527 | 5.566 | 15.2313 | FY36 | 97.2424 | 28.7239 | 0 | 0.067816 | 1.3534 | 0 | 6.2368e-05 | 0.21279 | 3.8671 | 5.566 | 137.0336 | FY36 | 0.10888 | 0.045221 | 0 | 550.4303 | 1.3534 | 0 | 0.21026 | 0.0016715 | 0.85406 | 5.566 | 558.5698 | FY36 | 97.2424 | 28.7239 | 0 | 0 | 1.3534 | 0 | 0.0071727 | 0.21279 | 3.8671 | 0 | 131.4069 | FY36 | 48.5365 | 12.3589 | 0.69885 | 199.7997 | 1.3474 | 75.9949 | 0.080997 | 1.1651 | 1.2589 | 4.834
FY37 | 82.1864 | 41.7144 | 2.1769 | 490.6258 | 43.9889 | 98.5408 | 0.40597 | 2.0745 | 5.9164 | 5.9297 | 773.56 | FY37 | 0.11653 | 0.16036 | 2.1769 | 0.0042064 | 0 | 0 | 0.0017845 | 0.56828 | 1.7879 | 5.9297 | 10.7457 | FY37 | 82.1864 | 41.7144 | 0 | 0.0042064 | 0 | 0 | 9.1192e-05 | 0.049824 | 5.9164 | 5.9297 | 135.8011 | FY37 | 0 | 0 | 0 | 490.6258 | 0 | 0 | 0.070245 | 0.0019373 | 1.0214 | 5.9297 | 497.6492 | FY37 | 82.1864 | 41.7144 | 0 | 0.0042064 | 0 | 0 | 0.0017845 | 0.049824 | 5.9164 | 0 | 129.8731 | FY37 | 1.6056 | 1.0671 | 2.1769 | 0.0042064 | 0.81064 | 0 | 0.024793 | 0.56828 | 2.8305 | 5.9297 | 15.0177 | FY37 | 82.1864 | 41.7144 | 0 | 0.0042064 | 1.6121 | 0 | 9.1192e-05 | 0.20138 | 5.9164 | 5.9297 | 137.5648 | FY37 | 0.11653 | 0.16036 | 0 | 490.6258 | 1.6121 | 0 | 0.28185 | 0.0019373 | 1.7879 | 5.9297 | 500.5162 | FY37 | 82.1864 | 41.7144 | 0 | 0 | 1.6121 | 0 | 0.012715 | 0.20138 | 5.9164 | 0 | 131.6435 | FY37 | 37.7559 | 18.6773 | 0.3583 | 162.0496 | 1.484 | 60.3094 | 0.11824 | 1.1705 | 2.3207 | 5.1437
FY38 | 118.6467 | 76.0622 | 6.8409 | 531.5785 | 79.0503 | 113.9545 | 0.56605 | 2.7399 | 9.1098 | 6.4336 | 944.9824 | FY38 | 0.26609 | 0.38516 | 6.8409 | 0.021929 | 0 | 0 | 0.0036579 | 0.87407 | 3.1876 | 6.4336 | 18.0131 | FY38 | 118.6467 | 76.0622 | 0 | 0.021929 | 0 | 0 | 0.00014081 | 0.10198 | 9.1098 | 6.4336 | 210.3763 | FY38 | 0.0041476 | 0.0053447 | 0 | 531.5785 | 0 | 0 | 0.12709 | 0.0028285 | 2.0677 | 6.4336 | 540.2193 | FY38 | 118.6467 | 76.0622 | 0 | 0.021929 | 0 | 0 | 0.0036579 | 0.10198 | 9.1098 | 0 | 203.9462 | FY38 | 4.008 | 3.382 | 6.8409 | 0.021929 | 2.4551 | 0 | 0.055679 | 0.87407 | 4.651 | 6.4336 | 28.7224 | FY38 | 118.6467 | 76.0622 | 0 | 0.021929 | 5.2611 | 0 | 0.00014081 | 0.36517 | 9.1098 | 6.4336 | 215.9006 | FY38 | 0.26609 | 0.38516 | 0 | 531.5785 | 5.2611 | 0 | 0.40968 | 0.0028285 | 3.1876 | 6.4336 | 547.5246 | FY38 | 118.6467 | 76.0622 | 0 | 0 | 5.2611 | 0 | 0.032362 | 0.36517 | 9.1098 | 0 | 209.4773 | FY38 | 60.1181 | 38.1473 | 1.4575 | 186.3699 | 4.1807 | 72.6711 | 0.19223 | 1.6141 | 3.8121 | 5.5923
FY39 | 162.1544 | 107.3756 | 8.7415 | 565.2239 | 130.1437 | 129.5956 | 0.55688 | 3.4606 | 13.1263 | 6.8363 | 1127.2149 | FY39 | 0.48954 | 0.8118 | 8.7415 | 0.054965 | 0 | 0 | 0.0028495 | 1.2726 | 5.2067 | 6.8363 | 23.4163 | FY39 | 162.1544 | 107.3756 | 0 | 0.054965 | 0 | 0 | 0.00015793 | 0.21623 | 13.1263 | 6.8363 | 289.764 | FY39 | 0.026201 | 0.073592 | 0 | 565.2239 | 0 | 0 | 0.1045 | 0.0037471 | 3.6601 | 6.8363 | 575.9283 | FY39 | 162.1544 | 107.3756 | 0 | 0.054965 | 0 | 0 | 0.0028495 | 0.21623 | 13.1263 | 0 | 282.9304 | FY39 | 9.1344 | 7.7605 | 8.7415 | 0.054965 | 8.4248 | 0 | 0.039643 | 1.2726 | 7.225 | 6.8363 | 49.4898 | FY39 | 162.1544 | 107.3756 | 0 | 0.054965 | 16.1138 | 0 | 0.00015793 | 0.61589 | 13.1263 | 6.8363 | 306.2774 | FY39 | 0.48954 | 0.8118 | 0 | 565.2239 | 16.1138 | 0 | 0.39188 | 0.0037471 | 5.2067 | 6.8363 | 595.0776 | FY39 | 162.1544 | 107.3756 | 0 | 0 | 16.1138 | 0 | 0.021257 | 0.61589 | 13.1263 | 0 | 299.4072 | FY39 | 88.8491 | 58.303 | 2.1669 | 207.1544 | 11.7284 | 85.3484 | 0.17043 | 2.1565 | 5.8906 | 5.9366
FY40 | [10 empty] | 1127.2149 | FY40 | [10 empty] | 23.4163 | FY40 | [10 empty] | 289.764 | FY40 | [10 empty] | 575.9283 | FY40 | [10 empty] | 282.9304 | FY40 | [10 empty] | 49.4898 | FY40 | [10 empty] | 306.2774 | FY40 | [10 empty] | 595.0776 | FY40 | [10 empty] | 299.4072 | FY40 | [10 empty] | 0
FY41 | [10 empty] | 1127.2149 | FY41 | [10 empty] | 23.4163 | FY41 | [10 empty] | 289.764 | FY41 | [10 empty] | 575.9283 | FY41 | [10 empty] | 282.9304 | FY41 | [10 empty] | 49.4898 | FY41 | [10 empty] | 306.2774 | FY41 | [10 empty] | 595.0776 | FY41 | [10 empty] | 299.4072 | FY41 | [10 empty] | 0
FY42 | [10 empty] | 1127.2149 | FY42 | [10 empty] | 23.4163 | FY42 | [10 empty] | 289.764 | FY42 | [10 empty] | 575.9283 | FY42 | [10 empty] | 282.9304 | FY42 | [10 empty] | 49.4898 | FY42 | [10 empty] | 306.2774 | FY42 | [10 empty] | 595.0776 | FY42 | [10 empty] | 299.4072 | FY42 | [10 empty] | 0
FY43 | [10 empty] | 1127.2149 | FY43 | [10 empty] | 23.4163 | FY43 | [10 empty] | 289.764 | FY43 | [10 empty] | 575.9283 | FY43 | [10 empty] | 282.9304 | FY43 | [10 empty] | 49.4898 | FY43 | [10 empty] | 306.2774 | FY43 | [10 empty] | 595.0776 | FY43 | [10 empty] | 299.4072 | FY43 | [10 empty] | 0
FY44 | [10 empty] | 1127.2149 | FY44 | [10 empty] | 23.4163 | FY44 | [10 empty] | 289.764 | FY44 | [10 empty] | 575.9283 | FY44 | [10 empty] | 282.9304 | FY44 | [10 empty] | 49.4898 | FY44 | [10 empty] | 306.2774 | FY44 | [10 empty] | 595.0776 | FY44 | [10 empty] | 299.4072 | FY44 | [10 empty] | 0
FY45 | [10 empty] | 1127.2149 | FY45 | [10 empty] | 23.4163 | FY45 | [10 empty] | 289.764 | FY45 | [10 empty] | 575.9283 | FY45 | [10 empty] | 282.9304 | FY45 | [10 empty] | 49.4898 | FY45 | [10 empty] | 306.2774 | FY45 | [10 empty] | 595.0776 | FY45 | [10 empty] | 299.4072 | FY45 | [10 empty] | 0
FY46 | [10 empty] | 1127.2149 | FY46 | [10 empty] | 23.4163 | FY46 | [10 empty] | 289.764 | FY46 | [10 empty] | 575.9283 | FY46 | [10 empty] | 282.9304 | FY46 | [10 empty] | 49.4898 | FY46 | [10 empty] | 306.2774 | FY46 | [10 empty] | 595.0776 | FY46 | [10 empty] | 299.4072 | FY46 | [10 empty] | 0
FY47 | [10 empty] | 1127.2149 | FY47 | [10 empty] | 23.4163 | FY47 | [10 empty] | 289.764 | FY47 | [10 empty] | 575.9283 | FY47 | [10 empty] | 282.9304 | FY47 | [10 empty] | 49.4898 | FY47 | [10 empty] | 306.2774 | FY47 | [10 empty] | 595.0776 | FY47 | [10 empty] | 299.4072 | FY47 | [10 empty] | 0
FY48 | [10 empty] | 1127.2149 | FY48 | [10 empty] | 23.4163 | FY48 | [10 empty] | 289.764 | FY48 | [10 empty] | 575.9283 | FY48 | [10 empty] | 282.9304 | FY48 | [10 empty] | 49.4898 | FY48 | [10 empty] | 306.2774 | FY48 | [10 empty] | 595.0776 | FY48 | [10 empty] | 299.4072 | FY48 | [10 empty] | 0
FY49 | [10 empty] | 1127.2149 | FY49 | [10 empty] | 23.4163 | FY49 | [10 empty] | 289.764 | FY49 | [10 empty] | 575.9283 | FY49 | [10 empty] | 282.9304 | FY49 | [10 empty] | 49.4898 | FY49 | [10 empty] | 306.2774 | FY49 | [10 empty] | 595.0776 | FY49 | [10 empty] | 299.4072 | FY49 | [10 empty] | 0
FY50 | [10 empty] | 1127.2149 | FY50 | [10 empty] | 23.4163 | FY50 | [10 empty] | 289.764 | FY50 | [10 empty] | 575.9283 | FY50 | [10 empty] | 282.9304 | FY50 | [10 empty] | 49.4898 | FY50 | [10 empty] | 306.2774 | FY50 | [10 empty] | 595.0776 | FY50 | [10 empty] | 299.4072 | FY50 | [10 empty] | 0
FY51 | [10 empty] | 1127.2149 | FY51 | [10 empty] | 23.4163 | FY51 | [10 empty] | 289.764 | FY51 | [10 empty] | 575.9283 | FY51 | [10 empty] | 282.9304 | FY51 | [10 empty] | 49.4898 | FY51 | [10 empty] | 306.2774 | FY51 | [10 empty] | 595.0776 | FY51 | [10 empty] | 299.4072 | FY51 | [10 empty] | 0
FY52 | [10 empty] | 1127.2149 | FY52 | [10 empty] | 23.4163 | FY52 | [10 empty] | 289.764 | FY52 | [10 empty] | 575.9283 | FY52 | [10 empty] | 282.9304 | FY52 | [10 empty] | 49.4898 | FY52 | [10 empty] | 306.2774 | FY52 | [10 empty] | 595.0776 | FY52 | [10 empty] | 299.4072 | FY52 | [10 empty] | 0
FY53 | [10 empty] | 1127.2149 | FY53 | [10 empty] | 23.4163 | FY53 | [10 empty] | 289.764 | FY53 | [10 empty] | 575.9283 | FY53 | [10 empty] | 282.9304 | FY53 | [10 empty] | 49.4898 | FY53 | [10 empty] | 306.2774 | FY53 | [10 empty] | 595.0776 | FY53 | [10 empty] | 299.4072 | FY53 | [10 empty] | 0
FY54 | [10 empty] | 1127.2149 | FY54 | [10 empty] | 23.4163 | FY54 | [10 empty] | 289.764 | FY54 | [10 empty] | 575.9283 | FY54 | [10 empty] | 282.9304 | FY54 | [10 empty] | 49.4898 | FY54 | [10 empty] | 306.2774 | FY54 | [10 empty] | 595.0776 | FY54 | [10 empty] | 299.4072 | FY54 | [10 empty] | 0

## 2.2.4 SupplyRisk$ High PoF
Option 1 - Do Nothing / Base Case | [11 empty] | Option 2 - 1A New PHS ZSS + Four new feeders | [11 empty] | Option 3 - 2A PHM 3rd Tx + Switchroom + Three new feeders + OFR12 New Feeder | [11 empty] | Option 4 - 3A OFR 3rd Tx + Switchroom + Three new feeders + OFR12 New Feeder | [11 empty] | Option 5 - 4A LLG 2nd Tx + Switchroom + Three new feeders + OFR12 New Feeder | [11 empty] | Option 6 - 1B New PHS ZSS + Three new feeders | [11 empty] | Option 7 - 2B PHM 3rd Tx + Switchroom + Two new feeders + OFR12 New Feeder | [11 empty] | Option 8 - 3B OFR 3rd Tx + Switchroom + Two new feeders + OFR12 New Feeder | [11 empty] | Option 9 - 4B LLG 2nd Tx + Switchroom + Two new feeders + OFR12 New Feeder | [11 empty] | Option 10 - 5 Non-Network
| Total Supply Risk $M by Asset and Year | [11 empty] | Total Supply Risk $M by Asset and Year | [11 empty] | Total Supply Risk $M by Asset and Year | [11 empty] | Total Supply Risk $M by Asset and Year | [11 empty] | Total Supply Risk $M by Asset and Year | [11 empty] | Total Supply Risk $M by Asset and Year | [11 empty] | Total Supply Risk $M by Asset and Year | [11 empty] | Total Supply Risk $M by Asset and Year | [11 empty] | Total Supply Risk $M by Asset and Year | [11 empty] | Total Supply Risk $M by Asset and Year
Source: | E@R CLN22 Feeder V2.7 POE10.xlsx¦Output for AusNet''s NPV model'!$B$5:$P$5 | E@R CLN23 Feeder V2.7 POE10.xlsx¦Output for AusNet''s NPV model'!$B$5:$P$5 | E@R OFR21 Feeder V2.7 POE10.xlsx¦Output for AusNet''s NPV model'!$B$5:$P$5 | E@R PHM21 Feeder V2.7 POE10.xlsx¦Output for AusNet''s NPV model'!$B$5:$P$5 | E@R PHM22 Feeder V2.7 POE10.xlsx¦Output for AusNet''s NPV model'!$B$5:$P$5 | E@R OFR14 Feeder V2.7 POE10.xlsx¦Output for AusNet''s NPV model'!$B$5:$P$5 | ZSS EaR PHM V2.3 POE10 High PoF.xlsx¦Output for AusNet''s NPV model'!$B$5:$P$5 | ZSS EaR OFR V2.3 POE10 High PoF.xlsx¦Output for AusNet''s NPV model'!$B$5:$P$5 | ZSS EaR CLN V2.3 POE10 High PoF.xlsx¦Output for AusNet''s NPV model'!$B$5:$P$5 | ZSS EaR LLG V2.3 POE10 High PoF.xlsx¦Output for AusNet''s NPV model'!$B$5:$P$5 |  |  | E@R CLN22 Feeder V2.7 POE10.xlsx¦Output for AusNet''s NPV model'!$B$10:$P$10 | E@R CLN23 Feeder V2.7 POE10.xlsx¦Output for AusNet''s NPV model'!$B$10:$P$10 | E@R OFR21 Feeder V2.7 POE10.xlsx¦Output for AusNet''s NPV model'!$B$10:$P$10 | E@R PHM21 Feeder V2.7 POE10.xlsx¦Output for AusNet''s NPV model'!$B$10:$P$10 | E@R PHM22 Feeder V2.7 POE10.xlsx¦Output for AusNet''s NPV model'!$B$10:$P$10 | E@R OFR14 Feeder V2.7 POE10.xlsx¦Output for AusNet''s NPV model'!$B$10:$P$10 | ZSS EaR PHM V2.3 POE10 High PoF.xlsx¦Output for AusNet''s NPV model'!$B$10:$P$10 | ZSS EaR OFR V2.3 POE10 High PoF.xlsx¦Output for AusNet''s NPV model'!$B$10:$P$10 | ZSS EaR CLN V2.3 POE10 High PoF.xlsx¦Output for AusNet''s NPV model'!$B$10:$P$10 | ZSS EaR LLG V2.3 POE10 High PoF.xlsx¦Output for AusNet''s NPV model'!$B$10:$P$10 |  |  | E@R CLN22 Feeder V2.7 POE10.xlsx¦Output for AusNet''s NPV model'!$B$13:$P$13 | E@R CLN23 Feeder V2.7 POE10.xlsx¦Output for AusNet''s NPV model'!$B$13:$P$13 | E@R OFR21 Feeder V2.7 POE10.xlsx¦Output for AusNet''s NPV model'!$B$13:$P$13 | E@R PHM21 Feeder V2.7 POE10.xlsx¦Output for AusNet''s NPV model'!$B$13:$P$13 | E@R PHM22 Feeder V2.7 POE10.xlsx¦Output for AusNet''s NPV model'!$B$13:$P$13 | E@R OFR14 Feeder V2.7 POE10.xlsx¦Output for AusNet''s NPV model'!$B$13:$P$13 | ZSS EaR PHM V2.3 POE10 High PoF.xlsx¦Output for AusNet''s NPV model'!$B$13:$P$13 | ZSS EaR OFR V2.3 POE10 High PoF.xlsx¦Output for AusNet''s NPV model'!B$13:$P$13 | ZSS EaR CLN V2.3 POE10 High PoF.xlsx¦Output for AusNet''s NPV model'!B$13:$P$13 | ZSS EaR LLG V2.3 POE10 High PoF.xlsx¦Output for AusNet''s NPV model'!B$13:$P$13 |  |  | E@R CLN22 Feeder V2.7 POE10.xlsx¦Output for AusNet''s NPV model'!$B$16:$P$16 | E@R CLN23 Feeder V2.7 POE10.xlsx¦Output for AusNet''s NPV model'!$B$16:$P$16 | E@R OFR21 Feeder V2.7 POE10.xlsx¦Output for AusNet''s NPV model'!$B$16:$P$16 | E@R PHM21 Feeder V2.7 POE10.xlsx¦Output for AusNet''s NPV model'!$B$16:$P$16 | E@R PHM22 Feeder V2.7 POE10.xlsx¦Output for AusNet''s NPV model'!$B$16:$P$16 | E@R OFR14 Feeder V2.7 POE10.xlsx¦Output for AusNet''s NPV model'!$B$16:$P$16 | ZSS EaR PHM V2.3 POE10 High PoF.xlsx¦Output for AusNet''s NPV model'!$B$16:$P$16 | ZSS EaR OFR V2.3 POE10 High PoF.xlsx¦Output for AusNet''s NPV model'!$B$16:$P$16 | ZSS EaR CLN V2.3 POE10 High PoF.xlsx¦Output for AusNet''s NPV model'!$B$16:$P$16 | ZSS EaR LLG V2.3 POE10 High PoF.xlsx¦Output for AusNet''s NPV model'!$B$16:$P$16 |  |  | E@R CLN22 Feeder V2.7 POE10.xlsx¦Output for AusNet''s NPV model'!$B$19:$P$19 | E@R CLN23 Feeder V2.7 POE10.xlsx¦Output for AusNet''s NPV model'!$B$19:$P$19 | E@R OFR21 Feeder V2.7 POE10.xlsx¦Output for AusNet''s NPV model'!$B$19:$P$19 | E@R PHM21 Feeder V2.7 POE10.xlsx¦Output for AusNet''s NPV model'!$B$19:$P$19 | E@R PHM22 Feeder V2.7 POE10.xlsx¦Output for AusNet''s NPV model'!$B$19:$P$19 | E@R OFR14 Feeder V2.7 POE10.xlsx¦Output for AusNet''s NPV model'!$B$19:$P$19 | ZSS EaR PHM V2.3 POE10 High PoF.xlsx¦Output for AusNet''s NPV model'!$B$19:$P$19 | ZSS EaR OFR V2.3 POE10 High PoF.xlsx¦Output for AusNet''s NPV model'!$B$19:$P$19 | ZSS EaR CLN V2.3 POE10 High PoF.xlsx¦Output for AusNet''s NPV model'!$B$19:$P$19 | ZSS EaR LLG V2.3 POE10 High PoF.xlsx¦Output for AusNet''s NPV model'!$B$19:$P$19 |  |  | E@R CLN22 Feeder V2.7 POE50.xlsx¦Output for AusNet''s NPV model'!$B$10:$P$10 | E@R CLN23 Feeder V2.7 POE50.xlsx¦Output for AusNet''s NPV model'!$B$10:$P$10 | E@R OFR21 Feeder V2.7 POE50.xlsx¦Output for AusNet''s NPV model'!$B$10:$P$10 | E@R PHM21 Feeder V2.7 POE50.xlsx¦Output for AusNet''s NPV model'!$B$10:$P$10 | E@R PHM22 Feeder V2.7 POE50.xlsx¦Output for AusNet''s NPV model'!$B$10:$P$10 | E@R OFR14 Feeder V2.7 POE50.xlsx¦Output for AusNet''s NPV model'!$B$10:$P$10 | ZSS EaR PHM V2.3 POE50 High PoF.xlsx¦Output for AusNet''s NPV model'!$B$10:$P$10 | ZSS EaR OFR V2.3 POE50 High PoF.xlsx¦Output for AusNet''s NPV model'!$B$10:$P$10 | ZSS EaR CLN V2.3 POE50 High PoF.xlsx¦Output for AusNet''s NPV model'!$B$10:$P$10 | ZSS EaR LLG V2.3 POE50 High PoF.xlsx¦Output for AusNet''s NPV model'!$B$10:$P$10 |  |  | E@R CLN22 Feeder V2.7 POE50.xlsx¦Output for AusNet''s NPV model'!$B$13:$P$13 | E@R CLN23 Feeder V2.7 POE50.xlsx¦Output for AusNet''s NPV model'!$B$13:$P$13 | E@R OFR21 Feeder V2.7 POE50.xlsx¦Output for AusNet''s NPV model'!$B$13:$P$13 | E@R PHM21 Feeder V2.7 POE50.xlsx¦Output for AusNet''s NPV model'!$B$13:$P$13 | E@R PHM22 Feeder V2.7 POE50.xlsx¦Output for AusNet''s NPV model'!$B$13:$P$13 | E@R OFR14 Feeder V2.7 POE50.xlsx¦Output for AusNet''s NPV model'!$B$13:$P$13 | ZSS EaR PHM V2.3 POE50 High PoF.xlsx¦Output for AusNet''s NPV model'!$B$13:$P$13 | ZSS EaR OFR V2.3 POE50 High PoF.xlsx¦Output for AusNet''s NPV model'!$B$13:$P$13 | ZSS EaR CLN V2.3 POE50 High PoF.xlsx¦Output for AusNet''s NPV model'!$B$13:$P$13 | ZSS EaR LLG V2.3 POE50 High PoF.xlsx¦Output for AusNet''s NPV model'!$B$13:$P$13 |  |  | E@R CLN22 Feeder V2.7 POE50.xlsx¦Output for AusNet''s NPV model'!$B$16:$P$16 | E@R CLN23 Feeder V2.7 POE50.xlsx¦Output for AusNet''s NPV model'!$B$16:$P$16 | E@R OFR21 Feeder V2.7 POE50.xlsx¦Output for AusNet''s NPV model'!$B$16:$P$16 | E@R PHM21 Feeder V2.7 POE50.xlsx¦Output for AusNet''s NPV model'!$B$16:$P$16 | E@R PHM22 Feeder V2.7 POE50.xlsx¦Output for AusNet''s NPV model'!$B$16:$P$16 | E@R OFR14 Feeder V2.7 POE50.xlsx¦Output for AusNet''s NPV model'!$B$16:$P$16 | ZSS EaR PHM V2.3 POE50 High PoF.xlsx¦Output for AusNet''s NPV model'!$B$16:$P$16 | ZSS EaR OFR V2.3 POE50 High PoF.xlsx¦Output for AusNet''s NPV model'!$B$16:$P$16 | ZSS EaR CLN V2.3 POE50 High PoF.xlsx¦Output for AusNet''s NPV model'!$B$16:$P$16 | ZSS EaR LLG V2.3 POE10 High PoF.xlsx¦Output for AusNet''s NPV model'!$B$16:$P$16 |  |  | E@R CLN22 Feeder V2.7 POE50.xlsx¦Output for AusNet''s NPV model'!$B$19:$P$19 | E@R CLN23 Feeder V2.7 POE50.xlsx¦Output for AusNet''s NPV model'!$B$19:$P$19 | E@R OFR21 Feeder V2.7 POE50.xlsx¦Output for AusNet''s NPV model'!$B$19:$P$19 | E@R PHM21 Feeder V2.7 POE50.xlsx¦Output for AusNet''s NPV model'!$B$19:$P$19 | E@R PHM22 Feeder V2.7 POE50.xlsx¦Output for AusNet''s NPV model'!$B$19:$P$19 | E@R OFR14 Feeder V2.7 POE50.xlsx¦Output for AusNet''s NPV model'!$B$19:$P$19 | ZSS EaR PHM V2.3 POE50 High PoF.xlsx¦Output for AusNet''s NPV model'!$B$19:$P$19 | ZSS EaR OFR V2.3 POE50 High PoF.xlsx¦Output for AusNet''s NPV model'!$B$19:$P$19 | ZSS EaR CLN V2.3 POE50 High PoF.xlsx¦Output for AusNet''s NPV model'!$B$19:$P$19 | ZSS EaR LLG V2.3 POE10 High PoF.xlsx¦Output for AusNet''s NPV model'!$B$19:$P$19 |  |  | E@R CLN22 Feeder V2.7 POE10.xlsx¦Output for AusNet''s NPV model'!$B$22:$P$22 | E@R CLN23 Feeder V2.7 POE10.xlsx¦Output for AusNet''s NPV model'!$B$22:$P$22 | E@R OFR21 Feeder V2.7 POE10.xlsx¦Output for AusNet''s NPV model'!$B$22:$P$22 | E@R PHM21 Feeder V2.7 POE10.xlsx¦Output for AusNet''s NPV model'!$B$22:$P$22 | E@R PHM22 Feeder V2.7 POE10.xlsx¦Output for AusNet''s NPV model'!$B$22:$P$22 | E@R OFR14 Feeder V2.7 POE10.xlsx¦Output for AusNet''s NPV model'!$B$22:$P$22 | ZSS EaR PHM V2.3 POE10 High PoF.xlsx¦Output for AusNet''s NPV model'!$B$22:$P$22 | ZSS EaR OFR V2.3 POE10 High PoF.xlsx¦Output for AusNet''s NPV model'!$B$22:$P$22 | ZSS EaR CLN V2.3 POE10 High PoF.xlsx¦Output for AusNet''s NPV model'!$B$22:$P$22 | ZSS EaR LLG V2.3 POE10 High PoF.xlsx¦Output for AusNet''s NPV model'!$B$22:$P$22
Year | CLN22 | CLN23 | OFR21 | PHM21 | PHM22 | OFR14 | PHM | OFR | CLN | LLG | Opt 1 Total | Year | CLN22 | CLN23 | OFR21 | PHM21 | PHM22 | OFR14 | PHM | OFR | CLN | LLG | Opt 2 Total | Year | CLN22 | CLN23 | OFR21 | PHM21 | PHM22 | OFR14 | PHM | OFR | CLN | LLG | Opt 3 Total | Year | CLN22 | CLN23 | OFR21 | PHM21 | PHM22 | OFR14 | PHM | OFR | CLN | LLG | Opt 4 Total | Year | CLN22 | CLN23 | OFR21 | PHM21 | PHM22 | OFR14 | PHM | OFR | CLN | LLG | Opt 5 Total | Year | CLN22 | CLN23 | OFR21 | PHM21 | PHM22 | OFR14 | PHM | OFR | CLN | LLG | Opt 6 Total | Year | CLN22 | CLN23 | OFR21 | PHM21 | PHM22 | OFR14 | PHM | OFR | CLN | LLG | Opt 7 Total | Year | CLN22 | CLN23 | OFR21 | PHM21 | PHM22 | OFR14 | PHM | OFR | CLN | LLG | Opt 8 Total | Year | CLN22 | CLN23 | OFR21 | PHM21 | PHM22 | OFR14 | PHM | OFR | CLN | LLG | Opt 9 Total | Year | CLN22 | CLN23 | OFR21 | PHM21 | PHM22 | OFR14 | PHM | OFR | CLN | LLG | Opt 10 Total
FY25 | 0 | 0 | 9.261e-05 | 0 | 0 | 0 | 0.00072127 | 0.046016 | 0.0048647 | 4.9258 | 4.9775 | FY25 | 0 | 0 | 9.261e-05 | 0 | 0 | 0 | 0.00072127 | 0.046016 | 0.0048647 | 4.9166 | 4.9683 | FY25 | 0 | 0 | 9.261e-05 | 0 | 0 | 0 | 0.00072127 | 0.046016 | 0.0048647 | 4.9166 | 4.9683 | FY25 | 0 | 0 | 9.261e-05 | 0 | 0 | 0 | 0.00072127 | 0.046016 | 0.0048647 | 4.9166 | 4.9683 | FY25 | 0 | 0 | 9.261e-05 | 0 | 0 | 0 | 0.00072127 | 0.046016 | 0.0048647 | 4.9166 | 4.9683 | FY25 | 0 | 0 | 9.261e-05 | 0 | 0 | 0 | 0.00072127 | 0.046016 | 0.0048647 | 4.9166 | 4.9683 | FY25 | 0 | 0 | 9.261e-05 | 0 | 0 | 0 | 0.00072127 | 0.046016 | 0.0048647 | 4.9166 | 4.9683 | FY25 | 0 | 0 | 9.261e-05 | 0 | 0 | 0 | 0.00072127 | 0.046016 | 0.0048647 | 4.9166 | 4.9683 | FY25 | 0 | 0 | 9.261e-05 | 0 | 0 | 0 | 0.00072127 | 0.046016 | 0.0048647 | 4.9166 | 4.9683 | FY25 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00014741 | 0.028375 | 0.0016885 | 4.2223 | 4.2525
FY26 | 0.33417 | 0 | 0.016561 | 61.2197 | 0.0049505 | 0.076122 | 0.02973 | 0.064327 | 0.002422 | 5.5777 | 67.3256 | FY26 | 0.33417 | 0 | 0.016561 | 61.2197 | 0.0049505 | 0.076122 | 0.02973 | 0.064327 | 0.002422 | 5.5777 | 67.3256 | FY26 | 0.33417 | 0 | 0.016561 | 61.2197 | 0.0049505 | 0.076122 | 0.02973 | 0.064327 | 0.002422 | 5.5777 | 67.3256 | FY26 | 0.33417 | 0 | 0.016561 | 61.2197 | 0.0049505 | 0.076122 | 0.02973 | 0.064327 | 0.002422 | 5.5777 | 67.3256 | FY26 | 0.33417 | 0 | 0.016561 | 61.2197 | 0.0049505 | 0.076122 | 0.02973 | 0.064327 | 0.002422 | 5.5777 | 67.3256 | FY26 | 0.33417 | 0 | 0.016561 | 61.2197 | 0.0049505 | 0.076122 | 0.02973 | 0.064327 | 0.002422 | 5.5777 | 67.3256 | FY26 | 0.33417 | 0 | 0.016561 | 61.2197 | 0.0049505 | 0.076122 | 0.02973 | 0.064327 | 0.002422 | 5.5777 | 67.3256 | FY26 | 0.33417 | 0 | 0.016561 | 61.2197 | 0.0049505 | 0.076122 | 0.02973 | 0.064327 | 0.002422 | 5.5777 | 67.3256 | FY26 | 0.33417 | 0 | 0.016561 | 61.2197 | 0.0049505 | 0.076122 | 0.02973 | 0.064327 | 0.002422 | 5.5777 | 67.3256 | FY26 | 0.047751 | 0 | 0 | 4.3361 | 0 | 0 | 0.0029733 | 0.032233 | 0.00032204 | 4.7967 | 9.2161
FY27 | 1.0189 | 0 | 0.095278 | 228.821 | 1.406 | 10.7476 | 0.079301 | 0.2653 | 0.0055077 | 7.2257 | 249.6646 | FY27 | 1.0189 | 0 | 0.095278 | 228.821 | 1.406 | 10.7476 | 0.079301 | 0.2653 | 0.0055077 | 7.2257 | 249.6646 | FY27 | 1.0189 | 0 | 0.095278 | 228.821 | 1.406 | 10.7476 | 0.079301 | 0.2653 | 0.0055077 | 7.2257 | 249.6646 | FY27 | 1.0189 | 0 | 0.095278 | 228.821 | 1.406 | 10.7476 | 0.079301 | 0.2653 | 0.0055077 | 7.2257 | 249.6646 | FY27 | 1.0189 | 0 | 0.095278 | 228.821 | 1.406 | 10.7476 | 0.079301 | 0.2653 | 0.0055077 | 7.2257 | 249.6646 | FY27 | 1.0189 | 0 | 0.095278 | 228.821 | 1.406 | 10.7476 | 0.079301 | 0.2653 | 0.0055077 | 7.2257 | 249.6646 | FY27 | 1.0189 | 0 | 0.095278 | 228.821 | 1.406 | 10.7476 | 0.079301 | 0.2653 | 0.0055077 | 7.2257 | 249.6646 | FY27 | 1.0189 | 0 | 0.095278 | 228.821 | 1.406 | 10.7476 | 0.079301 | 0.2653 | 0.0055077 | 7.2257 | 249.6646 | FY27 | 1.0189 | 0 | 0.095278 | 228.821 | 1.406 | 10.7476 | 0.079301 | 0.2653 | 0.0055077 | 7.2257 | 249.6646 | FY27 | 0.1413 | 0 | 0.0056705 | 49.59 | 0.010662 | 3.6807 | 0.011097 | 0.090851 | 0.0014755 | 6.232 | 59.7637
FY28 | 2.2918 | 0 | 0.13664 | 238.429 | 4.6943 | 31.6628 | 0.10845 | 0.69775 | 0.0099165 | 7.9986 | 286.0292 | FY28 | 0 | 0 | 0.13664 | 0 | 0 | 31.6628 | 0.00033807 | 0.69775 | 0.00094022 | 7.9986 | 40.497 | FY28 | 2.2918 | 0 | 0 | 0 | 0 | 31.6628 | 1.7678e-05 | 0.064805 | 0.0099165 | 7.9986 | 42.0279 | FY28 | 0 | 0 | 0 | 238.429 | 0 | 31.6628 | 0.0056944 | 0.00097812 | 0.00022584 | 7.9986 | 278.0973 | FY28 | 2.2918 | 0 | 0 | 0 | 0 | 31.6628 | 0.00033807 | 0.064805 | 0.0099165 | 0 | 34.0296 | FY28 | 0 | 0 | 0.13664 | 0 | 0.022623 | 31.6628 | 0.0018452 | 0.69775 | 0.0027235 | 7.9986 | 40.523 | FY28 | 2.2918 | 0 | 0 | 0 | 0.094159 | 31.6628 | 1.7678e-05 | 0.2329 | 0.0099165 | 7.9986 | 42.2902 | FY28 | 0 | 0 | 0 | 238.429 | 0.094159 | 31.6628 | 0.060605 | 0.00097812 | 0.00094022 | 7.9986 | 278.2471 | FY28 | 2.2918 | 0 | 0 | 0 | 0.094159 | 31.6628 | 0.0011918 | 0.2329 | 0.0099165 | 0 | 34.2927 | FY28 | 0.40168 | 0 | 0.0088494 | 54.0823 | 0.15497 | 15.9563 | 0.016234 | 0.27571 | 0.0033556 | 6.9067 | 77.8061
FY29 | 4.9069 | 0.00048597 | 0.19953 | 281.1681 | 12.1407 | 56.8773 | 0.14312 | 1.114 | 0.016365 | 8.8097 | 365.3762 | FY29 | 0 | 0 | 0.19953 | 0 | 0 | 56.8773 | 0.00050836 | 1.114 | 0.0025321 | 8.8097 | 67.0035 | FY29 | 4.9069 | 0.00048597 | 0 | 0 | 0 | 56.8773 | 2.9089e-05 | 0.12285 | 0.016365 | 8.8097 | 70.7336 | FY29 | 0 | 0 | 0 | 281.1681 | 0 | 56.8773 | 0.0079167 | 0.0016572 | 0.00075532 | 8.8097 | 346.8654 | FY29 | 4.9069 | 0.00048597 | 0 | 0 | 0 | 56.8773 | 0.00050836 | 0.12285 | 0.016365 | 0 | 61.9245 | FY29 | 0 | 0 | 0.19953 | 0 | 0.073892 | 0 | 0.0024559 | 0.12285 | 0.0054817 | 8.8097 | 9.2139 | FY29 | 4.9069 | 0.00048597 | 0 | 0 | 0.26192 | 0 | 2.9089e-05 | 0.0486 | 0.016365 | 8.8097 | 14.044 | FY29 | 0 | 0 | 0 | 281.1681 | 0.26192 | 0 | 0.081282 | 0.0016572 | 0.0025321 | 8.8097 | 290.3251 | FY29 | 4.9069 | 0.00048597 | 0 | 0 | 0.26192 | 0 | 0.0015962 | 0.0486 | 0.016365 | 0 | 5.2359 | FY29 | 0.99581 | 0 | 0.015334 | 77.3143 | 0.28503 | 32.501 | 0.022503 | 0.48684 | 0.0063223 | 7.6105 | 119.2376
FY30 | 8.7974 | 0.11571 | 0.31946 | 334.6302 | 13.2836 | 74.2782 | 0.19644 | 1.576 | 0.029127 | 9.7421 | 442.9683 | FY30 | 0 | 0 | 0.31946 | 0 | 0 | 0 | 0.00078642 | 0.21534 | 0.0067301 | 9.7421 | 10.2844 | FY30 | 8.7974 | 0.11571 | 0 | 0 | 0 | 0 | 4.8299e-05 | 0.043494 | 0.029127 | 9.7421 | 18.7279 | FY30 | 0 | 0 | 0 | 334.6302 | 0 | 0 | 0.012385 | 0.0025004 | 0.0032147 | 9.7421 | 344.3904 | FY30 | 8.7974 | 0.11571 | 0 | 0 | 0 | 0 | 0.00078642 | 0.043494 | 0.029127 | 0 | 8.9865 | FY30 | 0 | 0 | 0.31946 | 0 | 0.091808 | 0 | 0.0035995 | 0.21534 | 0.011855 | 9.7421 | 10.3841 | FY30 | 8.7974 | 0.11571 | 0 | 0 | 0.29729 | 0 | 4.8299e-05 | 0.069722 | 0.029127 | 9.7421 | 19.0514 | FY30 | 0 | 0 | 0 | 334.6302 | 0.29729 | 0 | 0.11502 | 0.0025004 | 0.0067301 | 9.7421 | 344.7939 | FY30 | 8.7974 | 0.11571 | 0 | 0 | 0.29729 | 0 | 0.0022783 | 0.069722 | 0.029127 | 0 | 9.3115 | FY30 | 1.9456 | 0.013516 | 0.03491 | 107.1324 | 0.31588 | 44.3161 | 0.033885 | 0.73582 | 0.012741 | 8.4264 | 162.9673
FY31 | 16.6417 | 0.35615 | 0.52199 | 457.8876 | 14.1055 | 82.9038 | 0.29486 | 2.1471 | 0.047433 | 10.8756 | 585.7817 | FY31 | 0 | 0 | 0.52199 | 5.3527e-05 | 0 | 0 | 0.0012849 | 0.3633 | 0.013656 | 10.8756 | 11.7759 | FY31 | 16.6417 | 0.35615 | 0 | 5.3527e-05 | 0 | 0 | 8.5258e-05 | 0.056325 | 0.047433 | 10.8756 | 27.9773 | FY31 | 0 | 0 | 0 | 457.8876 | 0 | 0 | 0.025831 | 0.003649 | 0.0078328 | 10.8756 | 468.8005 | FY31 | 16.6417 | 0.35615 | 0 | 5.3527e-05 | 0 | 0 | 0.0012849 | 0.056325 | 0.047433 | 0 | 17.1029 | FY31 | 0.0091261 | 0 | 0.52199 | 5.3527e-05 | 0.10353 | 0 | 0.0067205 | 0.3633 | 0.021612 | 10.8756 | 11.9019 | FY31 | 16.6417 | 0.35615 | 0 | 5.3527e-05 | 0.31926 | 0 | 8.5258e-05 | 0.10547 | 0.047433 | 10.8756 | 28.3457 | FY31 | 0 | 0 | 0 | 457.8876 | 0.31926 | 0 | 0.18333 | 0.003649 | 0.013656 | 10.8756 | 469.2831 | FY31 | 16.6417 | 0.35615 | 0 | 0 | 0.31926 | 0 | 0.003732 | 0.10547 | 0.047433 | 0 | 17.4737 | FY31 | 4.5985 | 0.14312 | 0.065291 | 178.9722 | 0.34228 | 50.5281 | 0.061742 | 1.0679 | 0.022354 | 9.4242 | 245.2256
FY32 | 26.7865 | 0.95811 | 0.78643 | 495.9347 | 15.1327 | 89.796 | 0.40694 | 2.7711 | 0.079452 | 12.0162 | 644.6681 | FY32 | 0 | 0 | 0.78643 | 0.00056072 | 0 | 0 | 0.0019287 | 0.55109 | 0.02812 | 12.0162 | 13.3843 | FY32 | 26.7865 | 0.95811 | 0 | 0.00056072 | 0 | 0 | 0.00013745 | 0.072881 | 0.079452 | 12.0162 | 39.9138 | FY32 | 0 | 0 | 0 | 495.9347 | 0 | 0 | 0.043706 | 0.0050396 | 0.018528 | 12.0162 | 508.0182 | FY32 | 26.7865 | 0.95811 | 0 | 0.00056072 | 0 | 0 | 0.0019287 | 0.072881 | 0.079452 | 0 | 27.8994 | FY32 | 0.052233 | 0 | 0.78643 | 0.00056072 | 0.12035 | 0 | 0.011957 | 0.55109 | 0.041305 | 12.0162 | 13.5801 | FY32 | 26.7865 | 0.95811 | 0 | 0.00056072 | 0.35052 | 0 | 0.00013745 | 0.16282 | 0.079452 | 12.0162 | 40.3542 | FY32 | 0 | 0 | 0 | 495.9347 | 0.35052 | 0 | 0.26171 | 0.0050396 | 0.02812 | 12.0162 | 508.5963 | FY32 | 26.7865 | 0.95811 | 0 | 0 | 0.35052 | 0 | 0.0061348 | 0.16282 | 0.079452 | 0 | 28.3435 | FY32 | 8.8963 | 0.38212 | 0.1097 | 181.9963 | 0.37379 | 55.3522 | 0.094926 | 1.439 | 0.041073 | 10.4261 | 259.1115
FY33 | 40.0426 | 3.0094 | 1.3478 | 534.1892 | 16.4822 | 95.9772 | 0.57048 | 3.5258 | 0.3519 | 13.0758 | 708.5723 | FY33 | 0 | 0 | 1.3478 | 0.0038838 | 0 | 0 | 0.0028184 | 0.81266 | 0.053257 | 13.0758 | 15.2963 | FY33 | 40.0426 | 3.0094 | 0 | 0.0038838 | 0 | 0 | 0.00022241 | 0.095726 | 0.3519 | 13.0758 | 56.5795 | FY33 | 0 | 0 | 0 | 534.1892 | 0 | 0 | 0.08024 | 0.00686 | 0.037139 | 13.0758 | 547.3893 | FY33 | 40.0426 | 3.0094 | 0 | 0.0038838 | 0 | 0 | 0.0028184 | 0.095726 | 0.3519 | 0 | 43.5063 | FY33 | 0.14846 | 0.00026684 | 1.3478 | 0.0038838 | 0.14268 | 0 | 0.024702 | 0.81266 | 0.073657 | 13.0758 | 15.63 | FY33 | 40.0426 | 3.0094 | 0 | 0.0038838 | 0.39173 | 0 | 0.00022241 | 0.25794 | 0.3519 | 13.0758 | 57.1335 | FY33 | 0 | 0 | 0 | 534.1892 | 0.39173 | 0 | 0.38244 | 0.00686 | 0.053257 | 13.0758 | 548.0993 | FY33 | 40.0426 | 3.0094 | 0 | 0 | 0.39173 | 0 | 0.012445 | 0.25794 | 0.3519 | 0 | 44.066 | FY33 | 14.8607 | 0.9701 | 0.20617 | 190.9768 | 0.41318 | 59.6092 | 0.15368 | 1.9112 | 0.071155 | 11.3411 | 280.5134
FY34 | 54.1546 | 7.3453 | 1.9107 | 539.4631 | 18.3115 | 99.0912 | 0.83062 | 4.1288 | 1.0193 | 14.1965 | 740.4517 | FY34 | 0.0066067 | 0 | 1.9107 | 0.014518 | 0 | 0 | 0.0091125 | 1.0195 | 0.087351 | 14.1965 | 17.2443 | FY34 | 54.1546 | 7.3453 | 0 | 0.014518 | 0 | 0 | 0.0003681 | 0.11916 | 1.0193 | 14.1965 | 76.8497 | FY34 | 0 | 0 | 0 | 539.4631 | 0 | 0 | 0.17183 | 0.0086181 | 0.063804 | 14.1965 | 553.9038 | FY34 | 54.1546 | 7.3453 | 0 | 0.014518 | 0 | 0 | 0.0091125 | 0.11916 | 1.0193 | 0 | 62.662 | FY34 | 0.29405 | 0.072968 | 1.9107 | 0.014518 | 0.18278 | 0 | 0.076841 | 1.0195 | 0.15063 | 14.1965 | 17.9185 | FY34 | 54.1546 | 7.3453 | 0 | 0.014518 | 0.46006 | 0 | 0.0003681 | 0.34198 | 1.0193 | 14.1965 | 77.5326 | FY34 | 0.0066067 | 0 | 0 | 539.4631 | 0.46006 | 0 | 0.58815 | 0.0086181 | 0.087351 | 14.1965 | 554.8103 | FY34 | 54.1546 | 7.3453 | 0 | 0 | 0.46006 | 0 | 0.048322 | 0.34198 | 1.0193 | 0 | 63.3696 | FY34 | 21.8914 | 2.5268 | 0.27527 | 191.8255 | 0.48679 | 61.794 | 0.27561 | 2.2852 | 0.12533 | 12.3193 | 293.8052
FY35 | 66.3986 | 16.096 | 2.6181 | 540.3509 | 23.4625 | 102.4399 | 0.8878 | 4.9221 | 1.969 | 15.421 | 774.5661 | FY35 | 0.025596 | 0 | 2.6181 | 0.072888 | 0 | 0 | 0.0056189 | 1.305 | 0.19911 | 15.421 | 19.6473 | FY35 | 66.3986 | 16.096 | 0 | 0.072888 | 0 | 0 | 0.00045944 | 0.15641 | 1.969 | 15.421 | 100.1145 | FY35 | 0 | 0 | 0 | 540.3509 | 0 | 0 | 0.15043 | 0.010988 | 0.10265 | 15.421 | 556.036 | FY35 | 66.3986 | 16.096 | 0 | 0.072888 | 0 | 0 | 0.0056189 | 0.15641 | 1.969 | 0 | 84.6986 | FY35 | 0.67279 | 0.22555 | 2.6181 | 0.072888 | 0.30197 | 0 | 0.052735 | 1.305 | 0.57543 | 15.421 | 21.2455 | FY35 | 66.3986 | 16.096 | 0 | 0.072888 | 0.65653 | 0 | 0.00045944 | 0.46837 | 1.969 | 15.421 | 101.083 | FY35 | 0.025596 | 0 | 0 | 540.3509 | 0.65653 | 0 | 0.61312 | 0.010988 | 0.19911 | 15.421 | 557.2773 | FY35 | 66.3986 | 16.096 | 0 | 0 | 0.65653 | 0 | 0.027519 | 0.46837 | 1.969 | 0 | 85.6161 | FY35 | 29.1184 | 6.6675 | 0.39705 | 185.5354 | 0.6886 | 64.008 | 0.25899 | 2.7815 | 0.45119 | 13.3846 | 303.2913
FY36 | 97.2424 | 28.7239 | 3.6767 | 550.4303 | 37.7816 | 117.1795 | 0.9404 | 6.1427 | 4.2416 | 16.6981 | 863.0572 | FY36 | 0.10888 | 0.045221 | 3.6767 | 0.067816 | 0 | 0 | 0.0073864 | 1.8344 | 1.0237 | 16.6981 | 23.4622 | FY36 | 97.2424 | 28.7239 | 0 | 0.067816 | 0 | 0 | 0.00056132 | 0.23327 | 4.2416 | 16.6981 | 147.2077 | FY36 | 0 | 0 | 0 | 550.4303 | 0 | 0 | 0.13963 | 0.01473 | 0.47902 | 16.6981 | 567.7617 | FY36 | 97.2424 | 28.7239 | 0 | 0.067816 | 0 | 0 | 0.0073864 | 0.23327 | 4.2416 | 0 | 130.5164 | FY36 | 2.5253 | 0.5777 | 3.6767 | 0.067816 | 0.67397 | 0 | 0.046518 | 1.8344 | 1.7713 | 16.6981 | 27.8718 | FY36 | 97.2424 | 28.7239 | 0 | 0.067816 | 1.3534 | 0 | 0.00056132 | 0.73147 | 4.2416 | 16.6981 | 149.0593 | FY36 | 0.10888 | 0.045221 | 0 | 550.4303 | 1.3534 | 0 | 0.63573 | 0.01473 | 1.0237 | 16.6981 | 570.3101 | FY36 | 97.2424 | 28.7239 | 0 | 0 | 1.3534 | 0 | 0.025264 | 0.73147 | 4.2416 | 0 | 132.3181 | FY36 | 48.5365 | 12.3589 | 0.69885 | 199.7997 | 1.3474 | 75.9949 | 0.24744 | 3.6094 | 1.4573 | 14.5021 | 358.5524
FY37 | 82.1864 | 41.7144 | 2.1769 | 490.6258 | 43.9889 | 98.5408 | 1.2248 | 6.3566 | 6.4187 | 17.7892 | 791.0227 | FY37 | 0.11653 | 0.16036 | 2.1769 | 0.0042064 | 0 | 0 | 0.0097056 | 1.8239 | 2.0189 | 17.7892 | 24.0997 | FY37 | 82.1864 | 41.7144 | 0 | 0.0042064 | 0 | 0 | 0.00082073 | 0.24424 | 6.4187 | 17.7892 | 148.358 | FY37 | 0 | 0 | 0 | 490.6258 | 0 | 0 | 0.21635 | 0.016562 | 1.2026 | 17.7892 | 509.8506 | FY37 | 82.1864 | 41.7144 | 0 | 0.0042064 | 0 | 0 | 0.0097056 | 0.24424 | 6.4187 | 0 | 130.5777 | FY37 | 1.6056 | 1.0671 | 2.1769 | 0.0042064 | 0.81064 | 0 | 0.079577 | 1.8239 | 3.1262 | 17.7892 | 28.4833 | FY37 | 82.1864 | 41.7144 | 0 | 0.0042064 | 1.6121 | 0 | 0.00082073 | 0.71106 | 6.4187 | 17.7892 | 150.4369 | FY37 | 0.11653 | 0.16036 | 0 | 490.6258 | 1.6121 | 0 | 0.85208 | 0.016562 | 2.0189 | 17.7892 | 513.1915 | FY37 | 82.1864 | 41.7144 | 0 | 0 | 1.6121 | 0 | 0.043132 | 0.71106 | 6.4187 | 0 | 132.6858 | FY37 | 37.7559 | 18.6773 | 0.3583 | 162.0496 | 1.484 | 60.3094 | 0.36063 | 3.6423 | 2.5845 | 15.431 | 302.6528
FY38 | 118.6467 | 76.0622 | 6.8409 | 531.5785 | 79.0503 | 113.9545 | 1.7072 | 8.3111 | 10.0002 | 19.3009 | 965.4525 | FY38 | 0.26609 | 0.38516 | 6.8409 | 0.021929 | 0 | 0 | 0.016809 | 2.7644 | 3.5517 | 19.3009 | 33.1479 | FY38 | 118.6467 | 76.0622 | 0 | 0.021929 | 0 | 0 | 0.0012673 | 0.42015 | 10.0002 | 19.3009 | 224.4532 | FY38 | 0.0041476 | 0.0053447 | 0 | 531.5785 | 0 | 0 | 0.38874 | 0.023352 | 2.3492 | 19.3009 | 553.6502 | FY38 | 118.6467 | 76.0622 | 0 | 0.021929 | 0 | 0 | 0.016809 | 0.42015 | 10.0002 | 0 | 205.1679 | FY38 | 4.008 | 3.382 | 6.8409 | 0.021929 | 2.4551 | 0 | 0.17396 | 2.7644 | 5.1289 | 19.3009 | 44.0761 | FY38 | 118.6467 | 76.0622 | 0 | 0.021929 | 5.2611 | 0 | 0.0012673 | 1.2237 | 10.0002 | 19.3009 | 230.5179 | FY38 | 0.26609 | 0.38516 | 0 | 531.5785 | 5.2611 | 0 | 1.2377 | 0.023352 | 3.5517 | 19.3009 | 561.6045 | FY38 | 118.6467 | 76.0622 | 0 | 0 | 5.2611 | 0 | 0.10373 | 1.2237 | 10.0002 | 0 | 211.2976 | FY38 | 60.1181 | 38.1473 | 1.4575 | 186.3699 | 4.1807 | 72.6711 | 0.5845 | 4.9976 | 4.2248 | 16.7769 | 389.5284
FY39 | 162.1544 | 107.3756 | 8.7415 | 565.2239 | 130.1437 | 129.5956 | 1.682 | 10.4858 | 14.6936 | 20.509 | 1150.6051 | FY39 | 0.48954 | 0.8118 | 8.7415 | 0.054965 | 0 | 0 | 0.015753 | 3.9853 | 5.7963 | 20.509 | 40.4042 | FY39 | 162.1544 | 107.3756 | 0 | 0.054965 | 0 | 0 | 0.0014213 | 0.78426 | 14.6936 | 20.509 | 305.5733 | FY39 | 0.026201 | 0.073592 | 0 | 565.2239 | 0 | 0 | 0.32276 | 0.031218 | 4.1029 | 20.509 | 590.2895 | FY39 | 162.1544 | 107.3756 | 0 | 0.054965 | 0 | 0 | 0.015753 | 0.78426 | 14.6936 | 0 | 285.0786 | FY39 | 9.1344 | 7.7605 | 8.7415 | 0.054965 | 8.4248 | 0 | 0.12751 | 3.9853 | 8.0367 | 20.509 | 66.7747 | FY39 | 162.1544 | 107.3756 | 0 | 0.054965 | 16.1138 | 0 | 0.0014213 | 1.9992 | 14.6936 | 20.509 | 322.902 | FY39 | 0.48954 | 0.8118 | 0 | 565.2239 | 16.1138 | 0 | 1.1864 | 0.031218 | 5.7963 | 20.509 | 610.1619 | FY39 | 162.1544 | 107.3756 | 0 | 0 | 16.1138 | 0 | 0.072008 | 1.9992 | 14.6936 | 0 | 302.4086 | FY39 | 88.8491 | 58.303 | 2.1669 | 207.1544 | 11.7284 | 85.3484 | 0.52102 | 6.6524 | 6.5534 | 17.8099 | 485.0868
FY40 | [10 empty] | 1150.6051 | FY40 | [10 empty] | 40.4042 | FY40 | [10 empty] | 305.5733 | FY40 | [10 empty] | 590.2895 | FY40 | [10 empty] | 285.0786 | FY40 | [10 empty] | 66.7747 | FY40 | [10 empty] | 322.902 | FY40 | [10 empty] | 610.1619 | FY40 | [10 empty] | 302.4086 | FY40 | [10 empty] | 485.0868
FY41 | [10 empty] | 1150.6051 | FY41 | [10 empty] | 40.4042 | FY41 | [10 empty] | 305.5733 | FY41 | [10 empty] | 590.2895 | FY41 | [10 empty] | 285.0786 | FY41 | [10 empty] | 66.7747 | FY41 | [10 empty] | 322.902 | FY41 | [10 empty] | 610.1619 | FY41 | [10 empty] | 302.4086 | FY41 | [10 empty] | 485.0868
FY42 | [10 empty] | 1150.6051 | FY42 | [10 empty] | 40.4042 | FY42 | [10 empty] | 305.5733 | FY42 | [10 empty] | 590.2895 | FY42 | [10 empty] | 285.0786 | FY42 | [10 empty] | 66.7747 | FY42 | [10 empty] | 322.902 | FY42 | [10 empty] | 610.1619 | FY42 | [10 empty] | 302.4086 | FY42 | [10 empty] | 485.0868
FY43 | [10 empty] | 1150.6051 | FY43 | [10 empty] | 40.4042 | FY43 | [10 empty] | 305.5733 | FY43 | [10 empty] | 590.2895 | FY43 | [10 empty] | 285.0786 | FY43 | [10 empty] | 66.7747 | FY43 | [10 empty] | 322.902 | FY43 | [10 empty] | 610.1619 | FY43 | [10 empty] | 302.4086 | FY43 | [10 empty] | 485.0868
FY44 | [10 empty] | 1150.6051 | FY44 | [10 empty] | 40.4042 | FY44 | [10 empty] | 305.5733 | FY44 | [10 empty] | 590.2895 | FY44 | [10 empty] | 285.0786 | FY44 | [10 empty] | 66.7747 | FY44 | [10 empty] | 322.902 | FY44 | [10 empty] | 610.1619 | FY44 | [10 empty] | 302.4086 | FY44 | [10 empty] | 485.0868
FY45 | [10 empty] | 1150.6051 | FY45 | [10 empty] | 40.4042 | FY45 | [10 empty] | 305.5733 | FY45 | [10 empty] | 590.2895 | FY45 | [10 empty] | 285.0786 | FY45 | [10 empty] | 66.7747 | FY45 | [10 empty] | 322.902 | FY45 | [10 empty] | 610.1619 | FY45 | [10 empty] | 302.4086 | FY45 | [10 empty] | 485.0868
FY46 | [10 empty] | 1150.6051 | FY46 | [10 empty] | 40.4042 | FY46 | [10 empty] | 305.5733 | FY46 | [10 empty] | 590.2895 | FY46 | [10 empty] | 285.0786 | FY46 | [10 empty] | 66.7747 | FY46 | [10 empty] | 322.902 | FY46 | [10 empty] | 610.1619 | FY46 | [10 empty] | 302.4086 | FY46 | [10 empty] | 485.0868
FY47 | [10 empty] | 1150.6051 | FY47 | [10 empty] | 40.4042 | FY47 | [10 empty] | 305.5733 | FY47 | [10 empty] | 590.2895 | FY47 | [10 empty] | 285.0786 | FY47 | [10 empty] | 66.7747 | FY47 | [10 empty] | 322.902 | FY47 | [10 empty] | 610.1619 | FY47 | [10 empty] | 302.4086 | FY47 | [10 empty] | 485.0868
FY48 | [10 empty] | 1150.6051 | FY48 | [10 empty] | 40.4042 | FY48 | [10 empty] | 305.5733 | FY48 | [10 empty] | 590.2895 | FY48 | [10 empty] | 285.0786 | FY48 | [10 empty] | 66.7747 | FY48 | [10 empty] | 322.902 | FY48 | [10 empty] | 610.1619 | FY48 | [10 empty] | 302.4086 | FY48 | [10 empty] | 485.0868
FY49 | [10 empty] | 1150.6051 | FY49 | [10 empty] | 40.4042 | FY49 | [10 empty] | 305.5733 | FY49 | [10 empty] | 590.2895 | FY49 | [10 empty] | 285.0786 | FY49 | [10 empty] | 66.7747 | FY49 | [10 empty] | 322.902 | FY49 | [10 empty] | 610.1619 | FY49 | [10 empty] | 302.4086 | FY49 | [10 empty] | 485.0868
FY50 | [10 empty] | 1150.6051 | FY50 | [10 empty] | 40.4042 | FY50 | [10 empty] | 305.5733 | FY50 | [10 empty] | 590.2895 | FY50 | [10 empty] | 285.0786 | FY50 | [10 empty] | 66.7747 | FY50 | [10 empty] | 322.902 | FY50 | [10 empty] | 610.1619 | FY50 | [10 empty] | 302.4086 | FY50 | [10 empty] | 485.0868
FY51 | [10 empty] | 1150.6051 | FY51 | [10 empty] | 40.4042 | FY51 | [10 empty] | 305.5733 | FY51 | [10 empty] | 590.2895 | FY51 | [10 empty] | 285.0786 | FY51 | [10 empty] | 66.7747 | FY51 | [10 empty] | 322.902 | FY51 | [10 empty] | 610.1619 | FY51 | [10 empty] | 302.4086 | FY51 | [10 empty] | 485.0868
FY52 | [10 empty] | 1150.6051 | FY52 | [10 empty] | 40.4042 | FY52 | [10 empty] | 305.5733 | FY52 | [10 empty] | 590.2895 | FY52 | [10 empty] | 285.0786 | FY52 | [10 empty] | 66.7747 | FY52 | [10 empty] | 322.902 | FY52 | [10 empty] | 610.1619 | FY52 | [10 empty] | 302.4086 | FY52 | [10 empty] | 485.0868
FY53 | [10 empty] | 1150.6051 | FY53 | [10 empty] | 40.4042 | FY53 | [10 empty] | 305.5733 | FY53 | [10 empty] | 590.2895 | FY53 | [10 empty] | 285.0786 | FY53 | [10 empty] | 66.7747 | FY53 | [10 empty] | 322.902 | FY53 | [10 empty] | 610.1619 | FY53 | [10 empty] | 302.4086 | FY53 | [10 empty] | 485.0868
FY54 | [10 empty] | 1150.6051 | FY54 | [10 empty] | 40.4042 | FY54 | [10 empty] | 305.5733 | FY54 | [10 empty] | 590.2895 | FY54 | [10 empty] | 285.0786 | FY54 | [10 empty] | 66.7747 | FY54 | [10 empty] | 322.902 | FY54 | [10 empty] | 610.1619 | FY54 | [10 empty] | 302.4086 | FY54 | [10 empty] | 485.0868

## 2.3.1 Cost_Sum
$millions (real $2024) |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30
Real $2025 to real $2024 conversion factor |  | 95.36% |  |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Option 1 | bar: 3 FY27 to 4 FY28; 7 FY31
Build up
| Capex |  |  |  | 3 FY27: 0; 4 FY28: 0; 5 FY29: 0; 6 FY30: 0; 7 FY31: 0
| Opex |  |  |  | 3 FY27: 0; 4 FY28: 0; 5 FY29: 0; 6 FY30: 0; 7 FY31: 0
Summary
| Capex total |  |  |  | 3 FY27: 0; 4 FY28: 0; 5 FY29: 0; 6 FY30: 0; 7 FY31: 0
Opex total | bar: 3 FY27 to 7 FY31
Option 2 | bar: 3 FY27 to 4 FY28; 7 FY31
Capex build up
|  | Incl in capex forecast | Incl in economic analysis | Inc in Lifecycle Replacment | bar: 3 FY27 to 7 FY31
| Design | 1 | 1 | 0 | 3 FY27: C-I-C; 4 FY28: C-I-C; 5 FY29: C-I-C; 6 FY30: C-I-C; 7 FY31: C-I-C
| Internal labour | 1 | 1 | 1 | 3 FY27: C-I-C; 4 FY28: C-I-C; 5 FY29: C-I-C; 6 FY30: C-I-C; 7 FY31: C-I-C
| Materials | 1 | 1 | 0 | 3 FY27: C-I-C; 4 FY28: C-I-C; 5 FY29: C-I-C; 6 FY30: C-I-C; 7 FY31: C-I-C
| Contract costs | 1 | 1 | 1 | 3 FY27: C-I-C; 4 FY28: C-I-C; 5 FY29: C-I-C; 6 FY30: C-I-C; 7 FY31: C-I-C
| P(50) risk allowance | 1 | 1 | 1 | 3 FY27: C-I-C; 4 FY28: C-I-C; 5 FY29: C-I-C; 6 FY30: C-I-C; 7 FY31: C-I-C
| Overheads | 0 | 1 | 1 | 3 FY27: C-I-C; 4 FY28: C-I-C; 5 FY29: C-I-C; 6 FY30: C-I-C; 7 FY31: C-I-C
| Finance charges | 0 | 1 | 1 | 3 FY27: C-I-C; 4 FY28: C-I-C; 5 FY29: C-I-C; 6 FY30: C-I-C; 7 FY31: C-I-C
Capex Timing
[7 empty] | 1 | 0 | 0 | 0 | 0
Estimated Lifecycle Replacment Cost
[12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Opex build up
| Item 1 | [5 empty] | 0 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105
Item 2 | bar: 3 FY27 to 7 FY31
Item 3 | bar: 3 FY27 to 7 FY31
Summary
| Capex total |  |  |  | 0 | 0 | 72.1048 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Opex total |  |  |  | 0 | 0 | 0 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105
Option 3 | bar: 3 FY27 to 4 FY28; 7 FY31
Capex build up
|  | Incl in capex forecast | Incl in economic analysis | Inc in Lifecycle Replacment | bar: 3 FY27 to 7 FY31
| Design | 1 | 1 | 0 | 3 FY27: C-I-C; 4 FY28: C-I-C; 5 FY29: C-I-C; 6 FY30: C-I-C; 7 FY31: C-I-C
| Internal labour | 1 | 1 | 1 | 3 FY27: C-I-C; 4 FY28: C-I-C; 5 FY29: C-I-C; 6 FY30: C-I-C; 7 FY31: C-I-C
| Materials | 1 | 1 | 0 | 3 FY27: C-I-C; 4 FY28: C-I-C; 5 FY29: C-I-C; 6 FY30: C-I-C; 7 FY31: C-I-C
| Contract costs | 1 | 1 | 1 | 3 FY27: C-I-C; 4 FY28: C-I-C; 5 FY29: C-I-C; 6 FY30: C-I-C; 7 FY31: C-I-C
| P(50) risk allowance | 1 | 1 | 1 | 3 FY27: C-I-C; 4 FY28: C-I-C; 5 FY29: C-I-C; 6 FY30: C-I-C; 7 FY31: C-I-C
| Overheads | 0 | 1 | 1 | 3 FY27: C-I-C; 4 FY28: C-I-C; 5 FY29: C-I-C; 6 FY30: C-I-C; 7 FY31: C-I-C
| Finance charges | 0 | 1 | 1 | 3 FY27: C-I-C; 4 FY28: C-I-C; 5 FY29: C-I-C; 6 FY30: C-I-C; 7 FY31: C-I-C
Capex Timing
[7 empty] | 1 | 0 | 0 | 0 | 0
Estimated Lifecycle Replacment Cost
[12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Opex build up
| Item 1 | [5 empty] | 0 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525
Item 2 | bar: 3 FY27 to 7 FY31
Item 3 | bar: 3 FY27 to 7 FY31
Summary
| Capex total |  |  |  | 0 | 0 | 43.5248 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Opex total |  |  |  | 0 | 0 | 0 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525
Option 4 | bar: 3 FY27 to 4 FY28; 7 FY31
Capex build up
|  | Incl in capex forecast | Incl in economic analysis | Inc in Lifecycle Replacment | bar: 3 FY27 to 7 FY31
| Design | 1 | 1 | 0 | 3 FY27: C-I-C; 4 FY28: C-I-C; 5 FY29: C-I-C; 6 FY30: C-I-C; 7 FY31: C-I-C
| Internal labour | 1 | 1 | 1 | 3 FY27: C-I-C; 4 FY28: C-I-C; 5 FY29: C-I-C; 6 FY30: C-I-C; 7 FY31: C-I-C
| Materials | 1 | 1 | 0 | 3 FY27: C-I-C; 4 FY28: C-I-C; 5 FY29: C-I-C; 6 FY30: C-I-C; 7 FY31: C-I-C
| Contract costs | 1 | 1 | 1 | 3 FY27: C-I-C; 4 FY28: C-I-C; 5 FY29: C-I-C; 6 FY30: C-I-C; 7 FY31: C-I-C
| P(50) risk allowance | 1 | 1 | 1 | 3 FY27: C-I-C; 4 FY28: C-I-C; 5 FY29: C-I-C; 6 FY30: C-I-C; 7 FY31: C-I-C
| Overheads | 0 | 1 | 1 | 3 FY27: C-I-C; 4 FY28: C-I-C; 5 FY29: C-I-C; 6 FY30: C-I-C; 7 FY31: C-I-C
| Finance charges | 0 | 1 | 1 | 3 FY27: C-I-C; 4 FY28: C-I-C; 5 FY29: C-I-C; 6 FY30: C-I-C; 7 FY31: C-I-C
Capex Timing
[7 empty] | 1 | 0 | 0 | 0 | 0
Estimated Lifecycle Replacment Cost
[12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Opex build up
| Item 1 | [5 empty] | 0 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545
Item 2 | bar: 3 FY27 to 7 FY31
Item 3 | bar: 3 FY27 to 7 FY31
Summary
| Capex total |  |  |  | 0 | 0 | 59.5447 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Opex total |  |  |  | 0 | 0 | 0 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545
Option 5 | bar: 3 FY27 to 4 FY28; 7 FY31
Capex build up
|  | Incl in capex forecast | Incl in economic analysis | Inc in Lifecycle Replacment | bar: 3 FY27 to 7 FY31
| Design | 1 | 1 | 0 | 3 FY27: C-I-C; 4 FY28: C-I-C; 5 FY29: C-I-C; 6 FY30: C-I-C; 7 FY31: C-I-C
| Internal labour | 1 | 1 | 1 | 3 FY27: C-I-C; 4 FY28: C-I-C; 5 FY29: C-I-C; 6 FY30: C-I-C; 7 FY31: C-I-C
| Materials | 1 | 1 | 0 | 3 FY27: C-I-C; 4 FY28: C-I-C; 5 FY29: C-I-C; 6 FY30: C-I-C; 7 FY31: C-I-C
| Contract costs | 1 | 1 | 1 | 3 FY27: C-I-C; 4 FY28: C-I-C; 5 FY29: C-I-C; 6 FY30: C-I-C; 7 FY31: C-I-C
| P(50) risk allowance | 1 | 1 | 1 | 3 FY27: C-I-C; 4 FY28: C-I-C; 5 FY29: C-I-C; 6 FY30: C-I-C; 7 FY31: C-I-C
| Overheads | 0 | 1 | 1 | 3 FY27: C-I-C; 4 FY28: C-I-C; 5 FY29: C-I-C; 6 FY30: C-I-C; 7 FY31: C-I-C
| Finance charges | 0 | 1 | 1 | 3 FY27: C-I-C; 4 FY28: C-I-C; 5 FY29: C-I-C; 6 FY30: C-I-C; 7 FY31: C-I-C
Capex Timing
[7 empty] | 1 | 0 | 0 | 0 | 0
Estimated Lifecycle Replacment Cost
[12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Opex build up
| Item 1 | [5 empty] | 0 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705
Item 2 | bar: 3 FY27 to 7 FY31
Item 3 | bar: 3 FY27 to 7 FY31
Summary
| Capex total |  |  |  | 0 | 0 | 55.7046 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Opex total |  |  |  | 0 | 0 | 0 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705
Option 6 | bar: 3 FY27 to 4 FY28; 7 FY31
Capex build up
|  | Incl in capex forecast | Incl in economic analysis | Inc in Lifecycle Replacment | bar: 3 FY27 to 7 FY31
| Design | 1 | 1 | 0 | 3 FY27: C-I-C; 4 FY28: C-I-C; 5 FY29: C-I-C; 6 FY30: C-I-C; 7 FY31: C-I-C
| Internal labour | 1 | 1 | 1 | 3 FY27: C-I-C; 4 FY28: C-I-C; 5 FY29: C-I-C; 6 FY30: C-I-C; 7 FY31: C-I-C
| Materials | 1 | 1 | 0 | 3 FY27: C-I-C; 4 FY28: C-I-C; 5 FY29: C-I-C; 6 FY30: C-I-C; 7 FY31: C-I-C
| Contract costs | 1 | 1 | 1 | 3 FY27: C-I-C; 4 FY28: C-I-C; 5 FY29: C-I-C; 6 FY30: C-I-C; 7 FY31: C-I-C
| P(50) risk allowance | 1 | 1 | 1 | 3 FY27: C-I-C; 4 FY28: C-I-C; 5 FY29: C-I-C; 6 FY30: C-I-C; 7 FY31: C-I-C
| Overheads | 0 | 1 | 1 | 3 FY27: C-I-C; 4 FY28: C-I-C; 5 FY29: C-I-C; 6 FY30: C-I-C; 7 FY31: C-I-C
| Finance charges | 0 | 1 | 1 | 3 FY27: C-I-C; 4 FY28: C-I-C; 5 FY29: C-I-C; 6 FY30: C-I-C; 7 FY31: C-I-C
Capex Timing
[7 empty] | 1 | 0 | 0 | 0 | 0
Estimated Lifecycle Replacment Cost
[12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Opex build up
| Item 1 | [5 empty] | 0 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185
Item 2 | bar: 3 FY27 to 7 FY31
Item 3 | bar: 3 FY27 to 7 FY31
Summary
| Capex total |  |  |  | 0 | 0 | 68.1854 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Opex total |  |  |  | 0 | 0 | 0 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185
Option 7
Capex build up
|  | Incl in capex forecast | Incl in economic analysis | Inc in Lifecycle Replacment | bar: 3 FY27 to 7 FY31
| Design | 1 | 1 | 0 | 3 FY27: C-I-C; 4 FY28: C-I-C; 5 FY29: C-I-C; 6 FY30: C-I-C; 7 FY31: C-I-C
| Internal labour | 1 | 1 | 1 | 3 FY27: C-I-C; 4 FY28: C-I-C; 5 FY29: C-I-C; 6 FY30: C-I-C; 7 FY31: C-I-C
| Materials | 1 | 1 | 0 | 3 FY27: C-I-C; 4 FY28: C-I-C; 5 FY29: C-I-C; 6 FY30: C-I-C; 7 FY31: C-I-C
| Contract costs | 1 | 1 | 1 | 3 FY27: C-I-C; 4 FY28: C-I-C; 5 FY29: C-I-C; 6 FY30: C-I-C; 7 FY31: C-I-C
| P(50) risk allowance | 1 | 1 | 1 | 3 FY27: C-I-C; 4 FY28: C-I-C; 5 FY29: C-I-C; 6 FY30: C-I-C; 7 FY31: C-I-C
| Overheads | 0 | 1 | 1 | 3 FY27: C-I-C; 4 FY28: C-I-C; 5 FY29: C-I-C; 6 FY30: C-I-C; 7 FY31: C-I-C
| Finance charges | 0 | 1 | 1 | 3 FY27: C-I-C; 4 FY28: C-I-C; 5 FY29: C-I-C; 6 FY30: C-I-C; 7 FY31: C-I-C
Capex Timing
[7 empty] | 1 | 0 | 0 | 0 | 0
Estimated Lifecycle Replacment Cost
[12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Opex build up
| Item 1 | [5 empty] | 0 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022
Item 2 | bar: 3 FY27 to 7 FY31
Item 3 | bar: 3 FY27 to 7 FY31
Summary
| Capex total |  |  |  | 0 | 0 | 37.0224 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Opex total |  |  |  | 0 | 0 | 0 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022
Option 8
Capex build up
|  | Incl in capex forecast | Incl in economic analysis | Inc in Lifecycle Replacment | bar: 3 FY27 to 7 FY31
| Design | 1 | 1 | 0 | 3 FY27: C-I-C; 4 FY28: C-I-C; 5 FY29: C-I-C; 6 FY30: C-I-C; 7 FY31: C-I-C
| Internal labour | 1 | 1 | 1 | 3 FY27: C-I-C; 4 FY28: C-I-C; 5 FY29: C-I-C; 6 FY30: C-I-C; 7 FY31: C-I-C
| Materials | 1 | 1 | 0 | 3 FY27: C-I-C; 4 FY28: C-I-C; 5 FY29: C-I-C; 6 FY30: C-I-C; 7 FY31: C-I-C
| Contract costs | 1 | 1 | 1 | 3 FY27: C-I-C; 4 FY28: C-I-C; 5 FY29: C-I-C; 6 FY30: C-I-C; 7 FY31: C-I-C
| P(50) risk allowance | 1 | 1 | 1 | 3 FY27: C-I-C; 4 FY28: C-I-C; 5 FY29: C-I-C; 6 FY30: C-I-C; 7 FY31: C-I-C
| Overheads | 0 | 1 | 1 | 3 FY27: C-I-C; 4 FY28: C-I-C; 5 FY29: C-I-C; 6 FY30: C-I-C; 7 FY31: C-I-C
| Finance charges | 0 | 1 | 1 | 3 FY27: C-I-C; 4 FY28: C-I-C; 5 FY29: C-I-C; 6 FY30: C-I-C; 7 FY31: C-I-C
Capex Timing
[7 empty] | 1 | 0 | 0 | 0 | 0
Estimated Lifecycle Replacment Cost
[12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Opex build up
| Item 1 | [5 empty] | 0 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042
Item 2 | bar: 3 FY27 to 7 FY31
Item 3 | bar: 3 FY27 to 7 FY31
Summary
| Capex total |  |  |  | 0 | 0 | 53.0422 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Opex total |  |  |  | 0 | 0 | 0 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042
Option 9
Capex build up
|  | Incl in capex forecast | Incl in economic analysis | Inc in Lifecycle Replacment | bar: 3 FY27 to 7 FY31
| Design | 1 | 1 | 0 | 3 FY27: C-I-C; 4 FY28: C-I-C; 5 FY29: C-I-C; 6 FY30: C-I-C; 7 FY31: C-I-C
| Internal labour | 1 | 1 | 1 | 3 FY27: C-I-C; 4 FY28: C-I-C; 5 FY29: C-I-C; 6 FY30: C-I-C; 7 FY31: C-I-C
| Materials | 1 | 1 | 0 | 3 FY27: C-I-C; 4 FY28: C-I-C; 5 FY29: C-I-C; 6 FY30: C-I-C; 7 FY31: C-I-C
| Contract costs | 1 | 1 | 1 | 3 FY27: C-I-C; 4 FY28: C-I-C; 5 FY29: C-I-C; 6 FY30: C-I-C; 7 FY31: C-I-C
| P(50) risk allowance | 1 | 1 | 1 | 3 FY27: C-I-C; 4 FY28: C-I-C; 5 FY29: C-I-C; 6 FY30: C-I-C; 7 FY31: C-I-C
| Overheads | 0 | 1 | 1 | 3 FY27: C-I-C; 4 FY28: C-I-C; 5 FY29: C-I-C; 6 FY30: C-I-C; 7 FY31: C-I-C
| Finance charges | 0 | 1 | 1 | 3 FY27: C-I-C; 4 FY28: C-I-C; 5 FY29: C-I-C; 6 FY30: C-I-C; 7 FY31: C-I-C
Capex Timing
[7 empty] | 1 | 0 | 0 | 0 | 0
Estimated Lifecycle Replacment Cost
[12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Opex build up
| Item 1 | [5 empty] | 0 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202
Item 2 | bar: 3 FY27 to 7 FY31
Item 3 | bar: 3 FY27 to 7 FY31
Summary
| Capex total |  |  |  | 0 | 0 | 49.2021 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Opex total |  |  |  | 0 | 0 | 0 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202
Option 10
Capex build up
|  | Incl in capex forecast | Incl in economic analysis | Inc in Lifecycle Replacment | bar: 3 FY27 to 7 FY31
| Design | 1 | 1 | 0 | 3 FY27: C-I-C; 4 FY28: C-I-C; 5 FY29: C-I-C; 6 FY30: C-I-C; 7 FY31: C-I-C
| Internal labour | 1 | 1 | 1 | 3 FY27: C-I-C; 4 FY28: C-I-C; 5 FY29: C-I-C; 6 FY30: C-I-C; 7 FY31: C-I-C
| Materials | 1 | 1 | 0 | 3 FY27: C-I-C; 4 FY28: C-I-C; 5 FY29: C-I-C; 6 FY30: C-I-C; 7 FY31: C-I-C
| Contract costs | 1 | 1 | 1 | 3 FY27: C-I-C; 4 FY28: C-I-C; 5 FY29: C-I-C; 6 FY30: C-I-C; 7 FY31: C-I-C
| P(50) risk allowance | 1 | 1 | 1 | 3 FY27: C-I-C; 4 FY28: C-I-C; 5 FY29: C-I-C; 6 FY30: C-I-C; 7 FY31: C-I-C
| Overheads | 0 | 1 | 1 | 3 FY27: C-I-C; 4 FY28: C-I-C; 5 FY29: C-I-C; 6 FY30: C-I-C; 7 FY31: C-I-C
| Finance charges | 0 | 1 | 1 | 3 FY27: C-I-C; 4 FY28: C-I-C; 5 FY29: C-I-C; 6 FY30: C-I-C; 7 FY31: C-I-C
Capex Timing
[7 empty] | 1 | 0 | 0 | 0 | 0
Estimated Lifecycle Replacment Cost
[12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Opex build up
| Item 1 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Item 2 |  |  |  | 0.48285 | 57.8283 | 189.4866 | 207.6844 | 245.4848 | 279.2209 | 339.624 | 384.4625 | 426.7802 | 445.1879 | 469.6214 | 502.6026 | 486.2654 | 573.3683 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055
Item 3 | bar: 3 FY27 to 7 FY31
Summary
| Capex total |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Opex total |  |  |  | 0.48285 | 57.8283 | 189.4866 | 207.6844 | 245.4848 | 279.2209 | 339.624 | 384.4625 | 426.7802 | 445.1879 | 469.6214 | 502.6026 | 486.2654 | 573.3683 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055

## 2.3.2 Option2 Cost
Dollar Basis
New Pakenham Sth ZSS + 4 Feeders |  | Real $2025
PROJECT EXPENDITURE FORECASTS | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | TOTAL | Design | 1 | 1 | C-I-C
DESIGN | 0 | 0 | 0 | 0 | 0 | 0 | C-I-C | Internal labour | 1 | 1 | C-I-C
INTERNAL LABOUR | 0 | 0 | 0 | 0 | 0 | 0 | C-I-C | Materials | 1 | 1 | C-I-C
MATERIALS | 0 | 0 | 0 | 0 | 0 | 0 | C-I-C | Contract costs | 1 | 1 | C-I-C
CONTRACT COSTS | 0 | 0 | 0 | 0 | 0 | 0 | C-I-C | P(50) risk allowance | 1 | 1 | C-I-C
PROJECT DIRECT EXPENDITURE | 0 | 0 | 0 | 0 | 0 | 0 | C-I-C | Overheads | 1 | 1 | C-I-C
P50 RISK | 0 | 0 | 0 | 0 | 0 | 0 | C-I-C | Finance charges | 0 | 0 | C-I-C
DIRECT + P50 RISK | 0 | 0 | 0 | 0 | 0 | 0 | C-I-C
OVERHEADS | 0 | 0 | 0 | 0 | 0 | 0 | C-I-C
FINANCE CHARGES | 0 | 0 | 0 | 0 | 0 | 0 | C-I-C
Direct + P50 RISK + INDIRECTS | 0 | 0 | 0 | 0 | 0 | 0 | C-I-C
P90-P50 RISK | 0 | 0 | 0 | 0 | 0 | 0 | C-I-C
DIRECT + P90 RISK + INDIRECTS | 0 | 0 | 0 | 0 | 0 | 0 | C-I-C

## 2.3.3 Option3 Cost
Dollar Basis
New PHM 3rd Tx & Switchroom with 3 feeders |  | Real $2025
PROJECT EXPENDITURE FORECASTS | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | TOTAL | Design | 1 | 1 | C-I-C
DESIGN | 0 | 0 | 0 | 0 | 0 | 0 | C-I-C | Internal labour | 1 | 1 | C-I-C
INTERNAL LABOUR | 0 | 0 | 0 | 0 | 0 | 0 | C-I-C | Materials | 1 | 1 | C-I-C
MATERIALS | 0 | 0 | 0 | 0 | 0 | 0 | C-I-C | Contract costs | 1 | 1 | C-I-C
CONTRACT COSTS | 0 | 0 | 0 | 0 | 0 | 0 | C-I-C | P(50) risk allowance | 1 | 1 | C-I-C
PROJECT DIRECT EXPENDITURE | 0 | 0 | 0 | 0 | 0 | 0 | C-I-C | Overheads | 1 | 1 | C-I-C
P50 RISK | 0 | 0 | 0 | 0 | 0 | 0 | C-I-C | Finance charges | 0 | 0 | C-I-C
DIRECT + P50 RISK | 0 | 0 | 0 | 0 | 0 | 0 | C-I-C
OVERHEADS | 0 | 0 | 0 | 0 | 0 | 0 | C-I-C
FINANCE CHARGES | 0 | 0 | 0 | 0 | 0 | 0 | C-I-C
Direct + P50 RISK + INDIRECTS | 0 | 0 | 0 | 0 | 0 | 0 | C-I-C
P90-P50 RISK | 0 | 0 | 0 | 0 | 0 | 0 | C-I-C
DIRECT + P90 RISK + INDIRECTS | 0 | 0 | 0 | 0 | 0 | 0 | C-I-C
Dollar Basis
OFR12 22kV Feeder |  | Real $2025
PROJECT EXPENDITURE FORECASTS | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | TOTAL
DESIGN | 0 | 0 | 0 | 0 | 0 | 0 | C-I-C
INTERNAL LABOUR | 0 | 0 | 0 | 0 | 0 | 0 | C-I-C
MATERIALS | 0 | 0 | 0 | 0 | 0 | 0 | C-I-C
CONTRACT COSTS | 0 | 0 | 0 | 0 | 0 | 0 | C-I-C
PROJECT DIRECT EXPENDITURE | 0 | 0 | 0 | 0 | 0 | 0 | C-I-C
P50 RISK | 0 | 0 | 0 | 0 | 0 | 0 | C-I-C
DIRECT + P50 RISK | 0 | 0 | 0 | 0 | 0 | 0 | C-I-C
OVERHEADS | 0 | 0 | 0 | 0 | 0 | 0 | C-I-C
FINANCE CHARGES | 0 | 0 | 0 | 0 | 0 | 0 | C-I-C
Direct + P50 RISK + INDIRECTS | 0 | 0 | 0 | 0 | 0 | 0 | C-I-C
P90-P50 RISK | 0 | 0 | 0 | 0 | 0 | 0 | C-I-C
DIRECT + P90 RISK + INDIRECTS | 0 | 0 | 0 | 0 | 0 | 0 | C-I-C

## 2.3.4 Option4 Cost
Dollar Basis
New OFR 3rd Tx & Switchroom with 3 feeders |  | Real $2025
PROJECT EXPENDITURE FORECASTS | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | TOTAL | Design | 1 | 1 | C-I-C
DESIGN | 0 | 0 | 0 | 0 | 0 | 0 | C-I-C | Internal labour | 1 | 1 | C-I-C
INTERNAL LABOUR | 0 | 0 | 0 | 0 | 0 | 0 | C-I-C | Materials | 1 | 1 | C-I-C
MATERIALS | 0 | 0 | 0 | 0 | 0 | 0 | C-I-C | Contract costs | 1 | 1 | C-I-C
CONTRACT COSTS | 0 | 0 | 0 | 0 | 0 | 0 | C-I-C | P(50) risk allowance | 1 | 1 | C-I-C
PROJECT DIRECT EXPENDITURE | 0 | 0 | 0 | 0 | 0 | 0 | C-I-C | Overheads | 1 | 1 | C-I-C
P50 RISK | 0 | 0 | 0 | 0 | 0 | 0 | C-I-C | Finance charges | 0 | 0 | C-I-C
DIRECT + P50 RISK | 0 | 0 | 0 | 0 | 0 | 0 | C-I-C
OVERHEADS | 0 | 0 | 0 | 0 | 0 | 0 | C-I-C
FINANCE CHARGES | 0 | 0 | 0 | 0 | 0 | 0 | C-I-C
Direct + P50 RISK + INDIRECTS | 0 | 0 | 0 | 0 | 0 | 0 | C-I-C
P90-P50 RISK | 0 | 0 | 0 | 0 | 0 | 0 | C-I-C
DIRECT + P90 RISK + INDIRECTS | 0 | 0 | 0 | 0 | 0 | 0 | C-I-C
Dollar Basis
OFR12 22kV Feeder |  | Real $2025
PROJECT EXPENDITURE FORECASTS | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | TOTAL
DESIGN | 0 | 0 | 0 | 0 | 0 | 0 | C-I-C
INTERNAL LABOUR | 0 | 0 | 0 | 0 | 0 | 0 | C-I-C
MATERIALS | 0 | 0 | 0 | 0 | 0 | 0 | C-I-C
CONTRACT COSTS | 0 | 0 | 0 | 0 | 0 | 0 | C-I-C
PROJECT DIRECT EXPENDITURE | 0 | 0 | 0 | 0 | 0 | 0 | C-I-C
P50 RISK | 0 | 0 | 0 | 0 | 0 | 0 | C-I-C
DIRECT + P50 RISK | 0 | 0 | 0 | 0 | 0 | 0 | C-I-C
OVERHEADS | 0 | 0 | 0 | 0 | 0 | 0 | C-I-C
FINANCE CHARGES | 0 | 0 | 0 | 0 | 0 | 0 | C-I-C
Direct + P50 RISK + INDIRECTS | 0 | 0 | 0 | 0 | 0 | 0 | C-I-C
P90-P50 RISK | 0 | 0 | 0 | 0 | 0 | 0 | C-I-C
DIRECT + P90 RISK + INDIRECTS | 0 | 0 | 0 | 0 | 0 | 0 | C-I-C

## 2.3.5 Option5 Cost
Dollar Basis
New LLG 3rd Tx & Switchroom with 3 feeders |  | Real $2025
PROJECT EXPENDITURE FORECASTS | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | TOTAL | Design | 1 | 1 | C-I-C
DESIGN | 0 | 0 | 0 | 0 | 0 | 0 | C-I-C | Internal labour | 1 | 1 | C-I-C
INTERNAL LABOUR | 0 | 0 | 0 | 0 | 0 | 0 | C-I-C | Materials | 1 | 1 | C-I-C
MATERIALS | 0 | 0 | 0 | 0 | 0 | 0 | C-I-C | Contract costs | 1 | 1 | C-I-C
CONTRACT COSTS | 0 | 0 | 0 | 0 | 0 | 0 | C-I-C | P(50) risk allowance | 1 | 1 | C-I-C
PROJECT DIRECT EXPENDITURE | 0 | 0 | 0 | 0 | 0 | 0 | C-I-C | Overheads | 1 | 1 | C-I-C
P50 RISK | 0 | 0 | 0 | 0 | 0 | 0 | C-I-C | Finance charges | 0 | 0 | C-I-C
DIRECT + P50 RISK | 0 | 0 | 0 | 0 | 0 | 0 | C-I-C
OVERHEADS | 0 | 0 | 0 | 0 | 0 | 0 | C-I-C
FINANCE CHARGES | 0 | 0 | 0 | 0 | 0 | 0 | C-I-C
Direct + P50 RISK + INDIRECTS | 0 | 0 | 0 | 0 | 0 | 0 | C-I-C
P90-P50 RISK | 0 | 0 | 0 | 0 | 0 | 0 | C-I-C
DIRECT + P90 RISK + INDIRECTS | 0 | 0 | 0 | 0 | 0 | 0 | C-I-C
Dollar Basis
OFR12 22kV Feeder |  | Real $2025
PROJECT EXPENDITURE FORECASTS | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | TOTAL
DESIGN | 0 | 0 | 0 | 0 | 0 | 0 | C-I-C
INTERNAL LABOUR | 0 | 0 | 0 | 0 | 0 | 0 | C-I-C
MATERIALS | 0 | 0 | 0 | 0 | 0 | 0 | C-I-C
CONTRACT COSTS | 0 | 0 | 0 | 0 | 0 | 0 | C-I-C
PROJECT DIRECT EXPENDITURE | 0 | 0 | 0 | 0 | 0 | 0 | C-I-C
P50 RISK | 0 | 0 | 0 | 0 | 0 | 0 | C-I-C
DIRECT + P50 RISK | 0 | 0 | 0 | 0 | 0 | 0 | C-I-C
OVERHEADS | 0 | 0 | 0 | 0 | 0 | 0 | C-I-C
FINANCE CHARGES | 0 | 0 | 0 | 0 | 0 | 0 | C-I-C
Direct + P50 RISK + INDIRECTS | 0 | 0 | 0 | 0 | 0 | 0 | C-I-C
P90-P50 RISK | 0 | 0 | 0 | 0 | 0 | 0 | C-I-C
DIRECT + P90 RISK + INDIRECTS | 0 | 0 | 0 | 0 | 0 | 0 | C-I-C

## 2.3.6 Option6 Cost
Dollar Basis
New Pakenham Sth ZSS with 3 feeders |  | Real $2025
PROJECT EXPENDITURE FORECASTS | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | TOTAL | Design | 1 | 1 | C-I-C
DESIGN | 0 | 0 | 0 | 0 | 0 | 0 | C-I-C | Internal labour | 1 | 1 | C-I-C
INTERNAL LABOUR | 0 | 0 | 0 | 0 | 0 | 0 | C-I-C | Materials | 1 | 1 | C-I-C
MATERIALS | 0 | 0 | 0 | 0 | 0 | 0 | C-I-C | Contract costs | 1 | 1 | C-I-C
CONTRACT COSTS | 0 | 0 | 0 | 0 | 0 | 0 | C-I-C | P(50) risk allowance | 1 | 1 | C-I-C
PROJECT DIRECT EXPENDITURE | 0 | 0 | 0 | 0 | 0 | 0 | C-I-C | Overheads | 1 | 1 | C-I-C
P50 RISK | 0 | 0 | 0 | 0 | 0 | 0 | C-I-C | Finance charges | 0 | 0 | C-I-C
DIRECT + P50 RISK | 0 | 0 | 0 | 0 | 0 | 0 | C-I-C
OVERHEADS | 0 | 0 | 0 | 0 | 0 | 0 | C-I-C
FINANCE CHARGES | 0 | 0 | 0 | 0 | 0 | 0 | C-I-C
Direct + P50 RISK + INDIRECTS | 0 | 0 | 0 | 0 | 0 | 0 | C-I-C
P90-P50 RISK | 0 | 0 | 0 | 0 | 0 | 0 | C-I-C
DIRECT + P90 RISK + INDIRECTS | 0 | 0 | 0 | 0 | 0 | 0 | C-I-C

## 2.3.7 Option7 Cost
Dollar Basis
New PHM 3rd Tx & Switchroom with 2 Feeders |  | Real $2025
PROJECT EXPENDITURE FORECASTS | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | TOTAL | Design | 1 | 1 | C-I-C
DESIGN | 0 | 0 | 0 | 0 | 0 | 0 | C-I-C | Internal labour | 1 | 1 | C-I-C
INTERNAL LABOUR | 0 | 0 | 0 | 0 | 0 | 0 | C-I-C | Materials | 1 | 1 | C-I-C
MATERIALS | 0 | 0 | 0 | 0 | 0 | 0 | C-I-C | Contract costs | 1 | 1 | C-I-C
CONTRACT COSTS | 0 | 0 | 0 | 0 | 0 | 0 | C-I-C | P(50) risk allowance | 1 | 1 | C-I-C
PROJECT DIRECT EXPENDITURE | 0 | 0 | 0 | 0 | 0 | 0 | C-I-C | Overheads | 1 | 1 | C-I-C
P50 RISK | 0 | 0 | 0 | 0 | 0 | 0 | C-I-C | Finance charges | 0 | 0 | C-I-C
DIRECT + P50 RISK | 0 | 0 | 0 | 0 | 0 | 0 | C-I-C
OVERHEADS | 0 | 0 | 0 | 0 | 0 | 0 | C-I-C
FINANCE CHARGES | 0 | 0 | 0 | 0 | 0 | 0 | C-I-C
Direct + P50 RISK + INDIRECTS | 0 | 0 | 0 | 0 | 0 | 0 | C-I-C
P90-P50 RISK | 0 | 0 | 0 | 0 | 0 | 0 | C-I-C
DIRECT + P90 RISK + INDIRECTS | 0 | 0 | 0 | 0 | 0 | 0 | C-I-C
Dollar Basis
OFR12 22kV Feeder |  | Real $2025
PROJECT EXPENDITURE FORECASTS | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | TOTAL
DESIGN | 0 | 0 | 0 | 0 | 0 | 0 | C-I-C
INTERNAL LABOUR | 0 | 0 | 0 | 0 | 0 | 0 | C-I-C
MATERIALS | 0 | 0 | 0 | 0 | 0 | 0 | C-I-C
CONTRACT COSTS | 0 | 0 | 0 | 0 | 0 | 0 | C-I-C
PROJECT DIRECT EXPENDITURE | 0 | 0 | 0 | 0 | 0 | 0 | C-I-C
P50 RISK | 0 | 0 | 0 | 0 | 0 | 0 | C-I-C
DIRECT + P50 RISK | 0 | 0 | 0 | 0 | 0 | 0 | C-I-C
OVERHEADS | 0 | 0 | 0 | 0 | 0 | 0 | C-I-C
FINANCE CHARGES | 0 | 0 | 0 | 0 | 0 | 0 | C-I-C
Direct + P50 RISK + INDIRECTS | 0 | 0 | 0 | 0 | 0 | 0 | C-I-C
P90-P50 RISK | 0 | 0 | 0 | 0 | 0 | 0 | C-I-C
DIRECT + P90 RISK + INDIRECTS | 0 | 0 | 0 | 0 | 0 | 0 | C-I-C

## 2.3.8 Option8 Cost
Dollar Basis
New OFR 3rd Tx & Switchroom with 2 feeders |  | Real $2025
PROJECT EXPENDITURE FORECASTS | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | TOTAL | Design | 1 | 1 | C-I-C
DESIGN | 0 | 0 | 0 | 0 | 0 | 0 | C-I-C | Internal labour | 1 | 1 | C-I-C
INTERNAL LABOUR | 0 | 0 | 0 | 0 | 0 | 0 | C-I-C | Materials | 1 | 1 | C-I-C
MATERIALS | 0 | 0 | 0 | 0 | 0 | 0 | C-I-C | Contract costs | 1 | 1 | C-I-C
CONTRACT COSTS | 0 | 0 | 0 | 0 | 0 | 0 | C-I-C | P(50) risk allowance | 1 | 1 | C-I-C
PROJECT DIRECT EXPENDITURE | 0 | 0 | 0 | 0 | 0 | 0 | C-I-C | Overheads | 1 | 1 | C-I-C
P50 RISK | 0 | 0 | 0 | 0 | 0 | 0 | C-I-C | Finance charges | 0 | 0 | C-I-C
DIRECT + P50 RISK | 0 | 0 | 0 | 0 | 0 | 0 | C-I-C
OVERHEADS | 0 | 0 | 0 | 0 | 0 | 0 | C-I-C
FINANCE CHARGES | 0 | 0 | 0 | 0 | 0 | 0 | C-I-C
Direct + P50 RISK + INDIRECTS | 0 | 0 | 0 | 0 | 0 | 0 | C-I-C
P90-P50 RISK | 0 | 0 | 0 | 0 | 0 | 0 | C-I-C
DIRECT + P90 RISK + INDIRECTS | 0 | 0 | 0 | 0 | 0 | 0 | C-I-C
Dollar Basis
OFR12 22kV Feeder |  | Real $2025
PROJECT EXPENDITURE FORECASTS | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | TOTAL
DESIGN | 0 | 0 | 0 | 0 | 0 | 0 | C-I-C
INTERNAL LABOUR | 0 | 0 | 0 | 0 | 0 | 0 | C-I-C
MATERIALS | 0 | 0 | 0 | 0 | 0 | 0 | C-I-C
CONTRACT COSTS | 0 | 0 | 0 | 0 | 0 | 0 | C-I-C
PROJECT DIRECT EXPENDITURE | 0 | 0 | 0 | 0 | 0 | 0 | C-I-C
P50 RISK | 0 | 0 | 0 | 0 | 0 | 0 | C-I-C
DIRECT + P50 RISK | 0 | 0 | 0 | 0 | 0 | 0 | C-I-C
OVERHEADS | 0 | 0 | 0 | 0 | 0 | 0 | C-I-C
FINANCE CHARGES | 0 | 0 | 0 | 0 | 0 | 0 | C-I-C
Direct + P50 RISK + INDIRECTS | 0 | 0 | 0 | 0 | 0 | 0 | C-I-C
P90-P50 RISK | 0 | 0 | 0 | 0 | 0 | 0 | C-I-C
DIRECT + P90 RISK + INDIRECTS | 0 | 0 | 0 | 0 | 0 | 0 | C-I-C

## 2.3.9 Option9 Cost
Dollar Basis
New LLG 3rd Tx & Switchroom with 2 feeders |  | Real $2025
PROJECT EXPENDITURE FORECASTS | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | TOTAL | Design | 1 | 1 | C-I-C
DESIGN | 0 | 0 | 0 | 0 | 0 | 0 | C-I-C | Internal labour | 1 | 1 | C-I-C
INTERNAL LABOUR | 0 | 0 | 0 | 0 | 0 | 0 | C-I-C | Materials | 1 | 1 | C-I-C
MATERIALS | 0 | 0 | 0 | 0 | 0 | 0 | C-I-C | Contract costs | 1 | 1 | C-I-C
CONTRACT COSTS | 0 | 0 | 0 | 0 | 0 | 0 | C-I-C | P(50) risk allowance | 1 | 1 | C-I-C
PROJECT DIRECT EXPENDITURE | 0 | 0 | 0 | 0 | 0 | 0 | C-I-C | Overheads | 1 | 1 | C-I-C
P50 RISK | 0 | 0 | 0 | 0 | 0 | 0 | C-I-C | Finance charges | 0 | 0 | C-I-C
DIRECT + P50 RISK | 0 | 0 | 0 | 0 | 0 | 0 | C-I-C
OVERHEADS | 0 | 0 | 0 | 0 | 0 | 0 | C-I-C
FINANCE CHARGES | 0 | 0 | 0 | 0 | 0 | 0 | C-I-C
Direct + P50 RISK + INDIRECTS | 0 | 0 | 0 | 0 | 0 | 0 | C-I-C
P90-P50 RISK | 0 | 0 | 0 | 0 | 0 | 0 | C-I-C
DIRECT + P90 RISK + INDIRECTS | 0 | 0 | 0 | 0 | 0 | 0 | C-I-C
Dollar Basis
OFR12 22kV Feeder |  | Real $2025
PROJECT EXPENDITURE FORECASTS | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | TOTAL
DESIGN | 0 | 0 | 0 | 0 | 0 | 0 | C-I-C
INTERNAL LABOUR | 0 | 0 | 0 | 0 | 0 | 0 | C-I-C
MATERIALS | 0 | 0 | 0 | 0 | 0 | 0 | C-I-C
CONTRACT COSTS | 0 | 0 | 0 | 0 | 0 | 0 | C-I-C
PROJECT DIRECT EXPENDITURE | 0 | 0 | 0 | 0 | 0 | 0 | C-I-C
P50 RISK | 0 | 0 | 0 | 0 | 0 | 0 | C-I-C
DIRECT + P50 RISK | 0 | 0 | 0 | 0 | 0 | 0 | C-I-C
OVERHEADS | 0 | 0 | 0 | 0 | 0 | 0 | C-I-C
FINANCE CHARGES | 0 | 0 | 0 | 0 | 0 | 0 | C-I-C
Direct + P50 RISK + INDIRECTS | 0 | 0 | 0 | 0 | 0 | 0 | C-I-C
P90-P50 RISK | 0 | 0 | 0 | 0 | 0 | 0 | C-I-C
DIRECT + P90 RISK + INDIRECTS | 0 | 0 | 0 | 0 | 0 | 0 | C-I-C

## 2.3.10 Option10 Cost (hidden)
Dollar Basis
Not Used | Real $2025
PROJECT EXPENDITURE FORECASTS | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | TOTAL | Design | 1 | 1 | 0
DESIGN | 0 | 0 | 0 | 0 | 0 | 0 |  | Internal labour | 1 | 1 | 0
INTERNAL LABOUR | 0 | 0 | 0 | 0 | 0 | 0 |  | Materials | 1 | 1 | 0
MATERIALS | 0 | 0 | 0 | 0 | 0 | 0 |  | Contract costs | 1 | 1 | 0
CONTRACT COSTS | 0 | 0 | 0 | 0 | 0 | 0 |  | P(50) risk allowance | 1 | 1 | 0
PROJECT DIRECT EXPENDITURE | 0 | 0 | 0 | 0 | 0 | 0 |  | Overheads | 1 | 1 | 0
P50 RISK | 0 | 0 | 0 | 0 | 0 | 0 |  | Finance charges | 0 | 0 | 0
DIRECT + P50 RISK | 0 | 0 | 0 | 0 | 0 | 0
OVERHEADS | 0 | 0 | 0 | 0 | 0 | 0
FINANCE CHARGES | 0 | 0 | 0 | 0 | 0 | 0
Direct + P50 RISK + INDIRECTS | 0 | 0 | 0 | 0 | 0 | 0
P90-P50 RISK | 0 | 0 | 0 | 0 | 0 | 0
DIRECT + P90 RISK + INDIRECTS | 0 | 0 | 0 | 0 | 0 | 0

## 3.1 NPV
Economic inputs and assumptions
Scenario | Discount rate | Central
| Cost | Central
| VCR | Central
|  | Central | Lower bound | Upper bound
| Discount rate | 5.56% | 4.11% | 7%
| Cost | 100% | 80% | 120%
| VCR | 100% | 80% | 120%
Asset life for calculating annualised capex (years) | Option 1 | 45
| Option 2 | 45
| Option 3 | 45
| Option 4 | 45
| Option 5 | 45
| Option 6 | 45
| Option 7 | 45
| Option 8 | 45
| Option 9 | 45
| Option 10 | 45
|  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30
|  |  |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Outputs | bar: 3 FY27; 7 FY31
Option 1
| Discounted | Undiscounted
| 0 | 0 | Capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Opex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Reduction in unserved energy | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Net benefit | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | EUE Value ($m, real $2024) | 3.3134 | 65.4291 | 247.1322 | 283.0814 | 362.0029 | 439.1049 | 581.3072 | 639.5522 | 702.7745 | 733.9632 | 767.342 | 854.8903 | 782.2544 | 955.1709 | 1138.8523 | 1138.8523 | 1138.8523 | 1138.8523 | 1138.8523 | 1138.8523 | 1138.8523 | 1138.8523 | 1138.8523 | 1138.8523 | 1138.8523 | 1138.8523 | 1138.8523 | 1138.8523 | 1138.8523 | 1138.8523
Option 2
Determining Optimal Timing: | Discounted | Undiscounted
| 64.7091 | 72.1048 | Capex | 0 | 0 | 72.1048 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 8.9381 | 19.4683 | Opex | 0 | 0 | 0 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105
| 9984.918 | 24591.0207 | Reduction in unserved energy | 0 | 0 | 0 | 245.4928 | 298.3199 | 432.154 | 573.2974 | 630.3857 | 692.15 | 721.8524 | 753.3537 | 837.7342 | 764.8598 | 929.6264 | 1106.9871 | 1106.9871 | 1106.9871 | 1106.9871 | 1106.9871 | 1106.9871 | 1106.9871 | 1106.9871 | 1106.9871 | 1106.9871 | 1106.9871 | 1106.9871 | 1106.9871 | 1106.9871 | 1106.9871 | 1106.9871
| 9911.2708 | 24499.4476 | Net benefit | 0 | 0 | -72.1048 | 244.7717 | 297.5989 | 431.4329 | 572.5764 | 629.6647 | 691.4289 | 721.1314 | 752.6327 | 837.0132 | 764.1388 | 928.9053 | 1106.2661 | 1106.2661 | 1106.2661 | 1106.2661 | 1106.2661 | 1106.2661 | 1106.2661 | 1106.2661 | 1106.2661 | 1106.2661 | 1106.2661 | 1106.2661 | 1106.2661 | 1106.2661 | 1106.2661 | 1106.2661
|  |  | EUE Value ($m, real $2024) | 3.3072 | 65.4291 | 247.1322 | 37.5886 | 63.683 | 6.9509 | 8.0097 | 9.1665 | 10.6245 | 12.1107 | 13.9883 | 17.1561 | 17.3946 | 25.5446 | 31.8652 | 31.8652 | 31.8652 | 31.8652 | 31.8652 | 31.8652 | 31.8652 | 31.8652 | 31.8652 | 31.8652 | 31.8652 | 31.8652 | 31.8652 | 31.8652 | 31.8652 | 31.8652
|  |  | Annualised capex | 0 | 0 | 3.9433 | 3.9433 | 3.9433 | 3.9433 | 3.9433 | 3.9433 | 3.9433 | 3.9433 | 3.9433 | 3.9433 | 3.9433 | 3.9433 | 3.9433 | 3.9433 | 3.9433 | 3.9433 | 3.9433 | 3.9433 | 3.9433 | 3.9433 | 3.9433 | 3.9433 | 3.9433 | 3.9433 | 3.9433 | 3.9433 | 3.9433 | 3.9433
|  |  | Annualised cost (capex+opex) | 0 | 0 | 3.9433 | 4.6643 | 4.6643 | 4.6643 | 4.6643 | 4.6643 | 4.6643 | 4.6643 | 4.6643 | 4.6643 | 4.6643 | 4.6643 | 4.6643 | 4.6643 | 4.6643 | 4.6643 | 4.6643 | 4.6643 | 4.6643 | 4.6643 | 4.6643 | 4.6643 | 4.6643 | 4.6643 | 4.6643 | 4.6643 | 4.6643 | 4.6643
|  |  | Optimal timing (interim calc) | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  |  | Optimal timing | - | - | - | Yes | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Adjusted For Optimal Timing: | 64.7091 | 72.1048 | Capex | 0 | 0 | 72.1048 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 8.9381 | 19.4683 | Opex | 0 | 0 | 0 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105
| 9984.918 | 24591.0207 | Reduction in unserved energy | 0 | 0 | 0 | 245.4928 | 298.3199 | 432.154 | 573.2974 | 630.3857 | 692.15 | 721.8524 | 753.3537 | 837.7342 | 764.8598 | 929.6264 | 1106.9871 | 1106.9871 | 1106.9871 | 1106.9871 | 1106.9871 | 1106.9871 | 1106.9871 | 1106.9871 | 1106.9871 | 1106.9871 | 1106.9871 | 1106.9871 | 1106.9871 | 1106.9871 | 1106.9871 | 1106.9871
| 9911.2708 | 24499.4476 | Net benefit | 0 | 0 | -72.1048 | 244.7717 | 297.5989 | 431.4329 | 572.5764 | 629.6647 | 691.4289 | 721.1314 | 752.6327 | 837.0132 | 764.1388 | 928.9053 | 1106.2661 | 1106.2661 | 1106.2661 | 1106.2661 | 1106.2661 | 1106.2661 | 1106.2661 | 1106.2661 | 1106.2661 | 1106.2661 | 1106.2661 | 1106.2661 | 1106.2661 | 1106.2661 | 1106.2661 | 1106.2661
Option 3
Determining Optimal Timing: | Discounted | Undiscounted
| 39.0606 | 43.5248 | Capex | 0 | 0 | 43.5248 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 5.3953 | 11.7517 | Opex | 0 | 0 | 0 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525
| 8234.1231 | 19658.7761 | Reduction in unserved energy | 0 | 0 | 0 | 243.7522 | 294.2621 | 423.6585 | 557.0025 | 603.7113 | 650.6498 | 661.9773 | 672.5539 | 713.5507 | 640.2026 | 737.792 | 841.229 | 841.229 | 841.229 | 841.229 | 841.229 | 841.229 | 841.229 | 841.229 | 841.229 | 841.229 | 841.229 | 841.229 | 841.229 | 841.229 | 841.229 | 841.229
| 8189.6672 | 19603.4996 | Net benefit | 0 | 0 | -43.5248 | 243.3169 | 293.8268 | 423.2232 | 556.5672 | 603.276 | 650.2145 | 661.542 | 672.1186 | 713.1155 | 639.7674 | 737.3567 | 840.7937 | 840.7937 | 840.7937 | 840.7937 | 840.7937 | 840.7937 | 840.7937 | 840.7937 | 840.7937 | 840.7937 | 840.7937 | 840.7937 | 840.7937 | 840.7937 | 840.7937 | 840.7937
|  |  | EUE Value ($m, real $2024) | 3.3072 | 65.4291 | 247.1322 | 39.3292 | 67.7408 | 15.4464 | 24.3047 | 35.8409 | 52.1247 | 71.9859 | 94.7882 | 141.3396 | 142.0518 | 217.3789 | 297.6234 | 297.6234 | 297.6234 | 297.6234 | 297.6234 | 297.6234 | 297.6234 | 297.6234 | 297.6234 | 297.6234 | 297.6234 | 297.6234 | 297.6234 | 297.6234 | 297.6234 | 297.6234
|  |  | Annualised capex | 0 | 0 | 2.3803 | 2.3803 | 2.3803 | 2.3803 | 2.3803 | 2.3803 | 2.3803 | 2.3803 | 2.3803 | 2.3803 | 2.3803 | 2.3803 | 2.3803 | 2.3803 | 2.3803 | 2.3803 | 2.3803 | 2.3803 | 2.3803 | 2.3803 | 2.3803 | 2.3803 | 2.3803 | 2.3803 | 2.3803 | 2.3803 | 2.3803 | 2.3803
|  |  | Annualised cost (capex+opex) | 0 | 0 | 2.3803 | 2.8155 | 2.8155 | 2.8155 | 2.8155 | 2.8155 | 2.8155 | 2.8155 | 2.8155 | 2.8155 | 2.8155 | 2.8155 | 2.8155 | 2.8155 | 2.8155 | 2.8155 | 2.8155 | 2.8155 | 2.8155 | 2.8155 | 2.8155 | 2.8155 | 2.8155 | 2.8155 | 2.8155 | 2.8155 | 2.8155 | 2.8155
|  |  | Optimal timing (interim calc) | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  |  | Optimal timing | - | - | - | Yes | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
[7 empty] | TRUE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
Adjusted For Optimal Timing: | 39.0606 | 43.5248 | Capex | 0 | 0 | 43.5248 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 5.3953 | 11.7517 | Opex | 0 | 0 | 0 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525
| 8234.1231 | 19658.7761 | Reduction in unserved energy | 0 | 0 | 0 | 243.7522 | 294.2621 | 423.6585 | 557.0025 | 603.7113 | 650.6498 | 661.9773 | 672.5539 | 713.5507 | 640.2026 | 737.792 | 841.229 | 841.229 | 841.229 | 841.229 | 841.229 | 841.229 | 841.229 | 841.229 | 841.229 | 841.229 | 841.229 | 841.229 | 841.229 | 841.229 | 841.229 | 841.229
| 8189.6672 | 19603.4996 | Net benefit | 0 | 0 | -43.5248 | 243.3169 | 293.8268 | 423.2232 | 556.5672 | 603.276 | 650.2145 | 661.542 | 672.1186 | 713.1155 | 639.7674 | 737.3567 | 840.7937 | 840.7937 | 840.7937 | 840.7937 | 840.7937 | 840.7937 | 840.7937 | 840.7937 | 840.7937 | 840.7937 | 840.7937 | 840.7937 | 840.7937 | 840.7937 | 840.7937 | 840.7937
Option 4
Determining Optimal Timing: | Discounted | Undiscounted
| 53.4373 | 59.5447 | Capex | 0 | 0 | 59.5447 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 7.3811 | 16.0771 | Opex | 0 | 0 | 0 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545
| 3990.3839 | 10808.4009 | Reduction in unserved energy | 0 | 0 | 0 | 7.653 | 18.0781 | 97.9688 | 116.1458 | 135.5643 | 159.7892 | 184.879 | 216.5434 | 292.8216 | 278.5136 | 408.2495 | 555.7622 | 555.7622 | 555.7622 | 555.7622 | 555.7622 | 555.7622 | 555.7622 | 555.7622 | 555.7622 | 555.7622 | 555.7622 | 555.7622 | 555.7622 | 555.7622 | 555.7622 | 555.7622
| 3929.5655 | 10732.7791 | Net benefit | 0 | 0 | -59.5447 | 7.0575 | 17.4827 | 97.3733 | 115.5503 | 134.9689 | 159.1938 | 184.2835 | 215.9479 | 292.2261 | 277.9181 | 407.6541 | 555.1667 | 555.1667 | 555.1667 | 555.1667 | 555.1667 | 555.1667 | 555.1667 | 555.1667 | 555.1667 | 555.1667 | 555.1667 | 555.1667 | 555.1667 | 555.1667 | 555.1667 | 555.1667
|  |  | EUE Value ($m, real $2024) | 3.3072 | 65.4291 | 247.1322 | 275.4284 | 343.9248 | 341.1361 | 465.1614 | 503.9879 | 542.9852 | 549.0842 | 550.7987 | 562.0687 | 503.7408 | 546.9214 | 583.0902 | 583.0902 | 583.0902 | 583.0902 | 583.0902 | 583.0902 | 583.0902 | 583.0902 | 583.0902 | 583.0902 | 583.0902 | 583.0902 | 583.0902 | 583.0902 | 583.0902 | 583.0902
|  |  | Annualised capex | 0 | 0 | 3.2564 | 3.2564 | 3.2564 | 3.2564 | 3.2564 | 3.2564 | 3.2564 | 3.2564 | 3.2564 | 3.2564 | 3.2564 | 3.2564 | 3.2564 | 3.2564 | 3.2564 | 3.2564 | 3.2564 | 3.2564 | 3.2564 | 3.2564 | 3.2564 | 3.2564 | 3.2564 | 3.2564 | 3.2564 | 3.2564 | 3.2564 | 3.2564
|  |  | Annualised cost (capex+opex) | 0 | 0 | 3.2564 | 3.8518 | 3.8518 | 3.8518 | 3.8518 | 3.8518 | 3.8518 | 3.8518 | 3.8518 | 3.8518 | 3.8518 | 3.8518 | 3.8518 | 3.8518 | 3.8518 | 3.8518 | 3.8518 | 3.8518 | 3.8518 | 3.8518 | 3.8518 | 3.8518 | 3.8518 | 3.8518 | 3.8518 | 3.8518 | 3.8518 | 3.8518
|  |  | Optimal timing (interim calc) | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  |  | Optimal timing | - | - | - | Yes | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
[11 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19
Adjusted For Optimal Timing: | 53.4373 | 59.5447 | Capex | 0 | 0 | 59.5447 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 7.3811 | 16.0771 | Opex | 0 | 0 | 0 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545
| 3990.3839 | 10808.4009 | Reduction in unserved energy | 0 | 0 | 0 | 7.653 | 18.0781 | 97.9688 | 116.1458 | 135.5643 | 159.7892 | 184.879 | 216.5434 | 292.8216 | 278.5136 | 408.2495 | 555.7622 | 555.7622 | 555.7622 | 555.7622 | 555.7622 | 555.7622 | 555.7622 | 555.7622 | 555.7622 | 555.7622 | 555.7622 | 555.7622 | 555.7622 | 555.7622 | 555.7622 | 555.7622
| 3929.5655 | 10732.7791 | Net benefit | 0 | 0 | -59.5447 | 7.0575 | 17.4827 | 97.3733 | 115.5503 | 134.9689 | 159.1938 | 184.2835 | 215.9479 | 292.2261 | 277.9181 | 407.6541 | 555.1667 | 555.1667 | 555.1667 | 555.1667 | 555.1667 | 555.1667 | 555.1667 | 555.1667 | 555.1667 | 555.1667 | 555.1667 | 555.1667 | 555.1667 | 555.1667 | 555.1667 | 555.1667
Option 5
Determining Optimal Timing: | Discounted | Undiscounted
| 49.9911 | 55.7046 | Capex | 0 | 0 | 55.7046 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 6.9051 | 15.0402 | Opex | 0 | 0 | 0 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705
| 8365.665 | 19974.6734 | Reduction in unserved energy | 0 | 0 | 0 | 249.0844 | 300.1349 | 430.1528 | 564.2523 | 611.7211 | 659.3657 | 671.4363 | 682.8319 | 724.6792 | 652.0574 | 750.6505 | 854.8942 | 854.8942 | 854.8942 | 854.8942 | 854.8942 | 854.8942 | 854.8942 | 854.8942 | 854.8942 | 854.8942 | 854.8942 | 854.8942 | 854.8942 | 854.8942 | 854.8942 | 854.8942
| 8308.7689 | 19903.9285 | Net benefit | 0 | 0 | -55.7046 | 248.5274 | 299.5779 | 429.5958 | 563.6952 | 611.1641 | 658.8086 | 670.8792 | 682.2748 | 724.1222 | 651.5004 | 750.0935 | 854.3371 | 854.3371 | 854.3371 | 854.3371 | 854.3371 | 854.3371 | 854.3371 | 854.3371 | 854.3371 | 854.3371 | 854.3371 | 854.3371 | 854.3371 | 854.3371 | 854.3371 | 854.3371
|  |  | EUE Value ($m, real $2024) | 3.3072 | 65.4291 | 247.1322 | 33.9969 | 61.868 | 8.9521 | 17.0549 | 27.8311 | 43.4088 | 62.5269 | 84.5102 | 130.2111 | 130.197 | 204.5204 | 283.9581 | 283.9581 | 283.9581 | 283.9581 | 283.9581 | 283.9581 | 283.9581 | 283.9581 | 283.9581 | 283.9581 | 283.9581 | 283.9581 | 283.9581 | 283.9581 | 283.9581 | 283.9581
|  |  | Annualised capex | 0 | 0 | 3.0464 | 3.0464 | 3.0464 | 3.0464 | 3.0464 | 3.0464 | 3.0464 | 3.0464 | 3.0464 | 3.0464 | 3.0464 | 3.0464 | 3.0464 | 3.0464 | 3.0464 | 3.0464 | 3.0464 | 3.0464 | 3.0464 | 3.0464 | 3.0464 | 3.0464 | 3.0464 | 3.0464 | 3.0464 | 3.0464 | 3.0464 | 3.0464
|  |  | Annualised cost (capex+opex) | 0 | 0 | 3.0464 | 3.6034 | 3.6034 | 3.6034 | 3.6034 | 3.6034 | 3.6034 | 3.6034 | 3.6034 | 3.6034 | 3.6034 | 3.6034 | 3.6034 | 3.6034 | 3.6034 | 3.6034 | 3.6034 | 3.6034 | 3.6034 | 3.6034 | 3.6034 | 3.6034 | 3.6034 | 3.6034 | 3.6034 | 3.6034 | 3.6034 | 3.6034
|  |  | Optimal timing (interim calc) | 0 | 0 | 0 | 1 | 1 | 1 | 1 | [19 empty] | 1 | 1 | 1 | 1 | bar: 1 to 19
|  |  | Optimal timing | - | - | - | Yes | - | - | - | [19 empty] | - | - | - | - | bar: 1 to 19
Adjusted For Optimal Timing: | 49.9911 | 55.7046 | Capex | 0 | 0 | 55.7046 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 6.9051 | 15.0402 | Opex | 0 | 0 | 0 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705
| 8365.665 | 19974.6734 | Reduction in unserved energy | 0 | 0 | 0 | 249.0844 | 300.1349 | 430.1528 | 564.2523 | 611.7211 | 659.3657 | 671.4363 | 682.8319 | 724.6792 | 652.0574 | 750.6505 | 854.8942 | 854.8942 | 854.8942 | 854.8942 | 854.8942 | 854.8942 | 854.8942 | 854.8942 | 854.8942 | 854.8942 | 854.8942 | 854.8942 | 854.8942 | 854.8942 | 854.8942 | 854.8942
| 8308.7689 | 19903.9285 | Net benefit | 0 | 0 | -55.7046 | 248.5274 | 299.5779 | 429.5958 | 563.6952 | 611.1641 | 658.8086 | 670.8792 | 682.2748 | 724.1222 | 651.5004 | 750.0935 | 854.3371 | 854.3371 | 854.3371 | 854.3371 | 854.3371 | 854.3371 | 854.3371 | 854.3371 | 854.3371 | 854.3371 | 854.3371 | 854.3371 | 854.3371 | 854.3371 | 854.3371 | 854.3371
Option 6
Determining Optimal Timing: | Discounted | Undiscounted
| 61.1918 | 68.1854 | Capex | 0 | 0 | 68.1854 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 8.4522 | 18.4101 | Opex | 0 | 0 | 0 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185
| 9884.1595 | 24206.4938 | Reduction in unserved energy | 0 | 0 | 0 | 245.468 | 355.7787 | 432.0571 | 573.1763 | 630.1983 | 691.8313 | 721.2116 | 751.7861 | 833.3634 | 760.5335 | 918.8095 | 1080.7675 | 1080.7675 | 1080.7675 | 1080.7675 | 1080.7675 | 1080.7675 | 1080.7675 | 1080.7675 | 1080.7675 | 1080.7675 | 1080.7675 | 1080.7675 | 1080.7675 | 1080.7675 | 1080.7675 | 1080.7675
| 9814.5155 | 24119.8983 | Net benefit | 0 | 0 | -68.1854 | 244.7862 | 355.0968 | 431.3753 | 572.4944 | 629.5165 | 691.1494 | 720.5298 | 751.1043 | 832.6816 | 759.8517 | 918.1277 | 1080.0856 | 1080.0856 | 1080.0856 | 1080.0856 | 1080.0856 | 1080.0856 | 1080.0856 | 1080.0856 | 1080.0856 | 1080.0856 | 1080.0856 | 1080.0856 | 1080.0856 | 1080.0856 | 1080.0856 | 1080.0856
|  |  | EUE Value ($m, real $2024) | 3.3072 | 65.4291 | 247.1322 | 37.6134 | 6.2242 | 7.0478 | 8.1309 | 9.3539 | 10.9432 | 12.7515 | 15.5559 | 21.5268 | 21.7209 | 36.3614 | 58.0848 | 58.0848 | 58.0848 | 58.0848 | 58.0848 | 58.0848 | 58.0848 | 58.0848 | 58.0848 | 58.0848 | 58.0848 | 58.0848 | 58.0848 | 58.0848 | 58.0848 | 58.0848
|  |  | Annualised capex | 0 | 0 | 3.7289 | 3.7289 | 3.7289 | 3.7289 | 3.7289 | 3.7289 | 3.7289 | 3.7289 | 3.7289 | 3.7289 | 3.7289 | 3.7289 | 3.7289 | 3.7289 | 3.7289 | 3.7289 | 3.7289 | 3.7289 | 3.7289 | 3.7289 | 3.7289 | 3.7289 | 3.7289 | 3.7289 | 3.7289 | 3.7289 | 3.7289 | 3.7289
|  |  | Annualised cost (capex+opex) | 0 | 0 | 3.7289 | 4.4108 | 4.4108 | 4.4108 | 4.4108 | 4.4108 | 4.4108 | 4.4108 | 4.4108 | 4.4108 | 4.4108 | 4.4108 | 4.4108 | 4.4108 | 4.4108 | 4.4108 | 4.4108 | 4.4108 | 4.4108 | 4.4108 | 4.4108 | 4.4108 | 4.4108 | 4.4108 | 4.4108 | 4.4108 | 4.4108 | 4.4108
|  |  | Optimal timing (interim calc) | 0 | 0 | 0 | 1 | 1 | 1 | 1 | [19 empty] | 1 | 1 | 1 | 1 | bar: 1 to 19
|  |  | Optimal timing | - | - | - | Yes | - | - | - | [19 empty] | - | - | - | - | bar: 1 to 19
Adjusted For Optimal Timing: | 61.1918 | 68.1854 | Capex | 0 | 0 | 68.1854 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 8.4522 | 18.4101 | Opex | 0 | 0 | 0 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185
| 9884.1595 | 24206.4938 | Reduction in unserved energy | 0 | 0 | 0 | 245.468 | 355.7787 | 432.0571 | 573.1763 | 630.1983 | 691.8313 | 721.2116 | 751.7861 | 833.3634 | 760.5335 | 918.8095 | 1080.7675 | 1080.7675 | 1080.7675 | 1080.7675 | 1080.7675 | 1080.7675 | 1080.7675 | 1080.7675 | 1080.7675 | 1080.7675 | 1080.7675 | 1080.7675 | 1080.7675 | 1080.7675 | 1080.7675 | 1080.7675
| 9814.5155 | 24119.8983 | Net benefit | 0 | 0 | -68.1854 | 244.7862 | 355.0968 | 431.3753 | 572.4944 | 629.5165 | 691.1494 | 720.5298 | 751.1043 | 832.6816 | 759.8517 | 918.1277 | 1080.0856 | 1080.0856 | 1080.0856 | 1080.0856 | 1080.0856 | 1080.0856 | 1080.0856 | 1080.0856 | 1080.0856 | 1080.0856 | 1080.0856 | 1080.0856 | 1080.0856 | 1080.0856 | 1080.0856 | 1080.0856
Option 7
Determining Optimal Timing: | Discounted | Undiscounted
| 33.225 | 37.0224 | Capex | 0 | 0 | 37.0224 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 4.5893 | 9.996 | Opex | 0 | 0 | 0 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022
| 8185.5885 | 19432.1091 | Reduction in unserved energy | 0 | 0 | 0 | 243.5469 | 350.9258 | 423.345 | 556.6521 | 603.3027 | 650.1521 | 661.3713 | 671.6924 | 711.8687 | 638.2834 | 731.9998 | 824.3106 | 824.3106 | 824.3106 | 824.3106 | 824.3106 | 824.3106 | 824.3106 | 824.3106 | 824.3106 | 824.3106 | 824.3106 | 824.3106 | 824.3106 | 824.3106 | 824.3106 | 824.3106
| 8147.7742 | 19385.0907 | Net benefit | 0 | 0 | -37.0224 | 243.1767 | 350.5556 | 422.9748 | 556.2818 | 602.9325 | 649.7819 | 661.0011 | 671.3222 | 711.4984 | 637.9131 | 731.6296 | 823.9403 | 823.9403 | 823.9403 | 823.9403 | 823.9403 | 823.9403 | 823.9403 | 823.9403 | 823.9403 | 823.9403 | 823.9403 | 823.9403 | 823.9403 | 823.9403 | 823.9403 | 823.9403
|  |  | EUE Value ($m, real $2024) | 3.3072 | 65.4291 | 247.1322 | 39.5345 | 11.0771 | 15.7599 | 24.6551 | 36.2495 | 52.6223 | 72.5919 | 95.6496 | 143.0216 | 143.9711 | 223.1711 | 314.5418 | 314.5418 | 314.5418 | 314.5418 | 314.5418 | 314.5418 | 314.5418 | 314.5418 | 314.5418 | 314.5418 | 314.5418 | 314.5418 | 314.5418 | 314.5418 | 314.5418 | 314.5418
|  |  | Annualised capex | 0 | 0 | 2.0247 | 2.0247 | 2.0247 | 2.0247 | 2.0247 | 2.0247 | 2.0247 | 2.0247 | 2.0247 | 2.0247 | 2.0247 | 2.0247 | 2.0247 | 2.0247 | 2.0247 | 2.0247 | 2.0247 | 2.0247 | 2.0247 | 2.0247 | 2.0247 | 2.0247 | 2.0247 | 2.0247 | 2.0247 | 2.0247 | 2.0247 | 2.0247
|  |  | Annualised cost (capex+opex) | 0 | 0 | 2.0247 | 2.3949 | 2.3949 | 2.3949 | 2.3949 | 2.3949 | 2.3949 | 2.3949 | 2.3949 | 2.3949 | 2.3949 | 2.3949 | 2.3949 | 2.3949 | 2.3949 | 2.3949 | 2.3949 | 2.3949 | 2.3949 | 2.3949 | 2.3949 | 2.3949 | 2.3949 | 2.3949 | 2.3949 | 2.3949 | 2.3949 | 2.3949
|  |  | Optimal timing (interim calc) | 0 | 0 | 0 | 1 | 1 | 1 | 1 | [19 empty] | 1 | 1 | 1 | 1 | bar: 1 to 19
|  |  | Optimal timing | - | - | - | Yes | - | - | - | [19 empty] | - | - | - | - | bar: 1 to 19
Adjusted For Optimal Timing: | 33.225 | 37.0224 | Capex | 0 | 0 | 37.0224 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 4.5893 | 9.996 | Opex | 0 | 0 | 0 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022
| 8185.5885 | 19432.1091 | Reduction in unserved energy | 0 | 0 | 0 | 243.5469 | 350.9258 | 423.345 | 556.6521 | 603.3027 | 650.1521 | 661.3713 | 671.6924 | 711.8687 | 638.2834 | 731.9998 | 824.3106 | 824.3106 | 824.3106 | 824.3106 | 824.3106 | 824.3106 | 824.3106 | 824.3106 | 824.3106 | 824.3106 | 824.3106 | 824.3106 | 824.3106 | 824.3106 | 824.3106 | 824.3106
| 8147.7742 | 19385.0907 | Net benefit | 0 | 0 | -37.0224 | 243.1767 | 350.5556 | 422.9748 | 556.2818 | 602.9325 | 649.7819 | 661.0011 | 671.3222 | 711.4984 | 637.9131 | 731.6296 | 823.9403 | 823.9403 | 823.9403 | 823.9403 | 823.9403 | 823.9403 | 823.9403 | 823.9403 | 823.9403 | 823.9403 | 823.9403 | 823.9403 | 823.9403 | 823.9403 | 823.9403 | 823.9403
Option 8
Determining Optimal Timing: | Discounted | Undiscounted
| 47.6017 | 53.0422 | Capex | 0 | 0 | 53.0422 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 6.5751 | 14.3214 | Opex | 0 | 0 | 0 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042
| 3926.1287 | 10535.8711 | Reduction in unserved energy | 0 | 0 | 0 | 7.5218 | 74.6435 | 97.6009 | 115.718 | 135.0626 | 159.1861 | 184.1202 | 215.4688 | 290.4585 | 275.411 | 400.6215 | 536.2536 | 536.2536 | 536.2536 | 536.2536 | 536.2536 | 536.2536 | 536.2536 | 536.2536 | 536.2536 | 536.2536 | 536.2536 | 536.2536 | 536.2536 | 536.2536 | 536.2536 | 536.2536
| 3871.9518 | 10468.5075 | Net benefit | 0 | 0 | -53.0422 | 6.9913 | 74.1131 | 97.0705 | 115.1875 | 134.5322 | 158.6557 | 183.5898 | 214.9384 | 289.9281 | 274.8806 | 400.0911 | 535.7232 | 535.7232 | 535.7232 | 535.7232 | 535.7232 | 535.7232 | 535.7232 | 535.7232 | 535.7232 | 535.7232 | 535.7232 | 535.7232 | 535.7232 | 535.7232 | 535.7232 | 535.7232
|  |  | EUE Value ($m, real $2024) | 3.3072 | 65.4291 | 247.1322 | 275.5596 | 287.3594 | 341.504 | 465.5892 | 504.4896 | 543.5884 | 549.8429 | 551.8732 | 564.4318 | 506.8434 | 554.5494 | 602.5987 | 602.5987 | 602.5987 | 602.5987 | 602.5987 | 602.5987 | 602.5987 | 602.5987 | 602.5987 | 602.5987 | 602.5987 | 602.5987 | 602.5987 | 602.5987 | 602.5987 | 602.5987
|  |  | Annualised capex | 0 | 0 | 2.9008 | 2.9008 | 2.9008 | 2.9008 | 2.9008 | 2.9008 | 2.9008 | 2.9008 | 2.9008 | 2.9008 | 2.9008 | 2.9008 | 2.9008 | 2.9008 | 2.9008 | 2.9008 | 2.9008 | 2.9008 | 2.9008 | 2.9008 | 2.9008 | 2.9008 | 2.9008 | 2.9008 | 2.9008 | 2.9008 | 2.9008 | 2.9008
|  |  | Annualised cost (capex+opex) | 0 | 0 | 2.9008 | 3.4312 | 3.4312 | 3.4312 | 3.4312 | 3.4312 | 3.4312 | 3.4312 | 3.4312 | 3.4312 | 3.4312 | 3.4312 | 3.4312 | 3.4312 | 3.4312 | 3.4312 | 3.4312 | 3.4312 | 3.4312 | 3.4312 | 3.4312 | 3.4312 | 3.4312 | 3.4312 | 3.4312 | 3.4312 | 3.4312 | 3.4312
|  |  | Optimal timing (interim calc) | 0 | 0 | 0 | 1 | 1 | 1 | 1 | [19 empty] | 1 | 1 | 1 | 1 | bar: 1 to 19
|  |  | Optimal timing | - | - | - | Yes | - | - | - | [19 empty] | - | - | - | - | bar: 1 to 19
Adjusted For Optimal Timing: | 47.6017 | 53.0422 | Capex | 0 | 0 | 53.0422 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 6.5751 | 14.3214 | Opex | 0 | 0 | 0 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042
| 3926.1287 | 10535.8711 | Reduction in unserved energy | 0 | 0 | 0 | 7.5218 | 74.6435 | 97.6009 | 115.718 | 135.0626 | 159.1861 | 184.1202 | 215.4688 | 290.4585 | 275.411 | 400.6215 | 536.2536 | 536.2536 | 536.2536 | 536.2536 | 536.2536 | 536.2536 | 536.2536 | 536.2536 | 536.2536 | 536.2536 | 536.2536 | 536.2536 | 536.2536 | 536.2536 | 536.2536 | 536.2536
| 3871.9518 | 10468.5075 | Net benefit | 0 | 0 | -53.0422 | 6.9913 | 74.1131 | 97.0705 | 115.1875 | 134.5322 | 158.6557 | 183.5898 | 214.9384 | 289.9281 | 274.8806 | 400.0911 | 535.7232 | 535.7232 | 535.7232 | 535.7232 | 535.7232 | 535.7232 | 535.7232 | 535.7232 | 535.7232 | 535.7232 | 535.7232 | 535.7232 | 535.7232 | 535.7232 | 535.7232 | 535.7232
Option 9
Determining Optimal Timing: | Discounted | Undiscounted
| 44.1555 | 49.2021 | Capex | 0 | 0 | 49.2021 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 6.0991 | 13.2846 | Opex | 0 | 0 | 0 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202
| 8317.247 | 19748.3321 | Reduction in unserved energy | 0 | 0 | 0 | 248.8786 | 356.798 | 429.8384 | 563.9003 | 611.3104 | 658.8656 | 670.8188 | 682.0288 | 723.0532 | 650.1203 | 744.8226 | 837.9936 | 837.9936 | 837.9936 | 837.9936 | 837.9936 | 837.9936 | 837.9936 | 837.9936 | 837.9936 | 837.9936 | 837.9936 | 837.9936 | 837.9936 | 837.9936 | 837.9936 | 837.9936
| 8266.9925 | 19685.8454 | Net benefit | 0 | 0 | -49.2021 | 248.3866 | 356.306 | 429.3464 | 563.4083 | 610.8183 | 658.3735 | 670.3267 | 681.5368 | 722.5612 | 649.6283 | 744.3306 | 837.5015 | 837.5015 | 837.5015 | 837.5015 | 837.5015 | 837.5015 | 837.5015 | 837.5015 | 837.5015 | 837.5015 | 837.5015 | 837.5015 | 837.5015 | 837.5015 | 837.5015 | 837.5015
|  |  | EUE Value ($m, real $2024) | 3.3072 | 65.4291 | 247.1322 | 34.2028 | 5.2049 | 9.2665 | 17.4069 | 28.2418 | 43.9089 | 63.1444 | 85.3132 | 131.8371 | 132.1341 | 210.3483 | 300.8588 | 300.8588 | 300.8588 | 300.8588 | 300.8588 | 300.8588 | 300.8588 | 300.8588 | 300.8588 | 300.8588 | 300.8588 | 300.8588 | 300.8588 | 300.8588 | 300.8588 | 300.8588
|  |  | Annualised capex | 0 | 0 | 2.6908 | 2.6908 | 2.6908 | 2.6908 | 2.6908 | 2.6908 | 2.6908 | 2.6908 | 2.6908 | 2.6908 | 2.6908 | 2.6908 | 2.6908 | 2.6908 | 2.6908 | 2.6908 | 2.6908 | 2.6908 | 2.6908 | 2.6908 | 2.6908 | 2.6908 | 2.6908 | 2.6908 | 2.6908 | 2.6908 | 2.6908 | 2.6908
|  |  | Annualised cost (capex+opex) | 0 | 0 | 2.6908 | 3.1828 | 3.1828 | 3.1828 | 3.1828 | 3.1828 | 3.1828 | 3.1828 | 3.1828 | 3.1828 | 3.1828 | 3.1828 | 3.1828 | 3.1828 | 3.1828 | 3.1828 | 3.1828 | 3.1828 | 3.1828 | 3.1828 | 3.1828 | 3.1828 | 3.1828 | 3.1828 | 3.1828 | 3.1828 | 3.1828 | 3.1828
|  |  | Optimal timing (interim calc) | 0 | 0 | 0 | 1 | 1 | 1 | 1 | [19 empty] | 1 | 1 | 1 | 1 | bar: 1 to 19
|  |  | Optimal timing | - | - | - | Yes | - | - | - | [19 empty] | - | - | - | - | bar: 1 to 19
Adjusted For Optimal Timing: | 44.1555 | 49.2021 | Capex | 0 | 0 | 49.2021 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 6.0991 | 13.2846 | Opex | 0 | 0 | 0 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202
| 8317.247 | 19748.3321 | Reduction in unserved energy | 0 | 0 | 0 | 248.8786 | 356.798 | 429.8384 | 563.9003 | 611.3104 | 658.8656 | 670.8188 | 682.0288 | 723.0532 | 650.1203 | 744.8226 | 837.9936 | 837.9936 | 837.9936 | 837.9936 | 837.9936 | 837.9936 | 837.9936 | 837.9936 | 837.9936 | 837.9936 | 837.9936 | 837.9936 | 837.9936 | 837.9936 | 837.9936 | 837.9936
| 8266.9925 | 19685.8454 | Net benefit | 0 | 0 | -49.2021 | 248.3866 | 356.306 | 429.3464 | 563.4083 | 610.8183 | 658.3735 | 670.3267 | 681.5368 | 722.5612 | 649.6283 | 744.3306 | 837.5015 | 837.5015 | 837.5015 | 837.5015 | 837.5015 | 837.5015 | 837.5015 | 837.5015 | 837.5015 | 837.5015 | 837.5015 | 837.5015 | 837.5015 | 837.5015 | 837.5015 | 837.5015
Option 10
Determining Optimal Timing: | Discounted | Undiscounted
| 0 | 0 | Capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 6375.8942 | 15208.189 | Opex | 0.48285 | 57.8283 | 189.4866 | 207.6844 | 245.4848 | 279.2209 | 339.624 | 384.4625 | 426.7802 | 445.1879 | 469.6214 | 502.6026 | 486.2654 | 573.3683 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055
| 6375.8942 | 15208.189 | Reduction in unserved energy | 0.48285 | 57.8283 | 189.4866 | 207.6844 | 245.4848 | 279.2209 | 339.624 | 384.4625 | 426.7802 | 445.1879 | 469.6214 | 502.6026 | 486.2654 | 573.3683 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055
| 0 | 0 | Net benefit | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | EUE Value ($m, real $2024) | 2.8305 | 7.6008 | 57.6455 | 75.397 | 116.5181 | 159.884 | 241.6832 | 255.0898 | 275.9942 | 288.7753 | 297.7206 | 352.2877 | 295.989 | 381.8026 | 476.3468 | 476.3468 | 476.3468 | 476.3468 | 476.3468 | 476.3468 | 476.3468 | 476.3468 | 476.3468 | 476.3468 | 476.3468 | 476.3468 | 476.3468 | 476.3468 | 476.3468 | 476.3468
|  |  | Annualised capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Annualised cost (capex+opex) | 0.48285 | 57.8283 | 189.4866 | 207.6844 | 245.4848 | 279.2209 | 339.624 | 384.4625 | 426.7802 | 445.1879 | 469.6214 | 502.6026 | 486.2654 | 573.3683 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055
|  |  | Optimal timing (interim calc) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Optimal timing | - | - | - | - | - | - | - | [19 empty] | - | - | - | - | bar: 1 to 19
Adjusted For Optimal Timing: | 0 | 0 | Capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 6375.8942 | 15208.189 | Opex | 0.48285 | 57.8283 | 189.4866 | 207.6844 | 245.4848 | 279.2209 | 339.624 | 384.4625 | 426.7802 | 445.1879 | 469.6214 | 502.6026 | 486.2654 | 573.3683 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055
| 6375.8942 | 15208.189 | Reduction in unserved energy | 0.48285 | 57.8283 | 189.4866 | 207.6844 | 245.4848 | 279.2209 | 339.624 | 384.4625 | 426.7802 | 445.1879 | 469.6214 | 502.6026 | 486.2654 | 573.3683 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055
| 0 | 0 | Net benefit | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## 3.2.1 NPV (LoDiscount)
Economic inputs and assumptions
Scenario | Discount rate | Lower bound
| Cost | Central
| VCR | Central
|  | Central | Lower bound | Upper bound
| Discount rate | 5.56% | 4.11% | 7%
| Cost | 100% | 80% | 120%
| VCR | 100% | 80% | 120%
Asset life for calculating annualised capex (years) | Option 1 | 45
| Option 2 | 45
| Option 3 | 45
| Option 4 | 45
| Option 5 | 45
| Option 6 | 45
| Option 7 | 45
| Option 8 | 45
| Option 9 | 45
| Option 10 | 45
|  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30
|  |  |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Outputs | bar: 3 FY27; 7 FY31
Option 1
| Discounted | Undiscounted
| 0 | 0 | Capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Opex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Reduction in unserved energy | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Net benefit | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | EUE Value ($m, real $2024) | 3.3134 | 65.4291 | 247.1322 | 283.0814 | 362.0029 | 439.1049 | 581.3072 | 639.5522 | 702.7745 | 733.9632 | 767.342 | 854.8903 | 782.2544 | 955.1709 | 1138.8523 | 1138.8523 | 1138.8523 | 1138.8523 | 1138.8523 | 1138.8523 | 1138.8523 | 1138.8523 | 1138.8523 | 1138.8523 | 1138.8523 | 1138.8523 | 1138.8523 | 1138.8523 | 1138.8523 | 1138.8523
Option 2
Determining Optimal Timing: | Discounted | Undiscounted
| 66.5241 | 72.1048 | Capex | 0 | 0 | 72.1048 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 10.7303 | 19.4683 | Opex | 0 | 0 | 0 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105
| 12397.6588 | 24591.0207 | Reduction in unserved energy | 0 | 0 | 0 | 245.4928 | 298.3199 | 432.154 | 573.2974 | 630.3857 | 692.15 | 721.8524 | 753.3537 | 837.7342 | 764.8598 | 929.6264 | 1106.9871 | 1106.9871 | 1106.9871 | 1106.9871 | 1106.9871 | 1106.9871 | 1106.9871 | 1106.9871 | 1106.9871 | 1106.9871 | 1106.9871 | 1106.9871 | 1106.9871 | 1106.9871 | 1106.9871 | 1106.9871
| 12320.4043 | 24499.4476 | Net benefit | 0 | 0 | -72.1048 | 244.7717 | 297.5989 | 431.4329 | 572.5764 | 629.6647 | 691.4289 | 721.1314 | 752.6327 | 837.0132 | 764.1388 | 928.9053 | 1106.2661 | 1106.2661 | 1106.2661 | 1106.2661 | 1106.2661 | 1106.2661 | 1106.2661 | 1106.2661 | 1106.2661 | 1106.2661 | 1106.2661 | 1106.2661 | 1106.2661 | 1106.2661 | 1106.2661 | 1106.2661
|  |  | EUE Value ($m, real $2024) | 3.3072 | 65.4291 | 247.1322 | 37.5886 | 63.683 | 6.9509 | 8.0097 | 9.1665 | 10.6245 | 12.1107 | 13.9883 | 17.1561 | 17.3946 | 25.5446 | 31.8652 | 31.8652 | 31.8652 | 31.8652 | 31.8652 | 31.8652 | 31.8652 | 31.8652 | 31.8652 | 31.8652 | 31.8652 | 31.8652 | 31.8652 | 31.8652 | 31.8652 | 31.8652
|  |  | Annualised capex | 0 | 0 | 4.0539 | 4.0539 | 4.0539 | 4.0539 | 4.0539 | 4.0539 | 4.0539 | 4.0539 | 4.0539 | 4.0539 | 4.0539 | 4.0539 | 4.0539 | 4.0539 | 4.0539 | 4.0539 | 4.0539 | 4.0539 | 4.0539 | 4.0539 | 4.0539 | 4.0539 | 4.0539 | 4.0539 | 4.0539 | 4.0539 | 4.0539 | 4.0539
|  |  | Annualised cost (capex+opex) | 0 | 0 | 4.0539 | 4.7749 | 4.7749 | 4.7749 | 4.7749 | 4.7749 | 4.7749 | 4.7749 | 4.7749 | 4.7749 | 4.7749 | 4.7749 | 4.7749 | 4.7749 | 4.7749 | 4.7749 | 4.7749 | 4.7749 | 4.7749 | 4.7749 | 4.7749 | 4.7749 | 4.7749 | 4.7749 | 4.7749 | 4.7749 | 4.7749 | 4.7749
|  |  | Optimal timing (interim calc) | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  |  | Optimal timing | - | - | - | Yes | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Adjusted For Optimal Timing: | 66.5241 | 72.1048 | Capex | 0 | 0 | 72.1048 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 10.7303 | 19.4683 | Opex | 0 | 0 | 0 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105
| 12397.6588 | 24591.0207 | Reduction in unserved energy | 0 | 0 | 0 | 245.4928 | 298.3199 | 432.154 | 573.2974 | 630.3857 | 692.15 | 721.8524 | 753.3537 | 837.7342 | 764.8598 | 929.6264 | 1106.9871 | 1106.9871 | 1106.9871 | 1106.9871 | 1106.9871 | 1106.9871 | 1106.9871 | 1106.9871 | 1106.9871 | 1106.9871 | 1106.9871 | 1106.9871 | 1106.9871 | 1106.9871 | 1106.9871 | 1106.9871
| 12320.4043 | 24499.4476 | Net benefit | 0 | 0 | -72.1048 | 244.7717 | 297.5989 | 431.4329 | 572.5764 | 629.6647 | 691.4289 | 721.1314 | 752.6327 | 837.0132 | 764.1388 | 928.9053 | 1106.2661 | 1106.2661 | 1106.2661 | 1106.2661 | 1106.2661 | 1106.2661 | 1106.2661 | 1106.2661 | 1106.2661 | 1106.2661 | 1106.2661 | 1106.2661 | 1106.2661 | 1106.2661 | 1106.2661 | 1106.2661
Option 3
Determining Optimal Timing: | Discounted | Undiscounted
| 40.1562 | 43.5248 | Capex | 0 | 0 | 43.5248 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 6.4772 | 11.7517 | Opex | 0 | 0 | 0 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525
| 10137.1844 | 19658.7761 | Reduction in unserved energy | 0 | 0 | 0 | 243.7522 | 294.2621 | 423.6585 | 557.0025 | 603.7113 | 650.6498 | 661.9773 | 672.5539 | 713.5507 | 640.2026 | 737.792 | 841.229 | 841.229 | 841.229 | 841.229 | 841.229 | 841.229 | 841.229 | 841.229 | 841.229 | 841.229 | 841.229 | 841.229 | 841.229 | 841.229 | 841.229 | 841.229
| 10090.551 | 19603.4996 | Net benefit | 0 | 0 | -43.5248 | 243.3169 | 293.8268 | 423.2232 | 556.5672 | 603.276 | 650.2145 | 661.542 | 672.1186 | 713.1155 | 639.7674 | 737.3567 | 840.7937 | 840.7937 | 840.7937 | 840.7937 | 840.7937 | 840.7937 | 840.7937 | 840.7937 | 840.7937 | 840.7937 | 840.7937 | 840.7937 | 840.7937 | 840.7937 | 840.7937 | 840.7937
|  |  | EUE Value ($m, real $2024) | 3.3072 | 65.4291 | 247.1322 | 39.3292 | 67.7408 | 15.4464 | 24.3047 | 35.8409 | 52.1247 | 71.9859 | 94.7882 | 141.3396 | 142.0518 | 217.3789 | 297.6234 | 297.6234 | 297.6234 | 297.6234 | 297.6234 | 297.6234 | 297.6234 | 297.6234 | 297.6234 | 297.6234 | 297.6234 | 297.6234 | 297.6234 | 297.6234 | 297.6234 | 297.6234
|  |  | Annualised capex | 0 | 0 | 2.4471 | 2.4471 | 2.4471 | 2.4471 | 2.4471 | 2.4471 | 2.4471 | 2.4471 | 2.4471 | 2.4471 | 2.4471 | 2.4471 | 2.4471 | 2.4471 | 2.4471 | 2.4471 | 2.4471 | 2.4471 | 2.4471 | 2.4471 | 2.4471 | 2.4471 | 2.4471 | 2.4471 | 2.4471 | 2.4471 | 2.4471 | 2.4471
|  |  | Annualised cost (capex+opex) | 0 | 0 | 2.4471 | 2.8823 | 2.8823 | 2.8823 | 2.8823 | 2.8823 | 2.8823 | 2.8823 | 2.8823 | 2.8823 | 2.8823 | 2.8823 | 2.8823 | 2.8823 | 2.8823 | 2.8823 | 2.8823 | 2.8823 | 2.8823 | 2.8823 | 2.8823 | 2.8823 | 2.8823 | 2.8823 | 2.8823 | 2.8823 | 2.8823 | 2.8823
|  |  | Optimal timing (interim calc) | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  |  | Optimal timing | - | - | - | Yes | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Adjusted For Optimal Timing: | 40.1562 | 43.5248 | Capex | 0 | 0 | 43.5248 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 6.4772 | 11.7517 | Opex | 0 | 0 | 0 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525
| 10137.1844 | 19658.7761 | Reduction in unserved energy | 0 | 0 | 0 | 243.7522 | 294.2621 | 423.6585 | 557.0025 | 603.7113 | 650.6498 | 661.9773 | 672.5539 | 713.5507 | 640.2026 | 737.792 | 841.229 | 841.229 | 841.229 | 841.229 | 841.229 | 841.229 | 841.229 | 841.229 | 841.229 | 841.229 | 841.229 | 841.229 | 841.229 | 841.229 | 841.229 | 841.229
| 10090.551 | 19603.4996 | Net benefit | 0 | 0 | -43.5248 | 243.3169 | 293.8268 | 423.2232 | 556.5672 | 603.276 | 650.2145 | 661.542 | 672.1186 | 713.1155 | 639.7674 | 737.3567 | 840.7937 | 840.7937 | 840.7937 | 840.7937 | 840.7937 | 840.7937 | 840.7937 | 840.7937 | 840.7937 | 840.7937 | 840.7937 | 840.7937 | 840.7937 | 840.7937 | 840.7937 | 840.7937
Option 4
Determining Optimal Timing: | Discounted | Undiscounted
| 54.9361 | 59.5447 | Capex | 0 | 0 | 59.5447 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 8.8612 | 16.0771 | Opex | 0 | 0 | 0 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545
| 5091.7761 | 10808.4009 | Reduction in unserved energy | 0 | 0 | 0 | 7.653 | 18.0781 | 97.9688 | 116.1458 | 135.5643 | 159.7892 | 184.879 | 216.5434 | 292.8216 | 278.5136 | 408.2495 | 555.7622 | 555.7622 | 555.7622 | 555.7622 | 555.7622 | 555.7622 | 555.7622 | 555.7622 | 555.7622 | 555.7622 | 555.7622 | 555.7622 | 555.7622 | 555.7622 | 555.7622 | 555.7622
| 5027.9788 | 10732.7791 | Net benefit | 0 | 0 | -59.5447 | 7.0575 | 17.4827 | 97.3733 | 115.5503 | 134.9689 | 159.1938 | 184.2835 | 215.9479 | 292.2261 | 277.9181 | 407.6541 | 555.1667 | 555.1667 | 555.1667 | 555.1667 | 555.1667 | 555.1667 | 555.1667 | 555.1667 | 555.1667 | 555.1667 | 555.1667 | 555.1667 | 555.1667 | 555.1667 | 555.1667 | 555.1667
|  |  | EUE Value ($m, real $2024) | 3.3072 | 65.4291 | 247.1322 | 275.4284 | 343.9248 | 341.1361 | 465.1614 | 503.9879 | 542.9852 | 549.0842 | 550.7987 | 562.0687 | 503.7408 | 546.9214 | 583.0902 | 583.0902 | 583.0902 | 583.0902 | 583.0902 | 583.0902 | 583.0902 | 583.0902 | 583.0902 | 583.0902 | 583.0902 | 583.0902 | 583.0902 | 583.0902 | 583.0902 | 583.0902
|  |  | Annualised capex | 0 | 0 | 3.3477 | 3.3477 | 3.3477 | 3.3477 | 3.3477 | 3.3477 | 3.3477 | 3.3477 | 3.3477 | 3.3477 | 3.3477 | 3.3477 | 3.3477 | 3.3477 | 3.3477 | 3.3477 | 3.3477 | 3.3477 | 3.3477 | 3.3477 | 3.3477 | 3.3477 | 3.3477 | 3.3477 | 3.3477 | 3.3477 | 3.3477 | 3.3477
|  |  | Annualised cost (capex+opex) | 0 | 0 | 3.3477 | 3.9432 | 3.9432 | 3.9432 | 3.9432 | 3.9432 | 3.9432 | 3.9432 | 3.9432 | 3.9432 | 3.9432 | 3.9432 | 3.9432 | 3.9432 | 3.9432 | 3.9432 | 3.9432 | 3.9432 | 3.9432 | 3.9432 | 3.9432 | 3.9432 | 3.9432 | 3.9432 | 3.9432 | 3.9432 | 3.9432 | 3.9432
|  |  | Optimal timing (interim calc) | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  |  | Optimal timing | - | - | - | Yes | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
[11 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19
Adjusted For Optimal Timing: | 54.9361 | 59.5447 | Capex | 0 | 0 | 59.5447 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 8.8612 | 16.0771 | Opex | 0 | 0 | 0 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545
| 5091.7761 | 10808.4009 | Reduction in unserved energy | 0 | 0 | 0 | 7.653 | 18.0781 | 97.9688 | 116.1458 | 135.5643 | 159.7892 | 184.879 | 216.5434 | 292.8216 | 278.5136 | 408.2495 | 555.7622 | 555.7622 | 555.7622 | 555.7622 | 555.7622 | 555.7622 | 555.7622 | 555.7622 | 555.7622 | 555.7622 | 555.7622 | 555.7622 | 555.7622 | 555.7622 | 555.7622 | 555.7622
| 5027.9788 | 10732.7791 | Net benefit | 0 | 0 | -59.5447 | 7.0575 | 17.4827 | 97.3733 | 115.5503 | 134.9689 | 159.1938 | 184.2835 | 215.9479 | 292.2261 | 277.9181 | 407.6541 | 555.1667 | 555.1667 | 555.1667 | 555.1667 | 555.1667 | 555.1667 | 555.1667 | 555.1667 | 555.1667 | 555.1667 | 555.1667 | 555.1667 | 555.1667 | 555.1667 | 555.1667 | 555.1667
Option 5
Determining Optimal Timing: | Discounted | Undiscounted
| 51.3933 | 55.7046 | Capex | 0 | 0 | 55.7046 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 8.2897 | 15.0402 | Opex | 0 | 0 | 0 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705
| 10299.3596 | 19974.6734 | Reduction in unserved energy | 0 | 0 | 0 | 249.0844 | 300.1349 | 430.1528 | 564.2523 | 611.7211 | 659.3657 | 671.4363 | 682.8319 | 724.6792 | 652.0574 | 750.6505 | 854.8942 | 854.8942 | 854.8942 | 854.8942 | 854.8942 | 854.8942 | 854.8942 | 854.8942 | 854.8942 | 854.8942 | 854.8942 | 854.8942 | 854.8942 | 854.8942 | 854.8942 | 854.8942
| 10239.6766 | 19903.9285 | Net benefit | 0 | 0 | -55.7046 | 248.5274 | 299.5779 | 429.5958 | 563.6952 | 611.1641 | 658.8086 | 670.8792 | 682.2748 | 724.1222 | 651.5004 | 750.0935 | 854.3371 | 854.3371 | 854.3371 | 854.3371 | 854.3371 | 854.3371 | 854.3371 | 854.3371 | 854.3371 | 854.3371 | 854.3371 | 854.3371 | 854.3371 | 854.3371 | 854.3371 | 854.3371
|  |  | EUE Value ($m, real $2024) | 3.3072 | 65.4291 | 247.1322 | 33.9969 | 61.868 | 8.9521 | 17.0549 | 27.8311 | 43.4088 | 62.5269 | 84.5102 | 130.2111 | 130.197 | 204.5204 | 283.9581 | 283.9581 | 283.9581 | 283.9581 | 283.9581 | 283.9581 | 283.9581 | 283.9581 | 283.9581 | 283.9581 | 283.9581 | 283.9581 | 283.9581 | 283.9581 | 283.9581 | 283.9581
|  |  | Annualised capex | 0 | 0 | 3.1318 | 3.1318 | 3.1318 | 3.1318 | 3.1318 | 3.1318 | 3.1318 | 3.1318 | 3.1318 | 3.1318 | 3.1318 | 3.1318 | 3.1318 | 3.1318 | 3.1318 | 3.1318 | 3.1318 | 3.1318 | 3.1318 | 3.1318 | 3.1318 | 3.1318 | 3.1318 | 3.1318 | 3.1318 | 3.1318 | 3.1318 | 3.1318
|  |  | Annualised cost (capex+opex) | 0 | 0 | 3.1318 | 3.6889 | 3.6889 | 3.6889 | 3.6889 | 3.6889 | 3.6889 | 3.6889 | 3.6889 | 3.6889 | 3.6889 | 3.6889 | 3.6889 | 3.6889 | 3.6889 | 3.6889 | 3.6889 | 3.6889 | 3.6889 | 3.6889 | 3.6889 | 3.6889 | 3.6889 | 3.6889 | 3.6889 | 3.6889 | 3.6889 | 3.6889
|  |  | Optimal timing (interim calc) | 0 | 0 | 0 | 1 | 1 | 1 | 1 | [19 empty] | 1 | 1 | 1 | 1 | bar: 1 to 19
|  |  | Optimal timing | - | - | - | Yes | - | - | - | [19 empty] | - | - | - | - | bar: 1 to 19
Adjusted For Optimal Timing: | 51.3933 | 55.7046 | Capex | 0 | 0 | 55.7046 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 8.2897 | 15.0402 | Opex | 0 | 0 | 0 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705
| 10299.3596 | 19974.6734 | Reduction in unserved energy | 0 | 0 | 0 | 249.0844 | 300.1349 | 430.1528 | 564.2523 | 611.7211 | 659.3657 | 671.4363 | 682.8319 | 724.6792 | 652.0574 | 750.6505 | 854.8942 | 854.8942 | 854.8942 | 854.8942 | 854.8942 | 854.8942 | 854.8942 | 854.8942 | 854.8942 | 854.8942 | 854.8942 | 854.8942 | 854.8942 | 854.8942 | 854.8942 | 854.8942
| 10239.6766 | 19903.9285 | Net benefit | 0 | 0 | -55.7046 | 248.5274 | 299.5779 | 429.5958 | 563.6952 | 611.1641 | 658.8086 | 670.8792 | 682.2748 | 724.1222 | 651.5004 | 750.0935 | 854.3371 | 854.3371 | 854.3371 | 854.3371 | 854.3371 | 854.3371 | 854.3371 | 854.3371 | 854.3371 | 854.3371 | 854.3371 | 854.3371 | 854.3371 | 854.3371 | 854.3371 | 854.3371
Option 6
Determining Optimal Timing: | Discounted | Undiscounted
| 62.9081 | 68.1854 | Capex | 0 | 0 | 68.1854 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 10.1471 | 18.4101 | Opex | 0 | 0 | 0 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185
| 12253.1003 | 24206.4938 | Reduction in unserved energy | 0 | 0 | 0 | 245.468 | 355.7787 | 432.0571 | 573.1763 | 630.1983 | 691.8313 | 721.2116 | 751.7861 | 833.3634 | 760.5335 | 918.8095 | 1080.7675 | 1080.7675 | 1080.7675 | 1080.7675 | 1080.7675 | 1080.7675 | 1080.7675 | 1080.7675 | 1080.7675 | 1080.7675 | 1080.7675 | 1080.7675 | 1080.7675 | 1080.7675 | 1080.7675 | 1080.7675
| 12180.0451 | 24119.8983 | Net benefit | 0 | 0 | -68.1854 | 244.7862 | 355.0968 | 431.3753 | 572.4944 | 629.5165 | 691.1494 | 720.5298 | 751.1043 | 832.6816 | 759.8517 | 918.1277 | 1080.0856 | 1080.0856 | 1080.0856 | 1080.0856 | 1080.0856 | 1080.0856 | 1080.0856 | 1080.0856 | 1080.0856 | 1080.0856 | 1080.0856 | 1080.0856 | 1080.0856 | 1080.0856 | 1080.0856 | 1080.0856
|  |  | EUE Value ($m, real $2024) | 3.3072 | 65.4291 | 247.1322 | 37.6134 | 6.2242 | 7.0478 | 8.1309 | 9.3539 | 10.9432 | 12.7515 | 15.5559 | 21.5268 | 21.7209 | 36.3614 | 58.0848 | 58.0848 | 58.0848 | 58.0848 | 58.0848 | 58.0848 | 58.0848 | 58.0848 | 58.0848 | 58.0848 | 58.0848 | 58.0848 | 58.0848 | 58.0848 | 58.0848 | 58.0848
|  |  | Annualised capex | 0 | 0 | 3.8335 | 3.8335 | 3.8335 | 3.8335 | 3.8335 | 3.8335 | 3.8335 | 3.8335 | 3.8335 | 3.8335 | 3.8335 | 3.8335 | 3.8335 | 3.8335 | 3.8335 | 3.8335 | 3.8335 | 3.8335 | 3.8335 | 3.8335 | 3.8335 | 3.8335 | 3.8335 | 3.8335 | 3.8335 | 3.8335 | 3.8335 | 3.8335
|  |  | Annualised cost (capex+opex) | 0 | 0 | 3.8335 | 4.5154 | 4.5154 | 4.5154 | 4.5154 | 4.5154 | 4.5154 | 4.5154 | 4.5154 | 4.5154 | 4.5154 | 4.5154 | 4.5154 | 4.5154 | 4.5154 | 4.5154 | 4.5154 | 4.5154 | 4.5154 | 4.5154 | 4.5154 | 4.5154 | 4.5154 | 4.5154 | 4.5154 | 4.5154 | 4.5154 | 4.5154
|  |  | Optimal timing (interim calc) | 0 | 0 | 0 | 1 | 1 | 1 | 1 | [19 empty] | 1 | 1 | 1 | 1 | bar: 1 to 19
|  |  | Optimal timing | - | - | - | Yes | - | - | - | [19 empty] | - | - | - | - | bar: 1 to 19
Adjusted For Optimal Timing: | 62.9081 | 68.1854 | Capex | 0 | 0 | 68.1854 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 10.1471 | 18.4101 | Opex | 0 | 0 | 0 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185
| 12253.1003 | 24206.4938 | Reduction in unserved energy | 0 | 0 | 0 | 245.468 | 355.7787 | 432.0571 | 573.1763 | 630.1983 | 691.8313 | 721.2116 | 751.7861 | 833.3634 | 760.5335 | 918.8095 | 1080.7675 | 1080.7675 | 1080.7675 | 1080.7675 | 1080.7675 | 1080.7675 | 1080.7675 | 1080.7675 | 1080.7675 | 1080.7675 | 1080.7675 | 1080.7675 | 1080.7675 | 1080.7675 | 1080.7675 | 1080.7675
| 12180.0451 | 24119.8983 | Net benefit | 0 | 0 | -68.1854 | 244.7862 | 355.0968 | 431.3753 | 572.4944 | 629.5165 | 691.1494 | 720.5298 | 751.1043 | 832.6816 | 759.8517 | 918.1277 | 1080.0856 | 1080.0856 | 1080.0856 | 1080.0856 | 1080.0856 | 1080.0856 | 1080.0856 | 1080.0856 | 1080.0856 | 1080.0856 | 1080.0856 | 1080.0856 | 1080.0856 | 1080.0856 | 1080.0856 | 1080.0856
Option 7
Determining Optimal Timing: | Discounted | Undiscounted
| 34.157 | 37.0224 | Capex | 0 | 0 | 37.0224 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 5.5095 | 9.996 | Opex | 0 | 0 | 0 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022
| 10061.5037 | 19432.1091 | Reduction in unserved energy | 0 | 0 | 0 | 243.5469 | 350.9258 | 423.345 | 556.6521 | 603.3027 | 650.1521 | 661.3713 | 671.6924 | 711.8687 | 638.2834 | 731.9998 | 824.3106 | 824.3106 | 824.3106 | 824.3106 | 824.3106 | 824.3106 | 824.3106 | 824.3106 | 824.3106 | 824.3106 | 824.3106 | 824.3106 | 824.3106 | 824.3106 | 824.3106 | 824.3106
| 10021.8372 | 19385.0907 | Net benefit | 0 | 0 | -37.0224 | 243.1767 | 350.5556 | 422.9748 | 556.2818 | 602.9325 | 649.7819 | 661.0011 | 671.3222 | 711.4984 | 637.9131 | 731.6296 | 823.9403 | 823.9403 | 823.9403 | 823.9403 | 823.9403 | 823.9403 | 823.9403 | 823.9403 | 823.9403 | 823.9403 | 823.9403 | 823.9403 | 823.9403 | 823.9403 | 823.9403 | 823.9403
|  |  | EUE Value ($m, real $2024) | 3.3072 | 65.4291 | 247.1322 | 39.5345 | 11.0771 | 15.7599 | 24.6551 | 36.2495 | 52.6223 | 72.5919 | 95.6496 | 143.0216 | 143.9711 | 223.1711 | 314.5418 | 314.5418 | 314.5418 | 314.5418 | 314.5418 | 314.5418 | 314.5418 | 314.5418 | 314.5418 | 314.5418 | 314.5418 | 314.5418 | 314.5418 | 314.5418 | 314.5418 | 314.5418
|  |  | Annualised capex | 0 | 0 | 2.0815 | 2.0815 | 2.0815 | 2.0815 | 2.0815 | 2.0815 | 2.0815 | 2.0815 | 2.0815 | 2.0815 | 2.0815 | 2.0815 | 2.0815 | 2.0815 | 2.0815 | 2.0815 | 2.0815 | 2.0815 | 2.0815 | 2.0815 | 2.0815 | 2.0815 | 2.0815 | 2.0815 | 2.0815 | 2.0815 | 2.0815 | 2.0815
|  |  | Annualised cost (capex+opex) | 0 | 0 | 2.0815 | 2.4517 | 2.4517 | 2.4517 | 2.4517 | 2.4517 | 2.4517 | 2.4517 | 2.4517 | 2.4517 | 2.4517 | 2.4517 | 2.4517 | 2.4517 | 2.4517 | 2.4517 | 2.4517 | 2.4517 | 2.4517 | 2.4517 | 2.4517 | 2.4517 | 2.4517 | 2.4517 | 2.4517 | 2.4517 | 2.4517 | 2.4517
|  |  | Optimal timing (interim calc) | 0 | 0 | 0 | 1 | 1 | 1 | 1 | [19 empty] | 1 | 1 | 1 | 1 | bar: 1 to 19
|  |  | Optimal timing | - | - | - | Yes | - | - | - | [19 empty] | - | - | - | - | bar: 1 to 19
Adjusted For Optimal Timing: | 34.157 | 37.0224 | Capex | 0 | 0 | 37.0224 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 5.5095 | 9.996 | Opex | 0 | 0 | 0 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022
| 10061.5037 | 19432.1091 | Reduction in unserved energy | 0 | 0 | 0 | 243.5469 | 350.9258 | 423.345 | 556.6521 | 603.3027 | 650.1521 | 661.3713 | 671.6924 | 711.8687 | 638.2834 | 731.9998 | 824.3106 | 824.3106 | 824.3106 | 824.3106 | 824.3106 | 824.3106 | 824.3106 | 824.3106 | 824.3106 | 824.3106 | 824.3106 | 824.3106 | 824.3106 | 824.3106 | 824.3106 | 824.3106
| 10021.8372 | 19385.0907 | Net benefit | 0 | 0 | -37.0224 | 243.1767 | 350.5556 | 422.9748 | 556.2818 | 602.9325 | 649.7819 | 661.0011 | 671.3222 | 711.4984 | 637.9131 | 731.6296 | 823.9403 | 823.9403 | 823.9403 | 823.9403 | 823.9403 | 823.9403 | 823.9403 | 823.9403 | 823.9403 | 823.9403 | 823.9403 | 823.9403 | 823.9403 | 823.9403 | 823.9403 | 823.9403
Option 8
Determining Optimal Timing: | Discounted | Undiscounted
| 48.9369 | 53.0422 | Capex | 0 | 0 | 53.0422 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 7.8935 | 14.3214 | Opex | 0 | 0 | 0 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042
| 4995.5878 | 10535.8711 | Reduction in unserved energy | 0 | 0 | 0 | 7.5218 | 74.6435 | 97.6009 | 115.718 | 135.0626 | 159.1861 | 184.1202 | 215.4688 | 290.4585 | 275.411 | 400.6215 | 536.2536 | 536.2536 | 536.2536 | 536.2536 | 536.2536 | 536.2536 | 536.2536 | 536.2536 | 536.2536 | 536.2536 | 536.2536 | 536.2536 | 536.2536 | 536.2536 | 536.2536 | 536.2536
| 4938.7573 | 10468.5075 | Net benefit | 0 | 0 | -53.0422 | 6.9913 | 74.1131 | 97.0705 | 115.1875 | 134.5322 | 158.6557 | 183.5898 | 214.9384 | 289.9281 | 274.8806 | 400.0911 | 535.7232 | 535.7232 | 535.7232 | 535.7232 | 535.7232 | 535.7232 | 535.7232 | 535.7232 | 535.7232 | 535.7232 | 535.7232 | 535.7232 | 535.7232 | 535.7232 | 535.7232 | 535.7232
|  |  | EUE Value ($m, real $2024) | 3.3072 | 65.4291 | 247.1322 | 275.5596 | 287.3594 | 341.504 | 465.5892 | 504.4896 | 543.5884 | 549.8429 | 551.8732 | 564.4318 | 506.8434 | 554.5494 | 602.5987 | 602.5987 | 602.5987 | 602.5987 | 602.5987 | 602.5987 | 602.5987 | 602.5987 | 602.5987 | 602.5987 | 602.5987 | 602.5987 | 602.5987 | 602.5987 | 602.5987 | 602.5987
|  |  | Annualised capex | 0 | 0 | 2.9821 | 2.9821 | 2.9821 | 2.9821 | 2.9821 | 2.9821 | 2.9821 | 2.9821 | 2.9821 | 2.9821 | 2.9821 | 2.9821 | 2.9821 | 2.9821 | 2.9821 | 2.9821 | 2.9821 | 2.9821 | 2.9821 | 2.9821 | 2.9821 | 2.9821 | 2.9821 | 2.9821 | 2.9821 | 2.9821 | 2.9821 | 2.9821
|  |  | Annualised cost (capex+opex) | 0 | 0 | 2.9821 | 3.5126 | 3.5126 | 3.5126 | 3.5126 | 3.5126 | 3.5126 | 3.5126 | 3.5126 | 3.5126 | 3.5126 | 3.5126 | 3.5126 | 3.5126 | 3.5126 | 3.5126 | 3.5126 | 3.5126 | 3.5126 | 3.5126 | 3.5126 | 3.5126 | 3.5126 | 3.5126 | 3.5126 | 3.5126 | 3.5126 | 3.5126
|  |  | Optimal timing (interim calc) | 0 | 0 | 0 | 1 | 1 | 1 | 1 | [19 empty] | 1 | 1 | 1 | 1 | bar: 1 to 19
|  |  | Optimal timing | - | - | - | Yes | - | - | - | [19 empty] | - | - | - | - | bar: 1 to 19
Adjusted For Optimal Timing: | 48.9369 | 53.0422 | Capex | 0 | 0 | 53.0422 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 7.8935 | 14.3214 | Opex | 0 | 0 | 0 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042
| 4995.5878 | 10535.8711 | Reduction in unserved energy | 0 | 0 | 0 | 7.5218 | 74.6435 | 97.6009 | 115.718 | 135.0626 | 159.1861 | 184.1202 | 215.4688 | 290.4585 | 275.411 | 400.6215 | 536.2536 | 536.2536 | 536.2536 | 536.2536 | 536.2536 | 536.2536 | 536.2536 | 536.2536 | 536.2536 | 536.2536 | 536.2536 | 536.2536 | 536.2536 | 536.2536 | 536.2536 | 536.2536
| 4938.7573 | 10468.5075 | Net benefit | 0 | 0 | -53.0422 | 6.9913 | 74.1131 | 97.0705 | 115.1875 | 134.5322 | 158.6557 | 183.5898 | 214.9384 | 289.9281 | 274.8806 | 400.0911 | 535.7232 | 535.7232 | 535.7232 | 535.7232 | 535.7232 | 535.7232 | 535.7232 | 535.7232 | 535.7232 | 535.7232 | 535.7232 | 535.7232 | 535.7232 | 535.7232 | 535.7232 | 535.7232
Option 9
Determining Optimal Timing: | Discounted | Undiscounted
| 45.394 | 49.2021 | Capex | 0 | 0 | 49.2021 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 7.3221 | 13.2846 | Opex | 0 | 0 | 0 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202
| 10223.8291 | 19748.3321 | Reduction in unserved energy | 0 | 0 | 0 | 248.8786 | 356.798 | 429.8384 | 563.9003 | 611.3104 | 658.8656 | 670.8188 | 682.0288 | 723.0532 | 650.1203 | 744.8226 | 837.9936 | 837.9936 | 837.9936 | 837.9936 | 837.9936 | 837.9936 | 837.9936 | 837.9936 | 837.9936 | 837.9936 | 837.9936 | 837.9936 | 837.9936 | 837.9936 | 837.9936 | 837.9936
| 10171.113 | 19685.8454 | Net benefit | 0 | 0 | -49.2021 | 248.3866 | 356.306 | 429.3464 | 563.4083 | 610.8183 | 658.3735 | 670.3267 | 681.5368 | 722.5612 | 649.6283 | 744.3306 | 837.5015 | 837.5015 | 837.5015 | 837.5015 | 837.5015 | 837.5015 | 837.5015 | 837.5015 | 837.5015 | 837.5015 | 837.5015 | 837.5015 | 837.5015 | 837.5015 | 837.5015 | 837.5015
|  |  | EUE Value ($m, real $2024) | 3.3072 | 65.4291 | 247.1322 | 34.2028 | 5.2049 | 9.2665 | 17.4069 | 28.2418 | 43.9089 | 63.1444 | 85.3132 | 131.8371 | 132.1341 | 210.3483 | 300.8588 | 300.8588 | 300.8588 | 300.8588 | 300.8588 | 300.8588 | 300.8588 | 300.8588 | 300.8588 | 300.8588 | 300.8588 | 300.8588 | 300.8588 | 300.8588 | 300.8588 | 300.8588
|  |  | Annualised capex | 0 | 0 | 2.7662 | 2.7662 | 2.7662 | 2.7662 | 2.7662 | 2.7662 | 2.7662 | 2.7662 | 2.7662 | 2.7662 | 2.7662 | 2.7662 | 2.7662 | 2.7662 | 2.7662 | 2.7662 | 2.7662 | 2.7662 | 2.7662 | 2.7662 | 2.7662 | 2.7662 | 2.7662 | 2.7662 | 2.7662 | 2.7662 | 2.7662 | 2.7662
|  |  | Annualised cost (capex+opex) | 0 | 0 | 2.7662 | 3.2583 | 3.2583 | 3.2583 | 3.2583 | 3.2583 | 3.2583 | 3.2583 | 3.2583 | 3.2583 | 3.2583 | 3.2583 | 3.2583 | 3.2583 | 3.2583 | 3.2583 | 3.2583 | 3.2583 | 3.2583 | 3.2583 | 3.2583 | 3.2583 | 3.2583 | 3.2583 | 3.2583 | 3.2583 | 3.2583 | 3.2583
|  |  | Optimal timing (interim calc) | 0 | 0 | 0 | 1 | 1 | 1 | 1 | [19 empty] | 1 | 1 | 1 | 1 | bar: 1 to 19
|  |  | Optimal timing | - | - | - | Yes | - | - | - | [19 empty] | - | - | - | - | bar: 1 to 19
Adjusted For Optimal Timing: | 45.394 | 49.2021 | Capex | 0 | 0 | 49.2021 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 7.3221 | 13.2846 | Opex | 0 | 0 | 0 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202
| 10223.8291 | 19748.3321 | Reduction in unserved energy | 0 | 0 | 0 | 248.8786 | 356.798 | 429.8384 | 563.9003 | 611.3104 | 658.8656 | 670.8188 | 682.0288 | 723.0532 | 650.1203 | 744.8226 | 837.9936 | 837.9936 | 837.9936 | 837.9936 | 837.9936 | 837.9936 | 837.9936 | 837.9936 | 837.9936 | 837.9936 | 837.9936 | 837.9936 | 837.9936 | 837.9936 | 837.9936 | 837.9936
| 10171.113 | 19685.8454 | Net benefit | 0 | 0 | -49.2021 | 248.3866 | 356.306 | 429.3464 | 563.4083 | 610.8183 | 658.3735 | 670.3267 | 681.5368 | 722.5612 | 649.6283 | 744.3306 | 837.5015 | 837.5015 | 837.5015 | 837.5015 | 837.5015 | 837.5015 | 837.5015 | 837.5015 | 837.5015 | 837.5015 | 837.5015 | 837.5015 | 837.5015 | 837.5015 | 837.5015 | 837.5015
Option 10
Determining Optimal Timing: | Discounted | Undiscounted
| 0 | 0 | Capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 7840.1635 | 15208.189 | Opex | 0.48285 | 57.8283 | 189.4866 | 207.6844 | 245.4848 | 279.2209 | 339.624 | 384.4625 | 426.7802 | 445.1879 | 469.6214 | 502.6026 | 486.2654 | 573.3683 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055
| 7840.1635 | 15208.189 | Reduction in unserved energy | 0.48285 | 57.8283 | 189.4866 | 207.6844 | 245.4848 | 279.2209 | 339.624 | 384.4625 | 426.7802 | 445.1879 | 469.6214 | 502.6026 | 486.2654 | 573.3683 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055
| 0 | 0 | Net benefit | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | EUE Value ($m, real $2024) | 2.8305 | 7.6008 | 57.6455 | 75.397 | 116.5181 | 159.884 | 241.6832 | 255.0898 | 275.9942 | 288.7753 | 297.7206 | 352.2877 | 295.989 | 381.8026 | 476.3468 | 476.3468 | 476.3468 | 476.3468 | 476.3468 | 476.3468 | 476.3468 | 476.3468 | 476.3468 | 476.3468 | 476.3468 | 476.3468 | 476.3468 | 476.3468 | 476.3468 | 476.3468
|  |  | Annualised capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Annualised cost (capex+opex) | 0.48285 | 57.8283 | 189.4866 | 207.6844 | 245.4848 | 279.2209 | 339.624 | 384.4625 | 426.7802 | 445.1879 | 469.6214 | 502.6026 | 486.2654 | 573.3683 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055
|  |  | Optimal timing (interim calc) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Optimal timing | - | - | - | - | - | - | - | [19 empty] | - | - | - | - | bar: 1 to 19
Adjusted For Optimal Timing: | 0 | 0 | Capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 7840.1635 | 15208.189 | Opex | 0.48285 | 57.8283 | 189.4866 | 207.6844 | 245.4848 | 279.2209 | 339.624 | 384.4625 | 426.7802 | 445.1879 | 469.6214 | 502.6026 | 486.2654 | 573.3683 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055
| 7840.1635 | 15208.189 | Reduction in unserved energy | 0.48285 | 57.8283 | 189.4866 | 207.6844 | 245.4848 | 279.2209 | 339.624 | 384.4625 | 426.7802 | 445.1879 | 469.6214 | 502.6026 | 486.2654 | 573.3683 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055
| 0 | 0 | Net benefit | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## 3.2.2 NPV (HiDiscount)
Economic inputs and assumptions
Scenario | Discount rate | Upper bound
| Cost | Central
| VCR | Central
|  | Central | Lower bound | Upper bound
| Discount rate | 5.56% | 4.11% | 7%
| Cost | 100% | 80% | 120%
| VCR | 100% | 80% | 120%
Asset life for calculating annualised capex (years) | Option 1 | 45
| Option 2 | 45
| Option 3 | 45
| Option 4 | 45
| Option 5 | 45
| Option 6 | 45
| Option 7 | 45
| Option 8 | 45
| Option 9 | 45
| Option 10 | 45
|  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30
|  |  |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Outputs | bar: 3 FY27; 7 FY31
Option 1
| Discounted | Undiscounted
| 0 | 0 | Capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Opex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Reduction in unserved energy | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Net benefit | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | EUE Value ($m, real $2024) | 3.3134 | 65.4291 | 247.1322 | 283.0814 | 362.0029 | 439.1049 | 581.3072 | 639.5522 | 702.7745 | 733.9632 | 767.342 | 854.8903 | 782.2544 | 955.1709 | 1138.8523 | 1138.8523 | 1138.8523 | 1138.8523 | 1138.8523 | 1138.8523 | 1138.8523 | 1138.8523 | 1138.8523 | 1138.8523 | 1138.8523 | 1138.8523 | 1138.8523 | 1138.8523 | 1138.8523 | 1138.8523
Option 2
Determining Optimal Timing: | Discounted | Undiscounted
| 62.9791 | 72.1048 | Capex | 0 | 0 | 72.1048 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 7.5491 | 19.4683 | Opex | 0 | 0 | 0 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105
| 8151.9167 | 24591.0207 | Reduction in unserved energy | 0 | 0 | 0 | 245.4928 | 298.3199 | 432.154 | 573.2974 | 630.3857 | 692.15 | 721.8524 | 753.3537 | 837.7342 | 764.8598 | 929.6264 | 1106.9871 | 1106.9871 | 1106.9871 | 1106.9871 | 1106.9871 | 1106.9871 | 1106.9871 | 1106.9871 | 1106.9871 | 1106.9871 | 1106.9871 | 1106.9871 | 1106.9871 | 1106.9871 | 1106.9871 | 1106.9871
| 8081.3885 | 24499.4476 | Net benefit | 0 | 0 | -72.1048 | 244.7717 | 297.5989 | 431.4329 | 572.5764 | 629.6647 | 691.4289 | 721.1314 | 752.6327 | 837.0132 | 764.1388 | 928.9053 | 1106.2661 | 1106.2661 | 1106.2661 | 1106.2661 | 1106.2661 | 1106.2661 | 1106.2661 | 1106.2661 | 1106.2661 | 1106.2661 | 1106.2661 | 1106.2661 | 1106.2661 | 1106.2661 | 1106.2661 | 1106.2661
|  |  | EUE Value ($m, real $2024) | 3.3072 | 65.4291 | 247.1322 | 37.5886 | 63.683 | 6.9509 | 8.0097 | 9.1665 | 10.6245 | 12.1107 | 13.9883 | 17.1561 | 17.3946 | 25.5446 | 31.8652 | 31.8652 | 31.8652 | 31.8652 | 31.8652 | 31.8652 | 31.8652 | 31.8652 | 31.8652 | 31.8652 | 31.8652 | 31.8652 | 31.8652 | 31.8652 | 31.8652 | 31.8652
|  |  | Annualised capex | 0 | 0 | 3.8379 | 3.8379 | 3.8379 | 3.8379 | 3.8379 | 3.8379 | 3.8379 | 3.8379 | 3.8379 | 3.8379 | 3.8379 | 3.8379 | 3.8379 | 3.8379 | 3.8379 | 3.8379 | 3.8379 | 3.8379 | 3.8379 | 3.8379 | 3.8379 | 3.8379 | 3.8379 | 3.8379 | 3.8379 | 3.8379 | 3.8379 | 3.8379
|  |  | Annualised cost (capex+opex) | 0 | 0 | 3.8379 | 4.5589 | 4.5589 | 4.5589 | 4.5589 | 4.5589 | 4.5589 | 4.5589 | 4.5589 | 4.5589 | 4.5589 | 4.5589 | 4.5589 | 4.5589 | 4.5589 | 4.5589 | 4.5589 | 4.5589 | 4.5589 | 4.5589 | 4.5589 | 4.5589 | 4.5589 | 4.5589 | 4.5589 | 4.5589 | 4.5589 | 4.5589
|  |  | Optimal timing (interim calc) | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  |  | Optimal timing | - | - | - | Yes | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Adjusted For Optimal Timing: | 62.9791 | 72.1048 | Capex | 0 | 0 | 72.1048 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 7.5491 | 19.4683 | Opex | 0 | 0 | 0 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105
| 8151.9167 | 24591.0207 | Reduction in unserved energy | 0 | 0 | 0 | 245.4928 | 298.3199 | 432.154 | 573.2974 | 630.3857 | 692.15 | 721.8524 | 753.3537 | 837.7342 | 764.8598 | 929.6264 | 1106.9871 | 1106.9871 | 1106.9871 | 1106.9871 | 1106.9871 | 1106.9871 | 1106.9871 | 1106.9871 | 1106.9871 | 1106.9871 | 1106.9871 | 1106.9871 | 1106.9871 | 1106.9871 | 1106.9871 | 1106.9871
| 8081.3885 | 24499.4476 | Net benefit | 0 | 0 | -72.1048 | 244.7717 | 297.5989 | 431.4329 | 572.5764 | 629.6647 | 691.4289 | 721.1314 | 752.6327 | 837.0132 | 764.1388 | 928.9053 | 1106.2661 | 1106.2661 | 1106.2661 | 1106.2661 | 1106.2661 | 1106.2661 | 1106.2661 | 1106.2661 | 1106.2661 | 1106.2661 | 1106.2661 | 1106.2661 | 1106.2661 | 1106.2661 | 1106.2661 | 1106.2661
Option 3
Determining Optimal Timing: | Discounted | Undiscounted
| 38.0163 | 43.5248 | Capex | 0 | 0 | 43.5248 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 4.5569 | 11.7517 | Opex | 0 | 0 | 0 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525
| 6780.3466 | 19658.7761 | Reduction in unserved energy | 0 | 0 | 0 | 243.7522 | 294.2621 | 423.6585 | 557.0025 | 603.7113 | 650.6498 | 661.9773 | 672.5539 | 713.5507 | 640.2026 | 737.792 | 841.229 | 841.229 | 841.229 | 841.229 | 841.229 | 841.229 | 841.229 | 841.229 | 841.229 | 841.229 | 841.229 | 841.229 | 841.229 | 841.229 | 841.229 | 841.229
| 6737.7734 | 19603.4996 | Net benefit | 0 | 0 | -43.5248 | 243.3169 | 293.8268 | 423.2232 | 556.5672 | 603.276 | 650.2145 | 661.542 | 672.1186 | 713.1155 | 639.7674 | 737.3567 | 840.7937 | 840.7937 | 840.7937 | 840.7937 | 840.7937 | 840.7937 | 840.7937 | 840.7937 | 840.7937 | 840.7937 | 840.7937 | 840.7937 | 840.7937 | 840.7937 | 840.7937 | 840.7937
|  |  | EUE Value ($m, real $2024) | 3.3072 | 65.4291 | 247.1322 | 39.3292 | 67.7408 | 15.4464 | 24.3047 | 35.8409 | 52.1247 | 71.9859 | 94.7882 | 141.3396 | 142.0518 | 217.3789 | 297.6234 | 297.6234 | 297.6234 | 297.6234 | 297.6234 | 297.6234 | 297.6234 | 297.6234 | 297.6234 | 297.6234 | 297.6234 | 297.6234 | 297.6234 | 297.6234 | 297.6234 | 297.6234
|  |  | Annualised capex | 0 | 0 | 2.3167 | 2.3167 | 2.3167 | 2.3167 | 2.3167 | 2.3167 | 2.3167 | 2.3167 | 2.3167 | 2.3167 | 2.3167 | 2.3167 | 2.3167 | 2.3167 | 2.3167 | 2.3167 | 2.3167 | 2.3167 | 2.3167 | 2.3167 | 2.3167 | 2.3167 | 2.3167 | 2.3167 | 2.3167 | 2.3167 | 2.3167 | 2.3167
|  |  | Annualised cost (capex+opex) | 0 | 0 | 2.3167 | 2.7519 | 2.7519 | 2.7519 | 2.7519 | 2.7519 | 2.7519 | 2.7519 | 2.7519 | 2.7519 | 2.7519 | 2.7519 | 2.7519 | 2.7519 | 2.7519 | 2.7519 | 2.7519 | 2.7519 | 2.7519 | 2.7519 | 2.7519 | 2.7519 | 2.7519 | 2.7519 | 2.7519 | 2.7519 | 2.7519 | 2.7519
|  |  | Optimal timing (interim calc) | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  |  | Optimal timing | - | - | - | Yes | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Adjusted For Optimal Timing: | 38.0163 | 43.5248 | Capex | 0 | 0 | 43.5248 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 4.5569 | 11.7517 | Opex | 0 | 0 | 0 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525
| 6780.3466 | 19658.7761 | Reduction in unserved energy | 0 | 0 | 0 | 243.7522 | 294.2621 | 423.6585 | 557.0025 | 603.7113 | 650.6498 | 661.9773 | 672.5539 | 713.5507 | 640.2026 | 737.792 | 841.229 | 841.229 | 841.229 | 841.229 | 841.229 | 841.229 | 841.229 | 841.229 | 841.229 | 841.229 | 841.229 | 841.229 | 841.229 | 841.229 | 841.229 | 841.229
| 6737.7734 | 19603.4996 | Net benefit | 0 | 0 | -43.5248 | 243.3169 | 293.8268 | 423.2232 | 556.5672 | 603.276 | 650.2145 | 661.542 | 672.1186 | 713.1155 | 639.7674 | 737.3567 | 840.7937 | 840.7937 | 840.7937 | 840.7937 | 840.7937 | 840.7937 | 840.7937 | 840.7937 | 840.7937 | 840.7937 | 840.7937 | 840.7937 | 840.7937 | 840.7937 | 840.7937 | 840.7937
Option 4
Determining Optimal Timing: | Discounted | Undiscounted
| 52.0086 | 59.5447 | Capex | 0 | 0 | 59.5447 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 6.2341 | 16.0771 | Opex | 0 | 0 | 0 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545
| 3166.1355 | 10808.4009 | Reduction in unserved energy | 0 | 0 | 0 | 7.653 | 18.0781 | 97.9688 | 116.1458 | 135.5643 | 159.7892 | 184.879 | 216.5434 | 292.8216 | 278.5136 | 408.2495 | 555.7622 | 555.7622 | 555.7622 | 555.7622 | 555.7622 | 555.7622 | 555.7622 | 555.7622 | 555.7622 | 555.7622 | 555.7622 | 555.7622 | 555.7622 | 555.7622 | 555.7622 | 555.7622
| 3107.8928 | 10732.7791 | Net benefit | 0 | 0 | -59.5447 | 7.0575 | 17.4827 | 97.3733 | 115.5503 | 134.9689 | 159.1938 | 184.2835 | 215.9479 | 292.2261 | 277.9181 | 407.6541 | 555.1667 | 555.1667 | 555.1667 | 555.1667 | 555.1667 | 555.1667 | 555.1667 | 555.1667 | 555.1667 | 555.1667 | 555.1667 | 555.1667 | 555.1667 | 555.1667 | 555.1667 | 555.1667
|  |  | EUE Value ($m, real $2024) | 3.3072 | 65.4291 | 247.1322 | 275.4284 | 343.9248 | 341.1361 | 465.1614 | 503.9879 | 542.9852 | 549.0842 | 550.7987 | 562.0687 | 503.7408 | 546.9214 | 583.0902 | 583.0902 | 583.0902 | 583.0902 | 583.0902 | 583.0902 | 583.0902 | 583.0902 | 583.0902 | 583.0902 | 583.0902 | 583.0902 | 583.0902 | 583.0902 | 583.0902 | 583.0902
|  |  | Annualised capex | 0 | 0 | 3.1693 | 3.1693 | 3.1693 | 3.1693 | 3.1693 | 3.1693 | 3.1693 | 3.1693 | 3.1693 | 3.1693 | 3.1693 | 3.1693 | 3.1693 | 3.1693 | 3.1693 | 3.1693 | 3.1693 | 3.1693 | 3.1693 | 3.1693 | 3.1693 | 3.1693 | 3.1693 | 3.1693 | 3.1693 | 3.1693 | 3.1693 | 3.1693
|  |  | Annualised cost (capex+opex) | 0 | 0 | 3.1693 | 3.7648 | 3.7648 | 3.7648 | 3.7648 | 3.7648 | 3.7648 | 3.7648 | 3.7648 | 3.7648 | 3.7648 | 3.7648 | 3.7648 | 3.7648 | 3.7648 | 3.7648 | 3.7648 | 3.7648 | 3.7648 | 3.7648 | 3.7648 | 3.7648 | 3.7648 | 3.7648 | 3.7648 | 3.7648 | 3.7648 | 3.7648
|  |  | Optimal timing (interim calc) | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  |  | Optimal timing | - | - | - | Yes | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
[11 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19
Adjusted For Optimal Timing: | 52.0086 | 59.5447 | Capex | 0 | 0 | 59.5447 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 6.2341 | 16.0771 | Opex | 0 | 0 | 0 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545
| 3166.1355 | 10808.4009 | Reduction in unserved energy | 0 | 0 | 0 | 7.653 | 18.0781 | 97.9688 | 116.1458 | 135.5643 | 159.7892 | 184.879 | 216.5434 | 292.8216 | 278.5136 | 408.2495 | 555.7622 | 555.7622 | 555.7622 | 555.7622 | 555.7622 | 555.7622 | 555.7622 | 555.7622 | 555.7622 | 555.7622 | 555.7622 | 555.7622 | 555.7622 | 555.7622 | 555.7622 | 555.7622
| 3107.8928 | 10732.7791 | Net benefit | 0 | 0 | -59.5447 | 7.0575 | 17.4827 | 97.3733 | 115.5503 | 134.9689 | 159.1938 | 184.2835 | 215.9479 | 292.2261 | 277.9181 | 407.6541 | 555.1667 | 555.1667 | 555.1667 | 555.1667 | 555.1667 | 555.1667 | 555.1667 | 555.1667 | 555.1667 | 555.1667 | 555.1667 | 555.1667 | 555.1667 | 555.1667 | 555.1667 | 555.1667
Option 5
Determining Optimal Timing: | Discounted | Undiscounted
| 48.6546 | 55.7046 | Capex | 0 | 0 | 55.7046 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 5.8321 | 15.0402 | Opex | 0 | 0 | 0 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705
| 6888.5262 | 19974.6734 | Reduction in unserved energy | 0 | 0 | 0 | 249.0844 | 300.1349 | 430.1528 | 564.2523 | 611.7211 | 659.3657 | 671.4363 | 682.8319 | 724.6792 | 652.0574 | 750.6505 | 854.8942 | 854.8942 | 854.8942 | 854.8942 | 854.8942 | 854.8942 | 854.8942 | 854.8942 | 854.8942 | 854.8942 | 854.8942 | 854.8942 | 854.8942 | 854.8942 | 854.8942 | 854.8942
| 6834.0396 | 19903.9285 | Net benefit | 0 | 0 | -55.7046 | 248.5274 | 299.5779 | 429.5958 | 563.6952 | 611.1641 | 658.8086 | 670.8792 | 682.2748 | 724.1222 | 651.5004 | 750.0935 | 854.3371 | 854.3371 | 854.3371 | 854.3371 | 854.3371 | 854.3371 | 854.3371 | 854.3371 | 854.3371 | 854.3371 | 854.3371 | 854.3371 | 854.3371 | 854.3371 | 854.3371 | 854.3371
|  |  | EUE Value ($m, real $2024) | 3.3072 | 65.4291 | 247.1322 | 33.9969 | 61.868 | 8.9521 | 17.0549 | 27.8311 | 43.4088 | 62.5269 | 84.5102 | 130.2111 | 130.197 | 204.5204 | 283.9581 | 283.9581 | 283.9581 | 283.9581 | 283.9581 | 283.9581 | 283.9581 | 283.9581 | 283.9581 | 283.9581 | 283.9581 | 283.9581 | 283.9581 | 283.9581 | 283.9581 | 283.9581
|  |  | Annualised capex | 0 | 0 | 2.9649 | 2.9649 | 2.9649 | 2.9649 | 2.9649 | 2.9649 | 2.9649 | 2.9649 | 2.9649 | 2.9649 | 2.9649 | 2.9649 | 2.9649 | 2.9649 | 2.9649 | 2.9649 | 2.9649 | 2.9649 | 2.9649 | 2.9649 | 2.9649 | 2.9649 | 2.9649 | 2.9649 | 2.9649 | 2.9649 | 2.9649 | 2.9649
|  |  | Annualised cost (capex+opex) | 0 | 0 | 2.9649 | 3.522 | 3.522 | 3.522 | 3.522 | 3.522 | 3.522 | 3.522 | 3.522 | 3.522 | 3.522 | 3.522 | 3.522 | 3.522 | 3.522 | 3.522 | 3.522 | 3.522 | 3.522 | 3.522 | 3.522 | 3.522 | 3.522 | 3.522 | 3.522 | 3.522 | 3.522 | 3.522
|  |  | Optimal timing (interim calc) | 0 | 0 | 0 | 1 | 1 | 1 | 1 | [19 empty] | 1 | 1 | 1 | 1 | bar: 1 to 19
|  |  | Optimal timing | - | - | - | Yes | - | - | - | [19 empty] | - | - | - | - | bar: 1 to 19
Adjusted For Optimal Timing: | 48.6546 | 55.7046 | Capex | 0 | 0 | 55.7046 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 5.8321 | 15.0402 | Opex | 0 | 0 | 0 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705
| 6888.5262 | 19974.6734 | Reduction in unserved energy | 0 | 0 | 0 | 249.0844 | 300.1349 | 430.1528 | 564.2523 | 611.7211 | 659.3657 | 671.4363 | 682.8319 | 724.6792 | 652.0574 | 750.6505 | 854.8942 | 854.8942 | 854.8942 | 854.8942 | 854.8942 | 854.8942 | 854.8942 | 854.8942 | 854.8942 | 854.8942 | 854.8942 | 854.8942 | 854.8942 | 854.8942 | 854.8942 | 854.8942
| 6834.0396 | 19903.9285 | Net benefit | 0 | 0 | -55.7046 | 248.5274 | 299.5779 | 429.5958 | 563.6952 | 611.1641 | 658.8086 | 670.8792 | 682.2748 | 724.1222 | 651.5004 | 750.0935 | 854.3371 | 854.3371 | 854.3371 | 854.3371 | 854.3371 | 854.3371 | 854.3371 | 854.3371 | 854.3371 | 854.3371 | 854.3371 | 854.3371 | 854.3371 | 854.3371 | 854.3371 | 854.3371
Option 6
Determining Optimal Timing: | Discounted | Undiscounted
| 59.5558 | 68.1854 | Capex | 0 | 0 | 68.1854 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 7.1388 | 18.4101 | Opex | 0 | 0 | 0 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185
| 8082.8664 | 24206.4938 | Reduction in unserved energy | 0 | 0 | 0 | 245.468 | 355.7787 | 432.0571 | 573.1763 | 630.1983 | 691.8313 | 721.2116 | 751.7861 | 833.3634 | 760.5335 | 918.8095 | 1080.7675 | 1080.7675 | 1080.7675 | 1080.7675 | 1080.7675 | 1080.7675 | 1080.7675 | 1080.7675 | 1080.7675 | 1080.7675 | 1080.7675 | 1080.7675 | 1080.7675 | 1080.7675 | 1080.7675 | 1080.7675
| 8016.1718 | 24119.8983 | Net benefit | 0 | 0 | -68.1854 | 244.7862 | 355.0968 | 431.3753 | 572.4944 | 629.5165 | 691.1494 | 720.5298 | 751.1043 | 832.6816 | 759.8517 | 918.1277 | 1080.0856 | 1080.0856 | 1080.0856 | 1080.0856 | 1080.0856 | 1080.0856 | 1080.0856 | 1080.0856 | 1080.0856 | 1080.0856 | 1080.0856 | 1080.0856 | 1080.0856 | 1080.0856 | 1080.0856 | 1080.0856
|  |  | EUE Value ($m, real $2024) | 3.3072 | 65.4291 | 247.1322 | 37.6134 | 6.2242 | 7.0478 | 8.1309 | 9.3539 | 10.9432 | 12.7515 | 15.5559 | 21.5268 | 21.7209 | 36.3614 | 58.0848 | 58.0848 | 58.0848 | 58.0848 | 58.0848 | 58.0848 | 58.0848 | 58.0848 | 58.0848 | 58.0848 | 58.0848 | 58.0848 | 58.0848 | 58.0848 | 58.0848 | 58.0848
|  |  | Annualised capex | 0 | 0 | 3.6292 | 3.6292 | 3.6292 | 3.6292 | 3.6292 | 3.6292 | 3.6292 | 3.6292 | 3.6292 | 3.6292 | 3.6292 | 3.6292 | 3.6292 | 3.6292 | 3.6292 | 3.6292 | 3.6292 | 3.6292 | 3.6292 | 3.6292 | 3.6292 | 3.6292 | 3.6292 | 3.6292 | 3.6292 | 3.6292 | 3.6292 | 3.6292
|  |  | Annualised cost (capex+opex) | 0 | 0 | 3.6292 | 4.3111 | 4.3111 | 4.3111 | 4.3111 | 4.3111 | 4.3111 | 4.3111 | 4.3111 | 4.3111 | 4.3111 | 4.3111 | 4.3111 | 4.3111 | 4.3111 | 4.3111 | 4.3111 | 4.3111 | 4.3111 | 4.3111 | 4.3111 | 4.3111 | 4.3111 | 4.3111 | 4.3111 | 4.3111 | 4.3111 | 4.3111
|  |  | Optimal timing (interim calc) | 0 | 0 | 0 | 1 | 1 | 1 | 1 | [19 empty] | 1 | 1 | 1 | 1 | bar: 1 to 19
|  |  | Optimal timing | - | - | - | Yes | - | - | - | [19 empty] | - | - | - | - | bar: 1 to 19
Adjusted For Optimal Timing: | 59.5558 | 68.1854 | Capex | 0 | 0 | 68.1854 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 7.1388 | 18.4101 | Opex | 0 | 0 | 0 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185
| 8082.8664 | 24206.4938 | Reduction in unserved energy | 0 | 0 | 0 | 245.468 | 355.7787 | 432.0571 | 573.1763 | 630.1983 | 691.8313 | 721.2116 | 751.7861 | 833.3634 | 760.5335 | 918.8095 | 1080.7675 | 1080.7675 | 1080.7675 | 1080.7675 | 1080.7675 | 1080.7675 | 1080.7675 | 1080.7675 | 1080.7675 | 1080.7675 | 1080.7675 | 1080.7675 | 1080.7675 | 1080.7675 | 1080.7675 | 1080.7675
| 8016.1718 | 24119.8983 | Net benefit | 0 | 0 | -68.1854 | 244.7862 | 355.0968 | 431.3753 | 572.4944 | 629.5165 | 691.1494 | 720.5298 | 751.1043 | 832.6816 | 759.8517 | 918.1277 | 1080.0856 | 1080.0856 | 1080.0856 | 1080.0856 | 1080.0856 | 1080.0856 | 1080.0856 | 1080.0856 | 1080.0856 | 1080.0856 | 1080.0856 | 1080.0856 | 1080.0856 | 1080.0856 | 1080.0856 | 1080.0856
Option 7
Determining Optimal Timing: | Discounted | Undiscounted
| 32.3368 | 37.0224 | Capex | 0 | 0 | 37.0224 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 3.8761 | 9.996 | Opex | 0 | 0 | 0 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022
| 6751.2636 | 19432.1091 | Reduction in unserved energy | 0 | 0 | 0 | 243.5469 | 350.9258 | 423.345 | 556.6521 | 603.3027 | 650.1521 | 661.3713 | 671.6924 | 711.8687 | 638.2834 | 731.9998 | 824.3106 | 824.3106 | 824.3106 | 824.3106 | 824.3106 | 824.3106 | 824.3106 | 824.3106 | 824.3106 | 824.3106 | 824.3106 | 824.3106 | 824.3106 | 824.3106 | 824.3106 | 824.3106
| 6715.0507 | 19385.0907 | Net benefit | 0 | 0 | -37.0224 | 243.1767 | 350.5556 | 422.9748 | 556.2818 | 602.9325 | 649.7819 | 661.0011 | 671.3222 | 711.4984 | 637.9131 | 731.6296 | 823.9403 | 823.9403 | 823.9403 | 823.9403 | 823.9403 | 823.9403 | 823.9403 | 823.9403 | 823.9403 | 823.9403 | 823.9403 | 823.9403 | 823.9403 | 823.9403 | 823.9403 | 823.9403
|  |  | EUE Value ($m, real $2024) | 3.3072 | 65.4291 | 247.1322 | 39.5345 | 11.0771 | 15.7599 | 24.6551 | 36.2495 | 52.6223 | 72.5919 | 95.6496 | 143.0216 | 143.9711 | 223.1711 | 314.5418 | 314.5418 | 314.5418 | 314.5418 | 314.5418 | 314.5418 | 314.5418 | 314.5418 | 314.5418 | 314.5418 | 314.5418 | 314.5418 | 314.5418 | 314.5418 | 314.5418 | 314.5418
|  |  | Annualised capex | 0 | 0 | 1.9706 | 1.9706 | 1.9706 | 1.9706 | 1.9706 | 1.9706 | 1.9706 | 1.9706 | 1.9706 | 1.9706 | 1.9706 | 1.9706 | 1.9706 | 1.9706 | 1.9706 | 1.9706 | 1.9706 | 1.9706 | 1.9706 | 1.9706 | 1.9706 | 1.9706 | 1.9706 | 1.9706 | 1.9706 | 1.9706 | 1.9706 | 1.9706
|  |  | Annualised cost (capex+opex) | 0 | 0 | 1.9706 | 2.3408 | 2.3408 | 2.3408 | 2.3408 | 2.3408 | 2.3408 | 2.3408 | 2.3408 | 2.3408 | 2.3408 | 2.3408 | 2.3408 | 2.3408 | 2.3408 | 2.3408 | 2.3408 | 2.3408 | 2.3408 | 2.3408 | 2.3408 | 2.3408 | 2.3408 | 2.3408 | 2.3408 | 2.3408 | 2.3408 | 2.3408
|  |  | Optimal timing (interim calc) | 0 | 0 | 0 | 1 | 1 | 1 | 1 | [19 empty] | 1 | 1 | 1 | 1 | bar: 1 to 19
|  |  | Optimal timing | - | - | - | Yes | - | - | - | [19 empty] | - | - | - | - | bar: 1 to 19
Adjusted For Optimal Timing: | 32.3368 | 37.0224 | Capex | 0 | 0 | 37.0224 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 3.8761 | 9.996 | Opex | 0 | 0 | 0 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022
| 6751.2636 | 19432.1091 | Reduction in unserved energy | 0 | 0 | 0 | 243.5469 | 350.9258 | 423.345 | 556.6521 | 603.3027 | 650.1521 | 661.3713 | 671.6924 | 711.8687 | 638.2834 | 731.9998 | 824.3106 | 824.3106 | 824.3106 | 824.3106 | 824.3106 | 824.3106 | 824.3106 | 824.3106 | 824.3106 | 824.3106 | 824.3106 | 824.3106 | 824.3106 | 824.3106 | 824.3106 | 824.3106
| 6715.0507 | 19385.0907 | Net benefit | 0 | 0 | -37.0224 | 243.1767 | 350.5556 | 422.9748 | 556.2818 | 602.9325 | 649.7819 | 661.0011 | 671.3222 | 711.4984 | 637.9131 | 731.6296 | 823.9403 | 823.9403 | 823.9403 | 823.9403 | 823.9403 | 823.9403 | 823.9403 | 823.9403 | 823.9403 | 823.9403 | 823.9403 | 823.9403 | 823.9403 | 823.9403 | 823.9403 | 823.9403
Option 8
Determining Optimal Timing: | Discounted | Undiscounted
| 46.3291 | 53.0422 | Capex | 0 | 0 | 53.0422 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 5.5533 | 14.3214 | Opex | 0 | 0 | 0 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042
| 3124.8726 | 10535.8711 | Reduction in unserved energy | 0 | 0 | 0 | 7.5218 | 74.6435 | 97.6009 | 115.718 | 135.0626 | 159.1861 | 184.1202 | 215.4688 | 290.4585 | 275.411 | 400.6215 | 536.2536 | 536.2536 | 536.2536 | 536.2536 | 536.2536 | 536.2536 | 536.2536 | 536.2536 | 536.2536 | 536.2536 | 536.2536 | 536.2536 | 536.2536 | 536.2536 | 536.2536 | 536.2536
| 3072.9902 | 10468.5075 | Net benefit | 0 | 0 | -53.0422 | 6.9913 | 74.1131 | 97.0705 | 115.1875 | 134.5322 | 158.6557 | 183.5898 | 214.9384 | 289.9281 | 274.8806 | 400.0911 | 535.7232 | 535.7232 | 535.7232 | 535.7232 | 535.7232 | 535.7232 | 535.7232 | 535.7232 | 535.7232 | 535.7232 | 535.7232 | 535.7232 | 535.7232 | 535.7232 | 535.7232 | 535.7232
|  |  | EUE Value ($m, real $2024) | 3.3072 | 65.4291 | 247.1322 | 275.5596 | 287.3594 | 341.504 | 465.5892 | 504.4896 | 543.5884 | 549.8429 | 551.8732 | 564.4318 | 506.8434 | 554.5494 | 602.5987 | 602.5987 | 602.5987 | 602.5987 | 602.5987 | 602.5987 | 602.5987 | 602.5987 | 602.5987 | 602.5987 | 602.5987 | 602.5987 | 602.5987 | 602.5987 | 602.5987 | 602.5987
|  |  | Annualised capex | 0 | 0 | 2.8232 | 2.8232 | 2.8232 | 2.8232 | 2.8232 | 2.8232 | 2.8232 | 2.8232 | 2.8232 | 2.8232 | 2.8232 | 2.8232 | 2.8232 | 2.8232 | 2.8232 | 2.8232 | 2.8232 | 2.8232 | 2.8232 | 2.8232 | 2.8232 | 2.8232 | 2.8232 | 2.8232 | 2.8232 | 2.8232 | 2.8232 | 2.8232
|  |  | Annualised cost (capex+opex) | 0 | 0 | 2.8232 | 3.3536 | 3.3536 | 3.3536 | 3.3536 | 3.3536 | 3.3536 | 3.3536 | 3.3536 | 3.3536 | 3.3536 | 3.3536 | 3.3536 | 3.3536 | 3.3536 | 3.3536 | 3.3536 | 3.3536 | 3.3536 | 3.3536 | 3.3536 | 3.3536 | 3.3536 | 3.3536 | 3.3536 | 3.3536 | 3.3536 | 3.3536
|  |  | Optimal timing (interim calc) | 0 | 0 | 0 | 1 | 1 | 1 | 1 | [19 empty] | 1 | 1 | 1 | 1 | bar: 1 to 19
|  |  | Optimal timing | - | - | - | Yes | - | - | - | [19 empty] | - | - | - | - | bar: 1 to 19
Adjusted For Optimal Timing: | 46.3291 | 53.0422 | Capex | 0 | 0 | 53.0422 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 5.5533 | 14.3214 | Opex | 0 | 0 | 0 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042
| 3124.8726 | 10535.8711 | Reduction in unserved energy | 0 | 0 | 0 | 7.5218 | 74.6435 | 97.6009 | 115.718 | 135.0626 | 159.1861 | 184.1202 | 215.4688 | 290.4585 | 275.411 | 400.6215 | 536.2536 | 536.2536 | 536.2536 | 536.2536 | 536.2536 | 536.2536 | 536.2536 | 536.2536 | 536.2536 | 536.2536 | 536.2536 | 536.2536 | 536.2536 | 536.2536 | 536.2536 | 536.2536
| 3072.9902 | 10468.5075 | Net benefit | 0 | 0 | -53.0422 | 6.9913 | 74.1131 | 97.0705 | 115.1875 | 134.5322 | 158.6557 | 183.5898 | 214.9384 | 289.9281 | 274.8806 | 400.0911 | 535.7232 | 535.7232 | 535.7232 | 535.7232 | 535.7232 | 535.7232 | 535.7232 | 535.7232 | 535.7232 | 535.7232 | 535.7232 | 535.7232 | 535.7232 | 535.7232 | 535.7232 | 535.7232
Option 9
Determining Optimal Timing: | Discounted | Undiscounted
| 42.975 | 49.2021 | Capex | 0 | 0 | 49.2021 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 5.1513 | 13.2846 | Opex | 0 | 0 | 0 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202
| 6859.5347 | 19748.3321 | Reduction in unserved energy | 0 | 0 | 0 | 248.8786 | 356.798 | 429.8384 | 563.9003 | 611.3104 | 658.8656 | 670.8188 | 682.0288 | 723.0532 | 650.1203 | 744.8226 | 837.9936 | 837.9936 | 837.9936 | 837.9936 | 837.9936 | 837.9936 | 837.9936 | 837.9936 | 837.9936 | 837.9936 | 837.9936 | 837.9936 | 837.9936 | 837.9936 | 837.9936 | 837.9936
| 6811.4084 | 19685.8454 | Net benefit | 0 | 0 | -49.2021 | 248.3866 | 356.306 | 429.3464 | 563.4083 | 610.8183 | 658.3735 | 670.3267 | 681.5368 | 722.5612 | 649.6283 | 744.3306 | 837.5015 | 837.5015 | 837.5015 | 837.5015 | 837.5015 | 837.5015 | 837.5015 | 837.5015 | 837.5015 | 837.5015 | 837.5015 | 837.5015 | 837.5015 | 837.5015 | 837.5015 | 837.5015
|  |  | EUE Value ($m, real $2024) | 3.3072 | 65.4291 | 247.1322 | 34.2028 | 5.2049 | 9.2665 | 17.4069 | 28.2418 | 43.9089 | 63.1444 | 85.3132 | 131.8371 | 132.1341 | 210.3483 | 300.8588 | 300.8588 | 300.8588 | 300.8588 | 300.8588 | 300.8588 | 300.8588 | 300.8588 | 300.8588 | 300.8588 | 300.8588 | 300.8588 | 300.8588 | 300.8588 | 300.8588 | 300.8588
|  |  | Annualised capex | 0 | 0 | 2.6188 | 2.6188 | 2.6188 | 2.6188 | 2.6188 | 2.6188 | 2.6188 | 2.6188 | 2.6188 | 2.6188 | 2.6188 | 2.6188 | 2.6188 | 2.6188 | 2.6188 | 2.6188 | 2.6188 | 2.6188 | 2.6188 | 2.6188 | 2.6188 | 2.6188 | 2.6188 | 2.6188 | 2.6188 | 2.6188 | 2.6188 | 2.6188
|  |  | Annualised cost (capex+opex) | 0 | 0 | 2.6188 | 3.1109 | 3.1109 | 3.1109 | 3.1109 | 3.1109 | 3.1109 | 3.1109 | 3.1109 | 3.1109 | 3.1109 | 3.1109 | 3.1109 | 3.1109 | 3.1109 | 3.1109 | 3.1109 | 3.1109 | 3.1109 | 3.1109 | 3.1109 | 3.1109 | 3.1109 | 3.1109 | 3.1109 | 3.1109 | 3.1109 | 3.1109
|  |  | Optimal timing (interim calc) | 0 | 0 | 0 | 1 | 1 | 1 | 1 | [19 empty] | 1 | 1 | 1 | 1 | bar: 1 to 19
|  |  | Optimal timing | - | - | - | Yes | - | - | - | [19 empty] | - | - | - | - | bar: 1 to 19
Adjusted For Optimal Timing: | 42.975 | 49.2021 | Capex | 0 | 0 | 49.2021 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 5.1513 | 13.2846 | Opex | 0 | 0 | 0 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202
| 6859.5347 | 19748.3321 | Reduction in unserved energy | 0 | 0 | 0 | 248.8786 | 356.798 | 429.8384 | 563.9003 | 611.3104 | 658.8656 | 670.8188 | 682.0288 | 723.0532 | 650.1203 | 744.8226 | 837.9936 | 837.9936 | 837.9936 | 837.9936 | 837.9936 | 837.9936 | 837.9936 | 837.9936 | 837.9936 | 837.9936 | 837.9936 | 837.9936 | 837.9936 | 837.9936 | 837.9936 | 837.9936
| 6811.4084 | 19685.8454 | Net benefit | 0 | 0 | -49.2021 | 248.3866 | 356.306 | 429.3464 | 563.4083 | 610.8183 | 658.3735 | 670.3267 | 681.5368 | 722.5612 | 649.6283 | 744.3306 | 837.5015 | 837.5015 | 837.5015 | 837.5015 | 837.5015 | 837.5015 | 837.5015 | 837.5015 | 837.5015 | 837.5015 | 837.5015 | 837.5015 | 837.5015 | 837.5015 | 837.5015 | 837.5015
Option 10
Determining Optimal Timing: | Discounted | Undiscounted
| 0 | 0 | Capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 5260.5844 | 15208.189 | Opex | 0.48285 | 57.8283 | 189.4866 | 207.6844 | 245.4848 | 279.2209 | 339.624 | 384.4625 | 426.7802 | 445.1879 | 469.6214 | 502.6026 | 486.2654 | 573.3683 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055
| 5260.5844 | 15208.189 | Reduction in unserved energy | 0.48285 | 57.8283 | 189.4866 | 207.6844 | 245.4848 | 279.2209 | 339.624 | 384.4625 | 426.7802 | 445.1879 | 469.6214 | 502.6026 | 486.2654 | 573.3683 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055
| 0 | 0 | Net benefit | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | EUE Value ($m, real $2024) | 2.8305 | 7.6008 | 57.6455 | 75.397 | 116.5181 | 159.884 | 241.6832 | 255.0898 | 275.9942 | 288.7753 | 297.7206 | 352.2877 | 295.989 | 381.8026 | 476.3468 | 476.3468 | 476.3468 | 476.3468 | 476.3468 | 476.3468 | 476.3468 | 476.3468 | 476.3468 | 476.3468 | 476.3468 | 476.3468 | 476.3468 | 476.3468 | 476.3468 | 476.3468
|  |  | Annualised capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Annualised cost (capex+opex) | 0.48285 | 57.8283 | 189.4866 | 207.6844 | 245.4848 | 279.2209 | 339.624 | 384.4625 | 426.7802 | 445.1879 | 469.6214 | 502.6026 | 486.2654 | 573.3683 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055
|  |  | Optimal timing (interim calc) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Optimal timing | - | - | - | - | - | - | - | [19 empty] | - | - | - | - | bar: 1 to 19
Adjusted For Optimal Timing: | 0 | 0 | Capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 5260.5844 | 15208.189 | Opex | 0.48285 | 57.8283 | 189.4866 | 207.6844 | 245.4848 | 279.2209 | 339.624 | 384.4625 | 426.7802 | 445.1879 | 469.6214 | 502.6026 | 486.2654 | 573.3683 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055
| 5260.5844 | 15208.189 | Reduction in unserved energy | 0.48285 | 57.8283 | 189.4866 | 207.6844 | 245.4848 | 279.2209 | 339.624 | 384.4625 | 426.7802 | 445.1879 | 469.6214 | 502.6026 | 486.2654 | 573.3683 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055
| 0 | 0 | Net benefit | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## 3.2.3 NPV (LoCost)
Economic inputs and assumptions
Scenario | Discount rate | Central
| Cost | Lower bound
| VCR | Central
|  | Central | Lower bound | Upper bound
| Discount rate | 5.56% | 4.11% | 7%
| Cost | 100% | 80% | 120%
| VCR | 100% | 80% | 120%
Asset life for calculating annualised capex (years) | Option 1 | 45
| Option 2 | 45
| Option 3 | 45
| Option 4 | 45
| Option 5 | 45
| Option 6 | 45
| Option 7 | 45
| Option 8 | 45
| Option 9 | 45
| Option 10 | 45
|  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30
|  |  |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Outputs | bar: 3 FY27; 7 FY31
Option 1
| Discounted | Undiscounted
| 0 | 0 | Capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Opex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Reduction in unserved energy | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Net benefit | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | EUE Value ($m, real $2024) | 3.3134 | 65.4291 | 247.1322 | 283.0814 | 362.0029 | 439.1049 | 581.3072 | 639.5522 | 702.7745 | 733.9632 | 767.342 | 854.8903 | 782.2544 | 955.1709 | 1138.8523 | 1138.8523 | 1138.8523 | 1138.8523 | 1138.8523 | 1138.8523 | 1138.8523 | 1138.8523 | 1138.8523 | 1138.8523 | 1138.8523 | 1138.8523 | 1138.8523 | 1138.8523 | 1138.8523 | 1138.8523
Option 2
Determining Optimal Timing: | Discounted | Undiscounted
| 51.7673 | 57.6838 | Capex | 0 | 0 | 57.6838 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 7.1504 | 15.5746 | Opex | 0 | 0 | 0 | 0.57684 | 0.57684 | 0.57684 | 0.57684 | 0.57684 | 0.57684 | 0.57684 | 0.57684 | 0.57684 | 0.57684 | 0.57684 | 0.57684 | 0.57684 | 0.57684 | 0.57684 | 0.57684 | 0.57684 | 0.57684 | 0.57684 | 0.57684 | 0.57684 | 0.57684 | 0.57684 | 0.57684 | 0.57684 | 0.57684 | 0.57684
| 9984.918 | 24591.0207 | Reduction in unserved energy | 0 | 0 | 0 | 245.4928 | 298.3199 | 432.154 | 573.2974 | 630.3857 | 692.15 | 721.8524 | 753.3537 | 837.7342 | 764.8598 | 929.6264 | 1106.9871 | 1106.9871 | 1106.9871 | 1106.9871 | 1106.9871 | 1106.9871 | 1106.9871 | 1106.9871 | 1106.9871 | 1106.9871 | 1106.9871 | 1106.9871 | 1106.9871 | 1106.9871 | 1106.9871 | 1106.9871
| 9926.0002 | 24517.7623 | Net benefit | 0 | 0 | -57.6838 | 244.9159 | 297.7431 | 431.5771 | 572.7206 | 629.8089 | 691.5731 | 721.2756 | 752.7769 | 837.1574 | 764.283 | 929.0495 | 1106.4103 | 1106.4103 | 1106.4103 | 1106.4103 | 1106.4103 | 1106.4103 | 1106.4103 | 1106.4103 | 1106.4103 | 1106.4103 | 1106.4103 | 1106.4103 | 1106.4103 | 1106.4103 | 1106.4103 | 1106.4103
|  |  | EUE Value ($m, real $2024) | 3.3072 | 65.4291 | 247.1322 | 37.5886 | 63.683 | 6.9509 | 8.0097 | 9.1665 | 10.6245 | 12.1107 | 13.9883 | 17.1561 | 17.3946 | 25.5446 | 31.8652 | 31.8652 | 31.8652 | 31.8652 | 31.8652 | 31.8652 | 31.8652 | 31.8652 | 31.8652 | 31.8652 | 31.8652 | 31.8652 | 31.8652 | 31.8652 | 31.8652 | 31.8652
|  |  | Annualised capex | 0 | 0 | 3.1546 | 3.1546 | 3.1546 | 3.1546 | 3.1546 | 3.1546 | 3.1546 | 3.1546 | 3.1546 | 3.1546 | 3.1546 | 3.1546 | 3.1546 | 3.1546 | 3.1546 | 3.1546 | 3.1546 | 3.1546 | 3.1546 | 3.1546 | 3.1546 | 3.1546 | 3.1546 | 3.1546 | 3.1546 | 3.1546 | 3.1546 | 3.1546
|  |  | Annualised cost (capex+opex) | 0 | 0 | 3.1546 | 3.7315 | 3.7315 | 3.7315 | 3.7315 | 3.7315 | 3.7315 | 3.7315 | 3.7315 | 3.7315 | 3.7315 | 3.7315 | 3.7315 | 3.7315 | 3.7315 | 3.7315 | 3.7315 | 3.7315 | 3.7315 | 3.7315 | 3.7315 | 3.7315 | 3.7315 | 3.7315 | 3.7315 | 3.7315 | 3.7315 | 3.7315
|  |  | Optimal timing (interim calc) | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  |  | Optimal timing | - | - | - | Yes | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Adjusted For Optimal Timing: | 51.7673 | 57.6838 | Capex | 0 | 0 | 57.6838 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 7.1504 | 15.5746 | Opex | 0 | 0 | 0 | 0.57684 | 0.57684 | 0.57684 | 0.57684 | 0.57684 | 0.57684 | 0.57684 | 0.57684 | 0.57684 | 0.57684 | 0.57684 | 0.57684 | 0.57684 | 0.57684 | 0.57684 | 0.57684 | 0.57684 | 0.57684 | 0.57684 | 0.57684 | 0.57684 | 0.57684 | 0.57684 | 0.57684 | 0.57684 | 0.57684 | 0.57684
| 9984.918 | 24591.0207 | Reduction in unserved energy | 0 | 0 | 0 | 245.4928 | 298.3199 | 432.154 | 573.2974 | 630.3857 | 692.15 | 721.8524 | 753.3537 | 837.7342 | 764.8598 | 929.6264 | 1106.9871 | 1106.9871 | 1106.9871 | 1106.9871 | 1106.9871 | 1106.9871 | 1106.9871 | 1106.9871 | 1106.9871 | 1106.9871 | 1106.9871 | 1106.9871 | 1106.9871 | 1106.9871 | 1106.9871 | 1106.9871
| 9926.0002 | 24517.7623 | Net benefit | 0 | 0 | -57.6838 | 244.9159 | 297.7431 | 431.5771 | 572.7206 | 629.8089 | 691.5731 | 721.2756 | 752.7769 | 837.1574 | 764.283 | 929.0495 | 1106.4103 | 1106.4103 | 1106.4103 | 1106.4103 | 1106.4103 | 1106.4103 | 1106.4103 | 1106.4103 | 1106.4103 | 1106.4103 | 1106.4103 | 1106.4103 | 1106.4103 | 1106.4103 | 1106.4103 | 1106.4103
Option 3
Determining Optimal Timing: | Discounted | Undiscounted
| 31.2484 | 34.8199 | Capex | 0 | 0 | 34.8199 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 4.3162 | 9.4014 | Opex | 0 | 0 | 0 | 0.3482 | 0.3482 | 0.3482 | 0.3482 | 0.3482 | 0.3482 | 0.3482 | 0.3482 | 0.3482 | 0.3482 | 0.3482 | 0.3482 | 0.3482 | 0.3482 | 0.3482 | 0.3482 | 0.3482 | 0.3482 | 0.3482 | 0.3482 | 0.3482 | 0.3482 | 0.3482 | 0.3482 | 0.3482 | 0.3482 | 0.3482
| 8234.1231 | 19658.7761 | Reduction in unserved energy | 0 | 0 | 0 | 243.7522 | 294.2621 | 423.6585 | 557.0025 | 603.7113 | 650.6498 | 661.9773 | 672.5539 | 713.5507 | 640.2026 | 737.792 | 841.229 | 841.229 | 841.229 | 841.229 | 841.229 | 841.229 | 841.229 | 841.229 | 841.229 | 841.229 | 841.229 | 841.229 | 841.229 | 841.229 | 841.229 | 841.229
| 8198.5584 | 19614.5549 | Net benefit | 0 | 0 | -34.8199 | 243.404 | 293.9139 | 423.3103 | 556.6543 | 603.3631 | 650.3016 | 661.6291 | 672.2057 | 713.2025 | 639.8544 | 737.4438 | 840.8808 | 840.8808 | 840.8808 | 840.8808 | 840.8808 | 840.8808 | 840.8808 | 840.8808 | 840.8808 | 840.8808 | 840.8808 | 840.8808 | 840.8808 | 840.8808 | 840.8808 | 840.8808
|  |  | EUE Value ($m, real $2024) | 3.3072 | 65.4291 | 247.1322 | 39.3292 | 67.7408 | 15.4464 | 24.3047 | 35.8409 | 52.1247 | 71.9859 | 94.7882 | 141.3396 | 142.0518 | 217.3789 | 297.6234 | 297.6234 | 297.6234 | 297.6234 | 297.6234 | 297.6234 | 297.6234 | 297.6234 | 297.6234 | 297.6234 | 297.6234 | 297.6234 | 297.6234 | 297.6234 | 297.6234 | 297.6234
|  |  | Annualised capex | 0 | 0 | 1.9042 | 1.9042 | 1.9042 | 1.9042 | 1.9042 | 1.9042 | 1.9042 | 1.9042 | 1.9042 | 1.9042 | 1.9042 | 1.9042 | 1.9042 | 1.9042 | 1.9042 | 1.9042 | 1.9042 | 1.9042 | 1.9042 | 1.9042 | 1.9042 | 1.9042 | 1.9042 | 1.9042 | 1.9042 | 1.9042 | 1.9042 | 1.9042
|  |  | Annualised cost (capex+opex) | 0 | 0 | 1.9042 | 2.2524 | 2.2524 | 2.2524 | 2.2524 | 2.2524 | 2.2524 | 2.2524 | 2.2524 | 2.2524 | 2.2524 | 2.2524 | 2.2524 | 2.2524 | 2.2524 | 2.2524 | 2.2524 | 2.2524 | 2.2524 | 2.2524 | 2.2524 | 2.2524 | 2.2524 | 2.2524 | 2.2524 | 2.2524 | 2.2524 | 2.2524
|  |  | Optimal timing (interim calc) | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  |  | Optimal timing | - | - | - | Yes | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Adjusted For Optimal Timing: | 31.2484 | 34.8199 | Capex | 0 | 0 | 34.8199 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 4.3162 | 9.4014 | Opex | 0 | 0 | 0 | 0.3482 | 0.3482 | 0.3482 | 0.3482 | 0.3482 | 0.3482 | 0.3482 | 0.3482 | 0.3482 | 0.3482 | 0.3482 | 0.3482 | 0.3482 | 0.3482 | 0.3482 | 0.3482 | 0.3482 | 0.3482 | 0.3482 | 0.3482 | 0.3482 | 0.3482 | 0.3482 | 0.3482 | 0.3482 | 0.3482 | 0.3482
| 8234.1231 | 19658.7761 | Reduction in unserved energy | 0 | 0 | 0 | 243.7522 | 294.2621 | 423.6585 | 557.0025 | 603.7113 | 650.6498 | 661.9773 | 672.5539 | 713.5507 | 640.2026 | 737.792 | 841.229 | 841.229 | 841.229 | 841.229 | 841.229 | 841.229 | 841.229 | 841.229 | 841.229 | 841.229 | 841.229 | 841.229 | 841.229 | 841.229 | 841.229 | 841.229
| 8198.5584 | 19614.5549 | Net benefit | 0 | 0 | -34.8199 | 243.404 | 293.9139 | 423.3103 | 556.6543 | 603.3631 | 650.3016 | 661.6291 | 672.2057 | 713.2025 | 639.8544 | 737.4438 | 840.8808 | 840.8808 | 840.8808 | 840.8808 | 840.8808 | 840.8808 | 840.8808 | 840.8808 | 840.8808 | 840.8808 | 840.8808 | 840.8808 | 840.8808 | 840.8808 | 840.8808 | 840.8808
Option 4
Determining Optimal Timing: | Discounted | Undiscounted
| 42.7498 | 47.6358 | Capex | 0 | 0 | 47.6358 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 5.9049 | 12.8617 | Opex | 0 | 0 | 0 | 0.47636 | 0.47636 | 0.47636 | 0.47636 | 0.47636 | 0.47636 | 0.47636 | 0.47636 | 0.47636 | 0.47636 | 0.47636 | 0.47636 | 0.47636 | 0.47636 | 0.47636 | 0.47636 | 0.47636 | 0.47636 | 0.47636 | 0.47636 | 0.47636 | 0.47636 | 0.47636 | 0.47636 | 0.47636 | 0.47636 | 0.47636
| 3990.3839 | 10808.4009 | Reduction in unserved energy | 0 | 0 | 0 | 7.653 | 18.0781 | 97.9688 | 116.1458 | 135.5643 | 159.7892 | 184.879 | 216.5434 | 292.8216 | 278.5136 | 408.2495 | 555.7622 | 555.7622 | 555.7622 | 555.7622 | 555.7622 | 555.7622 | 555.7622 | 555.7622 | 555.7622 | 555.7622 | 555.7622 | 555.7622 | 555.7622 | 555.7622 | 555.7622 | 555.7622
| 3941.7292 | 10747.9035 | Net benefit | 0 | 0 | -47.6358 | 7.1766 | 17.6018 | 97.4924 | 115.6694 | 135.088 | 159.3129 | 184.4026 | 216.067 | 292.3452 | 278.0372 | 407.7732 | 555.2858 | 555.2858 | 555.2858 | 555.2858 | 555.2858 | 555.2858 | 555.2858 | 555.2858 | 555.2858 | 555.2858 | 555.2858 | 555.2858 | 555.2858 | 555.2858 | 555.2858 | 555.2858
|  |  | EUE Value ($m, real $2024) | 3.3072 | 65.4291 | 247.1322 | 275.4284 | 343.9248 | 341.1361 | 465.1614 | 503.9879 | 542.9852 | 549.0842 | 550.7987 | 562.0687 | 503.7408 | 546.9214 | 583.0902 | 583.0902 | 583.0902 | 583.0902 | 583.0902 | 583.0902 | 583.0902 | 583.0902 | 583.0902 | 583.0902 | 583.0902 | 583.0902 | 583.0902 | 583.0902 | 583.0902 | 583.0902
|  |  | Annualised capex | 0 | 0 | 2.6051 | 2.6051 | 2.6051 | 2.6051 | 2.6051 | 2.6051 | 2.6051 | 2.6051 | 2.6051 | 2.6051 | 2.6051 | 2.6051 | 2.6051 | 2.6051 | 2.6051 | 2.6051 | 2.6051 | 2.6051 | 2.6051 | 2.6051 | 2.6051 | 2.6051 | 2.6051 | 2.6051 | 2.6051 | 2.6051 | 2.6051 | 2.6051
|  |  | Annualised cost (capex+opex) | 0 | 0 | 2.6051 | 3.0815 | 3.0815 | 3.0815 | 3.0815 | 3.0815 | 3.0815 | 3.0815 | 3.0815 | 3.0815 | 3.0815 | 3.0815 | 3.0815 | 3.0815 | 3.0815 | 3.0815 | 3.0815 | 3.0815 | 3.0815 | 3.0815 | 3.0815 | 3.0815 | 3.0815 | 3.0815 | 3.0815 | 3.0815 | 3.0815 | 3.0815
|  |  | Optimal timing (interim calc) | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  |  | Optimal timing | - | - | - | Yes | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
[11 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19
Adjusted For Optimal Timing: | 42.7498 | 47.6358 | Capex | 0 | 0 | 47.6358 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 5.9049 | 12.8617 | Opex | 0 | 0 | 0 | 0.47636 | 0.47636 | 0.47636 | 0.47636 | 0.47636 | 0.47636 | 0.47636 | 0.47636 | 0.47636 | 0.47636 | 0.47636 | 0.47636 | 0.47636 | 0.47636 | 0.47636 | 0.47636 | 0.47636 | 0.47636 | 0.47636 | 0.47636 | 0.47636 | 0.47636 | 0.47636 | 0.47636 | 0.47636 | 0.47636 | 0.47636
| 3990.3839 | 10808.4009 | Reduction in unserved energy | 0 | 0 | 0 | 7.653 | 18.0781 | 97.9688 | 116.1458 | 135.5643 | 159.7892 | 184.879 | 216.5434 | 292.8216 | 278.5136 | 408.2495 | 555.7622 | 555.7622 | 555.7622 | 555.7622 | 555.7622 | 555.7622 | 555.7622 | 555.7622 | 555.7622 | 555.7622 | 555.7622 | 555.7622 | 555.7622 | 555.7622 | 555.7622 | 555.7622
| 3941.7292 | 10747.9035 | Net benefit | 0 | 0 | -47.6358 | 7.1766 | 17.6018 | 97.4924 | 115.6694 | 135.088 | 159.3129 | 184.4026 | 216.067 | 292.3452 | 278.0372 | 407.7732 | 555.2858 | 555.2858 | 555.2858 | 555.2858 | 555.2858 | 555.2858 | 555.2858 | 555.2858 | 555.2858 | 555.2858 | 555.2858 | 555.2858 | 555.2858 | 555.2858 | 555.2858 | 555.2858
Option 5
Determining Optimal Timing: | Discounted | Undiscounted
| 39.9928 | 44.5637 | Capex | 0 | 0 | 44.5637 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 5.5241 | 12.0322 | Opex | 0 | 0 | 0 | 0.44564 | 0.44564 | 0.44564 | 0.44564 | 0.44564 | 0.44564 | 0.44564 | 0.44564 | 0.44564 | 0.44564 | 0.44564 | 0.44564 | 0.44564 | 0.44564 | 0.44564 | 0.44564 | 0.44564 | 0.44564 | 0.44564 | 0.44564 | 0.44564 | 0.44564 | 0.44564 | 0.44564 | 0.44564 | 0.44564 | 0.44564
| 8365.665 | 19974.6734 | Reduction in unserved energy | 0 | 0 | 0 | 249.0844 | 300.1349 | 430.1528 | 564.2523 | 611.7211 | 659.3657 | 671.4363 | 682.8319 | 724.6792 | 652.0574 | 750.6505 | 854.8942 | 854.8942 | 854.8942 | 854.8942 | 854.8942 | 854.8942 | 854.8942 | 854.8942 | 854.8942 | 854.8942 | 854.8942 | 854.8942 | 854.8942 | 854.8942 | 854.8942 | 854.8942
| 8320.1481 | 19918.0775 | Net benefit | 0 | 0 | -44.5637 | 248.6388 | 299.6893 | 429.7072 | 563.8066 | 611.2755 | 658.92 | 670.9907 | 682.3862 | 724.2336 | 651.6118 | 750.2049 | 854.4485 | 854.4485 | 854.4485 | 854.4485 | 854.4485 | 854.4485 | 854.4485 | 854.4485 | 854.4485 | 854.4485 | 854.4485 | 854.4485 | 854.4485 | 854.4485 | 854.4485 | 854.4485
|  |  | EUE Value ($m, real $2024) | 3.3072 | 65.4291 | 247.1322 | 33.9969 | 61.868 | 8.9521 | 17.0549 | 27.8311 | 43.4088 | 62.5269 | 84.5102 | 130.2111 | 130.197 | 204.5204 | 283.9581 | 283.9581 | 283.9581 | 283.9581 | 283.9581 | 283.9581 | 283.9581 | 283.9581 | 283.9581 | 283.9581 | 283.9581 | 283.9581 | 283.9581 | 283.9581 | 283.9581 | 283.9581
|  |  | Annualised capex | 0 | 0 | 2.4371 | 2.4371 | 2.4371 | 2.4371 | 2.4371 | 2.4371 | 2.4371 | 2.4371 | 2.4371 | 2.4371 | 2.4371 | 2.4371 | 2.4371 | 2.4371 | 2.4371 | 2.4371 | 2.4371 | 2.4371 | 2.4371 | 2.4371 | 2.4371 | 2.4371 | 2.4371 | 2.4371 | 2.4371 | 2.4371 | 2.4371 | 2.4371
|  |  | Annualised cost (capex+opex) | 0 | 0 | 2.4371 | 2.8827 | 2.8827 | 2.8827 | 2.8827 | 2.8827 | 2.8827 | 2.8827 | 2.8827 | 2.8827 | 2.8827 | 2.8827 | 2.8827 | 2.8827 | 2.8827 | 2.8827 | 2.8827 | 2.8827 | 2.8827 | 2.8827 | 2.8827 | 2.8827 | 2.8827 | 2.8827 | 2.8827 | 2.8827 | 2.8827 | 2.8827
|  |  | Optimal timing (interim calc) | 0 | 0 | 0 | 1 | 1 | 1 | 1 | [19 empty] | 1 | 1 | 1 | 1 | bar: 1 to 19
|  |  | Optimal timing | - | - | - | Yes | - | - | - | [19 empty] | - | - | - | - | bar: 1 to 19
Adjusted For Optimal Timing: | 39.9928 | 44.5637 | Capex | 0 | 0 | 44.5637 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 5.5241 | 12.0322 | Opex | 0 | 0 | 0 | 0.44564 | 0.44564 | 0.44564 | 0.44564 | 0.44564 | 0.44564 | 0.44564 | 0.44564 | 0.44564 | 0.44564 | 0.44564 | 0.44564 | 0.44564 | 0.44564 | 0.44564 | 0.44564 | 0.44564 | 0.44564 | 0.44564 | 0.44564 | 0.44564 | 0.44564 | 0.44564 | 0.44564 | 0.44564 | 0.44564 | 0.44564
| 8365.665 | 19974.6734 | Reduction in unserved energy | 0 | 0 | 0 | 249.0844 | 300.1349 | 430.1528 | 564.2523 | 611.7211 | 659.3657 | 671.4363 | 682.8319 | 724.6792 | 652.0574 | 750.6505 | 854.8942 | 854.8942 | 854.8942 | 854.8942 | 854.8942 | 854.8942 | 854.8942 | 854.8942 | 854.8942 | 854.8942 | 854.8942 | 854.8942 | 854.8942 | 854.8942 | 854.8942 | 854.8942
| 8320.1481 | 19918.0775 | Net benefit | 0 | 0 | -44.5637 | 248.6388 | 299.6893 | 429.7072 | 563.8066 | 611.2755 | 658.92 | 670.9907 | 682.3862 | 724.2336 | 651.6118 | 750.2049 | 854.4485 | 854.4485 | 854.4485 | 854.4485 | 854.4485 | 854.4485 | 854.4485 | 854.4485 | 854.4485 | 854.4485 | 854.4485 | 854.4485 | 854.4485 | 854.4485 | 854.4485 | 854.4485
Option 6
Determining Optimal Timing: | Discounted | Undiscounted
| 48.9534 | 54.5484 | Capex | 0 | 0 | 54.5484 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 6.7618 | 14.7281 | Opex | 0 | 0 | 0 | 0.54548 | 0.54548 | 0.54548 | 0.54548 | 0.54548 | 0.54548 | 0.54548 | 0.54548 | 0.54548 | 0.54548 | 0.54548 | 0.54548 | 0.54548 | 0.54548 | 0.54548 | 0.54548 | 0.54548 | 0.54548 | 0.54548 | 0.54548 | 0.54548 | 0.54548 | 0.54548 | 0.54548 | 0.54548 | 0.54548 | 0.54548
| 9884.1595 | 24206.4938 | Reduction in unserved energy | 0 | 0 | 0 | 245.468 | 355.7787 | 432.0571 | 573.1763 | 630.1983 | 691.8313 | 721.2116 | 751.7861 | 833.3634 | 760.5335 | 918.8095 | 1080.7675 | 1080.7675 | 1080.7675 | 1080.7675 | 1080.7675 | 1080.7675 | 1080.7675 | 1080.7675 | 1080.7675 | 1080.7675 | 1080.7675 | 1080.7675 | 1080.7675 | 1080.7675 | 1080.7675 | 1080.7675
| 9828.4443 | 24137.2174 | Net benefit | 0 | 0 | -54.5484 | 244.9225 | 355.2332 | 431.5116 | 572.6308 | 629.6528 | 691.2858 | 720.6661 | 751.2406 | 832.818 | 759.9881 | 918.264 | 1080.222 | 1080.222 | 1080.222 | 1080.222 | 1080.222 | 1080.222 | 1080.222 | 1080.222 | 1080.222 | 1080.222 | 1080.222 | 1080.222 | 1080.222 | 1080.222 | 1080.222 | 1080.222
|  |  | EUE Value ($m, real $2024) | 3.3072 | 65.4291 | 247.1322 | 37.6134 | 6.2242 | 7.0478 | 8.1309 | 9.3539 | 10.9432 | 12.7515 | 15.5559 | 21.5268 | 21.7209 | 36.3614 | 58.0848 | 58.0848 | 58.0848 | 58.0848 | 58.0848 | 58.0848 | 58.0848 | 58.0848 | 58.0848 | 58.0848 | 58.0848 | 58.0848 | 58.0848 | 58.0848 | 58.0848 | 58.0848
|  |  | Annualised capex | 0 | 0 | 2.9831 | 2.9831 | 2.9831 | 2.9831 | 2.9831 | 2.9831 | 2.9831 | 2.9831 | 2.9831 | 2.9831 | 2.9831 | 2.9831 | 2.9831 | 2.9831 | 2.9831 | 2.9831 | 2.9831 | 2.9831 | 2.9831 | 2.9831 | 2.9831 | 2.9831 | 2.9831 | 2.9831 | 2.9831 | 2.9831 | 2.9831 | 2.9831
|  |  | Annualised cost (capex+opex) | 0 | 0 | 2.9831 | 3.5286 | 3.5286 | 3.5286 | 3.5286 | 3.5286 | 3.5286 | 3.5286 | 3.5286 | 3.5286 | 3.5286 | 3.5286 | 3.5286 | 3.5286 | 3.5286 | 3.5286 | 3.5286 | 3.5286 | 3.5286 | 3.5286 | 3.5286 | 3.5286 | 3.5286 | 3.5286 | 3.5286 | 3.5286 | 3.5286 | 3.5286
|  |  | Optimal timing (interim calc) | 0 | 0 | 0 | 1 | 1 | 1 | 1 | [19 empty] | 1 | 1 | 1 | 1 | bar: 1 to 19
|  |  | Optimal timing | - | - | - | Yes | - | - | - | [19 empty] | - | - | - | - | bar: 1 to 19
Adjusted For Optimal Timing: | 48.9534 | 54.5484 | Capex | 0 | 0 | 54.5484 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 6.7618 | 14.7281 | Opex | 0 | 0 | 0 | 0.54548 | 0.54548 | 0.54548 | 0.54548 | 0.54548 | 0.54548 | 0.54548 | 0.54548 | 0.54548 | 0.54548 | 0.54548 | 0.54548 | 0.54548 | 0.54548 | 0.54548 | 0.54548 | 0.54548 | 0.54548 | 0.54548 | 0.54548 | 0.54548 | 0.54548 | 0.54548 | 0.54548 | 0.54548 | 0.54548 | 0.54548
| 9884.1595 | 24206.4938 | Reduction in unserved energy | 0 | 0 | 0 | 245.468 | 355.7787 | 432.0571 | 573.1763 | 630.1983 | 691.8313 | 721.2116 | 751.7861 | 833.3634 | 760.5335 | 918.8095 | 1080.7675 | 1080.7675 | 1080.7675 | 1080.7675 | 1080.7675 | 1080.7675 | 1080.7675 | 1080.7675 | 1080.7675 | 1080.7675 | 1080.7675 | 1080.7675 | 1080.7675 | 1080.7675 | 1080.7675 | 1080.7675
| 9828.4443 | 24137.2174 | Net benefit | 0 | 0 | -54.5484 | 244.9225 | 355.2332 | 431.5116 | 572.6308 | 629.6528 | 691.2858 | 720.6661 | 751.2406 | 832.818 | 759.9881 | 918.264 | 1080.222 | 1080.222 | 1080.222 | 1080.222 | 1080.222 | 1080.222 | 1080.222 | 1080.222 | 1080.222 | 1080.222 | 1080.222 | 1080.222 | 1080.222 | 1080.222 | 1080.222 | 1080.222
Option 7
Determining Optimal Timing: | Discounted | Undiscounted
| 26.58 | 29.6179 | Capex | 0 | 0 | 29.6179 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 3.6714 | 7.9968 | Opex | 0 | 0 | 0 | 0.29618 | 0.29618 | 0.29618 | 0.29618 | 0.29618 | 0.29618 | 0.29618 | 0.29618 | 0.29618 | 0.29618 | 0.29618 | 0.29618 | 0.29618 | 0.29618 | 0.29618 | 0.29618 | 0.29618 | 0.29618 | 0.29618 | 0.29618 | 0.29618 | 0.29618 | 0.29618 | 0.29618 | 0.29618 | 0.29618 | 0.29618
| 8185.5885 | 19432.1091 | Reduction in unserved energy | 0 | 0 | 0 | 243.5469 | 350.9258 | 423.345 | 556.6521 | 603.3027 | 650.1521 | 661.3713 | 671.6924 | 711.8687 | 638.2834 | 731.9998 | 824.3106 | 824.3106 | 824.3106 | 824.3106 | 824.3106 | 824.3106 | 824.3106 | 824.3106 | 824.3106 | 824.3106 | 824.3106 | 824.3106 | 824.3106 | 824.3106 | 824.3106 | 824.3106
| 8155.3371 | 19394.4943 | Net benefit | 0 | 0 | -29.6179 | 243.2507 | 350.6297 | 423.0489 | 556.3559 | 603.0065 | 649.856 | 661.0751 | 671.3962 | 711.5725 | 637.9872 | 731.7037 | 824.0144 | 824.0144 | 824.0144 | 824.0144 | 824.0144 | 824.0144 | 824.0144 | 824.0144 | 824.0144 | 824.0144 | 824.0144 | 824.0144 | 824.0144 | 824.0144 | 824.0144 | 824.0144
|  |  | EUE Value ($m, real $2024) | 3.3072 | 65.4291 | 247.1322 | 39.5345 | 11.0771 | 15.7599 | 24.6551 | 36.2495 | 52.6223 | 72.5919 | 95.6496 | 143.0216 | 143.9711 | 223.1711 | 314.5418 | 314.5418 | 314.5418 | 314.5418 | 314.5418 | 314.5418 | 314.5418 | 314.5418 | 314.5418 | 314.5418 | 314.5418 | 314.5418 | 314.5418 | 314.5418 | 314.5418 | 314.5418
|  |  | Annualised capex | 0 | 0 | 1.6197 | 1.6197 | 1.6197 | 1.6197 | 1.6197 | 1.6197 | 1.6197 | 1.6197 | 1.6197 | 1.6197 | 1.6197 | 1.6197 | 1.6197 | 1.6197 | 1.6197 | 1.6197 | 1.6197 | 1.6197 | 1.6197 | 1.6197 | 1.6197 | 1.6197 | 1.6197 | 1.6197 | 1.6197 | 1.6197 | 1.6197 | 1.6197
|  |  | Annualised cost (capex+opex) | 0 | 0 | 1.6197 | 1.9159 | 1.9159 | 1.9159 | 1.9159 | 1.9159 | 1.9159 | 1.9159 | 1.9159 | 1.9159 | 1.9159 | 1.9159 | 1.9159 | 1.9159 | 1.9159 | 1.9159 | 1.9159 | 1.9159 | 1.9159 | 1.9159 | 1.9159 | 1.9159 | 1.9159 | 1.9159 | 1.9159 | 1.9159 | 1.9159 | 1.9159
|  |  | Optimal timing (interim calc) | 0 | 0 | 0 | 1 | 1 | 1 | 1 | [19 empty] | 1 | 1 | 1 | 1 | bar: 1 to 19
|  |  | Optimal timing | - | - | - | Yes | - | - | - | [19 empty] | - | - | - | - | bar: 1 to 19
Adjusted For Optimal Timing: | 26.58 | 29.6179 | Capex | 0 | 0 | 29.6179 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 3.6714 | 7.9968 | Opex | 0 | 0 | 0 | 0.29618 | 0.29618 | 0.29618 | 0.29618 | 0.29618 | 0.29618 | 0.29618 | 0.29618 | 0.29618 | 0.29618 | 0.29618 | 0.29618 | 0.29618 | 0.29618 | 0.29618 | 0.29618 | 0.29618 | 0.29618 | 0.29618 | 0.29618 | 0.29618 | 0.29618 | 0.29618 | 0.29618 | 0.29618 | 0.29618 | 0.29618
| 8185.5885 | 19432.1091 | Reduction in unserved energy | 0 | 0 | 0 | 243.5469 | 350.9258 | 423.345 | 556.6521 | 603.3027 | 650.1521 | 661.3713 | 671.6924 | 711.8687 | 638.2834 | 731.9998 | 824.3106 | 824.3106 | 824.3106 | 824.3106 | 824.3106 | 824.3106 | 824.3106 | 824.3106 | 824.3106 | 824.3106 | 824.3106 | 824.3106 | 824.3106 | 824.3106 | 824.3106 | 824.3106
| 8155.3371 | 19394.4943 | Net benefit | 0 | 0 | -29.6179 | 243.2507 | 350.6297 | 423.0489 | 556.3559 | 603.0065 | 649.856 | 661.0751 | 671.3962 | 711.5725 | 637.9872 | 731.7037 | 824.0144 | 824.0144 | 824.0144 | 824.0144 | 824.0144 | 824.0144 | 824.0144 | 824.0144 | 824.0144 | 824.0144 | 824.0144 | 824.0144 | 824.0144 | 824.0144 | 824.0144 | 824.0144
Option 8
Determining Optimal Timing: | Discounted | Undiscounted
| 38.0814 | 42.4338 | Capex | 0 | 0 | 42.4338 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 5.2601 | 11.4571 | Opex | 0 | 0 | 0 | 0.42434 | 0.42434 | 0.42434 | 0.42434 | 0.42434 | 0.42434 | 0.42434 | 0.42434 | 0.42434 | 0.42434 | 0.42434 | 0.42434 | 0.42434 | 0.42434 | 0.42434 | 0.42434 | 0.42434 | 0.42434 | 0.42434 | 0.42434 | 0.42434 | 0.42434 | 0.42434 | 0.42434 | 0.42434 | 0.42434 | 0.42434
| 3926.1287 | 10535.8711 | Reduction in unserved energy | 0 | 0 | 0 | 7.5218 | 74.6435 | 97.6009 | 115.718 | 135.0626 | 159.1861 | 184.1202 | 215.4688 | 290.4585 | 275.411 | 400.6215 | 536.2536 | 536.2536 | 536.2536 | 536.2536 | 536.2536 | 536.2536 | 536.2536 | 536.2536 | 536.2536 | 536.2536 | 536.2536 | 536.2536 | 536.2536 | 536.2536 | 536.2536 | 536.2536
| 3882.7872 | 10481.9802 | Net benefit | 0 | 0 | -42.4338 | 7.0974 | 74.2192 | 97.1766 | 115.2936 | 134.6383 | 158.7617 | 183.6959 | 215.0445 | 290.0342 | 274.9867 | 400.1972 | 535.8293 | 535.8293 | 535.8293 | 535.8293 | 535.8293 | 535.8293 | 535.8293 | 535.8293 | 535.8293 | 535.8293 | 535.8293 | 535.8293 | 535.8293 | 535.8293 | 535.8293 | 535.8293
|  |  | EUE Value ($m, real $2024) | 3.3072 | 65.4291 | 247.1322 | 275.5596 | 287.3594 | 341.504 | 465.5892 | 504.4896 | 543.5884 | 549.8429 | 551.8732 | 564.4318 | 506.8434 | 554.5494 | 602.5987 | 602.5987 | 602.5987 | 602.5987 | 602.5987 | 602.5987 | 602.5987 | 602.5987 | 602.5987 | 602.5987 | 602.5987 | 602.5987 | 602.5987 | 602.5987 | 602.5987 | 602.5987
|  |  | Annualised capex | 0 | 0 | 2.3206 | 2.3206 | 2.3206 | 2.3206 | 2.3206 | 2.3206 | 2.3206 | 2.3206 | 2.3206 | 2.3206 | 2.3206 | 2.3206 | 2.3206 | 2.3206 | 2.3206 | 2.3206 | 2.3206 | 2.3206 | 2.3206 | 2.3206 | 2.3206 | 2.3206 | 2.3206 | 2.3206 | 2.3206 | 2.3206 | 2.3206 | 2.3206
|  |  | Annualised cost (capex+opex) | 0 | 0 | 2.3206 | 2.745 | 2.745 | 2.745 | 2.745 | 2.745 | 2.745 | 2.745 | 2.745 | 2.745 | 2.745 | 2.745 | 2.745 | 2.745 | 2.745 | 2.745 | 2.745 | 2.745 | 2.745 | 2.745 | 2.745 | 2.745 | 2.745 | 2.745 | 2.745 | 2.745 | 2.745 | 2.745
|  |  | Optimal timing (interim calc) | 0 | 0 | 0 | 1 | 1 | 1 | 1 | [19 empty] | 1 | 1 | 1 | 1 | bar: 1 to 19
|  |  | Optimal timing | - | - | - | Yes | - | - | - | [19 empty] | - | - | - | - | bar: 1 to 19
Adjusted For Optimal Timing: | 38.0814 | 42.4338 | Capex | 0 | 0 | 42.4338 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 5.2601 | 11.4571 | Opex | 0 | 0 | 0 | 0.42434 | 0.42434 | 0.42434 | 0.42434 | 0.42434 | 0.42434 | 0.42434 | 0.42434 | 0.42434 | 0.42434 | 0.42434 | 0.42434 | 0.42434 | 0.42434 | 0.42434 | 0.42434 | 0.42434 | 0.42434 | 0.42434 | 0.42434 | 0.42434 | 0.42434 | 0.42434 | 0.42434 | 0.42434 | 0.42434 | 0.42434
| 3926.1287 | 10535.8711 | Reduction in unserved energy | 0 | 0 | 0 | 7.5218 | 74.6435 | 97.6009 | 115.718 | 135.0626 | 159.1861 | 184.1202 | 215.4688 | 290.4585 | 275.411 | 400.6215 | 536.2536 | 536.2536 | 536.2536 | 536.2536 | 536.2536 | 536.2536 | 536.2536 | 536.2536 | 536.2536 | 536.2536 | 536.2536 | 536.2536 | 536.2536 | 536.2536 | 536.2536 | 536.2536
| 3882.7872 | 10481.9802 | Net benefit | 0 | 0 | -42.4338 | 7.0974 | 74.2192 | 97.1766 | 115.2936 | 134.6383 | 158.7617 | 183.6959 | 215.0445 | 290.0342 | 274.9867 | 400.1972 | 535.8293 | 535.8293 | 535.8293 | 535.8293 | 535.8293 | 535.8293 | 535.8293 | 535.8293 | 535.8293 | 535.8293 | 535.8293 | 535.8293 | 535.8293 | 535.8293 | 535.8293 | 535.8293
Option 9
Determining Optimal Timing: | Discounted | Undiscounted
| 35.3244 | 39.3617 | Capex | 0 | 0 | 39.3617 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 4.8792 | 10.6277 | Opex | 0 | 0 | 0 | 0.39362 | 0.39362 | 0.39362 | 0.39362 | 0.39362 | 0.39362 | 0.39362 | 0.39362 | 0.39362 | 0.39362 | 0.39362 | 0.39362 | 0.39362 | 0.39362 | 0.39362 | 0.39362 | 0.39362 | 0.39362 | 0.39362 | 0.39362 | 0.39362 | 0.39362 | 0.39362 | 0.39362 | 0.39362 | 0.39362 | 0.39362
| 8317.247 | 19748.3321 | Reduction in unserved energy | 0 | 0 | 0 | 248.8786 | 356.798 | 429.8384 | 563.9003 | 611.3104 | 658.8656 | 670.8188 | 682.0288 | 723.0532 | 650.1203 | 744.8226 | 837.9936 | 837.9936 | 837.9936 | 837.9936 | 837.9936 | 837.9936 | 837.9936 | 837.9936 | 837.9936 | 837.9936 | 837.9936 | 837.9936 | 837.9936 | 837.9936 | 837.9936 | 837.9936
| 8277.0434 | 19698.3427 | Net benefit | 0 | 0 | -39.3617 | 248.485 | 356.4044 | 429.4448 | 563.5067 | 610.9168 | 658.4719 | 670.4251 | 681.6352 | 722.6596 | 649.7267 | 744.429 | 837.6 | 837.6 | 837.6 | 837.6 | 837.6 | 837.6 | 837.6 | 837.6 | 837.6 | 837.6 | 837.6 | 837.6 | 837.6 | 837.6 | 837.6 | 837.6
|  |  | EUE Value ($m, real $2024) | 3.3072 | 65.4291 | 247.1322 | 34.2028 | 5.2049 | 9.2665 | 17.4069 | 28.2418 | 43.9089 | 63.1444 | 85.3132 | 131.8371 | 132.1341 | 210.3483 | 300.8588 | 300.8588 | 300.8588 | 300.8588 | 300.8588 | 300.8588 | 300.8588 | 300.8588 | 300.8588 | 300.8588 | 300.8588 | 300.8588 | 300.8588 | 300.8588 | 300.8588 | 300.8588
|  |  | Annualised capex | 0 | 0 | 2.1526 | 2.1526 | 2.1526 | 2.1526 | 2.1526 | 2.1526 | 2.1526 | 2.1526 | 2.1526 | 2.1526 | 2.1526 | 2.1526 | 2.1526 | 2.1526 | 2.1526 | 2.1526 | 2.1526 | 2.1526 | 2.1526 | 2.1526 | 2.1526 | 2.1526 | 2.1526 | 2.1526 | 2.1526 | 2.1526 | 2.1526 | 2.1526
|  |  | Annualised cost (capex+opex) | 0 | 0 | 2.1526 | 2.5462 | 2.5462 | 2.5462 | 2.5462 | 2.5462 | 2.5462 | 2.5462 | 2.5462 | 2.5462 | 2.5462 | 2.5462 | 2.5462 | 2.5462 | 2.5462 | 2.5462 | 2.5462 | 2.5462 | 2.5462 | 2.5462 | 2.5462 | 2.5462 | 2.5462 | 2.5462 | 2.5462 | 2.5462 | 2.5462 | 2.5462
|  |  | Optimal timing (interim calc) | 0 | 0 | 0 | 1 | 1 | 1 | 1 | [19 empty] | 1 | 1 | 1 | 1 | bar: 1 to 19
|  |  | Optimal timing | - | - | - | Yes | - | - | - | [19 empty] | - | - | - | - | bar: 1 to 19
Adjusted For Optimal Timing: | 35.3244 | 39.3617 | Capex | 0 | 0 | 39.3617 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 4.8792 | 10.6277 | Opex | 0 | 0 | 0 | 0.39362 | 0.39362 | 0.39362 | 0.39362 | 0.39362 | 0.39362 | 0.39362 | 0.39362 | 0.39362 | 0.39362 | 0.39362 | 0.39362 | 0.39362 | 0.39362 | 0.39362 | 0.39362 | 0.39362 | 0.39362 | 0.39362 | 0.39362 | 0.39362 | 0.39362 | 0.39362 | 0.39362 | 0.39362 | 0.39362 | 0.39362
| 8317.247 | 19748.3321 | Reduction in unserved energy | 0 | 0 | 0 | 248.8786 | 356.798 | 429.8384 | 563.9003 | 611.3104 | 658.8656 | 670.8188 | 682.0288 | 723.0532 | 650.1203 | 744.8226 | 837.9936 | 837.9936 | 837.9936 | 837.9936 | 837.9936 | 837.9936 | 837.9936 | 837.9936 | 837.9936 | 837.9936 | 837.9936 | 837.9936 | 837.9936 | 837.9936 | 837.9936 | 837.9936
| 8277.0434 | 19698.3427 | Net benefit | 0 | 0 | -39.3617 | 248.485 | 356.4044 | 429.4448 | 563.5067 | 610.9168 | 658.4719 | 670.4251 | 681.6352 | 722.6596 | 649.7267 | 744.429 | 837.6 | 837.6 | 837.6 | 837.6 | 837.6 | 837.6 | 837.6 | 837.6 | 837.6 | 837.6 | 837.6 | 837.6 | 837.6 | 837.6 | 837.6 | 837.6
Option 10
Determining Optimal Timing: | Discounted | Undiscounted
| 0 | 0 | Capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 5100.7154 | 12166.5512 | Opex | 0.38628 | 46.2627 | 151.5893 | 166.1475 | 196.3878 | 223.3767 | 271.6992 | 307.57 | 341.4242 | 356.1503 | 375.6971 | 402.0821 | 389.0123 | 458.6947 | 530.0044 | 530.0044 | 530.0044 | 530.0044 | 530.0044 | 530.0044 | 530.0044 | 530.0044 | 530.0044 | 530.0044 | 530.0044 | 530.0044 | 530.0044 | 530.0044 | 530.0044 | 530.0044
| 6375.8942 | 15208.189 | Reduction in unserved energy | 0.48285 | 57.8283 | 189.4866 | 207.6844 | 245.4848 | 279.2209 | 339.624 | 384.4625 | 426.7802 | 445.1879 | 469.6214 | 502.6026 | 486.2654 | 573.3683 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055
| 1275.1788 | 3041.6378 | Net benefit | 0.096569 | 11.5657 | 37.8973 | 41.5369 | 49.097 | 55.8442 | 67.9248 | 76.8925 | 85.356 | 89.0376 | 93.9243 | 100.5205 | 97.2531 | 114.6737 | 132.5011 | 132.5011 | 132.5011 | 132.5011 | 132.5011 | 132.5011 | 132.5011 | 132.5011 | 132.5011 | 132.5011 | 132.5011 | 132.5011 | 132.5011 | 132.5011 | 132.5011 | 132.5011
|  |  | EUE Value ($m, real $2024) | 2.8305 | 7.6008 | 57.6455 | 75.397 | 116.5181 | 159.884 | 241.6832 | 255.0898 | 275.9942 | 288.7753 | 297.7206 | 352.2877 | 295.989 | 381.8026 | 476.3468 | 476.3468 | 476.3468 | 476.3468 | 476.3468 | 476.3468 | 476.3468 | 476.3468 | 476.3468 | 476.3468 | 476.3468 | 476.3468 | 476.3468 | 476.3468 | 476.3468 | 476.3468
|  |  | Annualised capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Annualised cost (capex+opex) | 0.38628 | 46.2627 | 151.5893 | 166.1475 | 196.3878 | 223.3767 | 271.6992 | 307.57 | 341.4242 | 356.1503 | 375.6971 | 402.0821 | 389.0123 | 458.6947 | 530.0044 | 530.0044 | 530.0044 | 530.0044 | 530.0044 | 530.0044 | 530.0044 | 530.0044 | 530.0044 | 530.0044 | 530.0044 | 530.0044 | 530.0044 | 530.0044 | 530.0044 | 530.0044
|  |  | Optimal timing (interim calc) | 1 | 1 | 1 | 1 | 1 | 1 | 1 | [19 empty] | 1 | 1 | 1 | 1 | bar: 1 to 19
|  |  | Optimal timing | Yes | - | - | - | - | - | - | [19 empty] | - | - | - | - | bar: 1 to 19
Adjusted For Optimal Timing: | 0 | 0 | Capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 5100.7154 | 12166.5512 | Opex | 0.38628 | 46.2627 | 151.5893 | 166.1475 | 196.3878 | 223.3767 | 271.6992 | 307.57 | 341.4242 | 356.1503 | 375.6971 | 402.0821 | 389.0123 | 458.6947 | 530.0044 | 530.0044 | 530.0044 | 530.0044 | 530.0044 | 530.0044 | 530.0044 | 530.0044 | 530.0044 | 530.0044 | 530.0044 | 530.0044 | 530.0044 | 530.0044 | 530.0044 | 530.0044
| 6375.8942 | 15208.189 | Reduction in unserved energy | 0.48285 | 57.8283 | 189.4866 | 207.6844 | 245.4848 | 279.2209 | 339.624 | 384.4625 | 426.7802 | 445.1879 | 469.6214 | 502.6026 | 486.2654 | 573.3683 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055
| 1275.1788 | 3041.6378 | Net benefit | 0.096569 | 11.5657 | 37.8973 | 41.5369 | 49.097 | 55.8442 | 67.9248 | 76.8925 | 85.356 | 89.0376 | 93.9243 | 100.5205 | 97.2531 | 114.6737 | 132.5011 | 132.5011 | 132.5011 | 132.5011 | 132.5011 | 132.5011 | 132.5011 | 132.5011 | 132.5011 | 132.5011 | 132.5011 | 132.5011 | 132.5011 | 132.5011 | 132.5011 | 132.5011

## 3.2.4 NPV (HiCost)
Economic inputs and assumptions
Scenario | Discount rate | Central
| Cost | Upper bound
| VCR | Central
|  | Central | Lower bound | Upper bound
| Discount rate | 5.56% | 4.11% | 7%
| Cost | 100% | 80% | 120%
| VCR | 100% | 80% | 120%
Asset life for calculating annualised capex (years) | Option 1 | 45
| Option 2 | 45
| Option 3 | 45
| Option 4 | 45
| Option 5 | 45
| Option 6 | 45
| Option 7 | 45
| Option 8 | 45
| Option 9 | 45
| Option 10 | 45
|  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30
|  |  |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Outputs | bar: 3 FY27; 7 FY31
Option 1
| Discounted | Undiscounted
| 0 | 0 | Capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Opex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Reduction in unserved energy | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Net benefit | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | EUE Value ($m, real $2024) | 3.3134 | 65.4291 | 247.1322 | 283.0814 | 362.0029 | 439.1049 | 581.3072 | 639.5522 | 702.7745 | 733.9632 | 767.342 | 854.8903 | 782.2544 | 955.1709 | 1138.8523 | 1138.8523 | 1138.8523 | 1138.8523 | 1138.8523 | 1138.8523 | 1138.8523 | 1138.8523 | 1138.8523 | 1138.8523 | 1138.8523 | 1138.8523 | 1138.8523 | 1138.8523 | 1138.8523 | 1138.8523
Option 2
Determining Optimal Timing: | Discounted | Undiscounted
| 77.6509 | 86.5257 | Capex | 0 | 0 | 86.5257 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 10.7257 | 23.3619 | Opex | 0 | 0 | 0 | 0.86526 | 0.86526 | 0.86526 | 0.86526 | 0.86526 | 0.86526 | 0.86526 | 0.86526 | 0.86526 | 0.86526 | 0.86526 | 0.86526 | 0.86526 | 0.86526 | 0.86526 | 0.86526 | 0.86526 | 0.86526 | 0.86526 | 0.86526 | 0.86526 | 0.86526 | 0.86526 | 0.86526 | 0.86526 | 0.86526 | 0.86526
| 9984.918 | 24591.0207 | Reduction in unserved energy | 0 | 0 | 0 | 245.4928 | 298.3199 | 432.154 | 573.2974 | 630.3857 | 692.15 | 721.8524 | 753.3537 | 837.7342 | 764.8598 | 929.6264 | 1106.9871 | 1106.9871 | 1106.9871 | 1106.9871 | 1106.9871 | 1106.9871 | 1106.9871 | 1106.9871 | 1106.9871 | 1106.9871 | 1106.9871 | 1106.9871 | 1106.9871 | 1106.9871 | 1106.9871 | 1106.9871
| 9896.5414 | 24481.133 | Net benefit | 0 | 0 | -86.5257 | 244.6275 | 297.4546 | 431.2887 | 572.4322 | 629.5205 | 691.2847 | 720.9872 | 752.4885 | 836.869 | 763.9946 | 928.7611 | 1106.1219 | 1106.1219 | 1106.1219 | 1106.1219 | 1106.1219 | 1106.1219 | 1106.1219 | 1106.1219 | 1106.1219 | 1106.1219 | 1106.1219 | 1106.1219 | 1106.1219 | 1106.1219 | 1106.1219 | 1106.1219
|  |  | EUE Value ($m, real $2024) | 3.3072 | 65.4291 | 247.1322 | 37.5886 | 63.683 | 6.9509 | 8.0097 | 9.1665 | 10.6245 | 12.1107 | 13.9883 | 17.1561 | 17.3946 | 25.5446 | 31.8652 | 31.8652 | 31.8652 | 31.8652 | 31.8652 | 31.8652 | 31.8652 | 31.8652 | 31.8652 | 31.8652 | 31.8652 | 31.8652 | 31.8652 | 31.8652 | 31.8652 | 31.8652
|  |  | Annualised capex | 0 | 0 | 4.7319 | 4.7319 | 4.7319 | 4.7319 | 4.7319 | 4.7319 | 4.7319 | 4.7319 | 4.7319 | 4.7319 | 4.7319 | 4.7319 | 4.7319 | 4.7319 | 4.7319 | 4.7319 | 4.7319 | 4.7319 | 4.7319 | 4.7319 | 4.7319 | 4.7319 | 4.7319 | 4.7319 | 4.7319 | 4.7319 | 4.7319 | 4.7319
|  |  | Annualised cost (capex+opex) | 0 | 0 | 4.7319 | 5.5972 | 5.5972 | 5.5972 | 5.5972 | 5.5972 | 5.5972 | 5.5972 | 5.5972 | 5.5972 | 5.5972 | 5.5972 | 5.5972 | 5.5972 | 5.5972 | 5.5972 | 5.5972 | 5.5972 | 5.5972 | 5.5972 | 5.5972 | 5.5972 | 5.5972 | 5.5972 | 5.5972 | 5.5972 | 5.5972 | 5.5972
|  |  | Optimal timing (interim calc) | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  |  | Optimal timing | - | - | - | Yes | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Adjusted For Optimal Timing: | 77.6509 | 86.5257 | Capex | 0 | 0 | 86.5257 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 10.7257 | 23.3619 | Opex | 0 | 0 | 0 | 0.86526 | 0.86526 | 0.86526 | 0.86526 | 0.86526 | 0.86526 | 0.86526 | 0.86526 | 0.86526 | 0.86526 | 0.86526 | 0.86526 | 0.86526 | 0.86526 | 0.86526 | 0.86526 | 0.86526 | 0.86526 | 0.86526 | 0.86526 | 0.86526 | 0.86526 | 0.86526 | 0.86526 | 0.86526 | 0.86526 | 0.86526
| 9984.918 | 24591.0207 | Reduction in unserved energy | 0 | 0 | 0 | 245.4928 | 298.3199 | 432.154 | 573.2974 | 630.3857 | 692.15 | 721.8524 | 753.3537 | 837.7342 | 764.8598 | 929.6264 | 1106.9871 | 1106.9871 | 1106.9871 | 1106.9871 | 1106.9871 | 1106.9871 | 1106.9871 | 1106.9871 | 1106.9871 | 1106.9871 | 1106.9871 | 1106.9871 | 1106.9871 | 1106.9871 | 1106.9871 | 1106.9871
| 9896.5414 | 24481.133 | Net benefit | 0 | 0 | -86.5257 | 244.6275 | 297.4546 | 431.2887 | 572.4322 | 629.5205 | 691.2847 | 720.9872 | 752.4885 | 836.869 | 763.9946 | 928.7611 | 1106.1219 | 1106.1219 | 1106.1219 | 1106.1219 | 1106.1219 | 1106.1219 | 1106.1219 | 1106.1219 | 1106.1219 | 1106.1219 | 1106.1219 | 1106.1219 | 1106.1219 | 1106.1219 | 1106.1219 | 1106.1219
Option 3
Determining Optimal Timing: | Discounted | Undiscounted
| 46.8727 | 52.2298 | Capex | 0 | 0 | 52.2298 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 6.4744 | 14.102 | Opex | 0 | 0 | 0 | 0.5223 | 0.5223 | 0.5223 | 0.5223 | 0.5223 | 0.5223 | 0.5223 | 0.5223 | 0.5223 | 0.5223 | 0.5223 | 0.5223 | 0.5223 | 0.5223 | 0.5223 | 0.5223 | 0.5223 | 0.5223 | 0.5223 | 0.5223 | 0.5223 | 0.5223 | 0.5223 | 0.5223 | 0.5223 | 0.5223 | 0.5223
| 8234.1231 | 19658.7761 | Reduction in unserved energy | 0 | 0 | 0 | 243.7522 | 294.2621 | 423.6585 | 557.0025 | 603.7113 | 650.6498 | 661.9773 | 672.5539 | 713.5507 | 640.2026 | 737.792 | 841.229 | 841.229 | 841.229 | 841.229 | 841.229 | 841.229 | 841.229 | 841.229 | 841.229 | 841.229 | 841.229 | 841.229 | 841.229 | 841.229 | 841.229 | 841.229
| 8180.776 | 19592.4443 | Net benefit | 0 | 0 | -52.2298 | 243.2299 | 293.7398 | 423.1362 | 556.4802 | 603.189 | 650.1275 | 661.455 | 672.0316 | 713.0284 | 639.6803 | 737.2697 | 840.7067 | 840.7067 | 840.7067 | 840.7067 | 840.7067 | 840.7067 | 840.7067 | 840.7067 | 840.7067 | 840.7067 | 840.7067 | 840.7067 | 840.7067 | 840.7067 | 840.7067 | 840.7067
|  |  | EUE Value ($m, real $2024) | 3.3072 | 65.4291 | 247.1322 | 39.3292 | 67.7408 | 15.4464 | 24.3047 | 35.8409 | 52.1247 | 71.9859 | 94.7882 | 141.3396 | 142.0518 | 217.3789 | 297.6234 | 297.6234 | 297.6234 | 297.6234 | 297.6234 | 297.6234 | 297.6234 | 297.6234 | 297.6234 | 297.6234 | 297.6234 | 297.6234 | 297.6234 | 297.6234 | 297.6234 | 297.6234
|  |  | Annualised capex | 0 | 0 | 2.8563 | 2.8563 | 2.8563 | 2.8563 | 2.8563 | 2.8563 | 2.8563 | 2.8563 | 2.8563 | 2.8563 | 2.8563 | 2.8563 | 2.8563 | 2.8563 | 2.8563 | 2.8563 | 2.8563 | 2.8563 | 2.8563 | 2.8563 | 2.8563 | 2.8563 | 2.8563 | 2.8563 | 2.8563 | 2.8563 | 2.8563 | 2.8563
|  |  | Annualised cost (capex+opex) | 0 | 0 | 2.8563 | 3.3786 | 3.3786 | 3.3786 | 3.3786 | 3.3786 | 3.3786 | 3.3786 | 3.3786 | 3.3786 | 3.3786 | 3.3786 | 3.3786 | 3.3786 | 3.3786 | 3.3786 | 3.3786 | 3.3786 | 3.3786 | 3.3786 | 3.3786 | 3.3786 | 3.3786 | 3.3786 | 3.3786 | 3.3786 | 3.3786 | 3.3786
|  |  | Optimal timing (interim calc) | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  |  | Optimal timing | - | - | - | Yes | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Adjusted For Optimal Timing: | 46.8727 | 52.2298 | Capex | 0 | 0 | 52.2298 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 6.4744 | 14.102 | Opex | 0 | 0 | 0 | 0.5223 | 0.5223 | 0.5223 | 0.5223 | 0.5223 | 0.5223 | 0.5223 | 0.5223 | 0.5223 | 0.5223 | 0.5223 | 0.5223 | 0.5223 | 0.5223 | 0.5223 | 0.5223 | 0.5223 | 0.5223 | 0.5223 | 0.5223 | 0.5223 | 0.5223 | 0.5223 | 0.5223 | 0.5223 | 0.5223 | 0.5223
| 8234.1231 | 19658.7761 | Reduction in unserved energy | 0 | 0 | 0 | 243.7522 | 294.2621 | 423.6585 | 557.0025 | 603.7113 | 650.6498 | 661.9773 | 672.5539 | 713.5507 | 640.2026 | 737.792 | 841.229 | 841.229 | 841.229 | 841.229 | 841.229 | 841.229 | 841.229 | 841.229 | 841.229 | 841.229 | 841.229 | 841.229 | 841.229 | 841.229 | 841.229 | 841.229
| 8180.776 | 19592.4443 | Net benefit | 0 | 0 | -52.2298 | 243.2299 | 293.7398 | 423.1362 | 556.4802 | 603.189 | 650.1275 | 661.455 | 672.0316 | 713.0284 | 639.6803 | 737.2697 | 840.7067 | 840.7067 | 840.7067 | 840.7067 | 840.7067 | 840.7067 | 840.7067 | 840.7067 | 840.7067 | 840.7067 | 840.7067 | 840.7067 | 840.7067 | 840.7067 | 840.7067 | 840.7067
Option 4
Determining Optimal Timing: | Discounted | Undiscounted
| 64.1247 | 71.4536 | Capex | 0 | 0 | 71.4536 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 8.8573 | 19.2925 | Opex | 0 | 0 | 0 | 0.71454 | 0.71454 | 0.71454 | 0.71454 | 0.71454 | 0.71454 | 0.71454 | 0.71454 | 0.71454 | 0.71454 | 0.71454 | 0.71454 | 0.71454 | 0.71454 | 0.71454 | 0.71454 | 0.71454 | 0.71454 | 0.71454 | 0.71454 | 0.71454 | 0.71454 | 0.71454 | 0.71454 | 0.71454 | 0.71454 | 0.71454
| 3990.3839 | 10808.4009 | Reduction in unserved energy | 0 | 0 | 0 | 7.653 | 18.0781 | 97.9688 | 116.1458 | 135.5643 | 159.7892 | 184.879 | 216.5434 | 292.8216 | 278.5136 | 408.2495 | 555.7622 | 555.7622 | 555.7622 | 555.7622 | 555.7622 | 555.7622 | 555.7622 | 555.7622 | 555.7622 | 555.7622 | 555.7622 | 555.7622 | 555.7622 | 555.7622 | 555.7622 | 555.7622
| 3917.4019 | 10717.6548 | Net benefit | 0 | 0 | -71.4536 | 6.9384 | 17.3636 | 97.2543 | 115.4312 | 134.8498 | 159.0747 | 184.1645 | 215.8288 | 292.1071 | 277.7991 | 407.535 | 555.0476 | 555.0476 | 555.0476 | 555.0476 | 555.0476 | 555.0476 | 555.0476 | 555.0476 | 555.0476 | 555.0476 | 555.0476 | 555.0476 | 555.0476 | 555.0476 | 555.0476 | 555.0476
|  |  | EUE Value ($m, real $2024) | 3.3072 | 65.4291 | 247.1322 | 275.4284 | 343.9248 | 341.1361 | 465.1614 | 503.9879 | 542.9852 | 549.0842 | 550.7987 | 562.0687 | 503.7408 | 546.9214 | 583.0902 | 583.0902 | 583.0902 | 583.0902 | 583.0902 | 583.0902 | 583.0902 | 583.0902 | 583.0902 | 583.0902 | 583.0902 | 583.0902 | 583.0902 | 583.0902 | 583.0902 | 583.0902
|  |  | Annualised capex | 0 | 0 | 3.9077 | 3.9077 | 3.9077 | 3.9077 | 3.9077 | 3.9077 | 3.9077 | 3.9077 | 3.9077 | 3.9077 | 3.9077 | 3.9077 | 3.9077 | 3.9077 | 3.9077 | 3.9077 | 3.9077 | 3.9077 | 3.9077 | 3.9077 | 3.9077 | 3.9077 | 3.9077 | 3.9077 | 3.9077 | 3.9077 | 3.9077 | 3.9077
|  |  | Annualised cost (capex+opex) | 0 | 0 | 3.9077 | 4.6222 | 4.6222 | 4.6222 | 4.6222 | 4.6222 | 4.6222 | 4.6222 | 4.6222 | 4.6222 | 4.6222 | 4.6222 | 4.6222 | 4.6222 | 4.6222 | 4.6222 | 4.6222 | 4.6222 | 4.6222 | 4.6222 | 4.6222 | 4.6222 | 4.6222 | 4.6222 | 4.6222 | 4.6222 | 4.6222 | 4.6222
|  |  | Optimal timing (interim calc) | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  |  | Optimal timing | - | - | - | Yes | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
[11 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19
Adjusted For Optimal Timing: | 64.1247 | 71.4536 | Capex | 0 | 0 | 71.4536 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 8.8573 | 19.2925 | Opex | 0 | 0 | 0 | 0.71454 | 0.71454 | 0.71454 | 0.71454 | 0.71454 | 0.71454 | 0.71454 | 0.71454 | 0.71454 | 0.71454 | 0.71454 | 0.71454 | 0.71454 | 0.71454 | 0.71454 | 0.71454 | 0.71454 | 0.71454 | 0.71454 | 0.71454 | 0.71454 | 0.71454 | 0.71454 | 0.71454 | 0.71454 | 0.71454 | 0.71454
| 3990.3839 | 10808.4009 | Reduction in unserved energy | 0 | 0 | 0 | 7.653 | 18.0781 | 97.9688 | 116.1458 | 135.5643 | 159.7892 | 184.879 | 216.5434 | 292.8216 | 278.5136 | 408.2495 | 555.7622 | 555.7622 | 555.7622 | 555.7622 | 555.7622 | 555.7622 | 555.7622 | 555.7622 | 555.7622 | 555.7622 | 555.7622 | 555.7622 | 555.7622 | 555.7622 | 555.7622 | 555.7622
| 3917.4019 | 10717.6548 | Net benefit | 0 | 0 | -71.4536 | 6.9384 | 17.3636 | 97.2543 | 115.4312 | 134.8498 | 159.0747 | 184.1645 | 215.8288 | 292.1071 | 277.7991 | 407.535 | 555.0476 | 555.0476 | 555.0476 | 555.0476 | 555.0476 | 555.0476 | 555.0476 | 555.0476 | 555.0476 | 555.0476 | 555.0476 | 555.0476 | 555.0476 | 555.0476 | 555.0476 | 555.0476
Option 5
Determining Optimal Timing: | Discounted | Undiscounted
| 59.9893 | 66.8455 | Capex | 0 | 0 | 66.8455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 8.2861 | 18.0483 | Opex | 0 | 0 | 0 | 0.66846 | 0.66846 | 0.66846 | 0.66846 | 0.66846 | 0.66846 | 0.66846 | 0.66846 | 0.66846 | 0.66846 | 0.66846 | 0.66846 | 0.66846 | 0.66846 | 0.66846 | 0.66846 | 0.66846 | 0.66846 | 0.66846 | 0.66846 | 0.66846 | 0.66846 | 0.66846 | 0.66846 | 0.66846 | 0.66846 | 0.66846
| 8365.665 | 19974.6734 | Reduction in unserved energy | 0 | 0 | 0 | 249.0844 | 300.1349 | 430.1528 | 564.2523 | 611.7211 | 659.3657 | 671.4363 | 682.8319 | 724.6792 | 652.0574 | 750.6505 | 854.8942 | 854.8942 | 854.8942 | 854.8942 | 854.8942 | 854.8942 | 854.8942 | 854.8942 | 854.8942 | 854.8942 | 854.8942 | 854.8942 | 854.8942 | 854.8942 | 854.8942 | 854.8942
| 8297.3897 | 19889.7795 | Net benefit | 0 | 0 | -66.8455 | 248.416 | 299.4665 | 429.4844 | 563.5838 | 611.0527 | 658.6972 | 670.7678 | 682.1634 | 724.0107 | 651.389 | 749.9821 | 854.2257 | 854.2257 | 854.2257 | 854.2257 | 854.2257 | 854.2257 | 854.2257 | 854.2257 | 854.2257 | 854.2257 | 854.2257 | 854.2257 | 854.2257 | 854.2257 | 854.2257 | 854.2257
|  |  | EUE Value ($m, real $2024) | 3.3072 | 65.4291 | 247.1322 | 33.9969 | 61.868 | 8.9521 | 17.0549 | 27.8311 | 43.4088 | 62.5269 | 84.5102 | 130.2111 | 130.197 | 204.5204 | 283.9581 | 283.9581 | 283.9581 | 283.9581 | 283.9581 | 283.9581 | 283.9581 | 283.9581 | 283.9581 | 283.9581 | 283.9581 | 283.9581 | 283.9581 | 283.9581 | 283.9581 | 283.9581
|  |  | Annualised capex | 0 | 0 | 3.6557 | 3.6557 | 3.6557 | 3.6557 | 3.6557 | 3.6557 | 3.6557 | 3.6557 | 3.6557 | 3.6557 | 3.6557 | 3.6557 | 3.6557 | 3.6557 | 3.6557 | 3.6557 | 3.6557 | 3.6557 | 3.6557 | 3.6557 | 3.6557 | 3.6557 | 3.6557 | 3.6557 | 3.6557 | 3.6557 | 3.6557 | 3.6557
|  |  | Annualised cost (capex+opex) | 0 | 0 | 3.6557 | 4.3241 | 4.3241 | 4.3241 | 4.3241 | 4.3241 | 4.3241 | 4.3241 | 4.3241 | 4.3241 | 4.3241 | 4.3241 | 4.3241 | 4.3241 | 4.3241 | 4.3241 | 4.3241 | 4.3241 | 4.3241 | 4.3241 | 4.3241 | 4.3241 | 4.3241 | 4.3241 | 4.3241 | 4.3241 | 4.3241 | 4.3241
|  |  | Optimal timing (interim calc) | 0 | 0 | 0 | 1 | 1 | 1 | 1 | [19 empty] | 1 | 1 | 1 | 1 | bar: 1 to 19
|  |  | Optimal timing | - | - | - | Yes | - | - | - | [19 empty] | - | - | - | - | bar: 1 to 19
Adjusted For Optimal Timing: | 59.9893 | 66.8455 | Capex | 0 | 0 | 66.8455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 8.2861 | 18.0483 | Opex | 0 | 0 | 0 | 0.66846 | 0.66846 | 0.66846 | 0.66846 | 0.66846 | 0.66846 | 0.66846 | 0.66846 | 0.66846 | 0.66846 | 0.66846 | 0.66846 | 0.66846 | 0.66846 | 0.66846 | 0.66846 | 0.66846 | 0.66846 | 0.66846 | 0.66846 | 0.66846 | 0.66846 | 0.66846 | 0.66846 | 0.66846 | 0.66846 | 0.66846
| 8365.665 | 19974.6734 | Reduction in unserved energy | 0 | 0 | 0 | 249.0844 | 300.1349 | 430.1528 | 564.2523 | 611.7211 | 659.3657 | 671.4363 | 682.8319 | 724.6792 | 652.0574 | 750.6505 | 854.8942 | 854.8942 | 854.8942 | 854.8942 | 854.8942 | 854.8942 | 854.8942 | 854.8942 | 854.8942 | 854.8942 | 854.8942 | 854.8942 | 854.8942 | 854.8942 | 854.8942 | 854.8942
| 8297.3897 | 19889.7795 | Net benefit | 0 | 0 | -66.8455 | 248.416 | 299.4665 | 429.4844 | 563.5838 | 611.0527 | 658.6972 | 670.7678 | 682.1634 | 724.0107 | 651.389 | 749.9821 | 854.2257 | 854.2257 | 854.2257 | 854.2257 | 854.2257 | 854.2257 | 854.2257 | 854.2257 | 854.2257 | 854.2257 | 854.2257 | 854.2257 | 854.2257 | 854.2257 | 854.2257 | 854.2257
Option 6
Determining Optimal Timing: | Discounted | Undiscounted
| 73.4301 | 81.8225 | Capex | 0 | 0 | 81.8225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 10.1427 | 22.0921 | Opex | 0 | 0 | 0 | 0.81823 | 0.81823 | 0.81823 | 0.81823 | 0.81823 | 0.81823 | 0.81823 | 0.81823 | 0.81823 | 0.81823 | 0.81823 | 0.81823 | 0.81823 | 0.81823 | 0.81823 | 0.81823 | 0.81823 | 0.81823 | 0.81823 | 0.81823 | 0.81823 | 0.81823 | 0.81823 | 0.81823 | 0.81823 | 0.81823 | 0.81823
| 9884.1595 | 24206.4938 | Reduction in unserved energy | 0 | 0 | 0 | 245.468 | 355.7787 | 432.0571 | 573.1763 | 630.1983 | 691.8313 | 721.2116 | 751.7861 | 833.3634 | 760.5335 | 918.8095 | 1080.7675 | 1080.7675 | 1080.7675 | 1080.7675 | 1080.7675 | 1080.7675 | 1080.7675 | 1080.7675 | 1080.7675 | 1080.7675 | 1080.7675 | 1080.7675 | 1080.7675 | 1080.7675 | 1080.7675 | 1080.7675
| 9800.5867 | 24102.5792 | Net benefit | 0 | 0 | -81.8225 | 244.6498 | 354.9605 | 431.2389 | 572.358 | 629.3801 | 691.0131 | 720.3934 | 750.9679 | 832.5452 | 759.7153 | 917.9913 | 1079.9493 | 1079.9493 | 1079.9493 | 1079.9493 | 1079.9493 | 1079.9493 | 1079.9493 | 1079.9493 | 1079.9493 | 1079.9493 | 1079.9493 | 1079.9493 | 1079.9493 | 1079.9493 | 1079.9493 | 1079.9493
|  |  | EUE Value ($m, real $2024) | 3.3072 | 65.4291 | 247.1322 | 37.6134 | 6.2242 | 7.0478 | 8.1309 | 9.3539 | 10.9432 | 12.7515 | 15.5559 | 21.5268 | 21.7209 | 36.3614 | 58.0848 | 58.0848 | 58.0848 | 58.0848 | 58.0848 | 58.0848 | 58.0848 | 58.0848 | 58.0848 | 58.0848 | 58.0848 | 58.0848 | 58.0848 | 58.0848 | 58.0848 | 58.0848
|  |  | Annualised capex | 0 | 0 | 4.4747 | 4.4747 | 4.4747 | 4.4747 | 4.4747 | 4.4747 | 4.4747 | 4.4747 | 4.4747 | 4.4747 | 4.4747 | 4.4747 | 4.4747 | 4.4747 | 4.4747 | 4.4747 | 4.4747 | 4.4747 | 4.4747 | 4.4747 | 4.4747 | 4.4747 | 4.4747 | 4.4747 | 4.4747 | 4.4747 | 4.4747 | 4.4747
|  |  | Annualised cost (capex+opex) | 0 | 0 | 4.4747 | 5.2929 | 5.2929 | 5.2929 | 5.2929 | 5.2929 | 5.2929 | 5.2929 | 5.2929 | 5.2929 | 5.2929 | 5.2929 | 5.2929 | 5.2929 | 5.2929 | 5.2929 | 5.2929 | 5.2929 | 5.2929 | 5.2929 | 5.2929 | 5.2929 | 5.2929 | 5.2929 | 5.2929 | 5.2929 | 5.2929 | 5.2929
|  |  | Optimal timing (interim calc) | 0 | 0 | 0 | 1 | 1 | 1 | 1 | [19 empty] | 1 | 1 | 1 | 1 | bar: 1 to 19
|  |  | Optimal timing | - | - | - | Yes | - | - | - | [19 empty] | - | - | - | - | bar: 1 to 19
Adjusted For Optimal Timing: | 73.4301 | 81.8225 | Capex | 0 | 0 | 81.8225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 10.1427 | 22.0921 | Opex | 0 | 0 | 0 | 0.81823 | 0.81823 | 0.81823 | 0.81823 | 0.81823 | 0.81823 | 0.81823 | 0.81823 | 0.81823 | 0.81823 | 0.81823 | 0.81823 | 0.81823 | 0.81823 | 0.81823 | 0.81823 | 0.81823 | 0.81823 | 0.81823 | 0.81823 | 0.81823 | 0.81823 | 0.81823 | 0.81823 | 0.81823 | 0.81823 | 0.81823
| 9884.1595 | 24206.4938 | Reduction in unserved energy | 0 | 0 | 0 | 245.468 | 355.7787 | 432.0571 | 573.1763 | 630.1983 | 691.8313 | 721.2116 | 751.7861 | 833.3634 | 760.5335 | 918.8095 | 1080.7675 | 1080.7675 | 1080.7675 | 1080.7675 | 1080.7675 | 1080.7675 | 1080.7675 | 1080.7675 | 1080.7675 | 1080.7675 | 1080.7675 | 1080.7675 | 1080.7675 | 1080.7675 | 1080.7675 | 1080.7675
| 9800.5867 | 24102.5792 | Net benefit | 0 | 0 | -81.8225 | 244.6498 | 354.9605 | 431.2389 | 572.358 | 629.3801 | 691.0131 | 720.3934 | 750.9679 | 832.5452 | 759.7153 | 917.9913 | 1079.9493 | 1079.9493 | 1079.9493 | 1079.9493 | 1079.9493 | 1079.9493 | 1079.9493 | 1079.9493 | 1079.9493 | 1079.9493 | 1079.9493 | 1079.9493 | 1079.9493 | 1079.9493 | 1079.9493 | 1079.9493
Option 7
Determining Optimal Timing: | Discounted | Undiscounted
| 39.87 | 44.4268 | Capex | 0 | 0 | 44.4268 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 5.5071 | 11.9952 | Opex | 0 | 0 | 0 | 0.44427 | 0.44427 | 0.44427 | 0.44427 | 0.44427 | 0.44427 | 0.44427 | 0.44427 | 0.44427 | 0.44427 | 0.44427 | 0.44427 | 0.44427 | 0.44427 | 0.44427 | 0.44427 | 0.44427 | 0.44427 | 0.44427 | 0.44427 | 0.44427 | 0.44427 | 0.44427 | 0.44427 | 0.44427 | 0.44427 | 0.44427
| 8185.5885 | 19432.1091 | Reduction in unserved energy | 0 | 0 | 0 | 243.5469 | 350.9258 | 423.345 | 556.6521 | 603.3027 | 650.1521 | 661.3713 | 671.6924 | 711.8687 | 638.2834 | 731.9998 | 824.3106 | 824.3106 | 824.3106 | 824.3106 | 824.3106 | 824.3106 | 824.3106 | 824.3106 | 824.3106 | 824.3106 | 824.3106 | 824.3106 | 824.3106 | 824.3106 | 824.3106 | 824.3106
| 8140.2113 | 19375.687 | Net benefit | 0 | 0 | -44.4268 | 243.1026 | 350.4816 | 422.9008 | 556.2078 | 602.8584 | 649.7079 | 660.927 | 671.2481 | 711.4244 | 637.8391 | 731.5556 | 823.8663 | 823.8663 | 823.8663 | 823.8663 | 823.8663 | 823.8663 | 823.8663 | 823.8663 | 823.8663 | 823.8663 | 823.8663 | 823.8663 | 823.8663 | 823.8663 | 823.8663 | 823.8663
|  |  | EUE Value ($m, real $2024) | 3.3072 | 65.4291 | 247.1322 | 39.5345 | 11.0771 | 15.7599 | 24.6551 | 36.2495 | 52.6223 | 72.5919 | 95.6496 | 143.0216 | 143.9711 | 223.1711 | 314.5418 | 314.5418 | 314.5418 | 314.5418 | 314.5418 | 314.5418 | 314.5418 | 314.5418 | 314.5418 | 314.5418 | 314.5418 | 314.5418 | 314.5418 | 314.5418 | 314.5418 | 314.5418
|  |  | Annualised capex | 0 | 0 | 2.4296 | 2.4296 | 2.4296 | 2.4296 | 2.4296 | 2.4296 | 2.4296 | 2.4296 | 2.4296 | 2.4296 | 2.4296 | 2.4296 | 2.4296 | 2.4296 | 2.4296 | 2.4296 | 2.4296 | 2.4296 | 2.4296 | 2.4296 | 2.4296 | 2.4296 | 2.4296 | 2.4296 | 2.4296 | 2.4296 | 2.4296 | 2.4296
|  |  | Annualised cost (capex+opex) | 0 | 0 | 2.4296 | 2.8739 | 2.8739 | 2.8739 | 2.8739 | 2.8739 | 2.8739 | 2.8739 | 2.8739 | 2.8739 | 2.8739 | 2.8739 | 2.8739 | 2.8739 | 2.8739 | 2.8739 | 2.8739 | 2.8739 | 2.8739 | 2.8739 | 2.8739 | 2.8739 | 2.8739 | 2.8739 | 2.8739 | 2.8739 | 2.8739 | 2.8739
|  |  | Optimal timing (interim calc) | 0 | 0 | 0 | 1 | 1 | 1 | 1 | [19 empty] | 1 | 1 | 1 | 1 | bar: 1 to 19
|  |  | Optimal timing | - | - | - | Yes | - | - | - | [19 empty] | - | - | - | - | bar: 1 to 19
Adjusted For Optimal Timing: | 39.87 | 44.4268 | Capex | 0 | 0 | 44.4268 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 5.5071 | 11.9952 | Opex | 0 | 0 | 0 | 0.44427 | 0.44427 | 0.44427 | 0.44427 | 0.44427 | 0.44427 | 0.44427 | 0.44427 | 0.44427 | 0.44427 | 0.44427 | 0.44427 | 0.44427 | 0.44427 | 0.44427 | 0.44427 | 0.44427 | 0.44427 | 0.44427 | 0.44427 | 0.44427 | 0.44427 | 0.44427 | 0.44427 | 0.44427 | 0.44427 | 0.44427
| 8185.5885 | 19432.1091 | Reduction in unserved energy | 0 | 0 | 0 | 243.5469 | 350.9258 | 423.345 | 556.6521 | 603.3027 | 650.1521 | 661.3713 | 671.6924 | 711.8687 | 638.2834 | 731.9998 | 824.3106 | 824.3106 | 824.3106 | 824.3106 | 824.3106 | 824.3106 | 824.3106 | 824.3106 | 824.3106 | 824.3106 | 824.3106 | 824.3106 | 824.3106 | 824.3106 | 824.3106 | 824.3106
| 8140.2113 | 19375.687 | Net benefit | 0 | 0 | -44.4268 | 243.1026 | 350.4816 | 422.9008 | 556.2078 | 602.8584 | 649.7079 | 660.927 | 671.2481 | 711.4244 | 637.8391 | 731.5556 | 823.8663 | 823.8663 | 823.8663 | 823.8663 | 823.8663 | 823.8663 | 823.8663 | 823.8663 | 823.8663 | 823.8663 | 823.8663 | 823.8663 | 823.8663 | 823.8663 | 823.8663 | 823.8663
Option 8
Determining Optimal Timing: | Discounted | Undiscounted
| 57.1221 | 63.6507 | Capex | 0 | 0 | 63.6507 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 7.8901 | 17.1857 | Opex | 0 | 0 | 0 | 0.63651 | 0.63651 | 0.63651 | 0.63651 | 0.63651 | 0.63651 | 0.63651 | 0.63651 | 0.63651 | 0.63651 | 0.63651 | 0.63651 | 0.63651 | 0.63651 | 0.63651 | 0.63651 | 0.63651 | 0.63651 | 0.63651 | 0.63651 | 0.63651 | 0.63651 | 0.63651 | 0.63651 | 0.63651 | 0.63651 | 0.63651
| 3926.1287 | 10535.8711 | Reduction in unserved energy | 0 | 0 | 0 | 7.5218 | 74.6435 | 97.6009 | 115.718 | 135.0626 | 159.1861 | 184.1202 | 215.4688 | 290.4585 | 275.411 | 400.6215 | 536.2536 | 536.2536 | 536.2536 | 536.2536 | 536.2536 | 536.2536 | 536.2536 | 536.2536 | 536.2536 | 536.2536 | 536.2536 | 536.2536 | 536.2536 | 536.2536 | 536.2536 | 536.2536
| 3861.1165 | 10455.0348 | Net benefit | 0 | 0 | -63.6507 | 6.8853 | 74.007 | 96.9644 | 115.0814 | 134.4261 | 158.5496 | 183.4837 | 214.8323 | 289.822 | 274.7745 | 399.985 | 535.6171 | 535.6171 | 535.6171 | 535.6171 | 535.6171 | 535.6171 | 535.6171 | 535.6171 | 535.6171 | 535.6171 | 535.6171 | 535.6171 | 535.6171 | 535.6171 | 535.6171 | 535.6171
|  |  | EUE Value ($m, real $2024) | 3.3072 | 65.4291 | 247.1322 | 275.5596 | 287.3594 | 341.504 | 465.5892 | 504.4896 | 543.5884 | 549.8429 | 551.8732 | 564.4318 | 506.8434 | 554.5494 | 602.5987 | 602.5987 | 602.5987 | 602.5987 | 602.5987 | 602.5987 | 602.5987 | 602.5987 | 602.5987 | 602.5987 | 602.5987 | 602.5987 | 602.5987 | 602.5987 | 602.5987 | 602.5987
|  |  | Annualised capex | 0 | 0 | 3.4809 | 3.4809 | 3.4809 | 3.4809 | 3.4809 | 3.4809 | 3.4809 | 3.4809 | 3.4809 | 3.4809 | 3.4809 | 3.4809 | 3.4809 | 3.4809 | 3.4809 | 3.4809 | 3.4809 | 3.4809 | 3.4809 | 3.4809 | 3.4809 | 3.4809 | 3.4809 | 3.4809 | 3.4809 | 3.4809 | 3.4809 | 3.4809
|  |  | Annualised cost (capex+opex) | 0 | 0 | 3.4809 | 4.1174 | 4.1174 | 4.1174 | 4.1174 | 4.1174 | 4.1174 | 4.1174 | 4.1174 | 4.1174 | 4.1174 | 4.1174 | 4.1174 | 4.1174 | 4.1174 | 4.1174 | 4.1174 | 4.1174 | 4.1174 | 4.1174 | 4.1174 | 4.1174 | 4.1174 | 4.1174 | 4.1174 | 4.1174 | 4.1174 | 4.1174
|  |  | Optimal timing (interim calc) | 0 | 0 | 0 | 1 | 1 | 1 | 1 | [19 empty] | 1 | 1 | 1 | 1 | bar: 1 to 19
|  |  | Optimal timing | - | - | - | Yes | - | - | - | [19 empty] | - | - | - | - | bar: 1 to 19
Adjusted For Optimal Timing: | 57.1221 | 63.6507 | Capex | 0 | 0 | 63.6507 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 7.8901 | 17.1857 | Opex | 0 | 0 | 0 | 0.63651 | 0.63651 | 0.63651 | 0.63651 | 0.63651 | 0.63651 | 0.63651 | 0.63651 | 0.63651 | 0.63651 | 0.63651 | 0.63651 | 0.63651 | 0.63651 | 0.63651 | 0.63651 | 0.63651 | 0.63651 | 0.63651 | 0.63651 | 0.63651 | 0.63651 | 0.63651 | 0.63651 | 0.63651 | 0.63651 | 0.63651
| 3926.1287 | 10535.8711 | Reduction in unserved energy | 0 | 0 | 0 | 7.5218 | 74.6435 | 97.6009 | 115.718 | 135.0626 | 159.1861 | 184.1202 | 215.4688 | 290.4585 | 275.411 | 400.6215 | 536.2536 | 536.2536 | 536.2536 | 536.2536 | 536.2536 | 536.2536 | 536.2536 | 536.2536 | 536.2536 | 536.2536 | 536.2536 | 536.2536 | 536.2536 | 536.2536 | 536.2536 | 536.2536
| 3861.1165 | 10455.0348 | Net benefit | 0 | 0 | -63.6507 | 6.8853 | 74.007 | 96.9644 | 115.0814 | 134.4261 | 158.5496 | 183.4837 | 214.8323 | 289.822 | 274.7745 | 399.985 | 535.6171 | 535.6171 | 535.6171 | 535.6171 | 535.6171 | 535.6171 | 535.6171 | 535.6171 | 535.6171 | 535.6171 | 535.6171 | 535.6171 | 535.6171 | 535.6171 | 535.6171 | 535.6171
Option 9
Determining Optimal Timing: | Discounted | Undiscounted
| 52.9866 | 59.0425 | Capex | 0 | 0 | 59.0425 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 7.3189 | 15.9415 | Opex | 0 | 0 | 0 | 0.59043 | 0.59043 | 0.59043 | 0.59043 | 0.59043 | 0.59043 | 0.59043 | 0.59043 | 0.59043 | 0.59043 | 0.59043 | 0.59043 | 0.59043 | 0.59043 | 0.59043 | 0.59043 | 0.59043 | 0.59043 | 0.59043 | 0.59043 | 0.59043 | 0.59043 | 0.59043 | 0.59043 | 0.59043 | 0.59043 | 0.59043
| 8317.247 | 19748.3321 | Reduction in unserved energy | 0 | 0 | 0 | 248.8786 | 356.798 | 429.8384 | 563.9003 | 611.3104 | 658.8656 | 670.8188 | 682.0288 | 723.0532 | 650.1203 | 744.8226 | 837.9936 | 837.9936 | 837.9936 | 837.9936 | 837.9936 | 837.9936 | 837.9936 | 837.9936 | 837.9936 | 837.9936 | 837.9936 | 837.9936 | 837.9936 | 837.9936 | 837.9936 | 837.9936
| 8256.9415 | 19673.348 | Net benefit | 0 | 0 | -59.0425 | 248.2882 | 356.2076 | 429.248 | 563.3099 | 610.7199 | 658.2751 | 670.2283 | 681.4384 | 722.4628 | 649.5299 | 744.2322 | 837.4031 | 837.4031 | 837.4031 | 837.4031 | 837.4031 | 837.4031 | 837.4031 | 837.4031 | 837.4031 | 837.4031 | 837.4031 | 837.4031 | 837.4031 | 837.4031 | 837.4031 | 837.4031
|  |  | EUE Value ($m, real $2024) | 3.3072 | 65.4291 | 247.1322 | 34.2028 | 5.2049 | 9.2665 | 17.4069 | 28.2418 | 43.9089 | 63.1444 | 85.3132 | 131.8371 | 132.1341 | 210.3483 | 300.8588 | 300.8588 | 300.8588 | 300.8588 | 300.8588 | 300.8588 | 300.8588 | 300.8588 | 300.8588 | 300.8588 | 300.8588 | 300.8588 | 300.8588 | 300.8588 | 300.8588 | 300.8588
|  |  | Annualised capex | 0 | 0 | 3.2289 | 3.2289 | 3.2289 | 3.2289 | 3.2289 | 3.2289 | 3.2289 | 3.2289 | 3.2289 | 3.2289 | 3.2289 | 3.2289 | 3.2289 | 3.2289 | 3.2289 | 3.2289 | 3.2289 | 3.2289 | 3.2289 | 3.2289 | 3.2289 | 3.2289 | 3.2289 | 3.2289 | 3.2289 | 3.2289 | 3.2289 | 3.2289
|  |  | Annualised cost (capex+opex) | 0 | 0 | 3.2289 | 3.8194 | 3.8194 | 3.8194 | 3.8194 | 3.8194 | 3.8194 | 3.8194 | 3.8194 | 3.8194 | 3.8194 | 3.8194 | 3.8194 | 3.8194 | 3.8194 | 3.8194 | 3.8194 | 3.8194 | 3.8194 | 3.8194 | 3.8194 | 3.8194 | 3.8194 | 3.8194 | 3.8194 | 3.8194 | 3.8194 | 3.8194
|  |  | Optimal timing (interim calc) | 0 | 0 | 0 | 1 | 1 | 1 | 1 | [19 empty] | 1 | 1 | 1 | 1 | bar: 1 to 19
|  |  | Optimal timing | - | - | - | Yes | - | - | - | [19 empty] | - | - | - | - | bar: 1 to 19
Adjusted For Optimal Timing: | 52.9866 | 59.0425 | Capex | 0 | 0 | 59.0425 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 7.3189 | 15.9415 | Opex | 0 | 0 | 0 | 0.59043 | 0.59043 | 0.59043 | 0.59043 | 0.59043 | 0.59043 | 0.59043 | 0.59043 | 0.59043 | 0.59043 | 0.59043 | 0.59043 | 0.59043 | 0.59043 | 0.59043 | 0.59043 | 0.59043 | 0.59043 | 0.59043 | 0.59043 | 0.59043 | 0.59043 | 0.59043 | 0.59043 | 0.59043 | 0.59043 | 0.59043
| 8317.247 | 19748.3321 | Reduction in unserved energy | 0 | 0 | 0 | 248.8786 | 356.798 | 429.8384 | 563.9003 | 611.3104 | 658.8656 | 670.8188 | 682.0288 | 723.0532 | 650.1203 | 744.8226 | 837.9936 | 837.9936 | 837.9936 | 837.9936 | 837.9936 | 837.9936 | 837.9936 | 837.9936 | 837.9936 | 837.9936 | 837.9936 | 837.9936 | 837.9936 | 837.9936 | 837.9936 | 837.9936
| 8256.9415 | 19673.348 | Net benefit | 0 | 0 | -59.0425 | 248.2882 | 356.2076 | 429.248 | 563.3099 | 610.7199 | 658.2751 | 670.2283 | 681.4384 | 722.4628 | 649.5299 | 744.2322 | 837.4031 | 837.4031 | 837.4031 | 837.4031 | 837.4031 | 837.4031 | 837.4031 | 837.4031 | 837.4031 | 837.4031 | 837.4031 | 837.4031 | 837.4031 | 837.4031 | 837.4031 | 837.4031
Option 10
Determining Optimal Timing: | Discounted | Undiscounted
| 0 | 0 | Capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 7651.0731 | 18249.8268 | Opex | 0.57942 | 69.394 | 227.384 | 249.2213 | 294.5818 | 335.065 | 407.5488 | 461.355 | 512.1363 | 534.2255 | 563.5457 | 603.1232 | 583.5185 | 688.042 | 795.0067 | 795.0067 | 795.0067 | 795.0067 | 795.0067 | 795.0067 | 795.0067 | 795.0067 | 795.0067 | 795.0067 | 795.0067 | 795.0067 | 795.0067 | 795.0067 | 795.0067 | 795.0067
| 6375.8942 | 15208.189 | Reduction in unserved energy | 0.48285 | 57.8283 | 189.4866 | 207.6844 | 245.4848 | 279.2209 | 339.624 | 384.4625 | 426.7802 | 445.1879 | 469.6214 | 502.6026 | 486.2654 | 573.3683 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055
| -1275.1788 | -3041.6378 | Net benefit | -0.096569 | -11.5657 | -37.8973 | -41.5369 | -49.097 | -55.8442 | -67.9248 | -76.8925 | -85.356 | -89.0376 | -93.9243 | -100.5205 | -97.2531 | -114.6737 | -132.5011 | -132.5011 | -132.5011 | -132.5011 | -132.5011 | -132.5011 | -132.5011 | -132.5011 | -132.5011 | -132.5011 | -132.5011 | -132.5011 | -132.5011 | -132.5011 | -132.5011 | -132.5011
|  |  | EUE Value ($m, real $2024) | 2.8305 | 7.6008 | 57.6455 | 75.397 | 116.5181 | 159.884 | 241.6832 | 255.0898 | 275.9942 | 288.7753 | 297.7206 | 352.2877 | 295.989 | 381.8026 | 476.3468 | 476.3468 | 476.3468 | 476.3468 | 476.3468 | 476.3468 | 476.3468 | 476.3468 | 476.3468 | 476.3468 | 476.3468 | 476.3468 | 476.3468 | 476.3468 | 476.3468 | 476.3468
|  |  | Annualised capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Annualised cost (capex+opex) | 0.57942 | 69.394 | 227.384 | 249.2213 | 294.5818 | 335.065 | 407.5488 | 461.355 | 512.1363 | 534.2255 | 563.5457 | 603.1232 | 583.5185 | 688.042 | 795.0067 | 795.0067 | 795.0067 | 795.0067 | 795.0067 | 795.0067 | 795.0067 | 795.0067 | 795.0067 | 795.0067 | 795.0067 | 795.0067 | 795.0067 | 795.0067 | 795.0067 | 795.0067
|  |  | Optimal timing (interim calc) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Optimal timing | - | - | - | - | - | - | - | [19 empty] | - | - | - | - | bar: 1 to 19
Adjusted For Optimal Timing: | 0 | 0 | Capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 7651.0731 | 18249.8268 | Opex | 0.57942 | 69.394 | 227.384 | 249.2213 | 294.5818 | 335.065 | 407.5488 | 461.355 | 512.1363 | 534.2255 | 563.5457 | 603.1232 | 583.5185 | 688.042 | 795.0067 | 795.0067 | 795.0067 | 795.0067 | 795.0067 | 795.0067 | 795.0067 | 795.0067 | 795.0067 | 795.0067 | 795.0067 | 795.0067 | 795.0067 | 795.0067 | 795.0067 | 795.0067
| 7651.0731 | 18249.8268 | Reduction in unserved energy | 0.57942 | 69.394 | 227.384 | 249.2213 | 294.5818 | 335.065 | 407.5488 | 461.355 | 512.1363 | 534.2255 | 563.5457 | 603.1232 | 583.5185 | 688.042 | 795.0067 | 795.0067 | 795.0067 | 795.0067 | 795.0067 | 795.0067 | 795.0067 | 795.0067 | 795.0067 | 795.0067 | 795.0067 | 795.0067 | 795.0067 | 795.0067 | 795.0067 | 795.0067
| 0 | 0 | Net benefit | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## 3.2.5 NPV (Low Demand)
Economic inputs and assumptions
Scenario | Discount rate | Central
| Cost | Central
| VCR | Central
|  | Central | Lower bound | Upper bound
| Discount rate | 5.56% | 4.11% | 7%
| Cost | 100% | 80% | 120%
| VCR | 100% | 80% | 120%
Asset life for calculating annualised capex (years) | Option 1 | 45
| Option 2 | 45
| Option 3 | 45
| Option 4 | 45
| Option 5 | 45
| Option 6 | 45
| Option 7 | 45
| Option 8 | 45
| Option 9 | 45
| Option 10 | 45
|  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30
|  |  |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Outputs | bar: 3 FY27; 7 FY31
Option 1
| Discounted | Undiscounted
| 0 | 0 | Capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Opex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Reduction in unserved energy | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Net benefit | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | EUE Value ($m, real $2024) | 2.9693 | 21.7788 | 114.1785 | 131.7807 | 176.7525 | 225.7545 | 322.8437 | 352.8021 | 385.056 | 397.2848 | 409.7082 | 455.4351 | 394.2596 | 482.4799 | 584.1122 | 584.1122 | 584.1122 | 584.1122 | 584.1122 | 584.1122 | 584.1122 | 584.1122 | 584.1122 | 584.1122 | 584.1122 | 584.1122 | 584.1122 | 584.1122 | 584.1122 | 584.1122
Option 2
Determining Optimal Timing: | Discounted | Undiscounted
| 64.7091 | 72.1048 | Capex | 0 | 0 | 72.1048 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 8.9381 | 19.4683 | Opex | 0 | 0 | 0 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105
| 5173.1818 | 12704.3685 | Reduction in unserved energy | 0 | 0 | 0 | 114.4677 | 144.5456 | 219.8685 | 316.2496 | 345.4785 | 377.0117 | 388.4925 | 400.0559 | 444.7381 | 383.0178 | 469.382 | 568.8163 | 568.8163 | 568.8163 | 568.8163 | 568.8163 | 568.8163 | 568.8163 | 568.8163 | 568.8163 | 568.8163 | 568.8163 | 568.8163 | 568.8163 | 568.8163 | 568.8163 | 568.8163
| 5099.5347 | 12612.7954 | Net benefit | 0 | 0 | -72.1048 | 113.7467 | 143.8245 | 219.1475 | 315.5286 | 344.7574 | 376.2907 | 387.7715 | 399.3349 | 444.0171 | 382.2968 | 468.661 | 568.0952 | 568.0952 | 568.0952 | 568.0952 | 568.0952 | 568.0952 | 568.0952 | 568.0952 | 568.0952 | 568.0952 | 568.0952 | 568.0952 | 568.0952 | 568.0952 | 568.0952 | 568.0952
|  |  | EUE Value ($m, real $2024) | 2.9638 | 21.7788 | 114.1785 | 17.313 | 32.2069 | 5.886 | 6.594 | 7.3236 | 8.0442 | 8.7922 | 9.6523 | 10.697 | 11.2418 | 13.0979 | 15.296 | 15.296 | 15.296 | 15.296 | 15.296 | 15.296 | 15.296 | 15.296 | 15.296 | 15.296 | 15.296 | 15.296 | 15.296 | 15.296 | 15.296 | 15.296
|  |  | Annualised capex | 0 | 0 | 3.9433 | 3.9433 | 3.9433 | 3.9433 | 3.9433 | 3.9433 | 3.9433 | 3.9433 | 3.9433 | 3.9433 | 3.9433 | 3.9433 | 3.9433 | 3.9433 | 3.9433 | 3.9433 | 3.9433 | 3.9433 | 3.9433 | 3.9433 | 3.9433 | 3.9433 | 3.9433 | 3.9433 | 3.9433 | 3.9433 | 3.9433 | 3.9433
|  |  | Annualised cost (capex+opex) | 0 | 0 | 3.9433 | 4.6643 | 4.6643 | 4.6643 | 4.6643 | 4.6643 | 4.6643 | 4.6643 | 4.6643 | 4.6643 | 4.6643 | 4.6643 | 4.6643 | 4.6643 | 4.6643 | 4.6643 | 4.6643 | 4.6643 | 4.6643 | 4.6643 | 4.6643 | 4.6643 | 4.6643 | 4.6643 | 4.6643 | 4.6643 | 4.6643 | 4.6643
|  |  | Optimal timing (interim calc) | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  |  | Optimal timing | - | - | - | Yes | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Adjusted For Optimal Timing: | 64.7091 | 72.1048 | Capex | 0 | 0 | 72.1048 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 8.9381 | 19.4683 | Opex | 0 | 0 | 0 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105
| 5173.1818 | 12704.3685 | Reduction in unserved energy | 0 | 0 | 0 | 114.4677 | 144.5456 | 219.8685 | 316.2496 | 345.4785 | 377.0117 | 388.4925 | 400.0559 | 444.7381 | 383.0178 | 469.382 | 568.8163 | 568.8163 | 568.8163 | 568.8163 | 568.8163 | 568.8163 | 568.8163 | 568.8163 | 568.8163 | 568.8163 | 568.8163 | 568.8163 | 568.8163 | 568.8163 | 568.8163 | 568.8163
| 5099.5347 | 12612.7954 | Net benefit | 0 | 0 | -72.1048 | 113.7467 | 143.8245 | 219.1475 | 315.5286 | 344.7574 | 376.2907 | 387.7715 | 399.3349 | 444.0171 | 382.2968 | 468.661 | 568.0952 | 568.0952 | 568.0952 | 568.0952 | 568.0952 | 568.0952 | 568.0952 | 568.0952 | 568.0952 | 568.0952 | 568.0952 | 568.0952 | 568.0952 | 568.0952 | 568.0952 | 568.0952
Option 3
Determining Optimal Timing: | Discounted | Undiscounted
| 39.0606 | 43.5248 | Capex | 0 | 0 | 43.5248 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 5.3953 | 11.7517 | Opex | 0 | 0 | 0 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525
| 4499.9352 | 10753.7078 | Reduction in unserved energy | 0 | 0 | 0 | 114.499 | 144.4674 | 219.0819 | 314.256 | 341.0358 | 368.3757 | 374.0701 | 378.0611 | 403.9654 | 344.6633 | 399.2774 | 459.4972 | 459.4972 | 459.4972 | 459.4972 | 459.4972 | 459.4972 | 459.4972 | 459.4972 | 459.4972 | 459.4972 | 459.4972 | 459.4972 | 459.4972 | 459.4972 | 459.4972 | 459.4972
| 4455.4794 | 10698.4313 | Net benefit | 0 | 0 | -43.5248 | 114.0637 | 144.0322 | 218.6467 | 313.8207 | 340.6006 | 367.9405 | 373.6349 | 377.6259 | 403.5302 | 344.228 | 398.8422 | 459.0619 | 459.0619 | 459.0619 | 459.0619 | 459.0619 | 459.0619 | 459.0619 | 459.0619 | 459.0619 | 459.0619 | 459.0619 | 459.0619 | 459.0619 | 459.0619 | 459.0619 | 459.0619
|  |  | EUE Value ($m, real $2024) | 2.9638 | 21.7788 | 114.1785 | 17.2818 | 32.2851 | 6.6726 | 8.5877 | 11.7663 | 16.6803 | 23.2147 | 31.6471 | 51.4697 | 49.5964 | 83.2025 | 124.6151 | 124.6151 | 124.6151 | 124.6151 | 124.6151 | 124.6151 | 124.6151 | 124.6151 | 124.6151 | 124.6151 | 124.6151 | 124.6151 | 124.6151 | 124.6151 | 124.6151 | 124.6151
|  |  | Annualised capex | 0 | 0 | 2.3803 | 2.3803 | 2.3803 | 2.3803 | 2.3803 | 2.3803 | 2.3803 | 2.3803 | 2.3803 | 2.3803 | 2.3803 | 2.3803 | 2.3803 | 2.3803 | 2.3803 | 2.3803 | 2.3803 | 2.3803 | 2.3803 | 2.3803 | 2.3803 | 2.3803 | 2.3803 | 2.3803 | 2.3803 | 2.3803 | 2.3803 | 2.3803
|  |  | Annualised cost (capex+opex) | 0 | 0 | 2.3803 | 2.8155 | 2.8155 | 2.8155 | 2.8155 | 2.8155 | 2.8155 | 2.8155 | 2.8155 | 2.8155 | 2.8155 | 2.8155 | 2.8155 | 2.8155 | 2.8155 | 2.8155 | 2.8155 | 2.8155 | 2.8155 | 2.8155 | 2.8155 | 2.8155 | 2.8155 | 2.8155 | 2.8155 | 2.8155 | 2.8155 | 2.8155
|  |  | Optimal timing (interim calc) | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  |  | Optimal timing | - | - | - | Yes | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Adjusted For Optimal Timing: | 39.0606 | 43.5248 | Capex | 0 | 0 | 43.5248 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 5.3953 | 11.7517 | Opex | 0 | 0 | 0 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525
| 4499.9352 | 10753.7078 | Reduction in unserved energy | 0 | 0 | 0 | 114.499 | 144.4674 | 219.0819 | 314.256 | 341.0358 | 368.3757 | 374.0701 | 378.0611 | 403.9654 | 344.6633 | 399.2774 | 459.4972 | 459.4972 | 459.4972 | 459.4972 | 459.4972 | 459.4972 | 459.4972 | 459.4972 | 459.4972 | 459.4972 | 459.4972 | 459.4972 | 459.4972 | 459.4972 | 459.4972 | 459.4972
| 4455.4794 | 10698.4313 | Net benefit | 0 | 0 | -43.5248 | 114.0637 | 144.0322 | 218.6467 | 313.8207 | 340.6006 | 367.9405 | 373.6349 | 377.6259 | 403.5302 | 344.228 | 398.8422 | 459.0619 | 459.0619 | 459.0619 | 459.0619 | 459.0619 | 459.0619 | 459.0619 | 459.0619 | 459.0619 | 459.0619 | 459.0619 | 459.0619 | 459.0619 | 459.0619 | 459.0619 | 459.0619
Option 4
Determining Optimal Timing: | Discounted | Undiscounted
| 53.4373 | 59.5447 | Capex | 0 | 0 | 59.5447 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 7.3811 | 16.0771 | Opex | 0 | 0 | 0 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545
| 1631.5901 | 4458.5198 | Reduction in unserved energy | 0 | 0 | 0 | 0.97558 | 2.2785 | 40.1865 | 47.1968 | 54.38 | 63.0571 | 71.4269 | 82.3973 | 115.5296 | 101.3999 | 157.8982 | 232.6121 | 232.6121 | 232.6121 | 232.6121 | 232.6121 | 232.6121 | 232.6121 | 232.6121 | 232.6121 | 232.6121 | 232.6121 | 232.6121 | 232.6121 | 232.6121 | 232.6121 | 232.6121
| 1570.7717 | 4382.8981 | Net benefit | 0 | 0 | -59.5447 | 0.38013 | 1.6831 | 39.5911 | 46.6014 | 53.7845 | 62.4617 | 70.8315 | 81.8018 | 114.9342 | 100.8044 | 157.3028 | 232.0166 | 232.0166 | 232.0166 | 232.0166 | 232.0166 | 232.0166 | 232.0166 | 232.0166 | 232.0166 | 232.0166 | 232.0166 | 232.0166 | 232.0166 | 232.0166 | 232.0166 | 232.0166
|  |  | EUE Value ($m, real $2024) | 2.9638 | 21.7788 | 114.1785 | 130.8052 | 174.474 | 185.568 | 275.6469 | 298.4222 | 321.9988 | 325.8579 | 327.3109 | 339.9055 | 292.8598 | 324.5817 | 351.5002 | 351.5002 | 351.5002 | 351.5002 | 351.5002 | 351.5002 | 351.5002 | 351.5002 | 351.5002 | 351.5002 | 351.5002 | 351.5002 | 351.5002 | 351.5002 | 351.5002 | 351.5002
|  |  | Annualised capex | 0 | 0 | 3.2564 | 3.2564 | 3.2564 | 3.2564 | 3.2564 | 3.2564 | 3.2564 | 3.2564 | 3.2564 | 3.2564 | 3.2564 | 3.2564 | 3.2564 | 3.2564 | 3.2564 | 3.2564 | 3.2564 | 3.2564 | 3.2564 | 3.2564 | 3.2564 | 3.2564 | 3.2564 | 3.2564 | 3.2564 | 3.2564 | 3.2564 | 3.2564
|  |  | Annualised cost (capex+opex) | 0 | 0 | 3.2564 | 3.8518 | 3.8518 | 3.8518 | 3.8518 | 3.8518 | 3.8518 | 3.8518 | 3.8518 | 3.8518 | 3.8518 | 3.8518 | 3.8518 | 3.8518 | 3.8518 | 3.8518 | 3.8518 | 3.8518 | 3.8518 | 3.8518 | 3.8518 | 3.8518 | 3.8518 | 3.8518 | 3.8518 | 3.8518 | 3.8518 | 3.8518
|  |  | Optimal timing (interim calc) | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  |  | Optimal timing | - | - | - | - | - | Yes | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
[11 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19
Adjusted For Optimal Timing: | 47.9563 | 59.5447 | Capex | 0 | 0 | 0 | 0 | 59.5447 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 6.3953 | 14.8862 | Opex | 0 | 0 | 0 | 0 | 0 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545
| 1628.9256 | 4455.2658 | Reduction in unserved energy | 0 | 0 | 0 | 0 | 0 | 40.1865 | 47.1968 | 54.38 | 63.0571 | 71.4269 | 82.3973 | 115.5296 | 101.3999 | 157.8982 | 232.6121 | 232.6121 | 232.6121 | 232.6121 | 232.6121 | 232.6121 | 232.6121 | 232.6121 | 232.6121 | 232.6121 | 232.6121 | 232.6121 | 232.6121 | 232.6121 | 232.6121 | 232.6121
| 1574.574 | 4380.8349 | Net benefit | 0 | 0 | 0 | 0 | -59.5447 | 39.5911 | 46.6014 | 53.7845 | 62.4617 | 70.8315 | 81.8018 | 114.9342 | 100.8044 | 157.3028 | 232.0166 | 232.0166 | 232.0166 | 232.0166 | 232.0166 | 232.0166 | 232.0166 | 232.0166 | 232.0166 | 232.0166 | 232.0166 | 232.0166 | 232.0166 | 232.0166 | 232.0166 | 232.0166
Option 5
Determining Optimal Timing: | Discounted | Undiscounted
| 49.9911 | 55.7046 | Capex | 0 | 0 | 55.7046 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 6.9051 | 15.0402 | Opex | 0 | 0 | 0 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705
| 4618.3464 | 11038.0772 | Reduction in unserved energy | 0 | 0 | 0 | 119.298 | 149.7531 | 224.9269 | 320.781 | 348.245 | 376.2205 | 382.5871 | 387.3125 | 413.9826 | 355.3345 | 410.8549 | 471.7988 | 471.7988 | 471.7988 | 471.7988 | 471.7988 | 471.7988 | 471.7988 | 471.7988 | 471.7988 | 471.7988 | 471.7988 | 471.7988 | 471.7988 | 471.7988 | 471.7988 | 471.7988
| 4561.4502 | 10967.3324 | Net benefit | 0 | 0 | -55.7046 | 118.741 | 149.196 | 224.3699 | 320.224 | 347.688 | 375.6635 | 382.03 | 386.7554 | 413.4255 | 354.7774 | 410.2979 | 471.2418 | 471.2418 | 471.2418 | 471.2418 | 471.2418 | 471.2418 | 471.2418 | 471.2418 | 471.2418 | 471.2418 | 471.2418 | 471.2418 | 471.2418 | 471.2418 | 471.2418 | 471.2418
|  |  | EUE Value ($m, real $2024) | 2.9638 | 21.7788 | 114.1785 | 12.4827 | 26.9994 | 0.82759 | 2.0626 | 4.5571 | 8.8355 | 14.6977 | 22.3957 | 41.4525 | 38.9251 | 71.625 | 112.3134 | 112.3134 | 112.3134 | 112.3134 | 112.3134 | 112.3134 | 112.3134 | 112.3134 | 112.3134 | 112.3134 | 112.3134 | 112.3134 | 112.3134 | 112.3134 | 112.3134 | 112.3134
|  |  | Annualised capex | 0 | 0 | 3.0464 | 3.0464 | 3.0464 | 3.0464 | 3.0464 | 3.0464 | 3.0464 | 3.0464 | 3.0464 | 3.0464 | 3.0464 | 3.0464 | 3.0464 | 3.0464 | 3.0464 | 3.0464 | 3.0464 | 3.0464 | 3.0464 | 3.0464 | 3.0464 | 3.0464 | 3.0464 | 3.0464 | 3.0464 | 3.0464 | 3.0464 | 3.0464
|  |  | Annualised cost (capex+opex) | 0 | 0 | 3.0464 | 3.6034 | 3.6034 | 3.6034 | 3.6034 | 3.6034 | 3.6034 | 3.6034 | 3.6034 | 3.6034 | 3.6034 | 3.6034 | 3.6034 | 3.6034 | 3.6034 | 3.6034 | 3.6034 | 3.6034 | 3.6034 | 3.6034 | 3.6034 | 3.6034 | 3.6034 | 3.6034 | 3.6034 | 3.6034 | 3.6034 | 3.6034
|  |  | Optimal timing (interim calc) | 0 | 0 | 0 | 1 | 1 | 1 | 1 | [19 empty] | 1 | 1 | 1 | 1 | bar: 1 to 19
|  |  | Optimal timing | - | - | - | Yes | - | - | - | [19 empty] | - | - | - | - | bar: 1 to 19
Adjusted For Optimal Timing: | 49.9911 | 55.7046 | Capex | 0 | 0 | 55.7046 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 6.9051 | 15.0402 | Opex | 0 | 0 | 0 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705
| 4618.3464 | 11038.0772 | Reduction in unserved energy | 0 | 0 | 0 | 119.298 | 149.7531 | 224.9269 | 320.781 | 348.245 | 376.2205 | 382.5871 | 387.3125 | 413.9826 | 355.3345 | 410.8549 | 471.7988 | 471.7988 | 471.7988 | 471.7988 | 471.7988 | 471.7988 | 471.7988 | 471.7988 | 471.7988 | 471.7988 | 471.7988 | 471.7988 | 471.7988 | 471.7988 | 471.7988 | 471.7988
| 4561.4502 | 10967.3324 | Net benefit | 0 | 0 | -55.7046 | 118.741 | 149.196 | 224.3699 | 320.224 | 347.688 | 375.6635 | 382.03 | 386.7554 | 413.4255 | 354.7774 | 410.2979 | 471.2418 | 471.2418 | 471.2418 | 471.2418 | 471.2418 | 471.2418 | 471.2418 | 471.2418 | 471.2418 | 471.2418 | 471.2418 | 471.2418 | 471.2418 | 471.2418 | 471.2418 | 471.2418
Option 6
Determining Optimal Timing: | Discounted | Undiscounted
| 61.1918 | 68.1854 | Capex | 0 | 0 | 68.1854 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 8.4522 | 18.4101 | Opex | 0 | 0 | 0 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185
| 5178.1506 | 12680.8401 | Reduction in unserved energy | 0 | 0 | 0 | 114.4675 | 171.4428 | 219.8676 | 316.2475 | 345.4744 | 377.0051 | 388.4667 | 399.9994 | 444.4729 | 382.4832 | 467.9387 | 565.8109 | 565.8109 | 565.8109 | 565.8109 | 565.8109 | 565.8109 | 565.8109 | 565.8109 | 565.8109 | 565.8109 | 565.8109 | 565.8109 | 565.8109 | 565.8109 | 565.8109 | 565.8109
| 5108.5067 | 12594.2446 | Net benefit | 0 | 0 | -68.1854 | 113.7857 | 170.761 | 219.1857 | 315.5656 | 344.7925 | 376.3232 | 387.7849 | 399.3175 | 443.7911 | 381.8014 | 467.2569 | 565.129 | 565.129 | 565.129 | 565.129 | 565.129 | 565.129 | 565.129 | 565.129 | 565.129 | 565.129 | 565.129 | 565.129 | 565.129 | 565.129 | 565.129 | 565.129
|  |  | EUE Value ($m, real $2024) | 2.9638 | 21.7788 | 114.1785 | 17.3132 | 5.3097 | 5.887 | 6.5962 | 7.3278 | 8.0509 | 8.8181 | 9.7088 | 10.9622 | 11.7764 | 14.5412 | 18.3014 | 18.3014 | 18.3014 | 18.3014 | 18.3014 | 18.3014 | 18.3014 | 18.3014 | 18.3014 | 18.3014 | 18.3014 | 18.3014 | 18.3014 | 18.3014 | 18.3014 | 18.3014
|  |  | Annualised capex | 0 | 0 | 3.7289 | 3.7289 | 3.7289 | 3.7289 | 3.7289 | 3.7289 | 3.7289 | 3.7289 | 3.7289 | 3.7289 | 3.7289 | 3.7289 | 3.7289 | 3.7289 | 3.7289 | 3.7289 | 3.7289 | 3.7289 | 3.7289 | 3.7289 | 3.7289 | 3.7289 | 3.7289 | 3.7289 | 3.7289 | 3.7289 | 3.7289 | 3.7289
|  |  | Annualised cost (capex+opex) | 0 | 0 | 3.7289 | 4.4108 | 4.4108 | 4.4108 | 4.4108 | 4.4108 | 4.4108 | 4.4108 | 4.4108 | 4.4108 | 4.4108 | 4.4108 | 4.4108 | 4.4108 | 4.4108 | 4.4108 | 4.4108 | 4.4108 | 4.4108 | 4.4108 | 4.4108 | 4.4108 | 4.4108 | 4.4108 | 4.4108 | 4.4108 | 4.4108 | 4.4108
|  |  | Optimal timing (interim calc) | 0 | 0 | 0 | 1 | 1 | 1 | 1 | [19 empty] | 1 | 1 | 1 | 1 | bar: 1 to 19
|  |  | Optimal timing | - | - | - | Yes | - | - | - | [19 empty] | - | - | - | - | bar: 1 to 19
Adjusted For Optimal Timing: | 61.1918 | 68.1854 | Capex | 0 | 0 | 68.1854 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 8.4522 | 18.4101 | Opex | 0 | 0 | 0 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185
| 5178.1506 | 12680.8401 | Reduction in unserved energy | 0 | 0 | 0 | 114.4675 | 171.4428 | 219.8676 | 316.2475 | 345.4744 | 377.0051 | 388.4667 | 399.9994 | 444.4729 | 382.4832 | 467.9387 | 565.8109 | 565.8109 | 565.8109 | 565.8109 | 565.8109 | 565.8109 | 565.8109 | 565.8109 | 565.8109 | 565.8109 | 565.8109 | 565.8109 | 565.8109 | 565.8109 | 565.8109 | 565.8109
| 5108.5067 | 12594.2446 | Net benefit | 0 | 0 | -68.1854 | 113.7857 | 170.761 | 219.1857 | 315.5656 | 344.7925 | 376.3232 | 387.7849 | 399.3175 | 443.7911 | 381.8014 | 467.2569 | 565.129 | 565.129 | 565.129 | 565.129 | 565.129 | 565.129 | 565.129 | 565.129 | 565.129 | 565.129 | 565.129 | 565.129 | 565.129 | 565.129 | 565.129 | 565.129
Option 7
Determining Optimal Timing: | Discounted | Undiscounted
| 33.225 | 37.0224 | Capex | 0 | 0 | 37.0224 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 4.5893 | 9.996 | Opex | 0 | 0 | 0 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022
| 4509.9613 | 10745.723 | Reduction in unserved energy | 0 | 0 | 0 | 114.4797 | 171.126 | 219.0749 | 314.2467 | 341.0226 | 368.3563 | 374.0393 | 377.9908 | 403.7456 | 344.4111 | 398.5578 | 457.417 | 457.417 | 457.417 | 457.417 | 457.417 | 457.417 | 457.417 | 457.417 | 457.417 | 457.417 | 457.417 | 457.417 | 457.417 | 457.417 | 457.417 | 457.417
| 4472.147 | 10698.7046 | Net benefit | 0 | 0 | -37.0224 | 114.1095 | 170.7557 | 218.7046 | 313.8765 | 340.6524 | 367.9861 | 373.6691 | 377.6206 | 403.3754 | 344.0409 | 398.1876 | 457.0468 | 457.0468 | 457.0468 | 457.0468 | 457.0468 | 457.0468 | 457.0468 | 457.0468 | 457.0468 | 457.0468 | 457.0468 | 457.0468 | 457.0468 | 457.0468 | 457.0468 | 457.0468
|  |  | EUE Value ($m, real $2024) | 2.9638 | 21.7788 | 114.1785 | 17.3011 | 5.6265 | 6.6797 | 8.5969 | 11.7795 | 16.6996 | 23.2455 | 31.7174 | 51.6895 | 49.8486 | 83.9221 | 126.6952 | 126.6952 | 126.6952 | 126.6952 | 126.6952 | 126.6952 | 126.6952 | 126.6952 | 126.6952 | 126.6952 | 126.6952 | 126.6952 | 126.6952 | 126.6952 | 126.6952 | 126.6952
|  |  | Annualised capex | 0 | 0 | 2.0247 | 2.0247 | 2.0247 | 2.0247 | 2.0247 | 2.0247 | 2.0247 | 2.0247 | 2.0247 | 2.0247 | 2.0247 | 2.0247 | 2.0247 | 2.0247 | 2.0247 | 2.0247 | 2.0247 | 2.0247 | 2.0247 | 2.0247 | 2.0247 | 2.0247 | 2.0247 | 2.0247 | 2.0247 | 2.0247 | 2.0247 | 2.0247
|  |  | Annualised cost (capex+opex) | 0 | 0 | 2.0247 | 2.3949 | 2.3949 | 2.3949 | 2.3949 | 2.3949 | 2.3949 | 2.3949 | 2.3949 | 2.3949 | 2.3949 | 2.3949 | 2.3949 | 2.3949 | 2.3949 | 2.3949 | 2.3949 | 2.3949 | 2.3949 | 2.3949 | 2.3949 | 2.3949 | 2.3949 | 2.3949 | 2.3949 | 2.3949 | 2.3949 | 2.3949
|  |  | Optimal timing (interim calc) | 0 | 0 | 0 | 1 | 1 | 1 | 1 | [19 empty] | 1 | 1 | 1 | 1 | bar: 1 to 19
|  |  | Optimal timing | - | - | - | Yes | - | - | - | [19 empty] | - | - | - | - | bar: 1 to 19
Adjusted For Optimal Timing: | 33.225 | 37.0224 | Capex | 0 | 0 | 37.0224 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 4.5893 | 9.996 | Opex | 0 | 0 | 0 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022
| 4509.9613 | 10745.723 | Reduction in unserved energy | 0 | 0 | 0 | 114.4797 | 171.126 | 219.0749 | 314.2467 | 341.0226 | 368.3563 | 374.0393 | 377.9908 | 403.7456 | 344.4111 | 398.5578 | 457.417 | 457.417 | 457.417 | 457.417 | 457.417 | 457.417 | 457.417 | 457.417 | 457.417 | 457.417 | 457.417 | 457.417 | 457.417 | 457.417 | 457.417 | 457.417
| 4472.147 | 10698.7046 | Net benefit | 0 | 0 | -37.0224 | 114.1095 | 170.7557 | 218.7046 | 313.8765 | 340.6524 | 367.9861 | 373.6691 | 377.6206 | 403.3754 | 344.0409 | 398.1876 | 457.0468 | 457.0468 | 457.0468 | 457.0468 | 457.0468 | 457.0468 | 457.0468 | 457.0468 | 457.0468 | 457.0468 | 457.0468 | 457.0468 | 457.0468 | 457.0468 | 457.0468 | 457.0468
Option 8
Determining Optimal Timing: | Discounted | Undiscounted
| 47.6017 | 53.0422 | Capex | 0 | 0 | 53.0422 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 6.5751 | 14.3214 | Opex | 0 | 0 | 0 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042
| 1637.6586 | 4439.0465 | Reduction in unserved energy | 0 | 0 | 0 | 0.96727 | 28.9172 | 40.1667 | 47.1608 | 54.3233 | 62.9655 | 71.2737 | 82.2049 | 115.2043 | 100.9777 | 156.7708 | 229.8821 | 229.8821 | 229.8821 | 229.8821 | 229.8821 | 229.8821 | 229.8821 | 229.8821 | 229.8821 | 229.8821 | 229.8821 | 229.8821 | 229.8821 | 229.8821 | 229.8821 | 229.8821
| 1583.4817 | 4371.6829 | Net benefit | 0 | 0 | -53.0422 | 0.43685 | 28.3868 | 39.6363 | 46.6304 | 53.7929 | 62.4351 | 70.7433 | 81.6745 | 114.6739 | 100.4472 | 156.2404 | 229.3517 | 229.3517 | 229.3517 | 229.3517 | 229.3517 | 229.3517 | 229.3517 | 229.3517 | 229.3517 | 229.3517 | 229.3517 | 229.3517 | 229.3517 | 229.3517 | 229.3517 | 229.3517
|  |  | EUE Value ($m, real $2024) | 2.9638 | 21.7788 | 114.1785 | 130.8135 | 147.8353 | 185.5878 | 275.6828 | 298.4788 | 322.0905 | 326.0111 | 327.5033 | 340.2308 | 293.282 | 325.7091 | 354.2301 | 354.2301 | 354.2301 | 354.2301 | 354.2301 | 354.2301 | 354.2301 | 354.2301 | 354.2301 | 354.2301 | 354.2301 | 354.2301 | 354.2301 | 354.2301 | 354.2301 | 354.2301
|  |  | Annualised capex | 0 | 0 | 2.9008 | 2.9008 | 2.9008 | 2.9008 | 2.9008 | 2.9008 | 2.9008 | 2.9008 | 2.9008 | 2.9008 | 2.9008 | 2.9008 | 2.9008 | 2.9008 | 2.9008 | 2.9008 | 2.9008 | 2.9008 | 2.9008 | 2.9008 | 2.9008 | 2.9008 | 2.9008 | 2.9008 | 2.9008 | 2.9008 | 2.9008 | 2.9008
|  |  | Annualised cost (capex+opex) | 0 | 0 | 2.9008 | 3.4312 | 3.4312 | 3.4312 | 3.4312 | 3.4312 | 3.4312 | 3.4312 | 3.4312 | 3.4312 | 3.4312 | 3.4312 | 3.4312 | 3.4312 | 3.4312 | 3.4312 | 3.4312 | 3.4312 | 3.4312 | 3.4312 | 3.4312 | 3.4312 | 3.4312 | 3.4312 | 3.4312 | 3.4312 | 3.4312 | 3.4312
|  |  | Optimal timing (interim calc) | 0 | 0 | 0 | 0 | 1 | 1 | 1 | [19 empty] | 1 | 1 | 1 | 1 | bar: 1 to 19
|  |  | Optimal timing | - | - | - | - | Yes | - | - | [19 empty] | - | - | - | - | bar: 1 to 19
Adjusted For Optimal Timing: | 45.0945 | 53.0422 | Capex | 0 | 0 | 0 | 53.0422 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 6.1241 | 13.791 | Opex | 0 | 0 | 0 | 0 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042
| 1636.8362 | 4438.0793 | Reduction in unserved energy | 0 | 0 | 0 | 0 | 28.9172 | 40.1667 | 47.1608 | 54.3233 | 62.9655 | 71.2737 | 82.2049 | 115.2043 | 100.9777 | 156.7708 | 229.8821 | 229.8821 | 229.8821 | 229.8821 | 229.8821 | 229.8821 | 229.8821 | 229.8821 | 229.8821 | 229.8821 | 229.8821 | 229.8821 | 229.8821 | 229.8821 | 229.8821 | 229.8821
| 1585.6176 | 4371.2461 | Net benefit | 0 | 0 | 0 | -53.0422 | 28.3868 | 39.6363 | 46.6304 | 53.7929 | 62.4351 | 70.7433 | 81.6745 | 114.6739 | 100.4472 | 156.2404 | 229.3517 | 229.3517 | 229.3517 | 229.3517 | 229.3517 | 229.3517 | 229.3517 | 229.3517 | 229.3517 | 229.3517 | 229.3517 | 229.3517 | 229.3517 | 229.3517 | 229.3517 | 229.3517
Option 9
Determining Optimal Timing: | Discounted | Undiscounted
| 44.1555 | 49.2021 | Capex | 0 | 0 | 49.2021 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 6.0991 | 13.2846 | Opex | 0 | 0 | 0 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202
| 4628.3505 | 11030.0334 | Reduction in unserved energy | 0 | 0 | 0 | 119.2787 | 176.4115 | 224.9198 | 320.7715 | 348.2315 | 376.2006 | 382.5537 | 387.241 | 413.7612 | 355.0804 | 410.1315 | 469.7157 | 469.7157 | 469.7157 | 469.7157 | 469.7157 | 469.7157 | 469.7157 | 469.7157 | 469.7157 | 469.7157 | 469.7157 | 469.7157 | 469.7157 | 469.7157 | 469.7157 | 469.7157
| 4578.0959 | 10967.5467 | Net benefit | 0 | 0 | -49.2021 | 118.7867 | 175.9195 | 224.4277 | 320.2795 | 347.7394 | 375.7086 | 382.0617 | 386.749 | 413.2692 | 354.5884 | 409.6395 | 469.2237 | 469.2237 | 469.2237 | 469.2237 | 469.2237 | 469.2237 | 469.2237 | 469.2237 | 469.2237 | 469.2237 | 469.2237 | 469.2237 | 469.2237 | 469.2237 | 469.2237 | 469.2237
|  |  | EUE Value ($m, real $2024) | 2.9638 | 21.7788 | 114.1785 | 12.502 | 0.34095 | 0.83478 | 2.0721 | 4.5706 | 8.8554 | 14.7311 | 22.4672 | 41.6739 | 39.1792 | 72.3484 | 114.3965 | 114.3965 | 114.3965 | 114.3965 | 114.3965 | 114.3965 | 114.3965 | 114.3965 | 114.3965 | 114.3965 | 114.3965 | 114.3965 | 114.3965 | 114.3965 | 114.3965 | 114.3965
|  |  | Annualised capex | 0 | 0 | 2.6908 | 2.6908 | 2.6908 | 2.6908 | 2.6908 | 2.6908 | 2.6908 | 2.6908 | 2.6908 | 2.6908 | 2.6908 | 2.6908 | 2.6908 | 2.6908 | 2.6908 | 2.6908 | 2.6908 | 2.6908 | 2.6908 | 2.6908 | 2.6908 | 2.6908 | 2.6908 | 2.6908 | 2.6908 | 2.6908 | 2.6908 | 2.6908
|  |  | Annualised cost (capex+opex) | 0 | 0 | 2.6908 | 3.1828 | 3.1828 | 3.1828 | 3.1828 | 3.1828 | 3.1828 | 3.1828 | 3.1828 | 3.1828 | 3.1828 | 3.1828 | 3.1828 | 3.1828 | 3.1828 | 3.1828 | 3.1828 | 3.1828 | 3.1828 | 3.1828 | 3.1828 | 3.1828 | 3.1828 | 3.1828 | 3.1828 | 3.1828 | 3.1828 | 3.1828
|  |  | Optimal timing (interim calc) | 0 | 0 | 0 | 1 | 1 | 1 | 1 | [19 empty] | 1 | 1 | 1 | 1 | bar: 1 to 19
|  |  | Optimal timing | - | - | - | Yes | - | - | - | [19 empty] | - | - | - | - | bar: 1 to 19
Adjusted For Optimal Timing: | 44.1555 | 49.2021 | Capex | 0 | 0 | 49.2021 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 6.0991 | 13.2846 | Opex | 0 | 0 | 0 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202
| 4628.3505 | 11030.0334 | Reduction in unserved energy | 0 | 0 | 0 | 119.2787 | 176.4115 | 224.9198 | 320.7715 | 348.2315 | 376.2006 | 382.5537 | 387.241 | 413.7612 | 355.0804 | 410.1315 | 469.7157 | 469.7157 | 469.7157 | 469.7157 | 469.7157 | 469.7157 | 469.7157 | 469.7157 | 469.7157 | 469.7157 | 469.7157 | 469.7157 | 469.7157 | 469.7157 | 469.7157 | 469.7157
| 4578.0959 | 10967.5467 | Net benefit | 0 | 0 | -49.2021 | 118.7867 | 175.9195 | 224.4277 | 320.2795 | 347.7394 | 375.7086 | 382.0617 | 386.749 | 413.2692 | 354.5884 | 409.6395 | 469.2237 | 469.2237 | 469.2237 | 469.2237 | 469.2237 | 469.2237 | 469.2237 | 469.2237 | 469.2237 | 469.2237 | 469.2237 | 469.2237 | 469.2237 | 469.2237 | 469.2237 | 469.2237
Option 10
Determining Optimal Timing: | Discounted | Undiscounted
| 0 | 0 | Capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 6375.8942 | 15208.189 | Opex | 0.48285 | 57.8283 | 189.4866 | 207.6844 | 245.4848 | 279.2209 | 339.624 | 384.4625 | 426.7802 | 445.1879 | 469.6214 | 502.6026 | 486.2654 | 573.3683 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055
| 3882.595 | 9271.4174 | Reduction in unserved energy | 0.47304 | 18.7438 | 100.6276 | 112.4911 | 140.1135 | 168.7778 | 224.022 | 251.6469 | 278.4393 | 287.3959 | 299.1019 | 317.8005 | 289.9539 | 342.4209 | 402.4631 | 402.4631 | 402.4631 | 402.4631 | 402.4631 | 402.4631 | 402.4631 | 402.4631 | 402.4631 | 402.4631 | 402.4631 | 402.4631 | 402.4631 | 402.4631 | 402.4631 | 402.4631
| -2493.2992 | -5936.7716 | Net benefit | -0.009803 | -39.0845 | -88.859 | -95.1933 | -105.3713 | -110.443 | -115.602 | -132.8156 | -148.3409 | -157.792 | -170.5195 | -184.8021 | -196.3115 | -230.9474 | -260.0425 | -260.0425 | -260.0425 | -260.0425 | -260.0425 | -260.0425 | -260.0425 | -260.0425 | -260.0425 | -260.0425 | -260.0425 | -260.0425 | -260.0425 | -260.0425 | -260.0425 | -260.0425
|  |  | EUE Value ($m, real $2024) | 2.4962 | 3.0349 | 13.5509 | 19.2897 | 36.639 | 56.9767 | 98.8217 | 101.1552 | 106.6167 | 109.8889 | 110.6063 | 137.6346 | 104.3058 | 140.059 | 181.6492 | 181.6492 | 181.6492 | 181.6492 | 181.6492 | 181.6492 | 181.6492 | 181.6492 | 181.6492 | 181.6492 | 181.6492 | 181.6492 | 181.6492 | 181.6492 | 181.6492 | 181.6492
|  |  | Annualised capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Annualised cost (capex+opex) | 0.48285 | 57.8283 | 189.4866 | 207.6844 | 245.4848 | 279.2209 | 339.624 | 384.4625 | 426.7802 | 445.1879 | 469.6214 | 502.6026 | 486.2654 | 573.3683 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055
|  |  | Optimal timing (interim calc) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Optimal timing | - | - | - | - | - | - | - | [19 empty] | - | - | - | - | bar: 1 to 19
Adjusted For Optimal Timing: | 0 | 0 | Capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 6375.8942 | 15208.189 | Opex | 0.48285 | 57.8283 | 189.4866 | 207.6844 | 245.4848 | 279.2209 | 339.624 | 384.4625 | 426.7802 | 445.1879 | 469.6214 | 502.6026 | 486.2654 | 573.3683 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055
| 6375.8942 | 15208.189 | Reduction in unserved energy | 0.48285 | 57.8283 | 189.4866 | 207.6844 | 245.4848 | 279.2209 | 339.624 | 384.4625 | 426.7802 | 445.1879 | 469.6214 | 502.6026 | 486.2654 | 573.3683 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055
| 0 | 0 | Net benefit | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## 3.2.6 NPV (High Demand)
Economic inputs and assumptions
Scenario | Discount rate | Central
| Cost | Central
| VCR | Central
|  | Central | Lower bound | Upper bound
| Discount rate | 5.56% | 4.11% | 7%
| Cost | 100% | 80% | 120%
| VCR | 100% | 80% | 120%
Asset life for calculating annualised capex (years) | Option 1 | 45
| Option 2 | 45
| Option 3 | 45
| Option 4 | 45
| Option 5 | 45
| Option 6 | 45
| Option 7 | 45
| Option 8 | 45
| Option 9 | 45
| Option 10 | 45
|  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30
|  |  |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Outputs | bar: 3 FY27; 7 FY31
Option 1
| Discounted | Undiscounted
| 0 | 0 | Capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Opex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Reduction in unserved energy | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Net benefit | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | EUE Value ($m, real $2024) | 3.7852 | 148.6333 | 447.8825 | 519.6658 | 650.8055 | 764.1517 | 963.7359 | 1060.4142 | 1165.4077 | 1226.8406 | 1298.0628 | 1455.5553 | 1371.3047 | 1662.4831 | 1954.5638 | 1954.5638 | 1954.5638 | 1954.5638 | 1954.5638 | 1954.5638 | 1954.5638 | 1954.5638 | 1954.5638 | 1954.5638 | 1954.5638 | 1954.5638 | 1954.5638 | 1954.5638 | 1954.5638 | 1954.5638
Option 2
Determining Optimal Timing: | Discounted | Undiscounted
| 64.7091 | 72.1048 | Capex | 0 | 0 | 72.1048 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 8.9381 | 19.4683 | Opex | 0 | 0 | 0 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105
| 16890.9885 | 41538.162 | Reduction in unserved energy | 0 | 0 | 0 | 450.0479 | 540.2973 | 753.6738 | 948.4909 | 1041.7838 | 1142.0212 | 1198.4321 | 1264.1135 | 1410.5176 | 1332.408 | 1596.87 | 1866.2191 | 1866.2191 | 1866.2191 | 1866.2191 | 1866.2191 | 1866.2191 | 1866.2191 | 1866.2191 | 1866.2191 | 1866.2191 | 1866.2191 | 1866.2191 | 1866.2191 | 1866.2191 | 1866.2191 | 1866.2191
| 16817.3413 | 41446.5889 | Net benefit | 0 | 0 | -72.1048 | 449.3268 | 539.5763 | 752.9528 | 947.7698 | 1041.0628 | 1141.3002 | 1197.711 | 1263.3924 | 1409.7966 | 1331.6869 | 1596.149 | 1865.4981 | 1865.4981 | 1865.4981 | 1865.4981 | 1865.4981 | 1865.4981 | 1865.4981 | 1865.4981 | 1865.4981 | 1865.4981 | 1865.4981 | 1865.4981 | 1865.4981 | 1865.4981 | 1865.4981 | 1865.4981
|  |  | EUE Value ($m, real $2024) | 3.7784 | 148.6333 | 447.8825 | 69.6179 | 110.5081 | 10.4779 | 15.245 | 18.6303 | 23.3865 | 28.4085 | 33.9493 | 45.0377 | 38.8967 | 65.6131 | 88.3447 | 88.3447 | 88.3447 | 88.3447 | 88.3447 | 88.3447 | 88.3447 | 88.3447 | 88.3447 | 88.3447 | 88.3447 | 88.3447 | 88.3447 | 88.3447 | 88.3447 | 88.3447
|  |  | Annualised capex | 0 | 0 | 3.9433 | 3.9433 | 3.9433 | 3.9433 | 3.9433 | 3.9433 | 3.9433 | 3.9433 | 3.9433 | 3.9433 | 3.9433 | 3.9433 | 3.9433 | 3.9433 | 3.9433 | 3.9433 | 3.9433 | 3.9433 | 3.9433 | 3.9433 | 3.9433 | 3.9433 | 3.9433 | 3.9433 | 3.9433 | 3.9433 | 3.9433 | 3.9433
|  |  | Annualised cost (capex+opex) | 0 | 0 | 3.9433 | 4.6643 | 4.6643 | 4.6643 | 4.6643 | 4.6643 | 4.6643 | 4.6643 | 4.6643 | 4.6643 | 4.6643 | 4.6643 | 4.6643 | 4.6643 | 4.6643 | 4.6643 | 4.6643 | 4.6643 | 4.6643 | 4.6643 | 4.6643 | 4.6643 | 4.6643 | 4.6643 | 4.6643 | 4.6643 | 4.6643 | 4.6643
|  |  | Optimal timing (interim calc) | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  |  | Optimal timing | - | - | - | Yes | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Adjusted For Optimal Timing: | 64.7091 | 72.1048 | Capex | 0 | 0 | 72.1048 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 8.9381 | 19.4683 | Opex | 0 | 0 | 0 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105
| 16890.9885 | 41538.162 | Reduction in unserved energy | 0 | 0 | 0 | 450.0479 | 540.2973 | 753.6738 | 948.4909 | 1041.7838 | 1142.0212 | 1198.4321 | 1264.1135 | 1410.5176 | 1332.408 | 1596.87 | 1866.2191 | 1866.2191 | 1866.2191 | 1866.2191 | 1866.2191 | 1866.2191 | 1866.2191 | 1866.2191 | 1866.2191 | 1866.2191 | 1866.2191 | 1866.2191 | 1866.2191 | 1866.2191 | 1866.2191 | 1866.2191
| 16817.3413 | 41446.5889 | Net benefit | 0 | 0 | -72.1048 | 449.3268 | 539.5763 | 752.9528 | 947.7698 | 1041.0628 | 1141.3002 | 1197.711 | 1263.3924 | 1409.7966 | 1331.6869 | 1596.149 | 1865.4981 | 1865.4981 | 1865.4981 | 1865.4981 | 1865.4981 | 1865.4981 | 1865.4981 | 1865.4981 | 1865.4981 | 1865.4981 | 1865.4981 | 1865.4981 | 1865.4981 | 1865.4981 | 1865.4981 | 1865.4981
Option 3
Determining Optimal Timing: | Discounted | Undiscounted
| 39.0606 | 43.5248 | Capex | 0 | 0 | 43.5248 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 5.3953 | 11.7517 | Opex | 0 | 0 | 0 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525
| 13428.0105 | 32007.2593 | Reduction in unserved energy | 0 | 0 | 0 | 436.4877 | 517.4508 | 718.9978 | 894.4735 | 964.5245 | 1034.6607 | 1055.8181 | 1079.0174 | 1141.416 | 1054.9831 | 1211.535 | 1368.6184 | 1368.6184 | 1368.6184 | 1368.6184 | 1368.6184 | 1368.6184 | 1368.6184 | 1368.6184 | 1368.6184 | 1368.6184 | 1368.6184 | 1368.6184 | 1368.6184 | 1368.6184 | 1368.6184 | 1368.6184
| 13383.5546 | 31951.9828 | Net benefit | 0 | 0 | -43.5248 | 436.0525 | 517.0156 | 718.5625 | 894.0382 | 964.0893 | 1034.2254 | 1055.3829 | 1078.5821 | 1140.9807 | 1054.5479 | 1211.0997 | 1368.1832 | 1368.1832 | 1368.1832 | 1368.1832 | 1368.1832 | 1368.1832 | 1368.1832 | 1368.1832 | 1368.1832 | 1368.1832 | 1368.1832 | 1368.1832 | 1368.1832 | 1368.1832 | 1368.1832 | 1368.1832
|  |  | EUE Value ($m, real $2024) | 3.7784 | 148.6333 | 447.8825 | 83.178 | 133.3547 | 45.1539 | 69.2624 | 95.8896 | 130.747 | 171.0225 | 219.0454 | 314.1393 | 316.3216 | 450.9482 | 585.9454 | 585.9454 | 585.9454 | 585.9454 | 585.9454 | 585.9454 | 585.9454 | 585.9454 | 585.9454 | 585.9454 | 585.9454 | 585.9454 | 585.9454 | 585.9454 | 585.9454 | 585.9454
|  |  | Annualised capex | 0 | 0 | 2.3803 | 2.3803 | 2.3803 | 2.3803 | 2.3803 | 2.3803 | 2.3803 | 2.3803 | 2.3803 | 2.3803 | 2.3803 | 2.3803 | 2.3803 | 2.3803 | 2.3803 | 2.3803 | 2.3803 | 2.3803 | 2.3803 | 2.3803 | 2.3803 | 2.3803 | 2.3803 | 2.3803 | 2.3803 | 2.3803 | 2.3803 | 2.3803
|  |  | Annualised cost (capex+opex) | 0 | 0 | 2.3803 | 2.8155 | 2.8155 | 2.8155 | 2.8155 | 2.8155 | 2.8155 | 2.8155 | 2.8155 | 2.8155 | 2.8155 | 2.8155 | 2.8155 | 2.8155 | 2.8155 | 2.8155 | 2.8155 | 2.8155 | 2.8155 | 2.8155 | 2.8155 | 2.8155 | 2.8155 | 2.8155 | 2.8155 | 2.8155 | 2.8155 | 2.8155
|  |  | Optimal timing (interim calc) | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  |  | Optimal timing | - | - | - | Yes | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Adjusted For Optimal Timing: | 39.0606 | 43.5248 | Capex | 0 | 0 | 43.5248 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 5.3953 | 11.7517 | Opex | 0 | 0 | 0 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525
| 13428.0105 | 32007.2593 | Reduction in unserved energy | 0 | 0 | 0 | 436.4877 | 517.4508 | 718.9978 | 894.4735 | 964.5245 | 1034.6607 | 1055.8181 | 1079.0174 | 1141.416 | 1054.9831 | 1211.535 | 1368.6184 | 1368.6184 | 1368.6184 | 1368.6184 | 1368.6184 | 1368.6184 | 1368.6184 | 1368.6184 | 1368.6184 | 1368.6184 | 1368.6184 | 1368.6184 | 1368.6184 | 1368.6184 | 1368.6184 | 1368.6184
| 13383.5546 | 31951.9828 | Net benefit | 0 | 0 | -43.5248 | 436.0525 | 517.0156 | 718.5625 | 894.0382 | 964.0893 | 1034.2254 | 1055.3829 | 1078.5821 | 1140.9807 | 1054.5479 | 1211.0997 | 1368.1832 | 1368.1832 | 1368.1832 | 1368.1832 | 1368.1832 | 1368.1832 | 1368.1832 | 1368.1832 | 1368.1832 | 1368.1832 | 1368.1832 | 1368.1832 | 1368.1832 | 1368.1832 | 1368.1832 | 1368.1832
Option 4
Determining Optimal Timing: | Discounted | Undiscounted
| 53.4373 | 59.5447 | Capex | 0 | 0 | 59.5447 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 7.3811 | 16.0771 | Opex | 0 | 0 | 0 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545
| 8074.6727 | 21528.7356 | Reduction in unserved energy | 0 | 0 | 0 | 44.0697 | 79.6548 | 222.6057 | 260.9788 | 301.4863 | 351.2443 | 404.1007 | 472.9258 | 618.4767 | 605.2142 | 839.3333 | 1083.0403 | 1083.0403 | 1083.0403 | 1083.0403 | 1083.0403 | 1083.0403 | 1083.0403 | 1083.0403 | 1083.0403 | 1083.0403 | 1083.0403 | 1083.0403 | 1083.0403 | 1083.0403 | 1083.0403 | 1083.0403
| 8013.8543 | 21453.1139 | Net benefit | 0 | 0 | -59.5447 | 43.4743 | 79.0593 | 222.0103 | 260.3833 | 300.8909 | 350.6489 | 403.5052 | 472.3304 | 617.8812 | 604.6187 | 838.7379 | 1082.4449 | 1082.4449 | 1082.4449 | 1082.4449 | 1082.4449 | 1082.4449 | 1082.4449 | 1082.4449 | 1082.4449 | 1082.4449 | 1082.4449 | 1082.4449 | 1082.4449 | 1082.4449 | 1082.4449 | 1082.4449
|  |  | EUE Value ($m, real $2024) | 3.7784 | 148.6333 | 447.8825 | 475.596 | 571.1507 | 541.546 | 702.7571 | 758.9278 | 814.1633 | 822.74 | 825.1369 | 837.0786 | 766.0905 | 823.1498 | 871.5235 | 871.5235 | 871.5235 | 871.5235 | 871.5235 | 871.5235 | 871.5235 | 871.5235 | 871.5235 | 871.5235 | 871.5235 | 871.5235 | 871.5235 | 871.5235 | 871.5235 | 871.5235
|  |  | Annualised capex | 0 | 0 | 3.2564 | 3.2564 | 3.2564 | 3.2564 | 3.2564 | 3.2564 | 3.2564 | 3.2564 | 3.2564 | 3.2564 | 3.2564 | 3.2564 | 3.2564 | 3.2564 | 3.2564 | 3.2564 | 3.2564 | 3.2564 | 3.2564 | 3.2564 | 3.2564 | 3.2564 | 3.2564 | 3.2564 | 3.2564 | 3.2564 | 3.2564 | 3.2564
|  |  | Annualised cost (capex+opex) | 0 | 0 | 3.2564 | 3.8518 | 3.8518 | 3.8518 | 3.8518 | 3.8518 | 3.8518 | 3.8518 | 3.8518 | 3.8518 | 3.8518 | 3.8518 | 3.8518 | 3.8518 | 3.8518 | 3.8518 | 3.8518 | 3.8518 | 3.8518 | 3.8518 | 3.8518 | 3.8518 | 3.8518 | 3.8518 | 3.8518 | 3.8518 | 3.8518 | 3.8518
|  |  | Optimal timing (interim calc) | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  |  | Optimal timing | - | - | - | Yes | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
[11 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19
Adjusted For Optimal Timing: | 53.4373 | 59.5447 | Capex | 0 | 0 | 59.5447 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 7.3811 | 16.0771 | Opex | 0 | 0 | 0 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545
| 8074.6727 | 21528.7356 | Reduction in unserved energy | 0 | 0 | 0 | 44.0697 | 79.6548 | 222.6057 | 260.9788 | 301.4863 | 351.2443 | 404.1007 | 472.9258 | 618.4767 | 605.2142 | 839.3333 | 1083.0403 | 1083.0403 | 1083.0403 | 1083.0403 | 1083.0403 | 1083.0403 | 1083.0403 | 1083.0403 | 1083.0403 | 1083.0403 | 1083.0403 | 1083.0403 | 1083.0403 | 1083.0403 | 1083.0403 | 1083.0403
| 8013.8543 | 21453.1139 | Net benefit | 0 | 0 | -59.5447 | 43.4743 | 79.0593 | 222.0103 | 260.3833 | 300.8909 | 350.6489 | 403.5052 | 472.3304 | 617.8812 | 604.6187 | 838.7379 | 1082.4449 | 1082.4449 | 1082.4449 | 1082.4449 | 1082.4449 | 1082.4449 | 1082.4449 | 1082.4449 | 1082.4449 | 1082.4449 | 1082.4449 | 1082.4449 | 1082.4449 | 1082.4449 | 1082.4449 | 1082.4449
Option 5
Determining Optimal Timing: | Discounted | Undiscounted
| 49.9911 | 55.7046 | Capex | 0 | 0 | 55.7046 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 6.9051 | 15.0402 | Opex | 0 | 0 | 0 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705
| 13572.3606 | 32353.8028 | Reduction in unserved energy | 0 | 0 | 0 | 442.3526 | 523.9102 | 726.1405 | 902.4465 | 973.3322 | 1044.2403 | 1066.1893 | 1090.3048 | 1153.643 | 1067.9954 | 1225.6043 | 1383.6027 | 1383.6027 | 1383.6027 | 1383.6027 | 1383.6027 | 1383.6027 | 1383.6027 | 1383.6027 | 1383.6027 | 1383.6027 | 1383.6027 | 1383.6027 | 1383.6027 | 1383.6027 | 1383.6027 | 1383.6027
| 13515.4644 | 32283.058 | Net benefit | 0 | 0 | -55.7046 | 441.7956 | 523.3532 | 725.5835 | 901.8894 | 972.7752 | 1043.6833 | 1065.6322 | 1089.7477 | 1153.0859 | 1067.4384 | 1225.0473 | 1383.0457 | 1383.0457 | 1383.0457 | 1383.0457 | 1383.0457 | 1383.0457 | 1383.0457 | 1383.0457 | 1383.0457 | 1383.0457 | 1383.0457 | 1383.0457 | 1383.0457 | 1383.0457 | 1383.0457 | 1383.0457
|  |  | EUE Value ($m, real $2024) | 3.7784 | 148.6333 | 447.8825 | 77.3131 | 126.8953 | 38.0112 | 61.2894 | 87.082 | 121.1674 | 160.6513 | 207.758 | 301.9123 | 303.3093 | 436.8788 | 570.9611 | 570.9611 | 570.9611 | 570.9611 | 570.9611 | 570.9611 | 570.9611 | 570.9611 | 570.9611 | 570.9611 | 570.9611 | 570.9611 | 570.9611 | 570.9611 | 570.9611 | 570.9611
|  |  | Annualised capex | 0 | 0 | 3.0464 | 3.0464 | 3.0464 | 3.0464 | 3.0464 | 3.0464 | 3.0464 | 3.0464 | 3.0464 | 3.0464 | 3.0464 | 3.0464 | 3.0464 | 3.0464 | 3.0464 | 3.0464 | 3.0464 | 3.0464 | 3.0464 | 3.0464 | 3.0464 | 3.0464 | 3.0464 | 3.0464 | 3.0464 | 3.0464 | 3.0464 | 3.0464
|  |  | Annualised cost (capex+opex) | 0 | 0 | 3.0464 | 3.6034 | 3.6034 | 3.6034 | 3.6034 | 3.6034 | 3.6034 | 3.6034 | 3.6034 | 3.6034 | 3.6034 | 3.6034 | 3.6034 | 3.6034 | 3.6034 | 3.6034 | 3.6034 | 3.6034 | 3.6034 | 3.6034 | 3.6034 | 3.6034 | 3.6034 | 3.6034 | 3.6034 | 3.6034 | 3.6034 | 3.6034
|  |  | Optimal timing (interim calc) | 0 | 0 | 0 | 1 | 1 | 1 | 1 | [19 empty] | 1 | 1 | 1 | 1 | bar: 1 to 19
|  |  | Optimal timing | - | - | - | Yes | - | - | - | [19 empty] | - | - | - | - | bar: 1 to 19
Adjusted For Optimal Timing: | 49.9911 | 55.7046 | Capex | 0 | 0 | 55.7046 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 6.9051 | 15.0402 | Opex | 0 | 0 | 0 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705
| 13572.3606 | 32353.8028 | Reduction in unserved energy | 0 | 0 | 0 | 442.3526 | 523.9102 | 726.1405 | 902.4465 | 973.3322 | 1044.2403 | 1066.1893 | 1090.3048 | 1153.643 | 1067.9954 | 1225.6043 | 1383.6027 | 1383.6027 | 1383.6027 | 1383.6027 | 1383.6027 | 1383.6027 | 1383.6027 | 1383.6027 | 1383.6027 | 1383.6027 | 1383.6027 | 1383.6027 | 1383.6027 | 1383.6027 | 1383.6027 | 1383.6027
| 13515.4644 | 32283.058 | Net benefit | 0 | 0 | -55.7046 | 441.7956 | 523.3532 | 725.5835 | 901.8894 | 972.7752 | 1043.6833 | 1065.6322 | 1089.7477 | 1153.0859 | 1067.4384 | 1225.0473 | 1383.0457 | 1383.0457 | 1383.0457 | 1383.0457 | 1383.0457 | 1383.0457 | 1383.0457 | 1383.0457 | 1383.0457 | 1383.0457 | 1383.0457 | 1383.0457 | 1383.0457 | 1383.0457 | 1383.0457 | 1383.0457
Option 6
Determining Optimal Timing: | Discounted | Undiscounted
| 61.1918 | 68.1854 | Capex | 0 | 0 | 68.1854 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 8.4522 | 18.4101 | Opex | 0 | 0 | 0 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185
| 16314.0822 | 39690.8492 | Reduction in unserved energy | 0 | 0 | 0 | 449.6716 | 641.0551 | 752.5421 | 947.1347 | 1039.5999 | 1137.8897 | 1191.5984 | 1252.2642 | 1383.4065 | 1305.6882 | 1537.3546 | 1753.2903 | 1753.2903 | 1753.2903 | 1753.2903 | 1753.2903 | 1753.2903 | 1753.2903 | 1753.2903 | 1753.2903 | 1753.2903 | 1753.2903 | 1753.2903 | 1753.2903 | 1753.2903 | 1753.2903 | 1753.2903
| 16244.4383 | 39604.2537 | Net benefit | 0 | 0 | -68.1854 | 448.9898 | 640.3732 | 751.8603 | 946.4528 | 1038.9181 | 1137.2078 | 1190.9165 | 1251.5823 | 1382.7247 | 1305.0064 | 1536.6727 | 1752.6084 | 1752.6084 | 1752.6084 | 1752.6084 | 1752.6084 | 1752.6084 | 1752.6084 | 1752.6084 | 1752.6084 | 1752.6084 | 1752.6084 | 1752.6084 | 1752.6084 | 1752.6084 | 1752.6084 | 1752.6084
|  |  | EUE Value ($m, real $2024) | 3.7784 | 148.6333 | 447.8825 | 69.9941 | 9.7504 | 11.6096 | 16.6012 | 20.8143 | 27.518 | 35.2423 | 45.7986 | 72.1488 | 65.6165 | 125.1286 | 201.2736 | 201.2736 | 201.2736 | 201.2736 | 201.2736 | 201.2736 | 201.2736 | 201.2736 | 201.2736 | 201.2736 | 201.2736 | 201.2736 | 201.2736 | 201.2736 | 201.2736 | 201.2736
|  |  | Annualised capex | 0 | 0 | 3.7289 | 3.7289 | 3.7289 | 3.7289 | 3.7289 | 3.7289 | 3.7289 | 3.7289 | 3.7289 | 3.7289 | 3.7289 | 3.7289 | 3.7289 | 3.7289 | 3.7289 | 3.7289 | 3.7289 | 3.7289 | 3.7289 | 3.7289 | 3.7289 | 3.7289 | 3.7289 | 3.7289 | 3.7289 | 3.7289 | 3.7289 | 3.7289
|  |  | Annualised cost (capex+opex) | 0 | 0 | 3.7289 | 4.4108 | 4.4108 | 4.4108 | 4.4108 | 4.4108 | 4.4108 | 4.4108 | 4.4108 | 4.4108 | 4.4108 | 4.4108 | 4.4108 | 4.4108 | 4.4108 | 4.4108 | 4.4108 | 4.4108 | 4.4108 | 4.4108 | 4.4108 | 4.4108 | 4.4108 | 4.4108 | 4.4108 | 4.4108 | 4.4108 | 4.4108
|  |  | Optimal timing (interim calc) | 0 | 0 | 0 | 1 | 1 | 1 | 1 | [19 empty] | 1 | 1 | 1 | 1 | bar: 1 to 19
|  |  | Optimal timing | - | - | - | Yes | - | - | - | [19 empty] | - | - | - | - | bar: 1 to 19
Adjusted For Optimal Timing: | 61.1918 | 68.1854 | Capex | 0 | 0 | 68.1854 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 8.4522 | 18.4101 | Opex | 0 | 0 | 0 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185
| 16314.0822 | 39690.8492 | Reduction in unserved energy | 0 | 0 | 0 | 449.6716 | 641.0551 | 752.5421 | 947.1347 | 1039.5999 | 1137.8897 | 1191.5984 | 1252.2642 | 1383.4065 | 1305.6882 | 1537.3546 | 1753.2903 | 1753.2903 | 1753.2903 | 1753.2903 | 1753.2903 | 1753.2903 | 1753.2903 | 1753.2903 | 1753.2903 | 1753.2903 | 1753.2903 | 1753.2903 | 1753.2903 | 1753.2903 | 1753.2903 | 1753.2903
| 16244.4383 | 39604.2537 | Net benefit | 0 | 0 | -68.1854 | 448.9898 | 640.3732 | 751.8603 | 946.4528 | 1038.9181 | 1137.2078 | 1190.9165 | 1251.5823 | 1382.7247 | 1305.0064 | 1536.6727 | 1752.6084 | 1752.6084 | 1752.6084 | 1752.6084 | 1752.6084 | 1752.6084 | 1752.6084 | 1752.6084 | 1752.6084 | 1752.6084 | 1752.6084 | 1752.6084 | 1752.6084 | 1752.6084 | 1752.6084 | 1752.6084
Option 7
Determining Optimal Timing: | Discounted | Undiscounted
| 33.225 | 37.0224 | Capex | 0 | 0 | 37.0224 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 4.5893 | 9.996 | Opex | 0 | 0 | 0 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022
| 13092.5648 | 30876.4258 | Reduction in unserved energy | 0 | 0 | 0 | 435.4387 | 616.134 | 716.6311 | 891.8641 | 961.597 | 1031.2858 | 1051.9704 | 1073.6173 | 1129.9788 | 1041.0131 | 1176.9856 | 1296.8694 | 1296.8694 | 1296.8694 | 1296.8694 | 1296.8694 | 1296.8694 | 1296.8694 | 1296.8694 | 1296.8694 | 1296.8694 | 1296.8694 | 1296.8694 | 1296.8694 | 1296.8694 | 1296.8694 | 1296.8694
| 13054.7505 | 30829.4074 | Net benefit | 0 | 0 | -37.0224 | 435.0685 | 615.7638 | 716.2608 | 891.4939 | 961.2267 | 1030.9156 | 1051.6001 | 1073.2471 | 1129.6085 | 1040.6428 | 1176.6154 | 1296.4992 | 1296.4992 | 1296.4992 | 1296.4992 | 1296.4992 | 1296.4992 | 1296.4992 | 1296.4992 | 1296.4992 | 1296.4992 | 1296.4992 | 1296.4992 | 1296.4992 | 1296.4992 | 1296.4992 | 1296.4992
|  |  | EUE Value ($m, real $2024) | 3.7784 | 148.6333 | 447.8825 | 84.227 | 34.6715 | 47.5206 | 71.8718 | 98.8172 | 134.1218 | 174.8703 | 224.4455 | 325.5765 | 330.2916 | 485.4976 | 657.6945 | 657.6945 | 657.6945 | 657.6945 | 657.6945 | 657.6945 | 657.6945 | 657.6945 | 657.6945 | 657.6945 | 657.6945 | 657.6945 | 657.6945 | 657.6945 | 657.6945 | 657.6945
|  |  | Annualised capex | 0 | 0 | 2.0247 | 2.0247 | 2.0247 | 2.0247 | 2.0247 | 2.0247 | 2.0247 | 2.0247 | 2.0247 | 2.0247 | 2.0247 | 2.0247 | 2.0247 | 2.0247 | 2.0247 | 2.0247 | 2.0247 | 2.0247 | 2.0247 | 2.0247 | 2.0247 | 2.0247 | 2.0247 | 2.0247 | 2.0247 | 2.0247 | 2.0247 | 2.0247
|  |  | Annualised cost (capex+opex) | 0 | 0 | 2.0247 | 2.3949 | 2.3949 | 2.3949 | 2.3949 | 2.3949 | 2.3949 | 2.3949 | 2.3949 | 2.3949 | 2.3949 | 2.3949 | 2.3949 | 2.3949 | 2.3949 | 2.3949 | 2.3949 | 2.3949 | 2.3949 | 2.3949 | 2.3949 | 2.3949 | 2.3949 | 2.3949 | 2.3949 | 2.3949 | 2.3949 | 2.3949
|  |  | Optimal timing (interim calc) | 0 | 0 | 0 | 1 | 1 | 1 | 1 | [19 empty] | 1 | 1 | 1 | 1 | bar: 1 to 19
|  |  | Optimal timing | - | - | - | Yes | - | - | - | [19 empty] | - | - | - | - | bar: 1 to 19
Adjusted For Optimal Timing: | 33.225 | 37.0224 | Capex | 0 | 0 | 37.0224 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 4.5893 | 9.996 | Opex | 0 | 0 | 0 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022
| 13092.5648 | 30876.4258 | Reduction in unserved energy | 0 | 0 | 0 | 435.4387 | 616.134 | 716.6311 | 891.8641 | 961.597 | 1031.2858 | 1051.9704 | 1073.6173 | 1129.9788 | 1041.0131 | 1176.9856 | 1296.8694 | 1296.8694 | 1296.8694 | 1296.8694 | 1296.8694 | 1296.8694 | 1296.8694 | 1296.8694 | 1296.8694 | 1296.8694 | 1296.8694 | 1296.8694 | 1296.8694 | 1296.8694 | 1296.8694 | 1296.8694
| 13054.7505 | 30829.4074 | Net benefit | 0 | 0 | -37.0224 | 435.0685 | 615.7638 | 716.2608 | 891.4939 | 961.2267 | 1030.9156 | 1051.6001 | 1073.2471 | 1129.6085 | 1040.6428 | 1176.6154 | 1296.4992 | 1296.4992 | 1296.4992 | 1296.4992 | 1296.4992 | 1296.4992 | 1296.4992 | 1296.4992 | 1296.4992 | 1296.4992 | 1296.4992 | 1296.4992 | 1296.4992 | 1296.4992 | 1296.4992 | 1296.4992
Option 8
Determining Optimal Timing: | Discounted | Undiscounted
| 47.6017 | 53.0422 | Capex | 0 | 0 | 53.0422 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 6.5751 | 14.3214 | Opex | 0 | 0 | 0 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042
| 7646.6019 | 20121.6258 | Reduction in unserved energy | 0 | 0 | 0 | 43.2409 | 178.0134 | 220.1904 | 258.3528 | 298.5522 | 347.538 | 399.4615 | 466.206 | 603.6536 | 587.6486 | 796.9837 | 995.1115 | 995.1115 | 995.1115 | 995.1115 | 995.1115 | 995.1115 | 995.1115 | 995.1115 | 995.1115 | 995.1115 | 995.1115 | 995.1115 | 995.1115 | 995.1115 | 995.1115 | 995.1115
| 7592.425 | 20054.2622 | Net benefit | 0 | 0 | -53.0422 | 42.7105 | 177.483 | 219.66 | 257.8223 | 298.0218 | 347.0076 | 398.9311 | 465.6756 | 603.1232 | 587.1182 | 796.4532 | 994.5811 | 994.5811 | 994.5811 | 994.5811 | 994.5811 | 994.5811 | 994.5811 | 994.5811 | 994.5811 | 994.5811 | 994.5811 | 994.5811 | 994.5811 | 994.5811 | 994.5811 | 994.5811
|  |  | EUE Value ($m, real $2024) | 3.7784 | 148.6333 | 447.8825 | 476.4249 | 472.792 | 543.9613 | 705.3831 | 761.862 | 817.8697 | 827.3791 | 831.8568 | 851.9017 | 783.6561 | 865.4995 | 959.4523 | 959.4523 | 959.4523 | 959.4523 | 959.4523 | 959.4523 | 959.4523 | 959.4523 | 959.4523 | 959.4523 | 959.4523 | 959.4523 | 959.4523 | 959.4523 | 959.4523 | 959.4523
|  |  | Annualised capex | 0 | 0 | 2.9008 | 2.9008 | 2.9008 | 2.9008 | 2.9008 | 2.9008 | 2.9008 | 2.9008 | 2.9008 | 2.9008 | 2.9008 | 2.9008 | 2.9008 | 2.9008 | 2.9008 | 2.9008 | 2.9008 | 2.9008 | 2.9008 | 2.9008 | 2.9008 | 2.9008 | 2.9008 | 2.9008 | 2.9008 | 2.9008 | 2.9008 | 2.9008
|  |  | Annualised cost (capex+opex) | 0 | 0 | 2.9008 | 3.4312 | 3.4312 | 3.4312 | 3.4312 | 3.4312 | 3.4312 | 3.4312 | 3.4312 | 3.4312 | 3.4312 | 3.4312 | 3.4312 | 3.4312 | 3.4312 | 3.4312 | 3.4312 | 3.4312 | 3.4312 | 3.4312 | 3.4312 | 3.4312 | 3.4312 | 3.4312 | 3.4312 | 3.4312 | 3.4312 | 3.4312
|  |  | Optimal timing (interim calc) | 0 | 0 | 0 | 1 | 1 | 1 | 1 | [19 empty] | 1 | 1 | 1 | 1 | bar: 1 to 19
|  |  | Optimal timing | - | - | - | Yes | - | - | - | [19 empty] | - | - | - | - | bar: 1 to 19
Adjusted For Optimal Timing: | 47.6017 | 53.0422 | Capex | 0 | 0 | 53.0422 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 6.5751 | 14.3214 | Opex | 0 | 0 | 0 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042
| 7646.6019 | 20121.6258 | Reduction in unserved energy | 0 | 0 | 0 | 43.2409 | 178.0134 | 220.1904 | 258.3528 | 298.5522 | 347.538 | 399.4615 | 466.206 | 603.6536 | 587.6486 | 796.9837 | 995.1115 | 995.1115 | 995.1115 | 995.1115 | 995.1115 | 995.1115 | 995.1115 | 995.1115 | 995.1115 | 995.1115 | 995.1115 | 995.1115 | 995.1115 | 995.1115 | 995.1115 | 995.1115
| 7592.425 | 20054.2622 | Net benefit | 0 | 0 | -53.0422 | 42.7105 | 177.483 | 219.66 | 257.8223 | 298.0218 | 347.0076 | 398.9311 | 465.6756 | 603.1232 | 587.1182 | 796.4532 | 994.5811 | 994.5811 | 994.5811 | 994.5811 | 994.5811 | 994.5811 | 994.5811 | 994.5811 | 994.5811 | 994.5811 | 994.5811 | 994.5811 | 994.5811 | 994.5811 | 994.5811 | 994.5811
Option 9
Determining Optimal Timing: | Discounted | Undiscounted
| 44.1555 | 49.2021 | Capex | 0 | 0 | 49.2021 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 6.0991 | 13.2846 | Opex | 0 | 0 | 0 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202
| 13276.6125 | 31325.4929 | Reduction in unserved energy | 0 | 0 | 0 | 441.3006 | 622.5892 | 723.7669 | 902.0066 | 973.2302 | 1044.2198 | 1065.5562 | 1088.1089 | 1147.5272 | 1055.2797 | 1193.5772 | 1316.7706 | 1316.7706 | 1316.7706 | 1316.7706 | 1316.7706 | 1316.7706 | 1316.7706 | 1316.7706 | 1316.7706 | 1316.7706 | 1316.7706 | 1316.7706 | 1316.7706 | 1316.7706 | 1316.7706 | 1316.7706
| 13226.3579 | 31263.0062 | Net benefit | 0 | 0 | -49.2021 | 440.8086 | 622.0972 | 723.2749 | 901.5146 | 972.7382 | 1043.7278 | 1065.0642 | 1087.6169 | 1147.0351 | 1054.7877 | 1193.0852 | 1316.2786 | 1316.2786 | 1316.2786 | 1316.2786 | 1316.2786 | 1316.2786 | 1316.2786 | 1316.2786 | 1316.2786 | 1316.2786 | 1316.2786 | 1316.2786 | 1316.2786 | 1316.2786 | 1316.2786 | 1316.2786
|  |  | EUE Value ($m, real $2024) | 3.7784 | 148.6333 | 447.8825 | 78.3652 | 28.2163 | 40.3847 | 61.7293 | 87.184 | 121.1879 | 161.2844 | 209.9539 | 308.0281 | 316.025 | 468.9059 | 637.7932 | 637.7932 | 637.7932 | 637.7932 | 637.7932 | 637.7932 | 637.7932 | 637.7932 | 637.7932 | 637.7932 | 637.7932 | 637.7932 | 637.7932 | 637.7932 | 637.7932 | 637.7932
|  |  | Annualised capex | 0 | 0 | 2.6908 | 2.6908 | 2.6908 | 2.6908 | 2.6908 | 2.6908 | 2.6908 | 2.6908 | 2.6908 | 2.6908 | 2.6908 | 2.6908 | 2.6908 | 2.6908 | 2.6908 | 2.6908 | 2.6908 | 2.6908 | 2.6908 | 2.6908 | 2.6908 | 2.6908 | 2.6908 | 2.6908 | 2.6908 | 2.6908 | 2.6908 | 2.6908
|  |  | Annualised cost (capex+opex) | 0 | 0 | 2.6908 | 3.1828 | 3.1828 | 3.1828 | 3.1828 | 3.1828 | 3.1828 | 3.1828 | 3.1828 | 3.1828 | 3.1828 | 3.1828 | 3.1828 | 3.1828 | 3.1828 | 3.1828 | 3.1828 | 3.1828 | 3.1828 | 3.1828 | 3.1828 | 3.1828 | 3.1828 | 3.1828 | 3.1828 | 3.1828 | 3.1828 | 3.1828
|  |  | Optimal timing (interim calc) | 0 | 0 | 0 | 1 | 1 | 1 | 1 | [19 empty] | 1 | 1 | 1 | 1 | bar: 1 to 19
|  |  | Optimal timing | - | - | - | Yes | - | - | - | [19 empty] | - | - | - | - | bar: 1 to 19
Adjusted For Optimal Timing: | 44.1555 | 49.2021 | Capex | 0 | 0 | 49.2021 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 6.0991 | 13.2846 | Opex | 0 | 0 | 0 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202
| 13276.6125 | 31325.4929 | Reduction in unserved energy | 0 | 0 | 0 | 441.3006 | 622.5892 | 723.7669 | 902.0066 | 973.2302 | 1044.2198 | 1065.5562 | 1088.1089 | 1147.5272 | 1055.2797 | 1193.5772 | 1316.7706 | 1316.7706 | 1316.7706 | 1316.7706 | 1316.7706 | 1316.7706 | 1316.7706 | 1316.7706 | 1316.7706 | 1316.7706 | 1316.7706 | 1316.7706 | 1316.7706 | 1316.7706 | 1316.7706 | 1316.7706
| 13226.3579 | 31263.0062 | Net benefit | 0 | 0 | -49.2021 | 440.8086 | 622.0972 | 723.2749 | 901.5146 | 972.7382 | 1043.7278 | 1065.0642 | 1087.6169 | 1147.0351 | 1054.7877 | 1193.0852 | 1316.2786 | 1316.2786 | 1316.2786 | 1316.2786 | 1316.2786 | 1316.2786 | 1316.2786 | 1316.2786 | 1316.2786 | 1316.2786 | 1316.2786 | 1316.2786 | 1316.2786 | 1316.2786 | 1316.2786 | 1316.2786
Option 10
Determining Optimal Timing: | Discounted | Undiscounted
| 0 | 0 | Capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 6375.8942 | 15208.189 | Opex | 0.48285 | 57.8283 | 189.4866 | 207.6844 | 245.4848 | 279.2209 | 339.624 | 384.4625 | 426.7802 | 445.1879 | 469.6214 | 502.6026 | 486.2654 | 573.3683 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055
| 9382.3494 | 22274.4191 | Reduction in unserved energy | 0.59863 | 117.8161 | 291.8403 | 327.7587 | 383.8622 | 422.6887 | 493.1752 | 551.8803 | 605.6373 | 634.3685 | 678.0256 | 738.3591 | 726.4119 | 847.6575 | 965.8962 | 965.8962 | 965.8962 | 965.8962 | 965.8962 | 965.8962 | 965.8962 | 965.8962 | 965.8962 | 965.8962 | 965.8962 | 965.8962 | 965.8962 | 965.8962 | 965.8962 | 965.8962
| 3006.4552 | 7066.2301 | Net benefit | 0.11578 | 59.9877 | 102.3537 | 120.0743 | 138.3774 | 143.4678 | 153.5512 | 167.4178 | 178.8571 | 189.1806 | 208.4042 | 235.7564 | 240.1465 | 274.2892 | 303.3907 | 303.3907 | 303.3907 | 303.3907 | 303.3907 | 303.3907 | 303.3907 | 303.3907 | 303.3907 | 303.3907 | 303.3907 | 303.3907 | 303.3907 | 303.3907 | 303.3907 | 303.3907
|  |  | EUE Value ($m, real $2024) | 3.1866 | 30.8172 | 156.0422 | 191.907 | 266.9433 | 341.463 | 470.5607 | 508.5339 | 559.7704 | 592.4721 | 620.0372 | 717.1962 | 644.8928 | 814.8256 | 988.6676 | 988.6676 | 988.6676 | 988.6676 | 988.6676 | 988.6676 | 988.6676 | 988.6676 | 988.6676 | 988.6676 | 988.6676 | 988.6676 | 988.6676 | 988.6676 | 988.6676 | 988.6676
|  |  | Annualised capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Annualised cost (capex+opex) | 0.48285 | 57.8283 | 189.4866 | 207.6844 | 245.4848 | 279.2209 | 339.624 | 384.4625 | 426.7802 | 445.1879 | 469.6214 | 502.6026 | 486.2654 | 573.3683 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055
|  |  | Optimal timing (interim calc) | 1 | 1 | 1 | 1 | 1 | 1 | 1 | [19 empty] | 1 | 1 | 1 | 1 | bar: 1 to 19
|  |  | Optimal timing | Yes | - | - | - | - | - | - | [19 empty] | - | - | - | - | bar: 1 to 19
Adjusted For Optimal Timing: | 0 | 0 | Capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 6375.8942 | 15208.189 | Opex | 0.48285 | 57.8283 | 189.4866 | 207.6844 | 245.4848 | 279.2209 | 339.624 | 384.4625 | 426.7802 | 445.1879 | 469.6214 | 502.6026 | 486.2654 | 573.3683 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055
| 9382.3494 | 22274.4191 | Reduction in unserved energy | 0.59863 | 117.8161 | 291.8403 | 327.7587 | 383.8622 | 422.6887 | 493.1752 | 551.8803 | 605.6373 | 634.3685 | 678.0256 | 738.3591 | 726.4119 | 847.6575 | 965.8962 | 965.8962 | 965.8962 | 965.8962 | 965.8962 | 965.8962 | 965.8962 | 965.8962 | 965.8962 | 965.8962 | 965.8962 | 965.8962 | 965.8962 | 965.8962 | 965.8962 | 965.8962
| 3006.4552 | 7066.2301 | Net benefit | 0.11578 | 59.9877 | 102.3537 | 120.0743 | 138.3774 | 143.4678 | 153.5512 | 167.4178 | 178.8571 | 189.1806 | 208.4042 | 235.7564 | 240.1465 | 274.2892 | 303.3907 | 303.3907 | 303.3907 | 303.3907 | 303.3907 | 303.3907 | 303.3907 | 303.3907 | 303.3907 | 303.3907 | 303.3907 | 303.3907 | 303.3907 | 303.3907 | 303.3907 | 303.3907

## 3.2.7 NPV (Low VCR)
Economic inputs and assumptions
Scenario | Discount rate | Central
| Cost | Central
| VCR | Lower bound
|  | Central | Lower bound | Upper bound
| Discount rate | 5.56% | 4.11% | 7%
| Cost | 100% | 80% | 120%
| VCR | 100% | 80% | 120%
Asset life for calculating annualised capex (years) | Option 1 | 45
| Option 2 | 45
| Option 3 | 45
| Option 4 | 45
| Option 5 | 45
| Option 6 | 45
| Option 7 | 45
| Option 8 | 45
| Option 9 | 45
| Option 10 | 45
|  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30
|  |  |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Outputs | bar: 3 FY27; 7 FY31
Option 1
| Discounted | Undiscounted
| 0 | 0 | Capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Opex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Reduction in unserved energy | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Net benefit | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | EUE Value ($m, real $2024) | 2.6507 | 52.3433 | 197.7057 | 226.4651 | 289.6023 | 351.2839 | 465.0457 | 511.6418 | 562.2196 | 587.1705 | 613.8736 | 683.9122 | 625.8035 | 764.1367 | 911.0819 | 911.0819 | 911.0819 | 911.0819 | 911.0819 | 911.0819 | 911.0819 | 911.0819 | 911.0819 | 911.0819 | 911.0819 | 911.0819 | 911.0819 | 911.0819 | 911.0819 | 911.0819
Option 2
Determining Optimal Timing: | Discounted | Undiscounted
| 64.7091 | 72.1048 | Capex | 0 | 0 | 72.1048 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 8.9381 | 19.4683 | Opex | 0 | 0 | 0 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105
| 7987.9344 | 19672.8166 | Reduction in unserved energy | 0 | 0 | 0 | 196.3942 | 238.6559 | 345.7232 | 458.6379 | 504.3086 | 553.72 | 577.4819 | 602.683 | 670.1874 | 611.8879 | 743.7011 | 885.5897 | 885.5897 | 885.5897 | 885.5897 | 885.5897 | 885.5897 | 885.5897 | 885.5897 | 885.5897 | 885.5897 | 885.5897 | 885.5897 | 885.5897 | 885.5897 | 885.5897 | 885.5897
| 7914.2872 | 19581.2435 | Net benefit | 0 | 0 | -72.1048 | 195.6732 | 237.9349 | 345.0021 | 457.9169 | 503.5875 | 552.9989 | 576.7609 | 601.9619 | 669.4663 | 611.1668 | 742.9801 | 884.8687 | 884.8687 | 884.8687 | 884.8687 | 884.8687 | 884.8687 | 884.8687 | 884.8687 | 884.8687 | 884.8687 | 884.8687 | 884.8687 | 884.8687 | 884.8687 | 884.8687 | 884.8687
|  |  | EUE Value ($m, real $2024) | 2.6458 | 52.3433 | 197.7057 | 30.0709 | 50.9464 | 5.5607 | 6.4078 | 7.3332 | 8.4996 | 9.6886 | 11.1906 | 13.7249 | 13.9157 | 20.4356 | 25.4921 | 25.4921 | 25.4921 | 25.4921 | 25.4921 | 25.4921 | 25.4921 | 25.4921 | 25.4921 | 25.4921 | 25.4921 | 25.4921 | 25.4921 | 25.4921 | 25.4921 | 25.4921
|  |  | Annualised capex | 0 | 0 | 3.9433 | 3.9433 | 3.9433 | 3.9433 | 3.9433 | 3.9433 | 3.9433 | 3.9433 | 3.9433 | 3.9433 | 3.9433 | 3.9433 | 3.9433 | 3.9433 | 3.9433 | 3.9433 | 3.9433 | 3.9433 | 3.9433 | 3.9433 | 3.9433 | 3.9433 | 3.9433 | 3.9433 | 3.9433 | 3.9433 | 3.9433 | 3.9433
|  |  | Annualised cost (capex+opex) | 0 | 0 | 3.9433 | 4.6643 | 4.6643 | 4.6643 | 4.6643 | 4.6643 | 4.6643 | 4.6643 | 4.6643 | 4.6643 | 4.6643 | 4.6643 | 4.6643 | 4.6643 | 4.6643 | 4.6643 | 4.6643 | 4.6643 | 4.6643 | 4.6643 | 4.6643 | 4.6643 | 4.6643 | 4.6643 | 4.6643 | 4.6643 | 4.6643 | 4.6643
|  |  | Optimal timing (interim calc) | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  |  | Optimal timing | - | - | - | Yes | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Adjusted For Optimal Timing: | 64.7091 | 72.1048 | Capex | 0 | 0 | 72.1048 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 8.9381 | 19.4683 | Opex | 0 | 0 | 0 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105
| 7987.9344 | 19672.8166 | Reduction in unserved energy | 0 | 0 | 0 | 196.3942 | 238.6559 | 345.7232 | 458.6379 | 504.3086 | 553.72 | 577.4819 | 602.683 | 670.1874 | 611.8879 | 743.7011 | 885.5897 | 885.5897 | 885.5897 | 885.5897 | 885.5897 | 885.5897 | 885.5897 | 885.5897 | 885.5897 | 885.5897 | 885.5897 | 885.5897 | 885.5897 | 885.5897 | 885.5897 | 885.5897
| 7914.2872 | 19581.2435 | Net benefit | 0 | 0 | -72.1048 | 195.6732 | 237.9349 | 345.0021 | 457.9169 | 503.5875 | 552.9989 | 576.7609 | 601.9619 | 669.4663 | 611.1668 | 742.9801 | 884.8687 | 884.8687 | 884.8687 | 884.8687 | 884.8687 | 884.8687 | 884.8687 | 884.8687 | 884.8687 | 884.8687 | 884.8687 | 884.8687 | 884.8687 | 884.8687 | 884.8687 | 884.8687
Option 3
Determining Optimal Timing: | Discounted | Undiscounted
| 39.0606 | 43.5248 | Capex | 0 | 0 | 43.5248 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 5.3953 | 11.7517 | Opex | 0 | 0 | 0 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525
| 6587.2985 | 15727.0209 | Reduction in unserved energy | 0 | 0 | 0 | 195.0017 | 235.4097 | 338.9268 | 445.602 | 482.969 | 520.5198 | 529.5818 | 538.0431 | 570.8406 | 512.1621 | 590.2336 | 672.9832 | 672.9832 | 672.9832 | 672.9832 | 672.9832 | 672.9832 | 672.9832 | 672.9832 | 672.9832 | 672.9832 | 672.9832 | 672.9832 | 672.9832 | 672.9832 | 672.9832 | 672.9832
| 6542.8426 | 15671.7443 | Net benefit | 0 | 0 | -43.5248 | 194.5665 | 234.9744 | 338.4915 | 445.1667 | 482.5338 | 520.0846 | 529.1466 | 537.6078 | 570.4053 | 511.7268 | 589.7983 | 672.5479 | 672.5479 | 672.5479 | 672.5479 | 672.5479 | 672.5479 | 672.5479 | 672.5479 | 672.5479 | 672.5479 | 672.5479 | 672.5479 | 672.5479 | 672.5479 | 672.5479 | 672.5479
|  |  | EUE Value ($m, real $2024) | 2.6458 | 52.3433 | 197.7057 | 31.4634 | 54.1927 | 12.3571 | 19.4437 | 28.6727 | 41.6997 | 57.5887 | 75.8305 | 113.0717 | 113.6414 | 173.9032 | 238.0987 | 238.0987 | 238.0987 | 238.0987 | 238.0987 | 238.0987 | 238.0987 | 238.0987 | 238.0987 | 238.0987 | 238.0987 | 238.0987 | 238.0987 | 238.0987 | 238.0987 | 238.0987
|  |  | Annualised capex | 0 | 0 | 2.3803 | 2.3803 | 2.3803 | 2.3803 | 2.3803 | 2.3803 | 2.3803 | 2.3803 | 2.3803 | 2.3803 | 2.3803 | 2.3803 | 2.3803 | 2.3803 | 2.3803 | 2.3803 | 2.3803 | 2.3803 | 2.3803 | 2.3803 | 2.3803 | 2.3803 | 2.3803 | 2.3803 | 2.3803 | 2.3803 | 2.3803 | 2.3803
|  |  | Annualised cost (capex+opex) | 0 | 0 | 2.3803 | 2.8155 | 2.8155 | 2.8155 | 2.8155 | 2.8155 | 2.8155 | 2.8155 | 2.8155 | 2.8155 | 2.8155 | 2.8155 | 2.8155 | 2.8155 | 2.8155 | 2.8155 | 2.8155 | 2.8155 | 2.8155 | 2.8155 | 2.8155 | 2.8155 | 2.8155 | 2.8155 | 2.8155 | 2.8155 | 2.8155 | 2.8155
|  |  | Optimal timing (interim calc) | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  |  | Optimal timing | - | - | - | Yes | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Adjusted For Optimal Timing: | 39.0606 | 43.5248 | Capex | 0 | 0 | 43.5248 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 5.3953 | 11.7517 | Opex | 0 | 0 | 0 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525
| 6587.2985 | 15727.0209 | Reduction in unserved energy | 0 | 0 | 0 | 195.0017 | 235.4097 | 338.9268 | 445.602 | 482.969 | 520.5198 | 529.5818 | 538.0431 | 570.8406 | 512.1621 | 590.2336 | 672.9832 | 672.9832 | 672.9832 | 672.9832 | 672.9832 | 672.9832 | 672.9832 | 672.9832 | 672.9832 | 672.9832 | 672.9832 | 672.9832 | 672.9832 | 672.9832 | 672.9832 | 672.9832
| 6542.8426 | 15671.7443 | Net benefit | 0 | 0 | -43.5248 | 194.5665 | 234.9744 | 338.4915 | 445.1667 | 482.5338 | 520.0846 | 529.1466 | 537.6078 | 570.4053 | 511.7268 | 589.7983 | 672.5479 | 672.5479 | 672.5479 | 672.5479 | 672.5479 | 672.5479 | 672.5479 | 672.5479 | 672.5479 | 672.5479 | 672.5479 | 672.5479 | 672.5479 | 672.5479 | 672.5479 | 672.5479
Option 4
Determining Optimal Timing: | Discounted | Undiscounted
| 53.4373 | 59.5447 | Capex | 0 | 0 | 59.5447 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 7.3811 | 16.0771 | Opex | 0 | 0 | 0 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545
| 3192.3071 | 8646.7207 | Reduction in unserved energy | 0 | 0 | 0 | 6.1224 | 14.4625 | 78.375 | 92.9166 | 108.4515 | 127.8314 | 147.9032 | 173.2347 | 234.2573 | 222.8109 | 326.5996 | 444.6097 | 444.6097 | 444.6097 | 444.6097 | 444.6097 | 444.6097 | 444.6097 | 444.6097 | 444.6097 | 444.6097 | 444.6097 | 444.6097 | 444.6097 | 444.6097 | 444.6097 | 444.6097
| 3131.4888 | 8571.099 | Net benefit | 0 | 0 | -59.5447 | 5.5269 | 13.867 | 77.7796 | 92.3212 | 107.856 | 127.2359 | 147.3077 | 172.6392 | 233.6618 | 222.2154 | 326.0042 | 444.0143 | 444.0143 | 444.0143 | 444.0143 | 444.0143 | 444.0143 | 444.0143 | 444.0143 | 444.0143 | 444.0143 | 444.0143 | 444.0143 | 444.0143 | 444.0143 | 444.0143 | 444.0143
|  |  | EUE Value ($m, real $2024) | 2.6458 | 52.3433 | 197.7057 | 220.3427 | 275.1398 | 272.9089 | 372.1291 | 403.1903 | 434.3882 | 439.2673 | 440.6389 | 449.655 | 402.9927 | 437.5371 | 466.4721 | 466.4721 | 466.4721 | 466.4721 | 466.4721 | 466.4721 | 466.4721 | 466.4721 | 466.4721 | 466.4721 | 466.4721 | 466.4721 | 466.4721 | 466.4721 | 466.4721 | 466.4721
|  |  | Annualised capex | 0 | 0 | 3.2564 | 3.2564 | 3.2564 | 3.2564 | 3.2564 | 3.2564 | 3.2564 | 3.2564 | 3.2564 | 3.2564 | 3.2564 | 3.2564 | 3.2564 | 3.2564 | 3.2564 | 3.2564 | 3.2564 | 3.2564 | 3.2564 | 3.2564 | 3.2564 | 3.2564 | 3.2564 | 3.2564 | 3.2564 | 3.2564 | 3.2564 | 3.2564
|  |  | Annualised cost (capex+opex) | 0 | 0 | 3.2564 | 3.8518 | 3.8518 | 3.8518 | 3.8518 | 3.8518 | 3.8518 | 3.8518 | 3.8518 | 3.8518 | 3.8518 | 3.8518 | 3.8518 | 3.8518 | 3.8518 | 3.8518 | 3.8518 | 3.8518 | 3.8518 | 3.8518 | 3.8518 | 3.8518 | 3.8518 | 3.8518 | 3.8518 | 3.8518 | 3.8518 | 3.8518
|  |  | Optimal timing (interim calc) | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  |  | Optimal timing | - | - | - | Yes | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
[11 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19
Adjusted For Optimal Timing: | 53.4373 | 59.5447 | Capex | 0 | 0 | 59.5447 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 7.3811 | 16.0771 | Opex | 0 | 0 | 0 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545
| 3192.3071 | 8646.7207 | Reduction in unserved energy | 0 | 0 | 0 | 6.1224 | 14.4625 | 78.375 | 92.9166 | 108.4515 | 127.8314 | 147.9032 | 173.2347 | 234.2573 | 222.8109 | 326.5996 | 444.6097 | 444.6097 | 444.6097 | 444.6097 | 444.6097 | 444.6097 | 444.6097 | 444.6097 | 444.6097 | 444.6097 | 444.6097 | 444.6097 | 444.6097 | 444.6097 | 444.6097 | 444.6097
| 3131.4888 | 8571.099 | Net benefit | 0 | 0 | -59.5447 | 5.5269 | 13.867 | 77.7796 | 92.3212 | 107.856 | 127.2359 | 147.3077 | 172.6392 | 233.6618 | 222.2154 | 326.0042 | 444.0143 | 444.0143 | 444.0143 | 444.0143 | 444.0143 | 444.0143 | 444.0143 | 444.0143 | 444.0143 | 444.0143 | 444.0143 | 444.0143 | 444.0143 | 444.0143 | 444.0143 | 444.0143
Option 5
Determining Optimal Timing: | Discounted | Undiscounted
| 49.9911 | 55.7046 | Capex | 0 | 0 | 55.7046 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 6.9051 | 15.0402 | Opex | 0 | 0 | 0 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705
| 6692.532 | 15979.7387 | Reduction in unserved energy | 0 | 0 | 0 | 199.2675 | 240.108 | 344.1223 | 451.4018 | 489.3769 | 527.4925 | 537.149 | 546.2655 | 579.7434 | 521.6459 | 600.5204 | 683.9153 | 683.9153 | 683.9153 | 683.9153 | 683.9153 | 683.9153 | 683.9153 | 683.9153 | 683.9153 | 683.9153 | 683.9153 | 683.9153 | 683.9153 | 683.9153 | 683.9153 | 683.9153
| 6635.6359 | 15908.9938 | Net benefit | 0 | 0 | -55.7046 | 198.7105 | 239.5509 | 343.5652 | 450.8448 | 488.8199 | 526.9355 | 536.592 | 545.7084 | 579.1863 | 521.0889 | 599.9634 | 683.3583 | 683.3583 | 683.3583 | 683.3583 | 683.3583 | 683.3583 | 683.3583 | 683.3583 | 683.3583 | 683.3583 | 683.3583 | 683.3583 | 683.3583 | 683.3583 | 683.3583 | 683.3583
|  |  | EUE Value ($m, real $2024) | 2.6458 | 52.3433 | 197.7057 | 27.1976 | 49.4944 | 7.1617 | 13.6439 | 22.2649 | 34.727 | 50.0215 | 67.6081 | 104.1689 | 104.1576 | 163.6163 | 227.1665 | 227.1665 | 227.1665 | 227.1665 | 227.1665 | 227.1665 | 227.1665 | 227.1665 | 227.1665 | 227.1665 | 227.1665 | 227.1665 | 227.1665 | 227.1665 | 227.1665 | 227.1665
|  |  | Annualised capex | 0 | 0 | 3.0464 | 3.0464 | 3.0464 | 3.0464 | 3.0464 | 3.0464 | 3.0464 | 3.0464 | 3.0464 | 3.0464 | 3.0464 | 3.0464 | 3.0464 | 3.0464 | 3.0464 | 3.0464 | 3.0464 | 3.0464 | 3.0464 | 3.0464 | 3.0464 | 3.0464 | 3.0464 | 3.0464 | 3.0464 | 3.0464 | 3.0464 | 3.0464
|  |  | Annualised cost (capex+opex) | 0 | 0 | 3.0464 | 3.6034 | 3.6034 | 3.6034 | 3.6034 | 3.6034 | 3.6034 | 3.6034 | 3.6034 | 3.6034 | 3.6034 | 3.6034 | 3.6034 | 3.6034 | 3.6034 | 3.6034 | 3.6034 | 3.6034 | 3.6034 | 3.6034 | 3.6034 | 3.6034 | 3.6034 | 3.6034 | 3.6034 | 3.6034 | 3.6034 | 3.6034
|  |  | Optimal timing (interim calc) | 0 | 0 | 0 | 1 | 1 | 1 | 1 | [19 empty] | 1 | 1 | 1 | 1 | bar: 1 to 19
|  |  | Optimal timing | - | - | - | Yes | - | - | - | [19 empty] | - | - | - | - | bar: 1 to 19
Adjusted For Optimal Timing: | 49.9911 | 55.7046 | Capex | 0 | 0 | 55.7046 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 6.9051 | 15.0402 | Opex | 0 | 0 | 0 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705
| 6692.532 | 15979.7387 | Reduction in unserved energy | 0 | 0 | 0 | 199.2675 | 240.108 | 344.1223 | 451.4018 | 489.3769 | 527.4925 | 537.149 | 546.2655 | 579.7434 | 521.6459 | 600.5204 | 683.9153 | 683.9153 | 683.9153 | 683.9153 | 683.9153 | 683.9153 | 683.9153 | 683.9153 | 683.9153 | 683.9153 | 683.9153 | 683.9153 | 683.9153 | 683.9153 | 683.9153 | 683.9153
| 6635.6359 | 15908.9938 | Net benefit | 0 | 0 | -55.7046 | 198.7105 | 239.5509 | 343.5652 | 450.8448 | 488.8199 | 526.9355 | 536.592 | 545.7084 | 579.1863 | 521.0889 | 599.9634 | 683.3583 | 683.3583 | 683.3583 | 683.3583 | 683.3583 | 683.3583 | 683.3583 | 683.3583 | 683.3583 | 683.3583 | 683.3583 | 683.3583 | 683.3583 | 683.3583 | 683.3583 | 683.3583
Option 6
Determining Optimal Timing: | Discounted | Undiscounted
| 61.1918 | 68.1854 | Capex | 0 | 0 | 68.1854 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 8.4522 | 18.4101 | Opex | 0 | 0 | 0 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185
| 7907.3276 | 19365.1951 | Reduction in unserved energy | 0 | 0 | 0 | 196.3744 | 284.623 | 345.6457 | 458.541 | 504.1586 | 553.465 | 576.9693 | 601.4289 | 666.6908 | 608.4268 | 735.0476 | 864.614 | 864.614 | 864.614 | 864.614 | 864.614 | 864.614 | 864.614 | 864.614 | 864.614 | 864.614 | 864.614 | 864.614 | 864.614 | 864.614 | 864.614 | 864.614
| 7837.6836 | 19278.5996 | Net benefit | 0 | 0 | -68.1854 | 195.6926 | 283.9411 | 344.9638 | 457.8591 | 503.4768 | 552.7832 | 576.2874 | 600.747 | 666.0089 | 607.745 | 734.3658 | 863.9321 | 863.9321 | 863.9321 | 863.9321 | 863.9321 | 863.9321 | 863.9321 | 863.9321 | 863.9321 | 863.9321 | 863.9321 | 863.9321 | 863.9321 | 863.9321 | 863.9321 | 863.9321
|  |  | EUE Value ($m, real $2024) | 2.6458 | 52.3433 | 197.7057 | 30.0907 | 4.9794 | 5.6382 | 6.5047 | 7.4831 | 8.7545 | 10.2012 | 12.4447 | 17.2215 | 17.3767 | 29.0891 | 46.4679 | 46.4679 | 46.4679 | 46.4679 | 46.4679 | 46.4679 | 46.4679 | 46.4679 | 46.4679 | 46.4679 | 46.4679 | 46.4679 | 46.4679 | 46.4679 | 46.4679 | 46.4679
|  |  | Annualised capex | 0 | 0 | 3.7289 | 3.7289 | 3.7289 | 3.7289 | 3.7289 | 3.7289 | 3.7289 | 3.7289 | 3.7289 | 3.7289 | 3.7289 | 3.7289 | 3.7289 | 3.7289 | 3.7289 | 3.7289 | 3.7289 | 3.7289 | 3.7289 | 3.7289 | 3.7289 | 3.7289 | 3.7289 | 3.7289 | 3.7289 | 3.7289 | 3.7289 | 3.7289
|  |  | Annualised cost (capex+opex) | 0 | 0 | 3.7289 | 4.4108 | 4.4108 | 4.4108 | 4.4108 | 4.4108 | 4.4108 | 4.4108 | 4.4108 | 4.4108 | 4.4108 | 4.4108 | 4.4108 | 4.4108 | 4.4108 | 4.4108 | 4.4108 | 4.4108 | 4.4108 | 4.4108 | 4.4108 | 4.4108 | 4.4108 | 4.4108 | 4.4108 | 4.4108 | 4.4108 | 4.4108
|  |  | Optimal timing (interim calc) | 0 | 0 | 0 | 1 | 1 | 1 | 1 | [19 empty] | 1 | 1 | 1 | 1 | bar: 1 to 19
|  |  | Optimal timing | - | - | - | Yes | - | - | - | [19 empty] | - | - | - | - | bar: 1 to 19
Adjusted For Optimal Timing: | 61.1918 | 68.1854 | Capex | 0 | 0 | 68.1854 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 8.4522 | 18.4101 | Opex | 0 | 0 | 0 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185
| 7907.3276 | 19365.1951 | Reduction in unserved energy | 0 | 0 | 0 | 196.3744 | 284.623 | 345.6457 | 458.541 | 504.1586 | 553.465 | 576.9693 | 601.4289 | 666.6908 | 608.4268 | 735.0476 | 864.614 | 864.614 | 864.614 | 864.614 | 864.614 | 864.614 | 864.614 | 864.614 | 864.614 | 864.614 | 864.614 | 864.614 | 864.614 | 864.614 | 864.614 | 864.614
| 7837.6836 | 19278.5996 | Net benefit | 0 | 0 | -68.1854 | 195.6926 | 283.9411 | 344.9638 | 457.8591 | 503.4768 | 552.7832 | 576.2874 | 600.747 | 666.0089 | 607.745 | 734.3658 | 863.9321 | 863.9321 | 863.9321 | 863.9321 | 863.9321 | 863.9321 | 863.9321 | 863.9321 | 863.9321 | 863.9321 | 863.9321 | 863.9321 | 863.9321 | 863.9321 | 863.9321 | 863.9321
Option 7
Determining Optimal Timing: | Discounted | Undiscounted
| 33.225 | 37.0224 | Capex | 0 | 0 | 37.0224 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 4.5893 | 9.996 | Opex | 0 | 0 | 0 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022
| 6548.4708 | 15545.6872 | Reduction in unserved energy | 0 | 0 | 0 | 194.8375 | 280.7407 | 338.676 | 445.3217 | 482.6422 | 520.1217 | 529.097 | 537.3539 | 569.4949 | 510.6267 | 585.5999 | 659.4484 | 659.4484 | 659.4484 | 659.4484 | 659.4484 | 659.4484 | 659.4484 | 659.4484 | 659.4484 | 659.4484 | 659.4484 | 659.4484 | 659.4484 | 659.4484 | 659.4484 | 659.4484
| 6510.6565 | 15498.6689 | Net benefit | 0 | 0 | -37.0224 | 194.4673 | 280.3705 | 338.3058 | 444.9514 | 482.2719 | 519.7515 | 528.7268 | 536.9837 | 569.1247 | 510.2565 | 585.2296 | 659.0782 | 659.0782 | 659.0782 | 659.0782 | 659.0782 | 659.0782 | 659.0782 | 659.0782 | 659.0782 | 659.0782 | 659.0782 | 659.0782 | 659.0782 | 659.0782 | 659.0782 | 659.0782
|  |  | EUE Value ($m, real $2024) | 2.6458 | 52.3433 | 197.7057 | 31.6276 | 8.8617 | 12.6079 | 19.7241 | 28.9996 | 42.0979 | 58.0735 | 76.5197 | 114.4173 | 115.1768 | 178.5369 | 251.6334 | 251.6334 | 251.6334 | 251.6334 | 251.6334 | 251.6334 | 251.6334 | 251.6334 | 251.6334 | 251.6334 | 251.6334 | 251.6334 | 251.6334 | 251.6334 | 251.6334 | 251.6334
|  |  | Annualised capex | 0 | 0 | 2.0247 | 2.0247 | 2.0247 | 2.0247 | 2.0247 | 2.0247 | 2.0247 | 2.0247 | 2.0247 | 2.0247 | 2.0247 | 2.0247 | 2.0247 | 2.0247 | 2.0247 | 2.0247 | 2.0247 | 2.0247 | 2.0247 | 2.0247 | 2.0247 | 2.0247 | 2.0247 | 2.0247 | 2.0247 | 2.0247 | 2.0247 | 2.0247
|  |  | Annualised cost (capex+opex) | 0 | 0 | 2.0247 | 2.3949 | 2.3949 | 2.3949 | 2.3949 | 2.3949 | 2.3949 | 2.3949 | 2.3949 | 2.3949 | 2.3949 | 2.3949 | 2.3949 | 2.3949 | 2.3949 | 2.3949 | 2.3949 | 2.3949 | 2.3949 | 2.3949 | 2.3949 | 2.3949 | 2.3949 | 2.3949 | 2.3949 | 2.3949 | 2.3949 | 2.3949
|  |  | Optimal timing (interim calc) | 0 | 0 | 0 | 1 | 1 | 1 | 1 | [19 empty] | 1 | 1 | 1 | 1 | bar: 1 to 19
|  |  | Optimal timing | - | - | - | Yes | - | - | - | [19 empty] | - | - | - | - | bar: 1 to 19
Adjusted For Optimal Timing: | 33.225 | 37.0224 | Capex | 0 | 0 | 37.0224 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 4.5893 | 9.996 | Opex | 0 | 0 | 0 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022
| 6548.4708 | 15545.6872 | Reduction in unserved energy | 0 | 0 | 0 | 194.8375 | 280.7407 | 338.676 | 445.3217 | 482.6422 | 520.1217 | 529.097 | 537.3539 | 569.4949 | 510.6267 | 585.5999 | 659.4484 | 659.4484 | 659.4484 | 659.4484 | 659.4484 | 659.4484 | 659.4484 | 659.4484 | 659.4484 | 659.4484 | 659.4484 | 659.4484 | 659.4484 | 659.4484 | 659.4484 | 659.4484
| 6510.6565 | 15498.6689 | Net benefit | 0 | 0 | -37.0224 | 194.4673 | 280.3705 | 338.3058 | 444.9514 | 482.2719 | 519.7515 | 528.7268 | 536.9837 | 569.1247 | 510.2565 | 585.2296 | 659.0782 | 659.0782 | 659.0782 | 659.0782 | 659.0782 | 659.0782 | 659.0782 | 659.0782 | 659.0782 | 659.0782 | 659.0782 | 659.0782 | 659.0782 | 659.0782 | 659.0782 | 659.0782
Option 8
Determining Optimal Timing: | Discounted | Undiscounted
| 47.6017 | 53.0422 | Capex | 0 | 0 | 53.0422 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 6.5751 | 14.3214 | Opex | 0 | 0 | 0 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042
| 3140.9029 | 8428.6969 | Reduction in unserved energy | 0 | 0 | 0 | 6.0174 | 59.7148 | 78.0807 | 92.5744 | 108.0501 | 127.3489 | 147.2962 | 172.3751 | 232.3668 | 220.3288 | 320.4972 | 429.0029 | 429.0029 | 429.0029 | 429.0029 | 429.0029 | 429.0029 | 429.0029 | 429.0029 | 429.0029 | 429.0029 | 429.0029 | 429.0029 | 429.0029 | 429.0029 | 429.0029 | 429.0029
| 3086.7261 | 8361.3333 | Net benefit | 0 | 0 | -53.0422 | 5.487 | 59.1844 | 77.5503 | 92.0439 | 107.5197 | 126.8184 | 146.7658 | 171.8446 | 231.8364 | 219.7984 | 319.9668 | 428.4725 | 428.4725 | 428.4725 | 428.4725 | 428.4725 | 428.4725 | 428.4725 | 428.4725 | 428.4725 | 428.4725 | 428.4725 | 428.4725 | 428.4725 | 428.4725 | 428.4725 | 428.4725
|  |  | EUE Value ($m, real $2024) | 2.6458 | 52.3433 | 197.7057 | 220.4477 | 229.8875 | 273.2032 | 372.4714 | 403.5917 | 434.8707 | 439.8743 | 441.4986 | 451.5454 | 405.4747 | 443.6395 | 482.079 | 482.079 | 482.079 | 482.079 | 482.079 | 482.079 | 482.079 | 482.079 | 482.079 | 482.079 | 482.079 | 482.079 | 482.079 | 482.079 | 482.079 | 482.079
|  |  | Annualised capex | 0 | 0 | 2.9008 | 2.9008 | 2.9008 | 2.9008 | 2.9008 | 2.9008 | 2.9008 | 2.9008 | 2.9008 | 2.9008 | 2.9008 | 2.9008 | 2.9008 | 2.9008 | 2.9008 | 2.9008 | 2.9008 | 2.9008 | 2.9008 | 2.9008 | 2.9008 | 2.9008 | 2.9008 | 2.9008 | 2.9008 | 2.9008 | 2.9008 | 2.9008
|  |  | Annualised cost (capex+opex) | 0 | 0 | 2.9008 | 3.4312 | 3.4312 | 3.4312 | 3.4312 | 3.4312 | 3.4312 | 3.4312 | 3.4312 | 3.4312 | 3.4312 | 3.4312 | 3.4312 | 3.4312 | 3.4312 | 3.4312 | 3.4312 | 3.4312 | 3.4312 | 3.4312 | 3.4312 | 3.4312 | 3.4312 | 3.4312 | 3.4312 | 3.4312 | 3.4312 | 3.4312
|  |  | Optimal timing (interim calc) | 0 | 0 | 0 | 1 | 1 | 1 | 1 | [19 empty] | 1 | 1 | 1 | 1 | bar: 1 to 19
|  |  | Optimal timing | - | - | - | Yes | - | - | - | [19 empty] | - | - | - | - | bar: 1 to 19
Adjusted For Optimal Timing: | 47.6017 | 53.0422 | Capex | 0 | 0 | 53.0422 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 6.5751 | 14.3214 | Opex | 0 | 0 | 0 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042
| 3140.9029 | 8428.6969 | Reduction in unserved energy | 0 | 0 | 0 | 6.0174 | 59.7148 | 78.0807 | 92.5744 | 108.0501 | 127.3489 | 147.2962 | 172.3751 | 232.3668 | 220.3288 | 320.4972 | 429.0029 | 429.0029 | 429.0029 | 429.0029 | 429.0029 | 429.0029 | 429.0029 | 429.0029 | 429.0029 | 429.0029 | 429.0029 | 429.0029 | 429.0029 | 429.0029 | 429.0029 | 429.0029
| 3086.7261 | 8361.3333 | Net benefit | 0 | 0 | -53.0422 | 5.487 | 59.1844 | 77.5503 | 92.0439 | 107.5197 | 126.8184 | 146.7658 | 171.8446 | 231.8364 | 219.7984 | 319.9668 | 428.4725 | 428.4725 | 428.4725 | 428.4725 | 428.4725 | 428.4725 | 428.4725 | 428.4725 | 428.4725 | 428.4725 | 428.4725 | 428.4725 | 428.4725 | 428.4725 | 428.4725 | 428.4725
Option 9
Determining Optimal Timing: | Discounted | Undiscounted
| 44.1555 | 49.2021 | Capex | 0 | 0 | 49.2021 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 6.0991 | 13.2846 | Opex | 0 | 0 | 0 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202
| 6653.7976 | 15798.6657 | Reduction in unserved energy | 0 | 0 | 0 | 199.1029 | 285.4384 | 343.8707 | 451.1202 | 489.0483 | 527.0924 | 536.655 | 545.623 | 578.4426 | 520.0962 | 595.8581 | 670.3949 | 670.3949 | 670.3949 | 670.3949 | 670.3949 | 670.3949 | 670.3949 | 670.3949 | 670.3949 | 670.3949 | 670.3949 | 670.3949 | 670.3949 | 670.3949 | 670.3949 | 670.3949
| 6603.5431 | 15736.179 | Net benefit | 0 | 0 | -49.2021 | 198.6109 | 284.9464 | 343.3787 | 450.6282 | 488.5563 | 526.6004 | 536.163 | 545.131 | 577.9505 | 519.6042 | 595.3661 | 669.9028 | 669.9028 | 669.9028 | 669.9028 | 669.9028 | 669.9028 | 669.9028 | 669.9028 | 669.9028 | 669.9028 | 669.9028 | 669.9028 | 669.9028 | 669.9028 | 669.9028 | 669.9028
|  |  | EUE Value ($m, real $2024) | 2.6458 | 52.3433 | 197.7057 | 27.3622 | 4.1639 | 7.4132 | 13.9255 | 22.5935 | 35.1271 | 50.5155 | 68.2506 | 105.4697 | 105.7073 | 168.2786 | 240.687 | 240.687 | 240.687 | 240.687 | 240.687 | 240.687 | 240.687 | 240.687 | 240.687 | 240.687 | 240.687 | 240.687 | 240.687 | 240.687 | 240.687 | 240.687
|  |  | Annualised capex | 0 | 0 | 2.6908 | 2.6908 | 2.6908 | 2.6908 | 2.6908 | 2.6908 | 2.6908 | 2.6908 | 2.6908 | 2.6908 | 2.6908 | 2.6908 | 2.6908 | 2.6908 | 2.6908 | 2.6908 | 2.6908 | 2.6908 | 2.6908 | 2.6908 | 2.6908 | 2.6908 | 2.6908 | 2.6908 | 2.6908 | 2.6908 | 2.6908 | 2.6908
|  |  | Annualised cost (capex+opex) | 0 | 0 | 2.6908 | 3.1828 | 3.1828 | 3.1828 | 3.1828 | 3.1828 | 3.1828 | 3.1828 | 3.1828 | 3.1828 | 3.1828 | 3.1828 | 3.1828 | 3.1828 | 3.1828 | 3.1828 | 3.1828 | 3.1828 | 3.1828 | 3.1828 | 3.1828 | 3.1828 | 3.1828 | 3.1828 | 3.1828 | 3.1828 | 3.1828 | 3.1828
|  |  | Optimal timing (interim calc) | 0 | 0 | 0 | 1 | 1 | 1 | 1 | [19 empty] | 1 | 1 | 1 | 1 | bar: 1 to 19
|  |  | Optimal timing | - | - | - | Yes | - | - | - | [19 empty] | - | - | - | - | bar: 1 to 19
Adjusted For Optimal Timing: | 44.1555 | 49.2021 | Capex | 0 | 0 | 49.2021 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 6.0991 | 13.2846 | Opex | 0 | 0 | 0 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202
| 6653.7976 | 15798.6657 | Reduction in unserved energy | 0 | 0 | 0 | 199.1029 | 285.4384 | 343.8707 | 451.1202 | 489.0483 | 527.0924 | 536.655 | 545.623 | 578.4426 | 520.0962 | 595.8581 | 670.3949 | 670.3949 | 670.3949 | 670.3949 | 670.3949 | 670.3949 | 670.3949 | 670.3949 | 670.3949 | 670.3949 | 670.3949 | 670.3949 | 670.3949 | 670.3949 | 670.3949 | 670.3949
| 6603.5431 | 15736.179 | Net benefit | 0 | 0 | -49.2021 | 198.6109 | 284.9464 | 343.3787 | 450.6282 | 488.5563 | 526.6004 | 536.163 | 545.131 | 577.9505 | 519.6042 | 595.3661 | 669.9028 | 669.9028 | 669.9028 | 669.9028 | 669.9028 | 669.9028 | 669.9028 | 669.9028 | 669.9028 | 669.9028 | 669.9028 | 669.9028 | 669.9028 | 669.9028 | 669.9028 | 669.9028
Option 10
Determining Optimal Timing: | Discounted | Undiscounted
| 0 | 0 | Capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 6375.8942 | 15208.189 | Opex | 0.48285 | 57.8283 | 189.4866 | 207.6844 | 245.4848 | 279.2209 | 339.624 | 384.4625 | 426.7802 | 445.1879 | 469.6214 | 502.6026 | 486.2654 | 573.3683 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055
| 5100.7154 | 12166.5512 | Reduction in unserved energy | 0.38628 | 46.2627 | 151.5893 | 166.1475 | 196.3878 | 223.3767 | 271.6992 | 307.57 | 341.4242 | 356.1503 | 375.6971 | 402.0821 | 389.0123 | 458.6947 | 530.0044 | 530.0044 | 530.0044 | 530.0044 | 530.0044 | 530.0044 | 530.0044 | 530.0044 | 530.0044 | 530.0044 | 530.0044 | 530.0044 | 530.0044 | 530.0044 | 530.0044 | 530.0044
| -1275.1788 | -3041.6378 | Net benefit | -0.096569 | -11.5657 | -37.8973 | -41.5369 | -49.097 | -55.8442 | -67.9248 | -76.8925 | -85.356 | -89.0376 | -93.9243 | -100.5205 | -97.2531 | -114.6737 | -132.5011 | -132.5011 | -132.5011 | -132.5011 | -132.5011 | -132.5011 | -132.5011 | -132.5011 | -132.5011 | -132.5011 | -132.5011 | -132.5011 | -132.5011 | -132.5011 | -132.5011 | -132.5011
|  |  | EUE Value ($m, real $2024) | 2.2644 | 6.0806 | 46.1164 | 60.3176 | 93.2145 | 127.9072 | 193.3465 | 204.0718 | 220.7954 | 231.0202 | 238.1765 | 281.8301 | 236.7912 | 305.4421 | 381.0774 | 381.0774 | 381.0774 | 381.0774 | 381.0774 | 381.0774 | 381.0774 | 381.0774 | 381.0774 | 381.0774 | 381.0774 | 381.0774 | 381.0774 | 381.0774 | 381.0774 | 381.0774
|  |  | Annualised capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Annualised cost (capex+opex) | 0.48285 | 57.8283 | 189.4866 | 207.6844 | 245.4848 | 279.2209 | 339.624 | 384.4625 | 426.7802 | 445.1879 | 469.6214 | 502.6026 | 486.2654 | 573.3683 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055
|  |  | Optimal timing (interim calc) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Optimal timing | - | - | - | - | - | - | - | [19 empty] | - | - | - | - | bar: 1 to 19
Adjusted For Optimal Timing: | 0 | 0 | Capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 6375.8942 | 15208.189 | Opex | 0.48285 | 57.8283 | 189.4866 | 207.6844 | 245.4848 | 279.2209 | 339.624 | 384.4625 | 426.7802 | 445.1879 | 469.6214 | 502.6026 | 486.2654 | 573.3683 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055
| 6375.8942 | 15208.189 | Reduction in unserved energy | 0.48285 | 57.8283 | 189.4866 | 207.6844 | 245.4848 | 279.2209 | 339.624 | 384.4625 | 426.7802 | 445.1879 | 469.6214 | 502.6026 | 486.2654 | 573.3683 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055
| 0 | 0 | Net benefit | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## 3.2.8 NPV (High VCR)
Economic inputs and assumptions
Scenario | Discount rate | Central
| Cost | Central
| VCR | Upper bound
|  | Central | Lower bound | Upper bound
| Discount rate | 5.56% | 4.11% | 7%
| Cost | 100% | 80% | 120%
| VCR | 100% | 80% | 120%
Asset life for calculating annualised capex (years) | Option 1 | 45
| Option 2 | 45
| Option 3 | 45
| Option 4 | 45
| Option 5 | 45
| Option 6 | 45
| Option 7 | 45
| Option 8 | 45
| Option 9 | 45
| Option 10 | 45
|  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30
|  |  |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Outputs | bar: 3 FY27; 7 FY31
Option 1
| Discounted | Undiscounted
| 0 | 0 | Capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Opex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Reduction in unserved energy | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Net benefit | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | EUE Value ($m, real $2024) | 3.9761 | 78.5149 | 296.5586 | 339.6977 | 434.4035 | 526.9259 | 697.5686 | 767.4627 | 843.3294 | 880.7558 | 920.8104 | 1025.8684 | 938.7053 | 1146.2051 | 1366.6228 | 1366.6228 | 1366.6228 | 1366.6228 | 1366.6228 | 1366.6228 | 1366.6228 | 1366.6228 | 1366.6228 | 1366.6228 | 1366.6228 | 1366.6228 | 1366.6228 | 1366.6228 | 1366.6228 | 1366.6228
Option 2
Determining Optimal Timing: | Discounted | Undiscounted
| 64.7091 | 72.1048 | Capex | 0 | 0 | 72.1048 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 8.9381 | 19.4683 | Opex | 0 | 0 | 0 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105
| 11981.9016 | 29509.2248 | Reduction in unserved energy | 0 | 0 | 0 | 294.5913 | 357.9839 | 518.5848 | 687.9569 | 756.4629 | 830.58 | 866.2229 | 904.0245 | 1005.2811 | 917.8318 | 1115.5517 | 1328.3846 | 1328.3846 | 1328.3846 | 1328.3846 | 1328.3846 | 1328.3846 | 1328.3846 | 1328.3846 | 1328.3846 | 1328.3846 | 1328.3846 | 1328.3846 | 1328.3846 | 1328.3846 | 1328.3846 | 1328.3846
| 11908.2544 | 29417.6518 | Net benefit | 0 | 0 | -72.1048 | 293.8703 | 357.2628 | 517.8637 | 687.2359 | 755.7418 | 829.8589 | 865.5019 | 903.3034 | 1004.56 | 917.1108 | 1114.8306 | 1327.6635 | 1327.6635 | 1327.6635 | 1327.6635 | 1327.6635 | 1327.6635 | 1327.6635 | 1327.6635 | 1327.6635 | 1327.6635 | 1327.6635 | 1327.6635 | 1327.6635 | 1327.6635 | 1327.6635 | 1327.6635
|  |  | EUE Value ($m, real $2024) | 3.9687 | 78.5149 | 296.5586 | 45.1063 | 76.4196 | 8.3411 | 9.6117 | 10.9998 | 12.7494 | 14.5329 | 16.7859 | 20.5873 | 20.8735 | 30.6535 | 38.2382 | 38.2382 | 38.2382 | 38.2382 | 38.2382 | 38.2382 | 38.2382 | 38.2382 | 38.2382 | 38.2382 | 38.2382 | 38.2382 | 38.2382 | 38.2382 | 38.2382 | 38.2382
|  |  | Annualised capex | 0 | 0 | 3.9433 | 3.9433 | 3.9433 | 3.9433 | 3.9433 | 3.9433 | 3.9433 | 3.9433 | 3.9433 | 3.9433 | 3.9433 | 3.9433 | 3.9433 | 3.9433 | 3.9433 | 3.9433 | 3.9433 | 3.9433 | 3.9433 | 3.9433 | 3.9433 | 3.9433 | 3.9433 | 3.9433 | 3.9433 | 3.9433 | 3.9433 | 3.9433
|  |  | Annualised cost (capex+opex) | 0 | 0 | 3.9433 | 4.6643 | 4.6643 | 4.6643 | 4.6643 | 4.6643 | 4.6643 | 4.6643 | 4.6643 | 4.6643 | 4.6643 | 4.6643 | 4.6643 | 4.6643 | 4.6643 | 4.6643 | 4.6643 | 4.6643 | 4.6643 | 4.6643 | 4.6643 | 4.6643 | 4.6643 | 4.6643 | 4.6643 | 4.6643 | 4.6643 | 4.6643
|  |  | Optimal timing (interim calc) | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  |  | Optimal timing | - | - | - | Yes | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Adjusted For Optimal Timing: | 64.7091 | 72.1048 | Capex | 0 | 0 | 72.1048 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 8.9381 | 19.4683 | Opex | 0 | 0 | 0 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105
| 11981.9016 | 29509.2248 | Reduction in unserved energy | 0 | 0 | 0 | 294.5913 | 357.9839 | 518.5848 | 687.9569 | 756.4629 | 830.58 | 866.2229 | 904.0245 | 1005.2811 | 917.8318 | 1115.5517 | 1328.3846 | 1328.3846 | 1328.3846 | 1328.3846 | 1328.3846 | 1328.3846 | 1328.3846 | 1328.3846 | 1328.3846 | 1328.3846 | 1328.3846 | 1328.3846 | 1328.3846 | 1328.3846 | 1328.3846 | 1328.3846
| 11908.2544 | 29417.6518 | Net benefit | 0 | 0 | -72.1048 | 293.8703 | 357.2628 | 517.8637 | 687.2359 | 755.7418 | 829.8589 | 865.5019 | 903.3034 | 1004.56 | 917.1108 | 1114.8306 | 1327.6635 | 1327.6635 | 1327.6635 | 1327.6635 | 1327.6635 | 1327.6635 | 1327.6635 | 1327.6635 | 1327.6635 | 1327.6635 | 1327.6635 | 1327.6635 | 1327.6635 | 1327.6635 | 1327.6635 | 1327.6635
Option 3
Determining Optimal Timing: | Discounted | Undiscounted
| 39.0606 | 43.5248 | Capex | 0 | 0 | 43.5248 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 5.3953 | 11.7517 | Opex | 0 | 0 | 0 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525
| 9880.9477 | 23590.5313 | Reduction in unserved energy | 0 | 0 | 0 | 292.5026 | 353.1145 | 508.3902 | 668.403 | 724.4535 | 780.7797 | 794.3727 | 807.0646 | 856.2609 | 768.2431 | 885.3504 | 1009.4748 | 1009.4748 | 1009.4748 | 1009.4748 | 1009.4748 | 1009.4748 | 1009.4748 | 1009.4748 | 1009.4748 | 1009.4748 | 1009.4748 | 1009.4748 | 1009.4748 | 1009.4748 | 1009.4748 | 1009.4748
| 9836.4918 | 23535.2548 | Net benefit | 0 | 0 | -43.5248 | 292.0674 | 352.6792 | 507.9549 | 667.9677 | 724.0183 | 780.3445 | 793.9375 | 806.6294 | 855.8256 | 767.8079 | 884.9151 | 1009.0395 | 1009.0395 | 1009.0395 | 1009.0395 | 1009.0395 | 1009.0395 | 1009.0395 | 1009.0395 | 1009.0395 | 1009.0395 | 1009.0395 | 1009.0395 | 1009.0395 | 1009.0395 | 1009.0395 | 1009.0395
|  |  | EUE Value ($m, real $2024) | 3.9687 | 78.5149 | 296.5586 | 47.195 | 81.289 | 18.5357 | 29.1656 | 43.0091 | 62.5496 | 86.3831 | 113.7458 | 169.6075 | 170.4622 | 260.8547 | 357.148 | 357.148 | 357.148 | 357.148 | 357.148 | 357.148 | 357.148 | 357.148 | 357.148 | 357.148 | 357.148 | 357.148 | 357.148 | 357.148 | 357.148 | 357.148
|  |  | Annualised capex | 0 | 0 | 2.3803 | 2.3803 | 2.3803 | 2.3803 | 2.3803 | 2.3803 | 2.3803 | 2.3803 | 2.3803 | 2.3803 | 2.3803 | 2.3803 | 2.3803 | 2.3803 | 2.3803 | 2.3803 | 2.3803 | 2.3803 | 2.3803 | 2.3803 | 2.3803 | 2.3803 | 2.3803 | 2.3803 | 2.3803 | 2.3803 | 2.3803 | 2.3803
|  |  | Annualised cost (capex+opex) | 0 | 0 | 2.3803 | 2.8155 | 2.8155 | 2.8155 | 2.8155 | 2.8155 | 2.8155 | 2.8155 | 2.8155 | 2.8155 | 2.8155 | 2.8155 | 2.8155 | 2.8155 | 2.8155 | 2.8155 | 2.8155 | 2.8155 | 2.8155 | 2.8155 | 2.8155 | 2.8155 | 2.8155 | 2.8155 | 2.8155 | 2.8155 | 2.8155 | 2.8155
|  |  | Optimal timing (interim calc) | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  |  | Optimal timing | - | - | - | Yes | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Adjusted For Optimal Timing: | 39.0606 | 43.5248 | Capex | 0 | 0 | 43.5248 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 5.3953 | 11.7517 | Opex | 0 | 0 | 0 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525
| 9880.9477 | 23590.5313 | Reduction in unserved energy | 0 | 0 | 0 | 292.5026 | 353.1145 | 508.3902 | 668.403 | 724.4535 | 780.7797 | 794.3727 | 807.0646 | 856.2609 | 768.2431 | 885.3504 | 1009.4748 | 1009.4748 | 1009.4748 | 1009.4748 | 1009.4748 | 1009.4748 | 1009.4748 | 1009.4748 | 1009.4748 | 1009.4748 | 1009.4748 | 1009.4748 | 1009.4748 | 1009.4748 | 1009.4748 | 1009.4748
| 9836.4918 | 23535.2548 | Net benefit | 0 | 0 | -43.5248 | 292.0674 | 352.6792 | 507.9549 | 667.9677 | 724.0183 | 780.3445 | 793.9375 | 806.6294 | 855.8256 | 767.8079 | 884.9151 | 1009.0395 | 1009.0395 | 1009.0395 | 1009.0395 | 1009.0395 | 1009.0395 | 1009.0395 | 1009.0395 | 1009.0395 | 1009.0395 | 1009.0395 | 1009.0395 | 1009.0395 | 1009.0395 | 1009.0395 | 1009.0395
Option 4
Determining Optimal Timing: | Discounted | Undiscounted
| 53.4373 | 59.5447 | Capex | 0 | 0 | 59.5447 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 7.3811 | 16.0771 | Opex | 0 | 0 | 0 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545
| 4788.4607 | 12970.0811 | Reduction in unserved energy | 0 | 0 | 0 | 9.1836 | 21.6937 | 117.5626 | 139.3749 | 162.6772 | 191.7471 | 221.8548 | 259.852 | 351.3859 | 334.2163 | 489.8994 | 666.9146 | 666.9146 | 666.9146 | 666.9146 | 666.9146 | 666.9146 | 666.9146 | 666.9146 | 666.9146 | 666.9146 | 666.9146 | 666.9146 | 666.9146 | 666.9146 | 666.9146 | 666.9146
| 4727.6423 | 12894.4593 | Net benefit | 0 | 0 | -59.5447 | 8.5881 | 21.0983 | 116.9671 | 138.7795 | 162.0818 | 191.1516 | 221.2593 | 259.2566 | 350.7905 | 333.6209 | 489.304 | 666.3192 | 666.3192 | 666.3192 | 666.3192 | 666.3192 | 666.3192 | 666.3192 | 666.3192 | 666.3192 | 666.3192 | 666.3192 | 666.3192 | 666.3192 | 666.3192 | 666.3192 | 666.3192
|  |  | EUE Value ($m, real $2024) | 3.9687 | 78.5149 | 296.5586 | 330.5141 | 412.7098 | 409.3633 | 558.1937 | 604.7854 | 651.5823 | 658.901 | 660.9584 | 674.4825 | 604.489 | 656.3057 | 699.7082 | 699.7082 | 699.7082 | 699.7082 | 699.7082 | 699.7082 | 699.7082 | 699.7082 | 699.7082 | 699.7082 | 699.7082 | 699.7082 | 699.7082 | 699.7082 | 699.7082 | 699.7082
|  |  | Annualised capex | 0 | 0 | 3.2564 | 3.2564 | 3.2564 | 3.2564 | 3.2564 | 3.2564 | 3.2564 | 3.2564 | 3.2564 | 3.2564 | 3.2564 | 3.2564 | 3.2564 | 3.2564 | 3.2564 | 3.2564 | 3.2564 | 3.2564 | 3.2564 | 3.2564 | 3.2564 | 3.2564 | 3.2564 | 3.2564 | 3.2564 | 3.2564 | 3.2564 | 3.2564
|  |  | Annualised cost (capex+opex) | 0 | 0 | 3.2564 | 3.8518 | 3.8518 | 3.8518 | 3.8518 | 3.8518 | 3.8518 | 3.8518 | 3.8518 | 3.8518 | 3.8518 | 3.8518 | 3.8518 | 3.8518 | 3.8518 | 3.8518 | 3.8518 | 3.8518 | 3.8518 | 3.8518 | 3.8518 | 3.8518 | 3.8518 | 3.8518 | 3.8518 | 3.8518 | 3.8518 | 3.8518
|  |  | Optimal timing (interim calc) | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  |  | Optimal timing | - | - | - | Yes | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
[11 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19
Adjusted For Optimal Timing: | 53.4373 | 59.5447 | Capex | 0 | 0 | 59.5447 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 7.3811 | 16.0771 | Opex | 0 | 0 | 0 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545
| 4788.4607 | 12970.0811 | Reduction in unserved energy | 0 | 0 | 0 | 9.1836 | 21.6937 | 117.5626 | 139.3749 | 162.6772 | 191.7471 | 221.8548 | 259.852 | 351.3859 | 334.2163 | 489.8994 | 666.9146 | 666.9146 | 666.9146 | 666.9146 | 666.9146 | 666.9146 | 666.9146 | 666.9146 | 666.9146 | 666.9146 | 666.9146 | 666.9146 | 666.9146 | 666.9146 | 666.9146 | 666.9146
| 4727.6423 | 12894.4593 | Net benefit | 0 | 0 | -59.5447 | 8.5881 | 21.0983 | 116.9671 | 138.7795 | 162.0818 | 191.1516 | 221.2593 | 259.2566 | 350.7905 | 333.6209 | 489.304 | 666.3192 | 666.3192 | 666.3192 | 666.3192 | 666.3192 | 666.3192 | 666.3192 | 666.3192 | 666.3192 | 666.3192 | 666.3192 | 666.3192 | 666.3192 | 666.3192 | 666.3192 | 666.3192
Option 5
Determining Optimal Timing: | Discounted | Undiscounted
| 49.9911 | 55.7046 | Capex | 0 | 0 | 55.7046 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 6.9051 | 15.0402 | Opex | 0 | 0 | 0 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705
| 10038.7981 | 23969.608 | Reduction in unserved energy | 0 | 0 | 0 | 298.9013 | 360.1619 | 516.1834 | 677.1027 | 734.0654 | 791.2388 | 805.7236 | 819.3982 | 869.615 | 782.4689 | 900.7807 | 1025.873 | 1025.873 | 1025.873 | 1025.873 | 1025.873 | 1025.873 | 1025.873 | 1025.873 | 1025.873 | 1025.873 | 1025.873 | 1025.873 | 1025.873 | 1025.873 | 1025.873 | 1025.873
| 9981.9019 | 23898.8632 | Net benefit | 0 | 0 | -55.7046 | 298.3443 | 359.6049 | 515.6263 | 676.5457 | 733.5083 | 790.6817 | 805.1665 | 818.8412 | 869.058 | 781.9118 | 900.2236 | 1025.316 | 1025.316 | 1025.316 | 1025.316 | 1025.316 | 1025.316 | 1025.316 | 1025.316 | 1025.316 | 1025.316 | 1025.316 | 1025.316 | 1025.316 | 1025.316 | 1025.316 | 1025.316
|  |  | EUE Value ($m, real $2024) | 3.9687 | 78.5149 | 296.5586 | 40.7963 | 74.2416 | 10.7425 | 20.4659 | 33.3973 | 52.0906 | 75.0322 | 101.4122 | 156.2533 | 156.2364 | 245.4245 | 340.7498 | 340.7498 | 340.7498 | 340.7498 | 340.7498 | 340.7498 | 340.7498 | 340.7498 | 340.7498 | 340.7498 | 340.7498 | 340.7498 | 340.7498 | 340.7498 | 340.7498 | 340.7498
|  |  | Annualised capex | 0 | 0 | 3.0464 | 3.0464 | 3.0464 | 3.0464 | 3.0464 | 3.0464 | 3.0464 | 3.0464 | 3.0464 | 3.0464 | 3.0464 | 3.0464 | 3.0464 | 3.0464 | 3.0464 | 3.0464 | 3.0464 | 3.0464 | 3.0464 | 3.0464 | 3.0464 | 3.0464 | 3.0464 | 3.0464 | 3.0464 | 3.0464 | 3.0464 | 3.0464
|  |  | Annualised cost (capex+opex) | 0 | 0 | 3.0464 | 3.6034 | 3.6034 | 3.6034 | 3.6034 | 3.6034 | 3.6034 | 3.6034 | 3.6034 | 3.6034 | 3.6034 | 3.6034 | 3.6034 | 3.6034 | 3.6034 | 3.6034 | 3.6034 | 3.6034 | 3.6034 | 3.6034 | 3.6034 | 3.6034 | 3.6034 | 3.6034 | 3.6034 | 3.6034 | 3.6034 | 3.6034
|  |  | Optimal timing (interim calc) | 0 | 0 | 0 | 1 | 1 | 1 | 1 | [19 empty] | 1 | 1 | 1 | 1 | bar: 1 to 19
|  |  | Optimal timing | - | - | - | Yes | - | - | - | [19 empty] | - | - | - | - | bar: 1 to 19
Adjusted For Optimal Timing: | 49.9911 | 55.7046 | Capex | 0 | 0 | 55.7046 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 6.9051 | 15.0402 | Opex | 0 | 0 | 0 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705
| 10038.7981 | 23969.608 | Reduction in unserved energy | 0 | 0 | 0 | 298.9013 | 360.1619 | 516.1834 | 677.1027 | 734.0654 | 791.2388 | 805.7236 | 819.3982 | 869.615 | 782.4689 | 900.7807 | 1025.873 | 1025.873 | 1025.873 | 1025.873 | 1025.873 | 1025.873 | 1025.873 | 1025.873 | 1025.873 | 1025.873 | 1025.873 | 1025.873 | 1025.873 | 1025.873 | 1025.873 | 1025.873
| 9981.9019 | 23898.8632 | Net benefit | 0 | 0 | -55.7046 | 298.3443 | 359.6049 | 515.6263 | 676.5457 | 733.5083 | 790.6817 | 805.1665 | 818.8412 | 869.058 | 781.9118 | 900.2236 | 1025.316 | 1025.316 | 1025.316 | 1025.316 | 1025.316 | 1025.316 | 1025.316 | 1025.316 | 1025.316 | 1025.316 | 1025.316 | 1025.316 | 1025.316 | 1025.316 | 1025.316 | 1025.316
Option 6
Determining Optimal Timing: | Discounted | Undiscounted
| 61.1918 | 68.1854 | Capex | 0 | 0 | 68.1854 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 8.4522 | 18.4101 | Opex | 0 | 0 | 0 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185
| 11860.9914 | 29047.7926 | Reduction in unserved energy | 0 | 0 | 0 | 294.5616 | 426.9344 | 518.4685 | 687.8115 | 756.238 | 830.1975 | 865.4539 | 902.1434 | 1000.0361 | 912.6402 | 1102.5714 | 1296.921 | 1296.921 | 1296.921 | 1296.921 | 1296.921 | 1296.921 | 1296.921 | 1296.921 | 1296.921 | 1296.921 | 1296.921 | 1296.921 | 1296.921 | 1296.921 | 1296.921 | 1296.921
| 11791.3474 | 28961.1971 | Net benefit | 0 | 0 | -68.1854 | 293.8798 | 426.2526 | 517.7867 | 687.1296 | 755.5561 | 829.5157 | 864.7721 | 901.4615 | 999.3543 | 911.9584 | 1101.8896 | 1296.2391 | 1296.2391 | 1296.2391 | 1296.2391 | 1296.2391 | 1296.2391 | 1296.2391 | 1296.2391 | 1296.2391 | 1296.2391 | 1296.2391 | 1296.2391 | 1296.2391 | 1296.2391 | 1296.2391 | 1296.2391
|  |  | EUE Value ($m, real $2024) | 3.9687 | 78.5149 | 296.5586 | 45.136 | 7.4691 | 8.4573 | 9.7571 | 11.2247 | 13.1318 | 15.3018 | 18.6671 | 25.8322 | 26.065 | 43.6337 | 69.7018 | 69.7018 | 69.7018 | 69.7018 | 69.7018 | 69.7018 | 69.7018 | 69.7018 | 69.7018 | 69.7018 | 69.7018 | 69.7018 | 69.7018 | 69.7018 | 69.7018 | 69.7018
|  |  | Annualised capex | 0 | 0 | 3.7289 | 3.7289 | 3.7289 | 3.7289 | 3.7289 | 3.7289 | 3.7289 | 3.7289 | 3.7289 | 3.7289 | 3.7289 | 3.7289 | 3.7289 | 3.7289 | 3.7289 | 3.7289 | 3.7289 | 3.7289 | 3.7289 | 3.7289 | 3.7289 | 3.7289 | 3.7289 | 3.7289 | 3.7289 | 3.7289 | 3.7289 | 3.7289
|  |  | Annualised cost (capex+opex) | 0 | 0 | 3.7289 | 4.4108 | 4.4108 | 4.4108 | 4.4108 | 4.4108 | 4.4108 | 4.4108 | 4.4108 | 4.4108 | 4.4108 | 4.4108 | 4.4108 | 4.4108 | 4.4108 | 4.4108 | 4.4108 | 4.4108 | 4.4108 | 4.4108 | 4.4108 | 4.4108 | 4.4108 | 4.4108 | 4.4108 | 4.4108 | 4.4108 | 4.4108
|  |  | Optimal timing (interim calc) | 0 | 0 | 0 | 1 | 1 | 1 | 1 | [19 empty] | 1 | 1 | 1 | 1 | bar: 1 to 19
|  |  | Optimal timing | - | - | - | Yes | - | - | - | [19 empty] | - | - | - | - | bar: 1 to 19
Adjusted For Optimal Timing: | 61.1918 | 68.1854 | Capex | 0 | 0 | 68.1854 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 8.4522 | 18.4101 | Opex | 0 | 0 | 0 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185
| 11860.9914 | 29047.7926 | Reduction in unserved energy | 0 | 0 | 0 | 294.5616 | 426.9344 | 518.4685 | 687.8115 | 756.238 | 830.1975 | 865.4539 | 902.1434 | 1000.0361 | 912.6402 | 1102.5714 | 1296.921 | 1296.921 | 1296.921 | 1296.921 | 1296.921 | 1296.921 | 1296.921 | 1296.921 | 1296.921 | 1296.921 | 1296.921 | 1296.921 | 1296.921 | 1296.921 | 1296.921 | 1296.921
| 11791.3474 | 28961.1971 | Net benefit | 0 | 0 | -68.1854 | 293.8798 | 426.2526 | 517.7867 | 687.1296 | 755.5561 | 829.5157 | 864.7721 | 901.4615 | 999.3543 | 911.9584 | 1101.8896 | 1296.2391 | 1296.2391 | 1296.2391 | 1296.2391 | 1296.2391 | 1296.2391 | 1296.2391 | 1296.2391 | 1296.2391 | 1296.2391 | 1296.2391 | 1296.2391 | 1296.2391 | 1296.2391 | 1296.2391 | 1296.2391
Option 7
Determining Optimal Timing: | Discounted | Undiscounted
| 33.225 | 37.0224 | Capex | 0 | 0 | 37.0224 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 4.5893 | 9.996 | Opex | 0 | 0 | 0 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022
| 9822.7062 | 23318.5309 | Reduction in unserved energy | 0 | 0 | 0 | 292.2563 | 421.111 | 508.014 | 667.9825 | 723.9633 | 780.1826 | 793.6455 | 806.0309 | 854.2424 | 765.94 | 878.3998 | 989.1727 | 989.1727 | 989.1727 | 989.1727 | 989.1727 | 989.1727 | 989.1727 | 989.1727 | 989.1727 | 989.1727 | 989.1727 | 989.1727 | 989.1727 | 989.1727 | 989.1727 | 989.1727
| 9784.8919 | 23271.5125 | Net benefit | 0 | 0 | -37.0224 | 291.8861 | 420.7408 | 507.6438 | 667.6123 | 723.593 | 779.8123 | 793.2753 | 805.6607 | 853.8722 | 765.5698 | 878.0296 | 988.8024 | 988.8024 | 988.8024 | 988.8024 | 988.8024 | 988.8024 | 988.8024 | 988.8024 | 988.8024 | 988.8024 | 988.8024 | 988.8024 | 988.8024 | 988.8024 | 988.8024 | 988.8024
|  |  | EUE Value ($m, real $2024) | 3.9687 | 78.5149 | 296.5586 | 47.4414 | 13.2925 | 18.9118 | 29.5861 | 43.4994 | 63.1468 | 87.1103 | 114.7795 | 171.626 | 172.7653 | 267.8053 | 377.4501 | 377.4501 | 377.4501 | 377.4501 | 377.4501 | 377.4501 | 377.4501 | 377.4501 | 377.4501 | 377.4501 | 377.4501 | 377.4501 | 377.4501 | 377.4501 | 377.4501 | 377.4501
|  |  | Annualised capex | 0 | 0 | 2.0247 | 2.0247 | 2.0247 | 2.0247 | 2.0247 | 2.0247 | 2.0247 | 2.0247 | 2.0247 | 2.0247 | 2.0247 | 2.0247 | 2.0247 | 2.0247 | 2.0247 | 2.0247 | 2.0247 | 2.0247 | 2.0247 | 2.0247 | 2.0247 | 2.0247 | 2.0247 | 2.0247 | 2.0247 | 2.0247 | 2.0247 | 2.0247
|  |  | Annualised cost (capex+opex) | 0 | 0 | 2.0247 | 2.3949 | 2.3949 | 2.3949 | 2.3949 | 2.3949 | 2.3949 | 2.3949 | 2.3949 | 2.3949 | 2.3949 | 2.3949 | 2.3949 | 2.3949 | 2.3949 | 2.3949 | 2.3949 | 2.3949 | 2.3949 | 2.3949 | 2.3949 | 2.3949 | 2.3949 | 2.3949 | 2.3949 | 2.3949 | 2.3949 | 2.3949
|  |  | Optimal timing (interim calc) | 0 | 0 | 0 | 1 | 1 | 1 | 1 | [19 empty] | 1 | 1 | 1 | 1 | bar: 1 to 19
|  |  | Optimal timing | - | - | - | Yes | - | - | - | [19 empty] | - | - | - | - | bar: 1 to 19
Adjusted For Optimal Timing: | 33.225 | 37.0224 | Capex | 0 | 0 | 37.0224 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 4.5893 | 9.996 | Opex | 0 | 0 | 0 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022
| 9822.7062 | 23318.5309 | Reduction in unserved energy | 0 | 0 | 0 | 292.2563 | 421.111 | 508.014 | 667.9825 | 723.9633 | 780.1826 | 793.6455 | 806.0309 | 854.2424 | 765.94 | 878.3998 | 989.1727 | 989.1727 | 989.1727 | 989.1727 | 989.1727 | 989.1727 | 989.1727 | 989.1727 | 989.1727 | 989.1727 | 989.1727 | 989.1727 | 989.1727 | 989.1727 | 989.1727 | 989.1727
| 9784.8919 | 23271.5125 | Net benefit | 0 | 0 | -37.0224 | 291.8861 | 420.7408 | 507.6438 | 667.6123 | 723.593 | 779.8123 | 793.2753 | 805.6607 | 853.8722 | 765.5698 | 878.0296 | 988.8024 | 988.8024 | 988.8024 | 988.8024 | 988.8024 | 988.8024 | 988.8024 | 988.8024 | 988.8024 | 988.8024 | 988.8024 | 988.8024 | 988.8024 | 988.8024 | 988.8024 | 988.8024
Option 8
Determining Optimal Timing: | Discounted | Undiscounted
| 47.6017 | 53.0422 | Capex | 0 | 0 | 53.0422 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 6.5751 | 14.3214 | Opex | 0 | 0 | 0 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042
| 4711.3544 | 12643.0453 | Reduction in unserved energy | 0 | 0 | 0 | 9.0261 | 89.5722 | 117.1211 | 138.8615 | 162.0751 | 191.0233 | 220.9443 | 258.5626 | 348.5502 | 330.4932 | 480.7458 | 643.5044 | 643.5044 | 643.5044 | 643.5044 | 643.5044 | 643.5044 | 643.5044 | 643.5044 | 643.5044 | 643.5044 | 643.5044 | 643.5044 | 643.5044 | 643.5044 | 643.5044 | 643.5044
| 4657.1776 | 12575.6817 | Net benefit | 0 | 0 | -53.0422 | 8.4957 | 89.0418 | 116.5907 | 138.3311 | 161.5447 | 190.4929 | 220.4139 | 258.0322 | 348.0198 | 329.9628 | 480.2154 | 642.9739 | 642.9739 | 642.9739 | 642.9739 | 642.9739 | 642.9739 | 642.9739 | 642.9739 | 642.9739 | 642.9739 | 642.9739 | 642.9739 | 642.9739 | 642.9739 | 642.9739 | 642.9739
|  |  | EUE Value ($m, real $2024) | 3.9687 | 78.5149 | 296.5586 | 330.6715 | 344.8313 | 409.8048 | 558.707 | 605.3875 | 652.3061 | 659.8115 | 662.2478 | 677.3181 | 608.2121 | 665.4593 | 723.1184 | 723.1184 | 723.1184 | 723.1184 | 723.1184 | 723.1184 | 723.1184 | 723.1184 | 723.1184 | 723.1184 | 723.1184 | 723.1184 | 723.1184 | 723.1184 | 723.1184 | 723.1184
|  |  | Annualised capex | 0 | 0 | 2.9008 | 2.9008 | 2.9008 | 2.9008 | 2.9008 | 2.9008 | 2.9008 | 2.9008 | 2.9008 | 2.9008 | 2.9008 | 2.9008 | 2.9008 | 2.9008 | 2.9008 | 2.9008 | 2.9008 | 2.9008 | 2.9008 | 2.9008 | 2.9008 | 2.9008 | 2.9008 | 2.9008 | 2.9008 | 2.9008 | 2.9008 | 2.9008
|  |  | Annualised cost (capex+opex) | 0 | 0 | 2.9008 | 3.4312 | 3.4312 | 3.4312 | 3.4312 | 3.4312 | 3.4312 | 3.4312 | 3.4312 | 3.4312 | 3.4312 | 3.4312 | 3.4312 | 3.4312 | 3.4312 | 3.4312 | 3.4312 | 3.4312 | 3.4312 | 3.4312 | 3.4312 | 3.4312 | 3.4312 | 3.4312 | 3.4312 | 3.4312 | 3.4312 | 3.4312
|  |  | Optimal timing (interim calc) | 0 | 0 | 0 | 1 | 1 | 1 | 1 | [19 empty] | 1 | 1 | 1 | 1 | bar: 1 to 19
|  |  | Optimal timing | - | - | - | Yes | - | - | - | [19 empty] | - | - | - | - | bar: 1 to 19
Adjusted For Optimal Timing: | 47.6017 | 53.0422 | Capex | 0 | 0 | 53.0422 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 6.5751 | 14.3214 | Opex | 0 | 0 | 0 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042
| 4711.3544 | 12643.0453 | Reduction in unserved energy | 0 | 0 | 0 | 9.0261 | 89.5722 | 117.1211 | 138.8615 | 162.0751 | 191.0233 | 220.9443 | 258.5626 | 348.5502 | 330.4932 | 480.7458 | 643.5044 | 643.5044 | 643.5044 | 643.5044 | 643.5044 | 643.5044 | 643.5044 | 643.5044 | 643.5044 | 643.5044 | 643.5044 | 643.5044 | 643.5044 | 643.5044 | 643.5044 | 643.5044
| 4657.1776 | 12575.6817 | Net benefit | 0 | 0 | -53.0422 | 8.4957 | 89.0418 | 116.5907 | 138.3311 | 161.5447 | 190.4929 | 220.4139 | 258.0322 | 348.0198 | 329.9628 | 480.2154 | 642.9739 | 642.9739 | 642.9739 | 642.9739 | 642.9739 | 642.9739 | 642.9739 | 642.9739 | 642.9739 | 642.9739 | 642.9739 | 642.9739 | 642.9739 | 642.9739 | 642.9739 | 642.9739
Option 9
Determining Optimal Timing: | Discounted | Undiscounted
| 44.1555 | 49.2021 | Capex | 0 | 0 | 49.2021 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 6.0991 | 13.2846 | Opex | 0 | 0 | 0 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202
| 9980.6965 | 23697.9985 | Reduction in unserved energy | 0 | 0 | 0 | 298.6543 | 428.1576 | 515.8061 | 676.6804 | 733.5724 | 790.6387 | 804.9825 | 818.4346 | 867.6639 | 780.1444 | 893.7872 | 1005.5923 | 1005.5923 | 1005.5923 | 1005.5923 | 1005.5923 | 1005.5923 | 1005.5923 | 1005.5923 | 1005.5923 | 1005.5923 | 1005.5923 | 1005.5923 | 1005.5923 | 1005.5923 | 1005.5923 | 1005.5923
| 9930.4419 | 23635.5118 | Net benefit | 0 | 0 | -49.2021 | 298.1623 | 427.6656 | 515.3141 | 676.1883 | 733.0804 | 790.1466 | 804.4905 | 817.9425 | 867.1718 | 779.6523 | 893.2952 | 1005.1003 | 1005.1003 | 1005.1003 | 1005.1003 | 1005.1003 | 1005.1003 | 1005.1003 | 1005.1003 | 1005.1003 | 1005.1003 | 1005.1003 | 1005.1003 | 1005.1003 | 1005.1003 | 1005.1003 | 1005.1003
|  |  | EUE Value ($m, real $2024) | 3.9687 | 78.5149 | 296.5586 | 41.0433 | 6.2459 | 11.1198 | 20.8882 | 33.8902 | 52.6907 | 75.7733 | 102.3759 | 158.2045 | 158.5609 | 252.4179 | 361.0305 | 361.0305 | 361.0305 | 361.0305 | 361.0305 | 361.0305 | 361.0305 | 361.0305 | 361.0305 | 361.0305 | 361.0305 | 361.0305 | 361.0305 | 361.0305 | 361.0305 | 361.0305
|  |  | Annualised capex | 0 | 0 | 2.6908 | 2.6908 | 2.6908 | 2.6908 | 2.6908 | 2.6908 | 2.6908 | 2.6908 | 2.6908 | 2.6908 | 2.6908 | 2.6908 | 2.6908 | 2.6908 | 2.6908 | 2.6908 | 2.6908 | 2.6908 | 2.6908 | 2.6908 | 2.6908 | 2.6908 | 2.6908 | 2.6908 | 2.6908 | 2.6908 | 2.6908 | 2.6908
|  |  | Annualised cost (capex+opex) | 0 | 0 | 2.6908 | 3.1828 | 3.1828 | 3.1828 | 3.1828 | 3.1828 | 3.1828 | 3.1828 | 3.1828 | 3.1828 | 3.1828 | 3.1828 | 3.1828 | 3.1828 | 3.1828 | 3.1828 | 3.1828 | 3.1828 | 3.1828 | 3.1828 | 3.1828 | 3.1828 | 3.1828 | 3.1828 | 3.1828 | 3.1828 | 3.1828 | 3.1828
|  |  | Optimal timing (interim calc) | 0 | 0 | 0 | 1 | 1 | 1 | 1 | [19 empty] | 1 | 1 | 1 | 1 | bar: 1 to 19
|  |  | Optimal timing | - | - | - | Yes | - | - | - | [19 empty] | - | - | - | - | bar: 1 to 19
Adjusted For Optimal Timing: | 44.1555 | 49.2021 | Capex | 0 | 0 | 49.2021 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 6.0991 | 13.2846 | Opex | 0 | 0 | 0 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202
| 9980.6965 | 23697.9985 | Reduction in unserved energy | 0 | 0 | 0 | 298.6543 | 428.1576 | 515.8061 | 676.6804 | 733.5724 | 790.6387 | 804.9825 | 818.4346 | 867.6639 | 780.1444 | 893.7872 | 1005.5923 | 1005.5923 | 1005.5923 | 1005.5923 | 1005.5923 | 1005.5923 | 1005.5923 | 1005.5923 | 1005.5923 | 1005.5923 | 1005.5923 | 1005.5923 | 1005.5923 | 1005.5923 | 1005.5923 | 1005.5923
| 9930.4419 | 23635.5118 | Net benefit | 0 | 0 | -49.2021 | 298.1623 | 427.6656 | 515.3141 | 676.1883 | 733.0804 | 790.1466 | 804.4905 | 817.9425 | 867.1718 | 779.6523 | 893.2952 | 1005.1003 | 1005.1003 | 1005.1003 | 1005.1003 | 1005.1003 | 1005.1003 | 1005.1003 | 1005.1003 | 1005.1003 | 1005.1003 | 1005.1003 | 1005.1003 | 1005.1003 | 1005.1003 | 1005.1003 | 1005.1003
Option 10
Determining Optimal Timing: | Discounted | Undiscounted
| 0 | 0 | Capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 6375.8942 | 15208.189 | Opex | 0.48285 | 57.8283 | 189.4866 | 207.6844 | 245.4848 | 279.2209 | 339.624 | 384.4625 | 426.7802 | 445.1879 | 469.6214 | 502.6026 | 486.2654 | 573.3683 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055
| 7651.0731 | 18249.8268 | Reduction in unserved energy | 0.57942 | 69.394 | 227.384 | 249.2213 | 294.5818 | 335.065 | 407.5488 | 461.355 | 512.1363 | 534.2255 | 563.5457 | 603.1232 | 583.5185 | 688.042 | 795.0067 | 795.0067 | 795.0067 | 795.0067 | 795.0067 | 795.0067 | 795.0067 | 795.0067 | 795.0067 | 795.0067 | 795.0067 | 795.0067 | 795.0067 | 795.0067 | 795.0067 | 795.0067
| 1275.1788 | 3041.6378 | Net benefit | 0.096569 | 11.5657 | 37.8973 | 41.5369 | 49.097 | 55.8442 | 67.9248 | 76.8925 | 85.356 | 89.0376 | 93.9243 | 100.5205 | 97.2531 | 114.6737 | 132.5011 | 132.5011 | 132.5011 | 132.5011 | 132.5011 | 132.5011 | 132.5011 | 132.5011 | 132.5011 | 132.5011 | 132.5011 | 132.5011 | 132.5011 | 132.5011 | 132.5011 | 132.5011
|  |  | EUE Value ($m, real $2024) | 3.3966 | 9.1209 | 69.1747 | 90.4763 | 139.8217 | 191.8608 | 290.0198 | 306.1077 | 331.1931 | 346.5303 | 357.2647 | 422.7452 | 355.1868 | 458.1631 | 571.6161 | 571.6161 | 571.6161 | 571.6161 | 571.6161 | 571.6161 | 571.6161 | 571.6161 | 571.6161 | 571.6161 | 571.6161 | 571.6161 | 571.6161 | 571.6161 | 571.6161 | 571.6161
|  |  | Annualised capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Annualised cost (capex+opex) | 0.48285 | 57.8283 | 189.4866 | 207.6844 | 245.4848 | 279.2209 | 339.624 | 384.4625 | 426.7802 | 445.1879 | 469.6214 | 502.6026 | 486.2654 | 573.3683 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055
|  |  | Optimal timing (interim calc) | 1 | 1 | 1 | 1 | 1 | 1 | 1 | [19 empty] | 1 | 1 | 1 | 1 | bar: 1 to 19
|  |  | Optimal timing | Yes | - | - | - | - | - | - | [19 empty] | - | - | - | - | bar: 1 to 19
Adjusted For Optimal Timing: | 0 | 0 | Capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 6375.8942 | 15208.189 | Opex | 0.48285 | 57.8283 | 189.4866 | 207.6844 | 245.4848 | 279.2209 | 339.624 | 384.4625 | 426.7802 | 445.1879 | 469.6214 | 502.6026 | 486.2654 | 573.3683 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055
| 7651.0731 | 18249.8268 | Reduction in unserved energy | 0.57942 | 69.394 | 227.384 | 249.2213 | 294.5818 | 335.065 | 407.5488 | 461.355 | 512.1363 | 534.2255 | 563.5457 | 603.1232 | 583.5185 | 688.042 | 795.0067 | 795.0067 | 795.0067 | 795.0067 | 795.0067 | 795.0067 | 795.0067 | 795.0067 | 795.0067 | 795.0067 | 795.0067 | 795.0067 | 795.0067 | 795.0067 | 795.0067 | 795.0067
| 1275.1788 | 3041.6378 | Net benefit | 0.096569 | 11.5657 | 37.8973 | 41.5369 | 49.097 | 55.8442 | 67.9248 | 76.8925 | 85.356 | 89.0376 | 93.9243 | 100.5205 | 97.2531 | 114.6737 | 132.5011 | 132.5011 | 132.5011 | 132.5011 | 132.5011 | 132.5011 | 132.5011 | 132.5011 | 132.5011 | 132.5011 | 132.5011 | 132.5011 | 132.5011 | 132.5011 | 132.5011 | 132.5011

## 3.2.9 NPV (Low Tx PoF)
Economic inputs and assumptions
Scenario | Discount rate | Central
| Cost | Central
| VCR | Central
|  | Central | Lower bound | Upper bound
| Discount rate | 5.56% | 4.11% | 7%
| Cost | 100% | 80% | 120%
| VCR | 100% | 80% | 120%
Asset life for calculating annualised capex (years) | Option 1 | 45
| Option 2 | 45
| Option 3 | 45
| Option 4 | 45
| Option 5 | 45
| Option 6 | 45
| Option 7 | 45
| Option 8 | 45
| Option 9 | 45
| Option 10 | 45
|  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30
|  |  |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Outputs | bar: 3 FY27; 7 FY31
Option 1
| Discounted | Undiscounted
| 0 | 0 | Capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Opex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Reduction in unserved energy | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Net benefit | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | EUE Value ($m, real $2024) | 1.6542 | 63.5377 | 244.6069 | 280.1431 | 358.6419 | 435.257 | 576.8522 | 634.461 | 697.0077 | 727.5135 | 760.1665 | 846.7852 | 773.56 | 944.9824 | 1127.2149 | 1127.2149 | 1127.2149 | 1127.2149 | 1127.2149 | 1127.2149 | 1127.2149 | 1127.2149 | 1127.2149 | 1127.2149 | 1127.2149 | 1127.2149 | 1127.2149 | 1127.2149 | 1127.2149 | 1127.2149
Option 2
Determining Optimal Timing: | Discounted | Undiscounted
| 64.7091 | 72.1048 | Capex | 0 | 0 | 72.1048 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 8.9381 | 19.4683 | Opex | 0 | 0 | 0 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105
| 9961.0239 | 24527.2249 | Reduction in unserved energy | 0 | 0 | 0 | 245.4537 | 298.2678 | 431.6277 | 572.5937 | 629.4936 | 691.0314 | 720.507 | 751.8006 | 835.8882 | 762.8143 | 926.9694 | 1103.7986 | 1103.7986 | 1103.7986 | 1103.7986 | 1103.7986 | 1103.7986 | 1103.7986 | 1103.7986 | 1103.7986 | 1103.7986 | 1103.7986 | 1103.7986 | 1103.7986 | 1103.7986 | 1103.7986 | 1103.7986
| 9887.3767 | 24435.6519 | Net benefit | 0 | 0 | -72.1048 | 244.7327 | 297.5467 | 430.9067 | 571.8727 | 628.7726 | 690.3104 | 719.7859 | 751.0795 | 835.1672 | 762.0933 | 926.2483 | 1103.0776 | 1103.0776 | 1103.0776 | 1103.0776 | 1103.0776 | 1103.0776 | 1103.0776 | 1103.0776 | 1103.0776 | 1103.0776 | 1103.0776 | 1103.0776 | 1103.0776 | 1103.0776 | 1103.0776 | 1103.0776
|  |  | EUE Value ($m, real $2024) | 1.6512 | 63.5377 | 244.6069 | 34.6894 | 60.3741 | 3.6293 | 4.2585 | 4.9674 | 5.9763 | 7.0066 | 8.3659 | 10.897 | 10.7457 | 18.0131 | 23.4163 | 23.4163 | 23.4163 | 23.4163 | 23.4163 | 23.4163 | 23.4163 | 23.4163 | 23.4163 | 23.4163 | 23.4163 | 23.4163 | 23.4163 | 23.4163 | 23.4163 | 23.4163
|  |  | Annualised capex | 0 | 0 | 3.9433 | 3.9433 | 3.9433 | 3.9433 | 3.9433 | 3.9433 | 3.9433 | 3.9433 | 3.9433 | 3.9433 | 3.9433 | 3.9433 | 3.9433 | 3.9433 | 3.9433 | 3.9433 | 3.9433 | 3.9433 | 3.9433 | 3.9433 | 3.9433 | 3.9433 | 3.9433 | 3.9433 | 3.9433 | 3.9433 | 3.9433 | 3.9433
|  |  | Annualised cost (capex+opex) | 0 | 0 | 3.9433 | 4.6643 | 4.6643 | 4.6643 | 4.6643 | 4.6643 | 4.6643 | 4.6643 | 4.6643 | 4.6643 | 4.6643 | 4.6643 | 4.6643 | 4.6643 | 4.6643 | 4.6643 | 4.6643 | 4.6643 | 4.6643 | 4.6643 | 4.6643 | 4.6643 | 4.6643 | 4.6643 | 4.6643 | 4.6643 | 4.6643 | 4.6643
|  |  | Optimal timing (interim calc) | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  |  | Optimal timing | - | - | - | Yes | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Adjusted For Optimal Timing: | 64.7091 | 72.1048 | Capex | 0 | 0 | 72.1048 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 8.9381 | 19.4683 | Opex | 0 | 0 | 0 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105
| 9961.0239 | 24527.2249 | Reduction in unserved energy | 0 | 0 | 0 | 245.4537 | 298.2678 | 431.6277 | 572.5937 | 629.4936 | 691.0314 | 720.507 | 751.8006 | 835.8882 | 762.8143 | 926.9694 | 1103.7986 | 1103.7986 | 1103.7986 | 1103.7986 | 1103.7986 | 1103.7986 | 1103.7986 | 1103.7986 | 1103.7986 | 1103.7986 | 1103.7986 | 1103.7986 | 1103.7986 | 1103.7986 | 1103.7986 | 1103.7986
| 9887.3767 | 24435.6519 | Net benefit | 0 | 0 | -72.1048 | 244.7327 | 297.5467 | 430.9067 | 571.8727 | 628.7726 | 690.3104 | 719.7859 | 751.0795 | 835.1672 | 762.0933 | 926.2483 | 1103.0776 | 1103.0776 | 1103.0776 | 1103.0776 | 1103.0776 | 1103.0776 | 1103.0776 | 1103.0776 | 1103.0776 | 1103.0776 | 1103.0776 | 1103.0776 | 1103.0776 | 1103.0776 | 1103.0776 | 1103.0776
Option 3
Determining Optimal Timing: | Discounted | Undiscounted
| 39.0606 | 43.5248 | Capex | 0 | 0 | 43.5248 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 5.3953 | 11.7517 | Opex | 0 | 0 | 0 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525
| 8205.3402 | 19582.551 | Reduction in unserved energy | 0 | 0 | 0 | 243.5051 | 293.884 | 423.0822 | 556.2073 | 602.6763 | 649.3163 | 660.364 | 670.6695 | 711.2676 | 637.7589 | 734.6061 | 837.4509 | 837.4509 | 837.4509 | 837.4509 | 837.4509 | 837.4509 | 837.4509 | 837.4509 | 837.4509 | 837.4509 | 837.4509 | 837.4509 | 837.4509 | 837.4509 | 837.4509 | 837.4509
| 8160.8843 | 19527.2745 | Net benefit | 0 | 0 | -43.5248 | 243.0698 | 293.4487 | 422.6469 | 555.772 | 602.241 | 648.8811 | 659.9287 | 670.2343 | 710.8324 | 637.3236 | 734.1709 | 837.0156 | 837.0156 | 837.0156 | 837.0156 | 837.0156 | 837.0156 | 837.0156 | 837.0156 | 837.0156 | 837.0156 | 837.0156 | 837.0156 | 837.0156 | 837.0156 | 837.0156 | 837.0156
|  |  | EUE Value ($m, real $2024) | 1.6512 | 63.5377 | 244.6069 | 36.6381 | 64.7579 | 12.1748 | 20.6449 | 31.7847 | 47.6914 | 67.1496 | 89.497 | 135.5176 | 135.8011 | 210.3763 | 289.764 | 289.764 | 289.764 | 289.764 | 289.764 | 289.764 | 289.764 | 289.764 | 289.764 | 289.764 | 289.764 | 289.764 | 289.764 | 289.764 | 289.764 | 289.764
|  |  | Annualised capex | 0 | 0 | 2.3803 | 2.3803 | 2.3803 | 2.3803 | 2.3803 | 2.3803 | 2.3803 | 2.3803 | 2.3803 | 2.3803 | 2.3803 | 2.3803 | 2.3803 | 2.3803 | 2.3803 | 2.3803 | 2.3803 | 2.3803 | 2.3803 | 2.3803 | 2.3803 | 2.3803 | 2.3803 | 2.3803 | 2.3803 | 2.3803 | 2.3803 | 2.3803
|  |  | Annualised cost (capex+opex) | 0 | 0 | 2.3803 | 2.8155 | 2.8155 | 2.8155 | 2.8155 | 2.8155 | 2.8155 | 2.8155 | 2.8155 | 2.8155 | 2.8155 | 2.8155 | 2.8155 | 2.8155 | 2.8155 | 2.8155 | 2.8155 | 2.8155 | 2.8155 | 2.8155 | 2.8155 | 2.8155 | 2.8155 | 2.8155 | 2.8155 | 2.8155 | 2.8155 | 2.8155
|  |  | Optimal timing (interim calc) | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  |  | Optimal timing | - | - | - | Yes | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Adjusted For Optimal Timing: | 39.0606 | 43.5248 | Capex | 0 | 0 | 43.5248 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 5.3953 | 11.7517 | Opex | 0 | 0 | 0 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525
| 8205.3402 | 19582.551 | Reduction in unserved energy | 0 | 0 | 0 | 243.5051 | 293.884 | 423.0822 | 556.2073 | 602.6763 | 649.3163 | 660.364 | 670.6695 | 711.2676 | 637.7589 | 734.6061 | 837.4509 | 837.4509 | 837.4509 | 837.4509 | 837.4509 | 837.4509 | 837.4509 | 837.4509 | 837.4509 | 837.4509 | 837.4509 | 837.4509 | 837.4509 | 837.4509 | 837.4509 | 837.4509
| 8160.8843 | 19527.2745 | Net benefit | 0 | 0 | -43.5248 | 243.0698 | 293.4487 | 422.6469 | 555.772 | 602.241 | 648.8811 | 659.9287 | 670.2343 | 710.8324 | 637.3236 | 734.1709 | 837.0156 | 837.0156 | 837.0156 | 837.0156 | 837.0156 | 837.0156 | 837.0156 | 837.0156 | 837.0156 | 837.0156 | 837.0156 | 837.0156 | 837.0156 | 837.0156 | 837.0156 | 837.0156
Option 4
Determining Optimal Timing: | Discounted | Undiscounted
| 53.4373 | 59.5447 | Capex | 0 | 0 | 59.5447 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 7.3811 | 16.0771 | Opex | 0 | 0 | 0 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545
| 3957.5188 | 10720.1602 | Reduction in unserved energy | 0 | 0 | 0 | 7.3832 | 17.6571 | 97.3743 | 115.3284 | 134.5009 | 158.4225 | 183.2429 | 214.5962 | 290.3955 | 275.9108 | 404.7631 | 551.2866 | 551.2866 | 551.2866 | 551.2866 | 551.2866 | 551.2866 | 551.2866 | 551.2866 | 551.2866 | 551.2866 | 551.2866 | 551.2866 | 551.2866 | 551.2866 | 551.2866 | 551.2866
| 3896.7004 | 10644.5384 | Net benefit | 0 | 0 | -59.5447 | 6.7878 | 17.0616 | 96.7789 | 114.733 | 133.9055 | 157.8271 | 182.6475 | 214.0008 | 289.8001 | 275.3154 | 404.1677 | 550.6911 | 550.6911 | 550.6911 | 550.6911 | 550.6911 | 550.6911 | 550.6911 | 550.6911 | 550.6911 | 550.6911 | 550.6911 | 550.6911 | 550.6911 | 550.6911 | 550.6911 | 550.6911
|  |  | EUE Value ($m, real $2024) | 1.6512 | 63.5377 | 244.6069 | 272.7599 | 340.9848 | 337.8827 | 461.5237 | 499.9601 | 538.5852 | 544.2706 | 545.5703 | 556.3898 | 497.6492 | 540.2193 | 575.9283 | 575.9283 | 575.9283 | 575.9283 | 575.9283 | 575.9283 | 575.9283 | 575.9283 | 575.9283 | 575.9283 | 575.9283 | 575.9283 | 575.9283 | 575.9283 | 575.9283 | 575.9283
|  |  | Annualised capex | 0 | 0 | 3.2564 | 3.2564 | 3.2564 | 3.2564 | 3.2564 | 3.2564 | 3.2564 | 3.2564 | 3.2564 | 3.2564 | 3.2564 | 3.2564 | 3.2564 | 3.2564 | 3.2564 | 3.2564 | 3.2564 | 3.2564 | 3.2564 | 3.2564 | 3.2564 | 3.2564 | 3.2564 | 3.2564 | 3.2564 | 3.2564 | 3.2564 | 3.2564
|  |  | Annualised cost (capex+opex) | 0 | 0 | 3.2564 | 3.8518 | 3.8518 | 3.8518 | 3.8518 | 3.8518 | 3.8518 | 3.8518 | 3.8518 | 3.8518 | 3.8518 | 3.8518 | 3.8518 | 3.8518 | 3.8518 | 3.8518 | 3.8518 | 3.8518 | 3.8518 | 3.8518 | 3.8518 | 3.8518 | 3.8518 | 3.8518 | 3.8518 | 3.8518 | 3.8518 | 3.8518
|  |  | Optimal timing (interim calc) | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  |  | Optimal timing | - | - | - | Yes | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
[11 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19
Adjusted For Optimal Timing: | 53.4373 | 59.5447 | Capex | 0 | 0 | 59.5447 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 7.3811 | 16.0771 | Opex | 0 | 0 | 0 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545
| 3957.5188 | 10720.1602 | Reduction in unserved energy | 0 | 0 | 0 | 7.3832 | 17.6571 | 97.3743 | 115.3284 | 134.5009 | 158.4225 | 183.2429 | 214.5962 | 290.3955 | 275.9108 | 404.7631 | 551.2866 | 551.2866 | 551.2866 | 551.2866 | 551.2866 | 551.2866 | 551.2866 | 551.2866 | 551.2866 | 551.2866 | 551.2866 | 551.2866 | 551.2866 | 551.2866 | 551.2866 | 551.2866
| 3896.7004 | 10644.5384 | Net benefit | 0 | 0 | -59.5447 | 6.7878 | 17.0616 | 96.7789 | 114.733 | 133.9055 | 157.8271 | 182.6475 | 214.0008 | 289.8001 | 275.3154 | 404.1677 | 550.6911 | 550.6911 | 550.6911 | 550.6911 | 550.6911 | 550.6911 | 550.6911 | 550.6911 | 550.6911 | 550.6911 | 550.6911 | 550.6911 | 550.6911 | 550.6911 | 550.6911 | 550.6911
Option 5
Determining Optimal Timing: | Discounted | Undiscounted
| 49.9911 | 55.7046 | Capex | 0 | 0 | 55.7046 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 6.9051 | 15.0402 | Opex | 0 | 0 | 0 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705
| 8271.1183 | 19740.5195 | Reduction in unserved energy | 0 | 0 | 0 | 246.1712 | 296.8205 | 426.3294 | 559.8323 | 606.6813 | 653.6745 | 665.0937 | 675.8089 | 716.8324 | 643.6869 | 741.0362 | 844.2845 | 844.2845 | 844.2845 | 844.2845 | 844.2845 | 844.2845 | 844.2845 | 844.2845 | 844.2845 | 844.2845 | 844.2845 | 844.2845 | 844.2845 | 844.2845 | 844.2845 | 844.2845
| 8214.2222 | 19669.7746 | Net benefit | 0 | 0 | -55.7046 | 245.6142 | 296.2634 | 425.7724 | 559.2752 | 606.1243 | 653.1174 | 664.5367 | 675.2518 | 716.2753 | 643.1299 | 740.4792 | 843.7275 | 843.7275 | 843.7275 | 843.7275 | 843.7275 | 843.7275 | 843.7275 | 843.7275 | 843.7275 | 843.7275 | 843.7275 | 843.7275 | 843.7275 | 843.7275 | 843.7275 | 843.7275
|  |  | EUE Value ($m, real $2024) | 1.6512 | 63.5377 | 244.6069 | 33.9719 | 61.8214 | 8.9276 | 17.0199 | 27.7797 | 43.3333 | 62.4198 | 84.3576 | 129.9529 | 129.8731 | 203.9462 | 282.9304 | 282.9304 | 282.9304 | 282.9304 | 282.9304 | 282.9304 | 282.9304 | 282.9304 | 282.9304 | 282.9304 | 282.9304 | 282.9304 | 282.9304 | 282.9304 | 282.9304 | 282.9304
|  |  | Annualised capex | 0 | 0 | 3.0464 | 3.0464 | 3.0464 | 3.0464 | 3.0464 | 3.0464 | 3.0464 | 3.0464 | 3.0464 | 3.0464 | 3.0464 | 3.0464 | 3.0464 | 3.0464 | 3.0464 | 3.0464 | 3.0464 | 3.0464 | 3.0464 | 3.0464 | 3.0464 | 3.0464 | 3.0464 | 3.0464 | 3.0464 | 3.0464 | 3.0464 | 3.0464
|  |  | Annualised cost (capex+opex) | 0 | 0 | 3.0464 | 3.6034 | 3.6034 | 3.6034 | 3.6034 | 3.6034 | 3.6034 | 3.6034 | 3.6034 | 3.6034 | 3.6034 | 3.6034 | 3.6034 | 3.6034 | 3.6034 | 3.6034 | 3.6034 | 3.6034 | 3.6034 | 3.6034 | 3.6034 | 3.6034 | 3.6034 | 3.6034 | 3.6034 | 3.6034 | 3.6034 | 3.6034
|  |  | Optimal timing (interim calc) | 0 | 0 | 0 | 1 | 1 | 1 | 1 | [19 empty] | 1 | 1 | 1 | 1 | bar: 1 to 19
|  |  | Optimal timing | - | - | - | Yes | - | - | - | [19 empty] | - | - | - | - | bar: 1 to 19
Adjusted For Optimal Timing: | 49.9911 | 55.7046 | Capex | 0 | 0 | 55.7046 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 6.9051 | 15.0402 | Opex | 0 | 0 | 0 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705
| 8271.1183 | 19740.5195 | Reduction in unserved energy | 0 | 0 | 0 | 246.1712 | 296.8205 | 426.3294 | 559.8323 | 606.6813 | 653.6745 | 665.0937 | 675.8089 | 716.8324 | 643.6869 | 741.0362 | 844.2845 | 844.2845 | 844.2845 | 844.2845 | 844.2845 | 844.2845 | 844.2845 | 844.2845 | 844.2845 | 844.2845 | 844.2845 | 844.2845 | 844.2845 | 844.2845 | 844.2845 | 844.2845
| 8214.2222 | 19669.7746 | Net benefit | 0 | 0 | -55.7046 | 245.6142 | 296.2634 | 425.7724 | 559.2752 | 606.1243 | 653.1174 | 664.5367 | 675.2518 | 716.2753 | 643.1299 | 740.4792 | 843.7275 | 843.7275 | 843.7275 | 843.7275 | 843.7275 | 843.7275 | 843.7275 | 843.7275 | 843.7275 | 843.7275 | 843.7275 | 843.7275 | 843.7275 | 843.7275 | 843.7275 | 843.7275
Option 6
Determining Optimal Timing: | Discounted | Undiscounted
| 61.1918 | 68.1854 | Capex | 0 | 0 | 68.1854 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 8.4522 | 18.4101 | Opex | 0 | 0 | 0 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185
| 9860.9128 | 24144.9965 | Reduction in unserved energy | 0 | 0 | 0 | 245.4301 | 355.3978 | 431.5335 | 572.477 | 629.3139 | 690.7269 | 719.8983 | 750.2617 | 831.5539 | 758.5423 | 916.26 | 1077.7251 | 1077.7251 | 1077.7251 | 1077.7251 | 1077.7251 | 1077.7251 | 1077.7251 | 1077.7251 | 1077.7251 | 1077.7251 | 1077.7251 | 1077.7251 | 1077.7251 | 1077.7251 | 1077.7251 | 1077.7251
| 9791.2688 | 24058.401 | Net benefit | 0 | 0 | -68.1854 | 244.7482 | 354.7159 | 430.8517 | 571.7951 | 628.6321 | 690.045 | 719.2164 | 749.5799 | 830.872 | 757.8604 | 915.5782 | 1077.0432 | 1077.0432 | 1077.0432 | 1077.0432 | 1077.0432 | 1077.0432 | 1077.0432 | 1077.0432 | 1077.0432 | 1077.0432 | 1077.0432 | 1077.0432 | 1077.0432 | 1077.0432 | 1077.0432 | 1077.0432
|  |  | EUE Value ($m, real $2024) | 1.6512 | 63.5377 | 244.6069 | 34.7131 | 3.2441 | 3.7235 | 4.3752 | 5.1471 | 6.2809 | 7.6153 | 9.9048 | 15.2313 | 15.0177 | 28.7224 | 49.4898 | 49.4898 | 49.4898 | 49.4898 | 49.4898 | 49.4898 | 49.4898 | 49.4898 | 49.4898 | 49.4898 | 49.4898 | 49.4898 | 49.4898 | 49.4898 | 49.4898 | 49.4898
|  |  | Annualised capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Annualised cost (capex+opex) | 0 | 0 | 0 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185
|  |  | Optimal timing (interim calc) | 0 | 0 | 0 | 1 | 1 | 1 | 1 | [19 empty] | 1 | 1 | 1 | 1 | bar: 1 to 19
|  |  | Optimal timing | - | - | - | Yes | - | - | - | [19 empty] | - | - | - | - | bar: 1 to 19
Adjusted For Optimal Timing: | 61.1918 | 68.1854 | Capex | 0 | 0 | 68.1854 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 8.4522 | 18.4101 | Opex | 0 | 0 | 0 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185
| 9860.9128 | 24144.9965 | Reduction in unserved energy | 0 | 0 | 0 | 245.4301 | 355.3978 | 431.5335 | 572.477 | 629.3139 | 690.7269 | 719.8983 | 750.2617 | 831.5539 | 758.5423 | 916.26 | 1077.7251 | 1077.7251 | 1077.7251 | 1077.7251 | 1077.7251 | 1077.7251 | 1077.7251 | 1077.7251 | 1077.7251 | 1077.7251 | 1077.7251 | 1077.7251 | 1077.7251 | 1077.7251 | 1077.7251 | 1077.7251
| 9791.2688 | 24058.401 | Net benefit | 0 | 0 | -68.1854 | 244.7482 | 354.7159 | 430.8517 | 571.7951 | 628.6321 | 690.045 | 719.2164 | 749.5799 | 830.872 | 757.8604 | 915.5782 | 1077.0432 | 1077.0432 | 1077.0432 | 1077.0432 | 1077.0432 | 1077.0432 | 1077.0432 | 1077.0432 | 1077.0432 | 1077.0432 | 1077.0432 | 1077.0432 | 1077.0432 | 1077.0432 | 1077.0432 | 1077.0432
Option 7
Determining Optimal Timing: | Discounted | Undiscounted
| 33.225 | 37.0224 | Capex | 0 | 0 | 37.0224 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 4.5893 | 9.996 | Opex | 0 | 0 | 0 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022
| 8159.407 | 19363.2719 | Reduction in unserved energy | 0 | 0 | 0 | 243.3558 | 350.523 | 422.7775 | 555.8733 | 602.2977 | 648.8728 | 659.8322 | 669.912 | 709.7517 | 635.9952 | 729.0818 | 820.9374 | 820.9374 | 820.9374 | 820.9374 | 820.9374 | 820.9374 | 820.9374 | 820.9374 | 820.9374 | 820.9374 | 820.9374 | 820.9374 | 820.9374 | 820.9374 | 820.9374 | 820.9374
| 8121.5928 | 19316.2535 | Net benefit | 0 | 0 | -37.0224 | 242.9856 | 350.1528 | 422.4073 | 555.503 | 601.9274 | 648.5025 | 659.462 | 669.5418 | 709.3814 | 635.625 | 728.7116 | 820.5672 | 820.5672 | 820.5672 | 820.5672 | 820.5672 | 820.5672 | 820.5672 | 820.5672 | 820.5672 | 820.5672 | 820.5672 | 820.5672 | 820.5672 | 820.5672 | 820.5672 | 820.5672
|  |  | EUE Value ($m, real $2024) | 1.6512 | 63.5377 | 244.6069 | 36.7873 | 8.1188 | 12.4795 | 20.9789 | 32.1633 | 48.135 | 67.6813 | 90.2545 | 137.0336 | 137.5648 | 215.9006 | 306.2774 | 306.2774 | 306.2774 | 306.2774 | 306.2774 | 306.2774 | 306.2774 | 306.2774 | 306.2774 | 306.2774 | 306.2774 | 306.2774 | 306.2774 | 306.2774 | 306.2774 | 306.2774
|  |  | Annualised capex | 0 | 0 | 2.0247 | 2.0247 | 2.0247 | 2.0247 | 2.0247 | 2.0247 | 2.0247 | 2.0247 | 2.0247 | 2.0247 | 2.0247 | 2.0247 | 2.0247 | 2.0247 | 2.0247 | 2.0247 | 2.0247 | 2.0247 | 2.0247 | 2.0247 | 2.0247 | 2.0247 | 2.0247 | 2.0247 | 2.0247 | 2.0247 | 2.0247 | 2.0247
|  |  | Annualised cost (capex+opex) | 0 | 0 | 2.0247 | 2.3949 | 2.3949 | 2.3949 | 2.3949 | 2.3949 | 2.3949 | 2.3949 | 2.3949 | 2.3949 | 2.3949 | 2.3949 | 2.3949 | 2.3949 | 2.3949 | 2.3949 | 2.3949 | 2.3949 | 2.3949 | 2.3949 | 2.3949 | 2.3949 | 2.3949 | 2.3949 | 2.3949 | 2.3949 | 2.3949 | 2.3949
|  |  | Optimal timing (interim calc) | 0 | 0 | 0 | 1 | 1 | 1 | 1 | [19 empty] | 1 | 1 | 1 | 1 | bar: 1 to 19
|  |  | Optimal timing | - | - | - | Yes | - | - | - | [19 empty] | - | - | - | - | bar: 1 to 19
Adjusted For Optimal Timing: | 33.225 | 37.0224 | Capex | 0 | 0 | 37.0224 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 4.5893 | 9.996 | Opex | 0 | 0 | 0 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022
| 8159.407 | 19363.2719 | Reduction in unserved energy | 0 | 0 | 0 | 243.3558 | 350.523 | 422.7775 | 555.8733 | 602.2977 | 648.8728 | 659.8322 | 669.912 | 709.7517 | 635.9952 | 729.0818 | 820.9374 | 820.9374 | 820.9374 | 820.9374 | 820.9374 | 820.9374 | 820.9374 | 820.9374 | 820.9374 | 820.9374 | 820.9374 | 820.9374 | 820.9374 | 820.9374 | 820.9374 | 820.9374
| 8121.5928 | 19316.2535 | Net benefit | 0 | 0 | -37.0224 | 242.9856 | 350.1528 | 422.4073 | 555.503 | 601.9274 | 648.5025 | 659.462 | 669.5418 | 709.3814 | 635.625 | 728.7116 | 820.5672 | 820.5672 | 820.5672 | 820.5672 | 820.5672 | 820.5672 | 820.5672 | 820.5672 | 820.5672 | 820.5672 | 820.5672 | 820.5672 | 820.5672 | 820.5672 | 820.5672 | 820.5672
Option 8
Determining Optimal Timing: | Discounted | Undiscounted
| 47.6017 | 53.0422 | Capex | 0 | 0 | 53.0422 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 6.5751 | 14.3214 | Opex | 0 | 0 | 0 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042
| 3895.9086 | 10454.7463 | Reduction in unserved energy | 0 | 0 | 0 | 7.2706 | 74.2475 | 97.0418 | 114.955 | 134.0751 | 157.9255 | 182.6308 | 213.6868 | 288.2154 | 273.0438 | 397.4578 | 532.1373 | 532.1373 | 532.1373 | 532.1373 | 532.1373 | 532.1373 | 532.1373 | 532.1373 | 532.1373 | 532.1373 | 532.1373 | 532.1373 | 532.1373 | 532.1373 | 532.1373 | 532.1373
| 3841.7318 | 10387.3827 | Net benefit | 0 | 0 | -53.0422 | 6.7401 | 73.7171 | 96.5114 | 114.4246 | 133.5446 | 157.3951 | 182.1004 | 213.1564 | 287.685 | 272.5134 | 396.9274 | 531.6068 | 531.6068 | 531.6068 | 531.6068 | 531.6068 | 531.6068 | 531.6068 | 531.6068 | 531.6068 | 531.6068 | 531.6068 | 531.6068 | 531.6068 | 531.6068 | 531.6068 | 531.6068
|  |  | EUE Value ($m, real $2024) | 1.6512 | 63.5377 | 244.6069 | 272.8726 | 284.3944 | 338.2152 | 461.8971 | 500.3859 | 539.0823 | 544.8827 | 546.4797 | 558.5698 | 500.5162 | 547.5246 | 595.0776 | 595.0776 | 595.0776 | 595.0776 | 595.0776 | 595.0776 | 595.0776 | 595.0776 | 595.0776 | 595.0776 | 595.0776 | 595.0776 | 595.0776 | 595.0776 | 595.0776 | 595.0776
|  |  | Annualised capex | 0 | 0 | 2.9008 | 2.9008 | 2.9008 | 2.9008 | 2.9008 | 2.9008 | 2.9008 | 2.9008 | 2.9008 | 2.9008 | 2.9008 | 2.9008 | 2.9008 | 2.9008 | 2.9008 | 2.9008 | 2.9008 | 2.9008 | 2.9008 | 2.9008 | 2.9008 | 2.9008 | 2.9008 | 2.9008 | 2.9008 | 2.9008 | 2.9008 | 2.9008
|  |  | Annualised cost (capex+opex) | 0 | 0 | 2.9008 | 3.4312 | 3.4312 | 3.4312 | 3.4312 | 3.4312 | 3.4312 | 3.4312 | 3.4312 | 3.4312 | 3.4312 | 3.4312 | 3.4312 | 3.4312 | 3.4312 | 3.4312 | 3.4312 | 3.4312 | 3.4312 | 3.4312 | 3.4312 | 3.4312 | 3.4312 | 3.4312 | 3.4312 | 3.4312 | 3.4312 | 3.4312
|  |  | Optimal timing (interim calc) | 0 | 0 | 0 | 1 | 1 | 1 | 1 | [19 empty] | 1 | 1 | 1 | 1 | bar: 1 to 19
|  |  | Optimal timing | - | - | - | Yes | - | - | - | [19 empty] | - | - | - | - | bar: 1 to 19
Adjusted For Optimal Timing: | 47.6017 | 53.0422 | Capex | 0 | 0 | 53.0422 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 6.5751 | 14.3214 | Opex | 0 | 0 | 0 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042
| 3895.9086 | 10454.7463 | Reduction in unserved energy | 0 | 0 | 0 | 7.2706 | 74.2475 | 97.0418 | 114.955 | 134.0751 | 157.9255 | 182.6308 | 213.6868 | 288.2154 | 273.0438 | 397.4578 | 532.1373 | 532.1373 | 532.1373 | 532.1373 | 532.1373 | 532.1373 | 532.1373 | 532.1373 | 532.1373 | 532.1373 | 532.1373 | 532.1373 | 532.1373 | 532.1373 | 532.1373 | 532.1373
| 3841.7318 | 10387.3827 | Net benefit | 0 | 0 | -53.0422 | 6.7401 | 73.7171 | 96.5114 | 114.4246 | 133.5446 | 157.3951 | 182.1004 | 213.1564 | 287.685 | 272.5134 | 396.9274 | 531.6068 | 531.6068 | 531.6068 | 531.6068 | 531.6068 | 531.6068 | 531.6068 | 531.6068 | 531.6068 | 531.6068 | 531.6068 | 531.6068 | 531.6068 | 531.6068 | 531.6068 | 531.6068
Option 9
Determining Optimal Timing: | Discounted | Undiscounted
| 44.1555 | 49.2021 | Capex | 0 | 0 | 49.2021 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 6.0991 | 13.2846 | Opex | 0 | 0 | 0 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202
| 8225.4387 | 19521.9391 | Reduction in unserved energy | 0 | 0 | 0 | 246.0217 | 353.4591 | 426.0242 | 559.4975 | 606.3019 | 653.2316 | 664.5636 | 675.1171 | 715.3784 | 641.9165 | 735.5051 | 827.8076 | 827.8076 | 827.8076 | 827.8076 | 827.8076 | 827.8076 | 827.8076 | 827.8076 | 827.8076 | 827.8076 | 827.8076 | 827.8076 | 827.8076 | 827.8076 | 827.8076 | 827.8076
| 8175.1841 | 19459.4524 | Net benefit | 0 | 0 | -49.2021 | 245.5297 | 352.9671 | 425.5322 | 559.0055 | 605.8099 | 652.7396 | 664.0715 | 674.6251 | 714.8864 | 641.4245 | 735.0131 | 827.3156 | 827.3156 | 827.3156 | 827.3156 | 827.3156 | 827.3156 | 827.3156 | 827.3156 | 827.3156 | 827.3156 | 827.3156 | 827.3156 | 827.3156 | 827.3156 | 827.3156 | 827.3156
|  |  | EUE Value ($m, real $2024) | 1.6512 | 63.5377 | 244.6069 | 34.1215 | 5.1827 | 9.2328 | 17.3546 | 28.159 | 43.7761 | 62.95 | 85.0494 | 131.4069 | 131.6435 | 209.4773 | 299.4072 | 299.4072 | 299.4072 | 299.4072 | 299.4072 | 299.4072 | 299.4072 | 299.4072 | 299.4072 | 299.4072 | 299.4072 | 299.4072 | 299.4072 | 299.4072 | 299.4072 | 299.4072
|  |  | Annualised capex | 0 | 0 | 2.6908 | 2.6908 | 2.6908 | 2.6908 | 2.6908 | 2.6908 | 2.6908 | 2.6908 | 2.6908 | 2.6908 | 2.6908 | 2.6908 | 2.6908 | 2.6908 | 2.6908 | 2.6908 | 2.6908 | 2.6908 | 2.6908 | 2.6908 | 2.6908 | 2.6908 | 2.6908 | 2.6908 | 2.6908 | 2.6908 | 2.6908 | 2.6908
|  |  | Annualised cost (capex+opex) | 0 | 0 | 2.6908 | 3.1828 | 3.1828 | 3.1828 | 3.1828 | 3.1828 | 3.1828 | 3.1828 | 3.1828 | 3.1828 | 3.1828 | 3.1828 | 3.1828 | 3.1828 | 3.1828 | 3.1828 | 3.1828 | 3.1828 | 3.1828 | 3.1828 | 3.1828 | 3.1828 | 3.1828 | 3.1828 | 3.1828 | 3.1828 | 3.1828 | 3.1828
|  |  | Optimal timing (interim calc) | 0 | 0 | 0 | 1 | 1 | 1 | 1 | [19 empty] | 1 | 1 | 1 | 1 | bar: 1 to 19
|  |  | Optimal timing | - | - | - | Yes | - | - | - | [19 empty] | - | - | - | - | bar: 1 to 19
Adjusted For Optimal Timing: | 44.1555 | 49.2021 | Capex | 0 | 0 | 49.2021 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 6.0991 | 13.2846 | Opex | 0 | 0 | 0 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202
| 8225.4387 | 19521.9391 | Reduction in unserved energy | 0 | 0 | 0 | 246.0217 | 353.4591 | 426.0242 | 559.4975 | 606.3019 | 653.2316 | 664.5636 | 675.1171 | 715.3784 | 641.9165 | 735.5051 | 827.8076 | 827.8076 | 827.8076 | 827.8076 | 827.8076 | 827.8076 | 827.8076 | 827.8076 | 827.8076 | 827.8076 | 827.8076 | 827.8076 | 827.8076 | 827.8076 | 827.8076 | 827.8076
| 8175.1841 | 19459.4524 | Net benefit | 0 | 0 | -49.2021 | 245.5297 | 352.9671 | 425.5322 | 559.0055 | 605.8099 | 652.7396 | 664.0715 | 674.6251 | 714.8864 | 641.4245 | 735.0131 | 827.3156 | 827.3156 | 827.3156 | 827.3156 | 827.3156 | 827.3156 | 827.3156 | 827.3156 | 827.3156 | 827.3156 | 827.3156 | 827.3156 | 827.3156 | 827.3156 | 827.3156 | 827.3156
Option 10
Determining Optimal Timing: | Discounted | Undiscounted
| 0 | 0 | Capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 6375.8942 | 15208.189 | Opex | 0.48285 | 57.8283 | 189.4866 | 207.6844 | 245.4848 | 279.2209 | 339.624 | 384.4625 | 426.7802 | 445.1879 | 469.6214 | 502.6026 | 486.2654 | 573.3683 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055
| 10484.0735 | 25380.6075 | Reduction in unserved energy | 1.6542 | 63.5377 | 244.6069 | 280.1431 | 358.6419 | 435.257 | 576.8522 | 634.461 | 697.0077 | 727.5135 | 760.1665 | 846.7852 | 773.56 | 944.9824 | 1127.2149 | 1127.2149 | 1127.2149 | 1127.2149 | 1127.2149 | 1127.2149 | 1127.2149 | 1127.2149 | 1127.2149 | 1127.2149 | 1127.2149 | 1127.2149 | 1127.2149 | 1127.2149 | 1127.2149 | 1127.2149
| 4108.1793 | 10172.4185 | Net benefit | 1.1714 | 5.7094 | 55.1203 | 72.4587 | 113.1571 | 156.0362 | 237.2282 | 249.9985 | 270.2275 | 282.3256 | 290.5451 | 344.1826 | 287.2946 | 371.6141 | 464.7093 | 464.7093 | 464.7093 | 464.7093 | 464.7093 | 464.7093 | 464.7093 | 464.7093 | 464.7093 | 464.7093 | 464.7093 | 464.7093 | 464.7093 | 464.7093 | 464.7093 | 464.7093
|  |  | EUE Value ($m, real $2024) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Annualised capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Annualised cost (capex+opex) | 0.48285 | 57.8283 | 189.4866 | 207.6844 | 245.4848 | 279.2209 | 339.624 | 384.4625 | 426.7802 | 445.1879 | 469.6214 | 502.6026 | 486.2654 | 573.3683 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055
|  |  | Optimal timing (interim calc) | 1 | 1 | 1 | 1 | 1 | 1 | 1 | [19 empty] | 1 | 1 | 1 | 1 | bar: 1 to 19
|  |  | Optimal timing | Yes | - | - | - | - | - | - | [19 empty] | - | - | - | - | bar: 1 to 19
Adjusted For Optimal Timing: | 0 | 0 | Capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 6375.8942 | 15208.189 | Opex | 0.48285 | 57.8283 | 189.4866 | 207.6844 | 245.4848 | 279.2209 | 339.624 | 384.4625 | 426.7802 | 445.1879 | 469.6214 | 502.6026 | 486.2654 | 573.3683 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055
| 10484.0735 | 25380.6075 | Reduction in unserved energy | 1.6542 | 63.5377 | 244.6069 | 280.1431 | 358.6419 | 435.257 | 576.8522 | 634.461 | 697.0077 | 727.5135 | 760.1665 | 846.7852 | 773.56 | 944.9824 | 1127.2149 | 1127.2149 | 1127.2149 | 1127.2149 | 1127.2149 | 1127.2149 | 1127.2149 | 1127.2149 | 1127.2149 | 1127.2149 | 1127.2149 | 1127.2149 | 1127.2149 | 1127.2149 | 1127.2149 | 1127.2149
| 4108.1793 | 10172.4185 | Net benefit | 1.1714 | 5.7094 | 55.1203 | 72.4587 | 113.1571 | 156.0362 | 237.2282 | 249.9985 | 270.2275 | 282.3256 | 290.5451 | 344.1826 | 287.2946 | 371.6141 | 464.7093 | 464.7093 | 464.7093 | 464.7093 | 464.7093 | 464.7093 | 464.7093 | 464.7093 | 464.7093 | 464.7093 | 464.7093 | 464.7093 | 464.7093 | 464.7093 | 464.7093 | 464.7093

## 3.2.10 NPV (High Tx PoF)
Economic inputs and assumptions
Scenario | Discount rate | Central
| Cost | Central
| VCR | Central
|  | Central | Lower bound | Upper bound
| Discount rate | 5.56% | 4.11% | 7%
| Cost | 100% | 80% | 120%
| VCR | 100% | 80% | 120%
Asset life for calculating annualised capex (years) | Option 1 | 45
| Option 2 | 45
| Option 3 | 45
| Option 4 | 45
| Option 5 | 45
| Option 6 | 45
| Option 7 | 45
| Option 8 | 45
| Option 9 | 45
| Option 10 | 45
|  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30
|  |  |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Outputs | bar: 3 FY27; 7 FY31
Option 1
| Discounted | Undiscounted
| 0 | 0 | Capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Opex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Reduction in unserved energy | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | Net benefit | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | EUE Value ($m, real $2024) | 4.9775 | 67.3256 | 249.6646 | 286.0292 | 365.3762 | 442.9683 | 585.7817 | 644.6681 | 708.5723 | 740.4517 | 774.5661 | 863.0572 | 791.0227 | 965.4525 | 1150.6051 | 1150.6051 | 1150.6051 | 1150.6051 | 1150.6051 | 1150.6051 | 1150.6051 | 1150.6051 | 1150.6051 | 1150.6051 | 1150.6051 | 1150.6051 | 1150.6051 | 1150.6051 | 1150.6051 | 1150.6051
Option 2
Determining Optimal Timing: | Discounted | Undiscounted
| 64.7091 | 72.1048 | Capex | 0 | 0 | 72.1048 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 8.9381 | 19.4683 | Opex | 0 | 0 | 0 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105
| 10008.9983 | 24655.3168 | Reduction in unserved energy | 0 | 0 | 0 | 245.5321 | 298.3727 | 432.6839 | 574.0058 | 631.2838 | 693.2761 | 723.2074 | 754.9187 | 839.595 | 766.9229 | 932.3046 | 1110.2009 | 1110.2009 | 1110.2009 | 1110.2009 | 1110.2009 | 1110.2009 | 1110.2009 | 1110.2009 | 1110.2009 | 1110.2009 | 1110.2009 | 1110.2009 | 1110.2009 | 1110.2009 | 1110.2009 | 1110.2009
| 9935.3512 | 24563.7437 | Net benefit | 0 | 0 | -72.1048 | 244.8111 | 297.6516 | 431.9628 | 573.2848 | 630.5628 | 692.555 | 722.4864 | 754.1977 | 838.8739 | 766.2019 | 931.5836 | 1109.4798 | 1109.4798 | 1109.4798 | 1109.4798 | 1109.4798 | 1109.4798 | 1109.4798 | 1109.4798 | 1109.4798 | 1109.4798 | 1109.4798 | 1109.4798 | 1109.4798 | 1109.4798 | 1109.4798 | 1109.4798
|  |  | EUE Value ($m, real $2024) | 4.9683 | 67.3256 | 249.6646 | 40.497 | 67.0035 | 10.2844 | 11.7759 | 13.3843 | 15.2963 | 17.2443 | 19.6473 | 23.4622 | 24.0997 | 33.1479 | 40.4042 | 40.4042 | 40.4042 | 40.4042 | 40.4042 | 40.4042 | 40.4042 | 40.4042 | 40.4042 | 40.4042 | 40.4042 | 40.4042 | 40.4042 | 40.4042 | 40.4042 | 40.4042
|  |  | Annualised capex | 0 | 0 | 3.9433 | 3.9433 | 3.9433 | 3.9433 | 3.9433 | 3.9433 | 3.9433 | 3.9433 | 3.9433 | 3.9433 | 3.9433 | 3.9433 | 3.9433 | 3.9433 | 3.9433 | 3.9433 | 3.9433 | 3.9433 | 3.9433 | 3.9433 | 3.9433 | 3.9433 | 3.9433 | 3.9433 | 3.9433 | 3.9433 | 3.9433 | 3.9433
|  |  | Annualised cost (capex+opex) | 0 | 0 | 3.9433 | 4.6643 | 4.6643 | 4.6643 | 4.6643 | 4.6643 | 4.6643 | 4.6643 | 4.6643 | 4.6643 | 4.6643 | 4.6643 | 4.6643 | 4.6643 | 4.6643 | 4.6643 | 4.6643 | 4.6643 | 4.6643 | 4.6643 | 4.6643 | 4.6643 | 4.6643 | 4.6643 | 4.6643 | 4.6643 | 4.6643 | 4.6643
|  |  | Optimal timing (interim calc) | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  |  | Optimal timing | - | - | - | Yes | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Adjusted For Optimal Timing: | 64.7091 | 72.1048 | Capex | 0 | 0 | 72.1048 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 8.9381 | 19.4683 | Opex | 0 | 0 | 0 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105 | 0.72105
| 10008.9983 | 24655.3168 | Reduction in unserved energy | 0 | 0 | 0 | 245.5321 | 298.3727 | 432.6839 | 574.0058 | 631.2838 | 693.2761 | 723.2074 | 754.9187 | 839.595 | 766.9229 | 932.3046 | 1110.2009 | 1110.2009 | 1110.2009 | 1110.2009 | 1110.2009 | 1110.2009 | 1110.2009 | 1110.2009 | 1110.2009 | 1110.2009 | 1110.2009 | 1110.2009 | 1110.2009 | 1110.2009 | 1110.2009 | 1110.2009
| 9935.3512 | 24563.7437 | Net benefit | 0 | 0 | -72.1048 | 244.8111 | 297.6516 | 431.9628 | 573.2848 | 630.5628 | 692.555 | 722.4864 | 754.1977 | 838.8739 | 766.2019 | 931.5836 | 1109.4798 | 1109.4798 | 1109.4798 | 1109.4798 | 1109.4798 | 1109.4798 | 1109.4798 | 1109.4798 | 1109.4798 | 1109.4798 | 1109.4798 | 1109.4798 | 1109.4798 | 1109.4798 | 1109.4798 | 1109.4798
Option 3
Determining Optimal Timing: | Discounted | Undiscounted
| 39.0606 | 43.5248 | Capex | 0 | 0 | 43.5248 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 5.3953 | 11.7517 | Opex | 0 | 0 | 0 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525
| 8263.1018 | 19735.512 | Reduction in unserved energy | 0 | 0 | 0 | 244.0013 | 294.6426 | 424.2404 | 557.8044 | 604.7544 | 651.9928 | 663.6019 | 674.4516 | 715.8495 | 642.6647 | 740.9992 | 845.0318 | 845.0318 | 845.0318 | 845.0318 | 845.0318 | 845.0318 | 845.0318 | 845.0318 | 845.0318 | 845.0318 | 845.0318 | 845.0318 | 845.0318 | 845.0318 | 845.0318 | 845.0318
| 8218.6459 | 19680.2355 | Net benefit | 0 | 0 | -43.5248 | 243.566 | 294.2073 | 423.8052 | 557.3692 | 604.3191 | 651.5576 | 663.1667 | 674.0163 | 715.4142 | 642.2294 | 740.564 | 844.5966 | 844.5966 | 844.5966 | 844.5966 | 844.5966 | 844.5966 | 844.5966 | 844.5966 | 844.5966 | 844.5966 | 844.5966 | 844.5966 | 844.5966 | 844.5966 | 844.5966 | 844.5966
|  |  | EUE Value ($m, real $2024) | 4.9683 | 67.3256 | 249.6646 | 42.0279 | 70.7336 | 18.7279 | 27.9773 | 39.9138 | 56.5795 | 76.8497 | 100.1145 | 147.2077 | 148.358 | 224.4532 | 305.5733 | 305.5733 | 305.5733 | 305.5733 | 305.5733 | 305.5733 | 305.5733 | 305.5733 | 305.5733 | 305.5733 | 305.5733 | 305.5733 | 305.5733 | 305.5733 | 305.5733 | 305.5733
|  |  | Annualised capex | 0 | 0 | 2.3803 | 2.3803 | 2.3803 | 2.3803 | 2.3803 | 2.3803 | 2.3803 | 2.3803 | 2.3803 | 2.3803 | 2.3803 | 2.3803 | 2.3803 | 2.3803 | 2.3803 | 2.3803 | 2.3803 | 2.3803 | 2.3803 | 2.3803 | 2.3803 | 2.3803 | 2.3803 | 2.3803 | 2.3803 | 2.3803 | 2.3803 | 2.3803
|  |  | Annualised cost (capex+opex) | 0 | 0 | 2.3803 | 2.8155 | 2.8155 | 2.8155 | 2.8155 | 2.8155 | 2.8155 | 2.8155 | 2.8155 | 2.8155 | 2.8155 | 2.8155 | 2.8155 | 2.8155 | 2.8155 | 2.8155 | 2.8155 | 2.8155 | 2.8155 | 2.8155 | 2.8155 | 2.8155 | 2.8155 | 2.8155 | 2.8155 | 2.8155 | 2.8155 | 2.8155
|  |  | Optimal timing (interim calc) | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  |  | Optimal timing | - | - | - | Yes | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Adjusted For Optimal Timing: | 39.0606 | 43.5248 | Capex | 0 | 0 | 43.5248 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 5.3953 | 11.7517 | Opex | 0 | 0 | 0 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525 | 0.43525
| 8263.1018 | 19735.512 | Reduction in unserved energy | 0 | 0 | 0 | 244.0013 | 294.6426 | 424.2404 | 557.8044 | 604.7544 | 651.9928 | 663.6019 | 674.4516 | 715.8495 | 642.6647 | 740.9992 | 845.0318 | 845.0318 | 845.0318 | 845.0318 | 845.0318 | 845.0318 | 845.0318 | 845.0318 | 845.0318 | 845.0318 | 845.0318 | 845.0318 | 845.0318 | 845.0318 | 845.0318 | 845.0318
| 8218.6459 | 19680.2355 | Net benefit | 0 | 0 | -43.5248 | 243.566 | 294.2073 | 423.8052 | 557.3692 | 604.3191 | 651.5576 | 663.1667 | 674.0163 | 715.4142 | 642.2294 | 740.564 | 844.5966 | 844.5966 | 844.5966 | 844.5966 | 844.5966 | 844.5966 | 844.5966 | 844.5966 | 844.5966 | 844.5966 | 844.5966 | 844.5966 | 844.5966 | 844.5966 | 844.5966 | 844.5966
Option 4
Determining Optimal Timing: | Discounted | Undiscounted
| 53.4373 | 59.5447 | Capex | 0 | 0 | 59.5447 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 7.3811 | 16.0771 | Opex | 0 | 0 | 0 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545
| 4023.8558 | 10898.2313 | Reduction in unserved energy | 0 | 0 | 0 | 7.9319 | 18.5108 | 98.5779 | 116.9812 | 136.65 | 161.1831 | 186.5479 | 218.53 | 295.2954 | 281.1721 | 411.8023 | 560.3156 | 560.3156 | 560.3156 | 560.3156 | 560.3156 | 560.3156 | 560.3156 | 560.3156 | 560.3156 | 560.3156 | 560.3156 | 560.3156 | 560.3156 | 560.3156 | 560.3156 | 560.3156
| 3963.0374 | 10822.6096 | Net benefit | 0 | 0 | -59.5447 | 7.3365 | 17.9154 | 97.9824 | 116.3857 | 136.0545 | 160.5876 | 185.9524 | 217.9346 | 294.7 | 280.5766 | 411.2068 | 559.7201 | 559.7201 | 559.7201 | 559.7201 | 559.7201 | 559.7201 | 559.7201 | 559.7201 | 559.7201 | 559.7201 | 559.7201 | 559.7201 | 559.7201 | 559.7201 | 559.7201 | 559.7201
|  |  | EUE Value ($m, real $2024) | 4.9683 | 67.3256 | 249.6646 | 278.0973 | 346.8654 | 344.3904 | 468.8005 | 508.0182 | 547.3893 | 553.9038 | 556.036 | 567.7617 | 509.8506 | 553.6502 | 590.2895 | 590.2895 | 590.2895 | 590.2895 | 590.2895 | 590.2895 | 590.2895 | 590.2895 | 590.2895 | 590.2895 | 590.2895 | 590.2895 | 590.2895 | 590.2895 | 590.2895 | 590.2895
|  |  | Annualised capex | 0 | 0 | 3.2564 | 3.2564 | 3.2564 | 3.2564 | 3.2564 | 3.2564 | 3.2564 | 3.2564 | 3.2564 | 3.2564 | 3.2564 | 3.2564 | 3.2564 | 3.2564 | 3.2564 | 3.2564 | 3.2564 | 3.2564 | 3.2564 | 3.2564 | 3.2564 | 3.2564 | 3.2564 | 3.2564 | 3.2564 | 3.2564 | 3.2564 | 3.2564
|  |  | Annualised cost (capex+opex) | 0 | 0 | 3.2564 | 3.8518 | 3.8518 | 3.8518 | 3.8518 | 3.8518 | 3.8518 | 3.8518 | 3.8518 | 3.8518 | 3.8518 | 3.8518 | 3.8518 | 3.8518 | 3.8518 | 3.8518 | 3.8518 | 3.8518 | 3.8518 | 3.8518 | 3.8518 | 3.8518 | 3.8518 | 3.8518 | 3.8518 | 3.8518 | 3.8518 | 3.8518
|  |  | Optimal timing (interim calc) | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  |  | Optimal timing | - | - | - | Yes | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
[11 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19
Adjusted For Optimal Timing: | 53.4373 | 59.5447 | Capex | 0 | 0 | 59.5447 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 7.3811 | 16.0771 | Opex | 0 | 0 | 0 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545 | 0.59545
| 4023.8558 | 10898.2313 | Reduction in unserved energy | 0 | 0 | 0 | 7.9319 | 18.5108 | 98.5779 | 116.9812 | 136.65 | 161.1831 | 186.5479 | 218.53 | 295.2954 | 281.1721 | 411.8023 | 560.3156 | 560.3156 | 560.3156 | 560.3156 | 560.3156 | 560.3156 | 560.3156 | 560.3156 | 560.3156 | 560.3156 | 560.3156 | 560.3156 | 560.3156 | 560.3156 | 560.3156 | 560.3156
| 3963.0374 | 10822.6096 | Net benefit | 0 | 0 | -59.5447 | 7.3365 | 17.9154 | 97.9824 | 116.3857 | 136.0545 | 160.5876 | 185.9524 | 217.9346 | 294.7 | 280.5766 | 411.2068 | 559.7201 | 559.7201 | 559.7201 | 559.7201 | 559.7201 | 559.7201 | 559.7201 | 559.7201 | 559.7201 | 559.7201 | 559.7201 | 559.7201 | 559.7201 | 559.7201 | 559.7201 | 559.7201
Option 5
Determining Optimal Timing: | Discounted | Undiscounted
| 49.9911 | 55.7046 | Capex | 0 | 0 | 55.7046 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 6.9051 | 15.0402 | Opex | 0 | 0 | 0 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705
| 8460.3933 | 20209.2984 | Reduction in unserved energy | 0 | 0 | 0 | 251.9996 | 303.4517 | 433.9817 | 568.6788 | 616.7687 | 665.066 | 677.7896 | 689.8675 | 732.5408 | 660.445 | 760.2846 | 865.5265 | 865.5265 | 865.5265 | 865.5265 | 865.5265 | 865.5265 | 865.5265 | 865.5265 | 865.5265 | 865.5265 | 865.5265 | 865.5265 | 865.5265 | 865.5265 | 865.5265 | 865.5265
| 8403.4971 | 20138.5536 | Net benefit | 0 | 0 | -55.7046 | 251.4425 | 302.8947 | 433.4247 | 568.1218 | 616.2117 | 664.509 | 677.2326 | 689.3104 | 731.9837 | 659.8879 | 759.7275 | 864.9695 | 864.9695 | 864.9695 | 864.9695 | 864.9695 | 864.9695 | 864.9695 | 864.9695 | 864.9695 | 864.9695 | 864.9695 | 864.9695 | 864.9695 | 864.9695 | 864.9695 | 864.9695
|  |  | EUE Value ($m, real $2024) | 4.9683 | 67.3256 | 249.6646 | 34.0296 | 61.9245 | 8.9865 | 17.1029 | 27.8994 | 43.5063 | 62.662 | 84.6986 | 130.5164 | 130.5777 | 205.1679 | 285.0786 | 285.0786 | 285.0786 | 285.0786 | 285.0786 | 285.0786 | 285.0786 | 285.0786 | 285.0786 | 285.0786 | 285.0786 | 285.0786 | 285.0786 | 285.0786 | 285.0786 | 285.0786
|  |  | Annualised capex | 0 | 0 | 3.0464 | 3.0464 | 3.0464 | 3.0464 | 3.0464 | 3.0464 | 3.0464 | 3.0464 | 3.0464 | 3.0464 | 3.0464 | 3.0464 | 3.0464 | 3.0464 | 3.0464 | 3.0464 | 3.0464 | 3.0464 | 3.0464 | 3.0464 | 3.0464 | 3.0464 | 3.0464 | 3.0464 | 3.0464 | 3.0464 | 3.0464 | 3.0464
|  |  | Annualised cost (capex+opex) | 0 | 0 | 3.0464 | 3.6034 | 3.6034 | 3.6034 | 3.6034 | 3.6034 | 3.6034 | 3.6034 | 3.6034 | 3.6034 | 3.6034 | 3.6034 | 3.6034 | 3.6034 | 3.6034 | 3.6034 | 3.6034 | 3.6034 | 3.6034 | 3.6034 | 3.6034 | 3.6034 | 3.6034 | 3.6034 | 3.6034 | 3.6034 | 3.6034 | 3.6034
|  |  | Optimal timing (interim calc) | 0 | 0 | 0 | 1 | 1 | 1 | 1 | [19 empty] | 1 | 1 | 1 | 1 | bar: 1 to 19
|  |  | Optimal timing | - | - | - | Yes | - | - | - | [19 empty] | - | - | - | - | bar: 1 to 19
Adjusted For Optimal Timing: | 49.9911 | 55.7046 | Capex | 0 | 0 | 55.7046 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 6.9051 | 15.0402 | Opex | 0 | 0 | 0 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705 | 0.55705
| 8460.3933 | 20209.2984 | Reduction in unserved energy | 0 | 0 | 0 | 251.9996 | 303.4517 | 433.9817 | 568.6788 | 616.7687 | 665.066 | 677.7896 | 689.8675 | 732.5408 | 660.445 | 760.2846 | 865.5265 | 865.5265 | 865.5265 | 865.5265 | 865.5265 | 865.5265 | 865.5265 | 865.5265 | 865.5265 | 865.5265 | 865.5265 | 865.5265 | 865.5265 | 865.5265 | 865.5265 | 865.5265
| 8403.4971 | 20138.5536 | Net benefit | 0 | 0 | -55.7046 | 251.4425 | 302.8947 | 433.4247 | 568.1218 | 616.2117 | 664.509 | 677.2326 | 689.3104 | 731.9837 | 659.8879 | 759.7275 | 864.9695 | 864.9695 | 864.9695 | 864.9695 | 864.9695 | 864.9695 | 864.9695 | 864.9695 | 864.9695 | 864.9695 | 864.9695 | 864.9695 | 864.9695 | 864.9695 | 864.9695 | 864.9695
Option 6
Determining Optimal Timing: | Discounted | Undiscounted
| 61.1918 | 68.1854 | Capex | 0 | 0 | 68.1854 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 8.4522 | 18.4101 | Opex | 0 | 0 | 0 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185
| 9907.5616 | 24268.4035 | Reduction in unserved energy | 0 | 0 | 0 | 245.5062 | 356.1623 | 432.5841 | 573.8798 | 631.088 | 692.9424 | 722.5332 | 753.3206 | 835.1853 | 762.5394 | 921.3764 | 1083.8304 | 1083.8304 | 1083.8304 | 1083.8304 | 1083.8304 | 1083.8304 | 1083.8304 | 1083.8304 | 1083.8304 | 1083.8304 | 1083.8304 | 1083.8304 | 1083.8304 | 1083.8304 | 1083.8304 | 1083.8304
| 9837.9176 | 24181.808 | Net benefit | 0 | 0 | -68.1854 | 244.8244 | 355.4805 | 431.9023 | 573.1979 | 630.4062 | 692.2605 | 721.8514 | 752.6387 | 834.5035 | 761.8575 | 920.6945 | 1083.1485 | 1083.1485 | 1083.1485 | 1083.1485 | 1083.1485 | 1083.1485 | 1083.1485 | 1083.1485 | 1083.1485 | 1083.1485 | 1083.1485 | 1083.1485 | 1083.1485 | 1083.1485 | 1083.1485 | 1083.1485
|  |  | EUE Value ($m, real $2024) | 4.9683 | 67.3256 | 249.6646 | 40.523 | 9.2139 | 10.3841 | 11.9019 | 13.5801 | 15.63 | 17.9185 | 21.2455 | 27.8718 | 28.4833 | 44.0761 | 66.7747 | 66.7747 | 66.7747 | 66.7747 | 66.7747 | 66.7747 | 66.7747 | 66.7747 | 66.7747 | 66.7747 | 66.7747 | 66.7747 | 66.7747 | 66.7747 | 66.7747 | 66.7747
|  |  | Annualised capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Annualised cost (capex+opex) | 0 | 0 | 0 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185
|  |  | Optimal timing (interim calc) | 0 | 0 | 0 | 1 | 1 | 1 | 1 | [19 empty] | 1 | 1 | 1 | 1 | bar: 1 to 19
|  |  | Optimal timing | - | - | - | Yes | - | - | - | [19 empty] | - | - | - | - | bar: 1 to 19
Adjusted For Optimal Timing: | 61.1918 | 68.1854 | Capex | 0 | 0 | 68.1854 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 8.4522 | 18.4101 | Opex | 0 | 0 | 0 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185 | 0.68185
| 9907.5616 | 24268.4035 | Reduction in unserved energy | 0 | 0 | 0 | 245.5062 | 356.1623 | 432.5841 | 573.8798 | 631.088 | 692.9424 | 722.5332 | 753.3206 | 835.1853 | 762.5394 | 921.3764 | 1083.8304 | 1083.8304 | 1083.8304 | 1083.8304 | 1083.8304 | 1083.8304 | 1083.8304 | 1083.8304 | 1083.8304 | 1083.8304 | 1083.8304 | 1083.8304 | 1083.8304 | 1083.8304 | 1083.8304 | 1083.8304
| 9837.9176 | 24181.808 | Net benefit | 0 | 0 | -68.1854 | 244.8244 | 355.4805 | 431.9023 | 573.1979 | 630.4062 | 692.2605 | 721.8514 | 752.6387 | 834.5035 | 761.8575 | 920.6945 | 1083.1485 | 1083.1485 | 1083.1485 | 1083.1485 | 1083.1485 | 1083.1485 | 1083.1485 | 1083.1485 | 1083.1485 | 1083.1485 | 1083.1485 | 1083.1485 | 1083.1485 | 1083.1485 | 1083.1485 | 1083.1485
Option 7
Determining Optimal Timing: | Discounted | Undiscounted
| 33.225 | 37.0224 | Capex | 0 | 0 | 37.0224 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 4.5893 | 9.996 | Opex | 0 | 0 | 0 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022
| 8211.9237 | 19501.3471 | Reduction in unserved energy | 0 | 0 | 0 | 243.739 | 351.3322 | 423.9169 | 557.436 | 604.3139 | 651.4389 | 662.9191 | 673.4831 | 713.9978 | 640.5858 | 734.9346 | 827.7031 | 827.7031 | 827.7031 | 827.7031 | 827.7031 | 827.7031 | 827.7031 | 827.7031 | 827.7031 | 827.7031 | 827.7031 | 827.7031 | 827.7031 | 827.7031 | 827.7031 | 827.7031
| 8174.1094 | 19454.3287 | Net benefit | 0 | 0 | -37.0224 | 243.3688 | 350.962 | 423.5467 | 557.0658 | 603.9437 | 651.0686 | 662.5488 | 673.1129 | 713.6276 | 640.2155 | 734.5644 | 827.3329 | 827.3329 | 827.3329 | 827.3329 | 827.3329 | 827.3329 | 827.3329 | 827.3329 | 827.3329 | 827.3329 | 827.3329 | 827.3329 | 827.3329 | 827.3329 | 827.3329 | 827.3329
|  |  | EUE Value ($m, real $2024) | 4.9683 | 67.3256 | 249.6646 | 42.2902 | 14.044 | 19.0514 | 28.3457 | 40.3542 | 57.1335 | 77.5326 | 101.083 | 149.0593 | 150.4369 | 230.5179 | 322.902 | 322.902 | 322.902 | 322.902 | 322.902 | 322.902 | 322.902 | 322.902 | 322.902 | 322.902 | 322.902 | 322.902 | 322.902 | 322.902 | 322.902 | 322.902
|  |  | Annualised capex | 0 | 0 | 2.0247 | 2.0247 | 2.0247 | 2.0247 | 2.0247 | 2.0247 | 2.0247 | 2.0247 | 2.0247 | 2.0247 | 2.0247 | 2.0247 | 2.0247 | 2.0247 | 2.0247 | 2.0247 | 2.0247 | 2.0247 | 2.0247 | 2.0247 | 2.0247 | 2.0247 | 2.0247 | 2.0247 | 2.0247 | 2.0247 | 2.0247 | 2.0247
|  |  | Annualised cost (capex+opex) | 0 | 0 | 2.0247 | 2.3949 | 2.3949 | 2.3949 | 2.3949 | 2.3949 | 2.3949 | 2.3949 | 2.3949 | 2.3949 | 2.3949 | 2.3949 | 2.3949 | 2.3949 | 2.3949 | 2.3949 | 2.3949 | 2.3949 | 2.3949 | 2.3949 | 2.3949 | 2.3949 | 2.3949 | 2.3949 | 2.3949 | 2.3949 | 2.3949 | 2.3949
|  |  | Optimal timing (interim calc) | 0 | 0 | 0 | 1 | 1 | 1 | 1 | [19 empty] | 1 | 1 | 1 | 1 | bar: 1 to 19
|  |  | Optimal timing | - | - | - | Yes | - | - | - | [19 empty] | - | - | - | - | bar: 1 to 19
Adjusted For Optimal Timing: | 33.225 | 37.0224 | Capex | 0 | 0 | 37.0224 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 4.5893 | 9.996 | Opex | 0 | 0 | 0 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022 | 0.37022
| 8211.9237 | 19501.3471 | Reduction in unserved energy | 0 | 0 | 0 | 243.739 | 351.3322 | 423.9169 | 557.436 | 604.3139 | 651.4389 | 662.9191 | 673.4831 | 713.9978 | 640.5858 | 734.9346 | 827.7031 | 827.7031 | 827.7031 | 827.7031 | 827.7031 | 827.7031 | 827.7031 | 827.7031 | 827.7031 | 827.7031 | 827.7031 | 827.7031 | 827.7031 | 827.7031 | 827.7031 | 827.7031
| 8174.1094 | 19454.3287 | Net benefit | 0 | 0 | -37.0224 | 243.3688 | 350.962 | 423.5467 | 557.0658 | 603.9437 | 651.0686 | 662.5488 | 673.1129 | 713.6276 | 640.2155 | 734.5644 | 827.3329 | 827.3329 | 827.3329 | 827.3329 | 827.3329 | 827.3329 | 827.3329 | 827.3329 | 827.3329 | 827.3329 | 827.3329 | 827.3329 | 827.3329 | 827.3329 | 827.3329 | 827.3329
Option 8
Determining Optimal Timing: | Discounted | Undiscounted
| 47.6017 | 53.0422 | Capex | 0 | 0 | 53.0422 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 6.5751 | 14.3214 | Opex | 0 | 0 | 0 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042
| 3956.9241 | 10618.4981 | Reduction in unserved energy | 0 | 0 | 0 | 7.7821 | 75.0511 | 98.1744 | 116.4986 | 136.0719 | 160.473 | 185.6413 | 217.2888 | 292.7471 | 277.8311 | 403.8479 | 540.4432 | 540.4432 | 540.4432 | 540.4432 | 540.4432 | 540.4432 | 540.4432 | 540.4432 | 540.4432 | 540.4432 | 540.4432 | 540.4432 | 540.4432 | 540.4432 | 540.4432 | 540.4432
| 3902.7473 | 10551.1345 | Net benefit | 0 | 0 | -53.0422 | 7.2517 | 74.5207 | 97.644 | 115.9682 | 135.5414 | 159.9426 | 185.1109 | 216.7584 | 292.2167 | 277.3007 | 403.3175 | 539.9127 | 539.9127 | 539.9127 | 539.9127 | 539.9127 | 539.9127 | 539.9127 | 539.9127 | 539.9127 | 539.9127 | 539.9127 | 539.9127 | 539.9127 | 539.9127 | 539.9127 | 539.9127
|  |  | EUE Value ($m, real $2024) | 4.9683 | 67.3256 | 249.6646 | 278.2471 | 290.3251 | 344.7939 | 469.2831 | 508.5963 | 548.0993 | 554.8103 | 557.2773 | 570.3101 | 513.1915 | 561.6045 | 610.1619 | 610.1619 | 610.1619 | 610.1619 | 610.1619 | 610.1619 | 610.1619 | 610.1619 | 610.1619 | 610.1619 | 610.1619 | 610.1619 | 610.1619 | 610.1619 | 610.1619 | 610.1619
|  |  | Annualised capex | 0 | 0 | 2.9008 | 2.9008 | 2.9008 | 2.9008 | 2.9008 | 2.9008 | 2.9008 | 2.9008 | 2.9008 | 2.9008 | 2.9008 | 2.9008 | 2.9008 | 2.9008 | 2.9008 | 2.9008 | 2.9008 | 2.9008 | 2.9008 | 2.9008 | 2.9008 | 2.9008 | 2.9008 | 2.9008 | 2.9008 | 2.9008 | 2.9008 | 2.9008
|  |  | Annualised cost (capex+opex) | 0 | 0 | 2.9008 | 3.4312 | 3.4312 | 3.4312 | 3.4312 | 3.4312 | 3.4312 | 3.4312 | 3.4312 | 3.4312 | 3.4312 | 3.4312 | 3.4312 | 3.4312 | 3.4312 | 3.4312 | 3.4312 | 3.4312 | 3.4312 | 3.4312 | 3.4312 | 3.4312 | 3.4312 | 3.4312 | 3.4312 | 3.4312 | 3.4312 | 3.4312
|  |  | Optimal timing (interim calc) | 0 | 0 | 0 | 1 | 1 | 1 | 1 | [19 empty] | 1 | 1 | 1 | 1 | bar: 1 to 19
|  |  | Optimal timing | - | - | - | Yes | - | - | - | [19 empty] | - | - | - | - | bar: 1 to 19
Adjusted For Optimal Timing: | 47.6017 | 53.0422 | Capex | 0 | 0 | 53.0422 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 6.5751 | 14.3214 | Opex | 0 | 0 | 0 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042 | 0.53042
| 3956.9241 | 10618.4981 | Reduction in unserved energy | 0 | 0 | 0 | 7.7821 | 75.0511 | 98.1744 | 116.4986 | 136.0719 | 160.473 | 185.6413 | 217.2888 | 292.7471 | 277.8311 | 403.8479 | 540.4432 | 540.4432 | 540.4432 | 540.4432 | 540.4432 | 540.4432 | 540.4432 | 540.4432 | 540.4432 | 540.4432 | 540.4432 | 540.4432 | 540.4432 | 540.4432 | 540.4432 | 540.4432
| 3902.7473 | 10551.1345 | Net benefit | 0 | 0 | -53.0422 | 7.2517 | 74.5207 | 97.644 | 115.9682 | 135.5414 | 159.9426 | 185.1109 | 216.7584 | 292.2167 | 277.3007 | 403.3175 | 539.9127 | 539.9127 | 539.9127 | 539.9127 | 539.9127 | 539.9127 | 539.9127 | 539.9127 | 539.9127 | 539.9127 | 539.9127 | 539.9127 | 539.9127 | 539.9127 | 539.9127 | 539.9127
Option 9
Determining Optimal Timing: | Discounted | Undiscounted
| 44.1555 | 49.2021 | Capex | 0 | 0 | 49.2021 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 6.0991 | 13.2846 | Opex | 0 | 0 | 0 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202
| 8409.1924 | 19975.0796 | Reduction in unserved energy | 0 | 0 | 0 | 251.7365 | 360.1403 | 433.6567 | 568.308 | 616.3246 | 664.5064 | 677.0821 | 688.95 | 730.7391 | 658.3368 | 754.1549 | 848.1965 | 848.1965 | 848.1965 | 848.1965 | 848.1965 | 848.1965 | 848.1965 | 848.1965 | 848.1965 | 848.1965 | 848.1965 | 848.1965 | 848.1965 | 848.1965 | 848.1965 | 848.1965
| 8358.9379 | 19912.5929 | Net benefit | 0 | 0 | -49.2021 | 251.2445 | 359.6483 | 433.1647 | 567.816 | 615.8326 | 664.0143 | 676.5901 | 688.458 | 730.247 | 657.8448 | 753.6629 | 847.7045 | 847.7045 | 847.7045 | 847.7045 | 847.7045 | 847.7045 | 847.7045 | 847.7045 | 847.7045 | 847.7045 | 847.7045 | 847.7045 | 847.7045 | 847.7045 | 847.7045 | 847.7045
|  |  | EUE Value ($m, real $2024) | 4.9683 | 67.3256 | 249.6646 | 34.2927 | 5.2359 | 9.3115 | 17.4737 | 28.3435 | 44.066 | 63.3696 | 85.6161 | 132.3181 | 132.6858 | 211.2976 | 302.4086 | 302.4086 | 302.4086 | 302.4086 | 302.4086 | 302.4086 | 302.4086 | 302.4086 | 302.4086 | 302.4086 | 302.4086 | 302.4086 | 302.4086 | 302.4086 | 302.4086 | 302.4086
|  |  | Annualised capex | 0 | 0 | 2.6908 | 2.6908 | 2.6908 | 2.6908 | 2.6908 | 2.6908 | 2.6908 | 2.6908 | 2.6908 | 2.6908 | 2.6908 | 2.6908 | 2.6908 | 2.6908 | 2.6908 | 2.6908 | 2.6908 | 2.6908 | 2.6908 | 2.6908 | 2.6908 | 2.6908 | 2.6908 | 2.6908 | 2.6908 | 2.6908 | 2.6908 | 2.6908
|  |  | Annualised cost (capex+opex) | 0 | 0 | 2.6908 | 3.1828 | 3.1828 | 3.1828 | 3.1828 | 3.1828 | 3.1828 | 3.1828 | 3.1828 | 3.1828 | 3.1828 | 3.1828 | 3.1828 | 3.1828 | 3.1828 | 3.1828 | 3.1828 | 3.1828 | 3.1828 | 3.1828 | 3.1828 | 3.1828 | 3.1828 | 3.1828 | 3.1828 | 3.1828 | 3.1828 | 3.1828
|  |  | Optimal timing (interim calc) | 0 | 0 | 0 | 1 | 1 | 1 | 1 | [19 empty] | 1 | 1 | 1 | 1 | bar: 1 to 19
|  |  | Optimal timing | - | - | - | Yes | - | - | - | [19 empty] | - | - | - | - | bar: 1 to 19
Adjusted For Optimal Timing: | 44.1555 | 49.2021 | Capex | 0 | 0 | 49.2021 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 6.0991 | 13.2846 | Opex | 0 | 0 | 0 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202 | 0.49202
| 8409.1924 | 19975.0796 | Reduction in unserved energy | 0 | 0 | 0 | 251.7365 | 360.1403 | 433.6567 | 568.308 | 616.3246 | 664.5064 | 677.0821 | 688.95 | 730.7391 | 658.3368 | 754.1549 | 848.1965 | 848.1965 | 848.1965 | 848.1965 | 848.1965 | 848.1965 | 848.1965 | 848.1965 | 848.1965 | 848.1965 | 848.1965 | 848.1965 | 848.1965 | 848.1965 | 848.1965 | 848.1965
| 8358.9379 | 19912.5929 | Net benefit | 0 | 0 | -49.2021 | 251.2445 | 359.6483 | 433.1647 | 567.816 | 615.8326 | 664.0143 | 676.5901 | 688.458 | 730.247 | 657.8448 | 753.6629 | 847.7045 | 847.7045 | 847.7045 | 847.7045 | 847.7045 | 847.7045 | 847.7045 | 847.7045 | 847.7045 | 847.7045 | 847.7045 | 847.7045 | 847.7045 | 847.7045 | 847.7045 | 847.7045
Option 10
Determining Optimal Timing: | Discounted | Undiscounted
| 0 | 0 | Capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 6375.8942 | 15208.189 | Opex | 0.48285 | 57.8283 | 189.4866 | 207.6844 | 245.4848 | 279.2209 | 339.624 | 384.4625 | 426.7802 | 445.1879 | 469.6214 | 502.6026 | 486.2654 | 573.3683 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055
| 6401.4119 | 15272.282 | Reduction in unserved energy | 0.72502 | 58.1095 | 189.9009 | 208.2231 | 246.1386 | 280.001 | 340.5561 | 385.5567 | 428.0589 | 446.6465 | 471.2748 | 504.5048 | 488.3699 | 575.9241 | 665.5183 | 665.5183 | 665.5183 | 665.5183 | 665.5183 | 665.5183 | 665.5183 | 665.5183 | 665.5183 | 665.5183 | 665.5183 | 665.5183 | 665.5183 | 665.5183 | 665.5183 | 665.5183
| 25.5177 | 64.0931 | Net benefit | 0.24217 | 0.28117 | 0.41424 | 0.53866 | 0.65375 | 0.78017 | 0.93212 | 1.0942 | 1.2787 | 1.4586 | 1.6534 | 1.9021 | 2.1045 | 2.5557 | 3.0127 | 3.0127 | 3.0127 | 3.0127 | 3.0127 | 3.0127 | 3.0127 | 3.0127 | 3.0127 | 3.0127 | 3.0127 | 3.0127 | 3.0127 | 3.0127 | 3.0127 | 3.0127
|  |  | EUE Value ($m, real $2024) | 4.2525 | 9.2161 | 59.7637 | 77.8061 | 119.2376 | 162.9673 | 245.2256 | 259.1115 | 280.5134 | 293.8052 | 303.2913 | 358.5524 | 302.6528 | 389.5284 | 485.0868 | 485.0868 | 485.0868 | 485.0868 | 485.0868 | 485.0868 | 485.0868 | 485.0868 | 485.0868 | 485.0868 | 485.0868 | 485.0868 | 485.0868 | 485.0868 | 485.0868 | 485.0868
|  |  | Annualised capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Annualised cost (capex+opex) | 0.48285 | 57.8283 | 189.4866 | 207.6844 | 245.4848 | 279.2209 | 339.624 | 384.4625 | 426.7802 | 445.1879 | 469.6214 | 502.6026 | 486.2654 | 573.3683 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055
|  |  | Optimal timing (interim calc) | 1 | 1 | 1 | 1 | 1 | 1 | 1 | [19 empty] | 1 | 1 | 1 | 1 | bar: 1 to 19
|  |  | Optimal timing | Yes | - | - | - | - | - | - | [19 empty] | - | - | - | - | bar: 1 to 19
Adjusted For Optimal Timing: | 0 | 0 | Capex | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 6375.8942 | 15208.189 | Opex | 0.48285 | 57.8283 | 189.4866 | 207.6844 | 245.4848 | 279.2209 | 339.624 | 384.4625 | 426.7802 | 445.1879 | 469.6214 | 502.6026 | 486.2654 | 573.3683 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055 | 662.5055
| 6401.4119 | 15272.282 | Reduction in unserved energy | 0.72502 | 58.1095 | 189.9009 | 208.2231 | 246.1386 | 280.001 | 340.5561 | 385.5567 | 428.0589 | 446.6465 | 471.2748 | 504.5048 | 488.3699 | 575.9241 | 665.5183 | 665.5183 | 665.5183 | 665.5183 | 665.5183 | 665.5183 | 665.5183 | 665.5183 | 665.5183 | 665.5183 | 665.5183 | 665.5183 | 665.5183 | 665.5183 | 665.5183 | 665.5183
| 25.5177 | 64.0931 | Net benefit | 0.24217 | 0.28117 | 0.41424 | 0.53866 | 0.65375 | 0.78017 | 0.93212 | 1.0942 | 1.2787 | 1.4586 | 1.6534 | 1.9021 | 2.1045 | 2.5557 | 3.0127 | 3.0127 | 3.0127 | 3.0127 | 3.0127 | 3.0127 | 3.0127 | 3.0127 | 3.0127 | 3.0127 | 3.0127 | 3.0127 | 3.0127 | 3.0127 | 3.0127 | 3.0127

## 3.3 Adjustments
PREFERRED OPTION
$real $2024 (thousands)
|  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | Total
| Input capex (excl mgmt reserve and indirect) | 0 | 0 | 63089.6067 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 63089.6067
| Post modelling adjustment | 0 | 0 | -44406.0512 | 23332.2752 | 17644.4672 | 0 | 3429.3095 | 0 | 0 | 0 | 0 | 0 | 0.00072473
| Revised reg proposal capex | 0 | 0 | 18683.5555 | 23332.2752 | 17644.4672 | 0 | 3429.3095 | 0 | 0 | 0 | 0 | 0 | 63089.6075