## Cover
Distribution Network Service Provider
Annual reporting template
This template is to be used by a DNSP to fulfil its annual reporting obligations to the AER.
Colour coding of input sheets:
Dark blue = AER instructions/headings
Yellow = Input cells
Grey - Not applicable/No inputs required
Leave coloured cells blank if no information exists - PLEASE DO NOT ENTER TEXT unless specifically requested to do so.
All dollar amounts are to be unrounded, and in nominal terms.
DNSP - trading name: |  | SP AusNet
DNSP - Australian business number: |  | SPI Electricity Pty Ltd 91 064 651 118
Reporting year: |  | 2013
Business address | Address |  | L31, 2 Southbank Boulevard
| Suburb |  | Southbank
|  | State | Victoria | Postcode | 3006
Postal address | Address |  | Locked Bag 14051
| Suburb |  | Melbourne City Mail Centre
|  | State | Victoria | Postcode | 8001
Contact name/s | Mei Kwan See Toh, Regulatory Finance Manager
Contact phone/s | (03) 9695 6597
Contact email address/s | meikwan.seetoh@sp-ausnet.com.au

## Contents
Electricity Distribution Network Service Provider Annual Reporting Template
Table of contents
Cover Sheet
1. Service Target Performance Incentive Scheme |  | 2. Demand |  | 6. Outages
3. Asset Installation
4. Customer Service
5. General Information
Cover sheet
1a. STPIS - Reliability
1b. STPIS - Customer Service
1d. STPIS - MED Threshold
1c. STPIS - Daily Performance
6a. Planned Outages
1e. STPIS - Exclusions
2. Demand
6b. Annual Feeder Reliability
6c. Cause of Outages
3. Asset Installation
4. Customer Services
5. General Information

## 1a. STPIS Reliability (hidden)
SP AusNet
STPIS Data Reporting
2013
Reliability
Table 1: SAIDI (System Average Interruption Duration Index)
Network categorisation
Unplanned SAIDI 1 (refer note) | CBD | Urban | Rural short | Rural long | Whole network
Total | N/A | 108.8767 | 241.288 | 317.5284 | 196.9853
Total (after removing excluded events and MED) | N/A | 86.1623 | 165.1048 | 178.5646 | 133.1232
Table 2: SAIFI (System Average Interruption Frequency Index)
Network categorisation
Unplanned SAIFI 2 (refer note) | CBD | Urban | Rural short | Rural long | Whole network
Total | N/A | 1.7881 | 2.7049 | 3.2865 | 2.4075
Total (after removing excluded events and MED) | N/A | 1.3773 | 2.2328 | 2.4539 | 1.8993
Table 3: MAIFI (Momentary Average Interruption Frequency Index)
Network categorisation
MAIFI 3 (refer note) | CBD | Urban | Rural short | Rural long | Whole network
Total | N/A | 2.9893 | 6.2023 | 10.6345 | 5.5768
Total (after removing excluded events and MED) | N/A | 2.7849 | 5.6594 | 9.9247 | 5.1519
Table 4: Planned outages
Network categorisation
Planned outages | CBD | Urban | Rural short | Rural long | Whole network
SAIDI | N/A | 194.2711 | 668.242 | 207.967 | 282.1254
SAIFI | N/A | 0.72559 | 2.4455 | 0.71341 | 1.0202
Table 5: Average distribution customer numbers
| CBD | Urban | Rural short | Rural long | Whole network
Customer numbers at the start of period | N/A | 289421 | 253138 | 113148 | 655707
Customer numbers at the end of period | N/A | 284717 | 263349 | 116685 | 664751
Average distribution customer numbers | N/A | 287069 | 258243.5 | 114916.5 | 660229
Note - the AER's Electricity distribution network service providers, Service target performance incentive scheme, November 2009, p. 22, defines SAIDI and SAIFI as follows;
1) Unplanned SAIDI - The sum of the duration of each unplanned sustained customer interruption (in minutes) divided by the total number of distribution customers. Unplanned SAIDI excludes momentary interruptions (one minute or less).
2) Unplanned SAIFI - The total number of unplanned sustained customer interruptions divided by the total number of distribution customers. Unplanned SAIFI excludes momentary interruptions (one minute or less). SAIFI is expressed per 0.01 interruptions.
The AER will apply the ESCV's definition of MAIFI for transitional reasons. The ESCV's Information specification (Service performance) for Victorian Electricity Distributors, 1 January 2009, p. 30, defines MAIFI as follows:
3) MAIFI - The total number of momentary interruptions divided by the total number of distribution customers (where the distribution customers are network or per feeder based, as appropriate).
4) Total includes the impact of excluded events and MED.
Contents
Contents

## 1b. STPIS Customer Service (hidden)
SP AusNet
STPIS Data Reporting - AER Definitions
2013
Customer service
Table 1: Telephone answering
Telephone answering | Total | Total after removing MED
Number of calls received | 137172 | 124099
Number of calls answered within 30 seconds | 100920 | 97103
Percentage of calls answered within 30 seconds | 73.57% | 78.25%
Note:
Telephone answering has the same meaning as defined in the Electricity DNSPs' STPIS, November 2009.
Table 2: New connections
Note: This is for newly energised properties only
New connections | Total
Number of new connections | 12906
Number of new connections not provided on or before the agreed date | 230
Percentage of new connections not provided on or before the agreed date | 1.782%
Table 3: Streetlight repair
Note:
Streetlight repair has the same meaning as defined in the Electricity DNSPs' STPIS, November 2009
Streetlight repair | Total
Total number of streetlights | 136437
Total number of streetlight faults | 9346
Total number of streetlight faults reported by person who is the occupier of an immediately neighbouring residence or is the proprietor of an immediately neighbouring business | 6283
Faulty streetlights not repaired within 5 business days of fault report or agreed date | 178
Percentage of faulty streetlights not repaired within 5 business days of fault report or agreed date | 1.905%
Table 4 Guaranteed service levels - jurisdictional GSL scheme
Appointments
Customer arranged appointments Central - number |  |  | 4911
Appointments not met within 15 minutes of agreed time - number |  |  | 0
Appointments - GSL payments - number |  |  | 0
Appointments - GSL payments - ($) |  |  | 0
Connections
Connections made |  |  | 12906
Connections not made on agreed date |  |  | 230
Connections - GSL payments - 1-4 day delay - number |  |  | 116
Connections - GSL payments - 1-4 day delay - ($) |  |  | 10900
Connections - GSL payments - 5+ day delay - number |  |  | 114
Connections - GSL payments - 5+ day delay - ($) |  |  | 27900
Reliability of supply
Low reliability payments - 20 hours - number |  |  | 13732
Low reliability payments - 20 hours - ($) |  |  | 1373200
Low reliability payments - 30 hours - number |  |  | 10522
Low reliability payments - 30 hours - ($) |  |  | 1578300
Low reliability payments - 60 hours - number |  |  | 1036
Low reliability payments - 60 hours - ($) |  |  | 310800
Low reliability payments - 10 events - number |  |  | 7077
Low reliability payments - 10 events - ($) |  |  | 707700
Low reliability payments - 15 events - number |  |  | 2002
Low reliability payments - 15 events - ($) |  |  | 300300
Low reliability payments - 30 events - number |  |  | 0
Low reliability payments - 30 events - ($) |  |  | 0
Low reliability payments - 24 momentary events - number |  |  | 17021
Low reliability payments - 24 momentary events - ($) |  |  | 425525
Low reliability payments - 36 momentary events - number |  |  | 4773
Low reliability payments - 36 momentary events - ($) |  |  | 167055
Street lights
Street lights |  |  | 136437
Street lights "out" during period |  |  | 6283
Street lights not repaired by "fix by" date |  |  | 98
Street lights not repaired in 2 business days |  |  | 549
Street lights – number of business days to repair |  |  | 2
Street lights - GSL payments - number |  |  | 49
Street lights - GSL payments - ($) |  |  | 490
Planned interruptions
Planned interruptions - 4 business days notice not given |  |  | 0
Total GSL payments made ($) |  |  | 4902170
Contents

## 1c. STPIS Daily Performance (hidden)
SP AusNet
STPIS Data Reporting
2013
Daily Performance Data
Instruction This regulatory template requires the input of historical daily performance recorded for the calculation of the parameters under the STPIS, such as MED day boundary and performance targets. STPIS definitions apply to SAIDI and Calls not answered within 30 seconds. Please note: The AER's definition of calls answered within 30 seconds is as follows: Calls to the fault line answered in 30 seconds where the time to answer a call is measured from when the call enters the telephone system of the call centre (including that time when it may be ringing unanswered by any response) and the caller speaks with a human operator, but excluding the time that the caller is connected to an automated interactive service that provides substantive information. This measure does not apply to: - calls to payment lines and automated interactive services; - calls abandoned by the customer within 30 seconds of the call being queued for response by a human operator. Where the time in which a telephone call is abandoned is not measured, then an estimate of the number of calls abandoned within 30 seconds will be determined by taking 20 per cent of all calls abandoned. Note: Being placed in a queuing system (automated or otherwise) does not constitute a response. 'Calls answered within 30 seconds' and 'Calls received' should be calculated excluding calls abandoned within 30 seconds of being queued for a human operator; and calls to payment lines and automated interactive services. Exclusions refer to the exclusions listed in Section 3.3(a) of the STPIS.
Table 1 Daily Performance Data (unplanned)
Date | CBD SAIDI All events | CBD SAIDI (after removing excluded events) | Urban SAIDI All events | Urban SAIDI (after removing excluded events) | Long Rural SAIDI All events | Long Rural SAIDI (after removing excluded events) | Short Rural SAIDI All events | Short Rural SAIDI (after removing excluded events) | Network SAIDI All events | Network SAIDI (after removing excluded events) | CBD SAIFI All events | CBD SAIFI (after removing excluded events) | Urban SAIFI All events | Urban SAIFI (after removing excluded events) | Long Rural SAIFI All events | Long Rural SAIFI (after removing excluded events) | Short Rural SAIFI All events | Short Rural SAIFI (after removing excluded events) | Network SAIFI All events | Network SAIFI (after removing excluded events) | CBD MAIFI All events | CBD MAIFI (after removing excluded events) | Urban MAIFI All events | Urban MAIFI (after removing excluded events) | Long Rural MAIFI All events | Long Rural MAIFI (after removing excluded events) | Short Rural MAIFI All events | Short Rural MAIFI (after removing excluded events) | Network MAIFI All events | Network MAIFI (after removing excluded events) | Number of calls received | Calls Offered to an Operator | Calls Abandoned within 30 seconds | Calls not answered in 30 seconds | MED | Comments / basis for exclusion - refer to category of exclusion under 3.3(a) of STPIS
2013-01-01 | N/A | N/A | 0 | 0 | 0.2397 | 0.2397 | 0.0025945 | 0.0025945 | 0.042735 | 0.042735 | N/A | N/A | 0 | 0 | 0.0034895 | 0.0034895 | 3.0979e-05 | 3.0979e-05 | 0.00061948 | 0.00061948 | N/A | N/A | 3.6266e-07 | 3.6266e-07 | 0.099428 | 0.099428 | 0.015652 | 0.015652 | 0.023428 | 0.023428 | 132 | 66 | 8 | 2 | NO
2013-01-02 | N/A | N/A | 0.059076 | 0.059076 | 0.016116 | 0.016116 | 0.049023 | 0.049023 | 0.047667 | 0.047667 | N/A | N/A | 0.0010067 | 0.0010067 | 0.00016534 | 0.00016534 | 0.00063506 | 0.00063506 | 0.0007149 | 0.0007149 | N/A | N/A | 0.018418 | 0.018418 | 0.071138 | 0.071138 | 0.013108 | 0.013108 | 0.025517 | 0.025517 | 365 | 201 | 7 | 12 | NO
2013-01-03 | N/A | N/A | 0.019194 | 0.019194 | 1.5924 | 1.5924 | 0.26771 | 0.26771 | 0.39022 | 0.39022 | N/A | N/A | 0.00028913 | 0.00028913 | 0.0058825 | 0.0058825 | 0.0032605 | 0.0032605 | 0.0024249 | 0.0024249 | N/A | N/A | 3.6266e-07 | 3.6266e-07 | 0.11848 | 0.11848 | 0.035784 | 0.035784 | 0.03462 | 0.03462 | 947 | 352 | 14 | 47 | NO
2013-01-04 | N/A | N/A | 1.5912 | 1.5912 | 8.5989 | 7.4375 | 5.5537 | 5.5537 | 4.3608 | 4.1587 | N/A | N/A | 0.011495 | 0.011495 | 0.11255 | 0.10757 | 0.069818 | 0.069818 | 0.051897 | 0.051031 | N/A | N/A | 0.071426 | 0.071426 | 0.13784 | 0.13784 | 0.021712 | 0.021712 | 0.06354 | 0.06354 | 7815 | 1973 | 164 | 1227 | NO | TFB suppressed reclose operations
2013-01-05 | N/A | N/A | 0.21199 | 0.21199 | 3.029 | 3.029 | 0.19887 | 0.19887 | 0.69717 | 0.69717 | N/A | N/A | 0.0035706 | 0.0035706 | 0.025784 | 0.025784 | 0.00092161 | 0.00092161 | 0.0064008 | 0.0064008 | N/A | N/A | 0.017832 | 0.017832 | 0.019343 | 0.019343 | 0.020275 | 0.020275 | 0.019051 | 0.019051 | 1512 | 408 | 9 | 41 | NO
2013-01-06 | N/A | N/A | 0.30982 | 0.30982 | 0.069146 | 0.069146 | 0.63887 | 0.63887 | 0.39664 | 0.39664 | N/A | N/A | 0.0090745 | 0.0090745 | 0.0004612 | 0.0004612 | 0.019331 | 0.019331 | 0.011587 | 0.011587 | N/A | N/A | 0.021535 | 0.021535 | 0.045902 | 0.045902 | 0.029979 | 0.029979 | 0.029079 | 0.029079 | 701 | 218 | 12 | 27 | NO
2013-01-07 | N/A | N/A | 3.4315 | 3.4315 | 0.127 | 0.127 | 0.12946 | 0.12946 | 1.5648 | 1.5648 | N/A | N/A | 0.027014 | 0.027014 | 0.00029587 | 0.00029587 | 0.001456 | 0.001456 | 0.012367 | 0.012367 | N/A | N/A | 3.6266e-07 | 3.6266e-07 | 0.053629 | 0.053629 | 0.040725 | 0.040725 | 0.025264 | 0.025264 | 2416 | 696 | 32 | 249 | NO
2013-01-08 | N/A | N/A | 0.12518 | 0.12518 | 0.19416 | 0.19416 | 0.16795 | 0.16795 | 0.15391 | 0.15391 | N/A | N/A | 0.00056432 | 0.00056432 | 0.0011574 | 0.0011574 | 0.004004 | 0.004004 | 0.0020129 | 0.0020129 | N/A | N/A | 3.6266e-07 | 3.6266e-07 | 0.02124 | 0.02124 | 0.014475 | 0.014475 | 0.0093588 | 0.0093588 | 823 | 408 | 7 | 45 | NO
2013-01-09 | N/A | N/A | 0.21438 | 0.21438 | 0.72783 | 0.72783 | 1.7312 | 1.7312 | 0.89706 | 0.89706 | N/A | N/A | 0.0015223 | 0.0015223 | 0.029334 | 0.029334 | 0.017913 | 0.017913 | 0.012774 | 0.012774 | N/A | N/A | 3.6266e-07 | 3.6266e-07 | 0.053803 | 0.053803 | 0.021495 | 0.021495 | 0.017773 | 0.017773 | 1165 | 412 | 5 | 45 | NO
2013-01-10 | N/A | N/A | 0.00068276 | 0.00068276 | 3.4175 | 3.4175 | 0.026231 | 0.026231 | 0.60539 | 0.60539 | N/A | N/A | 1.045e-05 | 1.045e-05 | 0.052482 | 0.052482 | 0.00022847 | 0.00022847 | 0.0092286 | 0.0092286 | N/A | N/A | 0.0033619 | 0.0033619 | 0.053238 | 0.053238 | 0.014393 | 0.014393 | 0.016358 | 0.016358 | 673 | 360 | 3 | 70 | NO
2013-01-11 | N/A | N/A | 1.201 | 1.201 | 3.6495 | 3.6495 | 0.1191 | 0.1191 | 1.204 | 1.204 | N/A | N/A | 0.0094054 | 0.0094054 | 0.031197 | 0.031197 | 0.00082868 | 0.00082868 | 0.0098436 | 0.0098436 | N/A | N/A | 0.011834 | 0.011834 | 0.066778 | 0.066778 | 0.0041897 | 0.0041897 | 0.018407 | 0.018407 | 2026 | 527 | 21 | 86 | NO
2013-01-12 | N/A | N/A | 0.043812 | 0.043812 | 1.2825 | 1.2825 | 2.2982 | 2.2982 | 1.1412 | 1.1412 | N/A | N/A | 0.00051556 | 0.00051556 | 0.042805 | 0.042805 | 0.038925 | 0.038925 | 0.0229 | 0.0229 | N/A | N/A | 3.6266e-07 | 3.6266e-07 | 0.014053 | 0.014053 | 0.039362 | 0.039362 | 0.017842 | 0.017842 | 894 | 264 | 13 | 30 | NO
2013-01-13 | N/A | N/A | 0.33729 | 0.33729 | 0.26015 | 0.26015 | 0.068277 | 0.068277 | 0.21864 | 0.21864 | N/A | N/A | 0.0038423 | 0.0038423 | 0.0054996 | 0.0054996 | 0.0013592 | 0.0013592 | 0.0031595 | 0.0031595 | N/A | N/A | 0.0082667 | 0.0082667 | 0.034215 | 0.034215 | 0.031687 | 0.031687 | 0.021944 | 0.021944 | 491 | 159 | 4 | 12 | NO
2013-01-14 | N/A | N/A | 0.0013098 | 0.0013098 | 0.593 | 0.593 | 0.12374 | 0.12374 | 0.15219 | 0.15219 | N/A | N/A | 1.3934e-05 | 1.3934e-05 | 0.011321 | 0.011321 | 0.0027067 | 0.0027067 | 0.0030353 | 0.0030353 | N/A | N/A | 0.0094093 | 0.0094093 | 0.024512 | 0.024512 | 0.010219 | 0.010219 | 0.012355 | 0.012355 | 474 | 293 | 6 | 63 | NO
2013-01-15 | N/A | N/A | 0.0049779 | 0.0049779 | 0.023034 | 0.023034 | 1.0636 | 1.0636 | 0.42221 | 0.42221 | N/A | N/A | 0.00016372 | 0.00016372 | 0.00020885 | 0.00020885 | 0.016051 | 0.016051 | 0.0063857 | 0.0063857 | N/A | N/A | 0.00040445 | 0.00040445 | 0.011581 | 0.011581 | 0.04416 | 0.04416 | 0.019464 | 0.019464 | 726 | 328 | 9 | 52 | NO
2013-01-16 | N/A | N/A | 0.0054586 | 0.0054586 | 0.02326 | 0.02326 | 0.039881 | 0.039881 | 0.022021 | 0.022021 | N/A | N/A | 4.1802e-05 | 4.1802e-05 | 0.00022625 | 0.00022625 | 0.00027881 | 0.00027881 | 0.00016661 | 0.00016661 | N/A | N/A | 0.019184 | 0.019184 | 0.012643 | 0.012643 | 0.052989 | 0.052989 | 0.031268 | 0.031268 | 646 | 384 | 9 | 119 | NO
2013-01-17 | N/A | N/A | 1.1914 | 1.1914 | 0.024078 | 0.024078 | 0.2049 | 0.15402 | 0.60234 | 0.58244 | N/A | N/A | 0.013415 | 0.013415 | 0.00018274 | 0.00018274 | 0.0052586 | 0.0049837 | 0.0079215 | 0.007814 | N/A | N/A | 0.0056227 | 0.0056227 | 0.011538 | 0.011538 | 0.020345 | 0.020345 | 0.012411 | 0.012411 | 1294 | 496 | 15 | 55 | NO | TFB suppressed reclose operations
2013-01-18 | N/A | N/A | 0.12864 | 0.12864 | 5.2095 | 5.2095 | 0.53157 | 0.12008 | 1.1706 | 1.0096 | N/A | N/A | 0.00040757 | 0.00040757 | 0.0041508 | 0.0041508 | 0.0026642 | 0.00090612 | 0.0019418 | 0.0012541 | N/A | N/A | 0.0038217 | 0.0038217 | 0.018795 | 0.018795 | 0.024062 | 0.024062 | 0.014345 | 0.014345 | 1022 | 377 | 8 | 32 | NO | TFB suppressed reclose operations
2013-01-19 | N/A | N/A | 0.00033441 | 0.00033441 | 0.77707 | 0.77707 | 0.052632 | 0.052632 | 0.15599 | 0.15599 | N/A | N/A | 3.4835e-06 | 3.4835e-06 | 0.033476 | 0.033476 | 0.0004337 | 0.0004337 | 0.0059979 | 0.0059979 | N/A | N/A | 0.016453 | 0.016453 | 0.0028619 | 0.0028619 | 0.040218 | 0.040218 | 0.023383 | 0.023383 | 275 | 121 | 1 | 8 | NO
2013-01-20 | N/A | N/A | 0.097719 | 0.097719 | 0.041178 | 0.041178 | 0.035319 | 0.035319 | 0.06347 | 0.06347 | N/A | N/A | 0.0026927 | 0.0026927 | 0.00032197 | 0.00032197 | 0.00044532 | 0.00044532 | 0.001401 | 0.001401 | N/A | N/A | 0.018996 | 0.018996 | 0.07903 | 0.07903 | 0.011152 | 0.011152 | 0.026377 | 0.026377 | 269 | 113 | 2 | 5 | NO
2013-01-21 | N/A | N/A | 0.05545 | 0.05545 | 0.96259 | 0.96259 | 0.31071 | 0.31071 | 0.31318 | 0.31318 | N/A | N/A | 0.00027171 | 0.00027171 | 0.0078405 | 0.0078405 | 0.012062 | 0.012062 | 0.0062009 | 0.0062009 | N/A | N/A | 0.0081308 | 0.0081308 | 0.028228 | 0.028228 | 0.030037 | 0.030037 | 0.020197 | 0.020197 | 961 | 382 | 11 | 57 | NO
2013-01-22 | N/A | N/A | 0.19453 | 0.19453 | 0.14975 | 0.14975 | 0.086279 | 0.086279 | 0.14439 | 0.14439 | N/A | N/A | 0.00045285 | 0.00045285 | 0.0053604 | 0.0053604 | 0.00021298 | 0.00021298 | 0.0012132 | 0.0012132 | N/A | N/A | 0.0033619 | 0.0033619 | 0.011764 | 0.011764 | 0.0072217 | 0.0072217 | 0.0063341 | 0.0063341 | 656 | 277 | 3 | 35 | NO
2013-01-23 | N/A | N/A | 0.00032396 | 0.00032396 | 0.17535 | 0.17535 | 0.013677 | 0.013677 | 0.036012 | 0.036012 | N/A | N/A | 3.4835e-06 | 3.4835e-06 | 0.0014967 | 0.0014967 | 5.4212e-05 | 5.4212e-05 | 0.00028324 | 0.00028324 | N/A | N/A | 0.0048668 | 0.0048668 | 0.06824 | 0.06824 | 0.0082827 | 0.0082827 | 0.017233 | 0.017233 | 474 | 289 | 2 | 60 | NO
2013-01-24 | N/A | N/A | 0.24172 | 0.24172 | 0.46875 | 0.46875 | 0.19462 | 0.19462 | 0.26281 | 0.26281 | N/A | N/A | 0.0010207 | 0.0010207 | 0.0020015 | 0.0020015 | 0.0013437 | 0.0013437 | 0.0013177 | 0.0013177 | N/A | N/A | 0.016941 | 0.016941 | 0.011042 | 0.011042 | 0.02912 | 0.02912 | 0.020678 | 0.020678 | 1127 | 551 | 10 | 103 | NO
2013-01-25 | N/A | N/A | 4.4247 | 4.4247 | 0.41613 | 0.41613 | 1.5485 | 1.5485 | 2.602 | 2.602 | N/A | N/A | 0.032738 | 0.032738 | 0.00054822 | 0.00054822 | 0.020124 | 0.020124 | 0.022201 | 0.022201 | N/A | N/A | 0.01971 | 0.01971 | 0.00057323 | 0.00057323 | 0.026266 | 0.026266 | 0.018943 | 0.018943 | 3793 | 693 | 53 | 215 | NO
2013-01-26 | N/A | N/A | 0.023778 | 0.023778 | 0.413 | 0.413 | 0.1295 | 0.1295 | 0.13288 | 0.13288 | N/A | N/A | 0.00057826 | 0.00057826 | 0.0015141 | 0.0015141 | 0.0021182 | 0.0021182 | 0.0013435 | 0.0013435 | N/A | N/A | 3.6266e-07 | 3.6266e-07 | 0.1868 | 0.1868 | 0.044926 | 0.044926 | 0.050087 | 0.050087 | 420 | 261 | 8 | 54 | NO
2013-01-27 | N/A | N/A | 1.5156 | 1.5156 | 0.11313 | 0.11313 | 0.051455 | 0.051455 | 0.69882 | 0.69882 | N/A | N/A | 0.017525 | 0.017525 | 0.00072226 | 0.00072226 | 0.00056149 | 0.00056149 | 0.0079654 | 0.0079654 | N/A | N/A | 0.034992 | 0.034992 | 0.017281 | 0.017281 | 0.03882 | 0.03882 | 0.033406 | 0.033406 | 953 | 311 | 16 | 71 | NO
2013-01-28 | N/A | N/A | 0.65884 | 0.65884 | 0.11697 | 0.11697 | 0.025755 | 0.025755 | 0.3169 | 0.3169 | N/A | N/A | 0.012112 | 0.012112 | 0.00080928 | 0.00080928 | 0.000182 | 0.000182 | 0.0054784 | 0.0054784 | N/A | N/A | 0.00018847 | 0.00018847 | 0.033484 | 0.033484 | 0.017394 | 0.017394 | 0.012714 | 0.012714 | 284 | 140 | 3 | 8 | NO
2013-01-29 | N/A | N/A | 0.075961 | 0.075961 | 0.10388 | 0.10388 | 1.3033 | 1.3033 | 0.56089 | 0.56089 | N/A | N/A | 0.00086739 | 0.00086739 | 0.00063524 | 0.00063524 | 0.0045964 | 0.0045964 | 0.0022856 | 0.0022856 | N/A | N/A | 3.6266e-07 | 3.6266e-07 | 0.050375 | 0.050375 | 0.017599 | 0.017599 | 0.015652 | 0.015652 | 882 | 417 | 18 | 101 | NO
2013-01-30 | N/A | N/A | 0.11288 | 0.11288 | 0.0068833 | 0.0068833 | 0.06198 | 0.06198 | 0.074523 | 0.074523 | N/A | N/A | 0.0011321 | 0.0011321 | 7.8318e-05 | 7.8318e-05 | 0.0013708 | 0.0013708 | 0.0010421 | 0.0010421 | N/A | N/A | 0.009991 | 0.009991 | 0.02178 | 0.02178 | 0.028442 | 0.028442 | 0.01926 | 0.01926 | 527 | 329 | 8 | 63 | NO
2013-01-31 | N/A | N/A | 1.2926 | 1.2926 | 0.50091 | 0.50091 | 1.0292 | 1.0292 | 1.0518 | 1.0518 | N/A | N/A | 0.019089 | 0.019089 | 0.0026715 | 0.0026715 | 0.017913 | 0.017913 | 0.015772 | 0.015772 | N/A | N/A | 0.065772 | 0.065772 | 0.064185 | 0.064185 | 0.038545 | 0.038545 | 0.054846 | 0.054846 | 2131 | 695 | 36 | 305 | NO
2013-02-01 | N/A | N/A | 1.0392 | 1.0392 | 0.2879 | 0.2879 | 0.37557 | 0.37557 | 0.64885 | 0.64885 | N/A | N/A | 0.0044867 | 0.0044867 | 0.0015577 | 0.0015577 | 0.00070863 | 0.00070863 | 0.0024991 | 0.0024991 | N/A | N/A | 0.012433 | 0.012433 | 0.05208 | 0.05208 | 0.016577 | 0.016577 | 0.020955 | 0.020955 | 1292 | 556 | 11 | 97 | NO
2013-02-02 | N/A | N/A | 0.10813 | 0.10813 | 0.076073 | 0.076073 | 0.11463 | 0.11463 | 0.10509 | 0.10509 | N/A | N/A | 0.00043892 | 0.00043892 | 0.00062654 | 0.00062654 | 0.00041434 | 0.00041434 | 0.00046196 | 0.00046196 | N/A | N/A | 0.019219 | 0.019219 | 0.00016424 | 0.00016424 | 0.0069584 | 0.0069584 | 0.011107 | 0.011107 | 273 | 181 | 2 | 41 | NO
2013-02-03 | N/A | N/A | 0.031104 | 0.031104 | 0.019188 | 0.019188 | 0.013785 | 0.013785 | 0.022256 | 0.022256 | N/A | N/A | 0.00041453 | 0.00041453 | 8.702e-05 | 8.702e-05 | 0.00015876 | 0.00015876 | 0.00025749 | 0.00025749 | N/A | N/A | 3.6266e-07 | 3.6266e-07 | 0.016602 | 0.016602 | 0.014691 | 0.014691 | 0.0086363 | 0.0086363 | 175 | 133 | 9 | 5 | NO
2013-02-04 | N/A | N/A | 0.073634 | 0.073634 | 0.093772 | 0.093772 | 0.018816 | 0.018816 | 0.055697 | 0.055697 | N/A | N/A | 0.00047027 | 0.00047027 | 0.0028717 | 0.0028717 | 0.00010842 | 0.00010842 | 0.00074671 | 0.00074671 | N/A | N/A | 0.032766 | 0.032766 | 0.01541 | 0.01541 | 0.031242 | 0.031242 | 0.029149 | 0.029149 | 539 | 299 | 9 | 58 | NO
2013-02-05 | N/A | N/A | 0.074512 | 0.074512 | 0.020354 | 0.020354 | 0.060029 | 0.060029 | 0.05942 | 0.05942 | N/A | N/A | 0.00021946 | 0.00021946 | 0.00024366 | 0.00024366 | 0.00053438 | 0.00053438 | 0.00034685 | 0.00034685 | N/A | N/A | 0.010099 | 0.010099 | 0.017281 | 0.017281 | 0.01909 | 0.01909 | 0.014866 | 0.014866 | 531 | 367 | 12 | 63 | NO
2013-02-06 | N/A | N/A | 0.98885 | 0.98885 | 0.016891 | 0.016891 | 0.31264 | 0.31264 | 0.55518 | 0.55518 | N/A | N/A | 0.019013 | 0.019013 | 0.00014793 | 0.00014793 | 0.0050146 | 0.0050146 | 0.010254 | 0.010254 | N/A | N/A | 0.022242 | 0.022242 | 0.0031142 | 0.0031142 | 0.017905 | 0.017905 | 0.017217 | 0.017217 | 1649 | 503 | 10 | 94 | NO
2013-02-07 | N/A | N/A | 0.085474 | 0.052329 | 0.041326 | 0.041326 | 1.4204 | 1.1784 | 0.59993 | 0.49086 | N/A | N/A | 0.00069321 | 0.00050511 | 0.00052212 | 0.00052212 | 0.024415 | 0.014254 | 0.009942 | 0.0058858 | N/A | N/A | 0.025799 | 0.025799 | 0.032422 | 0.032422 | 0.014196 | 0.014196 | 0.022413 | 0.022413 | 1453 | 463 | 16 | 161 | NO | TFB suppressed reclose operations
2013-02-08 | N/A | N/A | 0.01493 | 0.01493 | 1.9004 | 1.9004 | 0.049012 | 0.049012 | 0.35643 | 0.35643 | N/A | N/A | 0.00064096 | 0.00064096 | 0.02574 | 0.02574 | 0.00024783 | 0.00024783 | 0.0048559 | 0.0048559 | N/A | N/A | 0.017825 | 0.017825 | 0.051123 | 0.051123 | 0.0052855 | 0.0052855 | 0.018716 | 0.018716 | 620 | 285 | 6 | 35 | NO
2013-02-09 | N/A | N/A | 0.0076637 | 0.0076637 | 0.033964 | 0.033964 | 0.17847 | 0.17847 | 0.079051 | 0.079051 | N/A | N/A | 0.00011844 | 0.00011844 | 0.00024366 | 0.00024366 | 0.00054987 | 0.00054987 | 0.00030898 | 0.00030898 | N/A | N/A | 0.037653 | 0.037653 | 0.016611 | 0.016611 | 0.034432 | 0.034432 | 0.032731 | 0.032731 | 371 | 200 | 5 | 24 | NO
2013-02-10 | N/A | N/A | 0.032261 | 0.032261 | 0.033668 | 0.033668 | 0.92308 | 0.92308 | 0.38094 | 0.38094 | N/A | N/A | 0.00019856 | 0.00019856 | 0.00035678 | 0.00035678 | 0.009948 | 0.009948 | 0.0040395 | 0.0040395 | N/A | N/A | 0.013785 | 0.013785 | 0.068327 | 0.068327 | 0.071924 | 0.071924 | 0.046019 | 0.046019 | 482 | 188 | 6 | 15 | NO
2013-02-11 | N/A | N/A | 0.080667 | 0.080667 | 0.037427 | 0.037427 | 0.16763 | 0.16763 | 0.10716 | 0.10716 | N/A | N/A | 0.00078378 | 0.00078378 | 0.00041769 | 0.00041769 | 0.0023195 | 0.0023195 | 0.0013208 | 0.0013208 | N/A | N/A | 3.6266e-07 | 3.6266e-07 | 0.020457 | 0.020457 | 0.0011421 | 0.0011421 | 0.0040076 | 0.0040076 | 1020 | 310 | 10 | 23 | NO
2013-02-12 | N/A | N/A | 0.98099 | 0.036653 | 0.16316 | 0.16316 | 0.048598 | 0.048598 | 0.47395 | 0.063345 | N/A | N/A | 0.050214 | 0.00038667 | 0.0012618 | 0.0012618 | 0.00054987 | 0.00054987 | 0.022268 | 0.00060282 | N/A | N/A | 0.012015 | 0.012015 | 0.034615 | 0.034615 | 0.0013784 | 0.0013784 | 0.011788 | 0.011788 | 1359 | 425 | 16 | 86 | NO | Transmission
2013-02-13 | N/A | N/A | 0.19826 | 0.19826 | 0.19523 | 0.19523 | 0.1183 | 0.1183 | 0.16646 | 0.16646 | N/A | N/A | 0.014422 | 0.014422 | 0.002454 | 0.002454 | 0.0010223 | 0.0010223 | 0.0070975 | 0.0070975 | N/A | N/A | 0.0063612 | 0.0063612 | 0.014035 | 0.014035 | 0.019869 | 0.019869 | 0.01298 | 0.01298 | 881 | 404 | 12 | 120 | NO
2013-02-14 | N/A | N/A | 0.16617 | 0.16617 | 1.2534 | 1.2534 | 1.3802 | 1.3802 | 0.83029 | 0.83029 | N/A | N/A | 0.001477 | 0.001477 | 0.00838 | 0.00838 | 0.0091774 | 0.0091774 | 0.0056904 | 0.0056904 | N/A | N/A | 0.035877 | 0.035877 | 0.14328 | 0.14328 | 0.050448 | 0.050448 | 0.06027 | 0.06027 | 2006 | 721 | 29 | 188 | NO
2013-02-15 | N/A | N/A | 0.11661 | 0.11661 | 0.58036 | 0.58036 | 0.9372 | 0.9372 | 0.5183 | 0.5183 | N/A | N/A | 0.00048072 | 0.00048072 | 0.004116 | 0.004116 | 0.051076 | 0.051076 | 0.020903 | 0.020903 | N/A | N/A | 0.026088 | 0.026088 | 0.058363 | 0.058363 | 0.023327 | 0.023327 | 0.030626 | 0.030626 | 1330 | 556 | 18 | 60 | NO
2013-02-16 | N/A | N/A | 0.061811 | 0.061811 | 0.043292 | 0.043292 | 0.60319 | 0.60319 | 0.27034 | 0.27034 | N/A | N/A | 0.00077682 | 0.00077682 | 0.00021755 | 0.00021755 | 0.013495 | 0.013495 | 0.0056541 | 0.0056541 | N/A | N/A | 3.6266e-07 | 3.6266e-07 | 0.043683 | 0.043683 | 0.0050261 | 0.0050261 | 0.0095693 | 0.0095693 | 626 | 242 | 4 | 33 | NO
2013-02-17 | N/A | N/A | 0.023789 | 0.023789 | 0.062924 | 0.062924 | 0.13435 | 0.13435 | 0.073847 | 0.073847 | N/A | N/A | 0.00028216 | 0.00028216 | 0.00071356 | 0.00071356 | 0.00048017 | 0.00048017 | 0.0004347 | 0.0004347 | N/A | N/A | 0.007152 | 0.007152 | 0.022232 | 0.022232 | 0.0023232 | 0.0023232 | 0.0078881 | 0.0078881 | 434 | 263 | 5 | 25 | NO
2013-02-18 | N/A | N/A | 0.30361 | 0.30361 | 0.3322 | 0.3322 | 0.060966 | 0.060966 | 0.21368 | 0.21368 | N/A | N/A | 0.0032083 | 0.0032083 | 0.00181 | 0.00181 | 0.0047126 | 0.0047126 | 0.0035533 | 0.0035533 | N/A | N/A | 0.030087 | 0.030087 | 0.020214 | 0.020214 | 0.037205 | 0.037205 | 0.031153 | 0.031153 | 1113 | 484 | 24 | 60 | NO
2013-02-19 | N/A | N/A | 0.48513 | 0.48513 | 0.1049 | 0.1049 | 0.065094 | 0.065094 | 0.25465 | 0.25465 | N/A | N/A | 0.0058383 | 0.0058383 | 0.0004264 | 0.0004264 | 0.00094484 | 0.00094484 | 0.0029823 | 0.0029823 | N/A | N/A | 0.013506 | 0.013506 | 0.001983 | 0.001983 | 0.019621 | 0.019621 | 0.013892 | 0.013892 | 1065 | 413 | 16 | 77 | NO
2013-02-20 | N/A | N/A | 0.65172 | 0.65172 | 2.5809 | 2.5809 | 1.8828 | 1.8828 | 1.469 | 1.469 | N/A | N/A | 0.02327 | 0.02327 | 0.029334 | 0.029334 | 0.047296 | 0.047296 | 0.033723 | 0.033723 | N/A | N/A | 3.6266e-07 | 3.6266e-07 | 0.010702 | 0.010702 | 0.017975 | 0.017975 | 0.0088938 | 0.0088938 | 2885 | 655 | 55 | 283 | NO
2013-02-21 | N/A | N/A | 0.92151 | 0.92151 | 1.7875 | 1.7875 | 2.8087 | 2.8087 | 1.8104 | 1.8104 | N/A | N/A | 0.0077682 | 0.0077682 | 0.044624 | 0.044624 | 0.026409 | 0.026409 | 0.021474 | 0.021474 | N/A | N/A | 0.077996 | 0.077996 | 0.2862 | 0.2862 | 0.1083 | 0.1083 | 0.12609 | 0.12609 | 2008 | 815 | 36 | 342 | NO
2013-02-22 | N/A | N/A | 0.076853 | 0.076853 | 0.42065 | 0.42065 | 0.52632 | 0.52632 | 0.3125 | 0.3125 | N/A | N/A | 0.00019508 | 0.00019508 | 0.030039 | 0.030039 | 0.0027919 | 0.0027919 | 0.0064054 | 0.0064054 | N/A | N/A | 8.0483e-05 | 8.0483e-05 | 0.012129 | 0.012129 | 0.0037405 | 0.0037405 | 0.0036092 | 0.0036092 | 1213 | 631 | 26 | 229 | NO
2013-02-23 | N/A | N/A | 0.2378 | 0.2378 | 0.019397 | 0.019397 | 0.027261 | 0.027261 | 0.11744 | 0.11744 | N/A | N/A | 0.00052601 | 0.00052601 | 0.00019144 | 0.00019144 | 0.0098396 | 0.0098396 | 0.0041107 | 0.0041107 | N/A | N/A | 3.6266e-07 | 3.6266e-07 | 0.012686 | 0.012686 | 0.014684 | 0.014684 | 0.0079517 | 0.0079517 | 510 | 232 | 6 | 38 | NO
2013-02-24 | N/A | N/A | 0.039318 | 0.039318 | 0.40623 | 0.40623 | 0.2261 | 0.2261 | 0.17624 | 0.17624 | N/A | N/A | 4.1802e-05 | 4.1802e-05 | 0.00295 | 0.00295 | 0.0020213 | 0.0020213 | 0.0013223 | 0.0013223 | N/A | N/A | 0.0038392 | 0.0038392 | 0.037339 | 0.037339 | 0.036063 | 0.036063 | 0.022274 | 0.022274 | 499 | 290 | 5 | 34 | NO
2013-02-25 | N/A | N/A | 0.16695 | 0.16695 | 0.39018 | 0.39018 | 0.62713 | 0.62713 | 0.3858 | 0.3858 | N/A | N/A | 0.0082559 | 0.0082559 | 0.0020537 | 0.0020537 | 0.029956 | 0.029956 | 0.015664 | 0.015664 | N/A | N/A | 0.0037556 | 0.0037556 | 0.011486 | 0.011486 | 0.01535 | 0.01535 | 0.0096359 | 0.0096359 | 1137 | 513 | 18 | 85 | NO
2013-02-26 | N/A | N/A | 0.76496 | 0.76496 | 0.92171 | 0.92171 | 0.50147 | 0.50147 | 0.68918 | 0.68918 | N/A | N/A | 0.012028 | 0.012028 | 0.0077535 | 0.0077535 | 0.011954 | 0.011954 | 0.011255 | 0.011255 | N/A | N/A | 0.0091341 | 0.0091341 | 0.15309 | 0.15309 | 0.076524 | 0.076524 | 0.06055 | 0.06055 | 1503 | 613 | 12 | 137 | NO
2013-02-27 | N/A | N/A | 1.688 | 1.688 | 0.18359 | 0.18359 | 1.3688 | 1.3688 | 1.3013 | 1.3013 | N/A | N/A | 0.027551 | 0.027551 | 0.0010616 | 0.0010616 | 0.013224 | 0.013224 | 0.017336 | 0.017336 | N/A | N/A | 3.6266e-07 | 3.6266e-07 | 0.024425 | 0.024425 | 0.04198 | 0.04198 | 0.020672 | 0.020672 | 2221 | 785 | 32 | 204 | NO
2013-02-28 | N/A | N/A | 0.0036611 | 0.0036611 | 0.22391 | 0.22391 | 2.3073 | 2.3073 | 0.94306 | 0.94306 | N/A | N/A | 1.3934e-05 | 1.3934e-05 | 0.0020276 | 0.0020276 | 0.028814 | 0.028814 | 0.011629 | 0.011629 | N/A | N/A | 0.0071624 | 0.0071624 | 0.030908 | 0.030908 | 0.018277 | 0.018277 | 0.015643 | 0.015643 | 1263 | 493 | 20 | 174 | NO
2013-03-01 | N/A | N/A | 0.14322 | 0.14322 | 0.013714 | 0.013714 | 1.237 | 1.237 | 0.54849 | 0.54849 | N/A | N/A | 0.010318 | 0.010318 | 0.00019144 | 0.00019144 | 0.050162 | 0.050162 | 0.02414 | 0.02414 | N/A | N/A | 0.0082283 | 0.0082283 | 0.00016424 | 0.00016424 | 0.023532 | 0.023532 | 0.012811 | 0.012811 | 1965 | 568 | 48 | 209 | NO
2013-03-02 | N/A | N/A | 0.034065 | 0.034065 | 0.066614 | 0.066614 | 0.052718 | 0.052718 | 0.047026 | 0.047026 | N/A | N/A | 0.00027171 | 0.00027171 | 0.0014793 | 0.0014793 | 0.0029081 | 0.0029081 | 0.0015131 | 0.0015131 | N/A | N/A | 0.01508 | 0.01508 | 0.040324 | 0.040324 | 0.0088713 | 0.0088713 | 0.017045 | 0.017045 | 248 | 180 | 3 | 18 | NO
2013-03-03 | N/A | N/A | 0.22154 | 0.22154 | 0.064325 | 0.064325 | 0.000728 | 0.000728 | 0.10781 | 0.10781 | N/A | N/A | 0.0010555 | 0.0010555 | 0.00049601 | 0.00049601 | 3.8723e-06 | 3.8723e-06 | 0.00054678 | 0.00054678 | N/A | N/A | 0.0033654 | 0.0033654 | 0.019726 | 0.019726 | 0.0019476 | 0.0019476 | 0.0056585 | 0.0056585 | 237 | 146 | 6 | 17 | NO
2013-03-04 | N/A | N/A | 0.077818 | 0.077818 | 0.39543 | 0.39543 | 0.92745 | 0.92745 | 0.46542 | 0.46542 | N/A | N/A | 0.00023339 | 0.00023339 | 0.017926 | 0.017926 | 0.018696 | 0.018696 | 0.010534 | 0.010534 | N/A | N/A | 0.030209 | 0.030209 | 0.011111 | 0.011111 | 0.012174 | 0.012174 | 0.019831 | 0.019831 | 995 | 406 | 16 | 73 | NO
2013-03-05 | N/A | N/A | 0.57316 | 0.57316 | 0.22105 | 0.22105 | 0.19886 | 0.19886 | 0.36547 | 0.36547 | N/A | N/A | 0.0034835 | 0.0034835 | 0.0015751 | 0.0015751 | 0.0013514 | 0.0013514 | 0.0023174 | 0.0023174 | N/A | N/A | 0.0033619 | 0.0033619 | 0.0044021 | 0.0044021 | 0.0035468 | 0.0035468 | 0.0036153 | 0.0036153 | 1341 | 499 | 17 | 158 | NO
2013-03-06 | N/A | N/A | 0.20949 | 0.20949 | 1.8451 | 1.8451 | 0.64074 | 0.64074 | 0.66286 | 0.66286 | N/A | N/A | 0.0012053 | 0.0012053 | 0.016116 | 0.016116 | 0.0019091 | 0.0019091 | 0.0040759 | 0.0040759 | N/A | N/A | 3.6266e-07 | 3.6266e-07 | 0.046807 | 0.046807 | 0.0079226 | 0.0079226 | 0.011246 | 0.011246 | 1334 | 484 | 12 | 101 | NO
2013-03-07 | N/A | N/A | 0.35256 | 0.35256 | 0.34915 | 0.34915 | 0.11904 | 0.11904 | 0.26063 | 0.26063 | N/A | N/A | 0.0074163 | 0.0074163 | 0.048522 | 0.048522 | 0.00096808 | 0.00096808 | 0.012049 | 0.012049 | N/A | N/A | 0.010005 | 0.010005 | 0.05711 | 0.05711 | 0.019067 | 0.019067 | 0.021748 | 0.021748 | 1271 | 629 | 18 | 232 | NO
2013-03-08 | N/A | N/A | 0.113 | 0.113 | 0.044972 | 0.044972 | 0.87213 | 0.87213 | 0.39809 | 0.39809 | N/A | N/A | 0.0053367 | 0.0053367 | 0.00063524 | 0.00063524 | 0.0074 | 0.0074 | 0.0053254 | 0.0053254 | N/A | N/A | 3.6266e-07 | 3.6266e-07 | 0.028202 | 0.028202 | 0.0063853 | 0.0063853 | 0.0074064 | 0.0074064 | 1238 | 458 | 7 | 79 | NO
2013-03-09 | N/A | N/A | 0.15259 | 0.15259 | 1.1164 | 1.1164 | 0.13301 | 0.13301 | 0.31268 | 0.31268 | N/A | N/A | 0.0012819 | 0.0012819 | 0.019675 | 0.019675 | 0.00085191 | 0.00085191 | 0.0043152 | 0.0043152 | N/A | N/A | 3.6266e-07 | 3.6266e-07 | 0.017246 | 0.017246 | 0.012213 | 0.012213 | 0.007779 | 0.007779 | 605 | 278 | 6 | 29 | NO
2013-03-10 | N/A | N/A | 0.0099453 | 0.0099453 | 0.063846 | 0.063846 | 0.81973 | 0.81973 | 0.33607 | 0.33607 | N/A | N/A | 5.9219e-05 | 5.9219e-05 | 0.00059173 | 0.00059173 | 0.021801 | 0.021801 | 0.0086561 | 0.0086561 | N/A | N/A | 0.0065737 | 0.0065737 | 0.012182 | 0.012182 | 0.021367 | 0.021367 | 0.013336 | 0.013336 | 1258 | 565 | 41 | 357 | NO
2013-03-11 | N/A | N/A | 0.24837 | 0.24837 | 0.044484 | 0.044484 | 0.046793 | 0.046793 | 0.13404 | 0.13404 | N/A | N/A | 0.0036054 | 0.0036054 | 0.0004351 | 0.0004351 | 0.00041047 | 0.00041047 | 0.0018039 | 0.0018039 | N/A | N/A | 0.010451 | 0.010451 | 0.016672 | 0.016672 | 0.020147 | 0.020147 | 0.015326 | 0.015326 | 459 | 225 | 2 | 12 | NO
2013-03-12 | N/A | N/A | 0.63791 | 0.63791 | 0.070825 | 0.070825 | 0.10313 | 0.10313 | 0.33003 | 0.33003 | N/A | N/A | 0.0033302 | 0.0033302 | 0.00071356 | 0.00071356 | 0.00087514 | 0.00087514 | 0.0019145 | 0.0019145 | N/A | N/A | 0.0068977 | 0.0068977 | 0.00016424 | 0.00016424 | 0.01126 | 0.01126 | 0.0074322 | 0.0074322 | 1348 | 562 | 16 | 145 | NO
2013-03-13 | N/A | N/A | 0.0047445 | 0.0047445 | 0.37761 | 0.37761 | 0.14083 | 0.14083 | 0.12287 | 0.12287 | N/A | N/A | 6.6186e-05 | 6.6186e-05 | 0.0051951 | 0.0051951 | 0.012213 | 0.012213 | 0.0057101 | 0.0057101 | N/A | N/A | 0.0077859 | 0.0077859 | 0.0059511 | 0.0059511 | 0.024345 | 0.024345 | 0.013944 | 0.013944 | 814 | 416 | 10 | 149 | NO
2013-03-14 | N/A | N/A | 0.0054969 | 0.0054969 | 0.79193 | 0.79193 | 0.10355 | 0.10355 | 0.18073 | 0.18073 | N/A | N/A | 5.9219e-05 | 5.9219e-05 | 0.038045 | 0.038045 | 0.00051115 | 0.00051115 | 0.0068476 | 0.0068476 | N/A | N/A | 3.6266e-07 | 3.6266e-07 | 0.027802 | 0.027802 | 0.021096 | 0.021096 | 0.013091 | 0.013091 | 782 | 403 | 19 | 98 | NO
2013-03-15 | N/A | N/A | 0.016972 | 0.016972 | 0.31412 | 0.31412 | 0.3139 | 0.3139 | 0.18483 | 0.18483 | N/A | N/A | 0.00052601 | 0.00052601 | 0.0016099 | 0.0016099 | 0.0028152 | 0.0028152 | 0.00161 | 0.00161 | N/A | N/A | 0.00672 | 0.00672 | 0.014279 | 0.014279 | 0.040516 | 0.040516 | 0.021255 | 0.021255 | 659 | 338 | 10 | 48 | NO
2013-03-16 | N/A | N/A | 0.30504 | 0.30504 | 1.2312 | 1.2312 | 1.4284 | 1.4284 | 0.90565 | 0.90565 | N/A | N/A | 0.0063504 | 0.0063504 | 0.0072574 | 0.0072574 | 0.023257 | 0.023257 | 0.013121 | 0.013121 | N/A | N/A | 0.0056332 | 0.0056332 | 0.09452 | 0.09452 | 0.060505 | 0.060505 | 0.042567 | 0.042567 | 1300 | 391 | 21 | 116 | NO
2013-03-17 | N/A | N/A | 0.16684 | 0.16684 | 0.43194 | 0.43194 | 0.1053 | 0.1053 | 0.18891 | 0.18891 | N/A | N/A | 0.0003379 | 0.0003379 | 0.0016186 | 0.0016186 | 0.00061957 | 0.00061957 | 0.00067098 | 0.00067098 | N/A | N/A | 3.6266e-07 | 3.6266e-07 | 0.022111 | 0.022111 | 0.0038837 | 0.0038837 | 0.0053677 | 0.0053677 | 425 | 190 | 4 | 47 | NO
2013-03-18 | N/A | N/A | 1.22 | 1.22 | 0.02306 | 0.02306 | 0.73799 | 0.73799 | 0.82312 | 0.82312 | N/A | N/A | 0.015007 | 0.015007 | 0.00012183 | 0.00012183 | 0.0039498 | 0.0039498 | 0.0080911 | 0.0080911 | N/A | N/A | 0.020097 | 0.020097 | 0.0090141 | 0.0090141 | 0.012461 | 0.012461 | 0.015181 | 0.015181 | 1006 | 422 | 18 | 114 | NO
2013-03-19 | N/A | N/A | 0.0012506 | 0.0012506 | 0.12001 | 0.12001 | 0.5245 | 0.5245 | 0.22659 | 0.22659 | N/A | N/A | 1.3934e-05 | 1.3934e-05 | 0.00067005 | 0.00067005 | 0.0085075 | 0.0085075 | 0.0034503 | 0.0034503 | N/A | N/A | 3.6266e-07 | 3.6266e-07 | 0.0072825 | 0.0072825 | 0.045256 | 0.045256 | 0.018969 | 0.018969 | 1082 | 412 | 12 | 80 | NO
2013-03-20 | N/A | N/A | 0.1951 | 0.1951 | 0.35169 | 0.35169 | 0.020771 | 0.020771 | 0.15417 | 0.15417 | N/A | N/A | 0.00061658 | 0.00061658 | 0.01629 | 0.01629 | 0.00029817 | 0.00029817 | 0.0032201 | 0.0032201 | N/A | N/A | 0.011189 | 0.011189 | 0.042969 | 0.042969 | 0.029608 | 0.029608 | 0.023925 | 0.023925 | 744 | 341 | 10 | 112 | NO
2013-03-21 | N/A | N/A | 4.2541 | 4.2541 | 38.973 | 38.973 | 12.8872 | 12.8872 | 13.6739 | 13.6739 | N/A | N/A | 0.049904 | 0.049904 | 0.092267 | 0.092267 | 0.10055 | 0.10055 | 0.077087 | 0.077087 | N/A | N/A | 0.035302 | 0.035302 | 0.33701 | 0.33701 | 0.13914 | 0.13914 | 0.12843 | 0.12843 | 11098 | 2161 | 146 | 1163 | Yes
2013-03-22 | N/A | N/A | 0.22442 | 0.22442 | 0.81624 | 0.81624 | 0.34656 | 0.34656 | 0.3752 | 0.3752 | N/A | N/A | 0.0011286 | 0.0011286 | 0.01267 | 0.01267 | 0.0053438 | 0.0053438 | 0.0047862 | 0.0047862 | N/A | N/A | 0.004818 | 0.004818 | 0.034041 | 0.034041 | 0.02364 | 0.02364 | 0.017267 | 0.017267 | 2915 | 934 | 27 | 279 | NO
2013-03-23 | N/A | N/A | 0.014397 | 0.014397 | 0.12584 | 0.12584 | 0.45763 | 0.45763 | 0.20716 | 0.20716 | N/A | N/A | 0.00024733 | 0.00024733 | 0.0011835 | 0.0011835 | 0.0086817 | 0.0086817 | 0.0037093 | 0.0037093 | N/A | N/A | 0.0026617 | 0.0026617 | 0.032266 | 0.032266 | 0.02182 | 0.02182 | 0.015308 | 0.015308 | 512 | 215 | 9 | 22 | NO
2013-03-24 | N/A | N/A | 0.0073501 | 0.0073501 | 0.045572 | 0.045572 | 0.045964 | 0.045964 | 0.029107 | 0.029107 | N/A | N/A | 6.2703e-05 | 6.2703e-05 | 0.00050471 | 0.00050471 | 0.00031753 | 0.00031753 | 0.00023931 | 0.00023931 | N/A | N/A | 3.6266e-07 | 3.6266e-07 | 0.081397 | 0.081397 | 0.012012 | 0.012012 | 0.018866 | 0.018866 | 260 | 172 | 2 | 27 | NO
2013-03-25 | N/A | N/A | 0.44258 | 0.44258 | 0.11486 | 0.11486 | 0.45751 | 0.45751 | 0.39137 | 0.39137 | N/A | N/A | 0.0088097 | 0.0088097 | 0.0014271 | 0.0014271 | 0.0035587 | 0.0035587 | 0.0054708 | 0.0054708 | N/A | N/A | 0.014342 | 0.014342 | 0.030952 | 0.030952 | 0.00027474 | 0.00027474 | 0.011731 | 0.011731 | 1005 | 394 | 7 | 40 | NO
2013-03-26 | N/A | N/A | 0.00020901 | 0.00020901 | 0.11177 | 0.11177 | 0.11541 | 0.11541 | 0.064688 | 0.064688 | N/A | N/A | 1.3934e-05 | 1.3934e-05 | 0.001079 | 0.001079 | 0.00074736 | 0.00074736 | 0.00048619 | 0.00048619 | N/A | N/A | 0.0037695 | 0.0037695 | 0.042186 | 0.042186 | 0.023141 | 0.023141 | 0.018033 | 0.018033 | 706 | 326 | 3 | 49 | NO
2013-03-27 | N/A | N/A | 0.23241 | 0.23241 | 1.7038 | 1.3004 | 1.5902 | 1.5902 | 1.0196 | 0.94938 | N/A | N/A | 0.0099767 | 0.0099767 | 0.016133 | 0.014176 | 0.032965 | 0.032965 | 0.02004 | 0.019699 | N/A | N/A | 0.020159 | 0.020159 | 0.078186 | 0.078186 | 0.00094078 | 0.00094078 | 0.022742 | 0.022742 | 2346 | 595 | 33 | 150 | NO | TFB suppressed reclose operations
2013-03-28 | N/A | N/A | 2.7507 | 2.7507 | 2.246 | 2.246 | 2.7825 | 2.7825 | 2.6753 | 2.6753 | N/A | N/A | 0.052162 | 0.052162 | 0.035957 | 0.035957 | 0.053744 | 0.053744 | 0.04996 | 0.04996 | N/A | N/A | 0.049246 | 0.049246 | 0.078586 | 0.078586 | 0.054367 | 0.054367 | 0.056356 | 0.056356 | 3633 | 894 | 51 | 433 | NO
2013-03-29 | N/A | N/A | 0.19362 | 0.19362 | 0.0050297 | 0.0050297 | 0.11062 | 0.11062 | 0.12833 | 0.12833 | N/A | N/A | 0.00034835 | 0.00034835 | 4.351e-05 | 4.351e-05 | 0.004368 | 0.004368 | 0.0018675 | 0.0018675 | N/A | N/A | 0.0015331 | 0.0015331 | 0.018047 | 0.018047 | 0.00051483 | 0.00051483 | 0.0040091 | 0.0040091 | 253 | 167 | 5 | 22 | NO
2013-03-30 | N/A | N/A | 0.019173 | 0.019173 | 1.1681 | 1.1681 | 1.1722 | 1.1722 | 0.67017 | 0.67017 | N/A | N/A | 0.00028565 | 0.00028565 | 0.033259 | 0.033259 | 0.017549 | 0.017549 | 0.012777 | 0.012777 | N/A | N/A | 3.6266e-07 | 3.6266e-07 | 0.058354 | 0.058354 | 0.041863 | 0.041863 | 0.026532 | 0.026532 | 525 | 175 | 9 | 20 | NO
2013-03-31 | N/A | N/A | 0.05977 | 0.05977 | 0.0057868 | 0.0057868 | 0.023087 | 0.023087 | 0.036025 | 0.036025 | N/A | N/A | 0.0004006 | 0.0004006 | 7.8318e-05 | 7.8318e-05 | 0.00034076 | 0.00034076 | 0.0003211 | 0.0003211 | N/A | N/A | 0.010263 | 0.010263 | 0.010441 | 0.010441 | 0.03183 | 0.03183 | 0.01873 | 0.01873 | 239 | 103 | 0 | 23 | NO
2013-04-01 | N/A | N/A | 0.48504 | 0.48504 | 0.034181 | 0.034181 | 0.060447 | 0.060447 | 0.24049 | 0.24049 | N/A | N/A | 0.013861 | 0.013861 | 0.00040029 | 0.00040029 | 0.00035625 | 0.00035625 | 0.0062357 | 0.0062357 | N/A | N/A | 3.6266e-07 | 3.6266e-07 | 0.017116 | 0.017116 | 0.0027337 | 0.0027337 | 0.0040485 | 0.0040485 | 619 | 179 | 4 | 31 | NO
2013-04-02 | N/A | N/A | 0.058355 | 0.058355 | 0.0086237 | 0.0086237 | 0.01133 | 0.01133 | 0.031306 | 0.031306 | N/A | N/A | 0.00063051 | 0.00063051 | 9.5722e-05 | 9.5722e-05 | 0.00015102 | 0.00015102 | 0.00034988 | 0.00034988 | N/A | N/A | 0.0092037 | 0.0092037 | 0.00016424 | 0.00016424 | 0.0012661 | 0.0012661 | 0.0045256 | 0.0045256 | 498 | 605 | 10 | 51 | NO
2013-04-03 | N/A | N/A | 0.045822 | 0.045822 | 0.0030805 | 0.0030805 | 0.070453 | 0.070453 | 0.048017 | 0.048017 | N/A | N/A | 0.00030306 | 0.00030306 | 4.351e-05 | 4.351e-05 | 0.0034038 | 0.0034038 | 0.0014707 | 0.0014707 | N/A | N/A | 3.6266e-07 | 3.6266e-07 | 0.016959 | 0.016959 | 0.0066679 | 0.0066679 | 0.0055601 | 0.0055601 | 556 | 314 | 9 | 83 | NO
2013-04-04 | N/A | N/A | 0.25468 | 0.25468 | 0.058895 | 0.058895 | 0.34121 | 0.34121 | 0.25445 | 0.25445 | N/A | N/A | 0.006967 | 0.006967 | 0.00063524 | 0.00063524 | 0.00066991 | 0.00066991 | 0.0034018 | 0.0034018 | N/A | N/A | 3.6266e-07 | 3.6266e-07 | 0.0076653 | 0.0076653 | 0.0077328 | 0.0077328 | 0.004359 | 0.004359 | 498 | 284 | 7 | 47 | NO
2013-04-05 | N/A | N/A | 0.066768 | 0.066768 | 0.15384 | 0.15384 | 0.041972 | 0.041972 | 0.072225 | 0.072225 | N/A | N/A | 0.00039712 | 0.00039712 | 0.0055345 | 0.0055345 | 0.00028655 | 0.00028655 | 0.0012481 | 0.0012481 | N/A | N/A | 3.6266e-07 | 3.6266e-07 | 0.0095537 | 0.0095537 | 0.0010105 | 0.0010105 | 0.0020583 | 0.0020583 | 675 | 339 | 6 | 85 | NO
2013-04-06 | N/A | N/A | 1.3622 | 1.3622 | 0.012 | 0.012 | 0.063684 | 0.063684 | 0.61928 | 0.61928 | N/A | N/A | 0.035842 | 0.035842 | 9.5722e-05 | 9.5722e-05 | 0.00054212 | 0.00054212 | 0.015813 | 0.015813 | N/A | N/A | 0.020149 | 0.020149 | 0.017072 | 0.017072 | 0.039447 | 0.039447 | 0.027162 | 0.027162 | 1061 | 231 | 10 | 53 | NO
2013-04-07 | N/A | N/A | 0.32999 | 0.32999 | 0.062898 | 0.062898 | 0.051467 | 0.051467 | 0.17456 | 0.17456 | N/A | N/A | 0.010395 | 0.010395 | 0.00054822 | 0.00054822 | 0.00047629 | 0.00047629 | 0.0048014 | 0.0048014 | N/A | N/A | 0.025607 | 0.025607 | 0.0065689 | 0.0065689 | 0.014955 | 0.014955 | 0.018127 | 0.018127 | 262 | 145 | 5 | 22 | NO
2013-04-08 | N/A | N/A | 0.046755 | 0.046755 | 0.041447 | 0.041447 | 0.17764 | 0.17764 | 0.097025 | 0.097025 | N/A | N/A | 0.00057129 | 0.00057129 | 0.00040029 | 0.00040029 | 0.0014831 | 0.0014831 | 0.00089817 | 0.00089817 | N/A | N/A | 0.02914 | 0.02914 | 0.0070736 | 0.0070736 | 0.060342 | 0.060342 | 0.037504 | 0.037504 | 535 | 343 | 7 | 83 | NO
2013-04-09 | N/A | N/A | 0.013209 | 0.013209 | 0.008876 | 0.008876 | 0.45911 | 0.45911 | 0.18686 | 0.18686 | N/A | N/A | 0.00011147 | 0.00011147 | 0.00012183 | 0.00012183 | 0.0051386 | 0.0051386 | 0.0020796 | 0.0020796 | N/A | N/A | 3.6266e-07 | 3.6266e-07 | 0.067091 | 0.067091 | 0.0056611 | 0.0056611 | 0.013892 | 0.013892 | 830 | 334 | 12 | 61 | NO
2013-04-10 | N/A | N/A | 0.072871 | 0.072871 | 0.020598 | 0.020598 | 0.0079382 | 0.0079382 | 0.038375 | 0.038375 | N/A | N/A | 0.00077333 | 0.00077333 | 0.00017404 | 0.00017404 | 6.9702e-05 | 6.9702e-05 | 0.0003938 | 0.0003938 | N/A | N/A | 0.016341 | 0.016341 | 0.010781 | 0.010781 | 0.010869 | 0.010869 | 0.013233 | 0.013233 | 821 | 406 | 20 | 72 | NO
2013-04-11 | N/A | N/A | 0.36498 | 0.36498 | 0.092084 | 0.092084 | 0.070565 | 0.070565 | 0.20232 | 0.20232 | N/A | N/A | 0.020448 | 0.020448 | 0.00046991 | 0.00046991 | 0.0030436 | 0.0030436 | 0.010163 | 0.010163 | N/A | N/A | 0.014363 | 0.014363 | 0.0055508 | 0.0055508 | 0.0089177 | 0.0089177 | 0.010699 | 0.010699 | 815 | 318 | 26 | 74 | NO
2013-04-12 | N/A | N/A | 0.00116 | 0.00116 | 0.0059783 | 0.0059783 | 0.36833 | 0.36833 | 0.14561 | 0.14561 | N/A | N/A | 4.5285e-05 | 4.5285e-05 | 8.702e-05 | 8.702e-05 | 0.0018742 | 0.0018742 | 0.00076792 | 0.00076792 | N/A | N/A | 0.0088449 | 0.0088449 | 0.075985 | 0.075985 | 0.0222 | 0.0222 | 0.025755 | 0.025755 | 560 | 336 | 16 | 72 | NO
2013-04-13 | N/A | N/A | 0.016076 | 0.016076 | 0.050219 | 0.050219 | 0.044477 | 0.044477 | 0.033128 | 0.033128 | N/A | N/A | 0.00022643 | 0.00022643 | 0.00051342 | 0.00051342 | 0.00023234 | 0.00023234 | 0.00027869 | 0.00027869 | N/A | N/A | 0.027562 | 0.027562 | 0.052802 | 0.052802 | 0.0060058 | 0.0060058 | 0.023524 | 0.023524 | 239 | 139 | 5 | 19 | NO
2013-04-14 | N/A | N/A | 0.048612 | 0.048612 | 0.38754 | 0.38754 | 0.0041976 | 0.0041976 | 0.090232 | 0.090232 | N/A | N/A | 0.00072108 | 0.00072108 | 0.0026367 | 0.0026367 | 4.2595e-05 | 4.2595e-05 | 0.00078912 | 0.00078912 | N/A | N/A | 3.6266e-07 | 3.6266e-07 | 0.06998 | 0.06998 | 0.017201 | 0.017201 | 0.018908 | 0.018908 | 203 | 142 | 2 | 15 | NO
2013-04-15 | N/A | N/A | 0.041826 | 0.041826 | 1.3558 | 1.3558 | 0.087197 | 0.087197 | 0.28828 | 0.28828 | N/A | N/A | 0.00037273 | 0.00037273 | 0.0087194 | 0.0087194 | 0.00059246 | 0.00059246 | 0.0019115 | 0.0019115 | N/A | N/A | 0.026008 | 0.026008 | 0.024652 | 0.024652 | 0.015009 | 0.015009 | 0.02147 | 0.02147 | 898 | 350 | 12 | 112 | NO
2013-04-16 | N/A | N/A | 0.0030933 | 0.0030933 | 0.0026541 | 0.0026541 | 0.07891 | 0.07891 | 0.032672 | 0.032672 | N/A | N/A | 2.4384e-05 | 2.4384e-05 | 7.8318e-05 | 7.8318e-05 | 0.0017696 | 0.0017696 | 0.00071642 | 0.00071642 | N/A | N/A | 3.6266e-07 | 3.6266e-07 | 0.00016424 | 0.00016424 | 0.037348 | 0.037348 | 0.014637 | 0.014637 | 617 | 379 | 11 | 74 | NO
2013-04-17 | N/A | N/A | 0.015303 | 0.015303 | 0.051864 | 0.051864 | 0.017604 | 0.017604 | 0.022566 | 0.022566 | N/A | N/A | 0.0002752 | 0.0002752 | 0.00068746 | 0.00068746 | 0.00024783 | 0.00024783 | 0.00033625 | 0.00033625 | N/A | N/A | 3.6266e-07 | 3.6266e-07 | 0.010058 | 0.010058 | 0.00058453 | 0.00058453 | 0.0019795 | 0.0019795 | 449 | 284 | 6 | 51 | NO
2013-04-18 | N/A | N/A | 0.01538 | 0.01538 | 1.3729 | 1.3729 | 0.50248 | 0.50248 | 0.44218 | 0.44218 | N/A | N/A | 0.00018462 | 0.00018462 | 0.0055693 | 0.0055693 | 0.0094213 | 0.0094213 | 0.0047347 | 0.0047347 | N/A | N/A | 0.00040445 | 0.00040445 | 0.035224 | 0.035224 | 0.013522 | 0.013522 | 0.011596 | 0.011596 | 610 | 292 | 11 | 75 | NO
2013-04-19 | N/A | N/A | 0.19382 | 0.19382 | 0.40336 | 0.40336 | 0.28471 | 0.28471 | 0.26584 | 0.26584 | N/A | N/A | 0.0064131 | 0.0064131 | 0.002454 | 0.002454 | 0.0061918 | 0.0061918 | 0.0056374 | 0.0056374 | N/A | N/A | 0.016596 | 0.016596 | 0.023938 | 0.023938 | 0.014866 | 0.014866 | 0.017197 | 0.017197 | 856 | 362 | 7 | 76 | NO
2013-04-20 | N/A | N/A | 0.00060613 | 0.00060613 | 0.021685 | 0.021685 | 0.001487 | 0.001487 | 0.0046196 | 0.0046196 | N/A | N/A | 1.045e-05 | 1.045e-05 | 0.00014793 | 0.00014793 | 1.5489e-05 | 1.5489e-05 | 3.6351e-05 | 3.6351e-05 | N/A | N/A | 3.6266e-07 | 3.6266e-07 | 0.00016424 | 0.00016424 | 2.6915e-05 | 2.6915e-05 | 3.9272e-05 | 3.9272e-05 | 364 | 204 | 5 | 87 | NO
2013-04-21 | N/A | N/A | 0.00092312 | 0.00092312 | 0.01549 | 0.01549 | 0.35482 | 0.35482 | 0.14188 | 0.14188 | N/A | N/A | 1.045e-05 | 1.045e-05 | 0.00020015 | 0.00020015 | 0.0050921 | 0.0050921 | 0.0020311 | 0.0020311 | N/A | N/A | 0.009998 | 0.009998 | 0.010624 | 0.010624 | 0.006908 | 0.006908 | 0.0088983 | 0.0088983 | 306 | 185 | 5 | 16 | NO
2013-04-22 | N/A | N/A | 0.053109 | 0.053109 | 1.4368 | 1.4368 | 1.1333 | 1.1333 | 0.71646 | 0.71646 | N/A | N/A | 0.00053646 | 0.00053646 | 0.025166 | 0.025166 | 0.0044183 | 0.0044183 | 0.0063417 | 0.0063417 | N/A | N/A | 3.6266e-07 | 3.6266e-07 | 0.01722 | 0.01722 | 0.0075469 | 0.0075469 | 0.0059493 | 0.0059493 | 827 | 271 | 5 | 32 | NO
2013-04-23 | N/A | N/A | 0.31358 | 0.31358 | 0.024244 | 0.024244 | 0.10375 | 0.10375 | 0.18115 | 0.18115 | N/A | N/A | 0.00093009 | 0.00093009 | 0.00020885 | 0.00020885 | 0.0011849 | 0.0011849 | 0.00090423 | 0.00090423 | N/A | N/A | 3.6266e-07 | 3.6266e-07 | 0.026209 | 0.026209 | 0.013719 | 0.013719 | 0.0099283 | 0.0099283 | 741 | 329 | 6 | 43 | NO
2013-04-24 | N/A | N/A | 0.1811 | 0.1811 | 0.43698 | 0.43698 | 0.015489 | 0.015489 | 0.16086 | 0.16086 | N/A | N/A | 0.001362 | 0.001362 | 0.017004 | 0.017004 | 0.0001394 | 0.0001394 | 0.0036063 | 0.0036063 | N/A | N/A | 0.013987 | 0.013987 | 0.011329 | 0.011329 | 1.9171e-05 | 1.9171e-05 | 0.0080607 | 0.0080607 | 751 | 373 | 9 | 79 | NO
2013-04-25 | N/A | N/A | 0.018396 | 0.018396 | 0.0067788 | 0.0067788 | 0.0050418 | 0.0050418 | 0.011151 | 0.011151 | N/A | N/A | 0.000317 | 0.000317 | 6.0914e-05 | 6.0914e-05 | 4.2595e-05 | 4.2595e-05 | 0.00016509 | 0.00016509 | N/A | N/A | 0.012652 | 0.012652 | 0.024295 | 0.024295 | 0.022967 | 0.022967 | 0.018713 | 0.018713 | 133 | 98 | 3 | 3 | NO
2013-04-26 | N/A | N/A | 0.092661 | 0.092661 | 0.20135 | 0.20135 | 0.019149 | 0.019149 | 0.082824 | 0.082824 | N/A | N/A | 0.0011983 | 0.0011983 | 0.000905 | 0.000905 | 0.0017193 | 0.0017193 | 0.001351 | 0.001351 | N/A | N/A | 3.6266e-07 | 3.6266e-07 | 0.00016424 | 0.00016424 | 0.0014326 | 0.0014326 | 0.00058908 | 0.00058908 | 601 | 304 | 12 | 30 | NO
2013-04-27 | N/A | N/A | 0.062999 | 0.062999 | 0.048983 | 0.048983 | 0.029155 | 0.029155 | 0.047321 | 0.047321 | N/A | N/A | 0.00019159 | 0.00019159 | 0.0017839 | 0.0017839 | 0.0002943 | 0.0002943 | 0.00050891 | 0.00050891 | N/A | N/A | 0.006511 | 0.006511 | 0.098531 | 0.098531 | 0.027245 | 0.027245 | 0.030638 | 0.030638 | 184 | 136 | 3 | 6 | NO
2013-04-28 | N/A | N/A | 0.90039 | 0.90039 | 0.081581 | 0.081581 | 0.78637 | 0.78637 | 0.71327 | 0.71327 | N/A | N/A | 0.0053053 | 0.0053053 | 0.0012618 | 0.0012618 | 0.0046003 | 0.0046003 | 0.0043258 | 0.0043258 | N/A | N/A | 0.010172 | 0.010172 | 0.0059859 | 0.0059859 | 0.010025 | 0.010025 | 0.009386 | 0.009386 | 655 | 213 | 9 | 27 | NO
2013-04-29 | N/A | N/A | 0.019455 | 0.019455 | 0.12218 | 0.12218 | 0.27287 | 0.27287 | 0.13646 | 0.13646 | N/A | N/A | 0.00026126 | 0.00026126 | 0.00054822 | 0.00054822 | 0.0027764 | 0.0027764 | 0.001295 | 0.001295 | N/A | N/A | 0.0068559 | 0.0068559 | 0.018143 | 0.018143 | 1.9171e-05 | 1.9171e-05 | 0.0061462 | 0.0061462 | 623 | 333 | 5 | 36 | NO
2013-04-30 | N/A | N/A | 0.045902 | 0.045902 | 0.029622 | 0.029622 | 0.036373 | 0.036373 | 0.039341 | 0.039341 | N/A | N/A | 0.0004842 | 0.0004842 | 0.00056563 | 0.00056563 | 0.00029042 | 0.00029042 | 0.00042258 | 0.00042258 | N/A | N/A | 0.022556 | 0.022556 | 0.021119 | 0.021119 | 1.9171e-05 | 1.9171e-05 | 0.013491 | 0.013491 | 454 | 324 | 2 | 52 | NO
2013-05-01 | N/A | N/A | 0.0023792 | 0.0023792 | 0.56908 | 0.56908 | 0.0063157 | 0.0063157 | 0.10256 | 0.10256 | N/A | N/A | 4.1802e-05 | 4.1802e-05 | 0.038289 | 0.038289 | 6.5829e-05 | 6.5829e-05 | 0.0067083 | 0.0067083 | N/A | N/A | 0.0065841 | 0.0065841 | 0.027193 | 0.027193 | 0.028709 | 0.028709 | 0.018825 | 0.018825 | 558 | 308 | 9 | 16 | NO
2013-05-02 | N/A | N/A | 0.0010973 | 0.0010973 | 0.25324 | 0.25324 | 0.25579 | 0.25579 | 0.14461 | 0.14461 | N/A | N/A | 1.3934e-05 | 1.3934e-05 | 0.017648 | 0.017648 | 0.00067378 | 0.00067378 | 0.0033413 | 0.0033413 | N/A | N/A | 3.6266e-07 | 3.6266e-07 | 0.00016424 | 0.00016424 | 0.0013861 | 0.0013861 | 0.00057091 | 0.00057091 | 672 | 267 | 7 | 35 | NO
2013-05-03 | N/A | N/A | 0.32861 | 0.32861 | 2.3773 | 2.3773 | 0.88979 | 0.88979 | 0.9047 | 0.9047 | N/A | N/A | 0.0082384 | 0.0082384 | 0.045224 | 0.045224 | 0.009189 | 0.009189 | 0.015048 | 0.015048 | N/A | N/A | 3.6266e-07 | 3.6266e-07 | 0.086244 | 0.086244 | 0.014227 | 0.014227 | 0.020576 | 0.020576 | 1170 | 420 | 15 | 76 | NO
2013-05-04 | N/A | N/A | 1.668 | 1.668 | 0.31863 | 0.31863 | 0.85852 | 0.85852 | 1.1165 | 1.1165 | N/A | N/A | 0.0093636 | 0.0093636 | 0.0029761 | 0.0029761 | 0.0044532 | 0.0044532 | 0.0063311 | 0.0063311 | N/A | N/A | 0.019403 | 0.019403 | 0.016881 | 0.016881 | 0.019342 | 0.019342 | 0.01894 | 0.01894 | 1230 | 322 | 14 | 56 | NO
2013-05-05 | N/A | N/A | 0.047933 | 0.047933 | 0.010695 | 0.010695 | 0.03506 | 0.03506 | 0.036416 | 0.036416 | N/A | N/A | 0.0003588 | 0.0003588 | 8.702e-05 | 8.702e-05 | 0.00034851 | 0.00034851 | 0.00030747 | 0.00030747 | N/A | N/A | 3.6266e-07 | 3.6266e-07 | 0.003471 | 0.003471 | 1.9171e-05 | 1.9171e-05 | 0.0006118 | 0.0006118 | 155 | 121 | 2 | 0 | NO
2013-05-06 | N/A | N/A | 0.53083 | 0.53083 | 0.11702 | 0.11702 | 0.046886 | 0.046886 | 0.26951 | 0.26951 | N/A | N/A | 0.011858 | 0.011858 | 0.0010007 | 0.0010007 | 0.00046468 | 0.00046468 | 0.0055117 | 0.0055117 | N/A | N/A | 0.0057411 | 0.0057411 | 0.021206 | 0.021206 | 0.015361 | 0.015361 | 0.012196 | 0.012196 | 715 | 388 | 5 | 74 | NO
2013-05-07 | N/A | N/A | 0.41786 | 0.41786 | 0.19338 | 0.19338 | 0.021778 | 0.021778 | 0.22387 | 0.22387 | N/A | N/A | 0.018779 | 0.018779 | 0.0036809 | 0.0036809 | 0.00051115 | 0.00051115 | 0.009006 | 0.009006 | N/A | N/A | 0.030474 | 0.030474 | 0.009397 | 0.009397 | 0.01691 | 0.01691 | 0.0215 | 0.0215 | 698 | 417 | 13 | 69 | NO
2013-05-08 | N/A | N/A | 0.88567 | 0.88567 | 0.015968 | 0.015968 | 0.067618 | 0.067618 | 0.41432 | 0.41432 | N/A | N/A | 0.012983 | 0.012983 | 4.351e-05 | 4.351e-05 | 0.00058085 | 0.00058085 | 0.0058798 | 0.0058798 | N/A | N/A | 0.01152 | 0.01152 | 0.011094 | 0.011094 | 0.0077522 | 0.0077522 | 0.0099722 | 0.0099722 | 935 | 333 | 12 | 27 | NO
2013-05-09 | N/A | N/A | 0.062591 | 0.062591 | 0.031014 | 0.031014 | 0.035114 | 0.035114 | 0.046348 | 0.046348 | N/A | N/A | 0.00030655 | 0.00030655 | 0.00082669 | 0.00082669 | 0.00042595 | 0.00042595 | 0.00044379 | 0.00044379 | N/A | N/A | 0.0099701 | 0.0099701 | 0.00016424 | 0.00016424 | 0.010742 | 0.010742 | 0.0085651 | 0.0085651 | 442 | 304 | 2 | 8 | NO
2013-05-10 | N/A | N/A | 0.028098 | 0.028098 | 0.11628 | 0.11628 | 0.12331 | 0.12331 | 0.08069 | 0.08069 | N/A | N/A | 0.00064793 | 0.00064793 | 0.0037767 | 0.0037767 | 0.0059905 | 0.0059905 | 0.0032822 | 0.0032822 | N/A | N/A | 0.009998 | 0.009998 | 0.0031142 | 0.0031142 | 0.0028692 | 0.0028692 | 0.0060114 | 0.0060114 | 464 | 266 | 8 | 12 | NO
2013-05-11 | N/A | N/A | 0.022535 | 0.022535 | 0.059287 | 0.059287 | 0.018134 | 0.018134 | 0.02721 | 0.02721 | N/A | N/A | 0.00025081 | 0.00025081 | 0.00029587 | 0.00029587 | 0.000182 | 0.000182 | 0.00023174 | 0.00023174 | N/A | N/A | 3.6266e-07 | 3.6266e-07 | 0.0064384 | 0.0064384 | 0.0073572 | 0.0073572 | 0.0039985 | 0.0039985 | 198 | 150 | 1 | 17 | NO
2013-05-12 | N/A | N/A | 0.089982 | 0.089982 | 0.006335 | 0.006335 | 0.22996 | 0.22996 | 0.13017 | 0.13017 | N/A | N/A | 0.0010276 | 0.0010276 | 5.2212e-05 | 5.2212e-05 | 0.0057155 | 0.0057155 | 0.0026915 | 0.0026915 | N/A | N/A | 0.012388 | 0.012388 | 0.0096755 | 0.0096755 | 1.9171e-05 | 1.9171e-05 | 0.0070777 | 0.0070777 | 402 | 90 | 1 | 7 | NO
2013-05-13 | N/A | N/A | 0.025513 | 0.025513 | 0.23387 | 0.23387 | 0.12709 | 0.12709 | 0.10151 | 0.10151 | N/A | N/A | 0.00013237 | 0.00013237 | 0.0015141 | 0.0015141 | 0.0008248 | 0.0008248 | 0.00064372 | 0.00064372 | N/A | N/A | 3.6266e-07 | 3.6266e-07 | 0.016855 | 0.016855 | 0.023501 | 0.023501 | 0.012126 | 0.012126 | 713 | 340 | 7 | 20 | NO
2013-05-14 | N/A | N/A | 0.049647 | 0.049647 | 0.0050907 | 0.0050907 | 0.10559 | 0.10559 | 0.063775 | 0.063775 | N/A | N/A | 0.00095447 | 0.00095447 | 5.2212e-05 | 5.2212e-05 | 0.00028655 | 0.00028655 | 0.00053618 | 0.00053618 | N/A | N/A | 3.6266e-07 | 3.6266e-07 | 0.024008 | 0.024008 | 0.020043 | 0.020043 | 0.012018 | 0.012018 | 512 | 242 | 7 | 18 | NO
2013-05-15 | N/A | N/A | 0.063169 | 0.063169 | 0.02641 | 0.02641 | 0.079406 | 0.079406 | 0.063122 | 0.063122 | N/A | N/A | 0.00053646 | 0.00053646 | 0.00037418 | 0.00037418 | 0.00063893 | 0.00063893 | 0.00054829 | 0.00054829 | N/A | N/A | 0.00013274 | 0.00013274 | 0.010276 | 0.010276 | 0.0033106 | 0.0033106 | 0.0031412 | 0.0031412 | 642 | 357 | 9 | 38 | NO
2013-05-16 | N/A | N/A | 0.011927 | 0.011927 | 0.27108 | 0.27108 | 1.6257 | 1.6257 | 0.68825 | 0.68825 | N/A | N/A | 0.00015676 | 0.00015676 | 0.0019318 | 0.0019318 | 0.0098512 | 0.0098512 | 0.0042576 | 0.0042576 | N/A | N/A | 3.6266e-07 | 3.6266e-07 | 0.01648 | 0.01648 | 0.035246 | 0.035246 | 0.016655 | 0.016655 | 861 | 334 | 4 | 28 | NO
2013-05-17 | N/A | N/A | 1.1317 | 1.1317 | 0.050967 | 0.050967 | 0.58847 | 0.58847 | 0.73113 | 0.73113 | N/A | N/A | 0.017229 | 0.017229 | 0.00029587 | 0.00029587 | 0.0067378 | 0.0067378 | 0.010178 | 0.010178 | N/A | N/A | 0.015892 | 0.015892 | 0.02057 | 0.02057 | 0.00046061 | 0.00046061 | 0.01067 | 0.01067 | 1044 | 357 | 11 | 31 | NO
2013-05-18 | N/A | N/A | 0.0015571 | 0.0015571 | 0.11767 | 0.11767 | 0.43713 | 0.43713 | 0.19214 | 0.19214 | N/A | N/A | 3.4835e-06 | 3.4835e-06 | 0.001401 | 0.001401 | 0.0046352 | 0.0046352 | 0.0020584 | 0.0020584 | N/A | N/A | 0.021831 | 0.021831 | 0.038096 | 0.038096 | 0.0026407 | 0.0026407 | 0.017156 | 0.017156 | 518 | 182 | 9 | 24 | NO
2013-05-19 | N/A | N/A | 0.0076532 | 0.0076532 | 0 | 0 | 0.065156 | 0.065156 | 0.028813 | 0.028813 | N/A | N/A | 0.00021249 | 0.00021249 | 0 | 0 | 0.00052663 | 0.00052663 | 0.00029838 | 0.00029838 | N/A | N/A | 0.00015015 | 0.00015015 | 0.026227 | 0.026227 | 1.9171e-05 | 1.9171e-05 | 0.0046377 | 0.0046377 | 231 | 174 | 3 | 26 | NO
2013-05-20 | N/A | N/A | 0.01051 | 0.01051 | 0.052934 | 0.052934 | 0.19349 | 0.19349 | 0.089466 | 0.089466 | N/A | N/A | 6.967e-05 | 6.967e-05 | 0.0004351 | 0.0004351 | 0.00060408 | 0.00060408 | 0.00034231 | 0.00034231 | N/A | N/A | 3.6266e-07 | 3.6266e-07 | 0.018525 | 0.018525 | 0.0065634 | 0.0065634 | 0.0057918 | 0.0057918 | 573 | 360 | 6 | 29 | NO
2013-05-21 | N/A | N/A | 0.01887 | 0.01887 | 0.0032023 | 0.0032023 | 0.043087 | 0.043087 | 0.025615 | 0.025615 | N/A | N/A | 7.6637e-05 | 7.6637e-05 | 5.2212e-05 | 5.2212e-05 | 0.00042595 | 0.00042595 | 0.00020902 | 0.00020902 | N/A | N/A | 3.6266e-07 | 3.6266e-07 | 0.0050896 | 0.0050896 | 0.0077677 | 0.0077677 | 0.0039243 | 0.0039243 | 494 | 281 | 1 | 38 | NO
2013-05-22 | N/A | N/A | 0.086171 | 0.086171 | 0.014889 | 0.014889 | 0.34927 | 0.34927 | 0.17667 | 0.17667 | N/A | N/A | 0.00079772 | 0.00079772 | 9.5722e-05 | 9.5722e-05 | 0.0015412 | 0.0015412 | 0.00096633 | 0.00096633 | N/A | N/A | 0.0074864 | 0.0074864 | 0.0075957 | 0.0075957 | 0.022657 | 0.022657 | 0.013439 | 0.013439 | 766 | 321 | 14 | 31 | NO
2013-05-23 | N/A | N/A | 0.079632 | 0.079632 | 0.087385 | 0.087385 | 0.23927 | 0.23927 | 0.14342 | 0.14342 | N/A | N/A | 0.00074198 | 0.00074198 | 0.00055693 | 0.00055693 | 0.0049023 | 0.0049023 | 0.0023371 | 0.0023371 | N/A | N/A | 0.010451 | 0.010451 | 0.0128 | 0.0128 | 1.9171e-05 | 1.9171e-05 | 0.0067794 | 0.0067794 | 746 | 251 | 0 | 18 | NO
2013-05-24 | N/A | N/A | 0.002104 | 0.002104 | 0.16554 | 0.16554 | 0.030831 | 0.030831 | 0.041787 | 0.041787 | N/A | N/A | 2.0901e-05 | 2.0901e-05 | 0.0021059 | 0.0021059 | 0.00020523 | 0.00020523 | 0.0004559 | 0.0004559 | N/A | N/A | 3.6266e-07 | 3.6266e-07 | 0.022041 | 0.022041 | 0.0016494 | 0.0016494 | 0.0044817 | 0.0044817 | 517 | 243 | 7 | 23 | NO
2013-05-25 | N/A | N/A | 0.028969 | 0.028969 | 0.006483 | 0.006483 | 0.025453 | 0.025453 | 0.02368 | 0.02368 | N/A | N/A | 0.00028913 | 0.00028913 | 6.0914e-05 | 6.0914e-05 | 0.0002517 | 0.0002517 | 0.00023477 | 0.00023477 | N/A | N/A | 3.6266e-07 | 3.6266e-07 | 0.00016424 | 0.00016424 | 0.00017794 | 0.00017794 | 9.8343e-05 | 9.8343e-05 | 233 | 112 | 5 | 9 | NO
2013-05-26 | N/A | N/A | 0.035608 | 0.035608 | 0.0072748 | 0.0072748 | 0.39353 | 0.39353 | 0.17068 | 0.17068 | N/A | N/A | 0.00027171 | 0.00027171 | 0.00032197 | 0.00032197 | 0.0031714 | 0.0031714 | 0.0014147 | 0.0014147 | N/A | N/A | 3.6266e-07 | 3.6266e-07 | 0.0026791 | 0.0026791 | 0.0084724 | 0.0084724 | 0.0037804 | 0.0037804 | 491 | 131 | 7 | 9 | NO
2013-05-27 | N/A | N/A | 0.1029 | 0.1029 | 0.019118 | 0.019118 | 0.15402 | 0.15402 | 0.10831 | 0.10831 | N/A | N/A | 0.00064444 | 0.00064444 | 0.00015664 | 0.00015664 | 0.0016883 | 0.0016883 | 0.00096785 | 0.00096785 | N/A | N/A | 0.0056471 | 0.0056471 | 0.032831 | 0.032831 | 0.022018 | 0.022018 | 0.016782 | 0.016782 | 667 | 280 | 3 | 15 | NO
2013-05-28 | N/A | N/A | 0.22248 | 0.22248 | 0.80172 | 0.80172 | 0.096002 | 0.096002 | 0.27383 | 0.27383 | N/A | N/A | 0.0019194 | 0.0019194 | 0.0036461 | 0.0036461 | 0.001789 | 0.001789 | 0.0021689 | 0.0021689 | N/A | N/A | 0.00010138 | 0.00010138 | 0.071355 | 0.071355 | 0.031164 | 0.031164 | 0.024653 | 0.024653 | 761 | 262 | 4 | 27 | NO
2013-05-29 | N/A | N/A | 0.022012 | 0.022012 | 0.0099464 | 0.0099464 | 0.044171 | 0.044171 | 0.028579 | 0.028579 | N/A | N/A | 0.00014282 | 0.00014282 | 7.8318e-05 | 7.8318e-05 | 0.00028268 | 0.00028268 | 0.0001863 | 0.0001863 | N/A | N/A | 3.6266e-07 | 3.6266e-07 | 0.0063078 | 0.0063078 | 0.0090765 | 0.0090765 | 0.0046483 | 0.0046483 | 548 | 271 | 4 | 13 | NO
2013-05-30 | N/A | N/A | 0.016383 | 0.016383 | 0.01877 | 0.01877 | 0.0038917 | 0.0038917 | 0.011913 | 0.011913 | N/A | N/A | 0.00017417 | 0.00017417 | 0.00016534 | 0.00016534 | 2.7106e-05 | 2.7106e-05 | 0.00011511 | 0.00011511 | N/A | N/A | 0.0056262 | 0.0056262 | 0.006273 | 0.006273 | 0.0044917 | 0.0044917 | 0.005295 | 0.005295 | 476 | 313 | 5 | 38 | NO
2013-05-31 | N/A | N/A | 0.00098931 | 0.00098931 | 0.50817 | 0.50817 | 0.040346 | 0.040346 | 0.10466 | 0.10466 | N/A | N/A | 5.2252e-05 | 5.2252e-05 | 0.023661 | 0.023661 | 0.0042092 | 0.0042092 | 0.0057874 | 0.0057874 | N/A | N/A | 3.6266e-07 | 3.6266e-07 | 0.018125 | 0.018125 | 0.022765 | 0.022765 | 0.012059 | 0.012059 | 622 | 280 | 8 | 15 | NO
2013-06-01 | N/A | N/A | 0.14244 | 0.14244 | 0.19369 | 0.19369 | 0.16735 | 0.16735 | 0.1611 | 0.1611 | N/A | N/A | 0.00026823 | 0.00026823 | 0.0011835 | 0.0011835 | 0.00083255 | 0.00083255 | 0.00064826 | 0.00064826 | N/A | N/A | 0.011231 | 0.011231 | 0.029194 | 0.029194 | 4.2404e-05 | 4.2404e-05 | 0.0099813 | 0.0099813 | 816 | 328 | 10 | 36 | NO
2013-06-02 | N/A | N/A | 0.078145 | 0.078145 | 0.045912 | 0.045912 | 0.03444 | 0.03444 | 0.05544 | 0.05544 | N/A | N/A | 0.00016721 | 0.00016721 | 0.00013053 | 0.00013053 | 0.00017425 | 0.00017425 | 0.00016358 | 0.00016358 | N/A | N/A | 0.012792 | 0.012792 | 0.0013825 | 0.0013825 | 0.0068964 | 0.0068964 | 0.0085 | 0.0085 | 324 | 188 | 6 | 30 | NO
2013-06-03 | N/A | N/A | 0.10657 | 0.10657 | 0.30453 | 0.30453 | 0.018998 | 0.018998 | 0.10677 | 0.10677 | N/A | N/A | 0.00073501 | 0.00073501 | 0.008293 | 0.008293 | 0.00013166 | 0.00013166 | 0.0018145 | 0.0018145 | N/A | N/A | 3.6266e-07 | 3.6266e-07 | 0.00016424 | 0.00016424 | 0.027563 | 0.027563 | 0.01081 | 0.01081 | 829 | 360 | 8 | 26 | NO
2013-06-04 | N/A | N/A | 0.082691 | 0.082691 | 0.038802 | 0.038802 | 0.018812 | 0.018812 | 0.050066 | 0.050066 | N/A | N/A | 0.00013237 | 0.00013237 | 0.00025236 | 0.00025236 | 0.00025945 | 0.00025945 | 0.00020296 | 0.00020296 | N/A | N/A | 3.6266e-07 | 3.6266e-07 | 0.020144 | 0.020144 | 1.9171e-05 | 1.9171e-05 | 0.0035138 | 0.0035138 | 481 | 279 | 3 | 21 | NO
2013-06-05 | N/A | N/A | 0.063009 | 0.063009 | 0.02098 | 0.02098 | 0.065051 | 0.065051 | 0.056493 | 0.056493 | N/A | N/A | 0.00066186 | 0.00066186 | 0.00028717 | 0.00028717 | 0.0002517 | 0.0002517 | 0.00043621 | 0.00043621 | N/A | N/A | 3.6266e-07 | 3.6266e-07 | 0.00569 | 0.00569 | 0.0048325 | 0.0048325 | 0.0028807 | 0.0028807 | 478 | 320 | 8 | 25 | NO
2013-06-06 | N/A | N/A | 0.000317 | 0.000317 | 0.19579 | 0.19579 | 0.005518 | 0.005518 | 0.036375 | 0.036375 | N/A | N/A | 3.4835e-06 | 3.4835e-06 | 0.0011052 | 0.0011052 | 3.4851e-05 | 3.4851e-05 | 0.0002075 | 0.0002075 | N/A | N/A | 3.6266e-07 | 3.6266e-07 | 0.036312 | 0.036312 | 0.01255 | 0.01255 | 0.011229 | 0.011229 | 416 | 264 | 5 | 32 | NO
2013-06-07 | N/A | N/A | 0.065841 | 0.065841 | 0.34667 | 0.34667 | 0.025894 | 0.025894 | 0.099096 | 0.099096 | N/A | N/A | 0.00078378 | 0.00078378 | 0.0054822 | 0.0054822 | 0.00015489 | 0.00015489 | 0.0013556 | 0.0013556 | N/A | N/A | 3.6266e-07 | 3.6266e-07 | 0.018682 | 0.018682 | 0.033368 | 0.033368 | 0.016303 | 0.016303 | 590 | 331 | 6 | 41 | NO
2013-06-08 | N/A | N/A | 0.00031003 | 0.00031003 | 0.015933 | 0.015933 | 0.26522 | 0.26522 | 0.10665 | 0.10665 | N/A | N/A | 3.4835e-06 | 3.4835e-06 | 0.00019144 | 0.00019144 | 0.0012662 | 0.0012662 | 0.00053012 | 0.00053012 | N/A | N/A | 0.0054172 | 0.0054172 | 0.03351 | 0.03351 | 0.0064317 | 0.0064317 | 0.010704 | 0.010704 | 204 | 153 | 3 | 20 | NO
2013-06-09 | N/A | N/A | 0.00032396 | 0.00032396 | 0.51745 | 0.51745 | 0.14437 | 0.14437 | 0.14667 | 0.14667 | N/A | N/A | 3.4835e-06 | 3.4835e-06 | 0.0015402 | 0.0015402 | 0.0029275 | 0.0029275 | 0.0014147 | 0.0014147 | N/A | N/A | 3.6266e-07 | 3.6266e-07 | 0.036042 | 0.036042 | 1.9171e-05 | 1.9171e-05 | 0.006281 | 0.006281 | 293 | 142 | 6 | 21 | NO
2013-06-10 | N/A | N/A | 0.036723 | 0.036723 | 0.4368 | 0.4368 | 0.014374 | 0.014374 | 0.097618 | 0.097618 | N/A | N/A | 0.00043195 | 0.00043195 | 0.0046033 | 0.0046033 | 0.00011617 | 0.00011617 | 0.0010345 | 0.0010345 | N/A | N/A | 3.6266e-07 | 3.6266e-07 | 0.0494 | 0.0494 | 0.0092934 | 0.0092934 | 0.012234 | 0.012234 | 208 | 134 | 6 | 19 | NO
2013-06-11 | N/A | N/A | 0.017316 | 0.017316 | 0.059156 | 0.059156 | 0.03216 | 0.03216 | 0.030405 | 0.030405 | N/A | N/A | 0.00016024 | 0.00016024 | 9.5722e-05 | 9.5722e-05 | 0.0015218 | 0.0015218 | 0.00068158 | 0.00068158 | N/A | N/A | 0.012367 | 0.012367 | 0.00016424 | 0.00016424 | 0.0046582 | 0.0046582 | 0.0072277 | 0.0072277 | 512 | 339 | 7 | 83 | NO
2013-06-12 | N/A | N/A | 0.00018811 | 0.00018811 | 0.93493 | 0.93493 | 0.20316 | 0.20316 | 0.24228 | 0.24228 | N/A | N/A | 3.4835e-06 | 3.4835e-06 | 0.020554 | 0.020554 | 0.0044687 | 0.0044687 | 0.0053269 | 0.0053269 | N/A | N/A | 3.6266e-07 | 3.6266e-07 | 0.031526 | 0.031526 | 0.012298 | 0.012298 | 0.010298 | 0.010298 | 925 | 342 | 8 | 15 | NO
2013-06-13 | N/A | N/A | 0.06511 | 0.06511 | 2.5064 | 2.5064 | 2.8459 | 2.8459 | 1.5777 | 1.5777 | N/A | N/A | 0.00056432 | 0.00056432 | 0.019162 | 0.019162 | 0.02134 | 0.02134 | 0.011928 | 0.011928 | N/A | N/A | 0.0033759 | 0.0033759 | 0.028802 | 0.028802 | 0.023389 | 0.023389 | 0.015629 | 0.015629 | 1934 | 481 | 6 | 49 | NO
2013-06-14 | N/A | N/A | 0.2654 | 0.2654 | 0.47661 | 0.47661 | 2.0076 | 2.0076 | 0.9836 | 0.9836 | N/A | N/A | 0.00086042 | 0.00086042 | 0.0081624 | 0.0081624 | 0.02524 | 0.02524 | 0.011667 | 0.011667 | N/A | N/A | 3.6266e-07 | 3.6266e-07 | 0.0026269 | 0.0026269 | 0.0066447 | 0.0066447 | 0.0030564 | 0.0030564 | 1513 | 434 | 10 | 37 | NO
2013-06-15 | N/A | N/A | 0.07556 | 0.07556 | 0.015559 | 0.015559 | 0.42905 | 0.42905 | 0.20338 | 0.20338 | N/A | N/A | 0.00043892 | 0.00043892 | 0.00025236 | 0.00025236 | 0.013301 | 0.013301 | 0.0054375 | 0.0054375 | N/A | N/A | 3.6266e-07 | 3.6266e-07 | 0.010824 | 0.010824 | 0.028996 | 0.028996 | 0.013226 | 0.013226 | 394 | 188 | 8 | 63 | NO
2013-06-16 | N/A | N/A | 0.54264 | 0.54264 | 0.65005 | 0.65005 | 0.062867 | 0.062867 | 0.37368 | 0.37368 | N/A | N/A | 0.0010764 | 0.0010764 | 0.010738 | 0.010738 | 0.00040272 | 0.00040272 | 0.0024946 | 0.0024946 | N/A | N/A | 3.6266e-07 | 3.6266e-07 | 0.039906 | 0.039906 | 0.0073572 | 0.0073572 | 0.0098238 | 0.0098238 | 870 | 210 | 10 | 31 | NO
2013-06-17 | N/A | N/A | 0.21025 | 0.21025 | 0.59354 | 0.59354 | 0.75964 | 0.75964 | 0.49185 | 0.49185 | N/A | N/A | 0.033772 | 0.033772 | 0.0062828 | 0.0062828 | 0.011586 | 0.011586 | 0.02031 | 0.02031 | N/A | N/A | 0.0019685 | 0.0019685 | 0.041264 | 0.041264 | 1.9171e-05 | 1.9171e-05 | 0.0080456 | 0.0080456 | 1426 | 460 | 8 | 82 | NO
2013-06-18 | N/A | N/A | 0.92041 | 0.92041 | 0.15514 | 0.15514 | 0.043715 | 0.043715 | 0.4443 | 0.4443 | N/A | N/A | 0.078539 | 0.078539 | 0.007649 | 0.007649 | 0.00056923 | 0.00056923 | 0.035703 | 0.035703 | N/A | N/A | 0.015126 | 0.015126 | 0.016585 | 0.016585 | 0.023698 | 0.023698 | 0.018733 | 0.018733 | 1803 | 578 | 53 | 309 | NO
2013-06-19 | N/A | N/A | 0.023259 | 0.023259 | 0.066022 | 0.066022 | 0.33532 | 0.33532 | 0.15276 | 0.15276 | N/A | N/A | 0.00051556 | 0.00051556 | 0.00061784 | 0.00061784 | 0.0010804 | 0.0010804 | 0.00075428 | 0.00075428 | N/A | N/A | 3.6266e-07 | 3.6266e-07 | 0.016637 | 0.016637 | 0.036826 | 0.036826 | 0.0173 | 0.0173 | 555 | 336 | 13 | 56 | NO
2013-06-20 | N/A | N/A | 0.1143 | 0.1143 | 0.049149 | 0.049149 | 0.052927 | 0.052927 | 0.078953 | 0.078953 | N/A | N/A | 0.0014213 | 0.0014213 | 0.00052212 | 0.00052212 | 0.00028655 | 0.00028655 | 0.00082093 | 0.00082093 | N/A | N/A | 0.0072181 | 0.0072181 | 0.064672 | 0.064672 | 0.014362 | 0.014362 | 0.020013 | 0.020013 | 741 | 462 | 3 | 103 | NO
2013-06-21 | N/A | N/A | 0.031693 | 0.031693 | 0.1389 | 0.1389 | 0.084308 | 0.084308 | 0.070933 | 0.070933 | N/A | N/A | 0.00026126 | 0.00026126 | 0.0058912 | 0.0058912 | 0.00064668 | 0.00064668 | 0.0013919 | 0.0013919 | N/A | N/A | 3.6266e-07 | 3.6266e-07 | 0.010433 | 0.010433 | 0.00254 | 0.00254 | 0.0028095 | 0.0028095 | 556 | 341 | 8 | 42 | NO
2013-06-22 | N/A | N/A | 0.12254 | 0.12254 | 1.9203 | 1.9203 | 0.48405 | 0.48405 | 0.57685 | 0.57685 | N/A | N/A | 0.0078622 | 0.0078622 | 0.025688 | 0.025688 | 0.0018781 | 0.0018781 | 0.0086243 | 0.0086243 | N/A | N/A | 3.6266e-07 | 3.6266e-07 | 0.005603 | 0.005603 | 0.0073611 | 0.0073611 | 0.0038546 | 0.0038546 | 622 | 317 | 14 | 102 | NO
2013-06-23 | N/A | N/A | 0.02282 | 0.02282 | 0.0295 | 0.0295 | 0.016666 | 0.016666 | 0.021576 | 0.021576 | N/A | N/A | 0.0001045 | 0.0001045 | 0.00031327 | 0.00031327 | 0.00030591 | 0.00030591 | 0.00021962 | 0.00021962 | N/A | N/A | 0.0026652 | 0.0026652 | 0.0046719 | 0.0046719 | 0.00037542 | 0.00037542 | 0.0021189 | 0.0021189 | 352 | 220 | 4 | 80 | NO
2013-06-24 | N/A | N/A | 0.00090222 | 0.00090222 | 0.021807 | 0.021807 | 0.023226 | 0.023226 | 0.013273 | 0.013273 | N/A | N/A | 1.045e-05 | 1.045e-05 | 0.00017404 | 0.00017404 | 0.00023234 | 0.00023234 | 0.00012571 | 0.00012571 | N/A | N/A | 3.6266e-07 | 3.6266e-07 | 0.00016424 | 0.00016424 | 1.9171e-05 | 1.9171e-05 | 3.6243e-05 | 3.6243e-05 | 645 | 373 | 15 | 101 | NO
2013-06-25 | N/A | N/A | 0.37339 | 0.37339 | 0.066239 | 0.066239 | 0.035974 | 0.035974 | 0.18795 | 0.18795 | N/A | N/A | 0.0031526 | 0.0031526 | 0.00073097 | 0.00073097 | 0.00037561 | 0.00037561 | 0.0016449 | 0.0016449 | N/A | N/A | 3.6266e-07 | 3.6266e-07 | 0.0047067 | 0.0047067 | 0.014436 | 0.014436 | 0.0064658 | 0.0064658 | 576 | 337 | 7 | 15 | NO
2013-06-26 | N/A | N/A | 0.056892 | 0.056892 | 0.030927 | 0.030927 | 0.057345 | 0.057345 | 0.05255 | 0.05255 | N/A | N/A | 0.00068973 | 0.00068973 | 0.00022625 | 0.00022625 | 0.00028268 | 0.00028268 | 0.00044984 | 0.00044984 | N/A | N/A | 0.017989 | 0.017989 | 0.047216 | 0.047216 | 0.0049486 | 0.0049486 | 0.017975 | 0.017975 | 566 | 382 | 3 | 40 | NO
2013-06-27 | N/A | N/A | 0.026509 | 0.026509 | 0.038637 | 0.038637 | 0.026994 | 0.026994 | 0.02881 | 0.02881 | N/A | N/A | 0.00023339 | 0.00023339 | 0.00020015 | 0.00020015 | 0.00047629 | 0.00047629 | 0.00032262 | 0.00032262 | N/A | N/A | 3.6266e-07 | 3.6266e-07 | 0.0070823 | 0.0070823 | 0.0067221 | 0.0067221 | 0.0038622 | 0.0038622 | 557 | 339 | 9 | 42 | NO
2013-06-28 | N/A | N/A | 0.079086 | 0.079086 | 0.1991 | 0.1991 | 0.0011501 | 0.0011501 | 0.069491 | 0.069491 | N/A | N/A | 0.00087435 | 0.00087435 | 0.0034199 | 0.0034199 | 1.9362e-05 | 1.9362e-05 | 0.00098299 | 0.00098299 | N/A | N/A | 8.745e-05 | 8.745e-05 | 0.0004427 | 0.0004427 | 0.0019902 | 0.0019902 | 0.00089352 | 0.00089352 | 443 | 316 | 4 | 45 | NO
2013-06-29 | N/A | N/A | 0.0027694 | 0.0027694 | 0.58851 | 0.58851 | 0.030669 | 0.030669 | 0.11563 | 0.11563 | N/A | N/A | 1.7417e-05 | 1.7417e-05 | 0.0032023 | 0.0032023 | 0.00021685 | 0.00021685 | 0.00064977 | 0.00064977 | N/A | N/A | 0.01128 | 0.01128 | 0.0081352 | 0.0081352 | 0.0076167 | 0.0076167 | 0.0092997 | 0.0092997 | 191 | 127 | 3 | 5 | NO
2013-06-30 | N/A | N/A | 0.032184 | 0.032184 | 0.024017 | 0.024017 | 0.092955 | 0.092955 | 0.054533 | 0.054533 | N/A | N/A | 0.00045982 | 0.00045982 | 9.5722e-05 | 9.5722e-05 | 0.0005731 | 0.0005731 | 0.00044076 | 0.00044076 | N/A | N/A | 3.6266e-07 | 3.6266e-07 | 0.012591 | 0.012591 | 0.025511 | 0.025511 | 0.01217 | 0.01217 | 244 | 139 | 4 | 8 | NO
2013-07-01 | N/A | N/A | 0.0026474 | 0.0026474 | 0.073601 | 0.073601 | 0.017631 | 0.017631 | 0.020858 | 0.020858 | N/A | N/A | 5.5736e-05 | 5.5736e-05 | 0.0018883 | 0.0018883 | 0.00018974 | 0.00018974 | 0.00042712 | 0.00042712 | N/A | N/A | 3.6266e-07 | 3.6266e-07 | 0.007587 | 0.007587 | 0.0013977 | 0.0013977 | 0.0018674 | 0.0018674 | 564 | 318 | 1 | 19 | NO
2013-07-02 | N/A | N/A | 0.034671 | 0.034671 | 0.14734 | 0.14734 | 0.0052392 | 0.0052392 | 0.04277 | 0.04277 | N/A | N/A | 0.00024733 | 0.00024733 | 0.00061784 | 0.00061784 | 6.5829e-05 | 6.5829e-05 | 0.00024083 | 0.00024083 | N/A | N/A | 3.6266e-07 | 3.6266e-07 | 0.0055856 | 0.0055856 | 1.9171e-05 | 1.9171e-05 | 0.00097986 | 0.00097986 | 618 | 377 | 13 | 59 | NO
2013-07-03 | N/A | N/A | 0.00051207 | 0.00051207 | 0.23151 | 0.23151 | 0.053287 | 0.053287 | 0.061361 | 0.061361 | N/A | N/A | 6.967e-06 | 6.967e-06 | 0.0028629 | 0.0028629 | 0.0009797 | 0.0009797 | 0.00088454 | 0.00088454 | N/A | N/A | 3.6266e-07 | 3.6266e-07 | 0.00016424 | 0.00016424 | 0.0114 | 0.0114 | 0.0044877 | 0.0044877 | 545 | 352 | 4 | 20 | NO
2013-07-04 | N/A | N/A | 0.13068 | 0.13068 | 0.92585 | 0.92585 | 0.59835 | 0.59835 | 0.45201 | 0.45201 | N/A | N/A | 0.0010032 | 0.0010032 | 0.0097723 | 0.0097723 | 0.0026564 | 0.0026564 | 0.0031762 | 0.0031762 | N/A | N/A | 0.0086499 | 0.0086499 | 0.18809 | 0.18809 | 0.051393 | 0.051393 | 0.056601 | 0.056601 | 1089 | 495 | 10 | 42 | NO
2013-07-05 | N/A | N/A | 0.19627 | 0.19627 | 2.6901 | 2.6901 | 1.1708 | 1.1708 | 1.0115 | 1.0115 | N/A | N/A | 0.00060264 | 0.00060264 | 0.010938 | 0.010938 | 0.010258 | 0.010258 | 0.0061782 | 0.0061782 | N/A | N/A | 0.011572 | 0.011572 | 0.065934 | 0.065934 | 0.020298 | 0.020298 | 0.024447 | 0.024447 | 1120 | 543 | 17 | 79 | NO
2013-07-06 | N/A | N/A | 0.77043 | 0.77043 | 0.032223 | 0.032223 | 0.19769 | 0.19769 | 0.41792 | 0.41792 | N/A | N/A | 0.0066987 | 0.0066987 | 0.00023495 | 0.00023495 | 0.00081319 | 0.00081319 | 0.0032716 | 0.0032716 | N/A | N/A | 0.0044662 | 0.0044662 | 0.00016424 | 0.00016424 | 0.022521 | 0.022521 | 0.010779 | 0.010779 | 1049 | 453 | 11 | 94 | NO
2013-07-07 | N/A | N/A | 0.043526 | 0.043526 | 0.69457 | 0.69457 | 0.043231 | 0.043231 | 0.15673 | 0.15673 | N/A | N/A | 0.00050859 | 0.00050859 | 0.0036287 | 0.0036287 | 0.0016264 | 0.0016264 | 0.0014889 | 0.0014889 | N/A | N/A | 0.0082458 | 0.0082458 | 0.03572 | 0.03572 | 1.9171e-05 | 1.9171e-05 | 0.0098101 | 0.0098101 | 277 | 153 | 5 | 13 | NO
2013-07-08 | N/A | N/A | 0.027666 | 0.027666 | 0.011817 | 0.011817 | 0.087259 | 0.087259 | 0.048217 | 0.048217 | N/A | N/A | 9.7538e-05 | 9.7538e-05 | 9.5722e-05 | 9.5722e-05 | 0.0076943 | 0.0076943 | 0.0030686 | 0.0030686 | N/A | N/A | 0.0033793 | 0.0033793 | 0.00046881 | 0.00046881 | 0.011683 | 0.011683 | 0.0061205 | 0.0061205 | 622 | 386 | 13 | 31 | NO
2013-07-09 | N/A | N/A | 0.18181 | 0.18181 | 0.038698 | 0.038698 | 0.20078 | 0.20078 | 0.16432 | 0.16432 | N/A | N/A | 0.011245 | 0.011245 | 0.00048731 | 0.00048731 | 0.0010455 | 0.0010455 | 0.005383 | 0.005383 | N/A | N/A | 3.6266e-07 | 3.6266e-07 | 0.0053245 | 0.0053245 | 0.017723 | 0.017723 | 0.0078593 | 0.0078593 | 890 | 501 | 11 | 109 | NO
2013-07-10 | N/A | N/A | 0.0029261 | 0.0029261 | 0.082651 | 0.082651 | 0.0021879 | 0.0021879 | 0.016514 | 0.016514 | N/A | N/A | 5.2252e-05 | 5.2252e-05 | 0.0075881 | 0.0075881 | 1.9362e-05 | 1.9362e-05 | 0.001351 | 0.001351 | N/A | N/A | 3.6266e-07 | 3.6266e-07 | 0.016741 | 0.016741 | 0.015803 | 0.015803 | 0.0090952 | 0.0090952 | 405 | 271 | 6 | 29 | NO
2013-07-11 | N/A | N/A | 0.016536 | 0.016536 | 0.030004 | 0.030004 | 0.042115 | 0.042115 | 0.028885 | 0.028885 | N/A | N/A | 0.00035183 | 0.00035183 | 0.00038289 | 0.00038289 | 0.001758 | 0.001758 | 0.00090726 | 0.00090726 | N/A | N/A | 3.6266e-07 | 3.6266e-07 | 0.0078655 | 0.0078655 | 1.9171e-05 | 1.9171e-05 | 0.0013767 | 0.0013767 | 447 | 289 | 7 | 38 | NO
2013-07-12 | N/A | N/A | 0.041945 | 0.041945 | 0.10046 | 0.10046 | 0.030142 | 0.030142 | 0.047512 | 0.047512 | N/A | N/A | 0.00030306 | 0.00030306 | 0.00073097 | 0.00073097 | 0.00031366 | 0.00031366 | 0.00038169 | 0.00038169 | N/A | N/A | 3.6266e-07 | 3.6266e-07 | 0.012878 | 0.012878 | 1.9171e-05 | 1.9171e-05 | 0.0022491 | 0.0022491 | 569 | 338 | 10 | 62 | NO
2013-07-13 | N/A | N/A | 0.44032 | 0.44032 | 0.15191 | 0.15191 | 0.0014831 | 0.0014831 | 0.21847 | 0.21847 | N/A | N/A | 0.017034 | 0.017034 | 0.0071791 | 0.0071791 | 4.2595e-05 | 4.2595e-05 | 0.0086727 | 0.0086727 | N/A | N/A | 0.010883 | 0.010883 | 0.00016424 | 0.00016424 | 0.0053088 | 0.0053088 | 0.0068369 | 0.0068369 | 302 | 171 | 3 | 16 | NO
2013-07-14 | N/A | N/A | 0.11075 | 0.11075 | 0.42057 | 0.42057 | 0.0381 | 0.0381 | 0.13626 | 0.13626 | N/A | N/A | 0.00050511 | 0.00050511 | 0.026793 | 0.026793 | 0.00028655 | 0.00028655 | 0.0049952 | 0.0049952 | N/A | N/A | 0.0047727 | 0.0047727 | 0.036234 | 0.036234 | 0.012298 | 0.012298 | 0.013192 | 0.013192 | 395 | 199 | 8 | 22 | NO
2013-07-15 | N/A | N/A | 0.058108 | 0.058108 | 0.3353 | 0.3353 | 0.64795 | 0.64795 | 0.33706 | 0.33706 | N/A | N/A | 0.00024384 | 0.00024384 | 0.0026889 | 0.0026889 | 0.0055916 | 0.0055916 | 0.0027612 | 0.0027612 | N/A | N/A | 3.6266e-07 | 3.6266e-07 | 0.0086313 | 0.0086313 | 1.9171e-05 | 1.9171e-05 | 0.00151 | 0.00151 | 1215 | 431 | 22 | 60 | NO
2013-07-16 | N/A | N/A | 0.020556 | 0.020556 | 0.20384 | 0.20384 | 0.094562 | 0.094562 | 0.081405 | 0.081405 | N/A | N/A | 0.00017766 | 0.00017766 | 0.00036548 | 0.00036548 | 0.0017425 | 0.0017425 | 0.00082244 | 0.00082244 | N/A | N/A | 3.6266e-07 | 3.6266e-07 | 0.0013216 | 0.0013216 | 0.033406 | 0.033406 | 0.013297 | 0.013297 | 412 | 318 | 6 | 22 | NO
2013-07-17 | N/A | N/A | 0.14489 | 0.14489 | 0.08742 | 0.08742 | 0.50969 | 0.50969 | 0.27758 | 0.27758 | N/A | N/A | 0.0012262 | 0.0012262 | 0.0015054 | 0.0015054 | 0.0018084 | 0.0018084 | 0.0015025 | 0.0015025 | N/A | N/A | 3.6266e-07 | 3.6266e-07 | 0.014888 | 0.014888 | 0.005452 | 0.005452 | 0.004724 | 0.004724 | 513 | 328 | 14 | 73 | NO
2013-07-18 | N/A | N/A | 0.3294 | 0.3294 | 0.089395 | 0.089395 | 0.84967 | 0.84967 | 0.49113 | 0.49113 | N/A | N/A | 0.012401 | 0.012401 | 0.0054909 | 0.0054909 | 0.017875 | 0.017875 | 0.013339 | 0.013339 | N/A | N/A | 0.022803 | 0.022803 | 0.099332 | 0.099332 | 0.1034 | 0.1034 | 0.067648 | 0.067648 | 983 | 640 | 18 | 60 | NO
2013-07-19 | N/A | N/A | 0.040994 | 0.040994 | 1.9045 | 1.9045 | 0.34941 | 0.34941 | 0.48598 | 0.48598 | N/A | N/A | 0.0034905 | 0.0034905 | 0.011217 | 0.011217 | 0.0073884 | 0.0073884 | 0.0063599 | 0.0063599 | N/A | N/A | 0.0076292 | 0.0076292 | 0.0027139 | 0.0027139 | 0.024372 | 0.024372 | 0.013323 | 0.013323 | 603 | 415 | 6 | 34 | NO
2013-07-20 | N/A | N/A | 0.00046679 | 0.00046679 | 0.0094416 | 0.0094416 | 0.040392 | 0.040392 | 0.017645 | 0.017645 | N/A | N/A | 3.4835e-06 | 3.4835e-06 | 0.00010442 | 0.00010442 | 0.00028655 | 0.00028655 | 0.00013177 | 0.00013177 | N/A | N/A | 3.6266e-07 | 3.6266e-07 | 0.016071 | 0.016071 | 0.0077561 | 0.0077561 | 0.0058312 | 0.0058312 | 165 | 170 | 2 | 18 | NO
2013-07-21 | N/A | N/A | 0.018316 | 0.018316 | 0.1568 | 0.1568 | 0.021019 | 0.021019 | 0.043477 | 0.043477 | N/A | N/A | 0.00010799 | 0.00010799 | 0.0016621 | 0.0016621 | 0.00037561 | 0.00037561 | 0.00048317 | 0.00048317 | N/A | N/A | 3.6266e-07 | 3.6266e-07 | 0.012025 | 0.012025 | 0.001754 | 0.001754 | 0.0027792 | 0.0027792 | 185 | 187 | 6 | 57 | NO
2013-07-22 | N/A | N/A | 0.016299 | 0.016299 | 0.059783 | 0.059783 | 0.11583 | 0.11583 | 0.062799 | 0.062799 | N/A | N/A | 8.3604e-05 | 8.3604e-05 | 0.0013314 | 0.0013314 | 0.00028268 | 0.00028268 | 0.00037866 | 0.00037866 | N/A | N/A | 0.0099422 | 0.0099422 | 0.021919 | 0.021919 | 1.9171e-05 | 1.9171e-05 | 0.0081456 | 0.0081456 | 310 | 244 | 5 | 31 | NO
2013-07-23 | N/A | N/A | 0.23851 | 0.23851 | 0.071495 | 0.071495 | 0.036632 | 0.036632 | 0.13048 | 0.13048 | N/A | N/A | 0.0030759 | 0.0030759 | 0.0031414 | 0.0031414 | 0.00020136 | 0.00020136 | 0.001963 | 0.001963 | N/A | N/A | 0.0065389 | 0.0065389 | 0.00016424 | 0.00016424 | 0.0059361 | 0.0059361 | 0.0051935 | 0.0051935 | 481 | 383 | 11 | 70 | NO
2013-07-24 | N/A | N/A | 0.010029 | 0.010029 | 1.7692 | 1.7692 | 0.18759 | 0.18759 | 0.38567 | 0.38567 | N/A | N/A | 0.0082524 | 0.0082524 | 0.0064482 | 0.0064482 | 0.0030707 | 0.0030707 | 0.0059116 | 0.0059116 | N/A | N/A | 3.6266e-07 | 3.6266e-07 | 0.016211 | 0.016211 | 0.0050454 | 0.0050454 | 0.0047952 | 0.0047952 | 447 | 297 | 9 | 49 | NO
2013-07-25 | N/A | N/A | 0.39953 | 0.38219 | 0.40552 | 0.14877 | 0.083019 | 0.054836 | 0.27677 | 0.21352 | N/A | N/A | 0.01925 | 0.0019055 | 0.25815 | 0.001636 | 0.028814 | 0.00063119 | 0.064573 | 0.0013601 | N/A | N/A | 0.011628 | 0.011628 | 0.00016424 | 0.00016424 | 1.9171e-05 | 1.9171e-05 | 0.0050921 | 0.0050921 | 543 | 413 | 16 | 47 | NO | Transmission
2013-07-26 | N/A | N/A | 0.014756 | 0.014756 | 0.3031 | 0.3031 | 0.06569 | 0.06569 | 0.084866 | 0.084866 | N/A | N/A | 3.8318e-05 | 3.8318e-05 | 0.0020798 | 0.0020798 | 0.00063893 | 0.00063893 | 0.00062857 | 0.00062857 | N/A | N/A | 0.020825 | 0.020825 | 0.012504 | 0.012504 | 0.029948 | 0.029948 | 0.022945 | 0.022945 | 314 | 241 | 4 | 9 | NO
2013-07-27 | N/A | N/A | 0.0010416 | 0.0010416 | 0.054213 | 0.054213 | 0.022676 | 0.022676 | 0.018759 | 0.018759 | N/A | N/A | 1.045e-05 | 1.045e-05 | 0.00049601 | 0.00049601 | 0.0001394 | 0.0001394 | 0.0001454 | 0.0001454 | N/A | N/A | 3.6266e-07 | 3.6266e-07 | 0.00016424 | 0.00016424 | 0.0070435 | 0.0070435 | 0.0027838 | 0.0027838 | 129 | 129 | 0 | 9 | NO
2013-07-28 | N/A | N/A | 0.10655 | 0.10655 | 0.077569 | 0.077569 | 0.27213 | 0.27213 | 0.16627 | 0.16627 | N/A | N/A | 0.00067928 | 0.00067928 | 0.0018448 | 0.0018448 | 0.0038336 | 0.0038336 | 0.0021159 | 0.0021159 | N/A | N/A | 0.0033724 | 0.0033724 | 0.024277 | 0.024277 | 0.0010144 | 0.0010144 | 0.0060887 | 0.0060887 | 159 | 139 | 0 | 9 | NO
2013-07-29 | N/A | N/A | 0.042568 | 0.042568 | 0.05504 | 0.05504 | 0.038646 | 0.038646 | 0.043205 | 0.043205 | N/A | N/A | 0.0014456 | 0.0014456 | 0.0011922 | 0.0011922 | 0.00018587 | 0.00018587 | 0.00090878 | 0.00090878 | N/A | N/A | 0.0022298 | 0.0022298 | 0.0068387 | 0.0068387 | 0.016782 | 0.016782 | 0.0087241 | 0.0087241 | 488 | 370 | 6 | 44 | NO
2013-07-30 | N/A | N/A | 1.131 | 1.131 | 0.057424 | 0.057424 | 0 | 0 | 0.50175 | 0.50175 | N/A | N/A | 0.019563 | 0.019563 | 0.00020885 | 0.00020885 | 0 | 0 | 0.0085425 | 0.0085425 | N/A | N/A | 3.6266e-07 | 3.6266e-07 | 0.0023223 | 0.0023223 | 1.9171e-05 | 1.9171e-05 | 0.00041187 | 0.00041187 | 732 | 493 | 19 | 36 | NO
2013-07-31 | N/A | N/A | 0.030477 | 0.030477 | 0.049854 | 0.049854 | 0.1977 | 0.1977 | 0.099256 | 0.099256 | N/A | N/A | 0.00017417 | 0.00017417 | 0.00058303 | 0.00058303 | 0.00057697 | 0.00057697 | 0.00040289 | 0.00040289 | N/A | N/A | 0.01368 | 0.01368 | 0.028794 | 0.028794 | 0.0030434 | 0.0030434 | 0.01215 | 0.01215 | 455 | 280 | 6 | 15 | NO
2013-08-01 | N/A | N/A | 0.90555 | 0.90555 | 1.4766 | 1.4766 | 0.14634 | 0.14634 | 0.70799 | 0.70799 | N/A | N/A | 0.014509 | 0.014509 | 0.029769 | 0.029769 | 0.0049643 | 0.0049643 | 0.013432 | 0.013432 | N/A | N/A | 0.0089007 | 0.0089007 | 0.017821 | 0.017821 | 0.0025672 | 0.0025672 | 0.0079759 | 0.0079759 | 1196 | 706 | 37 | 98 | NO
2013-08-02 | N/A | N/A | 0.097781 | 0.097781 | 0.04411 | 0.04411 | 0.20571 | 0.20571 | 0.13065 | 0.13065 | N/A | N/A | 0.0037761 | 0.0037761 | 0.0004264 | 0.0004264 | 0.00096808 | 0.00096808 | 0.0020947 | 0.0020947 | N/A | N/A | 3.6266e-07 | 3.6266e-07 | 0.014801 | 0.014801 | 1.9171e-05 | 1.9171e-05 | 0.0025838 | 0.0025838 | 431 | 308 | 10 | 35 | NO
2013-08-03 | N/A | N/A | 0.2914 | 0.2914 | 0.10449 | 0.10449 | 0.3241 | 0.3241 | 0.27166 | 0.27166 | N/A | N/A | 0.022388 | 0.022388 | 0.0010964 | 0.0010964 | 0.0010881 | 0.0010881 | 0.010351 | 0.010351 | N/A | N/A | 3.6266e-07 | 3.6266e-07 | 0.029725 | 0.029725 | 0.0025207 | 0.0025207 | 0.0061599 | 0.0061599 | 276 | 262 | 13 | 28 | NO
2013-08-04 | N/A | N/A | 0.038548 | 0.038548 | 0.11743 | 0.11743 | 0.010165 | 0.010165 | 0.041177 | 0.041177 | N/A | N/A | 0.00043195 | 0.00043195 | 0.0011052 | 0.0011052 | 0.00011617 | 0.00011617 | 0.00042561 | 0.00042561 | N/A | N/A | 3.6266e-07 | 3.6266e-07 | 0.020544 | 0.020544 | 0.015896 | 0.015896 | 0.0097935 | 0.0097935 | 285 | 244 | 5 | 36 | NO
2013-08-05 | N/A | N/A | 0.080043 | 0.080043 | 0.028386 | 0.028386 | 0.028988 | 0.028988 | 0.051082 | 0.051082 | N/A | N/A | 0.00059916 | 0.00059916 | 0.00022625 | 0.00022625 | 8.9063e-05 | 8.9063e-05 | 0.00033473 | 0.00033473 | N/A | N/A | 3.6266e-07 | 3.6266e-07 | 0.020414 | 0.020414 | 0.0020831 | 0.0020831 | 0.0043681 | 0.0043681 | 342 | 311 | 5 | 11 | NO
2013-08-06 | N/A | N/A | 0.018863 | 0.018863 | 0.4734 | 0.4734 | 1.3748 | 1.3748 | 0.62833 | 0.62833 | N/A | N/A | 0.0004424 | 0.0004424 | 0.0099115 | 0.0099115 | 0.015846 | 0.015846 | 0.0081154 | 0.0081154 | N/A | N/A | 0.007354 | 0.007354 | 0.0736 | 0.0736 | 0.035734 | 0.035734 | 0.029985 | 0.029985 | 972 | 619 | 26 | 182 | NO
2013-08-07 | N/A | N/A | 0.016763 | 0.016763 | 0.38223 | 0.38223 | 0.19379 | 0.19379 | 0.14962 | 0.14962 | N/A | N/A | 5.9219e-05 | 5.9219e-05 | 0.010033 | 0.010033 | 0.0049837 | 0.0049837 | 0.0037214 | 0.0037214 | N/A | N/A | 0.00019195 | 0.00019195 | 0.060408 | 0.060408 | 0.0091075 | 0.0091075 | 0.01416 | 0.01416 | 596 | 386 | 17 | 93 | NO
2013-08-08 | N/A | N/A | 0.0012715 | 0.0012715 | 5.9086 | 5.9086 | 1.011 | 1.011 | 1.4244 | 1.4244 | N/A | N/A | 6.967e-06 | 6.967e-06 | 0.18539 | 0.18539 | 0.12053 | 0.12053 | 0.079416 | 0.079416 | N/A | N/A | 0.0069186 | 0.0069186 | 0.0064906 | 0.0064906 | 0.0058044 | 0.0058044 | 0.0064083 | 0.0064083 | 1498 | 659 | 38 | 284 | NO
2013-08-09 | N/A | N/A | 0.44932 | 0.44932 | 0.079701 | 0.079701 | 0.90929 | 0.90929 | 0.5649 | 0.5649 | N/A | N/A | 0.0068485 | 0.0068485 | 0.00095722 | 0.00095722 | 0.003489 | 0.003489 | 0.004509 | 0.004509 | N/A | N/A | 0.011339 | 0.011339 | 0.0079438 | 0.0079438 | 0.013456 | 0.013456 | 0.011576 | 0.011576 | 1000 | 591 | 16 | 170 | NO
2013-08-10 | N/A | N/A | 0.00099279 | 0.00099279 | 0.14625 | 0.14625 | 0.047742 | 0.047742 | 0.04456 | 0.04456 | N/A | N/A | 6.967e-06 | 6.967e-06 | 0.00059173 | 0.00059173 | 0.00052276 | 0.00052276 | 0.0003105 | 0.0003105 | N/A | N/A | 3.6266e-07 | 3.6266e-07 | 0.023224 | 0.023224 | 0.0019515 | 0.0019515 | 0.0048058 | 0.0048058 | 204 | 159 | 2 | 13 | NO
2013-08-11 | N/A | N/A | 0.2558 | 0.2558 | 0.002715 | 0.002715 | 0.036969 | 0.036969 | 0.12615 | 0.12615 | N/A | N/A | 0.0047724 | 0.0047724 | 3.4808e-05 | 3.4808e-05 | 0.00021298 | 0.00021298 | 0.0021644 | 0.0021644 | N/A | N/A | 0.0040238 | 0.0040238 | 0.026836 | 0.026836 | 0.014289 | 0.014289 | 0.012009 | 0.012009 | 179 | 147 | 1 | 7 | NO
2013-08-12 | N/A | N/A | 6.5405 | 6.5405 | 9.8994 | 9.8994 | 11.9222 | 11.9222 | 9.2302 | 9.2302 | N/A | N/A | 0.082026 | 0.082026 | 0.083983 | 0.083983 | 0.062491 | 0.062491 | 0.074726 | 0.074726 | N/A | N/A | 0.038953 | 0.038953 | 0.11534 | 0.11534 | 0.016422 | 0.016422 | 0.043436 | 0.043436 | 9716 | 3807 | 490 | 2553 | Yes
2013-08-13 | N/A | N/A | 0.23161 | 0.23161 | 0.028351 | 0.028351 | 0.37005 | 0.37005 | 0.25038 | 0.25038 | N/A | N/A | 0.0035044 | 0.0035044 | 0.00018274 | 0.00018274 | 0.0018548 | 0.0018548 | 0.002281 | 0.002281 | N/A | N/A | 0.015429 | 0.015429 | 0.0077785 | 0.0077785 | 0.0033649 | 0.0033649 | 0.0093785 | 0.0093785 | 1048 | 617 | 28 | 118 | NO
2013-08-14 | N/A | N/A | 1.1452 | 1.1452 | 0.81187 | 0.81187 | 0.80408 | 0.80408 | 0.95378 | 0.95378 | N/A | N/A | 0.012129 | 0.012129 | 0.01502 | 0.01502 | 0.016093 | 0.016093 | 0.014183 | 0.014183 | N/A | N/A | 3.6266e-07 | 3.6266e-07 | 0.036025 | 0.036025 | 0.0021257 | 0.0021257 | 0.007102 | 0.007102 | 1306 | 717 | 36 | 178 | NO
2013-08-15 | N/A | N/A | 0.045216 | 0.045216 | 0.19189 | 0.19189 | 0.23647 | 0.23647 | 0.14555 | 0.14555 | N/A | N/A | 0.00026823 | 0.00026823 | 0.016542 | 0.016542 | 0.0024008 | 0.0024008 | 0.003935 | 0.003935 | N/A | N/A | 0.010688 | 0.010688 | 0.00032958 | 0.00032958 | 0.0097193 | 0.0097193 | 0.008506 | 0.008506 | 594 | 430 | 15 | 54 | NO
2013-08-16 | N/A | N/A | 4.3447 | 4.3447 | 20.2878 | 20.2878 | 16.9917 | 16.9917 | 12.0665 | 12.0665 | N/A | N/A | 0.040105 | 0.040105 | 0.037445 | 0.037445 | 0.059699 | 0.059699 | 0.047306 | 0.047306 | N/A | N/A | 0.012955 | 0.012955 | 0.050914 | 0.050914 | 0.07501 | 0.07501 | 0.043835 | 0.043835 | 2370 | 1076 | 66 | 291 | Yes
2013-08-17 | N/A | N/A | 0.67959 | 0.67959 | 2.2617 | 2.2617 | 9.2547 | 9.2547 | 4.309 | 4.309 | N/A | N/A | 0.0019717 | 0.0019717 | 0.005021 | 0.005021 | 0.02366 | 0.02366 | 0.010986 | 0.010986 | N/A | N/A | 0.0079706 | 0.0079706 | 0.013939 | 0.013939 | 0.026076 | 0.026076 | 0.016091 | 0.016091 | 7401 | 2591 | 276 | 1410 | NO
2013-08-18 | N/A | N/A | 0.068029 | 0.068029 | 0.6725 | 0.6725 | 1.2361 | 1.2361 | 0.63013 | 0.63013 | N/A | N/A | 0.00066883 | 0.00066883 | 0.0034025 | 0.0034025 | 0.0081473 | 0.0081473 | 0.0040698 | 0.0040698 | N/A | N/A | 0.033003 | 0.033003 | 0.030987 | 0.030987 | 0.031338 | 0.031338 | 0.032001 | 0.032001 | 1449 | 862 | 29 | 147 | NO
2013-08-19 | N/A | N/A | 0.01616 | 0.01616 | 0.54466 | 0.54466 | 1.1016 | 1.1016 | 0.53272 | 0.53272 | N/A | N/A | 0.00024036 | 0.00024036 | 0.0043162 | 0.0043162 | 0.012937 | 0.012937 | 0.0059161 | 0.0059161 | N/A | N/A | 3.6266e-07 | 3.6266e-07 | 0.010241 | 0.010241 | 0.00010823 | 0.00010823 | 0.001825 | 0.001825 | 1026 | 520 | 19 | 69 | NO
2013-08-20 | N/A | N/A | 0.31065 | 0.31065 | 0.36091 | 0.36091 | 0.051118 | 0.051118 | 0.21788 | 0.21788 | N/A | N/A | 0.00094751 | 0.00094751 | 0.0024191 | 0.0024191 | 0.00065442 | 0.00065442 | 0.001089 | 0.001089 | N/A | N/A | 0.0053475 | 0.0053475 | 0.044797 | 0.044797 | 0.0077561 | 0.0077561 | 0.013156 | 0.013156 | 652 | 460 | 25 | 86 | NO
2013-08-21 | N/A | N/A | 0.00058523 | 0.00058523 | 0.0095809 | 0.0095809 | 0.036938 | 0.036938 | 0.01637 | 0.01637 | N/A | N/A | 1.045e-05 | 1.045e-05 | 0.00011313 | 0.00011313 | 0.0006157 | 0.0006157 | 0.00026506 | 0.00026506 | N/A | N/A | 3.6266e-07 | 3.6266e-07 | 0.013339 | 0.013339 | 0.0076592 | 0.0076592 | 0.0053177 | 0.0053177 | 339 | 277 | 9 | 21 | NO
2013-08-22 | N/A | N/A | 0.1055 | 0.1055 | 0.00083539 | 0.00083539 | 0.56726 | 0.56726 | 0.2679 | 0.2679 | N/A | N/A | 8.7087e-05 | 8.7087e-05 | 3.4808e-05 | 3.4808e-05 | 0.0013863 | 0.0013863 | 0.00058616 | 0.00058616 | N/A | N/A | 3.6266e-07 | 3.6266e-07 | 0.00016424 | 0.00016424 | 0.017034 | 0.017034 | 0.0066915 | 0.0066915 | 619 | 313 | 5 | 27 | NO
2013-08-23 | N/A | N/A | 0.0095482 | 0.0095482 | 0.21415 | 0.21415 | 0.73241 | 0.73241 | 0.3279 | 0.3279 | N/A | N/A | 0.00011844 | 0.00011844 | 0.0027411 | 0.0027411 | 0.0072761 | 0.0072761 | 0.0033746 | 0.0033746 | N/A | N/A | 0.027408 | 0.027408 | 0.074653 | 0.074653 | 0.013654 | 0.013654 | 0.030252 | 0.030252 | 988 | 371 | 26 | 24 | NO
2013-08-24 | N/A | N/A | 0.035646 | 0.035646 | 0.004264 | 0.004264 | 0.12747 | 0.12747 | 0.066101 | 0.066101 | N/A | N/A | 0.00039015 | 0.00039015 | 3.4808e-05 | 3.4808e-05 | 0.012484 | 0.012484 | 0.0050589 | 0.0050589 | N/A | N/A | 3.6266e-07 | 3.6266e-07 | 0.0070562 | 0.0070562 | 0.013371 | 0.013371 | 0.0064583 | 0.0064583 | 426 | 200 | 12 | 25 | NO
2013-08-25 | N/A | N/A | 0.036918 | 0.036918 | 0.15443 | 0.15443 | 0.014936 | 0.014936 | 0.048774 | 0.048774 | N/A | N/A | 0.00022991 | 0.00022991 | 0.0020885 | 0.0020885 | 0.00063506 | 0.00063506 | 0.00071187 | 0.00071187 | N/A | N/A | 3.6266e-07 | 3.6266e-07 | 0.012921 | 0.012921 | 0.00032121 | 0.00032121 | 0.0023748 | 0.0023748 | 240 | 141 | 4 | 6 | NO
2013-08-26 | N/A | N/A | 1.3481 | 1.3481 | 0.34962 | 0.34962 | 0.0569 | 0.0569 | 0.66926 | 0.66926 | N/A | N/A | 0.02397 | 0.02397 | 0.013244 | 0.013244 | 0.00034851 | 0.00034851 | 0.012864 | 0.012864 | N/A | N/A | 3.6266e-07 | 3.6266e-07 | 0.015158 | 0.015158 | 1.9171e-05 | 1.9171e-05 | 0.0026459 | 0.0026459 | 1494 | 469 | 27 | 159 | NO
2013-08-27 | N/A | N/A | 0.02057 | 0.02057 | 0.4982 | 0.4982 | 0.017902 | 0.017902 | 0.10266 | 0.10266 | N/A | N/A | 9.0571e-05 | 9.0571e-05 | 0.0018361 | 0.0018361 | 0.00012004 | 0.00012004 | 0.00040592 | 0.00040592 | N/A | N/A | 0.011085 | 0.011085 | 0.015993 | 0.015993 | 0.024109 | 0.024109 | 0.017033 | 0.017033 | 614 | 326 | 19 | 59 | NO
2013-08-28 | N/A | N/A | 0.0066012 | 0.0066012 | 0.026167 | 0.026167 | 0.50206 | 0.50206 | 0.2038 | 0.2038 | N/A | N/A | 6.2703e-05 | 6.2703e-05 | 0.00028717 | 0.00028717 | 0.0082287 | 0.0082287 | 0.0032958 | 0.0032958 | N/A | N/A | 0.0024736 | 0.0024736 | 0.045371 | 0.045371 | 0.012112 | 0.012112 | 0.01371 | 0.01371 | 653 | 333 | 11 | 47 | NO
2013-08-29 | N/A | N/A | 0.022043 | 0.022043 | 0.02078 | 0.02078 | 0.32364 | 0.32364 | 0.13979 | 0.13979 | N/A | N/A | 0.0022782 | 0.0022782 | 0.00033938 | 0.00033938 | 0.0046545 | 0.0046545 | 0.0028702 | 0.0028702 | N/A | N/A | 0.007239 | 0.007239 | 0.01561 | 0.01561 | 0.0021838 | 0.0021838 | 0.0067188 | 0.0067188 | 414 | 297 | 4 | 22 | NO
2013-08-30 | N/A | N/A | 0.016271 | 0.016271 | 0.65082 | 0.65082 | 0.87737 | 0.87737 | 0.46353 | 0.46353 | N/A | N/A | 0.00012889 | 0.00012889 | 0.014367 | 0.014367 | 0.016868 | 0.016868 | 0.0091544 | 0.0091544 | N/A | N/A | 3.6266e-07 | 3.6266e-07 | 0.028889 | 0.028889 | 1.9171e-05 | 1.9171e-05 | 0.005036 | 0.005036 | 623 | 307 | 13 | 24 | NO
2013-08-31 | N/A | N/A | 0.037757 | 0.037757 | 0.090579 | 0.090579 | 0.48904 | 0.48904 | 0.22347 | 0.22347 | N/A | N/A | 0.00039015 | 0.00039015 | 0.00074837 | 0.00074837 | 0.006064 | 0.006064 | 0.0026718 | 0.0026718 | N/A | N/A | 3.6266e-07 | 3.6266e-07 | 0.0034623 | 0.0034623 | 0.005696 | 0.005696 | 0.0028307 | 0.0028307 | 442 | 168 | 3 | 16 | NO
2013-09-01 | N/A | N/A | 0.01059 | 0.01059 | 0.0008615 | 0.0008615 | 0.10515 | 0.10515 | 0.045884 | 0.045884 | N/A | N/A | 0.00013237 | 0.00013237 | 8.702e-06 | 8.702e-06 | 0.00046855 | 0.00046855 | 0.00024234 | 0.00024234 | N/A | N/A | 3.6266e-07 | 3.6266e-07 | 0.018743 | 0.018743 | 0.020275 | 0.020275 | 0.011193 | 0.011193 | 149 | 74 | 2 | 2 | NO
2013-09-02 | N/A | N/A | 0.020375 | 0.020375 | 0.1132 | 0.1132 | 0.015346 | 0.015346 | 0.034565 | 0.034565 | N/A | N/A | 8.3604e-05 | 8.3604e-05 | 0.00082669 | 0.00082669 | 8.9063e-05 | 8.9063e-05 | 0.00021508 | 0.00021508 | N/A | N/A | 3.6266e-07 | 3.6266e-07 | 0.001017 | 0.001017 | 0.0059554 | 0.0059554 | 0.0025066 | 0.0025066 | 369 | 217 | 7 | 22 | NO
2013-09-03 | N/A | N/A | 0.018713 | 0.018713 | 0.014741 | 0.014741 | 0.14583 | 0.14583 | 0.067743 | 0.067743 | N/A | N/A | 0.00013934 | 0.00013934 | 8.702e-05 | 8.702e-05 | 0.0037639 | 0.0037639 | 0.0015479 | 0.0015479 | N/A | N/A | 3.6266e-07 | 3.6266e-07 | 0.0042194 | 0.0042194 | 0.00086721 | 0.00086721 | 0.0010738 | 0.0010738 | 506 | 289 | 9 | 29 | NO
2013-09-04 | N/A | N/A | 0.0084997 | 0.0084997 | 0.63618 | 0.63618 | 0.035099 | 0.035099 | 0.12816 | 0.12816 | N/A | N/A | 0.00011495 | 0.00011495 | 0.0022103 | 0.0022103 | 0.0006428 | 0.0006428 | 0.00068613 | 0.00068613 | N/A | N/A | 3.6266e-07 | 3.6266e-07 | 0.005603 | 0.005603 | 0.0039844 | 0.0039844 | 0.0025339 | 0.0025339 | 374 | 224 | 4 | 19 | NO
2013-09-05 | N/A | N/A | 1.7705 | 1.7705 | 0.16685 | 0.16685 | 0.0050766 | 0.0050766 | 0.80083 | 0.80083 | N/A | N/A | 0.02205 | 0.02205 | 0.0052386 | 0.0052386 | 3.8723e-05 | 3.8723e-05 | 0.010515 | 0.010515 | N/A | N/A | 3.6266e-07 | 3.6266e-07 | 0.025948 | 0.025948 | 0.0060135 | 0.0060135 | 0.0068687 | 0.0068687 | 1352 | 422 | 24 | 27 | NO
2013-09-06 | N/A | N/A | 0.046731 | 0.046731 | 0.0047774 | 0.0047774 | 0.024969 | 0.024969 | 0.030917 | 0.030917 | N/A | N/A | 0.00056084 | 0.00056084 | 4.351e-05 | 4.351e-05 | 0.00025557 | 0.00025557 | 0.00035139 | 0.00035139 | N/A | N/A | 3.6266e-07 | 3.6266e-07 | 0.0052549 | 0.0052549 | 0.0090107 | 0.0090107 | 0.0044393 | 0.0044393 | 436 | 305 | 6 | 54 | NO
2013-09-07 | N/A | N/A | 0.016209 | 0.016209 | 0.044728 | 0.044728 | 0.00060408 | 0.00060408 | 0.015069 | 0.015069 | N/A | N/A | 0.00056781 | 0.00056781 | 0.00053082 | 0.00053082 | 3.4851e-05 | 3.4851e-05 | 0.00035291 | 0.00035291 | N/A | N/A | 3.6266e-07 | 3.6266e-07 | 0.0022614 | 0.0022614 | 0.0063465 | 0.0063465 | 0.0028762 | 0.0028762 | 242 | 161 | 1 | 35 | NO
2013-09-08 | N/A | N/A | 0.054802 | 0.054802 | 0.010199 | 0.010199 | 1.2861 | 1.2861 | 0.52866 | 0.52866 | N/A | N/A | 0.00042498 | 0.00042498 | 0.00011313 | 0.00011313 | 0.014556 | 0.014556 | 0.005898 | 0.005898 | N/A | N/A | 3.6266e-07 | 3.6266e-07 | 0.00016424 | 0.00016424 | 0.029228 | 0.029228 | 0.011461 | 0.011461 | 859 | 238 | 15 | 63 | NO
2013-09-09 | N/A | N/A | 0.41032 | 0.41032 | 0.071469 | 0.071469 | 0.14519 | 0.14519 | 0.24764 | 0.24764 | N/A | N/A | 0.0070854 | 0.0070854 | 0.0016186 | 0.0016186 | 0.00077834 | 0.00077834 | 0.0036669 | 0.0036669 | N/A | N/A | 0.011416 | 0.011416 | 0.019735 | 0.019735 | 0.008031 | 0.008031 | 0.01154 | 0.01154 | 1104 | 525 | 29 | 185 | NO
2013-09-10 | N/A | N/A | 0.0023897 | 0.0023897 | 0.0020363 | 0.0020363 | 1.5661 | 1.5661 | 0.61397 | 0.61397 | N/A | N/A | 1.7417e-05 | 1.7417e-05 | 1.7404e-05 | 1.7404e-05 | 0.0047475 | 0.0047475 | 0.0018675 | 0.0018675 | N/A | N/A | 3.6266e-07 | 3.6266e-07 | 0.019665 | 0.019665 | 0.017313 | 0.017313 | 0.010195 | 0.010195 | 468 | 244 | 15 | 20 | NO
2013-09-11 | N/A | N/A | 0.0078344 | 0.0078344 | 1.4432 | 1.4432 | 0.066294 | 0.066294 | 0.28053 | 0.28053 | N/A | N/A | 0.00015327 | 0.00015327 | 0.018118 | 0.018118 | 0.00047629 | 0.00047629 | 0.0034064 | 0.0034064 | N/A | N/A | 0.0011255 | 0.0011255 | 0.00074727 | 0.00074727 | 0.0026795 | 0.0026795 | 0.0016675 | 0.0016675 | 750 | 331 | 12 | 112 | NO
2013-09-12 | N/A | N/A | 0.00089526 | 0.00089526 | 0.1917 | 0.1917 | 0.87081 | 0.87081 | 0.37437 | 0.37437 | N/A | N/A | 6.967e-06 | 6.967e-06 | 0.00082669 | 0.00082669 | 0.013065 | 0.013065 | 0.0052573 | 0.0052573 | N/A | N/A | 0.021936 | 0.021936 | 0.024216 | 0.024216 | 0.024117 | 0.024117 | 0.023186 | 0.023186 | 913 | 390 | 17 | 39 | NO
2013-09-13 | N/A | N/A | 0.089909 | 0.089909 | 2.2165 | 2.2165 | 0.46406 | 0.46406 | 0.60639 | 0.60639 | N/A | N/A | 0.00050511 | 0.00050511 | 0.0025149 | 0.0025149 | 0.0032218 | 0.0032218 | 0.0019175 | 0.0019175 | N/A | N/A | 3.6266e-07 | 3.6266e-07 | 0.011964 | 0.011964 | 0.029712 | 0.029712 | 0.013704 | 0.013704 | 715 | 331 | 17 | 19 | NO
2013-09-14 | N/A | N/A | 0.0018323 | 0.0018323 | 0.0042814 | 0.0042814 | 0.018804 | 0.018804 | 0.0088969 | 0.0088969 | N/A | N/A | 2.0901e-05 | 2.0901e-05 | 4.351e-05 | 4.351e-05 | 0.00017813 | 0.00017813 | 8.6334e-05 | 8.6334e-05 | N/A | N/A | 3.6266e-07 | 3.6266e-07 | 0.00016424 | 0.00016424 | 0.0077638 | 0.0077638 | 0.0030655 | 0.0030655 | 479 | 190 | 2 | 17 | NO
2013-09-15 | N/A | N/A | 0 | 0 | 0.0012183 | 0.0012183 | 0.01928 | 0.01928 | 0.0077534 | 0.0077534 | N/A | N/A | 0 | 0 | 1.7404e-05 | 1.7404e-05 | 0.00024783 | 0.00024783 | 9.9965e-05 | 9.9965e-05 | N/A | N/A | 0.011694 | 0.011694 | 0.0080743 | 0.0080743 | 0.018324 | 0.018324 | 0.013657 | 0.013657 | 153 | 96 | 2 | 5 | NO
2013-09-16 | N/A | N/A | 0.22005 | 0.22005 | 0.59905 | 0.59905 | 0.12269 | 0.12269 | 0.24794 | 0.24794 | N/A | N/A | 0.0083673 | 0.0083673 | 0.0051864 | 0.0051864 | 0.00078221 | 0.00078221 | 0.0048468 | 0.0048468 | N/A | N/A | 0.0088867 | 0.0088867 | 0.0069257 | 0.0069257 | 0.014746 | 0.014746 | 0.010837 | 0.010837 | 740 | 346 | 15 | 72 | NO
2013-09-17 | N/A | N/A | 0.23362 | 0.23362 | 0.015046 | 0.015046 | 0.056315 | 0.056315 | 0.12622 | 0.12622 | N/A | N/A | 0.0020796 | 0.0020796 | 0.00010442 | 0.00010442 | 0.0002517 | 0.0002517 | 0.0010209 | 0.0010209 | N/A | N/A | 0.0081656 | 0.0081656 | 0.00016424 | 0.00016424 | 0.0016455 | 0.0016455 | 0.0042227 | 0.0042227 | 509 | 292 | 6 | 44 | NO
2013-09-18 | N/A | N/A | 0.28732 | 0.28732 | 0.74285 | 0.74285 | 0.21852 | 0.21852 | 0.3397 | 0.3397 | N/A | N/A | 0.00049465 | 0.00049465 | 0.0047513 | 0.0047513 | 0.0019749 | 0.0019749 | 0.0018145 | 0.0018145 | N/A | N/A | 0.00023376 | 0.00023376 | 0.027706 | 0.027706 | 0.0028731 | 0.0028731 | 0.0060478 | 0.0060478 | 800 | 397 | 24 | 59 | NO
2013-09-19 | N/A | N/A | 0.037538 | 0.037538 | 0.025262 | 0.025262 | 0.16141 | 0.16141 | 0.083853 | 0.083853 | N/A | N/A | 9.4054e-05 | 9.4054e-05 | 0.00028717 | 0.00028717 | 0.00066991 | 0.00066991 | 0.00035291 | 0.00035291 | N/A | N/A | 0.015286 | 0.015286 | 0.013052 | 0.013052 | 0.013619 | 0.013619 | 0.014245 | 0.014245 | 577 | 322 | 8 | 49 | NO
2013-09-20 | N/A | N/A | 0.00033093 | 0.00033093 | 1.1377 | 1.1377 | 0.044264 | 0.044264 | 0.21548 | 0.21548 | N/A | N/A | 3.4835e-06 | 3.4835e-06 | 0.0098767 | 0.0098767 | 0.00058859 | 0.00058859 | 0.0019508 | 0.0019508 | N/A | N/A | 3.6266e-07 | 3.6266e-07 | 0.010276 | 0.010276 | 0.0013977 | 0.0013977 | 0.0023354 | 0.0023354 | 513 | 252 | 4 | 22 | NO
2013-09-21 | N/A | N/A | 0.00099976 | 0.00099976 | 0.6829 | 0.6829 | 0.0045267 | 0.0045267 | 0.12107 | 0.12107 | N/A | N/A | 1.045e-05 | 1.045e-05 | 0.011078 | 0.011078 | 7.3574e-05 | 7.3574e-05 | 0.0019614 | 0.0019614 | N/A | N/A | 3.6266e-07 | 3.6266e-07 | 0.0036015 | 0.0036015 | 1.9171e-05 | 1.9171e-05 | 0.00063452 | 0.00063452 | 219 | 142 | 1 | 29 | NO
2013-09-22 | N/A | N/A | 0.060553 | 0.060553 | 0.036783 | 0.036783 | 0.02407 | 0.02407 | 0.042146 | 0.042146 | N/A | N/A | 0.00041105 | 0.00041105 | 0.00082669 | 0.00082669 | 0.00019749 | 0.00019749 | 0.00039986 | 0.00039986 | N/A | N/A | 3.6266e-07 | 3.6266e-07 | 0.0052897 | 0.0052897 | 0.0097697 | 0.0097697 | 0.0047422 | 0.0047422 | 171 | 133 | 4 | 13 | NO
2013-09-23 | N/A | N/A | 0.079441 | 0.079441 | 0.92465 | 0.92465 | 0.031037 | 0.031037 | 0.20762 | 0.20762 | N/A | N/A | 0.0004424 | 0.0004424 | 0.0016969 | 0.0016969 | 0.00049178 | 0.00049178 | 0.00068007 | 0.00068007 | N/A | N/A | 3.6266e-07 | 3.6266e-07 | 0.0057683 | 0.0057683 | 0.0014132 | 0.0014132 | 0.0015569 | 0.0015569 | 505 | 284 | 3 | 20 | NO
2013-09-24 | N/A | N/A | 0.1211 | 0.1211 | 0.0089108 | 0.0089108 | 0.00071638 | 0.00071638 | 0.054486 | 0.054486 | N/A | N/A | 0.00045634 | 0.00045634 | 7.8318e-05 | 7.8318e-05 | 1.1617e-05 | 1.1617e-05 | 0.00021659 | 0.00021659 | N/A | N/A | 3.6266e-07 | 3.6266e-07 | 0.00048621 | 0.00048621 | 0.012422 | 0.012422 | 0.0049436 | 0.0049436 | 429 | 296 | 5 | 48 | NO
2013-09-25 | N/A | N/A | 0.11535 | 0.11535 | 0.38305 | 0.38305 | 0.0065674 | 0.0065674 | 0.1194 | 0.1194 | N/A | N/A | 0.00052252 | 0.00052252 | 0.016003 | 0.016003 | 0.00022459 | 0.00022459 | 0.0031004 | 0.0031004 | N/A | N/A | 3.6266e-07 | 3.6266e-07 | 0.023016 | 0.023016 | 1.9171e-05 | 1.9171e-05 | 0.0040137 | 0.0040137 | 484 | 271 | 9 | 33 | NO
2013-09-26 | N/A | N/A | 2.5348 | 2.5348 | 35.2751 | 35.2751 | 21.2507 | 21.2507 | 15.554 | 15.554 | N/A | N/A | 0.023998 | 0.023998 | 0.16737 | 0.16737 | 0.10213 | 0.10213 | 0.079513 | 0.079513 | N/A | N/A | 0.046822 | 0.046822 | 0.11983 | 0.11983 | 0.19369 | 0.19369 | 0.11698 | 0.11698 | 17983 | 5169 | 560 | 4248 | Yes
2013-09-27 | N/A | N/A | 0.20373 | 0.20373 | 3.3711 | 3.3711 | 1.1931 | 1.1931 | 1.142 | 1.142 | N/A | N/A | 0.00022991 | 0.00022991 | 0.01012 | 0.01012 | 0.0075897 | 0.0075897 | 0.0048301 | 0.0048301 | N/A | N/A | 0.010444 | 0.010444 | 0.01481 | 0.01481 | 0.013657 | 0.013657 | 0.012461 | 0.012461 | 4799 | 1957 | 99 | 1149 | NO
2013-09-28 | N/A | N/A | 0.14938 | 0.14938 | 7.7321 | 7.7321 | 3.1648 | 3.1648 | 2.6487 | 2.6487 | N/A | N/A | 0.00070366 | 0.00070366 | 0.038428 | 0.038428 | 0.017089 | 0.017089 | 0.013679 | 0.013679 | N/A | N/A | 0.017167 | 0.017167 | 0.037061 | 0.037061 | 0.056175 | 0.056175 | 0.035887 | 0.035887 | 3835 | 996 | 98 | 463 | NO
2013-09-29 | N/A | N/A | 0.021315 | 0.021315 | 0.089587 | 0.089587 | 0.20574 | 0.20574 | 0.10533 | 0.10533 | N/A | N/A | 0.00018114 | 0.00018114 | 0.00015664 | 0.00015664 | 0.0044454 | 0.0044454 | 0.0018448 | 0.0018448 | N/A | N/A | 3.6266e-07 | 3.6266e-07 | 0.01528 | 0.01528 | 0.013925 | 0.013925 | 0.0081062 | 0.0081062 | 602 | 289 | 10 | 32 | NO
2013-09-30 | N/A | N/A | 0.29269 | 0.29269 | 7.656 | 7.656 | 2.4215 | 2.4215 | 2.407 | 2.407 | N/A | N/A | 0.0072979 | 0.0072979 | 0.040499 | 0.040499 | 0.019962 | 0.019962 | 0.01803 | 0.01803 | N/A | N/A | 3.6266e-07 | 3.6266e-07 | 0.063254 | 0.063254 | 0.038173 | 0.038173 | 0.025941 | 0.025941 | 1669 | 565 | 27 | 101 | NO
2013-10-01 | N/A | N/A | 3.475 | 3.475 | 32.7069 | 32.7069 | 12.3989 | 12.3989 | 12.0535 | 12.0535 | N/A | N/A | 0.048884 | 0.048884 | 0.18808 | 0.18808 | 0.10679 | 0.10679 | 0.095761 | 0.095761 | N/A | N/A | 0.070422 | 0.070422 | 0.086679 | 0.086679 | 0.11869 | 0.11869 | 0.092133 | 0.092133 | 12903 | 2358 | 236 | 1001 | Yes
2013-10-02 | N/A | N/A | 2.7995 | 2.7995 | 8.8173 | 8.8173 | 9.3886 | 9.3886 | 6.4242 | 6.4242 | N/A | N/A | 0.070983 | 0.070983 | 0.043971 | 0.043971 | 0.10759 | 0.10759 | 0.080599 | 0.080599 | N/A | N/A | 0.038716 | 0.038716 | 0.12017 | 0.12017 | 0.11009 | 0.11009 | 0.080813 | 0.080813 | 8233 | 2242 | 159 | 1319 | NO
2013-10-03 | N/A | N/A | 0.22923 | 0.22923 | 0.26515 | 0.26515 | 0.26756 | 0.26756 | 0.25048 | 0.25048 | N/A | N/A | 0.0060508 | 0.0060508 | 0.0032719 | 0.0032719 | 0.0013166 | 0.0013166 | 0.0037154 | 0.0037154 | N/A | N/A | 0.0088867 | 0.0088867 | 0.040324 | 0.040324 | 0.025271 | 0.025271 | 0.020767 | 0.020767 | 1228 | 492 | 12 | 108 | NO
2013-10-04 | N/A | N/A | 0.19934 | 0.19934 | 0.2369 | 0.2369 | 0.17532 | 0.17532 | 0.19648 | 0.19648 | N/A | N/A | 0.00058174 | 0.00058174 | 0.0028978 | 0.0028978 | 0.00078221 | 0.00078221 | 0.0010633 | 0.0010633 | N/A | N/A | 3.6266e-07 | 3.6266e-07 | 0.054995 | 0.054995 | 1.9171e-05 | 1.9171e-05 | 0.0095799 | 0.0095799 | 581 | 299 | 10 | 27 | NO
2013-10-05 | N/A | N/A | 0.11615 | 0.11615 | 1.0803 | 1.0803 | 0.14427 | 0.14427 | 0.29497 | 0.29497 | N/A | N/A | 0.0010903 | 0.0010903 | 0.021198 | 0.021198 | 0.00092161 | 0.00092161 | 0.0045242 | 0.0045242 | N/A | N/A | 0.011426 | 0.011426 | 0.0081875 | 0.0081875 | 0.0030899 | 0.0030899 | 0.0076018 | 0.0076018 | 720 | 284 | 21 | 83 | NO
2013-10-06 | N/A | N/A | 0.1995 | 0.1995 | 0.18184 | 0.18184 | 0.21419 | 0.21419 | 0.20217 | 0.20217 | N/A | N/A | 0.0007385 | 0.0007385 | 0.0012444 | 0.0012444 | 0.013867 | 0.013867 | 0.0059616 | 0.0059616 | N/A | N/A | 3.6266e-07 | 3.6266e-07 | 0.015367 | 0.015367 | 0.0073998 | 0.0073998 | 0.0055692 | 0.0055692 | 453 | 171 | 6 | 13 | NO
2013-10-07 | N/A | N/A | 0.0015014 | 0.0015014 | 0.81448 | 0.81448 | 0.3258 | 0.3258 | 0.26985 | 0.26985 | N/A | N/A | 1.7417e-05 | 1.7417e-05 | 0.037932 | 0.037932 | 0.020035 | 0.020035 | 0.014447 | 0.014447 | N/A | N/A | 0.00058907 | 0.00058907 | 0.023642 | 0.023642 | 1.9171e-05 | 1.9171e-05 | 0.0043787 | 0.0043787 | 973 | 398 | 27 | 129 | NO
2013-10-08 | N/A | N/A | 0.13714 | 0.13714 | 0.090561 | 0.090561 | 0.77666 | 0.77666 | 0.37918 | 0.37918 | N/A | N/A | 0.0065071 | 0.0065071 | 0.00080928 | 0.00080928 | 0.0037019 | 0.0037019 | 0.0044182 | 0.0044182 | N/A | N/A | 0.0092699 | 0.0092699 | 0.010772 | 0.010772 | 0.0021141 | 0.0021141 | 0.0067324 | 0.0067324 | 1006 | 374 | 12 | 97 | NO
2013-10-09 | N/A | N/A | 0.23638 | 0.23638 | 0.078126 | 0.078126 | 0.56428 | 0.56428 | 0.33709 | 0.33709 | N/A | N/A | 0.0054726 | 0.0054726 | 0.00057433 | 0.00057433 | 0.012775 | 0.012775 | 0.0074762 | 0.0074762 | N/A | N/A | 3.6266e-07 | 3.6266e-07 | 0.013052 | 0.013052 | 0.0097348 | 0.0097348 | 0.0060796 | 0.0060796 | 813 | 337 | 10 | 96 | NO
2013-10-10 | N/A | N/A | 0.037548 | 0.037548 | 0.00024366 | 0.00024366 | 0.17038 | 0.17038 | 0.083012 | 0.083012 | N/A | N/A | 0.00036925 | 0.00036925 | 3.4808e-05 | 3.4808e-05 | 0.0013592 | 0.0013592 | 0.00069824 | 0.00069824 | N/A | N/A | 3.6266e-07 | 3.6266e-07 | 0.0063861 | 0.0063861 | 0.0057696 | 0.0057696 | 0.0033684 | 0.0033684 | 674 | 331 | 7 | 23 | NO
2013-10-11 | N/A | N/A | 0.0027415 | 0.0027415 | 0.052856 | 0.052856 | 0.012705 | 0.012705 | 0.015361 | 0.015361 | N/A | N/A | 1.045e-05 | 1.045e-05 | 0.00060914 | 0.00060914 | 8.1319e-05 | 8.1319e-05 | 0.00014237 | 0.00014237 | N/A | N/A | 3.6266e-07 | 3.6266e-07 | 0.00016424 | 0.00016424 | 0.030355 | 0.030355 | 0.011902 | 0.011902 | 468 | 306 | 4 | 27 | NO
2013-10-12 | N/A | N/A | 0.023743 | 0.023743 | 0.17996 | 0.17996 | 0.14118 | 0.14118 | 0.096868 | 0.096868 | N/A | N/A | 0.00020553 | 0.00020553 | 0.0041073 | 0.0041073 | 0.00194 | 0.00194 | 0.0015631 | 0.0015631 | N/A | N/A | 0.0081831 | 0.0081831 | 0.069902 | 0.069902 | 0.0075005 | 0.0075005 | 0.018659 | 0.018659 | 278 | 167 | 6 | 27 | NO
2013-10-13 | N/A | N/A | 0.032006 | 0.032006 | 0.26847 | 0.26847 | 0.36398 | 0.36398 | 0.20301 | 0.20301 | N/A | N/A | 0.00039363 | 0.00039363 | 0.0046991 | 0.0046991 | 0.0059672 | 0.0059672 | 0.0033231 | 0.0033231 | N/A | N/A | 3.6266e-07 | 3.6266e-07 | 0.083764 | 0.083764 | 0.029058 | 0.029058 | 0.025945 | 0.025945 | 453 | 176 | 7 | 14 | NO
2013-10-14 | N/A | N/A | 0.061438 | 0.061438 | 0.031936 | 0.031936 | 0.15506 | 0.15506 | 0.092921 | 0.092921 | N/A | N/A | 0.00044589 | 0.00044589 | 0.00023495 | 0.00023495 | 0.0019439 | 0.0019439 | 0.00099511 | 0.00099511 | N/A | N/A | 3.6266e-07 | 3.6266e-07 | 0.016315 | 0.016315 | 0.015404 | 0.015404 | 0.008865 | 0.008865 | 514 | 328 | 7 | 25 | NO
2013-10-15 | N/A | N/A | 0.0013028 | 0.0013028 | 0.029378 | 0.029378 | 0.55316 | 0.55316 | 0.22205 | 0.22205 | N/A | N/A | 1.045e-05 | 1.045e-05 | 4.351e-05 | 4.351e-05 | 0.0019284 | 0.0019284 | 0.0007664 | 0.0007664 | N/A | N/A | 3.6266e-07 | 3.6266e-07 | 0.033101 | 0.033101 | 0.0079342 | 0.0079342 | 0.008865 | 0.008865 | 752 | 326 | 14 | 55 | NO
2013-10-16 | N/A | N/A | 1.0892 | 1.0892 | 2.2688 | 2.2688 | 1.7962 | 1.7962 | 1.5711 | 1.5711 | N/A | N/A | 0.030181 | 0.030181 | 0.0089021 | 0.0089021 | 0.013239 | 0.013239 | 0.019851 | 0.019851 | N/A | N/A | 0.010047 | 0.010047 | 0.023964 | 0.023964 | 0.026409 | 0.026409 | 0.018869 | 0.018869 | 3360 | 883 | 48 | 324 | NO
2013-10-17 | N/A | N/A | 2.0273 | 2.0273 | 0.34556 | 0.34556 | 5.1439 | 5.1439 | 2.9536 | 2.9536 | N/A | N/A | 0.017943 | 0.017943 | 0.0013401 | 0.0013401 | 0.036195 | 0.036195 | 0.022192 | 0.022192 | N/A | N/A | 0.019428 | 0.019428 | 0.012008 | 0.012008 | 0.054549 | 0.054549 | 0.031874 | 0.031874 | 2840 | 926 | 37 | 285 | NO
2013-10-18 | N/A | N/A | 0.10079 | 0.10079 | 0.15329 | 0.15329 | 0.7772 | 0.7772 | 0.3745 | 0.3745 | N/A | N/A | 0.0007803 | 0.0007803 | 0.018735 | 0.018735 | 0.0028384 | 0.0028384 | 0.0047105 | 0.0047105 | N/A | N/A | 3.6266e-07 | 3.6266e-07 | 0.0055334 | 0.0055334 | 0.0052468 | 0.0052468 | 0.0030155 | 0.0030155 | 876 | 471 | 17 | 86 | NO
2013-10-19 | N/A | N/A | 0.048292 | 0.048292 | 0.19328 | 0.19328 | 0.99162 | 0.99162 | 0.4425 | 0.4425 | N/A | N/A | 0.00045285 | 0.00045285 | 0.0011574 | 0.0011574 | 0.0228 | 0.0228 | 0.0093165 | 0.0093165 | N/A | N/A | 3.6266e-07 | 3.6266e-07 | 0.028228 | 0.028228 | 0.021491 | 0.021491 | 0.01332 | 0.01332 | 1367 | 325 | 11 | 58 | NO
2013-10-20 | N/A | N/A | 0.12059 | 0.12059 | 0.022625 | 0.022625 | 0.060613 | 0.060613 | 0.08008 | 0.08008 | N/A | N/A | 0.0013272 | 0.0013272 | 0.00014793 | 0.00014793 | 0.00016651 | 0.00016651 | 0.00066795 | 0.00066795 | N/A | N/A | 0.035647 | 0.035647 | 0.0059946 | 0.0059946 | 0.019601 | 0.019601 | 0.02421 | 0.02421 | 532 | 228 | 4 | 22 | NO
2013-10-21 | N/A | N/A | 0.0075278 | 0.0075278 | 0.54546 | 0.54546 | 0.51125 | 0.51125 | 0.29818 | 0.29818 | N/A | N/A | 0.00034138 | 0.00034138 | 0.0014967 | 0.0014967 | 0.0019788 | 0.0019788 | 0.0011829 | 0.0011829 | N/A | N/A | 3.6266e-07 | 3.6266e-07 | 0.024765 | 0.024765 | 0.0090804 | 0.0090804 | 0.0078623 | 0.0078623 | 855 | 326 | 8 | 20 | NO
2013-10-22 | N/A | N/A | 0.020981 | 0.020981 | 1.3816 | 1.3816 | 0.39707 | 0.39707 | 0.4049 | 0.4049 | N/A | N/A | 0.00034486 | 0.00034486 | 0.056049 | 0.056049 | 0.0020949 | 0.0020949 | 0.010725 | 0.010725 | N/A | N/A | 0.033957 | 0.033957 | 0.099741 | 0.099741 | 0.020895 | 0.020895 | 0.040298 | 0.040298 | 1483 | 522 | 32 | 152 | NO
2013-10-23 | N/A | N/A | 0.014136 | 0.014136 | 0.63959 | 0.63959 | 0.21425 | 0.21425 | 0.20127 | 0.20127 | N/A | N/A | 0.00023688 | 0.00023688 | 0.004029 | 0.004029 | 0.0012701 | 0.0012701 | 0.0013011 | 0.0013011 | N/A | N/A | 0.0089076 | 0.0089076 | 0.02681 | 0.02681 | 0.013042 | 0.013042 | 0.013641 | 0.013641 | 855 | 489 | 21 | 78 | NO
2013-10-24 | N/A | N/A | 0.023322 | 0.023322 | 0.010521 | 0.010521 | 0.15191 | 0.15191 | 0.07139 | 0.07139 | N/A | N/A | 0.00032745 | 0.00032745 | 0.00011313 | 0.00011313 | 0.0010184 | 0.0010184 | 0.00056041 | 0.00056041 | N/A | N/A | 3.6266e-07 | 3.6266e-07 | 0.01729 | 0.01729 | 0.0025323 | 0.0025323 | 0.004 | 0.004 | 561 | 370 | 8 | 34 | NO
2013-10-25 | N/A | N/A | 0.0048908 | 0.0048908 | 0.0059957 | 0.0059957 | 0.13544 | 0.13544 | 0.056146 | 0.056146 | N/A | N/A | 7.3153e-05 | 7.3153e-05 | 7.8318e-05 | 7.8318e-05 | 0.0013979 | 0.0013979 | 0.00059222 | 0.00059222 | N/A | N/A | 3.6266e-07 | 3.6266e-07 | 0.00016424 | 0.00016424 | 0.014347 | 0.014347 | 0.0056404 | 0.0056404 | 462 | 291 | 7 | 37 | NO
2013-10-26 | N/A | N/A | 0.013129 | 0.013129 | 0.0045337 | 0.0045337 | 1.0223 | 1.0223 | 0.40638 | 0.40638 | N/A | N/A | 0.00023339 | 0.00023339 | 3.4808e-05 | 3.4808e-05 | 0.0098899 | 0.0098899 | 0.0039759 | 0.0039759 | N/A | N/A | 3.6266e-07 | 3.6266e-07 | 0.01367 | 0.01367 | 0.0037366 | 0.0037366 | 0.003841 | 0.003841 | 692 | 158 | 13 | 31 | NO
2013-10-27 | N/A | N/A | 0.011454 | 0.011454 | 0.15128 | 0.15128 | 0.022862 | 0.022862 | 0.040254 | 0.040254 | N/A | N/A | 0.00021598 | 0.00021598 | 0.0008615 | 0.0008615 | 0.0032256 | 0.0032256 | 0.0015055 | 0.0015055 | N/A | N/A | 3.6266e-07 | 3.6266e-07 | 0.026888 | 0.026888 | 0.015137 | 0.015137 | 0.010601 | 0.010601 | 252 | 164 | 3 | 27 | NO
2013-10-28 | N/A | N/A | 0.62695 | 0.62695 | 0.27394 | 0.27394 | 1.0671 | 1.0671 | 0.73768 | 0.73768 | N/A | N/A | 0.0024768 | 0.0024768 | 0.0014532 | 0.0014532 | 0.008763 | 0.008763 | 0.0047574 | 0.0047574 | N/A | N/A | 7.3296e-06 | 7.3296e-06 | 0.0096233 | 0.0096233 | 0.020961 | 0.020961 | 0.0098768 | 0.0098768 | 1489 | 397 | 10 | 35 | NO
2013-10-29 | N/A | N/A | 0.024224 | 0.024224 | 0.10904 | 0.10904 | 0.064513 | 0.064513 | 0.054746 | 0.054746 | N/A | N/A | 0.00025081 | 0.00025081 | 0.00114 | 0.00114 | 0.0036787 | 0.0036787 | 0.0017464 | 0.0017464 | N/A | N/A | 3.6266e-07 | 3.6266e-07 | 0.014618 | 0.014618 | 0.014734 | 0.014734 | 0.0083076 | 0.0083076 | 538 | 302 | 13 | 6 | NO
2013-10-30 | N/A | N/A | 0.067419 | 0.067419 | 0.045973 | 0.045973 | 0.05841 | 0.05841 | 0.060162 | 0.060162 | N/A | N/A | 0.0006758 | 0.0006758 | 0.0040203 | 0.0040203 | 0.00060021 | 0.00060021 | 0.0012284 | 0.0012284 | N/A | N/A | 0.0065807 | 0.0065807 | 0.06683 | 0.06683 | 0.029402 | 0.029402 | 0.025994 | 0.025994 | 546 | 328 | 7 | 37 | NO
2013-10-31 | N/A | N/A | 0.0089735 | 0.0089735 | 0.111 | 0.111 | 0.088378 | 0.088378 | 0.057791 | 0.057791 | N/A | N/A | 0.00013237 | 0.00013237 | 0.0013923 | 0.0013923 | 0.0013205 | 0.0013205 | 0.00081638 | 0.00081638 | N/A | N/A | 3.6266e-07 | 3.6266e-07 | 0.0099975 | 0.0099975 | 0.013657 | 0.013657 | 0.0070823 | 0.0070823 | 515 | 260 | 1 | 16 | NO
2013-11-01 | N/A | N/A | 0.024029 | 0.024029 | 1.7245 | 1.7245 | 0.072486 | 0.072486 | 0.33896 | 0.33896 | N/A | N/A | 0.00047375 | 0.00047375 | 0.014637 | 0.014637 | 0.00049178 | 0.00049178 | 0.0029459 | 0.0029459 | N/A | N/A | 3.6266e-07 | 3.6266e-07 | 0.056675 | 0.056675 | 0.021878 | 0.021878 | 0.018422 | 0.018422 | 684 | 265 | 14 | 29 | NO
2013-11-02 | N/A | N/A | 0.27658 | 0.27658 | 0.025601 | 0.025601 | 0.089923 | 0.089923 | 0.15989 | 0.15989 | N/A | N/A | 0.0029679 | 0.0029679 | 0.00041769 | 0.00041769 | 0.0017309 | 0.0017309 | 0.0020402 | 0.0020402 | N/A | N/A | 3.6266e-07 | 3.6266e-07 | 0.011129 | 0.011129 | 0.0076012 | 0.0076012 | 0.0049103 | 0.0049103 | 445 | 210 | 5 | 31 | NO
2013-11-03 | N/A | N/A | 0.38793 | 0.38793 | 0.30861 | 0.30861 | 0.28363 | 0.28363 | 0.33333 | 0.33333 | N/A | N/A | 0.0094437 | 0.0094437 | 0.0022712 | 0.0022712 | 0.0093129 | 0.0093129 | 0.0081441 | 0.0081441 | N/A | N/A | 0.037887 | 0.037887 | 0.00016424 | 0.00016424 | 0.0033494 | 0.0033494 | 0.017812 | 0.017812 | 949 | 262 | 20 | 26 | NO
2013-11-04 | N/A | N/A | 0.021747 | 0.021747 | 0.095704 | 0.095704 | 0.66478 | 0.66478 | 0.28614 | 0.28614 | N/A | N/A | 0.0002752 | 0.0002752 | 0.00073967 | 0.00073967 | 0.0048869 | 0.0048869 | 0.0021599 | 0.0021599 | N/A | N/A | 3.6266e-07 | 3.6266e-07 | 0.021736 | 0.021736 | 0.015415 | 0.015415 | 0.0098132 | 0.0098132 | 723 | 371 | 14 | 34 | NO
2013-11-05 | N/A | N/A | 0.01052 | 0.01052 | 0.12798 | 0.12798 | 0.17525 | 0.17525 | 0.095399 | 0.095399 | N/A | N/A | 6.6186e-05 | 6.6186e-05 | 0.001723 | 0.001723 | 0.0014366 | 0.0014366 | 0.0008906 | 0.0008906 | N/A | N/A | 3.6266e-07 | 3.6266e-07 | 0.0097277 | 0.0097277 | 0.0048789 | 0.0048789 | 0.0036017 | 0.0036017 | 203 | 101 | 2 | 11 | NO
2013-11-06 | N/A | N/A | 0.045773 | 0.045773 | 0.067458 | 0.067458 | 0.31995 | 0.31995 | 0.15679 | 0.15679 | N/A | N/A | 0.00047375 | 0.00047375 | 0.00056563 | 0.00056563 | 0.0016845 | 0.0016845 | 0.0009633 | 0.0009633 | N/A | N/A | 0.0066225 | 0.0066225 | 0.0085965 | 0.0085965 | 0.012639 | 0.012639 | 0.0093194 | 0.0093194 | 656 | 370 | 11 | 38 | NO
2013-11-07 | N/A | N/A | 0.012401 | 0.012401 | 0.20769 | 0.20769 | 0.060687 | 0.060687 | 0.065279 | 0.065279 | N/A | N/A | 0.00016024 | 0.00016024 | 0.0016708 | 0.0016708 | 0.0021143 | 0.0021143 | 0.0011875 | 0.0011875 | N/A | N/A | 3.6266e-07 | 3.6266e-07 | 0.057562 | 0.057562 | 0.0050183 | 0.0050183 | 0.011982 | 0.011982 | 532 | 297 | 3 | 18 | NO
2013-11-08 | N/A | N/A | 0.16533 | 0.16533 | 0.91121 | 0.91121 | 0.075042 | 0.075042 | 0.25984 | 0.25984 | N/A | N/A | 0.0045285 | 0.0045285 | 0.0013662 | 0.0013662 | 0.0003911 | 0.0003911 | 0.0023598 | 0.0023598 | N/A | N/A | 0.01105 | 0.01105 | 0.047303 | 0.047303 | 0.035881 | 0.035881 | 0.027072 | 0.027072 | 749 | 337 | 11 | 53 | NO
2013-11-09 | N/A | N/A | 0.0283 | 0.0283 | 0.4022 | 0.4022 | 0.097915 | 0.097915 | 0.12061 | 0.12061 | N/A | N/A | 0.00019159 | 0.00019159 | 0.001897 | 0.001897 | 0.00071251 | 0.00071251 | 0.00069218 | 0.00069218 | N/A | N/A | 3.6266e-07 | 3.6266e-07 | 0.02225 | 0.02225 | 0.027238 | 0.027238 | 0.014527 | 0.014527 | 504 | 237 | 10 | 57 | NO
2013-11-10 | N/A | N/A | 1.3412 | 1.3412 | 0.49849 | 0.49849 | 0.1566 | 0.1566 | 0.73118 | 0.73118 | N/A | N/A | 0.0032954 | 0.0032954 | 0.0032545 | 0.0032545 | 0.0032256 | 0.0032256 | 0.003261 | 0.003261 | N/A | N/A | 3.6266e-07 | 3.6266e-07 | 0.014166 | 0.014166 | 0.011857 | 0.011857 | 0.0071035 | 0.0071035 | 879 | 304 | 18 | 42 | NO
2013-11-11 | N/A | N/A | 0.14288 | 0.14288 | 1.7391 | 1.7391 | 0.064869 | 0.064869 | 0.39019 | 0.39019 | N/A | N/A | 0.00041105 | 0.00041105 | 0.025758 | 0.025758 | 0.0044493 | 0.0044493 | 0.0064023 | 0.0064023 | N/A | N/A | 3.6266e-07 | 3.6266e-07 | 0.016741 | 0.016741 | 0.01291 | 0.01291 | 0.0079638 | 0.0079638 | 834 | 336 | 10 | 24 | NO
2013-11-12 | N/A | N/A | 0.64744 | 0.64744 | 0.3015 | 0.3015 | 1.8537 | 1.8537 | 1.059 | 1.059 | N/A | N/A | 0.00611 | 0.00611 | 0.0011226 | 0.0011226 | 0.0050495 | 0.0050495 | 0.0048271 | 0.0048271 | N/A | N/A | 3.6266e-07 | 3.6266e-07 | 0.044309 | 0.044309 | 0.0068964 | 0.0068964 | 0.01041 | 0.01041 | 812 | 391 | 12 | 52 | NO
2013-11-13 | N/A | N/A | 0.76718 | 0.76718 | 0.52288 | 0.52288 | 0.41859 | 0.41859 | 0.58831 | 0.58831 | N/A | N/A | 0.0045216 | 0.0045216 | 0.01951 | 0.01951 | 0.0012508 | 0.0012508 | 0.005851 | 0.005851 | N/A | N/A | 0.025907 | 0.025907 | 0.10559 | 0.10559 | 0.0051693 | 0.0051693 | 0.031665 | 0.031665 | 1661 | 486 | 24 | 76 | NO
2013-11-14 | N/A | N/A | 0.47761 | 0.47761 | 2.3098 | 2.3098 | 0.1403 | 0.1403 | 0.66458 | 0.66458 | N/A | N/A | 0.0099732 | 0.0099732 | 0.030614 | 0.030614 | 0.0010378 | 0.0010378 | 0.010071 | 0.010071 | N/A | N/A | 0.012823 | 0.012823 | 0.0090751 | 0.0090751 | 0.015694 | 0.015694 | 0.013294 | 0.013294 | 1231 | 414 | 11 | 57 | NO
2013-11-15 | N/A | N/A | 0.053318 | 0.053318 | 0.030735 | 0.030735 | 0.046375 | 0.046375 | 0.046672 | 0.046672 | N/A | N/A | 0.00059219 | 0.00059219 | 0.00020885 | 0.00020885 | 0.00026332 | 0.00026332 | 0.00039683 | 0.00039683 | N/A | N/A | 3.6266e-07 | 3.6266e-07 | 0.012469 | 0.012469 | 0.00039479 | 0.00039479 | 0.0023248 | 0.0023248 | 455 | 286 | 5 | 19 | NO
2013-11-16 | N/A | N/A | 0.023141 | 0.023141 | 0.70641 | 0.70641 | 0.18103 | 0.18103 | 0.20382 | 0.20382 | N/A | N/A | 0.00026126 | 0.00026126 | 0.0038376 | 0.0038376 | 0.0027726 | 0.0027726 | 0.001866 | 0.001866 | N/A | N/A | 3.6266e-07 | 3.6266e-07 | 0.00016424 | 0.00016424 | 0.00057291 | 0.00057291 | 0.00025283 | 0.00025283 | 448 | 156 | 6 | 22 | NO
2013-11-17 | N/A | N/A | 0.0051834 | 0.0051834 | 0.14139 | 0.14139 | 0.0020678 | 0.0020678 | 0.027672 | 0.027672 | N/A | N/A | 5.5736e-05 | 5.5736e-05 | 0.0014532 | 0.0014532 | 2.3234e-05 | 2.3234e-05 | 0.00028626 | 0.00028626 | N/A | N/A | 0.050814 | 0.050814 | 0.043987 | 0.043987 | 0.029054 | 0.029054 | 0.041114 | 0.041114 | 180 | 125 | 0 | 3 | NO
2013-11-18 | N/A | N/A | 0.0016581 | 0.0016581 | 0.14289 | 0.14289 | 0.026127 | 0.026127 | 0.03581 | 0.03581 | N/A | N/A | 6.967e-06 | 6.967e-06 | 0.0014619 | 0.0014619 | 0.00015102 | 0.00015102 | 0.00031656 | 0.00031656 | N/A | N/A | 0.011572 | 0.011572 | 0.028942 | 0.028942 | 0.01753 | 0.01753 | 0.016926 | 0.016926 | 487 | 303 | 8 | 17 | NO
2013-11-19 | N/A | N/A | 0.056662 | 0.056662 | 0.052255 | 0.052255 | 0.58713 | 0.58713 | 0.26338 | 0.26338 | N/A | N/A | 0.0091581 | 0.0091581 | 0.0070573 | 0.0070573 | 0.068672 | 0.068672 | 0.032071 | 0.032071 | N/A | N/A | 0.0069708 | 0.0069708 | 0.0084833 | 0.0084833 | 0.014111 | 0.014111 | 0.010027 | 0.010027 | 978 | 410 | 13 | 77 | NO
2013-11-20 | N/A | N/A | 0.3639 | 0.3639 | 0.04646 | 0.04646 | 0.30806 | 0.30806 | 0.28681 | 0.28681 | N/A | N/A | 0.0026091 | 0.0026091 | 0.00060914 | 0.00060914 | 0.0073961 | 0.0073961 | 0.0041334 | 0.0041334 | N/A | N/A | 0.015554 | 0.015554 | 0.040167 | 0.040167 | 0.0030783 | 0.0030783 | 0.014958 | 0.014958 | 1040 | 331 | 7 | 4 | NO
2013-11-21 | N/A | N/A | 0.96837 | 0.87977 | 1.0607 | 1.0607 | 0.0028616 | 0.0028616 | 0.60678 | 0.56826 | N/A | N/A | 0.030874 | 0.012582 | 0.018466 | 0.018466 | 0.00010068 | 0.00010068 | 0.016678 | 0.0087242 | N/A | N/A | 0.018696 | 0.018696 | 0.037113 | 0.037113 | 1.9171e-05 | 1.9171e-05 | 0.014596 | 0.014596 | 991 | 451 | 14 | 82 | NO | Transmission
2013-11-22 | N/A | N/A | 0.66542 | 0.66542 | 0.088603 | 0.088603 | 0.0587 | 0.0587 | 0.32771 | 0.32771 | N/A | N/A | 0.0076428 | 0.0076428 | 0.00094851 | 0.00094851 | 0.00055761 | 0.00055761 | 0.0037063 | 0.0037063 | N/A | N/A | 0.0053719 | 0.0053719 | 0.02057 | 0.02057 | 0.013297 | 0.013297 | 0.011117 | 0.011117 | 627 | 359 | 4 | 46 | NO
2013-11-23 | N/A | N/A | 0.13754 | 0.13754 | 0.26449 | 0.26449 | 1.6075 | 1.6075 | 0.7346 | 0.7346 | N/A | N/A | 0.001578 | 0.001578 | 0.0047774 | 0.0047774 | 0.071239 | 0.071239 | 0.029382 | 0.029382 | N/A | N/A | 3.6266e-07 | 3.6266e-07 | 0.12023 | 0.12023 | 0.026409 | 0.026409 | 0.031257 | 0.031257 | 2127 | 535 | 25 | 320 | NO
2013-11-24 | N/A | N/A | 0.168 | 0.168 | 0.081564 | 0.081564 | 0.31916 | 0.31916 | 0.21208 | 0.21208 | N/A | N/A | 0.0011495 | 0.0011495 | 0.00072226 | 0.00072226 | 0.0060214 | 0.0060214 | 0.0029808 | 0.0029808 | N/A | N/A | 0.0078347 | 0.0078347 | 0.044475 | 0.044475 | 0.012105 | 0.012105 | 0.015882 | 0.015882 | 521 | 207 | 4 | 30 | NO
2013-11-25 | N/A | N/A | 0.00082907 | 0.00082907 | 0.094312 | 0.094312 | 0.28769 | 0.28769 | 0.1293 | 0.1293 | N/A | N/A | 6.967e-06 | 6.967e-06 | 0.0010007 | 0.0010007 | 0.0016109 | 0.0016109 | 0.0008073 | 0.0008073 | N/A | N/A | 0.010284 | 0.010284 | 0.0092665 | 0.0092665 | 1.9171e-05 | 1.9171e-05 | 0.0060917 | 0.0060917 | 652 | 372 | 10 | 30 | NO
2013-11-26 | N/A | N/A | 0.025739 | 0.025739 | 0.02279 | 0.02279 | 1.1469 | 1.1469 | 0.46378 | 0.46378 | N/A | N/A | 0.00028216 | 0.00028216 | 0.00019144 | 0.00019144 | 0.0074465 | 0.0074465 | 0.0030686 | 0.0030686 | N/A | N/A | 3.6266e-07 | 3.6266e-07 | 0.052994 | 0.052994 | 0.016639 | 0.016639 | 0.015732 | 0.015732 | 1133 | 441 | 11 | 81 | NO
2013-11-27 | N/A | N/A | 0.061215 | 0.061215 | 0.0058999 | 0.0058999 | 0.1599 | 0.1599 | 0.090188 | 0.090188 | N/A | N/A | 6.967e-05 | 6.967e-05 | 5.2212e-05 | 5.2212e-05 | 0.0014173 | 0.0014173 | 0.00059373 | 0.00059373 | N/A | N/A | 0.011621 | 0.011621 | 0.01159 | 0.01159 | 1.9171e-05 | 1.9171e-05 | 0.0070777 | 0.0070777 | 616 | 327 | 4 | 32 | NO
2013-11-28 | N/A | N/A | 0.040454 | 0.040454 | 0.067884 | 0.067884 | 0.77812 | 0.77812 | 0.33376 | 0.33376 | N/A | N/A | 0.00043892 | 0.00043892 | 0.00097462 | 0.00097462 | 0.021313 | 0.021313 | 0.008697 | 0.008697 | N/A | N/A | 3.6266e-07 | 3.6266e-07 | 0.046885 | 0.046885 | 0.031896 | 0.031896 | 0.020637 | 0.020637 | 1110 | 415 | 10 | 61 | NO
2013-11-29 | N/A | N/A | 0.04059 | 0.04059 | 0.098219 | 0.098219 | 0.15357 | 0.15357 | 0.094813 | 0.094813 | N/A | N/A | 0.00051904 | 0.00051904 | 0.00076577 | 0.00076577 | 0.0015412 | 0.0015412 | 0.00096179 | 0.00096179 | N/A | N/A | 0.0043617 | 0.0043617 | 0.00016424 | 0.00016424 | 0.0011499 | 0.0011499 | 0.0023748 | 0.0023748 | 517 | 326 | 6 | 52 | NO
2013-11-30 | N/A | N/A | 0 | 0 | 0.088986 | 0.088986 | 0.10054 | 0.10054 | 0.054813 | 0.054813 | N/A | N/A | 0 | 0 | 0.00078318 | 0.00078318 | 0.0014095 | 0.0014095 | 0.00068764 | 0.00068764 | N/A | N/A | 0.022326 | 0.022326 | 0.0030359 | 0.0030359 | 0.0010453 | 0.0010453 | 0.010645 | 0.010645 | 604 | 65 | 7 | 16 | NO
2013-12-01 | N/A | N/A | 0.005274 | 0.005274 | 0.85493 | 0.85493 | 0.094415 | 0.094415 | 0.18803 | 0.18803 | N/A | N/A | 0.0001045 | 0.0001045 | 0.0078144 | 0.0078144 | 0.0012624 | 0.0012624 | 0.0018993 | 0.0018993 | N/A | N/A | 0.0136 | 0.0136 | 0.044805 | 0.044805 | 0.04596 | 0.04596 | 0.031689 | 0.031689 | 442 | 176 | 7 | 14 | NO
2013-12-02 | N/A | N/A | 0.0039329 | 0.0039329 | 0.13886 | 0.13886 | 0.23354 | 0.23354 | 0.11723 | 0.11723 | N/A | N/A | 5.5736e-05 | 5.5736e-05 | 0.003533 | 0.003533 | 0.0017348 | 0.0017348 | 0.0013177 | 0.0013177 | N/A | N/A | 0.0082353 | 0.0082353 | 0.029786 | 0.029786 | 0.0042748 | 0.0042748 | 0.010437 | 0.010437 | 641 | 366 | 5 | 49 | NO
2013-12-03 | N/A | N/A | 0.038949 | 0.038949 | 0.016177 | 0.016177 | 0.055029 | 0.055029 | 0.041275 | 0.041275 | N/A | N/A | 0.00082907 | 0.00082907 | 0.00017404 | 0.00017404 | 0.0004337 | 0.0004337 | 0.00056041 | 0.00056041 | N/A | N/A | 3.6266e-07 | 3.6266e-07 | 0.0044978 | 0.0044978 | 0.017104 | 0.017104 | 0.0074731 | 0.0074731 | 589 | 356 | 10 | 89 | NO
2013-12-04 | N/A | N/A | 2.8491 | 2.8491 | 2.2462 | 2.2462 | 2.5407 | 2.5407 | 2.6236 | 2.6236 | N/A | N/A | 0.047208 | 0.047208 | 0.066344 | 0.066344 | 0.046011 | 0.046011 | 0.050071 | 0.050071 | N/A | N/A | 0.023517 | 0.023517 | 0.048538 | 0.048538 | 0.034978 | 0.034978 | 0.032355 | 0.032355 | 2219 | 546 | 26 | 99 | NO
2013-12-05 | N/A | N/A | 1.0128 | 1.0128 | 0.16971 | 0.16971 | 0.72315 | 0.72315 | 0.75278 | 0.75278 | N/A | N/A | 0.015167 | 0.015167 | 0.0012183 | 0.0012183 | 0.0050146 | 0.0050146 | 0.0087682 | 0.0087682 | N/A | N/A | 0.01763 | 0.01763 | 0.092657 | 0.092657 | 0.011353 | 0.011353 | 0.028234 | 0.028234 | 1794 | 574 | 20 | 128 | NO
2013-12-06 | N/A | N/A | 0.0018985 | 0.0018985 | 0.21087 | 0.21087 | 0.54804 | 0.54804 | 0.25189 | 0.25189 | N/A | N/A | 1.7417e-05 | 1.7417e-05 | 0.0036635 | 0.0036635 | 0.0031095 | 0.0031095 | 0.0018615 | 0.0018615 | N/A | N/A | 3.6266e-07 | 3.6266e-07 | 0.025983 | 0.025983 | 0.011524 | 0.011524 | 0.0090301 | 0.0090301 | 712 | 267 | 5 | 35 | NO
2013-12-07 | N/A | N/A | 0.49115 | 0.0095343 | 0.022634 | 0.022634 | 0.070031 | 0.070031 | 0.24489 | 0.035477 | N/A | N/A | 0.080371 | 0.00010102 | 0.00011313 | 0.00011313 | 0.00066217 | 0.00066217 | 0.035224 | 0.00032262 | N/A | N/A | 3.6266e-07 | 3.6266e-07 | 0.0014521 | 0.0014521 | 0.022393 | 0.022393 | 0.0090119 | 0.0090119 | 604 | 257 | 13 | 63 | NO | Transmission
2013-12-08 | N/A | N/A | 0.44949 | 0.44949 | 0.0045076 | 0.0045076 | 1.0241 | 1.0241 | 0.59679 | 0.59679 | N/A | N/A | 0.025548 | 0.025548 | 6.9616e-05 | 6.9616e-05 | 0.015966 | 0.015966 | 0.017365 | 0.017365 | N/A | N/A | 0.011572 | 0.011572 | 0.021258 | 0.021258 | 0.040558 | 0.040558 | 0.024596 | 0.024596 | 1001 | 220 | 16 | 80 | NO
2013-12-09 | N/A | N/A | 0.3334 | 0.3334 | 0.17096 | 0.17096 | 0.14916 | 0.14916 | 0.23306 | 0.23306 | N/A | N/A | 0.0030829 | 0.0030829 | 0.0018622 | 0.0018622 | 0.0015915 | 0.0015915 | 0.0022871 | 0.0022871 | N/A | N/A | 0.080748 | 0.080748 | 0.00016424 | 0.00016424 | 0.015342 | 0.015342 | 0.041139 | 0.041139 | 789 | 380 | 9 | 41 | NO
2013-12-10 | N/A | N/A | 0.29491 | 0.29491 | 0.59222 | 0.59222 | 0.86769 | 0.86769 | 0.5707 | 0.5707 | N/A | N/A | 0.00076985 | 0.00076985 | 0.006483 | 0.006483 | 0.016206 | 0.016206 | 0.0078018 | 0.0078018 | N/A | N/A | 0.0081099 | 0.0081099 | 0.0026008 | 0.0026008 | 0.010482 | 0.010482 | 0.0080789 | 0.0080789 | 1134 | 385 | 8 | 57 | NO
2013-12-11 | N/A | N/A | 0.0076079 | 0.0076079 | 0.0035156 | 0.0035156 | 0.02826 | 0.02826 | 0.014974 | 0.014974 | N/A | N/A | 0.00011147 | 0.00011147 | 9.5722e-05 | 9.5722e-05 | 0.00021685 | 0.00021685 | 0.00014995 | 0.00014995 | N/A | N/A | 3.6266e-07 | 3.6266e-07 | 0.044188 | 0.044188 | 0.0033377 | 0.0033377 | 0.0089968 | 0.0089968 | 443 | 315 | 6 | 35 | NO
2013-12-12 | N/A | N/A | 0.55593 | 0.55593 | 0.1012 | 0.1012 | 0.013321 | 0.013321 | 0.26454 | 0.26454 | N/A | N/A | 0.0031978 | 0.0031978 | 0.00051342 | 0.00051342 | 0.00022459 | 0.00022459 | 0.0015676 | 0.0015676 | N/A | N/A | 3.6266e-07 | 3.6266e-07 | 0.00016424 | 0.00016424 | 0.0033532 | 0.0033532 | 0.0013403 | 0.0013403 | 756 | 357 | 13 | 31 | NO
2013-12-13 | N/A | N/A | 0.019243 | 0.019243 | 0.20396 | 0.20396 | 0.040671 | 0.040671 | 0.059775 | 0.059775 | N/A | N/A | 0.00049814 | 0.00049814 | 0.0011226 | 0.0011226 | 0.00015489 | 0.00015489 | 0.00047256 | 0.00047256 | N/A | N/A | 3.6266e-07 | 3.6266e-07 | 0.016916 | 0.016916 | 0.015884 | 0.015884 | 0.0091573 | 0.0091573 | 486 | 325 | 4 | 70 | NO
2013-12-14 | N/A | N/A | 0.0012506 | 0.0012506 | 0.12799 | 0.12799 | 0.022014 | 0.022014 | 0.031432 | 0.031432 | N/A | N/A | 6.967e-06 | 6.967e-06 | 0.0010964 | 0.0010964 | 0.00024396 | 0.00024396 | 0.00028929 | 0.00028929 | N/A | N/A | 3.6266e-07 | 3.6266e-07 | 0.039889 | 0.039889 | 0.0067067 | 0.0067067 | 0.0095663 | 0.0095663 | 426 | 213 | 4 | 60 | NO
2013-12-15 | N/A | N/A | 0.020061 | 0.020061 | 0.0037767 | 0.0037767 | 0.018332 | 0.018332 | 0.01655 | 0.01655 | N/A | N/A | 0.00026126 | 0.00026126 | 4.351e-05 | 4.351e-05 | 0.00021298 | 0.00021298 | 0.00020447 | 0.00020447 | N/A | N/A | 0.015972 | 0.015972 | 0.0049764 | 0.0049764 | 0.0018392 | 0.0018392 | 0.0085303 | 0.0085303 | 127 | 98 | 6 | 9 | NO
2013-12-16 | N/A | N/A | 0.030954 | 0.030954 | 0.13097 | 0.13097 | 0.0444 | 0.0444 | 0.053622 | 0.053622 | N/A | N/A | 0.00036925 | 0.00036925 | 0.0012966 | 0.0012966 | 0.00055761 | 0.00055761 | 0.00060434 | 0.00060434 | N/A | N/A | 3.6266e-07 | 3.6266e-07 | 0.021249 | 0.021249 | 1.9171e-05 | 1.9171e-05 | 0.0037062 | 0.0037062 | 546 | 312 | 2 | 47 | NO
2013-12-17 | N/A | N/A | 0.010412 | 0.010412 | 0.085819 | 0.085819 | 0.23651 | 0.23651 | 0.11197 | 0.11197 | N/A | N/A | 0.00015327 | 0.00015327 | 0.001488 | 0.001488 | 0.0042247 | 0.0042247 | 0.0019781 | 0.0019781 | N/A | N/A | 3.6266e-07 | 3.6266e-07 | 0.0053332 | 0.0053332 | 0.008395 | 0.008395 | 0.0042121 | 0.0042121 | 768 | 417 | 11 | 98 | NO
2013-12-18 | N/A | N/A | 0.035939 | 0.035939 | 0 | 0 | 0.020357 | 0.020357 | 0.023589 | 0.023589 | N/A | N/A | 0.00045982 | 0.00045982 | 0 | 0 | 0.00023621 | 0.00023621 | 0.00029232 | 0.00029232 | N/A | N/A | 3.6266e-07 | 3.6266e-07 | 0.00016424 | 0.00016424 | 0.0075508 | 0.0075508 | 0.0029822 | 0.0029822 | 428 | 302 | 11 | 29 | NO
2013-12-19 | N/A | N/A | 0.12285 | 0.12285 | 0.7968 | 0.7968 | 0.47142 | 0.47142 | 0.37649 | 0.37649 | N/A | N/A | 0.020131 | 0.020131 | 0.0030805 | 0.0030805 | 0.0029159 | 0.0029159 | 0.01043 | 0.01043 | N/A | N/A | 3.6266e-07 | 3.6266e-07 | 0.085365 | 0.085365 | 0.045476 | 0.045476 | 0.032646 | 0.032646 | 993 | 592 | 15 | 78 | NO
2013-12-20 | N/A | N/A | 0.00013237 | 0.00013237 | 0.46801 | 0.46801 | 0.44934 | 0.44934 | 0.25727 | 0.25727 | N/A | N/A | 3.4835e-06 | 3.4835e-06 | 0.0021059 | 0.0021059 | 0.0075626 | 0.0075626 | 0.0033261 | 0.0033261 | N/A | N/A | 0.016996 | 0.016996 | 0.019309 | 0.019309 | 0.01614 | 0.01614 | 0.017064 | 0.017064 | 1014 | 396 | 11 | 38 | NO
2013-12-21 | N/A | N/A | 0.0010311 | 0.0010311 | 0.2658 | 0.2658 | 1.2022 | 1.2022 | 0.51694 | 0.51694 | N/A | N/A | 6.967e-06 | 6.967e-06 | 0.0060653 | 0.0060653 | 0.010293 | 0.010293 | 0.0050846 | 0.0050846 | N/A | N/A | 0.034334 | 0.034334 | 0.073174 | 0.073174 | 0.030409 | 0.030409 | 0.039559 | 0.039559 | 904 | 299 | 16 | 45 | NO
2013-12-22 | N/A | N/A | 0.068189 | 0.068189 | 2.0474 | 2.0474 | 1.6586 | 1.6586 | 1.0348 | 1.0348 | N/A | N/A | 0.00049117 | 0.00049117 | 0.093685 | 0.093685 | 0.053395 | 0.053395 | 0.037405 | 0.037405 | N/A | N/A | 0.0008364 | 0.0008364 | 0.027001 | 0.027001 | 0.031749 | 0.031749 | 0.017482 | 0.017482 | 782 | 218 | 12 | 30 | NO
2013-12-23 | N/A | N/A | 0.45736 | 0.45736 | 0.41567 | 0.41567 | 1.0078 | 1.0078 | 0.66541 | 0.66541 | N/A | N/A | 0.011562 | 0.011562 | 0.0072139 | 0.0072139 | 0.011354 | 0.011354 | 0.010724 | 0.010724 | N/A | N/A | 0.007239 | 0.007239 | 0.076863 | 0.076863 | 0.015841 | 0.015841 | 0.022722 | 0.022722 | 1530 | 429 | 23 | 33 | NO
2013-12-24 | N/A | N/A | 0.0046365 | 0.0046365 | 0.076264 | 0.076264 | 0.017727 | 0.017727 | 0.022224 | 0.022224 | N/A | N/A | 4.1802e-05 | 4.1802e-05 | 0.00068746 | 0.00068746 | 0.00016651 | 0.00016651 | 0.00020296 | 0.00020296 | N/A | N/A | 0.0092107 | 0.0092107 | 0.0016523 | 0.0016523 | 0.0048363 | 0.0048363 | 0.0061841 | 0.0061841 | 199 | 126 | 1 | 1 | NO
2013-12-25 | N/A | N/A | 0.13242 | 0.13242 | 0.27024 | 0.27024 | 0.0021956 | 0.0021956 | 0.10547 | 0.10547 | N/A | N/A | 0.0013586 | 0.0013586 | 0.0023147 | 0.0023147 | 2.3234e-05 | 2.3234e-05 | 0.0010027 | 0.0010027 | N/A | N/A | 3.6266e-07 | 3.6266e-07 | 0.032466 | 0.032466 | 0.0039805 | 0.0039805 | 0.007208 | 0.007208 | 262 | 115 | 3 | 6 | NO
2013-12-26 | N/A | N/A | 0.017177 | 0.017177 | 0.052595 | 0.052595 | 0.037732 | 0.037732 | 0.031382 | 0.031382 | N/A | N/A | 0.00033093 | 0.00033093 | 0.00040899 | 0.00040899 | 0.00043757 | 0.00043757 | 0.00038623 | 0.00038623 | N/A | N/A | 0.01701 | 0.01701 | 0.10427 | 0.10427 | 0.0035623 | 0.0035623 | 0.026939 | 0.026939 | 162 | 98 | 3 | 2 | NO
2013-12-27 | N/A | N/A | 0.00057826 | 0.00057826 | 0.10329 | 0.10329 | 0.10906 | 0.10906 | 0.060888 | 0.060888 | N/A | N/A | 3.4835e-06 | 3.4835e-06 | 0.0012705 | 0.0012705 | 0.0017425 | 0.0017425 | 0.00090423 | 0.00090423 | N/A | N/A | 3.6266e-07 | 3.6266e-07 | 0.02855 | 0.02855 | 0.020209 | 0.020209 | 0.012874 | 0.012874 | 249 | 190 | 3 | 10 | NO
2013-12-28 | N/A | N/A | 0.012311 | 0.012311 | 0.58581 | 0.58581 | 0.78457 | 0.78457 | 0.41419 | 0.41419 | N/A | N/A | 0.00023688 | 0.00023688 | 0.039794 | 0.039794 | 0.019307 | 0.019307 | 0.014581 | 0.014581 | N/A | N/A | 3.6266e-07 | 3.6266e-07 | 0.07206 | 0.07206 | 0.038045 | 0.038045 | 0.027424 | 0.027424 | 422 | 262 | 8 | 21 | NO
2013-12-29 | N/A | N/A | 0.0004424 | 0.0004424 | 0.074785 | 0.074785 | 1.4511 | 1.4511 | 0.58079 | 0.58079 | N/A | N/A | 3.4835e-06 | 3.4835e-06 | 0.00053952 | 0.00053952 | 0.0062654 | 0.0062654 | 0.0025461 | 0.0025461 | N/A | N/A | 0.011572 | 0.011572 | 0.051906 | 0.051906 | 0.0012815 | 0.0012815 | 0.014568 | 0.014568 | 911 | 151 | 7 | 6 | NO
2013-12-30 | N/A | N/A | 0.003487 | 0.003487 | 0.020876 | 0.020876 | 0.36152 | 0.36152 | 0.14656 | 0.14656 | N/A | N/A | 2.4384e-05 | 2.4384e-05 | 0.00014793 | 0.00014793 | 0.0016612 | 0.0016612 | 0.00068613 | 0.00068613 | N/A | N/A | 0.015401 | 0.015401 | 0.014636 | 0.014636 | 0.030607 | 0.030607 | 0.021215 | 0.021215 | 457 | 207 | 3 | 12 | NO
2013-12-31 | N/A | N/A | 0.00044937 | 0.00044937 | 0.65907 | 0.65907 | 3.9633 | 3.9633 | 1.6651 | 1.6651 | N/A | N/A | 3.4835e-06 | 3.4835e-06 | 0.023025 | 0.023025 | 0.019795 | 0.019795 | 0.011752 | 0.011752 | N/A | N/A | 0.0055182 | 0.0055182 | 0.015375 | 0.015375 | 0.030854 | 0.030854 | 0.017144 | 0.017144 | 1892 | 354 | 20 | 100 | NO
Contents
Contents

## 1d. STPIS MED Threshold (hidden)
SP AusNet
STPIS Data Reporting
2013
MED Threshold
Table 1 MED Threshold
MED Threshold (Timed) year ending 31 December | 8.7804
Alpha - average of Ln(SAIDI) | -1.7996
Beta - Standard deviation of Ln(SAIDI) | 1.4186
X Beta from the mean | 2.8
Table 2 MED Calculation
Date | Network SAIDI All Events | Network SAIDI (after removing excluded events) | Ln (SAIDI)
2008-01-01 | 0.69948 | 0.69948 | -0.35742
2008-01-02 | 1.4029 | 1.4029 | 0.33854
2008-01-03 | 0.41287 | 0.41287 | -0.88463
2008-01-04 | 0.80583 | 0.80583 | -0.21588
2008-01-05 | 0.23692 | 0.23692 | -1.44
2008-01-06 | 0.10054 | 0.10054 | -2.2972
2008-01-07 | 0.093213 | 0.093213 | -2.3729
2008-01-08 | 0.034979 | 0.034979 | -3.353
2008-01-09 | 0.1939 | 0.1939 | -1.6404
2008-01-10 | 3.7646 | 3.7646 | 1.3256
2008-01-11 | 3.8903 | 3.8903 | 1.3585
2008-01-12 | 0.09568 | 0.09568 | -2.3467
2008-01-13 | 0.46742 | 0.46742 | -0.76052
2008-01-14 | 0.14291 | 0.14291 | -1.9455
2008-01-15 | 0.045259 | 0.045259 | -3.0953
2008-01-16 | 0.14854 | 0.14854 | -1.9069
2008-01-17 | 0.064274 | 0.064274 | -2.7446
2008-01-18 | 1.9617 | 1.9617 | 0.67383
2008-01-19 | 2.59 | 2.59 | 0.95164
2008-01-20 | 0.38763 | 0.38763 | -0.9477
2008-01-21 | 0.94758 | 0.94758 | -0.053847
2008-01-22 | 0.45443 | 0.45443 | -0.78872
2008-01-23 | 0.12019 | 0.12019 | -2.1187
2008-01-24 | 0.31596 | 0.31596 | -1.1521
2008-01-25 | 0.34781 | 0.34781 | -1.0561
2008-01-26 | 0.258 | 0.258 | -1.3548
2008-01-27 | 0.13473 | 0.13473 | -2.0045
2008-01-28 | 0.15266 | 0.15266 | -1.8795
2008-01-29 | 0.053286 | 0.053286 | -2.9321
2008-01-30 | 0.36402 | 0.36402 | -1.0106
2008-01-31 | 0.65152 | 0.65152 | -0.42845
2008-02-01 | 0.44298 | 0.44298 | -0.81424
2008-02-02 | 0.29392 | 0.29392 | -1.2244
2008-02-03 | 0.75746 | 0.75746 | -0.27778
2008-02-04 | 1.3266 | 1.3266 | 0.28265
2008-02-05 | 0.10713 | 0.10713 | -2.2337
2008-02-06 | 0.051808 | 0.051808 | -2.9602
2008-02-07 | 1.6266 | 1.6266 | 0.48647
2008-02-08 | 0.11988 | 0.11988 | -2.1212
2008-02-09 | 0.077468 | 0.077468 | -2.5579
2008-02-10 | 0.074004 | 0.074004 | -2.6036
2008-02-11 | 0.25952 | 0.25952 | -1.3489
2008-02-12 | 0.82166 | 0.82166 | -0.19643
2008-02-13 | 0.027324 | 0.027324 | -3.6
2008-02-14 | 0.48598 | 0.48598 | -0.7216
2008-02-15 | 0.097674 | 0.097674 | -2.3261
2008-02-16 | 0.63783 | 0.63783 | -0.44968
2008-02-17 | 0.21048 | 0.21048 | -1.5584
2008-02-18 | 0.41071 | 0.41071 | -0.88987
2008-02-19 | 0.14517 | 0.14517 | -1.9299
2008-02-20 | 0.95066 | 0.95066 | -0.050599
2008-02-21 | 0.90378 | 0.90378 | -0.10116
2008-02-22 | 0.23758 | 0.23758 | -1.4373
2008-02-23 | 0.47216 | 0.47216 | -0.75045
2008-02-24 | 0.033969 | 0.033969 | -3.3823
2008-02-25 | 0.14313 | 0.14313 | -1.944
2008-02-26 | 0.2368 | 0.2368 | -1.4406
2008-02-27 | 0.091573 | 0.091573 | -2.3906
2008-02-28 | 0.19189 | 0.19189 | -1.6509
2008-02-29 | 0.24347 | 0.24347 | -1.4128
2008-03-01 | 0.061982 | 0.061982 | -2.7809
2008-03-02 | 0.31255 | 0.31255 | -1.163
2008-03-03 | 0.096955 | 0.096955 | -2.3335
2008-03-04 | 0.18834 | 0.18834 | -1.6695
2008-03-05 | 0.64296 | 0.64296 | -0.44168
2008-03-06 | 0.036454 | 0.036454 | -3.3117
2008-03-07 | 0.33316 | 0.33316 | -1.0991
2008-03-08 | 0.062398 | 0.062398 | -2.7742
2008-03-09 | 0.040878 | 0.040878 | -3.1972
2008-03-10 | 0.064209 | 0.064209 | -2.7456
2008-03-11 | 0.29699 | 0.29699 | -1.2141
2008-03-12 | 0.50001 | 0.50001 | -0.69312
2008-03-13 | 0.38958 | 0.38958 | -0.94269
2008-03-14 | 0.47086 | 0.47086 | -0.7532
2008-03-15 | 0.22368 | 0.22368 | -1.4976
2008-03-16 | 1.5337 | 1.5337 | 0.4277
2008-03-17 | 0.67635 | 0.67635 | -0.39104
2008-03-18 | 0.15808 | 0.15808 | -1.8447
2008-03-19 | 0.017469 | 0.017469 | -4.0473
2008-03-20 | 0.15852 | 0.15852 | -1.8419
2008-03-21 | 0.67942 | 0.67942 | -0.38652
2008-03-22 | 0.29364 | 0.29364 | -1.2254
2008-03-23 | 0.1458 | 0.1458 | -1.9255
2008-03-24 | 0.40144 | 0.40144 | -0.91269
2008-03-25 | 1.6145 | 1.6145 | 0.47902
2008-03-26 | 0.94771 | 0.94771 | -0.05371
2008-03-27 | 0.050399 | 0.050399 | -2.9878
2008-03-28 | 0.12322 | 0.12322 | -2.0937
2008-03-29 | 0.056816 | 0.056816 | -2.8679
2008-03-30 | 0.37573 | 0.37573 | -0.97888
2008-03-31 | 0.08818 | 0.08818 | -2.4284
2008-04-01 | 0.89841 | 0.89841 | -0.10713
2008-04-02 | 176.1539 | 176.1539 | 5.1714
2008-04-03 | 3.5613 | 3.5613 | 1.2701
2008-04-04 | 1.9208 | 1.9208 | 0.65272
2008-04-05 | 0.36402 | 0.36402 | -1.0105
2008-04-06 | 0.44215 | 0.44215 | -0.81609
2008-04-07 | 0.16233 | 0.16233 | -1.8181
2008-04-08 | 0.26666 | 0.26666 | -1.3218
2008-04-09 | 0.10514 | 0.10514 | -2.2525
2008-04-10 | 0.03349 | 0.03349 | -3.3965
2008-04-11 | 0.35419 | 0.35419 | -1.0379
2008-04-12 | 0.20578 | 0.20578 | -1.581
2008-04-13 | 0.40662 | 0.40662 | -0.89987
2008-04-14 | 0.031236 | 0.031236 | -3.4662
2008-04-15 | 0.021789 | 0.021789 | -3.8264
2008-04-16 | 0.10855 | 0.10855 | -2.2206
2008-04-17 | 0.011831 | 0.011831 | -4.437
2008-04-18 | 0.029564 | 0.029564 | -3.5212
2008-04-19 | 0.042404 | 0.042404 | -3.1605
2008-04-20 | 0.044118 | 0.044118 | -3.1209
2008-04-21 | 0.0072219 | 0.0072219 | -4.9306
2008-04-22 | 0.11845 | 0.11845 | -2.1333
2008-04-23 | 0.079446 | 0.079446 | -2.5327
2008-04-24 | 0.12026 | 0.12026 | -2.1181
2008-04-25 | 0.01709 | 0.01709 | -4.0693
2008-04-26 | 0.03093 | 0.03093 | -3.476
2008-04-27 | 0.20438 | 0.20438 | -1.5878
2008-04-28 | 0.1686 | 0.1686 | -1.7802
2008-04-29 | 0.1176 | 0.1176 | -2.1405
2008-04-30 | 0.40614 | 0.40614 | -0.90107
2008-05-01 | 0.11999 | 0.11999 | -2.1203
2008-05-02 | 0.39746 | 0.39746 | -0.92266
2008-05-03 | 0.28528 | 0.28528 | -1.2543
2008-05-04 | 0.13582 | 0.13582 | -1.9964
2008-05-05 | 0.28215 | 0.28215 | -1.2653
2008-05-06 | 0.78446 | 0.78446 | -0.24275
2008-05-07 | 0.0166 | 0.0166 | -4.0984
2008-05-08 | 0.076514 | 0.076514 | -2.5703
2008-05-09 | 0.1378 | 0.1378 | -1.9819
2008-05-10 | 0.021918 | 0.021918 | -3.8204
2008-05-11 | 0.078224 | 0.078224 | -2.5482
2008-05-12 | 0.16345 | 0.16345 | -1.8113
2008-05-13 | 0.046175 | 0.046175 | -3.0753
2008-05-14 | 0.099677 | 0.099677 | -2.3058
2008-05-15 | 0.016452 | 0.016452 | -4.1073
2008-05-16 | 0.077408 | 0.077408 | -2.5587
2008-05-17 | 0.54509 | 0.54509 | -0.6068
2008-05-18 | 0.2675 | 0.2675 | -1.3186
2008-05-19 | 0.020414 | 0.020414 | -3.8915
2008-05-20 | 0.013254 | 0.013254 | -4.3235
2008-05-21 | 0.069678 | 0.069678 | -2.6639
2008-05-22 | 0.12505 | 0.12505 | -2.079
2008-05-23 | 0.13893 | 0.13893 | -1.9738
2008-05-24 | 0.47567 | 0.47567 | -0.74304
2008-05-25 | 0.28551 | 0.28551 | -1.2535
2008-05-26 | 0.28258 | 0.28258 | -1.2638
2008-05-27 | 0.07479 | 0.07479 | -2.5931
2008-05-28 | 0.053939 | 0.053939 | -2.9199
2008-05-29 | 0.061691 | 0.061691 | -2.7856
2008-05-30 | 0.0214 | 0.0214 | -3.8444
2008-05-31 | 0.035563 | 0.035563 | -3.3365
2008-06-01 | 0.02558 | 0.02558 | -3.6659
2008-06-02 | 0.15449 | 0.15449 | -1.8676
2008-06-03 | 0.084381 | 0.084381 | -2.4724
2008-06-04 | 0.041375 | 0.041375 | -3.1851
2008-06-05 | 0.081997 | 0.081997 | -2.5011
2008-06-06 | 0.0092563 | 0.0092563 | -4.6824
2008-06-07 | 0.024623 | 0.024623 | -3.7041
2008-06-08 | 0.23591 | 0.23591 | -1.4443
2008-06-09 | 0.028013 | 0.028013 | -3.5751
2008-06-10 | 0.11868 | 0.11868 | -2.1314
2008-06-11 | 0.070898 | 0.070898 | -2.6465
2008-06-12 | 0.1993 | 0.1993 | -1.6129
2008-06-13 | 3.0361 | 3.0361 | 1.1106
2008-06-14 | 0.46207 | 0.46207 | -0.77204
2008-06-15 | 0.39311 | 0.39311 | -0.93366
2008-06-16 | 0.11397 | 0.11397 | -2.1718
2008-06-17 | 0.068001 | 0.068001 | -2.6882
2008-06-18 | 0.021187 | 0.021187 | -3.8544
2008-06-19 | 0.082172 | 0.082172 | -2.4989
2008-06-20 | 0.07556 | 0.07556 | -2.5828
2008-06-21 | 0.043253 | 0.043253 | -3.1407
2008-06-22 | 0.10348 | 0.10348 | -2.2684
2008-06-23 | 0.28756 | 0.28756 | -1.2463
2008-06-24 | 0.0095555 | 0.0095555 | -4.6506
2008-06-25 | 1.8627 | 1.8627 | 0.62202
2008-06-26 | 1.1231 | 1.1231 | 0.11607
2008-06-27 | 0.097738 | 0.097738 | -2.3255
2008-06-28 | 0.030031 | 0.030031 | -3.5055
2008-06-29 | 0.52658 | 0.52658 | -0.64136
2008-06-30 | 0.85749 | 0.85749 | -0.15374
2008-07-01 | 4.95 | 4.95 | 1.5994
2008-07-02 | 1.2145 | 1.2145 | 0.19432
2008-07-03 | 0.017884 | 0.017884 | -4.0238
2008-07-04 | 0.28413 | 0.28413 | -1.2583
2008-07-05 | 0.18121 | 0.18121 | -1.7081
2008-07-06 | 0.045251 | 0.045251 | -3.0955
2008-07-07 | 0.13691 | 0.13691 | -1.9884
2008-07-08 | 0.35861 | 0.35861 | -1.0255
2008-07-09 | 0.048715 | 0.048715 | -3.0218
2008-07-10 | 0.49498 | 0.49498 | -0.70324
2008-07-11 | 0.11935 | 0.11837 | -2.1339
2008-07-12 | 0.039427 | 0.039427 | -3.2333
2008-07-13 | 0.153 | 0.153 | -1.8773
2008-07-14 | 0.061703 | 0.061703 | -2.7854
2008-07-15 | 0.03408 | 0.03408 | -3.379
2008-07-16 | 0.052671 | 0.052671 | -2.9437
2008-07-17 | 0.14439 | 0.14439 | -1.9352
2008-07-18 | 0.68484 | 0.68484 | -0.37857
2008-07-19 | 0.058628 | 0.058628 | -2.8365
2008-07-20 | 0.13461 | 0.13461 | -2.0053
2008-07-21 | 0.67474 | 0.67474 | -0.39344
2008-07-22 | 0.1898 | 0.1898 | -1.6618
2008-07-23 | 0.14004 | 0.14004 | -1.9658
2008-07-24 | 0.21351 | 0.21351 | -1.5441
2008-07-25 | 0.053048 | 0.053048 | -2.9366
2008-07-26 | 0.25952 | 0.25952 | -1.3489
2008-07-27 | 0.071828 | 0.071828 | -2.6335
2008-07-28 | 0.091516 | 0.091516 | -2.3912
2008-07-29 | 0.16917 | 0.16917 | -1.7769
2008-07-30 | 0.26556 | 0.26556 | -1.3259
2008-07-31 | 0.88506 | 0.22861 | -1.4758 | < Excluded transmission event.
2008-08-01 | 1.0897 | 1.0897 | 0.085919
2008-08-02 | 0.15982 | 0.15982 | -1.8337
2008-08-03 | 0.087153 | 0.087153 | -2.4401
2008-08-04 | 0.012489 | 0.012489 | -4.3829
2008-08-05 | 0.94758 | 0.94758 | -0.053846
2008-08-06 | 0.14618 | 0.14618 | -1.9229
2008-08-07 | 0.10907 | 0.10907 | -2.2158
2008-08-08 | 0.033628 | 0.033628 | -3.3924
2008-08-09 | 0.013722 | 0.013722 | -4.2887
2008-08-10 | 0.53084 | 0.53084 | -0.6333
2008-08-11 | 0.38464 | 0.38464 | -0.95546
2008-08-12 | 0.25581 | 0.25581 | -1.3633
2008-08-13 | 0.19782 | 0.19782 | -1.6204
2008-08-14 | 1.9045 | 1.9045 | 0.64423
2008-08-15 | 0.021619 | 0.021619 | -3.8342
2008-08-16 | 0.26077 | 0.26077 | -1.3441
2008-08-17 | 0.023381 | 0.023381 | -3.7558
2008-08-18 | 0.554 | 0.554 | -0.59059
2008-08-19 | 0.22661 | 0.22661 | -1.4845
2008-08-20 | 0.091867 | 0.091867 | -2.3874
2008-08-21 | 0.54479 | 0.54479 | -0.60736
2008-08-22 | 0.22952 | 0.22952 | -1.4718
2008-08-23 | 0.014522 | 0.014522 | -4.2321
2008-08-24 | 0.61593 | 0.61593 | -0.48463
2008-08-25 | 0.076426 | 0.076426 | -2.5714
2008-08-26 | 0.057184 | 0.057184 | -2.8615
2008-08-27 | 0.29181 | 0.29181 | -1.2316
2008-08-28 | 0.23486 | 0.23486 | -1.4488
2008-08-29 | 0.10278 | 0.10278 | -2.2751
2008-08-30 | 0.16892 | 0.16892 | -1.7784
2008-08-31 | 0.56305 | 0.56305 | -0.57438
2008-09-01 | 0.25066 | 0.25066 | -1.3837
2008-09-02 | 0.14938 | 0.14938 | -1.9012
2008-09-03 | 0.61102 | 0.61102 | -0.49262
2008-09-04 | 0.45959 | 0.45959 | -0.77743
2008-09-05 | 0.031338 | 0.031338 | -3.4629
2008-09-06 | 0.020271 | 0.020271 | -3.8986
2008-09-07 | 0.0071621 | 0.0071621 | -4.939
2008-09-08 | 0.050257 | 0.050257 | -2.9906
2008-09-09 | 0.024526 | 0.024526 | -3.708
2008-09-10 | 0.15276 | 0.15276 | -1.8789
2008-09-11 | 0.031791 | 0.031791 | -3.4486
2008-09-12 | 0.56676 | 0.56676 | -0.56783
2008-09-13 | 0.31735 | 0.31735 | -1.1478
2008-09-14 | 1.0094 | 1.0094 | 0.0093603
2008-09-15 | 1.5967 | 1.5967 | 0.46796
2008-09-16 | 0.06138 | 0.06138 | -2.7907
2008-09-17 | 0.094275 | 0.094275 | -2.3615
2008-09-18 | 0.19002 | 0.19002 | -1.6606
2008-09-19 | 0.030184 | 0.030184 | -3.5004
2008-09-20 | 0.027764 | 0.027764 | -3.584
2008-09-21 | 0.012822 | 0.012822 | -4.3566
2008-09-22 | 1.2796 | 1.2796 | 0.24651
2008-09-23 | 0.31227 | 0.31227 | -1.1639
2008-09-24 | 0.073276 | 0.073276 | -2.6135
2008-09-25 | 0.40041 | 0.40041 | -0.91527
2008-09-26 | 0.22736 | 0.22736 | -1.4812
2008-09-27 | 0.1687 | 0.1687 | -1.7796
2008-09-28 | 0.028691 | 0.028691 | -3.5512
2008-09-29 | 0.10785 | 0.10785 | -2.227
2008-09-30 | 0.036518 | 0.036518 | -3.3099
2008-10-01 | 0.18974 | 0.18974 | -1.6621
2008-10-02 | 0.07611 | 0.07611 | -2.5756
2008-10-03 | 0.42772 | 0.42772 | -0.8493
2008-10-04 | 0.05654 | 0.05654 | -2.8728
2008-10-05 | 0.063942 | 0.063942 | -2.7498
2008-10-06 | 0.27819 | 0.27819 | -1.2794
2008-10-07 | 0.46522 | 0.46522 | -0.76524
2008-10-08 | 0.041452 | 0.041452 | -3.1832
2008-10-09 | 0.1006 | 0.1006 | -2.2966
2008-10-10 | 0.24534 | 0.24534 | -1.4051
2008-10-11 | 0.15375 | 0.15375 | -1.8724
2008-10-12 | 0.041811 | 0.041811 | -3.1746
2008-10-13 | 0.4689 | 0.4689 | -0.75736
2008-10-14 | 0.11525 | 0.11525 | -2.1607
2008-10-15 | 0.026426 | 0.026426 | -3.6334
2008-10-16 | 0.063455 | 0.063455 | -2.7574
2008-10-17 | 0.10825 | 0.10825 | -2.2234
2008-10-18 | 0.13033 | 0.13033 | -2.0376
2008-10-19 | 0.032817 | 0.032817 | -3.4168
2008-10-20 | 0.86405 | 0.71232 | -0.33923
2008-10-21 | 0.93227 | 0.93227 | -0.070131
2008-10-22 | 0.65734 | 0.65734 | -0.41955
2008-10-23 | 0.0095372 | 0.0095372 | -4.6526
2008-10-24 | 0.051408 | 0.051408 | -2.968
2008-10-25 | 0.097344 | 0.097344 | -2.3295
2008-10-26 | 0.0086746 | 0.0086746 | -4.7474
2008-10-27 | 0.39485 | 0.39485 | -0.92924
2008-10-28 | 0.032074 | 0.032074 | -3.4397
2008-10-29 | 0.13759 | 0.13759 | -1.9835
2008-10-30 | 0.39001 | 0.39001 | -0.94158
2008-10-31 | 0.10981 | 0.10981 | -2.209
2008-11-01 | 0.53239 | 0.53239 | -0.63037
2008-11-02 | 0.15146 | 0.15146 | -1.8875
2008-11-03 | 0.22233 | 0.22233 | -1.5036
2008-11-04 | 0.11705 | 0.11705 | -2.1451
2008-11-05 | 0.017298 | 0.017298 | -4.0572
2008-11-06 | 0.044347 | 0.044347 | -3.1157
2008-11-07 | 0.55716 | 0.55716 | -0.5849
2008-11-08 | 0.084092 | 0.084092 | -2.4758
2008-11-09 | 0.041176 | 0.041176 | -3.1899
2008-11-10 | 0.05493 | 0.05493 | -2.9017
2008-11-11 | 0.04258 | 0.04258 | -3.1564
2008-11-12 | 0.20706 | 0.20706 | -1.5748
2008-11-13 | 0.26378 | 0.26378 | -1.3326
2008-11-14 | 0.96486 | 0.96486 | -0.035775
2008-11-15 | 0.26296 | 0.26296 | -1.3358
2008-11-16 | 0.023592 | 0.023592 | -3.7468
2008-11-17 | 0.10533 | 0.10533 | -2.2507
2008-11-18 | 0.04865 | 0.04865 | -3.0231
2008-11-19 | 0.069681 | 0.069681 | -2.6638
2008-11-20 | 0.12972 | 0.12972 | -2.0424
2008-11-21 | 0.38875 | 0.38875 | -0.94482
2008-11-22 | 1.5101 | 1.5101 | 0.41218
2008-11-23 | 1.7205 | 1.7205 | 0.54264
2008-11-24 | 0.022826 | 0.022826 | -3.7799
2008-11-25 | 0.027975 | 0.027975 | -3.5764
2008-11-26 | 0.014514 | 0.014514 | -4.2327
2008-11-27 | 0.40808 | 0.40611 | -0.90113
2008-11-28 | 1.3216 | 1.3216 | 0.27887
2008-11-29 | 0.20163 | 0.20163 | -1.6013
2008-11-30 | 0.015102 | 0.015102 | -4.1929
2008-12-01 | 0.044724 | 0.044724 | -3.1072
2008-12-02 | 0.40952 | 0.40952 | -0.89278
2008-12-03 | 0.035391 | 0.035391 | -3.3413
2008-12-04 | 0.21451 | 0.21451 | -1.5394
2008-12-05 | 0.043626 | 0.043626 | -3.1321
2008-12-06 | 0.11007 | 0.11007 | -2.2067
2008-12-07 | 0.011384 | 0.011384 | -4.4756
2008-12-08 | 0.093305 | 0.093305 | -2.3719
2008-12-09 | 0.37352 | 0.37352 | -0.98478
2008-12-10 | 0.076057 | 0.076057 | -2.5763
2008-12-11 | 0.065107 | 0.065107 | -2.7317
2008-12-12 | 0.14758 | 0.14758 | -1.9134
2008-12-13 | 4.6038 | 4.6038 | 1.5269
2008-12-14 | 0.23755 | 0.16332 | -1.8121 | < Excluded transmission event.
2008-12-15 | 0.0615 | 0.0615 | -2.7887
2008-12-16 | 0.93796 | 0.93796 | -0.064043
2008-12-17 | 0.37326 | 0.37326 | -0.98547
2008-12-18 | 1.1287 | 1.1287 | 0.12103
2008-12-19 | 0.46883 | 0.46883 | -0.75751
2008-12-20 | 0.20085 | 0.20085 | -1.6052
2008-12-21 | 0.19044 | 0.19044 | -1.6584
2008-12-22 | 0.75253 | 0.75253 | -0.28431
2008-12-23 | 1.1908 | 1.1908 | 0.17465
2008-12-24 | 0.4711 | 0.4711 | -0.75269
2008-12-25 | 0.054271 | 0.054271 | -2.9138
2008-12-26 | 0.02129 | 0.02129 | -3.8495
2008-12-27 | 0.30896 | 0.30896 | -1.1745
2008-12-28 | 0.032822 | 0.032822 | -3.4167
2008-12-29 | 0.43743 | 0.43743 | -0.82684
2008-12-30 | 0.27415 | 0.27415 | -1.2941
2008-12-31 | 0.072322 | 0.072322 | -2.6266
2009-01-01 | 0.037115 | 0.037115 | -3.2937
2009-01-02 | 0.098858 | 0.098858 | -2.3141
2009-01-03 | 0.14361 | 0.14361 | -1.9407
2009-01-04 | 0.44699 | 0.44699 | -0.80521
2009-01-05 | 0.046566 | 0.046566 | -3.0669
2009-01-06 | 0.16345 | 0.16345 | -1.8113
2009-01-07 | 0.04323 | 0.04323 | -3.1412
2009-01-08 | 0.071436 | 0.071436 | -2.639
2009-01-09 | 0.023825 | 0.023825 | -3.737
2009-01-10 | 0.029154 | 0.029154 | -3.5352
2009-01-11 | 0.015128 | 0.015128 | -4.1912
2009-01-12 | 0.016338 | 0.016338 | -4.1142
2009-01-13 | 0.63225 | 0.63225 | -0.45847
2009-01-14 | 0.56772 | 0.56648 | -0.56831
2009-01-15 | 0.22751 | 0.22751 | -1.4806
2009-01-16 | 0.3747 | 0.3747 | -0.98164
2009-01-17 | 0.31302 | 0.31302 | -1.1615
2009-01-18 | 0.26314 | 0.26314 | -1.3351
2009-01-19 | 0.22538 | 0.22507 | -1.4914
2009-01-20 | 1.3453 | 1.3453 | 0.29663
2009-01-21 | 0.19308 | 0.19308 | -1.6446
2009-01-22 | 12.4313 | 12.4313 | 2.5202
2009-01-23 | 1.0024 | 1.0024 | 0.0024319
2009-01-24 | 0.72687 | 0.72687 | -0.319
2009-01-25 | 0.046455 | 0.046455 | -3.0693
2009-01-26 | 0.068942 | 0.068942 | -2.6745
2009-01-27 | 0.37478 | 0.37478 | -0.98142
2009-01-28 | 7.5201 | 7.5201 | 2.0176
2009-01-29 | 8.6356 | 6.9641 | 1.9408 | < Excluded transmission event.
2009-01-30 | 11.1816 | 9.301 | 2.2301 | < Excluded transmission event.
2009-01-31 | 1.8679 | 1.8679 | 0.62482
2009-02-01 | 5.4211 | 5.4211 | 1.6903
2009-02-02 | 2.2101 | 2.2101 | 0.79302
2009-02-03 | 0.4785 | 0.4785 | -0.7371
2009-02-04 | 2.3333 | 0.31524 | -1.1544 | < Excluded transmission event.
2009-02-05 | 0.61922 | 0.61922 | -0.47929
2009-02-06 | 0.66873 | 0.66873 | -0.40237
2009-02-07 | 94.4837 | 94.4837 | 4.5484
2009-02-08 | 6.3261 | 6.3261 | 1.8447
2009-02-09 | 2.1289 | 2.1289 | 0.75559
2009-02-10 | 0.23686 | 0.23686 | -1.4403
2009-02-11 | 1.9453 | 1.9453 | 0.6654
2009-02-12 | 0.79591 | 0.79591 | -0.22827
2009-02-13 | 0.22633 | 0.22633 | -1.4858
2009-02-14 | 0.27355 | 0.27355 | -1.2963
2009-02-15 | 1.1468 | 1.1468 | 0.137
2009-02-16 | 0.54843 | 0.54843 | -0.6007
2009-02-17 | 0.24895 | 0.24895 | -1.3905
2009-02-18 | 0.1178 | 0.1178 | -2.1387
2009-02-19 | 0.37014 | 0.37014 | -0.99388
2009-02-20 | 0.13264 | 0.13264 | -2.0202
2009-02-21 | 1.8279 | 1.8279 | 0.60318
2009-02-22 | 0.19293 | 0.19293 | -1.6454
2009-02-23 | 1.0555 | 1.0555 | 0.053998
2009-02-24 | 0.45333 | 0.45333 | -0.79114
2009-02-25 | 1.4037 | 1.4037 | 0.33914
2009-02-26 | 0.77328 | 0.77328 | -0.25712
2009-02-27 | 0.58867 | 0.58867 | -0.52989
2009-02-28 | 0.02132 | 0.02132 | -3.8481
2009-03-01 | 0.67398 | 0.67398 | -0.39456
2009-03-02 | 0.12372 | 0.12372 | -2.0897
2009-03-03 | 4.2877 | 4.2877 | 1.4558
2009-03-04 | 1.7311 | 1.7311 | 0.54874
2009-03-05 | 0.22934 | 0.22934 | -1.4725
2009-03-06 | 0.13185 | 0.13185 | -2.0261
2009-03-07 | 0.18171 | 0.18171 | -1.7053
2009-03-08 | 0.026572 | 0.026572 | -3.6279
2009-03-09 | 0.0032676 | 0.0032676 | -5.7237
2009-03-10 | 0.31267 | 0.31267 | -1.1626
2009-03-11 | 0.49721 | 0.49721 | -0.69874
2009-03-12 | 0.17534 | 0.17534 | -1.741
2009-03-13 | 0.26541 | 0.26541 | -1.3265
2009-03-14 | 1.7213 | 1.7213 | 0.54307
2009-03-15 | 0.466 | 0.466 | -0.76358
2009-03-16 | 0.068206 | 0.068206 | -2.6852
2009-03-17 | 0.2053 | 0.2053 | -1.5833
2009-03-18 | 0.142 | 0.142 | -1.9519
2009-03-19 | 0.14859 | 0.14859 | -1.9066
2009-03-20 | 0.23707 | 0.23707 | -1.4394
2009-03-21 | 0.12308 | 0.12308 | -2.0949
2009-03-22 | 0.38153 | 0.38153 | -0.96355
2009-03-23 | 0.060834 | 0.060834 | -2.7996
2009-03-24 | 0.01965 | 0.01965 | -3.9297
2009-03-25 | 0.5674 | 0.5674 | -0.56669
2009-03-26 | 0.11523 | 0.11523 | -2.1608
2009-03-27 | 0.11063 | 0.11063 | -2.2015
2009-03-28 | 0.12026 | 0.12026 | -2.1181
2009-03-29 | 0.64125 | 0.64125 | -0.44434
2009-03-30 | 0.11638 | 0.11638 | -2.1509
2009-03-31 | 0.04705 | 0.04705 | -3.0565
2009-04-01 | 0.059592 | 0.059592 | -2.8202
2009-04-02 | 0.40806 | 0.40806 | -0.89634
2009-04-03 | 3.8627 | 3.4668 | 1.2432 | < Excluded transmission event.
2009-04-04 | 0.21947 | 0.21947 | -1.5166
2009-04-05 | 0.042093 | 0.041921 | -3.172
2009-04-06 | 1.1234 | 1.1234 | 0.11637
2009-04-07 | 0.14806 | 0.14806 | -1.9101
2009-04-08 | 0.16021 | 0.16021 | -1.8313
2009-04-09 | 0.57095 | 0.57095 | -0.56046
2009-04-10 | 0.25711 | 0.25711 | -1.3583
2009-04-11 | 1.8008 | 1.8008 | 0.58821
2009-04-12 | 0.047563 | 0.047563 | -3.0457
2009-04-13 | 1.1315 | 1.1315 | 0.12353
2009-04-14 | 0.29008 | 0.29008 | -1.2376
2009-04-15 | 9.4584 | 9.4584 | 2.2469
2009-04-16 | 0.138 | 0.138 | -1.9805
2009-04-17 | 0.20664 | 0.20664 | -1.5768
2009-04-18 | 0.024146 | 0.024146 | -3.7236
2009-04-19 | 0.22418 | 0.22418 | -1.4953
2009-04-20 | 0.68565 | 0.68565 | -0.37738
2009-04-21 | 0.54369 | 0.54369 | -0.60937
2009-04-22 | 0.20507 | 0.20507 | -1.5844
2009-04-23 | 0.4943 | 0.21382 | -1.5426 | < Excluded transmission event.
2009-04-24 | 0.52476 | 0.52476 | -0.64482
2009-04-25 | 1.1598 | 1.1598 | 0.14827
2009-04-26 | 4.1468 | 4.1468 | 1.4223
2009-04-27 | 0.44596 | 0.44596 | -0.80753
2009-04-28 | 0.32122 | 0.32122 | -1.1356
2009-04-29 | 0.5723 | 0.5723 | -0.55809
2009-04-30 | 0.05548 | 0.05548 | -2.8917
2009-05-01 | 0.04979 | 0.04979 | -3
2009-05-02 | 0.043943 | 0.043943 | -3.1249
2009-05-03 | 0.38897 | 0.38897 | -0.94424
2009-05-04 | 0.04621 | 0.04621 | -3.0746
2009-05-05 | 0.43088 | 0.43088 | -0.84192
2009-05-06 | 0.055074 | 0.055074 | -2.8991
2009-05-07 | 0.080854 | 0.080854 | -2.5151
2009-05-08 | 0.022572 | 0.022572 | -3.7911
2009-05-09 | 0.26737 | 0.26737 | -1.3191
2009-05-10 | 0.057054 | 0.057054 | -2.8638
2009-05-11 | 0.016159 | 0.016159 | -4.1253
2009-05-12 | 0.026177 | 0.026177 | -3.6429
2009-05-13 | 0.27137 | 0.27137 | -1.3043
2009-05-14 | 0.023624 | 0.023624 | -3.7455
2009-05-15 | 0.21914 | 0.21914 | -1.518
2009-05-16 | 0.31815 | 0.31815 | -1.1452
2009-05-17 | 0.12803 | 0.12803 | -2.0555
2009-05-18 | 0.13641 | 0.13641 | -1.9921
2009-05-19 | 0.11502 | 0.11502 | -2.1627
2009-05-20 | 0.24656 | 0.24656 | -1.4001
2009-05-21 | 0.019661 | 0.019661 | -3.9291
2009-05-22 | 0.058671 | 0.058671 | -2.8358
2009-05-23 | 0.10677 | 0.10677 | -2.2371
2009-05-24 | 0.13696 | 0.13696 | -1.988
2009-05-25 | 0.62798 | 0.62798 | -0.46525
2009-05-26 | 0.068475 | 0.068475 | -2.6813
2009-05-27 | 0.031011 | 0.031011 | -3.4734
2009-05-28 | 0.026989 | 0.026989 | -3.6123
2009-05-29 | 0.37005 | 0.37005 | -0.99413
2009-05-30 | 0.034698 | 0.034698 | -3.3611
2009-05-31 | 0.032906 | 0.032906 | -3.4141
2009-06-01 | 0.028761 | 0.028761 | -3.5487
2009-06-02 | 0.2916 | 0.2916 | -1.2324
2009-06-03 | 0.039266 | 0.039266 | -3.2374
2009-06-04 | 0.04015 | 0.04015 | -3.2151
2009-06-05 | 0.013292 | 0.013292 | -4.3206
2009-06-06 | 0.06558 | 0.06558 | -2.7245
2009-06-07 | 0.027973 | 0.027973 | -3.5765
2009-06-08 | 0.048804 | 0.048804 | -3.0199
2009-06-09 | 0.46668 | 0.46668 | -0.76211
2009-06-10 | 0.41984 | 0.41984 | -0.86788
2009-06-11 | 0.024565 | 0.023528 | -3.7496
2009-06-12 | 0.037634 | 0.037634 | -3.2798
2009-06-13 | 0.0087393 | 0.0087393 | -4.7399
2009-06-14 | 0.032053 | 0.032053 | -3.4404
2009-06-15 | 0.032179 | 0.032179 | -3.4364
2009-06-16 | 0.040393 | 0.040393 | -3.2091
2009-06-17 | 0.16426 | 0.16426 | -1.8063
2009-06-18 | 0.19411 | 0.19411 | -1.6393
2009-06-19 | 0.041042 | 0.041042 | -3.1932
2009-06-20 | 0.02597 | 0.02597 | -3.6508
2009-06-21 | 0.13653 | 0.13653 | -1.9912
2009-06-22 | 0.07024 | 0.07024 | -2.6558
2009-06-23 | 0.11791 | 0.11791 | -2.1379
2009-06-24 | 0.10035 | 0.10035 | -2.2991
2009-06-25 | 0.037761 | 0.037761 | -3.2765
2009-06-26 | 0.32748 | 0.32748 | -1.1163
2009-06-27 | 0.032291 | 0.032291 | -3.433
2009-06-28 | 0.028577 | 0.028577 | -3.5552
2009-06-29 | 0.023808 | 0.023808 | -3.7377
2009-06-30 | 4.8296 | 4.8296 | 1.5748
2009-07-01 | 0.33126 | 0.33126 | -1.1049
2009-07-02 | 1.92 | 0.10852 | -2.2208 | < Excluded transmission event.
2009-07-03 | 0.50725 | 0.50725 | -0.67876
2009-07-04 | 0.075957 | 0.075957 | -2.5776
2009-07-05 | 0.17503 | 0.17503 | -1.7428
2009-07-06 | 0.010922 | 0.010922 | -4.517
2009-07-07 | 0.015798 | 0.015798 | -4.1479
2009-07-08 | 0.29213 | 0.29213 | -1.2305
2009-07-09 | 0.17012 | 0.17012 | -1.7713
2009-07-10 | 0.01172 | 0.01172 | -4.4465
2009-07-11 | 2.7777 | 2.7777 | 1.0216
2009-07-12 | 0.027892 | 0.027892 | -3.5794
2009-07-13 | 0.13921 | 0.13921 | -1.9718
2009-07-14 | 0.020585 | 0.020585 | -3.8832
2009-07-15 | 0.038884 | 0.038884 | -3.2472
2009-07-16 | 0.049905 | 0.049905 | -2.9976
2009-07-17 | 0.14803 | 0.14803 | -1.9103
2009-07-18 | 0.075771 | 0.075771 | -2.58
2009-07-19 | 0.12461 | 0.12461 | -2.0826
2009-07-20 | 0.56529 | 0.56529 | -0.57041
2009-07-21 | 0.30605 | 0.30605 | -1.184
2009-07-22 | 0.27119 | 0.27119 | -1.3049
2009-07-23 | 0.38621 | 0.38621 | -0.95136
2009-07-24 | 0.053574 | 0.053574 | -2.9267
2009-07-25 | 1.0016 | 1.0016 | 0.001551
2009-07-26 | 0.76069 | 0.76069 | -0.27352
2009-07-27 | 0.11223 | 0.11223 | -2.1872
2009-07-28 | 0.068723 | 0.068723 | -2.6777
2009-07-29 | 0.19623 | 0.19623 | -1.6284
2009-07-30 | 0.18975 | 0.18975 | -1.662
2009-07-31 | 0.033259 | 0.033259 | -3.4034
2009-08-01 | 0.010881 | 0.010881 | -4.5207
2009-08-02 | 0.048613 | 0.048613 | -3.0239
2009-08-03 | 1.2442 | 1.2442 | 0.2185
2009-08-04 | 0.19983 | 0.19983 | -1.6103
2009-08-05 | 0.37528 | 0.37528 | -0.98008
2009-08-06 | 0.33191 | 0.33191 | -1.1029
2009-08-07 | 0.58831 | 0.58831 | -0.5305
2009-08-08 | 0.015474 | 0.015474 | -4.1686
2009-08-09 | 0.18663 | 0.18663 | -1.6786
2009-08-10 | 0.30432 | 0.30432 | -1.1897
2009-08-11 | 0.097305 | 0.097305 | -2.3299
2009-08-12 | 0.13628 | 0.13628 | -1.993
2009-08-13 | 0.37973 | 0.37973 | -0.9683
2009-08-14 | 0.6014 | 0.6014 | -0.5085
2009-08-15 | 0.82318 | 0.82318 | -0.19458
2009-08-16 | 10.5114 | 10.5114 | 2.3525
2009-08-17 | 0.38263 | 0.38263 | -0.96069
2009-08-18 | 0.067816 | 0.067816 | -2.691
2009-08-19 | 0.43963 | 0.43963 | -0.82183
2009-08-20 | 0.20019 | 0.20019 | -1.6085
2009-08-21 | 10.1159 | 10.1159 | 2.3141
2009-08-22 | 0.19696 | 0.19696 | -1.6248
2009-08-23 | 0.2796 | 0.2796 | -1.2744
2009-08-24 | 0.1616 | 0.1616 | -1.8227
2009-08-25 | 29.2953 | 29.2953 | 3.3774
2009-08-26 | 2.8177 | 2.8177 | 1.0359
2009-08-27 | 0.37841 | 0.37841 | -0.97177
2009-08-28 | 0.12217 | 0.12217 | -2.1023
2009-08-29 | 1.0606 | 1.0606 | 0.05879
2009-08-30 | 0.046191 | 0.046191 | -3.075
2009-08-31 | 0.023643 | 0.023643 | -3.7447
2009-09-01 | 0.098478 | 0.098478 | -2.3179
2009-09-02 | 0.0051356 | 0.0051356 | -5.2716
2009-09-03 | 0.58066 | 0.58066 | -0.54359
2009-09-04 | 0.27276 | 0.27276 | -1.2991
2009-09-05 | 0.015708 | 0.015708 | -4.1536
2009-09-06 | 0.01796 | 0.01796 | -4.0196
2009-09-07 | 0.021581 | 0.021581 | -3.8359
2009-09-08 | 0.051809 | 0.051809 | -2.9602
2009-09-09 | 0.47395 | 0.47395 | -0.74665
2009-09-10 | 0.40319 | 0.40319 | -0.90835
2009-09-11 | 10.5185 | 10.5185 | 2.3531
2009-09-12 | 1.9023 | 1.9023 | 0.64309
2009-09-13 | 0.52742 | 0.52742 | -0.63976
2009-09-14 | 0.024081 | 0.024081 | -3.7263
2009-09-15 | 0.51628 | 0.51628 | -0.66111
2009-09-16 | 0.13081 | 0.13081 | -2.034
2009-09-17 | 0.20683 | 0.20683 | -1.5759
2009-09-18 | 0.11679 | 0.11679 | -2.1474
2009-09-19 | 0.030159 | 0.030159 | -3.5013
2009-09-20 | 0.43674 | 0.43674 | -0.82843
2009-09-21 | 0.37921 | 0.37921 | -0.96967
2009-09-22 | 0.21157 | 0.21157 | -1.5532
2009-09-23 | 0.56733 | 0.56733 | -0.56681
2009-09-24 | 0.078699 | 0.078699 | -2.5421
2009-09-25 | 0.20722 | 0.20722 | -1.574
2009-09-26 | 0.60959 | 0.60959 | -0.49497
2009-09-27 | 6.9078 | 6.9078 | 1.9326
2009-09-28 | 0.2641 | 0.2641 | -1.3314
2009-09-29 | 0.20585 | 0.20585 | -1.5806
2009-09-30 | 0.41465 | 0.41465 | -0.88032
2009-10-01 | 0.6125 | 0.6125 | -0.4902
2009-10-02 | 0.463 | 0.463 | -0.77002
2009-10-03 | 0.0078029 | 0.0078029 | -4.8533
2009-10-04 | 0.087902 | 0.087902 | -2.4315
2009-10-05 | 0.044284 | 0.044284 | -3.1171
2009-10-06 | 0.044287 | 0.044287 | -3.1171
2009-10-07 | 0.092855 | 0.092855 | -2.3767
2009-10-08 | 0.37656 | 0.37656 | -0.97669
2009-10-09 | 0.39495 | 0.39495 | -0.92899
2009-10-10 | 0.015012 | 0.015012 | -4.1989
2009-10-11 | 0.18216 | 0.18216 | -1.7029
2009-10-12 | 0.29271 | 0.29271 | -1.2286
2009-10-13 | 0.10881 | 0.10881 | -2.2181
2009-10-14 | 0.27215 | 0.27215 | -1.3014
2009-10-15 | 0.45655 | 0.45655 | -0.78406
2009-10-16 | 0.061281 | 0.061281 | -2.7923
2009-10-17 | 0.032888 | 0.032888 | -3.4146
2009-10-18 | 0.050674 | 0.050674 | -2.9823
2009-10-19 | 0.034753 | 0.034753 | -3.3595
2009-10-20 | 0.064452 | 0.064452 | -2.7418
2009-10-21 | 0.36852 | 0.36852 | -0.99826
2009-10-22 | 0.13391 | 0.13391 | -2.0106
2009-10-23 | 0.078047 | 0.078047 | -2.5505
2009-10-24 | 0.062199 | 0.062199 | -2.7774
2009-10-25 | 0.77912 | 0.77912 | -0.24959
2009-10-26 | 0.050028 | 0.050028 | -2.9952
2009-10-27 | 0.37592 | 0.37592 | -0.97839
2009-10-28 | 0.29863 | 0.29863 | -1.2086
2009-10-29 | 0.26346 | 0.26346 | -1.3338
2009-10-30 | 0.16418 | 0.16418 | -1.8068
2009-10-31 | 1.6255 | 1.6255 | 0.48584
2009-11-01 | 0.12812 | 0.12812 | -2.0548
2009-11-02 | 0.051439 | 0.051439 | -2.9674
2009-11-03 | 0.27083 | 0.27083 | -1.3063
2009-11-04 | 0.035859 | 0.035859 | -3.3282
2009-11-05 | 0.20064 | 0.20064 | -1.6062
2009-11-06 | 0.14022 | 0.14022 | -1.9645
2009-11-07 | 0.19577 | 0.19577 | -1.6308
2009-11-08 | 0.21943 | 0.21943 | -1.5167
2009-11-09 | 0.61345 | 0.61345 | -0.48866
2009-11-10 | 0.19179 | 0.19179 | -1.6514
2009-11-11 | 0.34929 | 0.34929 | -1.0519
2009-11-12 | 0.64504 | 0.64504 | -0.43844
2009-11-13 | 0.019113 | 0.019113 | -3.9574
2009-11-14 | 0.093766 | 0.093766 | -2.3669
2009-11-15 | 0.06357 | 0.06357 | -2.7556
2009-11-16 | 0.48453 | 0.48453 | -0.72457
2009-11-17 | 0.023273 | 0.023273 | -3.7605
2009-11-18 | 0.077397 | 0.077397 | -2.5588
2009-11-19 | 1.0679 | 1.0679 | 0.06571
2009-11-20 | 4.679 | 4.679 | 1.5431
2009-11-21 | 0.63791 | 0.63791 | -0.44956
2009-11-22 | 0.31686 | 0.31686 | -1.1493
2009-11-23 | 0.28127 | 0.28127 | -1.2684
2009-11-24 | 0.4685 | 0.4685 | -0.75823
2009-11-25 | 0.071655 | 0.071655 | -2.6359
2009-11-26 | 3.7211 | 3.7211 | 1.314
2009-11-27 | 0.29685 | 0.29685 | -1.2145
2009-11-28 | 0.13977 | 0.13977 | -1.9677
2009-11-29 | 0.36083 | 0.36083 | -1.0193
2009-11-30 | 0.12932 | 0.12932 | -2.0455
2009-12-01 | 0.4224 | 0.4224 | -0.8618
2009-12-02 | 0.083242 | 0.083242 | -2.486
2009-12-03 | 0.46844 | 0.46844 | -0.75834
2009-12-04 | 0.040633 | 0.040633 | -3.2032
2009-12-05 | 0.048204 | 0.048204 | -3.0323
2009-12-06 | 0.083322 | 0.083322 | -2.485
2009-12-07 | 0.067193 | 0.067193 | -2.7002
2009-12-08 | 0.18042 | 0.18042 | -1.7125
2009-12-09 | 0.5227 | 0.5227 | -0.64875
2009-12-10 | 0.25965 | 0.25965 | -1.3484
2009-12-11 | 0.025242 | 0.025242 | -3.6792
2009-12-12 | 0.036494 | 0.036494 | -3.3106
2009-12-13 | 0.0066054 | 0.0066054 | -5.0199
2009-12-14 | 0.051679 | 0.051679 | -2.9627
2009-12-15 | 0.084146 | 0.084146 | -2.4752
2009-12-16 | 0.52324 | 0.52324 | -0.64772
2009-12-17 | 3.7503 | 3.7503 | 1.3218
2009-12-18 | 0.64087 | 0.64087 | -0.44493
2009-12-19 | 0.088504 | 0.088504 | -2.4247
2009-12-20 | 0.29348 | 0.29348 | -1.2259
2009-12-21 | 0.060584 | 0.060584 | -2.8037
2009-12-22 | 0.037192 | 0.037192 | -3.2917
2009-12-23 | 0.087938 | 0.087938 | -2.4311
2009-12-24 | 0.28721 | 0.28721 | -1.2475
2009-12-25 | 0.22987 | 0.22987 | -1.4703
2009-12-26 | 0.037523 | 0.037523 | -3.2828
2009-12-27 | 0.036448 | 0.036448 | -3.3119
2009-12-28 | 0.18352 | 0.18352 | -1.6954
2009-12-29 | 0.075994 | 0.075994 | -2.5771
2009-12-30 | 1.2612 | 1.2612 | 0.23208
2009-12-31 | 2.0184 | 2.0184 | 0.70231
2010-01-01 | 1.7296 | 1.7296 | 0.5479
2010-01-02 | 2.9634 | 2.9634 | 1.0863
2010-01-03 | 0.056109 | 0.056109 | -2.8805
2010-01-04 | 0.18844 | 0.18844 | -1.669
2010-01-05 | 0.20129 | 0.20129 | -1.603
2010-01-06 | 0.1971 | 0.1971 | -1.624
2010-01-07 | 0.23611 | 0.23611 | -1.4434
2010-01-08 | 0.14997 | 0.14997 | -1.8973
2010-01-09 | 0.34539 | 0.34539 | -1.0631
2010-01-10 | 0.11708 | 0.11708 | -2.1449
2010-01-11 | 5.5073 | 5.5073 | 1.7061
2010-01-12 | 2.4114 | 2.4114 | 0.88019
2010-01-13 | 0.21368 | 0.21368 | -1.5433
2010-01-14 | 0.020469 | 0.020469 | -3.8888
2010-01-15 | 0.045414 | 0.045414 | -3.0919
2010-01-16 | 0.46744 | 0.46744 | -0.76048
2010-01-17 | 0.70862 | 0.70862 | -0.34443
2010-01-18 | 0.42049 | 0.42049 | -0.86632
2010-01-19 | 0.11054 | 0.11054 | -2.2024
2010-01-20 | 0.18343 | 0.18343 | -1.6959
2010-01-21 | 0.049286 | 0.049286 | -3.0101
2010-01-22 | 2.9028 | 2.9028 | 1.0657
2010-01-23 | 1.2455 | 1.2455 | 0.2195
2010-01-24 | 0.17782 | 0.17782 | -1.727
2010-01-25 | 0.02537 | 0.02537 | -3.6742
2010-01-26 | 0.016554 | 0.016554 | -4.1011
2010-01-27 | 0.047825 | 0.047825 | -3.0402
2010-01-28 | 0.018149 | 0.018149 | -4.0091
2010-01-29 | 1.4136 | 1.4136 | 0.34613
2010-01-30 | 0.057723 | 0.057723 | -2.8521
2010-01-31 | 0.93612 | 0.93612 | -0.066013
2010-02-01 | 0.46232 | 0.46232 | -0.77149
2010-02-02 | 0.90386 | 0.90386 | -0.10108
2010-02-03 | 0.38997 | 0.38997 | -0.9417
2010-02-04 | 1.7553 | 1.7553 | 0.56265
2010-02-05 | 1.2105 | 1.2105 | 0.19103
2010-02-06 | 0.26595 | 0.26595 | -1.3245
2010-02-07 | 0.1379 | 0.1379 | -1.9812
2010-02-08 | 0.92809 | 0.92809 | -0.074622
2010-02-09 | 0.3089 | 0.3089 | -1.1747
2010-02-10 | 2.6581 | 2.6581 | 0.9776
2010-02-11 | 1.8527 | 1.8527 | 0.61663
2010-02-12 | 0.14686 | 0.14686 | -1.9183
2010-02-13 | 0.047691 | 0.047691 | -3.043
2010-02-14 | 0.82637 | 0.82637 | -0.19071
2010-02-15 | 0.25118 | 0.25118 | -1.3816
2010-02-16 | 0.10902 | 0.10902 | -2.2162
2010-02-17 | 0.069295 | 0.069295 | -2.6694
2010-02-18 | 0.1435 | 0.1435 | -1.9414
2010-02-19 | 0.1231 | 0.1231 | -2.0947
2010-02-20 | 0.094359 | 0.094359 | -2.3606
2010-02-21 | 0.26817 | 0.26817 | -1.3161
2010-02-22 | 0.65991 | 0.65991 | -0.41566
2010-02-23 | 0.075668 | 0.075668 | -2.5814
2010-02-24 | 0.17472 | 0.17472 | -1.7446
2010-02-25 | 0.39461 | 0.39461 | -0.92986
2010-02-26 | 0.33289 | 0.33289 | -1.0999
2010-02-27 | 1.985 | 1.985 | 0.68562
2010-02-28 | 0.78794 | 0.78794 | -0.23833
2010-03-01 | 0.39364 | 0.39364 | -0.93232
2010-03-02 | 0.087265 | 0.087265 | -2.4388
2010-03-03 | 0.032527 | 0.032527 | -3.4257
2010-03-04 | 0.14626 | 0.14626 | -1.9223
2010-03-05 | 0.084105 | 0.084105 | -2.4757
2010-03-06 | 11.7699 | 11.7699 | 2.4655
2010-03-07 | 1.3468 | 1.3468 | 0.29771
2010-03-08 | 0.52613 | 0.52613 | -0.6422
2010-03-09 | 0.06577 | 0.06577 | -2.7216
2010-03-10 | 0.1415 | 0.1415 | -1.9555
2010-03-11 | 0.035631 | 0.035631 | -3.3345
2010-03-12 | 0.065799 | 0.065799 | -2.7212
2010-03-13 | 0.039329 | 0.039329 | -3.2358
2010-03-14 | 0.031785 | 0.031785 | -3.4488
2010-03-15 | 0.061698 | 0.061698 | -2.7855
2010-03-16 | 0.31355 | 0.31355 | -1.1598
2010-03-17 | 0.74591 | 0.74591 | -0.29315
2010-03-18 | 0.34423 | 0.34423 | -1.0664
2010-03-19 | 0.56267 | 0.56267 | -0.57506
2010-03-20 | 0.0813 | 0.0813 | -2.5096
2010-03-21 | 0.15664 | 0.15664 | -1.8538
2010-03-22 | 0.39798 | 0.39798 | -0.92136
2010-03-23 | 0.02717 | 0.02717 | -3.6056
2010-03-24 | 0.24879 | 0.24879 | -1.3912
2010-03-25 | 0.027919 | 0.027919 | -3.5784
2010-03-26 | 0.31536 | 0.31536 | -1.154
2010-03-27 | 0.064312 | 0.064312 | -2.744
2010-03-28 | 0.71124 | 0.71124 | -0.34074
2010-03-29 | 0.36619 | 0.36619 | -1.0046
2010-03-30 | 0.62933 | 0.62933 | -0.4631
2010-03-31 | 0.27676 | 0.27676 | -1.2846
2010-04-01 | 0.50412 | 0.50412 | -0.68495
2010-04-02 | 0.028404 | 0.028404 | -3.5612
2010-04-03 | 0.26474 | 0.26474 | -1.329
2010-04-04 | 0.052262 | 0.052262 | -2.9515
2010-04-05 | 0.33876 | 0.33876 | -1.0825
2010-04-06 | 0.12912 | 0.12912 | -2.047
2010-04-07 | 0.20078 | 0.20078 | -1.6055
2010-04-08 | 0.084439 | 0.084439 | -2.4717
2010-04-09 | 0.051389 | 0.051389 | -2.9683
2010-04-10 | 0.034142 | 0.034142 | -3.3772
2010-04-11 | 0.71377 | 0.71377 | -0.33719
2010-04-12 | 0.044235 | 0.044235 | -3.1182
2010-04-13 | 0.026966 | 0.026966 | -3.6132
2010-04-14 | 0.18774 | 0.18774 | -1.6727
2010-04-15 | 0.037305 | 0.037305 | -3.2886
2010-04-16 | 0.14515 | 0.14515 | -1.93
2010-04-17 | 0.22039 | 0.22039 | -1.5124
2010-04-18 | 1.0328 | 1.0328 | 0.032231
2010-04-19 | 0.06229 | 0.06229 | -2.776
2010-04-20 | 0.23902 | 0.23902 | -1.4312
2010-04-21 | 0.31596 | 0.31596 | -1.1521
2010-04-22 | 0.054101 | 0.054101 | -2.9169
2010-04-23 | 0.17226 | 0.17226 | -1.7587
2010-04-24 | 0.20472 | 0.20472 | -1.5861
2010-04-25 | 0.46025 | 0.46025 | -0.77598
2010-04-26 | 0.021151 | 0.021151 | -3.8561
2010-04-27 | 0.18808 | 0.18808 | -1.6709
2010-04-28 | 0.058219 | 0.058219 | -2.8435
2010-04-29 | 0.21071 | 0.21071 | -1.5573
2010-04-30 | 0.40415 | 0.40415 | -0.90596
2010-05-01 | 0.078929 | 0.078929 | -2.5392
2010-05-02 | 0.049017 | 0.049017 | -3.0156
2010-05-03 | 0.206 | 0.206 | -1.5799
2010-05-04 | 0.40615 | 0.40615 | -0.90104
2010-05-05 | 0.094702 | 0.094702 | -2.357
2010-05-06 | 0.025709 | 0.025709 | -3.6609
2010-05-07 | 0.031999 | 0.031999 | -3.442
2010-05-08 | 0.075311 | 0.075311 | -2.5861
2010-05-09 | 0.01902 | 0.01902 | -3.9623
2010-05-10 | 0.10298 | 0.10298 | -2.2732
2010-05-11 | 0.12164 | 0.12164 | -2.1067
2010-05-12 | 0.12565 | 0.12565 | -2.0743
2010-05-13 | 0.036737 | 0.036737 | -3.304
2010-05-14 | 0.10016 | 0.10016 | -2.301
2010-05-15 | 0.04268 | 0.04268 | -3.154
2010-05-16 | 0.044368 | 0.044368 | -3.1152
2010-05-17 | 0.08734 | 0.08734 | -2.4379
2010-05-18 | 0.39694 | 0.39694 | -0.92397
2010-05-19 | 0.075639 | 0.075639 | -2.5818
2010-05-20 | 0.16549 | 0.16549 | -1.7988
2010-05-21 | 0.0056338 | 0.0056338 | -5.179
2010-05-22 | 0.056131 | 0.056131 | -2.8801
2010-05-23 | 0.58256 | 0.58256 | -0.54032
2010-05-24 | 0.03654 | 0.03654 | -3.3093
2010-05-25 | 0.2788 | 0.2788 | -1.2773
2010-05-26 | 0.40888 | 0.40888 | -0.89433
2010-05-27 | 0.19947 | 0.19947 | -1.6121
2010-05-28 | 0.27659 | 0.27659 | -1.2852
2010-05-29 | 0.19778 | 0.19778 | -1.6206
2010-05-30 | 0.91326 | 0.91326 | -0.090729
2010-05-31 | 0.019597 | 0.019597 | -3.9324
2010-06-01 | 0.0097763 | 0.0097763 | -4.6278
2010-06-02 | 0.094265 | 0.094265 | -2.3616
2010-06-03 | 0.038969 | 0.038969 | -3.245
2010-06-04 | 0.024361 | 0.024361 | -3.7148
2010-06-05 | 0.34142 | 0.34142 | -1.0746
2010-06-06 | 0.17902 | 0.17902 | -1.7203
2010-06-07 | 0.034215 | 0.034215 | -3.3751
2010-06-08 | 0.015687 | 0.015687 | -4.1549
2010-06-09 | 0.84843 | 0.84843 | -0.16437
2010-06-10 | 0.10891 | 0.10891 | -2.2172
2010-06-11 | 0.065328 | 0.065328 | -2.7283
2010-06-12 | 0.31622 | 0.31622 | -1.1513
2010-06-13 | 0.34307 | 0.34307 | -1.0698
2010-06-14 | 1.0987 | 1.0987 | 0.094128
2010-06-15 | 0.062301 | 0.062301 | -2.7758
2010-06-16 | 0.55536 | 0.55536 | -0.58815
2010-06-17 | 12.0837 | 12.0837 | 2.4919
2010-06-18 | 0.10322 | 0.10322 | -2.2709
2010-06-19 | 0.1637 | 0.1637 | -1.8097
2010-06-20 | 0.10054 | 0.10054 | -2.2972
2010-06-21 | 0.37032 | 0.37032 | -0.99339
2010-06-22 | 1.8157 | 1.8157 | 0.59646
2010-06-23 | 0.019813 | 0.019813 | -3.9214
2010-06-24 | 0.042912 | 0.042912 | -3.1486
2010-06-25 | 0.46694 | 0.46694 | -0.76155
2010-06-26 | 0.11435 | 0.11435 | -2.1685
2010-06-27 | 0.0419 | 0.0419 | -3.1725
2010-06-28 | 0.39261 | 0.39261 | -0.93494
2010-06-29 | 0.21589 | 0.21589 | -1.533
2010-06-30 | 0.17844 | 0.17844 | -1.7235
2010-07-01 | 0.024369 | 0.024369 | -3.7145
2010-07-02 | 0.023421 | 0.023421 | -3.7541
2010-07-03 | 0.020231 | 0.020231 | -3.9005
2010-07-04 | 0.0051521 | 0.0051521 | -5.2683
2010-07-05 | 0.20148 | 0.20148 | -1.6021
2010-07-06 | 0.022465 | 0.022465 | -3.7958
2010-07-07 | 0.08293 | 0.08293 | -2.4898
2010-07-08 | 0.021647 | 0.021647 | -3.8329
2010-07-09 | 0.17461 | 0.17461 | -1.7452
2010-07-10 | 1.1764 | 1.1764 | 0.16249
2010-07-11 | 0.1783 | 0.1783 | -1.7243
2010-07-12 | 0.046451 | 0.046451 | -3.0694
2010-07-13 | 0.55885 | 0.55885 | -0.58187
2010-07-14 | 0.51582 | 0.51582 | -0.66199
2010-07-15 | 0.23445 | 0.23445 | -1.4505
2010-07-16 | 0.10346 | 0.10346 | -2.2686
2010-07-17 | 0.032399 | 0.032399 | -3.4296
2010-07-18 | 0.013903 | 0.013903 | -4.2757
2010-07-19 | 0.090638 | 0.090638 | -2.4009
2010-07-20 | 0.05043 | 0.05043 | -2.9872
2010-07-21 | 0.05295 | 0.05295 | -2.9384
2010-07-22 | 0.017957 | 0.017957 | -4.0198
2010-07-23 | 0.069138 | 0.069138 | -2.6717
2010-07-24 | 0.011164 | 0.011164 | -4.4951
2010-07-25 | 0.4174 | 0.4174 | -0.8737
2010-07-26 | 0.022823 | 0.022823 | -3.78
2010-07-27 | 0.16735 | 0.16735 | -1.7877
2010-07-28 | 0.014188 | 0.014188 | -4.2554
2010-07-29 | 0.060155 | 0.060155 | -2.8108
2010-07-30 | 0.091423 | 0.091423 | -2.3923
2010-07-31 | 0.054989 | 0.054989 | -2.9006
2010-08-01 | 0.066936 | 0.066936 | -2.704
2010-08-02 | 0.32728 | 0.32728 | -1.1169
2010-08-03 | 0.085065 | 0.085065 | -2.4643
2010-08-04 | 0.68308 | 0.68308 | -0.38115
2010-08-05 | 0.10074 | 0.10074 | -2.2952
2010-08-06 | 0.077093 | 0.077093 | -2.5627
2010-08-07 | 0.013791 | 0.013791 | -4.2838
2010-08-08 | 0.010234 | 0.010234 | -4.5821
2010-08-09 | 0.019266 | 0.019266 | -3.9494
2010-08-10 | 0.32051 | 0.32051 | -1.1378
2010-08-11 | 0.04188 | 0.04188 | -3.173
2010-08-12 | 2.7934 | 2.7934 | 1.0272
2010-08-13 | 0.3948 | 0.3948 | -0.92937
2010-08-14 | 0.91251 | 0.91251 | -0.091557
2010-08-15 | 0.65009 | 0.65009 | -0.43065
2010-08-16 | 0.5238 | 0.5238 | -0.64665
2010-08-17 | 0.075735 | 0.075735 | -2.5805
2010-08-18 | 0.9157 | 0.9157 | -0.088061
2010-08-19 | 0.072495 | 0.072495 | -2.6242
2010-08-20 | 0.17066 | 0.17066 | -1.7681
2010-08-21 | 0.058715 | 0.058715 | -2.8351
2010-08-22 | 0.039782 | 0.039782 | -3.2243
2010-08-23 | 0.033206 | 0.033206 | -3.405
2010-08-24 | 0.62177 | 0.62177 | -0.47519
2010-08-25 | 0.40113 | 0.40113 | -0.91347
2010-08-26 | 0.13957 | 0.13957 | -1.9692
2010-08-27 | 0.010213 | 0.010213 | -4.5841
2010-08-28 | 0.75378 | 0.75378 | -0.28266
2010-08-29 | 0.047769 | 0.047769 | -3.0414
2010-08-30 | 0.18133 | 0.18133 | -1.7074
2010-08-31 | 0.61751 | 0.61751 | -0.48206
2010-09-01 | 0.11588 | 0.11588 | -2.1552
2010-09-02 | 0.011677 | 0.011677 | -4.4501
2010-09-03 | 0.08637 | 0.08637 | -2.4491
2010-09-04 | 2.2341 | 2.2341 | 0.80383
2010-09-05 | 24.6608 | 24.6608 | 3.2052
2010-09-06 | 1.4941 | 1.4941 | 0.40155
2010-09-07 | 0.084607 | 0.084607 | -2.4697
2010-09-08 | 0.10978 | 0.10978 | -2.2093
2010-09-09 | 0.33049 | 0.33049 | -1.1072
2010-09-10 | 0.40923 | 0.40923 | -0.89348
2010-09-11 | 0.020215 | 0.020215 | -3.9013
2010-09-12 | 0.0054385 | 0.0054385 | -5.2142
2010-09-13 | 0.019092 | 0.019092 | -3.9585
2010-09-14 | 0.17295 | 0.17295 | -1.7548
2010-09-15 | 0.11104 | 0.11104 | -2.1979
2010-09-16 | 0.77567 | 0.77567 | -0.25403
2010-09-17 | 0.2561 | 0.2561 | -1.3622
2010-09-18 | 0.18151 | 0.18151 | -1.7065
2010-09-19 | 0.1175 | 0.1175 | -2.1413
2010-09-20 | 0.50166 | 0.50166 | -0.68984
2010-09-21 | 0.12588 | 0.12588 | -2.0724
2010-09-22 | 0.020117 | 0.020117 | -3.9062
2010-09-23 | 0.011178 | 0.011178 | -4.4938
2010-09-24 | 0.019265 | 0.019265 | -3.9495
2010-09-25 | 0.021001 | 0.021001 | -3.8632
2010-09-26 | 0.077388 | 0.077388 | -2.5589
2010-09-27 | 0.44839 | 0.44839 | -0.80209
2010-09-28 | 0.24873 | 0.24873 | -1.3914
2010-09-29 | 0.082932 | 0.082932 | -2.4897
2010-09-30 | 0.3229 | 0.3229 | -1.1304
2010-10-01 | 0.065293 | 0.065293 | -2.7289
2010-10-02 | 0.075226 | 0.075226 | -2.5873
2010-10-03 | 0.0050897 | 0.0050897 | -5.2805
2010-10-04 | 0.04626 | 0.04626 | -3.0735
2010-10-05 | 0.69078 | 0.69078 | -0.36994
2010-10-06 | 1.3399 | 1.3399 | 0.29257
2010-10-07 | 0.41416 | 0.41416 | -0.8815
2010-10-08 | 0.0843 | 0.0843 | -2.4734
2010-10-09 | 0.05576 | 0.05576 | -2.8867
2010-10-10 | 0.18086 | 0.18086 | -1.71
2010-10-11 | 0.23739 | 0.23739 | -1.438
2010-10-12 | 0.70459 | 0.70459 | -0.35014
2010-10-13 | 0.48717 | 0.48717 | -0.71915
2010-10-14 | 0.092313 | 0.092313 | -2.3826
2010-10-15 | 0.87951 | 0.87951 | -0.12839
2010-10-16 | 0.50105 | 0.50105 | -0.69104
2010-10-17 | 0.13837 | 0.13837 | -1.9779
2010-10-18 | 0.086271 | 0.086271 | -2.4503
2010-10-19 | 0.024671 | 0.024671 | -3.7021
2010-10-20 | 0.037971 | 0.037971 | -3.2709
2010-10-21 | 0.32686 | 0.32686 | -1.1182
2010-10-22 | 0.006165 | 0.006165 | -5.0889
2010-10-23 | 0.11671 | 0.11671 | -2.1481
2010-10-24 | 0.17673 | 0.17673 | -1.7331
2010-10-25 | 0.51832 | 0.51832 | -0.65717
2010-10-26 | 0.13986 | 0.13986 | -1.9671
2010-10-27 | 0.67924 | 0.67924 | -0.38677
2010-10-28 | 0.037491 | 0.037491 | -3.2837
2010-10-29 | 0.12948 | 0.12948 | -2.0442
2010-10-30 | 0.28815 | 0.28815 | -1.2443
2010-10-31 | 2.0964 | 2.0964 | 0.74024
2010-11-01 | 2.2115 | 2.2115 | 0.79367
2010-11-02 | 0.17064 | 0.17064 | -1.7682
2010-11-03 | 0.03286 | 0.03286 | -3.4155
2010-11-04 | 0.042091 | 0.042091 | -3.1679
2010-11-05 | 0.093785 | 0.093785 | -2.3668
2010-11-06 | 0.20396 | 0.20396 | -1.5899
2010-11-07 | 0.4725 | 0.4725 | -0.74972
2010-11-08 | 0.092155 | 0.092155 | -2.3843
2010-11-09 | 0.034332 | 0.034332 | -3.3717
2010-11-10 | 0.10584 | 0.10584 | -2.2459
2010-11-11 | 0.066976 | 0.066976 | -2.7034
2010-11-12 | 0.71102 | 0.71102 | -0.34105
2010-11-13 | 1.1063 | 1.1063 | 0.10102
2010-11-14 | 0.1149 | 0.1149 | -2.1637
2010-11-15 | 0.54285 | 0.54285 | -0.61092
2010-11-16 | 0.10248 | 0.10248 | -2.2781
2010-11-17 | 0.28569 | 0.28569 | -1.2529
2010-11-18 | 0.65203 | 0.65203 | -0.42767
2010-11-19 | 0.02906 | 0.02906 | -3.5384
2010-11-20 | 0.21964 | 0.21964 | -1.5158
2010-11-21 | 0.90778 | 0.90778 | -0.096759
2010-11-22 | 0.086492 | 0.086492 | -2.4477
2010-11-23 | 0.097727 | 0.097727 | -2.3256
2010-11-24 | 0.50267 | 0.50267 | -0.68783
2010-11-25 | 0.31727 | 0.31727 | -1.148
2010-11-26 | 0.26563 | 0.26563 | -1.3257
2010-11-27 | 0.74498 | 0.74498 | -0.2944
2010-11-28 | 1.2179 | 1.2179 | 0.19716
2010-11-29 | 0.91692 | 0.91692 | -0.086732
2010-11-30 | 0.43636 | 0.43636 | -0.82928
2010-12-01 | 0.50553 | 0.50553 | -0.68214
2010-12-02 | 1.4822 | 1.4822 | 0.39354
2010-12-03 | 0.41934 | 0.41934 | -0.86908
2010-12-04 | 0.20645 | 0.20645 | -1.5777
2010-12-05 | 0.04791 | 0.04791 | -3.0384
2010-12-06 | 0.52039 | 0.52039 | -0.65318
2010-12-07 | 0.44623 | 0.44623 | -0.80692
2010-12-08 | 2.4513 | 2.4513 | 0.89663
2010-12-09 | 0.31957 | 0.31957 | -1.1408
2010-12-10 | 0.080484 | 0.080484 | -2.5197
2010-12-11 | 0.13826 | 0.13826 | -1.9786
2010-12-12 | 0.13987 | 0.13987 | -1.967
2010-12-13 | 0.037681 | 0.037681 | -3.2786
2010-12-14 | 0.14061 | 0.14061 | -1.9618
2010-12-15 | 0.14451 | 0.14451 | -1.9344
2010-12-16 | 0.049374 | 0.049374 | -3.0083
2010-12-17 | 0.25013 | 0.25013 | -1.3858
2010-12-18 | 0.86974 | 0.86974 | -0.13956
2010-12-19 | 0.53245 | 0.53245 | -0.63027
2010-12-20 | 1.3799 | 1.3799 | 0.322
2010-12-21 | 0.041833 | 0.041833 | -3.1741
2010-12-22 | 0.081858 | 0.081858 | -2.5028
2010-12-23 | 0.34669 | 0.34669 | -1.0593
2010-12-24 | 0.50019 | 0.50019 | -0.69276
2010-12-25 | 0.73014 | 0.73014 | -0.31451
2010-12-26 | 0.013669 | 0.013669 | -4.2926
2010-12-27 | 0.049723 | 0.049723 | -3.0013
2010-12-28 | 0.12377 | 0.12377 | -2.0893
2010-12-29 | 0.24894 | 0.24894 | -1.3905
2010-12-30 | 0.26546 | 0.26546 | -1.3263
2010-12-31 | 1.3684 | 1.3684 | 0.31364
2011-01-01 | 0.049196 | 0.049196 | -3.0119
2011-01-02 | 0.083487 | 0.083487 | -2.4831
2011-01-03 | 0.08415 | 0.08415 | -2.4751
2011-01-04 | 0.13996 | 0.13996 | -1.9664
2011-01-05 | 0.55484 | 0.55484 | -0.58907
2011-01-06 | 0.28984 | 0.28984 | -1.2384
2011-01-07 | 0.20755 | 0.20755 | -1.5724
2011-01-08 | 0.26954 | 0.26954 | -1.311
2011-01-09 | 0.17768 | 0.17768 | -1.7278
2011-01-10 | 2.4896 | 2.4896 | 0.91212
2011-01-11 | 0.21307 | 0.21307 | -1.5462
2011-01-12 | 0.48899 | 0.48899 | -0.71541
2011-01-13 | 0.48799 | 0.48799 | -0.71745
2011-01-14 | 6.9024 | 6.9024 | 1.9319
2011-01-15 | 0.91716 | 0.91716 | -0.08647
2011-01-16 | 0.036249 | 0.036249 | -3.3173
2011-01-17 | 0.16175 | 0.16175 | -1.8217
2011-01-18 | 0.30394 | 0.30394 | -1.1909
2011-01-19 | 0.13687 | 0.13687 | -1.9887
2011-01-20 | 0.096711 | 0.096711 | -2.336
2011-01-21 | 0.013096 | 0.013096 | -4.3354
2011-01-22 | 0.11194 | 0.11194 | -2.1898
2011-01-23 | 0.30835 | 0.30835 | -1.1765
2011-01-24 | 0.074231 | 0.074231 | -2.6006
2011-01-25 | 0.080977 | 0.080977 | -2.5136
2011-01-26 | 0.051142 | 0.051142 | -2.9731
2011-01-27 | 0.074133 | 0.074133 | -2.6019
2011-01-28 | 0.12766 | 0.12766 | -2.0584
2011-01-29 | 0.15951 | 0.15951 | -1.8357
2011-01-30 | 0.67472 | 0.67472 | -0.39346
2011-01-31 | 0.25854 | 0.25854 | -1.3527
2011-02-01 | 15.5008 | 15.5008 | 2.7409
2011-02-02 | 0.26901 | 0.26901 | -1.313
2011-02-03 | 0.72681 | 0.72681 | -0.31909
2011-02-04 | 5.8541 | 5.3257 | 1.6726 | < Excluded transmission event.
2011-02-05 | 4.6965 | 4.6965 | 1.5468
2011-02-06 | 1.2648 | 1.2648 | 0.23492
2011-02-07 | 1.241 | 1.241 | 0.21591
2011-02-08 | 0.10908 | 0.10908 | -2.2157
2011-02-09 | 0.25291 | 0.25291 | -1.3747
2011-02-10 | 0.44036 | 0.44036 | -0.82015
2011-02-11 | 0.19145 | 0.19145 | -1.6531
2011-02-12 | 0.37405 | 0.37405 | -0.98337
2011-02-13 | 0.089262 | 0.089262 | -2.4162
2011-02-14 | 0.15889 | 0.15889 | -1.8396
2011-02-15 | 0.50862 | 0.50862 | -0.67605
2011-02-16 | 0.66551 | 0.66551 | -0.4072
2011-02-17 | 0.13313 | 0.13313 | -2.0164
2011-02-18 | 0.22039 | 0.22039 | -1.5124
2011-02-19 | 1.3732 | 1.3732 | 0.31713
2011-02-20 | 0.11366 | 0.11366 | -2.1745
2011-02-21 | 0.22244 | 0.22244 | -1.5031
2011-02-22 | 0.27089 | 0.27089 | -1.306
2011-02-23 | 0.13973 | 0.13973 | -1.9681
2011-02-24 | 0.09111 | 0.09111 | -2.3957
2011-02-25 | 0.58294 | 0.58294 | -0.53968
2011-02-26 | 0.099912 | 0.099912 | -2.3035
2011-02-27 | 0.23364 | 0.23364 | -1.454
2011-02-28 | 0.10462 | 0.10462 | -2.2575
2011-03-01 | 0.22854 | 0.22854 | -1.4761
2011-03-02 | 0.060399 | 0.060399 | -2.8068
2011-03-03 | 0.63944 | 0.63944 | -0.44717
2011-03-04 | 0.086139 | 0.086139 | -2.4518
2011-03-05 | 0.18073 | 0.18073 | -1.7107
2011-03-06 | 0.4429 | 0.4429 | -0.81441
2011-03-07 | 0.55105 | 0.55105 | -0.59594
2011-03-08 | 0.051141 | 0.051141 | -2.9732
2011-03-09 | 0.42532 | 0.42532 | -0.85491
2011-03-10 | 0.13479 | 0.13479 | -2.0041
2011-03-11 | 0.42925 | 0.42925 | -0.84572
2011-03-12 | 0.030402 | 0.030402 | -3.4932
2011-03-13 | 0.47864 | 0.47864 | -0.73681
2011-03-14 | 0.25882 | 0.25882 | -1.3516
2011-03-15 | 0.18989 | 0.18989 | -1.6613
2011-03-16 | 0.070265 | 0.070265 | -2.6555
2011-03-17 | 0.040197 | 0.040197 | -3.214
2011-03-18 | 0.024162 | 0.024162 | -3.723
2011-03-19 | 0.036765 | 0.036765 | -3.3032
2011-03-20 | 0.33158 | 0.33158 | -1.1039
2011-03-21 | 0.48611 | 0.48611 | -0.72132
2011-03-22 | 0.9343 | 0.9343 | -0.067952
2011-03-23 | 0.10401 | 0.10401 | -2.2633
2011-03-24 | 0.96839 | 0.96839 | -0.032122
2011-03-25 | 1.0395 | 1.0395 | 0.038701
2011-03-26 | 0.19314 | 0.19314 | -1.6443
2011-03-27 | 0.015633 | 0.015633 | -4.1584
2011-03-28 | 0.025668 | 0.025668 | -3.6625
2011-03-29 | 0.080883 | 0.080883 | -2.5148
2011-03-30 | 0.026731 | 0.026731 | -3.6219
2011-03-31 | 0.043983 | 0.043983 | -3.1239
2011-04-01 | 0.22937 | 0.22937 | -1.4724
2011-04-02 | 1.0768 | 1.0768 | 0.073982
2011-04-03 | 0.38075 | 0.38075 | -0.9656
2011-04-04 | 0.046392 | 0.046392 | -3.0706
2011-04-05 | 0.092267 | 0.092267 | -2.3831
2011-04-06 | 0.011162 | 0.011162 | -4.4953
2011-04-07 | 0.020879 | 0.020879 | -3.869
2011-04-08 | 0.080373 | 0.080373 | -2.5211
2011-04-09 | 0.85285 | 0.85285 | -0.15918
2011-04-10 | 0.27482 | 0.27482 | -1.2916
2011-04-11 | 0.55004 | 0.55004 | -0.59777
2011-04-12 | 1.1687 | 1.1687 | 0.15588
2011-04-13 | 0.11206 | 0.11206 | -2.1887
2011-04-14 | 0.31567 | 0.31567 | -1.153
2011-04-15 | 0.089757 | 0.089757 | -2.4106
2011-04-16 | 0.0092771 | 0.0092771 | -4.6802
2011-04-17 | 0.024826 | 0.024826 | -3.6959
2011-04-18 | 0.084196 | 0.084196 | -2.4746
2011-04-19 | 0.065331 | 0.065331 | -2.7283
2011-04-20 | 0.39161 | 0.39161 | -0.93749
2011-04-21 | 0.060029 | 0.060029 | -2.8129
2011-04-22 | 0.07963 | 0.07963 | -2.5304
2011-04-23 | 0.20955 | 0.20955 | -1.5628
2011-04-24 | 0.022251 | 0.022251 | -3.8054
2011-04-25 | 0.029714 | 0.029714 | -3.5161
2011-04-26 | 0.0095326 | 0.0095326 | -4.653
2011-04-27 | 0.30469 | 0.30469 | -1.1885
2011-04-28 | 0.036854 | 0.036854 | -3.3008
2011-04-29 | 0.043786 | 0.043786 | -3.1284
2011-04-30 | 0.061906 | 0.061906 | -2.7821
2011-05-01 | 0.030867 | 0.030867 | -3.4781
2011-05-02 | 0.544 | 0.544 | -0.6088
2011-05-03 | 0.027925 | 0.027925 | -3.5782
2011-05-04 | 0.037226 | 0.037226 | -3.2908
2011-05-05 | 0.12735 | 0.12735 | -2.0608
2011-05-06 | 0.019438 | 0.019438 | -3.9405
2011-05-07 | 0.01852 | 0.01852 | -3.9889
2011-05-08 | 0.033936 | 0.033936 | -3.3833
2011-05-09 | 0.074008 | 0.074008 | -2.6036
2011-05-10 | 0.28021 | 0.28021 | -1.2722
2011-05-11 | 0.14873 | 0.14873 | -1.9056
2011-05-12 | 0.11937 | 0.11937 | -2.1255
2011-05-13 | 2.1103 | 2.1103 | 0.74683
2011-05-14 | 0.99544 | 0.99544 | -0.0045729
2011-05-15 | 0.061706 | 0.061706 | -2.7854
2011-05-16 | 0.27461 | 0.27461 | -1.2924
2011-05-17 | 0.036755 | 0.036755 | -3.3035
2011-05-18 | 0.071482 | 0.071482 | -2.6383
2011-05-19 | 0.017054 | 0.017054 | -4.0714
2011-05-20 | 0.24011 | 0.24011 | -1.4267
2011-05-21 | 0.053967 | 0.053967 | -2.9194
2011-05-22 | 0.5328 | 0.5328 | -0.62961
2011-05-23 | 0.11458 | 0.11458 | -2.1665
2011-05-24 | 0.11575 | 0.11575 | -2.1563
2011-05-25 | 0.041189 | 0.041189 | -3.1896
2011-05-26 | 0.098062 | 0.098062 | -2.3222
2011-05-27 | 0.070499 | 0.070499 | -2.6522
2011-05-28 | 0.065672 | 0.065672 | -2.7231
2011-05-29 | 0.25325 | 0.25325 | -1.3734
2011-05-30 | 0.095345 | 0.095345 | -2.3503
2011-05-31 | 0.13269 | 0.13269 | -2.0197
2011-06-01 | 0.12207 | 0.12207 | -2.1031
2011-06-02 | 0.21273 | 0.21273 | -1.5477
2011-06-03 | 0.033921 | 0.033921 | -3.3837
2011-06-04 | 0.12691 | 0.12691 | -2.0643
2011-06-05 | 0.62843 | 0.62843 | -0.46453
2011-06-06 | 0.04181 | 0.04181 | -3.1746
2011-06-07 | 0.41976 | 0.41976 | -0.86808
2011-06-08 | 1.3858 | 1.3858 | 0.32625
2011-06-09 | 0.099178 | 0.099178 | -2.3108
2011-06-10 | 0.029355 | 0.029355 | -3.5283
2011-06-11 | 0.038869 | 0.038869 | -3.2476
2011-06-12 | 0.043419 | 0.043419 | -3.1369
2011-06-13 | 0.14273 | 0.14273 | -1.9468
2011-06-14 | 0.0558 | 0.0558 | -2.886
2011-06-15 | 1.1576 | 1.1576 | 0.14638
2011-06-16 | 0.16263 | 0.16263 | -1.8163
2011-06-17 | 0.43663 | 0.43663 | -0.82866
2011-06-18 | 0.23343 | 0.23343 | -1.4549
2011-06-19 | 0.13836 | 0.13836 | -1.9779
2011-06-20 | 3.0524 | 3.0524 | 1.1159
2011-06-21 | 2.6154 | 2.6154 | 0.9614
2011-06-22 | 0.80242 | 0.80242 | -0.22013
2011-06-23 | 0.090839 | 0.090839 | -2.3987
2011-06-24 | 0.034297 | 0.034297 | -3.3727
2011-06-25 | 0.28125 | 0.28125 | -1.2685
2011-06-26 | 0.40823 | 0.40823 | -0.89593
2011-06-27 | 0.094478 | 0.094478 | -2.3594
2011-06-28 | 0.092259 | 0.092259 | -2.3832
2011-06-29 | 0.093525 | 0.093525 | -2.3695
2011-06-30 | 0.12229 | 0.12229 | -2.1014
2011-07-01 | 0.0080479 | 0.0080479 | -4.8224
2011-07-02 | 0.46196 | 0.46196 | -0.77228
2011-07-03 | 0.17623 | 0.17623 | -1.736
2011-07-04 | 0.32099 | 0.32099 | -1.1363
2011-07-05 | 3.6266 | 3.6266 | 1.2883
2011-07-06 | 0.47172 | 0.47172 | -0.75137
2011-07-07 | 0.36327 | 0.36327 | -1.0126
2011-07-08 | 0.13283 | 0.13283 | -2.0187
2011-07-09 | 0.15532 | 0.15532 | -1.8623
2011-07-10 | 4.2214 | 4.2214 | 1.4402
2011-07-11 | 0.38252 | 0.38252 | -0.96097
2011-07-12 | 0.11736 | 0.11736 | -2.1425
2011-07-13 | 0.30942 | 0.30942 | -1.173
2011-07-14 | 0.23272 | 0.23272 | -1.4579
2011-07-15 | 0.071981 | 0.071981 | -2.6314
2011-07-16 | 0.075929 | 0.075929 | -2.578
2011-07-17 | 0.076697 | 0.076697 | -2.5679
2011-07-18 | 1.1045 | 1.1045 | 0.099412
2011-07-19 | 0.043168 | 0.043168 | -3.1427
2011-07-20 | 0.46178 | 0.46178 | -0.77266
2011-07-21 | 0.78135 | 0.78135 | -0.24673
2011-07-22 | 0.29093 | 0.29093 | -1.2347
2011-07-23 | 0.022449 | 0.022449 | -3.7965
2011-07-24 | 0.025616 | 0.025616 | -3.6645
2011-07-25 | 0.021078 | 0.021078 | -3.8595
2011-07-26 | 0.37138 | 0.37138 | -0.99053
2011-07-27 | 0.20133 | 0.20133 | -1.6028
2011-07-28 | 0.035837 | 0.035837 | -3.3288
2011-07-29 | 0.2466 | 0.2466 | -1.4
2011-07-30 | 0.16174 | 0.16174 | -1.8218
2011-07-31 | 0.054571 | 0.054571 | -2.9083
2011-08-01 | 0.029479 | 0.029479 | -3.5241
2011-08-02 | 0.06553 | 0.06553 | -2.7252
2011-08-03 | 0.056459 | 0.056459 | -2.8742
2011-08-04 | 0.23274 | 0.23274 | -1.4578
2011-08-05 | 0.25581 | 0.25581 | -1.3633
2011-08-06 | 0.1696 | 0.1696 | -1.7743
2011-08-07 | 0.92412 | 0.92412 | -0.078912
2011-08-08 | 0.027698 | 0.027698 | -3.5864
2011-08-09 | 0.26693 | 0.26693 | -1.3208
2011-08-10 | 1.686 | 1.686 | 0.52238
2011-08-11 | 0.29128 | 0.29128 | -1.2335
2011-08-12 | 0.076327 | 0.076327 | -2.5727
2011-08-13 | 0.48428 | 0.48428 | -0.7251
2011-08-14 | 0.0030009 | 0.0030009 | -5.8088
2011-08-15 | 0.13692 | 0.13692 | -1.9883
2011-08-16 | 0.050035 | 0.050035 | -2.995
2011-08-17 | 0.79214 | 0.79214 | -0.23302
2011-08-18 | 0.14256 | 0.14256 | -1.948
2011-08-19 | 0.03123 | 0.03123 | -3.4664
2011-08-20 | 0.032282 | 0.032282 | -3.4332
2011-08-21 | 0.17187 | 0.17187 | -1.761
2011-08-22 | 0.026651 | 0.026651 | -3.6249
2011-08-23 | 0.042472 | 0.042472 | -3.1589
2011-08-24 | 0.11779 | 0.11779 | -2.1388
2011-08-25 | 0.17562 | 0.17562 | -1.7394
2011-08-26 | 0.11494 | 0.11494 | -2.1633
2011-08-27 | 0.056208 | 0.056208 | -2.8787
2011-08-28 | 0.019394 | 0.019394 | -3.9428
2011-08-29 | 0.19002 | 0.19002 | -1.6606
2011-08-30 | 0.042538 | 0.042538 | -3.1574
2011-08-31 | 0.012847 | 0.012847 | -4.3546
2011-09-01 | 0.15345 | 0.15345 | -1.8744
2011-09-02 | 0.66905 | 0.66905 | -0.4019
2011-09-03 | 0.22271 | 0.22271 | -1.5019
2011-09-04 | 0.69602 | 0.69602 | -0.36237
2011-09-05 | 0.27216 | 0.27216 | -1.3014
2011-09-06 | 0.4005 | 0.4005 | -0.91503
2011-09-07 | 0.047804 | 0.047804 | -3.0406
2011-09-08 | 0.0089556 | 0.0089556 | -4.7155
2011-09-09 | 0.59062 | 0.59062 | -0.52659
2011-09-10 | 0.017297 | 0.017297 | -4.0572
2011-09-11 | 0.53801 | 0.53801 | -0.61988
2011-09-12 | 0.019892 | 0.019892 | -3.9175
2011-09-13 | 0.083432 | 0.083432 | -2.4837
2011-09-14 | 0.0061256 | 0.0061256 | -5.0953
2011-09-15 | 0.026732 | 0.026732 | -3.6219
2011-09-16 | 0.084473 | 0.084473 | -2.4713
2011-09-17 | 0.64507 | 0.64507 | -0.4384
2011-09-18 | 0.18991 | 0.18991 | -1.6612
2011-09-19 | 1.766 | 1.766 | 0.56872
2011-09-20 | 1.004 | 1.004 | 0.0039995
2011-09-21 | 0.55512 | 0.55512 | -0.58857
2011-09-22 | 0.5695 | 0.5695 | -0.563
2011-09-23 | 0.44813 | 0.44813 | -0.80267
2011-09-24 | 0.13517 | 0.13517 | -2.0013
2011-09-25 | 0.04613 | 0.04613 | -3.0763
2011-09-26 | 0.37247 | 0.37247 | -0.98759
2011-09-27 | 0.056115 | 0.056115 | -2.8803
2011-09-28 | 1.5873 | 1.5873 | 0.46206
2011-09-29 | 4.827 | 4.827 | 1.5742
2011-09-30 | 0.27616 | 0.27616 | -1.2868
2011-10-01 | 0.30183 | 0.30183 | -1.1979
2011-10-02 | 0.10867 | 0.10867 | -2.2195
2011-10-03 | 0.1058 | 0.1058 | -2.2462
2011-10-04 | 0.24288 | 0.24288 | -1.4152
2011-10-05 | 0.1536 | 0.1536 | -1.8734
2011-10-06 | 0.094931 | 0.094931 | -2.3546
2011-10-07 | 0.035965 | 0.035965 | -3.3252
2011-10-08 | 0.17816 | 0.17816 | -1.7251
2011-10-09 | 0.23858 | 0.23858 | -1.4331
2011-10-10 | 0.16937 | 0.16937 | -1.7756
2011-10-11 | 0.43146 | 0.43146 | -0.84058
2011-10-12 | 0.22696 | 0.22696 | -1.483
2011-10-13 | 0.045015 | 0.045015 | -3.1008
2011-10-14 | 0.085881 | 0.085881 | -2.4548
2011-10-15 | 0.61271 | 0.61271 | -0.48987
2011-10-16 | 0.15877 | 0.15877 | -1.8403
2011-10-17 | 0.074875 | 0.074875 | -2.5919
2011-10-18 | 0.21563 | 0.21563 | -1.5342
2011-10-19 | 0.095011 | 0.095011 | -2.3538
2011-10-20 | 0.033853 | 0.033853 | -3.3857
2011-10-21 | 0.23591 | 0.23591 | -1.4443
2011-10-22 | 0.31242 | 0.31242 | -1.1634
2011-10-23 | 0.26004 | 0.26004 | -1.3469
2011-10-24 | 0.64893 | 0.64893 | -0.43243
2011-10-25 | 0.065046 | 0.065046 | -2.7327
2011-10-26 | 0.016249 | 0.016249 | -4.1197
2011-10-27 | 0.18916 | 0.18916 | -1.6652
2011-10-28 | 0.60676 | 0.60676 | -0.49963
2011-10-29 | 0.21697 | 0.21697 | -1.528
2011-10-30 | 0.43469 | 0.43469 | -0.83312
2011-10-31 | 0.031039 | 0.031039 | -3.4725
2011-11-01 | 0.037278 | 0.037278 | -3.2894
2011-11-02 | 0.071031 | 0.071031 | -2.6446
2011-11-03 | 0.074249 | 0.074249 | -2.6003
2011-11-04 | 0.012985 | 0.012985 | -4.344
2011-11-05 | 0.56531 | 0.56531 | -0.57039
2011-11-06 | 0.17397 | 0.17397 | -1.7489
2011-11-07 | 0.027621 | 0.027621 | -3.5892
2011-11-08 | 1.1562 | 1.1562 | 0.14511
2011-11-09 | 2.6352 | 2.6352 | 0.96896
2011-11-10 | 0.56441 | 0.56441 | -0.57197
2011-11-11 | 0.3052 | 0.3052 | -1.1868
2011-11-12 | 0.43238 | 0.43238 | -0.83845
2011-11-13 | 0.26502 | 0.26502 | -1.3279
2011-11-14 | 0.19364 | 0.19364 | -1.6418
2011-11-15 | 0.019059 | 0.019059 | -3.9602
2011-11-16 | 0.12824 | 0.12824 | -2.0538
2011-11-17 | 0.064698 | 0.064698 | -2.738
2011-11-18 | 6.8728 | 6.8728 | 1.9276
2011-11-19 | 0.75166 | 0.75166 | -0.28547
2011-11-20 | 0.059852 | 0.059852 | -2.8159
2011-11-21 | 0.13521 | 0.13521 | -2.0009
2011-11-22 | 0.11394 | 0.11394 | -2.172
2011-11-23 | 0.25538 | 0.25538 | -1.365
2011-11-24 | 0.047864 | 0.047864 | -3.0394
2011-11-25 | 0.077467 | 0.077467 | -2.5579
2011-11-26 | 1.3251 | 1.3251 | 0.28151
2011-11-27 | 2.1184 | 2.1184 | 0.75068
2011-11-28 | 0.10265 | 0.10265 | -2.2764
2011-11-29 | 1.0716 | 1.0716 | 0.069115
2011-11-30 | 0.5784 | 0.5784 | -0.54749
2011-12-01 | 0.12803 | 0.12803 | -2.0555
2011-12-02 | 1.1543 | 1.1543 | 0.14349
2011-12-03 | 0.03177 | 0.03177 | -3.4492
2011-12-04 | 0.076239 | 0.076239 | -2.5739
2011-12-05 | 0.19923 | 0.19923 | -1.6133
2011-12-06 | 0.73709 | 0.73709 | -0.30504
2011-12-07 | 0.11889 | 0.11889 | -2.1295
2011-12-08 | 0.30632 | 0.30632 | -1.1831
2011-12-09 | 0.34649 | 0.34649 | -1.0599
2011-12-10 | 1.0908 | 1.0908 | 0.086913
2011-12-11 | 0.3372 | 0.3372 | -1.0871
2011-12-12 | 0.32724 | 0.32724 | -1.1171
2011-12-13 | 0.2372 | 0.2372 | -1.4388
2011-12-14 | 0.47602 | 0.47602 | -0.7423
2011-12-15 | 0.17113 | 0.17113 | -1.7653
2011-12-16 | 0.19633 | 0.19633 | -1.628
2011-12-17 | 0.067439 | 0.067439 | -2.6965
2011-12-18 | 0.030023 | 0.030023 | -3.5058
2011-12-19 | 0.17821 | 0.17821 | -1.7248
2011-12-20 | 0.16202 | 0.16202 | -1.82
2011-12-21 | 0.089489 | 0.089489 | -2.4136
2011-12-22 | 0.075148 | 0.075148 | -2.5883
2011-12-23 | 0.031108 | 0.031108 | -3.4703
2011-12-24 | 0.58589 | 0.58589 | -0.53463
2011-12-25 | 10.4633 | 10.4633 | 2.3479
2011-12-26 | 1.0079 | 1.0079 | 0.0078196
2011-12-27 | 0.10943 | 0.10943 | -2.2125
2011-12-28 | 0.73765 | 0.73765 | -0.30429
2011-12-29 | 0.058177 | 0.058177 | -2.8443
2011-12-30 | 0.11349 | 0.11349 | -2.176
2011-12-31 | 0.049044 | 0.049044 | -3.015
2012-01-01 | 0.61008 | 0.61008 | -0.49417
2012-01-02 | 0.79762 | 0.79762 | -0.22612
2012-01-03 | 0.38053 | 0.38053 | -0.96619
2012-01-04 | 0.42452 | 0.42452 | -0.85679
2012-01-05 | 0.16122 | 0.16122 | -1.825
2012-01-06 | 0.66592 | 0.66592 | -0.40659
2012-01-07 | 0.071063 | 0.071063 | -2.6442
2012-01-08 | 0.19544 | 0.19544 | -1.6325
2012-01-09 | 0.081974 | 0.081974 | -2.5014
2012-01-10 | 0.12438 | 0.12438 | -2.0844
2012-01-11 | 5.9069 | 5.9069 | 1.7761
2012-01-12 | 0.11392 | 0.11392 | -2.1723
2012-01-13 | 0.25333 | 0.25333 | -1.373
2012-01-14 | 0.0052722 | 0.0052722 | -5.2453
2012-01-15 | 0.34951 | 0.34951 | -1.0512
2012-01-16 | 0.28085 | 0.28085 | -1.2699
2012-01-17 | 0.29287 | 0.29287 | -1.228
2012-01-18 | 0.10013 | 0.10013 | -2.3012
2012-01-19 | 0.30351 | 0.30351 | -1.1924
2012-01-20 | 0.12169 | 0.12169 | -2.1062
2012-01-21 | 0.22178 | 0.22178 | -1.5061
2012-01-22 | 0.446 | 0.446 | -0.80744
2012-01-23 | 0.074522 | 0.074522 | -2.5967
2012-01-24 | 0.025741 | 0.025741 | -3.6597
2012-01-25 | 0.37959 | 0.37959 | -0.96866
2012-01-26 | 0.14416 | 0.14416 | -1.9368
2012-01-27 | 0.27444 | 0.27444 | -1.293
2012-01-28 | 0.080929 | 0.080929 | -2.5142
2012-01-29 | 1.0454 | 1.0454 | 0.044434
2012-01-30 | 0.91796 | 0.91796 | -0.085598
2012-01-31 | 0.15751 | 0.15751 | -1.8483
2012-02-01 | 0.010768 | 0.010768 | -4.5312
2012-02-02 | 0.046729 | 0.046729 | -3.0634
2012-02-03 | 0.08813 | 0.08813 | -2.4289
2012-02-04 | 0.08585 | 0.08585 | -2.4552
2012-02-05 | 10.7243 | 10.7243 | 2.3725
2012-02-06 | 0.58399 | 0.58399 | -0.53787
2012-02-07 | 0.045053 | 0.045053 | -3.0999
2012-02-08 | 0.066208 | 0.066208 | -2.715
2012-02-09 | 0.32858 | 0.32858 | -1.113
2012-02-10 | 0.50926 | 0.50926 | -0.67479
2012-02-11 | 0.68116 | 0.68116 | -0.38396
2012-02-12 | 0.051598 | 0.051598 | -2.9643
2012-02-13 | 0.21004 | 0.21004 | -1.5605
2012-02-14 | 0.13177 | 0.13177 | -2.0267
2012-02-15 | 0.44799 | 0.44799 | -0.80298
2012-02-16 | 3.1949 | 3.1949 | 1.1616
2012-02-17 | 0.26272 | 0.26272 | -1.3367
2012-02-18 | 0.094789 | 0.094789 | -2.3561
2012-02-19 | 0.15182 | 0.15182 | -1.8851
2012-02-20 | 0.083004 | 0.083004 | -2.4889
2012-02-21 | 0.073041 | 0.073041 | -2.6167
2012-02-22 | 0.2326 | 0.2326 | -1.4584
2012-02-23 | 0.10062 | 0.10062 | -2.2964
2012-02-24 | 0.70605 | 0.70605 | -0.34807
2012-02-25 | 0.15356 | 0.15356 | -1.8737
2012-02-26 | 0.13564 | 0.13564 | -1.9978
2012-02-27 | 0.60265 | 0.60265 | -0.50642
2012-02-28 | 0.10178 | 0.10178 | -2.285
2012-02-29 | 0.17331 | 0.17331 | -1.7527
2012-03-01 | 1.5121 | 1.5121 | 0.41349
2012-03-02 | 1.675 | 1.675 | 0.51579
2012-03-03 | 0.22926 | 0.22926 | -1.4729
2012-03-04 | 0.36911 | 0.36911 | -0.99665
2012-03-05 | 0.48962 | 0.48962 | -0.71412
2012-03-06 | 0.19697 | 0.19697 | -1.6247
2012-03-07 | 0.35723 | 0.35723 | -1.0294
2012-03-08 | 0.14229 | 0.14229 | -1.9499
2012-03-09 | 0.17653 | 0.17653 | -1.7343
2012-03-10 | 0.032888 | 0.032888 | -3.4147
2012-03-11 | 0.043949 | 0.043949 | -3.1247
2012-03-12 | 0.12491 | 0.12491 | -2.0802
2012-03-13 | 0.97732 | 0.97732 | -0.022945
2012-03-14 | 1.6459 | 1.6459 | 0.49827
2012-03-15 | 0.61015 | 0.61015 | -0.49405
2012-03-16 | 0.74675 | 0.74675 | -0.29202
2012-03-17 | 0.027188 | 0.027188 | -3.605
2012-03-18 | 0.025836 | 0.025836 | -3.656
2012-03-19 | 0.15651 | 0.15651 | -1.8546
2012-03-20 | 0.11696 | 0.11696 | -2.1459
2012-03-21 | 0.17705 | 0.17705 | -1.7313
2012-03-22 | 0.10337 | 0.10337 | -2.2695
2012-03-23 | 1.0459 | 1.0459 | 0.044888
2012-03-24 | 0.13389 | 0.13389 | -2.0107
2012-03-25 | 0.031973 | 0.031973 | -3.4428
2012-03-26 | 0.11263 | 0.11263 | -2.1837
2012-03-27 | 0.049279 | 0.049279 | -3.0103
2012-03-28 | 0.074271 | 0.074271 | -2.6
2012-03-29 | 0.12707 | 0.12707 | -2.063
2012-03-30 | 0.2356 | 0.2356 | -1.4456
2012-03-31 | 0.36233 | 0.36233 | -1.0152
2012-04-01 | 0.032895 | 0.032895 | -3.4144
2012-04-02 | 0.39439 | 0.39439 | -0.9304
2012-04-03 | 0.20926 | 0.20926 | -1.5642
2012-04-04 | 0.021286 | 0.021286 | -3.8497
2012-04-05 | 0.050605 | 0.050605 | -2.9837
2012-04-06 | 2.5563 | 2.5563 | 0.93857
2012-04-07 | 0.53168 | 0.53168 | -0.63171
2012-04-08 | 0.32368 | 0.32368 | -1.128
2012-04-09 | 0.23846 | 0.23846 | -1.4336
2012-04-10 | 0.033996 | 0.033996 | -3.3815
2012-04-11 | 0.010875 | 0.010875 | -4.5213
2012-04-12 | 0.045687 | 0.045687 | -3.0859
2012-04-13 | 0.054634 | 0.054634 | -2.9071
2012-04-14 | 0.026344 | 0.026344 | -3.6365
2012-04-15 | 0.37048 | 0.37048 | -0.99296
2012-04-16 | 0.14175 | 0.14175 | -1.9537
2012-04-17 | 0.086253 | 0.086253 | -2.4505
2012-04-18 | 0.13149 | 0.13149 | -2.0288
2012-04-19 | 0.0091836 | 0.0091836 | -4.6903
2012-04-20 | 0.22213 | 0.22213 | -1.5045
2012-04-21 | 0.40025 | 0.40025 | -0.91566
2012-04-22 | 0.26166 | 0.26166 | -1.3407
2012-04-23 | 0.43226 | 0.43226 | -0.83873
2012-04-24 | 0.10878 | 0.10878 | -2.2184
2012-04-25 | 0.31843 | 0.31843 | -1.1444
2012-04-26 | 0.31537 | 0.31537 | -1.154
2012-04-27 | 0.55423 | 0.55423 | -0.59017
2012-04-28 | 0.025008 | 0.025008 | -3.6886
2012-04-29 | 0.014992 | 0.014992 | -4.2003
2012-04-30 | 0.02313 | 0.02313 | -3.7666
2012-05-01 | 0.028321 | 0.028321 | -3.5642
2012-05-02 | 0.22391 | 0.22391 | -1.4965
2012-05-03 | 0.17741 | 0.17741 | -1.7293
2012-05-04 | 1.3595 | 1.3595 | 0.3071
2012-05-05 | 0.56763 | 0.56763 | -0.56628
2012-05-06 | 0.041116 | 0.041116 | -3.1914
2012-05-07 | 0.029369 | 0.029369 | -3.5278
2012-05-08 | 0.10162 | 0.10162 | -2.2865
2012-05-09 | 0.052656 | 0.052656 | -2.944
2012-05-10 | 0.041984 | 0.041984 | -3.1705
2012-05-11 | 0.023974 | 0.023974 | -3.7308
2012-05-12 | 0.11513 | 0.11513 | -2.1617
2012-05-13 | 0.82663 | 0.82663 | -0.1904
2012-05-14 | 0.024337 | 0.024337 | -3.7158
2012-05-15 | 0.22389 | 0.22389 | -1.4966
2012-05-16 | 0.13628 | 0.13628 | -1.9931
2012-05-17 | 0.14495 | 0.14495 | -1.9314
2012-05-18 | 0.01396 | 0.01396 | -4.2715
2012-05-19 | 0.020011 | 0.020011 | -3.9115
2012-05-20 | 0.34873 | 0.34873 | -1.0535
2012-05-21 | 0.072005 | 0.072005 | -2.631
2012-05-22 | 0.084148 | 0.084148 | -2.4752
2012-05-23 | 0.20155 | 0.20155 | -1.6017
2012-05-24 | 0.2017 | 0.2017 | -1.601
2012-05-25 | 6.5817 | 6.5817 | 1.8843
2012-05-26 | 0.44188 | 0.44188 | -0.81671
2012-05-27 | 0.015934 | 0.015934 | -4.1393
2012-05-28 | 0.49944 | 0.49944 | -0.69427
2012-05-29 | 0.12143 | 0.12143 | -2.1084
2012-05-30 | 0.024823 | 0.024823 | -3.696
2012-05-31 | 0.12479 | 0.12479 | -2.0811
2012-06-01 | 0.16578 | 0.16578 | -1.7971
2012-06-02 | 0.49426 | 0.49426 | -0.7047
2012-06-03 | 0.11122 | 0.11122 | -2.1963
2012-06-04 | 22.4567 | 22.4567 | 3.1116
2012-06-05 | 5.9997 | 5.9997 | 1.7917
2012-06-06 | 0.53852 | 0.53852 | -0.61893
2012-06-07 | 0.1419 | 0.1419 | -1.9527
2012-06-08 | 0.43868 | 0.43868 | -0.82397
2012-06-09 | 0.66901 | 0.66901 | -0.40196
2012-06-10 | 0.28047 | 0.28047 | -1.2713
2012-06-11 | 0.16715 | 0.16715 | -1.7888
2012-06-12 | 0.17421 | 0.17421 | -1.7475
2012-06-13 | 0.13862 | 0.13862 | -1.976
2012-06-14 | 0.19193 | 0.19193 | -1.6506
2012-06-15 | 0.74312 | 0.74312 | -0.2969
2012-06-16 | 0.012025 | 0.012025 | -4.4207
2012-06-17 | 0.02005 | 0.02005 | -3.9095
2012-06-18 | 0.17289 | 0.17289 | -1.7551
2012-06-19 | 0.23589 | 0.23589 | -1.4444
2012-06-20 | 1.483 | 1.483 | 0.39404
2012-06-21 | 1.0719 | 1.0719 | 0.069389
2012-06-22 | 0.22115 | 0.22115 | -1.5089
2012-06-23 | 0.051254 | 0.051254 | -2.971
2012-06-24 | 0.033039 | 0.033039 | -3.4101
2012-06-25 | 0.077792 | 0.077792 | -2.5537
2012-06-26 | 0.022907 | 0.022907 | -3.7763
2012-06-27 | 0.047825 | 0.047825 | -3.0402
2012-06-28 | 0.079844 | 0.079844 | -2.5277
2012-06-29 | 0.2212 | 0.2212 | -1.5087
2012-06-30 | 0.59501 | 0.59501 | -0.51917
2012-07-01 | 0.39436 | 0.39436 | -0.93048
2012-07-02 | 0.30947 | 0.30947 | -1.1729
2012-07-03 | 0.25722 | 0.25722 | -1.3578
2012-07-04 | 0.11353 | 0.11353 | -2.1757
2012-07-05 | 0.026869 | 0.026869 | -3.6168
2012-07-06 | 0.024332 | 0.024332 | -3.716
2012-07-07 | 0.0092498 | 0.0092498 | -4.6831
2012-07-08 | 0.042901 | 0.042901 | -3.1489
2012-07-09 | 0.10433 | 0.10433 | -2.2602
2012-07-10 | 0.18154 | 0.18154 | -1.7063
2012-07-11 | 0.24963 | 0.24963 | -1.3878
2012-07-12 | 0.078021 | 0.078021 | -2.5508
2012-07-13 | 0.097312 | 0.097312 | -2.3298
2012-07-14 | 0.016158 | 0.016158 | -4.1253
2012-07-15 | 0.14359 | 0.14359 | -1.9408
2012-07-16 | 0.020044 | 0.020044 | -3.9098
2012-07-17 | 0.29507 | 0.29507 | -1.2205
2012-07-18 | 0.001995 | 0.001995 | -6.2171
2012-07-19 | 1.0856 | 1.0856 | 0.082163
2012-07-20 | 0.16314 | 0.16314 | -1.8132
2012-07-21 | 0.098098 | 0.098098 | -2.3218
2012-07-22 | 0.13869 | 0.13869 | -1.9755
2012-07-23 | 0.069017 | 0.069017 | -2.6734
2012-07-24 | 0.023955 | 0.023955 | -3.7316
2012-07-25 | 0.32213 | 0.32213 | -1.1328
2012-07-26 | 0.16091 | 0.16091 | -1.8269
2012-07-27 | 0.082443 | 0.082443 | -2.4956
2012-07-28 | 0.17724 | 0.17724 | -1.7302
2012-07-29 | 0.0045734 | 0.0045734 | -5.3875
2012-07-30 | 0.02372 | 0.02372 | -3.7415
2012-07-31 | 1.2086 | 0.074137 | -2.6018 | < Excluded transmission event.
2012-08-01 | 0.059517 | 0.059517 | -2.8215
2012-08-02 | 0.29401 | 0.29401 | -1.2241
2012-08-03 | 0.17131 | 0.17131 | -1.7643
2012-08-04 | 0.29135 | 0.29135 | -1.2332
2012-08-05 | 0.80297 | 0.80297 | -0.21944
2012-08-06 | 0.19976 | 0.19976 | -1.6107
2012-08-07 | 0.20469 | 0.20469 | -1.5862
2012-08-08 | 0.32791 | 0.32791 | -1.115
2012-08-09 | 0.53997 | 0.53997 | -0.61623
2012-08-10 | 1.1475 | 1.1475 | 0.13759
2012-08-11 | 0.25289 | 0.25289 | -1.3748
2012-08-12 | 0.11743 | 0.11743 | -2.1419
2012-08-13 | 0.035595 | 0.035595 | -3.3355
2012-08-14 | 0.45711 | 0.45711 | -0.78283
2012-08-15 | 0.15318 | 0.15318 | -1.8761
2012-08-16 | 0.06623 | 0.06623 | -2.7146
2012-08-17 | 0.1112 | 0.1112 | -2.1964
2012-08-18 | 0.55558 | 0.55558 | -0.58775
2012-08-19 | 0.024435 | 0.024435 | -3.7117
2012-08-20 | 0.10217 | 0.10217 | -2.2811
2012-08-21 | 0.57018 | 0.57018 | -0.56181
2012-08-22 | 0.19942 | 0.19942 | -1.6124
2012-08-23 | 0.42986 | 0.42986 | -0.84429
2012-08-24 | 0.20234 | 0.20234 | -1.5978
2012-08-25 | 0.078175 | 0.078175 | -2.5488
2012-08-26 | 0.010113 | 0.010113 | -4.5939
2012-08-27 | 0.062255 | 0.062255 | -2.7765
2012-08-28 | 0.061618 | 0.061618 | -2.7868
2012-08-29 | 0.3794 | 0.3794 | -0.96916
2012-08-30 | 0.68221 | 0.68221 | -0.38242
2012-08-31 | 0.31707 | 0.31707 | -1.1486
2012-09-01 | 0.014151 | 0.014151 | -4.258
2012-09-02 | 0.25354 | 0.25354 | -1.3722
2012-09-03 | 0.028604 | 0.028604 | -3.5542
2012-09-04 | 0.95416 | 0.95416 | -0.046925
2012-09-05 | 71.9293 | 71.9293 | 4.2757
2012-09-06 | 8.9397 | 8.9397 | 2.1905
2012-09-07 | 2.6191 | 2.6191 | 0.96285
2012-09-08 | 0.39526 | 0.39526 | -0.9282
2012-09-09 | 0.31855 | 0.31855 | -1.144
2012-09-10 | 0.058978 | 0.058978 | -2.8306
2012-09-11 | 0.13212 | 0.13212 | -2.0241
2012-09-12 | 0.48701 | 0.48701 | -0.71947
2012-09-13 | 0.33755 | 0.33755 | -1.086
2012-09-14 | 0.19698 | 0.19698 | -1.6247
2012-09-15 | 0.083633 | 0.083633 | -2.4813
2012-09-16 | 0.10691 | 0.10691 | -2.2358
2012-09-17 | 0.11001 | 0.11001 | -2.2072
2012-09-18 | 0.21631 | 0.21631 | -1.531
2012-09-19 | 0.10821 | 0.10821 | -2.2236
2012-09-20 | 0.2418 | 0.2418 | -1.4196
2012-09-21 | 0.064573 | 0.064573 | -2.74
2012-09-22 | 0.3797 | 0.3797 | -0.96838
2012-09-23 | 0.076205 | 0.076205 | -2.5743
2012-09-24 | 0.36757 | 0.36757 | -1.0009
2012-09-25 | 0.02184 | 0.02184 | -3.824
2012-09-26 | 0.31174 | 0.31174 | -1.1656
2012-09-27 | 0.93644 | 0.93644 | -0.065665
2012-09-28 | 0.83439 | 0.83439 | -0.18105
2012-09-29 | 0.21927 | 0.21927 | -1.5175
2012-09-30 | 0.19499 | 0.19499 | -1.6348
2012-10-01 | 0.10949 | 0.10949 | -2.2119
2012-10-02 | 0.27327 | 0.27327 | -1.2973
2012-10-03 | 0.30583 | 0.30583 | -1.1847
2012-10-04 | 0.38262 | 0.38262 | -0.96072
2012-10-05 | 0.28507 | 0.28507 | -1.255
2012-10-06 | 0.024679 | 0.024679 | -3.7018
2012-10-07 | 0.20675 | 0.20675 | -1.5762
2012-10-08 | 0.033851 | 0.033851 | -3.3858
2012-10-09 | 0.55755 | 0.55755 | -0.58419
2012-10-10 | 0.091461 | 0.091461 | -2.3918
2012-10-11 | 0.11971 | 0.11971 | -2.1227
2012-10-12 | 0.10643 | 0.10643 | -2.2403
2012-10-13 | 0.032155 | 0.032155 | -3.4372
2012-10-14 | 0.08063 | 0.08063 | -2.5179
2012-10-15 | 0.094536 | 0.094536 | -2.3588
2012-10-16 | 0.43707 | 0.43707 | -0.82765
2012-10-17 | 0.025932 | 0.025932 | -3.6523
2012-10-18 | 0.041988 | 0.041988 | -3.1704
2012-10-19 | 0.17685 | 0.17685 | -1.7324
2012-10-20 | 0.054922 | 0.054922 | -2.9018
2012-10-21 | 1.2882 | 1.2882 | 0.25327
2012-10-22 | 0.51611 | 0.51611 | -0.66143
2012-10-23 | 0.26701 | 0.26701 | -1.3205
2012-10-24 | 0.44388 | 0.44388 | -0.81219
2012-10-25 | 0.47729 | 0.47729 | -0.73963
2012-10-26 | 0.048246 | 0.048246 | -3.0314
2012-10-27 | 0.25176 | 0.25176 | -1.3793
2012-10-28 | 0.052568 | 0.052568 | -2.9456
2012-10-29 | 0.10432 | 0.10432 | -2.2603
2012-10-30 | 0.14308 | 0.14308 | -1.9443
2012-10-31 | 0.20667 | 0.20667 | -1.5766
2012-11-01 | 1.4093 | 1.4093 | 0.34307
2012-11-02 | 0.57621 | 0.57621 | -0.55128
2012-11-03 | 2.5817 | 2.5817 | 0.94846
2012-11-04 | 0.055904 | 0.055904 | -2.8841
2012-11-05 | 0.10685 | 0.10685 | -2.2364
2012-11-06 | 0.36031 | 0.36031 | -1.0208
2012-11-07 | 0.33196 | 0.33196 | -1.1027
2012-11-08 | 0.88736 | 0.88736 | -0.11951
2012-11-09 | 0.031224 | 0.031224 | -3.4666
2012-11-10 | 0.14883 | 0.14883 | -1.9049
2012-11-11 | 0.14701 | 0.14701 | -1.9173
2012-11-12 | 0.73311 | 0.73311 | -0.31046
2012-11-13 | 0.11441 | 0.11441 | -2.168
2012-11-14 | 1.1828 | 1.1828 | 0.16791
2012-11-15 | 0.17776 | 0.17776 | -1.7273
2012-11-16 | 0.020144 | 0.020144 | -3.9049
2012-11-17 | 0.18034 | 0.18034 | -1.7129
2012-11-18 | 0.068098 | 0.068098 | -2.6868
2012-11-19 | 0.69519 | 0.69519 | -0.36357
2012-11-20 | 0.12134 | 0.12134 | -2.1091
2012-11-21 | 0.015669 | 0.015669 | -4.1561
2012-11-22 | 1.2839 | 1.2839 | 0.24989
2012-11-23 | 0.072544 | 0.072544 | -2.6236
2012-11-24 | 0.34598 | 0.34598 | -1.0614
2012-11-25 | 0.088496 | 0.088496 | -2.4248
2012-11-26 | 0.21585 | 0.21585 | -1.5332
2012-11-27 | 0.80817 | 0.80817 | -0.21299
2012-11-28 | 0.17513 | 0.17513 | -1.7422
2012-11-29 | 0.54209 | 0.54209 | -0.61232
2012-11-30 | 0.1241 | 0.1241 | -2.0867
2012-12-01 | 0.36946 | 0.36946 | -0.99572
2012-12-02 | 0.17338 | 0.17338 | -1.7523
2012-12-03 | 0.18378 | 0.18378 | -1.694
2012-12-04 | 0.56343 | 0.56343 | -0.57371
2012-12-05 | 0.51502 | 0.51502 | -0.66355
2012-12-06 | 0.013739 | 0.013739 | -4.2876
2012-12-07 | 0.07797 | 0.07797 | -2.5514
2012-12-08 | 0.45482 | 0.45482 | -0.78785
2012-12-09 | 0.11373 | 0.11373 | -2.1739
2012-12-10 | 0.064958 | 0.064958 | -2.734
2012-12-11 | 0.062532 | 0.062532 | -2.7721
2012-12-12 | 0.022339 | 0.022339 | -3.8014
2012-12-13 | 0.54363 | 0.54363 | -0.60949
2012-12-14 | 0.084876 | 0.084876 | -2.4666
2012-12-15 | 1.4849 | 1.4849 | 0.39536
2012-12-16 | 0.3676 | 0.3676 | -1.0008
2012-12-17 | 0.23861 | 0.23861 | -1.4329
2012-12-18 | 0.048983 | 0.048983 | -3.0163
2012-12-19 | 0.027255 | 0.027255 | -3.6025
2012-12-20 | 0.5627 | 0.5627 | -0.575
2012-12-21 | 0.10103 | 0.10103 | -2.2924
2012-12-22 | 0.052847 | 0.052847 | -2.9404
2012-12-23 | 0.57789 | 0.57789 | -0.54836
2012-12-24 | 1.5937 | 1.5937 | 0.46607
2012-12-25 | 0.042438 | 0.042438 | -3.1597
2012-12-26 | 0.078618 | 0.078618 | -2.5432
2012-12-27 | 0.30214 | 0.30214 | -1.1969
2012-12-28 | 0.067929 | 0.067929 | -2.6893
2012-12-29 | 0.064636 | 0.064636 | -2.739
2012-12-30 | 0.23046 | 0.23046 | -1.4677
2012-12-31 | 0.020073 | 0.020073 | -3.9084
Note:
Exclusions refer to upstream events only and do not refer MED exclusions.
MED calculation starts from 5 years prior to the relevant regulatory reporting year (e.g. 2013 requires data from 1 January 2008 to 31 December 2012).
Contents

## 1e. STPIS Exclusions (hidden)
SP AusNet
STPIS Data Reporting
2013
Exclusions
Table 1: Exclusions
Date of event (DD/MM/YYYY) | Feeder ID / name | Feeder classification | Number of interruptions (unplanned) | Duration of interruption (unplanned) (mins) | Total unplanned minutes off supply | Event category (use Exclusion categories listed in section 3.3 (a) of the AER's STPIS) | Effect on unplanned SAIDI | Effect on unplanned SAIFI | Effect on unplaned MAIFI | Please provide separate explanation to confirm the outage was not due to inadequate transmission connection planning | Cause of event (Use categories listed in table 1, Template 6C)
2013-02-12 | RWT11 | URBAN | 2431 | 16.3332 | 39706 | 5 | 0.06014 | 0.0036821 | 0 | RWTS 22kV bus inadvertently tripped due to planned transmission works. | Transmission failure
2013-02-12 | RWT14 | URBAN | 734 | 10 | 7340 | 5 | 0.011117 | 0.0011117 | 0 | RWTS 22kV bus inadvertently tripped due to planned transmission works. | Transmission failure
2013-02-12 | RWT15 | URBAN | 2547 | 23.4888 | 59826 | 5 | 0.090614 | 0.0038578 | 0 | RWTS 22kV bus inadvertently tripped due to planned transmission works. | Transmission failure
2013-02-12 | RWT21 | URBAN | 2477 | 8.6346 | 21388 | 5 | 0.032395 | 0.0037517 | 0 | RWTS 22kV bus inadvertently tripped due to planned transmission works. | Transmission failure
2013-02-12 | RWT22 | URBAN | 3742 | 8.229 | 30793 | 5 | 0.04664 | 0.0056677 | 0 | RWTS 22kV bus inadvertently tripped due to planned transmission works. | Transmission failure
2013-02-12 | RWT25 | URBAN | 1266 | 18.3981 | 23292 | 5 | 0.035279 | 0.0019175 | 0 | RWTS 22kV bus inadvertently tripped due to planned transmission works. | Transmission failure
2013-02-12 | RWT26 | URBAN | 1106 | 80.1627 | 88660 | 5 | 0.13429 | 0.0016752 | 0 | RWTS 22kV bus inadvertently tripped due to planned transmission works. | Transmission failure
2013-02-12 | RWT29 | URBAN | 1 | 86 | 86 | 5 | 0.00013026 | 1.5146e-06 | 0 | RWTS 22kV bus inadvertently tripped due to planned transmission works. | Transmission failure
2013-07-25 | BN1 | LONG RURAL | 4413 | 1.0059 | 4439 | 5 | 0.0067234 | 0.006684 | 0 | GNTS No2 220/66kV bus inadvertently tripped due to planned transmission works. | Transmission failure
2013-07-25 | BN2 | LONG RURAL | 1099 | 1 | 1099 | 5 | 0.0016646 | 0.0016646 | 0 | GNTS No2 220/66kV bus inadvertently tripped due to planned transmission works. | Transmission failure
2013-07-25 | BN3 | SHORT RURAL | 646 | 1 | 646 | 5 | 0.00097845 | 0.00097845 | 0 | GNTS No2 220/66kV bus inadvertently tripped due to planned transmission works. | Transmission failure
2013-07-25 | BN4 | URBAN | 3320 | 1 | 3320 | 5 | 0.0050286 | 0.0050286 | 0 | GNTS No2 220/66kV bus inadvertently tripped due to planned transmission works. | Transmission failure
2013-07-25 | BN6 | LONG RURAL | 2300 | 1 | 2300 | 5 | 0.0034836 | 0.0034836 | 0 | GNTS No2 220/66kV bus inadvertently tripped due to planned transmission works. | Transmission failure
2013-07-25 | MJG11 | SHORT RURAL | 1335 | 1 | 1335 | 5 | 0.002022 | 0.002022 | 0 | GNTS No2 220/66kV bus inadvertently tripped due to planned transmission works. | Transmission failure
2013-07-25 | MSD1 | LONG RURAL | 1928 | 1 | 1928 | 5 | 0.0029202 | 0.0029202 | 0 | GNTS No2 220/66kV bus inadvertently tripped due to planned transmission works. | Transmission failure
2013-07-25 | MSD2 | LONG RURAL | 1599 | 1.0006 | 1600 | 5 | 0.0024234 | 0.0024219 | 0 | GNTS No2 220/66kV bus inadvertently tripped due to planned transmission works. | Transmission failure
2013-07-25 | MSD4 | LONG RURAL | 2417 | 1 | 2417 | 5 | 0.0036609 | 0.0036609 | 0 | GNTS No2 220/66kV bus inadvertently tripped due to planned transmission works. | Transmission failure
2013-07-25 | MYT1 | SHORT RURAL | 326 | 1 | 326 | 5 | 0.00049377 | 0.00049377 | 0 | GNTS No2 220/66kV bus inadvertently tripped due to planned transmission works. | Transmission failure
2013-07-25 | MYT2 | SHORT RURAL | 1722 | 1 | 1722 | 5 | 0.0026082 | 0.0026082 | 0 | GNTS No2 220/66kV bus inadvertently tripped due to planned transmission works. | Transmission failure
2013-07-25 | MYT7 | LONG RURAL | 2992 | 1 | 2992 | 5 | 0.0045318 | 0.0045318 | 0 | GNTS No2 220/66kV bus inadvertently tripped due to planned transmission works. | Transmission failure
2013-07-25 | MYT8 | SHORT RURAL | 687 | 1 | 687 | 5 | 0.0010405 | 0.0010405 | 0 | GNTS No2 220/66kV bus inadvertently tripped due to planned transmission works. | Transmission failure
2013-07-25 | WN1 | URBAN | 1556 | 1 | 1556 | 5 | 0.0023568 | 0.0023568 | 0 | GNTS No2 220/66kV bus inadvertently tripped due to planned transmission works. | Transmission failure
2013-07-25 | WN2 | LONG RURAL | 3292 | 1 | 3292 | 5 | 0.0049861 | 0.0049861 | 0 | GNTS No2 220/66kV bus inadvertently tripped due to planned transmission works. | Transmission failure
2013-07-25 | WN3 | LONG RURAL | 2804 | 1 | 2804 | 5 | 0.004247 | 0.004247 | 0 | GNTS No2 220/66kV bus inadvertently tripped due to planned transmission works. | Transmission failure
2013-07-25 | WN4 | SHORT RURAL | 2562 | 1 | 2562 | 5 | 0.0038805 | 0.0038805 | 0 | GNTS No2 220/66kV bus inadvertently tripped due to planned transmission works. | Transmission failure
2013-07-25 | WN5 | LONG RURAL | 2427 | 1 | 2427 | 5 | 0.003676 | 0.003676 | 0 | GNTS No2 220/66kV bus inadvertently tripped due to planned transmission works. | Transmission failure
2013-07-25 | WN6 | LONG RURAL | 4207 | 1 | 4207 | 5 | 0.006372 | 0.006372 | 0 | GNTS No2 220/66kV bus inadvertently tripped due to planned transmission works. | Transmission failure
2013-07-25 | WN7 | URBAN | 103 | 1 | 103 | 5 | 0.00015601 | 0.00015601 | 0 | GNTS No2 220/66kV bus inadvertently tripped due to planned transmission works. | Transmission failure
2013-11-21 | RWT22 | URBAN | 3760 | 3 | 11280 | 5 | 0.017085 | 0.005695 | 0 | RWTS No3 22kV bus tripped due to bus protection setting issue with Jemena RWT31 feeder. | Transmission failure
2013-11-21 | RWT25 | URBAN | 1271 | 3 | 3813 | 5 | 0.0057753 | 0.0019251 | 0 | RWTS No3 22kV bus tripped due to bus protection setting issue with Jemena RWT31 feeder. | Transmission failure
2013-11-21 | RWT36 | URBAN | 220 | 47 | 10340 | 5 | 0.015661 | 0.00033322 | 0 | RWTS No3 22kV bus tripped due to bus protection setting issue with Jemena RWT31 feeder. | Transmission failure
2013-12-07 | HPK11 | URBAN | 4043 | 6 | 24258 | 5 | 0.036742 | 0.0061236 | 0 | ERTS No 3 66KV bus tripped via protection following an incident related to planned transmission works inside ERTS. | Transmission failure
2013-12-07 | HPK12 | URBAN | 1544 | 6 | 9264 | 5 | 0.014031 | 0.0023386 | 0 | ERTS No 3 66KV bus tripped via protection following an incident related to planned transmission works inside ERTS. | Transmission failure
2013-12-07 | HPK13 | URBAN | 1935 | 6 | 11610 | 5 | 0.017585 | 0.0029308 | 0 | ERTS No 3 66KV bus tripped via protection following an incident related to planned transmission works inside ERTS. | Transmission failure
2013-12-07 | HPK14 | URBAN | 3975 | 6 | 23850 | 5 | 0.036124 | 0.0060206 | 0 | ERTS No 3 66KV bus tripped via protection following an incident related to planned transmission works inside ERTS. | Transmission failure
2013-12-07 | HPK21 | URBAN | 2936 | 6 | 17616 | 5 | 0.026682 | 0.0044469 | 0 | ERTS No 3 66KV bus tripped via protection following an incident related to planned transmission works inside ERTS. | Transmission failure
2013-12-07 | HPK22 | URBAN | 4103 | 6 | 24618 | 5 | 0.037287 | 0.0062145 | 0 | ERTS No 3 66KV bus tripped via protection following an incident related to planned transmission works inside ERTS. | Transmission failure
2013-12-07 | HPK23 | URBAN | 3060 | 6 | 18360 | 5 | 0.027809 | 0.0046348 | 0 | ERTS No 3 66KV bus tripped via protection following an incident related to planned transmission works inside ERTS. | Transmission failure
2013-12-07 | HPK24 | URBAN | 1447 | 6 | 8682 | 5 | 0.01315 | 0.0021917 | 0 | ERTS No 3 66KV bus tripped via protection following an incident related to planned transmission works inside ERTS. | Transmission failure
2013-01-04 | NLA31 | LONG RURAL | 365 | 103 | 37595 |  | 0.056942 | 0.00055284 | 0 | LE031 ACR tripped to lockout while reclose function is suppressed on TFB day. Line was surveyed but caused found. | TFB day outage
2013-01-04 | NLA31 | LONG RURAL | 82 | 260 | 21320 |  | 0.032292 | 0.0001242 | 0 | LE031 ACR tripped to lockout while reclose function is suppressed on TFB day. Line was surveyed but caused found. | TFB day outage
2013-01-04 | NLA31 | LONG RURAL | 15 | 428 | 6420 |  | 0.0097239 | 2.2719e-05 | 0 | LE031 ACR tripped to lockout while reclose function is suppressed on TFB day. Line was surveyed but caused found. | TFB day outage
2013-01-04 | NLA31 | LONG RURAL | 1 | 297 | 297 |  | 0.00044984 | 1.5146e-06 | 0 | LE031 ACR tripped to lockout while reclose function is suppressed on TFB day. Line was surveyed but caused found. | TFB day outage
2013-01-04 | NLA31 | LONG RURAL | 98 | 410 | 40180 |  | 0.060858 | 0.00014843 | 0 | LE031 ACR tripped to lockout while reclose function is suppressed on TFB day. Line was surveyed but caused found. | TFB day outage
2013-01-04 | NLA31 | LONG RURAL | 5 | 474 | 2370 |  | 0.0035897 | 7.5731e-06 | 0 | LE031 ACR tripped to lockout while reclose function is suppressed on TFB day. Line was surveyed but caused found. | TFB day outage
2013-01-04 | NLA31 | LONG RURAL | 6 | 466 | 2796 |  | 0.0042349 | 9.0878e-06 | 0 | LE031 ACR tripped to lockout while reclose function is suppressed on TFB day. Line was surveyed but caused found. | TFB day outage
2013-01-04 | NLA31 | LONG RURAL | 0 | 0 | 11680 |  | 0.017691 | 0 | 0 | LE031 ACR tripped to lockout while reclose function is suppressed on TFB day. Line was surveyed but caused found. | TFB day outage
2013-01-04 | NLA31 | LONG RURAL | 0 | 0 | 8760 |  | 0.013268 | 0 | 0 | LE031 ACR tripped to lockout while reclose function is suppressed on TFB day. Line was surveyed but caused found. | TFB day outage
2013-01-04 | NLA31 | LONG RURAL | 0 | 0 | 2050 |  | 0.003105 | 0 | 0 | LE031 ACR tripped to lockout while reclose function is suppressed on TFB day. Line was surveyed but caused found. | TFB day outage
2013-01-17 | KLK1 | SHORT RURAL | 71 | 185.0704 | 13140 |  | 0.019902 | 0.00010754 | 0 | HE224 ACR tripped to lockout while reclose function is suppressed on TFB day. Line was surveyed but caused found. | TFB day outage
2013-01-18 | MOE14 | SHORT RURAL | 454 | 234.0639 | 106265 |  | 0.16095 | 0.00068764 | 0 | MO002 ACR tripped to lockout while reclose function is suppressed on TFB day. Line was surveyed but caused found. | TFB day outage
2013-02-07 | WYK23 | SHORT RURAL | 2624 | 23.8171 | 62496 |  | 0.094658 | 0.0039744 | 0 | WT231 ACR tripped to lockout while reclose function is suppressed on TFB day. Line was surveyed but caused found. | TFB day outage
2013-02-07 | DRN12 | URBAN | 54 | 176.2037 | 9515 |  | 0.014412 | 8.179e-05 | 0 | GB1220 ACR tripped to lockout while reclose function is suppressed on TFB day. Line was surveyed but caused found. | TFB day outage
2013-03-27 | WGL12 | LONG RURAL | 225 | 206.0133 | 46353 |  | 0.070207 | 0.00034079 | 0 | BW1644 ACR tripped to lockout while reclose function is suppressed on TFB day. Line was surveyed but caused found. | TFB day outage
Note:
The AER's Electricity distribution network service providers, Service target performance incentive scheme, November 2009, p. 22, defines SAIDI and SAIFI.
The AER will apply the ESCV's definition of MAIFI for transitional reasons. The ESCV's Information specification (Service performance) for Victorian Electricity Distributors, 1 January 2009, p. 30, defines MAIFI as follows:
MAIFI - The total number of momentary interruptions divided by the average number of distribution customers over the regulatory reporting period. (where the distribution customers are network or per feeder based, as appropriate).
Contents

## 2. Demand (hidden)
SP AusNet
Demand
2013
THIS TEMPLATE NO LONGER REQUIRED BY AER (EMAIL FROM SCOTT HAIG TO TOM HALLAM 18/12/13)
Table 1 Customer Numbers by Voltage Level
Customer numbers by voltage level
Subtransmission
High Voltage
Low Voltage Residential
Low Voltage Non-Residential
Total - all customers | 0
Table 2 New Customer Connections
Note: 'Total customer numbers' is the total average of end of prior year customers and end of current year customers
New connections
Total new connections
New customer connections as a % of total customers | #DIV/0!
Table 3 Customer Disconnections
Note: 'Total customer numbers' is the total average of end of prior year customers and end of current year customers
Disconnections
Total disconnections
Disconnections as a % of total customers | #DIV/0!
Table 4 Electricity Consumption
Electricity consumption by voltage level (MWh)
Subtransmission
High Voltage
Low Voltage Residential
Low Voltage Non-Residential
Controlled load
Total consumption | 0
Table 5 Maximum Coincident Demand at the Network Level
Note: a) Maximum Coincident Demand at the Network Level is calculated as the sum of all maximum coincident demand for zone substations and all feeders from terminal stations.
b) Forecasts should be the demand forecasts for the relevant regulatory year that were made at the time of the regulatory proposal
c) t+1 forecasts should be the latest updates to the demand forecasts for the regulatory year t+1.
d) The PoE level only applies to the forecasts
Network coincident maximum demand |  |  |  |  | t+1 forecast
| Forecast | Actual: raw | Actual: weather normalised | Variation %
90% PoE level
Network coincident maximum demand (MW) |  |  |  | #DIV/0!
Network coincident maximum demand (MVA) |  |  |  | #DIV/0!
50% PoE level
Network coincident maximum demand (MW) |  |  |  | #DIV/0!
Network coincident maximum demand (MVA) |  |  |  | #DIV/0!
10% PoE level
Network coincident maximum demand (MW) |  |  |  | #DIV/0!
Network coincident maximum demand (MVA) |  |  |  | #DIV/0!
Table 6 Summer or winter non-coincident maximum demand by zone substation
Note: a) Forecasts should be the demand forecasts for the relevant regulatory year that were made at the time of the regulatory proposal
b) t+1 forecasts should be the latest updates to the demand forecasts for the regulatory year t+1.
c) The PoE level only applies to the forecasts
Summer and winter maximum demand - ZS | [12 empty] | t+1 forecast |  |  |  | Nameplate rating (MVA)
POE level = 50% | Forecast |  |  |  | Actual: raw |  |  |  | Actual: weather normalised
Location | MW | MVA | MVAr | PF | MW | MVA | MVAr | PF | MW | MVA | MVAr | PF | MW | MVA | MVAr | PF
<ZS 1> - Summer maximum demand |  |  |  | #DIV/0! |  |  |  | #DIV/0! |  |  |  | #DIV/0! |  |  |  | #DIV/0!
<ZS 1> - Winter maximum demand |  |  |  | #DIV/0! |  |  |  | #DIV/0! |  |  |  | #DIV/0! |  |  |  | #DIV/0!
<ZS 2> - Summer maximum demand |  |  |  | #DIV/0! |  |  |  | #DIV/0! |  |  |  | #DIV/0! |  |  |  | #DIV/0!
<ZS 2> - Winter maximum demand |  |  |  | #DIV/0! |  |  |  | #DIV/0! |  |  |  | #DIV/0! |  |  |  | #DIV/0!
<ZS 3> - Summer maximum demand |  |  |  | #DIV/0! |  |  |  | #DIV/0! |  |  |  | #DIV/0! |  |  |  | #DIV/0!
<ZS 3> - Winter maximum demand |  |  |  | #DIV/0! |  |  |  | #DIV/0! |  |  |  | #DIV/0! |  |  |  | #DIV/0!
<ZS n> - Summer maximum demand |  |  |  | #DIV/0! |  |  |  | #DIV/0! |  |  |  | #DIV/0! |  |  |  | #DIV/0!
<ZS n> - Winter maximum demand |  |  |  | #DIV/0! |  |  |  | #DIV/0! |  |  |  | #DIV/0! |  |  |  | #DIV/0!
Contents

## 3. Asset Installation (hidden)
SP AusNet
Asset Installation
2013
THIS TEMPLATE NO LONGER REQUIRED BY AER (EMAIL FROM SCOTT HAIG TO TOM HALLAM 18/12/13)
Instructions
Insert rows for each of its asset types under each high level asset group. Additional groups may be added if a particular asset is not encompassed by the asset groups in the table.
Develop a set of asset types under the high level asset groups that represent its network asset base.
In determining whether a new asset type is required, whether asset types should be aggregated or whether asset types should be disaggregated, the DNSP should consider:
- the proportion of the overall replacement expenditure forecast for the assets
- the differentiation of unit replacement costs into clear and distinguishable distributions
- the differentiation of replacement lives into clear and distinguishable distributions
- multiple 'end of life' actions such as 'replacement' or 'life extension' (eg pole staking) - in the case of 'life extension', the DNSP should appropriately account for this in defining the replacement life and unit cost for the asset category.
Table 1 For each asset type, provide:
a) the mean replacement asset life (years)
b) the standard deviation of the mean replacement asset life
c) the replacement unit cost ($ nominal).
d) the total number of asset failures during the regulatory year
e) the total quantity (number) of each asset type that was commissioned in the relevant regulatory reporting year.
Table 1 Asset age profile for distribution system assets
Statutory Account code or reference to account code | Asset group | Replacement life (years) |  | Replacement unit cost | Number of asset failures | Total quantity replaced | Total quantity installed | Year Commissioned (number of assets commissioned in each year)
|  | Mean | Standard Deviation |  |  |  |  | 1910 | 1911 | 1912 | 1913 | 1914 | 1915 | 1916 | 1917 | 1918 | 1919 | 1920 | 1921 | 1922 | 1923 | 1924 | 1925 | 1926 | 1927 | 1928 | 1929 | 1930 | 1931 | 1932 | 1933 | 1934 | 1935 | 1936 | 1937 | 1938 | 1939 | 1940 | 1941 | 1942 | 1943 | 1944 | 1945 | 1946 | 1947 | 1948 | 1949 | 1950 | 1951 | 1952 | 1953 | 1954 | 1955 | 1956 | 1957 | 1958 | 1959 | 1960 | 1961 | 1962 | 1963 | 1964 | 1965 | 1966 | 1967 | 1968 | 1969 | 1970 | 1971 | 1972 | 1973 | 1974 | 1975 | 1976 | 1977 | 1978 | 1979 | 1980 | 1981 | 1982 | 1983 | 1984 | 1985 | 1986 | 1987 | 1988 | 1989 | 1990 | 1991 | 1992 | 1993 | 1994 | 1995 | 1996 | 1997 | 1998 | 1999 | 2000 | 2001 | 2002 | 2003 | 2004 | 2005 | 2006 | 2007 | 2008 | 2009 | 2010 | 2011 | 2012
Poles
| <asset type 1> | [5 empty] | 0
| <asset type 2> | [5 empty] | 0
| <asset type 3> | [5 empty] | 0
Pole top structures
| <asset type 1> | [5 empty] | 0
| <asset type 2> | [5 empty] | 0
| <asset type 3> | [5 empty] | 0
Conductors
| <asset type 1> | [5 empty] | 0
| <asset type 2> | [5 empty] | 0
| <asset type 3> | [5 empty] | 0
Underground cables
| <asset type 1> | [5 empty] | 0
| <asset type 2> | [5 empty] | 0
| <asset type 3> | [5 empty] | 0
Services (incl. LV pillars and LV service pits)
| <asset type 1> | [5 empty] | 0
| <asset type 2> | [5 empty] | 0
| <asset type 3> | [5 empty] | 0
Distribution transformers
| <asset type 1> | [5 empty] | 0
| <asset type 2> | [5 empty] | 0
| <asset type 3> | [5 empty] | 0
Distribution switchgear
| <asset type 1> | [5 empty] | 0
| <asset type 2> | [5 empty] | 0
| <asset type 3> | [5 empty] | 0
Distribution 'other assets'
| <asset type 1> | [5 empty] | 0
| <asset type 2> | [5 empty] | 0
| <asset type 3> | [5 empty] | 0
Zone transformers
| <asset type 1> | [5 empty] | 0
| <asset type 2> | [5 empty] | 0
| <asset type 3> | [5 empty] | 0
Zone switchgear
| <asset type 1> | [5 empty] | 0
| <asset type 2> | [5 empty] | 0
| <asset type 3> | [5 empty] | 0
Zone 'other assets'
| <asset type 1> | [5 empty] | 0
| <asset type 2> | [5 empty] | 0
| <asset type 3> | [5 empty] | 0
SCADA and protection
| <asset type 1> | [5 empty] | 0
| <asset type 2> | [5 empty] | 0
| <asset type 3> | [5 empty] | 0
Other
| <asset type 1> | [5 empty] | 0
| <asset type 2> | [5 empty] | 0
| <asset type 3> | [5 empty] | 0
Contents

## 4. Customer Service
SP AusNet
Customer Service
2013
Table 1 Quality of supply
Over voltage events - due to high voltage injection
Customers receiving over-voltage - due to high voltage injection | 22
Over voltage events - due to lightning
Customers receiving over-voltage - due to lightning
Over voltage events - due to voltage regulation or other cause
Customers receiving over-voltage - due to voltage regulation or other cause
Voltage variations - steady state (zone sub) | 1945
Voltage variations - one minute (zone sub) | 168
Voltage variations - 10 seconds (zone sub) Min<0.7 | 690
Voltage variations - 10 seconds (zone sub) Min<0.8 | 1142
Voltage variations - 10 seconds (zone sub) Min<0.9 | 2387
Voltage variations - steady state (feeder) | 15326
Voltage variations - % zone subs monitored | 100%
Voltage variations - % feeders monitored | 81.48%
Comments:
· SPAusNet currently has Power Quality Meters (PQM) installed on all zone substations. However only about 56% of these meters are returning reliable data. Meter communication issue is the main problem and will be addressed during the course of the year.
· SPAusNet currently has PQMs installed on 81% of feeder extremity sites. New replacement meters will be rolled out in 2014 to cover the remaining 19%. It is estimated that only 50% of exiting feeder extremity meters are returning reliable data. Meter communication issue is the main problem and will be addressed during the course of the year.
Table 2 Complaints - technical quality of supply
Complaints - technical quality of supply - number | 19
Complaints by category (%)
Low voltage supply | 30
Voltage dips | 0
Voltage swell | 0
Voltage spike (impulsive transient) | 30
TV or radio interference | 10
Noise from appliances | 0
Other | 30
Complaints by Likely Cause (%)
Network equipment faulty | 15
Network interference by NSP equipment | 0
Network interference by another customer | 5
Network limitation | 15
Customer internal problem | 25
No problem identified | 20
Environmental | 20
Other | 0
Table 3 Customer service
Timely provision of services
Connections made | 12906
Connections not made on agreed date | 230
Timely repair of faulty streetlights
Streetlights - average monthly number "out" | 523
Streetlights - not repaired by "fix by" date | 98
Streetlights - average number of days to repair | 2
Total streetlights | 136437
Call Centre Performance (number, unless stated)
Calls to call centre fault line | 359719
Calls to fault line not answered within 30 seconds | 36252
Calls to fault line - average waiting time before call answered | 52
Calls abandoned - percentage | 11%
Call centre - number of overload events | 226
Customer complaints (number)
Complaint - reliability of supply | 161
Complaint - technical quality of supply | 19
Complaint - administrative process or customer service | 760
Complaint - connection or augmentation | 1655
Complaint - other | 307
Total complaints | 2902
Note: for Table 3 Calls to Call Centre Fault Line means the total number of calls to the fault line to be reported, including any answered by an automated response service and terminated without being answered by an operator. Excludes missed calls where the fault line is overloaded.
Contents
Note on H6: Author: Data unavailable - not captured in systems
Note on H8: Author: Data unavailable - not captured in systems
Note on H9: Author: Data unavailable - not captured in systems
Note on H10: Author: Data unavailable - not captured in systems
Note on H11: Author: Data unavailable - not captured in systems

## 5. General Information
SP AusNet
General Information
2013
Table 1 General Information
Number of metered supply points | Total no. | By type of customer |  | By supply voltage
|  | Domestic | Non-Domestic | ST | HV | LV
CBD | 0 | 0 | 0 | 0 | 0 | 0
Urban | 284717 | 258199 | 26518 | 1 | 45 | 284671
Rural Short | 263349 | 238134 | 25215 | 3 | 41 | 263305
Rural Long | 116685 | 96970 | 19715 | 2 | 6 | 116677
Total number of metered supply points | 664751 | 593303 | 71448 | 6 | 92 | 664653
Number of unmetered supply points | Network
Total no. | 9318
Energy delivered (GWh) | Total GWh | By type of customer |  | By supply voltage
|  | Domestic | Non-Domestic | ST | HV | LV
CBD | 0 | 0 | 0 | 0 | 0 | 0
Urban | 3452.1432 | 1306.5689 | 2145.5743 | 0.6091 | 372.7043 | 3076.8754
Rural Short | 2775.6457 | 1305.8881 | 1469.7576 | 274.2141 | 169.8385 | 2333.1733
Rural Long | 1202.8008 | 516.9218 | 685.879 | 41.8239 | 105.0782 | 1056.2729
Total energy | 7430.5898 | 3129.3789 | 4301.2109 | 316.6471 | 647.6211 | 6466.3216
Line length (km) | Total km | Underground |  |  | Overhead
|  | ST | HV | LV | ST | HV | LV
CBD | 0 | N/A | N/A | N/A | N/A | N/A | N/A
Urban | 3289.1372 | 0.68124 | 682.7239 | 613.7697 | 161.1752 | 1353.4144 | 477.3727
Rural Short | 17512.281 | 3.6271 | 823.0089 | 3267.8808 | 858.1418 | 10017.9576 | 2541.6648
Rural Long | 28811.9977 | 5.9675 | 208.3725 | 5376.4654 | 1411.8538 | 17627.6765 | 4181.6621
Total line length | 49613.4159 | 10.2758 | 1714.1053 | 9258.116 | 2431.1708 | 28999.0485 | 7200.6995
Number and total capacity of transformers | Total no. | Capacity (MVA)
Distribution | 60498 | 5597.87
Zone substations | 127 | 2816
Total | 60625 | 8413.87
Customer numbers
Subtransmission | 6
High voltage | 92
Low voltage - residential | 593303
Low voltage - non-residential | 71350
Total customer numbers | 664751
Number of poles
Subtransmission | 21126
Distribution | 303015
Total | 324141
Other information
Distribution losses (% of purchases) | 7.43%
Network Service area (sq.km) | 80000
Peak Coincident Demand (MW) | 1621
Note: Distribution Loss factors are to be reported on a financial year basis
Contents
Contents

## 6a. Planned Outages
SP AusNet
Planned Outages
2013
Table 1 Planned Outages
Date (DD/MM/YYYY) | Feeder ID / name | Feeder Classification | Reason for planned outage | Number of customers interrupted | Duration of interruption (mins) | Total minutes off supply (planned) | Effect on planned SAIDI | Effect on planned SAIFI | Effect on planned MAIFI
2013-01-20 07:22 | BWR13 | SHORT RURAL |  | 131 | 828 | 108468 | 0.94389 | 0.00114 | 0
2013-01-03 11:00 | MBY11 | SHORT RURAL |  | 3 | 215 | 645 | 0.0056128 | 2.6106e-05 | 0
2013-01-03 10:00 | LGA24 | SHORT RURAL |  | 71 | 424 | 30104 | 0.26196 | 0.00061784 | 0
2013-01-03 09:11 | WGI31 | SHORT RURAL |  | 2 | 99 | 198 | 0.001723 | 1.7404e-05 | 0
2013-01-02 09:05 | WN2 | LONG RURAL |  | 1 | 31 | 31 | 0.00012004 | 3.8723e-06 | 0
2013-01-02 10:50 | WN2 | LONG RURAL |  | 1 | 52 | 52 | 0.00020136 | 3.8723e-06 | 0
2013-01-03 09:00 | WOTS24 | LONG RURAL |  | 30 | 130 | 3900 | 0.015102 | 0.00011617 | 0
2013-01-02 08:53 | CLN13 | SHORT RURAL |  | 25 | 257 | 6425 | 0.05591 | 0.00021755 | 0
2013-01-02 09:24 | KLK1 | SHORT RURAL |  | 70 | 24 | 1680 | 0.014619 | 0.00060914 | 0
2013-01-03 09:00 | WN2 | LONG RURAL |  | 20 | 376 | 7520 | 0.02912 | 7.7446e-05 | 0
2013-01-02 09:15 | KLO24 | SHORT RURAL |  | 8 | 90 | 720 | 0.0062654 | 6.9616e-05 | 0
2013-01-02 11:05 | KLO24 | SHORT RURAL |  | 17 | 135 | 2295 | 0.019971 | 0.00014793 | 0
2013-01-02 11:05 | KLO24 | SHORT RURAL |  | 6 | 110 | 660 | 0.0057433 | 5.2212e-05 | 0
2013-01-03 09:35 | KLO14 | LONG RURAL |  | 26 | 240 | 6240 | 0.024163 | 0.00010068 | 0
2013-01-03 08:15 | RWT22 | URBAN |  | 1 | 305 | 305 | 0.0010625 | 3.4835e-06 | 0
2013-01-02 13:10 | RWN24 | SHORT RURAL |  | 21 | 15 | 315 | 0.0027411 | 0.00018274 | 0
2013-01-02 08:30 | BGE11 | SHORT RURAL |  | 8 | 195 | 1560 | 0.013575 | 6.9616e-05 | 0
2013-01-03 08:41 | OFR23 | LONG RURAL |  | 137 | 273 | 37401 | 0.14483 | 0.00053051 | 0
2013-01-03 09:16 | RWT22 | URBAN |  | 146 | 194 | 28324 | 0.098666 | 0.00050859 | 0
2013-01-04 08:30 | WOTS24 | LONG RURAL |  | 3 | 53 | 159 | 0.0006157 | 1.1617e-05 | 0
2013-01-04 08:45 | OFR23 | LONG RURAL |  | 5 | 53 | 265 | 0.0010262 | 1.9362e-05 | 0
2013-01-02 09:15 | FTR21 | LONG RURAL |  | 22 | 100 | 2200 | 0.0085191 | 8.5191e-05 | 0
2013-01-03 09:10 | BGE22 | SHORT RURAL |  | 73 | 45 | 3285 | 0.028586 | 0.00063524 | 0
2013-01-03 08:45 | LYD13 | URBAN |  | 32 | 120 | 3840 | 0.013377 | 0.00011147 | 0
2013-01-02 11:45 | FTR12 | LONG RURAL |  | 2 | 65 | 130 | 0.0005034 | 7.7446e-06 | 0
2013-01-13 09:04 | WO32 | URBAN |  | 428 | 354 | 151512 | 0.52779 | 0.0014909 | 0
2013-01-02 17:20 | TT6 | URBAN |  | 78 | 70 | 5460 | 0.01902 | 0.00027171 | 0
2013-01-03 17:00 | TT6 | URBAN |  | 66 | 180 | 11880 | 0.041384 | 0.00022991 | 0
2013-01-06 08:42 | BWR24 | URBAN |  | 5 | 310 | 1550 | 0.0053994 | 1.7417e-05 | 0
2013-01-06 08:30 | BWR33 | URBAN |  | 70 | 285 | 19950 | 0.069495 | 0.00024384 | 0
2013-01-06 08:40 | WOTS24 | LONG RURAL |  | 1 | 143 | 143 | 0.00055374 | 3.8723e-06 | 0
2013-01-07 09:30 | SLE21 | SHORT RURAL |  | 47 | 230 | 10810 | 0.094068 | 0.00040899 | 0
2013-01-07 09:10 | TGN31 | LONG RURAL |  | 24 | 100 | 2400 | 0.0092936 | 9.2936e-05 | 0
2013-01-07 09:35 | DRN14 | SHORT RURAL |  | 10 | 265 | 2650 | 0.02306 | 8.702e-05 | 0
2013-01-07 10:55 | ELM15 | SHORT RURAL |  | 87 | 275 | 23925 | 0.20819 | 0.00075707 | 0
2013-01-07 09:40 | WT13 | URBAN |  | 9 | 155 | 1395 | 0.0048595 | 3.1351e-05 | 0
2013-01-07 09:17 | FTR12 | LONG RURAL |  | 19 | 392 | 7448 | 0.028841 | 7.3574e-05 | 0
2013-01-07 09:30 | LDL23 | LONG RURAL |  | 3 | 555 | 1665 | 0.0064474 | 1.1617e-05 | 0
2013-01-07 09:10 | SMR5 | LONG RURAL |  | 52 | 235 | 12220 | 0.04732 | 0.00020136 | 0
2013-01-07 09:20 | RWN26 | SHORT RURAL |  | 84 | 140 | 11760 | 0.10234 | 0.00073097 | 0
2013-01-07 08:30 | PHM34 | URBAN |  | 11 | 265 | 2915 | 0.010154 | 3.8318e-05 | 0
2013-01-07 09:03 | OFR23 | LONG RURAL |  | 1 | 2 | 2 | 7.7446e-06 | 3.8723e-06 | 0
2013-01-07 09:20 | MDG1 | SHORT RURAL |  | 113 | 308 | 34804 | 0.30286 | 0.00098332 | 0
2013-01-07 10:00 | LDL13 | SHORT RURAL |  | 3 | 210 | 630 | 0.0054822 | 2.6106e-05 | 0
2013-01-07 10:00 | CYN13 | URBAN |  | 52 | 180 | 9360 | 0.032605 | 0.00018114 | 0
2013-01-09 09:15 | MFA21 | LONG RURAL |  | 1 | 60 | 60 | 0.00023234 | 3.8723e-06 | 0
2013-01-10 09:30 | CYN12 | URBAN |  | 43 | 420 | 18060 | 0.062912 | 0.00014979 | 0
2013-01-10 08:56 | RWN33 | URBAN |  | 515 | 512.268 | 263818 | 0.91901 | 0.001794 | 0
2013-01-07 12:10 | TGN31 | LONG RURAL |  | 11 | 90 | 990 | 0.0038336 | 4.2595e-05 | 0
2013-01-08 10:50 | WGL11 | SHORT RURAL |  | 1 | 30 | 30 | 0.00026106 | 8.702e-06 | 0
2013-01-08 08:59 | TGN23 | SHORT RURAL |  | 419 | 388 | 162572 | 1.4147 | 0.0036461 | 0
2013-01-09 09:40 | WGL11 | SHORT RURAL |  | 5 | 79 | 395 | 0.0034373 | 4.351e-05 | 0
2013-01-09 11:30 | WGL11 | SHORT RURAL |  | 2 | 39 | 78 | 0.00067875 | 1.7404e-05 | 0
2013-01-08 09:10 | FTR21 | LONG RURAL |  | 13 | 236 | 3068 | 0.01188 | 5.034e-05 | 0
2013-01-08 08:30 | BDL2 | SHORT RURAL |  | 1 | 300 | 300 | 0.0026106 | 8.702e-06 | 0
2013-01-08 10:20 | NLA34 | SHORT RURAL |  | 9 | 175 | 1575 | 0.013706 | 7.8318e-05 | 0
2013-01-09 09:00 | SLE31 | LONG RURAL |  | 2 | 200 | 400 | 0.0015489 | 7.7446e-06 | 0
2013-01-10 09:00 | WOTS24 | LONG RURAL |  | 66 | 165 | 10890 | 0.04217 | 0.00025557 | 0
2013-01-09 09:55 | NLA34 | SHORT RURAL |  | 499 | 335 | 167165 | 1.4547 | 0.0043423 | 0
2013-01-08 09:25 | WGL11 | SHORT RURAL |  | 1 | 35 | 35 | 0.00030457 | 8.702e-06 | 0
2013-01-09 11:20 | MFA21 | LONG RURAL |  | 9 | 95 | 855 | 0.0033108 | 3.4851e-05 | 0
2013-01-09 09:00 | FTR21 | LONG RURAL |  | 8 | 230 | 1840 | 0.0071251 | 3.0979e-05 | 0
2013-01-10 08:45 | MFA21 | LONG RURAL |  | 2 | 245 | 490 | 0.0018974 | 7.7446e-06 | 0
2013-01-08 09:06 | LGA12 | SHORT RURAL |  | 5 | 310 | 1550 | 0.013488 | 4.351e-05 | 0
2013-01-09 09:05 | LLG12 | SHORT RURAL |  | 145 | 517 | 74965 | 0.65234 | 0.0012618 | 0
2013-01-09 09:20 | LLG12 | SHORT RURAL |  | 26 | 265 | 6890 | 0.059957 | 0.00022625 | 0
2013-01-10 09:02 | WN2 | LONG RURAL |  | 17 | 121 | 2057 | 0.0079654 | 6.5829e-05 | 0
2013-01-09 09:20 | WGL15 | SHORT RURAL |  | 1 | 70 | 70 | 0.00060914 | 8.702e-06 | 0
2013-01-09 10:55 | MOE22 | LONG RURAL |  | 3 | 90 | 270 | 0.0010455 | 1.1617e-05 | 0
2013-01-09 09:45 | ELM33 | SHORT RURAL |  | 18 | 340 | 6120 | 0.053256 | 0.00015664 | 0
2013-01-10 09:30 | DRN11 | URBAN |  | 88 | 288 | 25344 | 0.088285 | 0.00030655 | 0
2013-01-08 09:15 | LGA12 | SHORT RURAL |  | 1 | 40 | 40 | 0.00034808 | 8.702e-06 | 0
2013-01-10 09:03 | LLG12 | SHORT RURAL |  | 91 | 278 | 25298 | 0.22014 | 0.00079188 | 0
2013-01-09 09:05 | WGI31 | SHORT RURAL |  | 51 | 265 | 13515 | 0.11761 | 0.0004438 | 0
2013-01-09 13:20 | WGL15 | SHORT RURAL |  | 2 | 48 | 96 | 0.00083539 | 1.7404e-05 | 0
2013-01-09 14:25 | WGL15 | SHORT RURAL |  | 2 | 60 | 120 | 0.0010442 | 1.7404e-05 | 0
2013-01-10 08:45 | WGL15 | SHORT RURAL |  | 3 | 48 | 144 | 0.0012531 | 2.6106e-05 | 0
2013-01-09 11:30 | WOTS24 | LONG RURAL |  | 8 | 85 | 680 | 0.0026332 | 3.0979e-05 | 0
2013-01-08 08:06 | LDL22 | SHORT RURAL |  | 36 | 369 | 13284 | 0.1156 | 0.00031327 | 0
2013-01-08 09:15 | LDL23 | LONG RURAL |  | 13 | 375 | 4875 | 0.018878 | 5.034e-05 | 0
2013-01-08 10:00 | LDL22 | SHORT RURAL |  | 75 | 310 | 23250 | 0.20232 | 0.00065265 | 0
2013-01-10 09:00 | MSD1 | LONG RURAL |  | 1 | 227 | 227 | 0.00087902 | 3.8723e-06 | 0
2013-01-09 10:00 | LDL22 | SHORT RURAL |  | 124 | 265 | 32860 | 0.28595 | 0.001079 | 0
2013-01-08 15:00 | TGN23 | SHORT RURAL |  | 1 | 40 | 40 | 0.00034808 | 8.702e-06 | 0
2013-01-09 08:35 | LDL22 | SHORT RURAL |  | 35 | 252 | 8820 | 0.076751 | 0.00030457 | 0
2013-01-10 08:50 | TGN11 | SHORT RURAL |  | 74 | 389 | 28786 | 0.25049 | 0.00064395 | 0
2013-01-08 09:42 | DRN12 | URBAN |  | 49 | 308 | 15092 | 0.052573 | 0.00017069 | 0
2013-01-09 09:20 | DRN11 | URBAN |  | 17 | 281 | 4777 | 0.016641 | 5.9219e-05 | 0
2013-01-07 13:10 | EPG34 | URBAN |  | 1 | 150 | 150 | 0.00052252 | 3.4835e-06 | 0
2013-01-09 09:15 | TT12 | URBAN |  | 34 | 135 | 4590 | 0.015989 | 0.00011844 | 0
2013-01-10 09:30 | WYK12 | SHORT RURAL |  | 22 | 347 | 7634 | 0.066431 | 0.00019144 | 0
2013-01-10 08:55 | WYK23 | SHORT RURAL |  | 4 | 325 | 1300 | 0.011313 | 3.4808e-05 | 0
2013-01-10 09:30 | LDL22 | SHORT RURAL |  | 4 | 65 | 260 | 0.0022625 | 3.4808e-05 | 0
2013-01-10 08:50 | WYK12 | SHORT RURAL |  | 111 | 305 | 33855 | 0.29461 | 0.00096592 | 0
2013-01-09 08:40 | MWTS24 | SHORT RURAL |  | 64 | 475 | 30400 | 0.26454 | 0.00055693 | 0
2013-01-08 09:00 | WGL15 | SHORT RURAL |  | 67 | 400 | 26800 | 0.23321 | 0.00058303 | 0
2013-01-10 09:30 | MDG1 | SHORT RURAL |  | 230 | 57 | 13110 | 0.11408 | 0.0020015 | 0
2013-01-10 09:55 | MOE22 | LONG RURAL |  | 87 | 305 | 26535 | 0.10275 | 0.00033689 | 0
2013-01-10 09:45 | TT9 | URBAN |  | 100 | 215 | 21500 | 0.074895 | 0.00034835 | 0
2013-01-10 10:00 | WGL15 | SHORT RURAL |  | 2 | 11 | 22 | 0.00019144 | 1.7404e-05 | 0
2013-01-08 08:50 | LGA11 | LONG RURAL |  | 48 | 585 | 28080 | 0.10873 | 0.00018587 | 0
2013-01-08 10:10 | RWT11 | URBAN |  | 89 | 260 | 23140 | 0.080608 | 0.00031003 | 0
2013-01-10 09:20 | DRN12 | URBAN |  | 80 | 70 | 5600 | 0.019508 | 0.00027868 | 0
2013-01-10 09:45 | WT6 | URBAN |  | 89 | 135 | 12015 | 0.041854 | 0.00031003 | 0
2013-01-09 08:42 | BDL1 | LONG RURAL |  | 99 | 343 | 33957 | 0.13149 | 0.00038336 | 0
2013-01-10 08:52 | SLE24 | URBAN |  | 115 | 358 | 41170 | 0.14341 | 0.0004006 | 0
2013-01-09 09:20 | SMR5 | LONG RURAL |  | 29 | 213 | 6177 | 0.023919 | 0.0001123 | 0
2013-01-09 09:45 | KMS21 | SHORT RURAL |  | 7 | 275 | 1925 | 0.016751 | 6.0914e-05 | 0
2013-01-10 09:05 | FTR21 | LONG RURAL |  | 87 | 395 | 34365 | 0.13307 | 0.00033689 | 0
2013-01-10 09:45 | MYT7 | LONG RURAL |  | 81 | 43 | 3483 | 0.013487 | 0.00031366 | 0
2013-01-10 09:09 | KMS21 | SHORT RURAL |  | 97 | 115 | 11155 | 0.09707 | 0.00084409 | 0
2013-01-09 08:32 | RWT11 | URBAN |  | 275 | 201 | 55275 | 0.19255 | 0.00095796 | 0
2013-01-08 08:35 | BWR32 | URBAN |  | 571 | 332.8301 | 190046 | 0.66202 | 0.0019891 | 0
2013-01-08 09:15 | PHM33 | SHORT RURAL |  | 27 | 115 | 3105 | 0.02702 | 0.00023495 | 0
2013-01-08 11:50 | PHM33 | SHORT RURAL |  | 2 | 30 | 60 | 0.00052212 | 1.7404e-05 | 0
2013-01-08 10:50 | OFR23 | LONG RURAL |  | 2 | 60 | 120 | 0.00046468 | 7.7446e-06 | 0
2013-01-08 12:45 | OFR23 | LONG RURAL |  | 5 | 15 | 75 | 0.00029042 | 1.9362e-05 | 0
2013-01-08 11:00 | OFR23 | LONG RURAL |  | 2 | 64 | 128 | 0.00049566 | 7.7446e-06 | 0
2013-01-09 09:02 | CLN23 | SHORT RURAL |  | 1 | 43 | 43 | 0.00037418 | 8.702e-06 | 0
2013-01-09 11:03 | CLN13 | SHORT RURAL |  | 9 | 24 | 216 | 0.0018796 | 7.8318e-05 | 0
2013-01-10 08:35 | CLN23 | SHORT RURAL |  | 48 | 249 | 11952 | 0.10401 | 0.00041769 | 0
2013-01-10 08:30 | OFR23 | LONG RURAL |  | 50 | 360 | 18000 | 0.069702 | 0.00019362 | 0
2013-01-10 08:40 | LGA11 | LONG RURAL |  | 45 | 450 | 20250 | 0.078414 | 0.00017425 | 0
2013-01-10 09:20 | FTR23 | LONG RURAL |  | 34 | 445 | 15130 | 0.058588 | 0.00013166 | 0
2013-01-08 12:30 | BRA32 | URBAN |  | 62 | 137 | 8494 | 0.029589 | 0.00021598 | 0
2013-01-10 09:02 | SMR2 | SHORT RURAL |  | 42 | 318 | 13356 | 0.11622 | 0.00036548 | 0
2013-01-08 09:15 | SFS1 | SHORT RURAL |  | 25 | 405 | 10125 | 0.088107 | 0.00021755 | 0
2013-01-09 10:50 | BWN14 | SHORT RURAL |  | 5 | 99 | 495 | 0.0043075 | 4.351e-05 | 0
2013-01-09 13:15 | BWN14 | SHORT RURAL |  | 1 | 40 | 40 | 0.00034808 | 8.702e-06 | 0
2013-01-09 13:20 | OFR24 | URBAN |  | 5 | 29 | 145 | 0.00050511 | 1.7417e-05 | 0
2013-01-10 08:35 | CLN23 | SHORT RURAL |  | 751 | 120 | 90120 | 0.78422 | 0.0065352 | 0
2013-01-08 09:50 | OFR22 | SHORT RURAL |  | 7 | 35 | 245 | 0.002132 | 6.0914e-05 | 0
2013-01-10 09:35 | HPK11 | URBAN |  | 377 | 135 | 50895 | 0.17729 | 0.0013133 | 0
2013-01-08 10:00 | ELM15 | SHORT RURAL |  | 6 | 220 | 1320 | 0.011487 | 5.2212e-05 | 0
2013-01-11 10:15 | WGL13 | SHORT RURAL |  | 2 | 65 | 130 | 0.0011313 | 1.7404e-05 | 0
2013-01-11 09:45 | WGL11 | SHORT RURAL |  | 2 | 25 | 50 | 0.0004351 | 1.7404e-05 | 0
2013-01-11 12:30 | WGL21 | LONG RURAL |  | 2 | 45 | 90 | 0.00034851 | 7.7446e-06 | 0
2013-01-10 11:50 | WGL15 | SHORT RURAL |  | 3 | 61 | 183 | 0.0015925 | 2.6106e-05 | 0
2013-01-11 09:00 | MOE22 | LONG RURAL |  | 12 | 125 | 1500 | 0.0058085 | 4.6468e-05 | 0
2013-01-10 12:40 | TT6 | URBAN |  | 103 | 100 | 10300 | 0.03588 | 0.0003588 | 0
2013-01-11 12:24 | MDG1 | SHORT RURAL |  | 6 | 145 | 870 | 0.0075707 | 5.2212e-05 | 0
2013-01-11 09:05 | TGN31 | LONG RURAL |  | 12 | 127 | 1524 | 0.0059014 | 4.6468e-05 | 0
2013-01-11 09:45 | LGA11 | LONG RURAL |  | 76 | 200 | 15200 | 0.058859 | 0.0002943 | 0
2013-01-10 12:00 | KMS21 | SHORT RURAL |  | 10 | 110 | 1100 | 0.0095722 | 8.702e-05 | 0
2013-01-11 14:40 | FTR12 | LONG RURAL |  | 405 | 0.99753 | 404 | 0.0015644 | 0.0015683 | 0
2013-01-12 09:25 | MOE22 | LONG RURAL |  | 10 | 190 | 1900 | 0.0073574 | 3.8723e-05 | 0
2013-01-11 12:15 | MOE22 | LONG RURAL |  | 19 | 55 | 1045 | 0.0040466 | 7.3574e-05 | 0
2013-01-11 12:11 | MOE22 | LONG RURAL |  | 49 | 38 | 1862 | 0.0072102 | 0.00018974 | 0
2013-01-11 08:40 | PHM14 | LONG RURAL |  | 2 | 52 | 104 | 0.00040272 | 7.7446e-06 | 0
2013-01-12 09:02 | FTR12 | LONG RURAL |  | 264 | 286 | 75504 | 0.29238 | 0.0010223 | 0
2013-01-18 09:38 | WOTS11 | LONG RURAL |  | 31 | 117 | 3627 | 0.014045 | 0.00012004 | 0
2013-01-13 11:07 | CLN13 | SHORT RURAL |  | 36 | 151 | 5436 | 0.047304 | 0.00031327 | 0
2013-01-14 09:25 | KMS21 | SHORT RURAL |  | 97 | 370 | 35890 | 0.31231 | 0.00084409 | 0
2013-01-14 10:10 | WGL12 | LONG RURAL |  | 19 | 340 | 6460 | 0.025015 | 7.3574e-05 | 0
2013-01-14 09:00 | WGL13 | SHORT RURAL |  | 2 | 40 | 80 | 0.00069616 | 1.7404e-05 | 0
2013-01-14 09:10 | WN2 | LONG RURAL |  | 15 | 203 | 3045 | 0.011791 | 5.8085e-05 | 0
2013-01-14 09:40 | WGL13 | SHORT RURAL |  | 182 | 223 | 40586 | 0.35318 | 0.0015838 | 0
2013-01-14 10:30 | WGL13 | SHORT RURAL |  | 1 | 40 | 40 | 0.00034808 | 8.702e-06 | 0
2013-01-14 09:25 | KLK1 | SHORT RURAL |  | 1 | 25 | 25 | 0.00021755 | 8.702e-06 | 0
2013-01-14 10:10 | KLK1 | SHORT RURAL |  | 2 | 65 | 130 | 0.0011313 | 1.7404e-05 | 0
2013-01-14 11:02 | DRN11 | URBAN |  | 153 | 282 | 43146 | 0.1503 | 0.00053297 | 0
2013-01-14 09:40 | WYK12 | SHORT RURAL |  | 1 | 100 | 100 | 0.0008702 | 8.702e-06 | 0
2013-01-14 10:30 | LDL22 | SHORT RURAL |  | 3 | 220 | 660 | 0.0057433 | 2.6106e-05 | 0
2013-01-14 09:05 | LDL22 | SHORT RURAL |  | 50 | 43 | 2150 | 0.018709 | 0.0004351 | 0
2013-01-14 08:45 | ELM33 | SHORT RURAL |  | 45 | 185 | 8325 | 0.072444 | 0.00039159 | 0
2013-01-14 09:55 | KLO24 | SHORT RURAL |  | 41 | 230 | 9430 | 0.08206 | 0.00035678 | 0
2013-01-14 08:35 | SLE32 | SHORT RURAL |  | 11 | 165 | 1815 | 0.015794 | 9.5722e-05 | 0
2013-01-14 09:45 | FTR22 | SHORT RURAL |  | 1 | 30 | 30 | 0.00026106 | 8.702e-06 | 0
2013-01-14 09:05 | FTR21 | LONG RURAL |  | 48 | 155 | 7440 | 0.02881 | 0.00018587 | 0
2013-01-14 11:20 | FTR22 | SHORT RURAL |  | 3 | 87.3333 | 262 | 0.0022799 | 2.6106e-05 | 0
2013-01-14 09:00 | OFR23 | LONG RURAL |  | 11 | 154 | 1694 | 0.0065597 | 4.2595e-05 | 0
2013-01-08 08:30 | PHM33 | SHORT RURAL |  | 4 | 75 | 300 | 0.0026106 | 3.4808e-05 | 0
2013-01-14 14:00 | FTR22 | SHORT RURAL |  | 1 | 40 | 40 | 0.00034808 | 8.702e-06 | 0
2013-01-16 10:05 | SMR8 | LONG RURAL |  | 5 | 185 | 925 | 0.0035819 | 1.9362e-05 | 0
2013-01-15 10:00 | NLA31 | LONG RURAL |  | 1 | 105 | 105 | 0.00040659 | 3.8723e-06 | 0
2013-01-15 11:30 | NLA31 | LONG RURAL |  | 3 | 70 | 210 | 0.00081319 | 1.1617e-05 | 0
2013-01-15 09:03 | WN2 | LONG RURAL |  | 21 | 311 | 6531 | 0.02529 | 8.1319e-05 | 0
2013-01-15 10:10 | MOE22 | LONG RURAL |  | 4 | 110 | 440 | 0.0017038 | 1.5489e-05 | 0
2013-01-15 09:15 | WGL21 | LONG RURAL |  | 2 | 40 | 80 | 0.00030979 | 7.7446e-06 | 0
2013-01-15 12:04 | WGL21 | LONG RURAL |  | 2 | 51 | 102 | 0.00039498 | 7.7446e-06 | 0
2013-01-16 09:05 | MWTS14 | SHORT RURAL |  | 1 | 35 | 35 | 0.00030457 | 8.702e-06 | 0
2013-01-16 10:05 | MWTS14 | SHORT RURAL |  | 3 | 65 | 195 | 0.0016969 | 2.6106e-05 | 0
2013-01-16 14:45 | MWTS14 | SHORT RURAL |  | 1 | 45 | 45 | 0.00039159 | 8.702e-06 | 0
2013-01-16 13:00 | MWTS14 | SHORT RURAL |  | 1 | 65 | 65 | 0.00056563 | 8.702e-06 | 0
2013-01-16 09:05 | WGL13 | SHORT RURAL |  | 49 | 340 | 16660 | 0.14497 | 0.0004264 | 0
2013-01-17 09:10 | WGL13 | SHORT RURAL |  | 2 | 155 | 310 | 0.0026976 | 1.7404e-05 | 0
2013-01-16 09:00 | MWTS31 | SHORT RURAL |  | 2 | 25 | 50 | 0.0004351 | 1.7404e-05 | 0
2013-01-16 09:55 | MWTS31 | SHORT RURAL |  | 2 | 65 | 130 | 0.0011313 | 1.7404e-05 | 0
2013-01-16 12:05 | MWTS31 | SHORT RURAL |  | 5 | 37 | 185 | 0.0016099 | 4.351e-05 | 0
2013-01-17 09:10 | TGN31 | LONG RURAL |  | 73 | 195 | 14235 | 0.055122 | 0.00028268 | 0
2013-01-15 09:00 | MOE24 | SHORT RURAL |  | 65 | 7 | 455 | 0.0039594 | 0.00056563 | 0
2013-01-17 10:50 | WGL13 | SHORT RURAL |  | 2 | 45 | 90 | 0.00078318 | 1.7404e-05 | 0
2013-01-17 11:45 | WGL13 | SHORT RURAL |  | 1 | 35 | 35 | 0.00030457 | 8.702e-06 | 0
2013-01-15 10:15 | BWA23 | SHORT RURAL |  | 3 | 285 | 855 | 0.0074402 | 2.6106e-05 | 0
2013-01-14 12:40 | KLK1 | SHORT RURAL |  | 13 | 90 | 1170 | 0.010181 | 0.00011313 | 0
2013-01-17 08:40 | MWTS14 | SHORT RURAL |  | 52 | 368 | 19136 | 0.16652 | 0.0004525 | 0
2013-01-15 09:25 | MFA21 | LONG RURAL |  | 3 | 150 | 450 | 0.0017425 | 1.1617e-05 | 0
2013-01-15 08:03 | MFA23 | SHORT RURAL |  | 2 | 227 | 454 | 0.0039507 | 1.7404e-05 | 0
2013-01-15 11:20 | SLE24 | URBAN |  | 10 | 60 | 600 | 0.0020901 | 3.4835e-05 | 0
2013-01-17 08:50 | MFA23 | SHORT RURAL |  | 4 | 258 | 1032 | 0.0089804 | 3.4808e-05 | 0
2013-01-15 14:00 | WGL21 | LONG RURAL |  | 4 | 103 | 412 | 0.0015954 | 1.5489e-05 | 0
2013-01-16 08:30 | BDL5 | LONG RURAL |  | 79 | 608 | 48032 | 0.186 | 0.00030591 | 0
2013-01-15 08:45 | TGN23 | SHORT RURAL |  | 1 | 68 | 68 | 0.00059173 | 8.702e-06 | 0
2013-01-15 11:15 | WGL21 | LONG RURAL |  | 7 | 15 | 105 | 0.00040659 | 2.7106e-05 | 0
2013-01-15 13:24 | WGL21 | LONG RURAL |  | 1 | 53 | 53 | 0.00020523 | 3.8723e-06 | 0
2013-01-16 11:30 | MOE22 | LONG RURAL |  | 3 | 30 | 90 | 0.00034851 | 1.1617e-05 | 0
2013-01-16 09:22 | MOE22 | LONG RURAL |  | 1 | 33 | 33 | 0.00012779 | 3.8723e-06 | 0
2013-01-16 13:00 | MOE22 | LONG RURAL |  | 1 | 26 | 26 | 0.00010068 | 3.8723e-06 | 0
2013-01-15 09:34 | KMS1 | SHORT RURAL |  | 120 | 271 | 32520 | 0.28299 | 0.0010442 | 0
2013-01-15 08:58 | FTR22 | SHORT RURAL |  | 25 | 77 | 1925 | 0.016751 | 0.00021755 | 0
2013-01-15 09:00 | LGA13 | LONG RURAL |  | 35 | 480 | 16800 | 0.065055 | 0.00013553 | 0
2013-01-16 09:05 | MFA21 | LONG RURAL |  | 5 | 556 | 2780 | 0.010765 | 1.9362e-05 | 0
2013-01-16 09:45 | MSD2 | LONG RURAL |  | 1 | 190 | 190 | 0.00073574 | 3.8723e-06 | 0
2013-01-16 08:55 | BN2 | LONG RURAL |  | 3 | 98 | 294 | 0.0011385 | 1.1617e-05 | 0
2013-01-16 08:35 | NLA31 | LONG RURAL |  | 3 | 45 | 135 | 0.00052276 | 1.1617e-05 | 0
2013-01-15 11:05 | FTR22 | SHORT RURAL |  | 67 | 103 | 6901 | 0.060052 | 0.00058303 | 0
2013-01-16 11:00 | NLA31 | LONG RURAL |  | 3 | 118 | 354 | 0.0013708 | 1.1617e-05 | 0
2013-01-15 09:00 | BRT21 | SHORT RURAL |  | 6 | 120 | 720 | 0.0062654 | 5.2212e-05 | 0
2013-01-16 09:35 | FTR21 | LONG RURAL |  | 2 | 115 | 230 | 0.00089063 | 7.7446e-06 | 0
2013-01-16 12:30 | NLA31 | LONG RURAL |  | 2 | 80 | 160 | 0.00061957 | 7.7446e-06 | 0
2013-01-16 09:38 | FTR23 | LONG RURAL |  | 3 | 85 | 255 | 0.00098744 | 1.1617e-05 | 0
2013-01-16 11:55 | FTR21 | LONG RURAL |  | 1 | 80 | 80 | 0.00030979 | 3.8723e-06 | 0
2013-01-15 10:05 | ALA01 | LONG RURAL |  | 1 | 345 | 345 | 0.0013359 | 3.8723e-06 | 0
2013-01-15 13:20 | DRN11 | URBAN |  | 1 | 52 | 52 | 0.00018114 | 3.4835e-06 | 0
2013-01-16 09:40 | KLO14 | LONG RURAL |  | 1 | 50 | 50 | 0.00019362 | 3.8723e-06 | 0
2013-01-16 09:25 | SMR8 | LONG RURAL |  | 12 | 310 | 3720 | 0.014405 | 4.6468e-05 | 0
2013-01-16 09:00 | SMR4 | SHORT RURAL |  | 2 | 135 | 270 | 0.0023495 | 1.7404e-05 | 0
2013-01-15 09:20 | WGI33 | SHORT RURAL |  | 69 | 390 | 26910 | 0.23417 | 0.00060044 | 0
2013-01-16 09:25 | WGI23 | SHORT RURAL |  | 61 | 210 | 12810 | 0.11147 | 0.00053082 | 0
2013-01-15 09:35 | MOE21 | SHORT RURAL |  | 5 | 145 | 725 | 0.0063089 | 4.351e-05 | 0
2013-01-16 08:30 | LDL14 | SHORT RURAL |  | 48 | 340 | 16320 | 0.14202 | 0.00041769 | 0
2013-01-15 09:45 | MWTS24 | SHORT RURAL |  | 6 | 75 | 450 | 0.0039159 | 5.2212e-05 | 0
2013-01-16 13:30 | KLK1 | SHORT RURAL |  | 2 | 45 | 90 | 0.00078318 | 1.7404e-05 | 0
2013-01-16 12:20 | KLK1 | SHORT RURAL |  | 1 | 40 | 40 | 0.00034808 | 8.702e-06 | 0
2013-01-16 10:40 | KLK1 | SHORT RURAL |  | 2 | 70 | 140 | 0.0012183 | 1.7404e-05 | 0
2013-01-16 08:30 | RWT11 | URBAN |  | 89 | 345 | 30705 | 0.10696 | 0.00031003 | 0
2013-01-15 11:00 | TGN11 | SHORT RURAL |  | 8 | 98.75 | 790 | 0.0068746 | 6.9616e-05 | 0
2013-01-15 08:32 | LLG12 | SHORT RURAL |  | 1000 | 135.665 | 135665 | 1.1806 | 0.008702 | 0
2013-01-15 13:05 | NLA31 | LONG RURAL |  | 1 | 80 | 80 | 0.00030979 | 3.8723e-06 | 0
2013-01-16 09:25 | KLK1 | SHORT RURAL |  | 1 | 65 | 65 | 0.00056563 | 8.702e-06 | 0
2013-01-15 09:50 | WYK23 | SHORT RURAL |  | 44 | 180 | 7920 | 0.06892 | 0.00038289 | 0
2013-01-16 08:55 | FTR21 | LONG RURAL |  | 60 | 375 | 22500 | 0.087127 | 0.00023234 | 0
2013-01-16 09:05 | LGA12 | SHORT RURAL |  | 299 | 581 | 173719 | 1.5117 | 0.0026019 | 0
2013-01-15 09:10 | RWN24 | SHORT RURAL |  | 46 | 270 | 12420 | 0.10808 | 0.00040029 | 0
2013-01-16 11:40 | MFA21 | LONG RURAL |  | 3 | 160 | 480 | 0.0018587 | 1.1617e-05 | 0
2013-01-17 09:40 | FTR21 | LONG RURAL |  | 368 | 340.625 | 125350 | 0.48539 | 0.001425 | 0
2013-01-17 11:20 | PHI12 | SHORT RURAL |  | 2 | 105 | 210 | 0.0018274 | 1.7404e-05 | 0
2013-01-16 12:10 | DRN11 | URBAN |  | 2 | 61 | 122 | 0.00042498 | 6.967e-06 | 0
2013-01-15 09:45 | BWR13 | SHORT RURAL |  | 117 | 55 | 6435 | 0.055997 | 0.0010181 | 0
2013-01-17 08:16 | WYK12 | SHORT RURAL |  | 111 | 134 | 14874 | 0.12943 | 0.00096592 | 0
2013-01-15 13:45 | MOE21 | SHORT RURAL |  | 2 | 50 | 100 | 0.0008702 | 1.7404e-05 | 0
2013-01-16 08:25 | RWN33 | URBAN |  | 3 | 280 | 840 | 0.0029261 | 1.045e-05 | 0
2013-01-16 09:20 | MWTS32 | SHORT RURAL |  | 11 | 270 | 2970 | 0.025845 | 9.5722e-05 | 0
2013-01-16 09:08 | WN2 | LONG RURAL |  | 2 | 52 | 104 | 0.00040272 | 7.7446e-06 | 0
2013-01-17 10:15 | MWTS14 | SHORT RURAL |  | 2 | 50 | 100 | 0.0008702 | 1.7404e-05 | 0
2013-01-15 11:35 | WOTS13 | LONG RURAL |  | 2 | 35 | 70 | 0.00027106 | 7.7446e-06 | 0
2013-01-16 11:30 | WOTS24 | LONG RURAL |  | 6 | 55 | 330 | 0.0012779 | 2.3234e-05 | 0
2013-01-15 09:00 | LGA11 | LONG RURAL |  | 17 | 168 | 2856 | 0.011059 | 6.5829e-05 | 0
2013-01-15 09:00 | KLO14 | LONG RURAL |  | 59 | 385 | 22715 | 0.08796 | 0.00022847 | 0
2013-01-17 09:35 | KLO14 | LONG RURAL |  | 1 | 150 | 150 | 0.00058085 | 3.8723e-06 | 0
2013-01-17 09:10 | LGA24 | SHORT RURAL |  | 71 | 376 | 26696 | 0.23231 | 0.00061784 | 0
2013-01-15 09:55 | ALA01 | LONG RURAL |  | 2 | 175 | 350 | 0.0013553 | 7.7446e-06 | 0
2013-01-17 08:50 | BDL1 | LONG RURAL |  | 1 | 120 | 120 | 0.00046468 | 3.8723e-06 | 0
2013-01-17 08:30 | NLA31 | LONG RURAL |  | 102 | 250 | 25500 | 0.098744 | 0.00039498 | 0
2013-01-17 09:00 | LGA11 | LONG RURAL |  | 36 | 325 | 11700 | 0.045306 | 0.0001394 | 0
2013-01-16 09:02 | BDL6 | SHORT RURAL |  | 17 | 10 | 170 | 0.0014793 | 0.00014793 | 0
2013-01-15 10:40 | WN3 | LONG RURAL |  | 2 | 295 | 590 | 0.0022847 | 7.7446e-06 | 0
2013-01-16 09:00 | KLO14 | LONG RURAL |  | 2 | 100 | 200 | 0.00077446 | 7.7446e-06 | 0
2013-01-16 09:35 | KLO14 | LONG RURAL |  | 69 | 225 | 15525 | 0.060118 | 0.00026719 | 0
2013-01-17 09:09 | MWTS22 | SHORT RURAL |  | 6 | 398 | 2388 | 0.02078 | 5.2212e-05 | 0
2013-01-15 08:30 | SFS1 | SHORT RURAL |  | 25 | 515 | 12875 | 0.11204 | 0.00021755 | 0
2013-01-13 09:30 | HPK12 | URBAN |  | 84 | 235 | 19740 | 0.068764 | 0.00029261 | 0
2013-01-16 08:45 | BGE11 | SHORT RURAL |  | 53 | 320 | 16960 | 0.14759 | 0.0004612 | 0
2013-01-16 08:30 | SFS1 | SHORT RURAL |  | 186 | 320 | 59520 | 0.51794 | 0.0016186 | 0
2013-01-14 09:59 | MSD4 | LONG RURAL |  | 2 | 54 | 108 | 0.00041821 | 7.7446e-06 | 0
2013-01-14 11:46 | MSD4 | LONG RURAL |  | 27 | 51 | 1377 | 0.0053322 | 0.00010455 | 0
2013-01-14 13:50 | MSD4 | LONG RURAL |  | 6 | 41 | 246 | 0.00095259 | 2.3234e-05 | 0
2013-01-14 08:25 | MSD4 | LONG RURAL |  | 12 | 79 | 948 | 0.003671 | 4.6468e-05 | 0
2013-01-15 08:16 | MSD4 | LONG RURAL |  | 43 | 49 | 2107 | 0.008159 | 0.00016651 | 0
2013-01-15 11:30 | PHM31 | SHORT RURAL |  | 7 | 120 | 840 | 0.0073097 | 6.0914e-05 | 0
2013-01-17 09:30 | WGL13 | SHORT RURAL |  | 1 | 100 | 100 | 0.0008702 | 8.702e-06 | 0
2013-01-17 14:35 | WGL24 | LONG RURAL |  | 2 | 30 | 60 | 0.00023234 | 7.7446e-06 | 0
2013-01-18 09:55 | WGI23 | SHORT RURAL |  | 18 | 195 | 3510 | 0.030544 | 0.00015664 | 0
2013-01-18 08:45 | RWT15 | URBAN |  | 573 | 430 | 246390 | 0.8583 | 0.001996 | 0
2013-01-17 12:10 | KLO14 | LONG RURAL |  | 1 | 85 | 85 | 0.00032915 | 3.8723e-06 | 0
2013-01-18 09:40 | LGA12 | SHORT RURAL |  | 3 | 10 | 30 | 0.00026106 | 2.6106e-05 | 0
2013-01-18 10:30 | KLK1 | SHORT RURAL |  | 3 | 23 | 69 | 0.00060044 | 2.6106e-05 | 0
2013-01-18 08:50 | KLK1 | SHORT RURAL |  | 3 | 60 | 180 | 0.0015664 | 2.6106e-05 | 0
2013-01-03 06:19 | TRC01 | SHORT RURAL |  | 20 | 61 | 1220 | 0.010616 | 0.00017404 | 0
2013-01-18 12:25 | KLK2 | SHORT RURAL |  | 2 | 45 | 90 | 0.00078318 | 1.7404e-05 | 0
2013-01-18 11:30 | KLK2 | SHORT RURAL |  | 2 | 45 | 90 | 0.00078318 | 1.7404e-05 | 0
2013-01-17 08:35 | MFA31 | SHORT RURAL |  | 215 | 175 | 37625 | 0.32741 | 0.0018709 | 0
2013-01-16 08:30 | WN3 | LONG RURAL |  | 2 | 116 | 232 | 0.00089838 | 7.7446e-06 | 0
2013-01-18 09:37 | SMR3 | LONG RURAL |  | 51 | 313 | 15963 | 0.061814 | 0.00019749 | 0
2013-01-17 08:00 | BGE11 | SHORT RURAL |  | 32 | 300 | 9600 | 0.083539 | 0.00027846 | 0
2013-01-20 09:00 | WGL24 | LONG RURAL |  | 50 | 250 | 12500 | 0.048404 | 0.00019362 | 0
2013-01-14 11:10 | BRA23 | URBAN |  | 57 | 92 | 5244 | 0.018267 | 0.00019856 | 0
2013-01-20 09:02 | MWE2 | SHORT RURAL |  | 5 | 425 | 2125 | 0.018492 | 4.351e-05 | 0
2013-01-20 09:02 | MWE3 | URBAN |  | 8 | 428 | 3424 | 0.011927 | 2.7868e-05 | 0
2013-01-20 09:02 | MWE6 | URBAN |  | 19 | 423 | 8037 | 0.027997 | 6.6186e-05 | 0
2013-01-16 08:00 | NLA31 | LONG RURAL |  | 3 | 58 | 174 | 0.00067378 | 1.1617e-05 | 0
2013-01-16 09:00 | BWA22 | LONG RURAL |  | 87 | 35 | 3045 | 0.011791 | 0.00033689 | 0
2013-01-15 13:07 | MSD4 | LONG RURAL |  | 5 | 35 | 175 | 0.00067766 | 1.9362e-05 | 0
2013-01-15 12:08 | MSD4 | LONG RURAL |  | 10 | 38 | 380 | 0.0014715 | 3.8723e-05 | 0
2013-01-10 12:30 | MSD4 | LONG RURAL |  | 45 | 60 | 2700 | 0.010455 | 0.00017425 | 0
2013-01-10 13:45 | MSD4 | LONG RURAL |  | 4 | 43 | 172 | 0.00066604 | 1.5489e-05 | 0
2013-01-13 09:30 | WN2 | LONG RURAL |  | 3 | 240 | 720 | 0.0027881 | 1.1617e-05 | 0
2013-01-21 10:10 | MOE22 | LONG RURAL |  | 1 | 130 | 130 | 0.0005034 | 3.8723e-06 | 0
2013-01-21 09:00 | MOE31 | LONG RURAL |  | 2 | 145 | 290 | 0.001123 | 7.7446e-06 | 0
2013-01-16 09:30 | TT4 | URBAN |  | 168 | 330 | 55440 | 0.19312 | 0.00058523 | 0
2013-01-17 09:40 | SFS1 | SHORT RURAL |  | 17 | 226 | 3842 | 0.033433 | 0.00014793 | 0
2013-01-17 09:00 | WN3 | LONG RURAL |  | 3 | 89 | 267 | 0.0010339 | 1.1617e-05 | 0
2013-01-19 08:30 | SFS1 | SHORT RURAL |  | 25 | 425 | 10625 | 0.092458 | 0.00021755 | 0
2013-01-19 08:40 | CYN13 | URBAN |  | 1 | 225 | 225 | 0.00078378 | 3.4835e-06 | 0
2013-01-16 09:20 | OFR23 | LONG RURAL |  | 44 | 273 | 12012 | 0.046514 | 0.00017038 | 0
2013-01-16 09:05 | LLG11 | SHORT RURAL |  | 2 | 50 | 100 | 0.0008702 | 1.7404e-05 | 0
2013-01-16 09:00 | PHM31 | SHORT RURAL |  | 2 | 270 | 540 | 0.0046991 | 1.7404e-05 | 0
2013-01-17 08:30 | OFR23 | LONG RURAL |  | 181 | 294 | 53214 | 0.20606 | 0.00070089 | 0
2013-01-18 08:45 | CLN22 | SHORT RURAL |  | 8 | 55 | 440 | 0.0038289 | 6.9616e-05 | 0
2013-01-23 09:00 | FTR22 | SHORT RURAL |  | 51 | 275 | 14025 | 0.12205 | 0.0004438 | 0
2013-01-22 11:50 | WGL24 | LONG RURAL |  | 1 | 70 | 70 | 0.00027106 | 3.8723e-06 | 0
2013-01-23 09:15 | MWTS24 | SHORT RURAL |  | 64 | 332 | 21248 | 0.1849 | 0.00055693 | 0
2013-01-23 09:20 | WGL24 | LONG RURAL |  | 1 | 50 | 50 | 0.00019362 | 3.8723e-06 | 0
2013-01-23 10:40 | WGL24 | LONG RURAL |  | 4 | 75 | 300 | 0.0011617 | 1.5489e-05 | 0
2013-01-22 09:15 | WGL24 | LONG RURAL |  | 1 | 120 | 120 | 0.00046468 | 3.8723e-06 | 0
2013-01-24 09:35 | TGN14 | LONG RURAL |  | 518 | 185 | 95830 | 0.37108 | 0.0020059 | 0
2013-01-23 13:35 | WGL24 | LONG RURAL |  | 3 | 35 | 105 | 0.00040659 | 1.1617e-05 | 0
2013-01-23 10:25 | WGL13 | SHORT RURAL |  | 6 | 211 | 1266 | 0.011017 | 5.2212e-05 | 0
2013-01-24 09:04 | WGL13 | SHORT RURAL |  | 182 | 321 | 58422 | 0.50839 | 0.0015838 | 0
2013-01-23 09:20 | WGI23 | SHORT RURAL |  | 419 | 325 | 136175 | 1.185 | 0.0036461 | 0
2013-01-24 09:04 | WGI14 | SHORT RURAL |  | 62 | 176 | 10912 | 0.094956 | 0.00053952 | 0
2013-01-25 09:05 | WGI14 | SHORT RURAL |  | 14 | 120 | 1680 | 0.014619 | 0.00012183 | 0
2013-01-25 09:45 | WGI14 | SHORT RURAL |  | 38 | 237 | 9006 | 0.07837 | 0.00033067 | 0
2013-01-21 13:35 | MOE22 | LONG RURAL |  | 1 | 130 | 130 | 0.0005034 | 3.8723e-06 | 0
2013-01-22 10:00 | BWR13 | SHORT RURAL |  | 91 | 230 | 20930 | 0.18213 | 0.00079188 | 0
2013-01-22 10:25 | WGI22 | LONG RURAL |  | 1 | 75 | 75 | 0.00029042 | 3.8723e-06 | 0
2013-01-22 13:30 | WGI22 | LONG RURAL |  | 2 | 60 | 120 | 0.00046468 | 7.7446e-06 | 0
2013-01-22 14:56 | WGI22 | LONG RURAL |  | 4 | 34 | 136 | 0.00052663 | 1.5489e-05 | 0
2013-01-22 13:30 | WGI22 | LONG RURAL |  | 3 | 40 | 120 | 0.00046468 | 1.1617e-05 | 0
2013-01-22 09:05 | WGI22 | LONG RURAL |  | 3 | 215 | 645 | 0.0024976 | 1.1617e-05 | 0
2013-01-22 09:00 | TGN14 | LONG RURAL |  | 46 | 400 | 18400 | 0.071251 | 0.00017813 | 0
2013-01-22 10:00 | LDL23 | LONG RURAL |  | 70 | 75 | 5250 | 0.02033 | 0.00027106 | 0
2013-01-22 13:22 | WYK12 | SHORT RURAL |  | 2 | 53 | 106 | 0.00092241 | 1.7404e-05 | 0
2013-01-22 08:45 | WYK12 | SHORT RURAL |  | 6 | 265 | 1590 | 0.013836 | 5.2212e-05 | 0
2013-01-22 09:05 | LDL23 | LONG RURAL |  | 13 | 135 | 1755 | 0.0067959 | 5.034e-05 | 0
2013-01-22 08:45 | WYK23 | SHORT RURAL |  | 26 | 360 | 9360 | 0.08145 | 0.00022625 | 0
2013-01-23 11:35 | WYK12 | SHORT RURAL |  | 3 | 107 | 321 | 0.0027933 | 2.6106e-05 | 0
2013-01-23 08:37 | KLK1 | SHORT RURAL |  | 266 | 387 | 102942 | 0.8958 | 0.0023147 | 0
2013-01-24 08:40 | KLK1 | SHORT RURAL |  | 85 | 392 | 33320 | 0.28995 | 0.00073967 | 0
2013-01-23 09:11 | MWTS31 | SHORT RURAL |  | 156 | 139 | 21684 | 0.18869 | 0.0013575 | 0
2013-01-22 10:55 | MWTS22 | SHORT RURAL |  | 20 | 263 | 5260 | 0.045772 | 0.00017404 | 0
2013-01-22 09:10 | FTR21 | LONG RURAL |  | 1 | 35 | 35 | 0.00013553 | 3.8723e-06 | 0
2013-01-22 08:50 | FTR21 | LONG RURAL |  | 3 | 200 | 600 | 0.0023234 | 1.1617e-05 | 0
2013-01-22 11:00 | FTR21 | LONG RURAL |  | 6 | 40 | 240 | 0.00092936 | 2.3234e-05 | 0
2013-01-22 13:05 | FTR21 | LONG RURAL |  | 3 | 45 | 135 | 0.00052276 | 1.1617e-05 | 0
2013-01-22 09:10 | LGA11 | LONG RURAL |  | 152 | 324 | 49248 | 0.1907 | 0.00058859 | 0
2013-01-22 09:10 | FTR21 | LONG RURAL |  | 23 | 375 | 8625 | 0.033399 | 8.9063e-05 | 0
2013-01-22 09:00 | WGI14 | SHORT RURAL |  | 61 | 60 | 3660 | 0.031849 | 0.00053082 | 0
2013-01-23 09:15 | FTR21 | LONG RURAL |  | 2 | 437 | 874 | 0.0033844 | 7.7446e-06 | 0
2013-01-23 13:50 | WGI22 | LONG RURAL |  | 2 | 170 | 340 | 0.0013166 | 7.7446e-06 | 0
2013-01-23 13:55 | WGI22 | LONG RURAL |  | 2 | 45 | 90 | 0.00034851 | 7.7446e-06 | 0
2013-01-22 12:20 | MFA23 | SHORT RURAL |  | 10 | 115 | 1150 | 0.010007 | 8.702e-05 | 0
2013-01-24 09:00 | FTR21 | LONG RURAL |  | 4 | 90 | 360 | 0.001394 | 1.5489e-05 | 0
2013-01-22 09:05 | SLE32 | SHORT RURAL |  | 1 | 137 | 137 | 0.0011922 | 8.702e-06 | 0
2013-01-24 09:00 | FTR21 | LONG RURAL |  | 87 | 228 | 19836 | 0.076811 | 0.00033689 | 0
2013-01-24 11:30 | FTR21 | LONG RURAL |  | 40 | 150 | 6000 | 0.023234 | 0.00015489 | 0
2013-01-23 09:35 | CNR3 | SHORT RURAL |  | 23 | 419 | 9637 | 0.083861 | 0.00020015 | 0
2013-01-23 09:40 | SLE31 | LONG RURAL |  | 5 | 315 | 1575 | 0.0060989 | 1.9362e-05 | 0
2013-01-23 08:35 | MFA34 | SHORT RURAL |  | 39 | 425 | 16575 | 0.14424 | 0.00033938 | 0
2013-01-23 09:22 | BDL5 | LONG RURAL |  | 3 | 218 | 654 | 0.0025325 | 1.1617e-05 | 0
2013-01-24 09:12 | BDL8 | LONG RURAL |  | 3 | 398.3333 | 1195 | 0.0046274 | 1.1617e-05 | 0
2013-01-24 12:45 | NLA34 | SHORT RURAL |  | 2 | 55 | 110 | 0.00095722 | 1.7404e-05 | 0
2013-01-21 11:50 | WN4 | SHORT RURAL |  | 1 | 37 | 37 | 0.00032197 | 8.702e-06 | 0
2013-01-22 09:40 | BN1 | LONG RURAL |  | 26 | 145 | 3770 | 0.014599 | 0.00010068 | 0
2013-01-24 09:40 | WGI22 | LONG RURAL |  | 2 | 150 | 300 | 0.0011617 | 7.7446e-06 | 0
2013-01-24 09:00 | WGI22 | LONG RURAL |  | 3 | 130 | 390 | 0.0015102 | 1.1617e-05 | 0
2013-01-25 09:05 | WGI22 | LONG RURAL |  | 5 | 115 | 575 | 0.0022266 | 1.9362e-05 | 0
2013-01-21 11:24 | WYK11 | SHORT RURAL |  | 101 | 116 | 11716 | 0.10195 | 0.0008789 | 0
2013-01-21 09:00 | WYK11 | SHORT RURAL |  | 2626 | 37.3267 | 98020 | 0.85297 | 0.022851 | 0
2013-01-24 09:02 | LDL21 | SHORT RURAL |  | 241 | 508 | 122428 | 1.0654 | 0.0020972 | 0
2013-01-23 09:00 | LDL21 | SHORT RURAL |  | 52 | 323 | 16796 | 0.14616 | 0.0004525 | 0
2013-01-24 10:30 | BDL5 | LONG RURAL |  | 13 | 210 | 2730 | 0.010571 | 5.034e-05 | 0
2013-01-21 09:03 | MSD2 | LONG RURAL |  | 2 | 52 | 104 | 0.00040272 | 7.7446e-06 | 0
2013-01-22 08:50 | KMS1 | SHORT RURAL |  | 9 | 100 | 900 | 0.0078318 | 7.8318e-05 | 0
2013-01-24 09:00 | BDL5 | LONG RURAL |  | 1 | 195 | 195 | 0.0007551 | 3.8723e-06 | 0
2013-01-25 08:30 | BDL1 | LONG RURAL |  | 1 | 95 | 95 | 0.00036787 | 3.8723e-06 | 0
2013-01-25 09:00 | BDL1 | LONG RURAL |  | 1 | 165 | 165 | 0.00063893 | 3.8723e-06 | 0
2013-01-16 11:35 | WT12 | URBAN |  | 479 | 158 | 75682 | 0.26364 | 0.0016686 | 0
2013-01-14 08:50 | PHM14 | LONG RURAL |  | 99 | 560 | 55440 | 0.21468 | 0.00038336 | 0
2013-01-18 09:16 | OFR23 | LONG RURAL |  | 39 | 205 | 7995 | 0.030959 | 0.00015102 | 0
2013-01-18 09:10 | CRE33 | SHORT RURAL |  | 17 | 140 | 2380 | 0.020711 | 0.00014793 | 0
2013-01-18 08:45 | OFR23 | LONG RURAL |  | 12 | 75 | 900 | 0.0034851 | 4.6468e-05 | 0
2013-01-18 10:25 | OFR23 | LONG RURAL |  | 2 | 40 | 80 | 0.00030979 | 7.7446e-06 | 0
2013-01-21 10:20 | BGE24 | SHORT RURAL |  | 22 | 127 | 2794 | 0.024313 | 0.00019144 | 0
2013-01-21 09:20 | BGE23 | SHORT RURAL |  | 3 | 240 | 720 | 0.0062654 | 2.6106e-05 | 0
2013-01-21 13:55 | BGE23 | SHORT RURAL |  | 2 | 25 | 50 | 0.0004351 | 1.7404e-05 | 0
2013-01-22 09:15 | SFS1 | SHORT RURAL |  | 226 | 400 | 90400 | 0.78666 | 0.0019666 | 0
2013-01-16 08:50 | ELM34 | URBAN |  | 166 | 470 | 78020 | 0.27178 | 0.00057826 | 0
2013-01-22 09:15 | BRT22 | SHORT RURAL |  | 45 | 285 | 12825 | 0.1116 | 0.00039159 | 0
2013-01-16 09:10 | WT13 | URBAN |  | 3 | 140 | 420 | 0.0014631 | 1.045e-05 | 0
2013-01-23 09:32 | MYT7 | LONG RURAL |  | 67 | 506 | 33902 | 0.13128 | 0.00025945 | 0
2013-01-22 09:25 | WN5 | LONG RURAL |  | 1 | 115 | 115 | 0.00044532 | 3.8723e-06 | 0
2013-01-21 09:20 | OFR23 | LONG RURAL |  | 67 | 228 | 15276 | 0.059153 | 0.00025945 | 0
2013-01-22 09:06 | WN4 | SHORT RURAL |  | 1 | 199 | 199 | 0.0017317 | 8.702e-06 | 0
2013-01-22 08:52 | OFR23 | LONG RURAL |  | 60 | 280 | 16800 | 0.065055 | 0.00023234 | 0
2013-01-22 09:00 | SMR5 | LONG RURAL |  | 4 | 245 | 980 | 0.0037949 | 1.5489e-05 | 0
2013-01-23 09:38 | WN5 | LONG RURAL |  | 8 | 292 | 2336 | 0.0090457 | 3.0979e-05 | 0
2013-01-23 09:47 | WN3 | LONG RURAL |  | 15 | 6 | 90 | 0.00034851 | 5.8085e-05 | 0
2013-01-25 08:52 | SLE21 | SHORT RURAL |  | 120 | 167.7833 | 20134 | 0.17521 | 0.0010442 | 0
2013-01-21 08:50 | BN6 | LONG RURAL |  | 3 | 210 | 630 | 0.0024396 | 1.1617e-05 | 0
2013-01-18 08:40 | WT13 | URBAN |  | 120 | 374 | 44880 | 0.15634 | 0.00041802 | 0
2013-01-18 10:30 | WT7 | URBAN |  | 246 | 270 | 66420 | 0.23137 | 0.00085694 | 0
2013-01-20 08:44 | CYN11 | URBAN |  | 5 | 461 | 2305 | 0.0080294 | 1.7417e-05 | 0
2013-01-21 09:00 | RWN26 | SHORT RURAL |  | 60 | 70 | 4200 | 0.036548 | 0.00052212 | 0
2013-01-21 11:10 | EPG12 | URBAN |  | 3 | 160 | 480 | 0.0016721 | 1.045e-05 | 0
2013-01-24 10:43 | SMR3 | LONG RURAL |  | 1 | 21 | 21 | 8.1319e-05 | 3.8723e-06 | 0
2013-01-25 08:45 | BN2 | LONG RURAL |  | 2 | 60 | 120 | 0.00046468 | 7.7446e-06 | 0
2013-01-25 09:25 | WYK12 | SHORT RURAL |  | 7 | 157 | 1099 | 0.0095635 | 6.0914e-05 | 0
2013-01-21 09:00 | RWN26 | SHORT RURAL |  | 6 | 140 | 840 | 0.0073097 | 5.2212e-05 | 0
2013-01-24 08:11 | WYK12 | SHORT RURAL |  | 28 | 224 | 6272 | 0.054579 | 0.00024366 | 0
2013-01-24 11:02 | WYK12 | SHORT RURAL |  | 3 | 42 | 126 | 0.0010964 | 2.6106e-05 | 0
2013-01-24 09:22 | MSD4 | LONG RURAL |  | 37 | 370 | 13690 | 0.053012 | 0.00014328 | 0
2013-01-22 10:42 | MYT2 | SHORT RURAL |  | 2 | 212 | 424 | 0.0036896 | 1.7404e-05 | 0
2013-01-21 11:40 | ELM12 | SHORT RURAL |  | 74 | 103 | 7622 | 0.066326 | 0.00064395 | 0
2013-01-23 08:20 | CYN22 | URBAN |  | 89 | 360 | 32040 | 0.11161 | 0.00031003 | 0
2013-01-24 08:35 | CYN22 | URBAN |  | 72 | 230 | 16560 | 0.057686 | 0.00025081 | 0
2013-01-24 09:47 | FTR12 | LONG RURAL |  | 148 | 479.1622 | 70916 | 0.27461 | 0.0005731 | 0
2013-01-23 08:30 | CLN23 | SHORT RURAL |  | 82 | 264.0122 | 21649 | 0.18839 | 0.00071356 | 0
2013-01-22 08:22 | LDL11 | URBAN |  | 13 | 477 | 6201 | 0.021601 | 4.5285e-05 | 0
2013-01-22 08:30 | RWN33 | URBAN |  | 120 | 422 | 50640 | 0.1764 | 0.00041802 | 0
2013-01-22 10:04 | FGY12 | URBAN |  | 77 | 393 | 30261 | 0.10541 | 0.00026823 | 0
2013-01-24 08:48 | RWN26 | SHORT RURAL |  | 238 | 242 | 57596 | 0.5012 | 0.0020711 | 0
2013-01-24 09:10 | BWR32 | URBAN |  | 105 | 160 | 16800 | 0.058523 | 0.00036577 | 0
2013-01-21 08:55 | FTR21 | LONG RURAL |  | 1 | 245 | 245 | 0.00094872 | 3.8723e-06 | 0
2013-01-21 09:25 | FTR21 | LONG RURAL |  | 1 | 20 | 20 | 7.7446e-05 | 3.8723e-06 | 0
2013-01-22 12:26 | EPG12 | URBAN |  | 1 | 277 | 277 | 0.00096492 | 3.4835e-06 | 0
2013-01-25 09:01 | WO22 | URBAN |  | 24 | 134 | 3216 | 0.011203 | 8.3604e-05 | 0
2013-01-21 12:00 | KLK1 | SHORT RURAL |  | 15 | 140 | 2100 | 0.018274 | 0.00013053 | 0
2013-01-23 09:20 | BWN14 | SHORT RURAL |  | 36 | 360 | 12960 | 0.11278 | 0.00031327 | 0
2013-01-24 08:40 | PHM33 | SHORT RURAL |  | 94 | 165 | 15510 | 0.13497 | 0.00081799 | 0
2013-01-24 08:45 | CLN22 | SHORT RURAL |  | 1 | 250 | 250 | 0.0021755 | 8.702e-06 | 0
2013-01-25 09:25 | BWN11 | SHORT RURAL |  | 183 | 234 | 42822 | 0.37264 | 0.0015925 | 0
2013-01-24 10:20 | CYN33 | SHORT RURAL |  | 578 | 281 | 162418 | 1.4134 | 0.0050297 | 0
2013-01-23 09:25 | KLO14 | LONG RURAL |  | 70 | 331 | 23170 | 0.089722 | 0.00027106 | 0
2013-01-30 08:05 | CYN22 | URBAN |  | 170 | 432.4353 | 73514 | 0.25608 | 0.00059219 | 0
2013-01-29 09:15 | WGL13 | SHORT RURAL |  | 1 | 195 | 195 | 0.0016969 | 8.702e-06 | 0
2013-01-29 09:15 | MOE32 | SHORT RURAL |  | 4 | 90 | 360 | 0.0031327 | 3.4808e-05 | 0
2013-01-31 09:45 | WGL13 | SHORT RURAL |  | 7 | 30 | 210 | 0.0018274 | 6.0914e-05 | 0
2013-01-31 11:10 | WGL13 | SHORT RURAL |  | 1 | 110 | 110 | 0.00095722 | 8.702e-06 | 0
2013-01-31 09:11 | TGN23 | SHORT RURAL |  | 12 | 419 | 5028 | 0.043754 | 0.00010442 | 0
2013-01-30 09:10 | WGL13 | SHORT RURAL |  | 1 | 250 | 250 | 0.0021755 | 8.702e-06 | 0
2013-01-30 09:35 | WGL13 | SHORT RURAL |  | 1 | 40 | 40 | 0.00034808 | 8.702e-06 | 0
2013-01-31 09:00 | PHI12 | SHORT RURAL |  | 282 | 420 | 118440 | 1.0307 | 0.002454 | 0
2013-01-30 09:15 | WGL13 | SHORT RURAL |  | 1 | 30 | 30 | 0.00026106 | 8.702e-06 | 0
2013-01-30 09:30 | MOE31 | LONG RURAL |  | 20 | 131 | 2620 | 0.010145 | 7.7446e-05 | 0
2013-01-30 09:10 | MWTS31 | SHORT RURAL |  | 16 | 200 | 3200 | 0.027846 | 0.00013923 | 0
2013-01-30 11:05 | WGL13 | SHORT RURAL |  | 1 | 30 | 30 | 0.00026106 | 8.702e-06 | 0
2013-01-30 11:15 | WGL13 | SHORT RURAL |  | 1 | 25 | 25 | 0.00021755 | 8.702e-06 | 0
2013-01-30 11:55 | WGL13 | SHORT RURAL |  | 1 | 48 | 48 | 0.00041769 | 8.702e-06 | 0
2013-01-30 12:20 | WGL13 | SHORT RURAL |  | 2 | 35 | 70 | 0.00060914 | 1.7404e-05 | 0
2013-01-30 13:12 | MWTS31 | SHORT RURAL |  | 8 | 68 | 544 | 0.0047339 | 6.9616e-05 | 0
2013-01-30 14:15 | WGL13 | SHORT RURAL |  | 2 | 35 | 70 | 0.00060914 | 1.7404e-05 | 0
2013-01-31 09:30 | TGN31 | LONG RURAL |  | 3 | 35 | 105 | 0.00040659 | 1.1617e-05 | 0
2013-01-31 10:40 | TGN31 | LONG RURAL |  | 2 | 45 | 90 | 0.00034851 | 7.7446e-06 | 0
2013-01-29 08:50 | WYK24 | SHORT RURAL |  | 21 | 465 | 9765 | 0.084975 | 0.00018274 | 0
2013-01-29 09:30 | FTR21 | LONG RURAL |  | 2 | 70 | 140 | 0.00054212 | 7.7446e-06 | 0
2013-01-29 09:05 | WYK24 | SHORT RURAL |  | 32 | 155 | 4960 | 0.043162 | 0.00027846 | 0
2013-01-30 09:40 | WGI22 | LONG RURAL |  | 13 | 212 | 2756 | 0.010672 | 5.034e-05 | 0
2013-01-30 09:15 | WGI22 | LONG RURAL |  | 11 | 130 | 1430 | 0.0055374 | 4.2595e-05 | 0
2013-01-29 08:30 | KLK1 | SHORT RURAL |  | 275 | 366 | 100650 | 0.87585 | 0.002393 | 0
2013-01-30 08:30 | WYK23 | SHORT RURAL |  | 135 | 372 | 50220 | 0.43701 | 0.0011748 | 0
2013-01-30 09:10 | WYK11 | SHORT RURAL |  | 1 | 70 | 70 | 0.00060914 | 8.702e-06 | 0
2013-01-30 10:40 | WYK11 | SHORT RURAL |  | 6 | 240 | 1440 | 0.012531 | 5.2212e-05 | 0
2013-01-30 09:25 | WGI31 | SHORT RURAL |  | 116 | 315 | 36540 | 0.31797 | 0.0010094 | 0
2013-01-30 09:00 | LGA11 | LONG RURAL |  | 2 | 335 | 670 | 0.0025945 | 7.7446e-06 | 0
2013-01-31 09:05 | FTR23 | LONG RURAL |  | 23 | 91 | 2093 | 0.0081048 | 8.9063e-05 | 0
2013-01-31 09:35 | WGI14 | SHORT RURAL |  | 38 | 205 | 7790 | 0.067788 | 0.00033067 | 0
2013-01-29 08:30 | BDL1 | LONG RURAL |  | 1 | 110 | 110 | 0.00042595 | 3.8723e-06 | 0
2013-01-31 09:00 | LGA11 | LONG RURAL |  | 149 | 298 | 44402 | 0.17194 | 0.00057697 | 0
2013-01-29 09:45 | SMR3 | LONG RURAL |  | 2 | 150 | 300 | 0.0011617 | 7.7446e-06 | 0
2013-01-29 09:32 | BN3 | SHORT RURAL |  | 15 | 203 | 3045 | 0.026498 | 0.00013053 | 0
2013-01-29 11:00 | BDL1 | LONG RURAL |  | 1 | 225 | 225 | 0.00087127 | 3.8723e-06 | 0
2013-01-31 08:58 | TGN14 | LONG RURAL |  | 306 | 255 | 78030 | 0.30216 | 0.0011849 | 0
2013-01-30 09:35 | WYK12 | SHORT RURAL |  | 342 | 245 | 83790 | 0.72914 | 0.0029761 | 0
2013-01-31 08:30 | WYK12 | SHORT RURAL |  | 9 | 90 | 810 | 0.0070486 | 7.8318e-05 | 0
2013-01-30 09:50 | BDL5 | LONG RURAL |  | 1 | 70 | 70 | 0.00027106 | 3.8723e-06 | 0
2013-01-30 11:40 | BDL1 | LONG RURAL |  | 1 | 170 | 170 | 0.00065829 | 3.8723e-06 | 0
2013-01-30 12:05 | BDL5 | LONG RURAL |  | 2 | 50 | 100 | 0.00038723 | 7.7446e-06 | 0
2013-01-31 08:42 | BDL1 | LONG RURAL |  | 2 | 98 | 196 | 0.00075897 | 7.7446e-06 | 0
2013-01-31 09:00 | BDL5 | LONG RURAL |  | 13 | 140 | 1820 | 0.0070476 | 5.034e-05 | 0
2013-01-31 09:15 | MFA21 | LONG RURAL |  | 28 | 138 | 3864 | 0.014963 | 0.00010842 | 0
2013-01-31 11:10 | BDL1 | LONG RURAL |  | 1 | 140 | 140 | 0.00054212 | 3.8723e-06 | 0
2013-01-31 09:00 | LGA11 | LONG RURAL |  | 39 | 535 | 20865 | 0.080796 | 0.00015102 | 0
2013-01-29 09:50 | LDL23 | LONG RURAL |  | 220 | 490 | 107800 | 0.41744 | 0.00085191 | 0
2013-01-30 09:30 | WYK23 | SHORT RURAL |  | 136 | 375 | 51000 | 0.4438 | 0.0011835 | 0
2013-01-30 14:15 | WGL13 | SHORT RURAL |  | 3 | 50 | 150 | 0.0013053 | 2.6106e-05 | 0
2013-01-29 09:41 | MYT7 | LONG RURAL |  | 16 | 94 | 1504 | 0.005824 | 6.1957e-05 | 0
2013-01-29 13:30 | BRT21 | SHORT RURAL |  | 1 | 50 | 50 | 0.0004351 | 8.702e-06 | 0
2013-01-30 09:03 | MBY12 | SHORT RURAL |  | 43 | 337 | 14491 | 0.1261 | 0.00037418 | 0
2013-01-30 09:15 | BRT21 | SHORT RURAL |  | 1 | 55 | 55 | 0.00047861 | 8.702e-06 | 0
2013-01-30 10:10 | WOTS24 | LONG RURAL |  | 2 | 90 | 180 | 0.00069702 | 7.7446e-06 | 0
2013-01-30 08:30 | CLN12 | SHORT RURAL |  | 80 | 304 | 24320 | 0.21163 | 0.00069616 | 0
2013-01-30 08:40 | CRE22 | URBAN |  | 104 | 360 | 37440 | 0.13042 | 0.00036228 | 0
2013-01-23 09:30 | ELM34 | URBAN |  | 238 | 405 | 96390 | 0.33577 | 0.00082907 | 0
2013-01-24 13:30 | BWR34 | URBAN |  | 143 | 150 | 21450 | 0.074721 | 0.00049814 | 0
2013-01-25 09:40 | CYN11 | URBAN |  | 50 | 380 | 19000 | 0.066186 | 0.00017417 | 0
2013-01-25 09:54 | BWR32 | URBAN |  | 217 | 398 | 86366 | 0.30085 | 0.00075592 | 0
2013-01-25 11:10 | TGN23 | SHORT RURAL |  | 1 | 60 | 60 | 0.00052212 | 8.702e-06 | 0
2013-01-27 10:20 | MOE32 | SHORT RURAL |  | 2 | 50 | 100 | 0.0008702 | 1.7404e-05 | 0
2013-01-21 13:20 | BN6 | LONG RURAL |  | 2 | 81 | 162 | 0.00062731 | 7.7446e-06 | 0
2013-01-23 09:20 | WT13 | URBAN |  | 394 | 425 | 167450 | 0.58331 | 0.0013725 | 0
2013-01-24 08:45 | KLO14 | LONG RURAL |  | 118 | 302 | 35636 | 0.13799 | 0.00045693 | 0
2013-01-27 13:10 | MOE32 | SHORT RURAL |  | 3 | 55 | 165 | 0.0014358 | 2.6106e-05 | 0
2013-01-27 11:35 | MOE32 | SHORT RURAL |  | 1 | 50 | 50 | 0.0004351 | 8.702e-06 | 0
2013-01-23 09:30 | WT13 | URBAN |  | 60 | 160 | 9600 | 0.033441 | 0.00020901 | 0
2013-01-25 09:59 | WT13 | URBAN |  | 95 | 219 | 20805 | 0.072474 | 0.00033093 | 0
2013-01-30 13:00 | BRT21 | SHORT RURAL |  | 2 | 70 | 140 | 0.0012183 | 1.7404e-05 | 0
2013-01-30 13:13 | MYT7 | LONG RURAL |  | 16 | 62 | 992 | 0.0038413 | 6.1957e-05 | 0
2013-01-31 09:50 | BRT21 | SHORT RURAL |  | 7 | 152 | 1064 | 0.0092589 | 6.0914e-05 | 0
2013-01-31 09:07 | BGE22 | SHORT RURAL |  | 24 | 353.9167 | 8494 | 0.073915 | 0.00020885 | 0
2013-01-30 13:10 | WN2 | LONG RURAL |  | 7 | 10 | 70 | 0.00027106 | 2.7106e-05 | 0
2013-01-24 09:00 | FGY33 | URBAN |  | 79 | 345 | 27255 | 0.094942 | 0.0002752 | 0
2013-01-24 08:45 | SFS1 | SHORT RURAL |  | 226 | 415 | 93790 | 0.81616 | 0.0019666 | 0
2013-01-24 09:15 | ELM33 | SHORT RURAL |  | 13 | 210 | 2730 | 0.023756 | 0.00011313 | 0
2013-01-31 13:20 | WGL13 | SHORT RURAL |  | 1 | 30 | 30 | 0.00026106 | 8.702e-06 | 0
2013-01-31 11:45 | TGN31 | LONG RURAL |  | 2 | 45 | 90 | 0.00034851 | 7.7446e-06 | 0
2013-01-31 13:45 | TGN31 | LONG RURAL |  | 1 | 65 | 65 | 0.0002517 | 3.8723e-06 | 0
2013-01-31 15:00 | TGN31 | LONG RURAL |  | 1 | 50 | 50 | 0.00019362 | 3.8723e-06 | 0
2013-02-01 11:22 | TGN31 | LONG RURAL |  | 2 | 23 | 46 | 0.00017813 | 7.7446e-06 | 0
2013-01-31 12:00 | WGI22 | LONG RURAL |  | 1 | 35 | 35 | 0.00013553 | 3.8723e-06 | 0
2013-01-31 12:30 | WGI22 | LONG RURAL |  | 2 | 60 | 120 | 0.00046468 | 7.7446e-06 | 0
2013-02-01 09:00 | FTR21 | LONG RURAL |  | 59 | 202 | 11918 | 0.04615 | 0.00022847 | 0
2013-02-01 09:04 | WGI14 | SHORT RURAL |  | 24 | 166 | 3984 | 0.034669 | 0.00020885 | 0
2013-02-01 09:35 | LDL24 | URBAN |  | 47 | 395 | 18565 | 0.064671 | 0.00016372 | 0
2013-02-01 09:13 | WGL13 | SHORT RURAL |  | 235 | 314 | 73790 | 0.64212 | 0.002045 | 0
2013-01-31 11:00 | WYK12 | SHORT RURAL |  | 3 | 50 | 150 | 0.0013053 | 2.6106e-05 | 0
2013-02-01 09:25 | TGN31 | LONG RURAL |  | 17 | 25 | 425 | 0.0016457 | 6.5829e-05 | 0
2013-02-01 13:10 | TGN23 | SHORT RURAL |  | 3 | 50 | 150 | 0.0013053 | 2.6106e-05 | 0
2013-02-01 09:00 | WYK12 | SHORT RURAL |  | 49 | 180 | 8820 | 0.076751 | 0.0004264 | 0
2013-01-31 13:40 | MFA21 | LONG RURAL |  | 8 | 105 | 840 | 0.0032527 | 3.0979e-05 | 0
2013-01-31 11:35 | BDL5 | LONG RURAL |  | 2 | 50 | 100 | 0.00038723 | 7.7446e-06 | 0
2013-02-01 09:40 | MFA22 | LONG RURAL |  | 343 | 241.4257 | 82809 | 0.32066 | 0.0013282 | 0
2013-02-01 08:45 | BDL1 | LONG RURAL |  | 3 | 305 | 915 | 0.0035432 | 1.1617e-05 | 0
2013-02-01 08:46 | CLN23 | SHORT RURAL |  | 191 | 254 | 48514 | 0.42217 | 0.0016621 | 0
2013-02-01 09:10 | LLG11 | SHORT RURAL |  | 2 | 65 | 130 | 0.0011313 | 1.7404e-05 | 0
2013-02-01 09:00 | OFR23 | LONG RURAL |  | 14 | 275 | 3850 | 0.014908 | 5.4212e-05 | 0
2013-02-01 09:00 | OFR21 | SHORT RURAL |  | 8 | 110 | 880 | 0.0076577 | 6.9616e-05 | 0
2013-02-01 10:50 | LLG12 | SHORT RURAL |  | 3 | 65 | 195 | 0.0016969 | 2.6106e-05 | 0
2013-01-29 09:10 | WN6 | LONG RURAL |  | 1 | 300 | 300 | 0.0011617 | 3.8723e-06 | 0
2013-01-31 09:18 | MYT7 | LONG RURAL |  | 228 | 397 | 90516 | 0.35051 | 0.00088289 | 0
2013-01-29 09:15 | WT13 | URBAN |  | 75 | 315 | 23625 | 0.082297 | 0.00026126 | 0
2013-01-26 09:00 | CYN13 | URBAN |  | 528 | 80 | 42240 | 0.14714 | 0.0018393 | 0
2013-01-18 09:45 | LLG11 | SHORT RURAL |  | 1 | 70 | 70 | 0.00060914 | 8.702e-06 | 0
2013-01-25 09:00 | RWN26 | SHORT RURAL |  | 12 | 270 | 3240 | 0.028194 | 0.00010442 | 0
2013-02-01 10:00 | WN2 | LONG RURAL |  | 15 | 260 | 3900 | 0.015102 | 5.8085e-05 | 0
2013-01-30 09:14 | WN2 | LONG RURAL |  | 16 | 248 | 3968 | 0.015365 | 6.1957e-05 | 0
2013-01-30 09:06 | EPG12 | URBAN |  | 423 | 134.0355 | 56697 | 0.1975 | 0.0014735 | 0
2013-01-21 13:45 | FTR12 | LONG RURAL |  | 4 | 62 | 248 | 0.00096033 | 1.5489e-05 | 0
2013-01-30 08:40 | SFS1 | SHORT RURAL |  | 227 | 365 | 82855 | 0.721 | 0.0019753 | 0
2013-01-31 08:10 | FGY14 | URBAN |  | 305 | 460 | 140300 | 0.48873 | 0.0010625 | 0
2013-01-29 09:40 | KLO14 | LONG RURAL |  | 429 | 305 | 130845 | 0.50667 | 0.0016612 | 0
2013-01-30 09:13 | KLO14 | LONG RURAL |  | 72 | 234 | 16848 | 0.065241 | 0.00027881 | 0
2013-01-30 09:12 | ELM33 | SHORT RURAL |  | 11 | 190 | 2090 | 0.018187 | 9.5722e-05 | 0
2013-01-30 12:05 | DRN11 | URBAN |  | 1 | 35 | 35 | 0.00012192 | 3.4835e-06 | 0
2013-01-30 14:00 | DRN11 | URBAN |  | 2 | 40 | 80 | 0.00027868 | 6.967e-06 | 0
2013-01-30 12:00 | ELM33 | SHORT RURAL |  | 22 | 95 | 2090 | 0.018187 | 0.00019144 | 0
2013-01-18 08:55 | ELM15 | SHORT RURAL |  | 13 | 321 | 4173 | 0.036313 | 0.00011313 | 0
2013-02-01 09:10 | WGI14 | SHORT RURAL |  | 1 | 80 | 80 | 0.00069616 | 8.702e-06 | 0
2013-02-01 14:25 | TGN23 | SHORT RURAL |  | 1 | 35 | 35 | 0.00030457 | 8.702e-06 | 0
2013-02-01 11:50 | BDL1 | LONG RURAL |  | 2 | 58 | 116 | 0.00044919 | 7.7446e-06 | 0
2013-02-01 13:15 | BDL1 | LONG RURAL |  | 1 | 75 | 75 | 0.00029042 | 3.8723e-06 | 0
2013-02-01 12:43 | LLG11 | SHORT RURAL |  | 9 | 62 | 558 | 0.0048557 | 7.8318e-05 | 0
2013-02-02 08:22 | OFR23 | LONG RURAL |  | 74 | 278 | 20572 | 0.079661 | 0.00028655 | 0
2013-01-29 09:20 | RWN31 | SHORT RURAL |  | 6 | 68 | 408 | 0.0035504 | 5.2212e-05 | 0
2013-01-30 14:30 | DRN11 | URBAN |  | 2 | 18 | 36 | 0.00012541 | 6.967e-06 | 0
2013-01-29 11:45 | RWN24 | SHORT RURAL |  | 5 | 60 | 300 | 0.0026106 | 4.351e-05 | 0
2013-01-31 08:05 | ELM33 | SHORT RURAL |  | 4 | 150 | 600 | 0.0052212 | 3.4808e-05 | 0
2013-01-29 12:55 | RWN24 | SHORT RURAL |  | 2 | 60 | 120 | 0.0010442 | 1.7404e-05 | 0
2013-01-31 15:00 | BDL6 | SHORT RURAL |  | 60 | 70 | 4200 | 0.036548 | 0.00052212 | 0
2013-01-29 09:20 | SMR5 | LONG RURAL |  | 44 | 200 | 8800 | 0.034076 | 0.00017038 | 0
2013-01-29 12:30 | WGL11 | SHORT RURAL |  | 1 | 50 | 50 | 0.0004351 | 8.702e-06 | 0
2013-01-30 10:30 | SMR3 | LONG RURAL |  | 1 | 235 | 235 | 0.00090999 | 3.8723e-06 | 0
2013-01-30 08:32 | RWT11 | URBAN |  | 90 | 358 | 32220 | 0.11224 | 0.00031351 | 0
2013-01-31 09:45 | SMR3 | LONG RURAL |  | 1 | 145 | 145 | 0.00056149 | 3.8723e-06 | 0
2013-01-31 08:05 | MFA21 | LONG RURAL |  | 2 | 265 | 530 | 0.0020523 | 7.7446e-06 | 0
2013-01-31 09:25 | SMR5 | LONG RURAL |  | 2 | 55 | 110 | 0.00042595 | 7.7446e-06 | 0
2013-01-25 08:37 | BN2 | LONG RURAL |  | 12 | 152 | 1824 | 0.0070631 | 4.6468e-05 | 0
2013-01-31 13:45 | BRT21 | SHORT RURAL |  | 3 | 40 | 120 | 0.0010442 | 2.6106e-05 | 0
2013-02-03 08:05 | WO31 | URBAN |  | 4 | 437.5 | 1750 | 0.0060961 | 1.3934e-05 | 0
2013-02-05 07:18 | MYT7 | LONG RURAL |  | 1 | 157 | 157 | 0.00060795 | 3.8723e-06 | 0
2013-01-31 12:35 | ELM33 | SHORT RURAL |  | 13 | 110 | 1430 | 0.012444 | 0.00011313 | 0
2013-01-31 09:45 | BWR13 | SHORT RURAL |  | 75 | 317 | 23775 | 0.20689 | 0.00065265 | 0
2013-02-01 09:36 | ELM32 | URBAN |  | 79 | 324 | 25596 | 0.089163 | 0.0002752 | 0
2013-02-01 08:32 | BGE22 | SHORT RURAL |  | 102 | 327 | 33354 | 0.29025 | 0.0008876 | 0
2013-02-01 08:40 | SFS1 | SHORT RURAL |  | 187 | 540 | 100980 | 0.87872 | 0.0016273 | 0
2013-02-01 08:20 | NRN13 | URBAN |  | 87 | 450 | 39150 | 0.13638 | 0.00030306 | 0
2013-02-02 09:00 | WT13 | URBAN |  | 3 | 110 | 330 | 0.0011495 | 1.045e-05 | 0
2013-02-02 08:52 | EPG32 | SHORT RURAL |  | 1 | 23 | 23 | 0.00020015 | 8.702e-06 | 0
2013-02-03 09:10 | WGL12 | LONG RURAL |  | 234 | 139 | 32526 | 0.12595 | 0.00090612 | 0
2013-02-03 08:35 | FTR23 | LONG RURAL |  | 88 | 210 | 18480 | 0.07156 | 0.00034076 | 0
2013-02-03 09:29 | WGI22 | LONG RURAL |  | 175 | 198 | 34650 | 0.13418 | 0.00067766 | 0
2013-02-03 09:10 | LLG12 | SHORT RURAL |  | 301 | 260 | 78260 | 0.68102 | 0.0026193 | 0
2013-02-03 08:35 | BWN13 | URBAN |  | 48 | 215 | 10320 | 0.03595 | 0.00016721 | 0
2013-02-03 08:50 | KLK1 | SHORT RURAL |  | 71 | 173 | 12283 | 0.10689 | 0.00061784 | 0
2013-02-02 13:09 | EPG32 | SHORT RURAL |  | 1 | 16 | 16 | 0.00013923 | 8.702e-06 | 0
2013-02-02 11:53 | EPG32 | SHORT RURAL |  | 1 | 9 | 9 | 7.8318e-05 | 8.702e-06 | 0
2013-01-30 09:00 | FTR23 | LONG RURAL |  | 5 | 127 | 635 | 0.0024589 | 1.9362e-05 | 0
2013-01-22 12:50 | BN1 | LONG RURAL |  | 4 | 100 | 400 | 0.0015489 | 1.5489e-05 | 0
2013-01-24 08:25 | EPG13 | SHORT RURAL |  | 224 | 636.9643 | 142680 | 1.2416 | 0.0019492 | 0
2013-01-31 08:43 | RWT11 | URBAN |  | 357 | 449 | 160293 | 0.55838 | 0.0012436 | 0
2013-01-29 08:45 | BGE12 | SHORT RURAL |  | 41 | 200 | 8200 | 0.071356 | 0.00035678 | 0
2013-01-29 10:50 | BGE12 | SHORT RURAL |  | 20 | 120 | 2400 | 0.020885 | 0.00017404 | 0
2013-01-22 09:11 | SMR8 | LONG RURAL |  | 6 | 189 | 1134 | 0.0043912 | 2.3234e-05 | 0
2013-02-01 09:02 | BN1 | LONG RURAL |  | 3 | 68 | 204 | 0.00078995 | 1.1617e-05 | 0
2013-02-01 12:30 | BN1 | LONG RURAL |  | 6 | 90 | 540 | 0.002091 | 2.3234e-05 | 0
2013-02-01 09:40 | BN1 | LONG RURAL |  | 3 | 78 | 234 | 0.00090612 | 1.1617e-05 | 0
2013-02-01 11:15 | BN1 | LONG RURAL |  | 2 | 65 | 130 | 0.0005034 | 7.7446e-06 | 0
2013-02-02 10:30 | EPG32 | SHORT RURAL |  | 1 | 66 | 66 | 0.00057433 | 8.702e-06 | 0
2013-01-30 08:30 | OFR21 | SHORT RURAL |  | 1 | 25 | 25 | 0.00021755 | 8.702e-06 | 0
2013-02-04 09:40 | TGN31 | LONG RURAL |  | 3 | 182 | 546 | 0.0021143 | 1.1617e-05 | 0
2013-02-04 09:15 | LGA11 | LONG RURAL |  | 3 | 164 | 492 | 0.0019052 | 1.1617e-05 | 0
2013-02-04 11:05 | TGN23 | SHORT RURAL |  | 11 | 15 | 165 | 0.0014358 | 9.5722e-05 | 0
2013-02-04 09:05 | WYK23 | SHORT RURAL |  | 74 | 305 | 22570 | 0.1964 | 0.00064395 | 0
2013-02-04 10:50 | WYK12 | SHORT RURAL |  | 23 | 174 | 4002 | 0.034825 | 0.00020015 | 0
2013-02-03 13:35 | WGL21 | LONG RURAL |  | 4 | 50 | 200 | 0.00077446 | 1.5489e-05 | 0
2013-02-04 09:46 | MOE22 | LONG RURAL |  | 101 | 174 | 17574 | 0.068052 | 0.0003911 | 0
2013-02-04 09:05 | LGA11 | LONG RURAL |  | 34 | 384 | 13056 | 0.050557 | 0.00013166 | 0
2013-02-04 09:15 | WGI22 | LONG RURAL |  | 2 | 38 | 76 | 0.0002943 | 7.7446e-06 | 0
2013-02-04 09:09 | MFA21 | LONG RURAL |  | 1017 | 376 | 382392 | 1.4807 | 0.0039381 | 0
2013-02-03 13:50 | WGL23 | SHORT RURAL |  | 6 | 105 | 630 | 0.0054822 | 5.2212e-05 | 0
2013-02-04 08:30 | RWN31 | SHORT RURAL |  | 87 | 155 | 13485 | 0.11735 | 0.00075707 | 0
2013-02-04 09:42 | FGY13 | SHORT RURAL |  | 126 | 354 | 44604 | 0.38814 | 0.0010964 | 0
2013-02-04 08:30 | SFS1 | SHORT RURAL |  | 227 | 478 | 108506 | 0.94422 | 0.0019753 | 0
2013-02-01 09:30 | SMR3 | LONG RURAL |  | 1 | 105 | 105 | 0.00040659 | 3.8723e-06 | 0
2013-01-30 09:05 | OFR23 | LONG RURAL |  | 4 | 70 | 280 | 0.0010842 | 1.5489e-05 | 0
2013-01-23 12:00 | MYT7 | LONG RURAL |  | 1 | 30 | 30 | 0.00011617 | 3.8723e-06 | 0
2013-01-30 08:30 | OFR21 | SHORT RURAL |  | 3 | 22 | 66 | 0.00057433 | 2.6106e-05 | 0
2013-01-30 10:20 | OFR21 | SHORT RURAL |  | 2 | 36 | 72 | 0.00062654 | 1.7404e-05 | 0
2013-01-29 09:00 | WO31 | URBAN |  | 36 | 255 | 9180 | 0.031978 | 0.00012541 | 0
2013-01-29 09:00 | WO31 | URBAN |  | 57 | 50 | 2850 | 0.0099279 | 0.00019856 | 0
2013-02-01 08:30 | BRA14 | URBAN |  | 143 | 268 | 38324 | 0.1335 | 0.00049814 | 0
2013-02-01 14:15 | BWR34 | URBAN |  | 39 | 120 | 4680 | 0.016303 | 0.00013586 | 0
2013-01-30 10:00 | WO31 | URBAN |  | 3 | 300 | 900 | 0.0031351 | 1.045e-05 | 0
2013-02-01 08:47 | OFR23 | LONG RURAL |  | 2 | 233 | 466 | 0.0018045 | 7.7446e-06 | 0
2013-02-05 09:05 | TGN14 | LONG RURAL |  | 106 | 156 | 16536 | 0.064033 | 0.00041047 | 0
2013-02-05 09:30 | WGL24 | LONG RURAL |  | 3 | 120 | 360 | 0.001394 | 1.1617e-05 | 0
2013-02-05 10:00 | WGL21 | LONG RURAL |  | 8 | 260 | 2080 | 0.0080544 | 3.0979e-05 | 0
2013-02-06 09:20 | WGL24 | LONG RURAL |  | 1 | 155 | 155 | 0.00060021 | 3.8723e-06 | 0
2013-02-06 09:00 | WGL24 | LONG RURAL |  | 28 | 210 | 5880 | 0.022769 | 0.00010842 | 0
2013-02-06 09:15 | WGL21 | LONG RURAL |  | 18 | 236 | 4248 | 0.01645 | 6.9702e-05 | 0
2013-02-06 12:10 | WGL24 | LONG RURAL |  | 2 | 25 | 50 | 0.00019362 | 7.7446e-06 | 0
2013-02-06 12:53 | WGL24 | LONG RURAL |  | 4 | 33 | 132 | 0.00051115 | 1.5489e-05 | 0
2013-02-07 09:00 | WGL23 | SHORT RURAL |  | 1 | 165 | 165 | 0.0014358 | 8.702e-06 | 0
2013-02-05 09:25 | LLG13 | SHORT RURAL |  | 30 | 230 | 6900 | 0.060044 | 0.00026106 | 0
2013-02-05 09:00 | MOE31 | LONG RURAL |  | 144 | 336 | 48384 | 0.18736 | 0.00055761 | 0
2013-02-05 09:15 | WGL24 | LONG RURAL |  | 26 | 330 | 8580 | 0.033224 | 0.00010068 | 0
2013-02-06 09:32 | TGN14 | LONG RURAL |  | 38 | 273 | 10374 | 0.040171 | 0.00014715 | 0
2013-02-06 09:00 | MWTS31 | SHORT RURAL |  | 2 | 90 | 180 | 0.0015664 | 1.7404e-05 | 0
2013-02-06 09:00 | MWTS31 | SHORT RURAL |  | 56 | 195 | 10920 | 0.095026 | 0.00048731 | 0
2013-02-06 08:57 | MWTS14 | SHORT RURAL |  | 125 | 537 | 67125 | 0.58412 | 0.0010877 | 0
2013-02-06 09:20 | TGN11 | SHORT RURAL |  | 2 | 175 | 350 | 0.0030457 | 1.7404e-05 | 0
2013-02-06 09:00 | TGN31 | LONG RURAL |  | 32 | 192 | 6144 | 0.023791 | 0.00012391 | 0
2013-02-05 09:40 | FTR21 | LONG RURAL |  | 98 | 250 | 24500 | 0.094872 | 0.00037949 | 0
2013-02-05 12:45 | LGA11 | LONG RURAL |  | 7 | 75 | 525 | 0.002033 | 2.7106e-05 | 0
2013-02-06 09:00 | FTR21 | LONG RURAL |  | 16 | 180 | 2880 | 0.011152 | 6.1957e-05 | 0
2013-02-06 09:00 | LGA23 | LONG RURAL |  | 49 | 325 | 15925 | 0.061667 | 0.00018974 | 0
2013-02-07 08:30 | TGN31 | LONG RURAL |  | 1 | 105 | 105 | 0.00040659 | 3.8723e-06 | 0
2013-02-05 08:55 | MDG1 | SHORT RURAL |  | 568 | 264 | 149952 | 1.3049 | 0.0049427 | 0
2013-02-05 12:00 | WYK12 | SHORT RURAL |  | 1 | 146 | 146 | 0.0012705 | 8.702e-06 | 0
2013-02-05 08:50 | WYK12 | SHORT RURAL |  | 4 | 179 | 716 | 0.0062306 | 3.4808e-05 | 0
2013-02-06 08:40 | BDL3 | SHORT RURAL |  | 10 | 160 | 1600 | 0.013923 | 8.702e-05 | 0
2013-02-06 09:05 | MWTS31 | SHORT RURAL |  | 1 | 65 | 65 | 0.00056563 | 8.702e-06 | 0
2013-02-07 09:30 | MOE32 | SHORT RURAL |  | 3 | 240 | 720 | 0.0062654 | 2.6106e-05 | 0
2013-02-06 08:30 | BN6 | LONG RURAL |  | 28 | 425 | 11900 | 0.046081 | 0.00010842 | 0
2013-02-07 09:45 | WGI23 | SHORT RURAL |  | 19 | 175 | 3325 | 0.028934 | 0.00016534 | 0
2013-02-07 09:12 | WGI23 | SHORT RURAL |  | 75 | 217.4 | 16305 | 0.14189 | 0.00065265 | 0
2013-02-06 08:30 | CLN23 | SHORT RURAL |  | 99 | 770 | 76230 | 0.66335 | 0.0008615 | 0
2013-02-06 09:50 | LGA22 | SHORT RURAL |  | 3 | 85 | 255 | 0.002219 | 2.6106e-05 | 0
2013-02-07 11:20 | CLN13 | SHORT RURAL |  | 2 | 80 | 160 | 0.0013923 | 1.7404e-05 | 0
2013-02-05 10:35 | WGL13 | SHORT RURAL |  | 1 | 260 | 260 | 0.0022625 | 8.702e-06 | 0
2013-02-06 08:05 | WYK11 | SHORT RURAL |  | 164 | 296 | 48544 | 0.42243 | 0.0014271 | 0
2013-02-05 10:20 | TGN31 | LONG RURAL |  | 3 | 55 | 165 | 0.00063893 | 1.1617e-05 | 0
2013-02-06 09:10 | WGI14 | SHORT RURAL |  | 124 | 380 | 47120 | 0.41004 | 0.001079 | 0
2013-02-05 09:14 | WO22 | URBAN |  | 34 | 14 | 476 | 0.0016581 | 0.00011844 | 0
2013-02-05 09:05 | TGN23 | SHORT RURAL |  | 17 | 297 | 5049 | 0.043936 | 0.00014793 | 0
2013-02-06 11:35 | MYT8 | SHORT RURAL |  | 2 | 35 | 70 | 0.00060914 | 1.7404e-05 | 0
2013-02-05 09:00 | TGN31 | LONG RURAL |  | 1 | 55 | 55 | 0.00021298 | 3.8723e-06 | 0
2013-02-07 09:00 | WYK23 | SHORT RURAL |  | 74 | 260 | 19240 | 0.16743 | 0.00064395 | 0
2013-02-05 09:50 | TGN23 | SHORT RURAL |  | 1 | 35 | 35 | 0.00030457 | 8.702e-06 | 0
2013-02-05 11:50 | TGN31 | LONG RURAL |  | 11 | 70 | 770 | 0.0029817 | 4.2595e-05 | 0
2013-02-05 08:00 | MFA23 | SHORT RURAL |  | 10 | 465 | 4650 | 0.040464 | 8.702e-05 | 0
2013-02-05 10:40 | TGN23 | SHORT RURAL |  | 1 | 35 | 35 | 0.00030457 | 8.702e-06 | 0
2013-02-05 11:15 | TGN23 | SHORT RURAL |  | 2 | 35 | 70 | 0.00060914 | 1.7404e-05 | 0
2013-02-05 13:00 | TGN23 | SHORT RURAL |  | 1 | 58 | 58 | 0.00050471 | 8.702e-06 | 0
2013-02-05 14:00 | TGN31 | LONG RURAL |  | 1 | 95 | 95 | 0.00036787 | 3.8723e-06 | 0
2013-02-05 09:36 | WGL21 | LONG RURAL |  | 5 | 65 | 325 | 0.0012585 | 1.9362e-05 | 0
2013-02-05 13:50 | WGL21 | LONG RURAL |  | 2 | 35 | 70 | 0.00027106 | 7.7446e-06 | 0
2013-02-05 09:02 | FTR23 | LONG RURAL |  | 17 | 271 | 4607 | 0.01784 | 6.5829e-05 | 0
2013-02-06 08:45 | LGA21 | SHORT RURAL |  | 2 | 130 | 260 | 0.0022625 | 1.7404e-05 | 0
2013-02-06 11:45 | LGA24 | SHORT RURAL |  | 1 | 120 | 120 | 0.0010442 | 8.702e-06 | 0
2013-02-07 09:35 | PHI11 | SHORT RURAL |  | 14 | 280 | 3920 | 0.034112 | 0.00012183 | 0
2013-02-05 09:15 | FTR12 | LONG RURAL |  | 4 | 175 | 700 | 0.0027106 | 1.5489e-05 | 0
2013-02-05 13:25 | FTR12 | LONG RURAL |  | 4 | 50 | 200 | 0.00077446 | 1.5489e-05 | 0
2013-02-05 08:45 | BDL4 | SHORT RURAL |  | 48 | 50 | 2400 | 0.020885 | 0.00041769 | 0
2013-02-05 08:45 | SLE31 | LONG RURAL |  | 1 | 50 | 50 | 0.00019362 | 3.8723e-06 | 0
2013-01-24 08:30 | DRN12 | URBAN |  | 212 | 590 | 125080 | 0.43571 | 0.0007385 | 0
2013-02-01 13:00 | RWT22 | URBAN |  | 91 | 75 | 6825 | 0.023775 | 0.000317 | 0
2013-02-02 08:00 | BWR24 | URBAN |  | 10 | 410 | 4100 | 0.014282 | 3.4835e-05 | 0
2013-02-01 10:20 | KLO24 | SHORT RURAL |  | 3 | 95 | 285 | 0.0024801 | 2.6106e-05 | 0
2013-02-04 09:20 | WT12 | URBAN |  | 94 | 85 | 7990 | 0.027833 | 0.00032745 | 0
2013-02-04 09:55 | ELM33 | SHORT RURAL |  | 5 | 115 | 575 | 0.0050036 | 4.351e-05 | 0
2013-02-04 09:25 | WT10 | URBAN |  | 177 | 185 | 32745 | 0.11407 | 0.00061658 | 0
2013-02-04 13:10 | ELM15 | SHORT RURAL |  | 74 | 70 | 5180 | 0.045076 | 0.00064395 | 0
2013-02-05 08:17 | ELM33 | SHORT RURAL |  | 119 | 341 | 40579 | 0.35312 | 0.0010355 | 0
2013-02-05 10:00 | NLA31 | LONG RURAL |  | 3 | 90 | 270 | 0.0010455 | 1.1617e-05 | 0
2013-02-04 09:15 | RWN24 | SHORT RURAL |  | 28 | 45 | 1260 | 0.010964 | 0.00024366 | 0
2013-02-02 09:30 | FTR12 | LONG RURAL |  | 1 | 185 | 185 | 0.00071638 | 3.8723e-06 | 0
2013-02-04 12:00 | RWN24 | SHORT RURAL |  | 24 | 90 | 2160 | 0.018796 | 0.00020885 | 0
2013-02-04 12:30 | RWN31 | SHORT RURAL |  | 108 | 135 | 14580 | 0.12687 | 0.00093981 | 0
2013-02-03 09:50 | SLE31 | LONG RURAL |  | 1 | 310 | 310 | 0.0012004 | 3.8723e-06 | 0
2013-02-05 10:20 | BDL8 | LONG RURAL |  | 2 | 120 | 240 | 0.00092936 | 7.7446e-06 | 0
2013-02-05 11:15 | NLA31 | LONG RURAL |  | 2 | 70 | 140 | 0.00054212 | 7.7446e-06 | 0
2013-02-05 12:50 | NLA31 | LONG RURAL |  | 1 | 85 | 85 | 0.00032915 | 3.8723e-06 | 0
2013-02-05 11:30 | BDL2 | SHORT RURAL |  | 82 | 40 | 3280 | 0.028542 | 0.00071356 | 0
2013-02-05 09:10 | NRN14 | URBAN |  | 80 | 364 | 29120 | 0.10144 | 0.00027868 | 0
2013-02-05 09:48 | NRN14 | URBAN |  | 145 | 420 | 60900 | 0.21214 | 0.00050511 | 0
2013-02-05 11:00 | SLE31 | LONG RURAL |  | 10 | 15 | 150 | 0.00058085 | 3.8723e-05 | 0
2013-02-05 09:15 | BGE22 | SHORT RURAL |  | 24 | 665 | 15960 | 0.13888 | 0.00020885 | 0
2013-02-05 13:00 | BGE11 | SHORT RURAL |  | 8 | 80 | 640 | 0.0055693 | 6.9616e-05 | 0
2013-02-02 08:45 | TT7 | URBAN |  | 1 | 15 | 15 | 5.2252e-05 | 3.4835e-06 | 0
2013-02-05 09:48 | DRN11 | URBAN |  | 107 | 198 | 21186 | 0.073801 | 0.00037273 | 0
2013-02-05 09:15 | WT11 | URBAN |  | 95 | 285 | 27075 | 0.094315 | 0.00033093 | 0
2013-02-08 09:55 | WGL13 | SHORT RURAL |  | 4 | 125 | 500 | 0.004351 | 3.4808e-05 | 0
2013-02-08 09:27 | WGL21 | LONG RURAL |  | 3 | 24 | 72 | 0.00027881 | 1.1617e-05 | 0
2013-02-08 08:31 | TGN14 | LONG RURAL |  | 39 | 123 | 4797 | 0.018575 | 0.00015102 | 0
2013-02-08 10:15 | WN5 | LONG RURAL |  | 4 | 45 | 180 | 0.00069702 | 1.5489e-05 | 0
2013-02-08 09:44 | PHI11 | SHORT RURAL |  | 10 | 226 | 2260 | 0.019666 | 8.702e-05 | 0
2013-02-08 10:30 | PHI12 | SHORT RURAL |  | 1 | 45 | 45 | 0.00039159 | 8.702e-06 | 0
2013-02-07 09:05 | LDL13 | SHORT RURAL |  | 2 | 65 | 130 | 0.0011313 | 1.7404e-05 | 0
2013-02-08 09:25 | FTR21 | LONG RURAL |  | 22 | 315 | 6930 | 0.026835 | 8.5191e-05 | 0
2013-02-08 09:20 | FTR21 | LONG RURAL |  | 65 | 195 | 12675 | 0.049082 | 0.0002517 | 0
2013-02-08 09:00 | LGA12 | SHORT RURAL |  | 67 | 200 | 13400 | 0.11661 | 0.00058303 | 0
2013-02-07 10:30 | OFR23 | LONG RURAL |  | 9 | 60 | 540 | 0.002091 | 3.4851e-05 | 0
2013-02-06 09:15 | MFA21 | LONG RURAL |  | 2 | 185 | 370 | 0.0014328 | 7.7446e-06 | 0
2013-02-06 09:25 | LGA13 | LONG RURAL |  | 2 | 35 | 70 | 0.00027106 | 7.7446e-06 | 0
2013-02-02 08:35 | TGN31 | LONG RURAL |  | 1 | 75 | 75 | 0.00029042 | 3.8723e-06 | 0
2013-02-02 10:20 | TGN31 | LONG RURAL |  | 1 | 55 | 55 | 0.00021298 | 3.8723e-06 | 0
2013-02-02 11:50 | TGN31 | LONG RURAL |  | 1 | 55 | 55 | 0.00021298 | 3.8723e-06 | 0
2013-02-07 09:00 | MWTS14 | SHORT RURAL |  | 2 | 65 | 130 | 0.0011313 | 1.7404e-05 | 0
2013-02-02 13:32 | TGN31 | LONG RURAL |  | 2 | 38 | 76 | 0.0002943 | 7.7446e-06 | 0
2013-02-07 08:40 | MWTS14 | SHORT RURAL |  | 1 | 45 | 45 | 0.00039159 | 8.702e-06 | 0
2013-02-07 09:50 | MWTS14 | SHORT RURAL |  | 1 | 50 | 50 | 0.0004351 | 8.702e-06 | 0
2013-02-07 11:00 | MWTS14 | SHORT RURAL |  | 2 | 75 | 150 | 0.0013053 | 1.7404e-05 | 0
2013-02-03 08:37 | TGN31 | LONG RURAL |  | 4 | 55 | 220 | 0.00085191 | 1.5489e-05 | 0
2013-02-07 11:10 | MWTS14 | SHORT RURAL |  | 2 | 50 | 100 | 0.0008702 | 1.7404e-05 | 0
2013-02-05 08:40 | RWN24 | SHORT RURAL |  | 55 | 135 | 7425 | 0.064612 | 0.00047861 | 0
2013-02-04 12:50 | MYT7 | LONG RURAL |  | 3 | 115 | 345 | 0.0013359 | 1.1617e-05 | 0
2013-02-03 10:12 | TGN31 | LONG RURAL |  | 1 | 28 | 28 | 0.00010842 | 3.8723e-06 | 0
2013-02-03 11:15 | TGN31 | LONG RURAL |  | 1 | 38 | 38 | 0.00014715 | 3.8723e-06 | 0
2013-02-03 12:18 | TGN31 | LONG RURAL |  | 3 | 27 | 81 | 0.00031366 | 1.1617e-05 | 0
2013-02-06 09:10 | BDL6 | SHORT RURAL |  | 61 | 550 | 33550 | 0.29195 | 0.00053082 | 0
2013-02-06 09:45 | RWN31 | SHORT RURAL |  | 2 | 28 | 56 | 0.00048731 | 1.7404e-05 | 0
2013-02-06 08:45 | RWN31 | SHORT RURAL |  | 4 | 25 | 100 | 0.0008702 | 3.4808e-05 | 0
2013-02-04 09:29 | SMR5 | LONG RURAL |  | 37 | 256 | 9472 | 0.036679 | 0.00014328 | 0
2013-02-04 09:50 | ALA01 | LONG RURAL |  | 17 | 185 | 3145 | 0.012178 | 6.5829e-05 | 0
2013-02-06 10:35 | RWN31 | SHORT RURAL |  | 10 | 27 | 270 | 0.0023495 | 8.702e-05 | 0
2013-02-08 11:00 | WGL11 | SHORT RURAL |  | 1 | 15 | 15 | 0.00013053 | 8.702e-06 | 0
2013-02-08 13:15 | CLN22 | SHORT RURAL |  | 1 | 126 | 126 | 0.0010964 | 8.702e-06 | 0
2013-02-09 09:00 | MWTS31 | SHORT RURAL |  | 3 | 45 | 135 | 0.0011748 | 2.6106e-05 | 0
2013-02-09 09:00 | MOE14 | SHORT RURAL |  | 11 | 401 | 4411 | 0.038384 | 9.5722e-05 | 0
2013-02-09 10:05 | MWTS31 | SHORT RURAL |  | 1 | 50 | 50 | 0.0004351 | 8.702e-06 | 0
2013-02-05 09:00 | SMR3 | LONG RURAL |  | 24 | 210 | 5040 | 0.019516 | 9.2936e-05 | 0
2013-02-05 13:12 | ALA01 | LONG RURAL |  | 7 | 73 | 511 | 0.0019788 | 2.7106e-05 | 0
2013-02-05 09:30 | SMR8 | LONG RURAL |  | 12 | 195 | 2340 | 0.0090612 | 4.6468e-05 | 0
2013-02-07 11:10 | MOE22 | LONG RURAL |  | 2 | 40 | 80 | 0.00030979 | 7.7446e-06 | 0
2013-02-07 12:25 | MOE22 | LONG RURAL |  | 2 | 35 | 70 | 0.00027106 | 7.7446e-06 | 0
2013-02-03 09:34 | WT11 | URBAN |  | 207 | 304 | 62928 | 0.21921 | 0.00072108 | 0
2013-01-24 10:01 | BN2 | LONG RURAL |  | 21 | 221 | 4641 | 0.017971 | 8.1319e-05 | 0
2013-02-05 09:00 | MBY11 | SHORT RURAL |  | 88 | 360 | 31680 | 0.27568 | 0.00076577 | 0
2013-02-05 09:20 | RWT25 | URBAN |  | 55 | 300 | 16500 | 0.057477 | 0.00019159 | 0
2013-02-05 08:45 | BRA11 | URBAN |  | 229 | 415 | 95035 | 0.33105 | 0.00079772 | 0
2013-02-10 09:00 | TGN31 | LONG RURAL |  | 107 | 344 | 36808 | 0.14253 | 0.00041434 | 0
2013-02-10 09:00 | MOE31 | LONG RURAL |  | 26 | 160 | 4160 | 0.016109 | 0.00010068 | 0
2013-02-10 08:32 | BWN13 | URBAN |  | 91 | 204 | 18564 | 0.064667 | 0.000317 | 0
2013-02-09 11:30 | MWTS31 | SHORT RURAL |  | 2 | 40 | 80 | 0.00069616 | 1.7404e-05 | 0
2013-02-10 08:03 | WN6 | LONG RURAL |  | 2 | 312 | 624 | 0.0024163 | 7.7446e-06 | 0
2013-02-09 12:50 | TGN11 | SHORT RURAL |  | 1 | 40 | 40 | 0.00034808 | 8.702e-06 | 0
2013-02-08 10:04 | MDG1 | SHORT RURAL |  | 49 | 191 | 9359 | 0.081442 | 0.0004264 | 0
2013-02-05 08:45 | EPG34 | URBAN |  | 85 | 525 | 44625 | 0.15545 | 0.0002961 | 0
2013-02-05 09:32 | ALA01 | LONG RURAL |  | 17 | 128 | 2176 | 0.0084262 | 6.5829e-05 | 0
2013-02-05 09:55 | ELM13 | URBAN |  | 157 | 225 | 35325 | 0.12305 | 0.00054691 | 0
2013-02-09 09:00 | SLE31 | LONG RURAL |  | 30 | 325 | 9750 | 0.037755 | 0.00011617 | 0
2013-02-04 10:00 | WN3 | LONG RURAL |  | 4 | 270 | 1080 | 0.0041821 | 1.5489e-05 | 0
2013-02-05 09:15 | DRN11 | URBAN |  | 4 | 360 | 1440 | 0.0050162 | 1.3934e-05 | 0
2013-02-08 09:00 | OFR23 | LONG RURAL |  | 39 | 140 | 5460 | 0.021143 | 0.00015102 | 0
2013-02-06 09:55 | ELM12 | SHORT RURAL |  | 1 | 120 | 120 | 0.0010442 | 8.702e-06 | 0
2013-02-06 08:30 | OFR22 | SHORT RURAL |  | 96 | 214 | 20544 | 0.17877 | 0.00083539 | 0
2013-02-09 08:50 | BN1 | LONG RURAL |  | 122 | 224 | 27328 | 0.10582 | 0.00047242 | 0
2013-02-07 09:35 | OFR23 | LONG RURAL |  | 6 | 40 | 240 | 0.00092936 | 2.3234e-05 | 0
2013-02-07 08:00 | FGY12 | URBAN |  | 303 | 180.1452 | 54584 | 0.19014 | 0.0010555 | 0
2013-02-07 09:42 | BGE22 | SHORT RURAL |  | 45 | 316 | 14220 | 0.12374 | 0.00039159 | 0
2013-02-07 11:00 | OFR23 | LONG RURAL |  | 2 | 60 | 120 | 0.00046468 | 7.7446e-06 | 0
2013-02-07 09:17 | RWN31 | SHORT RURAL |  | 65 | 197 | 12805 | 0.11143 | 0.00056563 | 0
2013-02-07 09:30 | BGE24 | SHORT RURAL |  | 31 | 185 | 5735 | 0.049906 | 0.00026976 | 0
2013-02-10 10:55 | BN1 | LONG RURAL |  | 15 | 90 | 1350 | 0.0052276 | 5.8085e-05 | 0
2013-02-08 10:14 | LLG14 | SHORT RURAL |  | 2 | 95 | 190 | 0.0016534 | 1.7404e-05 | 0
2013-02-08 08:30 | SFS1 | SHORT RURAL |  | 227 | 448 | 101696 | 0.88496 | 0.0019753 | 0
2013-02-08 10:05 | FGY12 | URBAN |  | 90 | 165 | 14850 | 0.05173 | 0.00031351 | 0
2013-02-08 09:17 | WGL12 | LONG RURAL |  | 176 | 259 | 45584 | 0.17652 | 0.00068153 | 0
2013-02-11 09:00 | WGL13 | SHORT RURAL |  | 4 | 30 | 120 | 0.0010442 | 3.4808e-05 | 0
2013-02-11 09:00 | WGL13 | SHORT RURAL |  | 3 | 40 | 120 | 0.0010442 | 2.6106e-05 | 0
2013-02-11 10:20 | WGL13 | SHORT RURAL |  | 1 | 35 | 35 | 0.00030457 | 8.702e-06 | 0
2013-02-11 10:10 | WGL13 | SHORT RURAL |  | 1 | 35 | 35 | 0.00030457 | 8.702e-06 | 0
2013-02-11 09:05 | WGL13 | SHORT RURAL |  | 2 | 210 | 420 | 0.0036548 | 1.7404e-05 | 0
2013-02-10 13:42 | WN6 | LONG RURAL |  | 2 | 108 | 216 | 0.00083642 | 7.7446e-06 | 0
2013-02-11 09:50 | WYK11 | SHORT RURAL |  | 1 | 35 | 35 | 0.00030457 | 8.702e-06 | 0
2013-02-11 09:03 | LGA12 | SHORT RURAL |  | 21 | 207 | 4347 | 0.037827 | 0.00018274 | 0
2013-02-11 09:05 | LGA22 | SHORT RURAL |  | 32 | 157 | 5024 | 0.043719 | 0.00027846 | 0
2013-02-11 09:15 | BN1 | LONG RURAL |  | 1 | 190 | 190 | 0.00073574 | 3.8723e-06 | 0
2013-02-11 09:00 | LGA14 | LONG RURAL |  | 3 | 280 | 840 | 0.0032527 | 1.1617e-05 | 0
2013-02-11 12:10 | SMR5 | LONG RURAL |  | 2 | 10 | 20 | 7.7446e-05 | 7.7446e-06 | 0
2013-02-11 09:25 | BRT21 | SHORT RURAL |  | 12 | 95 | 1140 | 0.0099202 | 0.00010442 | 0
2013-02-05 13:13 | BWN14 | SHORT RURAL |  | 39 | 21.0256 | 820 | 0.0071356 | 0.00033938 | 0
2013-02-02 08:40 | RWT25 | URBAN |  | 1 | 170 | 170 | 0.00059219 | 3.4835e-06 | 0
2013-02-08 09:40 | OFR23 | LONG RURAL |  | 3 | 87 | 261 | 0.0010107 | 1.1617e-05 | 0
2013-02-08 12:00 | OFR23 | LONG RURAL |  | 9 | 90 | 810 | 0.0031366 | 3.4851e-05 | 0
2013-02-06 08:50 | TGN31 | LONG RURAL |  | 1 | 175 | 175 | 0.00067766 | 3.8723e-06 | 0
2013-02-11 09:00 | WN3 | LONG RURAL |  | 150 | 378 | 56700 | 0.21956 | 0.00058085 | 0
2013-02-08 09:02 | RWN24 | SHORT RURAL |  | 448 | 268 | 120064 | 1.0448 | 0.0038985 | 0
2013-02-11 11:15 | WGL13 | SHORT RURAL |  | 1 | 45 | 45 | 0.00039159 | 8.702e-06 | 0
2013-02-11 11:00 | WGL13 | SHORT RURAL |  | 2 | 33 | 66 | 0.00057433 | 1.7404e-05 | 0
2013-02-11 13:45 | WGL13 | SHORT RURAL |  | 2 | 40 | 80 | 0.00069616 | 1.7404e-05 | 0
2013-02-12 09:33 | WGL21 | LONG RURAL |  | 33 | 298 | 9834 | 0.03808 | 0.00012779 | 0
2013-02-13 08:55 | TGN23 | SHORT RURAL |  | 19 | 330 | 6270 | 0.054561 | 0.00016534 | 0
2013-02-13 09:55 | WGL21 | LONG RURAL |  | 4 | 303 | 1212 | 0.0046932 | 1.5489e-05 | 0
2013-02-12 09:30 | WGL13 | SHORT RURAL |  | 1 | 210 | 210 | 0.0018274 | 8.702e-06 | 0
2013-02-12 11:00 | WGL13 | SHORT RURAL |  | 5 | 265 | 1325 | 0.01153 | 4.351e-05 | 0
2013-02-13 08:35 | PHM31 | SHORT RURAL |  | 6 | 525 | 3150 | 0.027411 | 5.2212e-05 | 0
2013-02-13 09:15 | PHM31 | SHORT RURAL |  | 2 | 265 | 530 | 0.004612 | 1.7404e-05 | 0
2013-02-12 11:55 | WGL13 | SHORT RURAL |  | 1 | 50 | 50 | 0.0004351 | 8.702e-06 | 0
2013-02-13 09:19 | TGN23 | SHORT RURAL |  | 350 | 186 | 65100 | 0.5665 | 0.0030457 | 0
2013-02-13 09:48 | WGL21 | LONG RURAL |  | 345 | 214 | 73830 | 0.28589 | 0.0013359 | 0
2013-02-13 09:10 | MOE31 | LONG RURAL |  | 8 | 340 | 2720 | 0.010533 | 3.0979e-05 | 0
2013-02-13 12:20 | WGL12 | LONG RURAL |  | 1 | 40 | 40 | 0.00015489 | 3.8723e-06 | 0
2013-02-13 13:50 | WGL21 | LONG RURAL |  | 13 | 70 | 910 | 0.0035238 | 5.034e-05 | 0
2013-02-14 09:15 | WGL13 | SHORT RURAL |  | 137 | 342 | 46854 | 0.40772 | 0.0011922 | 0
2013-02-13 09:00 | MOE22 | LONG RURAL |  | 3 | 380 | 1140 | 0.0044144 | 1.1617e-05 | 0
2013-02-12 09:39 | MOE14 | SHORT RURAL |  | 2 | 31 | 62 | 0.00053952 | 1.7404e-05 | 0
2013-02-12 09:14 | MWTS32 | SHORT RURAL |  | 4 | 136 | 544 | 0.0047339 | 3.4808e-05 | 0
2013-02-12 10:58 | MOE14 | SHORT RURAL |  | 7 | 48 | 336 | 0.0029239 | 6.0914e-05 | 0
2013-02-12 09:00 | WGL12 | LONG RURAL |  | 24 | 260 | 6240 | 0.024163 | 9.2936e-05 | 0
2013-02-12 13:20 | MOE14 | SHORT RURAL |  | 2 | 30 | 60 | 0.00052212 | 1.7404e-05 | 0
2013-02-14 09:30 | WGL21 | LONG RURAL |  | 1 | 31 | 31 | 0.00012004 | 3.8723e-06 | 0
2013-02-14 09:05 | MOE31 | LONG RURAL |  | 29 | 190 | 5510 | 0.021336 | 0.0001123 | 0
2013-02-14 09:34 | MOE14 | SHORT RURAL |  | 42 | 228 | 9576 | 0.08333 | 0.00036548 | 0
2013-02-12 09:25 | LGA23 | LONG RURAL |  | 70 | 615 | 43050 | 0.1667 | 0.00027106 | 0
2013-02-12 09:11 | WN5 | LONG RURAL |  | 2 | 159 | 318 | 0.0012314 | 7.7446e-06 | 0
2013-02-12 08:00 | SLE32 | SHORT RURAL |  | 1 | 220 | 220 | 0.0019144 | 8.702e-06 | 0
2013-02-13 08:45 | WN5 | LONG RURAL |  | 1 | 340 | 340 | 0.0013166 | 3.8723e-06 | 0
2013-02-12 10:25 | FTR12 | LONG RURAL |  | 1 | 245 | 245 | 0.00094872 | 3.8723e-06 | 0
2013-02-12 12:25 | FTR21 | LONG RURAL |  | 1 | 45 | 45 | 0.00017425 | 3.8723e-06 | 0
2013-02-12 11:54 | WN6 | LONG RURAL |  | 2 | 171 | 342 | 0.0013243 | 7.7446e-06 | 0
2013-02-12 11:30 | FTR21 | LONG RURAL |  | 1 | 40 | 40 | 0.00015489 | 3.8723e-06 | 0
2013-02-12 09:55 | FTR21 | LONG RURAL |  | 15 | 35 | 525 | 0.002033 | 5.8085e-05 | 0
2013-02-11 12:50 | LGA22 | SHORT RURAL |  | 18 | 110 | 1980 | 0.01723 | 0.00015664 | 0
2013-02-13 09:00 | LGA13 | LONG RURAL |  | 16 | 230 | 3680 | 0.01425 | 6.1957e-05 | 0
2013-02-13 11:10 | LGA23 | LONG RURAL |  | 59 | 250 | 14750 | 0.057117 | 0.00022847 | 0
2013-02-13 09:20 | FTR12 | LONG RURAL |  | 28 | 460 | 12880 | 0.049875 | 0.00010842 | 0
2013-02-13 10:28 | FTR21 | LONG RURAL |  | 48 | 7 | 336 | 0.0013011 | 0.00018587 | 0
2013-02-13 10:30 | FTR23 | LONG RURAL |  | 5 | 250 | 1250 | 0.0048404 | 1.9362e-05 | 0
2013-02-12 10:00 | BN6 | LONG RURAL |  | 5 | 280 | 1400 | 0.0054212 | 1.9362e-05 | 0
2013-02-13 08:37 | WN6 | LONG RURAL |  | 2 | 213 | 426 | 0.0016496 | 7.7446e-06 | 0
2013-02-14 08:30 | WN6 | LONG RURAL |  | 1 | 600 | 600 | 0.0023234 | 3.8723e-06 | 0
2013-02-13 08:45 | LDL23 | LONG RURAL |  | 43 | 441 | 18963 | 0.073431 | 0.00016651 | 0
2013-02-12 10:50 | WYK11 | SHORT RURAL |  | 2 | 115 | 230 | 0.0020015 | 1.7404e-05 | 0
2013-02-12 08:45 | WYK11 | SHORT RURAL |  | 3 | 125 | 375 | 0.0032632 | 2.6106e-05 | 0
2013-02-12 09:18 | WYK11 | SHORT RURAL |  | 2 | 62 | 124 | 0.001079 | 1.7404e-05 | 0
2013-02-13 06:52 | WYK23 | SHORT RURAL |  | 503 | 499 | 250997 | 2.1842 | 0.0043771 | 0
2013-02-12 11:45 | WYK12 | SHORT RURAL |  | 46 | 195 | 8970 | 0.078057 | 0.00040029 | 0
2013-02-12 09:11 | FTR21 | LONG RURAL |  | 16 | 194 | 3104 | 0.01202 | 6.1957e-05 | 0
2013-02-12 09:40 | LDL11 | URBAN |  | 108 | 275 | 29700 | 0.10346 | 0.00037622 | 0
2013-02-14 09:20 | WGL11 | SHORT RURAL |  | 254 | 326 | 82804 | 0.72056 | 0.0022103 | 0
2013-02-12 09:00 | FTR23 | LONG RURAL |  | 157 | 408 | 64056 | 0.24804 | 0.00060795 | 0
2013-02-13 09:15 | LGA11 | LONG RURAL |  | 2 | 450 | 900 | 0.0034851 | 7.7446e-06 | 0
2013-02-14 09:00 | LGA23 | LONG RURAL |  | 81 | 280 | 22680 | 0.087824 | 0.00031366 | 0
2013-02-13 09:20 | FTR21 | LONG RURAL |  | 3 | 92 | 276 | 0.0010688 | 1.1617e-05 | 0
2013-02-11 13:30 | ALA01 | LONG RURAL |  | 19 | 25 | 475 | 0.0018393 | 7.3574e-05 | 0
2013-02-13 12:31 | FTR21 | LONG RURAL |  | 2 | 44 | 88 | 0.00034076 | 7.7446e-06 | 0
2013-02-11 14:15 | ALA01 | LONG RURAL |  | 10 | 15 | 150 | 0.00058085 | 3.8723e-05 | 0
2013-02-14 10:00 | LGA12 | SHORT RURAL |  | 7 | 340 | 2380 | 0.020711 | 6.0914e-05 | 0
2013-02-12 09:30 | SMR8 | LONG RURAL |  | 3 | 60 | 180 | 0.00069702 | 1.1617e-05 | 0
2013-02-12 11:50 | SMR8 | LONG RURAL |  | 1 | 50 | 50 | 0.00019362 | 3.8723e-06 | 0
2013-02-14 09:50 | FTR12 | LONG RURAL |  | 47 | 95 | 4465 | 0.01729 | 0.000182 | 0
2013-02-14 09:00 | LGA11 | LONG RURAL |  | 40 | 252 | 10080 | 0.039033 | 0.00015489 | 0
2013-02-14 08:25 | LDL22 | SHORT RURAL |  | 181 | 280 | 50680 | 0.44102 | 0.0015751 | 0
2013-02-14 09:21 | LDL22 | SHORT RURAL |  | 9 | 44 | 396 | 0.003446 | 7.8318e-05 | 0
2013-02-14 11:00 | WYK12 | SHORT RURAL |  | 2 | 75 | 150 | 0.0013053 | 1.7404e-05 | 0
2013-02-12 09:00 | SMR5 | LONG RURAL |  | 261 | 404 | 105444 | 0.40831 | 0.0010107 | 0
2013-02-12 09:38 | SMR3 | LONG RURAL |  | 33 | 317 | 10461 | 0.040508 | 0.00012779 | 0
2013-02-11 14:00 | WGL13 | SHORT RURAL |  | 5 | 30 | 150 | 0.0013053 | 4.351e-05 | 0
2013-02-11 12:20 | MOE22 | LONG RURAL |  | 2 | 45 | 90 | 0.00034851 | 7.7446e-06 | 0
2013-02-14 09:30 | PHI12 | SHORT RURAL |  | 128 | 120 | 15360 | 0.13366 | 0.0011139 | 0
2013-02-12 09:03 | LLG12 | SHORT RURAL |  | 1 | 147 | 147 | 0.0012792 | 8.702e-06 | 0
2013-02-12 10:35 | WO31 | URBAN |  | 4 | 75 | 300 | 0.001045 | 1.3934e-05 | 0
2013-02-12 10:45 | BRT21 | SHORT RURAL |  | 3 | 45 | 135 | 0.0011748 | 2.6106e-05 | 0
2013-02-12 10:35 | TRC01 | SHORT RURAL |  | 6 | 105 | 630 | 0.0054822 | 5.2212e-05 | 0
2013-02-14 12:18 | WGL21 | LONG RURAL |  | 1 | 38 | 38 | 0.00014715 | 3.8723e-06 | 0
2013-02-15 09:00 | LGA13 | LONG RURAL |  | 35 | 300 | 10500 | 0.040659 | 0.00013553 | 0
2013-02-15 09:17 | WGL21 | LONG RURAL |  | 8 | 147 | 1176 | 0.0045538 | 3.0979e-05 | 0
2013-02-14 13:20 | WN5 | LONG RURAL |  | 2 | 75 | 150 | 0.00058085 | 7.7446e-06 | 0
2013-02-15 09:25 | WGL12 | LONG RURAL |  | 1 | 200 | 200 | 0.00077446 | 3.8723e-06 | 0
2013-02-15 10:25 | MOE31 | LONG RURAL |  | 3 | 105 | 315 | 0.0012198 | 1.1617e-05 | 0
2013-02-15 09:14 | WN5 | LONG RURAL |  | 6 | 158 | 948 | 0.003671 | 2.3234e-05 | 0
2013-02-15 08:30 | WN3 | LONG RURAL |  | 2 | 132 | 264 | 0.0010223 | 7.7446e-06 | 0
2013-02-15 09:40 | BN6 | LONG RURAL |  | 1 | 135 | 135 | 0.00052276 | 3.8723e-06 | 0
2013-02-15 09:20 | FTR12 | LONG RURAL |  | 44 | 327 | 14388 | 0.055715 | 0.00017038 | 0
2013-02-15 09:20 | FTR21 | LONG RURAL |  | 42 | 80 | 3360 | 0.013011 | 0.00016264 | 0
2013-02-15 09:10 | WYK23 | SHORT RURAL |  | 42 | 280 | 11760 | 0.10234 | 0.00036548 | 0
2013-02-15 09:20 | MOE22 | LONG RURAL |  | 78 | 50 | 3900 | 0.015102 | 0.00030204 | 0
2013-02-14 12:30 | PHI12 | SHORT RURAL |  | 18 | 80 | 1440 | 0.012531 | 0.00015664 | 0
2013-02-14 12:44 | WYK12 | SHORT RURAL |  | 2 | 86 | 172 | 0.0014967 | 1.7404e-05 | 0
2013-02-11 10:10 | WGL21 | LONG RURAL |  | 2 | 108 | 216 | 0.00083642 | 7.7446e-06 | 0
2013-02-11 09:25 | MOE22 | LONG RURAL |  | 4 | 110 | 440 | 0.0017038 | 1.5489e-05 | 0
2013-02-11 11:35 | MOE22 | LONG RURAL |  | 1 | 30 | 30 | 0.00011617 | 3.8723e-06 | 0
2013-02-11 12:20 | WGL21 | LONG RURAL |  | 2 | 97 | 194 | 0.00075123 | 7.7446e-06 | 0
2013-02-13 10:00 | SMR8 | LONG RURAL |  | 3 | 295 | 885 | 0.003427 | 1.1617e-05 | 0
2013-02-10 08:50 | SLE31 | LONG RURAL |  | 941 | 577 | 542957 | 2.1025 | 0.0036438 | 0
2013-02-12 10:39 | WGL21 | LONG RURAL |  | 2 | 30 | 60 | 0.00023234 | 7.7446e-06 | 0
2013-02-08 11:41 | BWR33 | URBAN |  | 93 | 94 | 8742 | 0.030453 | 0.00032396 | 0
2013-02-12 11:55 | WGL21 | LONG RURAL |  | 1 | 106 | 106 | 0.00041047 | 3.8723e-06 | 0
2013-02-13 09:50 | WGL21 | LONG RURAL |  | 2 | 77 | 154 | 0.00059634 | 7.7446e-06 | 0
2013-02-12 14:33 | WGL21 | LONG RURAL |  | 4 | 119 | 476 | 0.0018432 | 1.5489e-05 | 0
2013-02-13 11:25 | WGL21 | LONG RURAL |  | 2 | 127 | 254 | 0.00098357 | 7.7446e-06 | 0
2013-02-13 14:00 | WGL21 | LONG RURAL |  | 7 | 50 | 350 | 0.0013553 | 2.7106e-05 | 0
2013-02-13 09:30 | BRT22 | SHORT RURAL |  | 1 | 55 | 55 | 0.00047861 | 8.702e-06 | 0
2013-02-13 09:37 | ALA01 | LONG RURAL |  | 23 | 188 | 4324 | 0.016744 | 8.9063e-05 | 0
2013-02-10 08:30 | MFA22 | LONG RURAL |  | 464 | 347 | 161008 | 0.62347 | 0.0017968 | 0
2013-02-13 09:30 | SMR3 | LONG RURAL |  | 2 | 390 | 780 | 0.0030204 | 7.7446e-06 | 0
2013-02-13 09:20 | KMS1 | SHORT RURAL |  | 41 | 172 | 7052 | 0.061366 | 0.00035678 | 0
2013-02-14 08:30 | MFA21 | LONG RURAL |  | 323 | 412 | 133076 | 0.51531 | 0.0012508 | 0
2013-02-13 08:35 | SLE31 | LONG RURAL |  | 9 | 180 | 1620 | 0.0062731 | 3.4851e-05 | 0
2013-02-12 09:59 | NLA31 | LONG RURAL |  | 207 | 329 | 68103 | 0.26372 | 0.00080157 | 0
2013-02-14 09:08 | WOTS13 | LONG RURAL |  | 336 | 106 | 35616 | 0.13792 | 0.0013011 | 0
2013-02-12 10:30 | BDL1 | LONG RURAL |  | 114 | 117 | 13338 | 0.051649 | 0.00044144 | 0
2013-02-13 09:20 | SLE31 | LONG RURAL |  | 2 | 135 | 270 | 0.0010455 | 7.7446e-06 | 0
2013-02-13 09:00 | MFA23 | SHORT RURAL |  | 174 | 430 | 74820 | 0.65108 | 0.0015141 | 0
2013-02-11 09:05 | PHM14 | LONG RURAL |  | 1 | 140 | 140 | 0.00054212 | 3.8723e-06 | 0
2013-02-15 11:00 | MOE22 | LONG RURAL |  | 19 | 86 | 1634 | 0.0063274 | 7.3574e-05 | 0
2013-02-16 09:39 | FTR12 | LONG RURAL |  | 20 | 349 | 6980 | 0.027029 | 7.7446e-05 | 0
2013-02-14 09:03 | SMR8 | LONG RURAL |  | 83 | 189 | 15687 | 0.060745 | 0.0003214 | 0
2013-02-15 09:12 | LGA14 | LONG RURAL |  | 1 | 78 | 78 | 0.00030204 | 3.8723e-06 | 0
2013-02-14 09:10 | MVE01 | SHORT RURAL |  | 5 | 455 | 2275 | 0.019797 | 4.351e-05 | 0
2013-02-14 10:30 | SMR8 | LONG RURAL |  | 1 | 65 | 65 | 0.0002517 | 3.8723e-06 | 0
2013-02-13 09:55 | MYT8 | SHORT RURAL |  | 7 | 60 | 420 | 0.0036548 | 6.0914e-05 | 0
2013-02-13 11:50 | MYT8 | SHORT RURAL |  | 2 | 55 | 110 | 0.00095722 | 1.7404e-05 | 0
2013-02-13 13:50 | MYT8 | SHORT RURAL |  | 5 | 50 | 250 | 0.0021755 | 4.351e-05 | 0
2013-02-13 08:35 | SLE32 | SHORT RURAL |  | 8 | 165 | 1320 | 0.011487 | 6.9616e-05 | 0
2013-02-12 13:20 | WYK11 | SHORT RURAL |  | 2 | 95 | 190 | 0.0016534 | 1.7404e-05 | 0
2013-02-13 13:00 | BRT22 | SHORT RURAL |  | 3 | 45 | 135 | 0.0011748 | 2.6106e-05 | 0
2013-02-12 16:10 | WYK11 | SHORT RURAL |  | 1 | 50 | 50 | 0.0004351 | 8.702e-06 | 0
2013-02-14 11:45 | WGL21 | LONG RURAL |  | 2 | 74 | 148 | 0.0005731 | 7.7446e-06 | 0
2013-02-14 11:58 | WGL21 | LONG RURAL |  | 1 | 26 | 26 | 0.00010068 | 3.8723e-06 | 0
2013-02-14 11:48 | WGL21 | LONG RURAL |  | 1 | 28 | 28 | 0.00010842 | 3.8723e-06 | 0
2013-02-15 08:30 | WOTS11 | LONG RURAL |  | 1 | 236 | 236 | 0.00091387 | 3.8723e-06 | 0
2013-02-12 09:36 | WN5 | LONG RURAL |  | 1 | 314 | 314 | 0.0012159 | 3.8723e-06 | 0
2013-02-07 09:00 | KLO14 | LONG RURAL |  | 62 | 299.8548 | 18591 | 0.07199 | 0.00024008 | 0
2013-02-15 10:07 | FTR12 | LONG RURAL |  | 119 | 356 | 42364 | 0.16405 | 0.00046081 | 0
2013-02-09 08:50 | BWR12 | URBAN |  | 1 | 1915 | 1915 | 0.0066709 | 3.4835e-06 | 0
2013-02-09 08:37 | BWR32 | URBAN |  | 480 | 458 | 219840 | 0.76581 | 0.0016721 | 0
2013-02-09 08:56 | BWR34 | URBAN |  | 131 | 449 | 58819 | 0.20489 | 0.00045634 | 0
2013-02-02 10:15 | MOE24 | SHORT RURAL |  | 15 | 865 | 12975 | 0.11291 | 0.00013053 | 0
2013-02-11 09:45 | RWN24 | SHORT RURAL |  | 20 | 234 | 4680 | 0.040725 | 0.00017404 | 0
2013-02-11 09:05 | RWN24 | SHORT RURAL |  | 240 | 368.7625 | 88503 | 0.77015 | 0.0020885 | 0
2013-02-12 09:10 | RWN24 | SHORT RURAL |  | 24 | 235 | 5640 | 0.049079 | 0.00020885 | 0
2013-02-09 07:33 | CYN14 | URBAN |  | 1158 | 457 | 529206 | 1.8435 | 0.0040339 | 0
2013-02-14 12:00 | SMR8 | LONG RURAL |  | 1 | 30 | 30 | 0.00011617 | 3.8723e-06 | 0
2013-02-17 09:00 | MOE31 | LONG RURAL |  | 37 | 181 | 6697 | 0.025933 | 0.00014328 | 0
2013-02-17 09:03 | LDL23 | LONG RURAL |  | 1388 | 246 | 341448 | 1.3222 | 0.0053748 | 0
2013-02-17 08:04 | WGL13 | SHORT RURAL |  | 69 | 254 | 17526 | 0.15251 | 0.00060044 | 0
2013-02-08 09:00 | BRA11 | URBAN |  | 46 | 350 | 16100 | 0.056084 | 0.00016024 | 0
2013-02-15 09:10 | KMS1 | SHORT RURAL |  | 12 | 140 | 1680 | 0.014619 | 0.00010442 | 0
2013-02-15 09:16 | SMR2 | SHORT RURAL |  | 282 | 356 | 100392 | 0.87361 | 0.002454 | 0
2013-02-13 11:18 | WOTS13 | LONG RURAL |  | 49 | 22 | 1078 | 0.0041744 | 0.00018974 | 0
2013-02-13 13:50 | SLE24 | URBAN |  | 100 | 110 | 11000 | 0.038318 | 0.00034835 | 0
2013-02-14 09:35 | BRT22 | SHORT RURAL |  | 35 | 355 | 12425 | 0.10812 | 0.00030457 | 0
2013-02-14 10:05 | BWA22 | LONG RURAL |  | 1 | 36 | 36 | 0.0001394 | 3.8723e-06 | 0
2013-02-12 10:00 | BDL6 | SHORT RURAL |  | 8 | 220 | 1760 | 0.015315 | 6.9616e-05 | 0
2013-02-14 11:00 | BWA22 | LONG RURAL |  | 2 | 38 | 76 | 0.0002943 | 7.7446e-06 | 0
2013-02-12 09:10 | WYK12 | SHORT RURAL |  | 6 | 140 | 840 | 0.0073097 | 5.2212e-05 | 0
2013-02-17 09:20 | FTR22 | SHORT RURAL |  | 31 | 100 | 3100 | 0.026976 | 0.00026976 | 0
2013-02-11 09:10 | RWN26 | SHORT RURAL |  | 4 | 130 | 520 | 0.004525 | 3.4808e-05 | 0
2013-02-08 10:45 | TT5 | URBAN |  | 134 | 208.4179 | 27928 | 0.097287 | 0.00046679 | 0
2013-02-11 09:25 | ELM33 | SHORT RURAL |  | 42 | 265 | 11130 | 0.096853 | 0.00036548 | 0
2013-02-12 08:30 | OFR23 | LONG RURAL |  | 51 | 240 | 12240 | 0.047397 | 0.00019749 | 0
2013-02-12 08:31 | BGE22 | SHORT RURAL |  | 88 | 401 | 35288 | 0.30708 | 0.00076577 | 0
2013-02-13 08:32 | SFS1 | SHORT RURAL |  | 283 | 484 | 136972 | 1.1919 | 0.0024627 | 0
2013-02-14 08:45 | BGE22 | SHORT RURAL |  | 70 | 60 | 4200 | 0.036548 | 0.00060914 | 0
2013-02-14 08:45 | BGE12 | SHORT RURAL |  | 48 | 275 | 13200 | 0.11487 | 0.00041769 | 0
2013-02-14 08:42 | LLG11 | SHORT RURAL |  | 2 | 73 | 146 | 0.0012705 | 1.7404e-05 | 0
2013-02-14 12:15 | OFR23 | LONG RURAL |  | 1 | 50 | 50 | 0.00019362 | 3.8723e-06 | 0
2013-02-03 02:20 | LDL11 | URBAN |  | 1 | 144 | 144 | 0.00050162 | 3.4835e-06 | 0
2013-02-05 10:05 | MWE1 | URBAN |  | 1 | 139 | 139 | 0.0004842 | 3.4835e-06 | 0
2013-02-18 08:42 | WN5 | LONG RURAL |  | 3 | 163 | 489 | 0.0018936 | 1.1617e-05 | 0
2013-02-18 09:48 | WGL21 | LONG RURAL |  | 41 | 310 | 12710 | 0.049217 | 0.00015876 | 0
2013-02-18 09:25 | TGN31 | LONG RURAL |  | 28 | 290 | 8120 | 0.031443 | 0.00010842 | 0
2013-02-18 09:35 | WYK11 | SHORT RURAL |  | 55 | 215 | 11825 | 0.1029 | 0.00047861 | 0
2013-02-18 09:05 | WYK11 | SHORT RURAL |  | 13 | 275 | 3575 | 0.03111 | 0.00011313 | 0
2013-02-18 10:35 | ALA01 | LONG RURAL |  | 3 | 150 | 450 | 0.0017425 | 1.1617e-05 | 0
2013-02-18 10:00 | ALA01 | LONG RURAL |  | 2 | 85 | 170 | 0.00065829 | 7.7446e-06 | 0
2013-02-18 09:20 | KMS1 | SHORT RURAL |  | 22 | 122 | 2684 | 0.023356 | 0.00019144 | 0
2013-02-08 12:00 | MDI1 | SHORT RURAL |  | 1 | 60 | 60 | 0.00052212 | 8.702e-06 | 0
2013-02-18 10:30 | KMS21 | SHORT RURAL |  | 1 | 95 | 95 | 0.00082669 | 8.702e-06 | 0
2013-02-14 13:20 | BWA22 | LONG RURAL |  | 2 | 85 | 170 | 0.00065829 | 7.7446e-06 | 0
2013-02-14 10:10 | BWA22 | LONG RURAL |  | 2 | 135 | 270 | 0.0010455 | 7.7446e-06 | 0
2013-02-15 09:00 | BRT22 | SHORT RURAL |  | 10 | 290 | 2900 | 0.025236 | 8.702e-05 | 0
2013-02-14 08:35 | BDL5 | LONG RURAL |  | 79 | 279.9367 | 22115 | 0.085636 | 0.00030591 | 0
2013-02-18 09:50 | BWA22 | LONG RURAL |  | 1 | 110 | 110 | 0.00042595 | 3.8723e-06 | 0
2013-02-14 12:00 | MYT7 | LONG RURAL |  | 19 | 100 | 1900 | 0.0073574 | 7.3574e-05 | 0
2013-02-10 08:56 | WT13 | URBAN |  | 1 | 179 | 179 | 0.00062354 | 3.4835e-06 | 0
2013-02-13 09:19 | TGN23 | SHORT RURAL |  | 16 | 361 | 5776 | 0.050263 | 0.00013923 | 0
2013-02-17 08:59 | MSD4 | LONG RURAL |  | 34 | 376 | 12784 | 0.049504 | 0.00013166 | 0
2013-02-11 09:35 | TT6 | URBAN |  | 653 | 287 | 187411 | 0.65284 | 0.0022747 | 0
2013-02-18 11:35 | BN6 | LONG RURAL |  | 1 | 60 | 60 | 0.00023234 | 3.8723e-06 | 0
2013-02-11 09:50 | ELM13 | URBAN |  | 95 | 355 | 33725 | 0.11748 | 0.00033093 | 0
2013-02-11 09:40 | KLO14 | LONG RURAL |  | 2 | 200 | 400 | 0.0015489 | 7.7446e-06 | 0
2013-02-19 10:10 | WGL21 | LONG RURAL |  | 3 | 185 | 555 | 0.0021491 | 1.1617e-05 | 0
2013-02-18 14:40 | WYK11 | SHORT RURAL |  | 29 | 45 | 1305 | 0.011356 | 0.00025236 | 0
2013-02-19 09:00 | TGN14 | LONG RURAL |  | 307 | 439 | 134773 | 0.52188 | 0.0011888 | 0
2013-02-21 08:59 | MFA34 | SHORT RURAL |  | 1 | 520 | 520 | 0.004525 | 8.702e-06 | 0
2013-02-21 10:48 | TGN31 | LONG RURAL |  | 751 | 387 | 290637 | 1.1254 | 0.0029081 | 0
2013-02-19 11:20 | FTR21 | LONG RURAL |  | 1 | 40 | 40 | 0.00015489 | 3.8723e-06 | 0
2013-02-19 09:45 | MWTS24 | SHORT RURAL |  | 64 | 360 | 23040 | 0.20049 | 0.00055693 | 0
2013-02-19 09:17 | WGL21 | LONG RURAL |  | 8 | 338 | 2704 | 0.010471 | 3.0979e-05 | 0
2013-02-20 08:30 | MWTS14 | SHORT RURAL |  | 125 | 515 | 64375 | 0.56019 | 0.0010877 | 0
2013-02-20 09:36 | MWTS24 | SHORT RURAL |  | 4 | 282 | 1128 | 0.0098158 | 3.4808e-05 | 0
2013-02-20 09:35 | WGL21 | LONG RURAL |  | 1 | 115 | 115 | 0.00044532 | 3.8723e-06 | 0
2013-02-20 09:30 | WGL13 | SHORT RURAL |  | 2 | 15 | 30 | 0.00026106 | 1.7404e-05 | 0
2013-02-19 08:05 | WYK11 | SHORT RURAL |  | 119 | 285 | 33915 | 0.29513 | 0.0010355 | 0
2013-02-19 09:30 | LDL24 | URBAN |  | 44 | 267 | 11748 | 0.040924 | 0.00015327 | 0
2013-02-19 14:05 | WYK11 | SHORT RURAL |  | 8 | 42 | 336 | 0.0029239 | 6.9616e-05 | 0
2013-02-20 11:40 | WGL13 | SHORT RURAL |  | 1 | 95 | 95 | 0.00082669 | 8.702e-06 | 0
2013-02-21 09:05 | WGL24 | LONG RURAL |  | 4 | 25 | 100 | 0.00038723 | 1.5489e-05 | 0
2013-02-21 09:25 | WGL13 | SHORT RURAL |  | 2 | 75 | 150 | 0.0013053 | 1.7404e-05 | 0
2013-02-21 09:18 | WGL21 | LONG RURAL |  | 10 | 117 | 1170 | 0.0045306 | 3.8723e-05 | 0
2013-02-21 10:40 | WGL24 | LONG RURAL |  | 5 | 60 | 300 | 0.0011617 | 1.9362e-05 | 0
2013-02-19 09:15 | WGL15 | SHORT RURAL |  | 3 | 55 | 165 | 0.0014358 | 2.6106e-05 | 0
2013-02-20 09:05 | MOE22 | LONG RURAL |  | 8 | 85 | 680 | 0.0026332 | 3.0979e-05 | 0
2013-02-20 10:02 | MDG1 | SHORT RURAL |  | 25 | 113 | 2825 | 0.024583 | 0.00021755 | 0
2013-02-20 12:20 | WYK11 | SHORT RURAL |  | 2 | 78 | 156 | 0.0013575 | 1.7404e-05 | 0
2013-02-20 08:30 | WYK23 | SHORT RURAL |  | 13 | 414 | 5382 | 0.046834 | 0.00011313 | 0
2013-02-20 09:50 | WYK23 | SHORT RURAL |  | 31 | 95 | 2945 | 0.025627 | 0.00026976 | 0
2013-02-19 09:15 | LGA13 | LONG RURAL |  | 3 | 195 | 585 | 0.0022653 | 1.1617e-05 | 0
2013-02-21 09:25 | TGN23 | SHORT RURAL |  | 3 | 105 | 315 | 0.0027411 | 2.6106e-05 | 0
2013-02-21 09:55 | WGL21 | LONG RURAL |  | 6 | 315 | 1890 | 0.0073187 | 2.3234e-05 | 0
2013-02-19 09:00 | LGA12 | SHORT RURAL |  | 242 | 354 | 85668 | 0.74548 | 0.0021059 | 0
2013-02-19 09:30 | FTR22 | SHORT RURAL |  | 29 | 120 | 3480 | 0.030283 | 0.00025236 | 0
2013-02-21 10:25 | FTR12 | LONG RURAL |  | 67 | 356 | 23852 | 0.092362 | 0.00025945 | 0
2013-02-19 09:31 | FTR12 | LONG RURAL |  | 117 | 338 | 39546 | 0.15313 | 0.00045306 | 0
2013-02-20 09:00 | PHI11 | SHORT RURAL |  | 546 | 402 | 219492 | 1.91 | 0.0047513 | 0
2013-02-21 09:11 | PHI12 | SHORT RURAL |  | 202 | 439 | 88678 | 0.77167 | 0.0017578 | 0
2013-02-21 08:10 | WYK11 | SHORT RURAL |  | 95 | 403 | 38285 | 0.33315 | 0.00082669 | 0
2013-02-21 09:48 | MDG1 | SHORT RURAL |  | 46 | 40 | 1840 | 0.016012 | 0.00040029 | 0
2013-02-20 09:05 | LGA23 | LONG RURAL |  | 70 | 367 | 25690 | 0.09948 | 0.00027106 | 0
2013-02-20 09:22 | FTR12 | LONG RURAL |  | 124 | 102.8629 | 12755 | 0.049391 | 0.00048017 | 0
2013-02-18 13:09 | ALA01 | LONG RURAL |  | 56 | 27 | 1512 | 0.0058549 | 0.00021685 | 0
2013-02-18 14:10 | ALA01 | LONG RURAL |  | 1 | 90 | 90 | 0.00034851 | 3.8723e-06 | 0
2013-02-21 09:50 | FTR21 | LONG RURAL |  | 141 | 366 | 51606 | 0.19983 | 0.000546 | 0
2013-02-21 09:00 | LGA24 | SHORT RURAL |  | 69 | 415 | 28635 | 0.24918 | 0.00060044 | 0
2013-02-18 13:55 | BWA22 | LONG RURAL |  | 1 | 35 | 35 | 0.00013553 | 3.8723e-06 | 0
2013-02-19 09:00 | BWA22 | LONG RURAL |  | 14 | 180 | 2520 | 0.0097582 | 5.4212e-05 | 0
2013-02-18 12:35 | BWA22 | LONG RURAL |  | 1 | 35 | 35 | 0.00013553 | 3.8723e-06 | 0
2013-02-20 09:50 | WGL23 | SHORT RURAL |  | 13 | 55 | 715 | 0.0062219 | 0.00011313 | 0
2013-02-21 12:15 | TGN14 | LONG RURAL |  | 7 | 145 | 1015 | 0.0039304 | 2.7106e-05 | 0
2013-02-20 09:00 | BRT22 | SHORT RURAL |  | 155 | 314.2839 | 48714 | 0.42391 | 0.0013488 | 0
2013-02-11 10:31 | KLO14 | LONG RURAL |  | 3 | 74 | 222 | 0.00085965 | 1.1617e-05 | 0
2013-02-11 11:55 | KLO14 | LONG RURAL |  | 2 | 47 | 94 | 0.000364 | 7.7446e-06 | 0
2013-02-12 08:30 | ELM33 | SHORT RURAL |  | 8 | 138 | 1104 | 0.009607 | 6.9616e-05 | 0
2013-02-12 12:43 | ELM33 | SHORT RURAL |  | 4 | 60 | 240 | 0.0020885 | 3.4808e-05 | 0
2013-02-12 09:15 | RWN31 | SHORT RURAL |  | 5 | 120 | 600 | 0.0052212 | 4.351e-05 | 0
2013-02-12 11:50 | RWN31 | SHORT RURAL |  | 3 | 85 | 255 | 0.002219 | 2.6106e-05 | 0
2013-02-12 14:20 | RWN31 | SHORT RURAL |  | 1 | 80 | 80 | 0.00069616 | 8.702e-06 | 0
2013-02-13 10:30 | BRA23 | URBAN |  | 56 | 285 | 15960 | 0.055596 | 0.00019508 | 0
2013-02-13 08:30 | RWN26 | SHORT RURAL |  | 317 | 521.7981 | 165410 | 1.4394 | 0.0027585 | 0
2013-02-14 10:25 | RWN31 | SHORT RURAL |  | 2 | 160 | 320 | 0.0027846 | 1.7404e-05 | 0
2013-02-14 13:30 | RWN24 | SHORT RURAL |  | 3 | 95 | 285 | 0.0024801 | 2.6106e-05 | 0
2013-02-15 09:30 | RWN26 | SHORT RURAL |  | 8 | 180 | 1440 | 0.012531 | 6.9616e-05 | 0
2013-02-15 11:40 | RWN26 | SHORT RURAL |  | 10 | 80 | 800 | 0.0069616 | 8.702e-05 | 0
2013-02-16 08:40 | BWR12 | URBAN |  | 19 | 165 | 3135 | 0.010921 | 6.6186e-05 | 0
2013-02-17 09:30 | RWT11 | URBAN |  | 51 | 317 | 16167 | 0.056317 | 0.00017766 | 0
2013-02-17 08:30 | RWT25 | URBAN |  | 85 | 377 | 32045 | 0.11163 | 0.0002961 | 0
2013-02-13 08:15 | ELM33 | SHORT RURAL |  | 7 | 155 | 1085 | 0.0094416 | 6.0914e-05 | 0
2013-02-13 08:30 | RWT14 | URBAN |  | 134 | 430 | 57620 | 0.20072 | 0.00046679 | 0
2013-02-20 08:32 | WO14 | URBAN |  | 93 | 7 | 651 | 0.0022677 | 0.00032396 | 0
2013-02-19 11:13 | WO31 | URBAN |  | 1 | 162 | 162 | 0.00056432 | 3.4835e-06 | 0
2013-02-20 08:10 | WO31 | URBAN |  | 2 | 145 | 290 | 0.0010102 | 6.967e-06 | 0
2013-02-21 09:08 | WOTS11 | LONG RURAL |  | 1 | 162 | 162 | 0.00062731 | 3.8723e-06 | 0
2013-02-15 08:40 | LLG14 | SHORT RURAL |  | 1 | 55 | 55 | 0.00047861 | 8.702e-06 | 0
2013-02-21 10:15 | WOTS11 | LONG RURAL |  | 1 | 130 | 130 | 0.0005034 | 3.8723e-06 | 0
2013-02-15 12:00 | OFR22 | SHORT RURAL |  | 7 | 160 | 1120 | 0.0097462 | 6.0914e-05 | 0
2013-02-13 10:05 | DRN12 | URBAN |  | 4 | 170 | 680 | 0.0023688 | 1.3934e-05 | 0
2013-02-19 08:55 | WOTS11 | LONG RURAL |  | 1 | 95 | 95 | 0.00036787 | 3.8723e-06 | 0
2013-02-15 09:52 | LYD11 | SHORT RURAL |  | 161 | 201 | 32361 | 0.2816 | 0.001401 | 0
2013-02-21 11:00 | BRT22 | SHORT RURAL |  | 6 | 100 | 600 | 0.0052212 | 5.2212e-05 | 0
2013-02-15 09:10 | PHM14 | LONG RURAL |  | 4 | 130 | 520 | 0.0020136 | 1.5489e-05 | 0
2013-02-14 08:06 | ELM12 | SHORT RURAL |  | 216 | 51 | 11016 | 0.095861 | 0.0018796 | 0
2013-02-15 08:55 | WT6 | URBAN |  | 89 | 145 | 12905 | 0.044954 | 0.00031003 | 0
2013-02-22 09:15 | BWN14 | SHORT RURAL |  | 1 | 185 | 185 | 0.0016099 | 8.702e-06 | 0
2013-02-21 11:10 | WGL13 | SHORT RURAL |  | 1 | 30 | 30 | 0.00026106 | 8.702e-06 | 0
2013-02-21 12:15 | WGL13 | SHORT RURAL |  | 2 | 40 | 80 | 0.00069616 | 1.7404e-05 | 0
2013-02-21 12:00 | WGL13 | SHORT RURAL |  | 2 | 40 | 80 | 0.00069616 | 1.7404e-05 | 0
2013-02-22 09:53 | WGL12 | LONG RURAL |  | 106 | 169 | 17914 | 0.069369 | 0.00041047 | 0
2013-02-22 09:15 | MWTS31 | SHORT RURAL |  | 11 | 325 | 3575 | 0.03111 | 9.5722e-05 | 0
2013-02-22 09:00 | WGL21 | LONG RURAL |  | 64 | 315 | 20160 | 0.078066 | 0.00024783 | 0
2013-02-22 12:10 | LDL21 | SHORT RURAL |  | 42 | 145 | 6090 | 0.052995 | 0.00036548 | 0
2013-02-22 09:10 | FTR12 | LONG RURAL |  | 28 | 440 | 12320 | 0.047707 | 0.00010842 | 0
2013-02-22 09:00 | LGA23 | LONG RURAL |  | 11 | 305 | 3355 | 0.012992 | 4.2595e-05 | 0
2013-02-21 12:15 | MWTS11 | SHORT RURAL |  | 65 | 205 | 13325 | 0.11595 | 0.00056563 | 0
2013-02-22 09:02 | FTR23 | LONG RURAL |  | 329 | 296 | 97384 | 0.3771 | 0.001274 | 0
2013-02-22 09:10 | BWA22 | LONG RURAL |  | 2 | 80 | 160 | 0.00061957 | 7.7446e-06 | 0
2013-02-22 10:40 | WOTS11 | LONG RURAL |  | 1 | 80 | 80 | 0.00030979 | 3.8723e-06 | 0
2013-02-22 08:45 | WOTS11 | LONG RURAL |  | 1 | 60 | 60 | 0.00023234 | 3.8723e-06 | 0
2013-02-22 09:25 | MYT8 | SHORT RURAL |  | 12 | 45 | 540 | 0.0046991 | 0.00010442 | 0
2013-02-15 09:55 | WGL21 | LONG RURAL |  | 2 | 39 | 78 | 0.00030204 | 7.7446e-06 | 0
2013-02-15 10:25 | WGL13 | SHORT RURAL |  | 5 | 200 | 1000 | 0.008702 | 4.351e-05 | 0
2013-02-15 11:20 | WGL21 | LONG RURAL |  | 2 | 30 | 60 | 0.00023234 | 7.7446e-06 | 0
2013-02-15 12:28 | WGL21 | LONG RURAL |  | 3 | 47 | 141 | 0.000546 | 1.1617e-05 | 0
2013-02-22 08:47 | TGN12 | SHORT RURAL |  | 24 | 135 | 3240 | 0.028194 | 0.00020885 | 0
2013-02-13 08:49 | WN5 | LONG RURAL |  | 18 | 313 | 5634 | 0.021817 | 6.9702e-05 | 0
2013-02-21 12:08 | TGN23 | SHORT RURAL |  | 58 | 84 | 4872 | 0.042396 | 0.00050471 | 0
2013-02-18 08:55 | MFA23 | SHORT RURAL |  | 4 | 205 | 820 | 0.0071356 | 3.4808e-05 | 0
2013-02-16 09:00 | CYN21 | URBAN |  | 176 | 510 | 89760 | 0.31268 | 0.00061309 | 0
2013-02-19 09:20 | BDL6 | SHORT RURAL |  | 60 | 130 | 7800 | 0.067875 | 0.00052212 | 0
2013-02-19 10:12 | ELM12 | SHORT RURAL |  | 83 | 218 | 18094 | 0.15745 | 0.00072226 | 0
2013-02-17 08:00 | RWT22 | URBAN |  | 85 | 300 | 25500 | 0.088829 | 0.0002961 | 0
2013-02-19 10:00 | NLA32 | SHORT RURAL |  | 9 | 220 | 1980 | 0.01723 | 7.8318e-05 | 0
2013-02-14 09:00 | CYN32 | URBAN |  | 243 | 280 | 68040 | 0.23702 | 0.00084649 | 0
2013-02-14 09:35 | KLK3 | SHORT RURAL |  | 139 | 225 | 31275 | 0.27215 | 0.0012096 | 0
2013-02-14 10:00 | ELM33 | SHORT RURAL |  | 7 | 255 | 1785 | 0.015533 | 6.0914e-05 | 0
2013-02-19 09:03 | SMR8 | LONG RURAL |  | 2387 | 378 | 902286 | 3.4939 | 0.0092432 | 0
2013-02-21 09:20 | LGA13 | LONG RURAL |  | 5 | 225 | 1125 | 0.0043564 | 1.9362e-05 | 0
2013-02-13 13:25 | ELM13 | URBAN |  | 83 | 110 | 9130 | 0.031804 | 0.00028913 | 0
2013-02-12 08:00 | MDG1 | SHORT RURAL |  | 99 | 280 | 27720 | 0.24122 | 0.0008615 | 0
2013-02-13 09:39 | TT4 | URBAN |  | 29 | 331 | 9599 | 0.033438 | 0.00010102 | 0
2013-02-13 09:39 | TT5 | URBAN |  | 86 | 331 | 28466 | 0.099161 | 0.00029958 | 0
2013-02-13 08:30 | BWR32 | URBAN |  | 146 | 297 | 43362 | 0.15105 | 0.00050859 | 0
2013-02-15 09:10 | ELM13 | URBAN |  | 54 | 320 | 17280 | 0.060195 | 0.00018811 | 0
2013-02-22 09:10 | LGA13 | LONG RURAL |  | 4 | 385 | 1540 | 0.0059634 | 1.5489e-05 | 0
2013-02-17 08:59 | FGY22 | URBAN |  | 189 | 390 | 73710 | 0.25677 | 0.00065838 | 0
2013-02-17 08:00 | CRE22 | URBAN |  | 68 | 255 | 17340 | 0.060404 | 0.00023688 | 0
2013-02-13 08:54 | MSD1 | LONG RURAL |  | 1 | 139 | 139 | 0.00053825 | 3.8723e-06 | 0
2013-02-14 08:35 | MSD4 | LONG RURAL |  | 2 | 78 | 156 | 0.00060408 | 7.7446e-06 | 0
2013-02-23 08:30 | LDL13 | SHORT RURAL |  | 292 | 332 | 96944 | 0.8436 | 0.002541 | 0
2013-02-23 09:00 | LGA13 | LONG RURAL |  | 13 | 261 | 3393 | 0.013139 | 5.034e-05 | 0
2013-02-22 10:13 | WOTS11 | LONG RURAL |  | 4 | 78 | 312 | 0.0012082 | 1.5489e-05 | 0
2013-02-22 11:15 | MYT8 | SHORT RURAL |  | 9 | 115 | 1035 | 0.0090065 | 7.8318e-05 | 0
2013-02-23 09:00 | WO31 | URBAN |  | 201 | 460 | 92460 | 0.32208 | 0.00070018 | 0
2013-02-16 08:40 | EPG32 | SHORT RURAL |  | 5 | 20 | 100 | 0.0008702 | 4.351e-05 | 0
2013-02-16 13:15 | EPG32 | SHORT RURAL |  | 1 | 35 | 35 | 0.00030457 | 8.702e-06 | 0
2013-02-22 07:00 | MOE31 | LONG RURAL |  | 32 | 85 | 2720 | 0.010533 | 0.00012391 | 0
2013-02-20 09:05 | SMR3 | LONG RURAL |  | 14 | 265 | 3710 | 0.014366 | 5.4212e-05 | 0
2013-02-16 10:30 | EPG32 | SHORT RURAL |  | 2 | 10 | 20 | 0.00017404 | 1.7404e-05 | 0
2013-02-20 09:00 | KMS1 | SHORT RURAL |  | 2 | 5 | 10 | 8.702e-05 | 1.7404e-05 | 0
2013-02-22 12:00 | TGN12 | SHORT RURAL |  | 33 | 86 | 2838 | 0.024696 | 0.00028717 | 0
2013-02-17 06:22 | WOTS25 | SHORT RURAL |  | 277 | 364 | 100828 | 0.8774 | 0.0024104 | 0
2013-02-16 08:35 | OFR23 | LONG RURAL |  | 60 | 39.1667 | 2350 | 0.0090999 | 0.00023234 | 0
2013-02-21 09:15 | MYT7 | LONG RURAL |  | 2 | 125 | 250 | 0.00096808 | 7.7446e-06 | 0
2013-02-21 12:00 | MYT7 | LONG RURAL |  | 1 | 80 | 80 | 0.00030979 | 3.8723e-06 | 0
2013-02-20 09:51 | WGL21 | LONG RURAL |  | 2 | 34 | 68 | 0.00026332 | 7.7446e-06 | 0
2013-02-20 10:55 | WGL21 | LONG RURAL |  | 2 | 37 | 74 | 0.00028655 | 7.7446e-06 | 0
2013-02-21 09:35 | WGL21 | LONG RURAL |  | 3 | 48 | 144 | 0.00055761 | 1.1617e-05 | 0
2013-02-22 09:37 | FTR12 | LONG RURAL |  | 19 | 273 | 5187 | 0.020086 | 7.3574e-05 | 0
2013-02-21 11:22 | WGL21 | LONG RURAL |  | 1 | 48 | 48 | 0.00018587 | 3.8723e-06 | 0
2013-02-21 12:42 | WGL21 | LONG RURAL |  | 1 | 98 | 98 | 0.00037949 | 3.8723e-06 | 0
2013-02-21 11:43 | WGL21 | LONG RURAL |  | 1 | 52 | 52 | 0.00020136 | 3.8723e-06 | 0
2013-02-22 10:20 | LGA12 | SHORT RURAL |  | 112 | 301 | 33712 | 0.29336 | 0.00097462 | 0
2013-02-22 11:25 | WGL21 | LONG RURAL |  | 2 | 85 | 170 | 0.00065829 | 7.7446e-06 | 0
2013-02-22 13:35 | WGL21 | LONG RURAL |  | 3 | 45 | 135 | 0.00052276 | 1.1617e-05 | 0
2013-02-18 09:07 | MSD4 | LONG RURAL |  | 114 | 219 | 24966 | 0.096676 | 0.00044144 | 0
2013-02-14 12:15 | WN5 | LONG RURAL |  | 18 | 127 | 2286 | 0.0088521 | 6.9702e-05 | 0
2013-02-19 10:10 | WN5 | LONG RURAL |  | 1 | 134 | 134 | 0.00051889 | 3.8723e-06 | 0
2013-02-22 08:31 | BN3 | SHORT RURAL |  | 19 | 269 | 5111 | 0.044476 | 0.00016534 | 0
2013-02-14 08:32 | TT5 | URBAN |  | 18 | 208 | 3744 | 0.013042 | 6.2703e-05 | 0
2013-02-24 08:29 | LDL12 | URBAN |  | 147 | 243 | 35721 | 0.12443 | 0.00051207 | 0
2013-02-24 09:15 | MDG1 | SHORT RURAL |  | 161 | 312 | 50232 | 0.43712 | 0.001401 | 0
2013-02-24 09:15 | MWTS34 | SHORT RURAL |  | 657 | 388.898 | 255506 | 2.2234 | 0.0057172 | 0
2013-02-24 10:30 | LLG12 | SHORT RURAL |  | 7 | 195 | 1365 | 0.011878 | 6.0914e-05 | 0
2013-02-21 09:00 | SMR3 | LONG RURAL |  | 67 | 395 | 26465 | 0.10248 | 0.00025945 | 0
2013-02-19 09:30 | WT15 | URBAN |  | 56 | 115 | 6440 | 0.022434 | 0.00019508 | 0
2013-02-20 09:30 | TGN31 | LONG RURAL |  | 2 | 290 | 580 | 0.0022459 | 7.7446e-06 | 0
2013-02-18 09:00 | RWN24 | SHORT RURAL |  | 7 | 250 | 1750 | 0.015228 | 6.0914e-05 | 0
2013-02-18 08:32 | RWN24 | SHORT RURAL |  | 104 | 197 | 20488 | 0.17829 | 0.000905 | 0
2013-02-24 09:30 | MOE23 | SHORT RURAL |  | 42 | 410 | 17220 | 0.14985 | 0.00036548 | 0
2013-02-18 10:30 | RWN31 | SHORT RURAL |  | 1 | 45 | 45 | 0.00039159 | 8.702e-06 | 0
2013-02-18 09:00 | RWN24 | SHORT RURAL |  | 1 | 35 | 35 | 0.00030457 | 8.702e-06 | 0
2013-02-21 09:18 | LGA13 | LONG RURAL |  | 59 | 355 | 20945 | 0.081106 | 0.00022847 | 0
2013-02-20 09:30 | BDL1 | LONG RURAL |  | 2 | 130 | 260 | 0.0010068 | 7.7446e-06 | 0
2013-02-20 12:15 | BDL1 | LONG RURAL |  | 3 | 20 | 60 | 0.00023234 | 1.1617e-05 | 0
2013-02-20 12:10 | BDL1 | LONG RURAL |  | 3 | 20 | 60 | 0.00023234 | 1.1617e-05 | 0
2013-02-19 09:40 | SLE31 | LONG RURAL |  | 941 | 178.4346 | 167907 | 0.65019 | 0.0036438 | 0
2013-02-15 08:35 | ELM33 | SHORT RURAL |  | 22 | 290 | 6380 | 0.055519 | 0.00019144 | 0
2013-02-20 09:00 | SLE31 | LONG RURAL |  | 558 | 16.3548 | 9126 | 0.035339 | 0.0021608 | 0
2013-02-21 10:00 | SLE31 | LONG RURAL |  | 23 | 210 | 4830 | 0.018703 | 8.9063e-05 | 0
2013-02-21 08:55 | BDL1 | LONG RURAL |  | 2 | 125 | 250 | 0.00096808 | 7.7446e-06 | 0
2013-02-23 09:00 | WGL13 | SHORT RURAL |  | 69 | 400 | 27600 | 0.24017 | 0.00060044 | 0
2013-02-22 13:25 | BDL1 | LONG RURAL |  | 1 | 75 | 75 | 0.00029042 | 3.8723e-06 | 0
2013-02-18 09:00 | BGE22 | SHORT RURAL |  | 4 | 305 | 1220 | 0.010616 | 3.4808e-05 | 0
2013-02-22 09:00 | WN3 | LONG RURAL |  | 3 | 180 | 540 | 0.002091 | 1.1617e-05 | 0
2013-02-18 09:05 | BGE11 | SHORT RURAL |  | 118 | 420 | 49560 | 0.43127 | 0.0010268 | 0
2013-02-19 09:10 | BGE24 | SHORT RURAL |  | 7 | 275 | 1925 | 0.016751 | 6.0914e-05 | 0
2013-02-17 09:09 | FTR12 | LONG RURAL |  | 124 | 244.3306 | 30297 | 0.11732 | 0.00048017 | 0
2013-02-24 08:31 | SMR2 | SHORT RURAL |  | 14 | 108 | 1512 | 0.013157 | 0.00012183 | 0
2013-02-15 07:30 | DRN12 | URBAN |  | 1 | 555 | 555 | 0.0019333 | 3.4835e-06 | 0
2013-02-19 08:30 | OFR23 | LONG RURAL |  | 87 | 250 | 21750 | 0.084223 | 0.00033689 | 0
2013-02-19 08:30 | OFR23 | LONG RURAL |  | 74 | 388.8649 | 28776 | 0.11143 | 0.00028655 | 0
2013-02-20 09:42 | CRE21 | SHORT RURAL |  | 4 | 30 | 120 | 0.0010442 | 3.4808e-05 | 0
2013-02-20 10:45 | CRE32 | URBAN |  | 25 | 25 | 625 | 0.0021772 | 8.7087e-05 | 0
2013-02-20 13:20 | CRE32 | URBAN |  | 16 | 360 | 5760 | 0.020065 | 5.5736e-05 | 0
2013-02-11 12:10 | WYK11 | SHORT RURAL |  | 1 | 50 | 50 | 0.0004351 | 8.702e-06 | 0
2013-02-25 09:40 | WGL11 | SHORT RURAL |  | 9 | 60 | 540 | 0.0046991 | 7.8318e-05 | 0
2013-02-25 09:00 | WO31 | URBAN |  | 302 | 244.043 | 73701 | 0.25674 | 0.001052 | 0
2013-02-25 09:45 | LGA12 | SHORT RURAL |  | 3 | 145 | 435 | 0.0037854 | 2.6106e-05 | 0
2013-02-25 09:10 | WGL11 | SHORT RURAL |  | 62 | 215 | 13330 | 0.116 | 0.00053952 | 0
2013-02-25 09:00 | FTR21 | LONG RURAL |  | 19 | 175 | 3325 | 0.012875 | 7.3574e-05 | 0
2013-02-25 09:15 | BRT21 | SHORT RURAL |  | 2 | 135 | 270 | 0.0023495 | 1.7404e-05 | 0
2013-02-25 09:10 | WYK23 | SHORT RURAL |  | 238 | 175 | 41650 | 0.36244 | 0.0020711 | 0
2013-02-25 11:23 | WN4 | SHORT RURAL |  | 4 | 177 | 708 | 0.006161 | 3.4808e-05 | 0
2013-02-25 09:40 | ALA01 | LONG RURAL |  | 1 | 140 | 140 | 0.00054212 | 3.8723e-06 | 0
2013-02-19 08:58 | RWN31 | SHORT RURAL |  | 215 | 341.2419 | 73367 | 0.63844 | 0.0018709 | 0
2013-02-20 09:22 | BRA32 | URBAN |  | 84 | 224 | 18816 | 0.065545 | 0.00029261 | 0
2013-02-19 09:45 | WT12 | URBAN |  | 9 | 180 | 1620 | 0.0056432 | 3.1351e-05 | 0
2013-02-22 09:30 | BDL1 | LONG RURAL |  | 25 | 186 | 4650 | 0.018006 | 9.6808e-05 | 0
2013-02-19 11:40 | WT15 | URBAN |  | 67 | 85 | 5695 | 0.019838 | 0.00023339 | 0
2013-02-19 14:02 | WT15 | URBAN |  | 125 | 63 | 7875 | 0.027432 | 0.00043544 | 0
2013-02-21 09:00 | RWN24 | SHORT RURAL |  | 270 | 306 | 82620 | 0.71896 | 0.0023495 | 0
2013-02-20 09:35 | MDG1 | SHORT RURAL |  | 250 | 148 | 37000 | 0.32197 | 0.0021755 | 0
2013-02-14 10:35 | BWR34 | URBAN |  | 105 | 227 | 23835 | 0.083029 | 0.00036577 | 0
2013-02-22 12:30 | FTR22 | SHORT RURAL |  | 1 | 10 | 10 | 8.702e-05 | 8.702e-06 | 0
2013-02-20 10:00 | NRN14 | URBAN |  | 99 | 0 | 0 | 0 | 0.00034486 | 0
2013-02-21 08:22 | BGE22 | SHORT RURAL |  | 24 | 443 | 10632 | 0.092519 | 0.00020885 | 0
2013-02-19 09:20 | BWR34 | URBAN |  | 107 | 280 | 29960 | 0.10437 | 0.00037273 | 0
2013-02-20 09:10 | OFR23 | LONG RURAL |  | 6 | 75 | 450 | 0.0017425 | 2.3234e-05 | 0
2013-02-19 10:00 | DRN14 | SHORT RURAL |  | 191 | 249.2565 | 47608 | 0.41428 | 0.0016621 | 0
2013-02-21 09:00 | BGE12 | SHORT RURAL |  | 11 | 233 | 2563 | 0.022303 | 9.5722e-05 | 0
2013-02-21 09:06 | LLG11 | SHORT RURAL |  | 144 | 70 | 10080 | 0.087716 | 0.0012531 | 0
2013-02-21 11:45 | BGE12 | SHORT RURAL |  | 8 | 45 | 360 | 0.0031327 | 6.9616e-05 | 0
2013-02-21 11:30 | PHM14 | LONG RURAL |  | 2 | 20 | 40 | 0.00015489 | 7.7446e-06 | 0
2013-02-21 08:55 | RWT22 | URBAN |  | 56 | 430 | 24080 | 0.083882 | 0.00019508 | 0
2013-02-21 08:50 | RWT22 | URBAN |  | 275 | 400 | 110000 | 0.38318 | 0.00095796 | 0
2013-02-26 05:20 | MWTS21 | URBAN |  | 5 | 76 | 380 | 0.0013237 | 1.7417e-05 | 0
2013-02-25 12:30 | LGA12 | SHORT RURAL |  | 5 | 50 | 250 | 0.0021755 | 4.351e-05 | 0
2013-02-28 09:00 | WGI31 | SHORT RURAL |  | 710 | 227 | 161170 | 1.4025 | 0.0061784 | 0
2013-02-27 09:00 | LGA11 | LONG RURAL |  | 38 | 320 | 12160 | 0.047087 | 0.00014715 | 0
2013-02-26 11:35 | WGL12 | LONG RURAL |  | 9 | 95 | 855 | 0.0033108 | 3.4851e-05 | 0
2013-02-26 09:27 | WGL21 | LONG RURAL |  | 4 | 12 | 48 | 0.00018587 | 1.5489e-05 | 0
2013-02-28 09:00 | LGA13 | LONG RURAL |  | 84 | 420 | 35280 | 0.13662 | 0.00032527 | 0
2013-02-26 09:30 | WGL24 | LONG RURAL |  | 7 | 230 | 1610 | 0.0062344 | 2.7106e-05 | 0
2013-02-26 09:45 | TGN12 | SHORT RURAL |  | 2 | 45 | 90 | 0.00078318 | 1.7404e-05 | 0
2013-02-26 09:25 | MOE22 | LONG RURAL |  | 29 | 95 | 2755 | 0.010668 | 0.0001123 | 0
2013-02-26 11:35 | MOE22 | LONG RURAL |  | 3 | 45 | 135 | 0.00052276 | 1.1617e-05 | 0
2013-02-28 08:15 | WGI24 | URBAN |  | 35 | 17 | 595 | 0.0020727 | 0.00012192 | 0
2013-02-27 09:50 | MWTS14 | SHORT RURAL |  | 220 | 306 | 67320 | 0.58582 | 0.0019144 | 0
2013-02-27 08:30 | TGN23 | SHORT RURAL |  | 19 | 455 | 8645 | 0.075229 | 0.00016534 | 0
2013-02-27 09:50 | WYK23 | SHORT RURAL |  | 25 | 235 | 5875 | 0.051124 | 0.00021755 | 0
2013-02-26 08:37 | TGN22 | URBAN |  | 30 | 21 | 630 | 0.0021946 | 0.0001045 | 0
2013-02-27 10:00 | WYK23 | SHORT RURAL |  | 52 | 300 | 15600 | 0.13575 | 0.0004525 | 0
2013-02-27 09:10 | WGL21 | LONG RURAL |  | 4 | 170 | 680 | 0.0026332 | 1.5489e-05 | 0
2013-02-27 09:20 | WGL12 | LONG RURAL |  | 64 | 280 | 17920 | 0.069392 | 0.00024783 | 0
2013-02-27 09:00 | WGL21 | LONG RURAL |  | 3 | 130 | 390 | 0.0015102 | 1.1617e-05 | 0
2013-02-27 08:40 | LDL13 | SHORT RURAL |  | 365 | 245 | 89425 | 0.77817 | 0.0031762 | 0
2013-02-27 09:30 | LDL24 | URBAN |  | 7 | 140 | 980 | 0.0034138 | 2.4384e-05 | 0
2013-02-27 08:30 | WYK12 | SHORT RURAL |  | 39 | 285 | 11115 | 0.096722 | 0.00033938 | 0
2013-02-28 09:00 | WGL24 | LONG RURAL |  | 60 | 275 | 16500 | 0.063893 | 0.00023234 | 0
2013-02-28 09:30 | WGL21 | LONG RURAL |  | 36 | 190 | 6840 | 0.026487 | 0.0001394 | 0
2013-02-26 08:30 | WO31 | URBAN |  | 10 | 315 | 3150 | 0.010973 | 3.4835e-05 | 0
2013-02-26 09:30 | BWA22 | LONG RURAL |  | 1 | 125 | 125 | 0.00048404 | 3.8723e-06 | 0
2013-02-27 09:30 | FTR23 | LONG RURAL |  | 23 | 186 | 4278 | 0.016566 | 8.9063e-05 | 0
2013-02-26 10:00 | BWA22 | LONG RURAL |  | 11 | 188 | 2068 | 0.0080079 | 4.2595e-05 | 0
2013-02-25 12:14 | WYK23 | SHORT RURAL |  | 44 | 81 | 3564 | 0.031014 | 0.00038289 | 0
2013-02-27 09:00 | LGA13 | LONG RURAL |  | 102 | 180 | 18360 | 0.071096 | 0.00039498 | 0
2013-02-27 09:10 | WGL23 | SHORT RURAL |  | 3 | 335 | 1005 | 0.0087455 | 2.6106e-05 | 0
2013-02-27 09:01 | FTR23 | LONG RURAL |  | 41 | 377 | 15457 | 0.059854 | 0.00015876 | 0
2013-02-27 11:00 | MOE22 | LONG RURAL |  | 13 | 240 | 3120 | 0.012082 | 5.034e-05 | 0
2013-02-27 09:01 | FTR23 | LONG RURAL |  | 24 | 5 | 120 | 0.00046468 | 9.2936e-05 | 0
2013-02-27 15:13 | FTR23 | LONG RURAL |  | 24 | 5 | 120 | 0.00046468 | 9.2936e-05 | 0
2013-02-27 09:00 | WN5 | LONG RURAL |  | 4 | 123 | 492 | 0.0019052 | 1.5489e-05 | 0
2013-02-26 10:25 | MSD4 | LONG RURAL |  | 26 | 160 | 4160 | 0.016109 | 0.00010068 | 0
2013-02-27 09:05 | BWA22 | LONG RURAL |  | 4 | 55 | 220 | 0.00085191 | 1.5489e-05 | 0
2013-02-27 10:10 | BWA22 | LONG RURAL |  | 2 | 50 | 100 | 0.00038723 | 7.7446e-06 | 0
2013-02-27 11:35 | BWA22 | LONG RURAL |  | 2 | 40 | 80 | 0.00030979 | 7.7446e-06 | 0
2013-02-28 10:20 | MYT7 | LONG RURAL |  | 1 | 85 | 85 | 0.00032915 | 3.8723e-06 | 0
2013-02-28 09:30 | MBY11 | SHORT RURAL |  | 9 | 190 | 1710 | 0.01488 | 7.8318e-05 | 0
2013-02-27 08:39 | YN35 | URBAN |  | 2 | 72 | 144 | 0.00050162 | 6.967e-06 | 0
2013-02-27 11:29 | WN5 | LONG RURAL |  | 2 | 27 | 54 | 0.0002091 | 7.7446e-06 | 0
2013-02-28 09:18 | LLG12 | SHORT RURAL |  | 531 | 44.8192 | 23799 | 0.2071 | 0.0046207 | 0
2013-02-18 10:05 | CLN13 | SHORT RURAL |  | 27 | 158 | 4266 | 0.037123 | 0.00023495 | 0
2013-02-19 08:45 | WT13 | URBAN |  | 153 | 415 | 63495 | 0.22118 | 0.00053297 | 0
2013-02-20 08:45 | WT11 | URBAN |  | 332 | 445 | 147740 | 0.51465 | 0.0011565 | 0
2013-02-20 08:45 | ELM33 | SHORT RURAL |  | 1 | 285 | 285 | 0.0024801 | 8.702e-06 | 0
2013-02-20 08:30 | ELM33 | SHORT RURAL |  | 1 | 180 | 180 | 0.0015664 | 8.702e-06 | 0
2013-02-20 17:10 | ELM31 | URBAN |  | 110 | 140 | 15400 | 0.053646 | 0.00038318 | 0
2013-02-22 08:30 | OFR22 | SHORT RURAL |  | 30 | 195 | 5850 | 0.050907 | 0.00026106 | 0
2013-02-22 08:31 | BWN14 | SHORT RURAL |  | 102 | 264 | 26928 | 0.23433 | 0.0008876 | 0
2013-02-22 08:49 | BGE12 | SHORT RURAL |  | 148 | 375 | 55500 | 0.48296 | 0.0012879 | 0
2013-02-22 08:49 | BGE12 | SHORT RURAL |  | 424 | 1 | 424 | 0.0036896 | 0.0036896 | 0
2013-02-22 15:03 | BGE12 | SHORT RURAL |  | 424 | 1 | 424 | 0.0036896 | 0.0036896 | 0
2013-02-25 08:35 | SFS1 | SHORT RURAL |  | 106 | 423 | 44838 | 0.39018 | 0.00092241 | 0
2013-02-22 09:20 | WGL15 | SHORT RURAL |  | 16 | 130 | 2080 | 0.0181 | 0.00013923 | 0
2013-02-21 09:45 | DRN12 | URBAN |  | 3 | 135 | 405 | 0.0014108 | 1.045e-05 | 0
2013-02-21 09:30 | ELM15 | SHORT RURAL |  | 72 | 65 | 4680 | 0.040725 | 0.00062654 | 0
2013-02-21 10:15 | ELM33 | SHORT RURAL |  | 2 | 285 | 570 | 0.0049601 | 1.7404e-05 | 0
2013-02-21 10:00 | KLO14 | LONG RURAL |  | 3 | 105 | 315 | 0.0012198 | 1.1617e-05 | 0
2013-02-22 08:05 | SLE31 | LONG RURAL |  | 540 | 386 | 208440 | 0.80715 | 0.002091 | 0
2013-02-21 12:30 | DRN12 | URBAN |  | 1 | 75 | 75 | 0.00026126 | 3.4835e-06 | 0
2013-02-21 09:55 | WT13 | URBAN |  | 57 | 105 | 5985 | 0.020849 | 0.00019856 | 0
2013-02-21 12:15 | KLO14 | LONG RURAL |  | 22 | 90 | 1980 | 0.0076672 | 8.5191e-05 | 0
2013-02-22 08:05 | ELM33 | SHORT RURAL |  | 2 | 345 | 690 | 0.0060044 | 1.7404e-05 | 0
2013-02-22 09:10 | EPG32 | SHORT RURAL |  | 6 | 15 | 90 | 0.00078318 | 5.2212e-05 | 0
2013-02-22 09:45 | EPG32 | SHORT RURAL |  | 1 | 15 | 15 | 0.00013053 | 8.702e-06 | 0
2013-02-22 10:30 | EPG32 | SHORT RURAL |  | 9 | 20 | 180 | 0.0015664 | 7.8318e-05 | 0
2013-02-22 13:30 | EPG32 | SHORT RURAL |  | 2 | 25 | 50 | 0.0004351 | 1.7404e-05 | 0
2013-02-23 08:30 | EPG32 | SHORT RURAL |  | 8 | 30 | 240 | 0.0020885 | 6.9616e-05 | 0
2013-02-23 09:30 | EPG32 | SHORT RURAL |  | 2 | 25 | 50 | 0.0004351 | 1.7404e-05 | 0
2013-02-23 10:30 | EPG32 | SHORT RURAL |  | 16 | 20 | 320 | 0.0027846 | 0.00013923 | 0
2013-02-25 08:30 | ELM13 | URBAN |  | 4 | 500 | 2000 | 0.006967 | 1.3934e-05 | 0
2013-02-25 09:00 | ELM33 | SHORT RURAL |  | 22 | 485 | 10670 | 0.09285 | 0.00019144 | 0
2013-02-24 09:00 | WT13 | URBAN |  | 11 | 115 | 1265 | 0.0044066 | 3.8318e-05 | 0
2013-02-26 11:22 | WN5 | LONG RURAL |  | 1 | 118 | 118 | 0.00045693 | 3.8723e-06 | 0
2013-02-24 11:50 | WT13 | URBAN |  | 19 | 115 | 2185 | 0.0076114 | 6.6186e-05 | 0
2013-02-28 09:05 | MYT7 | LONG RURAL |  | 6 | 440 | 2640 | 0.010223 | 2.3234e-05 | 0
2013-02-28 09:05 | WN5 | LONG RURAL |  | 25 | 440 | 11000 | 0.042595 | 9.6808e-05 | 0
2013-02-25 09:35 | DRN11 | URBAN |  | 1 | 34 | 34 | 0.00011844 | 3.4835e-06 | 0
2013-02-25 09:40 | DRN12 | URBAN |  | 56 | 55 | 3080 | 0.010729 | 0.00019508 | 0
2013-02-22 09:22 | RWN24 | SHORT RURAL |  | 389 | 438 | 170382 | 1.4827 | 0.0033851 | 0
2013-03-01 09:05 | PHI12 | SHORT RURAL |  | 105 | 234 | 24570 | 0.21381 | 0.00091371 | 0
2013-03-01 09:00 | PHI11 | SHORT RURAL |  | 69 | 299 | 20631 | 0.17953 | 0.00060044 | 0
2013-03-01 09:01 | FTR21 | LONG RURAL |  | 50 | 349 | 17450 | 0.067572 | 0.00019362 | 0
2013-03-01 09:05 | WYK11 | SHORT RURAL |  | 4 | 50 | 200 | 0.0017404 | 3.4808e-05 | 0
2013-03-01 10:05 | WYK11 | SHORT RURAL |  | 24 | 55 | 1320 | 0.011487 | 0.00020885 | 0
2013-02-28 12:50 | MYT7 | LONG RURAL |  | 2 | 90 | 180 | 0.00069702 | 7.7446e-06 | 0
2013-03-01 08:55 | TGN11 | SHORT RURAL |  | 20 | 289 | 5780 | 0.050297 | 0.00017404 | 0
2013-03-01 09:03 | FTR12 | LONG RURAL |  | 7 | 95 | 665 | 0.0025751 | 2.7106e-05 | 0
2013-03-01 09:00 | MBY11 | SHORT RURAL |  | 31 | 200 | 6200 | 0.053952 | 0.00026976 | 0
2013-02-25 12:10 | DRN12 | URBAN |  | 6 | 55 | 330 | 0.0011495 | 2.0901e-05 | 0
2013-02-24 09:00 | BRT22 | SHORT RURAL |  | 19 | 235 | 4465 | 0.038854 | 0.00016534 | 0
2013-02-14 09:20 | WN5 | LONG RURAL |  | 6 | 170 | 1020 | 0.0039498 | 2.3234e-05 | 0
2013-02-25 09:30 | LDL24 | URBAN |  | 59 | 147 | 8673 | 0.030212 | 0.00020553 | 0
2013-02-25 09:30 | RWN33 | URBAN |  | 71 | 147 | 10437 | 0.036357 | 0.00024733 | 0
2013-03-01 08:40 | WO31 | URBAN |  | 123 | 147 | 18081 | 0.062985 | 0.00042847 | 0
2013-02-25 08:32 | RWN31 | SHORT RURAL |  | 2 | 186 | 372 | 0.0032371 | 1.7404e-05 | 0
2013-02-27 08:30 | RWN32 | URBAN |  | 135 | 395 | 53325 | 0.18576 | 0.00047027 | 0
2013-02-22 08:30 | MFA31 | SHORT RURAL |  | 76 | 260 | 19760 | 0.17195 | 0.00066135 | 0
2013-02-24 09:00 | WGL13 | SHORT RURAL |  | 1 | 130 | 130 | 0.0011313 | 8.702e-06 | 0
2013-03-01 09:30 | MOE14 | SHORT RURAL |  | 37 | 140 | 5180 | 0.045076 | 0.00032197 | 0
2013-02-27 08:33 | WN5 | LONG RURAL |  | 128 | 394 | 50432 | 0.19529 | 0.00049566 | 0
2013-02-18 09:41 | ALA01 | LONG RURAL |  | 12 | 164 | 1968 | 0.0076207 | 4.6468e-05 | 0
2013-02-24 10:05 | NLA31 | LONG RURAL |  | 1 | 118 | 118 | 0.00045693 | 3.8723e-06 | 0
2013-02-28 10:25 | BN1 | LONG RURAL |  | 2 | 145 | 290 | 0.001123 | 7.7446e-06 | 0
2013-03-01 09:05 | BN1 | LONG RURAL |  | 5 | 165 | 825 | 0.0031947 | 1.9362e-05 | 0
2013-02-28 09:35 | MYT7 | LONG RURAL |  | 104 | 230 | 23920 | 0.092626 | 0.00040272 | 0
2013-02-24 08:38 | RWT11 | URBAN |  | 119 | 397 | 47243 | 0.16457 | 0.00041453 | 0
2013-02-24 08:30 | BWR34 | URBAN |  | 11 | 100 | 1100 | 0.0038318 | 3.8318e-05 | 0
2013-02-24 09:10 | NLA32 | SHORT RURAL |  | 65 | 350 | 22750 | 0.19797 | 0.00056563 | 0
2013-02-26 12:25 | SMR8 | LONG RURAL |  | 2 | 145 | 290 | 0.001123 | 7.7446e-06 | 0
2013-02-19 09:00 | SMR5 | LONG RURAL |  | 14 | 164 | 2296 | 0.0088908 | 5.4212e-05 | 0
2013-03-02 08:30 | LDL23 | LONG RURAL |  | 11 | 435 | 4785 | 0.018529 | 4.2595e-05 | 0
2013-03-01 12:30 | WYK11 | SHORT RURAL |  | 12 | 45 | 540 | 0.0046991 | 0.00010442 | 0
2013-02-21 11:55 | KMS21 | SHORT RURAL |  | 1 | 50 | 50 | 0.0004351 | 8.702e-06 | 0
2013-02-18 11:25 | LLG14 | SHORT RURAL |  | 1 | 185 | 185 | 0.0016099 | 8.702e-06 | 0
2013-02-27 10:54 | SMR8 | LONG RURAL |  | 6 | 111 | 666 | 0.002579 | 2.3234e-05 | 0
2013-02-27 10:10 | SMR8 | LONG RURAL |  | 5 | 175 | 875 | 0.0033883 | 1.9362e-05 | 0
2013-02-27 09:45 | SMR8 | LONG RURAL |  | 11 | 55 | 605 | 0.0023428 | 4.2595e-05 | 0
2013-02-27 13:20 | SMR8 | LONG RURAL |  | 4 | 65 | 260 | 0.0010068 | 1.5489e-05 | 0
2013-02-27 09:00 | SMR5 | LONG RURAL |  | 59 | 230 | 13570 | 0.052547 | 0.00022847 | 0
2013-02-25 10:16 | FTR12 | LONG RURAL |  | 3 | 169 | 507 | 0.0019633 | 1.1617e-05 | 0
2013-03-01 09:20 | BWA22 | LONG RURAL |  | 1 | 60 | 60 | 0.00023234 | 3.8723e-06 | 0
2013-02-24 11:40 | WGL13 | SHORT RURAL |  | 2 | 80 | 160 | 0.0013923 | 1.7404e-05 | 0
2013-02-28 09:20 | SMR5 | LONG RURAL |  | 1 | 130 | 130 | 0.0005034 | 3.8723e-06 | 0
2013-02-25 10:30 | SMR5 | LONG RURAL |  | 49 | 106 | 5194 | 0.020113 | 0.00018974 | 0
2013-02-20 09:50 | CLN13 | SHORT RURAL |  | 5 | 75 | 375 | 0.0032632 | 4.351e-05 | 0
2013-02-25 08:28 | BWN14 | SHORT RURAL |  | 40 | 237 | 9480 | 0.082495 | 0.00034808 | 0
2013-02-27 08:55 | CLN22 | SHORT RURAL |  | 188 | 323 | 60724 | 0.52842 | 0.001636 | 0
2013-02-26 11:15 | BGE12 | SHORT RURAL |  | 1 | 45 | 45 | 0.00039159 | 8.702e-06 | 0
2013-02-27 11:10 | BDL5 | LONG RURAL |  | 90 | 138 | 12420 | 0.048094 | 0.00034851 | 0
2013-02-27 06:53 | PHM32 | URBAN |  | 49 | 39 | 1911 | 0.0066569 | 0.00017069 | 0
2013-02-14 14:52 | BDL6 | SHORT RURAL |  | 5 | 190 | 950 | 0.0082669 | 4.351e-05 | 0
2013-03-03 08:35 | BN4 | URBAN |  | 38 | 313 | 11894 | 0.041433 | 0.00013237 | 0
2013-03-03 09:43 | TGN23 | SHORT RURAL |  | 364 | 421 | 153244 | 1.3335 | 0.0031675 | 0
2013-03-03 09:00 | WO11 | URBAN |  | 160 | 446 | 71360 | 0.24858 | 0.00055736 | 0
2013-03-03 09:00 | BN1 | LONG RURAL |  | 68 | 260 | 17680 | 0.068463 | 0.00026332 | 0
2013-03-03 09:00 | MYT8 | SHORT RURAL |  | 65 | 365 | 23725 | 0.20645 | 0.00056563 | 0
2013-02-24 13:25 | WGL13 | SHORT RURAL |  | 2 | 75 | 150 | 0.0013053 | 1.7404e-05 | 0
2013-02-27 08:56 | EPG12 | URBAN |  | 71 | 189 | 13419 | 0.046745 | 0.00024733 | 0
2013-02-28 08:30 | ELM33 | SHORT RURAL |  | 18 | 225 | 4050 | 0.035243 | 0.00015664 | 0
2013-02-27 09:05 | ELM33 | SHORT RURAL |  | 1 | 115 | 115 | 0.0010007 | 8.702e-06 | 0
2013-02-28 08:20 | ELM33 | SHORT RURAL |  | 15 | 240 | 3600 | 0.031327 | 0.00013053 | 0
2013-02-28 12:30 | ELM33 | SHORT RURAL |  | 35 | 150 | 5250 | 0.045685 | 0.00030457 | 0
2013-02-28 13:30 | ELM33 | SHORT RURAL |  | 5 | 90 | 450 | 0.0039159 | 4.351e-05 | 0
2013-03-01 09:00 | ELM33 | SHORT RURAL |  | 1 | 125 | 125 | 0.0010877 | 8.702e-06 | 0
2013-02-28 09:33 | ALA01 | LONG RURAL |  | 4 | 117 | 468 | 0.0018122 | 1.5489e-05 | 0
2013-02-28 09:30 | SMR5 | LONG RURAL |  | 1 | 30 | 30 | 0.00011617 | 3.8723e-06 | 0
2013-02-28 14:19 | SMR5 | LONG RURAL |  | 4 | 34 | 136 | 0.00052663 | 1.5489e-05 | 0
2013-03-01 11:00 | EPG23 | URBAN |  | 1 | 45 | 45 | 0.00015676 | 3.4835e-06 | 0
2013-02-28 14:08 | SMR5 | LONG RURAL |  | 1 | 42 | 42 | 0.00016264 | 3.8723e-06 | 0
2013-02-28 10:45 | KMS1 | SHORT RURAL |  | 1 | 85 | 85 | 0.00073967 | 8.702e-06 | 0
2013-02-28 12:40 | SMR3 | LONG RURAL |  | 1 | 65 | 65 | 0.0002517 | 3.8723e-06 | 0
2013-02-22 09:00 | SMR3 | LONG RURAL |  | 1 | 75 | 75 | 0.00029042 | 3.8723e-06 | 0
2013-02-26 09:10 | MFA34 | SHORT RURAL |  | 22 | 205 | 4510 | 0.039246 | 0.00019144 | 0
2013-02-25 08:00 | DRN12 | URBAN |  | 1 | 450 | 450 | 0.0015676 | 3.4835e-06 | 0
2013-02-25 09:25 | BRA14 | URBAN |  | 102 | 285 | 29070 | 0.10126 | 0.00035532 | 0
2013-02-26 09:10 | BDL2 | SHORT RURAL |  | 85 | 135 | 11475 | 0.099855 | 0.00073967 | 0
2013-03-02 07:36 | WOTS12 | URBAN |  | 393 | 5.3715 | 2111 | 0.0073536 | 0.001369 | 0
2013-02-27 09:20 | RWN24 | SHORT RURAL |  | 21 | 400 | 8400 | 0.073097 | 0.00018274 | 0
2013-02-27 09:10 | RWN26 | SHORT RURAL |  | 193 | 315 | 60795 | 0.52904 | 0.0016795 | 0
2013-02-27 08:36 | RWN22 | URBAN |  | 347 | 269 | 93343 | 0.32516 | 0.0012088 | 0
2013-03-04 09:00 | WGL21 | LONG RURAL |  | 93 | 301 | 27993 | 0.1084 | 0.00036013 | 0
2013-03-04 09:58 | MOE22 | LONG RURAL |  | 3 | 458.3333 | 1375 | 0.0053244 | 1.1617e-05 | 0
2013-03-04 10:15 | MWTS32 | SHORT RURAL |  | 13 | 75 | 975 | 0.0084844 | 0.00011313 | 0
2013-03-04 09:00 | LGA12 | SHORT RURAL |  | 84 | 380 | 31920 | 0.27777 | 0.00073097 | 0
2013-03-04 09:22 | MSD4 | LONG RURAL |  | 1 | 368 | 368 | 0.001425 | 3.8723e-06 | 0
2013-03-04 09:25 | WN5 | LONG RURAL |  | 1 | 60 | 60 | 0.00023234 | 3.8723e-06 | 0
2013-03-04 09:20 | WN5 | LONG RURAL |  | 3 | 125 | 375 | 0.0014521 | 1.1617e-05 | 0
2013-03-04 09:12 | MOE21 | SHORT RURAL |  | 2 | 403 | 806 | 0.0070138 | 1.7404e-05 | 0
2013-03-03 13:10 | WYK11 | SHORT RURAL |  | 6 | 100 | 600 | 0.0052212 | 5.2212e-05 | 0
2013-03-01 09:30 | SMR5 | LONG RURAL |  | 1 | 45 | 45 | 0.00017425 | 3.8723e-06 | 0
2013-03-01 09:30 | SMR5 | LONG RURAL |  | 1 | 112 | 112 | 0.0004337 | 3.8723e-06 | 0
2013-03-01 11:45 | SMR5 | LONG RURAL |  | 1 | 75 | 75 | 0.00029042 | 3.8723e-06 | 0
2013-03-01 11:01 | SMR5 | LONG RURAL |  | 124 | 28.25 | 3503 | 0.013565 | 0.00048017 | 0
2013-02-26 08:30 | CNR2 | SHORT RURAL |  | 1034 | 403 | 416702 | 3.6261 | 0.0089978 | 0
2013-03-02 09:05 | SMR8 | LONG RURAL |  | 38 | 210 | 7980 | 0.030901 | 0.00014715 | 0
2013-02-27 12:30 | NLA31 | LONG RURAL |  | 2 | 125 | 250 | 0.00096808 | 7.7446e-06 | 0
2013-02-27 08:50 | BDL6 | SHORT RURAL |  | 211 | 205 | 43255 | 0.3764 | 0.0018361 | 0
2013-03-04 09:15 | SMR5 | LONG RURAL |  | 18 | 257 | 4626 | 0.017913 | 6.9702e-05 | 0
2013-03-04 09:45 | SMR8 | LONG RURAL |  | 51 | 300 | 15300 | 0.059246 | 0.00019749 | 0
2013-03-01 12:00 | ELM33 | SHORT RURAL |  | 11 | 90 | 990 | 0.008615 | 9.5722e-05 | 0
2013-02-24 11:08 | SMR2 | SHORT RURAL |  | 28 | 217 | 6076 | 0.052873 | 0.00024366 | 0
2013-03-02 08:40 | EPG32 | SHORT RURAL |  | 2 | 10 | 20 | 0.00017404 | 1.7404e-05 | 0
2013-03-02 09:30 | EPG32 | SHORT RURAL |  | 3 | 15 | 45 | 0.00039159 | 2.6106e-05 | 0
2013-03-02 10:30 | EPG32 | SHORT RURAL |  | 2 | 20 | 40 | 0.00034808 | 1.7404e-05 | 0
2013-03-02 11:30 | EPG32 | SHORT RURAL |  | 3 | 20 | 60 | 0.00052212 | 2.6106e-05 | 0
2013-03-02 12:40 | EPG32 | SHORT RURAL |  | 2 | 20 | 40 | 0.00034808 | 1.7404e-05 | 0
2013-03-06 09:00 | PHI11 | SHORT RURAL |  | 73 | 413 | 30149 | 0.26236 | 0.00063524 | 0
2013-03-04 14:31 | KLO24 | SHORT RURAL |  | 1 | 44 | 44 | 0.00038289 | 8.702e-06 | 0
2013-03-06 08:20 | RWT15 | URBAN |  | 496 | 525 | 260400 | 0.9071 | 0.0017278 | 0
2013-03-06 08:50 | MWTS14 | SHORT RURAL |  | 5 | 526 | 2630 | 0.022886 | 4.351e-05 | 0
2013-03-05 13:20 | WGL13 | SHORT RURAL |  | 3 | 80 | 240 | 0.0020885 | 2.6106e-05 | 0
2013-03-06 09:00 | MWTS11 | SHORT RURAL |  | 426 | 420 | 178920 | 1.557 | 0.003707 | 0
2013-03-06 09:12 | WGL23 | SHORT RURAL |  | 82 | 318 | 26076 | 0.22691 | 0.00071356 | 0
2013-03-06 09:15 | WGL23 | SHORT RURAL |  | 3 | 165 | 495 | 0.0043075 | 2.6106e-05 | 0
2013-03-05 09:00 | WGI33 | SHORT RURAL |  | 1055 | 530 | 559150 | 4.8657 | 0.0091806 | 0
2013-03-04 14:00 | WYK11 | SHORT RURAL |  | 3 | 30 | 90 | 0.00078318 | 2.6106e-05 | 0
2013-03-06 09:45 | WGL24 | LONG RURAL |  | 1 | 130 | 130 | 0.0005034 | 3.8723e-06 | 0
2013-03-06 12:18 | WGL24 | LONG RURAL |  | 1 | 117 | 117 | 0.00045306 | 3.8723e-06 | 0
2013-03-07 09:55 | WGL24 | LONG RURAL |  | 2 | 45 | 90 | 0.00034851 | 7.7446e-06 | 0
2013-03-05 09:00 | FTR23 | LONG RURAL |  | 34 | 378 | 12852 | 0.049767 | 0.00013166 | 0
2013-03-05 09:10 | WGL13 | SHORT RURAL |  | 285 | 200 | 57000 | 0.49601 | 0.0024801 | 0
2013-03-05 09:25 | LDL13 | SHORT RURAL |  | 15 | 215 | 3225 | 0.028064 | 0.00013053 | 0
2013-03-05 09:35 | MOE14 | SHORT RURAL |  | 5 | 310 | 1550 | 0.013488 | 4.351e-05 | 0
2013-03-06 11:10 | WYK23 | SHORT RURAL |  | 1 | 60 | 60 | 0.00052212 | 8.702e-06 | 0
2013-03-06 10:05 | WYK23 | SHORT RURAL |  | 2 | 45 | 90 | 0.00078318 | 1.7404e-05 | 0
2013-03-06 09:46 | LDL23 | LONG RURAL |  | 77 | 332 | 25564 | 0.098992 | 0.00029817 | 0
2013-03-06 09:10 | WYK23 | SHORT RURAL |  | 80 | 240 | 19200 | 0.16708 | 0.00069616 | 0
2013-03-06 08:45 | LDL23 | LONG RURAL |  | 11 | 327 | 3597 | 0.013929 | 4.2595e-05 | 0
2013-03-06 09:15 | LGA24 | SHORT RURAL |  | 4 | 130 | 520 | 0.004525 | 3.4808e-05 | 0
2013-03-04 12:00 | WN5 | LONG RURAL |  | 4 | 170 | 680 | 0.0026332 | 1.5489e-05 | 0
2013-03-04 11:40 | WN5 | LONG RURAL |  | 1 | 95 | 95 | 0.00036787 | 3.8723e-06 | 0
2013-03-05 09:35 | WOTS12 | URBAN |  | 2 | 245 | 490 | 0.0017069 | 6.967e-06 | 0
2013-03-05 10:00 | MYT8 | SHORT RURAL |  | 9 | 75 | 675 | 0.0058738 | 7.8318e-05 | 0
2013-03-05 10:35 | MYT8 | SHORT RURAL |  | 4 | 160 | 640 | 0.0055693 | 3.4808e-05 | 0
2013-03-05 09:04 | LLG12 | SHORT RURAL |  | 2 | 138 | 276 | 0.0024017 | 1.7404e-05 | 0
2013-03-05 09:44 | BN1 | LONG RURAL |  | 3 | 266 | 798 | 0.0030901 | 1.1617e-05 | 0
2013-03-06 09:03 | FTR12 | LONG RURAL |  | 6 | 149 | 894 | 0.0034618 | 2.3234e-05 | 0
2013-03-05 11:30 | MYT8 | SHORT RURAL |  | 20 | 75 | 1500 | 0.013053 | 0.00017404 | 0
2013-03-06 11:30 | LGA24 | SHORT RURAL |  | 20 | 338.25 | 6765 | 0.058869 | 0.00017404 | 0
2013-03-05 09:10 | WGL21 | LONG RURAL |  | 332 | 338 | 112216 | 0.43454 | 0.0012856 | 0
2013-03-07 09:05 | LGA11 | LONG RURAL |  | 664 | 11 | 7304 | 0.028283 | 0.0025712 | 0
2013-03-07 09:05 | LGA11 | LONG RURAL |  | 259 | 386 | 99974 | 0.38713 | 0.0010029 | 0
2013-03-05 09:01 | WO32 | URBAN |  | 83 | 299 | 24817 | 0.08645 | 0.00028913 | 0
2013-03-06 09:19 | FTR21 | LONG RURAL |  | 3 | 266 | 798 | 0.0030901 | 1.1617e-05 | 0
2013-03-06 09:00 | TGN11 | SHORT RURAL |  | 4 | 185 | 740 | 0.0064395 | 3.4808e-05 | 0
2013-03-07 09:10 | WGI34 | SHORT RURAL |  | 110 | 3 | 330 | 0.0028717 | 0.00095722 | 0
2013-03-05 09:10 | WOTS11 | LONG RURAL |  | 2 | 300 | 600 | 0.0023234 | 7.7446e-06 | 0
2013-03-06 08:55 | WOTS12 | URBAN |  | 2 | 28 | 56 | 0.00019508 | 6.967e-06 | 0
2013-03-06 11:40 | WOTS12 | URBAN |  | 3 | 182 | 546 | 0.001902 | 1.045e-05 | 0
2013-03-06 09:50 | WOTS12 | URBAN |  | 1 | 70 | 70 | 0.00024384 | 3.4835e-06 | 0
2013-03-07 09:00 | LGA11 | LONG RURAL |  | 3 | 295 | 885 | 0.003427 | 1.1617e-05 | 0
2013-03-07 09:10 | FTR12 | LONG RURAL |  | 147 | 285.8163 | 42015 | 0.1627 | 0.00056923 | 0
2013-03-07 09:25 | LDL23 | LONG RURAL |  | 15 | 327 | 4905 | 0.018994 | 5.8085e-05 | 0
2013-03-05 09:35 | BN1 | LONG RURAL |  | 6 | 310 | 1860 | 0.0072025 | 2.3234e-05 | 0
2013-03-06 08:53 | BN1 | LONG RURAL |  | 1 | 105 | 105 | 0.00040659 | 3.8723e-06 | 0
2013-03-06 13:05 | BN1 | LONG RURAL |  | 7 | 100 | 700 | 0.0027106 | 2.7106e-05 | 0
2013-03-05 13:40 | WGL11 | SHORT RURAL |  | 14 | 105 | 1470 | 0.012792 | 0.00012183 | 0
2013-03-05 10:00 | MOE21 | SHORT RURAL |  | 173 | 40.7803 | 7055 | 0.061392 | 0.0015054 | 0
2013-02-21 10:20 | LYD14 | SHORT RURAL |  | 1 | 88 | 88 | 0.00076577 | 8.702e-06 | 0
2013-02-28 09:05 | MFA23 | SHORT RURAL |  | 1 | 307 | 307 | 0.0026715 | 8.702e-06 | 0
2013-03-01 09:05 | BDL2 | SHORT RURAL |  | 28 | 215 | 6020 | 0.052386 | 0.00024366 | 0
2013-03-01 09:54 | BDL5 | LONG RURAL |  | 8 | 7 | 56 | 0.00021685 | 3.0979e-05 | 0
2013-02-28 08:50 | SLE21 | SHORT RURAL |  | 34 | 200 | 6800 | 0.059173 | 0.00029587 | 0
2013-03-01 10:15 | BDL3 | SHORT RURAL |  | 4 | 125 | 500 | 0.004351 | 3.4808e-05 | 0
2013-03-03 08:34 | SLE32 | SHORT RURAL |  | 163 | 307 | 50041 | 0.43546 | 0.0014184 | 0
2013-02-27 08:36 | OFR21 | SHORT RURAL |  | 2 | 34 | 68 | 0.00059173 | 1.7404e-05 | 0
2013-02-28 09:00 | CLN22 | SHORT RURAL |  | 21 | 105 | 2205 | 0.019188 | 0.00018274 | 0
2013-02-28 11:30 | LLG14 | SHORT RURAL |  | 9 | 28 | 252 | 0.0021929 | 7.8318e-05 | 0
2013-03-02 12:40 | EPG12 | URBAN |  | 315 | 77 | 24255 | 0.084492 | 0.0010973 | 0
2013-03-04 12:05 | SLE31 | LONG RURAL |  | 48 | 170 | 8160 | 0.031598 | 0.00018587 | 0
2013-03-05 09:20 | SMR5 | LONG RURAL |  | 1 | 40 | 40 | 0.00015489 | 3.8723e-06 | 0
2013-03-05 09:05 | SMR5 | LONG RURAL |  | 1 | 60 | 60 | 0.00023234 | 3.8723e-06 | 0
2013-03-05 09:10 | SMR5 | LONG RURAL |  | 1 | 110 | 110 | 0.00042595 | 3.8723e-06 | 0
2013-03-02 14:25 | TT7 | URBAN |  | 1 | 25 | 25 | 8.7087e-05 | 3.4835e-06 | 0
2013-03-05 09:45 | SMR5 | LONG RURAL |  | 1 | 60 | 60 | 0.00023234 | 3.8723e-06 | 0
2013-03-06 12:00 | BN1 | LONG RURAL |  | 1 | 27 | 27 | 0.00010455 | 3.8723e-06 | 0
2013-03-05 09:45 | BDL4 | SHORT RURAL |  | 37 | 395 | 14615 | 0.12718 | 0.00032197 | 0
2013-02-27 08:50 | RWN31 | SHORT RURAL |  | 221 | 169 | 37349 | 0.32501 | 0.0019231 | 0
2013-03-03 13:00 | BDL4 | SHORT RURAL |  | 223 | 397 | 88531 | 0.77039 | 0.0019405 | 0
2013-02-27 10:00 | BWR34 | URBAN |  | 119 | 130 | 15470 | 0.053889 | 0.00041453 | 0
2013-02-27 13:00 | RWT25 | URBAN |  | 149 | 90 | 13410 | 0.046714 | 0.00051904 | 0
2013-03-05 09:00 | KMS1 | SHORT RURAL |  | 130 | 277 | 36010 | 0.31336 | 0.0011313 | 0
2013-02-28 08:40 | BRA14 | URBAN |  | 340 | 430 | 146200 | 0.50929 | 0.0011844 | 0
2013-02-28 08:45 | KLO14 | LONG RURAL |  | 2 | 55 | 110 | 0.00042595 | 7.7446e-06 | 0
2013-03-04 09:00 | SLE31 | LONG RURAL |  | 43 | 165 | 7095 | 0.027474 | 0.00016651 | 0
2013-03-05 13:38 | SLE21 | SHORT RURAL |  | 109 | 68 | 7412 | 0.064499 | 0.00094851 | 0
2013-03-05 11:10 | SMR5 | LONG RURAL |  | 1 | 75 | 75 | 0.00029042 | 3.8723e-06 | 0
2013-03-06 08:40 | SLE21 | SHORT RURAL |  | 4 | 355 | 1420 | 0.012357 | 3.4808e-05 | 0
2013-03-05 14:10 | SMR5 | LONG RURAL |  | 3 | 86.6667 | 260 | 0.0010068 | 1.1617e-05 | 0
2013-03-06 08:30 | BDL3 | SHORT RURAL |  | 10 | 212 | 2120 | 0.018448 | 8.702e-05 | 0
2013-03-05 08:58 | SLE31 | LONG RURAL |  | 2559 | 470 | 1202730 | 4.6573 | 0.0099093 | 0
2013-02-27 09:00 | OFR23 | LONG RURAL |  | 6 | 30 | 180 | 0.00069702 | 2.3234e-05 | 0
2013-03-07 12:25 | NLA32 | SHORT RURAL |  | 35 | 120 | 4200 | 0.036548 | 0.00030457 | 0
2013-03-07 09:00 | BDL6 | SHORT RURAL |  | 11 | 348 | 3828 | 0.033311 | 9.5722e-05 | 0
2013-03-03 09:00 | SMR5 | LONG RURAL |  | 116 | 367 | 42572 | 0.16485 | 0.00044919 | 0
2013-02-20 11:50 | WGL21 | LONG RURAL |  | 3 | 270 | 810 | 0.0031366 | 1.1617e-05 | 0
2013-03-04 14:15 | SMR5 | LONG RURAL |  | 3 | 60 | 180 | 0.00069702 | 1.1617e-05 | 0
2013-03-01 09:30 | CYN22 | URBAN |  | 90 | 210 | 18900 | 0.065838 | 0.00031351 | 0
2013-03-04 09:30 | SMR5 | LONG RURAL |  | 10 | 240 | 2400 | 0.0092936 | 3.8723e-05 | 0
2013-02-28 08:35 | UWY1 | SHORT RURAL |  | 67 | 425 | 28475 | 0.24779 | 0.00058303 | 0
2013-02-28 09:15 | BGE22 | SHORT RURAL |  | 70 | 315 | 22050 | 0.19188 | 0.00060914 | 0
2013-02-28 09:51 | BGE22 | SHORT RURAL |  | 45 | 123 | 5535 | 0.048165 | 0.00039159 | 0
2013-03-03 11:30 | CRE32 | URBAN |  | 96 | 90 | 8640 | 0.030097 | 0.00033441 | 0
2013-03-01 10:58 | BGE22 | SHORT RURAL |  | 165 | 174 | 28710 | 0.24983 | 0.0014358 | 0
2013-03-08 09:30 | TGN31 | LONG RURAL |  | 84 | 100 | 8400 | 0.032527 | 0.00032527 | 0
2013-03-08 09:32 | LGA23 | LONG RURAL |  | 3 | 123 | 369 | 0.0014289 | 1.1617e-05 | 0
2013-03-08 10:06 | WGL11 | SHORT RURAL |  | 248 | 320 | 79360 | 0.69059 | 0.0021581 | 0
2013-03-08 09:17 | LLG12 | SHORT RURAL |  | 20 | 243 | 4860 | 0.042292 | 0.00017404 | 0
2013-03-08 08:15 | WYK11 | SHORT RURAL |  | 8 | 55 | 440 | 0.0038289 | 6.9616e-05 | 0
2013-03-08 08:45 | LDL21 | SHORT RURAL |  | 20 | 240 | 4800 | 0.041769 | 0.00017404 | 0
2013-03-08 08:45 | LDL21 | SHORT RURAL |  | 263 | 240 | 63120 | 0.54927 | 0.0022886 | 0
2013-03-07 15:26 | LDL23 | LONG RURAL |  | 4 | 59 | 236 | 0.00091387 | 1.5489e-05 | 0
2013-03-08 09:25 | WYK23 | SHORT RURAL |  | 158 | 273 | 43134 | 0.37535 | 0.0013749 | 0
2013-03-08 09:20 | FTR12 | LONG RURAL |  | 124 | 168.7742 | 20928 | 0.08104 | 0.00048017 | 0
2013-03-08 08:40 | LDL24 | URBAN |  | 67 | 375 | 25125 | 0.087523 | 0.00023339 | 0
2013-03-08 09:15 | TGN31 | LONG RURAL |  | 2 | 45 | 90 | 0.00034851 | 7.7446e-06 | 0
2013-03-08 10:00 | WYK11 | SHORT RURAL |  | 3 | 65 | 195 | 0.0016969 | 2.6106e-05 | 0
2013-03-08 09:30 | BDL4 | SHORT RURAL |  | 16 | 313 | 5008 | 0.043579 | 0.00013923 | 0
2013-03-07 13:50 | TGN14 | LONG RURAL |  | 30 | 35 | 1050 | 0.0040659 | 0.00011617 | 0
2013-03-07 09:35 | MFA23 | SHORT RURAL |  | 5 | 245 | 1225 | 0.01066 | 4.351e-05 | 0
2013-03-07 09:10 | LGA13 | LONG RURAL |  | 174 | 385 | 66990 | 0.25941 | 0.00067378 | 0
2013-03-07 12:00 | MFA21 | LONG RURAL |  | 5 | 90 | 450 | 0.0017425 | 1.9362e-05 | 0
2013-03-07 09:30 | RWN31 | SHORT RURAL |  | 62 | 375 | 23250 | 0.20232 | 0.00053952 | 0
2013-03-06 08:55 | SLE31 | LONG RURAL |  | 5 | 395 | 1975 | 0.0076478 | 1.9362e-05 | 0
2013-03-07 09:30 | RWN26 | SHORT RURAL |  | 14 | 125 | 1750 | 0.015228 | 0.00012183 | 0
2013-03-07 12:35 | RWN26 | SHORT RURAL |  | 13 | 140 | 1820 | 0.015838 | 0.00011313 | 0
2013-03-05 11:03 | WN5 | LONG RURAL |  | 6 | 37 | 222 | 0.00085965 | 2.3234e-05 | 0
2013-02-28 10:36 | KLO14 | LONG RURAL |  | 3 | 64 | 192 | 0.00074348 | 1.1617e-05 | 0
2013-03-08 09:50 | TGN11 | SHORT RURAL |  | 5 | 185 | 925 | 0.0080493 | 4.351e-05 | 0
2013-03-03 08:30 | HPK23 | URBAN |  | 1 | 142 | 142 | 0.00049465 | 3.4835e-06 | 0
2013-03-01 08:10 | BGE11 | SHORT RURAL |  | 305 | 216.5279 | 66041 | 0.57469 | 0.0026541 | 0
2013-03-04 08:40 | BGE22 | SHORT RURAL |  | 102 | 474 | 48348 | 0.42072 | 0.0008876 | 0
2013-02-27 13:37 | WN5 | LONG RURAL |  | 1 | 38 | 38 | 0.00014715 | 3.8723e-06 | 0
2013-03-05 09:40 | WN5 | LONG RURAL |  | 2 | 170 | 340 | 0.0013166 | 7.7446e-06 | 0
2013-02-21 08:45 | EPG12 | URBAN |  | 92 | 295 | 27140 | 0.094542 | 0.00032048 | 0
2013-03-08 14:00 | WYK11 | SHORT RURAL |  | 1 | 70 | 70 | 0.00060914 | 8.702e-06 | 0
2013-03-08 12:30 | WYK11 | SHORT RURAL |  | 11 | 40 | 440 | 0.0038289 | 9.5722e-05 | 0
2013-03-09 09:12 | FTR23 | LONG RURAL |  | 9 | 443 | 3987 | 0.015439 | 3.4851e-05 | 0
2013-03-08 11:30 | TGN31 | LONG RURAL |  | 1 | 30 | 30 | 0.00011617 | 3.8723e-06 | 0
2013-03-06 14:15 | SMR5 | LONG RURAL |  | 1 | 55 | 55 | 0.00021298 | 3.8723e-06 | 0
2013-02-28 12:45 | SMR5 | LONG RURAL |  | 2 | 30 | 60 | 0.00023234 | 7.7446e-06 | 0
2013-03-03 10:15 | TT6 | URBAN |  | 215 | 225.093 | 48395 | 0.16858 | 0.00074895 | 0
2013-02-28 13:40 | BN1 | LONG RURAL |  | 1 | 80 | 80 | 0.00030979 | 3.8723e-06 | 0
2013-03-06 08:37 | SMR5 | LONG RURAL |  | 1790 | 78.5961 | 140687 | 0.54478 | 0.0069314 | 0
2013-03-05 09:01 | BDL2 | SHORT RURAL |  | 215 | 307.8698 | 66192 | 0.576 | 0.0018709 | 0
2013-03-07 09:19 | ALA01 | LONG RURAL |  | 2 | 211 | 422 | 0.0016341 | 7.7446e-06 | 0
2013-03-02 08:51 | ELM11 | URBAN |  | 3 | 114 | 342 | 0.0011914 | 1.045e-05 | 0
2013-03-07 09:30 | SMR5 | LONG RURAL |  | 1 | 145 | 145 | 0.00056149 | 3.8723e-06 | 0
2013-03-02 09:25 | OFR23 | LONG RURAL |  | 327 | 373.6636 | 122188 | 0.47315 | 0.0012662 | 0
2013-03-07 09:05 | SMR5 | LONG RURAL |  | 2 | 115 | 230 | 0.00089063 | 7.7446e-06 | 0
2013-03-04 09:46 | ELM33 | SHORT RURAL |  | 6 | 59 | 354 | 0.0030805 | 5.2212e-05 | 0
2013-03-04 08:33 | BWN14 | SHORT RURAL |  | 23 | 112 | 2576 | 0.022416 | 0.00020015 | 0
2013-03-07 12:00 | SMR5 | LONG RURAL |  | 32 | 90 | 2880 | 0.011152 | 0.00012391 | 0
2013-03-04 09:25 | OFR23 | LONG RURAL |  | 59 | 425 | 25075 | 0.097098 | 0.00022847 | 0
2013-03-04 08:05 | ELM33 | SHORT RURAL |  | 9 | 300 | 2700 | 0.023495 | 7.8318e-05 | 0
2013-03-09 09:20 | WYK11 | SHORT RURAL |  | 89 | 229 | 20381 | 0.17735 | 0.00077448 | 0
2013-03-07 09:00 | LGA12 | SHORT RURAL |  | 3 | 270 | 810 | 0.0070486 | 2.6106e-05 | 0
2013-03-03 08:30 | RWT15 | URBAN |  | 588 | 272 | 159936 | 0.55713 | 0.0020483 | 0
2013-03-07 09:50 | WN3 | LONG RURAL |  | 39 | 290 | 11310 | 0.043796 | 0.00015102 | 0
2013-03-01 10:45 | KLO14 | LONG RURAL |  | 73 | 225 | 16425 | 0.063603 | 0.00028268 | 0
2013-03-07 13:10 | SMR5 | LONG RURAL |  | 1 | 55 | 55 | 0.00021298 | 3.8723e-06 | 0
2013-03-08 09:00 | KMS1 | SHORT RURAL |  | 39 | 400 | 15600 | 0.13575 | 0.00033938 | 0
2013-03-08 10:05 | SMR5 | LONG RURAL |  | 33 | 175 | 5775 | 0.022363 | 0.00012779 | 0
2013-03-01 09:45 | SMR5 | LONG RURAL |  | 5 | 315 | 1575 | 0.0060989 | 1.9362e-05 | 0
2013-03-06 09:00 | MBY11 | SHORT RURAL |  | 114 | 385 | 43890 | 0.38193 | 0.00099202 | 0
2013-03-05 08:45 | CYN33 | SHORT RURAL |  | 42 | 295 | 12390 | 0.10782 | 0.00036548 | 0
2013-03-06 09:15 | SMR5 | LONG RURAL |  | 53 | 305 | 16165 | 0.062596 | 0.00020523 | 0
2013-03-03 09:10 | WT13 | URBAN |  | 1 | 200 | 200 | 0.0006967 | 3.4835e-06 | 0
2013-03-04 09:25 | TT9 | URBAN |  | 86 | 374 | 32164 | 0.11204 | 0.00029958 | 0
2013-03-06 09:15 | WGL21 | LONG RURAL |  | 2 | 175 | 350 | 0.0013553 | 7.7446e-06 | 0
2013-03-05 08:12 | LYS36 | SHORT RURAL |  | 1 | 533 | 533 | 0.0046382 | 8.702e-06 | 0
2013-03-04 12:10 | ELM33 | SHORT RURAL |  | 3 | 155 | 465 | 0.0040464 | 2.6106e-05 | 0
2013-02-28 08:30 | SFS1 | SHORT RURAL |  | 198 | 453 | 89694 | 0.78051 | 0.001723 | 0
2013-03-04 17:20 | ELM32 | URBAN |  | 20 | 120 | 2400 | 0.0083604 | 6.967e-05 | 0
2013-03-05 08:34 | ELM33 | SHORT RURAL |  | 3 | 171 | 513 | 0.0044641 | 2.6106e-05 | 0
2013-03-05 12:02 | ELM33 | SHORT RURAL |  | 1 | 147 | 147 | 0.0012792 | 8.702e-06 | 0
2013-03-06 09:50 | WOTS11 | LONG RURAL |  | 49 | 250 | 12250 | 0.047436 | 0.00018974 | 0
2013-03-06 08:49 | DRN12 | URBAN |  | 24 | 384 | 9216 | 0.032104 | 8.3604e-05 | 0
2013-03-01 08:45 | BGE12 | SHORT RURAL |  | 49 | 180 | 8820 | 0.076751 | 0.0004264 | 0
2013-03-01 09:05 | BGE12 | SHORT RURAL |  | 105 | 92 | 9660 | 0.084061 | 0.00091371 | 0
2013-03-01 12:20 | BGE12 | SHORT RURAL |  | 3 | 37 | 111 | 0.00096592 | 2.6106e-05 | 0
2013-03-05 08:48 | BGE22 | SHORT RURAL |  | 55 | 319.2364 | 17558 | 0.15279 | 0.00047861 | 0
2013-03-05 08:45 | SFS1 | SHORT RURAL |  | 253 | 644 | 162932 | 1.4178 | 0.0022016 | 0
2013-03-05 09:28 | LYD14 | SHORT RURAL |  | 53 | 226 | 11978 | 0.10423 | 0.0004612 | 0
2013-03-05 08:52 | BGE12 | SHORT RURAL |  | 424 | 174 | 73776 | 0.642 | 0.0036896 | 0
2013-03-06 13:00 | ELM33 | SHORT RURAL |  | 2 | 95 | 190 | 0.0016534 | 1.7404e-05 | 0
2013-03-04 09:27 | CYN12 | URBAN |  | 79 | 13 | 1027 | 0.0035775 | 0.0002752 | 0
2013-02-28 09:02 | KMS21 | SHORT RURAL |  | 94 | 353 | 33182 | 0.28875 | 0.00081799 | 0
2013-03-07 09:25 | ELM33 | SHORT RURAL |  | 2 | 65 | 130 | 0.0011313 | 1.7404e-05 | 0
2013-03-05 09:58 | PHM31 | SHORT RURAL |  | 2 | 142 | 284 | 0.0024714 | 1.7404e-05 | 0
2013-03-07 12:05 | ELM33 | SHORT RURAL |  | 11 | 95 | 1045 | 0.0090936 | 9.5722e-05 | 0
2013-03-08 09:30 | DRN14 | SHORT RURAL |  | 3 | 120 | 360 | 0.0031327 | 2.6106e-05 | 0
2013-03-07 11:20 | WOTS12 | URBAN |  | 4 | 60 | 240 | 0.00083604 | 1.3934e-05 | 0
2013-03-07 08:30 | WOTS12 | URBAN |  | 4 | 160 | 640 | 0.0022294 | 1.3934e-05 | 0
2013-03-07 09:20 | BN1 | LONG RURAL |  | 59 | 175 | 10325 | 0.039982 | 0.00022847 | 0
2013-03-07 08:31 | WN5 | LONG RURAL |  | 170 | 377 | 64090 | 0.24818 | 0.00065829 | 0
2013-03-05 11:40 | LLG14 | SHORT RURAL |  | 2 | 35 | 70 | 0.00060914 | 1.7404e-05 | 0
2013-03-08 09:00 | WN5 | LONG RURAL |  | 2 | 90 | 180 | 0.00069702 | 7.7446e-06 | 0
2013-03-08 09:20 | BN3 | SHORT RURAL |  | 35 | 130 | 4550 | 0.039594 | 0.00030457 | 0
2013-03-08 10:20 | WO32 | URBAN |  | 63 | 188 | 11844 | 0.041258 | 0.00021946 | 0
2013-03-07 09:15 | PHM32 | URBAN |  | 565 | 340 | 192100 | 0.66918 | 0.0019682 | 0
2013-03-08 10:55 | WN5 | LONG RURAL |  | 5 | 40 | 200 | 0.00077446 | 1.9362e-05 | 0
2013-03-08 09:21 | PHM14 | LONG RURAL |  | 225 | 337 | 75825 | 0.29362 | 0.00087127 | 0
2013-03-08 12:33 | WGL12 | LONG RURAL |  | 3 | 19 | 57 | 0.00022072 | 1.1617e-05 | 0
2013-03-10 08:35 | CLN23 | SHORT RURAL |  | 637 | 524.741 | 334260 | 2.9087 | 0.0055432 | 0
2013-03-06 08:55 | BGE11 | SHORT RURAL |  | 41 | 350 | 14350 | 0.12487 | 0.00035678 | 0
2013-03-06 09:20 | FGY12 | URBAN |  | 69 | 64 | 4416 | 0.015383 | 0.00024036 | 0
2013-02-23 08:10 | WT9 | URBAN |  | 77 | 40 | 3080 | 0.010729 | 0.00026823 | 0
2013-03-12 11:00 | LLG13 | SHORT RURAL |  | 30 | 70 | 2100 | 0.018274 | 0.00026106 | 0
2013-03-14 09:00 | LGA24 | SHORT RURAL |  | 1 | 75 | 75 | 0.00065265 | 8.702e-06 | 0
2013-03-14 10:00 | WGL12 | LONG RURAL |  | 423 | 330 | 139590 | 0.54054 | 0.001638 | 0
2013-03-14 08:35 | TGN23 | SHORT RURAL |  | 19 | 477 | 9063 | 0.078866 | 0.00016534 | 0
2013-03-12 09:35 | FTR21 | LONG RURAL |  | 2 | 50 | 100 | 0.00038723 | 7.7446e-06 | 0
2013-03-12 13:25 | WYK23 | SHORT RURAL |  | 3 | 30 | 90 | 0.00078318 | 2.6106e-05 | 0
2013-03-12 11:54 | WYK23 | SHORT RURAL |  | 1 | 37 | 37 | 0.00032197 | 8.702e-06 | 0
2013-03-12 11:00 | WYK23 | SHORT RURAL |  | 2 | 37 | 74 | 0.00064395 | 1.7404e-05 | 0
2013-03-12 09:30 | WYK23 | SHORT RURAL |  | 1 | 54 | 54 | 0.00046991 | 8.702e-06 | 0
2013-03-13 12:15 | WYK23 | SHORT RURAL |  | 4 | 36 | 144 | 0.0012531 | 3.4808e-05 | 0
2013-03-13 08:35 | KLK1 | SHORT RURAL |  | 75 | 263 | 19725 | 0.17165 | 0.00065265 | 0
2013-03-13 09:50 | WYK23 | SHORT RURAL |  | 11 | 110 | 1210 | 0.010529 | 9.5722e-05 | 0
2013-03-12 09:10 | BDL2 | SHORT RURAL |  | 78 | 190 | 14820 | 0.12896 | 0.00067875 | 0
2013-03-13 09:00 | BDL2 | SHORT RURAL |  | 68 | 110 | 7480 | 0.065091 | 0.00059173 | 0
2013-03-12 10:35 | FTR21 | LONG RURAL |  | 2 | 50 | 100 | 0.00038723 | 7.7446e-06 | 0
2013-03-13 09:05 | TGN31 | LONG RURAL |  | 1 | 25 | 25 | 9.6808e-05 | 3.8723e-06 | 0
2013-03-13 08:57 | FTR12 | LONG RURAL |  | 67 | 441 | 29547 | 0.11442 | 0.00025945 | 0
2013-03-14 10:00 | YN31 | URBAN |  | 1 | 178 | 178 | 0.00062006 | 3.4835e-06 | 0
2013-03-13 13:10 | BDL2 | SHORT RURAL |  | 51 | 70 | 3570 | 0.031066 | 0.0004438 | 0
2013-03-13 08:30 | BDL1 | LONG RURAL |  | 1 | 30 | 30 | 0.00011617 | 3.8723e-06 | 0
2013-03-13 10:00 | BDL1 | LONG RURAL |  | 2 | 170 | 340 | 0.0013166 | 7.7446e-06 | 0
2013-03-13 09:15 | LLG12 | SHORT RURAL |  | 30 | 240 | 7200 | 0.062654 | 0.00026106 | 0
2013-03-13 09:55 | FTR23 | LONG RURAL |  | 9 | 305 | 2745 | 0.01063 | 3.4851e-05 | 0
2013-03-12 09:20 | WGL24 | LONG RURAL |  | 1 | 12 | 12 | 4.6468e-05 | 3.8723e-06 | 0
2013-03-13 09:40 | LGA24 | SHORT RURAL |  | 253 | 340 | 86020 | 0.74854 | 0.0022016 | 0
2013-03-14 09:05 | WGL11 | SHORT RURAL |  | 1 | 115 | 115 | 0.0010007 | 8.702e-06 | 0
2013-03-14 08:30 | WYK11 | SHORT RURAL |  | 89 | 240 | 21360 | 0.18587 | 0.00077448 | 0
2013-03-13 11:40 | FTR21 | LONG RURAL |  | 2 | 215 | 430 | 0.0016651 | 7.7446e-06 | 0
2013-03-14 09:00 | WYK11 | SHORT RURAL |  | 64 | 360 | 23040 | 0.20049 | 0.00055693 | 0
2013-03-14 08:30 | LDL23 | LONG RURAL |  | 51 | 350 | 17850 | 0.069121 | 0.00019749 | 0
2013-03-14 08:30 | WYK12 | SHORT RURAL |  | 39 | 370 | 14430 | 0.12557 | 0.00033938 | 0
2013-03-12 09:20 | WGL24 | LONG RURAL |  | 15 | 175 | 2625 | 0.010165 | 5.8085e-05 | 0
2013-03-14 09:05 | MWTS31 | SHORT RURAL |  | 5 | 60 | 300 | 0.0026106 | 4.351e-05 | 0
2013-03-14 11:15 | YN31 | URBAN |  | 13 | 32 | 416 | 0.0014491 | 4.5285e-05 | 0
2013-03-14 09:05 | MOE32 | SHORT RURAL |  | 3 | 35 | 105 | 0.00091371 | 2.6106e-05 | 0
2013-03-14 10:40 | WGL13 | SHORT RURAL |  | 2 | 120 | 240 | 0.0020885 | 1.7404e-05 | 0
2013-03-14 12:55 | WGL13 | SHORT RURAL |  | 1 | 90 | 90 | 0.00078318 | 8.702e-06 | 0
2013-03-13 09:13 | LGA23 | LONG RURAL |  | 84 | 731 | 61404 | 0.23778 | 0.00032527 | 0
2013-03-12 09:20 | WOTS11 | LONG RURAL |  | 3 | 40 | 120 | 0.00046468 | 1.1617e-05 | 0
2013-03-12 09:00 | BWN13 | URBAN |  | 118 | 195 | 23010 | 0.080155 | 0.00041105 | 0
2013-03-08 08:45 | BWN14 | SHORT RURAL |  | 11 | 177 | 1947 | 0.016943 | 9.5722e-05 | 0
2013-03-06 09:20 | BDL5 | LONG RURAL |  | 197 | 366 | 72102 | 0.2792 | 0.00076285 | 0
2013-03-12 13:10 | WGI22 | LONG RURAL |  | 1 | 65 | 65 | 0.0002517 | 3.8723e-06 | 0
2013-03-08 09:50 | KLO14 | LONG RURAL |  | 19 | 135 | 2565 | 0.0099325 | 7.3574e-05 | 0
2013-03-05 08:13 | CYN14 | URBAN |  | 202 | 334 | 67468 | 0.23502 | 0.00070366 | 0
2013-03-08 09:30 | MFA21 | LONG RURAL |  | 1 | 340 | 340 | 0.0013166 | 3.8723e-06 | 0
2013-03-08 14:00 | DRN11 | URBAN |  | 94 | 90 | 8460 | 0.02947 | 0.00032745 | 0
2013-03-08 09:30 | SLE31 | LONG RURAL |  | 2 | 275 | 550 | 0.0021298 | 7.7446e-06 | 0
2013-03-13 10:15 | LGA22 | SHORT RURAL |  | 373 | 235 | 87655 | 0.76277 | 0.0032458 | 0
2013-03-13 10:23 | LGA23 | LONG RURAL |  | 272 | 231 | 62832 | 0.24331 | 0.0010533 | 0
2013-03-12 09:55 | KLO24 | SHORT RURAL |  | 15 | 170 | 2550 | 0.02219 | 0.00013053 | 0
2013-03-08 09:31 | BDL5 | LONG RURAL |  | 328 | 102 | 33456 | 0.12955 | 0.0012701 | 0
2013-03-05 09:20 | BWR32 | URBAN |  | 46 | 265 | 12190 | 0.042464 | 0.00016024 | 0
2013-03-12 09:40 | MBY11 | SHORT RURAL |  | 9 | 160 | 1440 | 0.012531 | 7.8318e-05 | 0
2013-03-12 10:45 | WOTS11 | LONG RURAL |  | 1 | 85 | 85 | 0.00032915 | 3.8723e-06 | 0
2013-03-04 08:45 | OFR23 | LONG RURAL |  | 1 | 85 | 85 | 0.00032915 | 3.8723e-06 | 0
2013-03-07 09:15 | BRA14 | URBAN |  | 386 | 343 | 132398 | 0.46121 | 0.0013446 | 0
2013-03-10 09:00 | BDL3 | SHORT RURAL |  | 22 | 375 | 8250 | 0.071791 | 0.00019144 | 0
2013-03-04 11:00 | OFR23 | LONG RURAL |  | 1 | 90 | 90 | 0.00034851 | 3.8723e-06 | 0
2013-03-13 09:01 | MBY11 | SHORT RURAL |  | 241 | 193.3527 | 46598 | 0.40549 | 0.0020972 | 0
2013-03-05 09:40 | BGE12 | SHORT RURAL |  | 28 | 84 | 2352 | 0.020467 | 0.00024366 | 0
2013-03-05 13:00 | BGE12 | SHORT RURAL |  | 1 | 72 | 72 | 0.00062654 | 8.702e-06 | 0
2013-03-07 08:34 | NRN12 | URBAN |  | 80 | 486 | 38880 | 0.13544 | 0.00027868 | 0
2013-03-12 11:37 | WT13 | URBAN |  | 360 | 160 | 57600 | 0.20065 | 0.0012541 | 0
2013-03-08 12:20 | DRN11 | URBAN |  | 14 | 140 | 1960 | 0.0068276 | 4.8769e-05 | 0
2013-03-04 10:30 | WYK11 | SHORT RURAL |  | 40 | 43 | 1720 | 0.014967 | 0.00034808 | 0
2013-03-13 09:30 | DRN11 | URBAN |  | 4 | 70 | 280 | 0.00097538 | 1.3934e-05 | 0
2013-03-13 09:25 | DRN11 | URBAN |  | 71 | 245 | 17395 | 0.060595 | 0.00024733 | 0
2013-03-08 09:30 | BGE22 | SHORT RURAL |  | 12 | 303 | 3636 | 0.03164 | 0.00010442 | 0
2013-03-08 08:20 | BGE22 | SHORT RURAL |  | 38 | 130 | 4940 | 0.042988 | 0.00033067 | 0
2013-03-09 09:14 | BGE22 | SHORT RURAL |  | 163 | 226 | 36838 | 0.32056 | 0.0014184 | 0
2013-03-13 09:25 | BWN14 | SHORT RURAL |  | 72 | 295 | 21240 | 0.18483 | 0.00062654 | 0
2013-03-15 09:25 | PHI12 | SHORT RURAL |  | 93 | 101 | 9393 | 0.081738 | 0.00080928 | 0
2013-03-15 09:02 | WGL23 | SHORT RURAL |  | 83 | 343 | 28469 | 0.24774 | 0.00072226 | 0
2013-03-14 11:50 | BN3 | SHORT RURAL |  | 5 | 85 | 425 | 0.0036983 | 4.351e-05 | 0
2013-03-14 12:40 | LGA24 | SHORT RURAL |  | 6 | 35 | 210 | 0.0018274 | 5.2212e-05 | 0
2013-03-15 09:00 | LGA23 | LONG RURAL |  | 79 | 293 | 23147 | 0.089632 | 0.00030591 | 0
2013-03-15 08:50 | KLK2 | SHORT RURAL |  | 4 | 235 | 940 | 0.0081799 | 3.4808e-05 | 0
2013-03-14 12:10 | WGL11 | SHORT RURAL |  | 47 | 180 | 8460 | 0.073619 | 0.00040899 | 0
2013-03-15 09:00 | WGL23 | SHORT RURAL |  | 1 | 395 | 395 | 0.0034373 | 8.702e-06 | 0
2013-03-15 09:15 | WGL13 | SHORT RURAL |  | 2 | 85 | 170 | 0.0014793 | 1.7404e-05 | 0
2013-03-15 10:55 | WGL13 | SHORT RURAL |  | 1 | 60 | 60 | 0.00052212 | 8.702e-06 | 0
2013-03-15 09:00 | WGL11 | SHORT RURAL |  | 65 | 50 | 3250 | 0.028281 | 0.00056563 | 0
2013-03-08 09:08 | BWR34 | URBAN |  | 113 | 287 | 32431 | 0.11297 | 0.00039363 | 0
2013-03-08 10:38 | BWR23 | URBAN |  | 80 | 261 | 20880 | 0.072735 | 0.00027868 | 0
2013-03-15 08:55 | LGA14 | LONG RURAL |  | 1 | 305 | 305 | 0.0011811 | 3.8723e-06 | 0
2013-03-13 11:10 | DRN11 | URBAN |  | 1 | 60 | 60 | 0.00020901 | 3.4835e-06 | 0
2013-03-13 13:10 | DRN11 | URBAN |  | 8 | 110 | 880 | 0.0030655 | 2.7868e-05 | 0
2013-03-14 09:35 | DRN11 | URBAN |  | 1 | 85 | 85 | 0.0002961 | 3.4835e-06 | 0
2013-03-14 11:10 | DRN11 | URBAN |  | 6 | 155 | 930 | 0.0032396 | 2.0901e-05 | 0
2013-03-14 09:15 | LLG12 | SHORT RURAL |  | 4 | 115 | 460 | 0.0040029 | 3.4808e-05 | 0
2013-03-15 09:06 | LLG12 | SHORT RURAL |  | 52 | 242 | 12584 | 0.10951 | 0.0004525 | 0
2013-03-14 12:05 | DRN11 | URBAN |  | 2 | 70 | 140 | 0.00048769 | 6.967e-06 | 0
2013-03-13 09:30 | TT9 | URBAN |  | 66 | 365 | 24090 | 0.083917 | 0.00022991 | 0
2013-03-12 12:50 | WOTS11 | LONG RURAL |  | 2 | 70 | 140 | 0.00054212 | 7.7446e-06 | 0
2013-03-13 10:15 | ELM15 | SHORT RURAL |  | 115 | 65 | 7475 | 0.065047 | 0.0010007 | 0
2013-03-06 09:30 | WYK24 | SHORT RURAL |  | 1 | 149 | 149 | 0.0012966 | 8.702e-06 | 0
2013-03-13 10:15 | WOTS13 | LONG RURAL |  | 3 | 300 | 900 | 0.0034851 | 1.1617e-05 | 0
2013-03-12 09:00 | SMR5 | LONG RURAL |  | 6 | 373 | 2238 | 0.0086662 | 2.3234e-05 | 0
2013-03-14 13:30 | DRN11 | URBAN |  | 1 | 45 | 45 | 0.00015676 | 3.4835e-06 | 0
2013-03-14 09:40 | NLA34 | SHORT RURAL |  | 18 | 410 | 7380 | 0.064221 | 0.00015664 | 0
2013-03-12 09:15 | SMR5 | LONG RURAL |  | 12 | 145 | 1740 | 0.0067378 | 4.6468e-05 | 0
2013-03-15 08:35 | DRN11 | URBAN |  | 1 | 55 | 55 | 0.00019159 | 3.4835e-06 | 0
2013-03-10 08:30 | MWTS32 | SHORT RURAL |  | 4 | 294 | 1176 | 0.010234 | 3.4808e-05 | 0
2013-03-15 09:50 | PHI12 | SHORT RURAL |  | 59 | 152 | 8968 | 0.078039 | 0.00051342 | 0
2013-03-07 08:45 | BGE22 | SHORT RURAL |  | 10 | 300 | 3000 | 0.026106 | 8.702e-05 | 0
2013-03-12 13:40 | SMR5 | LONG RURAL |  | 3 | 97 | 291 | 0.0011268 | 1.1617e-05 | 0
2013-03-13 09:00 | WOTS11 | LONG RURAL |  | 49 | 390 | 19110 | 0.074 | 0.00018974 | 0
2013-03-14 12:44 | ELM13 | URBAN |  | 115 | 128 | 14720 | 0.051277 | 0.0004006 | 0
2013-03-12 08:35 | LYD14 | SHORT RURAL |  | 58 | 148 | 8584 | 0.074698 | 0.00050471 | 0
2013-03-13 09:20 | BRA14 | URBAN |  | 97 | 250 | 24250 | 0.084474 | 0.0003379 | 0
2013-03-08 12:35 | WGI31 | SHORT RURAL |  | 47 | 85 | 3995 | 0.034764 | 0.00040899 | 0
2013-03-12 10:00 | CYN24 | URBAN |  | 99 | 130 | 12870 | 0.044832 | 0.00034486 | 0
2013-03-12 09:30 | RWN32 | URBAN |  | 82 | 140 | 11480 | 0.03999 | 0.00028565 | 0
2013-03-15 10:00 | NLA34 | SHORT RURAL |  | 3 | 354 | 1062 | 0.0092415 | 2.6106e-05 | 0
2013-03-12 12:50 | CYN32 | URBAN |  | 81 | 120 | 9720 | 0.033859 | 0.00028216 | 0
2013-03-12 15:30 | RWN32 | URBAN |  | 36 | 80 | 2880 | 0.010032 | 0.00012541 | 0
2013-03-13 08:55 | CYN31 | URBAN |  | 75 | 355 | 26625 | 0.092748 | 0.00026126 | 0
2013-03-12 09:20 | WN2 | LONG RURAL |  | 6 | 15 | 90 | 0.00034851 | 2.3234e-05 | 0
2013-03-12 09:07 | WN5 | LONG RURAL |  | 10 | 323 | 3230 | 0.012508 | 3.8723e-05 | 0
2013-03-14 09:58 | EPG11 | URBAN |  | 594 | 243.1987 | 144460 | 0.50322 | 0.0020692 | 0
2013-03-13 09:30 | BWR32 | URBAN |  | 139 | 165 | 22935 | 0.079894 | 0.0004842 | 0
2013-03-15 11:50 | PHI12 | SHORT RURAL |  | 1 | 62 | 62 | 0.00053952 | 8.702e-06 | 0
2013-03-16 08:30 | WYK11 | SHORT RURAL |  | 66 | 260 | 17160 | 0.14933 | 0.00057433 | 0
2013-03-15 12:15 | BDL3 | SHORT RURAL |  | 4 | 165 | 660 | 0.0057433 | 3.4808e-05 | 0
2013-03-16 08:20 | KLK1 | SHORT RURAL |  | 70 | 190 | 13300 | 0.11574 | 0.00060914 | 0
2013-03-13 09:07 | SMR3 | LONG RURAL |  | 191 | 370 | 70670 | 0.27366 | 0.00073961 | 0
2013-03-06 09:00 | SMR5 | LONG RURAL |  | 4 | 326 | 1304 | 0.0050495 | 1.5489e-05 | 0
2013-03-13 09:14 | SMR5 | LONG RURAL |  | 51 | 349 | 17799 | 0.068923 | 0.00019749 | 0
2013-03-15 09:30 | DRN11 | URBAN |  | 2 | 130 | 260 | 0.00090571 | 6.967e-06 | 0
2013-03-15 09:40 | DRN11 | URBAN |  | 2 | 100 | 200 | 0.0006967 | 6.967e-06 | 0
2013-03-14 09:05 | SMR5 | LONG RURAL |  | 5 | 130 | 650 | 0.002517 | 1.9362e-05 | 0
2013-03-14 09:05 | SMR5 | LONG RURAL |  | 1 | 36 | 36 | 0.0001394 | 3.8723e-06 | 0
2013-03-12 09:35 | LGA13 | LONG RURAL |  | 8 | 385 | 3080 | 0.011927 | 3.0979e-05 | 0
2013-03-15 09:10 | DRN11 | URBAN |  | 1 | 40 | 40 | 0.00013934 | 3.4835e-06 | 0
2013-03-14 10:10 | KLO24 | SHORT RURAL |  | 92 | 403 | 37076 | 0.32263 | 0.00080058 | 0
2013-03-15 12:05 | DRN11 | URBAN |  | 1 | 115 | 115 | 0.0004006 | 3.4835e-06 | 0
2013-03-15 11:30 | DRN11 | URBAN |  | 3 | 45 | 135 | 0.00047027 | 1.045e-05 | 0
2013-03-15 12:40 | DRN11 | URBAN |  | 1 | 170 | 170 | 0.00059219 | 3.4835e-06 | 0
2013-03-15 10:01 | DRN11 | URBAN |  | 560 | 163 | 91280 | 0.31797 | 0.0019508 | 0
2013-03-14 11:00 | SMR5 | LONG RURAL |  | 1 | 42 | 42 | 0.00016264 | 3.8723e-06 | 0
2013-03-14 13:03 | SMR5 | LONG RURAL |  | 1 | 45 | 45 | 0.00017425 | 3.8723e-06 | 0
2013-03-13 09:21 | WN5 | LONG RURAL |  | 1 | 181 | 181 | 0.00070089 | 3.8723e-06 | 0
2013-03-15 08:55 | ELM34 | URBAN |  | 313 | 138 | 43194 | 0.15047 | 0.0010903 | 0
2013-03-15 10:00 | DRN11 | URBAN |  | 1 | 50 | 50 | 0.00017417 | 3.4835e-06 | 0
2013-03-08 08:30 | OFR23 | LONG RURAL |  | 50 | 100 | 5000 | 0.019362 | 0.00019362 | 0
2013-03-13 09:00 | CRE33 | SHORT RURAL |  | 6 | 330 | 1980 | 0.01723 | 5.2212e-05 | 0
2013-03-17 09:00 | WYK11 | SHORT RURAL |  | 15 | 234 | 3510 | 0.030544 | 0.00013053 | 0
2013-03-17 10:22 | LLG13 | SHORT RURAL |  | 41 | 240 | 9840 | 0.085627 | 0.00035678 | 0
2013-03-17 08:47 | SLE31 | LONG RURAL |  | 845 | 165.2095 | 139602 | 0.54058 | 0.0032721 | 0
2013-03-15 13:10 | DRN14 | SHORT RURAL |  | 1 | 40 | 40 | 0.00034808 | 8.702e-06 | 0
2013-03-15 10:40 | DRN14 | SHORT RURAL |  | 1 | 70 | 70 | 0.00060914 | 8.702e-06 | 0
2013-03-15 09:30 | DRN11 | URBAN |  | 2 | 125 | 250 | 0.00087087 | 6.967e-06 | 0
2013-03-15 11:50 | ELM13 | URBAN |  | 100 | 45 | 4500 | 0.015676 | 0.00034835 | 0
2013-03-12 09:10 | WYK11 | SHORT RURAL |  | 2 | 90 | 180 | 0.0015664 | 1.7404e-05 | 0
2013-03-13 09:05 | WYK11 | SHORT RURAL |  | 2 | 140 | 280 | 0.0024366 | 1.7404e-05 | 0
2013-03-13 09:45 | WYK11 | SHORT RURAL |  | 5 | 120 | 600 | 0.0052212 | 4.351e-05 | 0
2013-03-13 12:20 | WYK11 | SHORT RURAL |  | 1 | 55 | 55 | 0.00047861 | 8.702e-06 | 0
2013-03-13 12:00 | WYK11 | SHORT RURAL |  | 27 | 105 | 2835 | 0.02467 | 0.00023495 | 0
2013-03-17 09:35 | ELM33 | SHORT RURAL |  | 124 | 135 | 16740 | 0.14567 | 0.001079 | 0
2013-03-14 09:10 | MFA34 | SHORT RURAL |  | 21 | 335 | 7035 | 0.061218 | 0.00018274 | 0
2013-03-16 09:03 | BN1 | LONG RURAL |  | 31 | 185 | 5735 | 0.022208 | 0.00012004 | 0
2013-03-13 10:47 | WN5 | LONG RURAL |  | 2 | 99 | 198 | 0.00076672 | 7.7446e-06 | 0
2013-03-13 08:35 | BGE12 | SHORT RURAL |  | 19 | 91 | 1729 | 0.015046 | 0.00016534 | 0
2013-03-13 14:35 | BGE12 | SHORT RURAL |  | 6 | 15 | 90 | 0.00078318 | 5.2212e-05 | 0
2013-03-13 14:10 | BGE12 | SHORT RURAL |  | 6 | 11 | 66 | 0.00057433 | 5.2212e-05 | 0
2013-03-14 11:15 | HPK13 | URBAN |  | 33 | 170 | 5610 | 0.019542 | 0.00011495 | 0
2013-03-14 11:15 | HPK24 | URBAN |  | 90 | 170 | 15300 | 0.053297 | 0.00031351 | 0
2013-03-14 11:00 | BN6 | LONG RURAL |  | 2 | 55 | 110 | 0.00042595 | 7.7446e-06 | 0
2013-03-17 09:02 | BN2 | LONG RURAL |  | 193 | 234 | 45162 | 0.17488 | 0.00074736 | 0
2013-03-18 09:10 | TGN12 | SHORT RURAL |  | 41 | 310 | 12710 | 0.1106 | 0.00035678 | 0
2013-03-18 08:25 | WYK11 | SHORT RURAL |  | 9 | 60 | 540 | 0.0046991 | 7.8318e-05 | 0
2013-03-18 09:55 | WGL13 | SHORT RURAL |  | 2 | 160 | 320 | 0.0027846 | 1.7404e-05 | 0
2013-03-18 10:00 | WYK11 | SHORT RURAL |  | 1 | 75 | 75 | 0.00065265 | 8.702e-06 | 0
2013-03-18 09:38 | FTR23 | LONG RURAL |  | 12 | 160 | 1920 | 0.0074348 | 4.6468e-05 | 0
2013-03-18 09:05 | WGI34 | SHORT RURAL |  | 1 | 120 | 120 | 0.0010442 | 8.702e-06 | 0
2013-03-18 09:48 | LGA23 | LONG RURAL |  | 7 | 262 | 1834 | 0.0071018 | 2.7106e-05 | 0
2013-03-18 10:15 | RWN32 | URBAN |  | 79 | 165 | 13035 | 0.045407 | 0.0002752 | 0
2013-03-18 09:05 | KLK1 | SHORT RURAL |  | 11 | 200 | 2200 | 0.019144 | 9.5722e-05 | 0
2013-03-14 08:35 | WOTS11 | LONG RURAL |  | 82 | 300 | 24600 | 0.095259 | 0.00031753 | 0
2013-03-15 09:20 | SMR5 | LONG RURAL |  | 25 | 120 | 3000 | 0.011617 | 9.6808e-05 | 0
2013-03-15 11:20 | SMR8 | LONG RURAL |  | 1 | 135 | 135 | 0.00052276 | 3.8723e-06 | 0
2013-03-14 09:00 | MBY11 | SHORT RURAL |  | 11 | 190 | 2090 | 0.018187 | 9.5722e-05 | 0
2013-03-18 10:00 | LGA13 | LONG RURAL |  | 6 | 185 | 1110 | 0.0042983 | 2.3234e-05 | 0
2013-03-15 09:12 | SMR5 | LONG RURAL |  | 2 | 18 | 36 | 0.0001394 | 7.7446e-06 | 0
2013-03-18 09:05 | KLK1 | SHORT RURAL |  | 7 | 235 | 1645 | 0.014315 | 6.0914e-05 | 0
2013-03-15 09:25 | SMR5 | LONG RURAL |  | 1 | 40 | 40 | 0.00015489 | 3.8723e-06 | 0
2013-03-15 09:50 | SMR5 | LONG RURAL |  | 1 | 80 | 80 | 0.00030979 | 3.8723e-06 | 0
2013-03-14 09:31 | WOTS11 | LONG RURAL |  | 60 | 334 | 20040 | 0.077601 | 0.00023234 | 0
2013-03-14 09:40 | WOTS11 | LONG RURAL |  | 35 | 55 | 1925 | 0.0074542 | 0.00013553 | 0
2013-03-13 10:20 | CRE21 | SHORT RURAL |  | 1 | 415 | 415 | 0.0036113 | 8.702e-06 | 0
2013-03-13 09:38 | CLN21 | SHORT RURAL |  | 2 | 237 | 474 | 0.0041247 | 1.7404e-05 | 0
2013-03-14 08:50 | CRE31 | URBAN |  | 61 | 81 | 4941 | 0.017212 | 0.00021249 | 0
2013-03-15 12:40 | SMR5 | LONG RURAL |  | 1 | 60 | 60 | 0.00023234 | 3.8723e-06 | 0
2013-03-15 11:09 | SMR5 | LONG RURAL |  | 1 | 51 | 51 | 0.00019749 | 3.8723e-06 | 0
2013-03-17 07:32 | BGE12 | SHORT RURAL |  | 420 | 148 | 62160 | 0.54091 | 0.0036548 | 0
2013-03-14 11:05 | WOTS11 | LONG RURAL |  | 24 | 115 | 2760 | 0.010688 | 9.2936e-05 | 0
2013-03-15 09:40 | WOTS11 | LONG RURAL |  | 2 | 140 | 280 | 0.0010842 | 7.7446e-06 | 0
2013-03-15 09:32 | MBY12 | SHORT RURAL |  | 125 | 133 | 16625 | 0.14467 | 0.0010877 | 0
2013-03-12 13:35 | MBY11 | SHORT RURAL |  | 1 | 80 | 80 | 0.00069616 | 8.702e-06 | 0
2013-03-18 08:55 | FGY34 | URBAN |  | 83 | 115 | 9545 | 0.03325 | 0.00028913 | 0
2013-03-15 09:30 | MBY12 | SHORT RURAL |  | 70 | 320 | 22400 | 0.19492 | 0.00060914 | 0
2013-03-15 09:45 | MYT7 | LONG RURAL |  | 48 | 135 | 6480 | 0.025093 | 0.00018587 | 0
2013-03-15 11:20 | SMR5 | LONG RURAL |  | 1 | 50 | 50 | 0.00019362 | 3.8723e-06 | 0
2013-03-15 10:08 | MYT7 | LONG RURAL |  | 59 | 207 | 12213 | 0.047293 | 0.00022847 | 0
2013-03-18 08:40 | LYD14 | SHORT RURAL |  | 4 | 140 | 560 | 0.0048731 | 3.4808e-05 | 0
2013-03-15 12:45 | SMR5 | LONG RURAL |  | 1 | 40 | 40 | 0.00015489 | 3.8723e-06 | 0
2013-03-15 13:25 | MBY12 | SHORT RURAL |  | 3 | 50 | 150 | 0.0013053 | 2.6106e-05 | 0
2013-03-15 13:25 | SMR5 | LONG RURAL |  | 2 | 45 | 90 | 0.00034851 | 7.7446e-06 | 0
2013-03-15 10:10 | SMR8 | LONG RURAL |  | 2 | 40 | 80 | 0.00030979 | 7.7446e-06 | 0
2013-03-14 09:45 | SMR5 | LONG RURAL |  | 3 | 120 | 360 | 0.001394 | 1.1617e-05 | 0
2013-03-15 13:47 | SMR8 | LONG RURAL |  | 1 | 51 | 51 | 0.00019749 | 3.8723e-06 | 0
2013-03-19 09:30 | MOE32 | SHORT RURAL |  | 2 | 102 | 204 | 0.0017752 | 1.7404e-05 | 0
2013-03-19 09:15 | MWTS14 | SHORT RURAL |  | 5 | 485 | 2425 | 0.021102 | 4.351e-05 | 0
2013-03-18 14:05 | WYK11 | SHORT RURAL |  | 5 | 75 | 375 | 0.0032632 | 4.351e-05 | 0
2013-03-18 12:30 | WYK11 | SHORT RURAL |  | 9 | 90 | 810 | 0.0070486 | 7.8318e-05 | 0
2013-03-19 08:05 | WYK11 | SHORT RURAL |  | 3 | 61 | 183 | 0.0015925 | 2.6106e-05 | 0
2013-03-19 14:05 | WYK11 | SHORT RURAL |  | 17 | 55 | 935 | 0.0081363 | 0.00014793 | 0
2013-03-19 12:30 | WYK11 | SHORT RURAL |  | 6 | 65 | 390 | 0.0033938 | 5.2212e-05 | 0
2013-03-19 10:00 | WYK11 | SHORT RURAL |  | 1 | 50 | 50 | 0.0004351 | 8.702e-06 | 0
2013-03-19 09:15 | WGL13 | SHORT RURAL |  | 2 | 81 | 162 | 0.0014097 | 1.7404e-05 | 0
2013-03-19 11:00 | WGL13 | SHORT RURAL |  | 1 | 82 | 82 | 0.00071356 | 8.702e-06 | 0
2013-03-19 12:05 | WGL13 | SHORT RURAL |  | 3 | 130 | 390 | 0.0033938 | 2.6106e-05 | 0
2013-03-19 08:50 | WYK11 | SHORT RURAL |  | 58 | 205 | 11890 | 0.10347 | 0.00050471 | 0
2013-03-19 08:35 | WYK23 | SHORT RURAL |  | 321 | 356.1215 | 114315 | 0.99477 | 0.0027933 | 0
2013-03-19 09:18 | LDL23 | LONG RURAL |  | 70 | 447 | 31290 | 0.12116 | 0.00027106 | 0
2013-03-20 08:30 | WGL15 | SHORT RURAL |  | 3 | 20 | 60 | 0.00052212 | 2.6106e-05 | 0
2013-03-20 08:50 | LGA14 | LONG RURAL |  | 2 | 55 | 110 | 0.00042595 | 7.7446e-06 | 0
2013-03-20 10:05 | LGA14 | LONG RURAL |  | 2 | 40 | 80 | 0.00030979 | 7.7446e-06 | 0
2013-03-20 09:25 | WGL24 | LONG RURAL |  | 2 | 277 | 554 | 0.0021453 | 7.7446e-06 | 0
2013-03-19 10:58 | FTR22 | SHORT RURAL |  | 3 | 98 | 294 | 0.0025584 | 2.6106e-05 | 0
2013-03-19 09:25 | FTR21 | LONG RURAL |  | 11 | 50 | 550 | 0.0021298 | 4.2595e-05 | 0
2013-03-19 09:08 | WGI22 | LONG RURAL |  | 1 | 197 | 197 | 0.00076285 | 3.8723e-06 | 0
2013-03-20 09:25 | LGA23 | LONG RURAL |  | 26 | 200 | 5200 | 0.020136 | 0.00010068 | 0
2013-03-20 09:00 | WYK11 | SHORT RURAL |  | 2 | 60 | 120 | 0.0010442 | 1.7404e-05 | 0
2013-03-20 09:10 | LGA11 | LONG RURAL |  | 18 | 187 | 3366 | 0.013034 | 6.9702e-05 | 0
2013-03-20 14:00 | WYK11 | SHORT RURAL |  | 5 | 30 | 150 | 0.0013053 | 4.351e-05 | 0
2013-03-20 14:50 | WYK11 | SHORT RURAL |  | 3 | 40 | 120 | 0.0010442 | 2.6106e-05 | 0
2013-03-20 12:30 | WYK11 | SHORT RURAL |  | 3 | 37 | 111 | 0.00096592 | 2.6106e-05 | 0
2013-03-20 08:30 | LDL13 | SHORT RURAL |  | 14 | 280 | 3920 | 0.034112 | 0.00012183 | 0
2013-03-20 09:20 | PHI12 | SHORT RURAL |  | 191 | 337.4607 | 64455 | 0.56089 | 0.0016621 | 0
2013-03-20 09:10 | LLG12 | SHORT RURAL |  | 27 | 151 | 4077 | 0.035478 | 0.00023495 | 0
2013-03-21 08:50 | FTR22 | SHORT RURAL |  | 10 | 220 | 2200 | 0.019144 | 8.702e-05 | 0
2013-03-19 09:00 | BDL6 | SHORT RURAL |  | 863 | 297 | 256311 | 2.2304 | 0.0075098 | 0
2013-03-20 09:40 | MFA34 | SHORT RURAL |  | 6 | 320 | 1920 | 0.016708 | 5.2212e-05 | 0
2013-03-20 09:25 | BDL1 | LONG RURAL |  | 1 | 260 | 260 | 0.0010068 | 3.8723e-06 | 0
2013-03-20 11:11 | MFA21 | LONG RURAL |  | 1 | 179 | 179 | 0.00069314 | 3.8723e-06 | 0
2013-03-21 10:05 | WGI23 | SHORT RURAL |  | 116 | 273 | 31668 | 0.27557 | 0.0010094 | 0
2013-03-20 08:50 | LDL13 | SHORT RURAL |  | 34 | 290 | 9860 | 0.085801 | 0.00029587 | 0
2013-03-21 09:56 | WYK23 | SHORT RURAL |  | 74 | 396 | 29304 | 0.255 | 0.00064395 | 0
2013-03-19 09:15 | WGL24 | LONG RURAL |  | 1 | 165 | 165 | 0.00063893 | 3.8723e-06 | 0
2013-03-19 14:10 | WGL11 | SHORT RURAL |  | 45 | 60 | 2700 | 0.023495 | 0.00039159 | 0
2013-03-20 09:00 | MFA21 | LONG RURAL |  | 5 | 120 | 600 | 0.0023234 | 1.9362e-05 | 0
2013-03-21 08:40 | WYK11 | SHORT RURAL |  | 35 | 343 | 12005 | 0.10447 | 0.00030457 | 0
2013-03-19 10:00 | DRN14 | SHORT RURAL |  | 1 | 65 | 65 | 0.00056563 | 8.702e-06 | 0
2013-03-19 10:15 | LGA13 | LONG RURAL |  | 3 | 225 | 675 | 0.0026138 | 1.1617e-05 | 0
2013-03-19 09:35 | DRN11 | URBAN |  | 10 | 205 | 2050 | 0.0071411 | 3.4835e-05 | 0
2013-03-21 09:38 | LGA23 | LONG RURAL |  | 80 | 244 | 19520 | 0.075588 | 0.00030979 | 0
2013-03-19 13:30 | DRN11 | URBAN |  | 5 | 105 | 525 | 0.0018288 | 1.7417e-05 | 0
2013-03-19 12:25 | DRN14 | SHORT RURAL |  | 2 | 30 | 60 | 0.00052212 | 1.7404e-05 | 0
2013-03-19 13:10 | DRN14 | SHORT RURAL |  | 1 | 65 | 65 | 0.00056563 | 8.702e-06 | 0
2013-03-18 17:08 | TT6 | URBAN |  | 187 | 136.6791 | 25559 | 0.089034 | 0.00065141 | 0
2013-03-18 11:15 | LYD14 | SHORT RURAL |  | 28 | 50 | 1400 | 0.012183 | 0.00024366 | 0
2013-03-19 11:05 | FTR23 | LONG RURAL |  | 913 | 80.1928 | 73216 | 0.28352 | 0.0035354 | 0
2013-03-20 09:56 | FTR23 | LONG RURAL |  | 671 | 80.2712 | 53862 | 0.20857 | 0.0025983 | 0
2013-03-20 09:50 | WGI14 | SHORT RURAL |  | 44 | 90 | 3960 | 0.03446 | 0.00038289 | 0
2013-03-21 09:50 | WGI14 | SHORT RURAL |  | 51 | 10 | 510 | 0.004438 | 0.0004438 | 0
2013-03-19 08:50 | KLK1 | SHORT RURAL |  | 2 | 70 | 140 | 0.0012183 | 1.7404e-05 | 0
2013-03-18 10:40 | KMS21 | SHORT RURAL |  | 2 | 75 | 150 | 0.0013053 | 1.7404e-05 | 0
2013-03-19 12:30 | KLK1 | SHORT RURAL |  | 1 | 90 | 90 | 0.00078318 | 8.702e-06 | 0
2013-03-19 09:30 | KLK1 | SHORT RURAL |  | 1 | 120 | 120 | 0.0010442 | 8.702e-06 | 0
2013-03-19 14:25 | KLK1 | SHORT RURAL |  | 1 | 45 | 45 | 0.00039159 | 8.702e-06 | 0
2013-03-19 11:40 | KLK1 | SHORT RURAL |  | 2 | 31 | 62 | 0.00053952 | 1.7404e-05 | 0
2013-03-19 12:35 | KLK1 | SHORT RURAL |  | 1 | 94 | 94 | 0.00081799 | 8.702e-06 | 0
2013-03-19 09:10 | WYK23 | SHORT RURAL |  | 178 | 260 | 46280 | 0.40273 | 0.001549 | 0
2013-03-06 13:33 | MSD2 | LONG RURAL |  | 1 | 67 | 67 | 0.00025945 | 3.8723e-06 | 0
2013-03-19 09:55 | WT12 | URBAN |  | 111 | 350 | 38850 | 0.13533 | 0.00038667 | 0
2013-03-21 08:36 | WYK11 | SHORT RURAL |  | 390 | 359 | 140010 | 1.2184 | 0.0033938 | 0
2013-03-18 10:07 | KLO14 | LONG RURAL |  | 41 | 389 | 15949 | 0.06176 | 0.00015876 | 0
2013-03-05 09:10 | LLG12 | SHORT RURAL |  | 8 | 130 | 1040 | 0.00905 | 6.9616e-05 | 0
2013-03-10 08:30 | RWN24 | SHORT RURAL |  | 279 | 417 | 116343 | 1.0124 | 0.0024278 | 0
2013-03-06 11:45 | WN3 | LONG RURAL |  | 53 | 130 | 6890 | 0.02668 | 0.00020523 | 0
2013-03-20 09:00 | LGA13 | LONG RURAL |  | 9 | 465 | 4185 | 0.016206 | 3.4851e-05 | 0
2013-03-19 08:33 | BGE12 | SHORT RURAL |  | 1 | 23 | 23 | 0.00020015 | 8.702e-06 | 0
2013-03-19 09:12 | HPK22 | URBAN |  | 176 | 308 | 54208 | 0.18883 | 0.00061309 | 0
2013-03-14 08:50 | CYN21 | URBAN |  | 95 | 390 | 37050 | 0.12906 | 0.00033093 | 0
2013-03-14 09:25 | BWR23 | URBAN |  | 57 | 250 | 14250 | 0.04964 | 0.00019856 | 0
2013-03-17 09:00 | SMR5 | LONG RURAL |  | 22 | 379 | 8338 | 0.032287 | 8.5191e-05 | 0
2013-03-14 10:30 | CYN32 | URBAN |  | 105 | 270 | 28350 | 0.098757 | 0.00036577 | 0
2013-03-15 09:55 | RWN26 | SHORT RURAL |  | 10 | 185 | 1850 | 0.016099 | 8.702e-05 | 0
2013-03-15 08:45 | LLG14 | SHORT RURAL |  | 14 | 195 | 2730 | 0.023756 | 0.00012183 | 0
2013-03-15 10:00 | RWN26 | SHORT RURAL |  | 10 | 190 | 1900 | 0.016534 | 8.702e-05 | 0
2013-03-16 08:30 | RWN26 | SHORT RURAL |  | 331 | 268 | 88708 | 0.77193 | 0.0028804 | 0
2013-03-16 09:25 | ELM12 | SHORT RURAL |  | 52 | 195 | 10140 | 0.088238 | 0.0004525 | 0
2013-03-19 09:05 | LLG13 | SHORT RURAL |  | 13 | 70 | 910 | 0.0079188 | 0.00011313 | 0
2013-03-16 09:33 | LDL11 | URBAN |  | 798 | 406.5915 | 324460 | 1.1303 | 0.0027798 | 0
2013-03-16 08:30 | RWT11 | URBAN |  | 274 | 425 | 116450 | 0.40565 | 0.00095447 | 0
2013-03-17 08:05 | RWN26 | SHORT RURAL |  | 201 | 195 | 39195 | 0.34107 | 0.0017491 | 0
2013-03-17 09:10 | BRA14 | URBAN |  | 110 | 305 | 33550 | 0.11687 | 0.00038318 | 0
2013-03-17 11:40 | BWR24 | URBAN |  | 29 | 68 | 1972 | 0.0068694 | 0.00010102 | 0
2013-03-18 09:00 | BWR34 | URBAN |  | 123 | 255 | 31365 | 0.10926 | 0.00042847 | 0
2013-03-06 09:10 | NRN14 | URBAN |  | 324 | 400 | 129600 | 0.45146 | 0.0011286 | 0
2013-03-06 08:27 | BWR23 | URBAN |  | 81 | 546 | 44226 | 0.15406 | 0.00028216 | 0
2013-03-21 13:00 | FTR22 | SHORT RURAL |  | 21 | 85 | 1785 | 0.015533 | 0.00018274 | 0
2013-03-22 10:00 | LLG13 | SHORT RURAL |  | 5 | 140 | 700 | 0.0060914 | 4.351e-05 | 0
2013-03-22 12:10 | WGL24 | LONG RURAL |  | 26 | 65 | 1690 | 0.0065442 | 0.00010068 | 0
2013-03-22 09:10 | SLE31 | LONG RURAL |  | 62 | 305 | 18910 | 0.073225 | 0.00024008 | 0
2013-03-22 08:35 | LGA21 | SHORT RURAL |  | 2 | 120 | 240 | 0.0020885 | 1.7404e-05 | 0
2013-03-22 10:15 | LGA14 | LONG RURAL |  | 53 | 205 | 10865 | 0.042073 | 0.00020523 | 0
2013-03-22 09:35 | FTR23 | LONG RURAL |  | 15 | 316 | 4740 | 0.018355 | 5.8085e-05 | 0
2013-03-20 09:15 | TT5 | URBAN |  | 74 | 295 | 21830 | 0.076044 | 0.00025778 | 0
2013-03-19 09:03 | EPG32 | SHORT RURAL |  | 273 | 323.1282 | 88214 | 0.76764 | 0.0023756 | 0
2013-03-21 10:20 | WT13 | URBAN |  | 79 | 110 | 8690 | 0.030271 | 0.0002752 | 0
2013-03-22 08:50 | ELM33 | SHORT RURAL |  | 7 | 180 | 1260 | 0.010964 | 6.0914e-05 | 0
2013-03-18 09:50 | SMR5 | LONG RURAL |  | 20 | 265 | 5300 | 0.020523 | 7.7446e-05 | 0
2013-03-18 09:20 | SMR5 | LONG RURAL |  | 2 | 40 | 80 | 0.00030979 | 7.7446e-06 | 0
2013-03-18 11:02 | SMR5 | LONG RURAL |  | 1 | 35 | 35 | 0.00013553 | 3.8723e-06 | 0
2013-03-18 12:10 | SMR5 | LONG RURAL |  | 2 | 72 | 144 | 0.00055761 | 7.7446e-06 | 0
2013-03-21 08:57 | MFA22 | LONG RURAL |  | 117 | 356 | 41652 | 0.16129 | 0.00045306 | 0
2013-03-19 09:20 | SMR3 | LONG RURAL |  | 83 | 186 | 15438 | 0.059781 | 0.0003214 | 0
2013-03-22 09:00 | LGA12 | SHORT RURAL |  | 84 | 355 | 29820 | 0.25949 | 0.00073097 | 0
2013-03-22 09:00 | FTR22 | SHORT RURAL |  | 37 | 220 | 8140 | 0.070834 | 0.00032197 | 0
2013-03-19 10:40 | LYD13 | URBAN |  | 43 | 70 | 3010 | 0.010485 | 0.00014979 | 0
2013-03-18 09:45 | CYN32 | URBAN |  | 16 | 305 | 4880 | 0.016999 | 5.5736e-05 | 0
2013-03-19 12:30 | LYD14 | SHORT RURAL |  | 3 | 100 | 300 | 0.0026106 | 2.6106e-05 | 0
2013-03-22 09:00 | LLG13 | SHORT RURAL |  | 161 | 206 | 33166 | 0.28861 | 0.001401 | 0
2013-03-17 08:35 | WN2 | LONG RURAL |  | 140 | 115 | 16100 | 0.062344 | 0.00054212 | 0
2013-03-17 09:45 | MYT8 | SHORT RURAL |  | 3 | 130 | 390 | 0.0033938 | 2.6106e-05 | 0
2013-03-15 09:20 | MYT7 | LONG RURAL |  | 40 | 115 | 4600 | 0.017813 | 0.00015489 | 0
2013-03-17 09:30 | SMR5 | LONG RURAL |  | 3 | 80 | 240 | 0.00092936 | 1.1617e-05 | 0
2013-03-17 11:07 | SMR5 | LONG RURAL |  | 1 | 83 | 83 | 0.0003214 | 3.8723e-06 | 0
2013-03-12 09:59 | SMR5 | LONG RURAL |  | 37 | 325 | 12025 | 0.046565 | 0.00014328 | 0
2013-03-21 08:50 | BDL1 | LONG RURAL |  | 3 | 45 | 135 | 0.00052276 | 1.1617e-05 | 0
2013-03-15 09:15 | WN5 | LONG RURAL |  | 50 | 9 | 450 | 0.0017425 | 0.00019362 | 0
2013-03-15 10:32 | WN5 | LONG RURAL |  | 37 | 11 | 407 | 0.001576 | 0.00014328 | 0
2013-03-15 11:30 | WN5 | LONG RURAL |  | 18 | 10 | 180 | 0.00069702 | 6.9702e-05 | 0
2013-03-20 08:35 | SFS1 | SHORT RURAL |  | 93 | 445 | 41385 | 0.36013 | 0.00080928 | 0
2013-03-20 08:35 | UWY1 | SHORT RURAL |  | 3 | 445 | 1335 | 0.011617 | 2.6106e-05 | 0
2013-03-22 09:00 | LGA13 | LONG RURAL |  | 55 | 7 | 385 | 0.0014908 | 0.00021298 | 0
2013-03-22 09:00 | LGA13 | LONG RURAL |  | 47 | 394 | 18518 | 0.071708 | 0.000182 | 0
2013-03-19 09:08 | SMR5 | LONG RURAL |  | 2 | 54 | 108 | 0.00041821 | 7.7446e-06 | 0
2013-03-19 09:10 | SMR5 | LONG RURAL |  | 1 | 100 | 100 | 0.00038723 | 3.8723e-06 | 0
2013-03-19 11:35 | SMR5 | LONG RURAL |  | 1 | 85 | 85 | 0.00032915 | 3.8723e-06 | 0
2013-03-19 13:40 | SMR5 | LONG RURAL |  | 1 | 53 | 53 | 0.00020523 | 3.8723e-06 | 0
2013-03-22 09:25 | MFA21 | LONG RURAL |  | 36 | 120 | 4320 | 0.016728 | 0.0001394 | 0
2013-03-19 11:50 | SMR5 | LONG RURAL |  | 2 | 45 | 90 | 0.00034851 | 7.7446e-06 | 0
2013-03-19 09:14 | SFS1 | SHORT RURAL |  | 518 | 698 | 361564 | 3.1463 | 0.0045076 | 0
2013-03-22 09:00 | BDL8 | LONG RURAL |  | 61 | 153 | 9333 | 0.03614 | 0.00023621 | 0
2013-03-20 09:24 | TGN31 | LONG RURAL |  | 74 | 278 | 20572 | 0.079661 | 0.00028655 | 0
2013-03-19 09:18 | SMR5 | LONG RURAL |  | 1 | 47 | 47 | 0.000182 | 3.8723e-06 | 0
2013-03-19 11:45 | SMR5 | LONG RURAL |  | 1 | 51 | 51 | 0.00019749 | 3.8723e-06 | 0
2013-03-19 12:57 | SMR5 | LONG RURAL |  | 3 | 44 | 132 | 0.00051115 | 1.1617e-05 | 0
2013-03-20 10:24 | BGE12 | SHORT RURAL |  | 148 | 251 | 37148 | 0.32326 | 0.0012879 | 0
2013-03-20 08:30 | EPG32 | SHORT RURAL |  | 88 | 414.5 | 36476 | 0.31741 | 0.00076577 | 0
2013-03-22 10:15 | DRN13 | SHORT RURAL |  | 19 | 350 | 6650 | 0.057868 | 0.00016534 | 0
2013-03-21 09:35 | FTR21 | LONG RURAL |  | 69 | 196 | 13524 | 0.052369 | 0.00026719 | 0
2013-03-17 08:47 | BRA14 | URBAN |  | 529 | 360.1078 | 190497 | 0.66359 | 0.0018428 | 0
2013-03-17 07:45 | WN1 | URBAN |  | 68 | 335 | 22780 | 0.079354 | 0.00023688 | 0
2013-03-19 08:40 | BN2 | LONG RURAL |  | 40 | 320 | 12800 | 0.049566 | 0.00015489 | 0
2013-03-19 08:37 | WN5 | LONG RURAL |  | 268 | 396 | 106128 | 0.41096 | 0.0010378 | 0
2013-03-20 08:45 | LLG13 | SHORT RURAL |  | 16 | 372 | 5952 | 0.051794 | 0.00013923 | 0
2013-03-23 08:35 | MWTS24 | SHORT RURAL |  | 64 | 430 | 27520 | 0.23948 | 0.00055693 | 0
2013-03-23 09:00 | WGL11 | SHORT RURAL |  | 139 | 232 | 32248 | 0.28062 | 0.0012096 | 0
2013-03-22 15:11 | FTR23 | LONG RURAL |  | 503 | 3 | 1509 | 0.0058433 | 0.0019478 | 0
2013-03-22 12:20 | ELM33 | SHORT RURAL |  | 7 | 90 | 630 | 0.0054822 | 6.0914e-05 | 0
2013-03-22 15:29 | LGA13 | LONG RURAL |  | 102 | 5 | 510 | 0.0019749 | 0.00039498 | 0
2013-03-18 10:20 | BRA32 | URBAN |  | 84 | 245 | 20580 | 0.07169 | 0.00029261 | 0
2013-03-17 12:30 | BRT22 | SHORT RURAL |  | 3 | 60 | 180 | 0.0015664 | 2.6106e-05 | 0
2013-03-19 10:40 | DRN12 | URBAN |  | 1 | 140 | 140 | 0.00048769 | 3.4835e-06 | 0
2013-03-20 10:00 | DRN14 | SHORT RURAL |  | 1 | 35 | 35 | 0.00030457 | 8.702e-06 | 0
2013-03-18 08:50 | RWT22 | URBAN |  | 156 | 270 | 42120 | 0.14672 | 0.00054342 | 0
2013-03-20 10:48 | KMS21 | SHORT RURAL |  | 12 | 15 | 180 | 0.0015664 | 0.00010442 | 0
2013-03-17 09:03 | BN2 | LONG RURAL |  | 11 | 367 | 4037 | 0.015633 | 4.2595e-05 | 0
2013-03-17 14:00 | BRT22 | SHORT RURAL |  | 1 | 60 | 60 | 0.00052212 | 8.702e-06 | 0
2013-03-23 08:22 | EPG12 | URBAN |  | 301 | 405 | 121905 | 0.42465 | 0.0010485 | 0
2013-03-23 08:22 | EPG34 | URBAN |  | 98 | 419 | 41062 | 0.14304 | 0.00034138 | 0
2013-03-19 09:30 | MBY11 | SHORT RURAL |  | 115 | 245 | 28175 | 0.24518 | 0.0010007 | 0
2013-03-20 09:01 | WOTS12 | URBAN |  | 116 | 472 | 54752 | 0.19073 | 0.00040408 | 0
2013-03-20 09:03 | MBY11 | SHORT RURAL |  | 976 | 269.0697 | 262612 | 2.2852 | 0.0084931 | 0
2013-03-22 09:20 | BDL6 | SHORT RURAL |  | 86 | 294 | 25284 | 0.22002 | 0.00074837 | 0
2013-03-20 09:10 | SMR5 | LONG RURAL |  | 2 | 90 | 180 | 0.00069702 | 7.7446e-06 | 0
2013-03-18 09:14 | RWN24 | SHORT RURAL |  | 7 | 164 | 1148 | 0.0099899 | 6.0914e-05 | 0
2013-03-19 09:10 | BRA11 | URBAN |  | 94 | 50 | 4700 | 0.016372 | 0.00032745 | 0
2013-03-19 09:38 | RWN22 | URBAN |  | 369 | 336 | 123984 | 0.4319 | 0.0012854 | 0
2013-03-18 12:15 | WN5 | LONG RURAL |  | 3 | 100 | 300 | 0.0011617 | 1.1617e-05 | 0
2013-03-18 13:46 | WN5 | LONG RURAL |  | 3 | 55 | 165 | 0.00063893 | 1.1617e-05 | 0
2013-03-19 10:30 | WN5 | LONG RURAL |  | 1 | 210 | 210 | 0.00081319 | 3.8723e-06 | 0
2013-03-24 09:40 | BDL5 | LONG RURAL |  | 203 | 310 | 62930 | 0.24368 | 0.00078608 | 0
2013-03-19 09:30 | BRA13 | URBAN |  | 124 | 240 | 29760 | 0.10367 | 0.00043195 | 0
2013-03-19 08:02 | CYN13 | URBAN |  | 5 | 403 | 2015 | 0.0070192 | 1.7417e-05 | 0
2013-03-19 09:30 | RWN24 | SHORT RURAL |  | 104 | 210 | 21840 | 0.19005 | 0.000905 | 0
2013-03-20 09:20 | KMS1 | SHORT RURAL |  | 2 | 230 | 460 | 0.0040029 | 1.7404e-05 | 0
2013-03-14 17:12 | CYN13 | URBAN |  | 1 | 17 | 17 | 5.9219e-05 | 3.4835e-06 | 0
2013-03-20 11:15 | SMR5 | LONG RURAL |  | 1 | 50 | 50 | 0.00019362 | 3.8723e-06 | 0
2013-03-17 10:55 | WN4 | SHORT RURAL |  | 81 | 70 | 5670 | 0.04934 | 0.00070486 | 0
2013-03-20 08:30 | WOTS11 | LONG RURAL |  | 162 | 470 | 76140 | 0.29484 | 0.00062731 | 0
2013-03-20 09:50 | WOTS11 | LONG RURAL |  | 8 | 220 | 1760 | 0.0068153 | 3.0979e-05 | 0
2013-03-21 09:10 | WN3 | LONG RURAL |  | 1 | 168 | 168 | 0.00065055 | 3.8723e-06 | 0
2013-03-22 08:45 | DRN14 | SHORT RURAL |  | 1 | 39 | 39 | 0.00033938 | 8.702e-06 | 0
2013-03-24 10:08 | KLK1 | SHORT RURAL |  | 1 | 87 | 87 | 0.00075707 | 8.702e-06 | 0
2013-03-24 12:46 | KLK1 | SHORT RURAL |  | 2 | 41 | 82 | 0.00071356 | 1.7404e-05 | 0
2013-03-19 08:45 | RWN32 | URBAN |  | 84 | 330 | 27720 | 0.096562 | 0.00029261 | 0
2013-03-15 09:11 | SMR5 | LONG RURAL |  | 4 | 229 | 916 | 0.003547 | 1.5489e-05 | 0
2013-03-20 08:30 | CNR2 | SHORT RURAL |  | 54 | 170 | 9180 | 0.079884 | 0.00046991 | 0
2013-03-22 08:15 | WN6 | LONG RURAL |  | 2 | 101 | 202 | 0.00078221 | 7.7446e-06 | 0
2013-03-19 08:42 | CRE32 | URBAN |  | 88 | 153 | 13464 | 0.046902 | 0.00030655 | 0
2013-03-19 11:59 | RWT25 | URBAN |  | 1097 | 63 | 69111 | 0.24075 | 0.0038214 | 0
2013-03-12 09:50 | RWN22 | URBAN |  | 128 | 81 | 10368 | 0.036117 | 0.00044589 | 0
2013-03-25 10:28 | WGL13 | SHORT RURAL |  | 5 | 257 | 1285 | 0.011182 | 4.351e-05 | 0
2013-03-25 09:40 | WYK23 | SHORT RURAL |  | 51 | 265 | 13515 | 0.11761 | 0.0004438 | 0
2013-03-25 10:00 | WYK24 | SHORT RURAL |  | 42 | 82 | 3444 | 0.02997 | 0.00036548 | 0
2013-03-25 11:15 | EPG31 | URBAN |  | 102 | 225 | 22950 | 0.079946 | 0.00035532 | 0
2013-03-25 10:05 | SMR3 | LONG RURAL |  | 2 | 60 | 120 | 0.00046468 | 7.7446e-06 | 0
2013-03-25 09:00 | WN2 | LONG RURAL |  | 208 | 380.5144 | 79147 | 0.30648 | 0.00080544 | 0
2013-03-20 08:10 | CYN32 | URBAN |  | 54 | 210 | 11340 | 0.039503 | 0.00018811 | 0
2013-03-20 09:40 | CYN13 | URBAN |  | 68 | 165 | 11220 | 0.039085 | 0.00023688 | 0
2013-03-20 08:30 | RWT14 | URBAN |  | 423 | 375 | 158625 | 0.55257 | 0.0014735 | 0
2013-03-22 08:15 | DRN14 | SHORT RURAL |  | 1 | 25 | 25 | 0.00021755 | 8.702e-06 | 0
2013-03-22 08:50 | DRN14 | SHORT RURAL |  | 1 | 40 | 40 | 0.00034808 | 8.702e-06 | 0
2013-03-22 09:20 | DRN14 | SHORT RURAL |  | 1 | 40 | 40 | 0.00034808 | 8.702e-06 | 0
2013-03-20 09:55 | BWR13 | SHORT RURAL |  | 2 | 125 | 250 | 0.0021755 | 1.7404e-05 | 0
2013-03-22 11:08 | DRN14 | SHORT RURAL |  | 2 | 26 | 52 | 0.0004525 | 1.7404e-05 | 0
2013-03-21 10:02 | WGI34 | SHORT RURAL |  | 105 | 113 | 11865 | 0.10325 | 0.00091371 | 0
2013-03-24 10:20 | MOE23 | SHORT RURAL |  | 1016 | 11.4291 | 11612 | 0.10105 | 0.0088412 | 0
2013-03-20 12:10 | WGL21 | LONG RURAL |  | 7 | 78 | 546 | 0.0021143 | 2.7106e-05 | 0
2013-03-20 10:07 | RWN32 | URBAN |  | 137 | 88 | 12056 | 0.041997 | 0.00047724 | 0
2013-03-21 09:01 | BDL2 | SHORT RURAL |  | 174 | 166 | 28884 | 0.25135 | 0.0015141 | 0
2013-03-25 09:00 | WO32 | URBAN |  | 63 | 230 | 14490 | 0.050476 | 0.00021946 | 0
2013-03-25 09:00 | LGA22 | SHORT RURAL |  | 54 | 115 | 6210 | 0.054039 | 0.00046991 | 0
2013-03-21 10:40 | CRE32 | URBAN |  | 156 | 200 | 31200 | 0.10868 | 0.00054342 | 0
2013-03-23 08:30 | RWT15 | URBAN |  | 158 | 120 | 18960 | 0.066047 | 0.00055039 | 0
2013-03-23 11:18 | BWR32 | URBAN |  | 75 | 74 | 5550 | 0.019333 | 0.00026126 | 0
2013-03-26 09:16 | CYN21 | URBAN |  | 490 | 329 | 161210 | 0.56157 | 0.0017069 | 0
2013-03-26 09:20 | WGL23 | SHORT RURAL |  | 2 | 255 | 510 | 0.004438 | 1.7404e-05 | 0
2013-03-26 08:37 | FTR23 | LONG RURAL |  | 503 | 36.9642 | 18593 | 0.071998 | 0.0019478 | 0
2013-03-27 08:41 | FTR23 | LONG RURAL |  | 503 | 307.8966 | 154872 | 0.59971 | 0.0019478 | 0
2013-03-26 09:03 | MOE14 | SHORT RURAL |  | 149 | 312 | 46488 | 0.40454 | 0.0012966 | 0
2013-03-27 08:33 | TGN23 | SHORT RURAL |  | 19 | 369 | 7011 | 0.06101 | 0.00016534 | 0
2013-03-26 14:30 | LDL14 | SHORT RURAL |  | 60 | 49 | 2940 | 0.025584 | 0.00052212 | 0
2013-03-26 14:35 | WYK11 | SHORT RURAL |  | 1 | 40 | 40 | 0.00034808 | 8.702e-06 | 0
2013-03-26 14:05 | WYK11 | SHORT RURAL |  | 23 | 50 | 1150 | 0.010007 | 0.00020015 | 0
2013-03-26 12:30 | WYK11 | SHORT RURAL |  | 2 | 55 | 110 | 0.00095722 | 1.7404e-05 | 0
2013-03-26 12:30 | WYK11 | SHORT RURAL |  | 24 | 55 | 1320 | 0.011487 | 0.00020885 | 0
2013-03-26 10:00 | WYK23 | SHORT RURAL |  | 2 | 70 | 140 | 0.0012183 | 1.7404e-05 | 0
2013-03-26 10:22 | WYK11 | SHORT RURAL |  | 11 | 63 | 693 | 0.0060305 | 9.5722e-05 | 0
2013-03-26 09:15 | LDL13 | SHORT RURAL |  | 26 | 90 | 2340 | 0.020363 | 0.00022625 | 0
2013-03-26 09:00 | WYK23 | SHORT RURAL |  | 135 | 345 | 46575 | 0.40529 | 0.0011748 | 0
2013-03-26 08:30 | KLK1 | SHORT RURAL |  | 2 | 170 | 340 | 0.0029587 | 1.7404e-05 | 0
2013-03-26 11:12 | KLK1 | SHORT RURAL |  | 66 | 127 | 8382 | 0.07294 | 0.00057433 | 0
2013-03-26 09:30 | KLK1 | SHORT RURAL |  | 70 | 81 | 5670 | 0.04934 | 0.00060914 | 0
2013-03-26 08:30 | WYK12 | SHORT RURAL |  | 109 | 385 | 41965 | 0.36518 | 0.00094851 | 0
2013-03-26 09:35 | WYK23 | SHORT RURAL |  | 15 | 210 | 3150 | 0.027411 | 0.00013053 | 0
2013-03-26 12:50 | WYK24 | SHORT RURAL |  | 42 | 50 | 2100 | 0.018274 | 0.00036548 | 0
2013-03-27 09:05 | WGL23 | SHORT RURAL |  | 71 | 265 | 18815 | 0.16373 | 0.00061784 | 0
2013-03-27 09:00 | MOE22 | LONG RURAL |  | 4 | 12 | 48 | 0.00018587 | 1.5489e-05 | 0
2013-03-26 14:40 | LDL23 | LONG RURAL |  | 15 | 60 | 900 | 0.0034851 | 5.8085e-05 | 0
2013-03-28 10:05 | WT13 | URBAN |  | 97 | 190 | 18430 | 0.064201 | 0.0003379 | 0
2013-03-27 09:30 | LDL13 | SHORT RURAL |  | 68 | 790.6765 | 53766 | 0.46787 | 0.00059173 | 0
2013-03-27 13:15 | WYK11 | SHORT RURAL |  | 3 | 55 | 165 | 0.0014358 | 2.6106e-05 | 0
2013-03-27 08:30 | KLK1 | SHORT RURAL |  | 2 | 245 | 490 | 0.004264 | 1.7404e-05 | 0
2013-03-27 11:10 | LDL14 | SHORT RURAL |  | 26 | 65 | 1690 | 0.014706 | 0.00022625 | 0
2013-03-27 08:10 | WYK23 | SHORT RURAL |  | 36 | 285.8889 | 10292 | 0.089561 | 0.00031327 | 0
2013-03-28 09:26 | KLK1 | SHORT RURAL |  | 70 | 54 | 3780 | 0.032893 | 0.00060914 | 0
2013-03-25 12:10 | SMR3 | LONG RURAL |  | 1 | 60 | 60 | 0.00023234 | 3.8723e-06 | 0
2013-03-25 13:25 | MYT8 | SHORT RURAL |  | 1 | 40 | 40 | 0.00034808 | 8.702e-06 | 0
2013-03-26 09:35 | WGL11 | SHORT RURAL |  | 48 | 145 | 6960 | 0.060566 | 0.00041769 | 0
2013-03-25 09:30 | WGI23 | SHORT RURAL |  | 21 | 190 | 3990 | 0.034721 | 0.00018274 | 0
2013-03-26 09:10 | LLG13 | SHORT RURAL |  | 1067 | 88.6729 | 94614 | 0.82333 | 0.009285 | 0
2013-03-26 09:10 | FTR21 | LONG RURAL |  | 26 | 232 | 6032 | 0.023358 | 0.00010068 | 0
2013-03-26 11:05 | FTR12 | LONG RURAL |  | 47 | 205 | 9635 | 0.03731 | 0.000182 | 0
2013-03-26 09:15 | LGA24 | SHORT RURAL |  | 239 | 285 | 68115 | 0.59273 | 0.0020798 | 0
2013-03-26 09:30 | FTR21 | LONG RURAL |  | 7 | 55 | 385 | 0.0014908 | 2.7106e-05 | 0
2013-03-26 09:35 | WGI23 | SHORT RURAL |  | 55 | 280 | 15400 | 0.13401 | 0.00047861 | 0
2013-03-26 09:45 | PHI13 | URBAN |  | 2 | 230 | 460 | 0.0016024 | 6.967e-06 | 0
2013-03-21 08:29 | LLG11 | SHORT RURAL |  | 93 | 458 | 42594 | 0.37065 | 0.00080928 | 0
2013-03-23 12:08 | OFR23 | LONG RURAL |  | 1 | 31 | 31 | 0.00012004 | 3.8723e-06 | 0
2013-03-26 08:40 | WO32 | URBAN |  | 84 | 380 | 31920 | 0.11119 | 0.00029261 | 0
2013-03-25 10:10 | ELM33 | SHORT RURAL |  | 103 | 325.2913 | 33505 | 0.29156 | 0.0008963 | 0
2013-03-26 09:20 | BWA22 | LONG RURAL |  | 42 | 255 | 10710 | 0.041472 | 0.00016264 | 0
2013-03-27 10:25 | WGL13 | SHORT RURAL |  | 1 | 56 | 56 | 0.00048731 | 8.702e-06 | 0
2013-03-26 09:40 | WGL13 | SHORT RURAL |  | 13 | 260 | 3380 | 0.029413 | 0.00011313 | 0
2013-03-27 09:32 | WO31 | URBAN |  | 68 | 368 | 25024 | 0.087171 | 0.00023688 | 0
2013-03-27 09:32 | WO32 | URBAN |  | 159 | 368 | 58512 | 0.20383 | 0.00055387 | 0
2013-03-27 09:15 | WGL13 | SHORT RURAL |  | 1 | 240 | 240 | 0.0020885 | 8.702e-06 | 0
2013-03-27 10:40 | LLG12 | SHORT RURAL |  | 17 | 225 | 3825 | 0.033285 | 0.00014793 | 0
2013-03-27 10:00 | FTR22 | SHORT RURAL |  | 3 | 220 | 660 | 0.0057433 | 2.6106e-05 | 0
2013-03-27 09:10 | LGA13 | LONG RURAL |  | 31 | 350 | 10850 | 0.042015 | 0.00012004 | 0
2013-03-26 09:00 | WO22 | URBAN |  | 459 | 270 | 123930 | 0.43171 | 0.0015989 | 0
2013-03-25 09:10 | SFS1 | SHORT RURAL |  | 25 | 525 | 13125 | 0.11421 | 0.00021755 | 0
2013-03-27 09:05 | WGI34 | SHORT RURAL |  | 2 | 255 | 510 | 0.004438 | 1.7404e-05 | 0
2013-03-24 08:15 | NRN14 | URBAN |  | 79 | 368 | 29072 | 0.10127 | 0.0002752 | 0
2013-03-26 08:36 | FGY13 | SHORT RURAL |  | 261 | 277 | 72297 | 0.62913 | 0.0022712 | 0
2013-03-27 10:10 | FTR23 | LONG RURAL |  | 87 | 327 | 28449 | 0.11016 | 0.00033689 | 0
2013-03-24 08:00 | RWT14 | URBAN |  | 751 | 387 | 290637 | 1.0124 | 0.0026161 | 0
2013-03-27 10:11 | LGA11 | LONG RURAL |  | 1 | 256 | 256 | 0.00099131 | 3.8723e-06 | 0
2013-03-14 09:15 | BGE12 | SHORT RURAL |  | 27 | 155 | 4185 | 0.036418 | 0.00023495 | 0
2013-03-27 10:55 | FTR21 | LONG RURAL |  | 5 | 15 | 75 | 0.00029042 | 1.9362e-05 | 0
2013-03-27 12:30 | BN6 | LONG RURAL |  | 8 | 68 | 544 | 0.0021065 | 3.0979e-05 | 0
2013-03-20 08:38 | WN3 | LONG RURAL |  | 1 | 92 | 92 | 0.00035625 | 3.8723e-06 | 0
2013-03-25 08:30 | BN3 | SHORT RURAL |  | 1 | 220 | 220 | 0.0019144 | 8.702e-06 | 0
2013-03-14 08:47 | WN6 | LONG RURAL |  | 68 | 353 | 24004 | 0.092951 | 0.00026332 | 0
2013-03-27 10:10 | BDL1 | LONG RURAL |  | 2 | 50 | 100 | 0.00038723 | 7.7446e-06 | 0
2013-03-26 09:00 | SMR3 | LONG RURAL |  | 1 | 85 | 85 | 0.00032915 | 3.8723e-06 | 0
2013-03-25 09:00 | RWN33 | URBAN |  | 14 | 300 | 4200 | 0.014631 | 4.8769e-05 | 0
2013-03-25 08:30 | WT11 | URBAN |  | 697 | 425 | 296225 | 1.0319 | 0.002428 | 0
2013-03-21 14:16 | WYK11 | SHORT RURAL |  | 89 | 14 | 1246 | 0.010843 | 0.00077448 | 0
2013-03-26 09:32 | ELM31 | URBAN |  | 530 | 443 | 234790 | 0.81789 | 0.0018462 | 0
2013-03-27 09:10 | SMR5 | LONG RURAL |  | 9 | 160 | 1440 | 0.0055761 | 3.4851e-05 | 0
2013-03-24 09:26 | WT13 | URBAN |  | 210 | 223 | 46830 | 0.16313 | 0.00073153 | 0
2013-03-28 13:15 | DRN14 | SHORT RURAL |  | 49 | 35 | 1715 | 0.014924 | 0.0004264 | 0
2013-03-27 09:35 | EPG12 | URBAN |  | 23 | 385 | 8855 | 0.030846 | 8.012e-05 | 0
2013-03-26 09:20 | BN6 | LONG RURAL |  | 3 | 125 | 375 | 0.0014521 | 1.1617e-05 | 0
2013-03-26 11:50 | BN6 | LONG RURAL |  | 8 | 106 | 848 | 0.0032837 | 3.0979e-05 | 0
2013-03-27 09:55 | MSD2 | LONG RURAL |  | 2 | 165 | 330 | 0.0012779 | 7.7446e-06 | 0
2013-03-28 08:02 | BGE22 | SHORT RURAL |  | 113 | 365 | 41245 | 0.35891 | 0.00098332 | 0
2013-03-23 08:13 | OFR23 | LONG RURAL |  | 1 | 169 | 169 | 0.00065442 | 3.8723e-06 | 0
2013-03-25 09:00 | PHM32 | URBAN |  | 136 | 250 | 34000 | 0.11844 | 0.00047375 | 0
2013-03-28 11:16 | ELM33 | SHORT RURAL |  | 61 | 51 | 3111 | 0.027072 | 0.00053082 | 0
2013-03-25 09:45 | BWN13 | URBAN |  | 57 | 199 | 11343 | 0.039513 | 0.00019856 | 0
2013-03-26 08:40 | BWN12 | URBAN |  | 57 | 210 | 11970 | 0.041697 | 0.00019856 | 0
2013-03-24 09:00 | CYN21 | URBAN |  | 176 | 430 | 75680 | 0.26363 | 0.00061309 | 0
2013-03-24 12:33 | BWR22 | URBAN |  | 1 | 39 | 39 | 0.00013586 | 3.4835e-06 | 0
2013-03-25 09:45 | CYN24 | URBAN |  | 120 | 324 | 38880 | 0.13544 | 0.00041802 | 0
2013-03-25 09:35 | BRA11 | URBAN |  | 507 | 26.4675 | 13419 | 0.046745 | 0.0017661 | 0
2013-03-27 09:58 | TT6 | URBAN |  | 556 | 377 | 209612 | 0.73018 | 0.0019368 | 0
2013-03-26 08:31 | RWN26 | SHORT RURAL |  | 250 | 224 | 56000 | 0.48731 | 0.0021755 | 0
2013-03-26 09:00 | BWR13 | SHORT RURAL |  | 704 | 370 | 260480 | 2.2667 | 0.0061262 | 0
2013-03-27 09:15 | BRA14 | URBAN |  | 43 | 271 | 11653 | 0.040593 | 0.00014979 | 0
2013-03-27 09:45 | RWT14 | URBAN |  | 360 | 165 | 59400 | 0.20692 | 0.0012541 | 0
2013-03-28 12:09 | KMS1 | SHORT RURAL |  | 1 | 54 | 54 | 0.00046991 | 8.702e-06 | 0
2013-03-28 09:30 | NLA32 | SHORT RURAL |  | 75 | 372 | 27900 | 0.24278 | 0.00065265 | 0
2013-03-27 09:05 | CNR2 | SHORT RURAL |  | 2 | 10 | 20 | 0.00017404 | 1.7404e-05 | 0
2013-03-24 12:25 | WGL24 | LONG RURAL |  | 8 | 30 | 240 | 0.00092936 | 3.0979e-05 | 0
2013-03-24 13:15 | WGL24 | LONG RURAL |  | 3 | 45 | 135 | 0.00052276 | 1.1617e-05 | 0
2013-03-27 10:13 | CNR2 | SHORT RURAL |  | 2 | 10 | 20 | 0.00017404 | 1.7404e-05 | 0
2013-03-26 08:50 | BN2 | LONG RURAL |  | 1 | 85 | 85 | 0.00032915 | 3.8723e-06 | 0
2013-03-28 09:15 | BGE12 | SHORT RURAL |  | 4 | 104 | 416 | 0.00362 | 3.4808e-05 | 0
2013-03-26 08:50 | CLN23 | SHORT RURAL |  | 12 | 260 | 3120 | 0.02715 | 0.00010442 | 0
2013-03-28 10:07 | BWN12 | URBAN |  | 113 | 310 | 35030 | 0.12203 | 0.00039363 | 0
2013-03-26 09:15 | NRN11 | URBAN |  | 3 | 60 | 180 | 0.00062703 | 1.045e-05 | 0
2013-03-27 09:40 | RWN24 | SHORT RURAL |  | 92 | 195 | 17940 | 0.15611 | 0.00080058 | 0
2013-03-27 08:53 | RWN24 | SHORT RURAL |  | 104 | 221 | 22984 | 0.20001 | 0.000905 | 0
2013-03-15 08:10 | RWT11 | URBAN |  | 350 | 255 | 89250 | 0.3109 | 0.0012192 | 0
2013-03-17 09:26 | WO11 | URBAN |  | 1 | 279 | 279 | 0.00097189 | 3.4835e-06 | 0
2013-03-27 08:30 | BDL1 | LONG RURAL |  | 2 | 60 | 120 | 0.00046468 | 7.7446e-06 | 0
2013-03-28 08:30 | BDL6 | SHORT RURAL |  | 214 | 283 | 60562 | 0.52701 | 0.0018622 | 0
2013-03-26 08:10 | BN4 | URBAN |  | 33 | 47 | 1551 | 0.0054029 | 0.00011495 | 0
2013-03-28 11:12 | FTR21 | LONG RURAL |  | 597 | 115 | 68655 | 0.26585 | 0.0023118 | 0
2013-03-27 09:00 | CLN23 | SHORT RURAL |  | 160 | 430 | 68800 | 0.5987 | 0.0013923 | 0
2013-03-28 08:55 | CRE22 | URBAN |  | 42 | 100 | 4200 | 0.014631 | 0.00014631 | 0
2013-03-28 12:00 | CRE22 | URBAN |  | 65 | 65 | 4225 | 0.014718 | 0.00022643 | 0
2013-03-18 10:00 | WN5 | LONG RURAL |  | 3 | 90 | 270 | 0.0010455 | 1.1617e-05 | 0
2013-03-20 10:30 | WT13 | URBAN |  | 103 | 195 | 20085 | 0.069966 | 0.0003588 | 0
2013-04-03 09:00 | FTR21 | LONG RURAL |  | 31 | 205 | 6355 | 0.024609 | 0.00012004 | 0
2013-04-03 08:35 | TGN31 | LONG RURAL |  | 1 | 45 | 45 | 0.00017425 | 3.8723e-06 | 0
2013-04-03 09:30 | MOE21 | SHORT RURAL |  | 1 | 115 | 115 | 0.0010007 | 8.702e-06 | 0
2013-04-03 10:30 | TGN31 | LONG RURAL |  | 1 | 68 | 68 | 0.00026332 | 3.8723e-06 | 0
2013-04-03 11:15 | WGL11 | SHORT RURAL |  | 6 | 30 | 180 | 0.0015664 | 5.2212e-05 | 0
2013-04-03 12:00 | WGL11 | SHORT RURAL |  | 8 | 25 | 200 | 0.0017404 | 6.9616e-05 | 0
2013-04-03 12:26 | MOE21 | SHORT RURAL |  | 1 | 89 | 89 | 0.00077448 | 8.702e-06 | 0
2013-04-04 08:30 | CLN21 | SHORT RURAL |  | 6 | 250 | 1500 | 0.013053 | 5.2212e-05 | 0
2013-04-02 09:15 | MWTS31 | SHORT RURAL |  | 19 | 83 | 1577 | 0.013723 | 0.00016534 | 0
2013-04-03 09:15 | WGL11 | SHORT RURAL |  | 54 | 115 | 6210 | 0.054039 | 0.00046991 | 0
2013-04-02 09:00 | TGN11 | SHORT RURAL |  | 90 | 230 | 20700 | 0.18013 | 0.00078318 | 0
2013-04-03 09:00 | TGN31 | LONG RURAL |  | 32 | 225 | 7200 | 0.027881 | 0.00012391 | 0
2013-04-03 11:25 | WGL11 | SHORT RURAL |  | 75 | 50 | 3750 | 0.032632 | 0.00065265 | 0
2013-04-02 11:37 | WYK23 | SHORT RURAL |  | 52 | 183 | 9516 | 0.082808 | 0.0004525 | 0
2013-04-02 10:00 | WYK12 | SHORT RURAL |  | 77 | 220 | 16940 | 0.14741 | 0.00067005 | 0
2013-04-03 11:20 | WYK24 | SHORT RURAL |  | 84 | 175 | 14700 | 0.12792 | 0.00073097 | 0
2013-04-03 09:25 | WYK11 | SHORT RURAL |  | 78 | 195 | 15210 | 0.13236 | 0.00067875 | 0
2013-04-04 09:10 | MYT2 | SHORT RURAL |  | 5 | 110 | 550 | 0.0047861 | 4.351e-05 | 0
2013-04-03 08:30 | KLK2 | SHORT RURAL |  | 39 | 360 | 14040 | 0.12218 | 0.00033938 | 0
2013-04-03 08:45 | KLK1 | SHORT RURAL |  | 4 | 133 | 532 | 0.0046294 | 3.4808e-05 | 0
2013-04-03 09:17 | KMS1 | SHORT RURAL |  | 79 | 388 | 30652 | 0.26673 | 0.00068746 | 0
2013-04-02 08:45 | SLE24 | URBAN |  | 108 | 330 | 35640 | 0.12415 | 0.00037622 | 0
2013-04-03 08:50 | MFA31 | SHORT RURAL |  | 311 | 250 | 77750 | 0.67658 | 0.0027063 | 0
2013-04-02 09:40 | MSD4 | LONG RURAL |  | 1 | 80 | 80 | 0.00030979 | 3.8723e-06 | 0
2013-04-03 09:02 | MOE13 | SHORT RURAL |  | 41 | 238 | 9758 | 0.084914 | 0.00035678 | 0
2013-04-04 09:00 | SLE31 | LONG RURAL |  | 57 | 210 | 11970 | 0.046352 | 0.00022072 | 0
2013-04-02 08:40 | CRE33 | SHORT RURAL |  | 3 | 60 | 180 | 0.0015664 | 2.6106e-05 | 0
2013-04-02 10:05 | CRE33 | SHORT RURAL |  | 17 | 90 | 1530 | 0.013314 | 0.00014793 | 0
2013-04-03 09:00 | CYN12 | URBAN |  | 79 | 141 | 11139 | 0.038803 | 0.0002752 | 0
2013-04-03 09:30 | CYN32 | URBAN |  | 134 | 230 | 30820 | 0.10736 | 0.00046679 | 0
2013-04-03 10:00 | BGE11 | SHORT RURAL |  | 302 | 130 | 39260 | 0.34164 | 0.002628 | 0
2013-04-02 09:20 | BN1 | LONG RURAL |  | 6 | 115 | 690 | 0.0026719 | 2.3234e-05 | 0
2013-04-03 09:30 | BN1 | LONG RURAL |  | 27 | 335 | 9045 | 0.035025 | 0.00010455 | 0
2013-04-02 11:00 | OFR23 | LONG RURAL |  | 1 | 90 | 90 | 0.00034851 | 3.8723e-06 | 0
2013-04-03 09:56 | BWN11 | SHORT RURAL |  | 71 | 169 | 11999 | 0.10441 | 0.00061784 | 0
2013-04-04 08:40 | BWN14 | SHORT RURAL |  | 38 | 115 | 4370 | 0.038028 | 0.00033067 | 0
2013-04-03 12:30 | ELM33 | SHORT RURAL |  | 3 | 138 | 414 | 0.0036026 | 2.6106e-05 | 0
2013-04-03 10:05 | FTR21 | LONG RURAL |  | 2 | 20 | 40 | 0.00015489 | 7.7446e-06 | 0
2013-04-03 09:00 | FTR21 | LONG RURAL |  | 42 | 442 | 18564 | 0.071886 | 0.00016264 | 0
2013-04-03 09:50 | LLG13 | SHORT RURAL |  | 163 | 170 | 27710 | 0.24113 | 0.0014184 | 0
2013-04-04 09:05 | LDL13 | SHORT RURAL |  | 34 | 400 | 13600 | 0.11835 | 0.00029587 | 0
2013-04-02 09:50 | MDG1 | SHORT RURAL |  | 179 | 355 | 63545 | 0.55297 | 0.0015577 | 0
2013-04-04 10:45 | WYK23 | SHORT RURAL |  | 10 | 210 | 2100 | 0.018274 | 8.702e-05 | 0
2013-04-03 09:35 | WYK24 | SHORT RURAL |  | 61 | 70 | 4270 | 0.037157 | 0.00053082 | 0
2013-04-03 09:56 | LGA13 | LONG RURAL |  | 6 | 214 | 1284 | 0.0049721 | 2.3234e-05 | 0
2013-04-02 10:53 | ELM33 | SHORT RURAL |  | 3 | 106 | 318 | 0.0027672 | 2.6106e-05 | 0
2013-04-03 09:10 | LGA13 | LONG RURAL |  | 9 | 425 | 3825 | 0.014812 | 3.4851e-05 | 0
2013-04-03 10:00 | RWN31 | SHORT RURAL |  | 61 | 310 | 18910 | 0.16455 | 0.00053082 | 0
2013-04-05 08:55 | MOE21 | SHORT RURAL |  | 11 | 255 | 2805 | 0.024409 | 9.5722e-05 | 0
2013-04-05 09:05 | WGL11 | SHORT RURAL |  | 317 | 325 | 103025 | 0.89652 | 0.0027585 | 0
2013-04-05 09:15 | MOE23 | SHORT RURAL |  | 101 | 170 | 17170 | 0.14941 | 0.0008789 | 0
2013-04-04 13:46 | MYT2 | SHORT RURAL |  | 2 | 49 | 98 | 0.00085279 | 1.7404e-05 | 0
2013-04-05 10:40 | NLA32 | SHORT RURAL |  | 1 | 90 | 90 | 0.00078318 | 8.702e-06 | 0
2013-04-05 08:35 | BDL1 | LONG RURAL |  | 207 | 434 | 89838 | 0.34788 | 0.00080157 | 0
2013-04-05 08:30 | DRN11 | URBAN |  | 2 | 620 | 1240 | 0.0043195 | 6.967e-06 | 0
2013-04-04 12:31 | LDL13 | SHORT RURAL |  | 58 | 78 | 4524 | 0.039368 | 0.00050471 | 0
2013-04-04 09:09 | MWTS32 | SHORT RURAL |  | 1 | 143 | 143 | 0.0012444 | 8.702e-06 | 0
2013-04-03 10:30 | FTR21 | LONG RURAL |  | 3 | 30 | 90 | 0.00034851 | 1.1617e-05 | 0
2013-04-03 09:30 | FTR21 | LONG RURAL |  | 1 | 40 | 40 | 0.00015489 | 3.8723e-06 | 0
2013-03-28 08:50 | HPK24 | URBAN |  | 46 | 100 | 4600 | 0.016024 | 0.00016024 | 0
2013-04-03 09:02 | FTR23 | LONG RURAL |  | 1 | 258 | 258 | 0.00099906 | 3.8723e-06 | 0
2013-04-03 10:45 | FTR21 | LONG RURAL |  | 1 | 40 | 40 | 0.00015489 | 3.8723e-06 | 0
2013-04-03 10:00 | WYK24 | SHORT RURAL |  | 7 | 243 | 1701 | 0.014802 | 6.0914e-05 | 0
2013-04-02 09:30 | SMR3 | LONG RURAL |  | 13 | 280 | 3640 | 0.014095 | 5.034e-05 | 0
2013-04-02 09:13 | SMR3 | LONG RURAL |  | 18 | 100 | 1800 | 0.0069702 | 6.9702e-05 | 0
2013-04-03 09:00 | BRA14 | URBAN |  | 165 | 240 | 39600 | 0.13795 | 0.00057477 | 0
2013-04-03 09:00 | LDL24 | URBAN |  | 59 | 330 | 19470 | 0.067823 | 0.00020553 | 0
2013-04-03 09:00 | RWN33 | URBAN |  | 71 | 330 | 23430 | 0.081618 | 0.00024733 | 0
2013-04-02 09:25 | SMR8 | LONG RURAL |  | 19 | 415 | 7885 | 0.030533 | 7.3574e-05 | 0
2013-04-03 14:00 | BRA14 | URBAN |  | 53 | 95 | 5035 | 0.017539 | 0.00018462 | 0
2013-04-04 09:30 | CYN31 | URBAN |  | 800 | 253 | 202400 | 0.70506 | 0.0027868 | 0
2013-04-04 09:30 | LDL24 | URBAN |  | 171 | 253 | 43263 | 0.15071 | 0.00059568 | 0
2013-04-03 10:00 | SMR5 | LONG RURAL |  | 6 | 150 | 900 | 0.0034851 | 2.3234e-05 | 0
2013-04-03 08:05 | WO22 | URBAN |  | 5 | 10 | 50 | 0.00017417 | 1.7417e-05 | 0
2013-04-06 08:45 | SMR5 | LONG RURAL |  | 4 | 278 | 1112 | 0.004306 | 1.5489e-05 | 0
2013-04-03 13:00 | BN1 | LONG RURAL |  | 40 | 55 | 2200 | 0.0085191 | 0.00015489 | 0
2013-03-26 10:46 | WN5 | LONG RURAL |  | 1 | 61 | 61 | 0.00023621 | 3.8723e-06 | 0
2013-04-03 08:53 | WN2 | LONG RURAL |  | 20 | 92 | 1840 | 0.0071251 | 7.7446e-05 | 0
2013-04-03 08:31 | BN2 | LONG RURAL |  | 72 | 199 | 14328 | 0.055483 | 0.00027881 | 0
2013-03-27 09:20 | FTR23 | LONG RURAL |  | 1 | 126 | 126 | 0.00048791 | 3.8723e-06 | 0
2013-04-04 08:30 | BDL6 | SHORT RURAL |  | 60 | 445 | 26700 | 0.23234 | 0.00052212 | 0
2013-04-04 08:31 | FTR23 | LONG RURAL |  | 56 | 201.3929 | 11278 | 0.043672 | 0.00021685 | 0
2013-04-03 09:10 | KMS21 | SHORT RURAL |  | 24 | 357.25 | 8574 | 0.074611 | 0.00020885 | 0
2013-04-04 09:07 | LGA14 | LONG RURAL |  | 48 | 169 | 8112 | 0.031412 | 0.00018587 | 0
2013-04-02 09:05 | OFR24 | URBAN |  | 4 | 309 | 1236 | 0.0043056 | 1.3934e-05 | 0
2013-04-04 09:15 | SMR5 | LONG RURAL |  | 18 | 185 | 3330 | 0.012895 | 6.9702e-05 | 0
2013-04-05 09:10 | BGE12 | SHORT RURAL |  | 79 | 155 | 12245 | 0.10656 | 0.00068746 | 0
2013-04-04 08:50 | WOTS24 | LONG RURAL |  | 3 | 315 | 945 | 0.0036593 | 1.1617e-05 | 0
2013-04-04 09:30 | BGE12 | SHORT RURAL |  | 4 | 150 | 600 | 0.0052212 | 3.4808e-05 | 0
2013-04-04 13:12 | SMR5 | LONG RURAL |  | 66 | 45 | 2970 | 0.011501 | 0.00025557 | 0
2013-04-04 09:30 | FTR21 | LONG RURAL |  | 1 | 125 | 125 | 0.00048404 | 3.8723e-06 | 0
2013-04-04 09:04 | FTR21 | LONG RURAL |  | 25 | 310.24 | 7756 | 0.030034 | 9.6808e-05 | 0
2013-04-04 10:15 | LGA13 | LONG RURAL |  | 4 | 285 | 1140 | 0.0044144 | 1.5489e-05 | 0
2013-04-04 11:55 | FTR21 | LONG RURAL |  | 1 | 25 | 25 | 9.6808e-05 | 3.8723e-06 | 0
2013-04-04 13:20 | FTR21 | LONG RURAL |  | 1 | 65 | 65 | 0.0002517 | 3.8723e-06 | 0
2013-04-05 09:35 | FTR21 | LONG RURAL |  | 95 | 177 | 16815 | 0.065113 | 0.00036787 | 0
2013-03-21 10:30 | FTR23 | LONG RURAL |  | 3 | 220 | 660 | 0.0025557 | 1.1617e-05 | 0
2013-04-07 08:34 | WYK11 | SHORT RURAL |  | 399 | 241 | 96159 | 0.83677 | 0.0034721 | 0
2013-04-05 11:02 | BRT22 | SHORT RURAL |  | 8 | 238 | 1904 | 0.016569 | 6.9616e-05 | 0
2013-04-04 09:00 | LGA13 | LONG RURAL |  | 8 | 410 | 3280 | 0.012701 | 3.0979e-05 | 0
2013-04-05 09:42 | LYD14 | SHORT RURAL |  | 15 | 396 | 5940 | 0.05169 | 0.00013053 | 0
2013-04-05 09:25 | LYD14 | SHORT RURAL |  | 411 | 13 | 5343 | 0.046495 | 0.0035765 | 0
2013-04-05 16:35 | LYD14 | SHORT RURAL |  | 411 | 12 | 4932 | 0.042918 | 0.0035765 | 0
2013-04-05 09:45 | BGE24 | SHORT RURAL |  | 150 | 385 | 57750 | 0.50254 | 0.0013053 | 0
2013-04-04 10:00 | DRN13 | SHORT RURAL |  | 15 | 485 | 7275 | 0.063307 | 0.00013053 | 0
2013-04-04 09:38 | FGY33 | URBAN |  | 56 | 232 | 12992 | 0.045257 | 0.00019508 | 0
2013-04-07 08:40 | HPK12 | URBAN |  | 55 | 310 | 17050 | 0.059393 | 0.00019159 | 0
2013-04-05 09:15 | BDL1 | LONG RURAL |  | 1 | 27 | 27 | 0.00010455 | 3.8723e-06 | 0
2013-03-26 09:00 | WN5 | LONG RURAL |  | 1 | 360 | 360 | 0.001394 | 3.8723e-06 | 0
2013-04-05 08:35 | WOTS24 | LONG RURAL |  | 30 | 70 | 2100 | 0.0081319 | 0.00011617 | 0
2013-04-05 11:30 | WOTS24 | LONG RURAL |  | 27 | 75 | 2025 | 0.0078414 | 0.00010455 | 0
2013-04-07 10:00 | PHI13 | URBAN |  | 64 | 120 | 7680 | 0.026753 | 0.00022294 | 0
2013-04-02 09:15 | ELM12 | SHORT RURAL |  | 619 | 370 | 229030 | 1.993 | 0.0053865 | 0
2013-04-07 09:00 | SMR3 | LONG RURAL |  | 1 | 207 | 207 | 0.00080157 | 3.8723e-06 | 0
2013-04-04 08:45 | BWR32 | URBAN |  | 143 | 360 | 51480 | 0.17933 | 0.00049814 | 0
2013-04-04 08:50 | CYN33 | SHORT RURAL |  | 59 | 260 | 15340 | 0.13349 | 0.00051342 | 0
2013-04-02 11:40 | BN1 | LONG RURAL |  | 3 | 45 | 135 | 0.00052276 | 1.1617e-05 | 0
2013-03-27 09:15 | WN5 | LONG RURAL |  | 1 | 355 | 355 | 0.0013747 | 3.8723e-06 | 0
2013-04-05 09:15 | LGA13 | LONG RURAL |  | 5 | 185 | 925 | 0.0035819 | 1.9362e-05 | 0
2013-04-04 08:44 | MJG11 | SHORT RURAL |  | 2 | 69 | 138 | 0.0012009 | 1.7404e-05 | 0
2013-04-04 10:40 | MJG11 | SHORT RURAL |  | 1 | 90 | 90 | 0.00078318 | 8.702e-06 | 0
2013-04-04 09:20 | BN1 | LONG RURAL |  | 7 | 90 | 630 | 0.0024396 | 2.7106e-05 | 0
2013-04-04 12:50 | BN1 | LONG RURAL |  | 1 | 35 | 35 | 0.00013553 | 3.8723e-06 | 0
2013-04-05 08:35 | BN1 | LONG RURAL |  | 2 | 100 | 200 | 0.00077446 | 7.7446e-06 | 0
2013-04-05 11:55 | BN1 | LONG RURAL |  | 2 | 80 | 160 | 0.00061957 | 7.7446e-06 | 0
2013-04-05 09:50 | LLG13 | SHORT RURAL |  | 226 | 212.1858 | 47954 | 0.41729 | 0.0019666 | 0
2013-04-07 10:00 | MWTS32 | SHORT RURAL |  | 72 | 120 | 8640 | 0.075185 | 0.00062654 | 0
2013-04-08 09:05 | WGL11 | SHORT RURAL |  | 4 | 205 | 820 | 0.0071356 | 3.4808e-05 | 0
2013-04-08 11:15 | KLK1 | SHORT RURAL |  | 17 | 170 | 2890 | 0.025149 | 0.00014793 | 0
2013-04-08 10:34 | KLK2 | SHORT RURAL |  | 1 | 42 | 42 | 0.00036548 | 8.702e-06 | 0
2013-04-08 09:20 | CRE32 | URBAN |  | 90 | 65 | 5850 | 0.020378 | 0.00031351 | 0
2013-04-08 09:37 | LLG14 | SHORT RURAL |  | 10 | 145 | 1450 | 0.012618 | 8.702e-05 | 0
2013-04-08 09:15 | FTR21 | LONG RURAL |  | 52 | 45 | 2340 | 0.0090612 | 0.00020136 | 0
2013-04-05 09:30 | BRA11 | URBAN |  | 112 | 60 | 6720 | 0.023409 | 0.00039015 | 0
2013-04-08 09:45 | CYN21 | URBAN |  | 295 | 410 | 120950 | 0.42133 | 0.0010276 | 0
2013-03-24 10:40 | DRN14 | SHORT RURAL |  | 9 | 80 | 720 | 0.0062654 | 7.8318e-05 | 0
2013-03-24 13:14 | DRN14 | SHORT RURAL |  | 2 | 46 | 92 | 0.00080058 | 1.7404e-05 | 0
2013-03-26 10:00 | WOTS11 | LONG RURAL |  | 26 | 150 | 3900 | 0.015102 | 0.00010068 | 0
2013-04-09 09:45 | MFA21 | LONG RURAL |  | 6 | 120 | 720 | 0.0027881 | 2.3234e-05 | 0
2013-04-10 09:35 | WGL23 | SHORT RURAL |  | 136 | 340 | 46240 | 0.40238 | 0.0011835 | 0
2013-04-09 09:50 | TGN11 | SHORT RURAL |  | 19 | 300 | 5700 | 0.049601 | 0.00016534 | 0
2013-04-10 09:59 | MOE13 | SHORT RURAL |  | 281 | 322.6762 | 90672 | 0.78903 | 0.0024453 | 0
2013-04-11 09:35 | MWTS31 | SHORT RURAL |  | 151 | 292 | 44092 | 0.38369 | 0.001314 | 0
2013-04-09 08:28 | WGL12 | LONG RURAL |  | 175 | 441 | 77175 | 0.29885 | 0.00067766 | 0
2013-04-11 08:35 | BDL5 | LONG RURAL |  | 65 | 365 | 23725 | 0.091871 | 0.0002517 | 0
2013-04-11 08:35 | TGN11 | SHORT RURAL |  | 113 | 295 | 33335 | 0.29008 | 0.00098332 | 0
2013-04-09 09:20 | WYK24 | SHORT RURAL |  | 44 | 250 | 11000 | 0.095722 | 0.00038289 | 0
2013-04-09 08:30 | MDG1 | SHORT RURAL |  | 542 | 368.9668 | 199980 | 1.7402 | 0.0047165 | 0
2013-04-11 10:00 | WGL13 | SHORT RURAL |  | 2 | 110 | 220 | 0.0019144 | 1.7404e-05 | 0
2013-04-09 09:05 | LDL23 | LONG RURAL |  | 77 | 275 | 21175 | 0.081996 | 0.00029817 | 0
2013-04-09 09:05 | WGL21 | LONG RURAL |  | 32 | 325 | 10400 | 0.040272 | 0.00012391 | 0
2013-04-09 08:30 | MFA23 | SHORT RURAL |  | 5 | 125 | 625 | 0.0054387 | 4.351e-05 | 0
2013-04-10 09:30 | MFA22 | LONG RURAL |  | 56 | 180 | 10080 | 0.039033 | 0.00021685 | 0
2013-04-10 11:35 | MFA34 | SHORT RURAL |  | 3 | 195 | 585 | 0.0050907 | 2.6106e-05 | 0
2013-04-10 14:10 | MFA22 | LONG RURAL |  | 14 | 62 | 868 | 0.0033612 | 5.4212e-05 | 0
2013-04-10 09:35 | BDL5 | LONG RURAL |  | 93 | 260 | 24180 | 0.093633 | 0.00036013 | 0
2013-04-10 10:00 | WN5 | LONG RURAL |  | 2 | 190 | 380 | 0.0014715 | 7.7446e-06 | 0
2013-04-11 09:30 | KLK1 | SHORT RURAL |  | 290 | 271 | 78590 | 0.68389 | 0.0025236 | 0
2013-04-09 10:50 | WOTS24 | LONG RURAL |  | 3 | 205 | 615 | 0.0023815 | 1.1617e-05 | 0
2013-04-09 09:00 | BRT22 | SHORT RURAL |  | 60 | 270 | 16200 | 0.14097 | 0.00052212 | 0
2013-04-09 09:00 | WO32 | URBAN |  | 32 | 375 | 12000 | 0.041802 | 0.00011147 | 0
2013-04-11 08:30 | WOTS12 | URBAN |  | 33 | 295 | 9735 | 0.033912 | 0.00011495 | 0
2013-04-09 14:36 | WOTS24 | LONG RURAL |  | 1 | 24 | 24 | 9.2936e-05 | 3.8723e-06 | 0
2013-04-10 09:30 | WOTS12 | URBAN |  | 82 | 275 | 22550 | 0.078553 | 0.00028565 | 0
2013-04-10 09:00 | WOTS24 | LONG RURAL |  | 92 | 160 | 14720 | 0.057 | 0.00035625 | 0
2013-04-10 14:00 | MYT7 | LONG RURAL |  | 1 | 43 | 43 | 0.00016651 | 3.8723e-06 | 0
2013-04-09 10:18 | KLK3 | SHORT RURAL |  | 1 | 92 | 92 | 0.00080058 | 8.702e-06 | 0
2013-04-10 12:10 | MBY11 | SHORT RURAL |  | 89 | 123 | 10947 | 0.09526 | 0.00077448 | 0
2013-04-10 11:50 | WO31 | URBAN |  | 68 | 170 | 11560 | 0.040269 | 0.00023688 | 0
2013-04-09 12:22 | KLK3 | SHORT RURAL |  | 9 | 43 | 387 | 0.0033677 | 7.8318e-05 | 0
2013-04-11 09:00 | MYT2 | SHORT RURAL |  | 30 | 212 | 6360 | 0.055345 | 0.00026106 | 0
2013-04-09 09:00 | LGA13 | LONG RURAL |  | 5 | 270 | 1350 | 0.0052276 | 1.9362e-05 | 0
2013-04-09 10:15 | LGA13 | LONG RURAL |  | 2 | 60 | 120 | 0.00046468 | 7.7446e-06 | 0
2013-04-09 13:45 | LGA13 | LONG RURAL |  | 2 | 95 | 190 | 0.00073574 | 7.7446e-06 | 0
2013-04-09 11:30 | KLK3 | SHORT RURAL |  | 1 | 65 | 65 | 0.00056563 | 8.702e-06 | 0
2013-04-10 09:48 | CF1 | SHORT RURAL |  | 1 | 214 | 214 | 0.0018622 | 8.702e-06 | 0
2013-04-09 09:01 | FTR21 | LONG RURAL |  | 374 | 373 | 139502 | 0.5402 | 0.0014482 | 0
2013-04-10 09:20 | FTR12 | LONG RURAL |  | 6 | 125 | 750 | 0.0029042 | 2.3234e-05 | 0
2013-04-10 09:54 | LGA13 | LONG RURAL |  | 1 | 126 | 126 | 0.00048791 | 3.8723e-06 | 0
2013-04-04 09:52 | DRN12 | URBAN |  | 1 | 328 | 328 | 0.0011426 | 3.4835e-06 | 0
2013-04-04 11:08 | DRN12 | URBAN |  | 1 | 297 | 297 | 0.0010346 | 3.4835e-06 | 0
2013-04-04 09:45 | ELM15 | SHORT RURAL |  | 57 | 90 | 5130 | 0.044641 | 0.00049601 | 0
2013-04-04 10:10 | ELM15 | SHORT RURAL |  | 6 | 90 | 540 | 0.0046991 | 5.2212e-05 | 0
2013-04-03 11:40 | ELM31 | URBAN |  | 39 | 110 | 4290 | 0.014944 | 0.00013586 | 0
2013-04-05 09:25 | ELM12 | SHORT RURAL |  | 79 | 255 | 20145 | 0.1753 | 0.00068746 | 0
2013-04-05 11:12 | ELM13 | URBAN |  | 101 | 231 | 23331 | 0.081273 | 0.00035183 | 0
2013-04-05 09:51 | WT6 | URBAN |  | 67 | 193 | 12931 | 0.045045 | 0.00023339 | 0
2013-04-08 10:00 | EPG34 | URBAN |  | 34 | 100 | 3400 | 0.011844 | 0.00011844 | 0
2013-04-08 08:35 | ELM15 | SHORT RURAL |  | 86 | 335 | 28810 | 0.2507 | 0.00074837 | 0
2013-04-09 09:15 | WT15 | URBAN |  | 66 | 315 | 20790 | 0.072422 | 0.00022991 | 0
2013-04-09 08:37 | DRN11 | URBAN |  | 92 | 260 | 23920 | 0.083325 | 0.00032048 | 0
2013-04-07 09:10 | DRN11 | URBAN |  | 253 | 330 | 83490 | 0.29084 | 0.00088132 | 0
2013-04-11 09:10 | KLO14 | LONG RURAL |  | 70 | 115 | 8050 | 0.031172 | 0.00027106 | 0
2013-04-10 08:02 | ELM12 | SHORT RURAL |  | 357 | 487.7227 | 174117 | 1.5152 | 0.0031066 | 0
2013-04-04 10:00 | OFR23 | LONG RURAL |  | 109 | 20 | 2180 | 0.0084416 | 0.00042208 | 0
2013-04-08 09:35 | SMR3 | LONG RURAL |  | 2 | 37 | 74 | 0.00028655 | 7.7446e-06 | 0
2013-04-09 09:30 | KMS1 | SHORT RURAL |  | 1 | 70 | 70 | 0.00060914 | 8.702e-06 | 0
2013-04-09 09:50 | ALA01 | LONG RURAL |  | 2 | 322 | 644 | 0.0024938 | 7.7446e-06 | 0
2013-04-09 10:10 | BWR13 | SHORT RURAL |  | 244 | 165 | 40260 | 0.35034 | 0.0021233 | 0
2013-04-09 09:10 | BWR13 | SHORT RURAL |  | 50 | 195 | 9750 | 0.084844 | 0.0004351 | 0
2013-04-11 09:45 | DRN14 | SHORT RURAL |  | 49 | 290 | 14210 | 0.12366 | 0.0004264 | 0
2013-04-11 09:17 | DRN14 | SHORT RURAL |  | 46 | 313 | 14398 | 0.12529 | 0.00040029 | 0
2013-04-10 08:45 | CYN33 | SHORT RURAL |  | 89 | 480 | 42720 | 0.37175 | 0.00077448 | 0
2013-04-11 11:10 | WT9 | URBAN |  | 142 | 210 | 29820 | 0.10388 | 0.00049465 | 0
2013-04-09 09:15 | SMR5 | LONG RURAL |  | 1 | 60 | 60 | 0.00023234 | 3.8723e-06 | 0
2013-04-08 09:20 | BGE22 | SHORT RURAL |  | 13 | 280 | 3640 | 0.031675 | 0.00011313 | 0
2013-04-10 08:45 | BGE23 | SHORT RURAL |  | 217 | 202.7419 | 43995 | 0.38284 | 0.0018883 | 0
2013-04-02 11:35 | MSD4 | LONG RURAL |  | 1 | 60 | 60 | 0.00023234 | 3.8723e-06 | 0
2013-04-10 09:30 | LYD14 | SHORT RURAL |  | 21 | 130 | 2730 | 0.023756 | 0.00018274 | 0
2013-04-10 12:40 | LYD14 | SHORT RURAL |  | 4 | 25 | 100 | 0.0008702 | 3.4808e-05 | 0
2013-04-11 08:32 | BGE11 | SHORT RURAL |  | 82 | 88 | 7216 | 0.062793 | 0.00071356 | 0
2013-04-11 09:00 | TGN11 | SHORT RURAL |  | 53 | 60 | 3180 | 0.027672 | 0.0004612 | 0
2013-04-11 09:27 | LYD14 | SHORT RURAL |  | 1 | 243 | 243 | 0.0021146 | 8.702e-06 | 0
2013-04-11 08:30 | BGE22 | SHORT RURAL |  | 102 | 569 | 58038 | 0.50504 | 0.0008876 | 0
2013-04-10 13:50 | OFR23 | LONG RURAL |  | 1 | 115 | 115 | 0.00044532 | 3.8723e-06 | 0
2013-04-10 10:40 | OFR23 | LONG RURAL |  | 1 | 143 | 143 | 0.00055374 | 3.8723e-06 | 0
2013-04-10 11:10 | OFR23 | LONG RURAL |  | 2 | 82 | 164 | 0.00063506 | 7.7446e-06 | 0
2013-04-11 08:30 | RWN26 | SHORT RURAL |  | 56 | 345 | 19320 | 0.16812 | 0.00048731 | 0
2013-03-27 09:38 | MWTS31 | SHORT RURAL |  | 150 | 322 | 48300 | 0.42031 | 0.0013053 | 0
2013-04-12 08:30 | BDL1 | LONG RURAL |  | 7 | 400 | 2800 | 0.010842 | 2.7106e-05 | 0
2013-04-11 12:40 | WGL13 | SHORT RURAL |  | 2 | 70 | 140 | 0.0012183 | 1.7404e-05 | 0
2013-04-12 09:05 | WGL11 | SHORT RURAL |  | 94 | 215 | 20210 | 0.17587 | 0.00081799 | 0
2013-04-12 09:10 | MFA34 | SHORT RURAL |  | 4 | 330 | 1320 | 0.011487 | 3.4808e-05 | 0
2013-04-11 18:35 | WGL11 | SHORT RURAL |  | 61 | 25 | 1525 | 0.013271 | 0.00053082 | 0
2013-04-12 09:00 | MWTS24 | SHORT RURAL |  | 112 | 198 | 22176 | 0.19297 | 0.00097462 | 0
2013-04-12 09:40 | MBY11 | SHORT RURAL |  | 11 | 140 | 1540 | 0.013401 | 9.5722e-05 | 0
2013-04-12 09:00 | LLG11 | SHORT RURAL |  | 91 | 231 | 21021 | 0.18292 | 0.00079188 | 0
2013-04-11 13:00 | KLO14 | LONG RURAL |  | 29 | 49 | 1421 | 0.0055026 | 0.0001123 | 0
2013-04-12 09:00 | WT15 | URBAN |  | 56 | 70 | 3920 | 0.013655 | 0.00019508 | 0
2013-04-11 14:05 | WT12 | URBAN |  | 119 | 100 | 11900 | 0.041453 | 0.00041453 | 0
2013-04-12 08:53 | EPG14 | URBAN |  | 267 | 196 | 52332 | 0.1823 | 0.00093009 | 0
2013-04-11 12:20 | HPK14 | URBAN |  | 2 | 60 | 120 | 0.00041802 | 6.967e-06 | 0
2013-04-16 09:25 | WOTS11 | LONG RURAL |  | 3 | 95 | 285 | 0.0011036 | 1.1617e-05 | 0
2013-04-09 09:00 | LGA11 | LONG RURAL |  | 148 | 385 | 56980 | 0.22064 | 0.0005731 | 0
2013-04-05 09:30 | WYK11 | SHORT RURAL |  | 104 | 349 | 36296 | 0.31585 | 0.000905 | 0
2013-04-11 09:05 | WGI22 | LONG RURAL |  | 123 | 210 | 25830 | 0.10002 | 0.00047629 | 0
2013-04-10 09:15 | WYK11 | SHORT RURAL |  | 712 | 253 | 180136 | 1.5675 | 0.0061958 | 0
2013-04-10 09:30 | FTR21 | LONG RURAL |  | 2 | 87 | 174 | 0.00067378 | 7.7446e-06 | 0
2013-04-11 08:25 | LDL24 | URBAN |  | 108 | 245 | 26460 | 0.092173 | 0.00037622 | 0
2013-04-09 09:10 | WGI14 | SHORT RURAL |  | 82 | 476.1585 | 39045 | 0.33977 | 0.00071356 | 0
2013-04-09 09:24 | TGN31 | LONG RURAL |  | 55 | 226 | 12430 | 0.048133 | 0.00021298 | 0
2013-04-10 09:05 | FTR21 | LONG RURAL |  | 23 | 308 | 7084 | 0.027431 | 8.9063e-05 | 0
2013-04-10 13:20 | FTR21 | LONG RURAL |  | 1 | 54 | 54 | 0.0002091 | 3.8723e-06 | 0
2013-04-11 09:45 | WYK11 | SHORT RURAL |  | 2 | 45 | 90 | 0.00078318 | 1.7404e-05 | 0
2013-04-04 14:24 | WN2 | LONG RURAL |  | 1 | 32 | 32 | 0.00012391 | 3.8723e-06 | 0
2013-04-11 10:40 | WYK23 | SHORT RURAL |  | 177 | 90 | 15930 | 0.13862 | 0.0015402 | 0
2013-04-13 08:35 | ELM33 | SHORT RURAL |  | 120 | 347 | 41640 | 0.36235 | 0.0010442 | 0
2013-04-12 10:15 | ELM33 | SHORT RURAL |  | 18 | 130 | 2340 | 0.020363 | 0.00015664 | 0
2013-04-12 08:52 | LGA23 | LONG RURAL |  | 5 | 86 | 430 | 0.0016651 | 1.9362e-05 | 0
2013-04-11 10:50 | WYK11 | SHORT RURAL |  | 1 | 25 | 25 | 0.00021755 | 8.702e-06 | 0
2013-04-10 10:00 | SMR5 | LONG RURAL |  | 2 | 65 | 130 | 0.0005034 | 7.7446e-06 | 0
2013-04-12 09:09 | FTR21 | LONG RURAL |  | 87 | 231 | 20097 | 0.077822 | 0.00033689 | 0
2013-04-09 09:15 | BDL2 | SHORT RURAL |  | 125 | 140 | 17500 | 0.15228 | 0.0010877 | 0
2013-04-11 10:00 | SMR1 | SHORT RURAL |  | 26 | 100 | 2600 | 0.022625 | 0.00022625 | 0
2013-04-10 09:13 | KMS1 | SHORT RURAL |  | 229 | 422 | 96638 | 0.84094 | 0.0019928 | 0
2013-04-11 13:40 | SMR1 | SHORT RURAL |  | 1 | 40 | 40 | 0.00034808 | 8.702e-06 | 0
2013-04-10 08:30 | BDL5 | LONG RURAL |  | 59 | 380 | 22420 | 0.086817 | 0.00022847 | 0
2013-04-12 09:07 | ALA01 | LONG RURAL |  | 58 | 373 | 21634 | 0.083774 | 0.00022459 | 0
2013-04-10 09:13 | EPG35 | URBAN |  | 6 | 497 | 2982 | 0.010388 | 2.0901e-05 | 0
2013-04-10 09:03 | LGA11 | LONG RURAL |  | 108 | 341 | 36828 | 0.14261 | 0.00041821 | 0
2013-04-05 08:38 | MSD1 | LONG RURAL |  | 1 | 56 | 56 | 0.00021685 | 3.8723e-06 | 0
2013-04-05 10:44 | MJG11 | SHORT RURAL |  | 2 | 48 | 96 | 0.00083539 | 1.7404e-05 | 0
2013-04-09 08:52 | MJG11 | SHORT RURAL |  | 1 | 25 | 25 | 0.00021755 | 8.702e-06 | 0
2013-04-11 09:50 | FTR12 | LONG RURAL |  | 125 | 181.928 | 22741 | 0.08806 | 0.00048404 | 0
2013-04-12 09:05 | LLG13 | SHORT RURAL |  | 1 | 240 | 240 | 0.0020885 | 8.702e-06 | 0
2013-04-10 08:30 | LDL23 | LONG RURAL |  | 178 | 350 | 62300 | 0.24125 | 0.00068927 | 0
2013-04-12 08:35 | BDL2 | SHORT RURAL |  | 95 | 205 | 19475 | 0.16947 | 0.00082669 | 0
2013-04-04 13:45 | WN2 | LONG RURAL |  | 1 | 18 | 18 | 6.9702e-05 | 3.8723e-06 | 0
2013-04-04 10:54 | WN5 | LONG RURAL |  | 1 | 6 | 6 | 2.3234e-05 | 3.8723e-06 | 0
2013-04-11 08:53 | BGE12 | SHORT RURAL |  | 423 | 304 | 128592 | 1.119 | 0.0036809 | 0
2013-04-12 09:05 | BGE22 | SHORT RURAL |  | 112 | 280 | 31360 | 0.27289 | 0.00097462 | 0
2013-04-12 11:40 | HPK24 | URBAN |  | 120 | 110 | 13200 | 0.045982 | 0.00041802 | 0
2013-04-12 08:40 | BGE11 | SHORT RURAL |  | 140 | 185 | 25900 | 0.22538 | 0.0012183 | 0
2013-04-14 10:52 | MOE23 | SHORT RURAL |  | 1013 | 28.5094 | 28880 | 0.25131 | 0.0088151 | 0
2013-04-14 09:30 | TT1 | URBAN |  | 33 | 189 | 6237 | 0.021726 | 0.00011495 | 0
2013-04-14 07:30 | CYN22 | URBAN |  | 13 | 670 | 8710 | 0.030341 | 4.5285e-05 | 0
2013-04-12 09:15 | FTR22 | SHORT RURAL |  | 51 | 165 | 8415 | 0.073227 | 0.0004438 | 0
2013-04-10 09:53 | BWN12 | URBAN |  | 122 | 207 | 25254 | 0.087972 | 0.00042498 | 0
2013-04-14 08:25 | LDL23 | LONG RURAL |  | 170 | 365 | 62050 | 0.24028 | 0.00065829 | 0
2013-04-09 08:35 | BN1 | LONG RURAL |  | 124 | 368 | 45632 | 0.1767 | 0.00048017 | 0
2013-04-14 06:45 | FGY32 | URBAN |  | 12 | 110 | 1320 | 0.0045982 | 4.1802e-05 | 0
2013-04-13 08:30 | PHM34 | URBAN |  | 5 | 95 | 475 | 0.0016547 | 1.7417e-05 | 0
2013-04-10 08:55 | OFR23 | LONG RURAL |  | 1 | 50 | 50 | 0.00019362 | 3.8723e-06 | 0
2013-04-13 11:28 | PHM14 | LONG RURAL |  | 2 | 27 | 54 | 0.0002091 | 7.7446e-06 | 0
2013-04-14 08:25 | HPK11 | URBAN |  | 1345 | 390 | 524550 | 1.8273 | 0.0046853 | 0
2013-04-10 11:25 | MSD4 | LONG RURAL |  | 2 | 135 | 270 | 0.0010455 | 7.7446e-06 | 0
2013-04-12 09:07 | LGA23 | LONG RURAL |  | 49 | 408 | 19992 | 0.077415 | 0.00018974 | 0
2013-04-10 13:30 | WN3 | LONG RURAL |  | 1 | 60 | 60 | 0.00023234 | 3.8723e-06 | 0
2013-04-11 08:47 | MJG11 | SHORT RURAL |  | 2 | 20 | 40 | 0.00034808 | 1.7404e-05 | 0
2013-04-11 09:22 | BN1 | LONG RURAL |  | 4 | 408 | 1632 | 0.0063196 | 1.5489e-05 | 0
2013-04-12 10:15 | BN1 | LONG RURAL |  | 5 | 45 | 225 | 0.00087127 | 1.9362e-05 | 0
2013-04-15 09:15 | TGN12 | SHORT RURAL |  | 72 | 395 | 28440 | 0.24748 | 0.00062654 | 0
2013-04-15 09:10 | WGL11 | SHORT RURAL |  | 1 | 105 | 105 | 0.00091371 | 8.702e-06 | 0
2013-04-15 09:00 | MFA22 | LONG RURAL |  | 4 | 150 | 600 | 0.0023234 | 1.5489e-05 | 0
2013-04-15 09:40 | SLE31 | LONG RURAL |  | 1 | 60 | 60 | 0.00023234 | 3.8723e-06 | 0
2013-04-15 09:15 | KMS1 | SHORT RURAL |  | 3 | 307 | 921 | 0.0080145 | 2.6106e-05 | 0
2013-04-15 10:45 | LGA13 | LONG RURAL |  | 6 | 275 | 1650 | 0.0063893 | 2.3234e-05 | 0
2013-04-15 09:35 | FTR21 | LONG RURAL |  | 1 | 10 | 10 | 3.8723e-05 | 3.8723e-06 | 0
2013-03-31 01:22 | BGE22 | SHORT RURAL |  | 74 | 609 | 45066 | 0.39216 | 0.00064395 | 0
2013-04-16 09:54 | WGL12 | LONG RURAL |  | 1 | 189 | 189 | 0.00073187 | 3.8723e-06 | 0
2013-04-15 12:15 | WGL11 | SHORT RURAL |  | 18 | 200 | 3600 | 0.031327 | 0.00015664 | 0
2013-04-17 09:10 | TGN11 | SHORT RURAL |  | 1 | 40 | 40 | 0.00034808 | 8.702e-06 | 0
2013-04-16 08:35 | MFA21 | LONG RURAL |  | 1 | 170 | 170 | 0.00065829 | 3.8723e-06 | 0
2013-04-16 09:10 | MFA21 | LONG RURAL |  | 4 | 295 | 1180 | 0.0045693 | 1.5489e-05 | 0
2013-04-17 10:25 | MFA22 | LONG RURAL |  | 1 | 25 | 25 | 9.6808e-05 | 3.8723e-06 | 0
2013-04-18 09:30 | MFA23 | SHORT RURAL |  | 10 | 345 | 3450 | 0.030022 | 8.702e-05 | 0
2013-04-18 09:30 | NLA31 | LONG RURAL |  | 2 | 35 | 70 | 0.00027106 | 7.7446e-06 | 0
2013-04-18 08:09 | WO22 | URBAN |  | 605 | 71.1653 | 43055 | 0.14998 | 0.0021075 | 0
2013-04-16 09:30 | WGL11 | SHORT RURAL |  | 1 | 91 | 91 | 0.00079188 | 8.702e-06 | 0
2013-04-17 09:26 | CYN22 | URBAN |  | 360 | 96 | 34560 | 0.12039 | 0.0012541 | 0
2013-04-16 08:54 | MFA21 | LONG RURAL |  | 103 | 382 | 39346 | 0.15236 | 0.00039885 | 0
2013-04-17 08:55 | SLE31 | LONG RURAL |  | 8 | 305 | 2440 | 0.0094484 | 3.0979e-05 | 0
2013-04-17 09:00 | WGL11 | SHORT RURAL |  | 61 | 185 | 11285 | 0.098202 | 0.00053082 | 0
2013-04-18 09:25 | MFA22 | LONG RURAL |  | 121 | 274 | 33154 | 0.12838 | 0.00046855 | 0
2013-04-16 09:10 | TGN14 | LONG RURAL |  | 3 | 350 | 1050 | 0.0040659 | 1.1617e-05 | 0
2013-04-16 09:40 | SMR5 | LONG RURAL |  | 1 | 50 | 50 | 0.00019362 | 3.8723e-06 | 0
2013-04-16 09:27 | ALA01 | LONG RURAL |  | 11 | 98 | 1078 | 0.0041744 | 4.2595e-05 | 0
2013-04-15 10:05 | TT9 | URBAN |  | 101 | 180 | 18180 | 0.06333 | 0.00035183 | 0
2013-04-16 13:10 | WO32 | URBAN |  | 158 | 185 | 29230 | 0.10182 | 0.00055039 | 0
2013-04-17 08:56 | WOTS12 | URBAN |  | 126 | 330 | 41580 | 0.14484 | 0.00043892 | 0
2013-04-17 11:40 | MYT7 | LONG RURAL |  | 2 | 70 | 140 | 0.00054212 | 7.7446e-06 | 0
2013-04-17 09:10 | MYT8 | SHORT RURAL |  | 9 | 101 | 909 | 0.0079101 | 7.8318e-05 | 0
2013-04-17 08:38 | BWN13 | URBAN |  | 76 | 164 | 12464 | 0.043418 | 0.00026474 | 0
2013-04-16 09:35 | FTR21 | LONG RURAL |  | 2 | 274 | 548 | 0.002122 | 7.7446e-06 | 0
2013-04-18 09:05 | PHI11 | SHORT RURAL |  | 117 | 260 | 30420 | 0.26471 | 0.0010181 | 0
2013-04-16 10:05 | PHI12 | SHORT RURAL |  | 137 | 208 | 28496 | 0.24797 | 0.0011922 | 0
2013-04-16 09:10 | MSD1 | LONG RURAL |  | 7240 | 392.7852 | 2843765 | 11.012 | 0.028036 | 0
2013-04-15 09:00 | WYK23 | SHORT RURAL |  | 108 | 165.2778 | 17850 | 0.15533 | 0.00093981 | 0
2013-04-15 10:35 | WYK11 | SHORT RURAL |  | 35 | 235 | 8225 | 0.071574 | 0.00030457 | 0
2013-04-15 09:15 | LDL24 | URBAN |  | 184 | 270 | 49680 | 0.17306 | 0.00064096 | 0
2013-04-16 09:00 | WYK24 | SHORT RURAL |  | 278 | 308 | 85624 | 0.7451 | 0.0024191 | 0
2013-04-16 08:42 | WYK23 | SHORT RURAL |  | 26 | 368 | 9568 | 0.08326 | 0.00022625 | 0
2013-04-11 12:27 | LDL11 | URBAN |  | 197 | 141.2081 | 27818 | 0.096904 | 0.00068625 | 0
2013-04-12 09:55 | WT13 | URBAN |  | 387 | 180 | 69660 | 0.24266 | 0.0013481 | 0
2013-04-17 08:55 | WYK23 | SHORT RURAL |  | 29 | 395 | 11455 | 0.099681 | 0.00025236 | 0
2013-04-17 09:00 | WYK23 | SHORT RURAL |  | 122 | 200 | 24400 | 0.21233 | 0.0010616 | 0
2013-04-06 19:20 | WT13 | URBAN |  | 32 | 25.625 | 820 | 0.0028565 | 0.00011147 | 0
2013-04-17 08:50 | LDL14 | SHORT RURAL |  | 34 | 160 | 5440 | 0.047339 | 0.00029587 | 0
2013-04-17 13:05 | WYK23 | SHORT RURAL |  | 31 | 95 | 2945 | 0.025627 | 0.00026976 | 0
2013-04-09 10:20 | MJG11 | SHORT RURAL |  | 1 | 15 | 15 | 0.00013053 | 8.702e-06 | 0
2013-04-19 09:00 | TGN12 | SHORT RURAL |  | 69 | 220 | 15180 | 0.1321 | 0.00060044 | 0
2013-04-19 09:00 | TGN23 | SHORT RURAL |  | 71 | 205 | 14555 | 0.12666 | 0.00061784 | 0
2013-04-18 09:00 | KMS21 | SHORT RURAL |  | 2 | 105 | 210 | 0.0018274 | 1.7404e-05 | 0
2013-04-16 12:33 | LGA23 | LONG RURAL |  | 66 | 137 | 9042 | 0.035013 | 0.00025557 | 0
2013-04-17 09:00 | MYT7 | LONG RURAL |  | 14 | 230 | 3220 | 0.012469 | 5.4212e-05 | 0
2013-04-17 12:57 | RWN33 | URBAN |  | 182 | 138 | 25116 | 0.087491 | 0.00063399 | 0
2013-04-16 08:51 | LGA22 | SHORT RURAL |  | 191 | 243 | 46413 | 0.40388 | 0.0016621 | 0
2013-04-17 12:12 | RWN32 | URBAN |  | 84 | 98 | 8232 | 0.028676 | 0.00029261 | 0
2013-04-17 08:20 | LDL11 | URBAN |  | 70 | 245 | 17150 | 0.059742 | 0.00024384 | 0
2013-04-16 09:05 | LGA13 | LONG RURAL |  | 55 | 5 | 275 | 0.0010649 | 0.00021298 | 0
2013-04-16 09:05 | LGA13 | LONG RURAL |  | 102 | 189.8627 | 19366 | 0.074991 | 0.00039498 | 0
2013-04-17 09:00 | LGA21 | SHORT RURAL |  | 6 | 220 | 1320 | 0.011487 | 5.2212e-05 | 0
2013-04-17 09:10 | FTR21 | LONG RURAL |  | 32 | 329 | 10528 | 0.040768 | 0.00012391 | 0
2013-04-17 09:18 | FTR23 | LONG RURAL |  | 11 | 205 | 2255 | 0.0087321 | 4.2595e-05 | 0
2013-04-18 10:00 | WO14 | URBAN |  | 96 | 188.75 | 18120 | 0.063121 | 0.00033441 | 0
2013-04-16 10:55 | OFR23 | LONG RURAL |  | 2 | 55 | 110 | 0.00042595 | 7.7446e-06 | 0
2013-04-16 08:02 | FGY14 | URBAN |  | 287 | 366 | 105042 | 0.36591 | 0.00099976 | 0
2013-04-18 09:34 | ALA01 | LONG RURAL |  | 1 | 195 | 195 | 0.0007551 | 3.8723e-06 | 0
2013-04-19 09:15 | WO33 | URBAN |  | 56 | 270 | 15120 | 0.05267 | 0.00019508 | 0
2013-04-17 12:30 | LGA23 | LONG RURAL |  | 2 | 90 | 180 | 0.00069702 | 7.7446e-06 | 0
2013-04-17 12:05 | BWN13 | URBAN |  | 93 | 75 | 6975 | 0.024297 | 0.00032396 | 0
2013-04-08 09:15 | WN2 | LONG RURAL |  | 2 | 85 | 170 | 0.00065829 | 7.7446e-06 | 0
2013-04-16 11:00 | BGE22 | SHORT RURAL |  | 108 | 420 | 45360 | 0.39472 | 0.00093981 | 0
2013-04-12 08:55 | BN1 | LONG RURAL |  | 13 | 70 | 910 | 0.0035238 | 5.034e-05 | 0
2013-04-17 10:10 | WYK11 | SHORT RURAL |  | 6 | 205 | 1230 | 0.010703 | 5.2212e-05 | 0
2013-04-17 08:15 | WYK11 | SHORT RURAL |  | 6 | 60 | 360 | 0.0031327 | 5.2212e-05 | 0
2013-04-19 09:00 | LGA13 | LONG RURAL |  | 17 | 270 | 4590 | 0.017774 | 6.5829e-05 | 0
2013-04-12 08:45 | ELM11 | URBAN |  | 107 | 305 | 32635 | 0.11368 | 0.00037273 | 0
2013-04-19 09:04 | FTR21 | LONG RURAL |  | 1 | 316 | 316 | 0.0012237 | 3.8723e-06 | 0
2013-04-15 10:45 | WT12 | URBAN |  | 3 | 210 | 630 | 0.0021946 | 1.045e-05 | 0
2013-04-19 08:45 | CLN14 | SHORT RURAL |  | 86 | 275 | 23650 | 0.2058 | 0.00074837 | 0
2013-04-16 09:55 | WT13 | URBAN |  | 187 | 365 | 68255 | 0.23777 | 0.00065141 | 0
2013-04-12 09:50 | MSD2 | LONG RURAL |  | 50 | 130 | 6500 | 0.02517 | 0.00019362 | 0
2013-04-17 10:15 | DRN12 | URBAN |  | 2 | 108 | 216 | 0.00075243 | 6.967e-06 | 0
2013-04-18 12:30 | DRN13 | SHORT RURAL |  | 102 | 70 | 7140 | 0.062132 | 0.0008876 | 0
2013-04-03 10:36 | WN6 | LONG RURAL |  | 1 | 14 | 14 | 5.4212e-05 | 3.8723e-06 | 0
2013-04-20 08:30 | RWN24 | SHORT RURAL |  | 513 | 409 | 209817 | 1.8258 | 0.0044641 | 0
2013-04-16 08:47 | DRN12 | URBAN |  | 323 | 368 | 118864 | 0.41406 | 0.0011252 | 0
2013-04-18 08:02 | ELM12 | SHORT RURAL |  | 216 | 441 | 95256 | 0.82891 | 0.0018796 | 0
2013-04-18 10:30 | ELM33 | SHORT RURAL |  | 3 | 90 | 270 | 0.0023495 | 2.6106e-05 | 0
2013-04-19 12:20 | DRN13 | SHORT RURAL |  | 48 | 130 | 6240 | 0.0543 | 0.00041769 | 0
2013-04-18 09:05 | BDL1 | LONG RURAL |  | 1 | 35 | 35 | 0.00013553 | 3.8723e-06 | 0
2013-04-18 09:12 | LDL24 | URBAN |  | 110 | 228 | 25080 | 0.087366 | 0.00038318 | 0
2013-04-14 09:22 | BWR22 | URBAN |  | 23 | 91 | 2093 | 0.0072909 | 8.012e-05 | 0
2013-04-14 08:10 | CYN13 | URBAN |  | 127 | 15 | 1905 | 0.006636 | 0.0004424 | 0
2013-04-17 08:52 | WGI23 | SHORT RURAL |  | 3 | 357 | 1071 | 0.0093198 | 2.6106e-05 | 0
2013-04-16 08:35 | BN1 | LONG RURAL |  | 181 | 365 | 66065 | 0.25582 | 0.00070089 | 0
2013-04-17 08:45 | BN1 | LONG RURAL |  | 58 | 325 | 18850 | 0.072993 | 0.00022459 | 0
2013-04-18 10:05 | BN1 | LONG RURAL |  | 9 | 50 | 450 | 0.0017425 | 3.4851e-05 | 0
2013-04-18 09:01 | WN5 | LONG RURAL |  | 1089 | 445 | 484605 | 1.8765 | 0.004217 | 0
2013-04-16 08:30 | WO32 | URBAN |  | 44 | 290 | 12760 | 0.044449 | 0.00015327 | 0
2013-04-19 08:37 | BN1 | LONG RURAL |  | 3 | 283 | 849 | 0.0032876 | 1.1617e-05 | 0
2013-04-16 09:38 | RWT22 | URBAN |  | 1052 | 352 | 370304 | 1.2899 | 0.0036646 | 0
2013-04-18 11:00 | MYT7 | LONG RURAL |  | 1 | 230 | 230 | 0.00089063 | 3.8723e-06 | 0
2013-04-19 09:10 | FTR21 | LONG RURAL |  | 3 | 242 | 726 | 0.0028113 | 1.1617e-05 | 0
2013-04-17 09:00 | FTR22 | SHORT RURAL |  | 28 | 60 | 1680 | 0.014619 | 0.00024366 | 0
2013-04-19 09:13 | FTR21 | LONG RURAL |  | 42 | 251 | 10542 | 0.040822 | 0.00016264 | 0
2013-04-17 09:07 | LLG12 | SHORT RURAL |  | 35 | 263 | 9205 | 0.080102 | 0.00030457 | 0
2013-04-17 08:42 | LLG12 | SHORT RURAL |  | 413 | 298 | 123074 | 1.071 | 0.0035939 | 0
2013-04-18 10:50 | BWR24 | URBAN |  | 102 | 170 | 17340 | 0.060404 | 0.00035532 | 0
2013-04-18 09:20 | ELD01 | SHORT RURAL |  | 2 | 361 | 722 | 0.0062828 | 1.7404e-05 | 0
2013-04-11 09:28 | MJG11 | SHORT RURAL |  | 1 | 96 | 96 | 0.00083539 | 8.702e-06 | 0
2013-04-13 08:46 | EPG23 | URBAN |  | 12 | 149 | 1788 | 0.0062285 | 4.1802e-05 | 0
2013-04-12 08:45 | MSD2 | LONG RURAL |  | 1 | 77 | 77 | 0.00029817 | 3.8723e-06 | 0
2013-04-15 10:58 | LLG14 | SHORT RURAL |  | 3 | 58 | 174 | 0.0015141 | 2.6106e-05 | 0
2013-04-18 09:00 | OFR23 | LONG RURAL |  | 74 | 117 | 8658 | 0.033526 | 0.00028655 | 0
2013-04-18 11:00 | CRE21 | SHORT RURAL |  | 3 | 40 | 120 | 0.0010442 | 2.6106e-05 | 0
2013-04-19 09:00 | OFR23 | LONG RURAL |  | 22 | 270 | 5940 | 0.023002 | 8.5191e-05 | 0
2013-04-18 08:45 | BN1 | LONG RURAL |  | 6 | 35 | 210 | 0.00081319 | 2.3234e-05 | 0
2013-04-21 09:10 | MWE2 | SHORT RURAL |  | 5 | 160 | 800 | 0.0069616 | 4.351e-05 | 0
2013-04-21 09:15 | MWE3 | URBAN |  | 8 | 164 | 1312 | 0.0045703 | 2.7868e-05 | 0
2013-04-21 10:24 | WGL11 | SHORT RURAL |  | 775 | 305.5897 | 236832 | 2.0609 | 0.006744 | 0
2013-04-10 13:30 | BDL2 | SHORT RURAL |  | 48 | 40 | 1920 | 0.016708 | 0.00041769 | 0
2013-04-10 13:30 | BDL3 | SHORT RURAL |  | 67 | 40 | 2680 | 0.023321 | 0.00058303 | 0
2013-04-18 10:46 | WGL13 | SHORT RURAL |  | 1 | 99 | 99 | 0.0008615 | 8.702e-06 | 0
2013-04-14 09:00 | SLE31 | LONG RURAL |  | 1 | 164 | 164 | 0.00063506 | 3.8723e-06 | 0
2013-04-21 09:35 | FTR21 | LONG RURAL |  | 27 | 240 | 6480 | 0.025093 | 0.00010455 | 0
2013-04-18 09:00 | MYT2 | SHORT RURAL |  | 16 | 335 | 5360 | 0.046643 | 0.00013923 | 0
2013-04-19 09:30 | WOTS11 | LONG RURAL |  | 30 | 85 | 2550 | 0.0098744 | 0.00011617 | 0
2013-04-19 08:35 | DRN13 | SHORT RURAL |  | 200 | 245 | 49000 | 0.4264 | 0.0017404 | 0
2013-04-21 09:00 | WT13 | URBAN |  | 23 | 180 | 4140 | 0.014422 | 8.012e-05 | 0
2013-04-21 09:10 | WGL11 | SHORT RURAL |  | 339 | 358.1445 | 121411 | 1.0565 | 0.00295 | 0
2013-04-19 09:00 | FTR23 | LONG RURAL |  | 55 | 420 | 23100 | 0.08945 | 0.00021298 | 0
2013-04-18 11:01 | WN4 | SHORT RURAL |  | 44 | 149 | 6556 | 0.05705 | 0.00038289 | 0
2013-04-18 11:00 | WN4 | SHORT RURAL |  | 194 | 150 | 29100 | 0.25323 | 0.0016882 | 0
2013-04-22 09:56 | FTR21 | LONG RURAL |  | 119 | 236 | 28084 | 0.10875 | 0.00046081 | 0
2013-04-22 09:40 | FTR12 | LONG RURAL |  | 12 | 150 | 1800 | 0.0069702 | 4.6468e-05 | 0
2013-04-22 10:25 | MBY11 | SHORT RURAL |  | 35 | 205 | 7175 | 0.062437 | 0.00030457 | 0
2013-04-22 10:38 | WOTS11 | LONG RURAL |  | 2 | 44 | 88 | 0.00034076 | 7.7446e-06 | 0
2013-04-22 11:20 | EPG31 | URBAN |  | 152 | 196 | 29792 | 0.10378 | 0.00052949 | 0
2013-04-22 10:15 | LGA13 | LONG RURAL |  | 1 | 125 | 125 | 0.00048404 | 3.8723e-06 | 0
2013-04-22 09:00 | LGA11 | LONG RURAL |  | 150 | 355 | 53250 | 0.2062 | 0.00058085 | 0
2013-04-22 10:32 | FTR21 | LONG RURAL |  | 1 | 235 | 235 | 0.00090999 | 3.8723e-06 | 0
2013-04-19 09:20 | WGL13 | SHORT RURAL |  | 6 | 87 | 522 | 0.0045424 | 5.2212e-05 | 0
2013-04-22 09:01 | MOE31 | LONG RURAL |  | 66 | 63 | 4158 | 0.016101 | 0.00025557 | 0
2013-04-21 10:00 | RWT11 | URBAN |  | 144 | 575 | 82800 | 0.28843 | 0.00050162 | 0
2013-04-18 13:30 | MYT2 | SHORT RURAL |  | 31 | 25 | 775 | 0.006744 | 0.00026976 | 0
2013-04-20 09:00 | ELD01 | SHORT RURAL |  | 11 | 280 | 3080 | 0.026802 | 9.5722e-05 | 0
2013-04-18 08:45 | BDL6 | SHORT RURAL |  | 8 | 315 | 2520 | 0.021929 | 6.9616e-05 | 0
2013-04-17 10:15 | FGY14 | URBAN |  | 61 | 225 | 13725 | 0.047811 | 0.00021249 | 0
2013-04-10 08:44 | BN1 | LONG RURAL |  | 3401 | 164 | 557764 | 2.1598 | 0.01317 | 0
2013-04-20 11:10 | ELD01 | SHORT RURAL |  | 3 | 155 | 465 | 0.0040464 | 2.6106e-05 | 0
2013-04-17 09:00 | HPK24 | URBAN |  | 120 | 240 | 28800 | 0.10032 | 0.00041802 | 0
2013-04-17 09:50 | BGE12 | SHORT RURAL |  | 28 | 189 | 5292 | 0.046051 | 0.00024366 | 0
2013-04-17 12:35 | HPK14 | URBAN |  | 54 | 95 | 5130 | 0.01787 | 0.00018811 | 0
2013-04-18 09:40 | WO22 | URBAN |  | 24 | 260 | 6240 | 0.021737 | 8.3604e-05 | 0
2013-04-19 10:00 | ELD01 | SHORT RURAL |  | 3 | 268 | 804 | 0.0069964 | 2.6106e-05 | 0
2013-04-19 09:32 | HPK13 | URBAN |  | 452 | 232 | 104864 | 0.36529 | 0.0015745 | 0
2013-04-18 12:29 | BRA11 | URBAN |  | 484 | 4 | 1936 | 0.006744 | 0.001686 | 0
2013-04-21 09:49 | MDI1 | SHORT RURAL |  | 56 | 387 | 21672 | 0.18859 | 0.00048731 | 0
2013-04-22 09:20 | SMR5 | LONG RURAL |  | 18 | 240 | 4320 | 0.016728 | 6.9702e-05 | 0
2013-04-19 09:00 | DRN12 | URBAN |  | 21 | 85 | 1785 | 0.006218 | 7.3153e-05 | 0
2013-04-20 08:47 | OFR23 | LONG RURAL |  | 3 | 36 | 108 | 0.00041821 | 1.1617e-05 | 0
2013-04-08 13:00 | LDL13 | SHORT RURAL |  | 1 | 29 | 29 | 0.00025236 | 8.702e-06 | 0
2013-04-23 08:35 | TGN23 | SHORT RURAL |  | 2 | 513 | 1026 | 0.0089282 | 1.7404e-05 | 0
2013-04-24 08:46 | MFA22 | LONG RURAL |  | 1494 | 1 | 1494 | 0.0057852 | 0.0057852 | 0
2013-04-23 09:15 | BDL1 | LONG RURAL |  | 70 | 250.4286 | 17530 | 0.067882 | 0.00027106 | 0
2013-04-23 10:15 | WGL13 | SHORT RURAL |  | 15 | 235 | 3525 | 0.030674 | 0.00013053 | 0
2013-04-23 09:15 | WGL11 | SHORT RURAL |  | 96 | 300 | 28800 | 0.25062 | 0.00083539 | 0
2013-04-23 10:00 | MOE21 | SHORT RURAL |  | 2 | 285 | 570 | 0.0049601 | 1.7404e-05 | 0
2013-04-23 09:10 | WGL24 | LONG RURAL |  | 2 | 240 | 480 | 0.0018587 | 7.7446e-06 | 0
2013-04-24 11:00 | WGL15 | SHORT RURAL |  | 10 | 200 | 2000 | 0.017404 | 8.702e-05 | 0
2013-04-24 11:45 | WGL15 | SHORT RURAL |  | 2 | 55 | 110 | 0.00095722 | 1.7404e-05 | 0
2013-04-24 13:00 | MWTS11 | SHORT RURAL |  | 1 | 50 | 50 | 0.0004351 | 8.702e-06 | 0
2013-04-23 09:00 | PHI11 | SHORT RURAL |  | 76 | 300 | 22800 | 0.1984 | 0.00066135 | 0
2013-04-22 12:05 | WOTS11 | LONG RURAL |  | 2 | 77 | 154 | 0.00059634 | 7.7446e-06 | 0
2013-04-23 12:55 | WO32 | URBAN |  | 71 | 165 | 11715 | 0.040809 | 0.00024733 | 0
2013-04-23 10:00 | BRT22 | SHORT RURAL |  | 4 | 110 | 440 | 0.0038289 | 3.4808e-05 | 0
2013-04-23 14:00 | KLK3 | SHORT RURAL |  | 3 | 52 | 156 | 0.0013575 | 2.6106e-05 | 0
2013-04-23 10:01 | LGA13 | LONG RURAL |  | 4 | 97 | 388 | 0.0015025 | 1.5489e-05 | 0
2013-04-23 09:00 | LGA11 | LONG RURAL |  | 33 | 304 | 10032 | 0.038847 | 0.00012779 | 0
2013-04-24 08:50 | FTR23 | LONG RURAL |  | 2 | 368 | 736 | 0.00285 | 7.7446e-06 | 0
2013-04-24 09:03 | FTR22 | SHORT RURAL |  | 452 | 256 | 115712 | 1.0069 | 0.0039333 | 0
2013-04-23 09:00 | MYT7 | LONG RURAL |  | 104 | 370 | 38480 | 0.14901 | 0.00040272 | 0
2013-04-23 09:20 | MWTS32 | SHORT RURAL |  | 200 | 369 | 73800 | 0.64221 | 0.0017404 | 0
2013-04-24 09:20 | WGL23 | SHORT RURAL |  | 3 | 35 | 105 | 0.00091371 | 2.6106e-05 | 0
2013-04-24 09:05 | TGN11 | SHORT RURAL |  | 42 | 160 | 6720 | 0.058477 | 0.00036548 | 0
2013-04-23 09:00 | LGA11 | LONG RURAL |  | 93 | 348 | 32364 | 0.12532 | 0.00036013 | 0
2013-04-24 09:00 | MYT8 | SHORT RURAL |  | 1 | 105 | 105 | 0.00091371 | 8.702e-06 | 0
2013-04-23 13:50 | BRT11 | SHORT RURAL |  | 75 | 60 | 4500 | 0.039159 | 0.00065265 | 0
2013-04-19 09:45 | RWT26 | URBAN |  | 53 | 345 | 18285 | 0.063695 | 0.00018462 | 0
2013-04-19 08:56 | BRA33 | URBAN |  | 2 | 144 | 288 | 0.0010032 | 6.967e-06 | 0
2013-04-19 09:05 | RWN24 | SHORT RURAL |  | 3 | 120 | 360 | 0.0031327 | 2.6106e-05 | 0
2013-04-20 09:06 | CYN23 | URBAN |  | 768 | 235 | 180480 | 0.6287 | 0.0026753 | 0
2013-04-21 08:30 | NRN12 | URBAN |  | 62 | 240 | 14880 | 0.051834 | 0.00021598 | 0
2013-04-11 09:20 | LGA13 | LONG RURAL |  | 3 | 305 | 915 | 0.0035432 | 1.1617e-05 | 0
2013-04-18 08:15 | LDL14 | SHORT RURAL |  | 181 | 307 | 55567 | 0.48354 | 0.0015751 | 0
2013-04-23 09:31 | FTR22 | SHORT RURAL |  | 2 | 56 | 112 | 0.00097462 | 1.7404e-05 | 0
2013-04-23 11:49 | FTR22 | SHORT RURAL |  | 1 | 61 | 61 | 0.00053082 | 8.702e-06 | 0
2013-04-24 09:25 | WT11 | URBAN |  | 76 | 235 | 17860 | 0.062215 | 0.00026474 | 0
2013-04-21 10:48 | TT12 | URBAN |  | 38 | 234 | 8892 | 0.030975 | 0.00013237 | 0
2013-04-21 08:46 | BWR13 | SHORT RURAL |  | 107 | 134 | 14338 | 0.12477 | 0.00093111 | 0
2013-04-15 09:24 | MJG11 | SHORT RURAL |  | 1 | 3196 | 3196 | 0.027811 | 8.702e-06 | 0
2013-04-15 13:00 | MSD2 | LONG RURAL |  | 2 | 78 | 156 | 0.00060408 | 7.7446e-06 | 0
2013-04-21 09:15 | RWT21 | URBAN |  | 42 | 30 | 1260 | 0.0043892 | 0.00014631 | 0
2013-04-21 12:28 | BRA13 | URBAN |  | 391 | 162 | 63342 | 0.22065 | 0.001362 | 0
2013-04-18 08:35 | LDL23 | LONG RURAL |  | 220 | 305 | 67100 | 0.25983 | 0.00085191 | 0
2013-04-17 12:19 | MJG11 | SHORT RURAL |  | 27 | 16 | 432 | 0.0037593 | 0.00023495 | 0
2013-04-18 09:00 | WYK23 | SHORT RURAL |  | 190 | 188.4842 | 35812 | 0.31163 | 0.0016534 | 0
2013-04-17 11:21 | MJG11 | SHORT RURAL |  | 54 | 32 | 1728 | 0.015037 | 0.00046991 | 0
2013-04-17 09:58 | MJG11 | SHORT RURAL |  | 2 | 32 | 64 | 0.00055693 | 1.7404e-05 | 0
2013-04-24 09:00 | WN6 | LONG RURAL |  | 28 | 326 | 9128 | 0.035346 | 0.00010842 | 0
2013-04-20 10:45 | OFR23 | LONG RURAL |  | 1 | 46 | 46 | 0.00017813 | 3.8723e-06 | 0
2013-04-22 12:05 | OFR23 | LONG RURAL |  | 2 | 80 | 160 | 0.00061957 | 7.7446e-06 | 0
2013-04-22 09:30 | LLG14 | SHORT RURAL |  | 2 | 200 | 400 | 0.0034808 | 1.7404e-05 | 0
2013-04-09 09:48 | KLK3 | SHORT RURAL |  | 1 | 47 | 47 | 0.00040899 | 8.702e-06 | 0
2013-04-10 08:35 | RWN32 | URBAN |  | 371 | 115 | 42665 | 0.14862 | 0.0012924 | 0
2013-04-09 17:07 | WGI14 | SHORT RURAL |  | 2 | 103 | 206 | 0.0017926 | 1.7404e-05 | 0
2013-04-26 09:12 | WGL11 | SHORT RURAL |  | 68 | 265 | 18020 | 0.15681 | 0.00059173 | 0
2013-04-22 13:35 | FTR12 | LONG RURAL |  | 28 | 40 | 1120 | 0.004337 | 0.00010842 | 0
2013-04-19 11:45 | KLK1 | SHORT RURAL |  | 2 | 335 | 670 | 0.0058303 | 1.7404e-05 | 0
2013-04-19 09:10 | WYK23 | SHORT RURAL |  | 34 | 135 | 4590 | 0.039942 | 0.00029587 | 0
2013-04-19 12:15 | WYK24 | SHORT RURAL |  | 2 | 60 | 120 | 0.0010442 | 1.7404e-05 | 0
2013-04-21 08:15 | CRE31 | URBAN |  | 332 | 423.9458 | 140750 | 0.4903 | 0.0011565 | 0
2013-04-23 09:15 | KLK2 | SHORT RURAL |  | 1 | 43 | 43 | 0.00037418 | 8.702e-06 | 0
2013-04-23 09:30 | KLK2 | SHORT RURAL |  | 8 | 142 | 1136 | 0.0098854 | 6.9616e-05 | 0
2013-04-23 13:00 | KLK2 | SHORT RURAL |  | 1 | 30 | 30 | 0.00026106 | 8.702e-06 | 0
2013-04-23 12:50 | KLK2 | SHORT RURAL |  | 2 | 36 | 72 | 0.00062654 | 1.7404e-05 | 0
2013-04-23 10:25 | KLK2 | SHORT RURAL |  | 1 | 57 | 57 | 0.00049601 | 8.702e-06 | 0
2013-04-23 11:50 | KLK2 | SHORT RURAL |  | 1 | 37 | 37 | 0.00032197 | 8.702e-06 | 0
2013-04-23 09:15 | LDL23 | LONG RURAL |  | 116 | 315 | 36540 | 0.14149 | 0.00044919 | 0
2013-04-23 09:05 | SMR5 | LONG RURAL |  | 33 | 275 | 9075 | 0.035141 | 0.00012779 | 0
2013-04-24 08:10 | WYK11 | SHORT RURAL |  | 7 | 250 | 1750 | 0.015228 | 6.0914e-05 | 0
2013-04-24 08:25 | WYK11 | SHORT RURAL |  | 43 | 130 | 5590 | 0.048644 | 0.00037418 | 0
2013-04-21 08:30 | BDL5 | LONG RURAL |  | 139 | 435 | 60465 | 0.23414 | 0.00053825 | 0
2013-04-24 14:05 | WYK11 | SHORT RURAL |  | 2 | 37 | 74 | 0.00064395 | 1.7404e-05 | 0
2013-04-24 12:30 | WYK11 | SHORT RURAL |  | 25 | 84 | 2100 | 0.018274 | 0.00021755 | 0
2013-04-24 09:05 | WYK11 | SHORT RURAL |  | 255 | 251 | 64005 | 0.55697 | 0.002219 | 0
2013-04-24 12:50 | WYK11 | SHORT RURAL |  | 3 | 66 | 198 | 0.001723 | 2.6106e-05 | 0
2013-04-24 14:50 | WYK23 | SHORT RURAL |  | 2 | 53 | 106 | 0.00092241 | 1.7404e-05 | 0
2013-04-24 08:40 | WYK23 | SHORT RURAL |  | 322 | 325 | 104650 | 0.91066 | 0.002802 | 0
2013-04-26 08:30 | WYK11 | SHORT RURAL |  | 102 | 215 | 21930 | 0.19083 | 0.0008876 | 0
2013-04-23 22:00 | WT13 | URBAN |  | 32 | 465 | 14880 | 0.051834 | 0.00011147 | 0
2013-04-26 09:40 | LDL24 | URBAN |  | 61 | 296 | 18056 | 0.062898 | 0.00021249 | 0
2013-05-02 09:25 | WOTS24 | LONG RURAL |  | 110 | 97 | 10670 | 0.041318 | 0.00042595 | 0
2013-04-22 10:10 | CYN24 | URBAN |  | 86 | 210 | 18060 | 0.062912 | 0.00029958 | 0
2013-04-21 09:32 | KMS1 | SHORT RURAL |  | 65 | 368 | 23920 | 0.20815 | 0.00056563 | 0
2013-04-22 10:14 | RWT22 | URBAN |  | 90 | 161 | 14490 | 0.050476 | 0.00031351 | 0
2013-04-21 09:19 | KMS1 | SHORT RURAL |  | 208 | 416 | 86528 | 0.75296 | 0.00181 | 0
2013-04-10 14:19 | BRT21 | SHORT RURAL |  | 5 | 142 | 710 | 0.0061784 | 4.351e-05 | 0
2013-04-27 09:50 | ELM33 | SHORT RURAL |  | 10 | 65 | 650 | 0.0056563 | 8.702e-05 | 0
2013-04-22 09:45 | BRA11 | URBAN |  | 353 | 338 | 119314 | 0.41563 | 0.0012297 | 0
2013-04-26 12:25 | WYK11 | SHORT RURAL |  | 1 | 39 | 39 | 0.00033938 | 8.702e-06 | 0
2013-04-24 09:40 | WT11 | URBAN |  | 205 | 352 | 72160 | 0.25137 | 0.00071411 | 0
2013-04-23 09:15 | KMS1 | SHORT RURAL |  | 65 | 255 | 16575 | 0.14424 | 0.00056563 | 0
2013-04-26 09:32 | WGL13 | SHORT RURAL |  | 2 | 148 | 296 | 0.0025758 | 1.7404e-05 | 0
2013-04-24 09:10 | WOTS13 | LONG RURAL |  | 22 | 315 | 6930 | 0.026835 | 8.5191e-05 | 0
2013-04-18 09:00 | CRE21 | SHORT RURAL |  | 88 | 300 | 26400 | 0.22973 | 0.00076577 | 0
2013-04-22 10:00 | OFR23 | LONG RURAL |  | 5 | 240 | 1200 | 0.0046468 | 1.9362e-05 | 0
2013-04-22 11:15 | OFR23 | LONG RURAL |  | 1 | 35 | 35 | 0.00013553 | 3.8723e-06 | 0
2013-04-24 09:20 | ELM33 | SHORT RURAL |  | 101 | 571.7822 | 57750 | 0.50254 | 0.0008789 | 0
2013-04-23 08:12 | WYK11 | SHORT RURAL |  | 4 | 248 | 992 | 0.0086324 | 3.4808e-05 | 0
2013-04-23 12:13 | WYK11 | SHORT RURAL |  | 10 | 27 | 270 | 0.0023495 | 8.702e-05 | 0
2013-04-24 08:52 | WYK24 | SHORT RURAL |  | 3 | 175 | 525 | 0.0045685 | 2.6106e-05 | 0
2013-04-27 08:30 | WYK12 | SHORT RURAL |  | 39 | 507 | 19773 | 0.17206 | 0.00033938 | 0
2013-04-23 10:04 | CRE33 | SHORT RURAL |  | 95 | 47 | 4465 | 0.038854 | 0.00082669 | 0
2013-04-23 10:03 | LLG14 | SHORT RURAL |  | 1 | 97 | 97 | 0.00084409 | 8.702e-06 | 0
2013-04-24 08:30 | BGE11 | SHORT RURAL |  | 186 | 447 | 83142 | 0.7235 | 0.0016186 | 0
2013-04-23 11:10 | CRE33 | SHORT RURAL |  | 41 | 60 | 2460 | 0.021407 | 0.00035678 | 0
2013-04-23 12:25 | CRE33 | SHORT RURAL |  | 2 | 71 | 142 | 0.0012357 | 1.7404e-05 | 0
2013-04-22 08:45 | WN5 | LONG RURAL |  | 43 | 367 | 15781 | 0.061109 | 0.00016651 | 0
2013-04-24 08:43 | SFS1 | SHORT RURAL |  | 283 | 522 | 147726 | 1.2855 | 0.0024627 | 0
2013-04-24 09:20 | BWN13 | URBAN |  | 115 | 207 | 23805 | 0.082924 | 0.0004006 | 0
2013-04-24 09:30 | BGE22 | SHORT RURAL |  | 23 | 270 | 6210 | 0.054039 | 0.00020015 | 0
2013-04-24 10:37 | LLG11 | SHORT RURAL |  | 40 | 48 | 1920 | 0.016708 | 0.00034808 | 0
2013-04-23 12:05 | LLG14 | SHORT RURAL |  | 20 | 115 | 2300 | 0.020015 | 0.00017404 | 0
2013-04-23 10:00 | LLG14 | SHORT RURAL |  | 42 | 240 | 10080 | 0.087716 | 0.00036548 | 0
2013-04-23 13:05 | LLG14 | SHORT RURAL |  | 17 | 72 | 1224 | 0.010651 | 0.00014793 | 0
2013-04-26 09:05 | PHM34 | URBAN |  | 64 | 583 | 37312 | 0.12998 | 0.00022294 | 0
2013-04-27 09:00 | CLN21 | SHORT RURAL |  | 2 | 345 | 690 | 0.0060044 | 1.7404e-05 | 0
2013-04-23 09:15 | BWR32 | URBAN |  | 18 | 365 | 6570 | 0.022886 | 6.2703e-05 | 0
2013-04-22 13:01 | BRA21 | URBAN |  | 40 | 169 | 6760 | 0.023548 | 0.00013934 | 0
2013-04-23 08:36 | CYN32 | URBAN |  | 596 | 276 | 164496 | 0.57302 | 0.0020762 | 0
2013-04-23 09:00 | BRA21 | URBAN |  | 17 | 540 | 9180 | 0.031978 | 5.9219e-05 | 0
2013-04-23 12:05 | CYN23 | URBAN |  | 375 | 205 | 76875 | 0.26779 | 0.0013063 | 0
2013-04-27 12:30 | ELM33 | SHORT RURAL |  | 2 | 115 | 230 | 0.0020015 | 1.7404e-05 | 0
2013-04-28 09:00 | WT13 | URBAN |  | 13 | 183 | 2379 | 0.0082872 | 4.5285e-05 | 0
2013-04-28 08:45 | CLN23 | SHORT RURAL |  | 35 | 417 | 14595 | 0.12701 | 0.00030457 | 0
2013-04-26 09:40 | RWT14 | URBAN |  | 86 | 115 | 9890 | 0.034452 | 0.00029958 | 0
2013-04-24 10:00 | BDL2 | SHORT RURAL |  | 62 | 280 | 17360 | 0.15107 | 0.00053952 | 0
2013-04-23 08:33 | BDL5 | LONG RURAL |  | 4 | 197 | 788 | 0.0030514 | 1.5489e-05 | 0
2013-04-23 12:07 | KMS1 | SHORT RURAL |  | 7 | 139 | 973 | 0.008467 | 6.0914e-05 | 0
2013-04-23 09:00 | BDL5 | LONG RURAL |  | 5 | 305 | 1525 | 0.0059053 | 1.9362e-05 | 0
2013-04-24 08:50 | BDL6 | SHORT RURAL |  | 36 | 190 | 6840 | 0.059521 | 0.00031327 | 0
2013-04-24 11:32 | DRN11 | URBAN |  | 248 | 160.1492 | 39717 | 0.13835 | 0.0008639 | 0
2013-04-24 10:54 | ELD01 | SHORT RURAL |  | 6 | 27 | 162 | 0.0014097 | 5.2212e-05 | 0
2013-04-22 10:55 | CYN23 | URBAN |  | 159 | 149 | 23691 | 0.082527 | 0.00055387 | 0
2013-04-29 08:40 | LGA11 | LONG RURAL |  | 26 | 104 | 2704 | 0.010471 | 0.00010068 | 0
2013-04-29 10:45 | LGA13 | LONG RURAL |  | 1 | 90 | 90 | 0.00034851 | 3.8723e-06 | 0
2013-04-29 09:15 | LGA13 | LONG RURAL |  | 1 | 70 | 70 | 0.00027106 | 3.8723e-06 | 0
2013-04-28 13:30 | WT13 | URBAN |  | 4 | 135 | 540 | 0.0018811 | 1.3934e-05 | 0
2013-04-29 09:30 | EPG31 | URBAN |  | 121 | 120 | 14520 | 0.05058 | 0.0004215 | 0
2013-04-29 10:35 | WOTS11 | LONG RURAL |  | 61 | 240 | 14640 | 0.056691 | 0.00023621 | 0
2013-04-29 07:10 | BN1 | LONG RURAL |  | 1 | 105 | 105 | 0.00040659 | 3.8723e-06 | 0
2013-05-03 09:00 | WOTS24 | LONG RURAL |  | 61 | 60 | 3660 | 0.014173 | 0.00023621 | 0
2013-04-26 09:05 | KLK1 | SHORT RURAL |  | 1 | 43 | 43 | 0.00037418 | 8.702e-06 | 0
2013-04-26 13:03 | KLK1 | SHORT RURAL |  | 1 | 32 | 32 | 0.00027846 | 8.702e-06 | 0
2013-04-26 12:38 | KLK1 | SHORT RURAL |  | 3 | 78 | 234 | 0.0020363 | 2.6106e-05 | 0
2013-04-26 09:36 | KLK1 | SHORT RURAL |  | 2 | 48 | 96 | 0.00083539 | 1.7404e-05 | 0
2013-04-26 10:07 | KLK1 | SHORT RURAL |  | 1 | 129 | 129 | 0.0011226 | 8.702e-06 | 0
2013-04-26 09:40 | KLO14 | LONG RURAL |  | 4 | 238 | 952 | 0.0036864 | 1.5489e-05 | 0
2013-04-23 10:05 | WYK11 | SHORT RURAL |  | 19 | 20 | 380 | 0.0033067 | 0.00016534 | 0
2013-04-26 10:55 | KLK2 | SHORT RURAL |  | 2 | 30 | 60 | 0.00052212 | 1.7404e-05 | 0
2013-04-23 09:15 | WN5 | LONG RURAL |  | 11 | 355 | 3905 | 0.015121 | 4.2595e-05 | 0
2013-04-15 09:20 | MSD2 | LONG RURAL |  | 1 | 139 | 139 | 0.00053825 | 3.8723e-06 | 0
2013-04-30 09:05 | BRA14 | URBAN |  | 165 | 165 | 27225 | 0.094838 | 0.00057477 | 0
2013-04-30 13:00 | BRA14 | URBAN |  | 73 | 150 | 10950 | 0.038144 | 0.00025429 | 0
2013-04-29 13:18 | MWTS32 | SHORT RURAL |  | 1 | 97 | 97 | 0.00084409 | 8.702e-06 | 0
2013-04-29 10:57 | LGA11 | LONG RURAL |  | 12 | 35 | 420 | 0.0016264 | 4.6468e-05 | 0
2013-04-29 12:20 | LGA11 | LONG RURAL |  | 1 | 92 | 92 | 0.00035625 | 3.8723e-06 | 0
2013-04-29 13:35 | LGA13 | LONG RURAL |  | 2 | 55 | 110 | 0.00042595 | 7.7446e-06 | 0
2013-04-29 13:25 | LGA13 | LONG RURAL |  | 1 | 43 | 43 | 0.00016651 | 3.8723e-06 | 0
2013-04-30 09:20 | LGA13 | LONG RURAL |  | 4 | 120 | 480 | 0.0018587 | 1.5489e-05 | 0
2013-05-01 10:45 | WGL15 | SHORT RURAL |  | 23 | 55 | 1265 | 0.011008 | 0.00020015 | 0
2013-05-01 09:01 | LLG12 | SHORT RURAL |  | 20 | 234 | 4680 | 0.040725 | 0.00017404 | 0
2013-05-01 09:00 | WGI14 | SHORT RURAL |  | 781 | 115 | 89815 | 0.78157 | 0.0067962 | 0
2013-05-01 09:40 | LGA13 | LONG RURAL |  | 9 | 245 | 2205 | 0.0085385 | 3.4851e-05 | 0
2013-04-29 12:50 | DRN11 | URBAN |  | 3 | 90 | 270 | 0.00094054 | 1.045e-05 | 0
2013-04-30 09:20 | DRN11 | URBAN |  | 1 | 150 | 150 | 0.00052252 | 3.4835e-06 | 0
2013-04-30 09:05 | ELM34 | URBAN |  | 5 | 175 | 875 | 0.003048 | 1.7417e-05 | 0
2013-04-30 12:40 | DRN11 | URBAN |  | 2 | 100 | 200 | 0.0006967 | 6.967e-06 | 0
2013-05-02 09:45 | DRN11 | URBAN |  | 2 | 155 | 310 | 0.0010799 | 6.967e-06 | 0
2013-04-30 08:50 | SLE31 | LONG RURAL |  | 8 | 370 | 2960 | 0.011462 | 3.0979e-05 | 0
2013-04-30 08:00 | SLE31 | LONG RURAL |  | 538 | 463 | 249094 | 0.96457 | 0.0020833 | 0
2013-05-01 09:55 | LGA22 | SHORT RURAL |  | 142 | 239 | 33938 | 0.29533 | 0.0012357 | 0
2013-05-02 09:49 | FTR21 | LONG RURAL |  | 240 | 262 | 62880 | 0.24349 | 0.00092936 | 0
2013-05-01 08:13 | BDL1 | LONG RURAL |  | 81 | 325 | 26325 | 0.10194 | 0.00031366 | 0
2013-05-02 09:10 | TGN14 | LONG RURAL |  | 103 | 270 | 27810 | 0.10769 | 0.00039885 | 0
2013-05-02 09:10 | TGN14 | LONG RURAL |  | 103 | 440 | 45320 | 0.17549 | 0.00039885 | 0
2013-05-01 09:00 | WOTS11 | LONG RURAL |  | 8 | 168 | 1344 | 0.0052044 | 3.0979e-05 | 0
2013-04-30 10:50 | WGL11 | SHORT RURAL |  | 79 | 150 | 11850 | 0.10312 | 0.00068746 | 0
2013-05-02 09:20 | WGL15 | SHORT RURAL |  | 5 | 210 | 1050 | 0.0091371 | 4.351e-05 | 0
2013-05-01 09:25 | WGI33 | SHORT RURAL |  | 200 | 425 | 85000 | 0.73967 | 0.0017404 | 0
2013-05-02 09:00 | WO32 | URBAN |  | 80 | 209 | 16720 | 0.058244 | 0.00027868 | 0
2013-05-01 09:00 | WGI33 | SHORT RURAL |  | 257 | 290 | 74530 | 0.64856 | 0.0022364 | 0
2013-05-01 09:20 | WOTS24 | LONG RURAL |  | 76 | 175 | 13300 | 0.051502 | 0.0002943 | 0
2013-04-30 08:35 | WYK23 | SHORT RURAL |  | 27 | 345 | 9315 | 0.081059 | 0.00023495 | 0
2013-04-30 10:02 | WYK11 | SHORT RURAL |  | 10 | 36 | 360 | 0.0031327 | 8.702e-05 | 0
2013-04-30 13:00 | WYK11 | SHORT RURAL |  | 1 | 50 | 50 | 0.0004351 | 8.702e-06 | 0
2013-04-30 11:00 | WYK11 | SHORT RURAL |  | 1 | 30 | 30 | 0.00026106 | 8.702e-06 | 0
2013-04-30 10:00 | WYK11 | SHORT RURAL |  | 7 | 43 | 301 | 0.0026193 | 6.0914e-05 | 0
2013-04-30 08:35 | WYK24 | SHORT RURAL |  | 223 | 300 | 66900 | 0.58216 | 0.0019405 | 0
2013-04-30 08:35 | WYK24 | SHORT RURAL |  | 61 | 300 | 18300 | 0.15925 | 0.00053082 | 0
2013-04-30 09:25 | RWN24 | SHORT RURAL |  | 386 | 276 | 106536 | 0.92707 | 0.003359 | 0
2013-05-02 09:00 | ELM15 | SHORT RURAL |  | 44 | 290 | 12760 | 0.11104 | 0.00038289 | 0
2013-04-30 12:10 | WYK11 | SHORT RURAL |  | 11 | 55 | 605 | 0.0052647 | 9.5722e-05 | 0
2013-04-30 13:40 | WYK11 | SHORT RURAL |  | 2 | 55 | 110 | 0.00095722 | 1.7404e-05 | 0
2013-04-30 09:30 | BRT21 | SHORT RURAL |  | 8 | 260 | 2080 | 0.0181 | 6.9616e-05 | 0
2013-05-01 09:00 | WO22 | URBAN |  | 57 | 60 | 3420 | 0.011914 | 0.00019856 | 0
2013-05-01 13:40 | WOTS24 | LONG RURAL |  | 14 | 80 | 1120 | 0.004337 | 5.4212e-05 | 0
2013-05-02 09:00 | LDL23 | LONG RURAL |  | 68 | 300 | 20400 | 0.078995 | 0.00026332 | 0
2013-05-01 12:20 | WYK11 | SHORT RURAL |  | 4 | 47 | 188 | 0.001636 | 3.4808e-05 | 0
2013-05-01 08:10 | WYK11 | SHORT RURAL |  | 3 | 35 | 105 | 0.00091371 | 2.6106e-05 | 0
2013-04-30 09:15 | WGL11 | SHORT RURAL |  | 62 | 140 | 8680 | 0.075533 | 0.00053952 | 0
2013-05-02 09:05 | LGA11 | LONG RURAL |  | 46 | 475 | 21850 | 0.08461 | 0.00017813 | 0
2013-05-02 10:08 | ELM33 | SHORT RURAL |  | 72 | 132 | 9504 | 0.082704 | 0.00062654 | 0
2013-05-02 09:30 | DRN12 | URBAN |  | 12 | 60 | 720 | 0.0025081 | 4.1802e-05 | 0
2013-05-02 09:00 | DRN12 | URBAN |  | 135 | 207 | 27945 | 0.097346 | 0.00047027 | 0
2013-04-28 08:30 | OFR23 | LONG RURAL |  | 1 | 55 | 55 | 0.00021298 | 3.8723e-06 | 0
2013-04-28 10:10 | OFR23 | LONG RURAL |  | 1 | 153 | 153 | 0.00059246 | 3.8723e-06 | 0
2013-04-28 10:30 | OFR23 | LONG RURAL |  | 2 | 108 | 216 | 0.00083642 | 7.7446e-06 | 0
2013-05-01 10:00 | WYK12 | SHORT RURAL |  | 2 | 60 | 120 | 0.0010442 | 1.7404e-05 | 0
2013-05-01 11:22 | WYK12 | SHORT RURAL |  | 6 | 143 | 858 | 0.0074663 | 5.2212e-05 | 0
2013-04-29 11:03 | HPK22 | URBAN |  | 1 | 237 | 237 | 0.00082559 | 3.4835e-06 | 0
2013-05-01 09:20 | SLE31 | LONG RURAL |  | 2 | 160 | 320 | 0.0012391 | 7.7446e-06 | 0
2013-04-27 09:28 | KLK1 | SHORT RURAL |  | 1 | 62 | 62 | 0.00053952 | 8.702e-06 | 0
2013-04-27 08:54 | KLK1 | SHORT RURAL |  | 2 | 19 | 38 | 0.00033067 | 1.7404e-05 | 0
2013-04-27 10:50 | KLK1 | SHORT RURAL |  | 4 | 16 | 64 | 0.00055693 | 3.4808e-05 | 0
2013-04-27 12:30 | KLK1 | SHORT RURAL |  | 2 | 17 | 34 | 0.00029587 | 1.7404e-05 | 0
2013-04-29 09:00 | LLG13 | SHORT RURAL |  | 1 | 35 | 35 | 0.00030457 | 8.702e-06 | 0
2013-05-02 09:07 | RWT25 | URBAN |  | 616 | 123 | 75768 | 0.26394 | 0.0021458 | 0
2013-04-27 11:20 | KLK1 | SHORT RURAL |  | 1 | 55 | 55 | 0.00047861 | 8.702e-06 | 0
2013-04-27 10:50 | KLK1 | SHORT RURAL |  | 1 | 65 | 65 | 0.00056563 | 8.702e-06 | 0
2013-05-02 08:45 | LDL23 | LONG RURAL |  | 36 | 423.5833 | 15249 | 0.059049 | 0.0001394 | 0
2013-04-29 09:45 | KLO24 | SHORT RURAL |  | 102 | 315 | 32130 | 0.27959 | 0.0008876 | 0
2013-04-29 10:00 | SMR5 | LONG RURAL |  | 2 | 120 | 240 | 0.00092936 | 7.7446e-06 | 0
2013-04-30 08:55 | LLG14 | SHORT RURAL |  | 65 | 250 | 16250 | 0.14141 | 0.00056563 | 0
2013-05-01 13:45 | PHM14 | LONG RURAL |  | 1 | 90 | 90 | 0.00034851 | 3.8723e-06 | 0
2013-05-01 11:03 | PHM14 | LONG RURAL |  | 3 | 127 | 381 | 0.0014754 | 1.1617e-05 | 0
2013-04-17 10:00 | BN6 | LONG RURAL |  | 39 | 300 | 11700 | 0.045306 | 0.00015102 | 0
2013-05-03 09:00 | TGN14 | LONG RURAL |  | 46 | 343 | 15778 | 0.061097 | 0.00017813 | 0
2013-05-02 13:00 | LLG12 | SHORT RURAL |  | 25 | 125 | 3125 | 0.027194 | 0.00021755 | 0
2013-05-03 09:00 | WGL24 | LONG RURAL |  | 5 | 162 | 810 | 0.0031366 | 1.9362e-05 | 0
2013-05-03 09:25 | MWTS14 | SHORT RURAL |  | 2 | 230 | 460 | 0.0040029 | 1.7404e-05 | 0
2013-05-03 09:15 | WGL21 | LONG RURAL |  | 1 | 205 | 205 | 0.00079382 | 3.8723e-06 | 0
2013-05-03 09:00 | WO31 | URBAN |  | 31 | 40 | 1240 | 0.0043195 | 0.00010799 | 0
2013-05-03 09:05 | LLG12 | SHORT RURAL |  | 3 | 40 | 120 | 0.0010442 | 2.6106e-05 | 0
2013-05-03 09:00 | LLG12 | SHORT RURAL |  | 5 | 178 | 890 | 0.0077448 | 4.351e-05 | 0
2013-05-03 09:00 | LGA13 | LONG RURAL |  | 103 | 247 | 25441 | 0.098516 | 0.00039885 | 0
2013-05-03 09:35 | LGA21 | SHORT RURAL |  | 6 | 45 | 270 | 0.0023495 | 5.2212e-05 | 0
2013-05-03 09:50 | DRN11 | URBAN |  | 1 | 180 | 180 | 0.00062703 | 3.4835e-06 | 0
2013-05-02 13:30 | DRN11 | URBAN |  | 1 | 14 | 14 | 4.8769e-05 | 3.4835e-06 | 0
2013-05-02 12:40 | ELM33 | SHORT RURAL |  | 75 | 160 | 12000 | 0.10442 | 0.00065265 | 0
2013-05-03 09:28 | ELM33 | SHORT RURAL |  | 72 | 113 | 8136 | 0.070799 | 0.00062654 | 0
2013-05-03 09:15 | WYK12 | SHORT RURAL |  | 50 | 155 | 7750 | 0.06744 | 0.0004351 | 0
2013-04-30 09:44 | BDL5 | LONG RURAL |  | 3 | 256 | 768 | 0.0029739 | 1.1617e-05 | 0
2013-04-30 09:00 | KMS1 | SHORT RURAL |  | 1 | 190 | 190 | 0.0016534 | 8.702e-06 | 0
2013-04-30 10:00 | SMR8 | LONG RURAL |  | 2 | 210 | 420 | 0.0016264 | 7.7446e-06 | 0
2013-05-03 09:05 | CLN14 | SHORT RURAL |  | 374 | 27 | 10098 | 0.087872 | 0.0032545 | 0
2013-05-02 14:43 | DRN12 | URBAN |  | 1 | 45 | 45 | 0.00015676 | 3.4835e-06 | 0
2013-04-29 09:14 | WGL13 | SHORT RURAL |  | 5 | 113 | 565 | 0.0049166 | 4.351e-05 | 0
2013-05-02 08:55 | DRN12 | URBAN |  | 9 | 109 | 981 | 0.0034173 | 3.1351e-05 | 0
2013-04-29 11:50 | WGL13 | SHORT RURAL |  | 2 | 90 | 180 | 0.0015664 | 1.7404e-05 | 0
2013-05-02 09:10 | DRN12 | URBAN |  | 1 | 40 | 40 | 0.00013934 | 3.4835e-06 | 0
2013-05-03 09:00 | BDL2 | SHORT RURAL |  | 8 | 85 | 680 | 0.0059173 | 6.9616e-05 | 0
2013-05-01 09:25 | MWTS32 | SHORT RURAL |  | 667 | 335 | 223445 | 1.9444 | 0.0058042 | 0
2013-05-02 13:15 | ELM33 | SHORT RURAL |  | 1 | 37 | 37 | 0.00032197 | 8.702e-06 | 0
2013-05-02 10:00 | BDL5 | LONG RURAL |  | 143 | 335 | 47905 | 0.1855 | 0.00055374 | 0
2013-04-30 12:07 | HPK14 | URBAN |  | 4 | 78 | 312 | 0.0010868 | 1.3934e-05 | 0
2013-05-02 10:10 | DRN12 | URBAN |  | 1 | 30 | 30 | 0.0001045 | 3.4835e-06 | 0
2013-04-30 08:45 | MYT7 | LONG RURAL |  | 33 | 205 | 6765 | 0.026196 | 0.00012779 | 0
2013-05-01 08:45 | BGE22 | SHORT RURAL |  | 108 | 444.4444 | 48000 | 0.41769 | 0.00093981 | 0
2013-05-02 11:07 | DRN12 | URBAN |  | 2 | 103 | 206 | 0.0007176 | 6.967e-06 | 0
2013-05-02 11:13 | DRN12 | URBAN |  | 1 | 67 | 67 | 0.00023339 | 3.4835e-06 | 0
2013-05-02 13:18 | ELM33 | SHORT RURAL |  | 2 | 25 | 50 | 0.0004351 | 1.7404e-05 | 0
2013-05-02 13:00 | DRN12 | URBAN |  | 1 | 68 | 68 | 0.00023688 | 3.4835e-06 | 0
2013-05-02 14:12 | ELM33 | SHORT RURAL |  | 1 | 16 | 16 | 0.00013923 | 8.702e-06 | 0
2013-04-30 09:10 | MYT7 | LONG RURAL |  | 79 | 305 | 24095 | 0.093303 | 0.00030591 | 0
2013-05-02 09:15 | LGA13 | LONG RURAL |  | 41 | 240 | 9840 | 0.038104 | 0.00015876 | 0
2013-05-02 08:45 | DRN12 | URBAN |  | 1 | 67 | 67 | 0.00023339 | 3.4835e-06 | 0
2013-05-02 10:15 | DRN12 | URBAN |  | 1 | 36 | 36 | 0.00012541 | 3.4835e-06 | 0
2013-04-30 09:20 | RWN26 | SHORT RURAL |  | 108 | 381 | 41148 | 0.35807 | 0.00093981 | 0
2013-05-03 09:00 | ELM33 | SHORT RURAL |  | 2 | 210 | 420 | 0.0036548 | 1.7404e-05 | 0
2013-05-02 09:15 | SLE31 | LONG RURAL |  | 1 | 300 | 300 | 0.0011617 | 3.8723e-06 | 0
2013-04-29 08:45 | WT12 | URBAN |  | 353 | 405.1275 | 143010 | 0.49817 | 0.0012297 | 0
2013-04-30 09:00 | BN1 | LONG RURAL |  | 1 | 100 | 100 | 0.00038723 | 3.8723e-06 | 0
2013-04-18 09:00 | LGA23 | LONG RURAL |  | 69 | 363 | 25047 | 0.09699 | 0.00026719 | 0
2013-05-03 13:00 | LLG12 | SHORT RURAL |  | 1 | 25 | 25 | 0.00021755 | 8.702e-06 | 0
2013-05-03 10:38 | LLG12 | SHORT RURAL |  | 1 | 48 | 48 | 0.00041769 | 8.702e-06 | 0
2013-05-03 11:10 | WYK11 | SHORT RURAL |  | 1 | 170 | 170 | 0.0014793 | 8.702e-06 | 0
2013-05-03 13:40 | WYK12 | SHORT RURAL |  | 2 | 40 | 80 | 0.00069616 | 1.7404e-05 | 0
2013-05-03 13:50 | CRE22 | URBAN |  | 152 | 30 | 4560 | 0.015885 | 0.00052949 | 0
2013-05-03 13:00 | ELM33 | SHORT RURAL |  | 1 | 60 | 60 | 0.00052212 | 8.702e-06 | 0
2013-05-02 08:30 | MFA21 | LONG RURAL |  | 36 | 360 | 12960 | 0.050185 | 0.0001394 | 0
2013-05-02 14:00 | DRN13 | SHORT RURAL |  | 16 | 4 | 64 | 0.00055693 | 0.00013923 | 0
2013-05-03 12:30 | WGL23 | SHORT RURAL |  | 2 | 45 | 90 | 0.00078318 | 1.7404e-05 | 0
2013-04-27 08:40 | BRA32 | URBAN |  | 91 | 215 | 19565 | 0.068154 | 0.000317 | 0
2013-05-01 08:30 | RWT25 | URBAN |  | 35 | 66 | 2310 | 0.0080468 | 0.00012192 | 0
2013-05-03 10:08 | DRN11 | URBAN |  | 31 | 217 | 6727 | 0.023433 | 0.00010799 | 0
2013-04-30 10:00 | WN2 | LONG RURAL |  | 7 | 336 | 2352 | 0.0091077 | 2.7106e-05 | 0
2013-05-02 08:31 | WN6 | LONG RURAL |  | 1 | 39 | 39 | 0.00015102 | 3.8723e-06 | 0
2013-05-01 08:47 | BWN12 | URBAN |  | 121 | 286 | 34606 | 0.12055 | 0.0004215 | 0
2013-05-02 08:40 | PHM14 | LONG RURAL |  | 33 | 160 | 5280 | 0.020446 | 0.00012779 | 0
2013-05-05 08:57 | MOE21 | SHORT RURAL |  | 2 | 186 | 372 | 0.0032371 | 1.7404e-05 | 0
2013-05-05 09:20 | LDL12 | URBAN |  | 25 | 340 | 8500 | 0.02961 | 8.7087e-05 | 0
2013-05-05 09:30 | ELM33 | SHORT RURAL |  | 13 | 75 | 975 | 0.0084844 | 0.00011313 | 0
2013-05-05 08:00 | WGL11 | SHORT RURAL |  | 239 | 240 | 57360 | 0.49915 | 0.0020798 | 0
2013-05-05 08:30 | CYN14 | URBAN |  | 118 | 125 | 14750 | 0.051381 | 0.00041105 | 0
2013-05-03 08:40 | MFA21 | LONG RURAL |  | 14 | 290 | 4060 | 0.015722 | 5.4212e-05 | 0
2013-04-24 09:35 | WN5 | LONG RURAL |  | 20 | 379 | 7580 | 0.029352 | 7.7446e-05 | 0
2013-05-01 08:32 | EPG12 | URBAN |  | 89 | 509.6292 | 45357 | 0.158 | 0.00031003 | 0
2013-05-07 08:30 | WO32 | URBAN |  | 112 | 385 | 43120 | 0.15021 | 0.00039015 | 0
2013-05-03 08:57 | KLK3 | SHORT RURAL |  | 2 | 29 | 58 | 0.00050471 | 1.7404e-05 | 0
2013-05-03 10:10 | KLK3 | SHORT RURAL |  | 3 | 15 | 45 | 0.00039159 | 2.6106e-05 | 0
2013-05-03 08:44 | KLK3 | SHORT RURAL |  | 3 | 21 | 63 | 0.00054822 | 2.6106e-05 | 0
2013-05-10 08:35 | WO32 | URBAN |  | 83 | 388 | 32204 | 0.11218 | 0.00028913 | 0
2013-05-03 10:33 | KLK3 | SHORT RURAL |  | 1 | 24 | 24 | 0.00020885 | 8.702e-06 | 0
2013-05-02 09:48 | WN3 | LONG RURAL |  | 85 | 224 | 19040 | 0.073729 | 0.00032915 | 0
2013-04-27 11:45 | KLK1 | SHORT RURAL |  | 1 | 32 | 32 | 0.00027846 | 8.702e-06 | 0
2013-05-02 09:30 | ELM33 | SHORT RURAL |  | 279 | 515 | 143685 | 1.2503 | 0.0024278 | 0
2013-05-04 08:00 | BWR13 | SHORT RURAL |  | 245 | 187 | 45815 | 0.39868 | 0.002132 | 0
2013-05-05 09:27 | RWN22 | URBAN |  | 70 | 173 | 12110 | 0.042185 | 0.00024384 | 0
2013-04-28 08:45 | FGY34 | URBAN |  | 151 | 195 | 29445 | 0.10257 | 0.00052601 | 0
2013-05-02 10:10 | BN1 | LONG RURAL |  | 1 | 110 | 110 | 0.00042595 | 3.8723e-06 | 0
2013-05-02 09:31 | BN1 | LONG RURAL |  | 46 | 224 | 10304 | 0.0399 | 0.00017813 | 0
2013-05-03 09:46 | KLK3 | SHORT RURAL |  | 1 | 20 | 20 | 0.00017404 | 8.702e-06 | 0
2013-05-02 14:27 | WN3 | LONG RURAL |  | 2 | 48 | 96 | 0.00037174 | 7.7446e-06 | 0
2013-05-03 09:10 | WN4 | SHORT RURAL |  | 164 | 280 | 45920 | 0.39959 | 0.0014271 | 0
2013-05-06 09:40 | WGI22 | LONG RURAL |  | 4 | 165 | 660 | 0.0025557 | 1.5489e-05 | 0
2013-05-06 09:15 | WGL23 | SHORT RURAL |  | 10 | 300 | 3000 | 0.026106 | 8.702e-05 | 0
2013-05-06 09:00 | ELM15 | SHORT RURAL |  | 89 | 355 | 31595 | 0.27494 | 0.00077448 | 0
2013-05-06 09:30 | ELM13 | URBAN |  | 46 | 179 | 8234 | 0.028683 | 0.00016024 | 0
2013-05-06 09:30 | MBY12 | SHORT RURAL |  | 2 | 60 | 120 | 0.0010442 | 1.7404e-05 | 0
2013-05-05 11:15 | ELM33 | SHORT RURAL |  | 65 | 75 | 4875 | 0.042422 | 0.00056563 | 0
2013-05-06 11:00 | LDL11 | URBAN |  | 222 | 158.9865 | 35295 | 0.12295 | 0.00077333 | 0
2013-05-05 13:35 | WGL23 | SHORT RURAL |  | 6 | 55 | 330 | 0.0028717 | 5.2212e-05 | 0
2013-05-06 09:15 | WGL11 | SHORT RURAL |  | 21 | 135 | 2835 | 0.02467 | 0.00018274 | 0
2013-05-06 10:00 | WYK11 | SHORT RURAL |  | 576 | 483 | 278208 | 2.421 | 0.0050123 | 0
2013-05-05 12:45 | WT15 | URBAN |  | 72 | 45 | 3240 | 0.011286 | 0.00025081 | 0
2013-05-06 12:15 | WYK24 | SHORT RURAL |  | 1 | 70 | 70 | 0.00060914 | 8.702e-06 | 0
2013-05-06 09:40 | WYK24 | SHORT RURAL |  | 5 | 150 | 750 | 0.0065265 | 4.351e-05 | 0
2013-05-06 09:25 | ELM32 | URBAN |  | 79 | 101 | 7979 | 0.027795 | 0.0002752 | 0
2013-05-06 10:42 | KLO14 | LONG RURAL |  | 389 | 70.4833 | 27418 | 0.10617 | 0.0015063 | 0
2013-05-05 10:05 | BWR12 | URBAN |  | 1 | 105 | 105 | 0.00036577 | 3.4835e-06 | 0
2013-05-05 12:00 | BWR33 | URBAN |  | 14 | 135 | 1890 | 0.0065838 | 4.8769e-05 | 0
2013-05-06 09:08 | RWN24 | SHORT RURAL |  | 7 | 422 | 2954 | 0.025706 | 6.0914e-05 | 0
2013-05-06 09:30 | ALA01 | LONG RURAL |  | 2 | 195 | 390 | 0.0015102 | 7.7446e-06 | 0
2013-05-02 12:20 | BGE23 | SHORT RURAL |  | 68 | 140 | 9520 | 0.082843 | 0.00059173 | 0
2013-05-03 09:00 | OFR23 | LONG RURAL |  | 67 | 386 | 25862 | 0.10015 | 0.00025945 | 0
2013-05-03 08:30 | PHM14 | LONG RURAL |  | 34 | 407 | 13838 | 0.053585 | 0.00013166 | 0
2013-05-05 09:05 | DRN11 | URBAN |  | 48 | 220 | 10560 | 0.036786 | 0.00016721 | 0
2013-05-05 09:05 | KLO14 | LONG RURAL |  | 82 | 220 | 18040 | 0.069857 | 0.00031753 | 0
2013-05-01 10:07 | CF2 | SHORT RURAL |  | 3 | 83 | 249 | 0.0021668 | 2.6106e-05 | 0
2013-04-24 09:00 | CRE22 | URBAN |  | 78 | 495 | 38610 | 0.1345 | 0.00027171 | 0
2013-05-06 13:25 | ELM13 | URBAN |  | 57 | 125 | 7125 | 0.02482 | 0.00019856 | 0
2013-05-08 10:25 | TT6 | URBAN |  | 188 | 255.2128 | 47980 | 0.16714 | 0.00065489 | 0
2013-05-07 09:05 | MBY12 | SHORT RURAL |  | 43 | 305 | 13115 | 0.11413 | 0.00037418 | 0
2013-05-06 14:10 | WOTS13 | LONG RURAL |  | 2 | 60 | 120 | 0.00046468 | 7.7446e-06 | 0
2013-05-08 09:00 | MBY11 | SHORT RURAL |  | 3 | 340 | 1020 | 0.008876 | 2.6106e-05 | 0
2013-05-07 09:37 | WGI34 | SHORT RURAL |  | 125 | 55 | 6875 | 0.059826 | 0.0010877 | 0
2013-05-07 09:05 | LLG12 | SHORT RURAL |  | 6 | 57 | 342 | 0.0029761 | 5.2212e-05 | 0
2013-05-07 09:00 | LGA11 | LONG RURAL |  | 148 | 448 | 66304 | 0.25675 | 0.0005731 | 0
2013-05-07 09:10 | FTR21 | LONG RURAL |  | 703 | 317 | 222851 | 0.86295 | 0.0027222 | 0
2013-05-08 09:00 | LGA12 | SHORT RURAL |  | 84 | 300 | 25200 | 0.21929 | 0.00073097 | 0
2013-05-08 08:32 | FTR21 | LONG RURAL |  | 157 | 345 | 54165 | 0.20974 | 0.00060795 | 0
2013-05-08 08:45 | LLG12 | SHORT RURAL |  | 1 | 65 | 65 | 0.00056563 | 8.702e-06 | 0
2013-05-08 09:38 | WGI31 | SHORT RURAL |  | 3 | 117 | 351 | 0.0030544 | 2.6106e-05 | 0
2013-05-08 09:00 | LLG12 | SHORT RURAL |  | 2 | 52 | 104 | 0.000905 | 1.7404e-05 | 0
2013-05-07 13:10 | WYK12 | SHORT RURAL |  | 5 | 30 | 150 | 0.0013053 | 4.351e-05 | 0
2013-05-07 11:15 | WYK12 | SHORT RURAL |  | 78 | 30 | 2340 | 0.020363 | 0.00067875 | 0
2013-05-07 09:50 | WYK11 | SHORT RURAL |  | 1037 | 332 | 344284 | 2.9959 | 0.0090239 | 0
2013-05-07 10:00 | WYK12 | SHORT RURAL |  | 39 | 35 | 1365 | 0.011878 | 0.00033938 | 0
2013-05-06 12:10 | WGL24 | LONG RURAL |  | 2 | 20 | 40 | 0.00015489 | 7.7446e-06 | 0
2013-05-06 14:20 | WGL23 | SHORT RURAL |  | 2 | 40 | 80 | 0.00069616 | 1.7404e-05 | 0
2013-05-09 10:25 | FTR21 | LONG RURAL |  | 119 | 218 | 25942 | 0.10046 | 0.00046081 | 0
2013-05-07 09:25 | WGL24 | LONG RURAL |  | 1 | 125 | 125 | 0.00048404 | 3.8723e-06 | 0
2013-05-08 09:00 | MOE13 | SHORT RURAL |  | 60 | 170 | 10200 | 0.08876 | 0.00052212 | 0
2013-05-08 10:00 | WGL11 | SHORT RURAL |  | 190 | 150 | 28500 | 0.24801 | 0.0016534 | 0
2013-05-09 09:00 | FTR21 | LONG RURAL |  | 47 | 290 | 13630 | 0.05278 | 0.000182 | 0
2013-05-07 07:31 | BDL5 | LONG RURAL |  | 421 | 565 | 237865 | 0.92109 | 0.0016302 | 0
2013-05-08 09:24 | FTR23 | LONG RURAL |  | 2 | 60 | 120 | 0.00046468 | 7.7446e-06 | 0
2013-05-08 10:08 | LLG12 | SHORT RURAL |  | 2 | 55 | 110 | 0.00095722 | 1.7404e-05 | 0
2013-05-07 10:50 | WGL24 | LONG RURAL |  | 2 | 265 | 530 | 0.0020523 | 7.7446e-06 | 0
2013-05-08 10:30 | LLG12 | SHORT RURAL |  | 1 | 45 | 45 | 0.00039159 | 8.702e-06 | 0
2013-05-09 09:00 | TGN11 | SHORT RURAL |  | 395 | 343 | 135485 | 1.179 | 0.0034373 | 0
2013-05-08 13:08 | LLG12 | SHORT RURAL |  | 2 | 30 | 60 | 0.00052212 | 1.7404e-05 | 0
2013-05-08 09:15 | WO31 | URBAN |  | 3 | 23 | 69 | 0.00024036 | 1.045e-05 | 0
2013-05-09 09:00 | LLG12 | SHORT RURAL |  | 23 | 180 | 4140 | 0.036026 | 0.00020015 | 0
2013-05-08 13:40 | WYK12 | SHORT RURAL |  | 6 | 65 | 390 | 0.0033938 | 5.2212e-05 | 0
2013-05-08 11:50 | WYK12 | SHORT RURAL |  | 3 | 60 | 180 | 0.0015664 | 2.6106e-05 | 0
2013-05-08 09:20 | LDL23 | LONG RURAL |  | 2 | 10 | 20 | 7.7446e-05 | 7.7446e-06 | 0
2013-05-08 10:05 | LGA24 | SHORT RURAL |  | 1 | 125 | 125 | 0.0010877 | 8.702e-06 | 0
2013-05-09 09:00 | MOE13 | SHORT RURAL |  | 101 | 395 | 39895 | 0.34717 | 0.0008789 | 0
2013-05-08 09:00 | FTR22 | SHORT RURAL |  | 157 | 275 | 43175 | 0.37571 | 0.0013662 | 0
2013-05-09 08:45 | PHM14 | LONG RURAL |  | 41 | 221 | 9061 | 0.035087 | 0.00015876 | 0
2013-05-08 08:57 | TGN11 | SHORT RURAL |  | 18 | 187 | 3366 | 0.029291 | 0.00015664 | 0
2013-05-09 09:16 | WYK12 | SHORT RURAL |  | 22 | 94 | 2068 | 0.017996 | 0.00019144 | 0
2013-05-07 10:26 | WT7 | URBAN |  | 144 | 69 | 9936 | 0.034612 | 0.00050162 | 0
2013-05-07 09:05 | DRN12 | URBAN |  | 52 | 225 | 11700 | 0.040757 | 0.00018114 | 0
2013-05-09 08:35 | LDL13 | SHORT RURAL |  | 136 | 357 | 48552 | 0.4225 | 0.0011835 | 0
2013-05-09 08:33 | LDL23 | LONG RURAL |  | 68 | 344 | 23392 | 0.090581 | 0.00026332 | 0
2013-05-07 08:55 | MFA21 | LONG RURAL |  | 3 | 70 | 210 | 0.00081319 | 1.1617e-05 | 0
2013-05-07 09:10 | MFA21 | LONG RURAL |  | 2 | 55 | 110 | 0.00042595 | 7.7446e-06 | 0
2013-05-07 11:00 | MFA21 | LONG RURAL |  | 3 | 70 | 210 | 0.00081319 | 1.1617e-05 | 0
2013-05-07 09:00 | WT12 | URBAN |  | 63 | 230 | 14490 | 0.050476 | 0.00021946 | 0
2013-05-07 09:20 | WGL24 | LONG RURAL |  | 2 | 50 | 100 | 0.00038723 | 7.7446e-06 | 0
2013-05-08 08:30 | MFA21 | LONG RURAL |  | 12 | 230 | 2760 | 0.010688 | 4.6468e-05 | 0
2013-05-09 09:00 | MFA21 | LONG RURAL |  | 42 | 305 | 12810 | 0.049604 | 0.00016264 | 0
2013-05-09 09:00 | LGA11 | LONG RURAL |  | 77 | 326 | 25102 | 0.097203 | 0.00029817 | 0
2013-05-07 09:00 | LLG13 | SHORT RURAL |  | 15 | 255 | 3825 | 0.033285 | 0.00013053 | 0
2013-05-07 11:20 | WGL24 | LONG RURAL |  | 1 | 65 | 65 | 0.0002517 | 3.8723e-06 | 0
2013-05-07 13:50 | WGL24 | LONG RURAL |  | 1 | 60 | 60 | 0.00023234 | 3.8723e-06 | 0
2013-05-08 09:00 | WGL24 | LONG RURAL |  | 1 | 25 | 25 | 9.6808e-05 | 3.8723e-06 | 0
2013-05-08 09:15 | WGL24 | LONG RURAL |  | 1 | 135 | 135 | 0.00052276 | 3.8723e-06 | 0
2013-05-08 09:20 | DRN12 | URBAN |  | 55 | 70 | 3850 | 0.013411 | 0.00019159 | 0
2013-05-08 10:30 | WGL24 | LONG RURAL |  | 1 | 26 | 26 | 0.00010068 | 3.8723e-06 | 0
2013-05-08 11:40 | WGL24 | LONG RURAL |  | 4 | 50 | 200 | 0.00077446 | 1.5489e-05 | 0
2013-05-08 11:30 | WGL24 | LONG RURAL |  | 4 | 40 | 160 | 0.00061957 | 1.5489e-05 | 0
2013-05-08 14:35 | WGL24 | LONG RURAL |  | 5 | 40 | 200 | 0.00077446 | 1.9362e-05 | 0
2013-05-08 13:25 | WGL24 | LONG RURAL |  | 3 | 40 | 120 | 0.00046468 | 1.1617e-05 | 0
2013-05-08 14:00 | WGL24 | LONG RURAL |  | 1 | 90 | 90 | 0.00034851 | 3.8723e-06 | 0
2013-05-07 09:10 | FGY33 | URBAN |  | 27 | 60 | 1620 | 0.0056432 | 9.4054e-05 | 0
2013-05-07 09:25 | BDL2 | SHORT RURAL |  | 119 | 345 | 41055 | 0.35726 | 0.0010355 | 0
2013-05-09 10:15 | ELM15 | SHORT RURAL |  | 65 | 205 | 13325 | 0.11595 | 0.00056563 | 0
2013-05-09 13:25 | EPG11 | URBAN |  | 79 | 125 | 9875 | 0.034399 | 0.0002752 | 0
2013-05-09 10:20 | ELM15 | SHORT RURAL |  | 52 | 190 | 9880 | 0.085975 | 0.0004525 | 0
2013-05-08 09:00 | ELM33 | SHORT RURAL |  | 47 | 331 | 15557 | 0.13538 | 0.00040899 | 0
2013-05-08 14:10 | WGL24 | LONG RURAL |  | 3 | 45 | 135 | 0.00052276 | 1.1617e-05 | 0
2013-05-09 09:15 | WGL24 | LONG RURAL |  | 3 | 120 | 360 | 0.001394 | 1.1617e-05 | 0
2013-05-08 07:41 | LDL11 | URBAN |  | 374 | 378 | 141372 | 0.49247 | 0.0013028 | 0
2013-05-08 08:40 | CYN12 | URBAN |  | 435 | 245 | 106575 | 0.37125 | 0.0015153 | 0
2013-05-08 09:30 | BRA24 | URBAN |  | 90 | 175 | 15750 | 0.054865 | 0.00031351 | 0
2013-05-08 09:30 | CYN21 | URBAN |  | 297 | 681.4646 | 202395 | 0.70504 | 0.0010346 | 0
2013-05-08 12:15 | BGE12 | SHORT RURAL |  | 132 | 65 | 8580 | 0.074663 | 0.0011487 | 0
2013-05-08 08:44 | RWN24 | SHORT RURAL |  | 669 | 161 | 107709 | 0.93728 | 0.0058216 | 0
2013-05-08 12:16 | WGL13 | SHORT RURAL |  | 2 | 40 | 80 | 0.00069616 | 1.7404e-05 | 0
2013-05-02 09:06 | WN5 | LONG RURAL |  | 3 | 69 | 207 | 0.00080157 | 1.1617e-05 | 0
2013-05-08 08:36 | CYN33 | SHORT RURAL |  | 73 | 293 | 21389 | 0.18613 | 0.00063524 | 0
2013-05-02 09:46 | WN5 | LONG RURAL |  | 2 | 189 | 378 | 0.0014637 | 7.7446e-06 | 0
2013-05-02 11:01 | WN5 | LONG RURAL |  | 1 | 174 | 174 | 0.00067378 | 3.8723e-06 | 0
2013-05-02 13:25 | WN5 | LONG RURAL |  | 1 | 25 | 25 | 9.6808e-05 | 3.8723e-06 | 0
2013-04-24 09:00 | LDL23 | LONG RURAL |  | 39 | 340 | 13260 | 0.051347 | 0.00015102 | 0
2013-05-03 10:50 | WN5 | LONG RURAL |  | 6 | 150 | 900 | 0.0034851 | 2.3234e-05 | 0
2013-05-02 11:05 | WN5 | LONG RURAL |  | 2 | 55 | 110 | 0.00042595 | 7.7446e-06 | 0
2013-05-07 13:08 | BN3 | SHORT RURAL |  | 1 | 96 | 96 | 0.00083539 | 8.702e-06 | 0
2013-05-02 10:31 | WYK11 | SHORT RURAL |  | 4 | 64 | 256 | 0.0022277 | 3.4808e-05 | 0
2013-05-02 12:30 | WYK11 | SHORT RURAL |  | 1 | 35 | 35 | 0.00030457 | 8.702e-06 | 0
2013-05-02 14:18 | WYK11 | SHORT RURAL |  | 1 | 51 | 51 | 0.0004438 | 8.702e-06 | 0
2013-05-02 12:39 | WYK11 | SHORT RURAL |  | 16 | 61 | 976 | 0.0084931 | 0.00013923 | 0
2013-05-02 11:27 | WYK11 | SHORT RURAL |  | 1 | 33 | 33 | 0.00028717 | 8.702e-06 | 0
2013-05-09 13:15 | MYT2 | SHORT RURAL |  | 100 | 120 | 12000 | 0.10442 | 0.0008702 | 0
2013-05-09 12:20 | WOTS11 | LONG RURAL |  | 4 | 95 | 380 | 0.0014715 | 1.5489e-05 | 0
2013-05-10 09:56 | WGL15 | SHORT RURAL |  | 16 | 193 | 3088 | 0.026872 | 0.00013923 | 0
2013-05-09 11:45 | LLG12 | SHORT RURAL |  | 1 | 51 | 51 | 0.0004438 | 8.702e-06 | 0
2013-05-09 13:32 | LLG12 | SHORT RURAL |  | 1 | 39 | 39 | 0.00033938 | 8.702e-06 | 0
2013-05-10 09:25 | FTR21 | LONG RURAL |  | 1 | 95 | 95 | 0.00036787 | 3.8723e-06 | 0
2013-05-10 09:27 | FTR23 | LONG RURAL |  | 17 | 81 | 1377 | 0.0053322 | 6.5829e-05 | 0
2013-05-10 09:00 | LGA14 | LONG RURAL |  | 18 | 197 | 3546 | 0.013731 | 6.9702e-05 | 0
2013-05-10 09:01 | WGI14 | SHORT RURAL |  | 68 | 289 | 19652 | 0.17101 | 0.00059173 | 0
2013-05-10 11:30 | WGL24 | LONG RURAL |  | 7 | 140 | 980 | 0.0037949 | 2.7106e-05 | 0
2013-05-10 09:05 | TGN31 | LONG RURAL |  | 1 | 45 | 45 | 0.00017425 | 3.8723e-06 | 0
2013-05-10 08:40 | BDL5 | LONG RURAL |  | 1 | 180 | 180 | 0.00069702 | 3.8723e-06 | 0
2013-05-10 09:10 | TGN14 | LONG RURAL |  | 1 | 95 | 95 | 0.00036787 | 3.8723e-06 | 0
2013-05-15 08:45 | WO32 | URBAN |  | 84 | 75 | 6300 | 0.021946 | 0.00029261 | 0
2013-05-09 11:50 | WGL24 | LONG RURAL |  | 1 | 28 | 28 | 0.00010842 | 3.8723e-06 | 0
2013-05-09 12:30 | WGL24 | LONG RURAL |  | 1 | 40 | 40 | 0.00015489 | 3.8723e-06 | 0
2013-05-10 09:00 | WGL24 | LONG RURAL |  | 50 | 138 | 6900 | 0.026719 | 0.00019362 | 0
2013-05-10 09:20 | WGL24 | LONG RURAL |  | 5 | 190 | 950 | 0.0036787 | 1.9362e-05 | 0
2013-05-10 09:10 | WGL11 | SHORT RURAL |  | 135 | 95 | 12825 | 0.1116 | 0.0011748 | 0
2013-05-09 11:00 | CYN24 | URBAN |  | 60 | 195 | 11700 | 0.040757 | 0.00020901 | 0
2013-05-10 09:15 | BN1 | LONG RURAL |  | 2 | 215 | 430 | 0.0016651 | 7.7446e-06 | 0
2013-05-06 08:50 | BDL6 | SHORT RURAL |  | 1 | 195 | 195 | 0.0016969 | 8.702e-06 | 0
2013-05-02 10:30 | WYK11 | SHORT RURAL |  | 3 | 35 | 105 | 0.00091371 | 2.6106e-05 | 0
2013-05-06 11:45 | FGY13 | SHORT RURAL |  | 4 | 135 | 540 | 0.0046991 | 3.4808e-05 | 0
2013-05-06 09:10 | WYK24 | SHORT RURAL |  | 3 | 35 | 105 | 0.00091371 | 2.6106e-05 | 0
2013-05-09 13:50 | BGE24 | SHORT RURAL |  | 9 | 70 | 630 | 0.0054822 | 7.8318e-05 | 0
2013-05-06 09:33 | ALA01 | LONG RURAL |  | 97 | 322 | 31234 | 0.12095 | 0.00037561 | 0
2013-05-14 09:05 | MYT7 | LONG RURAL |  | 21 | 175 | 3675 | 0.014231 | 8.1319e-05 | 0
2013-05-06 11:18 | WYK24 | SHORT RURAL |  | 1 | 22 | 22 | 0.00019144 | 8.702e-06 | 0
2013-05-09 09:00 | ELM31 | URBAN |  | 58 | 275 | 15950 | 0.055562 | 0.00020204 | 0
2013-05-06 12:00 | WYK24 | SHORT RURAL |  | 1 | 35 | 35 | 0.00030457 | 8.702e-06 | 0
2013-05-06 14:15 | WYK24 | SHORT RURAL |  | 5 | 35 | 175 | 0.0015228 | 4.351e-05 | 0
2013-05-06 14:00 | WYK24 | SHORT RURAL |  | 2 | 20 | 40 | 0.00034808 | 1.7404e-05 | 0
2013-05-07 11:02 | WYK24 | SHORT RURAL |  | 1 | 30 | 30 | 0.00026106 | 8.702e-06 | 0
2013-05-10 08:50 | MFA21 | LONG RURAL |  | 27 | 325 | 8775 | 0.03398 | 0.00010455 | 0
2013-05-06 08:45 | RWN24 | SHORT RURAL |  | 22 | 360 | 7920 | 0.06892 | 0.00019144 | 0
2013-05-10 08:50 | RWN31 | SHORT RURAL |  | 66 | 240 | 15840 | 0.13784 | 0.00057433 | 0
2013-05-07 07:31 | BDL6 | SHORT RURAL |  | 3 | 574 | 1722 | 0.014985 | 2.6106e-05 | 0
2013-05-07 10:08 | BGE11 | SHORT RURAL |  | 160 | 282 | 45120 | 0.39263 | 0.0013923 | 0
2013-05-08 08:50 | BDL6 | SHORT RURAL |  | 1 | 355 | 355 | 0.0030892 | 8.702e-06 | 0
2013-05-08 09:25 | BDL5 | LONG RURAL |  | 10 | 265 | 2650 | 0.010262 | 3.8723e-05 | 0
2013-05-07 09:00 | WOTS24 | LONG RURAL |  | 76 | 220 | 16720 | 0.064745 | 0.0002943 | 0
2013-05-07 09:00 | MSD1 | LONG RURAL |  | 58 | 111.5517 | 6470 | 0.025054 | 0.00022459 | 0
2013-05-08 09:50 | WOTS24 | LONG RURAL |  | 8 | 128 | 1024 | 0.0039652 | 3.0979e-05 | 0
2013-05-06 09:05 | WN6 | LONG RURAL |  | 141 | 160 | 22560 | 0.087359 | 0.000546 | 0
2013-05-08 09:17 | KLO24 | SHORT RURAL |  | 19 | 403 | 7657 | 0.066631 | 0.00016534 | 0
2013-05-08 09:24 | WN2 | LONG RURAL |  | 2 | 143 | 286 | 0.0011075 | 7.7446e-06 | 0
2013-05-08 09:22 | BN1 | LONG RURAL |  | 31 | 408 | 12648 | 0.048977 | 0.00012004 | 0
2013-05-05 08:35 | BWR12 | URBAN |  | 12 | 75 | 900 | 0.0031351 | 4.1802e-05 | 0
2013-05-11 08:32 | MOE23 | SHORT RURAL |  | 283 | 284 | 80372 | 0.69939 | 0.0024627 | 0
2013-05-11 10:30 | WYK11 | SHORT RURAL |  | 8 | 300 | 2400 | 0.020885 | 6.9616e-05 | 0
2013-05-10 11:45 | ELM32 | URBAN |  | 101 | 15 | 1515 | 0.0052775 | 0.00035183 | 0
2013-05-11 08:35 | CYN33 | SHORT RURAL |  | 42 | 370 | 15540 | 0.13523 | 0.00036548 | 0
2013-05-08 13:55 | BDL6 | SHORT RURAL |  | 2 | 15 | 30 | 0.00026106 | 1.7404e-05 | 0
2013-05-09 08:40 | BDL5 | LONG RURAL |  | 2 | 320 | 640 | 0.0024783 | 7.7446e-06 | 0
2013-05-10 08:30 | BDL5 | LONG RURAL |  | 3 | 240 | 720 | 0.0027881 | 1.1617e-05 | 0
2013-05-10 09:00 | WO14 | URBAN |  | 99 | 235 | 23265 | 0.081043 | 0.00034486 | 0
2013-05-09 09:00 | WOTS13 | LONG RURAL |  | 4 | 334 | 1336 | 0.0051734 | 1.5489e-05 | 0
2013-05-07 08:30 | WYK23 | SHORT RURAL |  | 3 | 450 | 1350 | 0.011748 | 2.6106e-05 | 0
2013-05-10 11:26 | WGL13 | SHORT RURAL |  | 2 | 60 | 120 | 0.0010442 | 1.7404e-05 | 0
2013-05-10 09:15 | WGL12 | LONG RURAL |  | 1 | 112 | 112 | 0.0004337 | 3.8723e-06 | 0
2013-05-08 13:18 | WN2 | LONG RURAL |  | 2 | 62 | 124 | 0.00048017 | 7.7446e-06 | 0
2013-05-09 09:25 | BN1 | LONG RURAL |  | 73 | 310 | 22630 | 0.08763 | 0.00028268 | 0
2013-05-06 09:00 | BWN13 | URBAN |  | 49 | 180 | 8820 | 0.030724 | 0.00017069 | 0
2013-05-08 09:55 | OFR23 | LONG RURAL |  | 1 | 120 | 120 | 0.00046468 | 3.8723e-06 | 0
2013-05-08 09:30 | OFR23 | LONG RURAL |  | 2 | 35 | 70 | 0.00027106 | 7.7446e-06 | 0
2013-05-08 11:00 | PHM14 | LONG RURAL |  | 27 | 235 | 6345 | 0.02457 | 0.00010455 | 0
2013-05-08 14:45 | OFR23 | LONG RURAL |  | 2 | 21 | 42 | 0.00016264 | 7.7446e-06 | 0
2013-05-09 09:45 | CRE31 | URBAN |  | 736 | 140 | 103040 | 0.35894 | 0.0025638 | 0
2013-05-09 11:15 | OFR23 | LONG RURAL |  | 1 | 175 | 175 | 0.00067766 | 3.8723e-06 | 0
2013-05-10 11:40 | BN6 | LONG RURAL |  | 2 | 125 | 250 | 0.00096808 | 7.7446e-06 | 0
2013-05-09 11:40 | CRE32 | URBAN |  | 7 | 150 | 1050 | 0.0036577 | 2.4384e-05 | 0
2013-05-11 12:43 | WYK11 | SHORT RURAL |  | 5 | 27 | 135 | 0.0011748 | 4.351e-05 | 0
2013-05-11 13:26 | WYK11 | SHORT RURAL |  | 1 | 30 | 30 | 0.00026106 | 8.702e-06 | 0
2013-05-12 08:35 | WYK24 | SHORT RURAL |  | 10 | 30 | 300 | 0.0026106 | 8.702e-05 | 0
2013-05-12 09:30 | PHM34 | URBAN |  | 102 | 340 | 34680 | 0.12081 | 0.00035532 | 0
2013-05-13 09:10 | LLG12 | SHORT RURAL |  | 30 | 280 | 8400 | 0.073097 | 0.00026106 | 0
2013-05-12 13:40 | WYK24 | SHORT RURAL |  | 1 | 37 | 37 | 0.00032197 | 8.702e-06 | 0
2013-05-12 10:03 | WYK24 | SHORT RURAL |  | 7 | 18 | 126 | 0.0010964 | 6.0914e-05 | 0
2013-05-13 08:22 | WYK23 | SHORT RURAL |  | 2467 | 405.028 | 999204 | 8.695 | 0.021468 | 0
2013-05-13 11:30 | MWTS14 | SHORT RURAL |  | 4 | 50 | 200 | 0.0017404 | 3.4808e-05 | 0
2013-05-09 08:40 | BDL1 | LONG RURAL |  | 19 | 200 | 3800 | 0.014715 | 7.3574e-05 | 0
2013-05-12 14:00 | SMR3 | LONG RURAL |  | 49 | 80 | 3920 | 0.015179 | 0.00018974 | 0
2013-05-12 09:00 | SMR4 | SHORT RURAL |  | 49 | 147 | 7203 | 0.06268 | 0.0004264 | 0
2013-05-10 09:25 | SMR8 | LONG RURAL |  | 25 | 490 | 12250 | 0.047436 | 9.6808e-05 | 0
2013-05-13 09:01 | SMR4 | SHORT RURAL |  | 2 | 51 | 102 | 0.0008876 | 1.7404e-05 | 0
2013-05-13 09:20 | MOE13 | SHORT RURAL |  | 123 | 63 | 7749 | 0.067432 | 0.0010703 | 0
2013-04-28 07:39 | BWN12 | URBAN |  | 720 | 158.9028 | 114410 | 0.39855 | 0.0025081 | 0
2013-05-13 15:34 | LGA11 | LONG RURAL |  | 818 | 1490.9071 | 1219562 | 4.7225 | 0.0031676 | 0
2013-05-15 08:30 | LGA12 | SHORT RURAL |  | 1 | 20 | 20 | 0.00017404 | 8.702e-06 | 0
2013-05-15 09:15 | WGI24 | URBAN |  | 8 | 265 | 2120 | 0.007385 | 2.7868e-05 | 0
2013-05-14 08:46 | LGA21 | SHORT RURAL |  | 145 | 169 | 24505 | 0.21324 | 0.0012618 | 0
2013-05-14 09:12 | LGA14 | LONG RURAL |  | 3 | 85 | 255 | 0.00098744 | 1.1617e-05 | 0
2013-05-15 09:10 | PHI12 | SHORT RURAL |  | 419 | 290 | 121510 | 1.0574 | 0.0036461 | 0
2013-05-14 11:30 | LGA13 | LONG RURAL |  | 3 | 132 | 396 | 0.0015334 | 1.1617e-05 | 0
2013-05-14 09:00 | WO32 | URBAN |  | 78 | 255 | 19890 | 0.069286 | 0.00027171 | 0
2013-05-15 13:00 | MYT2 | SHORT RURAL |  | 29 | 25 | 725 | 0.0063089 | 0.00025236 | 0
2013-05-14 09:15 | LGA11 | LONG RURAL |  | 2 | 52 | 104 | 0.00040272 | 7.7446e-06 | 0
2013-05-15 08:45 | LGA12 | SHORT RURAL |  | 1 | 57 | 57 | 0.00049601 | 8.702e-06 | 0
2013-05-15 08:00 | DRN12 | URBAN |  | 240 | 360 | 86400 | 0.30097 | 0.00083604 | 0
2013-05-14 09:00 | LLG12 | SHORT RURAL |  | 19 | 300 | 5700 | 0.049601 | 0.00016534 | 0
2013-05-15 09:36 | SLE31 | LONG RURAL |  | 1 | 24 | 24 | 9.2936e-05 | 3.8723e-06 | 0
2013-05-14 09:05 | LLG12 | SHORT RURAL |  | 22 | 209 | 4598 | 0.040012 | 0.00019144 | 0
2013-05-15 09:05 | MOE13 | SHORT RURAL |  | 190 | 365 | 69350 | 0.60348 | 0.0016534 | 0
2013-05-14 09:00 | FTR12 | LONG RURAL |  | 18 | 394 | 7092 | 0.027462 | 6.9702e-05 | 0
2013-05-14 09:00 | WGL15 | SHORT RURAL |  | 36 | 290 | 10440 | 0.090849 | 0.00031327 | 0
2013-05-16 09:30 | ELM32 | URBAN |  | 131 | 380 | 49780 | 0.17341 | 0.00045634 | 0
2013-05-14 09:30 | MOE13 | SHORT RURAL |  | 60 | 200 | 12000 | 0.10442 | 0.00052212 | 0
2013-05-14 13:00 | LGA12 | SHORT RURAL |  | 21 | 70 | 1470 | 0.012792 | 0.00018274 | 0
2013-05-14 09:00 | FTR23 | LONG RURAL |  | 55 | 286 | 15730 | 0.060912 | 0.00021298 | 0
2013-05-14 08:35 | MFA21 | LONG RURAL |  | 1 | 95 | 95 | 0.00036787 | 3.8723e-06 | 0
2013-05-15 09:15 | MFA21 | LONG RURAL |  | 62 | 120 | 7440 | 0.02881 | 0.00024008 | 0
2013-05-16 09:14 | LLG12 | SHORT RURAL |  | 2 | 130 | 260 | 0.0022625 | 1.7404e-05 | 0
2013-05-15 08:40 | LGA11 | LONG RURAL |  | 2 | 380 | 760 | 0.002943 | 7.7446e-06 | 0
2013-05-14 08:50 | LDL14 | SHORT RURAL |  | 134 | 370 | 49580 | 0.43144 | 0.0011661 | 0
2013-05-14 08:30 | KLK1 | SHORT RURAL |  | 110 | 395 | 43450 | 0.3781 | 0.00095722 | 0
2013-05-16 09:20 | LDL23 | LONG RURAL |  | 219 | 340 | 74460 | 0.28833 | 0.00084804 | 0
2013-05-15 09:40 | MFA21 | LONG RURAL |  | 3 | 20 | 60 | 0.00023234 | 1.1617e-05 | 0
2013-05-15 11:45 | WYK24 | SHORT RURAL |  | 2 | 45 | 90 | 0.00078318 | 1.7404e-05 | 0
2013-05-15 13:30 | WYK24 | SHORT RURAL |  | 1 | 135 | 135 | 0.0011748 | 8.702e-06 | 0
2013-05-16 08:15 | WYK11 | SHORT RURAL |  | 9 | 37 | 333 | 0.0028978 | 7.8318e-05 | 0
2013-05-15 08:30 | WYK11 | SHORT RURAL |  | 3 | 55 | 165 | 0.0014358 | 2.6106e-05 | 0
2013-05-15 08:55 | LDL14 | SHORT RURAL |  | 232 | 305 | 70760 | 0.61575 | 0.0020189 | 0
2013-05-15 09:30 | FTR21 | LONG RURAL |  | 3 | 180 | 540 | 0.002091 | 1.1617e-05 | 0
2013-05-16 08:30 | WO32 | URBAN |  | 138 | 390 | 53820 | 0.18748 | 0.00048072 | 0
2013-05-15 09:10 | MYT7 | LONG RURAL |  | 1 | 30 | 30 | 0.00011617 | 3.8723e-06 | 0
2013-05-15 08:30 | RWN22 | URBAN |  | 113 | 413.1239 | 46683 | 0.16262 | 0.00039363 | 0
2013-05-16 08:40 | WYK12 | SHORT RURAL |  | 11 | 105 | 1155 | 0.010051 | 9.5722e-05 | 0
2013-05-16 08:45 | ELM32 | URBAN |  | 66 | 330 | 21780 | 0.07587 | 0.00022991 | 0
2013-05-15 12:00 | WN5 | LONG RURAL |  | 1 | 75 | 75 | 0.00029042 | 3.8723e-06 | 0
2013-05-15 09:30 | MYT7 | LONG RURAL |  | 2 | 160 | 320 | 0.0012391 | 7.7446e-06 | 0
2013-05-14 09:10 | TGN23 | SHORT RURAL |  | 3 | 96 | 288 | 0.0025062 | 2.6106e-05 | 0
2013-05-14 09:42 | WGL24 | LONG RURAL |  | 4 | 33 | 132 | 0.00051115 | 1.5489e-05 | 0
2013-05-14 10:40 | WGL24 | LONG RURAL |  | 1 | 55 | 55 | 0.00021298 | 3.8723e-06 | 0
2013-05-14 13:25 | WGL24 | LONG RURAL |  | 2 | 55 | 110 | 0.00042595 | 7.7446e-06 | 0
2013-05-15 09:21 | RWN24 | SHORT RURAL |  | 386 | 313 | 120818 | 1.0514 | 0.003359 | 0
2013-05-10 09:10 | SMR5 | LONG RURAL |  | 8 | 75 | 600 | 0.0023234 | 3.0979e-05 | 0
2013-05-14 08:45 | BDL5 | LONG RURAL |  | 6 | 380 | 2280 | 0.0088289 | 2.3234e-05 | 0
2013-05-15 08:50 | BDL1 | LONG RURAL |  | 70 | 248.0857 | 17366 | 0.067247 | 0.00027106 | 0
2013-05-15 11:45 | MFA21 | LONG RURAL |  | 4 | 90 | 360 | 0.001394 | 1.5489e-05 | 0
2013-05-14 09:30 | SMR5 | LONG RURAL |  | 4 | 140 | 560 | 0.0021685 | 1.5489e-05 | 0
2013-05-15 09:10 | WGL24 | LONG RURAL |  | 1 | 53 | 53 | 0.00020523 | 3.8723e-06 | 0
2013-05-16 09:00 | BDL1 | LONG RURAL |  | 81 | 358 | 28998 | 0.11229 | 0.00031366 | 0
2013-05-16 09:20 | CNR3 | SHORT RURAL |  | 22 | 254 | 5588 | 0.048627 | 0.00019144 | 0
2013-05-14 12:20 | SMR5 | LONG RURAL |  | 4 | 166 | 664 | 0.0025712 | 1.5489e-05 | 0
2013-05-14 08:40 | BGE11 | SHORT RURAL |  | 187 | 477 | 89199 | 0.77621 | 0.0016273 | 0
2013-05-15 11:20 | WGL24 | LONG RURAL |  | 1 | 45 | 45 | 0.00017425 | 3.8723e-06 | 0
2013-05-14 08:40 | WN4 | SHORT RURAL |  | 164 | 213.5976 | 35030 | 0.30483 | 0.0014271 | 0
2013-05-15 11:40 | WGL24 | LONG RURAL |  | 1 | 50 | 50 | 0.00019362 | 3.8723e-06 | 0
2013-05-09 11:00 | EPG23 | URBAN |  | 1 | 165 | 165 | 0.00057477 | 3.4835e-06 | 0
2013-05-13 08:45 | PHM14 | LONG RURAL |  | 9 | 80 | 720 | 0.0027881 | 3.4851e-05 | 0
2013-05-16 09:10 | DRN12 | URBAN |  | 105 | 220 | 23100 | 0.080468 | 0.00036577 | 0
2013-05-16 08:40 | EPG31 | URBAN |  | 51 | 292 | 14892 | 0.051876 | 0.00017766 | 0
2013-05-17 09:30 | TT6 | URBAN |  | 90 | 185 | 16650 | 0.058 | 0.00031351 | 0
2013-05-16 11:10 | WGL13 | SHORT RURAL |  | 182 | 102 | 18564 | 0.16154 | 0.0015838 | 0
2013-05-17 09:00 | FTR21 | LONG RURAL |  | 87 | 230 | 20010 | 0.077485 | 0.00033689 | 0
2013-05-17 08:07 | WO32 | URBAN |  | 47 | 403 | 18941 | 0.065981 | 0.00016372 | 0
2013-05-17 09:15 | MBY11 | SHORT RURAL |  | 6 | 30 | 180 | 0.0015664 | 5.2212e-05 | 0
2013-05-17 10:58 | WYK12 | SHORT RURAL |  | 3 | 72 | 216 | 0.0018796 | 2.6106e-05 | 0
2013-05-17 09:20 | WYK12 | SHORT RURAL |  | 1 | 23 | 23 | 0.00020015 | 8.702e-06 | 0
2013-05-16 11:45 | WYK12 | SHORT RURAL |  | 1 | 40 | 40 | 0.00034808 | 8.702e-06 | 0
2013-05-16 12:05 | WYK11 | SHORT RURAL |  | 4 | 25 | 100 | 0.0008702 | 3.4808e-05 | 0
2013-05-15 13:40 | WGL24 | LONG RURAL |  | 1 | 28 | 28 | 0.00010842 | 3.8723e-06 | 0
2013-05-17 09:00 | TGN23 | SHORT RURAL |  | 64 | 180 | 11520 | 0.10025 | 0.00055693 | 0
2013-05-16 08:45 | SLE31 | LONG RURAL |  | 8 | 380 | 3040 | 0.011772 | 3.0979e-05 | 0
2013-05-16 10:45 | MYT8 | SHORT RURAL |  | 1 | 90 | 90 | 0.00078318 | 8.702e-06 | 0
2013-05-14 09:00 | BDL8 | LONG RURAL |  | 2 | 180 | 360 | 0.001394 | 7.7446e-06 | 0
2013-05-22 09:45 | WOTS11 | LONG RURAL |  | 557 | 375 | 208875 | 0.80883 | 0.0021569 | 0
2013-05-17 08:35 | BWA23 | SHORT RURAL |  | 50 | 85 | 4250 | 0.036983 | 0.0004351 | 0
2013-05-15 09:10 | SMR5 | LONG RURAL |  | 23 | 30 | 690 | 0.0026719 | 8.9063e-05 | 0
2013-05-21 09:50 | WO22 | URBAN |  | 77 | 160 | 12320 | 0.042917 | 0.00026823 | 0
2013-05-13 09:30 | BDL4 | SHORT RURAL |  | 49 | 45 | 2205 | 0.019188 | 0.0004264 | 0
2013-05-15 09:20 | BDL5 | LONG RURAL |  | 38 | 360 | 13680 | 0.052973 | 0.00014715 | 0
2013-05-15 09:05 | MYT2 | SHORT RURAL |  | 60 | 120 | 7200 | 0.062654 | 0.00052212 | 0
2013-05-11 12:00 | BN4 | URBAN |  | 17 | 309.0588 | 5254 | 0.018302 | 5.9219e-05 | 0
2013-05-09 11:15 | OFR23 | LONG RURAL |  | 1 | 27 | 27 | 0.00010455 | 3.8723e-06 | 0
2013-05-17 13:30 | TT6 | URBAN |  | 86 | 100 | 8600 | 0.029958 | 0.00029958 | 0
2013-05-18 10:04 | MOE21 | SHORT RURAL |  | 527 | 331 | 174437 | 1.5179 | 0.0045859 | 0
2013-05-17 10:30 | MBY11 | SHORT RURAL |  | 4 | 40 | 160 | 0.0013923 | 3.4808e-05 | 0
2013-05-17 11:30 | MBY11 | SHORT RURAL |  | 7 | 40 | 280 | 0.0024366 | 6.0914e-05 | 0
2013-05-17 13:30 | WYK12 | SHORT RURAL |  | 5 | 47 | 235 | 0.002045 | 4.351e-05 | 0
2013-05-17 14:00 | WYK11 | SHORT RURAL |  | 18 | 49 | 882 | 0.0076751 | 0.00015664 | 0
2013-05-17 12:20 | WYK11 | SHORT RURAL |  | 2 | 44 | 88 | 0.00076577 | 1.7404e-05 | 0
2013-05-08 08:40 | BDL6 | SHORT RURAL |  | 2 | 158 | 316 | 0.0027498 | 1.7404e-05 | 0
2013-05-15 09:30 | CLN21 | SHORT RURAL |  | 268 | 77 | 20636 | 0.17957 | 0.0023321 | 0
2013-05-17 10:30 | MOE21 | SHORT RURAL |  | 27 | 320 | 8640 | 0.075185 | 0.00023495 | 0
2013-05-16 10:00 | BDL5 | LONG RURAL |  | 22 | 190 | 4180 | 0.016186 | 8.5191e-05 | 0
2013-05-14 09:11 | ALA01 | LONG RURAL |  | 54 | 259 | 13986 | 0.054158 | 0.0002091 | 0
2013-05-17 11:55 | BDL5 | LONG RURAL |  | 2 | 25 | 50 | 0.00019362 | 7.7446e-06 | 0
2013-05-17 09:05 | BDL5 | LONG RURAL |  | 5 | 50 | 250 | 0.00096808 | 1.9362e-05 | 0
2013-05-15 09:19 | MYT7 | LONG RURAL |  | 87 | 367 | 31929 | 0.12364 | 0.00033689 | 0
2013-05-16 10:15 | MBY12 | SHORT RURAL |  | 20 | 50 | 1000 | 0.008702 | 0.00017404 | 0
2013-05-14 09:10 | BN1 | LONG RURAL |  | 1 | 130 | 130 | 0.0005034 | 3.8723e-06 | 0
2013-05-14 08:30 | WGL12 | LONG RURAL |  | 46 | 365 | 16790 | 0.065016 | 0.00017813 | 0
2013-05-15 13:35 | SMR5 | LONG RURAL |  | 1 | 78 | 78 | 0.00030204 | 3.8723e-06 | 0
2013-05-14 08:30 | OFR23 | LONG RURAL |  | 4 | 95 | 380 | 0.0014715 | 1.5489e-05 | 0
2013-05-16 08:55 | WN6 | LONG RURAL |  | 2 | 35 | 70 | 0.00027106 | 7.7446e-06 | 0
2013-05-16 09:22 | BN6 | LONG RURAL |  | 28 | 230 | 6440 | 0.024938 | 0.00010842 | 0
2013-05-15 09:25 | OFR23 | LONG RURAL |  | 238 | 261 | 62118 | 0.24054 | 0.00092161 | 0
2013-05-16 09:00 | WGL12 | LONG RURAL |  | 2 | 300 | 600 | 0.0023234 | 7.7446e-06 | 0
2013-05-16 11:45 | WGL12 | LONG RURAL |  | 1 | 45 | 45 | 0.00017425 | 3.8723e-06 | 0
2013-05-16 11:17 | WGL12 | LONG RURAL |  | 1 | 40 | 40 | 0.00015489 | 3.8723e-06 | 0
2013-05-17 12:15 | PHM14 | LONG RURAL |  | 1 | 80 | 80 | 0.00030979 | 3.8723e-06 | 0
2013-05-17 08:43 | WGL12 | LONG RURAL |  | 2 | 29 | 58 | 0.00022459 | 7.7446e-06 | 0
2013-05-17 08:50 | WGL12 | LONG RURAL |  | 2 | 45 | 90 | 0.00034851 | 7.7446e-06 | 0
2013-05-17 08:55 | PHM14 | LONG RURAL |  | 7 | 60 | 420 | 0.0016264 | 2.7106e-05 | 0
2013-05-17 10:36 | PHM14 | LONG RURAL |  | 4 | 72 | 288 | 0.0011152 | 1.5489e-05 | 0
2013-05-02 13:00 | BGE11 | SHORT RURAL |  | 167 | 0 | 0 | 0 | 0.0014532 | 0
2013-05-19 09:00 | TGN12 | SHORT RURAL |  | 804 | 387 | 311148 | 2.7076 | 0.0069964 | 0
2013-05-19 08:25 | CYN13 | URBAN |  | 129 | 310 | 39990 | 0.1393 | 0.00044937 | 0
2013-05-19 09:32 | TT5 | URBAN |  | 1 | 215 | 215 | 0.00074895 | 3.4835e-06 | 0
2013-05-19 08:30 | LGA22 | SHORT RURAL |  | 23 | 320 | 7360 | 0.064047 | 0.00020015 | 0
2013-05-19 09:00 | WO22 | URBAN |  | 2 | 135 | 270 | 0.00094054 | 6.967e-06 | 0
2013-05-19 08:45 | WO22 | URBAN |  | 2 | 55 | 110 | 0.00038318 | 6.967e-06 | 0
2013-05-19 08:30 | BWN13 | URBAN |  | 111 | 166 | 18426 | 0.064187 | 0.00038667 | 0
2013-05-17 09:48 | WGL12 | LONG RURAL |  | 1 | 42 | 42 | 0.00016264 | 3.8723e-06 | 0
2013-05-17 09:45 | WGL12 | LONG RURAL |  | 1 | 35 | 35 | 0.00013553 | 3.8723e-06 | 0
2013-05-16 09:39 | ELD01 | SHORT RURAL |  | 130 | 111 | 14430 | 0.12557 | 0.0011313 | 0
2013-05-16 09:10 | LGA23 | LONG RURAL |  | 70 | 370 | 25900 | 0.10029 | 0.00027106 | 0
2013-05-14 16:45 | ELM33 | SHORT RURAL |  | 2 | 227 | 454 | 0.0039507 | 1.7404e-05 | 0
2013-05-19 10:11 | MOE13 | SHORT RURAL |  | 210 | 212 | 44520 | 0.38741 | 0.0018274 | 0
2013-05-17 11:21 | PHM14 | LONG RURAL |  | 5 | 65 | 325 | 0.0012585 | 1.9362e-05 | 0
2013-05-15 11:00 | ELM11 | URBAN |  | 170 | 185 | 31450 | 0.10956 | 0.00059219 | 0
2013-05-07 09:10 | MJG11 | SHORT RURAL |  | 4 | 278 | 1112 | 0.0096766 | 3.4808e-05 | 0
2013-05-17 09:55 | WOTS11 | LONG RURAL |  | 5 | 5 | 25 | 9.6808e-05 | 1.9362e-05 | 0
2013-05-10 09:27 | BN6 | LONG RURAL |  | 5 | 184 | 920 | 0.0035625 | 1.9362e-05 | 0
2013-05-14 09:01 | BN4 | URBAN |  | 114 | 352 | 40128 | 0.13979 | 0.00039712 | 0
2013-05-17 10:50 | WGL12 | LONG RURAL |  | 1 | 85 | 85 | 0.00032915 | 3.8723e-06 | 0
2013-05-16 13:50 | BN1 | LONG RURAL |  | 1 | 18 | 18 | 6.9702e-05 | 3.8723e-06 | 0
2013-05-19 09:30 | CLN23 | SHORT RURAL |  | 331 | 270 | 89370 | 0.7777 | 0.0028804 | 0
2013-05-15 11:34 | BN1 | LONG RURAL |  | 52 | 91 | 4732 | 0.018324 | 0.00020136 | 0
2013-05-17 10:00 | WN1 | URBAN |  | 1 | 45 | 45 | 0.00015676 | 3.4835e-06 | 0
2013-05-19 13:41 | TGN12 | SHORT RURAL |  | 2 | 57 | 114 | 0.00099202 | 1.7404e-05 | 0
2013-05-20 09:10 | WYK24 | SHORT RURAL |  | 5 | 50 | 250 | 0.0021755 | 4.351e-05 | 0
2013-05-20 09:10 | LGA22 | SHORT RURAL |  | 3 | 195 | 585 | 0.0050907 | 2.6106e-05 | 0
2013-05-19 14:15 | WO22 | URBAN |  | 5 | 70 | 350 | 0.0012192 | 1.7417e-05 | 0
2013-05-20 09:08 | LGA13 | LONG RURAL |  | 16 | 112 | 1792 | 0.0069392 | 6.1957e-05 | 0
2013-05-19 10:30 | WO22 | URBAN |  | 13 | 55 | 715 | 0.0024907 | 4.5285e-05 | 0
2013-05-19 12:05 | WO22 | URBAN |  | 5 | 45 | 225 | 0.00078378 | 1.7417e-05 | 0
2013-05-20 09:48 | FTR23 | LONG RURAL |  | 11 | 187 | 2057 | 0.0079654 | 4.2595e-05 | 0
2013-05-20 12:10 | LGA11 | LONG RURAL |  | 23 | 170 | 3910 | 0.015141 | 8.9063e-05 | 0
2013-05-17 10:55 | WOTS11 | LONG RURAL |  | 3 | 5 | 15 | 5.8085e-05 | 1.1617e-05 | 0
2013-05-20 08:45 | WO22 | URBAN |  | 611 | 412 | 251732 | 0.8769 | 0.0021284 | 0
2013-05-20 09:10 | MOE24 | SHORT RURAL |  | 81 | 234 | 18954 | 0.16494 | 0.00070486 | 0
2013-05-21 09:08 | DRN13 | SHORT RURAL |  | 81 | 108 | 8748 | 0.076125 | 0.00070486 | 0
2013-05-21 11:15 | TT9 | URBAN |  | 65 | 136 | 8840 | 0.030794 | 0.00022643 | 0
2013-05-21 12:45 | DRN13 | SHORT RURAL |  | 93 | 80 | 7440 | 0.064743 | 0.00080928 | 0
2013-05-22 09:20 | MOE13 | SHORT RURAL |  | 232 | 355 | 82360 | 0.71669 | 0.0020189 | 0
2013-05-23 09:11 | WGL11 | SHORT RURAL |  | 248 | 301 | 74648 | 0.64958 | 0.0021581 | 0
2013-05-21 09:57 | PHI13 | URBAN |  | 481 | 165 | 79365 | 0.27647 | 0.0016756 | 0
2013-05-21 09:00 | WGI22 | LONG RURAL |  | 3 | 425 | 1275 | 0.0049372 | 1.1617e-05 | 0
2013-05-21 08:50 | LGA13 | LONG RURAL |  | 3 | 230 | 690 | 0.0026719 | 1.1617e-05 | 0
2013-05-22 09:09 | PHI11 | SHORT RURAL |  | 131 | 298.6718 | 39126 | 0.34047 | 0.00114 | 0
2013-05-21 08:29 | WYK11 | SHORT RURAL |  | 37 | 67 | 2479 | 0.021572 | 0.00032197 | 0
2013-05-20 12:25 | WYK24 | SHORT RURAL |  | 30 | 52 | 1560 | 0.013575 | 0.00026106 | 0
2013-05-20 10:55 | WYK11 | SHORT RURAL |  | 16 | 51 | 816 | 0.0071008 | 0.00013923 | 0
2013-05-21 08:40 | BGE11 | SHORT RURAL |  | 160 | 360 | 57600 | 0.50123 | 0.0013923 | 0
2013-05-21 09:00 | WYK11 | SHORT RURAL |  | 575 | 553.8783 | 318480 | 2.7714 | 0.0050036 | 0
2013-05-21 09:00 | MYT2 | SHORT RURAL |  | 45 | 285 | 12825 | 0.1116 | 0.00039159 | 0
2013-05-21 09:05 | MYT2 | SHORT RURAL |  | 16 | 310 | 4960 | 0.043162 | 0.00013923 | 0
2013-05-21 09:05 | LGA14 | LONG RURAL |  | 1 | 338 | 338 | 0.0013088 | 3.8723e-06 | 0
2013-05-23 09:09 | LGA14 | LONG RURAL |  | 88 | 285 | 25080 | 0.097118 | 0.00034076 | 0
2013-05-22 13:40 | WYK24 | SHORT RURAL |  | 1 | 35 | 35 | 0.00030457 | 8.702e-06 | 0
2013-05-22 12:20 | WYK24 | SHORT RURAL |  | 5 | 55 | 275 | 0.002393 | 4.351e-05 | 0
2013-05-22 10:00 | WYK24 | SHORT RURAL |  | 19 | 40 | 760 | 0.0066135 | 0.00016534 | 0
2013-05-21 13:30 | WYK12 | SHORT RURAL |  | 1 | 45 | 45 | 0.00039159 | 8.702e-06 | 0
2013-05-21 08:58 | SLE31 | LONG RURAL |  | 557 | 398 | 221686 | 0.85844 | 0.0021569 | 0
2013-05-22 10:20 | WYK12 | SHORT RURAL |  | 11 | 220 | 2420 | 0.021059 | 9.5722e-05 | 0
2013-05-22 09:00 | WYK12 | SHORT RURAL |  | 66 | 60 | 3960 | 0.03446 | 0.00057433 | 0
2013-05-22 09:40 | BRT11 | SHORT RURAL |  | 24 | 200 | 4800 | 0.041769 | 0.00020885 | 0
2013-05-22 08:50 | WN5 | LONG RURAL |  | 41 | 367 | 15047 | 0.058267 | 0.00015876 | 0
2013-05-22 09:00 | FTR21 | LONG RURAL |  | 50 | 204 | 10200 | 0.039498 | 0.00019362 | 0
2013-05-22 09:25 | MWTS21 | URBAN |  | 88 | 101 | 8888 | 0.030961 | 0.00030655 | 0
2013-05-22 12:00 | MWTS11 | SHORT RURAL |  | 55 | 117 | 6435 | 0.055997 | 0.00047861 | 0
2013-05-22 09:30 | WGI22 | LONG RURAL |  | 2 | 115 | 230 | 0.00089063 | 7.7446e-06 | 0
2013-05-22 09:00 | LGA11 | LONG RURAL |  | 148 | 490 | 72520 | 0.28082 | 0.0005731 | 0
2013-05-23 09:40 | KLK1 | SHORT RURAL |  | 79 | 338 | 26702 | 0.23236 | 0.00068746 | 0
2013-05-22 08:05 | LDL23 | LONG RURAL |  | 39 | 125 | 4875 | 0.018878 | 0.00015102 | 0
2013-05-23 09:10 | KLK2 | SHORT RURAL |  | 39 | 240 | 9360 | 0.08145 | 0.00033938 | 0
2013-05-22 14:10 | BWA23 | SHORT RURAL |  | 1 | 20 | 20 | 0.00017404 | 8.702e-06 | 0
2013-05-17 08:30 | SLE32 | SHORT RURAL |  | 1 | 290 | 290 | 0.0025236 | 8.702e-06 | 0
2013-05-24 09:00 | BRT22 | SHORT RURAL |  | 72 | 255 | 18360 | 0.15977 | 0.00062654 | 0
2013-05-22 13:20 | SLE31 | LONG RURAL |  | 7 | 80 | 560 | 0.0021685 | 2.7106e-05 | 0
2013-05-22 08:35 | SLE31 | LONG RURAL |  | 3 | 370 | 1110 | 0.0042983 | 1.1617e-05 | 0
2013-05-22 09:40 | WGL21 | LONG RURAL |  | 55 | 215 | 11825 | 0.04579 | 0.00021298 | 0
2013-05-16 08:38 | WN5 | LONG RURAL |  | 9 | 297 | 2673 | 0.010351 | 3.4851e-05 | 0
2013-05-16 11:00 | BN1 | LONG RURAL |  | 1 | 70 | 70 | 0.00027106 | 3.8723e-06 | 0
2013-05-21 10:15 | WN4 | SHORT RURAL |  | 1 | 335 | 335 | 0.0029152 | 8.702e-06 | 0
2013-05-21 08:40 | WGL12 | LONG RURAL |  | 38 | 275 | 10450 | 0.040466 | 0.00014715 | 0
2013-05-22 08:30 | CLN12 | SHORT RURAL |  | 138 | 365 | 50370 | 0.43832 | 0.0012009 | 0
2013-05-23 11:10 | WT11 | URBAN |  | 78 | 115 | 8970 | 0.031247 | 0.00027171 | 0
2013-05-24 09:08 | DRN11 | URBAN |  | 283 | 217 | 61411 | 0.21392 | 0.00098583 | 0
2013-05-24 09:10 | LGA11 | LONG RURAL |  | 64 | 196.1875 | 12556 | 0.048621 | 0.00024783 | 0
2013-05-24 09:30 | LGA13 | LONG RURAL |  | 7 | 120 | 840 | 0.0032527 | 2.7106e-05 | 0
2013-05-24 12:20 | LGA13 | LONG RURAL |  | 1 | 80 | 80 | 0.00030979 | 3.8723e-06 | 0
2013-05-24 09:30 | PHI11 | SHORT RURAL |  | 40 | 235 | 9400 | 0.081799 | 0.00034808 | 0
2013-05-24 09:10 | FTR21 | LONG RURAL |  | 22 | 265 | 5830 | 0.022576 | 8.5191e-05 | 0
2013-05-24 09:00 | WGI22 | LONG RURAL |  | 4 | 405 | 1620 | 0.0062731 | 1.5489e-05 | 0
2013-05-24 09:45 | WYK12 | SHORT RURAL |  | 34 | 26 | 884 | 0.0076925 | 0.00029587 | 0
2013-05-24 09:00 | WO14 | URBAN |  | 53 | 205 | 10865 | 0.037848 | 0.00018462 | 0
2013-05-24 09:15 | MOE22 | LONG RURAL |  | 93 | 145 | 13485 | 0.052218 | 0.00036013 | 0
2013-05-24 09:20 | WYK24 | SHORT RURAL |  | 4 | 81 | 324 | 0.0028194 | 3.4808e-05 | 0
2013-05-24 08:43 | LLG14 | SHORT RURAL |  | 2 | 53 | 106 | 0.00092241 | 1.7404e-05 | 0
2013-05-19 09:00 | BRT11 | SHORT RURAL |  | 21 | 160 | 3360 | 0.029239 | 0.00018274 | 0
2013-05-19 12:00 | BRT11 | SHORT RURAL |  | 29 | 110 | 3190 | 0.027759 | 0.00025236 | 0
2013-05-22 14:10 | WGL12 | LONG RURAL |  | 5 | 50 | 250 | 0.00096808 | 1.9362e-05 | 0
2013-05-22 08:35 | ELM33 | SHORT RURAL |  | 62 | 413.4194 | 25632 | 0.22305 | 0.00053952 | 0
2013-05-20 09:13 | SLE32 | SHORT RURAL |  | 92 | 217 | 19964 | 0.17373 | 0.00080058 | 0
2013-05-22 08:45 | SLE31 | LONG RURAL |  | 9 | 145 | 1305 | 0.0050534 | 3.4851e-05 | 0
2013-05-23 08:10 | MWTS12 | URBAN |  | 88 | 262 | 23056 | 0.080315 | 0.00030655 | 0
2013-05-20 09:00 | BDL6 | SHORT RURAL |  | 1 | 40 | 40 | 0.00034808 | 8.702e-06 | 0
2013-05-19 09:00 | SMR2 | SHORT RURAL |  | 55 | 265 | 14575 | 0.12683 | 0.00047861 | 0
2013-05-20 09:45 | DRN21 | URBAN |  | 169 | 425 | 71825 | 0.2502 | 0.00058871 | 0
2013-05-17 09:00 | RWN24 | SHORT RURAL |  | 69 | 300 | 20700 | 0.18013 | 0.00060044 | 0
2013-05-14 12:40 | NRN12 | URBAN |  | 12 | 47 | 564 | 0.0019647 | 4.1802e-05 | 0
2013-05-20 10:30 | BGE12 | SHORT RURAL |  | 10 | 35 | 350 | 0.0030457 | 8.702e-05 | 0
2013-05-21 09:12 | HPK13 | URBAN |  | 269 | 361 | 97109 | 0.33828 | 0.00093706 | 0
2013-05-24 12:45 | DRN11 | URBAN |  | 67 | 120 | 8040 | 0.028007 | 0.00023339 | 0
2013-05-25 08:40 | WYK24 | SHORT RURAL |  | 60 | 310 | 18600 | 0.16186 | 0.00052212 | 0
2013-05-24 11:55 | WYK12 | SHORT RURAL |  | 76 | 197 | 14972 | 0.13029 | 0.00066135 | 0
2013-05-24 11:04 | WYK12 | SHORT RURAL |  | 80 | 121 | 9680 | 0.084235 | 0.00069616 | 0
2013-05-22 08:55 | OFR23 | LONG RURAL |  | 61 | 180 | 10980 | 0.042518 | 0.00023621 | 0
2013-05-24 08:50 | MFA22 | LONG RURAL |  | 25 | 175 | 4375 | 0.016941 | 9.6808e-05 | 0
2013-05-24 12:05 | WGL24 | LONG RURAL |  | 1 | 50 | 50 | 0.00019362 | 3.8723e-06 | 0
2013-05-24 03:45 | WGL24 | LONG RURAL |  | 4 | 650 | 2600 | 0.010068 | 1.5489e-05 | 0
2013-05-23 08:30 | BWN14 | SHORT RURAL |  | 87 | 356 | 30972 | 0.26952 | 0.00075707 | 0
2013-05-23 09:20 | WGL12 | LONG RURAL |  | 2 | 56 | 112 | 0.0004337 | 7.7446e-06 | 0
2013-05-23 10:55 | WGL12 | LONG RURAL |  | 2 | 75 | 150 | 0.00058085 | 7.7446e-06 | 0
2013-05-24 08:30 | PHM12 | SHORT RURAL |  | 3 | 135 | 405 | 0.0035243 | 2.6106e-05 | 0
2013-05-24 11:30 | WGL12 | LONG RURAL |  | 2 | 50 | 100 | 0.00038723 | 7.7446e-06 | 0
2013-05-20 10:30 | ELM15 | SHORT RURAL |  | 207 | 200.5652 | 41517 | 0.36128 | 0.0018013 | 0
2013-05-10 09:45 | PHI11 | SHORT RURAL |  | 3 | 65 | 195 | 0.0016969 | 2.6106e-05 | 0
2013-05-18 08:30 | CLN23 | SHORT RURAL |  | 6 | 85 | 510 | 0.004438 | 5.2212e-05 | 0
2013-05-24 08:47 | OFR23 | LONG RURAL |  | 74 | 364.8919 | 27002 | 0.10456 | 0.00028655 | 0
2013-05-19 09:10 | MSD4 | LONG RURAL |  | 8 | 240 | 1920 | 0.0074348 | 3.0979e-05 | 0
2013-05-18 10:56 | CLN23 | SHORT RURAL |  | 1 | 9 | 9 | 7.8318e-05 | 8.702e-06 | 0
2013-05-21 10:40 | EPG13 | SHORT RURAL |  | 5 | 155 | 775 | 0.006744 | 4.351e-05 | 0
2013-05-21 13:58 | BN6 | LONG RURAL |  | 2 | 84 | 168 | 0.00065055 | 7.7446e-06 | 0
2013-05-26 09:15 | WGL13 | SHORT RURAL |  | 250 | 315 | 78750 | 0.68528 | 0.0021755 | 0
2013-05-26 10:50 | MWTS32 | SHORT RURAL |  | 3 | 145 | 435 | 0.0037854 | 2.6106e-05 | 0
2013-05-26 09:00 | MWTS31 | SHORT RURAL |  | 44 | 185 | 8140 | 0.070834 | 0.00038289 | 0
2013-05-26 09:00 | MWTS32 | SHORT RURAL |  | 91 | 242 | 22022 | 0.19163 | 0.00079188 | 0
2013-05-26 08:30 | LGA11 | LONG RURAL |  | 5 | 255 | 1275 | 0.0049372 | 1.9362e-05 | 0
2013-05-26 08:48 | LGA22 | SHORT RURAL |  | 117 | 329 | 38493 | 0.33496 | 0.0010181 | 0
2013-05-26 10:20 | WYK24 | SHORT RURAL |  | 66 | 275 | 18150 | 0.15794 | 0.00057433 | 0
2013-05-26 09:30 | WYK24 | SHORT RURAL |  | 22 | 380 | 8360 | 0.072748 | 0.00019144 | 0
2013-05-26 08:35 | WYK11 | SHORT RURAL |  | 89 | 387 | 34443 | 0.29972 | 0.00077448 | 0
2013-05-26 08:30 | FTR12 | LONG RURAL |  | 70 | 510 | 35700 | 0.13824 | 0.00027106 | 0
2013-05-22 09:05 | ALA01 | LONG RURAL |  | 134 | 355 | 47570 | 0.18421 | 0.00051889 | 0
2013-05-24 09:38 | MYT7 | LONG RURAL |  | 17 | 140 | 2380 | 0.0092161 | 6.5829e-05 | 0
2013-05-24 09:15 | MYT7 | LONG RURAL |  | 4 | 145 | 580 | 0.0022459 | 1.5489e-05 | 0
2013-05-26 08:30 | BDL3 | SHORT RURAL |  | 633 | 186.128 | 117819 | 1.0253 | 0.0055083 | 0
2013-05-23 10:05 | MFA21 | LONG RURAL |  | 18 | 325 | 5850 | 0.022653 | 6.9702e-05 | 0
2013-05-24 09:15 | BDL5 | LONG RURAL |  | 14 | 25 | 350 | 0.0013553 | 5.4212e-05 | 0
2013-05-24 08:42 | BDL5 | LONG RURAL |  | 4 | 150 | 600 | 0.0023234 | 1.5489e-05 | 0
2013-05-24 11:25 | BDL5 | LONG RURAL |  | 1 | 75 | 75 | 0.00029042 | 3.8723e-06 | 0
2013-05-22 09:15 | BGE24 | SHORT RURAL |  | 27 | 120 | 3240 | 0.028194 | 0.00023495 | 0
2013-05-22 09:46 | HPK13 | URBAN |  | 114 | 191 | 21774 | 0.075849 | 0.00039712 | 0
2013-05-22 09:30 | UWY1 | SHORT RURAL |  | 18 | 405 | 7290 | 0.063437 | 0.00015664 | 0
2013-05-22 12:45 | FGY23 | URBAN |  | 67 | 160 | 10720 | 0.037343 | 0.00023339 | 0
2013-05-24 14:11 | BDL5 | LONG RURAL |  | 4 | 35 | 140 | 0.00054212 | 1.5489e-05 | 0
2013-05-23 09:33 | BGE24 | SHORT RURAL |  | 141 | 366 | 51606 | 0.44907 | 0.001227 | 0
2013-05-23 08:45 | BGE22 | SHORT RURAL |  | 108 | 488.7037 | 52780 | 0.45929 | 0.00093981 | 0
2013-05-23 08:30 | FGY22 | URBAN |  | 97 | 610 | 59170 | 0.20612 | 0.0003379 | 0
2013-05-22 08:50 | MFA21 | LONG RURAL |  | 4 | 170 | 680 | 0.0026332 | 1.5489e-05 | 0
2013-05-21 10:52 | ALA01 | LONG RURAL |  | 48 | 238 | 11424 | 0.044237 | 0.00018587 | 0
2013-05-11 09:45 | DRN12 | URBAN |  | 19 | 43 | 817 | 0.002846 | 6.6186e-05 | 0
2013-05-27 09:30 | MWTS13 | SHORT RURAL |  | 101 | 185 | 18685 | 0.1626 | 0.0008789 | 0
2013-05-27 10:25 | WGL13 | SHORT RURAL |  | 2 | 65 | 130 | 0.0011313 | 1.7404e-05 | 0
2013-05-27 09:15 | MOE21 | SHORT RURAL |  | 1 | 95 | 95 | 0.00082669 | 8.702e-06 | 0
2013-05-27 08:51 | WYK23 | SHORT RURAL |  | 647 | 385 | 249095 | 2.1676 | 0.0056302 | 0
2013-05-27 09:38 | WN4 | SHORT RURAL |  | 1 | 159 | 159 | 0.0013836 | 8.702e-06 | 0
2013-05-27 08:39 | SLE32 | SHORT RURAL |  | 165 | 211 | 34815 | 0.30296 | 0.0014358 | 0
2013-05-27 11:07 | MYT7 | LONG RURAL |  | 57 | 115 | 6555 | 0.025383 | 0.00022072 | 0
2013-05-27 10:20 | BN1 | LONG RURAL |  | 1 | 160 | 160 | 0.00061957 | 3.8723e-06 | 0
2013-05-27 09:45 | MYT7 | LONG RURAL |  | 1 | 120 | 120 | 0.00046468 | 3.8723e-06 | 0
2013-05-24 09:12 | BRT21 | SHORT RURAL |  | 5 | 388 | 1940 | 0.016882 | 4.351e-05 | 0
2013-05-21 09:05 | BWR23 | URBAN |  | 52 | 250 | 13000 | 0.045285 | 0.00018114 | 0
2013-05-24 13:35 | BDL5 | LONG RURAL |  | 2 | 40 | 80 | 0.00030979 | 7.7446e-06 | 0
2013-05-15 17:00 | MOE24 | SHORT RURAL |  | 24 | 135 | 3240 | 0.028194 | 0.00020885 | 0
2013-05-27 08:35 | MFA23 | SHORT RURAL |  | 69 | 45 | 3105 | 0.02702 | 0.00060044 | 0
2013-05-27 08:35 | SLE32 | SHORT RURAL |  | 35 | 325 | 11375 | 0.098985 | 0.00030457 | 0
2013-05-21 08:55 | CYN14 | URBAN |  | 72 | 185 | 13320 | 0.0464 | 0.00025081 | 0
2013-05-21 09:15 | TT5 | URBAN |  | 101 | 355 | 35855 | 0.1249 | 0.00035183 | 0
2013-05-21 08:55 | BWR23 | URBAN |  | 78 | 110 | 8580 | 0.029888 | 0.00027171 | 0
2013-05-21 09:45 | RWT22 | URBAN |  | 126 | 300 | 37800 | 0.13168 | 0.00043892 | 0
2013-05-28 09:00 | BRT22 | SHORT RURAL |  | 211 | 340 | 71740 | 0.62428 | 0.0018361 | 0
2013-05-29 08:32 | WO22 | URBAN |  | 248 | 373 | 92504 | 0.32224 | 0.0008639 | 0
2013-05-21 13:50 | BWR13 | SHORT RURAL |  | 97 | 85 | 8245 | 0.071748 | 0.00084409 | 0
2013-05-22 08:56 | EPG14 | URBAN |  | 124 | 334 | 41416 | 0.14427 | 0.00043195 | 0
2013-05-22 08:49 | RWN24 | SHORT RURAL |  | 271 | 431 | 116801 | 1.0164 | 0.0023582 | 0
2013-05-23 08:40 | RWT22 | URBAN |  | 93 | 335 | 31155 | 0.10853 | 0.00032396 | 0
2013-05-11 11:40 | WYK11 | SHORT RURAL |  | 2 | 35 | 70 | 0.00060914 | 1.7404e-05 | 0
2013-05-29 09:20 | TGN31 | LONG RURAL |  | 76 | 350 | 26600 | 0.103 | 0.0002943 | 0
2013-05-28 09:05 | MWTS21 | URBAN |  | 41 | 251 | 10291 | 0.035849 | 0.00014282 | 0
2013-05-27 13:25 | MOE21 | SHORT RURAL |  | 1 | 85 | 85 | 0.00073967 | 8.702e-06 | 0
2013-05-28 09:26 | MWE1 | URBAN |  | 1 | 85 | 85 | 0.0002961 | 3.4835e-06 | 0
2013-05-30 09:30 | WO32 | URBAN |  | 53 | 160 | 8480 | 0.02954 | 0.00018462 | 0
2013-05-30 09:50 | WO32 | URBAN |  | 39 | 80 | 3120 | 0.010868 | 0.00013586 | 0
2013-05-27 11:15 | MOE21 | SHORT RURAL |  | 2 | 55 | 110 | 0.00095722 | 1.7404e-05 | 0
2013-05-28 12:05 | TGN23 | SHORT RURAL |  | 1 | 40 | 40 | 0.00034808 | 8.702e-06 | 0
2013-05-28 09:49 | WGL13 | SHORT RURAL |  | 4 | 76 | 304 | 0.0026454 | 3.4808e-05 | 0
2013-05-28 09:00 | TGN23 | SHORT RURAL |  | 2 | 271 | 542 | 0.0047165 | 1.7404e-05 | 0
2013-05-28 09:20 | ELM13 | URBAN |  | 1 | 115 | 115 | 0.0004006 | 3.4835e-06 | 0
2013-05-28 13:05 | TGN31 | LONG RURAL |  | 1 | 106 | 106 | 0.00041047 | 3.8723e-06 | 0
2013-05-28 11:25 | WGL13 | SHORT RURAL |  | 4 | 75 | 300 | 0.0026106 | 3.4808e-05 | 0
2013-05-29 08:45 | MOE13 | SHORT RURAL |  | 57 | 229 | 13053 | 0.11359 | 0.00049601 | 0
2013-05-29 10:34 | MOE22 | LONG RURAL |  | 117 | 286 | 33462 | 0.12958 | 0.00045306 | 0
2013-05-29 09:28 | TGN11 | SHORT RURAL |  | 67 | 279 | 18693 | 0.16267 | 0.00058303 | 0
2013-05-30 09:05 | WGL21 | LONG RURAL |  | 194 | 273 | 52962 | 0.20509 | 0.00075123 | 0
2013-05-30 09:10 | TGN11 | SHORT RURAL |  | 71 | 175 | 12425 | 0.10812 | 0.00061784 | 0
2013-05-28 09:25 | WGI24 | URBAN |  | 107 | 160 | 17120 | 0.059637 | 0.00037273 | 0
2013-05-29 09:55 | FTR21 | LONG RURAL |  | 81 | 275 | 22275 | 0.086256 | 0.00031366 | 0
2013-05-28 09:34 | PHI13 | URBAN |  | 309 | 340 | 105060 | 0.36597 | 0.0010764 | 0
2013-05-28 08:50 | WYK24 | SHORT RURAL |  | 1 | 44 | 44 | 0.00038289 | 8.702e-06 | 0
2013-05-28 10:05 | WYK24 | SHORT RURAL |  | 1 | 40 | 40 | 0.00034808 | 8.702e-06 | 0
2013-05-28 11:17 | WYK24 | SHORT RURAL |  | 1 | 38 | 38 | 0.00033067 | 8.702e-06 | 0
2013-05-28 13:05 | WYK24 | SHORT RURAL |  | 2 | 80 | 160 | 0.0013923 | 1.7404e-05 | 0
2013-05-28 10:32 | WYK24 | SHORT RURAL |  | 2 | 31 | 62 | 0.00053952 | 1.7404e-05 | 0
2013-05-28 11:35 | WYK24 | SHORT RURAL |  | 1 | 38 | 38 | 0.00033067 | 8.702e-06 | 0
2013-05-28 08:32 | WYK12 | SHORT RURAL |  | 69 | 151 | 10419 | 0.090666 | 0.00060044 | 0
2013-05-28 12:00 | WYK12 | SHORT RURAL |  | 11 | 47 | 517 | 0.0044989 | 9.5722e-05 | 0
2013-05-29 09:03 | WGI23 | SHORT RURAL |  | 1 | 53 | 53 | 0.0004612 | 8.702e-06 | 0
2013-05-30 09:35 | MWTS31 | SHORT RURAL |  | 5 | 295 | 1475 | 0.012835 | 4.351e-05 | 0
2013-05-30 11:15 | MOE32 | SHORT RURAL |  | 2 | 245 | 490 | 0.004264 | 1.7404e-05 | 0
2013-05-29 09:10 | LGA11 | LONG RURAL |  | 38 | 130 | 4940 | 0.019129 | 0.00014715 | 0
2013-05-28 09:48 | WGI22 | LONG RURAL |  | 34 | 237 | 8058 | 0.031203 | 0.00013166 | 0
2013-05-28 09:26 | WGI22 | LONG RURAL |  | 35 | 2 | 70 | 0.00027106 | 0.00013553 | 0
2013-05-29 09:40 | FTR21 | LONG RURAL |  | 1 | 50 | 50 | 0.00019362 | 3.8723e-06 | 0
2013-05-29 09:19 | FTR21 | LONG RURAL |  | 1 | 297 | 297 | 0.0011501 | 3.8723e-06 | 0
2013-05-29 08:45 | CRE22 | URBAN |  | 1051 | 268 | 281668 | 0.98119 | 0.0036611 | 0
2013-05-29 09:10 | WYK12 | SHORT RURAL |  | 6 | 112 | 672 | 0.0058477 | 5.2212e-05 | 0
2013-05-29 11:50 | WYK12 | SHORT RURAL |  | 1 | 53 | 53 | 0.0004612 | 8.702e-06 | 0
2013-05-29 08:30 | WYK23 | SHORT RURAL |  | 34 | 380 | 12920 | 0.11243 | 0.00029587 | 0
2013-06-03 09:15 | WOTS12 | URBAN |  | 9 | 95 | 855 | 0.0029784 | 3.1351e-05 | 0
2013-05-28 09:00 | PHM14 | LONG RURAL |  | 128 | 230 | 29440 | 0.114 | 0.00049566 | 0
2013-05-28 09:00 | WGL13 | SHORT RURAL |  | 69 | 248 | 17112 | 0.14891 | 0.00060044 | 0
2013-05-28 09:30 | ELM13 | URBAN |  | 2 | 100 | 200 | 0.0006967 | 6.967e-06 | 0
2013-05-30 09:09 | LGA11 | LONG RURAL |  | 2 | 112 | 224 | 0.0008674 | 7.7446e-06 | 0
2013-05-27 12:15 | MYT7 | LONG RURAL |  | 4 | 125 | 500 | 0.0019362 | 1.5489e-05 | 0
2013-05-28 09:10 | BN1 | LONG RURAL |  | 28 | 330 | 9240 | 0.03578 | 0.00010842 | 0
2013-05-30 09:30 | FTR21 | LONG RURAL |  | 7 | 240 | 1680 | 0.0065055 | 2.7106e-05 | 0
2013-05-30 09:05 | WGI23 | SHORT RURAL |  | 23 | 295 | 6785 | 0.059043 | 0.00020015 | 0
2013-05-30 09:30 | MWTS14 | SHORT RURAL |  | 50 | 324 | 16200 | 0.14097 | 0.0004351 | 0
2013-05-27 13:30 | MYT7 | LONG RURAL |  | 2 | 50 | 100 | 0.00038723 | 7.7446e-06 | 0
2013-05-28 08:50 | BDL6 | SHORT RURAL |  | 2 | 310 | 620 | 0.0053952 | 1.7404e-05 | 0
2013-05-28 08:40 | SLE31 | LONG RURAL |  | 10 | 500 | 5000 | 0.019362 | 3.8723e-05 | 0
2013-05-28 08:55 | BDL5 | LONG RURAL |  | 14 | 347 | 4858 | 0.018812 | 5.4212e-05 | 0
2013-05-28 10:00 | SLE31 | LONG RURAL |  | 1 | 270 | 270 | 0.0010455 | 3.8723e-06 | 0
2013-05-28 09:15 | MYT7 | LONG RURAL |  | 9 | 215 | 1935 | 0.0074929 | 3.4851e-05 | 0
2013-05-29 09:04 | WGL11 | SHORT RURAL |  | 243 | 410 | 99630 | 0.86698 | 0.0021146 | 0
2013-05-30 10:10 | LGA24 | SHORT RURAL |  | 13 | 215 | 2795 | 0.024322 | 0.00011313 | 0
2013-05-23 09:00 | RWN31 | SHORT RURAL |  | 120 | 345 | 41400 | 0.36026 | 0.0010442 | 0
2013-05-29 09:40 | MFA22 | LONG RURAL |  | 19 | 375 | 7125 | 0.02759 | 7.3574e-05 | 0
2013-05-29 09:11 | BDL6 | SHORT RURAL |  | 16 | 209 | 3344 | 0.029099 | 0.00013923 | 0
2013-05-29 09:05 | MFA22 | LONG RURAL |  | 3 | 325 | 975 | 0.0037755 | 1.1617e-05 | 0
2013-05-30 09:35 | MOE22 | LONG RURAL |  | 3 | 175 | 525 | 0.002033 | 1.1617e-05 | 0
2013-05-30 09:40 | WN3 | LONG RURAL |  | 1 | 165 | 165 | 0.00063893 | 3.8723e-06 | 0
2013-05-28 09:20 | WGL24 | LONG RURAL |  | 3 | 210 | 630 | 0.0024396 | 1.1617e-05 | 0
2013-05-23 11:00 | KMS1 | SHORT RURAL |  | 49 | 135 | 6615 | 0.057564 | 0.0004264 | 0
2013-05-21 08:50 | WN2 | LONG RURAL |  | 7 | 355 | 2485 | 0.0096227 | 2.7106e-05 | 0
2013-05-27 13:35 | OFR23 | LONG RURAL |  | 13 | 25 | 325 | 0.0012585 | 5.034e-05 | 0
2013-05-23 08:55 | BGE12 | SHORT RURAL |  | 51 | 230 | 11730 | 0.10207 | 0.0004438 | 0
2013-05-26 08:40 | OFR23 | LONG RURAL |  | 36 | 175 | 6300 | 0.024396 | 0.0001394 | 0
2013-05-26 09:11 | WN2 | LONG RURAL |  | 249 | 375.498 | 93499 | 0.36206 | 0.00096421 | 0
2013-05-24 08:50 | OFR23 | LONG RURAL |  | 2 | 287 | 574 | 0.0022227 | 7.7446e-06 | 0
2013-05-24 09:05 | CRE33 | SHORT RURAL |  | 3 | 15 | 45 | 0.00039159 | 2.6106e-05 | 0
2013-05-24 10:30 | LLG14 | SHORT RURAL |  | 13 | 20 | 260 | 0.0022625 | 0.00011313 | 0
2013-05-24 10:20 | LLG14 | SHORT RURAL |  | 3 | 25 | 75 | 0.00065265 | 2.6106e-05 | 0
2013-05-24 11:05 | LLG14 | SHORT RURAL |  | 2 | 20 | 40 | 0.00034808 | 1.7404e-05 | 0
2013-05-24 11:10 | LLG14 | SHORT RURAL |  | 2 | 8 | 16 | 0.00013923 | 1.7404e-05 | 0
2013-05-24 11:40 | LLG14 | SHORT RURAL |  | 2 | 20 | 40 | 0.00034808 | 1.7404e-05 | 0
2013-05-24 11:45 | LLG14 | SHORT RURAL |  | 4 | 25 | 100 | 0.0008702 | 3.4808e-05 | 0
2013-05-31 09:20 | MWTS22 | SHORT RURAL |  | 20 | 185 | 3700 | 0.032197 | 0.00017404 | 0
2013-05-31 09:41 | MOE22 | LONG RURAL |  | 179 | 244 | 43676 | 0.16913 | 0.00069314 | 0
2013-05-31 09:00 | LGA22 | SHORT RURAL |  | 2 | 38 | 76 | 0.00066135 | 1.7404e-05 | 0
2013-05-31 10:00 | TGN31 | LONG RURAL |  | 55 | 90 | 4950 | 0.019168 | 0.00021298 | 0
2013-05-31 09:20 | TGN12 | SHORT RURAL |  | 96 | 204 | 19584 | 0.17042 | 0.00083539 | 0
2013-05-31 09:44 | LDL23 | LONG RURAL |  | 1 | 25 | 25 | 9.6808e-05 | 3.8723e-06 | 0
2013-05-31 09:12 | LGA14 | LONG RURAL |  | 41 | 163 | 6683 | 0.025879 | 0.00015876 | 0
2013-05-31 09:00 | FTR21 | LONG RURAL |  | 1 | 349 | 349 | 0.0013514 | 3.8723e-06 | 0
2013-05-31 09:25 | LGA13 | LONG RURAL |  | 23 | 35 | 805 | 0.0031172 | 8.9063e-05 | 0
2013-05-31 09:00 | LGA13 | LONG RURAL |  | 59 | 180 | 10620 | 0.041124 | 0.00022847 | 0
2013-05-31 08:45 | WYK11 | SHORT RURAL |  | 32 | 210 | 6720 | 0.058477 | 0.00027846 | 0
2013-05-31 08:05 | WYK11 | SHORT RURAL |  | 2 | 149 | 298 | 0.0025932 | 1.7404e-05 | 0
2013-05-31 09:05 | LGA11 | LONG RURAL |  | 40 | 15 | 600 | 0.0023234 | 0.00015489 | 0
2013-05-31 09:20 | MOE21 | SHORT RURAL |  | 8 | 145 | 1160 | 0.010094 | 6.9616e-05 | 0
2013-05-26 09:10 | CLN23 | SHORT RURAL |  | 82 | 415.4146 | 34064 | 0.29642 | 0.00071356 | 0
2013-05-26 09:30 | LLG13 | SHORT RURAL |  | 1227 | 3 | 3681 | 0.032032 | 0.010677 | 0
2013-05-30 09:40 | MYT7 | LONG RURAL |  | 2 | 38 | 76 | 0.0002943 | 7.7446e-06 | 0
2013-05-30 10:40 | MYT7 | LONG RURAL |  | 2 | 49 | 98 | 0.00037949 | 7.7446e-06 | 0
2013-05-29 09:00 | MWTS14 | SHORT RURAL |  | 37 | 447 | 16539 | 0.14392 | 0.00032197 | 0
2013-05-30 11:15 | WGL24 | LONG RURAL |  | 4 | 65 | 260 | 0.0010068 | 1.5489e-05 | 0
2013-05-30 08:30 | BDL1 | LONG RURAL |  | 10 | 270 | 2700 | 0.010455 | 3.8723e-05 | 0
2013-05-24 09:01 | RWN31 | SHORT RURAL |  | 216 | 231 | 49896 | 0.43419 | 0.0018796 | 0
2013-05-21 14:56 | LGA12 | SHORT RURAL |  | 533 | 1 | 533 | 0.0046382 | 0.0046382 | 0
2013-05-26 08:30 | BRA33 | URBAN |  | 169 | 210 | 35490 | 0.12363 | 0.00058871 | 0
2013-05-30 10:33 | CLN12 | SHORT RURAL |  | 154 | 237 | 36498 | 0.3176 | 0.0013401 | 0
2013-05-30 08:50 | MFA22 | LONG RURAL |  | 19 | 335 | 6365 | 0.024647 | 7.3574e-05 | 0
2013-05-30 08:30 | BWN12 | URBAN |  | 105 | 263 | 27615 | 0.096196 | 0.00036577 | 0
2013-05-23 10:40 | WT7 | URBAN |  | 90 | 256.5 | 23085 | 0.080416 | 0.00031351 | 0
2013-05-23 09:58 | WT15 | URBAN |  | 511 | 290 | 148190 | 0.51622 | 0.0017801 | 0
2013-05-30 09:10 | BDL5 | LONG RURAL |  | 13 | 181 | 2353 | 0.0091116 | 5.034e-05 | 0
2013-05-31 08:50 | WGL11 | SHORT RURAL |  | 1 | 335 | 335 | 0.0029152 | 8.702e-06 | 0
2013-05-25 08:30 | CYN21 | URBAN |  | 175 | 415 | 72625 | 0.25299 | 0.00060961 | 0
2013-05-27 09:15 | FGY34 | URBAN |  | 62 | 285 | 17670 | 0.061553 | 0.00021598 | 0
2013-05-27 08:45 | LYD14 | SHORT RURAL |  | 53 | 305 | 16165 | 0.14067 | 0.0004612 | 0
2013-05-26 08:15 | BWR12 | URBAN |  | 36 | 215 | 7740 | 0.026962 | 0.00012541 | 0
2013-05-24 09:09 | DRN14 | SHORT RURAL |  | 46 | 147 | 6762 | 0.058843 | 0.00040029 | 0
2013-05-31 10:30 | TGN14 | LONG RURAL |  | 5 | 59 | 295 | 0.0011423 | 1.9362e-05 | 0
2013-05-31 10:00 | LGA22 | SHORT RURAL |  | 2 | 28 | 56 | 0.00048731 | 1.7404e-05 | 0
2013-05-31 12:10 | LGA22 | SHORT RURAL |  | 2 | 45 | 90 | 0.00078318 | 1.7404e-05 | 0
2013-05-31 12:58 | MOE24 | SHORT RURAL |  | 32 | 22 | 704 | 0.0061262 | 0.00027846 | 0
2013-05-31 13:10 | LGA23 | LONG RURAL |  | 43 | 25 | 1075 | 0.0041627 | 0.00016651 | 0
2013-05-27 09:56 | CRE23 | URBAN |  | 40 | 93 | 3720 | 0.012959 | 0.00013934 | 0
2013-05-31 08:40 | BDL6 | SHORT RURAL |  | 9 | 215 | 1935 | 0.016838 | 7.8318e-05 | 0
2013-05-23 09:00 | WGL12 | LONG RURAL |  | 11 | 225 | 2475 | 0.009584 | 4.2595e-05 | 0
2013-05-31 09:00 | BDL1 | LONG RURAL |  | 3 | 174 | 522 | 0.0020213 | 1.1617e-05 | 0
2013-05-23 13:05 | DRN12 | URBAN |  | 1 | 50 | 50 | 0.00017417 | 3.4835e-06 | 0
2013-05-26 08:30 | DRN12 | URBAN |  | 124 | 430 | 53320 | 0.18574 | 0.00043195 | 0
2013-05-26 11:03 | ELM32 | URBAN |  | 64 | 18 | 1152 | 0.004013 | 0.00022294 | 0
2013-05-26 11:48 | LGA12 | SHORT RURAL |  | 131 | 157 | 20567 | 0.17897 | 0.00114 | 0
2013-05-27 10:12 | WT9 | URBAN |  | 35 | 142 | 4970 | 0.017313 | 0.00012192 | 0
2013-05-27 09:05 | ELM12 | SHORT RURAL |  | 56 | 350 | 19600 | 0.17056 | 0.00048731 | 0
2013-05-27 09:00 | EPG12 | URBAN |  | 128 | 355 | 45440 | 0.15829 | 0.00044589 | 0
2013-05-29 08:31 | HPK21 | URBAN |  | 30 | 299 | 8970 | 0.031247 | 0.0001045 | 0
2013-05-29 08:31 | HPK23 | URBAN |  | 170 | 309 | 52530 | 0.18299 | 0.00059219 | 0
2013-05-27 13:55 | ELM15 | SHORT RURAL |  | 53 | 115 | 6095 | 0.053039 | 0.0004612 | 0
2013-05-30 10:00 | CRE22 | URBAN |  | 99 | 255 | 25245 | 0.087941 | 0.00034486 | 0
2013-05-30 09:13 | CRE22 | URBAN |  | 325 | 267 | 86775 | 0.30228 | 0.0011321 | 0
2013-05-31 08:30 | BWN12 | URBAN |  | 53 | 280 | 14840 | 0.051695 | 0.00018462 | 0
2013-06-02 09:03 | TGN11 | SHORT RURAL |  | 312 | 87 | 27144 | 0.23621 | 0.002715 | 0
2013-06-02 09:00 | FTR21 | LONG RURAL |  | 104 | 250 | 26000 | 0.10068 | 0.00040272 | 0
2013-06-02 08:46 | BDL1 | LONG RURAL |  | 8 | 205 | 1640 | 0.0063506 | 3.0979e-05 | 0
2013-05-28 11:00 | WT11 | URBAN |  | 122 | 253 | 30866 | 0.10752 | 0.00042498 | 0
2013-05-31 13:55 | BN1 | LONG RURAL |  | 2 | 13 | 26 | 0.00010068 | 7.7446e-06 | 0
2013-06-02 08:35 | BDL3 | SHORT RURAL |  | 24 | 445 | 10680 | 0.092937 | 0.00020885 | 0
2013-06-02 08:30 | BDL1 | LONG RURAL |  | 241 | 203.5519 | 49056 | 0.18996 | 0.00093323 | 0
2013-05-29 09:20 | FGY33 | URBAN |  | 62 | 295 | 18290 | 0.063713 | 0.00021598 | 0
2013-05-29 08:45 | FGY23 | URBAN |  | 14 | 115 | 1610 | 0.0056084 | 4.8769e-05 | 0
2013-05-29 09:35 | WT10 | URBAN |  | 113 | 185 | 20905 | 0.072822 | 0.00039363 | 0
2013-05-30 09:40 | BGE22 | SHORT RURAL |  | 231 | 260 | 60060 | 0.52264 | 0.0020102 | 0
2013-05-30 09:05 | HPK24 | URBAN |  | 136 | 160 | 21760 | 0.075801 | 0.00047375 | 0
2013-05-28 10:17 | DRN12 | URBAN |  | 332 | 95 | 31540 | 0.10987 | 0.0011565 | 0
2013-05-29 09:45 | TT5 | URBAN |  | 136 | 336.7132 | 45793 | 0.15952 | 0.00047375 | 0
2013-05-27 09:15 | BRA33 | URBAN |  | 60 | 235 | 14100 | 0.049117 | 0.00020901 | 0
2013-06-03 09:44 | FTR22 | SHORT RURAL |  | 4 | 181 | 724 | 0.0063002 | 3.4808e-05 | 0
2013-06-03 09:56 | FTR21 | LONG RURAL |  | 2 | 294 | 588 | 0.0022769 | 7.7446e-06 | 0
2013-06-03 09:47 | WT9 | URBAN |  | 152 | 169 | 25688 | 0.089484 | 0.00052949 | 0
2013-05-28 08:45 | RWN26 | SHORT RURAL |  | 37 | 237.1351 | 8774 | 0.076351 | 0.00032197 | 0
2013-05-30 09:05 | WGL21 | LONG RURAL |  | 14 | 300 | 4200 | 0.016264 | 5.4212e-05 | 0
2013-05-31 08:34 | BWN12 | URBAN |  | 113 | 212 | 23956 | 0.08345 | 0.00039363 | 0
2013-05-29 08:40 | RWT11 | URBAN |  | 51 | 200 | 10200 | 0.035532 | 0.00017766 | 0
2013-05-30 08:55 | CYN31 | URBAN |  | 60 | 300 | 18000 | 0.062703 | 0.00020901 | 0
2013-05-30 11:30 | RWT22 | URBAN |  | 86 | 50 | 4300 | 0.014979 | 0.00029958 | 0
2013-05-31 11:10 | RWN31 | SHORT RURAL |  | 322 | 176 | 56672 | 0.49316 | 0.002802 | 0
2013-06-02 13:00 | RWT21 | URBAN |  | 41 | 1 | 41 | 0.00014282 | 0.00014282 | 0
2013-06-03 09:30 | RWN31 | SHORT RURAL |  | 9 | 200 | 1800 | 0.015664 | 7.8318e-05 | 0
2013-06-03 09:05 | BDL6 | SHORT RURAL |  | 2 | 25 | 50 | 0.0004351 | 1.7404e-05 | 0
2013-05-29 12:30 | MYT2 | SHORT RURAL |  | 1 | 18 | 18 | 0.00015664 | 8.702e-06 | 0
2013-05-27 13:20 | BRA33 | URBAN |  | 120 | 60 | 7200 | 0.025081 | 0.00041802 | 0
2013-05-30 08:55 | ELM33 | SHORT RURAL |  | 22 | 462 | 10164 | 0.088447 | 0.00019144 | 0
2013-05-28 09:30 | BWR13 | SHORT RURAL |  | 61 | 320 | 19520 | 0.16986 | 0.00053082 | 0
2013-05-30 08:30 | RWT22 | URBAN |  | 91 | 110 | 10010 | 0.03487 | 0.000317 | 0
2013-06-04 10:30 | TGN31 | LONG RURAL |  | 12 | 270 | 3240 | 0.012546 | 4.6468e-05 | 0
2013-06-04 09:10 | TGN12 | SHORT RURAL |  | 79 | 160 | 12640 | 0.10999 | 0.00068746 | 0
2013-06-04 13:03 | MWTS32 | SHORT RURAL |  | 43 | 37 | 1591 | 0.013845 | 0.00037418 | 0
2013-06-06 08:50 | MOE31 | LONG RURAL |  | 2 | 120 | 240 | 0.00092936 | 7.7446e-06 | 0
2013-06-06 09:35 | MWTS31 | SHORT RURAL |  | 9 | 310 | 2790 | 0.024278 | 7.8318e-05 | 0
2013-06-06 10:00 | MOE31 | LONG RURAL |  | 6 | 90 | 540 | 0.002091 | 2.3234e-05 | 0
2013-06-04 09:35 | MOE13 | SHORT RURAL |  | 113 | 310 | 35030 | 0.30483 | 0.00098332 | 0
2013-06-05 10:00 | MOE13 | SHORT RURAL |  | 30 | 225 | 6750 | 0.058738 | 0.00026106 | 0
2013-06-04 12:30 | WOTS24 | LONG RURAL |  | 2 | 35 | 70 | 0.00027106 | 7.7446e-06 | 0
2013-06-04 09:03 | LGA11 | LONG RURAL |  | 24 | 160 | 3840 | 0.01487 | 9.2936e-05 | 0
2013-06-04 09:05 | LGA14 | LONG RURAL |  | 71 | 305 | 21655 | 0.083855 | 0.00027493 | 0
2013-06-05 11:30 | LGA13 | LONG RURAL |  | 1 | 35 | 35 | 0.00013553 | 3.8723e-06 | 0
2013-06-05 09:40 | LGA13 | LONG RURAL |  | 3 | 45 | 135 | 0.00052276 | 1.1617e-05 | 0
2013-06-04 09:57 | FTR21 | LONG RURAL |  | 1 | 243 | 243 | 0.00094097 | 3.8723e-06 | 0
2013-06-06 09:02 | LGA13 | LONG RURAL |  | 173 | 115 | 19895 | 0.07704 | 0.00066991 | 0
2013-06-04 09:05 | LGA11 | LONG RURAL |  | 148 | 310 | 45880 | 0.17766 | 0.0005731 | 0
2013-06-06 09:10 | LLG12 | SHORT RURAL |  | 27 | 215 | 5805 | 0.050515 | 0.00023495 | 0
2013-06-06 09:15 | FTR21 | LONG RURAL |  | 1 | 95 | 95 | 0.00036787 | 3.8723e-06 | 0
2013-06-06 09:00 | LGA13 | LONG RURAL |  | 36 | 295 | 10620 | 0.041124 | 0.0001394 | 0
2013-06-04 10:10 | MOE22 | LONG RURAL |  | 26 | 10 | 260 | 0.0010068 | 0.00010068 | 0
2013-06-04 13:50 | WYK12 | SHORT RURAL |  | 1 | 40 | 40 | 0.00034808 | 8.702e-06 | 0
2013-06-05 09:55 | WGL13 | SHORT RURAL |  | 13 | 145 | 1885 | 0.016403 | 0.00011313 | 0
2013-06-04 11:45 | LDL22 | SHORT RURAL |  | 33 | 120 | 3960 | 0.03446 | 0.00028717 | 0
2013-06-04 10:25 | WYK12 | SHORT RURAL |  | 20 | 70 | 1400 | 0.012183 | 0.00017404 | 0
2013-06-04 08:50 | LDL22 | SHORT RURAL |  | 172 | 140 | 24080 | 0.20954 | 0.0014967 | 0
2013-06-04 09:20 | LDL14 | SHORT RURAL |  | 224 | 242 | 54208 | 0.47172 | 0.0019492 | 0
2013-06-04 09:00 | WYK12 | SHORT RURAL |  | 38 | 299 | 11362 | 0.098872 | 0.00033067 | 0
2013-06-06 09:15 | MWTS12 | URBAN |  | 209 | 220 | 45980 | 0.16017 | 0.00072805 | 0
2013-06-05 09:48 | LGA21 | SHORT RURAL |  | 354 | 308 | 109032 | 0.94879 | 0.0030805 | 0
2013-06-06 09:43 | WGI31 | SHORT RURAL |  | 185 | 50 | 9250 | 0.080493 | 0.0016099 | 0
2013-06-05 08:30 | WYK12 | SHORT RURAL |  | 36 | 156 | 5616 | 0.04887 | 0.00031327 | 0
2013-06-05 09:05 | WYK12 | SHORT RURAL |  | 15 | 65 | 975 | 0.0084844 | 0.00013053 | 0
2013-06-04 09:45 | WYK12 | SHORT RURAL |  | 11 | 58 | 638 | 0.0055519 | 9.5722e-05 | 0
2013-06-05 11:15 | WYK12 | SHORT RURAL |  | 9 | 45 | 405 | 0.0035243 | 7.8318e-05 | 0
2013-06-06 09:52 | WGL23 | SHORT RURAL |  | 2 | 88 | 176 | 0.0015315 | 1.7404e-05 | 0
2013-06-05 12:05 | WYK12 | SHORT RURAL |  | 1 | 42 | 42 | 0.00036548 | 8.702e-06 | 0
2013-06-05 13:10 | WYK12 | SHORT RURAL |  | 18 | 47 | 846 | 0.0073619 | 0.00015664 | 0
2013-06-05 13:15 | WYK12 | SHORT RURAL |  | 4 | 46 | 184 | 0.0016012 | 3.4808e-05 | 0
2013-06-05 09:10 | LGA11 | LONG RURAL |  | 111 | 321 | 35631 | 0.13797 | 0.00042983 | 0
2013-06-05 09:10 | FTR23 | LONG RURAL |  | 17 | 306 | 5202 | 0.020144 | 6.5829e-05 | 0
2013-06-04 15:00 | BN1 | LONG RURAL |  | 1 | 15 | 15 | 5.8085e-05 | 3.8723e-06 | 0
2013-05-31 09:25 | BN1 | LONG RURAL |  | 3 | 240 | 720 | 0.0027881 | 1.1617e-05 | 0
2013-06-05 14:25 | WYK12 | SHORT RURAL |  | 2 | 80 | 160 | 0.0013923 | 1.7404e-05 | 0
2013-06-06 08:43 | WYK12 | SHORT RURAL |  | 9 | 44 | 396 | 0.003446 | 7.8318e-05 | 0
2013-06-04 09:13 | WN2 | LONG RURAL |  | 8 | 221 | 1768 | 0.0068463 | 3.0979e-05 | 0
2013-06-04 10:00 | BN1 | LONG RURAL |  | 1 | 260 | 260 | 0.0010068 | 3.8723e-06 | 0
2013-06-06 08:40 | WO31 | URBAN |  | 30 | 210 | 6300 | 0.021946 | 0.0001045 | 0
2013-06-05 09:10 | WGL15 | SHORT RURAL |  | 28 | 155 | 4340 | 0.037767 | 0.00024366 | 0
2013-06-06 09:00 | FTR23 | LONG RURAL |  | 30 | 172 | 5160 | 0.019981 | 0.00011617 | 0
2013-06-04 09:25 | SLE31 | LONG RURAL |  | 1 | 45 | 45 | 0.00017425 | 3.8723e-06 | 0
2013-06-06 08:43 | BRA23 | URBAN |  | 461 | 302 | 139222 | 0.48498 | 0.0016059 | 0
2013-06-03 11:05 | BDL6 | SHORT RURAL |  | 1 | 55 | 55 | 0.00047861 | 8.702e-06 | 0
2013-06-03 12:30 | BDL6 | SHORT RURAL |  | 2 | 10 | 20 | 0.00017404 | 1.7404e-05 | 0
2013-06-05 09:06 | MFA22 | LONG RURAL |  | 45 | 342 | 15390 | 0.059595 | 0.00017425 | 0
2013-06-05 09:06 | SLE21 | SHORT RURAL |  | 14 | 342 | 4788 | 0.041665 | 0.00012183 | 0
2013-06-04 10:35 | BDL1 | LONG RURAL |  | 62 | 258 | 15996 | 0.061942 | 0.00024008 | 0
2013-06-04 14:50 | BDL1 | LONG RURAL |  | 70 | 3 | 210 | 0.00081319 | 0.00027106 | 0
2013-06-04 11:30 | BDL6 | SHORT RURAL |  | 13 | 160 | 2080 | 0.0181 | 0.00011313 | 0
2013-06-04 09:25 | BDL2 | SHORT RURAL |  | 95 | 185 | 17575 | 0.15294 | 0.00082669 | 0
2013-06-02 09:00 | DRN11 | URBAN |  | 6 | 491.5 | 2949 | 0.010273 | 2.0901e-05 | 0
2013-06-02 08:30 | DRN13 | SHORT RURAL |  | 81 | 540 | 43740 | 0.38062 | 0.00070486 | 0
2013-06-05 08:32 | BDL6 | SHORT RURAL |  | 88 | 368 | 32384 | 0.2818 | 0.00076577 | 0
2013-06-05 09:52 | SLE24 | URBAN |  | 64 | 34 | 2176 | 0.0075801 | 0.00022294 | 0
2013-05-29 08:45 | WYK24 | SHORT RURAL |  | 8 | 57 | 456 | 0.0039681 | 6.9616e-05 | 0
2013-06-06 08:30 | BDL6 | SHORT RURAL |  | 15 | 320 | 4800 | 0.041769 | 0.00013053 | 0
2013-05-29 12:30 | BWR13 | SHORT RURAL |  | 102 | 156 | 15912 | 0.13847 | 0.0008876 | 0
2013-05-30 08:55 | WT11 | URBAN |  | 191 | 200 | 38200 | 0.13307 | 0.00066535 | 0
2013-05-30 08:31 | CYN21 | URBAN |  | 739 | 404 | 298556 | 1.04 | 0.0025743 | 0
2013-05-31 10:00 | ELM33 | SHORT RURAL |  | 3 | 190 | 570 | 0.0049601 | 2.6106e-05 | 0
2013-05-30 12:20 | RWT15 | URBAN |  | 70 | 265 | 18550 | 0.064619 | 0.00024384 | 0
2013-05-30 13:20 | RWT22 | URBAN |  | 99 | 75 | 7425 | 0.025865 | 0.00034486 | 0
2013-05-31 08:30 | BWR32 | URBAN |  | 481 | 134 | 64454 | 0.22452 | 0.0016756 | 0
2013-05-31 08:50 | ELM33 | SHORT RURAL |  | 2 | 115 | 230 | 0.0020015 | 1.7404e-05 | 0
2013-06-02 08:30 | BRA14 | URBAN |  | 209 | 252 | 52668 | 0.18347 | 0.00072805 | 0
2013-05-29 08:04 | CYN21 | URBAN |  | 17 | 426 | 7242 | 0.025227 | 5.9219e-05 | 0
2013-06-04 08:54 | RWN24 | SHORT RURAL |  | 388 | 136 | 52768 | 0.45919 | 0.0033764 | 0
2013-06-04 08:40 | CYN31 | URBAN |  | 79 | 265 | 20935 | 0.072927 | 0.0002752 | 0
2013-06-06 12:15 | MOE31 | LONG RURAL |  | 9 | 105 | 945 | 0.0036593 | 3.4851e-05 | 0
2013-06-07 09:27 | WGI14 | SHORT RURAL |  | 784 | 291 | 228144 | 1.9853 | 0.0068223 | 0
2013-06-07 08:20 | MOE13 | SHORT RURAL |  | 59 | 385 | 22715 | 0.19767 | 0.00051342 | 0
2013-06-07 19:38 | MYT2 | SHORT RURAL |  | 360 | 1 | 360 | 0.0031327 | 0.0031327 | 0
2013-06-07 09:15 | MOE31 | LONG RURAL |  | 21 | 225 | 4725 | 0.018297 | 8.1319e-05 | 0
2013-06-06 11:56 | WGI31 | SHORT RURAL |  | 99 | 84 | 8316 | 0.072366 | 0.0008615 | 0
2013-06-06 12:20 | WGL23 | SHORT RURAL |  | 2 | 145 | 290 | 0.0025236 | 1.7404e-05 | 0
2013-06-06 10:00 | WYK12 | SHORT RURAL |  | 1 | 35 | 35 | 0.00030457 | 8.702e-06 | 0
2013-06-07 08:55 | WYK12 | SHORT RURAL |  | 1 | 145 | 145 | 0.0012618 | 8.702e-06 | 0
2013-06-07 09:00 | WYK12 | SHORT RURAL |  | 16 | 215 | 3440 | 0.029935 | 0.00013923 | 0
2013-06-07 08:30 | LDL23 | LONG RURAL |  | 219 | 390 | 85410 | 0.33073 | 0.00084804 | 0
2013-06-07 08:30 | WYK23 | SHORT RURAL |  | 323 | 280 | 90440 | 0.78701 | 0.0028107 | 0
2013-06-07 09:45 | BDL8 | LONG RURAL |  | 28 | 315 | 8820 | 0.034154 | 0.00010842 | 0
2013-06-07 10:20 | BDL6 | SHORT RURAL |  | 2 | 59 | 118 | 0.0010268 | 1.7404e-05 | 0
2013-06-03 09:00 | PHM14 | LONG RURAL |  | 2 | 83 | 166 | 0.0006428 | 7.7446e-06 | 0
2013-06-04 09:37 | LLG13 | SHORT RURAL |  | 15 | 256 | 3840 | 0.033416 | 0.00013053 | 0
2013-06-05 11:07 | BWN14 | SHORT RURAL |  | 38 | 68 | 2584 | 0.022486 | 0.00033067 | 0
2013-05-31 09:28 | BRA24 | URBAN |  | 457 | 204 | 93228 | 0.32476 | 0.001592 | 0
2013-06-06 09:15 | SLE31 | LONG RURAL |  | 1 | 190 | 190 | 0.00073574 | 3.8723e-06 | 0
2013-05-28 13:17 | MYT7 | LONG RURAL |  | 3 | 23 | 69 | 0.00026719 | 1.1617e-05 | 0
2013-05-30 10:35 | WOTS13 | LONG RURAL |  | 1 | 40 | 40 | 0.00015489 | 3.8723e-06 | 0
2013-05-31 12:00 | ELM33 | SHORT RURAL |  | 7 | 140 | 980 | 0.0085279 | 6.0914e-05 | 0
2013-06-06 10:15 | WGL24 | LONG RURAL |  | 4 | 200 | 800 | 0.0030979 | 1.5489e-05 | 0
2013-06-06 09:40 | WGL15 | SHORT RURAL |  | 2 | 180 | 360 | 0.0031327 | 1.7404e-05 | 0
2013-06-03 09:50 | ELM31 | URBAN |  | 112 | 238.5536 | 26718 | 0.093072 | 0.00039015 | 0
2013-06-04 09:40 | DRN14 | SHORT RURAL |  | 96 | 340 | 32640 | 0.28403 | 0.00083539 | 0
2013-06-06 08:33 | MFA31 | SHORT RURAL |  | 36 | 368 | 13248 | 0.11528 | 0.00031327 | 0
2013-06-02 08:00 | SLE21 | SHORT RURAL |  | 237 | 224 | 53088 | 0.46197 | 0.0020624 | 0
2013-06-07 11:15 | WGL15 | SHORT RURAL |  | 3 | 65 | 195 | 0.0016969 | 2.6106e-05 | 0
2013-06-04 09:45 | MYT8 | SHORT RURAL |  | 2 | 115 | 230 | 0.0020015 | 1.7404e-05 | 0
2013-06-02 10:00 | BWR13 | SHORT RURAL |  | 37 | 91.6216 | 3390 | 0.0295 | 0.00032197 | 0
2013-06-04 13:35 | MBY11 | SHORT RURAL |  | 9 | 55 | 495 | 0.0043075 | 7.8318e-05 | 0
2013-06-05 13:05 | MBY11 | SHORT RURAL |  | 1 | 65 | 65 | 0.00056563 | 8.702e-06 | 0
2013-06-02 12:30 | RWN33 | URBAN |  | 4 | 86 | 344 | 0.0011983 | 1.3934e-05 | 0
2013-06-05 09:00 | WO31 | URBAN |  | 3 | 200 | 600 | 0.0020901 | 1.045e-05 | 0
2013-06-07 11:40 | WGL15 | SHORT RURAL |  | 14 | 84 | 1176 | 0.010234 | 0.00012183 | 0
2013-05-31 10:05 | DRN14 | SHORT RURAL |  | 2 | 185 | 370 | 0.0032197 | 1.7404e-05 | 0
2013-06-04 09:50 | RWN33 | URBAN |  | 93 | 230 | 21390 | 0.074512 | 0.00032396 | 0
2013-05-29 12:00 | WYK24 | SHORT RURAL |  | 10 | 35 | 350 | 0.0030457 | 8.702e-05 | 0
2013-06-02 08:30 | WO14 | URBAN |  | 78 | 250 | 19500 | 0.067928 | 0.00027171 | 0
2013-05-29 14:00 | WYK24 | SHORT RURAL |  | 11 | 46 | 506 | 0.0044032 | 9.5722e-05 | 0
2013-06-05 08:30 | ELM33 | SHORT RURAL |  | 1 | 135 | 135 | 0.0011748 | 8.702e-06 | 0
2013-05-30 12:22 | WYK24 | SHORT RURAL |  | 25 | 45 | 1125 | 0.0097897 | 0.00021755 | 0
2013-05-30 14:22 | WYK24 | SHORT RURAL |  | 11 | 50 | 550 | 0.0047861 | 9.5722e-05 | 0
2013-06-05 10:31 | TT2 | URBAN |  | 1 | 104 | 104 | 0.00036228 | 3.4835e-06 | 0
2013-06-06 09:06 | TRC01 | SHORT RURAL |  | 67 | 414 | 27738 | 0.24138 | 0.00058303 | 0
2013-06-05 09:25 | DRN12 | URBAN |  | 16 | 384 | 6144 | 0.021403 | 5.5736e-05 | 0
2013-06-06 09:20 | MYT8 | SHORT RURAL |  | 2 | 45 | 90 | 0.00078318 | 1.7404e-05 | 0
2013-06-03 13:05 | KMS1 | SHORT RURAL |  | 2 | 55 | 110 | 0.00095722 | 1.7404e-05 | 0
2013-06-05 08:45 | RWN26 | SHORT RURAL |  | 237 | 355 | 84135 | 0.73214 | 0.0020624 | 0
2013-05-23 09:36 | BWA22 | LONG RURAL |  | 21 | 266 | 5586 | 0.021631 | 8.1319e-05 | 0
2013-06-07 11:40 | WGL23 | SHORT RURAL |  | 1 | 95 | 95 | 0.00082669 | 8.702e-06 | 0
2013-06-07 11:55 | WYK12 | SHORT RURAL |  | 12 | 120 | 1440 | 0.012531 | 0.00010442 | 0
2013-06-06 12:45 | MYT2 | SHORT RURAL |  | 56 | 85 | 4760 | 0.041421 | 0.00048731 | 0
2013-05-31 09:10 | PHI13 | URBAN |  | 3 | 140 | 420 | 0.0014631 | 1.045e-05 | 0
2013-06-05 11:22 | LLG11 | SHORT RURAL |  | 3 | 88 | 264 | 0.0022973 | 2.6106e-05 | 0
2013-06-07 10:55 | MFA34 | SHORT RURAL |  | 1 | 25 | 25 | 0.00021755 | 8.702e-06 | 0
2013-06-06 09:23 | KMS21 | SHORT RURAL |  | 10 | 272 | 2720 | 0.023669 | 8.702e-05 | 0
2013-06-07 11:40 | MFA34 | SHORT RURAL |  | 4 | 60 | 240 | 0.0020885 | 3.4808e-05 | 0
2013-06-05 11:05 | WGL12 | LONG RURAL |  | 4 | 115 | 460 | 0.0017813 | 1.5489e-05 | 0
2013-06-05 11:15 | WGL12 | LONG RURAL |  | 1 | 63 | 63 | 0.00024396 | 3.8723e-06 | 0
2013-06-07 07:20 | BRT22 | SHORT RURAL |  | 8 | 430 | 3440 | 0.029935 | 6.9616e-05 | 0
2013-06-05 09:30 | FTR21 | LONG RURAL |  | 51 | 105 | 5355 | 0.020736 | 0.00019749 | 0
2013-06-07 09:30 | ALA01 | LONG RURAL |  | 1 | 200 | 200 | 0.00077446 | 3.8723e-06 | 0
2013-06-04 09:30 | WGI23 | SHORT RURAL |  | 29 | 210 | 6090 | 0.052995 | 0.00025236 | 0
2013-06-05 08:00 | SLE31 | LONG RURAL |  | 946 | 403 | 381238 | 1.4763 | 0.0036632 | 0
2013-06-05 12:50 | BRT11 | SHORT RURAL |  | 27 | 70 | 1890 | 0.016447 | 0.00023495 | 0
2013-06-05 09:25 | FTR21 | LONG RURAL |  | 16 | 75 | 1200 | 0.0046468 | 6.1957e-05 | 0
2013-06-05 12:00 | FTR21 | LONG RURAL |  | 3 | 65 | 195 | 0.0007551 | 1.1617e-05 | 0
2013-06-06 09:52 | LGA14 | LONG RURAL |  | 75 | 128 | 9600 | 0.037174 | 0.00029042 | 0
2013-06-06 08:42 | LLG12 | SHORT RURAL |  | 113 | 196.7611 | 22234 | 0.19348 | 0.00098332 | 0
2013-06-06 09:40 | BN1 | LONG RURAL |  | 8 | 260 | 2080 | 0.0080544 | 3.0979e-05 | 0
2013-06-09 08:38 | RWN26 | SHORT RURAL |  | 39 | 291 | 11349 | 0.098759 | 0.00033938 | 0
2013-06-05 10:00 | TT5 | URBAN |  | 101 | 57 | 5757 | 0.020054 | 0.00035183 | 0
2013-06-05 10:54 | ELM33 | SHORT RURAL |  | 1 | 151 | 151 | 0.001314 | 8.702e-06 | 0
2013-06-04 09:50 | WGL11 | SHORT RURAL |  | 3 | 60 | 180 | 0.0015664 | 2.6106e-05 | 0
2013-06-07 09:00 | BRT21 | SHORT RURAL |  | 233 | 168 | 39144 | 0.34063 | 0.0020276 | 0
2013-06-06 09:30 | BRT22 | SHORT RURAL |  | 45 | 165 | 7425 | 0.064612 | 0.00039159 | 0
2013-05-30 09:13 | MSD4 | LONG RURAL |  | 1 | 162 | 162 | 0.00062731 | 3.8723e-06 | 0
2013-06-04 09:00 | KMS1 | SHORT RURAL |  | 19 | 451 | 8569 | 0.074567 | 0.00016534 | 0
2013-06-07 09:18 | KMS1 | SHORT RURAL |  | 12 | 320 | 3840 | 0.033416 | 0.00010442 | 0
2013-06-05 09:00 | WO22 | URBAN |  | 77 | 70 | 5390 | 0.018776 | 0.00026823 | 0
2013-06-06 08:50 | WN5 | LONG RURAL |  | 69 | 383 | 26427 | 0.10233 | 0.00026719 | 0
2013-05-25 02:29 | TT1 | URBAN |  | 2 | 116 | 232 | 0.00080817 | 6.967e-06 | 0
2013-06-05 09:10 | CYN24 | URBAN |  | 119 | 120 | 14280 | 0.049744 | 0.00041453 | 0
2013-06-05 12:20 | RWN33 | URBAN |  | 67 | 101 | 6767 | 0.023573 | 0.00023339 | 0
2013-06-06 13:45 | HPK21 | URBAN |  | 101 | 80 | 8080 | 0.028147 | 0.00035183 | 0
2013-06-05 09:46 | RWT15 | URBAN |  | 136 | 344 | 46784 | 0.16297 | 0.00047375 | 0
2013-06-06 08:40 | BWR23 | URBAN |  | 135 | 240 | 32400 | 0.11286 | 0.00047027 | 0
2013-06-06 08:40 | CYN32 | URBAN |  | 48 | 240 | 11520 | 0.04013 | 0.00016721 | 0
2013-06-06 13:10 | BWR23 | URBAN |  | 135 | 90 | 12150 | 0.042324 | 0.00047027 | 0
2013-06-07 08:06 | CYN14 | URBAN |  | 53 | 370 | 19610 | 0.068311 | 0.00018462 | 0
2013-06-13 08:46 | CYN14 | URBAN |  | 803 | 123 | 98769 | 0.34406 | 0.0027972 | 0
2013-06-02 08:16 | BWN14 | SHORT RURAL |  | 434 | 267.1912 | 115961 | 1.0091 | 0.0037767 | 0
2013-05-27 09:50 | BN6 | LONG RURAL |  | 6 | 295 | 1770 | 0.006854 | 2.3234e-05 | 0
2013-06-11 09:42 | FTR22 | SHORT RURAL |  | 2 | 278 | 556 | 0.0048383 | 1.7404e-05 | 0
2013-06-11 09:10 | MOE31 | LONG RURAL |  | 12 | 175 | 2100 | 0.0081319 | 4.6468e-05 | 0
2013-06-11 10:30 | TGN31 | LONG RURAL |  | 96 | 170 | 16320 | 0.063196 | 0.00037174 | 0
2013-06-11 10:00 | MOE31 | LONG RURAL |  | 1 | 80 | 80 | 0.00030979 | 3.8723e-06 | 0
2013-06-12 10:30 | MOE31 | LONG RURAL |  | 1 | 210 | 210 | 0.00081319 | 3.8723e-06 | 0
2013-06-12 09:35 | WGL23 | SHORT RURAL |  | 4 | 47 | 188 | 0.001636 | 3.4808e-05 | 0
2013-06-11 12:30 | MOE31 | LONG RURAL |  | 4 | 85 | 340 | 0.0013166 | 1.5489e-05 | 0
2013-06-12 09:00 | MWTS14 | SHORT RURAL |  | 37 | 475 | 17575 | 0.15294 | 0.00032197 | 0
2013-06-12 09:05 | LGA13 | LONG RURAL |  | 2 | 50 | 100 | 0.00038723 | 7.7446e-06 | 0
2013-06-12 09:00 | LGA13 | LONG RURAL |  | 1 | 40 | 40 | 0.00015489 | 3.8723e-06 | 0
2013-06-12 11:40 | LGA13 | LONG RURAL |  | 3 | 45 | 135 | 0.00052276 | 1.1617e-05 | 0
2013-06-12 10:47 | LGA13 | LONG RURAL |  | 2 | 53 | 106 | 0.00041047 | 7.7446e-06 | 0
2013-06-12 09:30 | BDL6 | SHORT RURAL |  | 16 | 275 | 4400 | 0.038289 | 0.00013923 | 0
2013-06-11 09:16 | SMR1 | SHORT RURAL |  | 10 | 128 | 1280 | 0.011139 | 8.702e-05 | 0
2013-06-13 08:30 | WO32 | URBAN |  | 84 | 165 | 13860 | 0.048281 | 0.00029261 | 0
2013-06-11 09:37 | MFA22 | LONG RURAL |  | 28 | 258 | 7224 | 0.027974 | 0.00010842 | 0
2013-06-11 08:55 | MFA22 | LONG RURAL |  | 16 | 180 | 2880 | 0.011152 | 6.1957e-05 | 0
2013-06-13 09:10 | WN3 | LONG RURAL |  | 31 | 198 | 6138 | 0.023768 | 0.00012004 | 0
2013-06-12 08:58 | BDL1 | LONG RURAL |  | 208 | 265 | 55120 | 0.21344 | 0.00080544 | 0
2013-06-11 09:00 | BN4 | URBAN |  | 51 | 274 | 13974 | 0.048678 | 0.00017766 | 0
2013-06-11 08:40 | BN6 | LONG RURAL |  | 12 | 350 | 4200 | 0.016264 | 4.6468e-05 | 0
2013-06-11 09:15 | WYK23 | SHORT RURAL |  | 297 | 375 | 111375 | 0.96918 | 0.0025845 | 0
2013-06-11 14:30 | WYK11 | SHORT RURAL |  | 204 | 180 | 36720 | 0.31954 | 0.0017752 | 0
2013-06-13 08:55 | BGE11 | SHORT RURAL |  | 160 | 310 | 49600 | 0.43162 | 0.0013923 | 0
2013-06-12 09:50 | MOE14 | SHORT RURAL |  | 2 | 225 | 450 | 0.0039159 | 1.7404e-05 | 0
2013-06-13 09:45 | MYT7 | LONG RURAL |  | 8 | 125 | 1000 | 0.0038723 | 3.0979e-05 | 0
2013-06-06 09:05 | CRE22 | URBAN |  | 220 | 125 | 27500 | 0.095796 | 0.00076637 | 0
2013-06-06 10:00 | PHM33 | SHORT RURAL |  | 1 | 199 | 199 | 0.0017317 | 8.702e-06 | 0
2013-06-06 08:56 | LLG11 | SHORT RURAL |  | 44 | 72 | 3168 | 0.027568 | 0.00038289 | 0
2013-06-07 10:50 | OFR24 | URBAN |  | 24 | 70 | 1680 | 0.0058523 | 8.3604e-05 | 0
2013-06-05 09:15 | LDL22 | SHORT RURAL |  | 48 | 305 | 14640 | 0.1274 | 0.00041769 | 0
2013-06-12 12:00 | MOE14 | SHORT RURAL |  | 4 | 90 | 360 | 0.0031327 | 3.4808e-05 | 0
2013-06-11 09:45 | KMS1 | SHORT RURAL |  | 4 | 250 | 1000 | 0.008702 | 3.4808e-05 | 0
2013-06-13 09:10 | BN6 | LONG RURAL |  | 1 | 160 | 160 | 0.00061957 | 3.8723e-06 | 0
2013-06-12 10:20 | MOE14 | SHORT RURAL |  | 4 | 50 | 200 | 0.0017404 | 3.4808e-05 | 0
2013-06-06 08:58 | MSD2 | LONG RURAL |  | 56 | 167 | 9352 | 0.036214 | 0.00021685 | 0
2013-06-12 09:00 | BWR24 | URBAN |  | 25 | 405 | 10125 | 0.03527 | 8.7087e-05 | 0
2013-06-12 08:30 | BRA14 | URBAN |  | 539 | 445 | 239855 | 0.83553 | 0.0018776 | 0
2013-06-03 09:05 | WN5 | LONG RURAL |  | 10 | 221 | 2210 | 0.0085578 | 3.8723e-05 | 0
2013-06-04 11:15 | FGY13 | SHORT RURAL |  | 51 | 45 | 2295 | 0.019971 | 0.0004438 | 0
2013-06-07 09:38 | MSD4 | LONG RURAL |  | 65 | 249 | 16185 | 0.062673 | 0.0002517 | 0
2013-06-06 09:19 | WT13 | URBAN |  | 772 | 39 | 30108 | 0.10488 | 0.0026892 | 0
2013-06-05 09:50 | DRN11 | URBAN |  | 8 | 155 | 1240 | 0.0043195 | 2.7868e-05 | 0
2013-06-06 09:00 | ELM33 | SHORT RURAL |  | 46 | 345 | 15870 | 0.1381 | 0.00040029 | 0
2013-06-09 10:28 | FGY21 | SHORT RURAL |  | 10 | 577 | 5770 | 0.05021 | 8.702e-05 | 0
2013-06-05 13:55 | KLO24 | SHORT RURAL |  | 90 | 75 | 6750 | 0.058738 | 0.00078318 | 0
2013-06-11 09:01 | WN5 | LONG RURAL |  | 6 | 284 | 1704 | 0.0065984 | 2.3234e-05 | 0
2013-06-11 09:05 | WGL12 | LONG RURAL |  | 3 | 270 | 810 | 0.0031366 | 1.1617e-05 | 0
2013-06-06 08:45 | KLK3 | SHORT RURAL |  | 4 | 360 | 1440 | 0.012531 | 3.4808e-05 | 0
2013-06-14 09:00 | MOE32 | SHORT RURAL |  | 65 | 125 | 8125 | 0.070704 | 0.00056563 | 0
2013-06-14 09:30 | MOE31 | LONG RURAL |  | 1 | 200 | 200 | 0.00077446 | 3.8723e-06 | 0
2013-06-14 09:33 | LGA13 | LONG RURAL |  | 17 | 160 | 2720 | 0.010533 | 6.5829e-05 | 0
2013-06-14 09:00 | WGI34 | SHORT RURAL |  | 84 | 160 | 13440 | 0.11695 | 0.00073097 | 0
2013-06-14 09:35 | MOE22 | LONG RURAL |  | 66 | 171 | 11286 | 0.043703 | 0.00025557 | 0
2013-06-13 12:20 | BN1 | LONG RURAL |  | 5 | 80 | 400 | 0.0015489 | 1.9362e-05 | 0
2013-06-14 08:44 | WYK11 | SHORT RURAL |  | 105 | 341 | 35805 | 0.31157 | 0.00091371 | 0
2013-06-14 09:00 | LLG12 | SHORT RURAL |  | 41 | 200 | 8200 | 0.071356 | 0.00035678 | 0
2013-06-07 10:02 | WT7 | URBAN |  | 143 | 160 | 22880 | 0.079702 | 0.00049814 | 0
2013-06-11 09:00 | DRN14 | SHORT RURAL |  | 2 | 68 | 136 | 0.0011835 | 1.7404e-05 | 0
2013-06-06 09:00 | RWT15 | URBAN |  | 102 | 328 | 33456 | 0.11654 | 0.00035532 | 0
2013-06-11 08:45 | ELM33 | SHORT RURAL |  | 3 | 370 | 1110 | 0.0096592 | 2.6106e-05 | 0
2013-06-11 09:32 | WT15 | URBAN |  | 126 | 313 | 39438 | 0.13738 | 0.00043892 | 0
2013-06-13 09:10 | SMR8 | LONG RURAL |  | 2 | 120 | 240 | 0.00092936 | 7.7446e-06 | 0
2013-06-11 10:00 | BGE24 | SHORT RURAL |  | 1 | 120 | 120 | 0.0010442 | 8.702e-06 | 0
2013-06-11 09:45 | WT12 | URBAN |  | 94 | 210 | 19740 | 0.068764 | 0.00032745 | 0
2013-06-12 09:30 | FGY22 | URBAN |  | 888 | 408 | 362304 | 1.2621 | 0.0030933 | 0
2013-06-11 09:00 | PHM34 | URBAN |  | 650 | 8 | 5200 | 0.018114 | 0.0022643 | 0
2013-06-13 09:00 | WN5 | LONG RURAL |  | 5 | 205 | 1025 | 0.0039691 | 1.9362e-05 | 0
2013-06-11 09:00 | PHM34 | URBAN |  | 1763 | 139.4691 | 245884 | 0.85653 | 0.0061414 | 0
2013-06-14 10:30 | BN1 | LONG RURAL |  | 1 | 45 | 45 | 0.00017425 | 3.8723e-06 | 0
2013-06-11 13:55 | WT12 | URBAN |  | 76 | 55 | 4180 | 0.014561 | 0.00026474 | 0
2013-05-30 08:45 | BGE11 | SHORT RURAL |  | 74 | 210 | 15540 | 0.13523 | 0.00064395 | 0
2013-06-12 08:45 | PHM33 | SHORT RURAL |  | 1 | 105 | 105 | 0.00091371 | 8.702e-06 | 0
2013-06-14 10:05 | BN6 | LONG RURAL |  | 1 | 30 | 30 | 0.00011617 | 3.8723e-06 | 0
2013-06-12 09:30 | RWT15 | URBAN |  | 72 | 260 | 18720 | 0.065211 | 0.00025081 | 0
2013-06-13 09:50 | WT15 | URBAN |  | 164 | 181.2134 | 29719 | 0.10353 | 0.00057129 | 0
2013-06-14 09:15 | WT12 | URBAN |  | 65 | 260 | 16900 | 0.058871 | 0.00022643 | 0
2013-06-12 08:35 | WGL12 | LONG RURAL |  | 1 | 178 | 178 | 0.00068927 | 3.8723e-06 | 0
2013-06-12 09:00 | OFR23 | LONG RURAL |  | 74 | 320 | 23680 | 0.091696 | 0.00028655 | 0
2013-06-13 09:40 | RWN31 | SHORT RURAL |  | 35 | 295 | 10325 | 0.089848 | 0.00030457 | 0
2013-06-16 08:35 | WGL11 | SHORT RURAL |  | 30 | 150 | 4500 | 0.039159 | 0.00026106 | 0
2013-06-16 08:30 | WYK11 | SHORT RURAL |  | 121 | 345 | 41745 | 0.36326 | 0.0010529 | 0
2013-06-16 08:40 | LDL12 | URBAN |  | 114 | 250 | 28500 | 0.099279 | 0.00039712 | 0
2013-06-16 08:45 | OFR24 | URBAN |  | 82 | 231.3415 | 18970 | 0.066082 | 0.00028565 | 0
2013-06-13 09:45 | MYT7 | LONG RURAL |  | 24 | 202 | 4848 | 0.018773 | 9.2936e-05 | 0
2013-06-13 09:40 | KMS21 | SHORT RURAL |  | 14 | 190 | 2660 | 0.023147 | 0.00012183 | 0
2013-06-14 09:00 | MBY11 | SHORT RURAL |  | 19 | 226 | 4294 | 0.037366 | 0.00016534 | 0
2013-06-13 09:35 | KMS21 | SHORT RURAL |  | 7 | 341 | 2387 | 0.020772 | 6.0914e-05 | 0
2013-06-14 13:55 | ELM11 | URBAN |  | 66 | 55 | 3630 | 0.012645 | 0.00022991 | 0
2013-06-13 09:00 | BGE22 | SHORT RURAL |  | 1 | 240 | 240 | 0.0020885 | 8.702e-06 | 0
2013-06-05 09:00 | WOTS24 | LONG RURAL |  | 57 | 300 | 17100 | 0.066217 | 0.00022072 | 0
2013-06-14 11:10 | BGE22 | SHORT RURAL |  | 70 | 230 | 16100 | 0.1401 | 0.00060914 | 0
2013-06-14 09:48 | MSD4 | LONG RURAL |  | 51 | 32 | 1632 | 0.0063196 | 0.00019749 | 0
2013-06-17 10:00 | WOTS13 | LONG RURAL |  | 65 | 215 | 13975 | 0.054116 | 0.0002517 | 0
2013-06-14 09:40 | RWN31 | SHORT RURAL |  | 43 | 190 | 8170 | 0.071095 | 0.00037418 | 0
2013-06-16 08:42 | MSD4 | LONG RURAL |  | 56 | 252 | 14112 | 0.054646 | 0.00021685 | 0
2013-06-05 08:31 | WN5 | LONG RURAL |  | 156 | 427 | 66612 | 0.25794 | 0.00060408 | 0
2013-06-16 12:00 | WGL23 | SHORT RURAL |  | 34 | 140 | 4760 | 0.041421 | 0.00029587 | 0
2013-06-17 09:15 | BWN14 | SHORT RURAL |  | 9 | 345 | 3105 | 0.02702 | 7.8318e-05 | 0
2013-06-17 08:55 | HPK22 | URBAN |  | 32 | 70 | 2240 | 0.007803 | 0.00011147 | 0
2013-06-17 10:40 | KMS1 | SHORT RURAL |  | 4 | 85 | 340 | 0.0029587 | 3.4808e-05 | 0
2013-06-17 09:25 | KMS1 | SHORT RURAL |  | 2 | 155 | 310 | 0.0026976 | 1.7404e-05 | 0
2013-06-19 09:05 | WOTS11 | LONG RURAL |  | 5 | 445 | 2225 | 0.0086159 | 1.9362e-05 | 0
2013-06-20 09:00 | WOTS11 | LONG RURAL |  | 5 | 340 | 1700 | 0.0065829 | 1.9362e-05 | 0
2013-06-18 10:30 | MOE31 | LONG RURAL |  | 8 | 190 | 1520 | 0.0058859 | 3.0979e-05 | 0
2013-06-18 09:45 | MWTS11 | SHORT RURAL |  | 358 | 408 | 146064 | 1.271 | 0.0031153 | 0
2013-06-18 09:30 | MOE13 | SHORT RURAL |  | 246 | 285 | 70110 | 0.6101 | 0.0021407 | 0
2013-06-19 09:30 | PHI11 | SHORT RURAL |  | 88 | 185 | 16280 | 0.14167 | 0.00076577 | 0
2013-06-19 08:38 | WO31 | URBAN |  | 64 | 37 | 2368 | 0.0082489 | 0.00022294 | 0
2013-06-19 09:30 | WOTS24 | LONG RURAL |  | 15 | 310 | 4650 | 0.018006 | 5.8085e-05 | 0
2013-06-18 10:20 | MOE21 | SHORT RURAL |  | 27 | 180 | 4860 | 0.042292 | 0.00023495 | 0
2013-06-19 08:40 | MOE13 | SHORT RURAL |  | 1 | 275 | 275 | 0.002393 | 8.702e-06 | 0
2013-06-19 09:30 | MOE21 | SHORT RURAL |  | 15 | 390 | 5850 | 0.050907 | 0.00013053 | 0
2013-06-20 11:15 | MWTS14 | SHORT RURAL |  | 125 | 309 | 38625 | 0.33611 | 0.0010877 | 0
2013-06-20 10:15 | WOTS11 | LONG RURAL |  | 1 | 303 | 303 | 0.0011733 | 3.8723e-06 | 0
2013-06-18 11:01 | CYN32 | URBAN |  | 33 | 229 | 7557 | 0.026325 | 0.00011495 | 0
2013-06-19 09:40 | RWT14 | URBAN |  | 81 | 38.0247 | 3080 | 0.010729 | 0.00028216 | 0
2013-06-17 10:10 | WYK11 | SHORT RURAL |  | 4 | 105 | 420 | 0.0036548 | 3.4808e-05 | 0
2013-06-17 12:25 | WYK11 | SHORT RURAL |  | 1 | 50 | 50 | 0.0004351 | 8.702e-06 | 0
2013-06-18 08:50 | WYK12 | SHORT RURAL |  | 1 | 95 | 95 | 0.00082669 | 8.702e-06 | 0
2013-06-18 09:05 | WYK23 | SHORT RURAL |  | 240 | 455 | 109200 | 0.95026 | 0.0020885 | 0
2013-06-18 09:49 | WYK11 | SHORT RURAL |  | 164 | 343 | 56252 | 0.4895 | 0.0014271 | 0
2013-06-18 08:51 | WYK12 | SHORT RURAL |  | 110 | 344 | 37840 | 0.32928 | 0.00095722 | 0
2013-06-19 09:50 | LGA13 | LONG RURAL |  | 15 | 140 | 2100 | 0.0081319 | 5.8085e-05 | 0
2013-06-20 09:45 | MOE22 | LONG RURAL |  | 61 | 310 | 18910 | 0.073225 | 0.00023621 | 0
2013-06-19 09:21 | MWTS14 | SHORT RURAL |  | 24 | 377 | 9048 | 0.078735 | 0.00020885 | 0
2013-06-20 09:15 | WGL13 | SHORT RURAL |  | 8 | 305 | 2440 | 0.021233 | 6.9616e-05 | 0
2013-06-20 10:00 | FTR21 | LONG RURAL |  | 24 | 161 | 3864 | 0.014963 | 9.2936e-05 | 0
2013-06-19 08:30 | WYK24 | SHORT RURAL |  | 1 | 65 | 65 | 0.00056563 | 8.702e-06 | 0
2013-06-19 10:00 | WYK24 | SHORT RURAL |  | 1 | 50 | 50 | 0.0004351 | 8.702e-06 | 0
2013-06-19 11:40 | WYK24 | SHORT RURAL |  | 1 | 42 | 42 | 0.00036548 | 8.702e-06 | 0
2013-06-20 09:20 | FTR12 | LONG RURAL |  | 18 | 440 | 7920 | 0.030669 | 6.9702e-05 | 0
2013-06-20 09:00 | TGN11 | SHORT RURAL |  | 1 | 66 | 66 | 0.00057433 | 8.702e-06 | 0
2013-06-18 09:12 | LLG11 | SHORT RURAL |  | 232 | 320 | 74240 | 0.64603 | 0.0020189 | 0
2013-06-18 09:00 | FTR21 | LONG RURAL |  | 23 | 310 | 7130 | 0.02761 | 8.9063e-05 | 0
2013-06-19 09:00 | TGN31 | LONG RURAL |  | 1 | 135 | 135 | 0.00052276 | 3.8723e-06 | 0
2013-06-20 09:00 | LGA21 | SHORT RURAL |  | 146 | 395 | 57670 | 0.50184 | 0.0012705 | 0
2013-06-18 09:10 | WO23 | URBAN |  | 114 | 350 | 39900 | 0.13899 | 0.00039712 | 0
2013-06-18 10:15 | MFA21 | LONG RURAL |  | 70 | 127 | 8890 | 0.034425 | 0.00027106 | 0
2013-06-20 09:18 | TGN11 | SHORT RURAL |  | 165 | 344 | 56760 | 0.49392 | 0.0014358 | 0
2013-06-19 09:25 | RWN31 | SHORT RURAL |  | 67 | 306 | 20502 | 0.17841 | 0.00058303 | 0
2013-06-19 08:30 | BDL3 | SHORT RURAL |  | 74 | 340 | 25160 | 0.21894 | 0.00064395 | 0
2013-06-18 10:00 | WGL21 | LONG RURAL |  | 60 | 370 | 22200 | 0.085965 | 0.00023234 | 0
2013-06-13 09:46 | MSD4 | LONG RURAL |  | 2 | 24 | 48 | 0.00018587 | 7.7446e-06 | 0
2013-06-19 12:10 | MOE14 | SHORT RURAL |  | 2 | 80 | 160 | 0.0013923 | 1.7404e-05 | 0
2013-06-12 09:20 | BWR32 | URBAN |  | 128 | 445 | 56960 | 0.19842 | 0.00044589 | 0
2013-06-16 08:35 | BWR34 | URBAN |  | 475 | 482 | 228950 | 0.79754 | 0.0016547 | 0
2013-06-18 11:15 | BWR32 | URBAN |  | 52 | 125 | 6500 | 0.022643 | 0.00018114 | 0
2013-06-17 10:55 | ELM32 | URBAN |  | 66 | 225 | 14850 | 0.05173 | 0.00022991 | 0
2013-06-20 09:16 | WGL12 | LONG RURAL |  | 308 | 307 | 94556 | 0.36615 | 0.0011927 | 0
2013-06-20 09:02 | WGL12 | LONG RURAL |  | 2130 | 1 | 2130 | 0.008248 | 0.008248 | 0
2013-06-17 09:00 | WN2 | LONG RURAL |  | 1 | 220 | 220 | 0.00085191 | 3.8723e-06 | 0
2013-06-21 09:58 | WOTS24 | LONG RURAL |  | 22 | 196 | 4312 | 0.016697 | 8.5191e-05 | 0
2013-06-21 08:45 | TGN14 | LONG RURAL |  | 2 | 125 | 250 | 0.00096808 | 7.7446e-06 | 0
2013-06-21 09:00 | FTR21 | LONG RURAL |  | 705 | 256 | 180480 | 0.69888 | 0.00273 | 0
2013-06-21 09:20 | FTR21 | LONG RURAL |  | 123 | 238 | 29274 | 0.11336 | 0.00047629 | 0
2013-06-21 10:25 | LGA14 | LONG RURAL |  | 1 | 275 | 275 | 0.0010649 | 3.8723e-06 | 0
2013-06-21 09:15 | WGI22 | LONG RURAL |  | 3 | 335 | 1005 | 0.0038917 | 1.1617e-05 | 0
2013-06-21 09:25 | LDL22 | SHORT RURAL |  | 107 | 300 | 32100 | 0.27933 | 0.00093111 | 0
2013-06-21 09:20 | WYK23 | SHORT RURAL |  | 75 | 290 | 21750 | 0.18927 | 0.00065265 | 0
2013-06-21 09:00 | WGL11 | SHORT RURAL |  | 63 | 390 | 24570 | 0.21381 | 0.00054822 | 0
2013-06-21 09:00 | BRT21 | SHORT RURAL |  | 8 | 240 | 1920 | 0.016708 | 6.9616e-05 | 0
2013-06-25 09:45 | BWA22 | LONG RURAL |  | 73 | 195 | 14235 | 0.055122 | 0.00028268 | 0
2013-06-20 14:45 | PHM14 | LONG RURAL |  | 2130 | 1 | 2130 | 0.008248 | 0.008248 | 0
2013-06-20 08:55 | MFA21 | LONG RURAL |  | 105 | 373 | 39165 | 0.15166 | 0.00040659 | 0
2013-06-19 09:50 | CYN23 | URBAN |  | 140 | 170 | 23800 | 0.082907 | 0.00048769 | 0
2013-06-19 09:00 | RWN24 | SHORT RURAL |  | 103 | 367 | 37801 | 0.32894 | 0.0008963 | 0
2013-06-20 09:35 | RWT11 | URBAN |  | 96 | 235 | 22560 | 0.078587 | 0.00033441 | 0
2013-06-20 09:10 | RWN24 | SHORT RURAL |  | 128 | 325 | 41600 | 0.362 | 0.0011139 | 0
2013-06-19 09:25 | MFA31 | SHORT RURAL |  | 99 | 410 | 40590 | 0.35321 | 0.0008615 | 0
2013-06-20 08:33 | BWR23 | URBAN |  | 271 | 317 | 85907 | 0.29926 | 0.00094402 | 0
2013-06-20 09:03 | WYK24 | SHORT RURAL |  | 31 | 112 | 3472 | 0.030213 | 0.00026976 | 0
2013-06-20 13:50 | BRA21 | URBAN |  | 322 | 100 | 32200 | 0.11217 | 0.0011217 | 0
2013-06-21 09:00 | WGL21 | LONG RURAL |  | 2 | 90 | 180 | 0.00069702 | 7.7446e-06 | 0
2013-06-17 08:55 | WN6 | LONG RURAL |  | 54 | 135 | 7290 | 0.028229 | 0.0002091 | 0
2013-06-20 09:00 | WGL15 | SHORT RURAL |  | 2 | 70 | 140 | 0.0012183 | 1.7404e-05 | 0
2013-06-20 09:50 | MOE14 | SHORT RURAL |  | 2 | 135 | 270 | 0.0023495 | 1.7404e-05 | 0
2013-06-17 13:47 | WN4 | SHORT RURAL |  | 45 | 13 | 585 | 0.0050907 | 0.00039159 | 0
2013-06-18 09:20 | BN6 | LONG RURAL |  | 4 | 178 | 712 | 0.0027571 | 1.5489e-05 | 0
2013-06-18 10:35 | KLO14 | LONG RURAL |  | 392 | 375 | 147000 | 0.56923 | 0.0015179 | 0
2013-06-18 09:45 | BGE24 | SHORT RURAL |  | 25 | 378 | 9450 | 0.082234 | 0.00021755 | 0
2013-06-14 08:33 | CRE33 | SHORT RURAL |  | 13 | 87 | 1131 | 0.0098419 | 0.00011313 | 0
2013-06-18 11:18 | BN1 | LONG RURAL |  | 1 | 32 | 32 | 0.00012391 | 3.8723e-06 | 0
2013-06-18 09:05 | WT13 | URBAN |  | 50 | 465 | 23250 | 0.080991 | 0.00017417 | 0
2013-06-18 09:12 | TT6 | URBAN |  | 86 | 90 | 7740 | 0.026962 | 0.00029958 | 0
2013-06-22 09:00 | MWTS31 | SHORT RURAL |  | 46 | 406 | 18676 | 0.16252 | 0.00040029 | 0
2013-06-19 08:38 | BWN14 | SHORT RURAL |  | 61 | 257 | 15677 | 0.13642 | 0.00053082 | 0
2013-06-19 08:32 | PHM11 | URBAN |  | 36 | 352 | 12672 | 0.044143 | 0.00012541 | 0
2013-06-19 08:35 | SMR8 | LONG RURAL |  | 69 | 319 | 22011 | 0.085234 | 0.00026719 | 0
2013-06-19 10:08 | CLN12 | SHORT RURAL |  | 113 | 132 | 14916 | 0.1298 | 0.00098332 | 0
2013-06-19 13:20 | BWN14 | SHORT RURAL |  | 13 | 93 | 1209 | 0.010521 | 0.00011313 | 0
2013-06-20 09:54 | BWN14 | SHORT RURAL |  | 127 | 282 | 35814 | 0.31165 | 0.0011052 | 0
2013-06-21 08:46 | WO32 | URBAN |  | 23 | 142 | 3266 | 0.011377 | 8.012e-05 | 0
2013-06-20 09:37 | SMR8 | LONG RURAL |  | 10 | 223 | 2230 | 0.0086353 | 3.8723e-05 | 0
2013-06-19 09:39 | WT12 | URBAN |  | 171 | 335.462 | 57364 | 0.19983 | 0.00059568 | 0
2013-06-18 08:50 | ELM34 | URBAN |  | 166 | 425 | 70550 | 0.24576 | 0.00057826 | 0
2013-06-20 08:45 | RWT15 | URBAN |  | 185 | 410 | 75850 | 0.26422 | 0.00064444 | 0
2013-06-07 07:40 | MYT2 | SHORT RURAL |  | 360 | 4 | 1440 | 0.012531 | 0.0031327 | 0
2013-06-23 09:17 | WO22 | URBAN |  | 4 | 228 | 912 | 0.0031769 | 1.3934e-05 | 0
2013-06-23 09:00 | TGN31 | LONG RURAL |  | 108 | 283 | 30564 | 0.11835 | 0.00041821 | 0
2013-06-23 09:10 | WGI24 | URBAN |  | 1 | 53 | 53 | 0.00018462 | 3.4835e-06 | 0
2013-06-23 09:13 | LGA11 | LONG RURAL |  | 976 | 375 | 366000 | 1.4173 | 0.0037794 | 0
2013-06-23 09:00 | MWTS24 | SHORT RURAL |  | 72 | 415 | 29880 | 0.26001 | 0.00062654 | 0
2013-06-23 09:11 | MWTS11 | SHORT RURAL |  | 243 | 299 | 72657 | 0.63226 | 0.0021146 | 0
2013-06-19 10:18 | BWA22 | LONG RURAL |  | 21 | 348 | 7308 | 0.028299 | 8.1319e-05 | 0
2013-06-19 09:25 | EPG14 | URBAN |  | 132 | 200 | 26400 | 0.091964 | 0.00045982 | 0
2013-06-18 09:20 | WN4 | SHORT RURAL |  | 39 | 190 | 7410 | 0.064482 | 0.00033938 | 0
2013-06-20 10:30 | EPG12 | URBAN |  | 95 | 332.2632 | 31565 | 0.10996 | 0.00033093 | 0
2013-06-21 08:30 | RWT22 | URBAN |  | 126 | 200 | 25200 | 0.087784 | 0.00043892 | 0
2013-06-21 12:25 | RWT15 | URBAN |  | 98 | 145 | 14210 | 0.0495 | 0.00034138 | 0
2013-06-20 09:10 | BGE11 | SHORT RURAL |  | 90 | 300 | 27000 | 0.23495 | 0.00078318 | 0
2013-06-21 09:00 | KMS1 | SHORT RURAL |  | 25 | 142 | 3550 | 0.030892 | 0.00021755 | 0
2013-06-24 09:40 | WGL21 | LONG RURAL |  | 4 | 305 | 1220 | 0.0047242 | 1.5489e-05 | 0
2013-06-24 08:34 | MOE13 | SHORT RURAL |  | 592 | 355 | 210160 | 1.8288 | 0.0051516 | 0
2013-06-24 09:20 | MOE31 | LONG RURAL |  | 2 | 170 | 340 | 0.0013166 | 7.7446e-06 | 0
2013-06-24 10:58 | FTR21 | LONG RURAL |  | 2 | 134 | 268 | 0.0010378 | 7.7446e-06 | 0
2013-06-22 09:00 | KMS1 | SHORT RURAL |  | 29 | 412 | 11948 | 0.10397 | 0.00025236 | 0
2013-06-17 10:35 | WOTS11 | LONG RURAL |  | 3 | 15 | 45 | 0.00017425 | 1.1617e-05 | 0
2013-06-24 10:10 | ALA01 | LONG RURAL |  | 8 | 156 | 1248 | 0.0048326 | 3.0979e-05 | 0
2013-06-24 09:45 | ALA01 | LONG RURAL |  | 6 | 210 | 1260 | 0.0048791 | 2.3234e-05 | 0
2013-06-24 08:46 | RWT25 | URBAN |  | 482 | 285 | 137370 | 0.47853 | 0.001679 | 0
2013-06-18 09:20 | PHM11 | URBAN |  | 197 | 347 | 68359 | 0.23813 | 0.00068625 | 0
2013-06-21 09:04 | BGE22 | SHORT RURAL |  | 15 | 379 | 5685 | 0.049471 | 0.00013053 | 0
2013-06-23 06:35 | FGY32 | URBAN |  | 12 | 137 | 1644 | 0.0057268 | 4.1802e-05 | 0
2013-06-23 09:35 | BGE23 | SHORT RURAL |  | 147 | 345 | 50715 | 0.44132 | 0.0012792 | 0
2013-06-23 08:35 | BGE22 | SHORT RURAL |  | 111 | 455 | 50505 | 0.43949 | 0.00096592 | 0
2013-06-21 09:20 | BRA14 | URBAN |  | 103 | 325 | 33475 | 0.11661 | 0.0003588 | 0
2013-06-20 08:50 | CRE23 | URBAN |  | 297 | 280 | 83160 | 0.28969 | 0.0010346 | 0
2013-06-24 08:40 | BWR13 | SHORT RURAL |  | 471 | 360 | 169560 | 1.4755 | 0.0040986 | 0
2013-06-23 08:45 | RWT14 | URBAN |  | 752 | 290 | 218080 | 0.75968 | 0.0026196 | 0
2013-06-24 09:30 | FGY33 | URBAN |  | 84 | 80 | 6720 | 0.023409 | 0.00029261 | 0
2013-06-23 08:35 | CYN11 | URBAN |  | 22 | 419 | 9218 | 0.032111 | 7.6637e-05 | 0
2013-06-20 09:23 | OFR23 | LONG RURAL |  | 41 | 174 | 7134 | 0.027625 | 0.00015876 | 0
2013-06-23 07:36 | BRA21 | URBAN |  | 4 | 192 | 768 | 0.0026753 | 1.3934e-05 | 0
2013-06-11 08:30 | KLK2 | SHORT RURAL |  | 365 | 46.0904 | 16823 | 0.14639 | 0.0031762 | 0
2013-06-25 09:30 | FTR21 | LONG RURAL |  | 1 | 300 | 300 | 0.0011617 | 3.8723e-06 | 0
2013-06-26 09:45 | TGN23 | SHORT RURAL |  | 142 | 150 | 21300 | 0.18535 | 0.0012357 | 0
2013-06-25 08:35 | MOE13 | SHORT RURAL |  | 43 | 225 | 9675 | 0.084192 | 0.00037418 | 0
2013-06-25 09:05 | TGN11 | SHORT RURAL |  | 75 | 312 | 23400 | 0.20363 | 0.00065265 | 0
2013-06-26 09:40 | TGN14 | LONG RURAL |  | 12 | 275 | 3300 | 0.012779 | 4.6468e-05 | 0
2013-06-26 09:24 | WGL24 | LONG RURAL |  | 65 | 231 | 15015 | 0.058143 | 0.0002517 | 0
2013-06-26 09:10 | MYT8 | SHORT RURAL |  | 10 | 390 | 3900 | 0.033938 | 8.702e-05 | 0
2013-06-25 11:40 | LGA11 | LONG RURAL |  | 33 | 200 | 6600 | 0.025557 | 0.00012779 | 0
2013-06-25 09:00 | LGA22 | SHORT RURAL |  | 67 | 220 | 14740 | 0.12827 | 0.00058303 | 0
2013-06-25 09:07 | LGA12 | SHORT RURAL |  | 1 | 248 | 248 | 0.0021581 | 8.702e-06 | 0
2013-06-26 09:15 | WGI14 | SHORT RURAL |  | 74 | 275 | 20350 | 0.17709 | 0.00064395 | 0
2013-06-25 10:05 | MOE13 | SHORT RURAL |  | 20 | 154 | 3080 | 0.026802 | 0.00017404 | 0
2013-06-26 10:25 | FTR22 | SHORT RURAL |  | 49 | 100 | 4900 | 0.04264 | 0.0004264 | 0
2013-06-26 09:00 | MOE22 | LONG RURAL |  | 65 | 295 | 19175 | 0.074252 | 0.0002517 | 0
2013-06-27 09:33 | TGN23 | SHORT RURAL |  | 34 | 207 | 7038 | 0.061244 | 0.00029587 | 0
2013-06-25 09:15 | KLK1 | SHORT RURAL |  | 51 | 440 | 22440 | 0.19527 | 0.0004438 | 0
2013-06-25 11:00 | WYK23 | SHORT RURAL |  | 3 | 210 | 630 | 0.0054822 | 2.6106e-05 | 0
2013-06-25 08:30 | WO32 | URBAN |  | 88 | 285 | 25080 | 0.087366 | 0.00030655 | 0
2013-06-26 08:34 | MOE32 | SHORT RURAL |  | 11 | 331 | 3641 | 0.031684 | 9.5722e-05 | 0
2013-06-27 09:18 | MOE13 | SHORT RURAL |  | 25 | 202 | 5050 | 0.043945 | 0.00021755 | 0
2013-06-27 09:00 | WGL13 | SHORT RURAL |  | 69 | 388 | 26772 | 0.23297 | 0.00060044 | 0
2013-06-26 09:07 | PHI13 | URBAN |  | 124 | 358 | 44392 | 0.15464 | 0.00043195 | 0
2013-06-26 09:25 | WO32 | URBAN |  | 145 | 250 | 36250 | 0.12628 | 0.00050511 | 0
2013-06-27 09:15 | WGI23 | SHORT RURAL |  | 5 | 15 | 75 | 0.00065265 | 4.351e-05 | 0
2013-06-27 11:15 | WOTS12 | URBAN |  | 159 | 170 | 27030 | 0.094159 | 0.00055387 | 0
2013-06-27 11:30 | MOE32 | SHORT RURAL |  | 2 | 122 | 244 | 0.0021233 | 1.7404e-05 | 0
2013-06-26 08:30 | LDL11 | URBAN |  | 323 | 330 | 106590 | 0.3713 | 0.0011252 | 0
2013-06-26 08:30 | WYK24 | SHORT RURAL |  | 1 | 199 | 199 | 0.0017317 | 8.702e-06 | 0
2013-06-26 13:35 | LDL13 | SHORT RURAL |  | 136 | 213 | 28968 | 0.25208 | 0.0011835 | 0
2013-06-27 08:55 | WO32 | URBAN |  | 80 | 261 | 20880 | 0.072735 | 0.00027868 | 0
2013-06-27 09:22 | WGI22 | LONG RURAL |  | 124 | 430 | 53320 | 0.20647 | 0.00048017 | 0
2013-06-26 09:40 | KLK1 | SHORT RURAL |  | 385 | 401 | 154385 | 1.3435 | 0.0033503 | 0
2013-06-27 08:30 | LDL21 | SHORT RURAL |  | 78 | 160 | 12480 | 0.1086 | 0.00067875 | 0
2013-06-27 09:30 | MDG1 | SHORT RURAL |  | 34 | 300 | 10200 | 0.08876 | 0.00029587 | 0
2013-06-25 10:00 | WGL15 | SHORT RURAL |  | 3 | 110 | 330 | 0.0028717 | 2.6106e-05 | 0
2013-06-25 10:00 | WGL15 | SHORT RURAL |  | 1 | 299 | 299 | 0.0026019 | 8.702e-06 | 0
2013-06-25 09:20 | SLE31 | LONG RURAL |  | 19 | 155 | 2945 | 0.011404 | 7.3574e-05 | 0
2013-06-25 08:30 | SLE31 | LONG RURAL |  | 4 | 270 | 1080 | 0.0041821 | 1.5489e-05 | 0
2013-06-27 09:05 | MYT2 | SHORT RURAL |  | 44 | 345 | 15180 | 0.1321 | 0.00038289 | 0
2013-06-25 12:25 | SLE31 | LONG RURAL |  | 4 | 85 | 340 | 0.0013166 | 1.5489e-05 | 0
2013-06-26 09:19 | SLE31 | LONG RURAL |  | 9 | 75 | 675 | 0.0026138 | 3.4851e-05 | 0
2013-06-25 09:10 | BDL1 | LONG RURAL |  | 3 | 185 | 555 | 0.0021491 | 1.1617e-05 | 0
2013-06-26 11:30 | SLE31 | LONG RURAL |  | 4 | 195 | 780 | 0.0030204 | 1.5489e-05 | 0
2013-06-27 08:45 | BDL8 | LONG RURAL |  | 15 | 340 | 5100 | 0.019749 | 5.8085e-05 | 0
2013-06-27 10:15 | SLE31 | LONG RURAL |  | 39 | 125 | 4875 | 0.018878 | 0.00015102 | 0
2013-06-27 10:20 | FTR22 | SHORT RURAL |  | 2 | 20 | 40 | 0.00034808 | 1.7404e-05 | 0
2013-06-27 11:00 | WOTS13 | LONG RURAL |  | 26 | 240 | 6240 | 0.024163 | 0.00010068 | 0
2013-06-24 13:38 | ALA01 | LONG RURAL |  | 3 | 88 | 264 | 0.0010223 | 1.1617e-05 | 0
2013-06-25 08:35 | SMR8 | LONG RURAL |  | 3 | 235 | 705 | 0.00273 | 1.1617e-05 | 0
2013-06-25 13:00 | SMR8 | LONG RURAL |  | 1 | 90 | 90 | 0.00034851 | 3.8723e-06 | 0
2013-06-25 09:20 | BN1 | LONG RURAL |  | 7 | 370 | 2590 | 0.010029 | 2.7106e-05 | 0
2013-06-25 08:56 | RWN26 | SHORT RURAL |  | 39 | 329 | 12831 | 0.11165 | 0.00033938 | 0
2013-06-25 08:50 | CYN14 | URBAN |  | 631 | 378 | 238518 | 0.83087 | 0.0021981 | 0
2013-06-21 09:05 | CLN23 | SHORT RURAL |  | 7 | 175 | 1225 | 0.01066 | 6.0914e-05 | 0
2013-06-21 08:30 | BWN13 | URBAN |  | 107 | 144 | 15408 | 0.053674 | 0.00037273 | 0
2013-06-21 09:00 | OFR23 | LONG RURAL |  | 4 | 300 | 1200 | 0.0046468 | 1.5489e-05 | 0
2013-06-21 08:56 | WGL12 | LONG RURAL |  | 102 | 105 | 10710 | 0.041472 | 0.00039498 | 0
2013-06-21 08:55 | WGL12 | LONG RURAL |  | 399 | 1 | 399 | 0.0015451 | 0.0015451 | 0
2013-06-21 11:17 | OFR23 | LONG RURAL |  | 29 | 98 | 2842 | 0.011005 | 0.0001123 | 0
2013-06-21 11:50 | PHM14 | LONG RURAL |  | 1 | 108 | 108 | 0.00041821 | 3.8723e-06 | 0
2013-06-26 08:30 | CLN23 | SHORT RURAL |  | 606 | 262 | 158772 | 1.3816 | 0.0052734 | 0
2013-06-26 12:35 | CLN14 | SHORT RURAL |  | 69 | 85 | 5865 | 0.051037 | 0.00060044 | 0
2013-06-27 08:48 | PHM14 | LONG RURAL |  | 85 | 359 | 30515 | 0.11816 | 0.00032915 | 0
2013-06-24 10:15 | ELM11 | URBAN |  | 52 | 230 | 11960 | 0.041662 | 0.00018114 | 0
2013-06-24 09:45 | TT6 | URBAN |  | 60 | 160 | 9600 | 0.033441 | 0.00020901 | 0
2013-06-24 09:30 | WT6 | URBAN |  | 97 | 270 | 26190 | 0.091232 | 0.0003379 | 0
2013-06-25 09:15 | RWN24 | SHORT RURAL |  | 15 | 250 | 3750 | 0.032632 | 0.00013053 | 0
2013-06-20 09:24 | WT5 | URBAN |  | 287 | 334.0174 | 95863 | 0.33394 | 0.00099976 | 0
2013-06-13 09:20 | WN5 | LONG RURAL |  | 41 | 430 | 17630 | 0.068269 | 0.00015876 | 0
2013-06-28 09:00 | MYT8 | SHORT RURAL |  | 10 | 375 | 3750 | 0.032632 | 8.702e-05 | 0
2013-06-28 09:15 | LGA22 | SHORT RURAL |  | 143 | 95 | 13585 | 0.11822 | 0.0012444 | 0
2013-06-28 08:35 | MOE13 | SHORT RURAL |  | 28 | 45 | 1260 | 0.010964 | 0.00024366 | 0
2013-06-28 09:15 | WGL13 | SHORT RURAL |  | 9 | 185 | 1665 | 0.014489 | 7.8318e-05 | 0
2013-06-28 09:00 | TGN14 | LONG RURAL |  | 1 | 162 | 162 | 0.00062731 | 3.8723e-06 | 0
2013-06-28 11:05 | WO22 | URBAN |  | 61 | 145 | 8845 | 0.030811 | 0.00021249 | 0
2013-06-27 12:05 | LDL23 | LONG RURAL |  | 109 | 131 | 14279 | 0.055293 | 0.00042208 | 0
2013-06-28 08:38 | MOE22 | LONG RURAL |  | 35 | 66 | 2310 | 0.008945 | 0.00013553 | 0
2013-06-28 08:38 | MOE32 | SHORT RURAL |  | 46 | 66 | 3036 | 0.026419 | 0.00040029 | 0
2013-06-28 10:04 | MOE32 | SHORT RURAL |  | 65 | 188 | 12220 | 0.10634 | 0.00056563 | 0
2013-06-28 09:13 | LDL23 | LONG RURAL |  | 3 | 307 | 921 | 0.0035664 | 1.1617e-05 | 0
2013-06-28 09:20 | LDL24 | URBAN |  | 104 | 195 | 20280 | 0.070645 | 0.00036228 | 0
2013-06-28 08:53 | CRE22 | URBAN |  | 197 | 297 | 58509 | 0.20382 | 0.00068625 | 0
2013-06-26 08:30 | RWN22 | URBAN |  | 53 | 295 | 15635 | 0.054464 | 0.00018462 | 0
2013-06-26 08:30 | CYN21 | URBAN |  | 112 | 265 | 29680 | 0.10339 | 0.00039015 | 0
2013-06-22 13:15 | CYN13 | URBAN |  | 1 | 90 | 90 | 0.00031351 | 3.4835e-06 | 0
2013-06-27 09:00 | LGA13 | LONG RURAL |  | 51 | 392.2549 | 20005 | 0.077466 | 0.00019749 | 0
2013-06-21 09:35 | ELM13 | URBAN |  | 11 | 245 | 2695 | 0.009388 | 3.8318e-05 | 0
2013-06-25 08:30 | RWN33 | URBAN |  | 67 | 59 | 3953 | 0.01377 | 0.00023339 | 0
2013-06-28 09:00 | MOE22 | LONG RURAL |  | 25 | 310 | 7750 | 0.03001 | 9.6808e-05 | 0
2013-06-24 08:45 | HPK14 | URBAN |  | 14 | 303 | 4242 | 0.014777 | 4.8769e-05 | 0
2013-06-24 09:25 | BGE24 | SHORT RURAL |  | 27 | 405 | 10935 | 0.095156 | 0.00023495 | 0
2013-06-24 09:08 | BGE22 | SHORT RURAL |  | 56 | 22 | 1232 | 0.010721 | 0.00048731 | 0
2013-06-24 16:00 | BGE22 | SHORT RURAL |  | 56 | 20 | 1120 | 0.0097462 | 0.00048731 | 0
2013-06-24 12:30 | FGY13 | SHORT RURAL |  | 51 | 50 | 2550 | 0.02219 | 0.0004438 | 0
2013-06-23 10:28 | EPG14 | URBAN |  | 332 | 372 | 123504 | 0.43022 | 0.0011565 | 0
2013-06-23 09:55 | TT4 | URBAN |  | 113 | 415 | 46895 | 0.16336 | 0.00039363 | 0
2013-06-21 12:25 | DRN12 | URBAN |  | 54 | 47.0926 | 2543 | 0.0088585 | 0.00018811 | 0
2013-06-24 09:40 | KMS21 | SHORT RURAL |  | 4 | 210 | 840 | 0.0073097 | 3.4808e-05 | 0
2013-06-25 09:20 | KMS21 | SHORT RURAL |  | 1 | 205 | 205 | 0.0017839 | 8.702e-06 | 0
2013-06-26 08:30 | BN6 | LONG RURAL |  | 107 | 430 | 46010 | 0.17817 | 0.00041434 | 0
2013-06-26 08:00 | BRA14 | URBAN |  | 114 | 420 | 47880 | 0.16679 | 0.00039712 | 0
2013-06-26 08:00 | BRA21 | URBAN |  | 174 | 420 | 73080 | 0.25457 | 0.00060613 | 0
2013-06-26 08:30 | BWR13 | SHORT RURAL |  | 5 | 170 | 850 | 0.0073967 | 4.351e-05 | 0
2013-06-26 08:32 | BWR13 | SHORT RURAL |  | 604 | 403 | 243412 | 2.1182 | 0.005256 | 0
2013-06-27 08:30 | RWT15 | URBAN |  | 322 | 470 | 151340 | 0.52719 | 0.0011217 | 0
2013-06-28 09:00 | MOE13 | SHORT RURAL |  | 47 | 140 | 6580 | 0.057259 | 0.00040899 | 0
2013-06-27 09:00 | WGL24 | LONG RURAL |  | 4 | 320 | 1280 | 0.0049566 | 1.5489e-05 | 0
2013-06-26 09:14 | KMS21 | SHORT RURAL |  | 2 | 161 | 322 | 0.002802 | 1.7404e-05 | 0
2013-06-25 09:40 | MBY14 | SHORT RURAL |  | 1 | 80 | 80 | 0.00069616 | 8.702e-06 | 0
2013-06-28 09:35 | TGN31 | LONG RURAL |  | 28 | 190 | 5320 | 0.020601 | 0.00010842 | 0
2013-06-20 09:00 | MYT2 | SHORT RURAL |  | 29 | 165 | 4785 | 0.041639 | 0.00025236 | 0
2013-06-20 13:20 | MYT8 | SHORT RURAL |  | 3 | 50 | 150 | 0.0013053 | 2.6106e-05 | 0
2013-06-25 10:48 | ELM32 | URBAN |  | 63 | 137 | 8631 | 0.030066 | 0.00021946 | 0
2013-06-21 07:30 | DRN11 | URBAN |  | 1 | 345 | 345 | 0.0012018 | 3.4835e-06 | 0
2013-06-28 09:20 | BRA32 | URBAN |  | 18 | 104 | 1872 | 0.0065211 | 6.2703e-05 | 0
2013-06-28 09:05 | RWN31 | SHORT RURAL |  | 149 | 285 | 42465 | 0.36953 | 0.0012966 | 0
2013-06-29 08:30 | CYN33 | SHORT RURAL |  | 42 | 365 | 15330 | 0.1334 | 0.00036548 | 0
2013-06-13 09:54 | BWR23 | URBAN |  | 199 | 251 | 49949 | 0.174 | 0.00069321 | 0
2013-06-30 08:45 | LGA22 | SHORT RURAL |  | 91 | 254 | 23114 | 0.20114 | 0.00079188 | 0
2013-06-30 08:00 | LDL22 | SHORT RURAL |  | 25 | 795 | 19875 | 0.17295 | 0.00021755 | 0
2013-06-30 09:21 | KLK1 | SHORT RURAL |  | 109 | 257 | 28013 | 0.24377 | 0.00094851 | 0
2013-06-30 08:40 | MOE22 | LONG RURAL |  | 4 | 185 | 740 | 0.0028655 | 1.5489e-05 | 0
2013-06-30 08:20 | BRA21 | URBAN |  | 20 | 363 | 7260 | 0.02529 | 6.967e-05 | 0
2013-06-28 10:15 | WOTS13 | LONG RURAL |  | 31 | 310 | 9610 | 0.037213 | 0.00012004 | 0
2013-06-27 09:05 | BN1 | LONG RURAL |  | 2 | 278 | 556 | 0.002153 | 7.7446e-06 | 0
2013-06-25 08:40 | NRN12 | URBAN |  | 291 | 30 | 8730 | 0.030411 | 0.0010137 | 0
2013-06-25 08:40 | FGY14 | URBAN |  | 64 | 245 | 15680 | 0.054621 | 0.00022294 | 0
2013-06-27 10:05 | KMS21 | SHORT RURAL |  | 5 | 250 | 1250 | 0.010877 | 4.351e-05 | 0
2013-06-25 13:45 | HPK21 | URBAN |  | 115 | 180 | 20700 | 0.072108 | 0.0004006 | 0
2013-06-25 09:15 | ELM31 | URBAN |  | 129 | 330 | 42570 | 0.14829 | 0.00044937 | 0
2013-06-26 09:05 | FGY33 | URBAN |  | 59 | 145 | 8555 | 0.029801 | 0.00020553 | 0
2013-06-26 08:30 | HPK22 | URBAN |  | 29 | 160 | 4640 | 0.016163 | 0.00010102 | 0
2013-06-26 09:40 | FGY23 | URBAN |  | 70 | 245 | 17150 | 0.059742 | 0.00024384 | 0
2013-06-26 09:00 | BGE12 | SHORT RURAL |  | 132 | 140 | 18480 | 0.16081 | 0.0011487 | 0
2013-06-15 05:52 | BRA31 | URBAN |  | 1 | 735 | 735 | 0.0025604 | 3.4835e-06 | 0
2013-07-01 09:15 | WGI14 | SHORT RURAL |  | 2 | 190 | 380 | 0.0033067 | 1.7404e-05 | 0
2013-06-30 13:00 | MOE22 | LONG RURAL |  | 11 | 85 | 935 | 0.0036206 | 4.2595e-05 | 0
2013-07-01 09:55 | MOE23 | SHORT RURAL |  | 46 | 195 | 8970 | 0.078057 | 0.00040029 | 0
2013-07-01 08:20 | WYK11 | SHORT RURAL |  | 20 | 116.5 | 2330 | 0.020276 | 0.00017404 | 0
2013-07-01 09:20 | LGA23 | LONG RURAL |  | 51 | 269.6078 | 13750 | 0.053244 | 0.00019749 | 0
2013-07-01 10:10 | WGI22 | LONG RURAL |  | 17 | 180 | 3060 | 0.011849 | 6.5829e-05 | 0
2013-07-01 08:30 | SLE31 | LONG RURAL |  | 47 | 367 | 17249 | 0.066794 | 0.000182 | 0
2013-07-01 09:00 | WO32 | URBAN |  | 91 | 220 | 20020 | 0.069739 | 0.000317 | 0
2013-06-27 13:30 | ALA01 | LONG RURAL |  | 4 | 60 | 240 | 0.00092936 | 1.5489e-05 | 0
2013-06-27 12:00 | ALA01 | LONG RURAL |  | 2 | 70 | 140 | 0.00054212 | 7.7446e-06 | 0
2013-06-27 09:25 | ALA01 | LONG RURAL |  | 2 | 125 | 250 | 0.00096808 | 7.7446e-06 | 0
2013-06-28 09:00 | ALA01 | LONG RURAL |  | 2 | 120 | 240 | 0.00092936 | 7.7446e-06 | 0
2013-06-28 09:35 | ALA01 | LONG RURAL |  | 1 | 35 | 35 | 0.00013553 | 3.8723e-06 | 0
2013-06-28 11:05 | ALA01 | LONG RURAL |  | 1 | 30 | 30 | 0.00011617 | 3.8723e-06 | 0
2013-06-25 09:48 | ELM32 | URBAN |  | 337 | 202 | 68074 | 0.23713 | 0.0011739 | 0
2013-06-30 09:13 | WN5 | LONG RURAL |  | 1 | 214 | 214 | 0.00082868 | 3.8723e-06 | 0
2013-06-25 09:40 | EPG14 | URBAN |  | 108 | 295 | 31860 | 0.11098 | 0.00037622 | 0
2013-06-25 08:40 | ELM15 | SHORT RURAL |  | 115 | 425 | 48875 | 0.42531 | 0.0010007 | 0
2013-07-02 09:21 | MOE14 | SHORT RURAL |  | 563 | 274 | 154262 | 1.3424 | 0.0048992 | 0
2013-07-02 09:35 | TGN11 | SHORT RURAL |  | 1041 | 360 | 374760 | 3.2612 | 0.0090588 | 0
2013-07-02 11:40 | MWTS21 | URBAN |  | 118 | 215 | 25370 | 0.088376 | 0.00041105 | 0
2013-07-03 08:05 | MOE13 | SHORT RURAL |  | 301 | 462 | 139062 | 1.2101 | 0.0026193 | 0
2013-07-03 09:50 | WGL13 | SHORT RURAL |  | 10 | 280 | 2800 | 0.024366 | 8.702e-05 | 0
2013-07-03 09:40 | MOE22 | LONG RURAL |  | 26 | 130 | 3380 | 0.013088 | 0.00010068 | 0
2013-07-03 09:56 | MWTS32 | SHORT RURAL |  | 2 | 74 | 148 | 0.0012879 | 1.7404e-05 | 0
2013-07-02 09:15 | MOE31 | LONG RURAL |  | 3 | 270 | 810 | 0.0031366 | 1.1617e-05 | 0
2013-07-04 09:25 | TGN14 | LONG RURAL |  | 36 | 151 | 5436 | 0.02105 | 0.0001394 | 0
2013-07-02 09:30 | PHI11 | SHORT RURAL |  | 537 | 105 | 56385 | 0.49066 | 0.004673 | 0
2013-07-03 09:03 | FTR21 | LONG RURAL |  | 1 | 235 | 235 | 0.00090999 | 3.8723e-06 | 0
2013-07-04 09:20 | LGA23 | LONG RURAL |  | 1 | 320 | 320 | 0.0012391 | 3.8723e-06 | 0
2013-07-01 11:20 | WYK24 | SHORT RURAL |  | 22 | 65 | 1430 | 0.012444 | 0.00019144 | 0
2013-07-01 13:15 | WYK24 | SHORT RURAL |  | 44 | 145 | 6380 | 0.055519 | 0.00038289 | 0
2013-07-02 10:03 | WYK24 | SHORT RURAL |  | 177 | 322 | 56994 | 0.49596 | 0.0015402 | 0
2013-07-02 09:00 | LGA13 | LONG RURAL |  | 2 | 240 | 480 | 0.0018587 | 7.7446e-06 | 0
2013-07-04 09:10 | LGA13 | LONG RURAL |  | 50 | 380 | 19000 | 0.073574 | 0.00019362 | 0
2013-07-03 09:00 | WGI22 | LONG RURAL |  | 54 | 315 | 17010 | 0.065868 | 0.0002091 | 0
2013-07-04 08:50 | DRN12 | URBAN |  | 48 | 319 | 15312 | 0.053339 | 0.00016721 | 0
2013-07-04 08:30 | WGI22 | LONG RURAL |  | 7 | 435 | 3045 | 0.011791 | 2.7106e-05 | 0
2013-07-03 13:45 | WYK11 | SHORT RURAL |  | 2 | 35 | 70 | 0.00060914 | 1.7404e-05 | 0
2013-07-03 08:15 | WYK11 | SHORT RURAL |  | 1 | 41 | 41 | 0.00035678 | 8.702e-06 | 0
2013-07-03 10:10 | WYK11 | SHORT RURAL |  | 5 | 40 | 200 | 0.0017404 | 4.351e-05 | 0
2013-07-03 12:00 | WYK11 | SHORT RURAL |  | 3 | 60 | 180 | 0.0015664 | 2.6106e-05 | 0
2013-07-02 09:00 | WGL13 | SHORT RURAL |  | 340 | 226.5 | 77010 | 0.67014 | 0.0029587 | 0
2013-07-04 09:22 | MOE13 | SHORT RURAL |  | 184 | 256 | 47104 | 0.4099 | 0.0016012 | 0
2013-07-02 09:00 | WGL11 | SHORT RURAL |  | 18 | 235 | 4230 | 0.036809 | 0.00015664 | 0
2013-07-02 09:30 | MWTS21 | URBAN |  | 83 | 85 | 7055 | 0.024576 | 0.00028913 | 0
2013-07-04 09:00 | LGA22 | SHORT RURAL |  | 18 | 169 | 3042 | 0.026471 | 0.00015664 | 0
2013-07-04 08:30 | WOTS24 | LONG RURAL |  | 2 | 347.5 | 695 | 0.0026913 | 7.7446e-06 | 0
2013-07-02 08:50 | RWN24 | SHORT RURAL |  | 95 | 360 | 34200 | 0.29761 | 0.00082669 | 0
2013-07-04 14:08 | LDL22 | SHORT RURAL |  | 171 | 67 | 11457 | 0.099698 | 0.001488 | 0
2013-07-04 09:50 | LDL22 | SHORT RURAL |  | 3 | 255 | 765 | 0.006657 | 2.6106e-05 | 0
2013-07-02 08:40 | RWT22 | URBAN |  | 122 | 445 | 54290 | 0.18912 | 0.00042498 | 0
2013-07-02 09:15 | WN2 | LONG RURAL |  | 1 | 160 | 160 | 0.00061957 | 3.8723e-06 | 0
2013-07-02 10:05 | WN5 | LONG RURAL |  | 1 | 50 | 50 | 0.00019362 | 3.8723e-06 | 0
2013-07-04 09:20 | MOE22 | LONG RURAL |  | 179 | 320 | 57280 | 0.22181 | 0.00069314 | 0
2013-07-02 08:45 | MSD2 | LONG RURAL |  | 309 | 245 | 75705 | 0.29315 | 0.0011965 | 0
2013-07-04 09:30 | LDL23 | LONG RURAL |  | 16 | 141 | 2256 | 0.0087359 | 6.1957e-05 | 0
2013-07-02 10:55 | BDL1 | LONG RURAL |  | 3 | 210 | 630 | 0.0024396 | 1.1617e-05 | 0
2013-07-02 08:40 | SLE31 | LONG RURAL |  | 69 | 360 | 24840 | 0.096188 | 0.00026719 | 0
2013-07-02 08:30 | SLE31 | LONG RURAL |  | 558 | 449 | 250542 | 0.97018 | 0.0021608 | 0
2013-07-03 09:08 | WN5 | LONG RURAL |  | 61 | 225 | 13725 | 0.053148 | 0.00023621 | 0
2013-07-03 09:00 | WGL11 | SHORT RURAL |  | 23 | 370 | 8510 | 0.074054 | 0.00020015 | 0
2013-07-03 08:35 | BDL1 | LONG RURAL |  | 901 | 403 | 363103 | 1.406 | 0.003489 | 0
2013-07-02 09:30 | WO31 | URBAN |  | 1 | 126 | 126 | 0.00043892 | 3.4835e-06 | 0
2013-07-03 11:30 | MOE24 | SHORT RURAL |  | 12 | 80 | 960 | 0.0083539 | 0.00010442 | 0
2013-07-01 09:55 | KMS1 | SHORT RURAL |  | 2 | 155 | 310 | 0.0026976 | 1.7404e-05 | 0
2013-07-03 09:35 | MOE24 | SHORT RURAL |  | 32 | 100 | 3200 | 0.027846 | 0.00027846 | 0
2013-07-03 13:55 | MOE24 | SHORT RURAL |  | 106 | 55 | 5830 | 0.050732 | 0.00092241 | 0
2013-07-03 09:15 | MYT7 | LONG RURAL |  | 19 | 318 | 6042 | 0.023397 | 7.3574e-05 | 0
2013-06-25 08:30 | WT5 | URBAN |  | 138 | 455 | 62790 | 0.21873 | 0.00048072 | 0
2013-06-25 12:15 | ELM31 | URBAN |  | 70 | 75 | 5250 | 0.018288 | 0.00024384 | 0
2013-06-25 14:05 | ELM31 | URBAN |  | 44 | 70 | 3080 | 0.010729 | 0.00015327 | 0
2013-06-27 09:15 | BGE11 | SHORT RURAL |  | 288 | 299 | 86112 | 0.74934 | 0.0025062 | 0
2013-06-27 08:35 | CLN14 | SHORT RURAL |  | 163 | 105 | 17115 | 0.14893 | 0.0014184 | 0
2013-06-27 08:35 | HPK14 | URBAN |  | 191 | 105 | 20055 | 0.069861 | 0.00066535 | 0
2013-06-27 08:35 | HPK23 | URBAN |  | 1 | 40 | 40 | 0.00013934 | 3.4835e-06 | 0
2013-07-04 09:05 | SLE32 | SHORT RURAL |  | 1 | 55 | 55 | 0.00047861 | 8.702e-06 | 0
2013-06-27 08:37 | HPK22 | URBAN |  | 196 | 306.8571 | 60144 | 0.20951 | 0.00068276 | 0
2013-06-27 08:35 | SFS1 | SHORT RURAL |  | 283 | 543 | 153669 | 1.3372 | 0.0024627 | 0
2013-06-26 10:00 | DRN12 | URBAN |  | 190 | 330 | 62700 | 0.21841 | 0.00066186 | 0
2013-06-28 09:25 | FGY34 | URBAN |  | 73 | 211 | 15403 | 0.053656 | 0.00025429 | 0
2013-06-28 08:55 | WT5 | URBAN |  | 123 | 275 | 33825 | 0.11783 | 0.00042847 | 0
2013-06-27 08:15 | EPG31 | URBAN |  | 210 | 463 | 97230 | 0.3387 | 0.00073153 | 0
2013-07-04 09:08 | MYT7 | LONG RURAL |  | 5 | 186 | 930 | 0.0036013 | 1.9362e-05 | 0
2013-06-27 09:00 | ELM33 | SHORT RURAL |  | 44 | 298 | 13112 | 0.1141 | 0.00038289 | 0
2013-06-28 09:13 | TT9 | URBAN |  | 94 | 117 | 10998 | 0.038311 | 0.00032745 | 0
2013-06-30 09:30 | FGY21 | SHORT RURAL |  | 10 | 410 | 4100 | 0.035678 | 8.702e-05 | 0
2013-07-04 08:00 | WYK24 | SHORT RURAL |  | 133 | 170 | 22610 | 0.19675 | 0.0011574 | 0
2013-07-03 09:50 | MFA31 | SHORT RURAL |  | 391 | 352 | 137632 | 1.1977 | 0.0034025 | 0
2013-06-28 11:20 | TT9 | URBAN |  | 123 | 115 | 14145 | 0.049274 | 0.00042847 | 0
2013-07-02 09:20 | RWN26 | SHORT RURAL |  | 17 | 95 | 1615 | 0.014054 | 0.00014793 | 0
2013-07-02 09:27 | BRA14 | URBAN |  | 182 | 243 | 44226 | 0.15406 | 0.00063399 | 0
2013-06-28 09:40 | PHM14 | LONG RURAL |  | 49 | 380 | 18620 | 0.072102 | 0.00018974 | 0
2013-07-02 09:40 | RWN31 | SHORT RURAL |  | 15 | 385 | 5775 | 0.050254 | 0.00013053 | 0
2013-07-02 09:30 | RWN22 | URBAN |  | 69 | 300 | 20700 | 0.072108 | 0.00024036 | 0
2013-07-01 09:15 | LLG11 | SHORT RURAL |  | 26 | 75 | 1950 | 0.016969 | 0.00022625 | 0
2013-07-01 08:00 | CRE32 | URBAN |  | 1 | 240 | 240 | 0.00083604 | 3.4835e-06 | 0
2013-06-26 08:45 | WT13 | URBAN |  | 362 | 375 | 135750 | 0.47288 | 0.001261 | 0
2013-07-02 11:30 | RWN26 | SHORT RURAL |  | 37 | 210 | 7770 | 0.067614 | 0.00032197 | 0
2013-07-02 13:18 | RWN26 | SHORT RURAL |  | 46 | 110 | 5060 | 0.044032 | 0.00040029 | 0
2013-07-03 08:45 | BRA14 | URBAN |  | 104 | 362 | 37648 | 0.13115 | 0.00036228 | 0
2013-07-03 09:00 | RWN33 | URBAN |  | 78 | 345 | 26910 | 0.093741 | 0.00027171 | 0
2013-06-27 08:52 | BN6 | LONG RURAL |  | 3 | 326 | 978 | 0.0037871 | 1.1617e-05 | 0
2013-07-01 12:30 | LLG11 | SHORT RURAL |  | 1 | 70 | 70 | 0.00060914 | 8.702e-06 | 0
2013-07-05 09:25 | TGN31 | LONG RURAL |  | 1 | 220 | 220 | 0.00085191 | 3.8723e-06 | 0
2013-07-05 08:50 | LLG12 | SHORT RURAL |  | 2 | 80 | 160 | 0.0013923 | 1.7404e-05 | 0
2013-07-05 08:45 | LGA12 | SHORT RURAL |  | 3 | 60 | 180 | 0.0015664 | 2.6106e-05 | 0
2013-07-04 11:30 | LDL14 | SHORT RURAL |  | 60 | 87 | 5220 | 0.045424 | 0.00052212 | 0
2013-07-05 09:38 | LDL24 | URBAN |  | 18 | 131 | 2358 | 0.0082141 | 6.2703e-05 | 0
2013-07-04 13:00 | LDL14 | SHORT RURAL |  | 12 | 90 | 1080 | 0.0093981 | 0.00010442 | 0
2013-07-04 13:35 | MYT7 | LONG RURAL |  | 3 | 55 | 165 | 0.00063893 | 1.1617e-05 | 0
2013-07-04 11:00 | WYK24 | SHORT RURAL |  | 31 | 50 | 1550 | 0.013488 | 0.00026976 | 0
2013-07-01 09:00 | KMS1 | SHORT RURAL |  | 187 | 257 | 48059 | 0.41821 | 0.0016273 | 0
2013-07-02 10:00 | ALA01 | LONG RURAL |  | 16 | 270 | 4320 | 0.016728 | 6.1957e-05 | 0
2013-07-02 09:00 | KMS21 | SHORT RURAL |  | 45 | 383 | 17235 | 0.14998 | 0.00039159 | 0
2013-06-20 08:50 | WN2 | LONG RURAL |  | 1 | 90 | 90 | 0.00034851 | 3.8723e-06 | 0
2013-07-02 11:35 | NRN15 | URBAN |  | 3 | 139 | 417 | 0.0014526 | 1.045e-05 | 0
2013-07-03 09:40 | BWR34 | URBAN |  | 125 | 465 | 58125 | 0.20248 | 0.00043544 | 0
2013-07-03 09:32 | BWR13 | SHORT RURAL |  | 542 | 285 | 154470 | 1.3442 | 0.0047165 | 0
2013-06-28 09:43 | TT6 | URBAN |  | 110 | 255 | 28050 | 0.097712 | 0.00038318 | 0
2013-07-05 10:40 | LLG12 | SHORT RURAL |  | 2 | 85 | 170 | 0.0014793 | 1.7404e-05 | 0
2013-07-05 10:35 | LLG12 | SHORT RURAL |  | 1 | 75 | 75 | 0.00065265 | 8.702e-06 | 0
2013-07-06 09:00 | MWTS31 | SHORT RURAL |  | 46 | 360 | 16560 | 0.1441 | 0.00040029 | 0
2013-06-30 10:18 | KLO11 | URBAN |  | 1 | 73 | 73 | 0.00025429 | 3.4835e-06 | 0
2013-06-30 08:30 | BWR12 | URBAN |  | 17 | 380 | 6460 | 0.022503 | 5.9219e-05 | 0
2013-07-04 08:50 | SLE31 | LONG RURAL |  | 725 | 328 | 237800 | 0.92084 | 0.0028074 | 0
2013-07-03 08:30 | BN2 | LONG RURAL |  | 34 | 365 | 12410 | 0.048055 | 0.00013166 | 0
2013-07-01 09:10 | DRN13 | SHORT RURAL |  | 2 | 10 | 20 | 0.00017404 | 1.7404e-05 | 0
2013-06-30 09:39 | TT12 | URBAN |  | 65 | 285 | 18525 | 0.064532 | 0.00022643 | 0
2013-07-01 10:36 | DRN13 | SHORT RURAL |  | 3 | 5 | 15 | 0.00013053 | 2.6106e-05 | 0
2013-07-03 09:45 | SMR5 | LONG RURAL |  | 4 | 270 | 1080 | 0.0041821 | 1.5489e-05 | 0
2013-07-01 12:39 | DRN13 | SHORT RURAL |  | 1 | 6 | 6 | 5.2212e-05 | 8.702e-06 | 0
2013-07-03 09:10 | SMR8 | LONG RURAL |  | 277 | 346 | 95842 | 0.37113 | 0.0010726 | 0
2013-07-03 09:30 | WN3 | LONG RURAL |  | 1 | 320 | 320 | 0.0012391 | 3.8723e-06 | 0
2013-07-02 09:00 | OFR23 | LONG RURAL |  | 30 | 385 | 11550 | 0.044725 | 0.00011617 | 0
2013-07-02 08:46 | CRE33 | SHORT RURAL |  | 36 | 249 | 8964 | 0.078004 | 0.00031327 | 0
2013-07-03 10:10 | PHM14 | LONG RURAL |  | 55 | 360 | 19800 | 0.076672 | 0.00021298 | 0
2013-07-03 10:38 | WGL12 | LONG RURAL |  | 50 | 202 | 10100 | 0.03911 | 0.00019362 | 0
2013-07-07 09:00 | WGI22 | LONG RURAL |  | 25 | 398 | 9950 | 0.03853 | 9.6808e-05 | 0
2013-07-07 09:00 | MWTS32 | SHORT RURAL |  | 10 | 90 | 900 | 0.0078318 | 8.702e-05 | 0
2013-07-01 14:30 | DRN13 | SHORT RURAL |  | 1 | 10 | 10 | 8.702e-05 | 8.702e-06 | 0
2013-07-04 09:20 | ALA01 | LONG RURAL |  | 1 | 135 | 135 | 0.00052276 | 3.8723e-06 | 0
2013-07-01 12:20 | ELM15 | SHORT RURAL |  | 1 | 52 | 52 | 0.0004525 | 8.702e-06 | 0
2013-07-01 14:20 | DRN12 | URBAN |  | 6 | 60 | 360 | 0.0012541 | 2.0901e-05 | 0
2013-07-04 09:15 | SMR8 | LONG RURAL |  | 1 | 168 | 168 | 0.00065055 | 3.8723e-06 | 0
2013-07-02 09:10 | WT11 | URBAN |  | 204 | 330 | 67320 | 0.23451 | 0.00071063 | 0
2013-07-04 10:28 | KLO14 | LONG RURAL |  | 138 | 262 | 36156 | 0.14001 | 0.00053438 | 0
2013-07-05 08:44 | BDL1 | LONG RURAL |  | 46 | 351 | 16146 | 0.062522 | 0.00017813 | 0
2013-07-04 09:40 | SMR5 | LONG RURAL |  | 3 | 155 | 465 | 0.0018006 | 1.1617e-05 | 0
2013-07-03 08:16 | EPG12 | URBAN |  | 270 | 311 | 83970 | 0.29251 | 0.00094054 | 0
2013-07-04 11:05 | BWR12 | URBAN |  | 84 | 118 | 9912 | 0.034528 | 0.00029261 | 0
2013-07-04 12:30 | ALA01 | LONG RURAL |  | 3 | 135 | 405 | 0.0015683 | 1.1617e-05 | 0
2013-07-04 13:00 | SMR8 | LONG RURAL |  | 4 | 52 | 208 | 0.00080544 | 1.5489e-05 | 0
2013-07-04 10:20 | BRA23 | URBAN |  | 85 | 138 | 11730 | 0.040861 | 0.0002961 | 0
2013-07-02 09:20 | KMS1 | SHORT RURAL |  | 3 | 315 | 945 | 0.0082234 | 2.6106e-05 | 0
2013-07-03 09:05 | ELM31 | URBAN |  | 74 | 260 | 19240 | 0.067022 | 0.00025778 | 0
2013-07-08 08:50 | TGN31 | LONG RURAL |  | 24 | 335 | 8040 | 0.031133 | 9.2936e-05 | 0
2013-07-08 09:00 | MOE31 | LONG RURAL |  | 72 | 200 | 14400 | 0.055761 | 0.00027881 | 0
2013-07-08 09:00 | WGI34 | SHORT RURAL |  | 125 | 220 | 27500 | 0.2393 | 0.0010877 | 0
2013-07-08 09:01 | WGI34 | SHORT RURAL |  | 91 | 237 | 21567 | 0.18768 | 0.00079188 | 0
2013-07-08 09:20 | MOE22 | LONG RURAL |  | 63 | 156 | 9828 | 0.038057 | 0.00024396 | 0
2013-07-07 12:15 | TGN11 | SHORT RURAL |  | 2 | 80 | 160 | 0.0013923 | 1.7404e-05 | 0
2013-07-08 09:00 | TGN23 | SHORT RURAL |  | 292 | 300 | 87600 | 0.76229 | 0.002541 | 0
2013-07-04 09:25 | WT13 | URBAN |  | 195 | 390 | 76050 | 0.26492 | 0.00067928 | 0
2013-07-03 12:40 | PHM34 | URBAN |  | 123 | 171 | 21033 | 0.073268 | 0.00042847 | 0
2013-07-05 09:05 | KMS1 | SHORT RURAL |  | 525 | 335 | 175875 | 1.5305 | 0.0045685 | 0
2013-07-05 09:40 | SMR8 | LONG RURAL |  | 2 | 70 | 140 | 0.00054212 | 7.7446e-06 | 0
2013-06-27 09:13 | BN4 | URBAN |  | 91 | 115 | 10465 | 0.036455 | 0.000317 | 0
2013-07-02 09:00 | WN6 | LONG RURAL |  | 2 | 14 | 28 | 0.00010842 | 7.7446e-06 | 0
2013-07-04 09:03 | BDL1 | LONG RURAL |  | 21 | 321 | 6741 | 0.026103 | 8.1319e-05 | 0
2013-07-05 08:30 | MFA23 | SHORT RURAL |  | 69 | 240 | 16560 | 0.1441 | 0.00060044 | 0
2013-07-03 12:18 | KLO24 | SHORT RURAL |  | 239 | 232 | 55448 | 0.48251 | 0.0020798 | 0
2013-07-07 08:15 | WO14 | URBAN |  | 66 | 65 | 4290 | 0.014944 | 0.00022991 | 0
2013-07-03 09:10 | ELM34 | URBAN |  | 640 | 390 | 249600 | 0.86948 | 0.0022294 | 0
2013-07-08 09:13 | BN6 | LONG RURAL |  | 22 | 355 | 7810 | 0.030243 | 8.5191e-05 | 0
2013-07-04 08:42 | BGE22 | SHORT RURAL |  | 70 | 272 | 19040 | 0.16569 | 0.00060914 | 0
2013-07-04 08:40 | BGE22 | SHORT RURAL |  | 674 | 498 | 335652 | 2.9208 | 0.0058651 | 0
2013-06-24 12:05 | TT9 | URBAN |  | 5796 | 210 | 1217160 | 4.24 | 0.02019 | 0
2013-07-09 09:00 | BWR32 | URBAN |  | 245 | 330 | 80850 | 0.28164 | 0.00085345 | 0
2013-07-10 09:05 | RWN31 | SHORT RURAL |  | 67 | 215 | 14405 | 0.12535 | 0.00058303 | 0
2013-07-08 12:50 | MOE31 | LONG RURAL |  | 8 | 115 | 920 | 0.0035625 | 3.0979e-05 | 0
2013-07-09 10:10 | MOE31 | LONG RURAL |  | 1 | 150 | 150 | 0.00058085 | 3.8723e-06 | 0
2013-07-09 09:10 | WGL21 | LONG RURAL |  | 37 | 210 | 7770 | 0.030088 | 0.00014328 | 0
2013-07-09 09:40 | MOE31 | LONG RURAL |  | 2 | 85 | 170 | 0.00065829 | 7.7446e-06 | 0
2013-07-09 11:36 | MOE31 | LONG RURAL |  | 2 | 29 | 58 | 0.00022459 | 7.7446e-06 | 0
2013-07-09 13:15 | MOE31 | LONG RURAL |  | 4 | 45 | 180 | 0.00069702 | 1.5489e-05 | 0
2013-07-10 08:20 | MOE13 | SHORT RURAL |  | 173 | 290 | 50170 | 0.43658 | 0.0015054 | 0
2013-07-10 09:15 | TGN31 | LONG RURAL |  | 64 | 302 | 19328 | 0.074844 | 0.00024783 | 0
2013-07-11 09:00 | TGN11 | SHORT RURAL |  | 1 | 320 | 320 | 0.0027846 | 8.702e-06 | 0
2013-07-09 09:35 | WN3 | LONG RURAL |  | 3 | 185 | 555 | 0.0021491 | 1.1617e-05 | 0
2013-07-08 13:30 | WGI34 | SHORT RURAL |  | 247 | 130 | 32110 | 0.27942 | 0.0021494 | 0
2013-07-09 09:00 | WGI34 | SHORT RURAL |  | 45 | 60 | 2700 | 0.023495 | 0.00039159 | 0
2013-07-09 11:00 | WGI34 | SHORT RURAL |  | 38 | 56 | 2128 | 0.018518 | 0.00033067 | 0
2013-07-09 09:00 | WGI34 | SHORT RURAL |  | 74 | 250 | 18500 | 0.16099 | 0.00064395 | 0
2013-07-11 09:25 | MOE24 | SHORT RURAL |  | 33 | 320 | 10560 | 0.091893 | 0.00028717 | 0
2013-07-09 09:25 | WGI23 | SHORT RURAL |  | 1 | 13 | 13 | 0.00011313 | 8.702e-06 | 0
2013-07-11 08:30 | MOE13 | SHORT RURAL |  | 28 | 72 | 2016 | 0.017543 | 0.00024366 | 0
2013-07-11 09:05 | TGN23 | SHORT RURAL |  | 108 | 220 | 23760 | 0.20676 | 0.00093981 | 0
2013-07-11 09:35 | TGN11 | SHORT RURAL |  | 1 | 25 | 25 | 0.00021755 | 8.702e-06 | 0
2013-07-10 08:30 | WO32 | URBAN |  | 63 | 147 | 9261 | 0.032261 | 0.00021946 | 0
2013-07-11 09:15 | WO32 | URBAN |  | 32 | 89 | 2848 | 0.009921 | 0.00011147 | 0
2013-07-10 09:05 | TGN23 | SHORT RURAL |  | 427 | 275 | 117425 | 1.0218 | 0.0037157 | 0
2013-07-10 09:00 | WGI31 | SHORT RURAL |  | 429 | 91 | 39039 | 0.33972 | 0.0037331 | 0
2013-07-09 09:45 | MYT8 | SHORT RURAL |  | 3 | 305 | 915 | 0.0079623 | 2.6106e-05 | 0
2013-07-10 13:15 | WGI31 | SHORT RURAL |  | 1 | 85 | 85 | 0.00073967 | 8.702e-06 | 0
2013-07-11 09:28 | LGA12 | SHORT RURAL |  | 36 | 133 | 4788 | 0.041665 | 0.00031327 | 0
2013-07-11 08:40 | WGI22 | LONG RURAL |  | 1 | 57 | 57 | 0.00022072 | 3.8723e-06 | 0
2013-07-09 09:06 | FTR12 | LONG RURAL |  | 5 | 398 | 1990 | 0.0077059 | 1.9362e-05 | 0
2013-07-09 08:15 | WYK24 | SHORT RURAL |  | 98 | 518 | 50764 | 0.44175 | 0.00085279 | 0
2013-07-09 09:40 | WGL12 | LONG RURAL |  | 19 | 225 | 4275 | 0.016554 | 7.3574e-05 | 0
2013-07-10 09:05 | WGL21 | LONG RURAL |  | 7 | 155 | 1085 | 0.0042015 | 2.7106e-05 | 0
2013-07-09 09:52 | WOTS13 | LONG RURAL |  | 1 | 143 | 143 | 0.00055374 | 3.8723e-06 | 0
2013-07-09 09:45 | LDL23 | LONG RURAL |  | 218 | 593 | 129274 | 0.50059 | 0.00084416 | 0
2013-07-11 09:30 | MOE14 | SHORT RURAL |  | 12 | 230 | 2760 | 0.024017 | 0.00010442 | 0
2013-07-09 09:45 | MOE14 | SHORT RURAL |  | 3 | 165 | 495 | 0.0043075 | 2.6106e-05 | 0
2013-07-09 10:15 | LDL12 | URBAN |  | 24 | 235 | 5640 | 0.019647 | 8.3604e-05 | 0
2013-07-11 10:00 | MBY11 | SHORT RURAL |  | 40 | 140 | 5600 | 0.048731 | 0.00034808 | 0
2013-07-10 14:00 | WYK11 | SHORT RURAL |  | 10 | 40 | 400 | 0.0034808 | 8.702e-05 | 0
2013-07-10 09:00 | TGN31 | LONG RURAL |  | 89 | 300 | 26700 | 0.10339 | 0.00034464 | 0
2013-07-11 10:05 | WGL21 | LONG RURAL |  | 356 | 245 | 87220 | 0.33774 | 0.0013785 | 0
2013-07-10 09:15 | MOE22 | LONG RURAL |  | 61 | 405 | 24705 | 0.095666 | 0.00023621 | 0
2013-07-11 08:25 | LDL11 | URBAN |  | 71 | 140 | 9940 | 0.034626 | 0.00024733 | 0
2013-07-11 09:00 | LDL22 | SHORT RURAL |  | 107 | 235 | 25145 | 0.21881 | 0.00093111 | 0
2013-07-11 09:27 | WYK11 | SHORT RURAL |  | 576 | 433 | 249408 | 2.1703 | 0.0050123 | 0
2013-07-10 09:41 | BDL2 | SHORT RURAL |  | 1 | 54 | 54 | 0.00046991 | 8.702e-06 | 0
2013-07-10 08:41 | BDL8 | LONG RURAL |  | 1152 | 416 | 479232 | 1.8557 | 0.0044609 | 0
2013-07-10 09:25 | LGA11 | LONG RURAL |  | 27 | 140 | 3780 | 0.014637 | 0.00010455 | 0
2013-07-11 09:05 | LGA14 | LONG RURAL |  | 41 | 204 | 8364 | 0.032388 | 0.00015876 | 0
2013-07-11 09:10 | LGA11 | LONG RURAL |  | 37 | 205 | 7585 | 0.029372 | 0.00014328 | 0
2013-07-09 09:00 | BN6 | LONG RURAL |  | 20 | 380 | 7600 | 0.02943 | 7.7446e-05 | 0
2013-07-09 09:05 | FTR12 | LONG RURAL |  | 42 | 445 | 18690 | 0.072374 | 0.00016264 | 0
2013-07-04 09:30 | RWN24 | SHORT RURAL |  | 157 | 380 | 59660 | 0.51916 | 0.0013662 | 0
2013-07-04 09:10 | BWR23 | URBAN |  | 122 | 130 | 15860 | 0.055248 | 0.00042498 | 0
2013-07-04 10:21 | RWT25 | URBAN |  | 84 | 265 | 22260 | 0.077542 | 0.00029261 | 0
2013-07-04 11:35 | BWR23 | URBAN |  | 132 | 182 | 24024 | 0.083687 | 0.00045982 | 0
2013-07-03 09:02 | KLO24 | SHORT RURAL |  | 64 | 53 | 3392 | 0.029517 | 0.00055693 | 0
2013-07-04 09:25 | WT12 | URBAN |  | 151 | 105 | 15855 | 0.055231 | 0.00052601 | 0
2013-07-04 13:45 | ELM33 | SHORT RURAL |  | 61 | 27 | 1647 | 0.014332 | 0.00053082 | 0
2013-07-05 09:05 | RWN31 | SHORT RURAL |  | 222 | 320 | 71040 | 0.61819 | 0.0019318 | 0
2013-07-04 09:00 | OFR23 | LONG RURAL |  | 1 | 380 | 380 | 0.0014715 | 3.8723e-06 | 0
2013-07-04 09:05 | PHM14 | LONG RURAL |  | 33 | 305 | 10065 | 0.038975 | 0.00012779 | 0
2013-07-05 09:10 | OFR23 | LONG RURAL |  | 1 | 65 | 65 | 0.0002517 | 3.8723e-06 | 0
2013-07-02 10:10 | KLK1 | SHORT RURAL |  | 1 | 170 | 170 | 0.0014793 | 8.702e-06 | 0
2013-07-09 09:45 | BDL5 | LONG RURAL |  | 24 | 127 | 3048 | 0.011803 | 9.2936e-05 | 0
2013-07-08 08:40 | MSD4 | LONG RURAL |  | 51 | 360 | 18360 | 0.071096 | 0.00019749 | 0
2013-07-08 09:34 | BGE24 | SHORT RURAL |  | 176 | 276 | 48576 | 0.42271 | 0.0015315 | 0
2013-07-04 09:40 | WT12 | URBAN |  | 79 | 262 | 20698 | 0.072101 | 0.0002752 | 0
2013-07-05 09:33 | BWN13 | URBAN |  | 190 | 102 | 19380 | 0.06751 | 0.00066186 | 0
2013-07-08 09:40 | ELM32 | URBAN |  | 131 | 160 | 20960 | 0.073014 | 0.00045634 | 0
2013-07-05 11:00 | OFR23 | LONG RURAL |  | 2 | 60 | 120 | 0.00046468 | 7.7446e-06 | 0
2013-07-08 09:15 | ELM15 | SHORT RURAL |  | 65 | 125 | 8125 | 0.070704 | 0.00056563 | 0
2013-07-06 08:06 | PHM11 | URBAN |  | 49 | 369 | 18081 | 0.062985 | 0.00017069 | 0
2013-07-08 11:55 | ELM34 | URBAN |  | 117 | 70 | 8190 | 0.02853 | 0.00040757 | 0
2013-07-08 12:40 | ELM32 | URBAN |  | 10 | 40 | 400 | 0.0013934 | 3.4835e-05 | 0
2013-07-05 08:45 | BN6 | LONG RURAL |  | 143 | 432.0909 | 61789 | 0.23927 | 0.00055374 | 0
2013-07-09 09:30 | ELM31 | URBAN |  | 410 | 375 | 153750 | 0.53559 | 0.0014282 | 0
2013-07-12 08:50 | WGL23 | SHORT RURAL |  | 3 | 113 | 339 | 0.00295 | 2.6106e-05 | 0
2013-07-12 08:30 | WGL23 | SHORT RURAL |  | 1 | 68 | 68 | 0.00059173 | 8.702e-06 | 0
2013-07-12 09:30 | MWTS24 | SHORT RURAL |  | 54 | 210 | 11340 | 0.09868 | 0.00046991 | 0
2013-07-12 09:05 | TGN12 | SHORT RURAL |  | 82 | 280 | 22960 | 0.1998 | 0.00071356 | 0
2013-07-12 09:30 | MOE31 | LONG RURAL |  | 2 | 65 | 130 | 0.0005034 | 7.7446e-06 | 0
2013-07-11 13:05 | LGA23 | LONG RURAL |  | 6 | 98 | 588 | 0.0022769 | 2.3234e-05 | 0
2013-07-12 09:40 | WGI24 | URBAN |  | 111 | 324 | 35964 | 0.12528 | 0.00038667 | 0
2013-07-12 09:00 | FTR23 | LONG RURAL |  | 291 | 440 | 128040 | 0.49581 | 0.0011268 | 0
2013-07-11 11:05 | WGI33 | SHORT RURAL |  | 2 | 40 | 80 | 0.00069616 | 1.7404e-05 | 0
2013-07-12 09:10 | FTR21 | LONG RURAL |  | 1 | 280 | 280 | 0.0010842 | 3.8723e-06 | 0
2013-07-11 13:00 | MBY11 | SHORT RURAL |  | 11 | 105 | 1155 | 0.010051 | 9.5722e-05 | 0
2013-07-12 09:30 | MBY11 | SHORT RURAL |  | 14 | 90 | 1260 | 0.010964 | 0.00012183 | 0
2013-07-11 12:55 | LDL22 | SHORT RURAL |  | 48 | 100 | 4800 | 0.041769 | 0.00041769 | 0
2013-07-11 10:30 | WYK23 | SHORT RURAL |  | 3 | 50 | 150 | 0.0013053 | 2.6106e-05 | 0
2013-07-12 09:05 | WGL24 | LONG RURAL |  | 18 | 480 | 8640 | 0.033457 | 6.9702e-05 | 0
2013-07-12 09:29 | LDL24 | URBAN |  | 840 | 151.9095 | 127604 | 0.44451 | 0.0029261 | 0
2013-07-08 10:00 | TT5 | URBAN |  | 111 | 280 | 31080 | 0.10827 | 0.00038667 | 0
2013-07-09 09:18 | ELM13 | URBAN |  | 101 | 307 | 31007 | 0.10801 | 0.00035183 | 0
2013-07-10 09:15 | WT11 | URBAN |  | 162 | 200 | 32400 | 0.11286 | 0.00056432 | 0
2013-07-11 08:37 | WT15 | URBAN |  | 163 | 449 | 73187 | 0.25495 | 0.00056781 | 0
2013-07-11 10:45 | DRN12 | URBAN |  | 16 | 105 | 1680 | 0.0058523 | 5.5736e-05 | 0
2013-06-27 08:32 | LDL23 | LONG RURAL |  | 15 | 118 | 1770 | 0.006854 | 5.8085e-05 | 0
2013-07-02 10:02 | WYK24 | SHORT RURAL |  | 109 | 187.5596 | 20444 | 0.1779 | 0.00094851 | 0
2013-07-09 08:32 | MFA23 | SHORT RURAL |  | 146 | 315 | 45990 | 0.4002 | 0.0012705 | 0
2013-07-11 09:10 | BDL1 | LONG RURAL |  | 3 | 370 | 1110 | 0.0042983 | 1.1617e-05 | 0
2013-07-11 08:40 | BDL2 | SHORT RURAL |  | 1 | 345 | 345 | 0.0030022 | 8.702e-06 | 0
2013-07-09 09:35 | MWTS31 | SHORT RURAL |  | 1 | 75 | 75 | 0.00065265 | 8.702e-06 | 0
2013-07-10 09:30 | MFA31 | SHORT RURAL |  | 48 | 180 | 8640 | 0.075185 | 0.00041769 | 0
2013-07-12 09:20 | TT6 | URBAN |  | 104 | 310 | 32240 | 0.11231 | 0.00036228 | 0
2013-07-10 09:10 | UWY1 | SHORT RURAL |  | 29 | 50 | 1450 | 0.012618 | 0.00025236 | 0
2013-07-07 08:35 | WN4 | SHORT RURAL |  | 10 | 210 | 2100 | 0.018274 | 8.702e-05 | 0
2013-07-09 08:35 | BN1 | LONG RURAL |  | 13 | 1172 | 15236 | 0.058999 | 5.034e-05 | 0
2013-07-08 12:10 | BN6 | LONG RURAL |  | 1 | 105 | 105 | 0.00040659 | 3.8723e-06 | 0
2013-07-09 09:23 | WT11 | URBAN |  | 94 | 141 | 13254 | 0.04617 | 0.00032745 | 0
2013-07-03 09:15 | LDL22 | SHORT RURAL |  | 2 | 365 | 730 | 0.0063524 | 1.7404e-05 | 0
2013-07-13 09:00 | WGI22 | LONG RURAL |  | 64 | 185 | 11840 | 0.045848 | 0.00024783 | 0
2013-07-11 09:20 | SLE31 | LONG RURAL |  | 34 | 260 | 8840 | 0.034231 | 0.00013166 | 0
2013-07-11 09:40 | MYT7 | LONG RURAL |  | 2 | 65 | 130 | 0.0005034 | 7.7446e-06 | 0
2013-07-11 11:15 | MYT7 | LONG RURAL |  | 2 | 45 | 90 | 0.00034851 | 7.7446e-06 | 0
2013-07-07 08:00 | BRA21 | URBAN |  | 73 | 140 | 10220 | 0.035601 | 0.00025429 | 0
2013-07-14 08:30 | LDL13 | SHORT RURAL |  | 3 | 220 | 660 | 0.0057433 | 2.6106e-05 | 0
2013-07-14 09:10 | WT12 | URBAN |  | 22 | 215 | 4730 | 0.016477 | 7.6637e-05 | 0
2013-07-09 14:20 | CYN33 | SHORT RURAL |  | 83 | 80 | 6640 | 0.057781 | 0.00072226 | 0
2013-07-09 09:02 | RWT15 | URBAN |  | 91 | 105 | 9555 | 0.033285 | 0.000317 | 0
2013-07-09 09:08 | RWT22 | URBAN |  | 293 | 95 | 27835 | 0.096963 | 0.0010207 | 0
2013-07-09 09:00 | PHM14 | LONG RURAL |  | 18 | 315 | 5670 | 0.021956 | 6.9702e-05 | 0
2013-07-09 08:55 | CYN33 | SHORT RURAL |  | 111 | 218 | 24198 | 0.21057 | 0.00096592 | 0
2013-07-09 09:10 | PHM14 | LONG RURAL |  | 62 | 288 | 17856 | 0.069144 | 0.00024008 | 0
2013-07-11 12:40 | CYN21 | URBAN |  | 188 | 108 | 20304 | 0.070729 | 0.00065489 | 0
2013-07-11 09:15 | MFA21 | LONG RURAL |  | 1 | 315 | 315 | 0.0012198 | 3.8723e-06 | 0
2013-07-09 08:50 | HPK22 | URBAN |  | 169 | 186 | 31434 | 0.1095 | 0.00058871 | 0
2013-07-11 12:30 | MYT7 | LONG RURAL |  | 1 | 30 | 30 | 0.00011617 | 3.8723e-06 | 0
2013-07-12 08:50 | MFA22 | LONG RURAL |  | 199 | 212 | 42188 | 0.16337 | 0.00077059 | 0
2013-07-12 09:25 | BWA23 | SHORT RURAL |  | 1 | 70 | 70 | 0.00060914 | 8.702e-06 | 0
2013-07-10 09:00 | KMS21 | SHORT RURAL |  | 1 | 300 | 300 | 0.0026106 | 8.702e-06 | 0
2013-07-08 09:30 | RWN24 | SHORT RURAL |  | 72 | 200 | 14400 | 0.12531 | 0.00062654 | 0
2013-07-11 09:10 | MFA31 | SHORT RURAL |  | 152 | 400 | 60800 | 0.52908 | 0.0013227 | 0
2013-07-10 10:11 | MYT7 | LONG RURAL |  | 358 | 131.2821 | 46999 | 0.18199 | 0.0013863 | 0
2013-07-12 09:20 | TGN41 | LONG RURAL |  | 1 | 245 | 245 | 0.00094872 | 3.8723e-06 | 0
2013-07-11 09:00 | FGY34 | URBAN |  | 91 | 280 | 25480 | 0.088759 | 0.000317 | 0
2013-07-08 08:40 | RWN24 | SHORT RURAL |  | 48 | 230 | 11040 | 0.09607 | 0.00041769 | 0
2013-07-12 09:20 | BDL1 | LONG RURAL |  | 2 | 322 | 644 | 0.0024938 | 7.7446e-06 | 0
2013-07-11 08:58 | BGE12 | SHORT RURAL |  | 96 | 277 | 26592 | 0.2314 | 0.00083539 | 0
2013-07-12 09:03 | MYT7 | LONG RURAL |  | 2 | 72 | 144 | 0.00055761 | 7.7446e-06 | 0
2013-07-09 10:08 | RWN24 | SHORT RURAL |  | 670 | 358 | 239860 | 2.0873 | 0.0058303 | 0
2013-07-10 11:15 | WN3 | LONG RURAL |  | 17 | 150 | 2550 | 0.0098744 | 6.5829e-05 | 0
2013-07-11 09:00 | KMS21 | SHORT RURAL |  | 59 | 395 | 23305 | 0.2028 | 0.00051342 | 0
2013-07-11 08:34 | CRE22 | URBAN |  | 154 | 383.2078 | 59014 | 0.20557 | 0.00053646 | 0
2013-07-10 08:36 | ALA01 | LONG RURAL |  | 35 | 329 | 11515 | 0.04459 | 0.00013553 | 0
2013-07-09 09:00 | RWN31 | SHORT RURAL |  | 40 | 270 | 10800 | 0.093981 | 0.00034808 | 0
2013-07-09 14:30 | RWN24 | SHORT RURAL |  | 34 | 39 | 1326 | 0.011539 | 0.00029587 | 0
2013-07-10 09:17 | BN1 | LONG RURAL |  | 2 | 268 | 536 | 0.0020756 | 7.7446e-06 | 0
2013-07-10 08:30 | CYN32 | URBAN |  | 173 | 390 | 67470 | 0.23503 | 0.00060264 | 0
2013-07-11 08:45 | BN1 | LONG RURAL |  | 2 | 155 | 310 | 0.0012004 | 7.7446e-06 | 0
2013-07-12 08:32 | BN3 | SHORT RURAL |  | 15 | 257 | 3855 | 0.033546 | 0.00013053 | 0
2013-07-10 11:25 | BRA32 | URBAN |  | 93 | 195 | 18135 | 0.063173 | 0.00032396 | 0
2013-07-15 09:45 | WGI23 | SHORT RURAL |  | 1 | 200 | 200 | 0.0017404 | 8.702e-06 | 0
2013-07-15 09:25 | BWA22 | LONG RURAL |  | 3 | 115 | 345 | 0.0013359 | 1.1617e-05 | 0
2013-07-15 09:10 | WGL21 | LONG RURAL |  | 27 | 305 | 8235 | 0.031889 | 0.00010455 | 0
2013-07-15 09:00 | LDL11 | URBAN |  | 28 | 315 | 8820 | 0.030724 | 9.7538e-05 | 0
2013-07-15 09:29 | WGL15 | SHORT RURAL |  | 254 | 254 | 64516 | 0.56142 | 0.0022103 | 0
2013-07-15 09:18 | LGA22 | SHORT RURAL |  | 52 | 307 | 15964 | 0.13892 | 0.0004525 | 0
2013-07-15 08:40 | MWTS22 | SHORT RURAL |  | 1 | 509 | 509 | 0.0044293 | 8.702e-06 | 0
2013-07-15 09:50 | CYN31 | URBAN |  | 260 | 300 | 78000 | 0.27171 | 0.00090571 | 0
2013-07-10 09:08 | LLG12 | SHORT RURAL |  | 42 | 372 | 15624 | 0.13596 | 0.00036548 | 0
2013-07-10 08:30 | CLN23 | SHORT RURAL |  | 751 | 6 | 4506 | 0.039211 | 0.0065352 | 0
2013-07-10 09:00 | PHM14 | LONG RURAL |  | 24 | 293 | 7032 | 0.02723 | 9.2936e-05 | 0
2013-07-12 08:30 | HPK14 | URBAN |  | 216 | 300 | 64800 | 0.22573 | 0.00075243 | 0
2013-07-15 09:50 | KMS1 | SHORT RURAL |  | 82 | 95 | 7790 | 0.067788 | 0.00071356 | 0
2013-07-15 09:20 | KMS21 | SHORT RURAL |  | 8 | 120 | 960 | 0.0083539 | 6.9616e-05 | 0
2013-07-11 08:33 | SMR5 | LONG RURAL |  | 22 | 377 | 8294 | 0.032117 | 8.5191e-05 | 0
2013-07-11 10:33 | ALA01 | LONG RURAL |  | 19 | 102 | 1938 | 0.0075045 | 7.3574e-05 | 0
2013-07-02 09:11 | BWN14 | SHORT RURAL |  | 349 | 379 | 132271 | 1.151 | 0.003037 | 0
2013-07-16 09:05 | WGI24 | URBAN |  | 11 | 180 | 1980 | 0.0068973 | 3.8318e-05 | 0
2013-07-16 09:00 | LGA21 | SHORT RURAL |  | 20 | 125 | 2500 | 0.021755 | 0.00017404 | 0
2013-07-16 08:35 | LGA14 | LONG RURAL |  | 3 | 107 | 321 | 0.001243 | 1.1617e-05 | 0
2013-07-17 11:10 | WGL23 | SHORT RURAL |  | 3 | 75 | 225 | 0.0019579 | 2.6106e-05 | 0
2013-07-18 09:00 | WGL23 | SHORT RURAL |  | 2 | 80 | 160 | 0.0013923 | 1.7404e-05 | 0
2013-07-17 09:00 | MOE24 | SHORT RURAL |  | 205 | 350 | 71750 | 0.62437 | 0.0017839 | 0
2013-07-16 10:20 | WGL24 | LONG RURAL |  | 5 | 203 | 1015 | 0.0039304 | 1.9362e-05 | 0
2013-07-16 09:35 | TGN41 | LONG RURAL |  | 13 | 314 | 4082 | 0.015807 | 5.034e-05 | 0
2013-07-16 08:31 | BWA22 | LONG RURAL |  | 20 | 334 | 6680 | 0.025867 | 7.7446e-05 | 0
2013-07-18 09:00 | MOE24 | SHORT RURAL |  | 206 | 215 | 44290 | 0.38541 | 0.0017926 | 0
2013-07-17 09:20 | MBY11 | SHORT RURAL |  | 1 | 65 | 65 | 0.00056563 | 8.702e-06 | 0
2013-07-17 08:31 | BWA22 | LONG RURAL |  | 12 | 234 | 2808 | 0.010873 | 4.6468e-05 | 0
2013-07-17 08:45 | RWN26 | SHORT RURAL |  | 10 | 275 | 2750 | 0.02393 | 8.702e-05 | 0
2013-07-17 11:15 | MBY11 | SHORT RURAL |  | 4 | 105 | 420 | 0.0036548 | 3.4808e-05 | 0
2013-07-17 09:00 | WGL21 | LONG RURAL |  | 20 | 260 | 5200 | 0.020136 | 7.7446e-05 | 0
2013-07-18 08:34 | WO31 | URBAN |  | 63 | 386 | 24318 | 0.084711 | 0.00021946 | 0
2013-07-16 09:00 | WGL21 | LONG RURAL |  | 4 | 150 | 600 | 0.0023234 | 1.5489e-05 | 0
2013-07-16 11:25 | WGL21 | LONG RURAL |  | 3 | 130 | 390 | 0.0015102 | 1.1617e-05 | 0
2013-07-16 09:20 | RWN26 | SHORT RURAL |  | 35 | 335 | 11725 | 0.10203 | 0.00030457 | 0
2013-07-16 10:00 | MOE14 | SHORT RURAL |  | 3 | 80 | 240 | 0.0020885 | 2.6106e-05 | 0
2013-07-16 12:10 | MOE14 | SHORT RURAL |  | 2 | 70 | 140 | 0.0012183 | 1.7404e-05 | 0
2013-07-16 12:00 | TGN41 | LONG RURAL |  | 102 | 105 | 10710 | 0.041472 | 0.00039498 | 0
2013-07-17 11:15 | WGL15 | SHORT RURAL |  | 1 | 55 | 55 | 0.00047861 | 8.702e-06 | 0
2013-07-16 09:30 | WGL11 | SHORT RURAL |  | 53 | 220 | 11660 | 0.10146 | 0.0004612 | 0
2013-07-16 09:18 | TGN41 | LONG RURAL |  | 2 | 122 | 244 | 0.00094484 | 7.7446e-06 | 0
2013-07-18 09:25 | WT12 | URBAN |  | 278 | 260 | 72280 | 0.25179 | 0.00096841 | 0
2013-07-17 09:30 | WGI31 | SHORT RURAL |  | 134 | 30 | 4020 | 0.034982 | 0.0011661 | 0
2013-07-16 09:55 | LGA24 | SHORT RURAL |  | 1 | 65 | 65 | 0.00056563 | 8.702e-06 | 0
2013-07-16 10:05 | FTR23 | LONG RURAL |  | 1 | 160 | 160 | 0.00061957 | 3.8723e-06 | 0
2013-07-16 11:20 | LGA14 | LONG RURAL |  | 2 | 26 | 52 | 0.00020136 | 7.7446e-06 | 0
2013-07-16 13:07 | FTR21 | LONG RURAL |  | 40 | 80 | 3200 | 0.012391 | 0.00015489 | 0
2013-07-18 09:35 | TGN23 | SHORT RURAL |  | 3 | 280 | 840 | 0.0073097 | 2.6106e-05 | 0
2013-07-17 09:00 | LGA13 | LONG RURAL |  | 102 | 310 | 31620 | 0.12244 | 0.00039498 | 0
2013-07-18 09:00 | WGI24 | URBAN |  | 78 | 275 | 21450 | 0.074721 | 0.00027171 | 0
2013-07-18 09:25 | FTR21 | LONG RURAL |  | 8 | 170 | 1360 | 0.0052663 | 3.0979e-05 | 0
2013-07-18 07:50 | FTR22 | SHORT RURAL |  | 28 | 130 | 3640 | 0.031675 | 0.00024366 | 0
2013-07-16 09:40 | DRN12 | URBAN |  | 1 | 255 | 255 | 0.00088829 | 3.4835e-06 | 0
2013-07-18 09:05 | MOE22 | LONG RURAL |  | 25 | 360 | 9000 | 0.034851 | 9.6808e-05 | 0
2013-07-15 13:15 | WT13 | URBAN |  | 75 | 120 | 9000 | 0.031351 | 0.00026126 | 0
2013-07-16 09:20 | WT6 | URBAN |  | 77 | 135 | 10395 | 0.036211 | 0.00026823 | 0
2013-07-16 08:30 | MDG1 | SHORT RURAL |  | 136 | 390 | 53040 | 0.46155 | 0.0011835 | 0
2013-07-16 09:35 | WGL15 | SHORT RURAL |  | 1 | 45 | 45 | 0.00039159 | 8.702e-06 | 0
2013-07-16 10:50 | WGL15 | SHORT RURAL |  | 1 | 60 | 60 | 0.00052212 | 8.702e-06 | 0
2013-07-17 13:20 | LDL24 | URBAN |  | 52 | 92 | 4784 | 0.016665 | 0.00018114 | 0
2013-07-17 09:10 | LDL24 | URBAN |  | 107 | 185 | 19795 | 0.068956 | 0.00037273 | 0
2013-07-16 13:30 | WGL11 | SHORT RURAL |  | 1 | 60 | 60 | 0.00052212 | 8.702e-06 | 0
2013-07-16 08:45 | WGI23 | SHORT RURAL |  | 477 | 357 | 170289 | 1.4818 | 0.0041508 | 0
2013-07-18 09:50 | MOE31 | LONG RURAL |  | 5 | 240 | 1200 | 0.0046468 | 1.9362e-05 | 0
2013-07-16 08:16 | LDL11 | URBAN |  | 196 | 338.0918 | 66266 | 0.23084 | 0.00068276 | 0
2013-07-16 08:42 | BN1 | LONG RURAL |  | 26 | 198 | 5148 | 0.019935 | 0.00010068 | 0
2013-07-16 08:30 | SLE31 | LONG RURAL |  | 20 | 358 | 7160 | 0.027726 | 7.7446e-05 | 0
2013-07-17 09:00 | WGI22 | LONG RURAL |  | 8 | 410 | 3280 | 0.012701 | 3.0979e-05 | 0
2013-07-18 09:00 | LLG12 | SHORT RURAL |  | 40 | 157 | 6280 | 0.054648 | 0.00034808 | 0
2013-07-17 08:35 | BDL1 | LONG RURAL |  | 68 | 235 | 15980 | 0.06188 | 0.00026332 | 0
2013-07-17 08:45 | BDL1 | LONG RURAL |  | 26 | 447.1154 | 11625 | 0.045016 | 0.00010068 | 0
2013-07-07 08:30 | RWT14 | URBAN |  | 48 | 435 | 20880 | 0.072735 | 0.00016721 | 0
2013-07-11 09:05 | BRA33 | URBAN |  | 2 | 220 | 440 | 0.0015327 | 6.967e-06 | 0
2013-07-15 08:50 | RWN32 | URBAN |  | 302 | 255 | 77010 | 0.26826 | 0.001052 | 0
2013-07-10 11:00 | CLN14 | SHORT RURAL |  | 85 | 95 | 8075 | 0.070268 | 0.00073967 | 0
2013-07-11 09:08 | WGL12 | LONG RURAL |  | 13 | 260 | 3380 | 0.013088 | 5.034e-05 | 0
2013-07-12 10:21 | DRN12 | URBAN |  | 62 | 202 | 12524 | 0.043627 | 0.00021598 | 0
2013-07-11 08:42 | OFR22 | SHORT RURAL |  | 266 | 348 | 92568 | 0.80552 | 0.0023147 | 0
2013-07-11 08:30 | OFR23 | LONG RURAL |  | 55 | 445 | 24475 | 0.094775 | 0.00021298 | 0
2013-07-12 09:30 | WGL12 | LONG RURAL |  | 30 | 130 | 3900 | 0.015102 | 0.00011617 | 0
2013-07-12 08:30 | WGL12 | LONG RURAL |  | 141 | 480 | 67680 | 0.26208 | 0.000546 | 0
2013-07-13 08:35 | WGL12 | LONG RURAL |  | 57 | 90 | 5130 | 0.019865 | 0.00022072 | 0
2013-07-14 09:03 | PHM12 | SHORT RURAL |  | 1 | 282 | 282 | 0.002454 | 8.702e-06 | 0
2013-07-16 08:59 | PHM14 | LONG RURAL |  | 68 | 276 | 18768 | 0.072676 | 0.00026332 | 0
2013-07-17 09:15 | CRE23 | URBAN |  | 120 | 325 | 39000 | 0.13586 | 0.00041802 | 0
2013-07-17 08:35 | PHM14 | LONG RURAL |  | 10 | 165 | 1650 | 0.0063893 | 3.8723e-05 | 0
2013-07-18 08:32 | CLN22 | SHORT RURAL |  | 62 | 297.6774 | 18456 | 0.1606 | 0.00053952 | 0
2013-07-18 09:06 | BGE22 | SHORT RURAL |  | 287 | 337 | 96719 | 0.84165 | 0.0024975 | 0
2013-07-18 09:20 | WGL12 | LONG RURAL |  | 26 | 672.3077 | 17480 | 0.067688 | 0.00010068 | 0
2013-07-12 10:21 | HPK21 | URBAN |  | 170 | 108 | 18360 | 0.063957 | 0.00059219 | 0
2013-07-07 07:34 | TT6 | URBAN |  | 1 | 441 | 441 | 0.0015362 | 3.4835e-06 | 0
2013-07-12 08:50 | BGE22 | SHORT RURAL |  | 80 | 375 | 30000 | 0.26106 | 0.00069616 | 0
2013-07-14 08:40 | HPK13 | URBAN |  | 11 | 99 | 1089 | 0.0037935 | 3.8318e-05 | 0
2013-07-14 09:15 | BRA21 | URBAN |  | 465 | 393.7527 | 183095 | 0.63781 | 0.0016198 | 0
2013-07-15 09:20 | HPK13 | URBAN |  | 235 | 180 | 42300 | 0.14735 | 0.00081862 | 0
2013-07-15 09:50 | BGE22 | SHORT RURAL |  | 54 | 150 | 8100 | 0.070486 | 0.00046991 | 0
2013-07-15 09:50 | NRN14 | URBAN |  | 86 | 230 | 19780 | 0.068903 | 0.00029958 | 0
2013-07-11 09:30 | PHM33 | SHORT RURAL |  | 43 | 465 | 19995 | 0.174 | 0.00037418 | 0
2013-07-15 09:55 | LLG13 | SHORT RURAL |  | 13 | 252 | 3276 | 0.028508 | 0.00011313 | 0
2013-07-16 08:30 | DRN12 | URBAN |  | 26 | 464.4231 | 12075 | 0.042063 | 9.0571e-05 | 0
2013-07-09 08:40 | BRA24 | URBAN |  | 1086 | 286 | 310596 | 1.082 | 0.0037831 | 0
2013-07-16 08:47 | BDL6 | SHORT RURAL |  | 1207 | 352.0149 | 424882 | 3.6973 | 0.010503 | 0
2013-07-16 09:25 | MFA31 | SHORT RURAL |  | 253 | 385 | 97405 | 0.84762 | 0.0022016 | 0
2013-07-15 08:45 | BN6 | LONG RURAL |  | 33 | 459 | 15147 | 0.058654 | 0.00012779 | 0
2013-07-10 09:45 | WN3 | LONG RURAL |  | 1 | 290 | 290 | 0.001123 | 3.8723e-06 | 0
2013-07-11 09:17 | KLK1 | SHORT RURAL |  | 75 | 83 | 6225 | 0.05417 | 0.00065265 | 0
2013-07-16 11:30 | BN6 | LONG RURAL |  | 1 | 170 | 170 | 0.00065829 | 3.8723e-06 | 0
2013-07-17 09:05 | BN6 | LONG RURAL |  | 10 | 170 | 1700 | 0.0065829 | 3.8723e-05 | 0
2013-07-11 09:45 | BWR32 | URBAN |  | 128 | 365 | 46720 | 0.16275 | 0.00044589 | 0
2013-07-16 09:25 | RWT11 | URBAN |  | 87 | 220 | 19140 | 0.066674 | 0.00030306 | 0
2013-07-03 09:43 | FTR12 | LONG RURAL |  | 150 | 235 | 35250 | 0.1365 | 0.00058085 | 0
2013-07-03 09:03 | LGA12 | SHORT RURAL |  | 449 | 346 | 155354 | 1.3519 | 0.0039072 | 0
2013-07-03 08:05 | TGN31 | LONG RURAL |  | 560 | 75.2429 | 42136 | 0.16316 | 0.0021685 | 0
2013-07-19 09:02 | BWA22 | LONG RURAL |  | 15 | 231 | 3465 | 0.013418 | 5.8085e-05 | 0
2013-07-18 10:30 | TGN41 | LONG RURAL |  | 41 | 100 | 4100 | 0.015876 | 0.00015876 | 0
2013-07-19 09:10 | FTR21 | LONG RURAL |  | 2 | 150 | 300 | 0.0011617 | 7.7446e-06 | 0
2013-07-18 10:38 | FTR21 | LONG RURAL |  | 1 | 50 | 50 | 0.00019362 | 3.8723e-06 | 0
2013-07-18 13:00 | FTR21 | LONG RURAL |  | 1 | 70 | 70 | 0.00027106 | 3.8723e-06 | 0
2013-07-19 09:45 | FTR21 | LONG RURAL |  | 2 | 90 | 180 | 0.00069702 | 7.7446e-06 | 0
2013-07-19 09:25 | MOE24 | SHORT RURAL |  | 177 | 305 | 53985 | 0.46978 | 0.0015402 | 0
2013-07-19 13:50 | WYK23 | SHORT RURAL |  | 101 | 108 | 10908 | 0.094921 | 0.0008789 | 0
2013-07-19 09:08 | CLN14 | SHORT RURAL |  | 162 | 177 | 28674 | 0.24952 | 0.0014097 | 0
2013-07-19 09:55 | MWTS11 | SHORT RURAL |  | 44 | 115 | 5060 | 0.044032 | 0.00038289 | 0
2013-07-20 08:30 | CRE21 | SHORT RURAL |  | 72 | 480 | 34560 | 0.30074 | 0.00062654 | 0
2013-07-11 14:00 | MYT7 | LONG RURAL |  | 2 | 35 | 70 | 0.00027106 | 7.7446e-06 | 0
2013-07-12 09:20 | MYT7 | LONG RURAL |  | 51 | 36 | 1836 | 0.0071096 | 0.00019749 | 0
2013-07-18 09:35 | WYK11 | SHORT RURAL |  | 53 | 29 | 1537 | 0.013375 | 0.0004612 | 0
2013-07-15 09:55 | MOE23 | SHORT RURAL |  | 64 | 250 | 16000 | 0.13923 | 0.00055693 | 0
2013-07-12 09:35 | RWN24 | SHORT RURAL |  | 224 | 257 | 57568 | 0.50096 | 0.0019492 | 0
2013-07-18 11:25 | WYK24 | SHORT RURAL |  | 3 | 35 | 105 | 0.00091371 | 2.6106e-05 | 0
2013-07-18 12:25 | WYK11 | SHORT RURAL |  | 8 | 15 | 120 | 0.0010442 | 6.9616e-05 | 0
2013-07-12 09:19 | FTR12 | LONG RURAL |  | 1 | 103 | 103 | 0.00039885 | 3.8723e-06 | 0
2013-07-16 10:00 | WT13 | URBAN |  | 509 | 316 | 160844 | 0.5603 | 0.0017731 | 0
2013-07-17 09:00 | BN6 | LONG RURAL |  | 37 | 350 | 12950 | 0.050146 | 0.00014328 | 0
2013-07-15 07:50 | MOE24 | SHORT RURAL |  | 23 | 375 | 8625 | 0.075054 | 0.00020015 | 0
2013-07-13 08:30 | WGL21 | LONG RURAL |  | 2 | 206 | 412 | 0.0015954 | 7.7446e-06 | 0
2013-07-16 09:10 | RWT11 | URBAN |  | 143 | 305 | 43615 | 0.15193 | 0.00049814 | 0
2013-07-16 08:30 | RWT15 | URBAN |  | 136 | 255 | 34680 | 0.12081 | 0.00047375 | 0
2013-07-17 08:50 | BN6 | LONG RURAL |  | 4 | 85 | 340 | 0.0013166 | 1.5489e-05 | 0
2013-07-17 12:30 | BN6 | LONG RURAL |  | 16 | 160 | 2560 | 0.0099131 | 6.1957e-05 | 0
2013-07-21 09:21 | MOE13 | SHORT RURAL |  | 597 | 268 | 159996 | 1.3923 | 0.0051951 | 0
2013-07-20 09:05 | MWTS31 | SHORT RURAL |  | 46 | 381 | 17526 | 0.15251 | 0.00040029 | 0
2013-07-12 09:13 | SMR5 | LONG RURAL |  | 1 | 212 | 212 | 0.00082093 | 3.8723e-06 | 0
2013-07-17 09:50 | MFA14 | URBAN |  | 26 | 200 | 5200 | 0.018114 | 9.0571e-05 | 0
2013-07-18 08:52 | SLE31 | LONG RURAL |  | 2481 | 445 | 1104045 | 4.2752 | 0.0096072 | 0
2013-07-19 08:45 | PHI12 | SHORT RURAL |  | 58 | 225 | 13050 | 0.11356 | 0.00050471 | 0
2013-07-17 08:32 | EPG12 | URBAN |  | 98 | 493 | 48314 | 0.1683 | 0.00034138 | 0
2013-07-17 10:38 | WOTS24 | LONG RURAL |  | 37 | 202 | 7474 | 0.028942 | 0.00014328 | 0
2013-07-18 09:00 | MYT7 | LONG RURAL |  | 19 | 145 | 2755 | 0.010668 | 7.3574e-05 | 0
2013-07-15 09:30 | MBY11 | SHORT RURAL |  | 1 | 70 | 70 | 0.00060914 | 8.702e-06 | 0
2013-07-18 09:00 | WN4 | SHORT RURAL |  | 113 | 150 | 16950 | 0.1475 | 0.00098332 | 0
2013-07-17 09:00 | KMS1 | SHORT RURAL |  | 322 | 359 | 115598 | 1.0059 | 0.002802 | 0
2013-07-12 09:28 | CYN13 | URBAN |  | 1 | 82 | 82 | 0.00028565 | 3.4835e-06 | 0
2013-07-15 09:40 | RWN32 | URBAN |  | 29 | 215 | 6235 | 0.02172 | 0.00010102 | 0
2013-07-18 08:39 | BN6 | LONG RURAL |  | 8 | 356 | 2848 | 0.011028 | 3.0979e-05 | 0
2013-07-19 10:55 | BN1 | LONG RURAL |  | 1 | 155 | 155 | 0.00060021 | 3.8723e-06 | 0
2013-07-11 09:10 | CYN33 | SHORT RURAL |  | 64 | 125 | 8000 | 0.069616 | 0.00055693 | 0
2013-07-22 09:05 | MOE22 | LONG RURAL |  | 61 | 355 | 21655 | 0.083855 | 0.00023621 | 0
2013-07-22 09:05 | MOE31 | LONG RURAL |  | 1 | 303 | 303 | 0.0011733 | 3.8723e-06 | 0
2013-07-22 10:10 | WGL12 | LONG RURAL |  | 46 | 315 | 14490 | 0.05611 | 0.00017813 | 0
2013-07-22 09:30 | OFR23 | LONG RURAL |  | 34 | 180 | 6120 | 0.023699 | 0.00013166 | 0
2013-07-22 09:02 | WGI24 | URBAN |  | 42 | 238 | 9996 | 0.034821 | 0.00014631 | 0
2013-07-22 08:40 | SLE31 | LONG RURAL |  | 1 | 100 | 100 | 0.00038723 | 3.8723e-06 | 0
2013-07-17 09:10 | RWN24 | SHORT RURAL |  | 20 | 2 | 40 | 0.00034808 | 0.00017404 | 0
2013-07-18 09:30 | BRA21 | URBAN |  | 103 | 105 | 10815 | 0.037674 | 0.0003588 | 0
2013-07-18 08:45 | BRA14 | URBAN |  | 366 | 183 | 66978 | 0.23332 | 0.001275 | 0
2013-07-18 09:20 | WT8 | URBAN |  | 79 | 270 | 21330 | 0.074303 | 0.0002752 | 0
2013-07-19 08:34 | BDL6 | SHORT RURAL |  | 225 | 346 | 77850 | 0.67745 | 0.0019579 | 0
2013-07-17 09:00 | CLN13 | SHORT RURAL |  | 48 | 285 | 13680 | 0.11904 | 0.00041769 | 0
2013-07-19 09:30 | WT15 | URBAN |  | 58 | 213 | 12354 | 0.043035 | 0.00020204 | 0
2013-07-09 09:02 | RWT15 | URBAN |  | 99 | 105 | 10395 | 0.036211 | 0.00034486 | 0
2013-07-19 09:25 | MOE31 | LONG RURAL |  | 28 | 430 | 12040 | 0.046623 | 0.00010842 | 0
2013-07-16 09:25 | BWR13 | SHORT RURAL |  | 98 | 415 | 40670 | 0.35391 | 0.00085279 | 0
2013-07-18 08:35 | BGE22 | SHORT RURAL |  | 70 | 253 | 17710 | 0.15411 | 0.00060914 | 0
2013-07-18 08:30 | CYN31 | URBAN |  | 1214 | 351.2916 | 426468 | 1.4856 | 0.0042289 | 0
2013-07-19 09:45 | KMS1 | SHORT RURAL |  | 9 | 245 | 2205 | 0.019188 | 7.8318e-05 | 0
2013-07-19 08:45 | RWN33 | URBAN |  | 54 | 195 | 10530 | 0.036681 | 0.00018811 | 0
2013-07-19 09:00 | RWN24 | SHORT RURAL |  | 21 | 305 | 6405 | 0.055736 | 0.00018274 | 0
2013-07-19 09:10 | BRA14 | URBAN |  | 113 | 165 | 18645 | 0.06495 | 0.00039363 | 0
2013-07-25 09:15 | BRT21 | SHORT RURAL |  | 2 | 345 | 690 | 0.0060044 | 1.7404e-05 | 0
2013-07-23 09:03 | WT12 | URBAN |  | 63 | 327 | 20601 | 0.071763 | 0.00021946 | 0
2013-07-24 09:30 | MOE31 | LONG RURAL |  | 8 | 305 | 2440 | 0.0094484 | 3.0979e-05 | 0
2013-07-23 08:46 | PHM14 | LONG RURAL |  | 444 | 378 | 167832 | 0.6499 | 0.0017193 | 0
2013-07-23 08:34 | WGI24 | URBAN |  | 5 | 64 | 320 | 0.0011147 | 1.7417e-05 | 0
2013-07-23 09:26 | TGN31 | LONG RURAL |  | 1 | 149 | 149 | 0.00057697 | 3.8723e-06 | 0
2013-07-23 11:00 | WGL11 | SHORT RURAL |  | 7 | 170 | 1190 | 0.010355 | 6.0914e-05 | 0
2013-07-23 09:15 | FTR21 | LONG RURAL |  | 2 | 60 | 120 | 0.00046468 | 7.7446e-06 | 0
2013-07-23 10:50 | FTR21 | LONG RURAL |  | 3 | 30 | 90 | 0.00034851 | 1.1617e-05 | 0
2013-07-23 14:03 | WGI24 | URBAN |  | 1 | 37 | 37 | 0.00012889 | 3.4835e-06 | 0
2013-07-25 09:15 | MOE22 | LONG RURAL |  | 14 | 335 | 4690 | 0.018161 | 5.4212e-05 | 0
2013-07-24 09:00 | FTR21 | LONG RURAL |  | 88 | 261 | 22968 | 0.088939 | 0.00034076 | 0
2013-07-23 09:20 | TGN12 | SHORT RURAL |  | 2 | 10 | 20 | 0.00017404 | 1.7404e-05 | 0
2013-07-23 09:00 | MOE13 | SHORT RURAL |  | 42 | 275 | 11550 | 0.10051 | 0.00036548 | 0
2013-07-23 09:10 | MOE13 | SHORT RURAL |  | 64 | 60 | 3840 | 0.033416 | 0.00055693 | 0
2013-07-23 12:00 | MOE13 | SHORT RURAL |  | 42 | 75 | 3150 | 0.027411 | 0.00036548 | 0
2013-07-23 14:00 | WGI24 | URBAN |  | 33 | 19 | 627 | 0.0021841 | 0.00011495 | 0
2013-07-25 09:15 | TGN11 | SHORT RURAL |  | 8 | 124 | 992 | 0.0086324 | 6.9616e-05 | 0
2013-07-24 09:09 | WGI24 | URBAN |  | 104 | 19 | 1976 | 0.0068834 | 0.00036228 | 0
2013-07-23 10:30 | LDL13 | SHORT RURAL |  | 24 | 305 | 7320 | 0.063698 | 0.00020885 | 0
2013-07-24 09:05 | WGI34 | SHORT RURAL |  | 2 | 82 | 164 | 0.0014271 | 1.7404e-05 | 0
2013-07-24 09:00 | FTR23 | LONG RURAL |  | 35 | 230 | 8050 | 0.031172 | 0.00013553 | 0
2013-07-24 09:06 | TGN31 | LONG RURAL |  | 32 | 154 | 4928 | 0.019083 | 0.00012391 | 0
2013-07-24 09:05 | FTR12 | LONG RURAL |  | 13 | 310 | 4030 | 0.015605 | 5.034e-05 | 0
2013-07-25 09:15 | FTR21 | LONG RURAL |  | 2 | 48 | 96 | 0.00037174 | 7.7446e-06 | 0
2013-07-23 09:05 | FTR21 | LONG RURAL |  | 20 | 265 | 5300 | 0.020523 | 7.7446e-05 | 0
2013-07-24 11:24 | WO32 | URBAN |  | 89 | 74.0337 | 6589 | 0.022953 | 0.00031003 | 0
2013-07-25 09:20 | TGN41 | LONG RURAL |  | 5 | 137 | 685 | 0.0026525 | 1.9362e-05 | 0
2013-07-25 09:08 | WGI22 | LONG RURAL |  | 2 | 192 | 384 | 0.001487 | 7.7446e-06 | 0
2013-07-25 09:06 | LGA22 | SHORT RURAL |  | 138 | 264 | 36432 | 0.31703 | 0.0012009 | 0
2013-07-25 09:06 | LGA21 | SHORT RURAL |  | 14 | 292 | 4088 | 0.035574 | 0.00012183 | 0
2013-07-25 09:45 | FTR23 | LONG RURAL |  | 62 | 90 | 5580 | 0.021608 | 0.00024008 | 0
2013-07-24 09:20 | BN1 | LONG RURAL |  | 77 | 420 | 32340 | 0.12523 | 0.00029817 | 0
2013-07-24 09:13 | WN6 | LONG RURAL |  | 2 | 199 | 398 | 0.0015412 | 7.7446e-06 | 0
2013-07-24 07:55 | ELM34 | URBAN |  | 194 | 530 | 102820 | 0.35817 | 0.0006758 | 0
2013-07-24 09:07 | MWTS21 | URBAN |  | 99 | 144 | 14256 | 0.049661 | 0.00034486 | 0
2013-07-17 09:20 | WT5 | URBAN |  | 71 | 155 | 11005 | 0.038336 | 0.00024733 | 0
2013-07-17 08:46 | DRN11 | URBAN |  | 12 | 454 | 5448 | 0.018978 | 4.1802e-05 | 0
2013-07-17 09:25 | DRN12 | URBAN |  | 64 | 355 | 22720 | 0.079145 | 0.00022294 | 0
2013-07-22 10:00 | WT12 | URBAN |  | 94 | 175 | 16450 | 0.057303 | 0.00032745 | 0
2013-07-24 08:50 | LDL11 | URBAN |  | 168 | 120 | 20160 | 0.070227 | 0.00058523 | 0
2013-07-22 11:00 | SLE31 | LONG RURAL |  | 2 | 30 | 60 | 0.00023234 | 7.7446e-06 | 0
2013-07-22 10:20 | KMS1 | SHORT RURAL |  | 2 | 350 | 700 | 0.0060914 | 1.7404e-05 | 0
2013-07-24 08:30 | SLE32 | SHORT RURAL |  | 89 | 225 | 20025 | 0.17426 | 0.00077448 | 0
2013-07-23 10:35 | BDL4 | SHORT RURAL |  | 51 | 15 | 765 | 0.006657 | 0.0004438 | 0
2013-07-24 08:40 | SLE31 | LONG RURAL |  | 10 | 320 | 3200 | 0.012391 | 3.8723e-05 | 0
2013-07-24 08:55 | SLE32 | SHORT RURAL |  | 64 | 231 | 14784 | 0.12865 | 0.00055693 | 0
2013-07-23 08:45 | BDL2 | SHORT RURAL |  | 69 | 229 | 15801 | 0.1375 | 0.00060044 | 0
2013-07-25 09:00 | TGN12 | SHORT RURAL |  | 31 | 180 | 5580 | 0.048557 | 0.00026976 | 0
2013-07-15 10:00 | RWN33 | URBAN |  | 75 | 210 | 15750 | 0.054865 | 0.00026126 | 0
2013-07-20 08:25 | BRA12 | URBAN |  | 10 | 1835 | 18350 | 0.063922 | 3.4835e-05 | 0
2013-07-23 09:00 | BN4 | URBAN |  | 114 | 343 | 39102 | 0.13621 | 0.00039712 | 0
2013-07-21 09:10 | BRA14 | URBAN |  | 146 | 349 | 50954 | 0.1775 | 0.00050859 | 0
2013-07-21 08:30 | RWN26 | SHORT RURAL |  | 85 | 420 | 35700 | 0.31066 | 0.00073967 | 0
2013-07-21 10:30 | BRA23 | URBAN |  | 26 | 50 | 1300 | 0.0045285 | 9.0571e-05 | 0
2013-07-26 09:05 | MOE31 | LONG RURAL |  | 48 | 202 | 9696 | 0.037546 | 0.00018587 | 0
2013-07-26 10:00 | LYD14 | SHORT RURAL |  | 2 | 120 | 240 | 0.0020885 | 1.7404e-05 | 0
2013-07-25 13:10 | FTR21 | LONG RURAL |  | 1 | 30 | 30 | 0.00011617 | 3.8723e-06 | 0
2013-07-25 11:20 | FTR21 | LONG RURAL |  | 2 | 22 | 44 | 0.00017038 | 7.7446e-06 | 0
2013-07-26 09:00 | MOE32 | SHORT RURAL |  | 119 | 370 | 44030 | 0.38315 | 0.0010355 | 0
2013-07-26 08:45 | MOE31 | LONG RURAL |  | 1 | 190 | 190 | 0.00073574 | 3.8723e-06 | 0
2013-07-26 10:25 | MBY12 | SHORT RURAL |  | 42 | 140 | 5880 | 0.051168 | 0.00036548 | 0
2013-07-26 08:20 | KLK2 | SHORT RURAL |  | 9 | 182 | 1638 | 0.014254 | 7.8318e-05 | 0
2013-07-25 09:11 | BN1 | LONG RURAL |  | 35 | 239 | 8365 | 0.032392 | 0.00013553 | 0
2013-07-23 09:30 | SLE24 | URBAN |  | 17 | 137 | 2329 | 0.008113 | 5.9219e-05 | 0
2013-07-24 09:08 | BDL5 | LONG RURAL |  | 139 | 166 | 23074 | 0.08935 | 0.00053825 | 0
2013-07-21 08:50 | WT8 | URBAN |  | 66 | 230 | 15180 | 0.052879 | 0.00022991 | 0
2013-07-25 09:05 | BN1 | LONG RURAL |  | 23 | 380 | 8740 | 0.033844 | 8.9063e-05 | 0
2013-07-22 09:00 | KMS1 | SHORT RURAL |  | 9 | 180 | 1620 | 0.014097 | 7.8318e-05 | 0
2013-07-18 08:30 | LDL23 | LONG RURAL |  | 7 | 142 | 994 | 0.0038491 | 2.7106e-05 | 0
2013-07-22 09:08 | KMS1 | SHORT RURAL |  | 3 | 317 | 951 | 0.0082756 | 2.6106e-05 | 0
2013-07-22 09:10 | BRA14 | URBAN |  | 150 | 115 | 17250 | 0.06009 | 0.00052252 | 0
2013-07-27 09:00 | FTR12 | LONG RURAL |  | 245 | 237 | 58065 | 0.22485 | 0.00094872 | 0
2013-07-27 09:00 | WGI22 | LONG RURAL |  | 110 | 347 | 38170 | 0.14781 | 0.00042595 | 0
2013-07-23 09:00 | SLE31 | LONG RURAL |  | 56 | 210 | 11760 | 0.045538 | 0.00021685 | 0
2013-07-23 09:00 | MYT7 | LONG RURAL |  | 49 | 105 | 5145 | 0.019923 | 0.00018974 | 0
2013-07-28 13:37 | BRA11 | URBAN |  | 1 | 28 | 28 | 9.7538e-05 | 3.4835e-06 | 0
2013-07-26 09:15 | SLE24 | URBAN |  | 1 | 60 | 60 | 0.00020901 | 3.4835e-06 | 0
2013-07-24 09:45 | RWN26 | SHORT RURAL |  | 28 | 317 | 8876 | 0.077239 | 0.00024366 | 0
2013-07-22 10:15 | WN5 | LONG RURAL |  | 11 | 298 | 3278 | 0.012693 | 4.2595e-05 | 0
2013-07-26 08:30 | BDL5 | LONG RURAL |  | 137 | 300 | 41100 | 0.15915 | 0.00053051 | 0
2013-07-26 08:30 | SLE32 | SHORT RURAL |  | 6 | 145 | 870 | 0.0075707 | 5.2212e-05 | 0
2013-07-26 10:40 | BDL5 | LONG RURAL |  | 103 | 12 | 1236 | 0.0047862 | 0.00039885 | 0
2013-07-26 11:10 | SLE31 | LONG RURAL |  | 1 | 50 | 50 | 0.00019362 | 3.8723e-06 | 0
2013-07-25 08:55 | WN5 | LONG RURAL |  | 1 | 140 | 140 | 0.00054212 | 3.8723e-06 | 0
2013-07-25 09:25 | MSD1 | LONG RURAL |  | 1 | 81 | 81 | 0.00031366 | 3.8723e-06 | 0
2013-07-25 09:30 | BN1 | LONG RURAL |  | 40 | 350 | 14000 | 0.054212 | 0.00015489 | 0
2013-07-22 14:40 | DRN12 | URBAN |  | 49 | 42 | 2058 | 0.007169 | 0.00017069 | 0
2013-07-22 09:00 | BN2 | LONG RURAL |  | 2 | 125 | 250 | 0.00096808 | 7.7446e-06 | 0
2013-07-26 09:14 | MSD2 | LONG RURAL |  | 29 | 388 | 11252 | 0.043571 | 0.0001123 | 0
2013-07-26 08:40 | BN1 | LONG RURAL |  | 2 | 165 | 330 | 0.0012779 | 7.7446e-06 | 0
2013-07-22 09:07 | DRN12 | URBAN |  | 735 | 209 | 153615 | 0.53512 | 0.0025604 | 0
2013-07-28 08:30 | RWT22 | URBAN |  | 288 | 345 | 99360 | 0.34612 | 0.0010032 | 0
2013-07-23 12:10 | DRN21 | URBAN |  | 14 | 380 | 5320 | 0.018532 | 4.8769e-05 | 0
2013-07-23 10:30 | TT9 | URBAN |  | 93 | 325 | 30225 | 0.10529 | 0.00032396 | 0
2013-07-23 13:50 | ELM32 | URBAN |  | 66 | 130 | 8580 | 0.029888 | 0.00022991 | 0
2013-07-25 08:30 | BWA23 | SHORT RURAL |  | 17 | 210 | 3570 | 0.031066 | 0.00014793 | 0
2013-07-26 08:40 | MFA31 | SHORT RURAL |  | 25 | 155 | 3875 | 0.03372 | 0.00021755 | 0
2013-07-24 10:20 | DRN11 | URBAN |  | 16 | 376 | 6016 | 0.020957 | 5.5736e-05 | 0
2013-07-23 08:03 | RWT15 | URBAN |  | 192 | 432 | 82944 | 0.28893 | 0.00066883 | 0
2013-07-23 09:35 | DRN11 | URBAN |  | 68 | 165 | 11220 | 0.039085 | 0.00023688 | 0
2013-07-23 09:35 | DRN13 | SHORT RURAL |  | 42 | 165 | 6930 | 0.060305 | 0.00036548 | 0
2013-07-23 10:35 | BRA11 | URBAN |  | 106 | 385 | 40810 | 0.14216 | 0.00036925 | 0
2013-07-23 10:35 | BRA32 | URBAN |  | 58 | 385 | 22330 | 0.077786 | 0.00020204 | 0
2013-07-23 09:00 | RWT11 | URBAN |  | 170 | 352 | 59840 | 0.20845 | 0.00059219 | 0
2013-07-25 09:20 | LGA23 | LONG RURAL |  | 13 | 265 | 3445 | 0.01334 | 5.034e-05 | 0
2013-07-24 09:00 | WT10 | URBAN |  | 78 | 190 | 14820 | 0.051625 | 0.00027171 | 0
2013-07-25 08:30 | DRN12 | URBAN |  | 8 | 345 | 2760 | 0.0096144 | 2.7868e-05 | 0
2013-07-25 10:50 | WT10 | URBAN |  | 405 | 305 | 123525 | 0.4303 | 0.0014108 | 0
2013-07-25 09:30 | ELM32 | URBAN |  | 37 | 265 | 9805 | 0.034156 | 0.00012889 | 0
2013-07-28 09:00 | TGN11 | SHORT RURAL |  | 1 | 400 | 400 | 0.0034808 | 8.702e-06 | 0
2013-07-25 09:00 | RWN26 | SHORT RURAL |  | 67 | 300 | 20100 | 0.17491 | 0.00058303 | 0
2013-07-26 10:25 | WT11 | URBAN |  | 96 | 75 | 7200 | 0.025081 | 0.00033441 | 0
2013-07-21 09:02 | CYN13 | URBAN |  | 116 | 233 | 27028 | 0.094152 | 0.00040408 | 0
2013-07-25 09:06 | KMS1 | SHORT RURAL |  | 5 | 284 | 1420 | 0.012357 | 4.351e-05 | 0
2013-07-22 05:00 | CYN32 | URBAN |  | 51 | 160 | 8160 | 0.028425 | 0.00017766 | 0
2013-07-25 09:30 | KMS1 | SHORT RURAL |  | 35 | 212 | 7420 | 0.064569 | 0.00030457 | 0
2013-07-22 10:32 | CYN14 | URBAN |  | 30 | 498 | 14940 | 0.052043 | 0.0001045 | 0
2013-07-19 09:30 | BGE22 | SHORT RURAL |  | 71 | 290 | 20590 | 0.17917 | 0.00061784 | 0
2013-07-24 09:25 | RWN24 | SHORT RURAL |  | 278 | 345 | 95910 | 0.83461 | 0.0024191 | 0
2013-07-18 09:10 | SMR1 | SHORT RURAL |  | 21 | 140 | 2940 | 0.025584 | 0.00018274 | 0
2013-07-19 09:00 | OFR23 | LONG RURAL |  | 55 | 280 | 15400 | 0.059634 | 0.00021298 | 0
2013-07-19 12:20 | HPK14 | URBAN |  | 3 | 35 | 105 | 0.00036577 | 1.045e-05 | 0
2013-07-21 08:30 | LYD14 | SHORT RURAL |  | 452 | 99 | 44748 | 0.3894 | 0.0039333 | 0
2013-07-21 11:30 | LYD11 | SHORT RURAL |  | 123 | 99 | 12177 | 0.10596 | 0.0010703 | 0
2013-07-25 09:30 | BWR24 | URBAN |  | 25 | 245 | 6125 | 0.021336 | 8.7087e-05 | 0
2013-07-21 09:00 | FGY22 | URBAN |  | 128 | 228 | 29184 | 0.10166 | 0.00044589 | 0
2013-07-21 11:45 | FGY31 | URBAN |  | 6 | 105 | 630 | 0.0021946 | 2.0901e-05 | 0
2013-07-29 09:45 | WGI14 | SHORT RURAL |  | 2 | 280 | 560 | 0.0048731 | 1.7404e-05 | 0
2013-07-29 09:00 | WO31 | URBAN |  | 30 | 210 | 6300 | 0.021946 | 0.0001045 | 0
2013-07-29 08:04 | RWT15 | URBAN |  | 987 | 65 | 64155 | 0.22348 | 0.0034382 | 0
2013-07-29 12:00 | LDL13 | SHORT RURAL |  | 74 | 130 | 9620 | 0.083713 | 0.00064395 | 0
2013-07-29 09:06 | KMS1 | SHORT RURAL |  | 6 | 369 | 2214 | 0.019266 | 5.2212e-05 | 0
2013-07-23 08:40 | WT8 | URBAN |  | 91 | 185 | 16835 | 0.058644 | 0.000317 | 0
2013-07-29 10:30 | BDL5 | LONG RURAL |  | 3 | 225 | 675 | 0.0026138 | 1.1617e-05 | 0
2013-07-25 12:20 | RWT22 | URBAN |  | 140 | 180 | 25200 | 0.087784 | 0.00048769 | 0
2013-07-26 09:30 | RWN26 | SHORT RURAL |  | 60 | 113 | 6780 | 0.058999 | 0.00052212 | 0
2013-07-19 09:30 | EPG31 | URBAN |  | 78 | 330 | 25740 | 0.089665 | 0.00027171 | 0
2013-07-13 12:05 | WGI22 | LONG RURAL |  | 64 | 185 | 11840 | 0.045848 | 0.00024783 | 0
2013-07-17 09:00 | BWR23 | URBAN |  | 80 | 330 | 26400 | 0.091964 | 0.00027868 | 0
2013-07-16 08:18 | RWT15 | URBAN |  | 344 | 502 | 172688 | 0.60156 | 0.0011983 | 0
2013-08-01 09:45 | ELM33 | SHORT RURAL |  | 473 | 340 | 160820 | 1.3995 | 0.004116 | 0
2013-07-30 09:25 | WGL21 | LONG RURAL |  | 27 | 349 | 9423 | 0.036489 | 0.00010455 | 0
2013-08-01 08:55 | BWA22 | LONG RURAL |  | 681 | 1 | 681 | 0.002637 | 0.002637 | 0
2013-08-01 15:22 | BWA22 | LONG RURAL |  | 681 | 1 | 681 | 0.002637 | 0.002637 | 0
2013-07-30 08:20 | LDL23 | LONG RURAL |  | 37 | 355 | 13135 | 0.050863 | 0.00014328 | 0
2013-07-30 12:02 | LDL23 | LONG RURAL |  | 3 | 143 | 429 | 0.0016612 | 1.1617e-05 | 0
2013-07-30 10:20 | LDL23 | LONG RURAL |  | 2 | 55 | 110 | 0.00042595 | 7.7446e-06 | 0
2013-07-30 09:30 | LDL22 | SHORT RURAL |  | 35 | 360 | 12600 | 0.10964 | 0.00030457 | 0
2013-07-31 09:05 | TGN12 | SHORT RURAL |  | 112 | 415 | 46480 | 0.40447 | 0.00097462 | 0
2013-08-01 09:00 | WGL21 | LONG RURAL |  | 4 | 120 | 480 | 0.0018587 | 1.5489e-05 | 0
2013-07-31 09:00 | TGN41 | LONG RURAL |  | 30 | 280 | 8400 | 0.032527 | 0.00011617 | 0
2013-07-31 08:13 | LYS36 | SHORT RURAL |  | 1 | 524 | 524 | 0.0045598 | 8.702e-06 | 0
2013-07-31 09:15 | LDL24 | URBAN |  | 50 | 120 | 6000 | 0.020901 | 0.00017417 | 0
2013-07-30 08:31 | BN6 | LONG RURAL |  | 407 | 378 | 153846 | 0.59574 | 0.001576 | 0
2013-07-30 11:00 | YN35 | URBAN |  | 2 | 84 | 168 | 0.00058523 | 6.967e-06 | 0
2013-08-01 10:00 | FTR23 | LONG RURAL |  | 122 | 385 | 46970 | 0.18188 | 0.00047242 | 0
2013-07-31 09:25 | MOE23 | SHORT RURAL |  | 160 | 94 | 15040 | 0.13088 | 0.0013923 | 0
2013-07-31 09:30 | MOE24 | SHORT RURAL |  | 9 | 79 | 711 | 0.0061871 | 7.8318e-05 | 0
2013-07-31 09:20 | WOTS11 | LONG RURAL |  | 2 | 180 | 360 | 0.001394 | 7.7446e-06 | 0
2013-07-31 09:00 | LGA23 | LONG RURAL |  | 70 | 225 | 15750 | 0.060989 | 0.00027106 | 0
2013-07-30 09:40 | MOE32 | SHORT RURAL |  | 119 | 290 | 34510 | 0.30031 | 0.0010355 | 0
2013-07-30 09:25 | KMS1 | SHORT RURAL |  | 3 | 325 | 975 | 0.0084844 | 2.6106e-05 | 0
2013-07-31 09:00 | TGN31 | LONG RURAL |  | 90 | 375 | 33750 | 0.13069 | 0.00034851 | 0
2013-07-31 09:00 | TGN31 | LONG RURAL |  | 44 | 375 | 16500 | 0.063893 | 0.00017038 | 0
2013-08-01 10:30 | BGE22 | SHORT RURAL |  | 4 | 190 | 760 | 0.0066135 | 3.4808e-05 | 0
2013-07-23 08:35 | FGY14 | URBAN |  | 64 | 310 | 19840 | 0.069112 | 0.00022294 | 0
2013-07-23 08:40 | FGY14 | URBAN |  | 60 | 240 | 14400 | 0.050162 | 0.00020901 | 0
2013-07-24 09:12 | CRE22 | URBAN |  | 185 | 338 | 62530 | 0.21782 | 0.00064444 | 0
2013-07-24 08:35 | BGE22 | SHORT RURAL |  | 182 | 405 | 73710 | 0.64142 | 0.0015838 | 0
2013-07-24 09:10 | CRE32 | URBAN |  | 154 | 210 | 32340 | 0.11266 | 0.00053646 | 0
2013-07-25 09:20 | FGY23 | URBAN |  | 70 | 130 | 9100 | 0.0317 | 0.00024384 | 0
2013-07-25 13:20 | FGY13 | SHORT RURAL |  | 120 | 125 | 15000 | 0.13053 | 0.0010442 | 0
2013-07-25 09:00 | LLG14 | SHORT RURAL |  | 65 | 341 | 22165 | 0.19288 | 0.00056563 | 0
2013-07-25 09:25 | BGE12 | SHORT RURAL |  | 104 | 410 | 42640 | 0.37105 | 0.000905 | 0
2013-07-25 09:00 | OFR23 | LONG RURAL |  | 12 | 310 | 3720 | 0.014405 | 4.6468e-05 | 0
2013-07-25 09:50 | BGE22 | SHORT RURAL |  | 15 | 425 | 6375 | 0.055475 | 0.00013053 | 0
2013-07-25 17:37 | ELM34 | URBAN |  | 7 | 5 | 35 | 0.00012192 | 2.4384e-05 | 0
2013-07-26 09:45 | LLG11 | SHORT RURAL |  | 2 | 64 | 128 | 0.0011139 | 1.7404e-05 | 0
2013-07-26 08:56 | CLN23 | SHORT RURAL |  | 1 | 99 | 99 | 0.0008615 | 8.702e-06 | 0
2013-07-26 13:00 | HPK21 | URBAN |  | 293 | 150 | 43950 | 0.1531 | 0.0010207 | 0
2013-08-01 09:25 | LDL22 | SHORT RURAL |  | 3 | 85 | 255 | 0.002219 | 2.6106e-05 | 0
2013-07-29 09:10 | BDL5 | LONG RURAL |  | 2 | 45 | 90 | 0.00034851 | 7.7446e-06 | 0
2013-07-30 08:34 | SLE31 | LONG RURAL |  | 98 | 383.9286 | 37625 | 0.1457 | 0.00037949 | 0
2013-07-30 08:45 | SLE31 | LONG RURAL |  | 48 | 342 | 16416 | 0.063568 | 0.00018587 | 0
2013-07-26 11:40 | WT7 | URBAN |  | 77 | 135 | 10395 | 0.036211 | 0.00026823 | 0
2013-07-30 08:50 | BDL6 | SHORT RURAL |  | 879 | 20 | 17580 | 0.15298 | 0.007649 | 0
2013-07-31 09:30 | BN1 | LONG RURAL |  | 2 | 172 | 344 | 0.0013321 | 7.7446e-06 | 0
2013-07-31 08:30 | BDL1 | LONG RURAL |  | 7 | 390 | 2730 | 0.010571 | 2.7106e-05 | 0
2013-07-26 11:20 | LLG11 | SHORT RURAL |  | 1 | 55 | 55 | 0.00047861 | 8.702e-06 | 0
2013-07-26 12:45 | LYD11 | SHORT RURAL |  | 233 | 30 | 6990 | 0.060827 | 0.0020276 | 0
2013-07-25 09:30 | BWR13 | SHORT RURAL |  | 267 | 310 | 82770 | 0.72026 | 0.0023234 | 0
2013-08-02 09:31 | PHI12 | SHORT RURAL |  | 132 | 473 | 62436 | 0.54332 | 0.0011487 | 0
2013-08-01 09:17 | BWA22 | LONG RURAL |  | 97 | 352 | 34144 | 0.13222 | 0.00037561 | 0
2013-08-02 09:00 | LGA11 | LONG RURAL |  | 34 | 170 | 5780 | 0.022382 | 0.00013166 | 0
2013-08-02 09:06 | LGA12 | SHORT RURAL |  | 103 | 254 | 26162 | 0.22766 | 0.0008963 | 0
2013-08-02 09:15 | WGL21 | LONG RURAL |  | 2 | 135 | 270 | 0.0010455 | 7.7446e-06 | 0
2013-08-01 12:20 | LDL22 | SHORT RURAL |  | 6 | 80 | 480 | 0.0041769 | 5.2212e-05 | 0
2013-08-02 09:00 | MYT2 | SHORT RURAL |  | 3 | 170 | 510 | 0.004438 | 2.6106e-05 | 0
2013-08-02 09:06 | FTR23 | LONG RURAL |  | 55 | 296 | 16280 | 0.063041 | 0.00021298 | 0
2013-08-02 09:20 | MBY11 | SHORT RURAL |  | 16 | 370 | 5920 | 0.051516 | 0.00013923 | 0
2013-07-26 09:20 | RWN24 | SHORT RURAL |  | 5 | 150 | 750 | 0.0065265 | 4.351e-05 | 0
2013-07-28 09:00 | BWR34 | URBAN |  | 54 | 120 | 6480 | 0.022573 | 0.00018811 | 0
2013-08-02 09:00 | TGN31 | LONG RURAL |  | 85 | 355 | 30175 | 0.11685 | 0.00032915 | 0
2013-07-29 09:15 | WN5 | LONG RURAL |  | 66 | 339 | 22374 | 0.086639 | 0.00025557 | 0
2013-07-29 09:25 | TT6 | URBAN |  | 90 | 220 | 19800 | 0.068973 | 0.00031351 | 0
2013-08-01 09:04 | FTR12 | LONG RURAL |  | 243 | 380 | 92340 | 0.35757 | 0.00094097 | 0
2013-07-29 09:05 | WT11 | URBAN |  | 120 | 270 | 32400 | 0.11286 | 0.00041802 | 0
2013-07-31 10:15 | KLO24 | SHORT RURAL |  | 241 | 355 | 85555 | 0.7445 | 0.0020972 | 0
2013-08-01 09:20 | BDL5 | LONG RURAL |  | 71 | 342 | 24282 | 0.094028 | 0.00027493 | 0
2013-07-28 08:42 | BWR12 | URBAN |  | 167 | 197 | 32899 | 0.1146 | 0.00058174 | 0
2013-07-31 09:22 | KMS1 | SHORT RURAL |  | 4 | 343 | 1372 | 0.011939 | 3.4808e-05 | 0
2013-07-30 10:45 | BN1 | LONG RURAL |  | 2 | 230 | 460 | 0.0017813 | 7.7446e-06 | 0
2013-07-28 08:30 | NRN12 | URBAN |  | 289 | 335 | 96815 | 0.33725 | 0.0010067 | 0
2013-07-26 09:00 | RWN33 | URBAN |  | 116 | 70 | 8120 | 0.028286 | 0.00040408 | 0
2013-07-24 13:30 | MBY11 | SHORT RURAL |  | 17 | 10 | 170 | 0.0014793 | 0.00014793 | 0
2013-07-29 09:35 | BGE22 | SHORT RURAL |  | 13 | 105 | 1365 | 0.011878 | 0.00011313 | 0
2013-08-01 09:00 | MFA31 | SHORT RURAL |  | 504 | 375 | 189000 | 1.6447 | 0.0043858 | 0
2013-08-02 08:50 | BDL2 | SHORT RURAL |  | 39 | 340 | 13260 | 0.11539 | 0.00033938 | 0
2013-07-30 10:00 | ELM12 | SHORT RURAL |  | 97 | 300 | 29100 | 0.25323 | 0.00084409 | 0
2013-07-31 08:40 | ALA01 | LONG RURAL |  | 16 | 93 | 1488 | 0.005762 | 6.1957e-05 | 0
2013-08-02 09:00 | BDL2 | SHORT RURAL |  | 22 | 170 | 3740 | 0.032545 | 0.00019144 | 0
2013-08-02 09:20 | BDL2 | SHORT RURAL |  | 79 | 265 | 20935 | 0.18218 | 0.00068746 | 0
2013-07-31 09:13 | BN1 | LONG RURAL |  | 464 | 212 | 98368 | 0.38091 | 0.0017968 | 0
2013-07-29 10:00 | BWR13 | SHORT RURAL |  | 46 | 59 | 2714 | 0.023617 | 0.00040029 | 0
2013-07-31 08:40 | SMR3 | LONG RURAL |  | 1 | 220 | 220 | 0.00085191 | 3.8723e-06 | 0
2013-07-31 09:40 | DRN12 | URBAN |  | 57 | 1097.5789 | 62562 | 0.21793 | 0.00019856 | 0
2013-07-28 09:17 | TT1 | URBAN |  | 33 | 191 | 6303 | 0.021956 | 0.00011495 | 0
2013-07-28 11:35 | BWR33 | URBAN |  | 56 | 15 | 840 | 0.0029261 | 0.00019508 | 0
2013-08-02 09:00 | WGL23 | SHORT RURAL |  | 72 | 325 | 23400 | 0.20363 | 0.00062654 | 0
2013-08-01 09:05 | BN1 | LONG RURAL |  | 4 | 75 | 300 | 0.0011617 | 1.5489e-05 | 0
2013-08-01 09:15 | BN1 | LONG RURAL |  | 2 | 35 | 70 | 0.00027106 | 7.7446e-06 | 0
2013-07-26 09:30 | BWR34 | URBAN |  | 124 | 435 | 53940 | 0.1879 | 0.00043195 | 0
2013-08-02 09:00 | BN1 | LONG RURAL |  | 95 | 147.8105 | 14042 | 0.054375 | 0.00036787 | 0
2013-07-26 10:25 | CYN13 | URBAN |  | 51 | 95 | 4845 | 0.016877 | 0.00017766 | 0
2013-07-19 09:45 | FTR23 | LONG RURAL |  | 1 | 205 | 205 | 0.00079382 | 3.8723e-06 | 0
2013-08-04 10:15 | WO14 | URBAN |  | 61 | 105 | 6405 | 0.022312 | 0.00021249 | 0
2013-07-25 11:47 | ELM33 | SHORT RURAL |  | 231 | 208 | 48048 | 0.41811 | 0.0020102 | 0
2013-07-25 08:50 | DRN12 | URBAN |  | 94 | 160 | 15040 | 0.052392 | 0.00032745 | 0
2013-08-03 10:30 | MYT7 | LONG RURAL |  | 51 | 160 | 8160 | 0.031598 | 0.00019749 | 0
2013-08-01 08:40 | SMR3 | LONG RURAL |  | 1 | 115 | 115 | 0.00044532 | 3.8723e-06 | 0
2013-08-03 09:00 | MFA23 | SHORT RURAL |  | 939 | 425.1321 | 399199 | 3.4738 | 0.0081712 | 0
2013-08-04 08:30 | MFA21 | LONG RURAL |  | 311 | 426 | 132486 | 0.51303 | 0.0012043 | 0
2013-07-27 08:50 | BWR12 | URBAN |  | 104 | 410 | 42640 | 0.14854 | 0.00036228 | 0
2013-07-29 08:50 | BGE12 | SHORT RURAL |  | 133 | 220 | 29260 | 0.25462 | 0.0011574 | 0
2013-07-30 08:30 | FGY23 | URBAN |  | 192 | 270 | 51840 | 0.18058 | 0.00066883 | 0
2013-07-31 09:42 | ELM12 | SHORT RURAL |  | 49 | 363 | 17787 | 0.15478 | 0.0004264 | 0
2013-08-01 09:20 | KMS1 | SHORT RURAL |  | 2 | 280 | 560 | 0.0048731 | 1.7404e-05 | 0
2013-07-28 07:22 | TT1 | URBAN |  | 2 | 355 | 710 | 0.0024733 | 6.967e-06 | 0
2013-08-01 09:25 | TGN11 | SHORT RURAL |  | 2 | 155 | 310 | 0.0026976 | 1.7404e-05 | 0
2013-08-01 13:10 | KMS1 | SHORT RURAL |  | 7 | 95 | 665 | 0.0057868 | 6.0914e-05 | 0
2013-08-02 11:07 | KMS1 | SHORT RURAL |  | 4 | 108 | 432 | 0.0037593 | 3.4808e-05 | 0
2013-08-02 10:55 | KMS1 | SHORT RURAL |  | 1 | 70 | 70 | 0.00060914 | 8.702e-06 | 0
2013-07-30 08:35 | OFR23 | LONG RURAL |  | 181 | 441 | 79821 | 0.30909 | 0.00070089 | 0
2013-08-01 13:10 | KMS1 | SHORT RURAL |  | 2 | 95 | 190 | 0.0016534 | 1.7404e-05 | 0
2013-08-02 09:10 | WN5 | LONG RURAL |  | 65 | 237 | 15405 | 0.059653 | 0.0002517 | 0
2013-08-02 09:10 | WN5 | LONG RURAL |  | 49 | 232 | 11368 | 0.04402 | 0.00018974 | 0
2013-07-30 09:50 | SMR5 | LONG RURAL |  | 3 | 200 | 600 | 0.0023234 | 1.1617e-05 | 0
2013-07-30 09:10 | OFR23 | LONG RURAL |  | 29 | 355 | 10295 | 0.039865 | 0.0001123 | 0
2013-07-30 12:15 | RWT22 | URBAN |  | 118 | 165 | 19470 | 0.067823 | 0.00041105 | 0
2013-07-30 08:00 | RWT22 | URBAN |  | 230 | 204.3478 | 47000 | 0.16372 | 0.0008012 | 0
2013-07-31 08:50 | UWY1 | SHORT RURAL |  | 51 | 330 | 16830 | 0.14645 | 0.0004438 | 0
2013-07-30 08:45 | CRE32 | URBAN |  | 87 | 335 | 29145 | 0.10153 | 0.00030306 | 0
2013-07-31 09:45 | LLG13 | SHORT RURAL |  | 12 | 405 | 4860 | 0.042292 | 0.00010442 | 0
2013-07-20 06:52 | BRA22 | URBAN |  | 2 | 398 | 796 | 0.0027729 | 6.967e-06 | 0
2013-07-21 08:22 | WO11 | URBAN |  | 1 | 80 | 80 | 0.00027868 | 3.4835e-06 | 0
2013-08-07 09:15 | LGA21 | SHORT RURAL |  | 22 | 415 | 9130 | 0.079449 | 0.00019144 | 0
2013-08-06 09:00 | TGN23 | SHORT RURAL |  | 48 | 75 | 3600 | 0.031327 | 0.00041769 | 0
2013-08-05 09:15 | WGI22 | LONG RURAL |  | 3 | 215 | 645 | 0.0024976 | 1.1617e-05 | 0
2013-08-07 09:20 | WGI34 | SHORT RURAL |  | 55 | 95 | 5225 | 0.045468 | 0.00047861 | 0
2013-08-05 09:27 | TGN23 | SHORT RURAL |  | 23 | 283 | 6509 | 0.056641 | 0.00020015 | 0
2013-08-05 09:10 | TGN23 | SHORT RURAL |  | 39 | 170 | 6630 | 0.057694 | 0.00033938 | 0
2013-08-06 09:40 | TGN23 | SHORT RURAL |  | 4 | 160 | 640 | 0.0055693 | 3.4808e-05 | 0
2013-08-06 13:20 | TGN23 | SHORT RURAL |  | 29 | 60 | 1740 | 0.015141 | 0.00025236 | 0
2013-08-06 09:15 | TGN12 | SHORT RURAL |  | 164 | 240 | 39360 | 0.34251 | 0.0014271 | 0
2013-08-06 12:00 | MYT7 | LONG RURAL |  | 5 | 55 | 275 | 0.0010649 | 1.9362e-05 | 0
2013-08-06 10:05 | LGA21 | SHORT RURAL |  | 23 | 208 | 4784 | 0.04163 | 0.00020015 | 0
2013-08-06 08:39 | WYK23 | SHORT RURAL |  | 2456 | 468.4507 | 1150515 | 10.0117 | 0.021372 | 0
2013-08-05 09:00 | LLG12 | SHORT RURAL |  | 167 | 399 | 66633 | 0.57984 | 0.0014532 | 0
2013-08-05 09:00 | LLG12 | SHORT RURAL |  | 833 | 2 | 1666 | 0.014497 | 0.0072487 | 0
2013-08-06 09:00 | WGL21 | LONG RURAL |  | 18 | 255 | 4590 | 0.017774 | 6.9702e-05 | 0
2013-08-06 11:20 | WGL24 | LONG RURAL |  | 57 | 70 | 3990 | 0.015451 | 0.00022072 | 0
2013-08-08 09:55 | WOTS13 | LONG RURAL |  | 1 | 40 | 40 | 0.00015489 | 3.8723e-06 | 0
2013-08-08 09:15 | BRT21 | SHORT RURAL |  | 8 | 95 | 760 | 0.0066135 | 6.9616e-05 | 0
2013-08-07 09:10 | LDL23 | LONG RURAL |  | 209 | 352 | 73568 | 0.28488 | 0.00080931 | 0
2013-08-07 09:10 | WYK23 | SHORT RURAL |  | 90 | 140 | 12600 | 0.10964 | 0.00078318 | 0
2013-08-07 11:00 | WYK24 | SHORT RURAL |  | 14 | 156 | 2184 | 0.019005 | 0.00012183 | 0
2013-08-08 09:20 | LGA13 | LONG RURAL |  | 1 | 90 | 90 | 0.00034851 | 3.8723e-06 | 0
2013-08-06 09:02 | WGL15 | SHORT RURAL |  | 149 | 293 | 43657 | 0.3799 | 0.0012966 | 0
2013-08-07 09:00 | BRT21 | SHORT RURAL |  | 46 | 310 | 14260 | 0.12409 | 0.00040029 | 0
2013-08-08 09:20 | WGL21 | LONG RURAL |  | 4 | 170 | 680 | 0.0026332 | 1.5489e-05 | 0
2013-08-08 09:23 | MOE31 | LONG RURAL |  | 144 | 312 | 44928 | 0.17398 | 0.00055761 | 0
2013-08-07 09:45 | WGI31 | SHORT RURAL |  | 70 | 300 | 21000 | 0.18274 | 0.00060914 | 0
2013-08-08 09:38 | WOTS13 | LONG RURAL |  | 3 | 57 | 171 | 0.00066217 | 1.1617e-05 | 0
2013-08-05 09:10 | MSD2 | LONG RURAL |  | 57 | 195 | 11115 | 0.043041 | 0.00022072 | 0
2013-08-07 09:14 | MSD2 | LONG RURAL |  | 36 | 346 | 12456 | 0.048234 | 0.0001394 | 0
2013-07-31 13:15 | BRA14 | URBAN |  | 123 | 76 | 9348 | 0.032564 | 0.00042847 | 0
2013-08-05 09:30 | SLE31 | LONG RURAL |  | 36 | 65 | 2340 | 0.0090612 | 0.0001394 | 0
2013-08-01 08:50 | LLG11 | SHORT RURAL |  | 9 | 276 | 2484 | 0.021616 | 7.8318e-05 | 0
2013-08-07 09:06 | LLG12 | SHORT RURAL |  | 51 | 160.2941 | 8175 | 0.071139 | 0.0004438 | 0
2013-08-01 08:50 | LLG11 | SHORT RURAL |  | 22 | 175 | 3850 | 0.033503 | 0.00019144 | 0
2013-08-05 09:25 | MFA31 | SHORT RURAL |  | 162 | 355 | 57510 | 0.50045 | 0.0014097 | 0
2013-08-05 11:25 | SLE31 | LONG RURAL |  | 20 | 80 | 1600 | 0.0061957 | 7.7446e-05 | 0
2013-08-05 13:45 | SLE31 | LONG RURAL |  | 4 | 60 | 240 | 0.00092936 | 1.5489e-05 | 0
2013-08-01 09:35 | WGL12 | LONG RURAL |  | 40 | 216 | 8640 | 0.033457 | 0.00015489 | 0
2013-08-01 09:30 | OFR23 | LONG RURAL |  | 1 | 25 | 25 | 9.6808e-05 | 3.8723e-06 | 0
2013-08-01 11:00 | PHM33 | SHORT RURAL |  | 95 | 129.7684 | 12328 | 0.10728 | 0.00082669 | 0
2013-07-31 09:39 | BRA14 | URBAN |  | 378 | 299 | 113022 | 0.39371 | 0.0013168 | 0
2013-07-31 09:30 | EPG11 | URBAN |  | 78 | 311 | 24258 | 0.084502 | 0.00027171 | 0
2013-07-31 12:25 | BRA13 | URBAN |  | 393 | 135 | 53055 | 0.18482 | 0.001369 | 0
2013-08-01 08:35 | ELM31 | URBAN |  | 143 | 135 | 19305 | 0.067249 | 0.00049814 | 0
2013-08-01 10:03 | RWT11 | URBAN |  | 158 | 287 | 45346 | 0.15796 | 0.00055039 | 0
2013-08-01 09:15 | RWN26 | SHORT RURAL |  | 192 | 310 | 59520 | 0.51794 | 0.0016708 | 0
2013-08-01 10:10 | DRN12 | URBAN |  | 23 | 335 | 7705 | 0.02684 | 8.012e-05 | 0
2013-08-02 08:30 | BWN14 | SHORT RURAL |  | 23 | 194 | 4462 | 0.038828 | 0.00020015 | 0
2013-07-25 08:52 | BWR23 | URBAN |  | 43 | 296 | 12728 | 0.044338 | 0.00014979 | 0
2013-08-02 11:56 | BWN14 | SHORT RURAL |  | 28 | 84 | 2352 | 0.020467 | 0.00024366 | 0
2013-08-04 08:34 | WGL12 | LONG RURAL |  | 613 | 463 | 283819 | 1.099 | 0.0023737 | 0
2013-08-05 10:00 | WN2 | LONG RURAL |  | 233 | 144 | 33552 | 0.12992 | 0.00090225 | 0
2013-08-04 08:30 | RWT11 | URBAN |  | 500 | 388 | 194000 | 0.6758 | 0.0017417 | 0
2013-08-05 12:05 | CRE22 | URBAN |  | 68 | 130 | 8840 | 0.030794 | 0.00023688 | 0
2013-07-31 09:30 | BGE22 | SHORT RURAL |  | 70 | 355 | 24850 | 0.21624 | 0.00060914 | 0
2013-08-01 08:03 | DRN11 | URBAN |  | 181 | 406 | 73486 | 0.25599 | 0.00063051 | 0
2013-08-02 09:25 | DRN14 | SHORT RURAL |  | 1 | 195 | 195 | 0.0016969 | 8.702e-06 | 0
2013-08-02 09:15 | WT9 | URBAN |  | 141 | 150 | 21150 | 0.073676 | 0.00049117 | 0
2013-08-02 12:20 | WT9 | URBAN |  | 142 | 48 | 6816 | 0.023743 | 0.00049465 | 0
2013-08-03 08:00 | DRN14 | SHORT RURAL |  | 8 | 270 | 2160 | 0.018796 | 6.9616e-05 | 0
2013-08-07 08:40 | SMR3 | LONG RURAL |  | 1 | 230 | 230 | 0.00089063 | 3.8723e-06 | 0
2013-08-01 09:25 | DRN11 | URBAN |  | 92 | 268 | 24656 | 0.085889 | 0.00032048 | 0
2013-07-31 13:47 | BGE22 | SHORT RURAL |  | 76 | 93 | 7068 | 0.061506 | 0.00066135 | 0
2013-08-02 09:05 | BGE22 | SHORT RURAL |  | 101 | 397 | 40097 | 0.34892 | 0.0008789 | 0
2013-07-31 11:40 | ALA01 | LONG RURAL |  | 2 | 80 | 160 | 0.00061957 | 7.7446e-06 | 0
2013-08-06 09:55 | WGL13 | SHORT RURAL |  | 8 | 135 | 1080 | 0.0093981 | 6.9616e-05 | 0
2013-08-02 09:30 | SLE24 | URBAN |  | 64 | 100 | 6400 | 0.022294 | 0.00022294 | 0
2013-08-02 08:50 | BGE22 | SHORT RURAL |  | 19 | 145 | 2755 | 0.023974 | 0.00016534 | 0
2013-08-07 09:10 | MOE22 | LONG RURAL |  | 2 | 130 | 260 | 0.0010068 | 7.7446e-06 | 0
2013-08-07 11:40 | MOE22 | LONG RURAL |  | 4 | 65 | 260 | 0.0010068 | 1.5489e-05 | 0
2013-08-08 09:30 | ALA01 | LONG RURAL |  | 2 | 180 | 360 | 0.001394 | 7.7446e-06 | 0
2013-08-01 11:45 | RWT11 | URBAN |  | 116 | 130 | 15080 | 0.052531 | 0.00040408 | 0
2013-07-31 08:30 | WT13 | URBAN |  | 50 | 398 | 19900 | 0.069321 | 0.00017417 | 0
2013-07-29 11:20 | WT11 | URBAN |  | 137 | 120 | 16440 | 0.057268 | 0.00047724 | 0
2013-08-02 11:30 | BGE22 | SHORT RURAL |  | 34 | 45 | 1530 | 0.013314 | 0.00029587 | 0
2013-08-02 09:15 | RWN24 | SHORT RURAL |  | 3 | 200 | 600 | 0.0052212 | 2.6106e-05 | 0
2013-08-08 09:21 | MOE24 | SHORT RURAL |  | 37 | 12 | 444 | 0.0038637 | 0.00032197 | 0
2013-07-26 10:00 | BWR23 | URBAN |  | 68 | 110 | 7480 | 0.026056 | 0.00023688 | 0
2013-07-24 09:48 | LDL24 | URBAN |  | 144 | 157 | 22608 | 0.078755 | 0.00050162 | 0
2013-08-09 09:45 | MBY11 | SHORT RURAL |  | 66 | 147 | 9702 | 0.084427 | 0.00057433 | 0
2013-08-09 09:00 | WGI14 | SHORT RURAL |  | 1723 | 158 | 272234 | 2.369 | 0.014993 | 0
2013-08-09 08:40 | WOTS13 | LONG RURAL |  | 1 | 35 | 35 | 0.00013553 | 3.8723e-06 | 0
2013-08-09 08:42 | WOTS13 | LONG RURAL |  | 1 | 43 | 43 | 0.00016651 | 3.8723e-06 | 0
2013-08-08 13:35 | WGL21 | LONG RURAL |  | 2 | 70 | 140 | 0.00054212 | 7.7446e-06 | 0
2013-08-09 09:03 | TGN31 | LONG RURAL |  | 75 | 548.88 | 41166 | 0.15941 | 0.00029042 | 0
2013-07-30 10:13 | CYN11 | URBAN |  | 272 | 257 | 69904 | 0.24351 | 0.00094751 | 0
2013-08-05 09:10 | SMR4 | SHORT RURAL |  | 5 | 75 | 375 | 0.0032632 | 4.351e-05 | 0
2013-08-06 10:25 | CLN21 | SHORT RURAL |  | 10 | 195 | 1950 | 0.016969 | 8.702e-05 | 0
2013-08-06 09:15 | KMS1 | SHORT RURAL |  | 19 | 300 | 5700 | 0.049601 | 0.00016534 | 0
2013-07-28 08:20 | FGY22 | URBAN |  | 62 | 215 | 13330 | 0.046435 | 0.00021598 | 0
2013-08-05 08:55 | BN2 | LONG RURAL |  | 7 | 60 | 420 | 0.0016264 | 2.7106e-05 | 0
2013-08-06 08:45 | BWN11 | SHORT RURAL |  | 160 | 315 | 50400 | 0.43858 | 0.0013923 | 0
2013-08-05 11:25 | BN2 | LONG RURAL |  | 2 | 82 | 164 | 0.00063506 | 7.7446e-06 | 0
2013-08-07 12:09 | PHM14 | LONG RURAL |  | 6 | 117 | 702 | 0.0027184 | 2.3234e-05 | 0
2013-08-07 09:10 | CLN22 | SHORT RURAL |  | 14 | 305 | 4270 | 0.037157 | 0.00012183 | 0
2013-08-08 08:47 | MSD2 | LONG RURAL |  | 14 | 314 | 4396 | 0.017023 | 5.4212e-05 | 0
2013-08-08 10:26 | BN1 | LONG RURAL |  | 2 | 94 | 188 | 0.000728 | 7.7446e-06 | 0
2013-08-09 08:40 | BN6 | LONG RURAL |  | 2 | 35 | 70 | 0.00027106 | 7.7446e-06 | 0
2013-07-31 08:15 | CYN31 | URBAN |  | 298 | 29 | 8642 | 0.030104 | 0.0010381 | 0
2013-08-02 11:05 | WYK11 | SHORT RURAL |  | 64 | 125 | 8000 | 0.069616 | 0.00055693 | 0
2013-08-01 08:45 | DRN12 | URBAN |  | 10 | 411 | 4110 | 0.014317 | 3.4835e-05 | 0
2013-08-08 08:35 | SLE31 | LONG RURAL |  | 76 | 349 | 26524 | 0.10271 | 0.0002943 | 0
2013-07-31 08:40 | CYN14 | URBAN |  | 47 | 315 | 14805 | 0.051573 | 0.00016372 | 0
2013-08-07 08:31 | BN1 | LONG RURAL |  | 49 | 413 | 20237 | 0.078364 | 0.00018974 | 0
2013-08-09 11:05 | MFA21 | LONG RURAL |  | 1 | 70 | 70 | 0.00027106 | 3.8723e-06 | 0
2013-07-31 11:35 | CYN31 | URBAN |  | 89 | 81 | 7209 | 0.025112 | 0.00031003 | 0
2013-08-05 08:35 | SFS1 | SHORT RURAL |  | 116 | 442 | 51272 | 0.44617 | 0.0010094 | 0
2013-08-01 08:35 | CYN32 | URBAN |  | 33 | 143 | 4719 | 0.016439 | 0.00011495 | 0
2013-08-06 08:30 | OFR23 | LONG RURAL |  | 2 | 470 | 940 | 0.00364 | 7.7446e-06 | 0
2013-08-01 08:00 | CYN24 | URBAN |  | 164 | 450 | 73800 | 0.25708 | 0.00057129 | 0
2013-08-07 08:40 | OFR23 | LONG RURAL |  | 16 | 465 | 7440 | 0.02881 | 6.1957e-05 | 0
2013-08-05 09:08 | CYN32 | URBAN |  | 69 | 132 | 9108 | 0.031728 | 0.00024036 | 0
2013-08-08 08:40 | OFR23 | LONG RURAL |  | 39 | 452 | 17628 | 0.068261 | 0.00015102 | 0
2013-08-15 10:22 | WO22 | URBAN |  | 612 | 290 | 177480 | 0.61825 | 0.0021319 | 0
2013-08-08 09:30 | MWTS34 | SHORT RURAL |  | 44 | 355 | 15620 | 0.13592 | 0.00038289 | 0
2013-07-31 08:59 | BWR23 | URBAN |  | 116 | 286 | 33176 | 0.11557 | 0.00040408 | 0
2013-08-04 09:20 | BWR13 | SHORT RURAL |  | 21 | 135 | 2835 | 0.02467 | 0.00018274 | 0
2013-08-07 09:08 | FTR12 | LONG RURAL |  | 91 | 156 | 14196 | 0.054971 | 0.00035238 | 0
2013-08-08 14:02 | TGN12 | SHORT RURAL |  | 2 | 46 | 92 | 0.00080058 | 1.7404e-05 | 0
2013-08-06 08:30 | SLE32 | SHORT RURAL |  | 3 | 320 | 960 | 0.0083539 | 2.6106e-05 | 0
2013-08-06 08:50 | BDL3 | SHORT RURAL |  | 67 | 175 | 11725 | 0.10203 | 0.00058303 | 0
2013-08-06 09:00 | WN6 | LONG RURAL |  | 99 | 330 | 32670 | 0.12651 | 0.00038336 | 0
2013-07-31 09:43 | BWR13 | SHORT RURAL |  | 112 | 226 | 25312 | 0.22026 | 0.00097462 | 0
2013-08-08 10:15 | OFR22 | SHORT RURAL |  | 36 | 395 | 14220 | 0.12374 | 0.00031327 | 0
2013-08-01 09:12 | CYN14 | URBAN |  | 111 | 218 | 24198 | 0.084293 | 0.00038667 | 0
2013-08-11 09:25 | MFA34 | SHORT RURAL |  | 1 | 15 | 15 | 0.00013053 | 8.702e-06 | 0
2013-08-11 10:05 | MFA34 | SHORT RURAL |  | 1 | 7 | 7 | 6.0914e-05 | 8.702e-06 | 0
2013-08-11 08:32 | NRN14 | URBAN |  | 5 | 398 | 1990 | 0.0069321 | 1.7417e-05 | 0
2013-08-11 09:47 | MWTS32 | SHORT RURAL |  | 19 | 388 | 7372 | 0.064151 | 0.00016534 | 0
2013-08-07 09:20 | KMS1 | SHORT RURAL |  | 2 | 250 | 500 | 0.004351 | 1.7404e-05 | 0
2013-08-08 08:45 | SMR3 | LONG RURAL |  | 2 | 175 | 350 | 0.0013553 | 7.7446e-06 | 0
2013-08-05 09:10 | DRN12 | URBAN |  | 11 | 366 | 4026 | 0.014025 | 3.8318e-05 | 0
2013-07-31 10:20 | MBY11 | SHORT RURAL |  | 40 | 243 | 9720 | 0.084583 | 0.00034808 | 0
2013-08-07 08:38 | BDL5 | LONG RURAL |  | 134 | 374 | 50116 | 0.19406 | 0.00051889 | 0
2013-08-09 09:45 | MFA34 | SHORT RURAL |  | 1 | 185 | 185 | 0.0016099 | 8.702e-06 | 0
2013-08-06 09:45 | HPK23 | URBAN |  | 8 | 255 | 2040 | 0.0071063 | 2.7868e-05 | 0
2013-08-08 09:10 | KMS1 | SHORT RURAL |  | 95 | 225 | 21375 | 0.186 | 0.00082669 | 0
2013-08-08 09:08 | WN6 | LONG RURAL |  | 45 | 175 | 7875 | 0.030494 | 0.00017425 | 0
2013-08-06 13:35 | BGE21 | URBAN |  | 2 | 40 | 80 | 0.00027868 | 6.967e-06 | 0
2013-08-03 08:40 | DRN11 | URBAN |  | 9 | 1775 | 15975 | 0.055649 | 3.1351e-05 | 0
2013-08-08 08:40 | BGE11 | SHORT RURAL |  | 47 | 185 | 8695 | 0.075664 | 0.00040899 | 0
2013-08-08 09:07 | BGE11 | SHORT RURAL |  | 32 | 243 | 7776 | 0.067667 | 0.00027846 | 0
2013-08-08 09:30 | SFS1 | SHORT RURAL |  | 145 | 245 | 35525 | 0.30914 | 0.0012618 | 0
2013-08-08 08:30 | BGE22 | SHORT RURAL |  | 56 | 212 | 11872 | 0.10331 | 0.00048731 | 0
2013-08-08 11:55 | BGE11 | SHORT RURAL |  | 49 | 115 | 5635 | 0.049036 | 0.0004264 | 0
2013-08-05 09:45 | RWN24 | SHORT RURAL |  | 142 | 205 | 29110 | 0.25331 | 0.0012357 | 0
2013-08-05 08:30 | RWT11 | URBAN |  | 122 | 296 | 36112 | 0.1258 | 0.00042498 | 0
2013-08-05 08:30 | RWN31 | SHORT RURAL |  | 43 | 310 | 13330 | 0.116 | 0.00037418 | 0
2013-08-06 09:15 | RWN31 | SHORT RURAL |  | 8 | 105 | 840 | 0.0073097 | 6.9616e-05 | 0
2013-08-06 13:05 | RWN31 | SHORT RURAL |  | 1 | 160 | 160 | 0.0013923 | 8.702e-06 | 0
2013-08-09 08:50 | SMR3 | LONG RURAL |  | 2 | 145 | 290 | 0.001123 | 7.7446e-06 | 0
2013-08-05 10:10 | ELM13 | URBAN |  | 1 | 155 | 155 | 0.00053994 | 3.4835e-06 | 0
2013-08-12 10:40 | LDL24 | URBAN |  | 61 | 210 | 12810 | 0.044623 | 0.00021249 | 0
2013-08-12 07:59 | LDL14 | SHORT RURAL |  | 63 | 211 | 13293 | 0.11568 | 0.00054822 | 0
2013-08-12 09:10 | WGL21 | LONG RURAL |  | 14 | 120 | 1680 | 0.0065055 | 5.4212e-05 | 0
2013-08-12 08:30 | MWTS14 | SHORT RURAL |  | 115 | 359 | 41285 | 0.35926 | 0.0010007 | 0
2013-08-12 08:30 | SLE32 | SHORT RURAL |  | 3 | 324 | 972 | 0.0084583 | 2.6106e-05 | 0
2013-08-07 08:32 | BRA14 | URBAN |  | 497 | 473 | 235081 | 0.8189 | 0.0017313 | 0
2013-08-07 08:30 | KLO24 | SHORT RURAL |  | 116 | 420 | 48720 | 0.42396 | 0.0010094 | 0
2013-08-07 09:20 | RWN24 | SHORT RURAL |  | 128 | 415 | 53120 | 0.46225 | 0.0011139 | 0
2013-08-07 09:40 | RWN26 | SHORT RURAL |  | 40 | 285 | 11400 | 0.099202 | 0.00034808 | 0
2013-08-12 10:25 | SMR2 | SHORT RURAL |  | 3 | 255 | 765 | 0.006657 | 2.6106e-05 | 0
2013-08-05 13:05 | ELM13 | URBAN |  | 82 | 105 | 8610 | 0.029993 | 0.00028565 | 0
2013-08-06 08:30 | TT9 | URBAN |  | 270 | 475 | 128250 | 0.44676 | 0.00094054 | 0
2013-08-05 13:25 | ELM13 | URBAN |  | 504 | 71 | 35784 | 0.12465 | 0.0017557 | 0
2013-08-07 10:30 | ELM32 | URBAN |  | 22 | 95 | 2090 | 0.0072805 | 7.6637e-05 | 0
2013-08-07 10:10 | WT6 | URBAN |  | 97 | 165 | 16005 | 0.055753 | 0.0003379 | 0
2013-08-07 12:35 | DRN12 | URBAN |  | 27 | 145 | 3915 | 0.013638 | 9.4054e-05 | 0
2013-08-06 14:20 | CYN14 | URBAN |  | 195 | 84 | 16380 | 0.057059 | 0.00067928 | 0
2013-08-08 09:00 | ELM12 | SHORT RURAL |  | 115 | 470 | 54050 | 0.47034 | 0.0010007 | 0
2013-08-08 09:00 | ELM32 | URBAN |  | 29 | 470 | 13630 | 0.04748 | 0.00010102 | 0
2013-08-05 08:30 | CRE22 | URBAN |  | 58 | 125 | 7250 | 0.025255 | 0.00020204 | 0
2013-08-08 11:02 | ELM11 | URBAN |  | 122 | 363 | 44286 | 0.15427 | 0.00042498 | 0
2013-08-08 09:55 | LLG11 | SHORT RURAL |  | 1 | 55 | 55 | 0.00047861 | 8.702e-06 | 0
2013-08-11 09:09 | TT5 | URBAN |  | 31 | 189 | 5859 | 0.02041 | 0.00010799 | 0
2013-08-13 10:40 | MOE31 | LONG RURAL |  | 3 | 135 | 405 | 0.0015683 | 1.1617e-05 | 0
2013-08-14 09:45 | WOTS13 | LONG RURAL |  | 1 | 80 | 80 | 0.00030979 | 3.8723e-06 | 0
2013-08-13 09:10 | LGA14 | LONG RURAL |  | 15 | 230 | 3450 | 0.013359 | 5.8085e-05 | 0
2013-08-13 09:31 | KLK1 | SHORT RURAL |  | 51 | 89 | 4539 | 0.039498 | 0.0004438 | 0
2013-08-15 09:00 | WGL24 | LONG RURAL |  | 1 | 215 | 215 | 0.00083255 | 3.8723e-06 | 0
2013-08-15 09:45 | TGN31 | LONG RURAL |  | 8 | 345 | 2760 | 0.010688 | 3.0979e-05 | 0
2013-08-14 12:37 | WOTS13 | LONG RURAL |  | 1 | 48 | 48 | 0.00018587 | 3.8723e-06 | 0
2013-08-14 08:25 | LDL11 | URBAN |  | 65 | 240 | 15600 | 0.054342 | 0.00022643 | 0
2013-08-14 11:00 | LDL24 | URBAN |  | 1365 | 215 | 293475 | 1.0223 | 0.004755 | 0
2013-08-15 09:45 | WGL21 | LONG RURAL |  | 15 | 217 | 3255 | 0.012604 | 5.8085e-05 | 0
2013-08-13 09:00 | WGL21 | LONG RURAL |  | 3 | 70 | 210 | 0.00081319 | 1.1617e-05 | 0
2013-08-13 08:40 | SLE31 | LONG RURAL |  | 20 | 335 | 6700 | 0.025945 | 7.7446e-05 | 0
2013-08-13 08:36 | SLE32 | SHORT RURAL |  | 297 | 424 | 125928 | 1.0958 | 0.0025845 | 0
2013-08-14 09:05 | TGN31 | LONG RURAL |  | 43 | 345 | 14835 | 0.057446 | 0.00016651 | 0
2013-08-14 10:05 | BDL5 | LONG RURAL |  | 24 | 100 | 2400 | 0.0092936 | 9.2936e-05 | 0
2013-08-13 10:30 | WGL21 | LONG RURAL |  | 4 | 135 | 540 | 0.002091 | 1.5489e-05 | 0
2013-08-14 08:30 | MWTS14 | SHORT RURAL |  | 37 | 361 | 13357 | 0.11623 | 0.00032197 | 0
2013-08-14 09:00 | WGL21 | LONG RURAL |  | 2 | 150 | 300 | 0.0011617 | 7.7446e-06 | 0
2013-08-13 09:20 | MFA22 | LONG RURAL |  | 29 | 235 | 6815 | 0.02639 | 0.0001123 | 0
2013-08-15 09:25 | WYK12 | SHORT RURAL |  | 66 | 290 | 19140 | 0.16656 | 0.00057433 | 0
2013-08-14 09:25 | BN1 | LONG RURAL |  | 4 | 165 | 660 | 0.0025557 | 1.5489e-05 | 0
2013-08-14 10:50 | BN1 | LONG RURAL |  | 3 | 30 | 90 | 0.00034851 | 1.1617e-05 | 0
2013-08-14 12:34 | BN1 | LONG RURAL |  | 7 | 36 | 252 | 0.00097582 | 2.7106e-05 | 0
2013-08-14 14:40 | BN1 | LONG RURAL |  | 1 | 45 | 45 | 0.00017425 | 3.8723e-06 | 0
2013-08-14 13:25 | BN1 | LONG RURAL |  | 1 | 35 | 35 | 0.00013553 | 3.8723e-06 | 0
2013-08-14 11:54 | BN1 | LONG RURAL |  | 1 | 45 | 45 | 0.00017425 | 3.8723e-06 | 0
2013-08-15 09:45 | BN1 | LONG RURAL |  | 1 | 60 | 60 | 0.00023234 | 3.8723e-06 | 0
2013-08-15 09:55 | BN1 | LONG RURAL |  | 3 | 60 | 180 | 0.00069702 | 1.1617e-05 | 0
2013-08-15 11:25 | BN1 | LONG RURAL |  | 1 | 35 | 35 | 0.00013553 | 3.8723e-06 | 0
2013-08-14 09:00 | MYT2 | SHORT RURAL |  | 363 | 3.3471 | 1215 | 0.010573 | 0.0031588 | 0
2013-08-15 09:35 | MOE14 | SHORT RURAL |  | 49 | 55 | 2695 | 0.023452 | 0.0004264 | 0
2013-08-15 09:00 | MWTS34 | SHORT RURAL |  | 89 | 219 | 19491 | 0.16961 | 0.00077448 | 0
2013-08-14 09:15 | WGL21 | LONG RURAL |  | 37 | 245 | 9065 | 0.035103 | 0.00014328 | 0
2013-08-14 08:30 | CNR2 | SHORT RURAL |  | 5 | 315 | 1575 | 0.013706 | 4.351e-05 | 0
2013-08-14 10:15 | BDL1 | LONG RURAL |  | 3 | 185 | 555 | 0.0021491 | 1.1617e-05 | 0
2013-08-07 08:35 | RWT11 | URBAN |  | 2 | 327 | 654 | 0.0022782 | 6.967e-06 | 0
2013-08-08 09:00 | RWT11 | URBAN |  | 360 | 62 | 22320 | 0.077751 | 0.0012541 | 0
2013-08-08 08:45 | BWR23 | URBAN |  | 80 | 315 | 25200 | 0.087784 | 0.00027868 | 0
2013-08-08 09:15 | RWN22 | URBAN |  | 64 | 583 | 37312 | 0.12998 | 0.00022294 | 0
2013-08-08 09:20 | BRA33 | URBAN |  | 108 | 330 | 35640 | 0.12415 | 0.00037622 | 0
2013-08-11 08:00 | ELM31 | URBAN |  | 249 | 425 | 105825 | 0.36864 | 0.00086739 | 0
2013-08-02 09:20 | MSD2 | LONG RURAL |  | 1 | 180 | 180 | 0.00069702 | 3.8723e-06 | 0
2013-08-09 10:03 | BWR23 | URBAN |  | 292 | 151 | 44092 | 0.15359 | 0.0010172 | 0
2013-08-14 08:50 | SLE31 | LONG RURAL |  | 29 | 235 | 6815 | 0.02639 | 0.0001123 | 0
2013-08-12 08:32 | SFS1 | SHORT RURAL |  | 231 | 568 | 131208 | 1.1418 | 0.0020102 | 0
2013-08-04 08:30 | HPK24 | URBAN |  | 1 | 90 | 90 | 0.00031351 | 3.4835e-06 | 0
2013-08-16 09:00 | MYT7 | LONG RURAL |  | 4 | 195 | 780 | 0.0030204 | 1.5489e-05 | 0
2013-08-16 09:15 | FTR21 | LONG RURAL |  | 44 | 75 | 3300 | 0.012779 | 0.00017038 | 0
2013-08-16 09:00 | PHI12 | SHORT RURAL |  | 58 | 285 | 16530 | 0.14384 | 0.00050471 | 0
2013-08-16 09:45 | WGI22 | LONG RURAL |  | 64 | 365 | 23360 | 0.090457 | 0.00024783 | 0
2013-08-16 09:25 | WOTS13 | LONG RURAL |  | 1 | 135 | 135 | 0.00052276 | 3.8723e-06 | 0
2013-08-15 12:40 | BN1 | LONG RURAL |  | 2 | 45 | 90 | 0.00034851 | 7.7446e-06 | 0
2013-08-15 13:05 | BN1 | LONG RURAL |  | 2 | 40 | 80 | 0.00030979 | 7.7446e-06 | 0
2013-08-15 13:55 | BN1 | LONG RURAL |  | 1 | 55 | 55 | 0.00021298 | 3.8723e-06 | 0
2013-08-16 09:10 | MSD4 | LONG RURAL |  | 26 | 360 | 9360 | 0.036245 | 0.00010068 | 0
2013-08-16 09:37 | TGN41 | LONG RURAL |  | 403 | 433 | 174499 | 0.67571 | 0.0015605 | 0
2013-08-16 09:00 | WGL24 | LONG RURAL |  | 2 | 180 | 360 | 0.001394 | 7.7446e-06 | 0
2013-08-16 09:00 | BRT21 | SHORT RURAL |  | 32 | 213 | 6816 | 0.059313 | 0.00027846 | 0
2013-08-16 09:30 | WGL21 | LONG RURAL |  | 8 | 235 | 1880 | 0.00728 | 3.0979e-05 | 0
2013-08-16 10:15 | CNR3 | SHORT RURAL |  | 11 | 161 | 1771 | 0.015411 | 9.5722e-05 | 0
2013-08-08 08:50 | RWN26 | SHORT RURAL |  | 2 | 370 | 740 | 0.0064395 | 1.7404e-05 | 0
2013-08-08 09:35 | LLG11 | SHORT RURAL |  | 2 | 10 | 20 | 0.00017404 | 1.7404e-05 | 0
2013-08-14 09:05 | MFA22 | LONG RURAL |  | 15 | 294 | 4410 | 0.017077 | 5.8085e-05 | 0
2013-08-16 08:45 | SLE31 | LONG RURAL |  | 27 | 345 | 9315 | 0.036071 | 0.00010455 | 0
2013-08-14 09:25 | MFA22 | LONG RURAL |  | 6 | 130 | 780 | 0.0030204 | 2.3234e-05 | 0
2013-08-11 09:35 | BWR32 | URBAN |  | 138 | 420 | 57960 | 0.2019 | 0.00048072 | 0
2013-08-16 09:15 | MFA22 | LONG RURAL |  | 3 | 220 | 660 | 0.0025557 | 1.1617e-05 | 0
2013-08-16 09:15 | TGN31 | LONG RURAL |  | 11 | 180 | 1980 | 0.0076672 | 4.2595e-05 | 0
2013-08-09 09:35 | KLO14 | LONG RURAL |  | 8 | 100 | 800 | 0.0030979 | 3.0979e-05 | 0
2013-08-13 08:30 | ALA01 | LONG RURAL |  | 137 | 477 | 65349 | 0.25305 | 0.00053051 | 0
2013-08-16 09:10 | TGN31 | LONG RURAL |  | 37 | 185 | 6845 | 0.026506 | 0.00014328 | 0
2013-08-12 09:10 | BDL6 | SHORT RURAL |  | 1 | 202 | 202 | 0.0017578 | 8.702e-06 | 0
2013-08-13 09:30 | SMR3 | LONG RURAL |  | 2 | 180 | 360 | 0.001394 | 7.7446e-06 | 0
2013-08-15 09:05 | MFA22 | LONG RURAL |  | 58 | 425 | 24650 | 0.095453 | 0.00022459 | 0
2013-08-14 08:36 | HPK22 | URBAN |  | 30 | 244 | 7320 | 0.025499 | 0.0001045 | 0
2013-08-15 09:02 | MSD4 | LONG RURAL |  | 3 | 198 | 594 | 0.0023002 | 1.1617e-05 | 0
2013-08-15 09:12 | BN6 | LONG RURAL |  | 13 | 255 | 3315 | 0.012837 | 5.034e-05 | 0
2013-08-16 11:13 | FTR21 | LONG RURAL |  | 23 | 87 | 2001 | 0.0077485 | 8.9063e-05 | 0
2013-08-17 09:15 | MWTS32 | SHORT RURAL |  | 588 | 380 | 223440 | 1.9444 | 0.0051168 | 0
2013-08-11 08:30 | RWN33 | URBAN |  | 3 | 300 | 900 | 0.0031351 | 1.045e-05 | 0
2013-08-11 09:16 | RWN26 | SHORT RURAL |  | 39 | 318 | 12402 | 0.10792 | 0.00033938 | 0
2013-08-14 08:30 | BDL3 | SHORT RURAL |  | 1 | 75 | 75 | 0.00065265 | 8.702e-06 | 0
2013-08-11 08:08 | BRA14 | URBAN |  | 94 | 372 | 34968 | 0.12181 | 0.00032745 | 0
2013-08-15 10:17 | BDL6 | SHORT RURAL |  | 85 | 323 | 27455 | 0.23891 | 0.00073967 | 0
2013-08-15 09:20 | HPK12 | URBAN |  | 93 | 370 | 34410 | 0.11987 | 0.00032396 | 0
2013-08-16 09:26 | TGN23 | SHORT RURAL |  | 4 | 111 | 444 | 0.0038637 | 3.4808e-05 | 0
2013-08-11 09:00 | BWR32 | URBAN |  | 60 | 261 | 15660 | 0.054551 | 0.00020901 | 0
2013-08-12 08:40 | BWR32 | URBAN |  | 20 | 215 | 4300 | 0.014979 | 6.967e-05 | 0
2013-08-12 08:30 | RWN24 | SHORT RURAL |  | 29 | 490 | 14210 | 0.12366 | 0.00025236 | 0
2013-08-15 09:00 | BDL5 | LONG RURAL |  | 264 | 518 | 136752 | 0.52955 | 0.0010223 | 0
2013-08-14 08:30 | SMR3 | LONG RURAL |  | 1 | 140 | 140 | 0.00054212 | 3.8723e-06 | 0
2013-08-16 11:05 | BN1 | LONG RURAL |  | 2 | 145 | 290 | 0.001123 | 7.7446e-06 | 0
2013-08-18 08:30 | MWTS14 | SHORT RURAL |  | 126 | 376 | 47376 | 0.41226 | 0.0010964 | 0
2013-08-18 09:00 | MWTS11 | SHORT RURAL |  | 51 | 440 | 22440 | 0.19527 | 0.0004438 | 0
2013-08-14 09:34 | SMR5 | LONG RURAL |  | 8 | 182 | 1456 | 0.0056381 | 3.0979e-05 | 0
2013-08-16 09:10 | BN1 | LONG RURAL |  | 1 | 66 | 66 | 0.00025557 | 3.8723e-06 | 0
2013-08-14 09:02 | KMS1 | SHORT RURAL |  | 52 | 313 | 16276 | 0.14163 | 0.0004525 | 0
2013-08-15 09:45 | SMR3 | LONG RURAL |  | 31 | 290 | 8990 | 0.034812 | 0.00012004 | 0
2013-08-08 09:27 | RWN26 | SHORT RURAL |  | 44 | 211 | 9284 | 0.080789 | 0.00038289 | 0
2013-08-16 09:10 | BN1 | LONG RURAL |  | 28 | 85 | 2380 | 0.0092161 | 0.00010842 | 0
2013-08-16 11:50 | BN1 | LONG RURAL |  | 1 | 35 | 35 | 0.00013553 | 3.8723e-06 | 0
2013-08-16 10:07 | BN1 | LONG RURAL |  | 1 | 46 | 46 | 0.00017813 | 3.8723e-06 | 0
2013-08-11 08:18 | BRA33 | URBAN |  | 702 | 287 | 201474 | 0.70183 | 0.0024454 | 0
2013-08-14 08:30 | CYN32 | URBAN |  | 173 | 480 | 83040 | 0.28927 | 0.00060264 | 0
2013-08-13 09:28 | BWR12 | URBAN |  | 87 | 326 | 28362 | 0.098799 | 0.00030306 | 0
2013-08-13 10:29 | RWN26 | SHORT RURAL |  | 62 | 278 | 17236 | 0.14999 | 0.00053952 | 0
2013-08-19 09:40 | LDL11 | URBAN |  | 124 | 245 | 30380 | 0.10583 | 0.00043195 | 0
2013-08-19 09:35 | MSD1 | LONG RURAL |  | 5 | 125 | 625 | 0.0024202 | 1.9362e-05 | 0
2013-08-19 10:05 | MFA22 | LONG RURAL |  | 28 | 195 | 5460 | 0.021143 | 0.00010842 | 0
2013-08-19 09:20 | BN1 | LONG RURAL |  | 2 | 80 | 160 | 0.00061957 | 7.7446e-06 | 0
2013-08-19 09:12 | BN1 | LONG RURAL |  | 1 | 29 | 29 | 0.0001123 | 3.8723e-06 | 0
2013-08-14 08:55 | RWN22 | URBAN |  | 63 | 375 | 23625 | 0.082297 | 0.00021946 | 0
2013-08-14 10:15 | BRA14 | URBAN |  | 375 | 236 | 88500 | 0.30829 | 0.0013063 | 0
2013-08-13 09:15 | BWR32 | URBAN |  | 38 | 225 | 8550 | 0.029784 | 0.00013237 | 0
2013-08-15 09:14 | ELM15 | SHORT RURAL |  | 207 | 423 | 87561 | 0.76195 | 0.0018013 | 0
2013-08-19 09:35 | MWTS14 | SHORT RURAL |  | 2 | 19 | 38 | 0.00033067 | 1.7404e-05 | 0
2013-08-14 09:05 | ELM11 | URBAN |  | 66 | 305 | 20130 | 0.070123 | 0.00022991 | 0
2013-08-19 10:05 | BN1 | LONG RURAL |  | 1 | 50 | 50 | 0.00019362 | 3.8723e-06 | 0
2013-08-08 08:40 | RWN24 | SHORT RURAL |  | 52 | 240 | 12480 | 0.1086 | 0.0004525 | 0
2013-08-19 09:00 | SLE31 | LONG RURAL |  | 25 | 235 | 5875 | 0.02275 | 9.6808e-05 | 0
2013-08-15 08:37 | BGE22 | SHORT RURAL |  | 63 | 243 | 15309 | 0.13322 | 0.00054822 | 0
2013-08-15 11:35 | HPK23 | URBAN |  | 171 | 10 | 1710 | 0.0059568 | 0.00059568 | 0
2013-08-14 08:38 | BWN11 | SHORT RURAL |  | 3 | 102 | 306 | 0.0026628 | 2.6106e-05 | 0
2013-08-14 08:30 | PHM14 | LONG RURAL |  | 1 | 120 | 120 | 0.00046468 | 3.8723e-06 | 0
2013-08-14 10:00 | PHM14 | LONG RURAL |  | 14 | 25 | 350 | 0.0013553 | 5.4212e-05 | 0
2013-08-14 11:45 | PHM14 | LONG RURAL |  | 2 | 25 | 50 | 0.00019362 | 7.7446e-06 | 0
2013-08-14 09:38 | CYN12 | URBAN |  | 202 | 247 | 49894 | 0.1738 | 0.00070366 | 0
2013-08-14 11:30 | BWN11 | SHORT RURAL |  | 6 | 55 | 330 | 0.0028717 | 5.2212e-05 | 0
2013-08-15 08:50 | CYN33 | SHORT RURAL |  | 121 | 215 | 26015 | 0.22638 | 0.0010529 | 0
2013-08-14 09:20 | BRA11 | URBAN |  | 91 | 330 | 30030 | 0.10461 | 0.000317 | 0
2013-08-15 09:30 | CYN22 | URBAN |  | 474 | 320 | 151680 | 0.52837 | 0.0016512 | 0
2013-08-14 09:10 | RWN24 | SHORT RURAL |  | 139 | 190 | 26410 | 0.22982 | 0.0012096 | 0
2013-08-15 09:07 | RWN24 | SHORT RURAL |  | 105 | 321 | 33705 | 0.2933 | 0.00091371 | 0
2013-08-05 13:49 | FGY13 | SHORT RURAL |  | 2500 | 125 | 312500 | 2.7194 | 0.021755 | 0
2013-08-21 11:47 | FTR23 | LONG RURAL |  | 2 | 19 | 38 | 0.00014715 | 7.7446e-06 | 0
2013-08-21 09:40 | WGI33 | SHORT RURAL |  | 132 | 320 | 42240 | 0.36757 | 0.0011487 | 0
2013-08-20 09:48 | FTR21 | LONG RURAL |  | 94 | 59 | 5546 | 0.021476 | 0.000364 | 0
2013-08-20 09:05 | WGL21 | LONG RURAL |  | 18 | 145 | 2610 | 0.010107 | 6.9702e-05 | 0
2013-08-20 08:30 | WOTS13 | LONG RURAL |  | 1 | 195 | 195 | 0.0007551 | 3.8723e-06 | 0
2013-08-21 09:00 | FTR12 | LONG RURAL |  | 13 | 461 | 5993 | 0.023207 | 5.034e-05 | 0
2013-08-20 09:45 | BN1 | LONG RURAL |  | 3 | 230 | 690 | 0.0026719 | 1.1617e-05 | 0
2013-08-20 09:45 | WGL21 | LONG RURAL |  | 24 | 285 | 6840 | 0.026487 | 9.2936e-05 | 0
2013-08-22 09:00 | LGA11 | LONG RURAL |  | 668 | 271 | 181028 | 0.701 | 0.0025867 | 0
2013-08-20 09:29 | LDL13 | SHORT RURAL |  | 58 | 276 | 16008 | 0.1393 | 0.00050471 | 0
2013-08-22 09:15 | WGL21 | LONG RURAL |  | 17 | 270 | 4590 | 0.017774 | 6.5829e-05 | 0
2013-08-22 08:35 | MWTS14 | SHORT RURAL |  | 4 | 190 | 760 | 0.0066135 | 3.4808e-05 | 0
2013-08-21 09:00 | WGL21 | LONG RURAL |  | 27 | 180 | 4860 | 0.018819 | 0.00010455 | 0
2013-08-22 09:00 | WGL21 | LONG RURAL |  | 27 | 225 | 6075 | 0.023524 | 0.00010455 | 0
2013-08-21 09:25 | MOE23 | SHORT RURAL |  | 160 | 270 | 43200 | 0.37593 | 0.0013923 | 0
2013-08-21 09:25 | MOE24 | SHORT RURAL |  | 9 | 265 | 2385 | 0.020754 | 7.8318e-05 | 0
2013-08-22 08:30 | WYK23 | SHORT RURAL |  | 86 | 215 | 18490 | 0.1609 | 0.00074837 | 0
2013-08-21 08:45 | LDL23 | LONG RURAL |  | 69 | 335 | 23115 | 0.089509 | 0.00026719 | 0
2013-08-20 11:10 | WGL24 | LONG RURAL |  | 2 | 30 | 60 | 0.00023234 | 7.7446e-06 | 0
2013-08-20 09:05 | WYK11 | SHORT RURAL |  | 120 | 308 | 36960 | 0.32162 | 0.0010442 | 0
2013-08-19 11:30 | BN1 | LONG RURAL |  | 3 | 45 | 135 | 0.00052276 | 1.1617e-05 | 0
2013-08-19 11:20 | CNR3 | SHORT RURAL |  | 2 | 52 | 104 | 0.000905 | 1.7404e-05 | 0
2013-08-20 13:20 | WGL15 | SHORT RURAL |  | 17 | 60 | 1020 | 0.008876 | 0.00014793 | 0
2013-08-20 10:10 | MWTS14 | SHORT RURAL |  | 50 | 87 | 4350 | 0.037854 | 0.0004351 | 0
2013-08-20 10:00 | CYN33 | SHORT RURAL |  | 68 | 320 | 21760 | 0.18935 | 0.00059173 | 0
2013-08-14 09:35 | BWR34 | URBAN |  | 306 | 310 | 94860 | 0.33044 | 0.0010659 | 0
2013-08-16 08:57 | ELM12 | SHORT RURAL |  | 52 | 130 | 6760 | 0.058825 | 0.0004525 | 0
2013-08-16 12:05 | ELM15 | SHORT RURAL |  | 134 | 133 | 17822 | 0.15509 | 0.0011661 | 0
2013-08-21 10:10 | ELM13 | URBAN |  | 83 | 195 | 16185 | 0.05638 | 0.00028913 | 0
2013-08-19 12:35 | CNR3 | SHORT RURAL |  | 2 | 90 | 180 | 0.0015664 | 1.7404e-05 | 0
2013-08-20 09:45 | MFA31 | SHORT RURAL |  | 58 | 25 | 1450 | 0.012618 | 0.00050471 | 0
2013-08-20 08:40 | MFA34 | SHORT RURAL |  | 105 | 380 | 39900 | 0.34721 | 0.00091371 | 0
2013-08-20 09:30 | MFA31 | SHORT RURAL |  | 2 | 110 | 220 | 0.0019144 | 1.7404e-05 | 0
2013-08-21 10:50 | CNR3 | SHORT RURAL |  | 4 | 145 | 580 | 0.0050471 | 3.4808e-05 | 0
2013-08-21 13:55 | CNR3 | SHORT RURAL |  | 1 | 55 | 55 | 0.00047861 | 8.702e-06 | 0
2013-08-22 09:10 | CNR3 | SHORT RURAL |  | 13 | 240 | 3120 | 0.02715 | 0.00011313 | 0
2013-08-15 09:05 | LLG13 | SHORT RURAL |  | 12 | 260 | 3120 | 0.02715 | 0.00010442 | 0
2013-08-15 11:37 | WGL12 | LONG RURAL |  | 2 | 88 | 176 | 0.00068153 | 7.7446e-06 | 0
2013-08-15 13:25 | LLG13 | SHORT RURAL |  | 6 | 60 | 360 | 0.0031327 | 5.2212e-05 | 0
2013-08-16 08:56 | WGL12 | LONG RURAL |  | 4 | 67 | 268 | 0.0010378 | 1.5489e-05 | 0
2013-08-16 11:22 | LLG11 | SHORT RURAL |  | 1 | 22 | 22 | 0.00019144 | 8.702e-06 | 0
2013-08-16 12:58 | BWN11 | SHORT RURAL |  | 3 | 37 | 111 | 0.00096592 | 2.6106e-05 | 0
2013-08-16 09:05 | SMR2 | SHORT RURAL |  | 58 | 315 | 18270 | 0.15899 | 0.00050471 | 0
2013-08-19 13:45 | SLE31 | LONG RURAL |  | 48 | 125 | 6000 | 0.023234 | 0.00018587 | 0
2013-08-22 09:20 | CNR3 | SHORT RURAL |  | 1 | 225 | 225 | 0.0019579 | 8.702e-06 | 0
2013-08-15 08:46 | SLE31 | LONG RURAL |  | 23 | 425 | 9775 | 0.037852 | 8.9063e-05 | 0
2013-08-16 08:35 | BWR22 | URBAN |  | 56 | 357 | 19992 | 0.069642 | 0.00019508 | 0
2013-08-14 09:45 | RWN31 | SHORT RURAL |  | 83 | 255 | 21165 | 0.18418 | 0.00072226 | 0
2013-08-19 09:05 | SMR2 | SHORT RURAL |  | 58 | 295 | 17110 | 0.14889 | 0.00050471 | 0
2013-08-21 09:10 | WGL23 | SHORT RURAL |  | 6 | 130 | 780 | 0.0067875 | 5.2212e-05 | 0
2013-08-15 09:25 | BRA13 | URBAN |  | 124 | 295 | 36580 | 0.12743 | 0.00043195 | 0
2013-08-18 09:02 | BWR12 | URBAN |  | 142 | 115 | 16330 | 0.056885 | 0.00049465 | 0
2013-08-20 08:42 | RWT15 | URBAN |  | 104 | 441 | 45864 | 0.15977 | 0.00036228 | 0
2013-08-15 09:00 | RWN26 | SHORT RURAL |  | 59 | 225 | 13275 | 0.11552 | 0.00051342 | 0
2013-08-14 08:54 | TT1 | URBAN |  | 23 | 366 | 8418 | 0.029324 | 8.012e-05 | 0
2013-08-22 09:05 | MFA22 | LONG RURAL |  | 30 | 365 | 10950 | 0.042402 | 0.00011617 | 0
2013-08-14 08:24 | EPG12 | URBAN |  | 156 | 546 | 85176 | 0.29671 | 0.00054342 | 0
2013-08-18 08:33 | RWN24 | SHORT RURAL |  | 1025 | 446 | 457150 | 3.9781 | 0.0089195 | 0
2013-08-19 08:30 | WYK12 | SHORT RURAL |  | 62 | 236 | 14632 | 0.12733 | 0.00053952 | 0
2013-08-16 09:04 | WN6 | LONG RURAL |  | 1 | 211 | 211 | 0.00081706 | 3.8723e-06 | 0
2013-08-19 09:10 | SMR2 | SHORT RURAL |  | 61 | 311 | 18971 | 0.16509 | 0.00053082 | 0
2013-08-19 09:45 | BN1 | LONG RURAL |  | 13 | 155 | 2015 | 0.0078027 | 5.034e-05 | 0
2013-08-14 12:02 | CYN22 | URBAN |  | 47 | 110 | 5170 | 0.01801 | 0.00016372 | 0
2013-08-18 08:57 | WN4 | SHORT RURAL |  | 1811 | 404.0712 | 731773 | 6.3679 | 0.015759 | 0
2013-08-07 12:10 | CRE23 | URBAN |  | 1 | 125 | 125 | 0.00043544 | 3.4835e-06 | 0
2013-08-23 07:45 | WGL23 | SHORT RURAL |  | 7 | 40 | 280 | 0.0024366 | 6.0914e-05 | 0
2013-08-23 10:22 | FTR23 | LONG RURAL |  | 17 | 83 | 1411 | 0.0054638 | 6.5829e-05 | 0
2013-08-23 10:25 | WOTS24 | LONG RURAL |  | 3 | 85 | 255 | 0.00098744 | 1.1617e-05 | 0
2013-08-13 09:28 | BWR12 | URBAN |  | 85 | 326 | 27710 | 0.096527 | 0.0002961 | 0
2013-08-20 09:10 | OFR23 | LONG RURAL |  | 3 | 140 | 420 | 0.0016264 | 1.1617e-05 | 0
2013-08-16 12:39 | LLG11 | SHORT RURAL |  | 1 | 18 | 18 | 0.00015664 | 8.702e-06 | 0
2013-08-20 09:00 | SMR2 | SHORT RURAL |  | 279 | 438 | 122202 | 1.0634 | 0.0024278 | 0
2013-08-19 11:00 | BN1 | LONG RURAL |  | 1 | 35 | 35 | 0.00013553 | 3.8723e-06 | 0
2013-08-20 11:35 | SLE31 | LONG RURAL |  | 1 | 70 | 70 | 0.00027106 | 3.8723e-06 | 0
2013-08-19 11:55 | BN1 | LONG RURAL |  | 1 | 35 | 35 | 0.00013553 | 3.8723e-06 | 0
2013-08-19 12:45 | BN1 | LONG RURAL |  | 1 | 40 | 40 | 0.00015489 | 3.8723e-06 | 0
2013-08-19 13:20 | BN1 | LONG RURAL |  | 2 | 47 | 94 | 0.000364 | 7.7446e-06 | 0
2013-08-21 10:00 | MFA21 | LONG RURAL |  | 70 | 194 | 13580 | 0.052586 | 0.00027106 | 0
2013-08-21 09:20 | WOTS13 | LONG RURAL |  | 1 | 32 | 32 | 0.00012391 | 3.8723e-06 | 0
2013-08-20 13:30 | BWR32 | URBAN |  | 5 | 102 | 510 | 0.0017766 | 1.7417e-05 | 0
2013-08-22 09:00 | SLE31 | LONG RURAL |  | 6 | 340 | 2040 | 0.0078995 | 2.3234e-05 | 0
2013-08-21 10:45 | WOTS13 | LONG RURAL |  | 1 | 35 | 35 | 0.00013553 | 3.8723e-06 | 0
2013-08-21 10:30 | MFA21 | LONG RURAL |  | 5 | 180 | 900 | 0.0034851 | 1.9362e-05 | 0
2013-08-20 09:00 | CRE22 | URBAN |  | 197 | 225 | 44325 | 0.15441 | 0.00068625 | 0
2013-08-15 09:15 | HPK23 | URBAN |  | 1 | 17 | 17 | 5.9219e-05 | 3.4835e-06 | 0
2013-08-21 09:15 | BN1 | LONG RURAL |  | 2 | 45 | 90 | 0.00034851 | 7.7446e-06 | 0
2013-08-21 09:23 | BN1 | LONG RURAL |  | 2 | 42 | 84 | 0.00032527 | 7.7446e-06 | 0
2013-08-20 09:27 | BWR32 | URBAN |  | 6 | 128 | 768 | 0.0026753 | 2.0901e-05 | 0
2013-08-21 11:27 | BN1 | LONG RURAL |  | 1 | 38 | 38 | 0.00014715 | 3.8723e-06 | 0
2013-08-21 12:17 | BN1 | LONG RURAL |  | 1 | 103 | 103 | 0.00039885 | 3.8723e-06 | 0
2013-08-21 10:30 | BN1 | LONG RURAL |  | 2 | 50 | 100 | 0.00038723 | 7.7446e-06 | 0
2013-08-21 10:30 | BN1 | LONG RURAL |  | 2 | 40 | 80 | 0.00030979 | 7.7446e-06 | 0
2013-08-24 12:35 | MWTS14 | SHORT RURAL |  | 3 | 35 | 105 | 0.00091371 | 2.6106e-05 | 0
2013-08-24 08:45 | MWTS14 | SHORT RURAL |  | 7 | 173 | 1211 | 0.010538 | 6.0914e-05 | 0
2013-08-24 09:00 | MWTS32 | SHORT RURAL |  | 211 | 419 | 88409 | 0.76933 | 0.0018361 | 0
2013-08-24 09:40 | WGL24 | LONG RURAL |  | 59 | 391 | 23069 | 0.08933 | 0.00022847 | 0
2013-08-25 09:00 | BGE11 | SHORT RURAL |  | 164 | 441.5549 | 72415 | 0.63015 | 0.0014271 | 0
2013-08-24 08:30 | MWTS14 | SHORT RURAL |  | 7 | 375 | 2625 | 0.022843 | 6.0914e-05 | 0
2013-08-19 08:50 | FGY34 | URBAN |  | 41 | 10 | 410 | 0.0014282 | 0.00014282 | 0
2013-08-19 14:40 | FGY34 | URBAN |  | 41 | 5 | 205 | 0.00071411 | 0.00014282 | 0
2013-08-19 09:05 | FGY34 | URBAN |  | 41 | 325 | 13325 | 0.046417 | 0.00014282 | 0
2013-08-19 08:35 | BGE23 | SHORT RURAL |  | 47 | 235 | 11045 | 0.096113 | 0.00040899 | 0
2013-08-19 09:00 | HPK14 | URBAN |  | 4 | 95 | 380 | 0.0013237 | 1.3934e-05 | 0
2013-08-21 08:50 | FGY13 | SHORT RURAL |  | 53 | 240 | 12720 | 0.11069 | 0.0004612 | 0
2013-08-21 09:10 | BGE23 | SHORT RURAL |  | 222 | 401 | 89022 | 0.77467 | 0.0019318 | 0
2013-08-21 11:30 | BN1 | LONG RURAL |  | 1 | 40 | 40 | 0.00015489 | 3.8723e-06 | 0
2013-08-22 13:07 | BDL3 | SHORT RURAL |  | 2 | 108 | 216 | 0.0018796 | 1.7404e-05 | 0
2013-08-21 13:00 | BN1 | LONG RURAL |  | 2 | 60 | 120 | 0.00046468 | 7.7446e-06 | 0
2013-08-22 11:10 | BN1 | LONG RURAL |  | 1 | 40 | 40 | 0.00015489 | 3.8723e-06 | 0
2013-08-22 12:08 | BN1 | LONG RURAL |  | 1 | 47 | 47 | 0.000182 | 3.8723e-06 | 0
2013-08-22 13:45 | BN1 | LONG RURAL |  | 2 | 52 | 104 | 0.00040272 | 7.7446e-06 | 0
2013-08-22 08:45 | BDL3 | SHORT RURAL |  | 3 | 190 | 570 | 0.0049601 | 2.6106e-05 | 0
2013-08-23 09:05 | BDL3 | SHORT RURAL |  | 1 | 15 | 15 | 0.00013053 | 8.702e-06 | 0
2013-08-23 09:25 | BN1 | LONG RURAL |  | 1 | 100 | 100 | 0.00038723 | 3.8723e-06 | 0
2013-08-23 09:20 | BN1 | LONG RURAL |  | 2 | 50 | 100 | 0.00038723 | 7.7446e-06 | 0
2013-08-19 08:01 | LDL13 | SHORT RURAL |  | 67 | 206 | 13802 | 0.1201 | 0.00058303 | 0
2013-08-15 09:30 | CYN21 | URBAN |  | 62 | 330 | 20460 | 0.071272 | 0.00021598 | 0
2013-08-20 11:40 | CYN24 | URBAN |  | 120 | 96 | 11520 | 0.04013 | 0.00041802 | 0
2013-08-20 10:26 | LLG11 | SHORT RURAL |  | 2 | 41 | 82 | 0.00071356 | 1.7404e-05 | 0
2013-08-20 08:50 | WGL12 | LONG RURAL |  | 11 | 180 | 1980 | 0.0076672 | 4.2595e-05 | 0
2013-08-20 12:20 | PHM14 | LONG RURAL |  | 2 | 50 | 100 | 0.00038723 | 7.7446e-06 | 0
2013-08-19 09:30 | BRA11 | URBAN |  | 47 | 290 | 13630 | 0.04748 | 0.00016372 | 0
2013-08-20 09:00 | RWN31 | SHORT RURAL |  | 28 | 300 | 8400 | 0.073097 | 0.00024366 | 0
2013-08-22 09:00 | CYN23 | URBAN |  | 43 | 235 | 10105 | 0.035201 | 0.00014979 | 0
2013-08-23 09:10 | RWN24 | SHORT RURAL |  | 2 | 250 | 500 | 0.004351 | 1.7404e-05 | 0
2013-08-20 10:05 | FTR23 | LONG RURAL |  | 31 | 265 | 8215 | 0.031811 | 0.00012004 | 0
2013-08-26 09:22 | WO14 | URBAN |  | 57 | 265 | 15105 | 0.052618 | 0.00019856 | 0
2013-08-22 10:15 | FGY14 | URBAN |  | 168 | 345 | 57960 | 0.2019 | 0.00058523 | 0
2013-08-25 08:23 | WO14 | URBAN |  | 100 | 252 | 25200 | 0.087784 | 0.00034835 | 0
2013-08-21 09:25 | MSD4 | LONG RURAL |  | 3 | 145 | 435 | 0.0016845 | 1.1617e-05 | 0
2013-08-20 09:20 | MYT7 | LONG RURAL |  | 2 | 115 | 230 | 0.00089063 | 7.7446e-06 | 0
2013-08-20 12:35 | MYT7 | LONG RURAL |  | 3 | 45 | 135 | 0.00052276 | 1.1617e-05 | 0
2013-08-22 10:45 | BN6 | LONG RURAL |  | 1 | 225 | 225 | 0.00087127 | 3.8723e-06 | 0
2013-08-19 13:20 | DRN21 | URBAN |  | 13 | 190 | 2470 | 0.0086042 | 4.5285e-05 | 0
2013-08-22 10:25 | SMR3 | LONG RURAL |  | 10 | 60 | 600 | 0.0023234 | 3.8723e-05 | 0
2013-08-21 09:15 | CYN31 | URBAN |  | 487 | 390 | 189930 | 0.66162 | 0.0016965 | 0
2013-08-23 13:45 | BRA32 | URBAN |  | 92 | 45 | 4140 | 0.014422 | 0.00032048 | 0
2013-08-24 09:15 | WN1 | URBAN |  | 31 | 410 | 12710 | 0.044275 | 0.00010799 | 0
2013-08-16 10:30 | CLN21 | SHORT RURAL |  | 1 | 105 | 105 | 0.00091371 | 8.702e-06 | 0
2013-08-16 09:00 | CLN21 | SHORT RURAL |  | 1 | 75 | 75 | 0.00065265 | 8.702e-06 | 0
2013-08-16 11:05 | CLN21 | SHORT RURAL |  | 1 | 90 | 90 | 0.00078318 | 8.702e-06 | 0
2013-08-16 09:35 | CLN21 | SHORT RURAL |  | 2 | 85 | 170 | 0.0014793 | 1.7404e-05 | 0
2013-08-20 09:00 | RWT11 | URBAN |  | 115 | 278 | 31970 | 0.11137 | 0.0004006 | 0
2013-08-20 08:40 | ELM31 | URBAN |  | 60 | 260 | 15600 | 0.054342 | 0.00020901 | 0
2013-08-20 09:25 | ELM32 | URBAN |  | 59 | 175 | 10325 | 0.035967 | 0.00020553 | 0
2013-08-26 09:05 | LGA23 | LONG RURAL |  | 4 | 135 | 540 | 0.002091 | 1.5489e-05 | 0
2013-08-26 09:05 | WGL21 | LONG RURAL |  | 7 | 155 | 1085 | 0.0042015 | 2.7106e-05 | 0
2013-08-26 08:50 | LDL23 | LONG RURAL |  | 58 | 245 | 14210 | 0.055026 | 0.00022459 | 0
2013-08-21 08:46 | WYK12 | SHORT RURAL |  | 77 | 212 | 16324 | 0.14205 | 0.00067005 | 0
2013-08-21 09:00 | MFA22 | LONG RURAL |  | 25 | 155 | 3875 | 0.015005 | 9.6808e-05 | 0
2013-08-22 09:05 | RWN33 | URBAN |  | 71 | 345 | 24495 | 0.085328 | 0.00024733 | 0
2013-08-20 09:00 | WT13 | URBAN |  | 1 | 122 | 122 | 0.00042498 | 3.4835e-06 | 0
2013-08-21 09:15 | CYN21 | URBAN |  | 113 | 305 | 34465 | 0.12006 | 0.00039363 | 0
2013-08-21 10:05 | OFR23 | LONG RURAL |  | 75 | 303 | 22725 | 0.087998 | 0.00029042 | 0
2013-08-21 09:12 | OFR23 | LONG RURAL |  | 41 | 153 | 6273 | 0.024291 | 0.00015876 | 0
2013-08-21 12:15 | OFR23 | LONG RURAL |  | 13 | 93 | 1209 | 0.0046816 | 5.034e-05 | 0
2013-08-20 09:30 | CYN31 | URBAN |  | 437 | 285 | 124545 | 0.43385 | 0.0015223 | 0
2013-08-21 09:15 | LLG11 | SHORT RURAL |  | 27 | 102 | 2754 | 0.023965 | 0.00023495 | 0
2013-08-22 09:23 | BGE23 | SHORT RURAL |  | 58 | 171 | 9918 | 0.086306 | 0.00050471 | 0
2013-08-22 09:00 | PHM14 | LONG RURAL |  | 40 | 292 | 11680 | 0.045229 | 0.00015489 | 0
2013-08-23 09:40 | LYD13 | URBAN |  | 56 | 85 | 4760 | 0.016581 | 0.00019508 | 0
2013-08-26 13:20 | FTR21 | LONG RURAL |  | 3 | 83 | 249 | 0.00096421 | 1.1617e-05 | 0
2013-08-26 14:20 | FTR21 | LONG RURAL |  | 3 | 39 | 117 | 0.00045306 | 1.1617e-05 | 0
2013-08-27 09:30 | PHI13 | URBAN |  | 153 | 262.9869 | 40237 | 0.14016 | 0.00053297 | 0
2013-08-27 09:05 | MOE13 | SHORT RURAL |  | 64 | 260 | 16640 | 0.1448 | 0.00055693 | 0
2013-08-27 09:43 | WGL21 | LONG RURAL |  | 12 | 305 | 3660 | 0.014173 | 4.6468e-05 | 0
2013-08-28 09:15 | MYT1 | SHORT RURAL |  | 1 | 225 | 225 | 0.0019579 | 8.702e-06 | 0
2013-08-26 11:15 | WGL21 | LONG RURAL |  | 2 | 165 | 330 | 0.0012779 | 7.7446e-06 | 0
2013-08-27 09:00 | FTR12 | LONG RURAL |  | 3 | 336 | 1008 | 0.0039033 | 1.1617e-05 | 0
2013-08-28 10:02 | FTR23 | LONG RURAL |  | 21 | 73 | 1533 | 0.0059363 | 8.1319e-05 | 0
2013-08-27 09:20 | WGL21 | LONG RURAL |  | 3 | 110 | 330 | 0.0012779 | 1.1617e-05 | 0
2013-08-28 08:30 | MWTS14 | SHORT RURAL |  | 12 | 360 | 4320 | 0.037593 | 0.00010442 | 0
2013-08-28 09:10 | TGN31 | LONG RURAL |  | 8 | 270 | 2160 | 0.0083642 | 3.0979e-05 | 0
2013-08-28 09:00 | FTR12 | LONG RURAL |  | 65 | 400 | 26000 | 0.10068 | 0.0002517 | 0
2013-08-27 09:50 | MOE31 | LONG RURAL |  | 28 | 298 | 8344 | 0.032311 | 0.00010842 | 0
2013-08-29 09:15 | WGL11 | SHORT RURAL |  | 64 | 235 | 15040 | 0.13088 | 0.00055693 | 0
2013-08-29 09:00 | MYT1 | SHORT RURAL |  | 13 | 195 | 2535 | 0.022059 | 0.00011313 | 0
2013-08-27 08:32 | RWN26 | SHORT RURAL |  | 115 | 339 | 38985 | 0.33925 | 0.0010007 | 0
2013-08-29 09:15 | WGI22 | LONG RURAL |  | 64 | 360 | 23040 | 0.089218 | 0.00024783 | 0
2013-08-28 12:55 | MOE31 | LONG RURAL |  | 1 | 130 | 130 | 0.0005034 | 3.8723e-06 | 0
2013-08-28 10:09 | LGA24 | SHORT RURAL |  | 70 | 215 | 15050 | 0.13096 | 0.00060914 | 0
2013-08-28 10:00 | WOTS13 | LONG RURAL |  | 2 | 200 | 400 | 0.0015489 | 7.7446e-06 | 0
2013-08-28 09:03 | WOTS13 | LONG RURAL |  | 2 | 47 | 94 | 0.000364 | 7.7446e-06 | 0
2013-08-29 10:22 | WOTS13 | LONG RURAL |  | 2 | 193 | 386 | 0.0014947 | 7.7446e-06 | 0
2013-08-28 09:18 | MSD4 | LONG RURAL |  | 32 | 372 | 11904 | 0.046096 | 0.00012391 | 0
2013-08-29 09:15 | MFA22 | LONG RURAL |  | 122 | 395 | 48190 | 0.18661 | 0.00047242 | 0
2013-08-29 08:34 | SLE21 | SHORT RURAL |  | 44 | 364 | 16016 | 0.13937 | 0.00038289 | 0
2013-08-29 10:50 | WT13 | URBAN |  | 4 | 310 | 1240 | 0.0043195 | 1.3934e-05 | 0
2013-08-27 08:30 | WT11 | URBAN |  | 95 | 261 | 24795 | 0.086373 | 0.00033093 | 0
2013-08-26 14:00 | KMS21 | SHORT RURAL |  | 1 | 35 | 35 | 0.00030457 | 8.702e-06 | 0
2013-08-27 09:40 | TGN31 | LONG RURAL |  | 69 | 304 | 20976 | 0.081226 | 0.00026719 | 0
2013-08-27 09:30 | TGN31 | LONG RURAL |  | 2 | 130 | 260 | 0.0010068 | 7.7446e-06 | 0
2013-08-29 09:30 | LDL22 | SHORT RURAL |  | 35 | 200 | 7000 | 0.060914 | 0.00030457 | 0
2013-08-27 09:15 | NLA34 | SHORT RURAL |  | 3 | 123 | 369 | 0.003211 | 2.6106e-05 | 0
2013-08-28 09:20 | MFA34 | SHORT RURAL |  | 1 | 190 | 190 | 0.0016534 | 8.702e-06 | 0
2013-08-29 08:43 | BDL1 | LONG RURAL |  | 17 | 362 | 6154 | 0.02383 | 6.5829e-05 | 0
2013-08-27 09:30 | BDL1 | LONG RURAL |  | 13 | 373 | 4849 | 0.018777 | 5.034e-05 | 0
2013-08-29 08:48 | RWN31 | SHORT RURAL |  | 61 | 357 | 21777 | 0.1895 | 0.00053082 | 0
2013-08-29 08:30 | CYN14 | URBAN |  | 155 | 400 | 62000 | 0.21598 | 0.00053994 | 0
2013-08-27 13:30 | WGL15 | SHORT RURAL |  | 2 | 61 | 122 | 0.0010616 | 1.7404e-05 | 0
2013-08-19 12:10 | WYK12 | SHORT RURAL |  | 105 | 15 | 1575 | 0.013706 | 0.00091371 | 0
2013-08-25 09:16 | BWN11 | SHORT RURAL |  | 270 | 324 | 87480 | 0.76125 | 0.0023495 | 0
2013-08-26 12:50 | LLG12 | SHORT RURAL |  | 3 | 50 | 150 | 0.0013053 | 2.6106e-05 | 0
2013-08-27 08:55 | LLG13 | SHORT RURAL |  | 195 | 195 | 38025 | 0.33089 | 0.0016969 | 0
2013-08-27 08:42 | BDL4 | SHORT RURAL |  | 264 | 408 | 107712 | 0.93731 | 0.0022973 | 0
2013-08-27 09:30 | MOE22 | LONG RURAL |  | 43 | 140 | 6020 | 0.023311 | 0.00016651 | 0
2013-08-28 09:41 | MOE22 | LONG RURAL |  | 136 | 297 | 40392 | 0.15641 | 0.00052663 | 0
2013-08-21 09:20 | ELM13 | URBAN |  | 57 | 320 | 18240 | 0.063539 | 0.00019856 | 0
2013-08-21 11:22 | WT5 | URBAN |  | 11 | 198 | 2178 | 0.007587 | 3.8318e-05 | 0
2013-08-22 10:10 | TT9 | URBAN |  | 94 | 150 | 14100 | 0.049117 | 0.00032745 | 0
2013-08-25 09:00 | TT9 | URBAN |  | 41 | 140 | 5740 | 0.019995 | 0.00014282 | 0
2013-08-23 08:42 | DRN13 | SHORT RURAL |  | 1 | 12 | 12 | 0.00010442 | 8.702e-06 | 0
2013-08-23 10:02 | DRN13 | SHORT RURAL |  | 3 | 12 | 36 | 0.00031327 | 2.6106e-05 | 0
2013-08-23 12:30 | DRN13 | SHORT RURAL |  | 16 | 17 | 272 | 0.0023669 | 0.00013923 | 0
2013-08-27 10:45 | SMR3 | LONG RURAL |  | 1 | 215 | 215 | 0.00083255 | 3.8723e-06 | 0
2013-08-23 08:36 | DRN14 | SHORT RURAL |  | 48 | 221.4167 | 10628 | 0.092485 | 0.00041769 | 0
2013-08-22 09:06 | FGY34 | URBAN |  | 93 | 285 | 26505 | 0.09233 | 0.00032396 | 0
2013-08-25 09:27 | FGY31 | URBAN |  | 731 | 267.2312 | 195346 | 0.68048 | 0.0025464 | 0
2013-08-18 09:20 | KLO24 | SHORT RURAL |  | 62 | 220 | 13640 | 0.11869 | 0.00053952 | 0
2013-08-26 08:45 | CYN12 | URBAN |  | 314 | 270 | 84780 | 0.29533 | 0.0010938 | 0
2013-08-13 13:55 | MOE21 | SHORT RURAL |  | 1 | 20 | 20 | 0.00017404 | 8.702e-06 | 0
2013-08-30 09:30 | FTR12 | LONG RURAL |  | 2 | 105 | 210 | 0.00081319 | 7.7446e-06 | 0
2013-08-30 09:30 | WGI33 | SHORT RURAL |  | 4 | 50 | 200 | 0.0017404 | 3.4808e-05 | 0
2013-08-30 09:00 | MYT1 | SHORT RURAL |  | 7 | 280 | 1960 | 0.017056 | 6.0914e-05 | 0
2013-08-30 09:10 | MOE31 | LONG RURAL |  | 28 | 190 | 5320 | 0.020601 | 0.00010842 | 0
2013-08-30 09:10 | MWTS14 | SHORT RURAL |  | 24 | 225 | 5400 | 0.046991 | 0.00020885 | 0
2013-08-30 09:25 | LLG13 | SHORT RURAL |  | 3 | 30 | 90 | 0.00078318 | 2.6106e-05 | 0
2013-08-30 08:55 | WOTS13 | LONG RURAL |  | 1 | 105 | 105 | 0.00040659 | 3.8723e-06 | 0
2013-08-30 09:30 | MOE31 | LONG RURAL |  | 8 | 165 | 1320 | 0.0051115 | 3.0979e-05 | 0
2013-08-30 09:08 | FTR23 | LONG RURAL |  | 60 | 369 | 22140 | 0.085733 | 0.00023234 | 0
2013-08-30 09:07 | WOTS13 | LONG RURAL |  | 1 | 53 | 53 | 0.00020523 | 3.8723e-06 | 0
2013-08-30 13:30 | WGL21 | LONG RURAL |  | 13 | 100 | 1300 | 0.005034 | 5.034e-05 | 0
2013-08-27 10:00 | BN1 | LONG RURAL |  | 2 | 120 | 240 | 0.00092936 | 7.7446e-06 | 0
2013-08-27 12:50 | BN1 | LONG RURAL |  | 2 | 32 | 64 | 0.00024783 | 7.7446e-06 | 0
2013-08-27 13:50 | BN1 | LONG RURAL |  | 2 | 37 | 74 | 0.00028655 | 7.7446e-06 | 0
2013-08-28 09:30 | BN1 | LONG RURAL |  | 1 | 45 | 45 | 0.00017425 | 3.8723e-06 | 0
2013-08-28 09:10 | WOTS11 | LONG RURAL |  | 50 | 320 | 16000 | 0.061957 | 0.00019362 | 0
2013-08-21 09:35 | EPG32 | SHORT RURAL |  | 8 | 285 | 2280 | 0.01984 | 6.9616e-05 | 0
2013-08-26 08:55 | FGY34 | URBAN |  | 45 | 135 | 6075 | 0.021162 | 0.00015676 | 0
2013-08-30 08:31 | BDL8 | LONG RURAL |  | 13 | 189 | 2457 | 0.0095143 | 5.034e-05 | 0
2013-08-26 09:25 | BGE12 | SHORT RURAL |  | 51 | 120.8824 | 6165 | 0.053648 | 0.0004438 | 0
2013-08-26 11:34 | FGY34 | URBAN |  | 83 | 51 | 4233 | 0.014746 | 0.00028913 | 0
2013-08-26 12:50 | BGE22 | SHORT RURAL |  | 50 | 95.9 | 4795 | 0.041726 | 0.0004351 | 0
2013-08-27 09:40 | RWT26 | URBAN |  | 155 | 148 | 22940 | 0.079911 | 0.00053994 | 0
2013-09-04 09:15 | WN3 | LONG RURAL |  | 39 | 250 | 9750 | 0.037755 | 0.00015102 | 0
2013-08-30 11:08 | WOTS13 | LONG RURAL |  | 1 | 27 | 27 | 0.00010455 | 3.8723e-06 | 0
2013-08-28 11:00 | BRA14 | URBAN |  | 229 | 80 | 18320 | 0.063817 | 0.00079772 | 0
2013-08-27 10:15 | RWT21 | URBAN |  | 226 | 40 | 9040 | 0.031491 | 0.00078727 | 0
2013-08-28 08:01 | RWT11 | URBAN |  | 214 | 389 | 83246 | 0.28999 | 0.00074547 | 0
2013-08-28 08:30 | RWN26 | SHORT RURAL |  | 90 | 360 | 32400 | 0.28194 | 0.00078318 | 0
2013-08-28 08:50 | BRA24 | URBAN |  | 1 | 50 | 50 | 0.00017417 | 3.4835e-06 | 0
2013-08-20 08:00 | TT6 | URBAN |  | 263 | 456.2395 | 119991 | 0.41799 | 0.00091616 | 0
2013-08-21 08:30 | KLO14 | LONG RURAL |  | 5 | 465 | 2325 | 0.0090031 | 1.9362e-05 | 0
2013-08-28 09:00 | KMS1 | SHORT RURAL |  | 35 | 232 | 8120 | 0.07066 | 0.00030457 | 0
2013-08-29 09:20 | ALA01 | LONG RURAL |  | 48 | 369 | 17712 | 0.068586 | 0.00018587 | 0
2013-08-29 09:00 | SMR2 | SHORT RURAL |  | 93 | 330 | 30690 | 0.26706 | 0.00080928 | 0
2013-08-29 11:00 | SMR2 | SHORT RURAL |  | 79 | 100 | 7900 | 0.068746 | 0.00068746 | 0
2013-08-26 11:15 | MWTS14 | SHORT RURAL |  | 6 | 140 | 840 | 0.0073097 | 5.2212e-05 | 0
2013-08-26 08:35 | MWTS14 | SHORT RURAL |  | 4 | 130 | 520 | 0.004525 | 3.4808e-05 | 0
2013-08-29 09:40 | TGN31 | LONG RURAL |  | 11 | 160 | 1760 | 0.0068153 | 4.2595e-05 | 0
2013-08-30 09:07 | TGN23 | SHORT RURAL |  | 36 | 63 | 2268 | 0.019736 | 0.00031327 | 0
2013-08-30 08:55 | BDL1 | LONG RURAL |  | 21 | 163 | 3423 | 0.013255 | 8.1319e-05 | 0
2013-08-28 09:30 | BWR32 | URBAN |  | 100 | 100 | 10000 | 0.034835 | 0.00034835 | 0
2013-08-29 09:30 | ALA01 | LONG RURAL |  | 2 | 40 | 80 | 0.00030979 | 7.7446e-06 | 0
2013-08-25 08:05 | ELM34 | URBAN |  | 17 | 115 | 1955 | 0.0068102 | 5.9219e-05 | 0
2013-08-30 09:25 | DRN11 | URBAN |  | 2 | 125 | 250 | 0.00087087 | 6.967e-06 | 0
2013-08-29 09:30 | MOE14 | SHORT RURAL |  | 74 | 380.7027 | 28172 | 0.24515 | 0.00064395 | 0
2013-08-27 12:40 | CYN32 | URBAN |  | 138 | 225 | 31050 | 0.10816 | 0.00048072 | 0
2013-08-25 08:33 | RWT26 | URBAN |  | 4 | 297 | 1188 | 0.0041384 | 1.3934e-05 | 0
2013-08-19 10:25 | CNR3 | SHORT RURAL |  | 2 | 30 | 60 | 0.00052212 | 1.7404e-05 | 0
2013-08-28 09:05 | LLG11 | SHORT RURAL |  | 1 | 65 | 65 | 0.00056563 | 8.702e-06 | 0
2013-08-28 09:20 | ALA01 | LONG RURAL |  | 3 | 134 | 402 | 0.0015567 | 1.1617e-05 | 0
2013-08-28 09:16 | LLG13 | SHORT RURAL |  | 2 | 104 | 208 | 0.00181 | 1.7404e-05 | 0
2013-08-28 08:35 | PHM12 | SHORT RURAL |  | 21 | 243 | 5103 | 0.044406 | 0.00018274 | 0
2013-08-22 10:10 | TGN23 | SHORT RURAL |  | 86 | 330 | 28380 | 0.24696 | 0.00074837 | 0
2013-08-30 09:15 | MOE31 | LONG RURAL |  | 12 | 330 | 3960 | 0.015334 | 4.6468e-05 | 0
2013-08-28 11:00 | LLG13 | SHORT RURAL |  | 2 | 40 | 80 | 0.00069616 | 1.7404e-05 | 0
2013-08-28 12:15 | LLG11 | SHORT RURAL |  | 2 | 65 | 130 | 0.0011313 | 1.7404e-05 | 0
2013-08-28 08:30 | CYN21 | URBAN |  | 116 | 305 | 35380 | 0.12325 | 0.00040408 | 0
2013-08-26 10:05 | DRN12 | URBAN |  | 56 | 83 | 4648 | 0.016191 | 0.00019508 | 0
2013-08-30 09:00 | WN6 | LONG RURAL |  | 293 | 300 | 87900 | 0.34038 | 0.0011346 | 0
2013-08-28 09:50 | BN1 | LONG RURAL |  | 1 | 100 | 100 | 0.00038723 | 3.8723e-06 | 0
2013-08-28 10:30 | BN1 | LONG RURAL |  | 1 | 40 | 40 | 0.00015489 | 3.8723e-06 | 0
2013-08-28 09:15 | RWN22 | URBAN |  | 65 | 410 | 26650 | 0.092835 | 0.00022643 | 0
2013-08-28 11:52 | BN1 | LONG RURAL |  | 2 | 48 | 96 | 0.00037174 | 7.7446e-06 | 0
2013-08-29 10:07 | ALA01 | LONG RURAL |  | 1 | 55 | 55 | 0.00021298 | 3.8723e-06 | 0
2013-08-28 10:25 | BRA13 | URBAN |  | 124 | 165 | 20460 | 0.071272 | 0.00043195 | 0
2013-08-29 11:00 | ALA01 | LONG RURAL |  | 1 | 55 | 55 | 0.00021298 | 3.8723e-06 | 0
2013-08-28 09:15 | RWT22 | URBAN |  | 64 | 165 | 10560 | 0.036786 | 0.00022294 | 0
2013-08-28 09:00 | ELM11 | URBAN |  | 63 | 383 | 24129 | 0.084053 | 0.00021946 | 0
2013-08-28 12:20 | RWT22 | URBAN |  | 105 | 160 | 16800 | 0.058523 | 0.00036577 | 0
2013-08-30 09:00 | SMR2 | SHORT RURAL |  | 96 | 90 | 8640 | 0.075185 | 0.00083539 | 0
2013-08-29 10:45 | RWN26 | SHORT RURAL |  | 95 | 185 | 17575 | 0.15294 | 0.00082669 | 0
2013-08-29 08:51 | RWN22 | URBAN |  | 32 | 84 | 2688 | 0.0093636 | 0.00011147 | 0
2013-08-28 13:20 | BN1 | LONG RURAL |  | 1 | 90 | 90 | 0.00034851 | 3.8723e-06 | 0
2013-08-28 11:30 | BN1 | LONG RURAL |  | 1 | 40 | 40 | 0.00015489 | 3.8723e-06 | 0
2013-08-29 09:35 | BN1 | LONG RURAL |  | 1 | 35 | 35 | 0.00013553 | 3.8723e-06 | 0
2013-08-29 09:55 | BN1 | LONG RURAL |  | 4 | 40 | 160 | 0.00061957 | 1.5489e-05 | 0
2013-08-28 09:01 | DRN11 | URBAN |  | 5 | 234 | 1170 | 0.0040757 | 1.7417e-05 | 0
2013-08-22 11:20 | WOTS13 | LONG RURAL |  | 5 | 160 | 800 | 0.0030979 | 1.9362e-05 | 0
2013-08-29 10:55 | BN1 | LONG RURAL |  | 1 | 35 | 35 | 0.00013553 | 3.8723e-06 | 0
2013-08-30 10:00 | BN1 | LONG RURAL |  | 2 | 110 | 220 | 0.00085191 | 7.7446e-06 | 0
2013-08-29 12:00 | BN1 | LONG RURAL |  | 1 | 60 | 60 | 0.00023234 | 3.8723e-06 | 0
2013-08-27 08:33 | UWY1 | SHORT RURAL |  | 99 | 127 | 12573 | 0.10941 | 0.0008615 | 0
2013-08-29 11:40 | MSD4 | LONG RURAL |  | 5 | 50 | 250 | 0.00096808 | 1.9362e-05 | 0
2013-08-27 08:50 | HPK21 | URBAN |  | 101 | 488 | 49288 | 0.17169 | 0.00035183 | 0
2013-08-29 09:35 | FGY33 | URBAN |  | 60 | 335 | 20100 | 0.070018 | 0.00020901 | 0
2013-08-29 08:50 | BGE22 | SHORT RURAL |  | 137 | 295 | 40415 | 0.35169 | 0.0011922 | 0
2013-08-29 09:11 | BGE22 | SHORT RURAL |  | 50 | 162 | 8100 | 0.070486 | 0.0004351 | 0
2013-08-30 08:33 | LYD13 | URBAN |  | 24 | 354 | 8496 | 0.029596 | 8.3604e-05 | 0
2013-09-02 09:45 | MOE21 | SHORT RURAL |  | 10 | 345 | 3450 | 0.030022 | 8.702e-05 | 0
2013-09-02 09:30 | TGN31 | LONG RURAL |  | 32 | 110 | 3520 | 0.013631 | 0.00012391 | 0
2013-09-02 09:35 | BN1 | LONG RURAL |  | 1 | 35 | 35 | 0.00013553 | 3.8723e-06 | 0
2013-09-02 09:20 | ALA01 | LONG RURAL |  | 1 | 275 | 275 | 0.0010649 | 3.8723e-06 | 0
2013-08-31 09:00 | KMS1 | SHORT RURAL |  | 128 | 420 | 53760 | 0.46782 | 0.0011139 | 0
2013-08-29 13:00 | TT6 | URBAN |  | 179 | 185 | 33115 | 0.11536 | 0.00062354 | 0
2013-09-02 09:10 | TGN31 | LONG RURAL |  | 20 | 140 | 2800 | 0.010842 | 7.7446e-05 | 0
2013-09-01 08:33 | KMS1 | SHORT RURAL |  | 30 | 533 | 15990 | 0.13914 | 0.00026106 | 0
2013-08-30 08:30 | RWN26 | SHORT RURAL |  | 6 | 232 | 1392 | 0.012113 | 5.2212e-05 | 0
2013-08-30 11:40 | SMR8 | LONG RURAL |  | 13 | 80 | 1040 | 0.0040272 | 5.034e-05 | 0
2013-08-28 12:45 | LLG13 | SHORT RURAL |  | 1 | 35 | 35 | 0.00030457 | 8.702e-06 | 0
2013-08-29 09:30 | BWN11 | SHORT RURAL |  | 71 | 255 | 18105 | 0.15755 | 0.00061784 | 0
2013-08-30 09:45 | PHM14 | LONG RURAL |  | 11 | 275 | 3025 | 0.011714 | 4.2595e-05 | 0
2013-08-30 09:40 | LLG11 | SHORT RURAL |  | 1 | 40 | 40 | 0.00034808 | 8.702e-06 | 0
2013-08-30 09:20 | OFR23 | LONG RURAL |  | 1 | 100 | 100 | 0.00038723 | 3.8723e-06 | 0
2013-08-30 09:50 | OFR21 | SHORT RURAL |  | 2 | 75 | 150 | 0.0013053 | 1.7404e-05 | 0
2013-08-30 11:00 | LLG11 | SHORT RURAL |  | 3 | 60 | 180 | 0.0015664 | 2.6106e-05 | 0
2013-09-02 10:30 | MOE31 | LONG RURAL |  | 20 | 271 | 5420 | 0.020988 | 7.7446e-05 | 0
2013-09-03 09:00 | MOE31 | LONG RURAL |  | 24 | 350 | 8400 | 0.032527 | 9.2936e-05 | 0
2013-09-03 09:06 | WGL21 | LONG RURAL |  | 13 | 164 | 2132 | 0.0082558 | 5.034e-05 | 0
2013-09-03 09:00 | MOE32 | SHORT RURAL |  | 12 | 395 | 4740 | 0.041247 | 0.00010442 | 0
2013-09-03 08:30 | WOTS13 | LONG RURAL |  | 1 | 180 | 180 | 0.00069702 | 3.8723e-06 | 0
2013-09-05 09:10 | WN3 | LONG RURAL |  | 71 | 85 | 6035 | 0.023369 | 0.00027493 | 0
2013-09-04 08:50 | WOTS13 | LONG RURAL |  | 1 | 170 | 170 | 0.00065829 | 3.8723e-06 | 0
2013-09-03 09:50 | MOE31 | LONG RURAL |  | 1 | 280 | 280 | 0.0010842 | 3.8723e-06 | 0
2013-09-05 09:20 | MYT1 | SHORT RURAL |  | 8 | 250 | 2000 | 0.017404 | 6.9616e-05 | 0
2013-09-04 09:00 | TGN41 | LONG RURAL |  | 2 | 165 | 330 | 0.0012779 | 7.7446e-06 | 0
2013-09-04 09:20 | WGI22 | LONG RURAL |  | 109 | 415 | 45235 | 0.17516 | 0.00042208 | 0
2013-09-04 11:53 | TGN41 | LONG RURAL |  | 4 | 65 | 260 | 0.0010068 | 1.5489e-05 | 0
2013-09-03 09:20 | WGI14 | SHORT RURAL |  | 116 | 430 | 49880 | 0.43405 | 0.0010094 | 0
2013-09-03 09:00 | TGN23 | SHORT RURAL |  | 81 | 383 | 31023 | 0.26996 | 0.00070486 | 0
2013-09-03 08:45 | WYK23 | SHORT RURAL |  | 80 | 315 | 25200 | 0.21929 | 0.00069616 | 0
2013-09-03 09:00 | MYT8 | SHORT RURAL |  | 11 | 120 | 1320 | 0.011487 | 9.5722e-05 | 0
2013-09-05 08:28 | WYK11 | SHORT RURAL |  | 246 | 177.8943 | 43762 | 0.38082 | 0.0021407 | 0
2013-09-04 09:00 | LGA13 | LONG RURAL |  | 18 | 259.1667 | 4665 | 0.018064 | 6.9702e-05 | 0
2013-09-04 09:02 | LGA24 | SHORT RURAL |  | 20 | 458 | 9160 | 0.07971 | 0.00017404 | 0
2013-09-05 09:10 | WGL21 | LONG RURAL |  | 5 | 140 | 700 | 0.0027106 | 1.9362e-05 | 0
2013-09-04 08:40 | LDL13 | SHORT RURAL |  | 45 | 210 | 9450 | 0.082234 | 0.00039159 | 0
2013-09-05 08:55 | WYK11 | SHORT RURAL |  | 102 | 330 | 33660 | 0.29291 | 0.0008876 | 0
2013-09-05 09:10 | LDL14 | SHORT RURAL |  | 99 | 91 | 9009 | 0.078396 | 0.0008615 | 0
2013-09-05 09:00 | WYK23 | SHORT RURAL |  | 20 | 15 | 300 | 0.0026106 | 0.00017404 | 0
2013-09-03 08:25 | CYN14 | URBAN |  | 328 | 511.0366 | 167620 | 0.5839 | 0.0011426 | 0
2013-09-04 08:50 | CYN32 | URBAN |  | 136 | 80 | 10880 | 0.0379 | 0.00047375 | 0
2013-09-02 10:40 | BN1 | LONG RURAL |  | 3 | 25 | 75 | 0.00029042 | 1.1617e-05 | 0
2013-09-02 11:20 | BN1 | LONG RURAL |  | 3 | 90 | 270 | 0.0010455 | 1.1617e-05 | 0
2013-09-02 12:40 | BN1 | LONG RURAL |  | 1 | 45 | 45 | 0.00017425 | 3.8723e-06 | 0
2013-09-03 09:35 | BN1 | LONG RURAL |  | 1 | 45 | 45 | 0.00017425 | 3.8723e-06 | 0
2013-09-03 10:40 | BN1 | LONG RURAL |  | 1 | 50 | 50 | 0.00019362 | 3.8723e-06 | 0
2013-09-03 12:05 | BN1 | LONG RURAL |  | 1 | 50 | 50 | 0.00019362 | 3.8723e-06 | 0
2013-09-02 13:00 | TGN31 | LONG RURAL |  | 3 | 42 | 126 | 0.00048791 | 1.1617e-05 | 0
2013-09-03 09:40 | BN1 | LONG RURAL |  | 3 | 60 | 180 | 0.00069702 | 1.1617e-05 | 0
2013-09-03 11:00 | BN1 | LONG RURAL |  | 1 | 40 | 40 | 0.00015489 | 3.8723e-06 | 0
2013-09-04 13:52 | BN1 | LONG RURAL |  | 2 | 26 | 52 | 0.00020136 | 7.7446e-06 | 0
2013-09-04 10:12 | BN1 | LONG RURAL |  | 3 | 183 | 549 | 0.0021259 | 1.1617e-05 | 0
2013-09-03 12:30 | BN1 | LONG RURAL |  | 2 | 80 | 160 | 0.00061957 | 7.7446e-06 | 0
2013-09-05 08:45 | WN3 | LONG RURAL |  | 11 | 373 | 4103 | 0.015888 | 4.2595e-05 | 0
2013-09-04 09:00 | SMR2 | SHORT RURAL |  | 108 | 470 | 50760 | 0.44171 | 0.00093981 | 0
2013-09-03 09:10 | BDL1 | LONG RURAL |  | 3 | 85 | 255 | 0.00098744 | 1.1617e-05 | 0
2013-09-03 13:00 | BDL1 | LONG RURAL |  | 4 | 75 | 300 | 0.0011617 | 1.5489e-05 | 0
2013-09-04 09:00 | BDL1 | LONG RURAL |  | 5 | 150 | 750 | 0.0029042 | 1.9362e-05 | 0
2013-09-04 12:45 | BDL1 | LONG RURAL |  | 2 | 35 | 70 | 0.00027106 | 7.7446e-06 | 0
2013-09-05 09:15 | BDL1 | LONG RURAL |  | 5 | 97 | 485 | 0.0018781 | 1.9362e-05 | 0
2013-09-05 09:57 | MFA21 | LONG RURAL |  | 1 | 153 | 153 | 0.00059246 | 3.8723e-06 | 0
2013-09-03 09:30 | WGL15 | SHORT RURAL |  | 1 | 38 | 38 | 0.00033067 | 8.702e-06 | 0
2013-08-30 08:40 | PHM14 | LONG RURAL |  | 88 | 186.5341 | 16415 | 0.063564 | 0.00034076 | 0
2013-09-03 09:50 | WGL15 | SHORT RURAL |  | 1 | 75 | 75 | 0.00065265 | 8.702e-06 | 0
2013-09-03 08:37 | BGE22 | SHORT RURAL |  | 36 | 382 | 13752 | 0.11967 | 0.00031327 | 0
2013-09-03 11:20 | WGL15 | SHORT RURAL |  | 1 | 50 | 50 | 0.0004351 | 8.702e-06 | 0
2013-09-03 13:15 | WGL15 | SHORT RURAL |  | 1 | 25 | 25 | 0.00021755 | 8.702e-06 | 0
2013-09-03 08:00 | RWT15 | URBAN |  | 69 | 360 | 24840 | 0.08653 | 0.00024036 | 0
2013-09-04 09:13 | TGN31 | LONG RURAL |  | 4 | 152 | 608 | 0.0023544 | 1.5489e-05 | 0
2013-09-03 09:00 | RWN22 | URBAN |  | 117 | 190 | 22230 | 0.077438 | 0.00040757 | 0
2013-09-04 09:03 | CYN14 | URBAN |  | 199 | 204.2864 | 40653 | 0.14161 | 0.00069321 | 0
2013-09-04 09:00 | BRA32 | URBAN |  | 59 | 105 | 6195 | 0.02158 | 0.00020553 | 0
2013-08-26 07:40 | ALA01 | LONG RURAL |  | 1 | 50 | 50 | 0.00019362 | 3.8723e-06 | 0
2013-09-04 09:08 | BRA21 | URBAN |  | 88 | 257 | 22616 | 0.078782 | 0.00030655 | 0
2013-09-04 10:00 | MFA31 | SHORT RURAL |  | 12 | 140 | 1680 | 0.014619 | 0.00010442 | 0
2013-08-28 08:31 | BRA33 | URBAN |  | 77 | 459 | 35343 | 0.12312 | 0.00026823 | 0
2013-09-04 09:00 | RWN26 | SHORT RURAL |  | 4 | 164 | 656 | 0.0057085 | 3.4808e-05 | 0
2013-09-04 12:10 | BRA32 | URBAN |  | 98 | 125 | 12250 | 0.042673 | 0.00034138 | 0
2013-09-03 09:35 | NLA32 | SHORT RURAL |  | 61 | 54 | 3294 | 0.028664 | 0.00053082 | 0
2013-09-04 08:45 | BDL4 | SHORT RURAL |  | 167 | 425 | 70975 | 0.61762 | 0.0014532 | 0
2013-09-05 09:15 | BDL4 | SHORT RURAL |  | 105 | 415 | 43575 | 0.37919 | 0.00091371 | 0
2013-08-29 09:15 | WT12 | URBAN |  | 316 | 290 | 91640 | 0.31923 | 0.0011008 | 0
2013-08-31 09:03 | WGI22 | LONG RURAL |  | 5 | 262 | 1310 | 0.0050727 | 1.9362e-05 | 0
2013-09-04 08:25 | RWT14 | URBAN |  | 150 | 200 | 30000 | 0.1045 | 0.00052252 | 0
2013-09-02 10:08 | DRN12 | URBAN |  | 35 | 594.3429 | 20802 | 0.072463 | 0.00012192 | 0
2013-09-03 08:54 | ELM33 | SHORT RURAL |  | 23 | 269 | 6187 | 0.053839 | 0.00020015 | 0
2013-09-04 10:00 | RWN24 | SHORT RURAL |  | 157 | 370 | 58090 | 0.5055 | 0.0013662 | 0
2013-09-03 10:10 | RWN24 | SHORT RURAL |  | 432 | 320 | 138240 | 1.203 | 0.0037593 | 0
2013-09-03 10:38 | DRN12 | URBAN |  | 53 | 130 | 6890 | 0.024001 | 0.00018462 | 0
2013-09-05 08:43 | RWN26 | SHORT RURAL |  | 7 | 162 | 1134 | 0.009868 | 6.0914e-05 | 0
2013-09-04 09:30 | ELM33 | SHORT RURAL |  | 18 | 215 | 3870 | 0.033677 | 0.00015664 | 0
2013-09-05 09:00 | RWN26 | SHORT RURAL |  | 47 | 232 | 10904 | 0.094886 | 0.00040899 | 0
2013-09-05 09:10 | ELM33 | SHORT RURAL |  | 10 | 231.3 | 2313 | 0.020128 | 8.702e-05 | 0
2013-09-05 08:55 | EPG34 | URBAN |  | 155 | 355 | 55025 | 0.19168 | 0.00053994 | 0
2013-09-05 09:00 | ELM15 | SHORT RURAL |  | 15 | 155.4 | 2331 | 0.020284 | 0.00013053 | 0
2013-09-05 11:05 | WN3 | LONG RURAL |  | 39 | 80 | 3120 | 0.012082 | 0.00015102 | 0
2013-09-06 08:33 | RWT11 | URBAN |  | 898 | 365 | 327770 | 1.1418 | 0.0031282 | 0
2013-09-06 09:31 | MOE13 | SHORT RURAL |  | 50 | 157 | 7850 | 0.06831 | 0.0004351 | 0
2013-09-06 09:15 | LDL24 | URBAN |  | 66 | 173 | 11418 | 0.039774 | 0.00022991 | 0
2013-09-06 08:35 | LDL23 | LONG RURAL |  | 27 | 360 | 9720 | 0.037639 | 0.00010455 | 0
2013-09-06 10:39 | MOE13 | SHORT RURAL |  | 112 | 121 | 13552 | 0.11793 | 0.00097462 | 0
2013-09-05 13:30 | BDL1 | LONG RURAL |  | 1 | 70 | 70 | 0.00027106 | 3.8723e-06 | 0
2013-09-04 11:35 | BDL1 | LONG RURAL |  | 3 | 55 | 165 | 0.00063893 | 1.1617e-05 | 0
2013-09-06 09:55 | NLA34 | SHORT RURAL |  | 1 | 65 | 65 | 0.00056563 | 8.702e-06 | 0
2013-09-06 10:00 | ELM31 | URBAN |  | 177 | 355 | 62835 | 0.21888 | 0.00061658 | 0
2013-09-04 09:03 | ALA01 | LONG RURAL |  | 31 | 372 | 11532 | 0.044656 | 0.00012004 | 0
2013-09-06 09:00 | WYK12 | SHORT RURAL |  | 66 | 245 | 16170 | 0.14071 | 0.00057433 | 0
2013-09-05 09:10 | ALA01 | LONG RURAL |  | 27 | 395 | 10665 | 0.041298 | 0.00010455 | 0
2013-09-06 08:50 | ALA01 | LONG RURAL |  | 33 | 340 | 11220 | 0.043447 | 0.00012779 | 0
2013-08-22 14:30 | BN1 | LONG RURAL |  | 2 | 35 | 70 | 0.00027106 | 7.7446e-06 | 0
2013-09-06 09:00 | WN3 | LONG RURAL |  | 8 | 110 | 880 | 0.0034076 | 3.0979e-05 | 0
2013-09-02 10:10 | BN1 | LONG RURAL |  | 2 | 43 | 86 | 0.00033302 | 7.7446e-06 | 0
2013-09-04 10:30 | MOE32 | SHORT RURAL |  | 1 | 90 | 90 | 0.00078318 | 8.702e-06 | 0
2013-09-04 10:00 | MWTS14 | SHORT RURAL |  | 1 | 55 | 55 | 0.00047861 | 8.702e-06 | 0
2013-09-04 11:30 | MWTS14 | SHORT RURAL |  | 4 | 70 | 280 | 0.0024366 | 3.4808e-05 | 0
2013-09-04 13:40 | MWTS14 | SHORT RURAL |  | 3 | 57 | 171 | 0.001488 | 2.6106e-05 | 0
2013-09-06 10:10 | PHI12 | SHORT RURAL |  | 194 | 120 | 23280 | 0.20258 | 0.0016882 | 0
2013-09-04 08:30 | BDL3 | SHORT RURAL |  | 54 | 367 | 19818 | 0.17246 | 0.00046991 | 0
2013-08-28 10:15 | BWA22 | LONG RURAL |  | 60 | 205 | 12300 | 0.047629 | 0.00023234 | 0
2013-09-01 08:30 | NRN12 | URBAN |  | 4 | 144 | 576 | 0.0020065 | 1.3934e-05 | 0
2013-09-05 08:30 | MFA22 | LONG RURAL |  | 282 | 368 | 103776 | 0.40185 | 0.001092 | 0
2013-09-02 09:30 | NLA32 | SHORT RURAL |  | 40 | 165 | 6600 | 0.057433 | 0.00034808 | 0
2013-09-05 12:30 | MOE32 | SHORT RURAL |  | 4 | 30 | 120 | 0.0010442 | 3.4808e-05 | 0
2013-09-05 09:05 | WGL15 | SHORT RURAL |  | 2 | 140 | 280 | 0.0024366 | 1.7404e-05 | 0
2013-09-06 09:40 | RWT15 | URBAN |  | 112 | 95 | 10640 | 0.037064 | 0.00039015 | 0
2013-09-06 09:20 | RWN31 | SHORT RURAL |  | 8 | 245 | 1960 | 0.017056 | 6.9616e-05 | 0
2013-09-03 08:50 | HPK21 | URBAN |  | 19 | 355 | 6745 | 0.023496 | 6.6186e-05 | 0
2013-09-03 08:40 | BGE11 | SHORT RURAL |  | 32 | 95 | 3040 | 0.026454 | 0.00027846 | 0
2013-08-28 09:45 | LLG14 | SHORT RURAL |  | 5 | 120 | 600 | 0.0052212 | 4.351e-05 | 0
2013-09-07 09:00 | WGL24 | LONG RURAL |  | 59 | 275 | 16225 | 0.062828 | 0.00022847 | 0
2013-09-06 11:29 | BDL8 | LONG RURAL |  | 1 | 211 | 211 | 0.00081706 | 3.8723e-06 | 0
2013-09-06 12:00 | NLA34 | SHORT RURAL |  | 2 | 69 | 138 | 0.0012009 | 1.7404e-05 | 0
2013-09-06 11:15 | NLA34 | SHORT RURAL |  | 4 | 23 | 92 | 0.00080058 | 3.4808e-05 | 0
2013-08-22 11:10 | BN1 | LONG RURAL |  | 2 | 145 | 290 | 0.001123 | 7.7446e-06 | 0
2013-09-06 13:55 | WGI34 | SHORT RURAL |  | 2 | 64 | 128 | 0.0011139 | 1.7404e-05 | 0
2013-09-06 10:30 | RWN26 | SHORT RURAL |  | 46 | 134 | 6164 | 0.053639 | 0.00040029 | 0
2013-09-06 12:00 | FTR23 | LONG RURAL |  | 1 | 55 | 55 | 0.00021298 | 3.8723e-06 | 0
2013-09-05 09:05 | CNR3 | SHORT RURAL |  | 22 | 483 | 10626 | 0.092467 | 0.00019144 | 0
2013-09-04 09:15 | MFA31 | SHORT RURAL |  | 32 | 120 | 3840 | 0.033416 | 0.00027846 | 0
2013-09-06 08:15 | SLE31 | LONG RURAL |  | 11 | 375 | 4125 | 0.015973 | 4.2595e-05 | 0
2013-09-03 08:50 | WN3 | LONG RURAL |  | 8 | 182 | 1456 | 0.0056381 | 3.0979e-05 | 0
2013-09-04 08:50 | WN3 | LONG RURAL |  | 5 | 70 | 350 | 0.0013553 | 1.9362e-05 | 0
2013-09-04 10:30 | WN3 | LONG RURAL |  | 5 | 65 | 325 | 0.0012585 | 1.9362e-05 | 0
2013-09-04 13:00 | WN3 | LONG RURAL |  | 4 | 75 | 300 | 0.0011617 | 1.5489e-05 | 0
2013-09-05 09:23 | MSD1 | LONG RURAL |  | 7 | 192 | 1344 | 0.0052044 | 2.7106e-05 | 0
2013-09-04 09:40 | BDL2 | SHORT RURAL |  | 19 | 110 | 2090 | 0.018187 | 0.00016534 | 0
2013-09-04 10:19 | WN2 | LONG RURAL |  | 3 | 270.3333 | 811 | 0.0031404 | 1.1617e-05 | 0
2013-09-05 10:05 | UWY1 | SHORT RURAL |  | 3 | 140 | 420 | 0.0036548 | 2.6106e-05 | 0
2013-09-06 09:10 | BGE22 | SHORT RURAL |  | 48 | 170 | 8160 | 0.071008 | 0.00041769 | 0
2013-09-06 08:30 | BGE22 | SHORT RURAL |  | 110 | 200 | 22000 | 0.19144 | 0.00095722 | 0
2013-09-04 08:35 | BGE12 | SHORT RURAL |  | 139 | 380 | 52820 | 0.45964 | 0.0012096 | 0
2013-09-04 10:30 | PHM14 | LONG RURAL |  | 6 | 95 | 570 | 0.0022072 | 2.3234e-05 | 0
2013-09-07 08:30 | FGY22 | URBAN |  | 366 | 270 | 98820 | 0.34424 | 0.001275 | 0
2013-09-04 12:35 | PHM14 | LONG RURAL |  | 14 | 25 | 350 | 0.0013553 | 5.4212e-05 | 0
2013-09-08 08:12 | CYN21 | URBAN |  | 33 | 208 | 6864 | 0.023911 | 0.00011495 | 0
2013-09-08 08:00 | BWR12 | URBAN |  | 74 | 376 | 27824 | 0.096924 | 0.00025778 | 0
2013-09-08 08:45 | RWT36 | URBAN |  | 15 | 195 | 2925 | 0.010189 | 5.2252e-05 | 0
2013-09-08 09:36 | RWT26 | URBAN |  | 115 | 194 | 22310 | 0.077717 | 0.0004006 | 0
2013-09-06 09:20 | TGN31 | LONG RURAL |  | 3 | 50 | 150 | 0.00058085 | 1.1617e-05 | 0
2013-09-06 11:30 | TGN31 | LONG RURAL |  | 1 | 30 | 30 | 0.00011617 | 3.8723e-06 | 0
2013-09-06 12:33 | TGN31 | LONG RURAL |  | 2 | 42 | 84 | 0.00032527 | 7.7446e-06 | 0
2013-09-08 09:00 | MWTS32 | SHORT RURAL |  | 10 | 145 | 1450 | 0.012618 | 8.702e-05 | 0
2013-09-06 08:30 | BDL8 | LONG RURAL |  | 11 | 215 | 2365 | 0.009158 | 4.2595e-05 | 0
2013-09-06 13:30 | BDL8 | LONG RURAL |  | 30 | 75 | 2250 | 0.0087127 | 0.00011617 | 0
2013-09-07 08:50 | BGE11 | SHORT RURAL |  | 203 | 140 | 28420 | 0.24731 | 0.0017665 | 0
2013-09-06 10:22 | MOE24 | SHORT RURAL |  | 80 | 166 | 13280 | 0.11556 | 0.00069616 | 0
2013-09-06 09:31 | NLA34 | SHORT RURAL |  | 3 | 44 | 132 | 0.0011487 | 2.6106e-05 | 0
2013-09-05 11:15 | BN1 | LONG RURAL |  | 1 | 35 | 35 | 0.00013553 | 3.8723e-06 | 0
2013-09-06 08:50 | BN2 | LONG RURAL |  | 1 | 60 | 60 | 0.00023234 | 3.8723e-06 | 0
2013-09-06 10:15 | BN2 | LONG RURAL |  | 2 | 75 | 150 | 0.00058085 | 7.7446e-06 | 0
2013-09-06 11:55 | BN2 | LONG RURAL |  | 1 | 60 | 60 | 0.00023234 | 3.8723e-06 | 0
2013-09-03 09:00 | RWN31 | SHORT RURAL |  | 20 | 405 | 8100 | 0.070486 | 0.00017404 | 0
2013-09-05 09:30 | RWN24 | SHORT RURAL |  | 20 | 355 | 7100 | 0.061784 | 0.00017404 | 0
2013-09-06 08:40 | WYK12 | SHORT RURAL |  | 38 | 390 | 14820 | 0.12896 | 0.00033067 | 0
2013-09-06 08:40 | BN2 | LONG RURAL |  | 1 | 35 | 35 | 0.00013553 | 3.8723e-06 | 0
2013-09-06 09:40 | BN2 | LONG RURAL |  | 1 | 40 | 40 | 0.00015489 | 3.8723e-06 | 0
2013-09-06 10:55 | BN2 | LONG RURAL |  | 1 | 35 | 35 | 0.00013553 | 3.8723e-06 | 0
2013-09-08 08:50 | BWR23 | URBAN |  | 544 | 255 | 138720 | 0.48323 | 0.001895 | 0
2013-09-06 11:15 | OFR23 | LONG RURAL |  | 43 | 59 | 2537 | 0.0098241 | 0.00016651 | 0
2013-09-03 09:07 | EPG32 | SHORT RURAL |  | 525 | 449.52 | 235998 | 2.0536 | 0.0045685 | 0
2013-08-23 10:00 | BWN14 | SHORT RURAL |  | 1 | 120 | 120 | 0.0010442 | 8.702e-06 | 0
2013-09-09 09:45 | WGL21 | LONG RURAL |  | 2 | 210 | 420 | 0.0016264 | 7.7446e-06 | 0
2013-09-09 09:45 | FTR23 | LONG RURAL |  | 2 | 62 | 124 | 0.00048017 | 7.7446e-06 | 0
2013-09-09 09:00 | WGI34 | SHORT RURAL |  | 51 | 240 | 12240 | 0.10651 | 0.0004438 | 0
2013-09-09 09:00 | WGI14 | SHORT RURAL |  | 64 | 240 | 15360 | 0.13366 | 0.00055693 | 0
2013-09-09 09:00 | LDL11 | URBAN |  | 616 | 540 | 332640 | 1.1587 | 0.0021458 | 0
2013-09-09 09:00 | MYT2 | SHORT RURAL |  | 4 | 305 | 1220 | 0.010616 | 3.4808e-05 | 0
2013-09-09 09:45 | WN3 | LONG RURAL |  | 8 | 275 | 2200 | 0.0085191 | 3.0979e-05 | 0
2013-09-08 09:00 | SMR2 | SHORT RURAL |  | 212 | 397 | 84164 | 0.73239 | 0.0018448 | 0
2013-09-05 08:44 | PHM14 | LONG RURAL |  | 444 | 384 | 170496 | 0.66021 | 0.0017193 | 0
2013-09-08 08:35 | OFR23 | LONG RURAL |  | 7 | 215 | 1505 | 0.0058278 | 2.7106e-05 | 0
2013-09-08 07:37 | MOE23 | SHORT RURAL |  | 64 | 207.5156 | 13281 | 0.11557 | 0.00055693 | 0
2013-08-31 08:53 | KLO14 | LONG RURAL |  | 1 | 532 | 532 | 0.0020601 | 3.8723e-06 | 0
2013-09-09 09:05 | SMR8 | LONG RURAL |  | 1 | 280 | 280 | 0.0010842 | 3.8723e-06 | 0
2013-09-09 09:00 | SMR8 | LONG RURAL |  | 10 | 208 | 2080 | 0.0080544 | 3.8723e-05 | 0
2013-09-10 10:10 | WGL21 | LONG RURAL |  | 10 | 311 | 3110 | 0.012043 | 3.8723e-05 | 0
2013-09-12 10:30 | WGL21 | LONG RURAL |  | 37 | 215 | 7955 | 0.030804 | 0.00014328 | 0
2013-09-11 14:18 | MOE31 | LONG RURAL |  | 144 | 137 | 19728 | 0.076393 | 0.00055761 | 0
2013-09-10 09:05 | LGA14 | LONG RURAL |  | 29 | 199 | 5771 | 0.022347 | 0.0001123 | 0
2013-09-12 09:05 | WGI24 | URBAN |  | 1122 | 307 | 344454 | 1.1999 | 0.0039085 | 0
2013-09-10 08:50 | CYN21 | URBAN |  | 87 | 242 | 21054 | 0.073341 | 0.00030306 | 0
2013-09-10 07:02 | KLO11 | URBAN |  | 1 | 353 | 353 | 0.0012297 | 3.4835e-06 | 0
2013-09-12 09:16 | WGI22 | LONG RURAL |  | 64 | 309 | 19776 | 0.076579 | 0.00024783 | 0
2013-09-10 09:35 | BN3 | SHORT RURAL |  | 34 | 748.8235 | 25460 | 0.22155 | 0.00029587 | 0
2013-09-11 09:00 | FTR12 | LONG RURAL |  | 65 | 425 | 27625 | 0.10697 | 0.0002517 | 0
2013-09-11 09:28 | FTR12 | LONG RURAL |  | 378 | 266 | 100548 | 0.38935 | 0.0014637 | 0
2013-09-11 08:30 | LDL13 | SHORT RURAL |  | 205 | 350 | 71750 | 0.62437 | 0.0017839 | 0
2013-09-11 08:31 | LDL24 | URBAN |  | 321 | 371 | 119091 | 0.41485 | 0.0011182 | 0
2013-09-12 08:35 | LDL24 | URBAN |  | 170 | 350 | 59500 | 0.20727 | 0.00059219 | 0
2013-09-09 13:15 | MYT7 | LONG RURAL |  | 1 | 70 | 70 | 0.00027106 | 3.8723e-06 | 0
2013-09-11 09:42 | MWTS31 | SHORT RURAL |  | 4 | 21 | 84 | 0.00073097 | 3.4808e-05 | 0
2013-09-10 08:30 | LDL21 | SHORT RURAL |  | 10 | 445 | 4450 | 0.038724 | 8.702e-05 | 0
2013-09-11 09:35 | MBY12 | SHORT RURAL |  | 3 | 40 | 120 | 0.0010442 | 2.6106e-05 | 0
2013-09-10 09:40 | MBY12 | SHORT RURAL |  | 1 | 45 | 45 | 0.00039159 | 8.702e-06 | 0
2013-09-10 09:10 | WOTS11 | LONG RURAL |  | 1 | 190 | 190 | 0.00073574 | 3.8723e-06 | 0
2013-09-11 08:35 | LDL13 | SHORT RURAL |  | 91 | 180 | 16380 | 0.14254 | 0.00079188 | 0
2013-09-11 08:52 | WOTS13 | LONG RURAL |  | 2 | 38 | 76 | 0.0002943 | 7.7446e-06 | 0
2013-09-11 10:33 | WOTS13 | LONG RURAL |  | 1 | 37 | 37 | 0.00014328 | 3.8723e-06 | 0
2013-09-11 09:05 | WGL24 | LONG RURAL |  | 59 | 252 | 14868 | 0.057574 | 0.00022847 | 0
2013-09-11 09:40 | MFA31 | SHORT RURAL |  | 75 | 160 | 12000 | 0.10442 | 0.00065265 | 0
2013-09-12 09:30 | ELM33 | SHORT RURAL |  | 62 | 326.6129 | 20250 | 0.17621 | 0.00053952 | 0
2013-09-10 09:00 | WN5 | LONG RURAL |  | 2 | 200 | 400 | 0.0015489 | 7.7446e-06 | 0
2013-09-11 09:00 | BN2 | LONG RURAL |  | 23 | 389.5652 | 8960 | 0.034696 | 8.9063e-05 | 0
2013-09-12 08:30 | WOTS11 | LONG RURAL |  | 66 | 290.1061 | 19147 | 0.074143 | 0.00025557 | 0
2013-09-10 09:10 | TGN31 | LONG RURAL |  | 3 | 50 | 150 | 0.00058085 | 1.1617e-05 | 0
2013-09-10 10:50 | TGN31 | LONG RURAL |  | 1 | 30 | 30 | 0.00011617 | 3.8723e-06 | 0
2013-09-10 11:50 | TGN31 | LONG RURAL |  | 2 | 30 | 60 | 0.00023234 | 7.7446e-06 | 0
2013-09-11 08:15 | MOE32 | SHORT RURAL |  | 2 | 280 | 560 | 0.0048731 | 1.7404e-05 | 0
2013-09-10 08:38 | RWT15 | URBAN |  | 879 | 356 | 312924 | 1.0901 | 0.003062 | 0
2013-09-10 09:10 | TGN31 | LONG RURAL |  | 1 | 35 | 35 | 0.00013553 | 3.8723e-06 | 0
2013-09-10 10:40 | TGN31 | LONG RURAL |  | 4 | 35 | 140 | 0.00054212 | 1.5489e-05 | 0
2013-09-10 11:25 | TGN31 | LONG RURAL |  | 4 | 25 | 100 | 0.00038723 | 1.5489e-05 | 0
2013-09-11 09:00 | TGN31 | LONG RURAL |  | 1 | 165 | 165 | 0.00063893 | 3.8723e-06 | 0
2013-09-11 12:00 | TGN31 | LONG RURAL |  | 1 | 25 | 25 | 9.6808e-05 | 3.8723e-06 | 0
2013-09-11 13:30 | TGN31 | LONG RURAL |  | 2 | 34 | 68 | 0.00026332 | 7.7446e-06 | 0
2013-09-09 11:20 | SMR8 | LONG RURAL |  | 1 | 50 | 50 | 0.00019362 | 3.8723e-06 | 0
2013-09-04 08:30 | ELM34 | URBAN |  | 238 | 420 | 99960 | 0.34821 | 0.00082907 | 0
2013-09-11 09:39 | DRN12 | URBAN |  | 49 | 289 | 14161 | 0.04933 | 0.00017069 | 0
2013-09-12 09:37 | ELM33 | SHORT RURAL |  | 14 | 227 | 3178 | 0.027655 | 0.00012183 | 0
2013-09-03 08:35 | BDL3 | SHORT RURAL |  | 1 | 163 | 163 | 0.0014184 | 8.702e-06 | 0
2013-09-09 13:15 | BDL6 | SHORT RURAL |  | 1 | 25 | 25 | 0.00021755 | 8.702e-06 | 0
2013-09-10 08:10 | SLE31 | LONG RURAL |  | 4 | 140 | 560 | 0.0021685 | 1.5489e-05 | 0
2013-09-10 08:50 | BWR13 | SHORT RURAL |  | 37 | 115 | 4255 | 0.037027 | 0.00032197 | 0
2013-09-11 09:00 | CYN23 | URBAN |  | 143 | 327 | 46761 | 0.16289 | 0.00049814 | 0
2013-09-09 09:10 | MOE22 | LONG RURAL |  | 2 | 55 | 110 | 0.00042595 | 7.7446e-06 | 0
2013-09-10 14:15 | MOE22 | LONG RURAL |  | 1 | 75 | 75 | 0.00029042 | 3.8723e-06 | 0
2013-09-10 09:30 | MOE22 | LONG RURAL |  | 4 | 115 | 460 | 0.0017813 | 1.5489e-05 | 0
2013-09-12 10:05 | KLK1 | SHORT RURAL |  | 1 | 85 | 85 | 0.00073967 | 8.702e-06 | 0
2013-09-10 10:55 | MOE22 | LONG RURAL |  | 1 | 45 | 45 | 0.00017425 | 3.8723e-06 | 0
2013-09-11 09:30 | WGL15 | SHORT RURAL |  | 17 | 308 | 5236 | 0.045564 | 0.00014793 | 0
2013-09-08 08:00 | FGY21 | SHORT RURAL |  | 4 | 550 | 2200 | 0.019144 | 3.4808e-05 | 0
2013-09-09 09:05 | MDG1 | SHORT RURAL |  | 148 | 409 | 60532 | 0.52675 | 0.0012879 | 0
2013-09-09 09:35 | BGE11 | SHORT RURAL |  | 39 | 335 | 13065 | 0.11369 | 0.00033938 | 0
2013-09-13 09:00 | MBY12 | SHORT RURAL |  | 84 | 235 | 19740 | 0.17178 | 0.00073097 | 0
2013-09-13 09:00 | FTR23 | LONG RURAL |  | 60 | 360 | 21600 | 0.083642 | 0.00023234 | 0
2013-09-13 08:30 | DRN12 | URBAN |  | 11 | 405 | 4455 | 0.015519 | 3.8318e-05 | 0
2013-09-12 12:00 | KLK1 | SHORT RURAL |  | 26 | 56 | 1456 | 0.01267 | 0.00022625 | 0
2013-09-13 09:00 | MYT7 | LONG RURAL |  | 57 | 85 | 4845 | 0.018761 | 0.00022072 | 0
2013-09-13 09:00 | WN3 | LONG RURAL |  | 7 | 285 | 1995 | 0.0077253 | 2.7106e-05 | 0
2013-09-13 09:58 | DRN14 | SHORT RURAL |  | 49 | 215 | 10535 | 0.091675 | 0.0004264 | 0
2013-09-13 09:10 | RWN31 | SHORT RURAL |  | 29 | 235 | 6815 | 0.059304 | 0.00025236 | 0
2013-09-13 09:15 | MOE21 | SHORT RURAL |  | 4 | 255 | 1020 | 0.008876 | 3.4808e-05 | 0
2013-09-05 09:00 | SMR8 | LONG RURAL |  | 4 | 315 | 1260 | 0.0048791 | 1.5489e-05 | 0
2013-09-09 14:05 | SMR8 | LONG RURAL |  | 1 | 60 | 60 | 0.00023234 | 3.8723e-06 | 0
2013-09-09 09:00 | SMR8 | LONG RURAL |  | 2 | 75 | 150 | 0.00058085 | 7.7446e-06 | 0
2013-09-09 13:17 | SMR8 | LONG RURAL |  | 2 | 43 | 86 | 0.00033302 | 7.7446e-06 | 0
2013-09-10 09:30 | SMR8 | LONG RURAL |  | 3 | 315 | 945 | 0.0036593 | 1.1617e-05 | 0
2013-09-10 09:20 | SMR8 | LONG RURAL |  | 2 | 375 | 750 | 0.0029042 | 7.7446e-06 | 0
2013-09-11 09:07 | SMR8 | LONG RURAL |  | 7 | 348 | 2436 | 0.009433 | 2.7106e-05 | 0
2013-09-05 12:45 | BN3 | SHORT RURAL |  | 2 | 46 | 92 | 0.00080058 | 1.7404e-05 | 0
2013-09-04 13:05 | BDL3 | SHORT RURAL |  | 68 | 40 | 2720 | 0.023669 | 0.00059173 | 0
2013-09-13 09:07 | TGN31 | LONG RURAL |  | 2 | 58 | 116 | 0.00044919 | 7.7446e-06 | 0
2013-09-05 11:08 | BN3 | SHORT RURAL |  | 1 | 73 | 73 | 0.00063524 | 8.702e-06 | 0
2013-09-10 09:50 | BDL8 | LONG RURAL |  | 9 | 360 | 3240 | 0.012546 | 3.4851e-05 | 0
2013-09-11 08:50 | BDL6 | SHORT RURAL |  | 1 | 310 | 310 | 0.0026976 | 8.702e-06 | 0
2013-09-11 12:00 | CNR2 | SHORT RURAL |  | 3 | 85 | 255 | 0.002219 | 2.6106e-05 | 0
2013-09-10 09:00 | HPK22 | URBAN |  | 12 | 446 | 5352 | 0.018644 | 4.1802e-05 | 0
2013-09-11 08:50 | SLE31 | LONG RURAL |  | 151 | 355 | 53605 | 0.20758 | 0.00058472 | 0
2013-09-11 08:55 | BGE22 | SHORT RURAL |  | 54 | 320 | 17280 | 0.15037 | 0.00046991 | 0
2013-09-04 13:05 | BWN13 | URBAN |  | 114 | 125 | 14250 | 0.04964 | 0.00039712 | 0
2013-09-11 08:50 | BGE11 | SHORT RURAL |  | 23 | 285 | 6555 | 0.057041 | 0.00020015 | 0
2013-09-11 08:32 | BGE12 | SHORT RURAL |  | 425 | 264 | 112200 | 0.97636 | 0.0036983 | 0
2013-09-05 10:24 | BN1 | LONG RURAL |  | 3 | 41 | 123 | 0.00047629 | 1.1617e-05 | 0
2013-09-05 14:14 | BN3 | SHORT RURAL |  | 1 | 66 | 66 | 0.00057433 | 8.702e-06 | 0
2013-09-11 08:50 | FGY34 | URBAN |  | 57 | 338 | 19266 | 0.067113 | 0.00019856 | 0
2013-09-11 10:10 | FGY13 | SHORT RURAL |  | 54 | 122 | 6588 | 0.057329 | 0.00046991 | 0
2013-09-09 09:20 | PHM14 | LONG RURAL |  | 15 | 215 | 3225 | 0.012488 | 5.8085e-05 | 0
2013-09-09 09:10 | LLG11 | SHORT RURAL |  | 2 | 40 | 80 | 0.00069616 | 1.7404e-05 | 0
2013-09-09 11:25 | LLG12 | SHORT RURAL |  | 1 | 75 | 75 | 0.00065265 | 8.702e-06 | 0
2013-09-10 09:03 | WGL12 | LONG RURAL |  | 336 | 204.6369 | 68758 | 0.26625 | 0.0013011 | 0
2013-09-10 09:10 | LLG12 | SHORT RURAL |  | 5 | 80 | 400 | 0.0034808 | 4.351e-05 | 0
2013-09-13 10:10 | WGI31 | SHORT RURAL |  | 4 | 160 | 640 | 0.0055693 | 3.4808e-05 | 0
2013-09-13 11:00 | MYT7 | LONG RURAL |  | 55 | 155 | 8525 | 0.033011 | 0.00021298 | 0
2013-09-13 11:00 | TGN31 | LONG RURAL |  | 1 | 53 | 53 | 0.00020523 | 3.8723e-06 | 0
2013-09-13 12:55 | TGN31 | LONG RURAL |  | 1 | 38 | 38 | 0.00014715 | 3.8723e-06 | 0
2013-09-12 09:25 | SMR8 | LONG RURAL |  | 1 | 275 | 275 | 0.0010649 | 3.8723e-06 | 0
2013-09-12 09:22 | SMR8 | LONG RURAL |  | 1 | 38 | 38 | 0.00014715 | 3.8723e-06 | 0
2013-09-13 09:00 | SMR8 | LONG RURAL |  | 1 | 300 | 300 | 0.0011617 | 3.8723e-06 | 0
2013-09-11 09:45 | CNR2 | SHORT RURAL |  | 6 | 90 | 540 | 0.0046991 | 5.2212e-05 | 0
2013-09-11 14:02 | LYD14 | SHORT RURAL |  | 28 | 53 | 1484 | 0.012914 | 0.00024366 | 0
2013-09-11 09:55 | NLA31 | LONG RURAL |  | 22 | 125 | 2750 | 0.010649 | 8.5191e-05 | 0
2013-09-11 10:15 | NLA31 | LONG RURAL |  | 20 | 180 | 3600 | 0.01394 | 7.7446e-05 | 0
2013-09-10 09:54 | WN2 | LONG RURAL |  | 2 | 61 | 122 | 0.00047242 | 7.7446e-06 | 0
2013-09-11 09:55 | BDL1 | LONG RURAL |  | 7 | 232 | 1624 | 0.0062886 | 2.7106e-05 | 0
2013-09-10 09:55 | WN2 | LONG RURAL |  | 1 | 34 | 34 | 0.00013166 | 3.8723e-06 | 0
2013-09-13 09:30 | DRN11 | URBAN |  | 2 | 270 | 540 | 0.0018811 | 6.967e-06 | 0
2013-09-05 08:00 | ELM31 | URBAN |  | 118 | 415 | 48970 | 0.17059 | 0.00041105 | 0
2013-09-10 08:35 | BN2 | LONG RURAL |  | 1 | 55 | 55 | 0.00021298 | 3.8723e-06 | 0
2013-09-10 09:04 | BN6 | LONG RURAL |  | 102 | 213 | 21726 | 0.08413 | 0.00039498 | 0
2013-09-10 10:30 | BN2 | LONG RURAL |  | 1 | 25 | 25 | 9.6808e-05 | 3.8723e-06 | 0
2013-09-10 11:20 | BN2 | LONG RURAL |  | 2 | 55 | 110 | 0.00042595 | 7.7446e-06 | 0
2013-09-10 11:00 | WN2 | LONG RURAL |  | 2 | 30 | 60 | 0.00023234 | 7.7446e-06 | 0
2013-09-10 11:45 | WN2 | LONG RURAL |  | 1 | 55 | 55 | 0.00021298 | 3.8723e-06 | 0
2013-09-10 13:00 | WN2 | LONG RURAL |  | 1 | 30 | 30 | 0.00011617 | 3.8723e-06 | 0
2013-09-11 08:30 | BN3 | SHORT RURAL |  | 2 | 152 | 304 | 0.0026454 | 1.7404e-05 | 0
2013-09-12 08:30 | WN3 | LONG RURAL |  | 51 | 435 | 22185 | 0.085907 | 0.00019749 | 0
2013-09-10 11:10 | RWT11 | URBAN |  | 90 | 135 | 12150 | 0.042324 | 0.00031351 | 0
2013-09-11 08:45 | RWN22 | URBAN |  | 429 | 345 | 148005 | 0.51557 | 0.0014944 | 0
2013-09-11 08:30 | RWT15 | URBAN |  | 221 | 349.3846 | 77214 | 0.26897 | 0.00076985 | 0
2013-09-15 09:00 | WGL13 | SHORT RURAL |  | 535 | 308.7738 | 165194 | 1.4375 | 0.0046556 | 0
2013-09-15 07:05 | CYN32 | URBAN |  | 230 | 370 | 85100 | 0.29644 | 0.0008012 | 0
2013-09-15 09:00 | MWTS11 | SHORT RURAL |  | 52 | 270 | 14040 | 0.12218 | 0.0004525 | 0
2013-09-15 08:54 | FGY22 | URBAN |  | 191 | 628 | 119948 | 0.41784 | 0.00066535 | 0
2013-09-10 10:50 | SLE31 | LONG RURAL |  | 1 | 275 | 275 | 0.0010649 | 3.8723e-06 | 0
2013-09-10 11:05 | LLG12 | SHORT RURAL |  | 1 | 55 | 55 | 0.00047861 | 8.702e-06 | 0
2013-09-11 09:26 | PHM14 | LONG RURAL |  | 4 | 33 | 132 | 0.00051115 | 1.5489e-05 | 0
2013-09-13 09:02 | LLG11 | SHORT RURAL |  | 34 | 253 | 8602 | 0.074854 | 0.00029587 | 0
2013-09-11 09:00 | RWN26 | SHORT RURAL |  | 37 | 340 | 12580 | 0.10947 | 0.00032197 | 0
2013-09-12 09:36 | RWT15 | URBAN |  | 580 | 239 | 138620 | 0.48288 | 0.0020204 | 0
2013-09-12 13:20 | ELM32 | URBAN |  | 131 | 120 | 15720 | 0.05476 | 0.00045634 | 0
2013-09-13 12:30 | BWR32 | URBAN |  | 52 | 165 | 8580 | 0.029888 | 0.00018114 | 0
2013-09-14 08:35 | BWR24 | URBAN |  | 1 | 230 | 230 | 0.0008012 | 3.4835e-06 | 0
2013-09-16 09:31 | WGL24 | LONG RURAL |  | 81 | 169 | 13689 | 0.053008 | 0.00031366 | 0
2013-09-16 09:00 | TGN31 | LONG RURAL |  | 38 | 285 | 10830 | 0.041937 | 0.00014715 | 0
2013-09-16 09:00 | MOE21 | SHORT RURAL |  | 12 | 340 | 4080 | 0.035504 | 0.00010442 | 0
2013-09-16 10:05 | WN2 | LONG RURAL |  | 1 | 173 | 173 | 0.00066991 | 3.8723e-06 | 0
2013-09-16 10:15 | SMR8 | LONG RURAL |  | 4 | 195 | 780 | 0.0030204 | 1.5489e-05 | 0
2013-09-16 09:55 | SMR8 | LONG RURAL |  | 1 | 175 | 175 | 0.00067766 | 3.8723e-06 | 0
2013-09-12 09:25 | DRN12 | URBAN |  | 23 | 150 | 3450 | 0.012018 | 8.012e-05 | 0
2013-09-12 09:30 | LLG11 | SHORT RURAL |  | 21 | 236 | 4956 | 0.043127 | 0.00018274 | 0
2013-09-12 09:35 | PHM14 | LONG RURAL |  | 9 | 342 | 3078 | 0.011919 | 3.4851e-05 | 0
2013-09-12 09:30 | BDL1 | LONG RURAL |  | 18 | 110 | 1980 | 0.0076672 | 6.9702e-05 | 0
2013-09-12 09:10 | MFA34 | SHORT RURAL |  | 85 | 298 | 25330 | 0.22042 | 0.00073967 | 0
2013-09-13 08:40 | BDL1 | LONG RURAL |  | 2 | 230 | 460 | 0.0017813 | 7.7446e-06 | 0
2013-09-13 10:00 | BDL1 | LONG RURAL |  | 3 | 210 | 630 | 0.0024396 | 1.1617e-05 | 0
2013-09-15 08:25 | BWR32 | URBAN |  | 159 | 115 | 18285 | 0.063695 | 0.00055387 | 0
2013-09-15 08:30 | BRA12 | URBAN |  | 1 | 180 | 180 | 0.00062703 | 3.4835e-06 | 0
2013-09-22 08:11 | BRA12 | URBAN |  | 121 | 419 | 50699 | 0.17661 | 0.0004215 | 0
2013-09-10 09:40 | ELM15 | SHORT RURAL |  | 6 | 190 | 1140 | 0.0099202 | 5.2212e-05 | 0
2013-09-18 09:00 | MYT7 | LONG RURAL |  | 9 | 115 | 1035 | 0.0040078 | 3.4851e-05 | 0
2013-09-18 09:00 | MYT2 | SHORT RURAL |  | 154 | 135 | 20790 | 0.18091 | 0.0013401 | 0
2013-09-17 09:00 | LGA24 | SHORT RURAL |  | 20 | 430 | 8600 | 0.074837 | 0.00017404 | 0
2013-09-19 09:00 | MYT7 | LONG RURAL |  | 52 | 220 | 11440 | 0.044299 | 0.00020136 | 0
2013-09-18 09:00 | LGA22 | SHORT RURAL |  | 61 | 175 | 10675 | 0.092894 | 0.00053082 | 0
2013-09-19 09:23 | LGA11 | LONG RURAL |  | 18 | 57 | 1026 | 0.003973 | 6.9702e-05 | 0
2013-09-19 09:32 | FTR21 | LONG RURAL |  | 7 | 110 | 770 | 0.0029817 | 2.7106e-05 | 0
2013-09-19 08:08 | CYN31 | URBAN |  | 422 | 372 | 156984 | 0.54685 | 0.00147 | 0
2013-09-17 10:15 | WYK24 | SHORT RURAL |  | 1 | 115 | 115 | 0.0010007 | 8.702e-06 | 0
2013-09-17 08:15 | LDL11 | URBAN |  | 1 | 345 | 345 | 0.0012018 | 3.4835e-06 | 0
2013-09-18 09:10 | WGL15 | SHORT RURAL |  | 151 | 364 | 54964 | 0.4783 | 0.001314 | 0
2013-09-17 08:40 | WYK24 | SHORT RURAL |  | 66 | 355 | 23430 | 0.20389 | 0.00057433 | 0
2013-09-19 09:00 | WGL24 | LONG RURAL |  | 18 | 175 | 3150 | 0.012198 | 6.9702e-05 | 0
2013-09-17 09:20 | WGI31 | SHORT RURAL |  | 20 | 320 | 6400 | 0.055693 | 0.00017404 | 0
2013-09-18 08:33 | LDL13 | SHORT RURAL |  | 82 | 446 | 36572 | 0.31825 | 0.00071356 | 0
2013-09-16 11:15 | MOE21 | SHORT RURAL |  | 5 | 75 | 375 | 0.0032632 | 4.351e-05 | 0
2013-09-18 07:51 | CYN32 | URBAN |  | 174 | 422.9253 | 73589 | 0.25635 | 0.00060613 | 0
2013-09-17 08:30 | LDL11 | URBAN |  | 748 | 330 | 246840 | 0.85986 | 0.0026056 | 0
2013-09-17 09:10 | WGL23 | SHORT RURAL |  | 8 | 40 | 320 | 0.0027846 | 6.9616e-05 | 0
2013-09-18 08:30 | MWTS14 | SHORT RURAL |  | 24 | 85 | 2040 | 0.017752 | 0.00020885 | 0
2013-09-18 10:45 | MWTS14 | SHORT RURAL |  | 18 | 260 | 4680 | 0.040725 | 0.00015664 | 0
2013-09-19 09:18 | LDL23 | LONG RURAL |  | 43 | 222 | 9546 | 0.036965 | 0.00016651 | 0
2013-09-17 11:05 | WGL23 | SHORT RURAL |  | 1 | 30 | 30 | 0.00026106 | 8.702e-06 | 0
2013-09-17 12:05 | WGL23 | SHORT RURAL |  | 1 | 75 | 75 | 0.00065265 | 8.702e-06 | 0
2013-09-18 08:30 | WGL24 | LONG RURAL |  | 2 | 40 | 80 | 0.00030979 | 7.7446e-06 | 0
2013-09-19 10:10 | MOE22 | LONG RURAL |  | 1 | 110 | 110 | 0.00042595 | 3.8723e-06 | 0
2013-09-17 11:45 | MOE22 | LONG RURAL |  | 1 | 40 | 40 | 0.00015489 | 3.8723e-06 | 0
2013-09-17 08:38 | PHM14 | LONG RURAL |  | 75 | 366 | 27450 | 0.1063 | 0.00029042 | 0
2013-09-17 12:40 | WGL15 | SHORT RURAL |  | 1 | 35 | 35 | 0.00030457 | 8.702e-06 | 0
2013-09-17 11:45 | BN2 | LONG RURAL |  | 1 | 70 | 70 | 0.00027106 | 3.8723e-06 | 0
2013-09-18 09:50 | BN2 | LONG RURAL |  | 1 | 40 | 40 | 0.00015489 | 3.8723e-06 | 0
2013-09-18 08:51 | BN2 | LONG RURAL |  | 1 | 29 | 29 | 0.0001123 | 3.8723e-06 | 0
2013-09-18 11:00 | BN2 | LONG RURAL |  | 1 | 25 | 25 | 9.6808e-05 | 3.8723e-06 | 0
2013-09-17 09:35 | BN2 | LONG RURAL |  | 3 | 55 | 165 | 0.00063893 | 1.1617e-05 | 0
2013-09-18 09:10 | BN2 | LONG RURAL |  | 1 | 40 | 40 | 0.00015489 | 3.8723e-06 | 0
2013-09-18 10:00 | BN2 | LONG RURAL |  | 3 | 40 | 120 | 0.00046468 | 1.1617e-05 | 0
2013-09-18 12:10 | BN2 | LONG RURAL |  | 2 | 95 | 190 | 0.00073574 | 7.7446e-06 | 0
2013-09-19 12:40 | BRT21 | SHORT RURAL |  | 1 | 40 | 40 | 0.00034808 | 8.702e-06 | 0
2013-09-17 11:15 | BN2 | LONG RURAL |  | 2 | 120 | 240 | 0.00092936 | 7.7446e-06 | 0
2013-09-18 09:16 | ELM33 | SHORT RURAL |  | 38 | 251 | 9538 | 0.082999 | 0.00033067 | 0
2013-09-17 10:10 | BWN11 | SHORT RURAL |  | 139 | 130 | 18070 | 0.15724 | 0.0012096 | 0
2013-09-18 08:01 | RWT15 | URBAN |  | 137 | 464 | 63568 | 0.22144 | 0.00047724 | 0
2013-09-18 08:55 | RWT22 | URBAN |  | 166 | 339 | 56274 | 0.19603 | 0.00057826 | 0
2013-09-10 08:30 | ELM11 | URBAN |  | 26 | 180 | 4680 | 0.016303 | 9.0571e-05 | 0
2013-09-12 08:40 | CNR2 | SHORT RURAL |  | 218 | 426 | 92868 | 0.80813 | 0.001897 | 0
2013-09-13 08:30 | CNR2 | SHORT RURAL |  | 4 | 225 | 900 | 0.0078318 | 3.4808e-05 | 0
2013-09-13 08:30 | BDL8 | LONG RURAL |  | 6 | 340 | 2040 | 0.0078995 | 2.3234e-05 | 0
2013-09-13 09:00 | MFA22 | LONG RURAL |  | 13 | 330 | 4290 | 0.016612 | 5.034e-05 | 0
2013-09-13 10:30 | MFA22 | LONG RURAL |  | 10 | 180 | 1800 | 0.0069702 | 3.8723e-05 | 0
2013-09-14 08:40 | CNR2 | SHORT RURAL |  | 45 | 220 | 9900 | 0.08615 | 0.00039159 | 0
2013-09-14 13:15 | CNR2 | SHORT RURAL |  | 22 | 65 | 1430 | 0.012444 | 0.00019144 | 0
2013-09-10 10:10 | BDL6 | SHORT RURAL |  | 1 | 60 | 60 | 0.00052212 | 8.702e-06 | 0
2013-09-13 09:10 | WN3 | LONG RURAL |  | 3 | 337 | 1011 | 0.0039149 | 1.1617e-05 | 0
2013-09-14 15:10 | CNR2 | SHORT RURAL |  | 58 | 74 | 4292 | 0.037349 | 0.00050471 | 0
2013-09-17 10:30 | WN2 | LONG RURAL |  | 2 | 240 | 480 | 0.0018587 | 7.7446e-06 | 0
2013-09-15 08:50 | BDL8 | LONG RURAL |  | 3 | 165 | 495 | 0.0019168 | 1.1617e-05 | 0
2013-09-14 09:00 | SLE31 | LONG RURAL |  | 9 | 400 | 3600 | 0.01394 | 3.4851e-05 | 0
2013-09-15 14:20 | NLA34 | SHORT RURAL |  | 5 | 35 | 175 | 0.0015228 | 4.351e-05 | 0
2013-09-15 12:05 | BDL8 | LONG RURAL |  | 2 | 35 | 70 | 0.00027106 | 7.7446e-06 | 0
2013-09-17 14:25 | BN2 | LONG RURAL |  | 1 | 40 | 40 | 0.00015489 | 3.8723e-06 | 0
2013-09-20 09:00 | MYT7 | LONG RURAL |  | 51 | 231 | 11781 | 0.04562 | 0.00019749 | 0
2013-09-20 09:03 | LGA11 | LONG RURAL |  | 27 | 147 | 3969 | 0.015369 | 0.00010455 | 0
2013-09-20 10:10 | TGN31 | LONG RURAL |  | 2 | 52 | 104 | 0.00040272 | 7.7446e-06 | 0
2013-09-20 09:00 | MOE22 | LONG RURAL |  | 3 | 385 | 1155 | 0.0044725 | 1.1617e-05 | 0
2013-09-19 13:10 | TGN41 | LONG RURAL |  | 40 | 83 | 3320 | 0.012856 | 0.00015489 | 0
2013-09-20 09:00 | BRT21 | SHORT RURAL |  | 12 | 275 | 3300 | 0.028717 | 0.00010442 | 0
2013-09-19 09:05 | SMR8 | LONG RURAL |  | 11 | 390 | 4290 | 0.016612 | 4.2595e-05 | 0
2013-09-19 09:18 | ELM12 | SHORT RURAL |  | 626 | 341 | 213466 | 1.8576 | 0.0054474 | 0
2013-09-15 09:00 | SLE31 | LONG RURAL |  | 5 | 340 | 1700 | 0.0065829 | 1.9362e-05 | 0
2013-09-20 10:15 | LGA22 | SHORT RURAL |  | 95 | 245 | 23275 | 0.20254 | 0.00082669 | 0
2013-09-17 09:35 | MFA34 | SHORT RURAL |  | 3 | 155 | 465 | 0.0040464 | 2.6106e-05 | 0
2013-09-18 09:05 | WN2 | LONG RURAL |  | 17 | 385 | 6545 | 0.025344 | 6.5829e-05 | 0
2013-09-18 11:15 | BN2 | LONG RURAL |  | 2 | 45 | 90 | 0.00034851 | 7.7446e-06 | 0
2013-09-19 09:02 | BN1 | LONG RURAL |  | 36 | 336 | 12096 | 0.04684 | 0.0001394 | 0
2013-09-19 09:05 | BN2 | LONG RURAL |  | 1 | 95 | 95 | 0.00036787 | 3.8723e-06 | 0
2013-09-19 11:05 | BN2 | LONG RURAL |  | 1 | 30 | 30 | 0.00011617 | 3.8723e-06 | 0
2013-09-19 12:50 | BN2 | LONG RURAL |  | 2 | 55 | 110 | 0.00042595 | 7.7446e-06 | 0
2013-09-20 12:50 | TGN31 | LONG RURAL |  | 2 | 80 | 160 | 0.00061957 | 7.7446e-06 | 0
2013-09-20 12:05 | TGN31 | LONG RURAL |  | 2 | 60 | 120 | 0.00046468 | 7.7446e-06 | 0
2013-09-21 08:35 | LDL12 | URBAN |  | 215 | 493 | 105995 | 0.36923 | 0.00074895 | 0
2013-09-21 08:30 | LDL12 | URBAN |  | 106 | 532 | 56392 | 0.19644 | 0.00036925 | 0
2013-09-18 08:55 | BGE22 | SHORT RURAL |  | 42 | 240 | 10080 | 0.087716 | 0.00036548 | 0
2013-09-18 08:48 | SLE31 | LONG RURAL |  | 31 | 312 | 9672 | 0.037453 | 0.00012004 | 0
2013-09-18 08:30 | BDL1 | LONG RURAL |  | 215 | 383 | 82345 | 0.31887 | 0.00083255 | 0
2013-09-19 08:55 | BDL4 | SHORT RURAL |  | 320 | 370 | 118400 | 1.0303 | 0.0027846 | 0
2013-09-19 09:10 | MFA21 | LONG RURAL |  | 39 | 182 | 7098 | 0.027486 | 0.00015102 | 0
2013-09-19 09:10 | BN1 | LONG RURAL |  | 14 | 230 | 3220 | 0.012469 | 5.4212e-05 | 0
2013-09-18 09:55 | SMR8 | LONG RURAL |  | 2 | 150 | 300 | 0.0011617 | 7.7446e-06 | 0
2013-09-20 10:02 | LLG11 | SHORT RURAL |  | 129 | 272 | 35088 | 0.30533 | 0.0011226 | 0
2013-09-20 09:11 | OFR23 | LONG RURAL |  | 49 | 194 | 9506 | 0.03681 | 0.00018974 | 0
2013-09-22 08:00 | CYN22 | URBAN |  | 112 | 257 | 28784 | 0.10027 | 0.00039015 | 0
2013-09-22 09:00 | RWT26 | URBAN |  | 496 | 169 | 83824 | 0.292 | 0.0017278 | 0
2013-09-22 08:40 | CYN21 | URBAN |  | 40 | 235 | 9400 | 0.032745 | 0.00013934 | 0
2013-09-22 09:15 | TT7 | URBAN |  | 7 | 205 | 1435 | 0.0049988 | 2.4384e-05 | 0
2013-09-22 09:00 | LGA22 | SHORT RURAL |  | 582 | 316 | 183912 | 1.6004 | 0.0050645 | 0
2013-09-18 10:25 | PHM14 | LONG RURAL |  | 2 | 45 | 90 | 0.00034851 | 7.7446e-06 | 0
2013-09-18 09:20 | PHM14 | LONG RURAL |  | 1 | 35 | 35 | 0.00013553 | 3.8723e-06 | 0
2013-09-18 08:40 | CNR2 | SHORT RURAL |  | 6 | 370 | 2220 | 0.019318 | 5.2212e-05 | 0
2013-09-19 13:50 | MFA21 | LONG RURAL |  | 2 | 35 | 70 | 0.00027106 | 7.7446e-06 | 0
2013-09-15 03:20 | NLA34 | SHORT RURAL |  | 1 | 645 | 645 | 0.0056128 | 8.702e-06 | 0
2013-09-18 09:50 | NLA31 | LONG RURAL |  | 6 | 130 | 780 | 0.0030204 | 2.3234e-05 | 0
2013-09-18 12:45 | NLA31 | LONG RURAL |  | 1 | 65 | 65 | 0.0002517 | 3.8723e-06 | 0
2013-09-18 10:45 | CYN14 | URBAN |  | 231 | 284 | 65604 | 0.22853 | 0.00080468 | 0
2013-09-21 08:35 | FGY22 | URBAN |  | 1 | 565 | 565 | 0.0019682 | 3.4835e-06 | 0
2013-09-22 09:05 | BGE12 | SHORT RURAL |  | 57 | 315 | 17955 | 0.15624 | 0.00049601 | 0
2013-09-22 09:05 | BGE12 | SHORT RURAL |  | 367 | 125 | 45875 | 0.3992 | 0.0031936 | 0
2013-09-20 09:32 | NLA31 | LONG RURAL |  | 1 | 43 | 43 | 0.00016651 | 3.8723e-06 | 0
2013-09-22 08:30 | FGY21 | SHORT RURAL |  | 19 | 430 | 8170 | 0.071095 | 0.00016534 | 0
2013-09-20 10:04 | MSD1 | LONG RURAL |  | 46 | 206 | 9476 | 0.036694 | 0.00017813 | 0
2013-09-14 08:31 | TT6 | URBAN |  | 658 | 299.7599 | 197242 | 0.68709 | 0.0022921 | 0
2013-09-23 09:00 | WO22 | URBAN |  | 79 | 70 | 5530 | 0.019264 | 0.0002752 | 0
2013-09-23 10:15 | BWA23 | SHORT RURAL |  | 1 | 230 | 230 | 0.0020015 | 8.702e-06 | 0
2013-09-23 09:15 | MOE22 | LONG RURAL |  | 9 | 205 | 1845 | 0.0071444 | 3.4851e-05 | 0
2013-09-23 09:05 | MOE22 | LONG RURAL |  | 1 | 106 | 106 | 0.00041047 | 3.8723e-06 | 0
2013-09-23 09:15 | LGA24 | SHORT RURAL |  | 21 | 225 | 4725 | 0.041117 | 0.00018274 | 0
2013-09-23 09:34 | KMS1 | SHORT RURAL |  | 9 | 254 | 2286 | 0.019893 | 7.8318e-05 | 0
2013-09-23 08:50 | OFR23 | LONG RURAL |  | 41 | 170 | 6970 | 0.02699 | 0.00015876 | 0
2013-09-23 08:47 | BN6 | LONG RURAL |  | 9 | 418 | 3762 | 0.014568 | 3.4851e-05 | 0
2013-09-18 08:30 | BRA11 | URBAN |  | 291 | 445.9691 | 129777 | 0.45208 | 0.0010137 | 0
2013-09-19 11:30 | BRA14 | URBAN |  | 169 | 120 | 20280 | 0.070645 | 0.00058871 | 0
2013-09-19 09:00 | RWN26 | SHORT RURAL |  | 78 | 170 | 13260 | 0.11539 | 0.00067875 | 0
2013-09-19 09:00 | CNR3 | SHORT RURAL |  | 58 | 428 | 24824 | 0.21602 | 0.00050471 | 0
2013-09-17 11:15 | ELM33 | SHORT RURAL |  | 42 | 260 | 10920 | 0.095026 | 0.00036548 | 0
2013-09-17 11:15 | RWN24 | SHORT RURAL |  | 157 | 264 | 41448 | 0.36068 | 0.0013662 | 0
2013-09-20 09:40 | NLA31 | LONG RURAL |  | 2 | 90 | 180 | 0.00069702 | 7.7446e-06 | 0
2013-09-22 09:07 | BDL8 | LONG RURAL |  | 1 | 158 | 158 | 0.00061183 | 3.8723e-06 | 0
2013-09-22 09:30 | NLA31 | LONG RURAL |  | 1 | 180 | 180 | 0.00069702 | 3.8723e-06 | 0
2013-09-22 14:30 | NLA31 | LONG RURAL |  | 1 | 105 | 105 | 0.00040659 | 3.8723e-06 | 0
2013-09-19 10:50 | BWR12 | URBAN |  | 180 | 199.2889 | 35872 | 0.12496 | 0.00062703 | 0
2013-09-19 10:03 | OFR23 | LONG RURAL |  | 278 | 195 | 54210 | 0.20992 | 0.0010765 | 0
2013-09-20 10:00 | DRN12 | URBAN |  | 79 | 291.6329 | 23039 | 0.080256 | 0.0002752 | 0
2013-09-23 10:50 | MBY12 | SHORT RURAL |  | 2 | 70 | 140 | 0.0012183 | 1.7404e-05 | 0
2013-09-25 09:00 | MYT7 | LONG RURAL |  | 20 | 335 | 6700 | 0.025945 | 7.7446e-05 | 0
2013-09-25 10:40 | MYT7 | LONG RURAL |  | 11 | 97 | 1067 | 0.0041318 | 4.2595e-05 | 0
2013-09-24 09:35 | TGN31 | LONG RURAL |  | 14 | 115 | 1610 | 0.0062344 | 5.4212e-05 | 0
2013-09-24 09:10 | TGN31 | LONG RURAL |  | 2 | 115 | 230 | 0.00089063 | 7.7446e-06 | 0
2013-09-25 09:40 | MWTS21 | URBAN |  | 332 | 284 | 94288 | 0.32845 | 0.0011565 | 0
2013-09-24 09:04 | LGA14 | LONG RURAL |  | 88 | 348 | 30624 | 0.11859 | 0.00034076 | 0
2013-09-24 11:40 | TGN31 | LONG RURAL |  | 1 | 50 | 50 | 0.00019362 | 3.8723e-06 | 0
2013-09-24 10:00 | CYN14 | URBAN |  | 50 | 300 | 15000 | 0.052252 | 0.00017417 | 0
2013-09-24 10:20 | TGN31 | LONG RURAL |  | 1 | 105 | 105 | 0.00040659 | 3.8723e-06 | 0
2013-09-25 09:25 | MOE13 | SHORT RURAL |  | 188 | 300 | 56400 | 0.49079 | 0.001636 | 0
2013-09-24 08:37 | WOTS25 | SHORT RURAL |  | 1 | 43 | 43 | 0.00037418 | 8.702e-06 | 0
2013-09-25 09:05 | WGL23 | SHORT RURAL |  | 9 | 175 | 1575 | 0.013706 | 7.8318e-05 | 0
2013-09-24 09:00 | MYT8 | SHORT RURAL |  | 101 | 180 | 18180 | 0.1582 | 0.0008789 | 0
2013-09-23 11:30 | MOE22 | LONG RURAL |  | 2 | 20 | 40 | 0.00015489 | 7.7446e-06 | 0
2013-09-26 11:35 | TRC01 | SHORT RURAL |  | 5 | 105 | 525 | 0.0045685 | 4.351e-05 | 0
2013-09-24 09:30 | FTR23 | LONG RURAL |  | 31 | 174 | 5394 | 0.020887 | 0.00012004 | 0
2013-09-24 09:18 | WGI24 | URBAN |  | 327 | 196 | 64092 | 0.22326 | 0.0011391 | 0
2013-09-24 11:33 | WGI34 | SHORT RURAL |  | 74 | 9 | 666 | 0.0057955 | 0.00064395 | 0
2013-09-25 09:30 | LGA24 | SHORT RURAL |  | 50 | 255 | 12750 | 0.11095 | 0.0004351 | 0
2013-09-24 10:00 | LLG12 | SHORT RURAL |  | 39 | 295 | 11505 | 0.10012 | 0.00033938 | 0
2013-09-24 09:00 | RWN33 | URBAN |  | 312 | 445 | 138840 | 0.48365 | 0.0010868 | 0
2013-09-24 09:00 | LDL11 | URBAN |  | 65 | 180 | 11700 | 0.040757 | 0.00022643 | 0
2013-09-24 08:57 | WYK11 | SHORT RURAL |  | 138 | 428 | 59064 | 0.51397 | 0.0012009 | 0
2013-09-25 09:00 | FTR12 | LONG RURAL |  | 66 | 330 | 21780 | 0.084339 | 0.00025557 | 0
2013-09-24 09:05 | BN1 | LONG RURAL |  | 2 | 365 | 730 | 0.0028268 | 7.7446e-06 | 0
2013-09-24 08:30 | WYK24 | SHORT RURAL |  | 23 | 441 | 10143 | 0.088264 | 0.00020015 | 0
2013-09-24 13:09 | LDL21 | SHORT RURAL |  | 420 | 60 | 25200 | 0.21929 | 0.0036548 | 0
2013-09-25 09:15 | WYK24 | SHORT RURAL |  | 1 | 314 | 314 | 0.0027324 | 8.702e-06 | 0
2013-09-25 08:30 | WYK23 | SHORT RURAL |  | 322 | 466 | 150052 | 1.3057 | 0.002802 | 0
2013-09-26 09:18 | LDL11 | URBAN |  | 89 | 152 | 13528 | 0.047125 | 0.00031003 | 0
2013-09-24 09:14 | BN1 | LONG RURAL |  | 2 | 166 | 332 | 0.0012856 | 7.7446e-06 | 0
2013-09-26 09:40 | WYK23 | SHORT RURAL |  | 28 | 105 | 2940 | 0.025584 | 0.00024366 | 0
2013-09-24 08:35 | BN2 | LONG RURAL |  | 2 | 35 | 70 | 0.00027106 | 7.7446e-06 | 0
2013-09-24 09:08 | WN4 | SHORT RURAL |  | 1082 | 406 | 439292 | 3.8227 | 0.0094155 | 0
2013-09-26 08:55 | CYN13 | URBAN |  | 479 | 5 | 2395 | 0.0083429 | 0.0016686 | 0
2013-09-24 10:30 | BN2 | LONG RURAL |  | 6 | 60 | 360 | 0.001394 | 2.3234e-05 | 0
2013-09-24 11:50 | BN2 | LONG RURAL |  | 1 | 50 | 50 | 0.00019362 | 3.8723e-06 | 0
2013-09-24 09:12 | BN2 | LONG RURAL |  | 1 | 58 | 58 | 0.00022459 | 3.8723e-06 | 0
2013-09-24 12:35 | BN1 | LONG RURAL |  | 37 | 139 | 5143 | 0.019915 | 0.00014328 | 0
2013-09-25 08:53 | BN2 | LONG RURAL |  | 44 | 253 | 11132 | 0.043107 | 0.00017038 | 0
2013-09-24 12:10 | SMR8 | LONG RURAL |  | 2 | 140 | 280 | 0.0010842 | 7.7446e-06 | 0
2013-09-24 09:45 | SMR8 | LONG RURAL |  | 3 | 110 | 330 | 0.0012779 | 1.1617e-05 | 0
2013-09-24 09:07 | SLE32 | SHORT RURAL |  | 298 | 345 | 102810 | 0.89465 | 0.0025932 | 0
2013-09-24 08:56 | MFA21 | LONG RURAL |  | 343 | 88 | 30184 | 0.11688 | 0.0013282 | 0
2013-09-24 08:45 | PHM14 | LONG RURAL |  | 22 | 125 | 2750 | 0.010649 | 8.5191e-05 | 0
2013-09-25 08:58 | LLG13 | SHORT RURAL |  | 1 | 62 | 62 | 0.00053952 | 8.702e-06 | 0
2013-09-26 08:20 | ELM13 | URBAN |  | 505 | 272.4455 | 137585 | 0.47928 | 0.0017592 | 0
2013-09-24 09:00 | MOE32 | SHORT RURAL |  | 15 | 365 | 5475 | 0.047643 | 0.00013053 | 0
2013-09-25 08:54 | DRN12 | URBAN |  | 22 | 216 | 4752 | 0.016554 | 7.6637e-05 | 0
2013-09-19 08:00 | RWT22 | URBAN |  | 99 | 360 | 35640 | 0.12415 | 0.00034486 | 0
2013-09-26 10:55 | TGN31 | LONG RURAL |  | 2 | 70 | 140 | 0.00054212 | 7.7446e-06 | 0
2013-09-25 11:00 | WN3 | LONG RURAL |  | 2 | 100 | 200 | 0.00077446 | 7.7446e-06 | 0
2013-09-25 13:15 | WN3 | LONG RURAL |  | 2 | 145 | 290 | 0.001123 | 7.7446e-06 | 0
2013-09-15 08:37 | WT11 | URBAN |  | 241 | 472 | 113752 | 0.39625 | 0.00083952 | 0
2013-09-19 09:30 | RWN24 | SHORT RURAL |  | 173 | 263 | 45499 | 0.39593 | 0.0015054 | 0
2013-09-19 09:20 | RWN22 | URBAN |  | 97 | 175 | 16975 | 0.059132 | 0.0003379 | 0
2013-09-20 09:00 | RWN31 | SHORT RURAL |  | 43 | 340 | 14620 | 0.12722 | 0.00037418 | 0
2013-09-20 09:10 | RWN22 | URBAN |  | 97 | 77 | 7469 | 0.026018 | 0.0003379 | 0
2013-09-20 09:15 | RWN24 | SHORT RURAL |  | 34 | 179 | 6086 | 0.05296 | 0.00029587 | 0
2013-09-20 08:55 | BN2 | LONG RURAL |  | 1 | 70 | 70 | 0.00027106 | 3.8723e-06 | 0
2013-09-27 09:00 | WO11 | URBAN |  | 100 | 195 | 19500 | 0.067928 | 0.00034835 | 0
2013-09-24 09:01 | BRA33 | URBAN |  | 61 | 79 | 4819 | 0.016787 | 0.00021249 | 0
2013-09-19 09:05 | KLO24 | SHORT RURAL |  | 66 | 355 | 23430 | 0.20389 | 0.00057433 | 0
2013-09-24 09:05 | MOE22 | LONG RURAL |  | 8 | 235 | 1880 | 0.00728 | 3.0979e-05 | 0
2013-09-24 13:50 | TGN23 | SHORT RURAL |  | 1 | 30 | 30 | 0.00026106 | 8.702e-06 | 0
2013-09-25 09:00 | KMS1 | SHORT RURAL |  | 4 | 110 | 440 | 0.0038289 | 3.4808e-05 | 0
2013-09-25 09:20 | SMR8 | LONG RURAL |  | 2 | 70 | 140 | 0.00054212 | 7.7446e-06 | 0
2013-09-19 09:35 | MSD1 | LONG RURAL |  | 65 | 275 | 17875 | 0.069218 | 0.0002517 | 0
2013-09-25 09:05 | SMR4 | SHORT RURAL |  | 30 | 370 | 11100 | 0.096592 | 0.00026106 | 0
2013-09-20 11:40 | NLA31 | LONG RURAL |  | 1 | 20 | 20 | 7.7446e-05 | 3.8723e-06 | 0
2013-09-27 09:02 | BRT22 | SHORT RURAL |  | 78 | 284 | 22152 | 0.19277 | 0.00067875 | 0
2013-09-21 08:30 | RWN31 | SHORT RURAL |  | 83 | 315 | 26145 | 0.22751 | 0.00072226 | 0
2013-09-24 09:05 | BDL1 | LONG RURAL |  | 49 | 356 | 17444 | 0.067549 | 0.00018974 | 0
2013-09-25 08:35 | BN3 | SHORT RURAL |  | 3 | 70 | 210 | 0.0018274 | 2.6106e-05 | 0
2013-09-17 09:00 | HPK12 | URBAN |  | 76 | 392 | 29792 | 0.10378 | 0.00026474 | 0
2013-09-25 09:10 | WN3 | LONG RURAL |  | 2 | 355 | 710 | 0.0027493 | 7.7446e-06 | 0
2013-09-20 08:37 | WYK24 | SHORT RURAL |  | 36 | 276 | 9936 | 0.086463 | 0.00031327 | 0
2013-09-25 09:10 | HPK13 | URBAN |  | 100 | 260 | 26000 | 0.090571 | 0.00034835 | 0
2013-09-26 08:45 | CNR2 | SHORT RURAL |  | 8 | 365 | 2920 | 0.02541 | 6.9616e-05 | 0
2013-09-25 09:00 | BN3 | SHORT RURAL |  | 2 | 200 | 400 | 0.0034808 | 1.7404e-05 | 0
2013-09-23 09:00 | RWT15 | URBAN |  | 87 | 224 | 19488 | 0.067886 | 0.00030306 | 0
2013-09-24 09:36 | RWT15 | URBAN |  | 195 | 320 | 62400 | 0.21737 | 0.00067928 | 0
2013-09-24 09:21 | BRA14 | URBAN |  | 35 | 159 | 5565 | 0.019386 | 0.00012192 | 0
2013-09-25 08:43 | BWR32 | URBAN |  | 261 | 315 | 82215 | 0.28639 | 0.00090919 | 0
2013-09-26 09:01 | SMR8 | LONG RURAL |  | 16 | 256 | 4096 | 0.015861 | 6.1957e-05 | 0
2013-09-24 08:30 | NLA31 | LONG RURAL |  | 9 | 346 | 3114 | 0.012058 | 3.4851e-05 | 0
2013-09-25 08:37 | WT6 | URBAN |  | 167 | 146 | 24382 | 0.084934 | 0.00058174 | 0
2013-09-26 09:25 | BDL1 | LONG RURAL |  | 251 | 287 | 72037 | 0.27895 | 0.00097195 | 0
2013-09-25 08:55 | PHM14 | LONG RURAL |  | 27 | 140 | 3780 | 0.014637 | 0.00010455 | 0
2013-09-25 10:27 | DRN14 | SHORT RURAL |  | 49 | 143 | 7007 | 0.060975 | 0.0004264 | 0
2013-09-25 12:15 | PHM14 | LONG RURAL |  | 2 | 35 | 70 | 0.00027106 | 7.7446e-06 | 0
2013-09-25 10:35 | LLG13 | SHORT RURAL |  | 2 | 30 | 60 | 0.00052212 | 1.7404e-05 | 0
2013-09-26 09:25 | PHM14 | LONG RURAL |  | 104 | 240 | 24960 | 0.096653 | 0.00040272 | 0
2013-09-24 09:40 | DRN12 | URBAN |  | 4 | 330 | 1320 | 0.0045982 | 1.3934e-05 | 0
2013-09-25 09:10 | BRA21 | URBAN |  | 98 | 321 | 31458 | 0.10958 | 0.00034138 | 0
2013-09-25 09:40 | BWN14 | SHORT RURAL |  | 72 | 223 | 16056 | 0.13972 | 0.00062654 | 0
2013-09-13 09:55 | SMR5 | LONG RURAL |  | 1 | 140 | 140 | 0.00054212 | 3.8723e-06 | 0
2013-09-12 13:02 | WOTS13 | LONG RURAL |  | 1 | 28 | 28 | 0.00010842 | 3.8723e-06 | 0
2013-09-12 11:23 | WOTS13 | LONG RURAL |  | 1 | 47 | 47 | 0.000182 | 3.8723e-06 | 0
2013-09-12 10:07 | WOTS13 | LONG RURAL |  | 1 | 33 | 33 | 0.00012779 | 3.8723e-06 | 0
2013-09-29 09:05 | MOE21 | SHORT RURAL |  | 32 | 291 | 9312 | 0.081033 | 0.00027846 | 0
2013-09-27 09:40 | WN3 | LONG RURAL |  | 5 | 280 | 1400 | 0.0054212 | 1.9362e-05 | 0
2013-09-18 11:05 | LLG11 | SHORT RURAL |  | 2 | 55 | 110 | 0.00095722 | 1.7404e-05 | 0
2013-09-25 08:40 | CYN33 | SHORT RURAL |  | 25 | 90 | 2250 | 0.019579 | 0.00021755 | 0
2013-09-25 10:40 | CYN21 | URBAN |  | 74 | 140 | 10360 | 0.036089 | 0.00025778 | 0
2013-09-25 09:35 | RWT14 | URBAN |  | 356 | 247 | 87932 | 0.30631 | 0.0012401 | 0
2013-09-18 08:00 | RWT15 | URBAN |  | 190 | 461.7474 | 87732 | 0.30561 | 0.00066186 | 0
2013-09-26 08:40 | WN3 | LONG RURAL |  | 333 | 384 | 127872 | 0.49516 | 0.0012895 | 0
2013-09-24 09:35 | MOE22 | LONG RURAL |  | 25 | 169 | 4225 | 0.016361 | 9.6808e-05 | 0
2013-09-26 09:30 | WOTS24 | LONG RURAL |  | 1 | 135 | 135 | 0.00052276 | 3.8723e-06 | 0
2013-09-24 10:32 | BRA33 | URBAN |  | 94 | 118 | 11092 | 0.038639 | 0.00032745 | 0
2013-09-26 10:00 | RWT11 | URBAN |  | 145 | 30 | 4350 | 0.015153 | 0.00050511 | 0
2013-09-29 08:43 | BWR12 | URBAN |  | 29 | 277 | 8033 | 0.027983 | 0.00010102 | 0
2013-09-30 10:00 | TGN23 | SHORT RURAL |  | 220 | 137.2 | 30184 | 0.26266 | 0.0019144 | 0
2013-09-30 09:35 | WYK24 | SHORT RURAL |  | 69 | 345 | 23805 | 0.20715 | 0.00060044 | 0
2013-09-30 08:40 | BWN13 | URBAN |  | 58 | 85 | 4930 | 0.017174 | 0.00020204 | 0
2013-09-30 10:30 | ELD01 | SHORT RURAL |  | 7 | 255 | 1785 | 0.015533 | 6.0914e-05 | 0
2013-09-30 09:15 | WN3 | LONG RURAL |  | 2 | 235 | 470 | 0.00182 | 7.7446e-06 | 0
2013-09-30 09:55 | BN1 | LONG RURAL |  | 1 | 125 | 125 | 0.00048404 | 3.8723e-06 | 0
2013-09-25 08:40 | WO31 | URBAN |  | 340 | 215 | 73100 | 0.25464 | 0.0011844 | 0
2013-09-25 09:30 | MFA22 | LONG RURAL |  | 29 | 365 | 10585 | 0.040988 | 0.0001123 | 0
2013-09-25 09:09 | CNR3 | SHORT RURAL |  | 47 | 315 | 14805 | 0.12883 | 0.00040899 | 0
2013-09-30 09:02 | SMR2 | SHORT RURAL |  | 241 | 368 | 88688 | 0.77176 | 0.0020972 | 0
2013-09-29 08:33 | CLN21 | SHORT RURAL |  | 658 | 428.1687 | 281735 | 2.4516 | 0.0057259 | 0
2013-09-28 10:00 | PHM11 | URBAN |  | 15 | 85 | 1275 | 0.0044414 | 5.2252e-05 | 0
2013-10-02 09:05 | WOTS11 | LONG RURAL |  | 35 | 240 | 8400 | 0.032527 | 0.00013553 | 0
2013-10-03 10:40 | WOTS11 | LONG RURAL |  | 1 | 175 | 175 | 0.00067766 | 3.8723e-06 | 0
2013-10-02 09:15 | WOTS24 | LONG RURAL |  | 12 | 145 | 1740 | 0.0067378 | 4.6468e-05 | 0
2013-10-03 09:00 | WOTS24 | LONG RURAL |  | 12 | 220 | 2640 | 0.010223 | 4.6468e-05 | 0
2013-10-01 11:05 | WOTS24 | LONG RURAL |  | 118 | 110 | 12980 | 0.050263 | 0.00045693 | 0
2013-10-03 09:10 | MBY11 | SHORT RURAL |  | 43 | 28 | 1204 | 0.010477 | 0.00037418 | 0
2013-10-03 09:45 | LDL23 | LONG RURAL |  | 27 | 360 | 9720 | 0.037639 | 0.00010455 | 0
2013-10-03 09:20 | WYK12 | SHORT RURAL |  | 81 | 231 | 18711 | 0.16282 | 0.00070486 | 0
2013-10-01 09:50 | WN2 | LONG RURAL |  | 5 | 345 | 1725 | 0.0066797 | 1.9362e-05 | 0
2013-10-02 09:00 | WOTS13 | LONG RURAL |  | 2 | 117 | 234 | 0.00090612 | 7.7446e-06 | 0
2013-10-01 11:50 | BWA23 | SHORT RURAL |  | 2 | 110 | 220 | 0.0019144 | 1.7404e-05 | 0
2013-10-02 08:45 | WN3 | LONG RURAL |  | 26 | 315 | 8190 | 0.031714 | 0.00010068 | 0
2013-10-02 09:35 | BN1 | LONG RURAL |  | 1 | 135 | 135 | 0.00052276 | 3.8723e-06 | 0
2013-10-01 08:37 | BN4 | URBAN |  | 32 | 242 | 7744 | 0.026976 | 0.00011147 | 0
2013-10-02 09:00 | BN1 | LONG RURAL |  | 49 | 402 | 19698 | 0.076277 | 0.00018974 | 0
2013-10-03 09:23 | BN1 | LONG RURAL |  | 40 | 443 | 17720 | 0.068617 | 0.00015489 | 0
2013-10-08 09:19 | CF1 | SHORT RURAL |  | 49 | 296 | 14504 | 0.12621 | 0.0004264 | 0
2013-09-30 08:45 | CNR2 | SHORT RURAL |  | 3 | 280 | 840 | 0.0073097 | 2.6106e-05 | 0
2013-09-30 09:26 | NLA34 | SHORT RURAL |  | 53 | 409 | 21677 | 0.18863 | 0.0004612 | 0
2013-09-30 13:01 | CNR2 | SHORT RURAL |  | 1 | 104 | 104 | 0.000905 | 8.702e-06 | 0
2013-10-01 08:30 | CNR2 | SHORT RURAL |  | 44 | 202 | 8888 | 0.077343 | 0.00038289 | 0
2013-10-03 10:30 | BDL1 | LONG RURAL |  | 1 | 65 | 65 | 0.0002517 | 3.8723e-06 | 0
2013-10-03 10:15 | BDL1 | LONG RURAL |  | 1 | 100 | 100 | 0.00038723 | 3.8723e-06 | 0
2013-09-30 09:11 | MFA22 | LONG RURAL |  | 12 | 169 | 2028 | 0.0078531 | 4.6468e-05 | 0
2013-09-30 09:20 | MFA21 | LONG RURAL |  | 52 | 160 | 8320 | 0.032218 | 0.00020136 | 0
2013-09-30 09:10 | MFA22 | LONG RURAL |  | 11 | 225 | 2475 | 0.009584 | 4.2595e-05 | 0
2013-10-03 09:50 | BN1 | LONG RURAL |  | 8 | 30 | 240 | 0.00092936 | 3.0979e-05 | 0
2013-09-24 09:37 | LGA14 | LONG RURAL |  | 1 | 221 | 221 | 0.00085578 | 3.8723e-06 | 0
2013-10-02 09:15 | SMR8 | LONG RURAL |  | 1 | 50 | 50 | 0.00019362 | 3.8723e-06 | 0
2013-09-30 11:00 | WT6 | URBAN |  | 75 | 100 | 7500 | 0.026126 | 0.00026126 | 0
2013-09-30 09:36 | BRA33 | URBAN |  | 172 | 324 | 55728 | 0.19413 | 0.00059916 | 0
2013-09-30 13:31 | WT6 | URBAN |  | 61 | 64 | 3904 | 0.0136 | 0.00021249 | 0
2013-10-02 11:20 | SMR8 | LONG RURAL |  | 1 | 50 | 50 | 0.00019362 | 3.8723e-06 | 0
2013-09-24 09:00 | BGE12 | SHORT RURAL |  | 62 | 330 | 20460 | 0.17804 | 0.00053952 | 0
2013-10-02 09:28 | KMS21 | SHORT RURAL |  | 1 | 92 | 92 | 0.00080058 | 8.702e-06 | 0
2013-10-04 09:04 | BWA22 | LONG RURAL |  | 25 | 266 | 6650 | 0.025751 | 9.6808e-05 | 0
2013-10-04 12:30 | WGL21 | LONG RURAL |  | 5 | 170 | 850 | 0.0032915 | 1.9362e-05 | 0
2013-10-04 09:30 | LLG12 | SHORT RURAL |  | 1 | 120 | 120 | 0.0010442 | 8.702e-06 | 0
2013-10-03 10:03 | WGI34 | SHORT RURAL |  | 125 | 78 | 9750 | 0.084844 | 0.0010877 | 0
2013-10-04 09:00 | LGA11 | LONG RURAL |  | 76 | 202 | 15352 | 0.059448 | 0.0002943 | 0
2013-10-04 08:55 | KLK1 | SHORT RURAL |  | 108 | 357 | 38556 | 0.33551 | 0.00093981 | 0
2013-10-04 09:30 | WYK23 | SHORT RURAL |  | 5 | 165 | 825 | 0.0071791 | 4.351e-05 | 0
2013-10-04 09:45 | WYK24 | SHORT RURAL |  | 90 | 335 | 30150 | 0.26236 | 0.00078318 | 0
2013-10-04 09:01 | WGL21 | LONG RURAL |  | 18 | 211 | 3798 | 0.014707 | 6.9702e-05 | 0
2013-10-04 09:20 | DRN12 | URBAN |  | 2 | 60 | 120 | 0.00041802 | 6.967e-06 | 0
2013-10-04 09:08 | MYT2 | SHORT RURAL |  | 360 | 186 | 66960 | 0.58268 | 0.0031327 | 0
2013-10-04 12:10 | BN6 | LONG RURAL |  | 1 | 40 | 40 | 0.00015489 | 3.8723e-06 | 0
2013-10-04 10:07 | WYK11 | SHORT RURAL |  | 282 | 304 | 85728 | 0.746 | 0.002454 | 0
2013-10-04 09:00 | MWTS31 | SHORT RURAL |  | 12 | 215 | 2580 | 0.022451 | 0.00010442 | 0
2013-10-04 09:31 | BGE12 | SHORT RURAL |  | 1 | 164 | 164 | 0.0014271 | 8.702e-06 | 0
2013-10-05 09:00 | ALA01 | LONG RURAL |  | 2 | 45 | 90 | 0.00034851 | 7.7446e-06 | 0
2013-09-25 08:43 | BWR32 | URBAN |  | 85 | 315 | 26775 | 0.09327 | 0.0002961 | 0
2013-09-25 09:20 | MSD1 | LONG RURAL |  | 44 | 230 | 10120 | 0.039188 | 0.00017038 | 0
2013-10-09 10:20 | CYN21 | URBAN |  | 15 | 195 | 2925 | 0.010189 | 5.2252e-05 | 0
2013-10-03 07:27 | WT7 | URBAN |  | 164 | 541 | 88724 | 0.30907 | 0.00057129 | 0
2013-10-06 08:55 | MWTS11 | SHORT RURAL |  | 1 | 515 | 515 | 0.0044815 | 8.702e-06 | 0
2013-10-06 08:45 | WOTS11 | LONG RURAL |  | 66 | 455 | 30030 | 0.11629 | 0.00025557 | 0
2013-10-05 10:40 | ALA01 | LONG RURAL |  | 2 | 55 | 110 | 0.00042595 | 7.7446e-06 | 0
2013-09-30 10:10 | DRN12 | URBAN |  | 2 | 170 | 340 | 0.0011844 | 6.967e-06 | 0
2013-09-29 08:30 | WGL15 | SHORT RURAL |  | 2 | 280 | 560 | 0.0048731 | 1.7404e-05 | 0
2013-10-04 09:10 | BN2 | LONG RURAL |  | 1 | 140 | 140 | 0.00054212 | 3.8723e-06 | 0
2013-10-03 12:50 | BDL1 | LONG RURAL |  | 1 | 50 | 50 | 0.00019362 | 3.8723e-06 | 0
2013-10-02 08:34 | BDL6 | SHORT RURAL |  | 142 | 328 | 46576 | 0.4053 | 0.0012357 | 0
2013-10-03 09:20 | CYN14 | URBAN |  | 187 | 400 | 74800 | 0.26056 | 0.00065141 | 0
2013-10-06 10:23 | TT12 | URBAN |  | 44 | 337 | 14828 | 0.051653 | 0.00015327 | 0
2013-10-04 08:45 | MFA22 | LONG RURAL |  | 13 | 240 | 3120 | 0.012082 | 5.034e-05 | 0
2013-10-04 09:00 | NLA34 | SHORT RURAL |  | 5 | 236 | 1180 | 0.010268 | 4.351e-05 | 0
2013-10-04 11:10 | DRN12 | URBAN |  | 2 | 40 | 80 | 0.00027868 | 6.967e-06 | 0
2013-10-06 08:32 | CYN13 | URBAN |  | 46 | 97 | 4462 | 0.015543 | 0.00016024 | 0
2013-10-06 08:00 | CYN31 | URBAN |  | 506 | 278 | 140668 | 0.49001 | 0.0017626 | 0
2013-10-03 09:00 | BRA13 | URBAN |  | 157 | 255 | 40035 | 0.13946 | 0.00054691 | 0
2013-10-04 11:01 | BRA13 | URBAN |  | 442 | 134 | 59228 | 0.20632 | 0.0015397 | 0
2013-10-05 08:00 | BRA21 | URBAN |  | 76 | 245 | 18620 | 0.064862 | 0.00026474 | 0
2013-10-05 10:00 | BWR32 | URBAN |  | 161 | 210 | 33810 | 0.11778 | 0.00056084 | 0
2013-10-06 08:31 | BRA13 | URBAN |  | 55 | 415 | 22825 | 0.079511 | 0.00019159 | 0
2013-10-07 10:57 | LGA13 | LONG RURAL |  | 4 | 70 | 280 | 0.0010842 | 1.5489e-05 | 0
2013-10-07 09:30 | WOTS24 | LONG RURAL |  | 6 | 290 | 1740 | 0.0067378 | 2.3234e-05 | 0
2013-10-07 10:23 | FTR23 | LONG RURAL |  | 2 | 37 | 74 | 0.00028655 | 7.7446e-06 | 0
2013-10-07 11:33 | FTR23 | LONG RURAL |  | 1 | 42 | 42 | 0.00016264 | 3.8723e-06 | 0
2013-10-07 09:45 | WN3 | LONG RURAL |  | 1 | 130 | 130 | 0.0005034 | 3.8723e-06 | 0
2013-10-07 13:05 | FTR23 | LONG RURAL |  | 1 | 75 | 75 | 0.00029042 | 3.8723e-06 | 0
2013-10-07 09:08 | RWN33 | URBAN |  | 4 | 410 | 1640 | 0.0057129 | 1.3934e-05 | 0
2013-10-07 09:40 | CYN12 | URBAN |  | 94 | 365 | 34310 | 0.11952 | 0.00032745 | 0
2013-10-06 13:00 | ELM33 | SHORT RURAL |  | 50 | 43 | 2150 | 0.018709 | 0.0004351 | 0
2013-09-27 09:20 | WOTS13 | LONG RURAL |  | 2 | 115 | 230 | 0.00089063 | 7.7446e-06 | 0
2013-10-07 08:50 | BDL1 | LONG RURAL |  | 10 | 406 | 4060 | 0.015722 | 3.8723e-05 | 0
2013-10-07 11:50 | BDL4 | SHORT RURAL |  | 2 | 145 | 290 | 0.0025236 | 1.7404e-05 | 0
2013-10-05 08:40 | BGE12 | SHORT RURAL |  | 49 | 355 | 17395 | 0.15137 | 0.0004264 | 0
2013-09-30 09:17 | MSD1 | LONG RURAL |  | 68 | 347 | 23596 | 0.091371 | 0.00026332 | 0
2013-10-07 09:30 | CYN32 | URBAN |  | 173 | 190 | 32870 | 0.1145 | 0.00060264 | 0
2013-10-04 10:15 | BWN13 | URBAN |  | 115 | 227 | 26105 | 0.090936 | 0.0004006 | 0
2013-10-04 20:00 | BWN13 | URBAN |  | 54 | 50 | 2700 | 0.0094054 | 0.00018811 | 0
2013-10-05 00:34 | BWN13 | URBAN |  | 54 | 11 | 594 | 0.0020692 | 0.00018811 | 0
2013-10-07 09:00 | OFR23 | LONG RURAL |  | 32 | 305 | 9760 | 0.037794 | 0.00012391 | 0
2013-10-07 14:06 | LGA13 | LONG RURAL |  | 2 | 48 | 96 | 0.00037174 | 7.7446e-06 | 0
2013-10-08 09:10 | TGN31 | LONG RURAL |  | 57 | 255 | 14535 | 0.056284 | 0.00022072 | 0
2013-10-08 09:05 | WOTS24 | LONG RURAL |  | 15 | 230 | 3450 | 0.013359 | 5.8085e-05 | 0
2013-10-09 09:20 | LGA21 | SHORT RURAL |  | 6 | 235 | 1410 | 0.01227 | 5.2212e-05 | 0
2013-10-09 09:11 | TGN31 | LONG RURAL |  | 4 | 96 | 384 | 0.001487 | 1.5489e-05 | 0
2013-10-08 09:15 | WGI22 | LONG RURAL |  | 109 | 525 | 57225 | 0.22159 | 0.00042208 | 0
2013-10-09 09:00 | WGI22 | LONG RURAL |  | 64 | 645 | 41280 | 0.15985 | 0.00024783 | 0
2013-10-09 09:10 | WOTS24 | LONG RURAL |  | 5 | 190 | 950 | 0.0036787 | 1.9362e-05 | 0
2013-10-09 09:00 | MYT8 | SHORT RURAL |  | 11 | 280 | 3080 | 0.026802 | 9.5722e-05 | 0
2013-10-09 09:30 | WOTS24 | LONG RURAL |  | 15 | 175 | 2625 | 0.010165 | 5.8085e-05 | 0
2013-10-07 13:16 | LGA13 | LONG RURAL |  | 1 | 24 | 24 | 9.2936e-05 | 3.8723e-06 | 0
2013-10-08 09:05 | LGA11 | LONG RURAL |  | 154 | 293 | 45122 | 0.17473 | 0.00059634 | 0
2013-10-09 09:00 | FTR12 | LONG RURAL |  | 66 | 365 | 24090 | 0.093284 | 0.00025557 | 0
2013-10-08 10:04 | BN1 | LONG RURAL |  | 123 | 77 | 9471 | 0.036675 | 0.00047629 | 0
2013-10-09 09:20 | BN1 | LONG RURAL |  | 3 | 270 | 810 | 0.0031366 | 1.1617e-05 | 0
2013-10-08 10:00 | LDL24 | URBAN |  | 56 | 285 | 15960 | 0.055596 | 0.00019508 | 0
2013-10-10 09:55 | WGI33 | SHORT RURAL |  | 27 | 145 | 3915 | 0.034068 | 0.00023495 | 0
2013-10-07 12:30 | MOE22 | LONG RURAL |  | 3 | 40 | 120 | 0.00046468 | 1.1617e-05 | 0
2013-10-08 10:15 | MWTS32 | SHORT RURAL |  | 2 | 170 | 340 | 0.0029587 | 1.7404e-05 | 0
2013-10-08 12:35 | BN1 | LONG RURAL |  | 1 | 105 | 105 | 0.00040659 | 3.8723e-06 | 0
2013-10-10 09:15 | WN5 | LONG RURAL |  | 22 | 177 | 3894 | 0.015079 | 8.5191e-05 | 0
2013-10-09 09:40 | LGA14 | LONG RURAL |  | 43 | 245 | 10535 | 0.040795 | 0.00016651 | 0
2013-10-08 12:40 | BN1 | LONG RURAL |  | 1 | 40 | 40 | 0.00015489 | 3.8723e-06 | 0
2013-10-08 09:25 | TGN31 | LONG RURAL |  | 46 | 95 | 4370 | 0.016922 | 0.00017813 | 0
2013-10-10 10:43 | WN2 | LONG RURAL |  | 38 | 387 | 14706 | 0.056946 | 0.00014715 | 0
2013-10-09 09:00 | BWA22 | LONG RURAL |  | 42 | 398 | 16716 | 0.06473 | 0.00016264 | 0
2013-10-09 09:33 | FTR22 | SHORT RURAL |  | 1 | 72 | 72 | 0.00062654 | 8.702e-06 | 0
2013-10-08 08:50 | WYK23 | SHORT RURAL |  | 567 | 201 | 113967 | 0.99174 | 0.004934 | 0
2013-10-09 08:30 | WYK24 | SHORT RURAL |  | 40 | 300.5 | 12020 | 0.1046 | 0.00034808 | 0
2013-10-07 10:30 | MOE22 | LONG RURAL |  | 2 | 43 | 86 | 0.00033302 | 7.7446e-06 | 0
2013-10-08 09:20 | MOE22 | LONG RURAL |  | 2 | 55 | 110 | 0.00042595 | 7.7446e-06 | 0
2013-10-08 13:45 | MOE22 | LONG RURAL |  | 5 | 45 | 225 | 0.00087127 | 1.9362e-05 | 0
2013-10-08 12:05 | MOE22 | LONG RURAL |  | 2 | 30 | 60 | 0.00023234 | 7.7446e-06 | 0
2013-10-09 09:40 | WGL24 | LONG RURAL |  | 29 | 290 | 8410 | 0.032566 | 0.0001123 | 0
2013-10-10 08:30 | WYK24 | SHORT RURAL |  | 66 | 348 | 22968 | 0.19987 | 0.00057433 | 0
2013-10-09 14:35 | TGN11 | SHORT RURAL |  | 105 | 10 | 1050 | 0.0091371 | 0.00091371 | 0
2013-10-10 05:35 | WOTS25 | SHORT RURAL |  | 33 | 25 | 825 | 0.0071791 | 0.00028717 | 0
2013-10-10 09:30 | MOE22 | LONG RURAL |  | 1 | 45 | 45 | 0.00017425 | 3.8723e-06 | 0
2013-10-08 09:00 | SMR8 | LONG RURAL |  | 2 | 115 | 230 | 0.00089063 | 7.7446e-06 | 0
2013-10-08 11:45 | SMR8 | LONG RURAL |  | 3 | 182 | 546 | 0.0021143 | 1.1617e-05 | 0
2013-10-09 09:30 | SMR8 | LONG RURAL |  | 4 | 135 | 540 | 0.002091 | 1.5489e-05 | 0
2013-10-10 09:18 | SMR8 | LONG RURAL |  | 4 | 142 | 568 | 0.0021995 | 1.5489e-05 | 0
2013-10-10 09:50 | DRN12 | URBAN |  | 10 | 225 | 2250 | 0.0078378 | 3.4835e-05 | 0
2013-10-10 09:22 | MYT7 | LONG RURAL |  | 60 | 268 | 16080 | 0.062267 | 0.00023234 | 0
2013-10-09 08:50 | CYN21 | URBAN |  | 116 | 190 | 22040 | 0.076776 | 0.00040408 | 0
2013-10-07 13:25 | BRA14 | URBAN |  | 171 | 85 | 14535 | 0.050632 | 0.00059568 | 0
2013-10-08 09:57 | BWR12 | URBAN |  | 18 | 88 | 1584 | 0.0055178 | 6.2703e-05 | 0
2013-10-07 10:46 | WT7 | URBAN |  | 72 | 175 | 12600 | 0.043892 | 0.00025081 | 0
2013-10-09 09:40 | ELM33 | SHORT RURAL |  | 72 | 300 | 21600 | 0.18796 | 0.00062654 | 0
2013-10-08 09:38 | NLA34 | SHORT RURAL |  | 9 | 402 | 3618 | 0.031484 | 7.8318e-05 | 0
2013-10-08 09:00 | MFA22 | LONG RURAL |  | 5 | 155 | 775 | 0.003001 | 1.9362e-05 | 0
2013-10-08 09:45 | SLE31 | LONG RURAL |  | 6 | 265 | 1590 | 0.006157 | 2.3234e-05 | 0
2013-10-09 08:35 | MFA22 | LONG RURAL |  | 15 | 230 | 3450 | 0.013359 | 5.8085e-05 | 0
2013-10-09 09:00 | DRN21 | URBAN |  | 2 | 150 | 300 | 0.001045 | 6.967e-06 | 0
2013-10-09 11:30 | BDL1 | LONG RURAL |  | 2 | 115 | 230 | 0.00089063 | 7.7446e-06 | 0
2013-10-10 09:10 | BDL4 | SHORT RURAL |  | 63 | 220 | 13860 | 0.12061 | 0.00054822 | 0
2013-10-10 09:00 | BDL1 | LONG RURAL |  | 11 | 390 | 4290 | 0.016612 | 4.2595e-05 | 0
2013-10-10 09:30 | NLA34 | SHORT RURAL |  | 3 | 290 | 870 | 0.0075707 | 2.6106e-05 | 0
2013-10-10 09:35 | NLA34 | SHORT RURAL |  | 3 | 340 | 1020 | 0.008876 | 2.6106e-05 | 0
2013-10-10 08:30 | WYK11 | SHORT RURAL |  | 138 | 249 | 34362 | 0.29902 | 0.0012009 | 0
2013-09-29 10:30 | BRA13 | URBAN |  | 238 | 187.2647 | 44569 | 0.15526 | 0.00082907 | 0
2013-10-03 08:30 | BN6 | LONG RURAL |  | 93 | 475 | 44175 | 0.17106 | 0.00036013 | 0
2013-10-08 10:05 | TT6 | URBAN |  | 456 | 326 | 148656 | 0.51784 | 0.0015885 | 0
2013-10-09 09:30 | FGY14 | URBAN |  | 73 | 275 | 20075 | 0.069931 | 0.00025429 | 0
2013-10-10 10:30 | CNR2 | SHORT RURAL |  | 2 | 260 | 520 | 0.004525 | 1.7404e-05 | 0
2013-10-04 09:35 | MSD1 | LONG RURAL |  | 37 | 149 | 5513 | 0.021348 | 0.00014328 | 0
2013-10-08 09:35 | MSD1 | LONG RURAL |  | 78 | 362 | 28236 | 0.10934 | 0.00030204 | 0
2013-10-10 09:10 | MFA22 | LONG RURAL |  | 39 | 375 | 14625 | 0.056633 | 0.00015102 | 0
2013-10-10 09:13 | SLE21 | SHORT RURAL |  | 14 | 370 | 5180 | 0.045076 | 0.00012183 | 0
2013-10-10 11:40 | WOTS25 | SHORT RURAL |  | 1 | 120 | 120 | 0.0010442 | 8.702e-06 | 0
2013-10-11 09:50 | TGN31 | LONG RURAL |  | 2 | 120 | 240 | 0.00092936 | 7.7446e-06 | 0
2013-10-11 09:02 | TGN31 | LONG RURAL |  | 12 | 203 | 2436 | 0.009433 | 4.6468e-05 | 0
2013-10-10 11:30 | WOTS24 | LONG RURAL |  | 2 | 170 | 340 | 0.0013166 | 7.7446e-06 | 0
2013-10-11 08:44 | WOTS11 | LONG RURAL |  | 506 | 14 | 7084 | 0.027431 | 0.0019594 | 0
2013-10-11 08:58 | WOTS11 | LONG RURAL |  | 84 | 271 | 22764 | 0.088149 | 0.00032527 | 0
2013-10-11 09:20 | WOTS24 | LONG RURAL |  | 2 | 45 | 90 | 0.00034851 | 7.7446e-06 | 0
2013-10-11 09:05 | WOTS24 | LONG RURAL |  | 3 | 160 | 480 | 0.0018587 | 1.1617e-05 | 0
2013-10-11 09:45 | FTR23 | LONG RURAL |  | 18 | 100 | 1800 | 0.0069702 | 6.9702e-05 | 0
2013-10-11 09:20 | WOTS24 | LONG RURAL |  | 11 | 205 | 2255 | 0.0087321 | 4.2595e-05 | 0
2013-10-11 09:00 | FTR23 | LONG RURAL |  | 23 | 330 | 7590 | 0.029391 | 8.9063e-05 | 0
2013-10-11 09:00 | FTR23 | LONG RURAL |  | 60 | 470 | 28200 | 0.1092 | 0.00023234 | 0
2013-10-11 08:40 | WYK11 | SHORT RURAL |  | 72 | 120 | 8640 | 0.075185 | 0.00062654 | 0
2013-10-11 09:15 | MWTS21 | URBAN |  | 51 | 253 | 12903 | 0.044947 | 0.00017766 | 0
2013-10-11 09:10 | MOE22 | LONG RURAL |  | 1 | 75 | 75 | 0.00029042 | 3.8723e-06 | 0
2013-10-11 10:55 | MOE22 | LONG RURAL |  | 3 | 60 | 180 | 0.00069702 | 1.1617e-05 | 0
2013-10-10 12:55 | SMR8 | LONG RURAL |  | 1 | 120 | 120 | 0.00046468 | 3.8723e-06 | 0
2013-10-11 06:30 | DRN14 | SHORT RURAL |  | 45 | 120 | 5400 | 0.046991 | 0.00039159 | 0
2013-10-11 10:10 | ELM33 | SHORT RURAL |  | 471 | 352 | 165792 | 1.4427 | 0.0040986 | 0
2013-10-10 13:20 | BDL4 | SHORT RURAL |  | 63 | 150 | 9450 | 0.082234 | 0.00054822 | 0
2013-10-11 09:40 | DRN14 | SHORT RURAL |  | 49 | 470 | 23030 | 0.20041 | 0.0004264 | 0
2013-10-10 09:35 | ELM33 | SHORT RURAL |  | 45 | 185 | 8325 | 0.072444 | 0.00039159 | 0
2013-10-08 09:30 | WGL24 | LONG RURAL |  | 2 | 100 | 200 | 0.00077446 | 7.7446e-06 | 0
2013-10-10 09:20 | WGL23 | SHORT RURAL |  | 1 | 225 | 225 | 0.0019579 | 8.702e-06 | 0
2013-10-08 07:05 | MDG1 | SHORT RURAL |  | 62 | 753 | 46686 | 0.40626 | 0.00053952 | 0
2013-10-11 10:00 | KMS1 | SHORT RURAL |  | 11 | 171 | 1881 | 0.016368 | 9.5722e-05 | 0
2013-10-11 13:20 | WOTS11 | LONG RURAL |  | 506 | 9 | 4554 | 0.017635 | 0.0019594 | 0
2013-10-11 11:30 | WN3 | LONG RURAL |  | 4 | 182 | 728 | 0.002819 | 1.5489e-05 | 0
2013-10-12 09:10 | TGN11 | SHORT RURAL |  | 65 | 220 | 14300 | 0.12444 | 0.00056563 | 0
2013-10-12 09:00 | WGL23 | SHORT RURAL |  | 115 | 266 | 30590 | 0.26619 | 0.0010007 | 0
2013-10-07 09:30 | WOTS13 | LONG RURAL |  | 2 | 50 | 100 | 0.00038723 | 7.7446e-06 | 0
2013-10-07 11:30 | WOTS11 | LONG RURAL |  | 3 | 75 | 225 | 0.00087127 | 1.1617e-05 | 0
2013-10-10 09:05 | MFA22 | LONG RURAL |  | 79 | 325 | 25675 | 0.099422 | 0.00030591 | 0
2013-10-07 08:44 | WOTS11 | LONG RURAL |  | 1 | 96 | 96 | 0.00037174 | 3.8723e-06 | 0
2013-10-09 08:45 | SMR3 | LONG RURAL |  | 1 | 110 | 110 | 0.00042595 | 3.8723e-06 | 0
2013-10-11 08:35 | MFA21 | LONG RURAL |  | 18 | 375 | 6750 | 0.026138 | 6.9702e-05 | 0
2013-10-10 08:30 | SMR3 | LONG RURAL |  | 19 | 345 | 6555 | 0.025383 | 7.3574e-05 | 0
2013-10-11 08:40 | SMR3 | LONG RURAL |  | 12 | 270 | 3240 | 0.012546 | 4.6468e-05 | 0
2013-10-11 09:10 | BDL1 | LONG RURAL |  | 18 | 300 | 5400 | 0.02091 | 6.9702e-05 | 0
2013-10-11 09:25 | NLA31 | LONG RURAL |  | 1 | 105 | 105 | 0.00040659 | 3.8723e-06 | 0
2013-10-10 09:00 | SLE31 | LONG RURAL |  | 5 | 395 | 1975 | 0.0076478 | 1.9362e-05 | 0
2013-10-04 09:16 | LLG11 | SHORT RURAL |  | 2 | 304 | 608 | 0.0052908 | 1.7404e-05 | 0
2013-10-11 09:00 | MFA22 | LONG RURAL |  | 1 | 85 | 85 | 0.00032915 | 3.8723e-06 | 0
2013-10-08 09:05 | CYN31 | URBAN |  | 111 | 400 | 44400 | 0.15467 | 0.00038667 | 0
2013-10-11 10:40 | ALA01 | LONG RURAL |  | 7 | 170 | 1190 | 0.0046081 | 2.7106e-05 | 0
2013-10-04 10:10 | LLG11 | SHORT RURAL |  | 5 | 55 | 275 | 0.002393 | 4.351e-05 | 0
2013-10-08 08:30 | PHM14 | LONG RURAL |  | 34 | 415 | 14110 | 0.054638 | 0.00013166 | 0
2013-10-08 08:30 | PHM31 | SHORT RURAL |  | 9 | 415 | 3735 | 0.032502 | 7.8318e-05 | 0
2013-10-09 08:40 | BWN14 | SHORT RURAL |  | 5 | 220 | 1100 | 0.0095722 | 4.351e-05 | 0
2013-10-08 08:55 | CYN23 | URBAN |  | 150 | 269 | 40350 | 0.14056 | 0.00052252 | 0
2013-09-27 09:34 | MSD2 | LONG RURAL |  | 13 | 144 | 1872 | 0.007249 | 5.034e-05 | 0
2013-10-09 12:00 | CYN23 | URBAN |  | 129 | 240 | 30960 | 0.10785 | 0.00044937 | 0
2013-10-11 11:30 | BRT11 | SHORT RURAL |  | 12 | 75 | 900 | 0.0078318 | 0.00010442 | 0
2013-10-10 09:06 | CYN14 | URBAN |  | 134 | 364 | 48776 | 0.16991 | 0.00046679 | 0
2013-10-09 08:12 | CYN31 | URBAN |  | 298 | 402 | 119796 | 0.41731 | 0.0010381 | 0
2013-10-10 09:00 | CYN11 | URBAN |  | 177 | 180 | 31860 | 0.11098 | 0.00061658 | 0
2013-10-06 08:43 | BWR12 | URBAN |  | 111 | 307 | 34077 | 0.11871 | 0.00038667 | 0
2013-10-09 09:05 | BN2 | LONG RURAL |  | 1 | 108 | 108 | 0.00041821 | 3.8723e-06 | 0
2013-10-10 08:32 | BN6 | LONG RURAL |  | 2 | 286 | 572 | 0.002215 | 7.7446e-06 | 0
2013-10-10 12:05 | BN6 | LONG RURAL |  | 8 | 238 | 1904 | 0.0073729 | 3.0979e-05 | 0
2013-10-11 08:50 | BN2 | LONG RURAL |  | 8 | 130 | 1040 | 0.0040272 | 3.0979e-05 | 0
2013-10-10 09:55 | ELM15 | SHORT RURAL |  | 6 | 190 | 1140 | 0.0099202 | 5.2212e-05 | 0
2013-10-09 09:20 | LLG11 | SHORT RURAL |  | 6 | 310 | 1860 | 0.016186 | 5.2212e-05 | 0
2013-10-08 08:30 | WOTS13 | LONG RURAL |  | 1 | 170 | 170 | 0.00065829 | 3.8723e-06 | 0
2013-10-08 11:35 | WOTS13 | LONG RURAL |  | 1 | 50 | 50 | 0.00019362 | 3.8723e-06 | 0
2013-10-10 09:00 | BGE12 | SHORT RURAL |  | 423 | 570 | 241110 | 2.0981 | 0.0036809 | 0
2013-10-08 09:40 | BRA21 | URBAN |  | 597 | 248 | 148056 | 0.51575 | 0.0020796 | 0
2013-09-26 18:50 | SFS1 | SHORT RURAL |  | 112 | 70 | 7840 | 0.068223 | 0.00097462 | 0
2013-10-14 11:10 | TGN31 | LONG RURAL |  | 1 | 70 | 70 | 0.00027106 | 3.8723e-06 | 0
2013-10-14 09:15 | TGN31 | LONG RURAL |  | 1 | 330 | 330 | 0.0012779 | 3.8723e-06 | 0
2013-10-14 08:33 | WN3 | LONG RURAL |  | 35 | 406 | 14210 | 0.055026 | 0.00013553 | 0
2013-10-14 09:15 | MOE31 | LONG RURAL |  | 40 | 364 | 14560 | 0.056381 | 0.00015489 | 0
2013-10-13 11:17 | WT12 | URBAN |  | 226 | 73 | 16498 | 0.057471 | 0.00078727 | 0
2013-10-14 10:00 | KLO14 | LONG RURAL |  | 70 | 260 | 18200 | 0.070476 | 0.00027106 | 0
2013-10-14 09:13 | SMR8 | LONG RURAL |  | 16 | 172 | 2752 | 0.010657 | 6.1957e-05 | 0
2013-10-11 13:35 | SMR3 | LONG RURAL |  | 1 | 130 | 130 | 0.0005034 | 3.8723e-06 | 0
2013-10-14 08:55 | SMR3 | LONG RURAL |  | 1 | 185 | 185 | 0.00071638 | 3.8723e-06 | 0
2013-10-08 09:25 | WOTS11 | LONG RURAL |  | 1 | 275 | 275 | 0.0010649 | 3.8723e-06 | 0
2013-10-09 09:00 | WGL12 | LONG RURAL |  | 40 | 270 | 10800 | 0.041821 | 0.00015489 | 0
2013-10-10 08:50 | CYN21 | URBAN |  | 570 | 325 | 185250 | 0.64532 | 0.0019856 | 0
2013-10-10 08:45 | PHM14 | LONG RURAL |  | 49 | 265 | 12985 | 0.050282 | 0.00018974 | 0
2013-10-10 08:45 | PHM14 | LONG RURAL |  | 41 | 300 | 12300 | 0.047629 | 0.00015876 | 0
2013-10-10 08:45 | PHM14 | LONG RURAL |  | 90 | 265 | 23850 | 0.092355 | 0.00034851 | 0
2013-10-10 08:45 | PHM14 | LONG RURAL |  | 363 | 208 | 75504 | 0.29238 | 0.0014057 | 0
2013-10-11 08:55 | PHM14 | LONG RURAL |  | 1 | 75 | 75 | 0.00029042 | 3.8723e-06 | 0
2013-10-11 08:35 | OFR23 | LONG RURAL |  | 147 | 351 | 51597 | 0.1998 | 0.00056923 | 0
2013-10-14 08:40 | LLG14 | SHORT RURAL |  | 2 | 90 | 180 | 0.0015664 | 1.7404e-05 | 0
2013-10-11 09:00 | CYN14 | URBAN |  | 232 | 460 | 106720 | 0.37176 | 0.00080817 | 0
2013-10-09 09:00 | BN3 | SHORT RURAL |  | 12 | 240 | 2880 | 0.025062 | 0.00010442 | 0
2013-10-09 13:35 | BN3 | SHORT RURAL |  | 2 | 80 | 160 | 0.0013923 | 1.7404e-05 | 0
2013-10-11 08:50 | CYN22 | URBAN |  | 315 | 415 | 130725 | 0.45538 | 0.0010973 | 0
2013-10-09 08:22 | RWT14 | URBAN |  | 106 | 440 | 46640 | 0.16247 | 0.00036925 | 0
2013-10-13 08:30 | CYN21 | URBAN |  | 9 | 225 | 2025 | 0.0070541 | 3.1351e-05 | 0
2013-10-14 09:45 | BRA33 | URBAN |  | 69 | 175 | 12075 | 0.042063 | 0.00024036 | 0
2013-10-14 09:15 | BRA14 | URBAN |  | 99 | 220 | 21780 | 0.07587 | 0.00034486 | 0
2013-09-30 14:03 | SMG23 | URBAN |  | 380 | 60 | 22800 | 0.079423 | 0.0013237 | 0
2013-10-15 09:43 | BWA23 | SHORT RURAL |  | 14 | 407 | 5698 | 0.049584 | 0.00012183 | 0
2013-10-17 09:10 | BWA23 | SHORT RURAL |  | 4 | 315 | 1260 | 0.010964 | 3.4808e-05 | 0
2013-10-15 09:20 | ELM33 | SHORT RURAL |  | 10 | 118 | 1180 | 0.010268 | 8.702e-05 | 0
2013-10-15 09:05 | LGA23 | LONG RURAL |  | 8 | 375 | 3000 | 0.011617 | 3.0979e-05 | 0
2013-10-16 09:40 | WOTS24 | LONG RURAL |  | 20 | 28.5 | 570 | 0.0022072 | 7.7446e-05 | 0
2013-10-16 08:47 | WOTS24 | LONG RURAL |  | 1 | 238 | 238 | 0.00092161 | 3.8723e-06 | 0
2013-10-15 09:00 | MSD1 | LONG RURAL |  | 52 | 335 | 17420 | 0.067456 | 0.00020136 | 0
2013-10-17 09:25 | MYT1 | SHORT RURAL |  | 12 | 260 | 3120 | 0.02715 | 0.00010442 | 0
2013-10-16 09:15 | MSD4 | LONG RURAL |  | 49 | 319.898 | 15675 | 0.060699 | 0.00018974 | 0
2013-10-17 09:05 | MSD2 | LONG RURAL |  | 25 | 393.4 | 9835 | 0.038084 | 9.6808e-05 | 0
2013-10-16 08:51 | TGN23 | SHORT RURAL |  | 79 | 402 | 31758 | 0.27636 | 0.00068746 | 0
2013-10-17 10:03 | BN1 | LONG RURAL |  | 45 | 326.8444 | 14708 | 0.056954 | 0.00017425 | 0
2013-10-15 09:05 | MOE31 | LONG RURAL |  | 20 | 270 | 5400 | 0.02091 | 7.7446e-05 | 0
2013-10-17 09:02 | WOTS24 | LONG RURAL |  | 146 | 317 | 46282 | 0.17922 | 0.00056536 | 0
2013-10-15 09:20 | LGA24 | SHORT RURAL |  | 41 | 297 | 12177 | 0.10596 | 0.00035678 | 0
2013-10-16 09:00 | WO32 | URBAN |  | 2 | 315 | 630 | 0.0021946 | 6.967e-06 | 0
2013-10-16 09:05 | MOE31 | LONG RURAL |  | 36 | 360 | 12960 | 0.050185 | 0.0001394 | 0
2013-10-16 08:05 | LDL13 | SHORT RURAL |  | 84 | 235 | 19740 | 0.17178 | 0.00073097 | 0
2013-10-16 09:00 | KLK1 | SHORT RURAL |  | 367 | 294 | 107898 | 0.93893 | 0.0031936 | 0
2013-10-16 09:45 | LDL11 | URBAN |  | 203 | 405 | 82215 | 0.28639 | 0.00070715 | 0
2013-10-16 09:10 | LDL24 | URBAN |  | 53 | 440 | 23320 | 0.081235 | 0.00018462 | 0
2013-10-17 09:00 | WOTS13 | LONG RURAL |  | 23 | 217 | 4991 | 0.019327 | 8.9063e-05 | 0
2013-10-16 08:39 | WYK23 | SHORT RURAL |  | 1207 | 507.2999 | 612311 | 5.3283 | 0.010503 | 0
2013-10-15 09:20 | WGL23 | SHORT RURAL |  | 8 | 290 | 2320 | 0.020189 | 6.9616e-05 | 0
2013-10-15 09:30 | DRN12 | URBAN |  | 63 | 310 | 19530 | 0.068032 | 0.00021946 | 0
2013-10-16 09:10 | WGI23 | SHORT RURAL |  | 23 | 170 | 3910 | 0.034025 | 0.00020015 | 0
2013-10-15 09:15 | LDL13 | SHORT RURAL |  | 55 | 370 | 20350 | 0.17709 | 0.00047861 | 0
2013-10-16 09:53 | FTR12 | LONG RURAL |  | 2 | 59 | 118 | 0.00045693 | 7.7446e-06 | 0
2013-10-16 09:45 | WGI33 | SHORT RURAL |  | 12 | 185 | 2220 | 0.019318 | 0.00010442 | 0
2013-10-17 09:00 | WGI33 | SHORT RURAL |  | 97 | 120 | 11640 | 0.10129 | 0.00084409 | 0
2013-10-17 09:15 | FTR23 | LONG RURAL |  | 137 | 395 | 54115 | 0.20955 | 0.00053051 | 0
2013-10-17 10:37 | LDL13 | SHORT RURAL |  | 74 | 347 | 25678 | 0.22345 | 0.00064395 | 0
2013-10-17 09:18 | WYK11 | SHORT RURAL |  | 2 | 32 | 64 | 0.00055693 | 1.7404e-05 | 0
2013-10-17 09:00 | MOE31 | LONG RURAL |  | 24 | 180 | 4320 | 0.016728 | 9.2936e-05 | 0
2013-10-17 11:30 | WYK23 | SHORT RURAL |  | 43 | 286 | 12298 | 0.10702 | 0.00037418 | 0
2013-10-14 13:05 | SMR3 | LONG RURAL |  | 1 | 155 | 155 | 0.00060021 | 3.8723e-06 | 0
2013-10-17 10:35 | LGA11 | LONG RURAL |  | 41 | 70 | 2870 | 0.011114 | 0.00015876 | 0
2013-10-16 11:30 | LDL13 | SHORT RURAL |  | 132 | 255 | 33660 | 0.29291 | 0.0011487 | 0
2013-10-17 10:00 | WYK23 | SHORT RURAL |  | 26 | 450 | 11700 | 0.10181 | 0.00022625 | 0
2013-10-15 08:30 | MSD1 | LONG RURAL |  | 242 | 445 | 107690 | 0.41701 | 0.0009371 | 0
2013-10-16 09:30 | BWA23 | SHORT RURAL |  | 7 | 285 | 1995 | 0.01736 | 6.0914e-05 | 0
2013-10-16 09:10 | DRN12 | URBAN |  | 43 | 312 | 13416 | 0.046734 | 0.00014979 | 0
2013-10-16 09:30 | WGL23 | SHORT RURAL |  | 1 | 20 | 20 | 0.00017404 | 8.702e-06 | 0
2013-10-16 12:08 | BN2 | LONG RURAL |  | 4 | 39 | 156 | 0.00060408 | 1.5489e-05 | 0
2013-10-17 10:15 | KLK2 | SHORT RURAL |  | 3 | 360 | 1080 | 0.0093981 | 2.6106e-05 | 0
2013-10-16 09:30 | DRN12 | URBAN |  | 51 | 335 | 17085 | 0.059515 | 0.00017766 | 0
2013-10-12 06:36 | BGE12 | SHORT RURAL |  | 1622 | 302.2022 | 490172 | 4.2655 | 0.014115 | 0
2013-10-15 07:10 | CYN22 | URBAN |  | 74 | 172 | 12728 | 0.044338 | 0.00025778 | 0
2013-10-17 08:45 | BRA21 | URBAN |  | 4 | 350 | 1400 | 0.0048769 | 1.3934e-05 | 0
2013-10-14 09:00 | NLA34 | SHORT RURAL |  | 1 | 80 | 80 | 0.00069616 | 8.702e-06 | 0
2013-10-14 09:30 | MFA34 | SHORT RURAL |  | 2 | 50 | 100 | 0.0008702 | 1.7404e-05 | 0
2013-10-14 11:15 | MFA34 | SHORT RURAL |  | 4 | 60 | 240 | 0.0020885 | 3.4808e-05 | 0
2013-10-14 13:15 | MFA34 | SHORT RURAL |  | 1 | 60 | 60 | 0.00052212 | 8.702e-06 | 0
2013-10-15 09:30 | BDL1 | LONG RURAL |  | 1 | 190 | 190 | 0.00073574 | 3.8723e-06 | 0
2013-10-15 09:00 | SLE21 | SHORT RURAL |  | 1 | 45 | 45 | 0.00039159 | 8.702e-06 | 0
2013-10-15 09:00 | BDL1 | LONG RURAL |  | 1 | 190 | 190 | 0.00073574 | 3.8723e-06 | 0
2013-10-17 09:15 | CYN14 | URBAN |  | 131 | 300 | 39300 | 0.1369 | 0.00045634 | 0
2013-10-15 12:50 | MFA22 | LONG RURAL |  | 2 | 175 | 350 | 0.0013553 | 7.7446e-06 | 0
2013-10-14 09:04 | RWN22 | URBAN |  | 57 | 281 | 16017 | 0.055795 | 0.00019856 | 0
2013-10-15 09:30 | ELM33 | SHORT RURAL |  | 46 | 295 | 13570 | 0.11809 | 0.00040029 | 0
2013-10-15 12:40 | RWN24 | SHORT RURAL |  | 1 | 180 | 180 | 0.0015664 | 8.702e-06 | 0
2013-10-16 08:10 | RWN26 | SHORT RURAL |  | 40 | 462 | 18480 | 0.16081 | 0.00034808 | 0
2013-10-16 09:30 | BRA32 | URBAN |  | 63 | 230 | 14490 | 0.050476 | 0.00021946 | 0
2013-10-10 09:50 | DRN13 | SHORT RURAL |  | 106 | 260 | 27560 | 0.23983 | 0.00092241 | 0
2013-10-11 09:05 | SMR3 | LONG RURAL |  | 10 | 200 | 2000 | 0.0077446 | 3.8723e-05 | 0
2013-10-13 09:05 | KMS1 | SHORT RURAL |  | 26 | 375 | 9750 | 0.084844 | 0.00022625 | 0
2013-10-17 09:15 | LLG12 | SHORT RURAL |  | 4 | 65 | 260 | 0.0022625 | 3.4808e-05 | 0
2013-10-17 09:30 | ELM33 | SHORT RURAL |  | 12 | 225 | 2700 | 0.023495 | 0.00010442 | 0
2013-10-15 08:30 | SMR3 | LONG RURAL |  | 18 | 115 | 2070 | 0.0080157 | 6.9702e-05 | 0
2013-10-06 08:30 | BRA13 | URBAN |  | 31 | 419 | 12989 | 0.045247 | 0.00010799 | 0
2013-10-09 13:40 | OFR23 | LONG RURAL |  | 1 | 40 | 40 | 0.00015489 | 3.8723e-06 | 0
2013-10-16 08:30 | CYN32 | URBAN |  | 128 | 330 | 42240 | 0.14714 | 0.00044589 | 0
2013-10-18 09:00 | WGL23 | SHORT RURAL |  | 76 | 254.3421 | 19330 | 0.16821 | 0.00066135 | 0
2013-10-18 10:50 | FTR12 | LONG RURAL |  | 4 | 137 | 548 | 0.002122 | 1.5489e-05 | 0
2013-10-17 12:55 | MOE31 | LONG RURAL |  | 3 | 5 | 15 | 5.8085e-05 | 1.1617e-05 | 0
2013-10-18 11:20 | WYK12 | SHORT RURAL |  | 23 | 300 | 6900 | 0.060044 | 0.00020015 | 0
2013-10-18 09:40 | WYK23 | SHORT RURAL |  | 7 | 205 | 1435 | 0.012487 | 6.0914e-05 | 0
2013-10-18 08:45 | BN3 | SHORT RURAL |  | 1 | 94 | 94 | 0.00081799 | 8.702e-06 | 0
2013-10-15 13:45 | SLE21 | SHORT RURAL |  | 5 | 65 | 325 | 0.0028281 | 4.351e-05 | 0
2013-10-27 08:34 | BRA21 | URBAN |  | 286 | 391 | 111826 | 0.38954 | 0.00099628 | 0
2013-10-17 11:50 | LGA12 | SHORT RURAL |  | 5 | 125 | 625 | 0.0054387 | 4.351e-05 | 0
2013-10-15 08:30 | ELM33 | SHORT RURAL |  | 2 | 370 | 740 | 0.0064395 | 1.7404e-05 | 0
2013-10-16 08:41 | MFA34 | SHORT RURAL |  | 8 | 309 | 2472 | 0.021511 | 6.9616e-05 | 0
2013-10-16 09:45 | NLA34 | SHORT RURAL |  | 1 | 130 | 130 | 0.0011313 | 8.702e-06 | 0
2013-10-16 09:25 | BDL1 | LONG RURAL |  | 26 | 420 | 10920 | 0.042286 | 0.00010068 | 0
2013-10-15 09:05 | SFS1 | SHORT RURAL |  | 6 | 420 | 2520 | 0.021929 | 5.2212e-05 | 0
2013-10-16 09:20 | BDL6 | SHORT RURAL |  | 1 | 225 | 225 | 0.0019579 | 8.702e-06 | 0
2013-10-16 09:00 | BGE22 | SHORT RURAL |  | 111 | 173 | 19203 | 0.1671 | 0.00096592 | 0
2013-10-16 09:20 | NLA34 | SHORT RURAL |  | 1 | 278 | 278 | 0.0024191 | 8.702e-06 | 0
2013-10-16 09:00 | MFA22 | LONG RURAL |  | 3 | 185 | 555 | 0.0021491 | 1.1617e-05 | 0
2013-10-16 13:00 | NLA34 | SHORT RURAL |  | 1 | 70 | 70 | 0.00060914 | 8.702e-06 | 0
2013-10-15 08:00 | CYN14 | URBAN |  | 86 | 400 | 34400 | 0.11983 | 0.00029958 | 0
2013-10-17 08:58 | LYD14 | SHORT RURAL |  | 151 | 287 | 43337 | 0.37712 | 0.001314 | 0
2013-10-16 14:00 | BDL6 | SHORT RURAL |  | 2 | 40 | 80 | 0.00069616 | 1.7404e-05 | 0
2013-10-18 11:30 | MOE22 | LONG RURAL |  | 2 | 35 | 70 | 0.00027106 | 7.7446e-06 | 0
2013-10-18 09:10 | MOE22 | LONG RURAL |  | 8 | 120 | 960 | 0.0037174 | 3.0979e-05 | 0
2013-10-17 09:00 | SLE21 | SHORT RURAL |  | 1 | 43 | 43 | 0.00037418 | 8.702e-06 | 0
2013-10-17 09:12 | MFA22 | LONG RURAL |  | 26 | 148 | 3848 | 0.014901 | 0.00010068 | 0
2013-10-18 09:10 | MOE22 | LONG RURAL |  | 2 | 45 | 90 | 0.00034851 | 7.7446e-06 | 0
2013-10-08 10:20 | BN6 | LONG RURAL |  | 1 | 130 | 130 | 0.0005034 | 3.8723e-06 | 0
2013-10-17 09:00 | BDL4 | SHORT RURAL |  | 515 | 356 | 183340 | 1.5954 | 0.0044815 | 0
2013-10-18 09:05 | MOE22 | LONG RURAL |  | 1 | 70 | 70 | 0.00027106 | 3.8723e-06 | 0
2013-10-19 09:00 | WGL11 | SHORT RURAL |  | 1100 | 57.7745 | 63552 | 0.55303 | 0.0095722 | 0
2013-10-18 13:50 | FTR12 | LONG RURAL |  | 2 | 54 | 108 | 0.00041821 | 7.7446e-06 | 0
2013-10-19 08:32 | BDL5 | LONG RURAL |  | 599 | 504.7462 | 302343 | 1.1708 | 0.0023195 | 0
2013-10-19 08:30 | BDL8 | LONG RURAL |  | 2063 | 456.0722 | 940877 | 3.6434 | 0.0079886 | 0
2013-10-19 08:36 | CNR1 | SHORT RURAL |  | 154 | 510 | 78540 | 0.68345 | 0.0013401 | 0
2013-10-19 08:36 | CNR2 | SHORT RURAL |  | 1187 | 510 | 605370 | 5.2679 | 0.010329 | 0
2013-10-19 08:36 | CNR3 | SHORT RURAL |  | 63 | 510 | 32130 | 0.27959 | 0.00054822 | 0
2013-10-19 08:36 | NLA31 | LONG RURAL |  | 897 | 506 | 453882 | 1.7576 | 0.0034735 | 0
2013-10-19 08:36 | NLA32 | SHORT RURAL |  | 1451 | 507 | 735657 | 6.4017 | 0.012627 | 0
2013-10-17 09:20 | NLA34 | SHORT RURAL |  | 5 | 280 | 1400 | 0.012183 | 4.351e-05 | 0
2013-10-17 11:20 | MFA23 | SHORT RURAL |  | 4 | 50 | 200 | 0.0017404 | 3.4808e-05 | 0
2013-10-17 13:10 | MFA23 | SHORT RURAL |  | 1 | 11 | 11 | 9.5722e-05 | 8.702e-06 | 0
2013-10-13 10:33 | BDL3 | SHORT RURAL |  | 48 | 132 | 6336 | 0.055136 | 0.00041769 | 0
2013-10-18 08:50 | BDL1 | LONG RURAL |  | 4 | 95 | 380 | 0.0014715 | 1.5489e-05 | 0
2013-10-18 10:25 | MOE22 | LONG RURAL |  | 2 | 40 | 80 | 0.00030979 | 7.7446e-06 | 0
2013-10-04 11:35 | LLG11 | SHORT RURAL |  | 3 | 55 | 165 | 0.0014358 | 2.6106e-05 | 0
2013-10-18 09:25 | ELM33 | SHORT RURAL |  | 61 | 362 | 22082 | 0.19216 | 0.00053082 | 0
2013-10-17 09:30 | ELM32 | URBAN |  | 9 | 70 | 630 | 0.0021946 | 3.1351e-05 | 0
2013-10-18 11:10 | MOE22 | LONG RURAL |  | 1 | 40 | 40 | 0.00015489 | 3.8723e-06 | 0
2013-10-17 11:10 | ELM31 | URBAN |  | 128 | 75 | 9600 | 0.033441 | 0.00044589 | 0
2013-10-18 10:00 | WGL24 | LONG RURAL |  | 6 | 10 | 60 | 0.00023234 | 2.3234e-05 | 0
2013-10-17 09:50 | EPG11 | URBAN |  | 89 | 140 | 12460 | 0.043404 | 0.00031003 | 0
2013-10-15 09:00 | LLG11 | SHORT RURAL |  | 57 | 310 | 17670 | 0.15376 | 0.00049601 | 0
2013-10-16 10:26 | PHM14 | LONG RURAL |  | 133 | 169 | 22477 | 0.087038 | 0.00051502 | 0
2013-10-03 10:30 | MBY11 | SHORT RURAL |  | 43 | 260 | 11180 | 0.097288 | 0.00037418 | 0
2013-10-20 08:33 | BDL5 | LONG RURAL |  | 2583 | 480 | 1239840 | 4.8011 | 0.010002 | 0
2013-10-20 08:33 | CNR1 | SHORT RURAL |  | 1404 | 480 | 673920 | 5.8644 | 0.012218 | 0
2013-10-17 09:20 | SMR8 | LONG RURAL |  | 2 | 110 | 220 | 0.00085191 | 7.7446e-06 | 0
2013-10-17 12:05 | SMR8 | LONG RURAL |  | 1 | 45 | 45 | 0.00017425 | 3.8723e-06 | 0
2013-10-13 09:00 | CF1 | SHORT RURAL |  | 2 | 374 | 748 | 0.0065091 | 1.7404e-05 | 0
2013-10-13 09:00 | CF2 | SHORT RURAL |  | 2 | 381 | 762 | 0.0066309 | 1.7404e-05 | 0
2013-10-05 09:15 | LGA11 | LONG RURAL |  | 157 | 375 | 58875 | 0.22798 | 0.00060795 | 0
2013-10-21 11:00 | CYN31 | URBAN |  | 425 | 270 | 114750 | 0.39973 | 0.0014805 | 0
2013-10-24 08:47 | CYN13 | URBAN |  | 132 | 433 | 57156 | 0.1991 | 0.00045982 | 0
2013-10-17 09:10 | RWN22 | URBAN |  | 147 | 275 | 40425 | 0.14082 | 0.00051207 | 0
2013-10-21 11:50 | FTR21 | LONG RURAL |  | 1 | 25 | 25 | 9.6808e-05 | 3.8723e-06 | 0
2013-10-21 09:35 | ELM33 | SHORT RURAL |  | 2 | 295 | 590 | 0.0051342 | 1.7404e-05 | 0
2013-10-17 08:40 | BN3 | SHORT RURAL |  | 30 | 245 | 7350 | 0.063959 | 0.00026106 | 0
2013-10-21 08:30 | LDL21 | SHORT RURAL |  | 244 | 420 | 102480 | 0.89178 | 0.0021233 | 0
2013-10-21 10:03 | NLA34 | SHORT RURAL |  | 1 | 25 | 25 | 0.00021755 | 8.702e-06 | 0
2013-10-21 09:55 | NLA34 | SHORT RURAL |  | 64 | 105 | 6720 | 0.058477 | 0.00055693 | 0
2013-10-21 08:35 | BDL3 | SHORT RURAL |  | 2 | 55 | 110 | 0.00095722 | 1.7404e-05 | 0
2013-10-21 09:00 | SLE31 | LONG RURAL |  | 53 | 465 | 24645 | 0.095433 | 0.00020523 | 0
2013-10-21 10:35 | BDL3 | SHORT RURAL |  | 2 | 55 | 110 | 0.00095722 | 1.7404e-05 | 0
2013-10-15 10:40 | WOTS13 | LONG RURAL |  | 2 | 180 | 360 | 0.001394 | 7.7446e-06 | 0
2013-10-21 08:55 | CNR2 | SHORT RURAL |  | 10 | 510 | 5100 | 0.04438 | 8.702e-05 | 0
2013-10-15 09:35 | WYK24 | SHORT RURAL |  | 44 | 360 | 15840 | 0.13784 | 0.00038289 | 0
2013-10-17 09:50 | WT13 | URBAN |  | 49 | 325 | 15925 | 0.055474 | 0.00017069 | 0
2013-10-17 09:40 | BGE11 | SHORT RURAL |  | 13 | 0 | 0 | 0 | 0.00011313 | 0
2013-10-17 08:32 | WYK24 | SHORT RURAL |  | 8 | 176 | 1408 | 0.012252 | 6.9616e-05 | 0
2013-10-13 09:00 | TT2 | URBAN |  | 24 | 110 | 2640 | 0.0091964 | 8.3604e-05 | 0
2013-10-16 10:45 | PHM14 | LONG RURAL |  | 40 | 240 | 9600 | 0.037174 | 0.00015489 | 0
2013-10-17 08:53 | CRE31 | URBAN |  | 64 | 282 | 18048 | 0.06287 | 0.00022294 | 0
2013-10-17 09:10 | OFR23 | LONG RURAL |  | 122 | 332 | 40504 | 0.15684 | 0.00047242 | 0
2013-10-17 09:00 | PHM31 | SHORT RURAL |  | 2 | 235 | 470 | 0.0040899 | 1.7404e-05 | 0
2013-10-18 09:00 | PHM14 | LONG RURAL |  | 2 | 75 | 150 | 0.00058085 | 7.7446e-06 | 0
2013-10-18 09:30 | PHM14 | LONG RURAL |  | 10 | 175 | 1750 | 0.0067766 | 3.8723e-05 | 0
2013-10-18 10:38 | PHM14 | LONG RURAL |  | 1 | 4 | 4 | 1.5489e-05 | 3.8723e-06 | 0
2013-10-20 08:30 | CRE32 | URBAN |  | 30 | 305 | 9150 | 0.031874 | 0.0001045 | 0
2013-10-20 08:38 | OFR24 | URBAN |  | 2 | 344 | 688 | 0.0023966 | 6.967e-06 | 0
2013-10-05 11:43 | BRA13 | URBAN |  | 197 | 273 | 53781 | 0.18735 | 0.00068625 | 0
2013-10-08 08:35 | BDL6 | SHORT RURAL |  | 1202 | 510 | 613020 | 5.3345 | 0.01046 | 0
2013-10-22 09:26 | BWA23 | SHORT RURAL |  | 16 | 184 | 2944 | 0.025619 | 0.00013923 | 0
2013-10-22 09:00 | WOTS24 | LONG RURAL |  | 19 | 240 | 4560 | 0.017658 | 7.3574e-05 | 0
2013-10-25 09:13 | BN2 | LONG RURAL |  | 637 | 159.9058 | 101860 | 0.39443 | 0.0024667 | 0
2013-10-23 08:50 | WN3 | LONG RURAL |  | 7 | 400 | 2800 | 0.010842 | 2.7106e-05 | 0
2013-10-25 09:00 | WN3 | LONG RURAL |  | 8 | 330 | 2640 | 0.010223 | 3.0979e-05 | 0
2013-10-23 08:39 | BN2 | LONG RURAL |  | 21 | 481 | 10101 | 0.039114 | 8.1319e-05 | 0
2013-10-22 09:03 | WGL15 | SHORT RURAL |  | 101 | 302 | 30502 | 0.26543 | 0.0008789 | 0
2013-10-24 09:01 | WOTS24 | LONG RURAL |  | 96 | 395 | 37920 | 0.14684 | 0.00037174 | 0
2013-10-25 09:40 | WOTS24 | LONG RURAL |  | 22 | 185 | 4070 | 0.01576 | 8.5191e-05 | 0
2013-10-24 08:55 | WN2 | LONG RURAL |  | 17 | 355 | 6035 | 0.023369 | 6.5829e-05 | 0
2013-10-22 09:00 | MOE31 | LONG RURAL |  | 9 | 422 | 3798 | 0.014707 | 3.4851e-05 | 0
2013-10-22 10:10 | MOE31 | LONG RURAL |  | 1 | 125 | 125 | 0.00048404 | 3.8723e-06 | 0
2013-10-25 09:56 | WN2 | LONG RURAL |  | 2 | 22 | 44 | 0.00017038 | 7.7446e-06 | 0
2013-10-25 08:50 | BN1 | LONG RURAL |  | 2 | 155 | 310 | 0.0012004 | 7.7446e-06 | 0
2013-10-22 09:45 | BWR34 | URBAN |  | 588 | 275 | 161700 | 0.56328 | 0.0020483 | 0
2013-10-25 09:04 | BWR13 | SHORT RURAL |  | 114 | 343 | 39102 | 0.34026 | 0.00099202 | 0
2013-10-22 10:10 | MOE21 | SHORT RURAL |  | 1 | 138 | 138 | 0.0012009 | 8.702e-06 | 0
2013-10-22 09:10 | LDL23 | LONG RURAL |  | 41 | 297 | 12177 | 0.047153 | 0.00015876 | 0
2013-10-23 09:40 | MOE21 | SHORT RURAL |  | 17 | 270 | 4590 | 0.039942 | 0.00014793 | 0
2013-10-24 08:30 | MOE32 | SHORT RURAL |  | 11 | 149 | 1639 | 0.014263 | 9.5722e-05 | 0
2013-10-25 09:30 | MWTS14 | SHORT RURAL |  | 50 | 343 | 17150 | 0.14924 | 0.0004351 | 0
2013-10-23 08:38 | WGI22 | LONG RURAL |  | 62 | 429 | 26598 | 0.103 | 0.00024008 | 0
2013-10-23 09:20 | WGL15 | SHORT RURAL |  | 77 | 10 | 770 | 0.0067005 | 0.00067005 | 0
2013-10-23 10:05 | WGL15 | SHORT RURAL |  | 11 | 10 | 110 | 0.00095722 | 9.5722e-05 | 0
2013-10-25 09:00 | MOE31 | LONG RURAL |  | 72 | 189 | 13608 | 0.052694 | 0.00027881 | 0
2013-10-25 08:00 | WGI33 | SHORT RURAL |  | 1 | 115 | 115 | 0.0010007 | 8.702e-06 | 0
2013-10-24 09:00 | FTR23 | LONG RURAL |  | 33 | 320 | 10560 | 0.040892 | 0.00012779 | 0
2013-10-24 10:15 | ELM34 | URBAN |  | 45 | 225 | 10125 | 0.03527 | 0.00015676 | 0
2013-10-24 09:35 | MWTS14 | SHORT RURAL |  | 23 | 275 | 6325 | 0.05504 | 0.00020015 | 0
2013-10-22 09:30 | WYK12 | SHORT RURAL |  | 3 | 156 | 468 | 0.0040725 | 2.6106e-05 | 0
2013-10-24 08:32 | LDL23 | LONG RURAL |  | 23 | 448 | 10304 | 0.0399 | 8.9063e-05 | 0
2013-10-25 09:40 | LDL23 | LONG RURAL |  | 58 | 450 | 26100 | 0.10107 | 0.00022459 | 0
2013-10-25 08:55 | KLK1 | SHORT RURAL |  | 70 | 290 | 20300 | 0.17665 | 0.00060914 | 0
2013-10-24 09:00 | LGA23 | LONG RURAL |  | 5 | 145 | 725 | 0.0028074 | 1.9362e-05 | 0
2013-10-24 08:40 | LDL23 | LONG RURAL |  | 125 | 170 | 21250 | 0.082287 | 0.00048404 | 0
2013-10-24 10:40 | MWTS14 | SHORT RURAL |  | 1 | 40 | 40 | 0.00034808 | 8.702e-06 | 0
2013-10-22 08:40 | WYK24 | SHORT RURAL |  | 35 | 155 | 5425 | 0.047208 | 0.00030457 | 0
2013-10-23 08:45 | LDL23 | LONG RURAL |  | 37 | 245 | 9065 | 0.035103 | 0.00014328 | 0
2013-10-21 12:35 | NLA34 | SHORT RURAL |  | 4 | 105 | 420 | 0.0036548 | 3.4808e-05 | 0
2013-10-23 11:15 | MOE22 | LONG RURAL |  | 4 | 220 | 880 | 0.0034076 | 1.5489e-05 | 0
2013-10-23 12:05 | MOE22 | LONG RURAL |  | 2 | 25 | 50 | 0.00019362 | 7.7446e-06 | 0
2013-10-24 11:50 | LGA23 | LONG RURAL |  | 1 | 46 | 46 | 0.00017813 | 3.8723e-06 | 0
2013-10-24 12:50 | LGA23 | LONG RURAL |  | 2 | 125 | 250 | 0.00096808 | 7.7446e-06 | 0
2013-10-22 11:00 | SMR3 | LONG RURAL |  | 2 | 270 | 540 | 0.002091 | 7.7446e-06 | 0
2013-10-22 09:30 | SMR8 | LONG RURAL |  | 3 | 195 | 585 | 0.0022653 | 1.1617e-05 | 0
2013-10-25 09:25 | LGA14 | LONG RURAL |  | 3 | 345 | 1035 | 0.0040078 | 1.1617e-05 | 0
2013-10-22 08:32 | SLE31 | LONG RURAL |  | 1 | 386 | 386 | 0.0014947 | 3.8723e-06 | 0
2013-10-22 08:50 | MFA21 | LONG RURAL |  | 29 | 48 | 1392 | 0.0053903 | 0.0001123 | 0
2013-10-24 12:20 | MOE22 | LONG RURAL |  | 2 | 10 | 20 | 7.7446e-05 | 7.7446e-06 | 0
2013-10-24 09:20 | MSD2 | LONG RURAL |  | 36 | 355 | 12780 | 0.049488 | 0.0001394 | 0
2013-10-24 14:00 | MOE22 | LONG RURAL |  | 2 | 55 | 110 | 0.00042595 | 7.7446e-06 | 0
2013-10-24 09:04 | MSD2 | LONG RURAL |  | 14 | 335 | 4690 | 0.018161 | 5.4212e-05 | 0
2013-10-23 10:00 | TGN31 | LONG RURAL |  | 3 | 28 | 84 | 0.00032527 | 1.1617e-05 | 0
2013-10-22 09:57 | DRN23 | LONG RURAL |  | 963 | 97 | 93411 | 0.36172 | 0.003729 | 0
2013-10-22 08:30 | LDL13 | SHORT RURAL |  | 31 | 420 | 13020 | 0.1133 | 0.00026976 | 0
2013-10-25 09:35 | WYK24 | SHORT RURAL |  | 5 | 265 | 1325 | 0.01153 | 4.351e-05 | 0
2013-10-15 10:51 | NLA34 | SHORT RURAL |  | 2 | 354 | 708 | 0.006161 | 1.7404e-05 | 0
2013-10-22 09:20 | BDL1 | LONG RURAL |  | 5 | 440 | 2200 | 0.0085191 | 1.9362e-05 | 0
2013-10-23 09:05 | MWTS31 | SHORT RURAL |  | 90 | 185 | 16650 | 0.14489 | 0.00078318 | 0
2013-10-23 08:35 | BDL6 | SHORT RURAL |  | 8 | 238 | 1904 | 0.016569 | 6.9616e-05 | 0
2013-10-23 09:55 | MWTS31 | SHORT RURAL |  | 2 | 55 | 110 | 0.00095722 | 1.7404e-05 | 0
2013-10-23 09:00 | MFA31 | SHORT RURAL |  | 52 | 160 | 8320 | 0.0724 | 0.0004525 | 0
2013-10-23 09:00 | SLE31 | LONG RURAL |  | 1 | 315 | 315 | 0.0012198 | 3.8723e-06 | 0
2013-10-23 10:00 | SLE31 | LONG RURAL |  | 55 | 80 | 4400 | 0.017038 | 0.00021298 | 0
2013-10-25 09:10 | CYN14 | URBAN |  | 186 | 208.4839 | 38778 | 0.13508 | 0.00064793 | 0
2013-10-24 08:55 | MFA22 | LONG RURAL |  | 18 | 185 | 3330 | 0.012895 | 6.9702e-05 | 0
2013-10-25 08:30 | SLE31 | LONG RURAL |  | 78 | 335 | 26130 | 0.10118 | 0.00030204 | 0
2013-10-23 09:30 | BDL5 | LONG RURAL |  | 265 | 302 | 80030 | 0.3099 | 0.0010262 | 0
2013-10-13 08:50 | MSD1 | LONG RURAL |  | 61 | 445 | 27145 | 0.10511 | 0.00023621 | 0
2013-10-23 09:45 | CNR1 | SHORT RURAL |  | 11 | 285 | 3135 | 0.027281 | 9.5722e-05 | 0
2013-10-23 09:45 | CNR1 | SHORT RURAL |  | 3 | 234 | 702 | 0.0061088 | 2.6106e-05 | 0
2013-10-25 10:48 | FTR23 | LONG RURAL |  | 1 | 22 | 22 | 8.5191e-05 | 3.8723e-06 | 0
2013-10-23 12:45 | MWTS31 | SHORT RURAL |  | 158 | 140 | 22120 | 0.19249 | 0.0013749 | 0
2013-10-24 11:20 | CNR2 | SHORT RURAL |  | 2 | 45 | 90 | 0.00078318 | 1.7404e-05 | 0
2013-10-16 09:52 | OFR23 | LONG RURAL |  | 21 | 253 | 5313 | 0.020574 | 8.1319e-05 | 0
2013-10-20 10:02 | RWT15 | URBAN |  | 98 | 366 | 35868 | 0.12495 | 0.00034138 | 0
2013-10-20 10:02 | RWT22 | URBAN |  | 293 | 358 | 104894 | 0.3654 | 0.0010207 | 0
2013-10-24 11:10 | CNR2 | SHORT RURAL |  | 1 | 30 | 30 | 0.00026106 | 8.702e-06 | 0
2013-10-24 09:00 | CNR2 | SHORT RURAL |  | 1 | 110 | 110 | 0.00095722 | 8.702e-06 | 0
2013-10-24 08:35 | NLA34 | SHORT RURAL |  | 6 | 197 | 1182 | 0.010286 | 5.2212e-05 | 0
2013-10-17 13:50 | FGY33 | URBAN |  | 47 | 68 | 3196 | 0.011133 | 0.00016372 | 0
2013-10-16 08:40 | SMR3 | LONG RURAL |  | 2 | 300 | 600 | 0.0023234 | 7.7446e-06 | 0
2013-10-21 09:00 | BGE24 | SHORT RURAL |  | 11 | 450 | 4950 | 0.043075 | 9.5722e-05 | 0
2013-10-24 12:30 | NLA34 | SHORT RURAL |  | 2 | 140 | 280 | 0.0024366 | 1.7404e-05 | 0
2013-10-22 08:44 | BGE12 | SHORT RURAL |  | 119 | 344 | 40936 | 0.35622 | 0.0010355 | 0
2013-10-22 09:00 | WT11 | URBAN |  | 207 | 370 | 76590 | 0.2668 | 0.00072108 | 0
2013-10-22 10:45 | SFS1 | SHORT RURAL |  | 246 | 350 | 86100 | 0.74924 | 0.0021407 | 0
2013-10-11 09:03 | RWN26 | SHORT RURAL |  | 26 | 181 | 4706 | 0.040951 | 0.00022625 | 0
2013-10-25 09:10 | WN2 | LONG RURAL |  | 1 | 34 | 34 | 0.00013166 | 3.8723e-06 | 0
2013-10-26 10:30 | YN31 | URBAN |  | 10 | 155 | 1550 | 0.0053994 | 3.4835e-05 | 0
2013-10-26 08:00 | LDL14 | SHORT RURAL |  | 268 | 68 | 18224 | 0.15858 | 0.0023321 | 0
2013-10-25 11:35 | MOE32 | SHORT RURAL |  | 1 | 37 | 37 | 0.00032197 | 8.702e-06 | 0
2013-10-25 12:20 | MOE32 | SHORT RURAL |  | 3 | 65 | 195 | 0.0016969 | 2.6106e-05 | 0
2013-10-25 11:30 | FTR23 | LONG RURAL |  | 6 | 47 | 282 | 0.001092 | 2.3234e-05 | 0
2013-10-25 12:22 | FTR23 | LONG RURAL |  | 1 | 16 | 16 | 6.1957e-05 | 3.8723e-06 | 0
2013-10-26 09:10 | MOE22 | LONG RURAL |  | 2 | 120 | 240 | 0.00092936 | 7.7446e-06 | 0
2013-10-21 13:15 | ALA01 | LONG RURAL |  | 14 | 17 | 238 | 0.00092161 | 5.4212e-05 | 0
2013-10-23 08:40 | SMR3 | LONG RURAL |  | 1 | 245 | 245 | 0.00094872 | 3.8723e-06 | 0
2013-10-23 13:15 | SMR3 | LONG RURAL |  | 1 | 210 | 210 | 0.00081319 | 3.8723e-06 | 0
2013-10-24 13:08 | NLA34 | SHORT RURAL |  | 1 | 135 | 135 | 0.0011748 | 8.702e-06 | 0
2013-10-24 09:45 | BGE11 | SHORT RURAL |  | 195 | 313 | 61035 | 0.53112 | 0.0016969 | 0
2013-10-24 09:50 | SMR5 | LONG RURAL |  | 2 | 275 | 550 | 0.0021298 | 7.7446e-06 | 0
2013-10-15 10:48 | CYN22 | URBAN |  | 47 | 92 | 4324 | 0.015063 | 0.00016372 | 0
2013-10-24 09:40 | SLE21 | SHORT RURAL |  | 6 | 260 | 1560 | 0.013575 | 5.2212e-05 | 0
2013-10-24 08:58 | BDL6 | SHORT RURAL |  | 75 | 215 | 16125 | 0.14032 | 0.00065265 | 0
2013-10-24 08:35 | MSD2 | LONG RURAL |  | 998 | 113.0381 | 112812 | 0.43684 | 0.0038646 | 0
2013-10-21 09:55 | LLG11 | SHORT RURAL |  | 46 | 165 | 7590 | 0.066048 | 0.00040029 | 0
2013-10-21 13:55 | LLG11 | SHORT RURAL |  | 2 | 80 | 160 | 0.0013923 | 1.7404e-05 | 0
2013-10-27 09:03 | MWTS32 | SHORT RURAL |  | 307 | 361 | 110827 | 0.96441 | 0.0026715 | 0
2013-10-26 12:07 | LDL22 | SHORT RURAL |  | 186 | 63 | 11718 | 0.10197 | 0.0016186 | 0
2013-10-27 09:45 | MOE14 | SHORT RURAL |  | 34 | 180 | 6120 | 0.053256 | 0.00029587 | 0
2013-10-27 09:00 | LGA14 | LONG RURAL |  | 12 | 345 | 4140 | 0.016031 | 4.6468e-05 | 0
2013-10-26 11:55 | MOE22 | LONG RURAL |  | 4 | 145 | 580 | 0.0022459 | 1.5489e-05 | 0
2013-10-22 08:50 | PHM32 | URBAN |  | 296 | 180 | 53280 | 0.1856 | 0.0010311 | 0
2013-10-24 09:00 | DRN14 | SHORT RURAL |  | 6 | 115 | 690 | 0.0060044 | 5.2212e-05 | 0
2013-10-25 08:35 | BDL5 | LONG RURAL |  | 62 | 303 | 18786 | 0.072745 | 0.00024008 | 0
2013-10-22 13:20 | CLN22 | SHORT RURAL |  | 1 | 45 | 45 | 0.00039159 | 8.702e-06 | 0
2013-10-23 08:55 | PHM14 | LONG RURAL |  | 5 | 50 | 250 | 0.00096808 | 1.9362e-05 | 0
2013-10-21 11:00 | ELM33 | SHORT RURAL |  | 8 | 170 | 1360 | 0.011835 | 6.9616e-05 | 0
2013-10-23 08:40 | OFR23 | LONG RURAL |  | 12 | 438 | 5256 | 0.020353 | 4.6468e-05 | 0
2013-10-23 09:55 | PHM14 | LONG RURAL |  | 23 | 71 | 1633 | 0.0063235 | 8.9063e-05 | 0
2013-10-25 08:55 | BDL1 | LONG RURAL |  | 3 | 75 | 225 | 0.00087127 | 1.1617e-05 | 0
2013-10-23 09:10 | NLA34 | SHORT RURAL |  | 9 | 232 | 2088 | 0.01817 | 7.8318e-05 | 0
2013-10-25 10:20 | BDL1 | LONG RURAL |  | 3 | 95 | 285 | 0.0011036 | 1.1617e-05 | 0
2013-10-27 08:50 | MFA22 | LONG RURAL |  | 4 | 340 | 1360 | 0.0052663 | 1.5489e-05 | 0
2013-10-27 08:30 | MFA23 | SHORT RURAL |  | 7 | 172 | 1204 | 0.010477 | 6.0914e-05 | 0
2013-10-24 09:30 | PHM14 | LONG RURAL |  | 186 | 314 | 58404 | 0.22616 | 0.00072025 | 0
2013-10-24 09:30 | PHM14 | LONG RURAL |  | 51 | 335 | 17085 | 0.066158 | 0.00019749 | 0
2013-10-25 08:45 | PHM14 | LONG RURAL |  | 37 | 175 | 6475 | 0.025073 | 0.00014328 | 0
2013-10-25 09:00 | PHM33 | SHORT RURAL |  | 4 | 140 | 560 | 0.0048731 | 3.4808e-05 | 0
2013-10-25 12:01 | PHM14 | LONG RURAL |  | 1 | 69 | 69 | 0.00026719 | 3.8723e-06 | 0
2013-10-25 11:15 | PHM33 | SHORT RURAL |  | 3 | 276 | 828 | 0.0072052 | 2.6106e-05 | 0
2013-10-25 10:50 | KMS1 | SHORT RURAL |  | 1 | 215 | 215 | 0.0018709 | 8.702e-06 | 0
2013-10-26 09:35 | PHM14 | LONG RURAL |  | 65 | 562 | 36530 | 0.14146 | 0.0002517 | 0
2013-10-28 08:40 | WN3 | LONG RURAL |  | 23 | 430 | 9890 | 0.038297 | 8.9063e-05 | 0
2013-10-28 10:10 | WN5 | LONG RURAL |  | 28 | 145 | 4060 | 0.015722 | 0.00010842 | 0
2013-10-28 09:05 | MWTS24 | SHORT RURAL |  | 3 | 190 | 570 | 0.0049601 | 2.6106e-05 | 0
2013-10-28 08:35 | LDL23 | LONG RURAL |  | 50 | 256 | 12800 | 0.049566 | 0.00019362 | 0
2013-10-28 11:20 | WYK24 | SHORT RURAL |  | 22 | 260 | 5720 | 0.049775 | 0.00019144 | 0
2013-10-28 08:30 | LDL23 | LONG RURAL |  | 217 | 598 | 129766 | 0.50249 | 0.00084029 | 0
2013-10-28 12:45 | MWTS24 | SHORT RURAL |  | 2 | 105 | 210 | 0.0018274 | 1.7404e-05 | 0
2013-10-28 10:45 | MWTS24 | SHORT RURAL |  | 2 | 170 | 340 | 0.0029587 | 1.7404e-05 | 0
2013-10-28 10:42 | TGN31 | LONG RURAL |  | 1 | 98 | 98 | 0.00037949 | 3.8723e-06 | 0
2013-10-28 08:50 | SLE21 | SHORT RURAL |  | 4 | 55 | 220 | 0.0019144 | 3.4808e-05 | 0
2013-10-27 12:00 | MFA23 | SHORT RURAL |  | 21 | 180 | 3780 | 0.032893 | 0.00018274 | 0
2013-10-22 10:05 | ELM34 | URBAN |  | 60 | 230 | 13800 | 0.048072 | 0.00020901 | 0
2013-10-25 08:30 | RWN26 | SHORT RURAL |  | 67 | 400 | 26800 | 0.23321 | 0.00058303 | 0
2013-10-28 09:30 | BDL5 | LONG RURAL |  | 1 | 176 | 176 | 0.00068153 | 3.8723e-06 | 0
2013-10-24 08:32 | SMG23 | URBAN |  | 471 | 416 | 195936 | 0.68254 | 0.0016407 | 0
2013-10-24 09:05 | ELM13 | URBAN |  | 46 | 265 | 12190 | 0.042464 | 0.00016024 | 0
2013-10-18 11:20 | WYK12 | SHORT RURAL |  | 14 | 300 | 4200 | 0.036548 | 0.00012183 | 0
2013-10-24 09:10 | SMR3 | LONG RURAL |  | 201 | 7.4328 | 1494 | 0.0057852 | 0.00077834 | 0
2013-10-28 10:15 | KLK2 | SHORT RURAL |  | 13 | 167 | 2171 | 0.018892 | 0.00011313 | 0
2013-10-24 11:01 | ELM32 | URBAN |  | 59 | 180 | 10620 | 0.036995 | 0.00020553 | 0
2013-10-28 10:00 | LDL13 | SHORT RURAL |  | 516 | 88 | 45408 | 0.39514 | 0.0044902 | 0
2013-10-25 10:00 | SMR3 | LONG RURAL |  | 3 | 45 | 135 | 0.00052276 | 1.1617e-05 | 0
2013-10-27 08:30 | FGY22 | URBAN |  | 40 | 236 | 9440 | 0.032884 | 0.00013934 | 0
2013-10-27 09:00 | BGE12 | SHORT RURAL |  | 5 | 150 | 750 | 0.0065265 | 4.351e-05 | 0
2013-10-24 09:57 | KLO14 | LONG RURAL |  | 524 | 301 | 157724 | 0.61076 | 0.0020291 | 0
2013-10-27 10:48 | CYN14 | URBAN |  | 291 | 252 | 73332 | 0.25545 | 0.0010137 | 0
2013-10-21 11:50 | KLK2 | SHORT RURAL |  | 10 | 145 | 1450 | 0.012618 | 8.702e-05 | 0
2013-10-26 09:45 | SMR3 | LONG RURAL |  | 1 | 80 | 80 | 0.00030979 | 3.8723e-06 | 0
2013-10-29 09:03 | WN3 | LONG RURAL |  | 181 | 357 | 64617 | 0.25022 | 0.00070089 | 0
2013-10-30 09:00 | BN1 | LONG RURAL |  | 615 | 424 | 260760 | 1.0097 | 0.0023815 | 0
2013-10-29 09:40 | WOTS24 | LONG RURAL |  | 1 | 115 | 115 | 0.00044532 | 3.8723e-06 | 0
2013-10-29 12:05 | WOTS24 | LONG RURAL |  | 1 | 58 | 58 | 0.00022459 | 3.8723e-06 | 0
2013-10-29 13:35 | WOTS24 | LONG RURAL |  | 1 | 50 | 50 | 0.00019362 | 3.8723e-06 | 0
2013-10-30 09:40 | WOTS24 | LONG RURAL |  | 4 | 35 | 140 | 0.00054212 | 1.5489e-05 | 0
2013-10-30 10:45 | WOTS24 | LONG RURAL |  | 2 | 45 | 90 | 0.00034851 | 7.7446e-06 | 0
2013-10-29 09:29 | MFA34 | SHORT RURAL |  | 58 | 292 | 16936 | 0.14738 | 0.00050471 | 0
2013-10-30 09:53 | TGN31 | LONG RURAL |  | 29 | 238 | 6902 | 0.026727 | 0.0001123 | 0
2013-10-30 08:30 | BWA22 | LONG RURAL |  | 5 | 135 | 675 | 0.0026138 | 1.9362e-05 | 0
2013-10-29 09:00 | WGL24 | LONG RURAL |  | 62 | 300 | 18600 | 0.072025 | 0.00024008 | 0
2013-10-29 14:30 | MOE22 | LONG RURAL |  | 2 | 30 | 60 | 0.00023234 | 7.7446e-06 | 0
2013-10-31 10:45 | TGN31 | LONG RURAL |  | 1 | 45 | 45 | 0.00017425 | 3.8723e-06 | 0
2013-10-30 10:52 | WOTS24 | LONG RURAL |  | 1 | 23 | 23 | 8.9063e-05 | 3.8723e-06 | 0
2013-10-30 11:25 | WOTS24 | LONG RURAL |  | 1 | 23 | 23 | 8.9063e-05 | 3.8723e-06 | 0
2013-10-30 12:04 | WOTS24 | LONG RURAL |  | 1 | 44 | 44 | 0.00017038 | 3.8723e-06 | 0
2013-10-31 09:55 | WOTS24 | LONG RURAL |  | 2 | 105 | 210 | 0.00081319 | 7.7446e-06 | 0
2013-10-29 09:15 | WGI33 | SHORT RURAL |  | 9 | 315 | 2835 | 0.02467 | 7.8318e-05 | 0
2013-10-31 08:51 | WOTS11 | LONG RURAL |  | 19 | 259 | 4921 | 0.019056 | 7.3574e-05 | 0
2013-10-30 09:00 | LGA21 | SHORT RURAL |  | 116 | 272 | 31552 | 0.27456 | 0.0010094 | 0
2013-10-31 10:46 | WOTS24 | LONG RURAL |  | 20 | 52 | 1040 | 0.0040272 | 7.7446e-05 | 0
2013-10-31 09:00 | CF1 | SHORT RURAL |  | 9 | 1619 | 14571 | 0.1268 | 7.8318e-05 | 0
2013-10-29 11:15 | MOE22 | LONG RURAL |  | 1 | 108 | 108 | 0.00041821 | 3.8723e-06 | 0
2013-10-29 11:00 | MOE22 | LONG RURAL |  | 14 | 25 | 350 | 0.0013553 | 5.4212e-05 | 0
2013-10-30 09:26 | LGA24 | SHORT RURAL |  | 536 | 418 | 224048 | 1.9497 | 0.0046643 | 0
2013-10-29 09:38 | WYK24 | SHORT RURAL |  | 206 | 318 | 65508 | 0.57005 | 0.0017926 | 0
2013-10-29 09:00 | KLK1 | SHORT RURAL |  | 158 | 572 | 90376 | 0.78645 | 0.0013749 | 0
2013-10-29 12:10 | LGA23 | LONG RURAL |  | 2 | 165 | 330 | 0.0012779 | 7.7446e-06 | 0
2013-10-29 09:10 | WYK24 | SHORT RURAL |  | 30 | 275 | 8250 | 0.071791 | 0.00026106 | 0
2013-10-30 10:48 | TGN41 | LONG RURAL |  | 15 | 269 | 4035 | 0.015625 | 5.8085e-05 | 0
2013-10-31 10:00 | MOE22 | LONG RURAL |  | 20 | 369 | 7380 | 0.028578 | 7.7446e-05 | 0
2013-10-30 11:30 | FTR12 | LONG RURAL |  | 1 | 70 | 70 | 0.00027106 | 3.8723e-06 | 0
2013-10-31 09:10 | LGA23 | LONG RURAL |  | 79 | 384 | 30336 | 0.11747 | 0.00030591 | 0
2013-10-31 08:40 | WGL13 | SHORT RURAL |  | 47 | 10 | 470 | 0.0040899 | 0.00040899 | 0
2013-10-31 09:30 | LGA14 | LONG RURAL |  | 1 | 240 | 240 | 0.00092936 | 3.8723e-06 | 0
2013-10-31 08:00 | FTR12 | LONG RURAL |  | 2 | 230 | 460 | 0.0017813 | 7.7446e-06 | 0
2013-10-30 08:50 | FTR12 | LONG RURAL |  | 1 | 215 | 215 | 0.00083255 | 3.8723e-06 | 0
2013-10-31 09:30 | LGA23 | LONG RURAL |  | 31 | 305 | 9455 | 0.036613 | 0.00012004 | 0
2013-10-29 09:00 | LLG11 | SHORT RURAL |  | 106 | 370 | 39220 | 0.34129 | 0.00092241 | 0
2013-10-30 09:40 | KLK1 | SHORT RURAL |  | 1 | 290 | 290 | 0.0025236 | 8.702e-06 | 0
2013-10-29 08:35 | MWTS31 | SHORT RURAL |  | 4 | 50 | 200 | 0.0017404 | 3.4808e-05 | 0
2013-10-30 09:40 | LDL13 | SHORT RURAL |  | 25 | 190 | 4750 | 0.041334 | 0.00021755 | 0
2013-10-29 10:25 | MWTS31 | SHORT RURAL |  | 4 | 65 | 260 | 0.0022625 | 3.4808e-05 | 0
2013-10-29 13:20 | MWTS31 | SHORT RURAL |  | 11 | 85 | 935 | 0.0081363 | 9.5722e-05 | 0
2013-10-30 08:35 | MOE31 | LONG RURAL |  | 2 | 55 | 110 | 0.00042595 | 7.7446e-06 | 0
2013-10-31 08:30 | KLK1 | SHORT RURAL |  | 85 | 358 | 30430 | 0.2648 | 0.00073967 | 0
2013-10-30 08:48 | BN6 | LONG RURAL |  | 2 | 127 | 254 | 0.00098357 | 7.7446e-06 | 0
2013-10-28 11:05 | SLE31 | LONG RURAL |  | 4 | 115 | 460 | 0.0017813 | 1.5489e-05 | 0
2013-10-30 09:00 | SLE31 | LONG RURAL |  | 3 | 389.3333 | 1168 | 0.0045229 | 1.1617e-05 | 0
2013-10-30 09:50 | SLE31 | LONG RURAL |  | 2 | 425 | 850 | 0.0032915 | 7.7446e-06 | 0
2013-10-30 09:30 | LDL21 | SHORT RURAL |  | 573 | 365 | 209145 | 1.82 | 0.0049862 | 0
2013-10-31 09:15 | LDL13 | SHORT RURAL |  | 376 | 190 | 71440 | 0.62167 | 0.0032719 | 0
2013-10-28 13:50 | BDL5 | LONG RURAL |  | 2 | 45 | 90 | 0.00034851 | 7.7446e-06 | 0
2013-10-30 08:00 | WYK24 | SHORT RURAL |  | 276 | 405 | 111780 | 0.97271 | 0.0024017 | 0
2013-10-31 10:00 | KLK2 | SHORT RURAL |  | 8 | 280 | 2240 | 0.019492 | 6.9616e-05 | 0
2013-10-29 13:45 | CNR2 | SHORT RURAL |  | 1 | 112 | 112 | 0.00097462 | 8.702e-06 | 0
2013-10-25 09:10 | ELM34 | URBAN |  | 70 | 481.5714 | 33710 | 0.11743 | 0.00024384 | 0
2013-10-28 08:54 | OFR21 | SHORT RURAL |  | 83 | 336 | 27888 | 0.24268 | 0.00072226 | 0
2013-10-28 08:40 | LLG12 | SHORT RURAL |  | 5 | 320 | 1600 | 0.013923 | 4.351e-05 | 0
2013-10-25 08:50 | ELM12 | SHORT RURAL |  | 42 | 290 | 12180 | 0.10599 | 0.00036548 | 0
2013-10-30 08:55 | LLG13 | SHORT RURAL |  | 57 | 275 | 15675 | 0.1364 | 0.00049601 | 0
2013-10-26 12:05 | SMR3 | LONG RURAL |  | 2 | 165 | 330 | 0.0012779 | 7.7446e-06 | 0
2013-10-31 09:00 | SMR3 | LONG RURAL |  | 365 | 385 | 140525 | 0.54416 | 0.0014134 | 0
2013-10-30 08:40 | LDL23 | LONG RURAL |  | 307 | 365 | 112055 | 0.43391 | 0.0011888 | 0
2013-10-28 12:05 | SMR3 | LONG RURAL |  | 1 | 90 | 90 | 0.00034851 | 3.8723e-06 | 0
2013-10-28 14:40 | SMR3 | LONG RURAL |  | 7 | 125 | 875 | 0.0033883 | 2.7106e-05 | 0
2013-10-27 09:00 | SMR1 | SHORT RURAL |  | 9 | 155 | 1395 | 0.012139 | 7.8318e-05 | 0
2013-10-27 10:00 | ELM33 | SHORT RURAL |  | 16 | 80 | 1280 | 0.011139 | 0.00013923 | 0
2013-10-28 09:21 | SMR8 | LONG RURAL |  | 12 | 259 | 3108 | 0.012035 | 4.6468e-05 | 0
2013-10-26 08:45 | BRA11 | URBAN |  | 9 | 389 | 3501 | 0.012196 | 3.1351e-05 | 0
2013-10-28 09:01 | WN2 | LONG RURAL |  | 54 | 424 | 22896 | 0.088661 | 0.0002091 | 0
2013-10-28 09:50 | DRN12 | URBAN |  | 8 | 281 | 2248 | 0.0078309 | 2.7868e-05 | 0
2013-10-22 08:42 | MSD1 | LONG RURAL |  | 106 | 388 | 41128 | 0.15926 | 0.00041047 | 0
2013-10-28 08:35 | BDL8 | LONG RURAL |  | 6 | 335 | 2010 | 0.0077834 | 2.3234e-05 | 0
2013-10-29 08:30 | SMR3 | LONG RURAL |  | 2 | 260 | 520 | 0.0020136 | 7.7446e-06 | 0
2013-10-31 09:00 | BN6 | LONG RURAL |  | 53 | 359 | 19027 | 0.073679 | 0.00020523 | 0
2013-10-29 10:30 | BDL5 | LONG RURAL |  | 2 | 66 | 132 | 0.00051115 | 7.7446e-06 | 0
2013-10-29 08:50 | CYN14 | URBAN |  | 197 | 303 | 59691 | 0.20793 | 0.00068625 | 0
2013-10-27 08:30 | RWN24 | SHORT RURAL |  | 108 | 280 | 30240 | 0.26315 | 0.00093981 | 0
2013-10-27 10:35 | BWR34 | URBAN |  | 44 | 170 | 7480 | 0.026056 | 0.00015327 | 0
2013-10-27 08:32 | RWT15 | URBAN |  | 196 | 457 | 89572 | 0.31202 | 0.00068276 | 0
2013-10-28 10:30 | BRA32 | URBAN |  | 138 | 295 | 40710 | 0.14181 | 0.00048072 | 0
2013-10-29 09:00 | ALA01 | LONG RURAL |  | 45 | 410 | 18450 | 0.071444 | 0.00017425 | 0
2013-10-29 14:20 | SMR3 | LONG RURAL |  | 1 | 140 | 140 | 0.00054212 | 3.8723e-06 | 0
2013-11-01 08:35 | BN2 | LONG RURAL |  | 12 | 205 | 2460 | 0.0095259 | 4.6468e-05 | 0
2013-10-31 13:35 | WOTS24 | LONG RURAL |  | 2 | 45 | 90 | 0.00034851 | 7.7446e-06 | 0
2013-11-01 09:05 | BN1 | LONG RURAL |  | 4 | 165 | 660 | 0.0025557 | 1.5489e-05 | 0
2013-10-31 09:47 | TGN31 | LONG RURAL |  | 18 | 224.7222 | 4045 | 0.015664 | 6.9702e-05 | 0
2013-10-31 11:50 | WOTS24 | LONG RURAL |  | 2 | 50 | 100 | 0.00038723 | 7.7446e-06 | 0
2013-10-31 12:05 | WOTS24 | LONG RURAL |  | 1 | 90 | 90 | 0.00034851 | 3.8723e-06 | 0
2013-10-31 11:20 | MOE22 | LONG RURAL |  | 1 | 65 | 65 | 0.0002517 | 3.8723e-06 | 0
2013-11-01 09:10 | MOE32 | SHORT RURAL |  | 5 | 225 | 1125 | 0.0097897 | 4.351e-05 | 0
2013-11-01 09:30 | MOE22 | LONG RURAL |  | 3 | 90 | 270 | 0.0010455 | 1.1617e-05 | 0
2013-11-01 11:05 | MOE22 | LONG RURAL |  | 2 | 45 | 90 | 0.00034851 | 7.7446e-06 | 0
2013-11-01 09:10 | MOE22 | LONG RURAL |  | 2 | 50 | 100 | 0.00038723 | 7.7446e-06 | 0
2013-11-01 09:15 | FTR23 | LONG RURAL |  | 55 | 430 | 23650 | 0.09158 | 0.00021298 | 0
2013-11-01 09:02 | FTR23 | LONG RURAL |  | 1 | 68 | 68 | 0.00026332 | 3.8723e-06 | 0
2013-11-01 09:00 | LGA24 | SHORT RURAL |  | 42 | 240 | 10080 | 0.087716 | 0.00036548 | 0
2013-11-01 09:31 | PHM14 | LONG RURAL |  | 61 | 76 | 4636 | 0.017952 | 0.00023621 | 0
2013-11-01 09:00 | LLG13 | SHORT RURAL |  | 8 | 125 | 1000 | 0.008702 | 6.9616e-05 | 0
2013-11-01 09:53 | LLG13 | SHORT RURAL |  | 12 | 117 | 1404 | 0.012218 | 0.00010442 | 0
2013-11-01 09:00 | PHM14 | LONG RURAL |  | 13 | 135 | 1755 | 0.0067959 | 5.034e-05 | 0
2013-11-01 11:55 | LLG13 | SHORT RURAL |  | 10 | 143 | 1430 | 0.012444 | 8.702e-05 | 0
2013-11-01 10:50 | PHM14 | LONG RURAL |  | 4 | 35 | 140 | 0.00054212 | 1.5489e-05 | 0
2013-11-01 08:45 | SLE32 | SHORT RURAL |  | 296 | 287 | 84952 | 0.73925 | 0.0025758 | 0
2013-11-01 09:26 | MSD2 | LONG RURAL |  | 4 | 369 | 1476 | 0.0057155 | 1.5489e-05 | 0
2013-10-27 08:10 | BRA14 | URBAN |  | 499 | 365 | 182135 | 0.63446 | 0.0017383 | 0
2013-10-29 09:15 | KMS21 | SHORT RURAL |  | 13 | 360 | 4680 | 0.040725 | 0.00011313 | 0
2013-10-29 09:05 | BDL1 | LONG RURAL |  | 2 | 85 | 170 | 0.00065829 | 7.7446e-06 | 0
2013-10-28 14:42 | BN1 | LONG RURAL |  | 1 | 58 | 58 | 0.00022459 | 3.8723e-06 | 0
2013-10-29 09:10 | CYN31 | URBAN |  | 61 | 338 | 20618 | 0.071822 | 0.00021249 | 0
2013-10-27 08:42 | MSD1 | LONG RURAL |  | 44 | 333 | 14652 | 0.056737 | 0.00017038 | 0
2013-10-29 11:50 | BDL1 | LONG RURAL |  | 1 | 65 | 65 | 0.0002517 | 3.8723e-06 | 0
2013-10-30 08:35 | CYN23 | URBAN |  | 69 | 10 | 690 | 0.0024036 | 0.00024036 | 0
2013-10-29 08:30 | BDL8 | LONG RURAL |  | 47 | 106 | 4982 | 0.019292 | 0.000182 | 0
2013-11-01 09:10 | WOTS24 | LONG RURAL |  | 1 | 65 | 65 | 0.0002517 | 3.8723e-06 | 0
2013-10-27 08:30 | BGE12 | SHORT RURAL |  | 244 | 374 | 91256 | 0.79411 | 0.0021233 | 0
2013-10-30 08:20 | KMS1 | SHORT RURAL |  | 129 | 495 | 63855 | 0.55566 | 0.0011226 | 0
2013-10-31 09:17 | TGN23 | SHORT RURAL |  | 1 | 123 | 123 | 0.0010703 | 8.702e-06 | 0
2013-10-27 09:00 | BRA21 | URBAN |  | 139 | 623.741 | 86700 | 0.30202 | 0.0004842 | 0
2013-10-31 11:50 | TGN23 | SHORT RURAL |  | 3 | 31 | 93 | 0.00080928 | 2.6106e-05 | 0
2013-10-28 08:47 | RWT15 | URBAN |  | 87 | 201 | 17487 | 0.060916 | 0.00030306 | 0
2013-10-28 09:04 | RWN26 | SHORT RURAL |  | 6 | 310 | 1860 | 0.016186 | 5.2212e-05 | 0
2013-10-28 12:38 | RWT15 | URBAN |  | 79 | 110 | 8690 | 0.030271 | 0.0002752 | 0
2013-10-30 08:42 | FGY34 | URBAN |  | 85 | 403 | 34255 | 0.11933 | 0.0002961 | 0
2013-10-29 09:22 | RWT15 | URBAN |  | 104 | 201 | 20904 | 0.072819 | 0.00036228 | 0
2013-10-29 08:30 | RWN26 | SHORT RURAL |  | 238 | 400 | 95200 | 0.82843 | 0.0020711 | 0
2013-10-30 09:30 | HPK23 | URBAN |  | 99 | 100 | 9900 | 0.034486 | 0.00034486 | 0
2013-10-30 09:10 | BGE22 | SHORT RURAL |  | 199 | 285 | 56715 | 0.49353 | 0.0017317 | 0
2013-10-30 10:15 | BGE22 | SHORT RURAL |  | 132 | 180 | 23760 | 0.20676 | 0.0011487 | 0
2013-11-01 12:35 | MOE22 | LONG RURAL |  | 2 | 30 | 60 | 0.00023234 | 7.7446e-06 | 0
2013-11-01 11:25 | MOE22 | LONG RURAL |  | 1 | 45 | 45 | 0.00017425 | 3.8723e-06 | 0
2013-11-02 09:00 | MWTS31 | SHORT RURAL |  | 12 | 220 | 2640 | 0.022973 | 0.00010442 | 0
2013-11-02 09:05 | MOE22 | LONG RURAL |  | 1 | 100 | 100 | 0.00038723 | 3.8723e-06 | 0
2013-11-02 09:00 | WGL23 | SHORT RURAL |  | 30 | 250 | 7500 | 0.065265 | 0.00026106 | 0
2013-11-01 11:40 | PHM14 | LONG RURAL |  | 7 | 40 | 280 | 0.0010842 | 2.7106e-05 | 0
2013-11-01 12:01 | PHM14 | LONG RURAL |  | 2 | 84 | 168 | 0.00065055 | 7.7446e-06 | 0
2013-11-02 09:30 | WGI22 | LONG RURAL |  | 108 | 320 | 34560 | 0.13383 | 0.00041821 | 0
2013-10-22 06:35 | SMG21 | URBAN |  | 22 | 2 | 44 | 0.00015327 | 7.6637e-05 | 0
2013-10-31 09:00 | SLE31 | LONG RURAL |  | 2 | 396 | 792 | 0.0030669 | 7.7446e-06 | 0
2013-10-23 09:10 | WOTS13 | LONG RURAL |  | 25 | 105 | 2625 | 0.010165 | 9.6808e-05 | 0
2013-10-29 14:08 | NLA31 | LONG RURAL |  | 1 | 52 | 52 | 0.00020136 | 3.8723e-06 | 0
2013-10-27 08:00 | PHM11 | URBAN |  | 49 | 145 | 7105 | 0.02475 | 0.00017069 | 0
2013-11-01 14:30 | LLG11 | SHORT RURAL |  | 15 | 40 | 600 | 0.0052212 | 0.00013053 | 0
2013-10-29 09:35 | ELM33 | SHORT RURAL |  | 1 | 40 | 40 | 0.00034808 | 8.702e-06 | 0
2013-11-02 11:05 | MOE22 | LONG RURAL |  | 4 | 45 | 180 | 0.00069702 | 1.5489e-05 | 0
2013-10-29 08:55 | BDL1 | LONG RURAL |  | 2 | 360 | 720 | 0.0027881 | 7.7446e-06 | 0
2013-11-01 09:50 | WGI31 | SHORT RURAL |  | 21 | 280 | 5880 | 0.051168 | 0.00018274 | 0
2013-10-28 08:40 | ELM33 | SHORT RURAL |  | 2 | 140 | 280 | 0.0024366 | 1.7404e-05 | 0
2013-10-31 12:00 | SMR3 | LONG RURAL |  | 2 | 164 | 328 | 0.0012701 | 7.7446e-06 | 0
2013-10-26 09:20 | CYN11 | URBAN |  | 19 | 342 | 6498 | 0.022636 | 6.6186e-05 | 0
2013-10-29 10:14 | BDL8 | LONG RURAL |  | 119 | 2 | 238 | 0.00092161 | 0.00046081 | 0
2013-10-29 10:12 | NLA31 | LONG RURAL |  | 2 | 241 | 482 | 0.0018665 | 7.7446e-06 | 0
2013-10-30 08:30 | BDL8 | LONG RURAL |  | 37 | 377 | 13949 | 0.054015 | 0.00014328 | 0
2013-10-30 09:20 | NLA31 | LONG RURAL |  | 20 | 368 | 7360 | 0.0285 | 7.7446e-05 | 0
2013-11-01 09:31 | LYD14 | SHORT RURAL |  | 9 | 76 | 684 | 0.0059521 | 7.8318e-05 | 0
2013-11-01 09:40 | BGE12 | SHORT RURAL |  | 1 | 95 | 95 | 0.00082669 | 8.702e-06 | 0
2013-11-01 11:35 | BGE12 | SHORT RURAL |  | 1 | 100 | 100 | 0.0008702 | 8.702e-06 | 0
2013-11-04 08:50 | BN6 | LONG RURAL |  | 3 | 185 | 555 | 0.0021491 | 1.1617e-05 | 0
2013-11-04 08:50 | BN1 | LONG RURAL |  | 6 | 335 | 2010 | 0.0077834 | 2.3234e-05 | 0
2013-10-29 09:45 | DRN14 | SHORT RURAL |  | 49 | 190 | 9310 | 0.081015 | 0.0004264 | 0
2013-10-31 09:55 | CNR1 | SHORT RURAL |  | 4 | 140 | 560 | 0.0048731 | 3.4808e-05 | 0
2013-10-30 09:04 | BDL5 | LONG RURAL |  | 28 | 313 | 8764 | 0.033937 | 0.00010842 | 0
2013-10-31 08:35 | BDL8 | LONG RURAL |  | 12 | 295 | 3540 | 0.013708 | 4.6468e-05 | 0
2013-10-29 12:00 | DRN12 | URBAN |  | 2 | 120 | 240 | 0.00083604 | 6.967e-06 | 0
2013-10-31 09:15 | BDL8 | LONG RURAL |  | 64 | 320 | 20480 | 0.079305 | 0.00024783 | 0
2013-10-31 08:35 | BDL8 | LONG RURAL |  | 10 | 185 | 1850 | 0.0071638 | 3.8723e-05 | 0
2013-11-01 09:00 | SLE31 | LONG RURAL |  | 9 | 480 | 4320 | 0.016728 | 3.4851e-05 | 0
2013-11-01 08:30 | BDL8 | LONG RURAL |  | 66 | 225 | 14850 | 0.057504 | 0.00025557 | 0
2013-11-01 08:45 | BDL8 | LONG RURAL |  | 1 | 321 | 321 | 0.001243 | 3.8723e-06 | 0
2013-11-01 09:15 | LGA11 | LONG RURAL |  | 154 | 212 | 32648 | 0.12642 | 0.00059634 | 0
2013-10-31 09:30 | BDL4 | SHORT RURAL |  | 116 | 380 | 44080 | 0.38358 | 0.0010094 | 0
2013-10-29 09:55 | KLO14 | LONG RURAL |  | 1 | 155 | 155 | 0.00060021 | 3.8723e-06 | 0
2013-10-29 09:50 | ELM15 | SHORT RURAL |  | 384 | 288 | 110592 | 0.96237 | 0.0033416 | 0
2013-10-31 09:26 | DRN14 | SHORT RURAL |  | 46 | 364 | 16744 | 0.14571 | 0.00040029 | 0
2013-10-31 12:25 | DRN13 | SHORT RURAL |  | 2 | 70 | 140 | 0.0012183 | 1.7404e-05 | 0
2013-11-02 09:20 | BWA23 | SHORT RURAL |  | 24 | 255.625 | 6135 | 0.053387 | 0.00020885 | 0
2013-10-29 09:16 | DRN12 | URBAN |  | 25 | 126 | 3150 | 0.010973 | 8.7087e-05 | 0
2013-10-30 10:28 | SMG22 | URBAN |  | 193 | 262 | 50566 | 0.17615 | 0.00067231 | 0
2013-10-30 08:55 | DRN23 | LONG RURAL |  | 197 | 270 | 53190 | 0.20597 | 0.00076285 | 0
2013-11-01 09:15 | KMS1 | SHORT RURAL |  | 26 | 145 | 3770 | 0.032806 | 0.00022625 | 0
2013-11-06 09:55 | MOE32 | SHORT RURAL |  | 15 | 395 | 5925 | 0.051559 | 0.00013053 | 0
2013-11-06 09:18 | WGL21 | LONG RURAL |  | 16 | 177 | 2832 | 0.010966 | 6.1957e-05 | 0
2013-11-06 09:30 | MOE22 | LONG RURAL |  | 4 | 265 | 1060 | 0.0041047 | 1.5489e-05 | 0
2013-11-07 09:10 | MOE22 | LONG RURAL |  | 11 | 290 | 3190 | 0.012353 | 4.2595e-05 | 0
2013-11-07 10:10 | MWTS31 | SHORT RURAL |  | 9 | 250 | 2250 | 0.019579 | 7.8318e-05 | 0
2013-11-07 09:10 | MWTS31 | SHORT RURAL |  | 68 | 277 | 18836 | 0.16391 | 0.00059173 | 0
2013-11-06 10:13 | MOE32 | SHORT RURAL |  | 26 | 442 | 11492 | 0.1 | 0.00022625 | 0
2013-11-07 11:00 | MOE22 | LONG RURAL |  | 5 | 195 | 975 | 0.0037755 | 1.9362e-05 | 0
2013-11-07 08:30 | MOE22 | LONG RURAL |  | 4 | 265 | 1060 | 0.0041047 | 1.5489e-05 | 0
2013-11-06 10:30 | TGN31 | LONG RURAL |  | 1 | 175 | 175 | 0.00067766 | 3.8723e-06 | 0
2013-11-06 09:10 | LGA23 | LONG RURAL |  | 48 | 120 | 5760 | 0.022305 | 0.00018587 | 0
2013-11-06 09:05 | MWTS32 | SHORT RURAL |  | 1 | 105 | 105 | 0.00091371 | 8.702e-06 | 0
2013-11-06 09:45 | MWTS32 | SHORT RURAL |  | 1 | 120 | 120 | 0.0010442 | 8.702e-06 | 0
2013-11-06 11:00 | MWTS32 | SHORT RURAL |  | 2 | 30 | 60 | 0.00052212 | 1.7404e-05 | 0
2013-11-06 12:10 | MWTS32 | SHORT RURAL |  | 1 | 65 | 65 | 0.00056563 | 8.702e-06 | 0
2013-11-06 13:10 | MWTS32 | SHORT RURAL |  | 3 | 45 | 135 | 0.0011748 | 2.6106e-05 | 0
2013-11-06 13:40 | MWTS32 | SHORT RURAL |  | 2 | 50 | 100 | 0.0008702 | 1.7404e-05 | 0
2013-11-06 09:18 | FTR21 | LONG RURAL |  | 1 | 57 | 57 | 0.00022072 | 3.8723e-06 | 0
2013-11-06 10:05 | LGA24 | SHORT RURAL |  | 36 | 325 | 11700 | 0.10181 | 0.00031327 | 0
2013-11-06 09:10 | TGN41 | LONG RURAL |  | 3 | 142 | 426 | 0.0016496 | 1.1617e-05 | 0
2013-11-06 09:00 | RWN33 | URBAN |  | 128 | 435 | 55680 | 0.19396 | 0.00044589 | 0
2013-11-06 09:35 | WYK24 | SHORT RURAL |  | 30 | 220 | 6600 | 0.057433 | 0.00026106 | 0
2013-11-07 09:50 | WGI23 | SHORT RURAL |  | 3 | 154 | 462 | 0.0040203 | 2.6106e-05 | 0
2013-11-06 11:35 | MOE22 | LONG RURAL |  | 45 | 218 | 9810 | 0.037987 | 0.00017425 | 0
2013-11-06 09:50 | FTR23 | LONG RURAL |  | 1 | 30 | 30 | 0.00011617 | 3.8723e-06 | 0
2013-11-07 09:30 | LLG13 | SHORT RURAL |  | 4 | 30 | 120 | 0.0010442 | 3.4808e-05 | 0
2013-11-07 09:30 | LGA23 | LONG RURAL |  | 74 | 435 | 32190 | 0.12465 | 0.00028655 | 0
2013-11-07 09:00 | FTR23 | LONG RURAL |  | 23 | 343 | 7889 | 0.030549 | 8.9063e-05 | 0
2013-11-07 10:58 | LLG12 | SHORT RURAL |  | 4 | 71 | 284 | 0.0024714 | 3.4808e-05 | 0
2013-11-07 08:08 | LDL13 | SHORT RURAL |  | 139 | 472 | 65608 | 0.57092 | 0.0012096 | 0
2013-11-06 09:50 | KLK1 | SHORT RURAL |  | 106 | 260 | 27560 | 0.23983 | 0.00092241 | 0
2013-11-07 09:15 | FTR23 | LONG RURAL |  | 55 | 264 | 14520 | 0.056226 | 0.00021298 | 0
2013-11-07 09:14 | BN6 | LONG RURAL |  | 2 | 81 | 162 | 0.00062731 | 7.7446e-06 | 0
2013-11-06 09:15 | MSD1 | LONG RURAL |  | 5 | 405 | 2025 | 0.0078414 | 1.9362e-05 | 0
2013-11-06 09:15 | WOTS11 | LONG RURAL |  | 2 | 310 | 620 | 0.0024008 | 7.7446e-06 | 0
2013-11-06 12:45 | PHM14 | LONG RURAL |  | 90 | 110 | 9900 | 0.038336 | 0.00034851 | 0
2013-11-06 09:44 | WN5 | LONG RURAL |  | 44 | 311 | 13684 | 0.052989 | 0.00017038 | 0
2013-11-07 09:01 | WGI23 | SHORT RURAL |  | 28 | 174 | 4872 | 0.042396 | 0.00024366 | 0
2013-11-07 09:55 | KLK1 | SHORT RURAL |  | 97 | 273 | 26481 | 0.23044 | 0.00084409 | 0
2013-11-07 09:15 | WYK11 | SHORT RURAL |  | 6 | 445 | 2670 | 0.023234 | 5.2212e-05 | 0
2013-11-07 09:00 | TGN23 | SHORT RURAL |  | 187 | 345 | 64515 | 0.56141 | 0.0016273 | 0
2013-10-31 11:40 | CYN14 | URBAN |  | 70 | 156 | 10920 | 0.03804 | 0.00024384 | 0
2013-10-31 11:40 | CYN31 | URBAN |  | 91 | 156 | 14196 | 0.049452 | 0.000317 | 0
2013-11-01 08:30 | BDL8 | LONG RURAL |  | 2 | 265 | 530 | 0.0020523 | 7.7446e-06 | 0
2013-10-31 08:00 | RWN26 | SHORT RURAL |  | 40 | 590 | 23600 | 0.20537 | 0.00034808 | 0
2013-11-01 09:50 | RWN26 | SHORT RURAL |  | 6 | 250 | 1500 | 0.013053 | 5.2212e-05 | 0
2013-11-01 12:38 | PHM14 | LONG RURAL |  | 4 | 10 | 40 | 0.00015489 | 1.5489e-05 | 0
2013-11-01 09:35 | CYN23 | URBAN |  | 146 | 393 | 57378 | 0.19988 | 0.00050859 | 0
2013-11-03 08:00 | BWR13 | SHORT RURAL |  | 110 | 268 | 29480 | 0.25653 | 0.00095722 | 0
2013-11-07 09:40 | BGE22 | SHORT RURAL |  | 188 | 178 | 33464 | 0.2912 | 0.001636 | 0
2013-11-07 08:45 | PHM31 | SHORT RURAL |  | 2 | 255 | 510 | 0.004438 | 1.7404e-05 | 0
2013-11-06 09:45 | BRA11 | URBAN |  | 97 | 53 | 5141 | 0.017909 | 0.0003379 | 0
2013-11-07 09:40 | OFR23 | LONG RURAL |  | 15 | 363 | 5445 | 0.021085 | 5.8085e-05 | 0
2013-11-07 08:12 | WT15 | URBAN |  | 138 | 423 | 58374 | 0.20334 | 0.00048072 | 0
2013-11-01 09:15 | BDL8 | LONG RURAL |  | 5 | 285 | 1425 | 0.005518 | 1.9362e-05 | 0
2013-11-01 09:15 | BDL1 | LONG RURAL |  | 2 | 30 | 60 | 0.00023234 | 7.7446e-06 | 0
2013-11-06 10:30 | BDL1 | LONG RURAL |  | 1 | 240 | 240 | 0.00092936 | 3.8723e-06 | 0
2013-10-31 08:30 | OFR23 | LONG RURAL |  | 276 | 412 | 113712 | 0.44033 | 0.0010688 | 0
2013-10-31 09:20 | MWTS21 | URBAN |  | 57 | 160 | 9120 | 0.031769 | 0.00019856 | 0
2013-11-08 09:15 | TGN31 | LONG RURAL |  | 3 | 100 | 300 | 0.0011617 | 1.1617e-05 | 0
2013-11-08 09:55 | WGL21 | LONG RURAL |  | 2 | 95 | 190 | 0.00073574 | 7.7446e-06 | 0
2013-11-07 11:15 | MOE22 | LONG RURAL |  | 4 | 25 | 100 | 0.00038723 | 1.5489e-05 | 0
2013-11-08 09:15 | MOE22 | LONG RURAL |  | 1 | 60 | 60 | 0.00023234 | 3.8723e-06 | 0
2013-11-08 10:25 | MOE22 | LONG RURAL |  | 2 | 65 | 130 | 0.0005034 | 7.7446e-06 | 0
2013-11-08 11:25 | MOE22 | LONG RURAL |  | 1 | 56 | 56 | 0.00021685 | 3.8723e-06 | 0
2013-11-07 13:25 | WGI23 | SHORT RURAL |  | 2 | 57 | 114 | 0.00099202 | 1.7404e-05 | 0
2013-11-08 09:10 | TGN31 | LONG RURAL |  | 1 | 20 | 20 | 7.7446e-05 | 3.8723e-06 | 0
2013-11-07 11:00 | LLG12 | SHORT RURAL |  | 2 | 135 | 270 | 0.0023495 | 1.7404e-05 | 0
2013-11-08 10:20 | TGN31 | LONG RURAL |  | 3 | 50 | 150 | 0.00058085 | 1.1617e-05 | 0
2013-11-07 13:40 | LLG12 | SHORT RURAL |  | 3 | 150 | 450 | 0.0039159 | 2.6106e-05 | 0
2013-11-08 09:35 | MOE22 | LONG RURAL |  | 2 | 70 | 140 | 0.00054212 | 7.7446e-06 | 0
2013-11-07 13:00 | LLG12 | SHORT RURAL |  | 2 | 20 | 40 | 0.00034808 | 1.7404e-05 | 0
2013-11-08 09:25 | LGA21 | SHORT RURAL |  | 145 | 102 | 14790 | 0.1287 | 0.0012618 | 0
2013-11-08 08:50 | BN6 | LONG RURAL |  | 38 | 265 | 10070 | 0.038994 | 0.00014715 | 0
2013-11-08 09:35 | TGN31 | LONG RURAL |  | 2 | 92 | 184 | 0.00071251 | 7.7446e-06 | 0
2013-11-08 09:00 | LGA24 | SHORT RURAL |  | 20 | 330 | 6600 | 0.057433 | 0.00017404 | 0
2013-11-08 11:30 | TGN31 | LONG RURAL |  | 1 | 5 | 5 | 1.9362e-05 | 3.8723e-06 | 0
2013-11-08 12:00 | TGN31 | LONG RURAL |  | 3 | 52 | 156 | 0.00060408 | 1.1617e-05 | 0
2013-11-08 09:25 | MSD1 | LONG RURAL |  | 3 | 170 | 510 | 0.0019749 | 1.1617e-05 | 0
2013-11-08 09:00 | FTR23 | LONG RURAL |  | 59 | 409 | 24131 | 0.093443 | 0.00022847 | 0
2013-11-08 09:10 | WYK23 | SHORT RURAL |  | 31 | 345 | 10695 | 0.093068 | 0.00026976 | 0
2013-11-08 10:15 | MOE31 | LONG RURAL |  | 1 | 120 | 120 | 0.00046468 | 3.8723e-06 | 0
2013-11-08 09:00 | WYK12 | SHORT RURAL |  | 69 | 255 | 17595 | 0.15311 | 0.00060044 | 0
2013-11-08 12:55 | MOE31 | LONG RURAL |  | 3 | 45 | 135 | 0.00052276 | 1.1617e-05 | 0
2013-11-08 09:50 | CLN13 | SHORT RURAL |  | 6 | 190 | 1140 | 0.0099202 | 5.2212e-05 | 0
2013-11-07 13:20 | PHM14 | LONG RURAL |  | 49 | 65 | 3185 | 0.012333 | 0.00018974 | 0
2013-11-08 05:05 | CRE23 | URBAN |  | 6 | 135 | 810 | 0.0028216 | 2.0901e-05 | 0
2013-10-29 09:10 | WN3 | LONG RURAL |  | 1 | 180 | 180 | 0.00069702 | 3.8723e-06 | 0
2013-11-08 10:48 | MSD1 | LONG RURAL |  | 2 | 182 | 364 | 0.0014095 | 7.7446e-06 | 0
2013-10-29 11:05 | DRN12 | URBAN |  | 5 | 80 | 400 | 0.0013934 | 1.7417e-05 | 0
2013-11-07 11:45 | MOE22 | LONG RURAL |  | 35 | 320 | 11200 | 0.04337 | 0.00013553 | 0
2013-11-07 11:45 | MOE32 | SHORT RURAL |  | 46 | 320 | 14720 | 0.12809 | 0.00040029 | 0
2013-10-30 09:35 | CF1 | SHORT RURAL |  | 2 | 264 | 528 | 0.0045946 | 1.7404e-05 | 0
2013-10-30 10:42 | DRN11 | URBAN |  | 7121 | 253 | 1801613 | 6.2759 | 0.024806 | 0
2013-11-06 13:50 | CNR1 | SHORT RURAL |  | 35 | 35 | 1225 | 0.01066 | 0.00030457 | 0
2013-10-31 09:54 | CYN31 | URBAN |  | 441 | 306 | 134946 | 0.47008 | 0.0015362 | 0
2013-10-31 11:00 | WOTS13 | LONG RURAL |  | 2 | 115 | 230 | 0.00089063 | 7.7446e-06 | 0
2013-11-04 09:40 | MBY11 | SHORT RURAL |  | 30 | 115 | 3450 | 0.030022 | 0.00026106 | 0
2013-11-04 11:30 | MYT7 | LONG RURAL |  | 4 | 190 | 760 | 0.002943 | 1.5489e-05 | 0
2013-11-04 11:50 | MBY11 | SHORT RURAL |  | 1 | 30 | 30 | 0.00026106 | 8.702e-06 | 0
2013-11-06 08:30 | MDG1 | SHORT RURAL |  | 148 | 383 | 56684 | 0.49326 | 0.0012879 | 0
2013-11-07 08:30 | DRN23 | LONG RURAL |  | 964 | 441 | 425124 | 1.6462 | 0.0037329 | 0
2013-11-06 08:52 | FGY34 | URBAN |  | 51 | 418 | 21318 | 0.074261 | 0.00017766 | 0
2013-11-09 09:00 | WGL13 | SHORT RURAL |  | 2 | 330 | 660 | 0.0057433 | 1.7404e-05 | 0
2013-11-08 11:35 | TGN31 | LONG RURAL |  | 1 | 75 | 75 | 0.00029042 | 3.8723e-06 | 0
2013-11-08 11:15 | MOE22 | LONG RURAL |  | 1 | 55 | 55 | 0.00021298 | 3.8723e-06 | 0
2013-11-08 11:50 | MOE22 | LONG RURAL |  | 2 | 60 | 120 | 0.00046468 | 7.7446e-06 | 0
2013-11-09 09:30 | WGL24 | LONG RURAL |  | 32 | 110 | 3520 | 0.013631 | 0.00012391 | 0
2013-11-09 11:45 | WGL24 | LONG RURAL |  | 1 | 225 | 225 | 0.00087127 | 3.8723e-06 | 0
2013-11-08 10:50 | LGA23 | LONG RURAL |  | 1 | 72 | 72 | 0.00027881 | 3.8723e-06 | 0
2013-11-08 11:33 | LGA23 | LONG RURAL |  | 1 | 17 | 17 | 6.5829e-05 | 3.8723e-06 | 0
2013-11-08 11:30 | FTR12 | LONG RURAL |  | 27 | 53 | 1431 | 0.0055413 | 0.00010455 | 0
2013-11-10 09:15 | WGL23 | SHORT RURAL |  | 10 | 350 | 3500 | 0.030457 | 8.702e-05 | 0
2013-11-10 08:30 | RWN32 | URBAN |  | 87 | 558.6437 | 48602 | 0.1693 | 0.00030306 | 0
2013-11-10 08:33 | WYK24 | SHORT RURAL |  | 56 | 322 | 18032 | 0.15691 | 0.00048731 | 0
2013-11-10 09:00 | TGN31 | LONG RURAL |  | 10 | 315 | 3150 | 0.012198 | 3.8723e-05 | 0
2013-11-10 08:35 | BRA21 | URBAN |  | 155 | 185 | 28675 | 0.099889 | 0.00053994 | 0
2013-11-10 08:55 | BWR32 | URBAN |  | 64 | 155 | 9920 | 0.034556 | 0.00022294 | 0
2013-11-10 08:30 | BWR24 | URBAN |  | 47 | 420 | 19740 | 0.068764 | 0.00016372 | 0
2013-11-10 10:15 | LGA13 | LONG RURAL |  | 4 | 140 | 560 | 0.0021685 | 1.5489e-05 | 0
2013-11-10 09:00 | MOE22 | LONG RURAL |  | 101 | 457.4851 | 46206 | 0.17892 | 0.0003911 | 0
2013-11-10 09:20 | MWTS21 | URBAN |  | 111 | 415 | 46065 | 0.16047 | 0.00038667 | 0
2013-11-10 09:05 | MWTS32 | SHORT RURAL |  | 231 | 426 | 98406 | 0.85633 | 0.0020102 | 0
2013-11-01 09:15 | DRN22 | SHORT RURAL |  | 2 | 285 | 570 | 0.0049601 | 1.7404e-05 | 0
2013-11-08 09:00 | MOE22 | LONG RURAL |  | 5 | 230 | 1150 | 0.0044532 | 1.9362e-05 | 0
2013-11-06 11:50 | SLE31 | LONG RURAL |  | 1 | 55 | 55 | 0.00021298 | 3.8723e-06 | 0
2013-11-06 09:00 | MYT7 | LONG RURAL |  | 19 | 220 | 4180 | 0.016186 | 7.3574e-05 | 0
2013-11-06 09:45 | BRT22 | SHORT RURAL |  | 33 | 100 | 3300 | 0.028717 | 0.00028717 | 0
2013-11-06 10:35 | BRT21 | SHORT RURAL |  | 1 | 20 | 20 | 0.00017404 | 8.702e-06 | 0
2013-11-06 09:50 | CNR2 | SHORT RURAL |  | 6 | 275 | 1650 | 0.014358 | 5.2212e-05 | 0
2013-11-06 12:00 | SMR8 | LONG RURAL |  | 1 | 60 | 60 | 0.00023234 | 3.8723e-06 | 0
2013-11-01 12:15 | BGE24 | SHORT RURAL |  | 3 | 75 | 225 | 0.0019579 | 2.6106e-05 | 0
2013-11-06 11:13 | WOTS24 | LONG RURAL |  | 2 | 62 | 124 | 0.00048017 | 7.7446e-06 | 0
2013-11-06 12:00 | BRT22 | SHORT RURAL |  | 3 | 40 | 120 | 0.0010442 | 2.6106e-05 | 0
2013-11-06 14:00 | SMR8 | LONG RURAL |  | 1 | 82 | 82 | 0.00031753 | 3.8723e-06 | 0
2013-11-07 08:50 | SFS1 | SHORT RURAL |  | 10 | 560 | 5600 | 0.048731 | 8.702e-05 | 0
2013-11-07 10:25 | FGY34 | URBAN |  | 255 | 220 | 56100 | 0.19542 | 0.00088829 | 0
2013-11-10 08:36 | MSD2 | LONG RURAL |  | 276 | 93 | 25668 | 0.099395 | 0.0010688 | 0
2013-11-07 09:37 | FGY34 | URBAN |  | 91 | 188 | 17108 | 0.059595 | 0.000317 | 0
2013-11-07 09:40 | BGE22 | SHORT RURAL |  | 49 | 350 | 17150 | 0.14924 | 0.0004264 | 0
2013-11-08 08:00 | SMR3 | LONG RURAL |  | 2 | 280 | 560 | 0.0021685 | 7.7446e-06 | 0
2013-11-08 09:00 | MBY11 | SHORT RURAL |  | 116 | 320 | 37120 | 0.32302 | 0.0010094 | 0
2013-11-07 08:56 | BWA23 | SHORT RURAL |  | 198 | 366 | 72468 | 0.63061 | 0.001723 | 0
2013-11-06 14:05 | BRT21 | SHORT RURAL |  | 6 | 79 | 474 | 0.0041247 | 5.2212e-05 | 0
2013-11-08 09:10 | MBY12 | SHORT RURAL |  | 4 | 215 | 860 | 0.0074837 | 3.4808e-05 | 0
2013-11-06 08:51 | CYN14 | URBAN |  | 112 | 180 | 20160 | 0.070227 | 0.00039015 | 0
2013-11-08 13:30 | SMR3 | LONG RURAL |  | 77 | 50 | 3850 | 0.014908 | 0.00029817 | 0
2013-11-07 08:45 | BWA23 | SHORT RURAL |  | 52 | 360 | 18720 | 0.1629 | 0.0004525 | 0
2013-11-06 10:45 | SLE31 | LONG RURAL |  | 1 | 45 | 45 | 0.00017425 | 3.8723e-06 | 0
2013-11-06 09:50 | DRN22 | SHORT RURAL |  | 492 | 343 | 168756 | 1.4685 | 0.0042814 | 0
2013-11-01 08:43 | NLA34 | SHORT RURAL |  | 15 | 262 | 3930 | 0.034199 | 0.00013053 | 0
2013-11-08 08:38 | BGE24 | SHORT RURAL |  | 6 | 269 | 1614 | 0.014045 | 5.2212e-05 | 0
2013-11-08 09:05 | BGE22 | SHORT RURAL |  | 66 | 380 | 25080 | 0.21825 | 0.00057433 | 0
2013-11-09 09:22 | BGE11 | SHORT RURAL |  | 31 | 365 | 11315 | 0.098463 | 0.00026976 | 0
2013-11-09 08:39 | BGE22 | SHORT RURAL |  | 20 | 201 | 4020 | 0.034982 | 0.00017404 | 0
2013-11-04 09:10 | SLE31 | LONG RURAL |  | 28 | 328 | 9184 | 0.035563 | 0.00010842 | 0
2013-11-09 14:05 | BGE24 | SHORT RURAL |  | 1 | 45 | 45 | 0.00039159 | 8.702e-06 | 0
2013-11-07 08:08 | LDL13 | SHORT RURAL |  | 13 | 472 | 6136 | 0.053395 | 0.00011313 | 0
2013-11-07 09:20 | BRT21 | SHORT RURAL |  | 32 | 324 | 10368 | 0.090222 | 0.00027846 | 0
2013-10-27 08:20 | LDL11 | URBAN |  | 1 | 413 | 413 | 0.0014387 | 3.4835e-06 | 0
2013-10-25 10:20 | FTR23 | LONG RURAL |  | 60 | 415 | 24900 | 0.096421 | 0.00023234 | 0
2013-11-11 09:10 | MWTS12 | URBAN |  | 123 | 210 | 25830 | 0.089978 | 0.00042847 | 0
2013-11-11 10:45 | TGN31 | LONG RURAL |  | 1 | 120 | 120 | 0.00046468 | 3.8723e-06 | 0
2013-11-11 09:40 | RWN33 | URBAN |  | 160 | 480 | 76800 | 0.26753 | 0.00055736 | 0
2013-11-11 09:30 | LDL23 | LONG RURAL |  | 288 | 145 | 41760 | 0.16171 | 0.0011152 | 0
2013-11-11 09:20 | WYK24 | SHORT RURAL |  | 100 | 287 | 28700 | 0.24975 | 0.0008702 | 0
2013-11-11 10:25 | RWN33 | URBAN |  | 63 | 310 | 19530 | 0.068032 | 0.00021946 | 0
2013-11-10 13:10 | WGL23 | SHORT RURAL |  | 1 | 200 | 200 | 0.0017404 | 8.702e-06 | 0
2013-11-10 13:06 | MSD1 | LONG RURAL |  | 7 | 111 | 777 | 0.0030088 | 2.7106e-05 | 0
2013-11-11 08:31 | MSD1 | LONG RURAL |  | 904 | 459 | 414936 | 1.6068 | 0.0035006 | 0
2013-11-11 09:10 | BWR32 | URBAN |  | 155 | 353 | 54715 | 0.1906 | 0.00053994 | 0
2013-11-07 10:00 | WOTS24 | LONG RURAL |  | 5 | 225 | 1125 | 0.0043564 | 1.9362e-05 | 0
2013-11-06 09:25 | NLA34 | SHORT RURAL |  | 4 | 80 | 320 | 0.0027846 | 3.4808e-05 | 0
2013-11-10 08:50 | MFA34 | SHORT RURAL |  | 14 | 195 | 2730 | 0.023756 | 0.00012183 | 0
2013-11-06 12:08 | NLA34 | SHORT RURAL |  | 12 | 212 | 2544 | 0.022138 | 0.00010442 | 0
2013-10-31 08:34 | BN6 | LONG RURAL |  | 408 | 425 | 173400 | 0.67146 | 0.0015799 | 0
2013-11-07 08:30 | BDL8 | LONG RURAL |  | 69 | 323 | 22287 | 0.086302 | 0.00026719 | 0
2013-11-07 11:15 | BDL8 | LONG RURAL |  | 1 | 198 | 198 | 0.00076672 | 3.8723e-06 | 0
2013-11-07 09:30 | BDL5 | LONG RURAL |  | 11 | 250 | 2750 | 0.010649 | 4.2595e-05 | 0
2013-11-07 09:21 | NLA31 | LONG RURAL |  | 34 | 236 | 8024 | 0.031071 | 0.00013166 | 0
2013-11-07 08:45 | OFR23 | LONG RURAL |  | 2 | 30 | 60 | 0.00023234 | 7.7446e-06 | 0
2013-11-09 09:00 | WOTS13 | LONG RURAL |  | 25 | 340 | 8500 | 0.032915 | 9.6808e-05 | 0
2013-11-07 09:40 | PHM33 | SHORT RURAL |  | 1 | 55 | 55 | 0.00047861 | 8.702e-06 | 0
2013-11-07 11:12 | PHM33 | SHORT RURAL |  | 6 | 33 | 198 | 0.001723 | 5.2212e-05 | 0
2013-11-07 12:00 | PHM33 | SHORT RURAL |  | 1 | 45 | 45 | 0.00039159 | 8.702e-06 | 0
2013-10-29 09:10 | WN2 | LONG RURAL |  | 1 | 170 | 170 | 0.00065829 | 3.8723e-06 | 0
2013-11-07 13:10 | PHM33 | SHORT RURAL |  | 5 | 70 | 350 | 0.0030457 | 4.351e-05 | 0
2013-11-08 09:15 | LLG12 | SHORT RURAL |  | 12 | 345 | 4140 | 0.036026 | 0.00010442 | 0
2013-11-08 09:00 | BGE22 | SHORT RURAL |  | 17 | 330 | 5610 | 0.048818 | 0.00014793 | 0
2013-11-08 09:00 | PHM14 | LONG RURAL |  | 41 | 260 | 10660 | 0.041279 | 0.00015876 | 0
2013-11-09 09:00 | OFR23 | LONG RURAL |  | 59 | 415 | 24485 | 0.094814 | 0.00022847 | 0
2013-10-26 10:24 | WYK23 | SHORT RURAL |  | 2 | 356 | 712 | 0.0061958 | 1.7404e-05 | 0
2013-11-12 10:50 | MOE22 | LONG RURAL |  | 1 | 90 | 90 | 0.00034851 | 3.8723e-06 | 0
2013-11-12 09:35 | WGL23 | SHORT RURAL |  | 1 | 30 | 30 | 0.00026106 | 8.702e-06 | 0
2013-11-12 14:10 | MOE22 | LONG RURAL |  | 1 | 45 | 45 | 0.00017425 | 3.8723e-06 | 0
2013-11-12 09:10 | WN6 | LONG RURAL |  | 10 | 305 | 3050 | 0.011811 | 3.8723e-05 | 0
2013-11-12 09:45 | FTR22 | SHORT RURAL |  | 1 | 50 | 50 | 0.0004351 | 8.702e-06 | 0
2013-11-12 11:05 | FTR22 | SHORT RURAL |  | 4 | 40 | 160 | 0.0013923 | 3.4808e-05 | 0
2013-11-12 09:26 | LGA11 | LONG RURAL |  | 49 | 208 | 10192 | 0.039467 | 0.00018974 | 0
2013-11-12 10:08 | WGI14 | SHORT RURAL |  | 96 | 277 | 26592 | 0.2314 | 0.00083539 | 0
2013-11-12 14:50 | WGL23 | SHORT RURAL |  | 6 | 30 | 180 | 0.0015664 | 5.2212e-05 | 0
2013-11-12 09:35 | MWTS11 | SHORT RURAL |  | 17 | 299 | 5083 | 0.044232 | 0.00014793 | 0
2013-11-12 09:15 | MOE22 | LONG RURAL |  | 11 | 174 | 1914 | 0.0074116 | 4.2595e-05 | 0
2013-11-12 09:45 | WYK23 | SHORT RURAL |  | 1 | 302 | 302 | 0.002628 | 8.702e-06 | 0
2013-11-12 10:25 | KLK1 | SHORT RURAL |  | 195 | 210 | 40950 | 0.35635 | 0.0016969 | 0
2013-11-12 09:15 | BN1 | LONG RURAL |  | 2 | 65 | 130 | 0.0005034 | 7.7446e-06 | 0
2013-11-12 08:40 | WYK24 | SHORT RURAL |  | 18 | 350 | 6300 | 0.054822 | 0.00015664 | 0
2013-11-14 09:06 | FTR23 | LONG RURAL |  | 4 | 19 | 76 | 0.0002943 | 1.5489e-05 | 0
2013-11-12 10:00 | LDL23 | LONG RURAL |  | 223 | 188 | 41924 | 0.16234 | 0.00086353 | 0
2013-11-12 08:30 | LDL23 | LONG RURAL |  | 179 | 275 | 49225 | 0.19061 | 0.00069314 | 0
2013-11-12 09:32 | WN5 | LONG RURAL |  | 1 | 153 | 153 | 0.00059246 | 3.8723e-06 | 0
2013-11-12 10:00 | WYK24 | SHORT RURAL |  | 3 | 159 | 477 | 0.0041508 | 2.6106e-05 | 0
2013-11-12 09:00 | KLK1 | SHORT RURAL |  | 4 | 318 | 1272 | 0.011069 | 3.4808e-05 | 0
2013-11-12 09:09 | WYK24 | SHORT RURAL |  | 1 | 234 | 234 | 0.0020363 | 8.702e-06 | 0
2013-11-13 08:15 | WYK23 | SHORT RURAL |  | 80 | 337 | 26960 | 0.23461 | 0.00069616 | 0
2013-11-13 10:14 | DRN23 | LONG RURAL |  | 734 | 287 | 210658 | 0.81573 | 0.0028423 | 0
2013-11-12 08:45 | CYN14 | URBAN |  | 72 | 345 | 24840 | 0.08653 | 0.00025081 | 0
2013-11-14 10:35 | FTR23 | LONG RURAL |  | 360 | 257 | 92520 | 0.35827 | 0.001394 | 0
2013-11-14 09:10 | WYK23 | SHORT RURAL |  | 36 | 110 | 3960 | 0.03446 | 0.00031327 | 0
2013-11-14 09:10 | WYK23 | SHORT RURAL |  | 383 | 386 | 147838 | 1.2865 | 0.0033329 | 0
2013-11-13 10:20 | WGI14 | SHORT RURAL |  | 97 | 155 | 15035 | 0.13083 | 0.00084409 | 0
2013-11-12 10:20 | MWTS11 | SHORT RURAL |  | 6 | 215 | 1290 | 0.011226 | 5.2212e-05 | 0
2013-11-14 12:10 | WGI14 | SHORT RURAL |  | 86 | 155 | 13330 | 0.116 | 0.00074837 | 0
2013-11-12 08:00 | EPG31 | URBAN |  | 125 | 330 | 41250 | 0.14369 | 0.00043544 | 0
2013-11-12 14:35 | WN6 | LONG RURAL |  | 2 | 40 | 80 | 0.00030979 | 7.7446e-06 | 0
2013-11-13 09:17 | BN2 | LONG RURAL |  | 14 | 309 | 4326 | 0.016752 | 5.4212e-05 | 0
2013-11-13 08:20 | BN6 | LONG RURAL |  | 2 | 440 | 880 | 0.0034076 | 7.7446e-06 | 0
2013-11-14 11:00 | MOE23 | SHORT RURAL |  | 40 | 190 | 7600 | 0.066135 | 0.00034808 | 0
2013-11-14 09:00 | CYN23 | URBAN |  | 35 | 285 | 9975 | 0.034748 | 0.00012192 | 0
2013-11-14 09:40 | WGI14 | SHORT RURAL |  | 61 | 85 | 5185 | 0.04512 | 0.00053082 | 0
2013-11-14 09:50 | ELM15 | SHORT RURAL |  | 12 | 270 | 3240 | 0.028194 | 0.00010442 | 0
2013-11-14 10:45 | ELM15 | SHORT RURAL |  | 47 | 315 | 14805 | 0.12883 | 0.00040899 | 0
2013-11-12 09:00 | SMR3 | LONG RURAL |  | 2 | 450 | 900 | 0.0034851 | 7.7446e-06 | 0
2013-11-12 08:40 | WOTS11 | LONG RURAL |  | 2 | 30 | 60 | 0.00023234 | 7.7446e-06 | 0
2013-11-12 09:48 | ELM33 | SHORT RURAL |  | 472 | 269 | 126968 | 1.1049 | 0.0041073 | 0
2013-11-12 09:54 | SMR8 | LONG RURAL |  | 78 | 296 | 23088 | 0.089404 | 0.00030204 | 0
2013-11-12 09:00 | ELM15 | SHORT RURAL |  | 238 | 245 | 58310 | 0.50741 | 0.0020711 | 0
2013-11-12 10:25 | WOTS13 | LONG RURAL |  | 1 | 38 | 38 | 0.00014715 | 3.8723e-06 | 0
2013-11-12 08:50 | CYN14 | URBAN |  | 68 | 400 | 27200 | 0.094751 | 0.00023688 | 0
2013-11-13 09:40 | MSD2 | LONG RURAL |  | 2 | 290 | 580 | 0.0022459 | 7.7446e-06 | 0
2013-11-12 09:15 | BRT11 | SHORT RURAL |  | 17 | 250 | 4250 | 0.036983 | 0.00014793 | 0
2013-11-12 10:40 | WOTS11 | LONG RURAL |  | 1 | 20 | 20 | 7.7446e-05 | 3.8723e-06 | 0
2013-11-12 09:50 | TRC01 | SHORT RURAL |  | 2 | 303 | 606 | 0.0052734 | 1.7404e-05 | 0
2013-11-12 09:35 | BN6 | LONG RURAL |  | 2 | 315 | 630 | 0.0024396 | 7.7446e-06 | 0
2013-11-14 09:05 | LGA23 | LONG RURAL |  | 25 | 395 | 9875 | 0.038239 | 9.6808e-05 | 0
2013-11-14 08:04 | KLK1 | SHORT RURAL |  | 95 | 447 | 42465 | 0.36953 | 0.00082669 | 0
2013-11-13 09:52 | MSD1 | LONG RURAL |  | 1 | 60 | 60 | 0.00023234 | 3.8723e-06 | 0
2013-11-14 08:41 | WOTS24 | LONG RURAL |  | 1563 | 423 | 661149 | 2.5602 | 0.0060524 | 0
2013-11-12 12:20 | WGL23 | SHORT RURAL |  | 5 | 125 | 625 | 0.0054387 | 4.351e-05 | 0
2013-11-08 09:50 | CNR3 | SHORT RURAL |  | 1 | 105 | 105 | 0.00091371 | 8.702e-06 | 0
2013-11-08 09:05 | NLA32 | SHORT RURAL |  | 62 | 191 | 11842 | 0.10305 | 0.00053952 | 0
2013-11-09 09:00 | SLE31 | LONG RURAL |  | 10 | 530 | 5300 | 0.020523 | 3.8723e-05 | 0
2013-11-10 08:40 | BGE12 | SHORT RURAL |  | 176 | 378 | 66528 | 0.57892 | 0.0015315 | 0
2013-11-10 08:45 | HPK13 | URBAN |  | 4 | 160 | 640 | 0.0022294 | 1.3934e-05 | 0
2013-10-29 09:10 | ALA01 | LONG RURAL |  | 2 | 395 | 790 | 0.0030591 | 7.7446e-06 | 0
2013-11-15 09:05 | WGL21 | LONG RURAL |  | 35 | 195 | 6825 | 0.026429 | 0.00013553 | 0
2013-11-15 08:37 | BWR13 | SHORT RURAL |  | 114 | 412 | 46968 | 0.40871 | 0.00099202 | 0
2013-11-14 13:23 | FTR23 | LONG RURAL |  | 1 | 63 | 63 | 0.00024396 | 3.8723e-06 | 0
2013-11-14 11:30 | FTR23 | LONG RURAL |  | 3 | 83 | 249 | 0.00096421 | 1.1617e-05 | 0
2013-11-14 13:15 | MOE22 | LONG RURAL |  | 26 | 165 | 4290 | 0.016612 | 0.00010068 | 0
2013-11-15 08:30 | MWTS22 | SHORT RURAL |  | 1 | 80 | 80 | 0.00069616 | 8.702e-06 | 0
2013-11-15 09:05 | MWTS11 | SHORT RURAL |  | 2 | 125 | 250 | 0.0021755 | 1.7404e-05 | 0
2013-11-15 13:10 | MWTS14 | SHORT RURAL |  | 1 | 50 | 50 | 0.0004351 | 8.702e-06 | 0
2013-11-15 09:36 | WYK24 | SHORT RURAL |  | 2 | 69 | 138 | 0.0012009 | 1.7404e-05 | 0
2013-11-15 09:10 | WYK12 | SHORT RURAL |  | 37 | 352 | 13024 | 0.11333 | 0.00032197 | 0
2013-11-15 09:25 | WGI14 | SHORT RURAL |  | 43 | 140 | 6020 | 0.052386 | 0.00037418 | 0
2013-11-15 09:40 | ELM33 | SHORT RURAL |  | 62 | 280 | 17360 | 0.15107 | 0.00053952 | 0
2013-11-15 09:00 | FTR23 | LONG RURAL |  | 55 | 288 | 15840 | 0.061337 | 0.00021298 | 0
2013-11-15 09:00 | LGA21 | SHORT RURAL |  | 355 | 292 | 103660 | 0.90205 | 0.0030892 | 0
2013-11-15 08:20 | BN6 | LONG RURAL |  | 7 | 285 | 1995 | 0.0077253 | 2.7106e-05 | 0
2013-11-15 09:00 | MSD1 | LONG RURAL |  | 451 | 161 | 72611 | 0.28117 | 0.0017464 | 0
2013-11-14 10:50 | ALA01 | LONG RURAL |  | 3 | 120 | 360 | 0.001394 | 1.1617e-05 | 0
2013-11-11 09:15 | MFA34 | SHORT RURAL |  | 14 | 276 | 3864 | 0.033624 | 0.00012183 | 0
2013-11-11 09:13 | NLA34 | SHORT RURAL |  | 9 | 65 | 585 | 0.0050907 | 7.8318e-05 | 0
2013-11-10 08:30 | BGE11 | SHORT RURAL |  | 76 | 335 | 25460 | 0.22155 | 0.00066135 | 0
2013-11-09 10:00 | SMG31 | URBAN |  | 115 | 401 | 46115 | 0.16064 | 0.0004006 | 0
2013-11-08 10:08 | WYK23 | SHORT RURAL |  | 1 | 134 | 134 | 0.0011661 | 8.702e-06 | 0
2013-11-10 08:30 | UWY1 | SHORT RURAL |  | 225 | 299 | 67275 | 0.58543 | 0.0019579 | 0
2013-11-14 10:50 | MOE31 | LONG RURAL |  | 1 | 50 | 50 | 0.00019362 | 3.8723e-06 | 0
2013-11-10 14:10 | FGY31 | URBAN |  | 13 | 165 | 2145 | 0.0074721 | 4.5285e-05 | 0
2013-11-12 06:10 | TGN42 | URBAN |  | 1 | 125 | 125 | 0.00043544 | 3.4835e-06 | 0
2013-11-14 09:00 | WGI23 | SHORT RURAL |  | 10 | 264 | 2640 | 0.022973 | 8.702e-05 | 0
2013-11-11 12:50 | CRE31 | URBAN |  | 57 | 84 | 4788 | 0.016679 | 0.00019856 | 0
2013-11-11 08:30 | BGE12 | SHORT RURAL |  | 69 | 246 | 16974 | 0.14771 | 0.00060044 | 0
2013-11-11 09:00 | OFR23 | LONG RURAL |  | 5 | 32 | 160 | 0.00061957 | 1.9362e-05 | 0
2013-11-11 11:00 | PHM14 | LONG RURAL |  | 23 | 100 | 2300 | 0.0089063 | 8.9063e-05 | 0
2013-11-11 13:56 | CF1 | SHORT RURAL |  | 2 | 108 | 216 | 0.0018796 | 1.7404e-05 | 0
2013-11-11 09:25 | PHM14 | LONG RURAL |  | 3 | 55 | 165 | 0.00063893 | 1.1617e-05 | 0
2013-11-11 10:15 | OFR23 | LONG RURAL |  | 1 | 25 | 25 | 9.6808e-05 | 3.8723e-06 | 0
2013-11-12 09:09 | WGL12 | LONG RURAL |  | 24 | 11 | 264 | 0.0010223 | 9.2936e-05 | 0
2013-11-12 09:15 | WGL12 | LONG RURAL |  | 62 | 187.4194 | 11620 | 0.044996 | 0.00024008 | 0
2013-11-12 10:15 | BGE22 | SHORT RURAL |  | 23 | 265 | 6095 | 0.053039 | 0.00020015 | 0
2013-11-12 10:40 | PHM14 | LONG RURAL |  | 1 | 115 | 115 | 0.00044532 | 3.8723e-06 | 0
2013-11-12 09:20 | PHM14 | LONG RURAL |  | 28 | 205 | 5740 | 0.022227 | 0.00010842 | 0
2013-10-28 12:10 | ALA01 | LONG RURAL |  | 4 | 7.25 | 29 | 0.0001123 | 1.5489e-05 | 0
2013-10-29 14:00 | ALA01 | LONG RURAL |  | 2 | 50 | 100 | 0.00038723 | 7.7446e-06 | 0
2013-10-28 13:51 | ALA01 | LONG RURAL |  | 12 | 20.25 | 243 | 0.00094097 | 4.6468e-05 | 0
2013-11-16 09:00 | MWTS22 | SHORT RURAL |  | 34 | 245 | 8330 | 0.072487 | 0.00029587 | 0
2013-11-15 12:10 | WGI14 | SHORT RURAL |  | 56 | 129 | 7224 | 0.062863 | 0.00048731 | 0
2013-11-16 09:15 | BN1 | LONG RURAL |  | 1 | 35 | 35 | 0.00013553 | 3.8723e-06 | 0
2013-11-16 09:15 | BN1 | LONG RURAL |  | 1 | 40 | 40 | 0.00015489 | 3.8723e-06 | 0
2013-11-16 10:20 | BN1 | LONG RURAL |  | 1 | 25 | 25 | 9.6808e-05 | 3.8723e-06 | 0
2013-11-16 10:35 | BN1 | LONG RURAL |  | 2 | 65 | 130 | 0.0005034 | 7.7446e-06 | 0
2013-11-16 08:08 | RWN24 | SHORT RURAL |  | 17 | 542 | 9214 | 0.08018 | 0.00014793 | 0
2013-10-31 10:00 | KLK2 | SHORT RURAL |  | 3 | 280 | 840 | 0.0073097 | 2.6106e-05 | 0
2013-11-15 09:20 | TRC01 | SHORT RURAL |  | 2 | 225 | 450 | 0.0039159 | 1.7404e-05 | 0
2013-11-13 09:35 | SMR4 | SHORT RURAL |  | 3 | 45 | 135 | 0.0011748 | 2.6106e-05 | 0
2013-11-13 08:40 | BDL5 | LONG RURAL |  | 3 | 215 | 645 | 0.0024976 | 1.1617e-05 | 0
2013-11-13 08:30 | MFA22 | LONG RURAL |  | 60 | 427 | 25620 | 0.099209 | 0.00023234 | 0
2013-11-12 08:36 | BGE24 | SHORT RURAL |  | 25 | 324 | 8100 | 0.070486 | 0.00021755 | 0
2013-11-13 09:15 | BDL1 | LONG RURAL |  | 21 | 330 | 6930 | 0.026835 | 8.1319e-05 | 0
2013-11-13 11:00 | WOTS13 | LONG RURAL |  | 64 | 105 | 6720 | 0.026022 | 0.00024783 | 0
2013-11-13 08:30 | BDL5 | LONG RURAL |  | 1 | 68 | 68 | 0.00026332 | 3.8723e-06 | 0
2013-11-11 09:15 | OFR23 | LONG RURAL |  | 10 | 96 | 960 | 0.0037174 | 3.8723e-05 | 0
2013-11-14 09:30 | MOE31 | LONG RURAL |  | 3 | 245 | 735 | 0.0028462 | 1.1617e-05 | 0
2013-11-14 09:57 | LGA23 | LONG RURAL |  | 232 | 211 | 48952 | 0.18956 | 0.00089838 | 0
2013-11-12 08:31 | WOTS13 | LONG RURAL |  | 558 | 524 | 292392 | 1.1322 | 0.0021608 | 0
2013-11-13 08:30 | WN6 | LONG RURAL |  | 70 | 342 | 23940 | 0.092703 | 0.00027106 | 0
2013-10-30 09:00 | ALA01 | LONG RURAL |  | 6 | 37.5 | 225 | 0.00087127 | 2.3234e-05 | 0
2013-11-17 08:04 | RWT15 | URBAN |  | 240 | 434 | 104160 | 0.36284 | 0.00083604 | 0
2013-11-17 09:03 | FTR23 | LONG RURAL |  | 157 | 320 | 50240 | 0.19455 | 0.00060795 | 0
2013-11-17 09:00 | FTR12 | LONG RURAL |  | 34 | 500 | 17000 | 0.065829 | 0.00013166 | 0
2013-11-16 12:40 | BN1 | LONG RURAL |  | 1 | 20 | 20 | 7.7446e-05 | 3.8723e-06 | 0
2013-11-13 09:29 | NLA31 | LONG RURAL |  | 130 | 279 | 36270 | 0.14045 | 0.0005034 | 0
2013-11-15 09:30 | BRT11 | SHORT RURAL |  | 4 | 72 | 288 | 0.0025062 | 3.4808e-05 | 0
2013-11-15 09:35 | BRT11 | SHORT RURAL |  | 2 | 35 | 70 | 0.00060914 | 1.7404e-05 | 0
2013-11-15 10:40 | BRT11 | SHORT RURAL |  | 2 | 50 | 100 | 0.0008702 | 1.7404e-05 | 0
2013-11-15 13:00 | BRT11 | SHORT RURAL |  | 2 | 25 | 50 | 0.0004351 | 1.7404e-05 | 0
2013-11-08 09:25 | DRN23 | LONG RURAL |  | 14 | 240 | 3360 | 0.013011 | 5.4212e-05 | 0
2013-11-13 09:00 | SLE31 | LONG RURAL |  | 53 | 607 | 32171 | 0.12458 | 0.00020523 | 0
2013-11-13 10:00 | MFA22 | LONG RURAL |  | 2 | 145 | 290 | 0.001123 | 7.7446e-06 | 0
2013-11-14 09:10 | SLE32 | SHORT RURAL |  | 8 | 260 | 2080 | 0.0181 | 6.9616e-05 | 0
2013-11-14 08:50 | ELM15 | SHORT RURAL |  | 230 | 327 | 75210 | 0.65448 | 0.0020015 | 0
2013-11-15 09:45 | WOTS13 | LONG RURAL |  | 26 | 102 | 2652 | 0.010269 | 0.00010068 | 0
2013-11-14 09:15 | SMR3 | LONG RURAL |  | 117 | 270 | 31590 | 0.12233 | 0.00045306 | 0
2013-11-14 09:06 | SMR8 | LONG RURAL |  | 38 | 219.5789 | 8344 | 0.032311 | 0.00014715 | 0
2013-11-17 09:00 | WN6 | LONG RURAL |  | 289 | 416 | 120224 | 0.46555 | 0.0011191 | 0
2013-10-31 12:05 | ALA01 | LONG RURAL |  | 12 | 15.4167 | 185 | 0.00071638 | 4.6468e-05 | 0
2013-11-18 09:15 | WGL23 | SHORT RURAL |  | 20 | 214.5 | 4290 | 0.037331 | 0.00017404 | 0
2013-11-18 10:30 | FTR12 | LONG RURAL |  | 2 | 38 | 76 | 0.0002943 | 7.7446e-06 | 0
2013-11-18 09:06 | FTR12 | LONG RURAL |  | 4 | 77 | 308 | 0.0011927 | 1.5489e-05 | 0
2013-11-18 09:02 | LGA24 | SHORT RURAL |  | 47 | 212 | 9964 | 0.086706 | 0.00040899 | 0
2013-11-18 10:33 | LDL13 | SHORT RURAL |  | 655 | 224.887 | 147301 | 1.2818 | 0.0056998 | 0
2013-11-18 09:20 | LGA23 | LONG RURAL |  | 6 | 355 | 2130 | 0.008248 | 2.3234e-05 | 0
2013-11-18 10:20 | WGL13 | SHORT RURAL |  | 37 | 285 | 10545 | 0.091762 | 0.00032197 | 0
2013-11-18 08:45 | TGN31 | LONG RURAL |  | 7 | 350 | 2450 | 0.0094872 | 2.7106e-05 | 0
2013-11-18 09:02 | MOE31 | LONG RURAL |  | 128 | 216 | 27648 | 0.10706 | 0.00049566 | 0
2013-11-18 09:55 | MVE01 | SHORT RURAL |  | 3 | 145 | 435 | 0.0037854 | 2.6106e-05 | 0
2013-11-18 10:30 | BRT21 | SHORT RURAL |  | 6 | 72 | 432 | 0.0037593 | 5.2212e-05 | 0
2013-11-18 10:30 | MVE01 | SHORT RURAL |  | 20 | 160 | 3200 | 0.027846 | 0.00017404 | 0
2013-11-14 09:00 | BDL1 | LONG RURAL |  | 20 | 350 | 7000 | 0.027106 | 7.7446e-05 | 0
2013-11-14 09:35 | BDL1 | LONG RURAL |  | 1 | 70 | 70 | 0.00027106 | 3.8723e-06 | 0
2013-11-14 11:40 | BDL1 | LONG RURAL |  | 2 | 50 | 100 | 0.00038723 | 7.7446e-06 | 0
2013-11-14 10:40 | BDL1 | LONG RURAL |  | 1 | 125 | 125 | 0.00048404 | 3.8723e-06 | 0
2013-11-14 09:00 | SLE32 | SHORT RURAL |  | 1 | 115 | 115 | 0.0010007 | 8.702e-06 | 0
2013-11-15 10:05 | FTR12 | LONG RURAL |  | 2 | 375 | 750 | 0.0029042 | 7.7446e-06 | 0
2013-11-14 11:15 | SLE32 | SHORT RURAL |  | 13 | 60 | 780 | 0.0067875 | 0.00011313 | 0
2013-11-10 08:55 | WOTS11 | LONG RURAL |  | 11 | 142 | 1562 | 0.0060486 | 4.2595e-05 | 0
2013-11-06 03:05 | RWT26 | URBAN |  | 34 | 97 | 3298 | 0.011489 | 0.00011844 | 0
2013-11-15 11:13 | BRT22 | SHORT RURAL |  | 8 | 362 | 2896 | 0.025201 | 6.9616e-05 | 0
2013-11-15 09:00 | SLE32 | SHORT RURAL |  | 22 | 175 | 3850 | 0.033503 | 0.00019144 | 0
2013-11-14 08:05 | WT11 | URBAN |  | 284 | 440 | 124960 | 0.4353 | 0.00098931 | 0
2013-11-14 09:45 | BGE11 | SHORT RURAL |  | 51 | 692 | 35292 | 0.30711 | 0.0004438 | 0
2013-11-14 09:50 | BGE11 | SHORT RURAL |  | 42 | 186 | 7812 | 0.06798 | 0.00036548 | 0
2013-11-01 08:30 | ALA01 | LONG RURAL |  | 7 | 28.5714 | 200 | 0.00077446 | 2.7106e-05 | 0
2013-11-19 09:05 | MOE22 | LONG RURAL |  | 1 | 95 | 95 | 0.00036787 | 3.8723e-06 | 0
2013-11-19 09:15 | MOE22 | LONG RURAL |  | 3 | 55 | 165 | 0.00063893 | 1.1617e-05 | 0
2013-11-19 11:10 | MOE22 | LONG RURAL |  | 2 | 70 | 140 | 0.00054212 | 7.7446e-06 | 0
2013-11-20 09:03 | WGL15 | SHORT RURAL |  | 137 | 375 | 51375 | 0.44706 | 0.0011922 | 0
2013-11-18 11:19 | FTR12 | LONG RURAL |  | 2 | 36 | 72 | 0.00027881 | 7.7446e-06 | 0
2013-11-19 09:20 | FTR23 | LONG RURAL |  | 4 | 88 | 352 | 0.0013631 | 1.5489e-05 | 0
2013-11-19 12:30 | FTR23 | LONG RURAL |  | 2 | 35 | 70 | 0.00027106 | 7.7446e-06 | 0
2013-11-20 09:25 | WYK11 | SHORT RURAL |  | 64 | 195 | 12480 | 0.1086 | 0.00055693 | 0
2013-11-20 08:25 | LDL13 | SHORT RURAL |  | 8 | 350 | 2800 | 0.024366 | 6.9616e-05 | 0
2013-11-19 09:00 | WYK24 | SHORT RURAL |  | 134 | 310 | 41540 | 0.36148 | 0.0011661 | 0
2013-11-19 09:38 | WYK23 | SHORT RURAL |  | 10 | 12 | 120 | 0.0010442 | 8.702e-05 | 0
2013-11-18 13:55 | LDL22 | SHORT RURAL |  | 2 | 47 | 94 | 0.00081799 | 1.7404e-05 | 0
2013-11-19 09:05 | LDL22 | SHORT RURAL |  | 2 | 323 | 646 | 0.0056215 | 1.7404e-05 | 0
2013-11-19 10:30 | DRN14 | SHORT RURAL |  | 49 | 315 | 15435 | 0.13431 | 0.0004264 | 0
2013-11-19 09:30 | RWN24 | SHORT RURAL |  | 366 | 75 | 27450 | 0.23887 | 0.0031849 | 0
2013-11-19 10:25 | WYK23 | SHORT RURAL |  | 2468 | 359 | 886012 | 7.7101 | 0.021476 | 0
2013-11-19 10:15 | LGA24 | SHORT RURAL |  | 4 | 81 | 324 | 0.0028194 | 3.4808e-05 | 0
2013-11-19 12:20 | LGA24 | SHORT RURAL |  | 2 | 103 | 206 | 0.0017926 | 1.7404e-05 | 0
2013-11-21 09:10 | WGL23 | SHORT RURAL |  | 146 | 395 | 57670 | 0.50184 | 0.0012705 | 0
2013-11-20 09:00 | LGA12 | SHORT RURAL |  | 2 | 63 | 126 | 0.0010964 | 1.7404e-05 | 0
2013-11-20 09:00 | LGA24 | SHORT RURAL |  | 1 | 270 | 270 | 0.0023495 | 8.702e-06 | 0
2013-11-19 12:50 | MWTS31 | SHORT RURAL |  | 1 | 120 | 120 | 0.0010442 | 8.702e-06 | 0
2013-11-19 11:00 | MWTS31 | SHORT RURAL |  | 2 | 25 | 50 | 0.0004351 | 1.7404e-05 | 0
2013-11-19 10:20 | MFA34 | SHORT RURAL |  | 81 | 320 | 25920 | 0.22556 | 0.00070486 | 0
2013-11-19 09:04 | LGA23 | LONG RURAL |  | 2 | 176 | 352 | 0.0013631 | 7.7446e-06 | 0
2013-11-19 09:45 | BN6 | LONG RURAL |  | 2 | 265 | 530 | 0.0020523 | 7.7446e-06 | 0
2013-11-19 09:48 | MSD2 | LONG RURAL |  | 5 | 92 | 460 | 0.0017813 | 1.9362e-05 | 0
2013-11-19 09:30 | LGA23 | LONG RURAL |  | 52 | 310 | 16120 | 0.062422 | 0.00020136 | 0
2013-11-18 11:00 | BN6 | LONG RURAL |  | 5 | 140 | 700 | 0.0027106 | 1.9362e-05 | 0
2013-11-21 10:05 | WYK12 | SHORT RURAL |  | 10 | 160 | 1600 | 0.013923 | 8.702e-05 | 0
2013-11-19 12:45 | MSD2 | LONG RURAL |  | 3 | 40 | 120 | 0.00046468 | 1.1617e-05 | 0
2013-11-21 11:14 | LDL23 | LONG RURAL |  | 204 | 370 | 75480 | 0.29228 | 0.00078995 | 0
2013-11-19 14:40 | MSD2 | LONG RURAL |  | 1 | 15 | 15 | 5.8085e-05 | 3.8723e-06 | 0
2013-11-19 12:10 | WN6 | LONG RURAL |  | 1 | 60 | 60 | 0.00023234 | 3.8723e-06 | 0
2013-11-19 09:00 | LGA11 | LONG RURAL |  | 5 | 265 | 1325 | 0.0051308 | 1.9362e-05 | 0
2013-11-18 17:05 | MOE32 | SHORT RURAL |  | 32 | 25 | 800 | 0.0069616 | 0.00027846 | 0
2013-11-19 09:35 | WGL23 | SHORT RURAL |  | 1 | 60 | 60 | 0.00052212 | 8.702e-06 | 0
2013-11-19 09:00 | MWTS31 | SHORT RURAL |  | 90 | 303 | 27270 | 0.2373 | 0.00078318 | 0
2013-11-19 09:00 | WGL23 | SHORT RURAL |  | 2 | 175 | 350 | 0.0030457 | 1.7404e-05 | 0
2013-11-20 09:42 | WN6 | LONG RURAL |  | 2 | 458 | 916 | 0.003547 | 7.7446e-06 | 0
2013-11-19 12:50 | WGL23 | SHORT RURAL |  | 3 | 40 | 120 | 0.0010442 | 2.6106e-05 | 0
2013-11-20 10:10 | MSD1 | LONG RURAL |  | 5 | 365 | 1825 | 0.007067 | 1.9362e-05 | 0
2013-11-19 13:50 | WGL23 | SHORT RURAL |  | 1 | 40 | 40 | 0.00034808 | 8.702e-06 | 0
2013-11-20 10:37 | LGA12 | SHORT RURAL |  | 3 | 108 | 324 | 0.0028194 | 2.6106e-05 | 0
2013-11-20 12:25 | BN1 | LONG RURAL |  | 12 | 90 | 1080 | 0.0041821 | 4.6468e-05 | 0
2013-11-20 10:55 | LLG12 | SHORT RURAL |  | 1 | 185 | 185 | 0.0016099 | 8.702e-06 | 0
2013-11-19 09:00 | MOE22 | LONG RURAL |  | 50 | 395 | 19750 | 0.076478 | 0.00019362 | 0
2013-11-21 09:00 | FTR23 | LONG RURAL |  | 225 | 382.72 | 86112 | 0.33345 | 0.00087127 | 0
2013-11-20 10:50 | WGL12 | LONG RURAL |  | 38 | 290 | 11020 | 0.042673 | 0.00014715 | 0
2013-11-20 09:00 | MOE31 | LONG RURAL |  | 92 | 425 | 39100 | 0.15141 | 0.00035625 | 0
2013-11-20 09:05 | WGL24 | LONG RURAL |  | 50 | 239 | 11950 | 0.046274 | 0.00019362 | 0
2013-11-20 12:55 | TGN31 | LONG RURAL |  | 1 | 31 | 31 | 0.00012004 | 3.8723e-06 | 0
2013-11-20 09:20 | LGA23 | LONG RURAL |  | 2 | 245 | 490 | 0.0018974 | 7.7446e-06 | 0
2013-11-20 13:30 | LGA12 | SHORT RURAL |  | 9 | 101 | 909 | 0.0079101 | 7.8318e-05 | 0
2013-11-21 09:00 | LGA12 | SHORT RURAL |  | 21 | 387 | 8127 | 0.070721 | 0.00018274 | 0
2013-11-21 09:30 | LGA13 | LONG RURAL |  | 36 | 320 | 11520 | 0.044609 | 0.0001394 | 0
2013-11-21 09:06 | LLG12 | SHORT RURAL |  | 1015 | 21.3803 | 21701 | 0.18884 | 0.0088325 | 0
2013-11-18 14:10 | MVE01 | SHORT RURAL |  | 14 | 50 | 700 | 0.0060914 | 0.00012183 | 0
2013-11-18 13:20 | BRT21 | SHORT RURAL |  | 5 | 105 | 525 | 0.0045685 | 4.351e-05 | 0
2013-11-20 08:36 | WGL23 | SHORT RURAL |  | 2 | 335 | 670 | 0.0058303 | 1.7404e-05 | 0
2013-11-20 14:24 | WGL23 | SHORT RURAL |  | 5 | 56 | 280 | 0.0024366 | 4.351e-05 | 0
2013-11-20 08:35 | TGN11 | SHORT RURAL |  | 1 | 180 | 180 | 0.0015664 | 8.702e-06 | 0
2013-11-19 09:30 | KMS1 | SHORT RURAL |  | 3 | 180 | 540 | 0.0046991 | 2.6106e-05 | 0
2013-11-19 09:25 | MVE01 | SHORT RURAL |  | 21 | 145 | 3045 | 0.026498 | 0.00018274 | 0
2013-11-21 09:20 | WGI24 | URBAN |  | 47 | 330 | 15510 | 0.054029 | 0.00016372 | 0
2013-11-14 12:30 | WGL12 | LONG RURAL |  | 1 | 5 | 5 | 1.9362e-05 | 3.8723e-06 | 0
2013-11-15 09:20 | PHM31 | SHORT RURAL |  | 94 | 271 | 25474 | 0.22167 | 0.00081799 | 0
2013-11-15 08:30 | BDL4 | SHORT RURAL |  | 2 | 260 | 520 | 0.004525 | 1.7404e-05 | 0
2013-11-15 09:20 | BDL5 | LONG RURAL |  | 1 | 50 | 50 | 0.00019362 | 3.8723e-06 | 0
2013-11-15 08:35 | BDL4 | SHORT RURAL |  | 15 | 321 | 4815 | 0.0419 | 0.00013053 | 0
2013-11-15 13:45 | BDL1 | LONG RURAL |  | 3 | 30 | 90 | 0.00034851 | 1.1617e-05 | 0
2013-11-15 11:10 | BDL5 | LONG RURAL |  | 1 | 30 | 30 | 0.00011617 | 3.8723e-06 | 0
2013-11-18 10:35 | BDL6 | SHORT RURAL |  | 1 | 60 | 60 | 0.00052212 | 8.702e-06 | 0
2013-11-18 08:35 | BDL8 | LONG RURAL |  | 1 | 45 | 45 | 0.00017425 | 3.8723e-06 | 0
2013-11-18 10:50 | BDL5 | LONG RURAL |  | 1 | 30 | 30 | 0.00011617 | 3.8723e-06 | 0
2013-11-18 13:50 | BDL5 | LONG RURAL |  | 4 | 45 | 180 | 0.00069702 | 1.5489e-05 | 0
2013-11-19 09:30 | BDL1 | LONG RURAL |  | 1 | 390 | 390 | 0.0015102 | 3.8723e-06 | 0
2013-11-19 09:13 | BDL8 | LONG RURAL |  | 1 | 217 | 217 | 0.00084029 | 3.8723e-06 | 0
2013-11-21 08:30 | BDL8 | LONG RURAL |  | 47 | 355 | 16685 | 0.06461 | 0.000182 | 0
2013-11-17 09:05 | SLE31 | LONG RURAL |  | 4 | 325 | 1300 | 0.005034 | 1.5489e-05 | 0
2013-11-19 08:37 | WOTS11 | LONG RURAL |  | 610 | 360.3803 | 219832 | 0.85126 | 0.0023621 | 0
2013-11-15 09:05 | LLG11 | SHORT RURAL |  | 3 | 20 | 60 | 0.00052212 | 2.6106e-05 | 0
2013-11-21 08:35 | LDL24 | URBAN |  | 52 | 365 | 18980 | 0.066117 | 0.00018114 | 0
2013-11-15 09:00 | LLG11 | SHORT RURAL |  | 69 | 343 | 23667 | 0.20595 | 0.00060044 | 0
2013-11-15 10:08 | LLG11 | SHORT RURAL |  | 2 | 52 | 104 | 0.000905 | 1.7404e-05 | 0
2013-11-18 09:23 | LLG11 | SHORT RURAL |  | 80 | 52 | 4160 | 0.0362 | 0.00069616 | 0
2013-11-18 09:25 | PHM31 | SHORT RURAL |  | 21 | 107 | 2247 | 0.019553 | 0.00018274 | 0
2013-11-18 10:55 | LLG13 | SHORT RURAL |  | 49 | 70 | 3430 | 0.029848 | 0.0004264 | 0
2013-11-12 10:40 | KLO24 | SHORT RURAL |  | 1 | 225 | 225 | 0.0019579 | 8.702e-06 | 0
2013-11-18 12:30 | LLG14 | SHORT RURAL |  | 4 | 60 | 240 | 0.0020885 | 3.4808e-05 | 0
2013-11-18 12:30 | KLO14 | LONG RURAL |  | 118 | 330 | 38940 | 0.15079 | 0.00045693 | 0
2013-11-18 14:10 | LLG12 | SHORT RURAL |  | 1 | 50 | 50 | 0.0004351 | 8.702e-06 | 0
2013-11-20 06:34 | CLN14 | SHORT RURAL |  | 10 | 1 | 10 | 8.702e-05 | 8.702e-05 | 0
2013-11-19 08:45 | CRE21 | SHORT RURAL |  | 10 | 280 | 2800 | 0.024366 | 8.702e-05 | 0
2013-11-14 12:20 | BGE22 | SHORT RURAL |  | 13 | 60 | 780 | 0.0067875 | 0.00011313 | 0
2013-11-21 08:00 | PHM34 | URBAN |  | 7 | 441 | 3087 | 0.010754 | 2.4384e-05 | 0
2013-11-14 09:00 | BGE22 | SHORT RURAL |  | 20 | 170 | 3400 | 0.029587 | 0.00017404 | 0
2013-11-14 09:00 | SFS1 | SHORT RURAL |  | 12 | 140 | 1680 | 0.014619 | 0.00010442 | 0
2013-11-14 09:35 | BGE24 | SHORT RURAL |  | 29 | 140 | 4060 | 0.03533 | 0.00025236 | 0
2013-11-21 09:45 | LLG11 | SHORT RURAL |  | 16 | 270 | 4320 | 0.037593 | 0.00013923 | 0
2013-11-14 09:15 | BGE12 | SHORT RURAL |  | 6 | 120 | 720 | 0.0062654 | 5.2212e-05 | 0
2013-11-14 13:00 | SFS1 | SHORT RURAL |  | 6 | 20 | 120 | 0.0010442 | 5.2212e-05 | 0
2013-11-15 09:35 | BGE12 | SHORT RURAL |  | 58 | 225 | 13050 | 0.11356 | 0.00050471 | 0
2013-11-21 08:30 | CRE33 | SHORT RURAL |  | 484 | 320 | 154880 | 1.3478 | 0.0042118 | 0
2013-11-18 09:25 | DRN14 | SHORT RURAL |  | 181 | 418.8619 | 75814 | 0.65973 | 0.0015751 | 0
2013-11-15 08:50 | BGE24 | SHORT RURAL |  | 12 | 118 | 1416 | 0.012322 | 0.00010442 | 0
2013-11-14 09:52 | FTR23 | LONG RURAL |  | 1 | 41 | 41 | 0.00015876 | 3.8723e-06 | 0
2013-11-14 09:45 | WGL12 | LONG RURAL |  | 114 | 220 | 25080 | 0.097118 | 0.00044144 | 0
2013-11-15 09:00 | BGE12 | SHORT RURAL |  | 3 | 180 | 540 | 0.0046991 | 2.6106e-05 | 0
2013-11-15 11:20 | BGE24 | SHORT RURAL |  | 1 | 120 | 120 | 0.0010442 | 8.702e-06 | 0
2013-11-19 09:04 | BRT11 | SHORT RURAL |  | 297 | 354 | 105138 | 0.91491 | 0.0025845 | 0
2013-11-15 08:45 | BGE12 | SHORT RURAL |  | 67 | 473 | 31691 | 0.27577 | 0.00058303 | 0
2013-11-17 08:30 | BGE12 | SHORT RURAL |  | 17 | 418 | 7106 | 0.061836 | 0.00014793 | 0
2013-11-18 09:25 | BGE24 | SHORT RURAL |  | 35 | 95 | 3325 | 0.028934 | 0.00030457 | 0
2013-11-18 09:17 | BGE11 | SHORT RURAL |  | 195 | 381 | 74295 | 0.64651 | 0.0016969 | 0
2013-11-18 09:40 | BGE12 | SHORT RURAL |  | 73 | 440 | 32120 | 0.27951 | 0.00063524 | 0
2013-11-20 08:35 | OFR23 | LONG RURAL |  | 274 | 328 | 89872 | 0.34801 | 0.001061 | 0
2013-11-22 08:40 | RWN26 | SHORT RURAL |  | 25 | 310 | 7750 | 0.06744 | 0.00021755 | 0
2013-11-22 09:54 | LDL23 | LONG RURAL |  | 4 | 350 | 1400 | 0.0054212 | 1.5489e-05 | 0
2013-11-22 09:03 | LDL13 | SHORT RURAL |  | 572 | 413 | 236236 | 2.0557 | 0.0049775 | 0
2013-11-22 10:10 | MOE31 | LONG RURAL |  | 8 | 230 | 1840 | 0.0071251 | 3.0979e-05 | 0
2013-11-22 08:33 | MOE21 | SHORT RURAL |  | 25 | 339 | 8475 | 0.073749 | 0.00021755 | 0
2013-11-22 09:33 | WGL15 | SHORT RURAL |  | 101 | 188 | 18988 | 0.16523 | 0.0008789 | 0
2013-11-22 09:05 | LGA21 | SHORT RURAL |  | 6 | 75 | 450 | 0.0039159 | 5.2212e-05 | 0
2013-11-21 14:20 | BDL8 | LONG RURAL |  | 119 | 5 | 595 | 0.002304 | 0.00046081 | 0
2013-11-21 09:05 | BWN14 | SHORT RURAL |  | 2 | 48 | 96 | 0.00083539 | 1.7404e-05 | 0
2013-11-22 08:35 | KLK1 | SHORT RURAL |  | 39 | 400 | 15600 | 0.13575 | 0.00033938 | 0
2013-11-22 14:50 | MWTS32 | SHORT RURAL |  | 1 | 30 | 30 | 0.00026106 | 8.702e-06 | 0
2013-11-23 09:00 | LDL14 | SHORT RURAL |  | 332 | 420 | 139440 | 1.2134 | 0.0028891 | 0
2013-11-23 08:35 | RWN26 | SHORT RURAL |  | 332 | 290 | 96280 | 0.83783 | 0.0028891 | 0
2013-11-20 09:05 | KMS21 | SHORT RURAL |  | 2 | 355 | 710 | 0.0061784 | 1.7404e-05 | 0
2013-11-21 09:30 | WGI22 | LONG RURAL |  | 2 | 285 | 570 | 0.0022072 | 7.7446e-06 | 0
2013-11-21 08:15 | WGL24 | LONG RURAL |  | 106 | 505 | 53530 | 0.20728 | 0.00041047 | 0
2013-11-21 08:30 | MSD1 | LONG RURAL |  | 109 | 477 | 51993 | 0.20133 | 0.00042208 | 0
2013-11-20 09:30 | MYT7 | LONG RURAL |  | 41 | 65 | 2665 | 0.01032 | 0.00015876 | 0
2013-11-21 09:00 | TGN31 | LONG RURAL |  | 28 | 330 | 9240 | 0.03578 | 0.00010842 | 0
2013-11-22 09:05 | LLG12 | SHORT RURAL |  | 91 | 83 | 7553 | 0.065726 | 0.00079188 | 0
2013-11-22 11:05 | LLG12 | SHORT RURAL |  | 2 | 45 | 90 | 0.00078318 | 1.7404e-05 | 0
2013-11-19 08:30 | SLE31 | LONG RURAL |  | 31 | 430 | 13330 | 0.051618 | 0.00012004 | 0
2013-11-23 10:20 | LGA13 | LONG RURAL |  | 6 | 200 | 1200 | 0.0046468 | 2.3234e-05 | 0
2013-11-19 10:11 | DRN22 | SHORT RURAL |  | 237 | 584 | 138408 | 1.2044 | 0.0020624 | 0
2013-11-22 09:15 | WN6 | LONG RURAL |  | 1 | 300 | 300 | 0.0011617 | 3.8723e-06 | 0
2013-11-20 10:10 | TRC01 | SHORT RURAL |  | 19 | 75 | 1425 | 0.0124 | 0.00016534 | 0
2013-11-20 09:10 | FTR12 | LONG RURAL |  | 43 | 470 | 20210 | 0.078259 | 0.00016651 | 0
2013-11-21 09:05 | FTR23 | LONG RURAL |  | 16 | 505 | 8080 | 0.031288 | 6.1957e-05 | 0
2013-11-20 09:05 | BRT21 | SHORT RURAL |  | 63 | 186.619 | 11757 | 0.10231 | 0.00054822 | 0
2013-11-21 09:00 | MSD2 | LONG RURAL |  | 91 | 270 | 24570 | 0.095143 | 0.00035238 | 0
2013-11-24 09:00 | FTR23 | LONG RURAL |  | 60 | 465 | 27900 | 0.10804 | 0.00023234 | 0
2013-11-24 09:05 | FTR23 | LONG RURAL |  | 136 | 235 | 31960 | 0.12376 | 0.00052663 | 0
2013-11-20 14:20 | WYK24 | SHORT RURAL |  | 1 | 33 | 33 | 0.00028717 | 8.702e-06 | 0
2013-11-19 08:20 | SLE31 | LONG RURAL |  | 28 | 440 | 12320 | 0.047707 | 0.00010842 | 0
2013-11-22 08:45 | BN6 | LONG RURAL |  | 95 | 145 | 13775 | 0.053341 | 0.00036787 | 0
2013-11-20 08:03 | EPG31 | URBAN |  | 162 | 482.9012 | 78230 | 0.27251 | 0.00056432 | 0
2013-11-22 10:00 | LGA12 | SHORT RURAL |  | 105 | 261 | 27405 | 0.23848 | 0.00091371 | 0
2013-11-23 09:00 | WGI14 | SHORT RURAL |  | 45 | 265 | 11925 | 0.10377 | 0.00039159 | 0
2013-11-19 09:20 | NLA31 | LONG RURAL |  | 8 | 175 | 1400 | 0.0054212 | 3.0979e-05 | 0
2013-11-20 09:00 | BDL4 | SHORT RURAL |  | 38 | 390 | 14820 | 0.12896 | 0.00033067 | 0
2013-11-20 08:54 | MFA34 | SHORT RURAL |  | 110 | 354 | 38940 | 0.33885 | 0.00095722 | 0
2013-11-21 09:00 | MFA22 | LONG RURAL |  | 887 | 565 | 501155 | 1.9406 | 0.0034347 | 0
2013-11-21 08:45 | SLE31 | LONG RURAL |  | 20 | 415 | 8300 | 0.03214 | 7.7446e-05 | 0
2013-11-22 08:30 | SLE31 | LONG RURAL |  | 17 | 250 | 4250 | 0.016457 | 6.5829e-05 | 0
2013-11-15 10:15 | EPG13 | SHORT RURAL |  | 86 | 364 | 31304 | 0.27241 | 0.00074837 | 0
2013-11-19 10:00 | BDL6 | SHORT RURAL |  | 4 | 170 | 680 | 0.0059173 | 3.4808e-05 | 0
2013-11-20 09:10 | BDL8 | LONG RURAL |  | 68 | 365 | 24820 | 0.096111 | 0.00026332 | 0
2013-11-19 08:48 | SFS1 | SHORT RURAL |  | 66 | 144 | 9504 | 0.082704 | 0.00057433 | 0
2013-11-19 08:32 | BGE22 | SHORT RURAL |  | 70 | 418 | 29260 | 0.25462 | 0.00060914 | 0
2013-11-23 10:10 | WN3 | LONG RURAL |  | 18 | 230 | 4140 | 0.016031 | 6.9702e-05 | 0
2013-11-19 08:40 | FGY21 | SHORT RURAL |  | 132 | 340 | 44880 | 0.39054 | 0.0011487 | 0
2013-11-19 09:25 | BGE24 | SHORT RURAL |  | 45 | 95 | 4275 | 0.037201 | 0.00039159 | 0
2013-11-19 08:35 | BGE11 | SHORT RURAL |  | 2 | 50 | 100 | 0.0008702 | 1.7404e-05 | 0
2013-11-20 09:50 | MVE01 | SHORT RURAL |  | 1 | 335 | 335 | 0.0029152 | 8.702e-06 | 0
2013-11-19 12:20 | BGE24 | SHORT RURAL |  | 23 | 117 | 2691 | 0.023417 | 0.00020015 | 0
2013-11-18 09:00 | BWN14 | SHORT RURAL |  | 3 | 385 | 1155 | 0.010051 | 2.6106e-05 | 0
2013-11-19 12:35 | BGE11 | SHORT RURAL |  | 2 | 45 | 90 | 0.00078318 | 1.7404e-05 | 0
2013-11-19 09:15 | BGE12 | SHORT RURAL |  | 137 | 367.4818 | 50345 | 0.4381 | 0.0011922 | 0
2013-11-20 10:30 | BGE11 | SHORT RURAL |  | 72 | 30 | 2160 | 0.018796 | 0.00062654 | 0
2013-11-20 09:18 | BGE11 | SHORT RURAL |  | 48 | 87 | 4176 | 0.036339 | 0.00041769 | 0
2013-11-20 09:19 | BGE23 | SHORT RURAL |  | 33 | 111 | 3663 | 0.031875 | 0.00028717 | 0
2013-11-20 09:10 | UWY1 | SHORT RURAL |  | 9 | 125 | 1125 | 0.0097897 | 7.8318e-05 | 0
2013-11-21 08:55 | WGL12 | LONG RURAL |  | 40 | 235 | 9400 | 0.0364 | 0.00015489 | 0
2013-11-20 10:00 | FGY23 | URBAN |  | 6 | 145 | 870 | 0.0030306 | 2.0901e-05 | 0
2013-11-22 09:10 | CRE33 | SHORT RURAL |  | 71 | 219 | 15549 | 0.13531 | 0.00061784 | 0
2013-11-20 09:00 | BGE11 | SHORT RURAL |  | 89 | 355 | 31595 | 0.27494 | 0.00077448 | 0
2013-11-22 08:40 | LLG14 | SHORT RURAL |  | 11 | 55 | 605 | 0.0052647 | 9.5722e-05 | 0
2013-11-20 11:55 | BGE11 | SHORT RURAL |  | 30 | 60 | 1800 | 0.015664 | 0.00026106 | 0
2013-11-22 09:00 | PHM12 | SHORT RURAL |  | 36 | 221 | 7956 | 0.069233 | 0.00031327 | 0
2013-11-22 10:10 | PHM14 | LONG RURAL |  | 2 | 50 | 100 | 0.00038723 | 7.7446e-06 | 0
2013-11-22 10:07 | WGL12 | LONG RURAL |  | 3 | 36 | 108 | 0.00041821 | 1.1617e-05 | 0
2013-11-20 13:10 | BGE24 | SHORT RURAL |  | 4 | 110 | 440 | 0.0038289 | 3.4808e-05 | 0
2013-11-20 09:27 | MDG1 | SHORT RURAL |  | 86 | 403 | 34658 | 0.30159 | 0.00074837 | 0
2013-11-22 12:35 | PHM31 | SHORT RURAL |  | 4 | 70 | 280 | 0.0024366 | 3.4808e-05 | 0
2013-11-23 08:30 | LLG11 | SHORT RURAL |  | 3 | 60 | 180 | 0.0015664 | 2.6106e-05 | 0
2013-11-25 10:15 | TGN31 | LONG RURAL |  | 2 | 150 | 300 | 0.0011617 | 7.7446e-06 | 0
2013-11-25 11:42 | LDL13 | SHORT RURAL |  | 139 | 308 | 42812 | 0.37255 | 0.0012096 | 0
2013-11-25 09:34 | LDL23 | LONG RURAL |  | 38 | 377 | 14326 | 0.055475 | 0.00014715 | 0
2013-11-25 09:00 | LGA12 | SHORT RURAL |  | 15 | 220 | 3300 | 0.028717 | 0.00013053 | 0
2013-11-25 08:35 | MDG1 | SHORT RURAL |  | 67 | 400 | 26800 | 0.23321 | 0.00058303 | 0
2013-11-25 09:48 | WYK12 | SHORT RURAL |  | 2 | 65 | 130 | 0.0011313 | 1.7404e-05 | 0
2013-11-25 08:15 | LDL23 | LONG RURAL |  | 16 | 450 | 7200 | 0.027881 | 6.1957e-05 | 0
2013-11-25 09:05 | LDL23 | LONG RURAL |  | 23 | 310 | 7130 | 0.02761 | 8.9063e-05 | 0
2013-11-25 11:50 | WYK24 | SHORT RURAL |  | 222 | 120 | 26640 | 0.23182 | 0.0019318 | 0
2013-11-25 09:50 | FTR21 | LONG RURAL |  | 172 | 216 | 37152 | 0.14386 | 0.00066604 | 0
2013-11-25 09:45 | OFR21 | SHORT RURAL |  | 83 | 380 | 31540 | 0.27446 | 0.00072226 | 0
2013-11-20 10:00 | WOTS24 | LONG RURAL |  | 19 | 110 | 2090 | 0.0080931 | 7.3574e-05 | 0
2013-11-20 09:50 | CNR3 | SHORT RURAL |  | 1 | 120 | 120 | 0.0010442 | 8.702e-06 | 0
2013-11-22 08:46 | MSD4 | LONG RURAL |  | 553 | 399 | 220647 | 0.85441 | 0.0021414 | 0
2013-11-23 08:53 | BRA11 | URBAN |  | 9 | 198 | 1782 | 0.0062076 | 3.1351e-05 | 0
2013-11-20 12:00 | UWY1 | SHORT RURAL |  | 10 | 150 | 1500 | 0.013053 | 8.702e-05 | 0
2013-11-21 16:40 | MOE22 | LONG RURAL |  | 2 | 125 | 250 | 0.00096808 | 7.7446e-06 | 0
2013-11-25 10:05 | MOE32 | SHORT RURAL |  | 37 | 195 | 7215 | 0.062785 | 0.00032197 | 0
2013-11-25 08:50 | WN5 | LONG RURAL |  | 172 | 370 | 63640 | 0.24643 | 0.00066604 | 0
2013-11-23 09:20 | KLK1 | SHORT RURAL |  | 46 | 264 | 12144 | 0.10568 | 0.00040029 | 0
2013-11-14 09:23 | WN5 | LONG RURAL |  | 1 | 17 | 17 | 6.5829e-05 | 3.8723e-06 | 0
2013-11-21 10:35 | CF2 | SHORT RURAL |  | 36 | 265 | 9540 | 0.083017 | 0.00031327 | 0
2013-11-20 12:50 | CNR3 | SHORT RURAL |  | 1 | 25 | 25 | 0.00021755 | 8.702e-06 | 0
2013-11-21 09:18 | NLA31 | LONG RURAL |  | 108 | 305 | 32940 | 0.12755 | 0.00041821 | 0
2013-11-22 13:45 | SLE31 | LONG RURAL |  | 7 | 40 | 280 | 0.0010842 | 2.7106e-05 | 0
2013-11-22 08:50 | BDL8 | LONG RURAL |  | 9 | 235 | 2115 | 0.0081899 | 3.4851e-05 | 0
2013-11-24 08:40 | BDL8 | LONG RURAL |  | 1058 | 451 | 477158 | 1.8477 | 0.0040969 | 0
2013-11-22 10:00 | BDL1 | LONG RURAL |  | 3 | 245 | 735 | 0.0028462 | 1.1617e-05 | 0
2013-11-22 09:20 | SLE31 | LONG RURAL |  | 2 | 190 | 380 | 0.0014715 | 7.7446e-06 | 0
2013-11-21 09:10 | MYT7 | LONG RURAL |  | 1 | 160 | 160 | 0.00061957 | 3.8723e-06 | 0
2013-11-22 10:30 | BDL5 | LONG RURAL |  | 41 | 216 | 8856 | 0.034293 | 0.00015876 | 0
2013-11-21 08:45 | FGY23 | URBAN |  | 116 | 405 | 46980 | 0.16365 | 0.00040408 | 0
2013-11-21 09:15 | WOTS24 | LONG RURAL |  | 3 | 35 | 105 | 0.00040659 | 1.1617e-05 | 0
2013-11-21 08:50 | BGE22 | SHORT RURAL |  | 87 | 377 | 32799 | 0.28542 | 0.00075707 | 0
2013-11-21 09:00 | WOTS24 | LONG RURAL |  | 20 | 185 | 3700 | 0.014328 | 7.7446e-05 | 0
2013-11-21 08:45 | LLG13 | SHORT RURAL |  | 57 | 420 | 23940 | 0.20833 | 0.00049601 | 0
2013-11-21 13:19 | MYT7 | LONG RURAL |  | 1 | 44 | 44 | 0.00017038 | 3.8723e-06 | 0
2013-11-22 09:20 | BRT11 | SHORT RURAL |  | 18 | 180 | 3240 | 0.028194 | 0.00015664 | 0
2013-11-22 09:20 | BRT21 | SHORT RURAL |  | 7 | 250 | 1750 | 0.015228 | 6.0914e-05 | 0
2013-11-22 09:10 | TRC01 | SHORT RURAL |  | 37 | 329 | 12173 | 0.10593 | 0.00032197 | 0
2013-11-24 09:15 | BRT11 | SHORT RURAL |  | 33 | 225 | 7425 | 0.064612 | 0.00028717 | 0
2013-11-22 12:45 | BRT11 | SHORT RURAL |  | 6 | 35 | 210 | 0.0018274 | 5.2212e-05 | 0
2013-11-22 09:34 | LGA12 | SHORT RURAL |  | 292 | 89 | 25988 | 0.22615 | 0.002541 | 0
2013-11-22 08:30 | SMR3 | LONG RURAL |  | 14 | 250 | 3500 | 0.013553 | 5.4212e-05 | 0
2013-11-22 09:05 | BGE22 | SHORT RURAL |  | 23 | 280 | 6440 | 0.056041 | 0.00020015 | 0
2013-11-24 09:00 | SMR8 | LONG RURAL |  | 2 | 555 | 1110 | 0.0042983 | 7.7446e-06 | 0
2013-11-25 10:05 | SMR3 | LONG RURAL |  | 1 | 105 | 105 | 0.00040659 | 3.8723e-06 | 0
2013-11-22 09:30 | BGE12 | SHORT RURAL |  | 41 | 205 | 8405 | 0.07314 | 0.00035678 | 0
2013-11-25 09:55 | KMS21 | SHORT RURAL |  | 3 | 125 | 375 | 0.0032632 | 2.6106e-05 | 0
2013-11-23 09:10 | BGE12 | SHORT RURAL |  | 64 | 60 | 3840 | 0.033416 | 0.00055693 | 0
2013-11-11 10:50 | BRT21 | SHORT RURAL |  | 5 | 120 | 600 | 0.0052212 | 4.351e-05 | 0
2013-11-26 09:25 | BWR13 | SHORT RURAL |  | 203 | 359 | 72877 | 0.63417 | 0.0017665 | 0
2013-11-27 08:13 | RWN33 | URBAN |  | 584 | 510 | 297840 | 1.0375 | 0.0020344 | 0
2013-11-26 09:54 | TGN43 | SHORT RURAL |  | 92 | 78.3696 | 7210 | 0.062741 | 0.00080058 | 0
2013-11-26 09:30 | WGL13 | SHORT RURAL |  | 9 | 350 | 3150 | 0.027411 | 7.8318e-05 | 0
2013-11-26 11:00 | WGL23 | SHORT RURAL |  | 2 | 45 | 90 | 0.00078318 | 1.7404e-05 | 0
2013-11-26 13:45 | MWTS32 | SHORT RURAL |  | 3 | 99 | 297 | 0.0025845 | 2.6106e-05 | 0
2013-11-28 09:00 | WGL23 | SHORT RURAL |  | 76 | 314 | 23864 | 0.20766 | 0.00066135 | 0
2013-11-26 10:00 | WYK12 | SHORT RURAL |  | 6 | 353 | 2118 | 0.018431 | 5.2212e-05 | 0
2013-11-26 08:32 | WYK23 | SHORT RURAL |  | 43 | 473 | 20339 | 0.17699 | 0.00037418 | 0
2013-11-26 08:53 | WYK24 | SHORT RURAL |  | 66 | 292 | 19272 | 0.1677 | 0.00057433 | 0
2013-11-25 12:00 | WYK12 | SHORT RURAL |  | 1 | 105 | 105 | 0.00091371 | 8.702e-06 | 0
2013-11-26 09:22 | FTR21 | LONG RURAL |  | 82 | 278 | 22796 | 0.088273 | 0.00031753 | 0
2013-11-26 13:15 | TGN31 | LONG RURAL |  | 3 | 110 | 330 | 0.0012779 | 1.1617e-05 | 0
2013-11-26 09:00 | LGA23 | LONG RURAL |  | 74 | 370 | 27380 | 0.10602 | 0.00028655 | 0
2013-11-27 09:00 | WGL24 | LONG RURAL |  | 190 | 369 | 70110 | 0.27149 | 0.00073574 | 0
2013-11-26 09:56 | FTR23 | LONG RURAL |  | 2 | 44 | 88 | 0.00034076 | 7.7446e-06 | 0
2013-11-28 11:28 | MOE21 | SHORT RURAL |  | 4 | 185 | 740 | 0.0064395 | 3.4808e-05 | 0
2013-11-27 09:00 | WGI14 | SHORT RURAL |  | 15 | 280 | 4200 | 0.036548 | 0.00013053 | 0
2013-11-27 10:00 | WYK24 | SHORT RURAL |  | 2 | 200 | 400 | 0.0034808 | 1.7404e-05 | 0
2013-11-27 09:20 | WYK12 | SHORT RURAL |  | 53 | 408 | 21624 | 0.18817 | 0.0004612 | 0
2013-11-27 09:49 | WYK24 | SHORT RURAL |  | 9 | 122 | 1098 | 0.0095548 | 7.8318e-05 | 0
2013-11-26 09:00 | MWTS14 | SHORT RURAL |  | 123 | 240 | 29520 | 0.25688 | 0.0010703 | 0
2013-11-27 09:00 | WGL24 | LONG RURAL |  | 8 | 397 | 3176 | 0.012298 | 3.0979e-05 | 0
2013-11-28 09:40 | MOE32 | SHORT RURAL |  | 3 | 120 | 360 | 0.0031327 | 2.6106e-05 | 0
2013-11-26 08:45 | LDL23 | LONG RURAL |  | 56 | 235 | 13160 | 0.05096 | 0.00021685 | 0
2013-11-26 08:50 | LDL22 | SHORT RURAL |  | 2 | 350 | 700 | 0.0060914 | 1.7404e-05 | 0
2013-11-28 10:09 | LDL21 | SHORT RURAL |  | 73 | 91 | 6643 | 0.057807 | 0.00063524 | 0
2013-11-28 08:35 | WYK24 | SHORT RURAL |  | 54 | 255 | 13770 | 0.11983 | 0.00046991 | 0
2013-11-27 09:20 | MOE32 | SHORT RURAL |  | 119 | 430 | 51170 | 0.44528 | 0.0010355 | 0
2013-11-28 09:15 | CLN22 | SHORT RURAL |  | 8 | 210 | 1680 | 0.014619 | 6.9616e-05 | 0
2013-11-26 10:13 | PHI12 | SHORT RURAL |  | 384 | 176 | 67584 | 0.58811 | 0.0033416 | 0
2013-11-26 09:10 | LGA12 | SHORT RURAL |  | 4 | 360 | 1440 | 0.012531 | 3.4808e-05 | 0
2013-11-26 09:30 | LGA11 | LONG RURAL |  | 39 | 330 | 12870 | 0.049837 | 0.00015102 | 0
2013-11-26 08:53 | KLK1 | SHORT RURAL |  | 794 | 446.2355 | 354311 | 3.0832 | 0.0069094 | 0
2013-11-27 11:00 | FTR12 | LONG RURAL |  | 1 | 196 | 196 | 0.00075897 | 3.8723e-06 | 0
2013-11-26 09:10 | LLG11 | SHORT RURAL |  | 15 | 185 | 2775 | 0.024148 | 0.00013053 | 0
2013-11-26 09:20 | OFR23 | LONG RURAL |  | 53 | 615 | 32595 | 0.12622 | 0.00020523 | 0
2013-11-25 13:05 | SMR3 | LONG RURAL |  | 1 | 125 | 125 | 0.00048404 | 3.8723e-06 | 0
2013-11-26 13:20 | LLG11 | SHORT RURAL |  | 68 | 27.9265 | 1899 | 0.016525 | 0.00059173 | 0
2013-11-18 11:10 | LDL24 | URBAN |  | 82 | 58 | 4756 | 0.016567 | 0.00028565 | 0
2013-11-24 09:11 | WN4 | SHORT RURAL |  | 453 | 412 | 186636 | 1.6241 | 0.003942 | 0
2013-11-28 08:45 | LGA12 | SHORT RURAL |  | 1 | 113 | 113 | 0.00098332 | 8.702e-06 | 0
2013-11-26 09:28 | KLK3 | SHORT RURAL |  | 139 | 76 | 10564 | 0.091928 | 0.0012096 | 0
2013-11-28 10:07 | LGA12 | SHORT RURAL |  | 70 | 413 | 28910 | 0.25157 | 0.00060914 | 0
2013-11-28 11:40 | LGA12 | SHORT RURAL |  | 2 | 35 | 70 | 0.00060914 | 1.7404e-05 | 0
2013-11-20 09:46 | DRN23 | LONG RURAL |  | 93 | 311 | 28923 | 0.112 | 0.00036013 | 0
2013-11-25 09:00 | WN6 | LONG RURAL |  | 53 | 11 | 583 | 0.0022576 | 0.00020523 | 0
2013-11-18 09:25 | SMR3 | LONG RURAL |  | 4 | 45 | 180 | 0.00069702 | 1.5489e-05 | 0
2013-11-20 13:15 | LDL13 | SHORT RURAL |  | 3 | 45 | 135 | 0.0011748 | 2.6106e-05 | 0
2013-11-21 09:30 | ELM15 | SHORT RURAL |  | 139 | 122 | 16958 | 0.14757 | 0.0012096 | 0
2013-11-21 09:10 | ELM13 | URBAN |  | 233 | 332 | 77356 | 0.26947 | 0.00081165 | 0
2013-11-27 08:30 | KLK1 | SHORT RURAL |  | 95 | 425 | 40375 | 0.35134 | 0.00082669 | 0
2013-11-28 09:15 | FTR12 | LONG RURAL |  | 1499 | 39.6197 | 59390 | 0.22998 | 0.0058046 | 0
2013-11-28 09:05 | MOE31 | LONG RURAL |  | 14 | 205 | 2870 | 0.011114 | 5.4212e-05 | 0
2013-11-28 10:25 | MOE31 | LONG RURAL |  | 1 | 220 | 220 | 0.00085191 | 3.8723e-06 | 0
2013-11-25 09:05 | BN1 | LONG RURAL |  | 1 | 328 | 328 | 0.0012701 | 3.8723e-06 | 0
2013-11-22 09:30 | DRN23 | LONG RURAL |  | 38 | 280 | 10640 | 0.041201 | 0.00014715 | 0
2013-11-25 10:30 | BN2 | LONG RURAL |  | 31 | 220 | 6820 | 0.026409 | 0.00012004 | 0
2013-11-26 08:30 | SMR3 | LONG RURAL |  | 1 | 130 | 130 | 0.0005034 | 3.8723e-06 | 0
2013-11-17 09:45 | KLK1 | SHORT RURAL |  | 4 | 270 | 1080 | 0.0093981 | 3.4808e-05 | 0
2013-11-21 13:00 | EPG32 | SHORT RURAL |  | 4 | 103 | 412 | 0.0035852 | 3.4808e-05 | 0
2013-11-27 09:10 | SMR3 | LONG RURAL |  | 2 | 50 | 100 | 0.00038723 | 7.7446e-06 | 0
2013-11-27 12:00 | SMR3 | LONG RURAL |  | 1 | 80 | 80 | 0.00030979 | 3.8723e-06 | 0
2013-11-28 08:30 | SMR3 | LONG RURAL |  | 2 | 140 | 280 | 0.0010842 | 7.7446e-06 | 0
2013-11-07 09:40 | ALA01 | LONG RURAL |  | 17 | 26.4706 | 450 | 0.0017425 | 6.5829e-05 | 0
2013-11-08 08:55 | ALA01 | LONG RURAL |  | 22 | 22.7273 | 500 | 0.0019362 | 8.5191e-05 | 0
2013-11-08 08:30 | ALA01 | LONG RURAL |  | 5 | 42 | 210 | 0.00081319 | 1.9362e-05 | 0
2013-11-07 09:10 | ALA01 | LONG RURAL |  | 20 | 20.5 | 410 | 0.0015876 | 7.7446e-05 | 0
2013-10-31 14:05 | ALA01 | LONG RURAL |  | 2 | 15 | 30 | 0.00011617 | 7.7446e-06 | 0
2013-11-11 08:20 | ALA01 | LONG RURAL |  | 6 | 13.3333 | 80 | 0.00030979 | 2.3234e-05 | 0
2013-11-11 10:00 | ALA01 | LONG RURAL |  | 16 | 19.6875 | 315 | 0.0012198 | 6.1957e-05 | 0
2013-11-29 09:23 | RWN26 | SHORT RURAL |  | 1 | 82 | 82 | 0.00071356 | 8.702e-06 | 0
2013-11-28 14:40 | MOE22 | LONG RURAL |  | 19 | 35 | 665 | 0.0025751 | 7.3574e-05 | 0
2013-11-29 09:22 | TGN23 | SHORT RURAL |  | 1 | 44 | 44 | 0.00038289 | 8.702e-06 | 0
2013-11-29 10:49 | TGN23 | SHORT RURAL |  | 1 | 44 | 44 | 0.00038289 | 8.702e-06 | 0
2013-11-29 08:30 | RWN26 | SHORT RURAL |  | 56 | 160 | 8960 | 0.07797 | 0.00048731 | 0
2013-11-29 09:05 | MWTS24 | SHORT RURAL |  | 7 | 412 | 2884 | 0.025096 | 6.0914e-05 | 0
2013-11-29 09:45 | WGL13 | SHORT RURAL |  | 2 | 35 | 70 | 0.00060914 | 1.7404e-05 | 0
2013-11-29 08:55 | WN5 | LONG RURAL |  | 25 | 145 | 3625 | 0.014037 | 9.6808e-05 | 0
2013-11-29 09:00 | WYK12 | SHORT RURAL |  | 48 | 302 | 14496 | 0.12614 | 0.00041769 | 0
2013-11-28 12:35 | LGA12 | SHORT RURAL |  | 34 | 122 | 4148 | 0.036096 | 0.00029587 | 0
2013-11-28 13:20 | LGA12 | SHORT RURAL |  | 1 | 60 | 60 | 0.00052212 | 8.702e-06 | 0
2013-11-29 09:00 | WN6 | LONG RURAL |  | 26 | 264 | 6864 | 0.02658 | 0.00010068 | 0
2013-11-27 10:00 | ELM13 | URBAN |  | 189 | 283 | 53487 | 0.18632 | 0.00065838 | 0
2013-11-28 09:05 | TGN23 | SHORT RURAL |  | 34 | 175 | 5950 | 0.051777 | 0.00029587 | 0
2013-11-26 09:25 | DRN13 | SHORT RURAL |  | 33 | 190 | 6270 | 0.054561 | 0.00028717 | 0
2013-11-28 09:45 | EPG32 | SHORT RURAL |  | 564 | 303 | 170892 | 1.4871 | 0.0049079 | 0
2013-11-28 09:05 | TGN23 | SHORT RURAL |  | 19 | 295 | 5605 | 0.048775 | 0.00016534 | 0
2013-11-22 09:00 | FTR22 | SHORT RURAL |  | 3 | 164 | 492 | 0.0042814 | 2.6106e-05 | 0
2013-11-28 10:26 | TGN31 | LONG RURAL |  | 2 | 24 | 48 | 0.00018587 | 7.7446e-06 | 0
2013-11-26 09:30 | NLA34 | SHORT RURAL |  | 1 | 315 | 315 | 0.0027411 | 8.702e-06 | 0
2013-11-27 09:08 | PHI11 | SHORT RURAL |  | 4 | 168 | 672 | 0.0058477 | 3.4808e-05 | 0
2013-11-24 09:00 | FGY34 | URBAN |  | 94 | 115 | 10810 | 0.037656 | 0.00032745 | 0
2013-11-27 09:20 | KLO14 | LONG RURAL |  | 187 | 322 | 60214 | 0.23317 | 0.00072412 | 0
2013-11-24 09:18 | MDG1 | SHORT RURAL |  | 199 | 381 | 75819 | 0.65977 | 0.0017317 | 0
2013-11-27 10:20 | WN2 | LONG RURAL |  | 2 | 115 | 230 | 0.00089063 | 7.7446e-06 | 0
2013-11-28 09:00 | MSD2 | LONG RURAL |  | 10 | 60 | 600 | 0.0023234 | 3.8723e-05 | 0
2013-11-24 11:25 | FGY14 | URBAN |  | 32 | 185 | 5920 | 0.020622 | 0.00011147 | 0
2013-11-26 08:29 | DRN23 | LONG RURAL |  | 733 | 435 | 318855 | 1.2347 | 0.0028384 | 0
2013-11-25 08:45 | BGE12 | SHORT RURAL |  | 1 | 70 | 70 | 0.00060914 | 8.702e-06 | 0
2013-11-25 10:37 | LYD14 | SHORT RURAL |  | 2 | 85 | 170 | 0.0014793 | 1.7404e-05 | 0
2013-11-20 13:15 | WN3 | LONG RURAL |  | 3 | 10 | 30 | 0.00011617 | 1.1617e-05 | 0
2013-11-26 08:43 | WN6 | LONG RURAL |  | 51 | 399 | 20349 | 0.078798 | 0.00019749 | 0
2013-11-29 12:47 | TGN23 | SHORT RURAL |  | 1 | 73 | 73 | 0.00063524 | 8.702e-06 | 0
2013-11-30 08:35 | WN2 | LONG RURAL |  | 160 | 400 | 64000 | 0.24783 | 0.00061957 | 0
2013-11-28 08:30 | MSD2 | LONG RURAL |  | 276 | 348 | 96048 | 0.37193 | 0.0010688 | 0
2013-11-26 10:22 | NLA31 | LONG RURAL |  | 3 | 68 | 204 | 0.00078995 | 1.1617e-05 | 0
2013-11-26 12:00 | NLA31 | LONG RURAL |  | 1 | 115 | 115 | 0.00044532 | 3.8723e-06 | 0
2013-11-27 08:40 | MFA22 | LONG RURAL |  | 1 | 150 | 150 | 0.00058085 | 3.8723e-06 | 0
2013-11-22 09:10 | LGA13 | LONG RURAL |  | 1 | 65 | 65 | 0.0002517 | 3.8723e-06 | 0
2013-11-22 09:00 | FTR23 | LONG RURAL |  | 1 | 115 | 115 | 0.00044532 | 3.8723e-06 | 0
2013-11-27 08:15 | MFA22 | LONG RURAL |  | 2 | 198 | 396 | 0.0015334 | 7.7446e-06 | 0
2013-11-28 09:30 | WYK24 | SHORT RURAL |  | 86 | 191 | 16426 | 0.14294 | 0.00074837 | 0
2013-11-28 09:35 | LGA23 | LONG RURAL |  | 42 | 299 | 12558 | 0.048629 | 0.00016264 | 0
2013-11-28 10:42 | RWN33 | URBAN |  | 283 | 223 | 63109 | 0.21984 | 0.00098583 | 0
2013-11-27 08:30 | BDL6 | SHORT RURAL |  | 219 | 390 | 85410 | 0.74324 | 0.0019057 | 0
2013-11-26 08:35 | SLE31 | LONG RURAL |  | 19 | 215 | 4085 | 0.015818 | 7.3574e-05 | 0
2013-11-26 09:01 | SLE24 | URBAN |  | 3 | 253 | 759 | 0.002644 | 1.045e-05 | 0
2013-11-27 10:15 | NLA34 | SHORT RURAL |  | 3 | 270 | 810 | 0.0070486 | 2.6106e-05 | 0
2013-11-27 09:30 | MFA21 | LONG RURAL |  | 1 | 250 | 250 | 0.00096808 | 3.8723e-06 | 0
2013-11-29 09:00 | LGA11 | LONG RURAL |  | 76 | 385 | 29260 | 0.1133 | 0.0002943 | 0
2013-11-23 09:00 | FTR22 | SHORT RURAL |  | 356 | 80 | 28480 | 0.24783 | 0.0030979 | 0
2013-11-27 09:00 | MFA22 | LONG RURAL |  | 38 | 420 | 15960 | 0.061802 | 0.00014715 | 0
2013-11-27 11:55 | MFA22 | LONG RURAL |  | 2 | 242 | 484 | 0.0018742 | 7.7446e-06 | 0
2013-11-28 10:10 | RWN33 | URBAN |  | 8 | 80 | 640 | 0.0022294 | 2.7868e-05 | 0
2013-11-27 08:45 | MFA21 | LONG RURAL |  | 4 | 345 | 1380 | 0.0053438 | 1.5489e-05 | 0
2013-11-27 09:35 | MFA34 | SHORT RURAL |  | 2 | 55 | 110 | 0.00095722 | 1.7404e-05 | 0
2013-11-27 11:25 | MFA34 | SHORT RURAL |  | 1 | 25 | 25 | 0.00021755 | 8.702e-06 | 0
2013-11-27 14:32 | MFA22 | LONG RURAL |  | 1 | 141 | 141 | 0.000546 | 3.8723e-06 | 0
2013-11-27 12:10 | MFA34 | SHORT RURAL |  | 1 | 35 | 35 | 0.00030457 | 8.702e-06 | 0
2013-11-27 14:05 | MFA34 | SHORT RURAL |  | 1 | 43 | 43 | 0.00037418 | 8.702e-06 | 0
2013-11-27 09:35 | FTR21 | LONG RURAL |  | 93 | 274 | 25482 | 0.098674 | 0.00036013 | 0
2013-11-28 13:00 | MSD1 | LONG RURAL |  | 7 | 62 | 434 | 0.0016806 | 2.7106e-05 | 0
2013-11-27 08:30 | NLA34 | SHORT RURAL |  | 1 | 240 | 240 | 0.0020885 | 8.702e-06 | 0
2013-11-28 09:00 | SLE31 | LONG RURAL |  | 2506 | 185 | 463610 | 1.7952 | 0.009704 | 0
2013-11-29 09:15 | TGN31 | LONG RURAL |  | 4 | 115 | 460 | 0.0017813 | 1.5489e-05 | 0
2013-11-28 09:05 | LGA23 | LONG RURAL |  | 31 | 405 | 12555 | 0.048617 | 0.00012004 | 0
2013-11-28 12:10 | RWN33 | URBAN |  | 2 | 60 | 120 | 0.00041802 | 6.967e-06 | 0
2013-11-21 13:15 | KMS21 | SHORT RURAL |  | 33 | 105 | 3465 | 0.030152 | 0.00028717 | 0
2013-11-22 09:20 | DRN22 | SHORT RURAL |  | 3219 | 13.8966 | 44733 | 0.38927 | 0.028012 | 0
2013-11-26 09:20 | SFS1 | SHORT RURAL |  | 16 | 166 | 2656 | 0.023112 | 0.00013923 | 0
2013-11-26 08:32 | BGE22 | SHORT RURAL |  | 18 | 319 | 5742 | 0.049967 | 0.00015664 | 0
2013-11-30 08:30 | WYK11 | SHORT RURAL |  | 206 | 390 | 80340 | 0.69912 | 0.0017926 | 0
2013-11-26 09:05 | BGE22 | SHORT RURAL |  | 53 | 359 | 19027 | 0.16557 | 0.0004612 | 0
2013-11-26 09:05 | BGE24 | SHORT RURAL |  | 148 | 377.5338 | 55875 | 0.48622 | 0.0012879 | 0
2013-11-26 09:20 | BGE12 | SHORT RURAL |  | 6 | 128 | 768 | 0.0066831 | 5.2212e-05 | 0
2013-11-26 09:20 | OFR23 | LONG RURAL |  | 17 | 170 | 2890 | 0.011191 | 6.5829e-05 | 0
2013-11-26 13:25 | LLG14 | SHORT RURAL |  | 1 | 70 | 70 | 0.00060914 | 8.702e-06 | 0
2013-11-28 08:30 | WN4 | SHORT RURAL |  | 12 | 405 | 4860 | 0.042292 | 0.00010442 | 0
2013-11-12 08:52 | ALA01 | LONG RURAL |  | 14 | 10.6429 | 149 | 0.00057697 | 5.4212e-05 | 0
2013-12-01 08:43 | RWN26 | SHORT RURAL |  | 202 | 403 | 81406 | 0.70839 | 0.0017578 | 0
2013-12-01 09:05 | LGA11 | LONG RURAL |  | 147 | 355 | 52185 | 0.20208 | 0.00056923 | 0
2013-12-01 09:30 | MFA34 | SHORT RURAL |  | 116 | 282 | 32712 | 0.28466 | 0.0010094 | 0
2013-11-25 08:40 | CLN23 | SHORT RURAL |  | 3 | 340 | 1020 | 0.008876 | 2.6106e-05 | 0
2013-11-28 09:15 | YN31 | URBAN |  | 8 | 83 | 664 | 0.002313 | 2.7868e-05 | 0
2013-11-25 09:34 | BDL4 | SHORT RURAL |  | 36 | 416 | 14976 | 0.13032 | 0.00031327 | 0
2013-11-26 09:18 | BDL5 | LONG RURAL |  | 53 | 147 | 7791 | 0.030169 | 0.00020523 | 0
2013-11-30 09:30 | TGN11 | SHORT RURAL |  | 199 | 270 | 53730 | 0.46756 | 0.0017317 | 0
2013-11-28 11:00 | DRN11 | URBAN |  | 14 | 240 | 3360 | 0.011705 | 4.8769e-05 | 0
2013-11-30 08:45 | MOE22 | LONG RURAL |  | 122 | 473 | 57706 | 0.22346 | 0.00047242 | 0
2013-12-01 09:30 | MOE31 | LONG RURAL |  | 184 | 389 | 71576 | 0.27716 | 0.00071251 | 0
2013-11-27 08:30 | BDL1 | LONG RURAL |  | 3 | 240 | 720 | 0.0027881 | 1.1617e-05 | 0
2013-11-27 08:20 | DRN23 | LONG RURAL |  | 1 | 70 | 70 | 0.00027106 | 3.8723e-06 | 0
2013-11-28 09:00 | NLA34 | SHORT RURAL |  | 21 | 295 | 6195 | 0.053909 | 0.00018274 | 0
2013-11-26 09:10 | WN3 | LONG RURAL |  | 35 | 185 | 6475 | 0.025073 | 0.00013553 | 0
2013-11-29 09:20 | WGL24 | LONG RURAL |  | 33 | 134 | 4422 | 0.017123 | 0.00012779 | 0
2013-11-26 09:20 | BRT11 | SHORT RURAL |  | 50 | 175 | 8750 | 0.076142 | 0.0004351 | 0
2013-11-28 08:30 | BDL8 | LONG RURAL |  | 61 | 315 | 19215 | 0.074407 | 0.00023621 | 0
2013-11-27 12:35 | NLA34 | SHORT RURAL |  | 3 | 75 | 225 | 0.0019579 | 2.6106e-05 | 0
2013-11-22 09:05 | WOTS11 | LONG RURAL |  | 6 | 55 | 330 | 0.0012779 | 2.3234e-05 | 0
2013-11-29 12:40 | WGL24 | LONG RURAL |  | 55 | 135 | 7425 | 0.028752 | 0.00021298 | 0
2013-11-28 09:00 | BDL1 | LONG RURAL |  | 4 | 310 | 1240 | 0.0048017 | 1.5489e-05 | 0
2013-11-29 09:05 | MYT7 | LONG RURAL |  | 4 | 345 | 1380 | 0.0053438 | 1.5489e-05 | 0
2013-11-27 09:20 | BGE11 | SHORT RURAL |  | 49 | 370 | 18130 | 0.15777 | 0.0004264 | 0
2013-11-27 09:15 | UWY1 | SHORT RURAL |  | 99 | 380 | 37620 | 0.32737 | 0.0008615 | 0
2013-11-27 09:00 | FGY34 | URBAN |  | 381 | 220 | 83820 | 0.29199 | 0.0013272 | 0
2013-11-27 08:40 | BGE22 | SHORT RURAL |  | 2 | 410 | 820 | 0.0071356 | 1.7404e-05 | 0
2013-11-27 10:00 | PHM14 | LONG RURAL |  | 37 | 153 | 5661 | 0.021921 | 0.00014328 | 0
2013-11-27 09:00 | OFR23 | LONG RURAL |  | 76 | 400 | 30400 | 0.11772 | 0.0002943 | 0
2013-11-27 15:00 | UWY1 | SHORT RURAL |  | 21 | 10 | 210 | 0.0018274 | 0.00018274 | 0
2013-11-28 09:00 | UWY1 | SHORT RURAL |  | 30 | 270 | 8100 | 0.070486 | 0.00026106 | 0
2013-11-28 08:26 | WN6 | LONG RURAL |  | 173 | 283 | 48959 | 0.18958 | 0.00066991 | 0
2013-11-16 08:04 | BGE24 | SHORT RURAL |  | 1 | 122 | 122 | 0.0010616 | 8.702e-06 | 0
2013-12-02 09:15 | WGL23 | SHORT RURAL |  | 2 | 105 | 210 | 0.0018274 | 1.7404e-05 | 0
2013-12-02 09:10 | WGL15 | SHORT RURAL |  | 2 | 130 | 260 | 0.0022625 | 1.7404e-05 | 0
2013-12-02 09:15 | FTR12 | LONG RURAL |  | 5 | 285 | 1425 | 0.005518 | 1.9362e-05 | 0
2013-12-02 09:45 | LDL22 | SHORT RURAL |  | 74 | 210 | 15540 | 0.13523 | 0.00064395 | 0
2013-12-02 09:20 | LGA13 | LONG RURAL |  | 47 | 405 | 19035 | 0.07371 | 0.000182 | 0
2013-12-02 09:15 | WN3 | LONG RURAL |  | 6 | 245 | 1470 | 0.0056923 | 2.3234e-05 | 0
2013-12-02 09:15 | WN3 | LONG RURAL |  | 43 | 331.1628 | 14240 | 0.055142 | 0.00016651 | 0
2013-12-02 11:50 | WGL12 | LONG RURAL |  | 17 | 370 | 6290 | 0.024357 | 6.5829e-05 | 0
2013-12-02 09:05 | WGI14 | SHORT RURAL |  | 6 | 215 | 1290 | 0.011226 | 5.2212e-05 | 0
2013-11-28 08:40 | PHM14 | LONG RURAL |  | 1 | 20 | 20 | 7.7446e-05 | 3.8723e-06 | 0
2013-11-27 11:10 | WOTS24 | LONG RURAL |  | 7 | 60 | 420 | 0.0016264 | 2.7106e-05 | 0
2013-11-28 08:57 | FGY33 | URBAN |  | 39 | 254 | 9906 | 0.034507 | 0.00013586 | 0
2013-11-28 08:40 | OFR23 | LONG RURAL |  | 22 | 125 | 2750 | 0.010649 | 8.5191e-05 | 0
2013-11-28 09:10 | PHM14 | LONG RURAL |  | 2 | 30 | 60 | 0.00023234 | 7.7446e-06 | 0
2013-11-28 09:30 | PHM14 | LONG RURAL |  | 1 | 30 | 30 | 0.00011617 | 3.8723e-06 | 0
2013-11-28 08:45 | PHM14 | LONG RURAL |  | 26 | 145 | 3770 | 0.014599 | 0.00010068 | 0
2013-11-28 12:30 | OFR23 | LONG RURAL |  | 2 | 50 | 100 | 0.00038723 | 7.7446e-06 | 0
2013-11-28 09:15 | WOTS24 | LONG RURAL |  | 3 | 155 | 465 | 0.0018006 | 1.1617e-05 | 0
2013-11-28 11:15 | PHM14 | LONG RURAL |  | 18 | 175 | 3150 | 0.012198 | 6.9702e-05 | 0
2013-11-28 12:00 | BGE22 | SHORT RURAL |  | 34 | 84 | 2856 | 0.024853 | 0.00029587 | 0
2013-11-28 13:35 | OFR23 | LONG RURAL |  | 2 | 55 | 110 | 0.00042595 | 7.7446e-06 | 0
2013-11-29 09:10 | WOTS24 | LONG RURAL |  | 9 | 245 | 2205 | 0.0085385 | 3.4851e-05 | 0
2013-11-28 09:00 | WGI23 | SHORT RURAL |  | 5 | 75 | 375 | 0.0032632 | 4.351e-05 | 0
2013-11-29 09:38 | SFS1 | SHORT RURAL |  | 45 | 307.2222 | 13825 | 0.1203 | 0.00039159 | 0
2013-11-21 08:38 | ALA01 | LONG RURAL |  | 3 | 387 | 1161 | 0.0044958 | 1.1617e-05 | 0
2013-11-29 09:50 | BDL1 | LONG RURAL |  | 6 | 340 | 2040 | 0.0078995 | 2.3234e-05 | 0
2013-11-29 09:15 | BDL5 | LONG RURAL |  | 137 | 262 | 35894 | 0.13899 | 0.00053051 | 0
2013-11-29 08:45 | BDL8 | LONG RURAL |  | 11 | 360 | 3960 | 0.015334 | 4.2595e-05 | 0
2013-11-29 09:25 | MFA34 | SHORT RURAL |  | 7 | 320 | 2240 | 0.019492 | 6.0914e-05 | 0
2013-11-29 10:50 | SLE32 | SHORT RURAL |  | 5 | 240 | 1200 | 0.010442 | 4.351e-05 | 0
2013-12-01 09:04 | WO13 | SHORT RURAL |  | 83 | 116 | 9628 | 0.083783 | 0.00072226 | 0
2013-11-25 09:25 | WN5 | LONG RURAL |  | 1 | 40 | 40 | 0.00015489 | 3.8723e-06 | 0
2013-12-02 09:40 | WOTS24 | LONG RURAL |  | 2 | 170 | 340 | 0.0013166 | 7.7446e-06 | 0
2013-12-02 09:25 | MOE31 | LONG RURAL |  | 1 | 60 | 60 | 0.00023234 | 3.8723e-06 | 0
2013-11-29 10:10 | ELM15 | SHORT RURAL |  | 69 | 410 | 28290 | 0.24618 | 0.00060044 | 0
2013-11-29 08:40 | SFS1 | SHORT RURAL |  | 76 | 206 | 15656 | 0.13624 | 0.00066135 | 0
2013-11-29 09:30 | BGE22 | SHORT RURAL |  | 212 | 360 | 76320 | 0.66413 | 0.0018448 | 0
2013-12-04 10:05 | TGN23 | SHORT RURAL |  | 10 | 135 | 1350 | 0.011748 | 8.702e-05 | 0
2013-12-04 10:10 | TGN23 | SHORT RURAL |  | 22 | 85 | 1870 | 0.016273 | 0.00019144 | 0
2013-12-05 09:02 | TGN23 | SHORT RURAL |  | 15 | 208 | 3120 | 0.02715 | 0.00013053 | 0
2013-12-05 09:00 | TGN23 | SHORT RURAL |  | 40 | 210 | 8400 | 0.073097 | 0.00034808 | 0
2013-12-05 09:15 | TGN23 | SHORT RURAL |  | 5 | 177 | 885 | 0.0077012 | 4.351e-05 | 0
2013-12-03 08:45 | MOE31 | LONG RURAL |  | 2 | 142 | 284 | 0.0010997 | 7.7446e-06 | 0
2013-12-03 13:10 | MOE31 | LONG RURAL |  | 12 | 250 | 3000 | 0.011617 | 4.6468e-05 | 0
2013-12-02 12:00 | MOE22 | LONG RURAL |  | 1 | 30 | 30 | 0.00011617 | 3.8723e-06 | 0
2013-12-03 09:35 | MOE31 | LONG RURAL |  | 2 | 165 | 330 | 0.0012779 | 7.7446e-06 | 0
2013-12-03 10:15 | MOE31 | LONG RURAL |  | 1 | 100 | 100 | 0.00038723 | 3.8723e-06 | 0
2013-12-04 09:10 | LGA13 | LONG RURAL |  | 24 | 210 | 5040 | 0.019516 | 9.2936e-05 | 0
2013-12-02 12:00 | FTR12 | LONG RURAL |  | 13 | 110 | 1430 | 0.0055374 | 5.034e-05 | 0
2013-12-03 08:40 | LGA12 | SHORT RURAL |  | 17 | 220 | 3740 | 0.032545 | 0.00014793 | 0
2013-12-03 10:05 | FTR12 | LONG RURAL |  | 3 | 124 | 372 | 0.0014405 | 1.1617e-05 | 0
2013-12-04 09:10 | MOE31 | LONG RURAL |  | 28 | 360 | 10080 | 0.039033 | 0.00010842 | 0
2013-12-03 09:20 | LGA13 | LONG RURAL |  | 50 | 425 | 21250 | 0.082287 | 0.00019362 | 0
2013-12-04 08:35 | LGA12 | SHORT RURAL |  | 16 | 135 | 2160 | 0.018796 | 0.00013923 | 0
2013-12-04 09:30 | LDL23 | LONG RURAL |  | 3 | 205 | 615 | 0.0023815 | 1.1617e-05 | 0
2013-12-03 09:01 | FTR21 | LONG RURAL |  | 23 | 264 | 6072 | 0.023513 | 8.9063e-05 | 0
2013-12-03 08:40 | WYK24 | SHORT RURAL |  | 221 | 135 | 29835 | 0.25962 | 0.0019231 | 0
2013-12-04 08:31 | LGA23 | LONG RURAL |  | 48 | 69 | 3312 | 0.012825 | 0.00018587 | 0
2013-12-03 08:53 | BN6 | LONG RURAL |  | 144 | 513 | 73872 | 0.28606 | 0.00055761 | 0
2013-12-04 09:00 | LGA13 | LONG RURAL |  | 214 | 230 | 49220 | 0.1906 | 0.00082868 | 0
2013-12-05 08:45 | KLK1 | SHORT RURAL |  | 136 | 410 | 55760 | 0.48522 | 0.0011835 | 0
2013-12-04 08:00 | LDL13 | SHORT RURAL |  | 34 | 430 | 14620 | 0.12722 | 0.00029587 | 0
2013-12-03 09:00 | WN3 | LONG RURAL |  | 37 | 254 | 9398 | 0.036392 | 0.00014328 | 0
2013-12-03 10:38 | WN3 | LONG RURAL |  | 1 | 65 | 65 | 0.0002517 | 3.8723e-06 | 0
2013-12-04 09:08 | WGI31 | SHORT RURAL |  | 433 | 165 | 71445 | 0.62171 | 0.003768 | 0
2013-12-04 08:40 | WN3 | LONG RURAL |  | 1 | 225 | 225 | 0.00087127 | 3.8723e-06 | 0
2013-12-03 09:00 | WGI14 | SHORT RURAL |  | 66 | 317 | 20922 | 0.18206 | 0.00057433 | 0
2013-12-05 10:05 | WN6 | LONG RURAL |  | 1 | 73 | 73 | 0.00028268 | 3.8723e-06 | 0
2013-12-04 09:25 | TGN31 | LONG RURAL |  | 4 | 125 | 500 | 0.0019362 | 1.5489e-05 | 0
2013-12-05 08:50 | WGL24 | LONG RURAL |  | 93 | 530 | 49290 | 0.19087 | 0.00036013 | 0
2013-12-05 11:49 | WN6 | LONG RURAL |  | 1 | 43 | 43 | 0.00016651 | 3.8723e-06 | 0
2013-12-04 09:05 | TGN41 | LONG RURAL |  | 4 | 325 | 1300 | 0.005034 | 1.5489e-05 | 0
2013-11-29 09:30 | BGE24 | SHORT RURAL |  | 133 | 345 | 45885 | 0.39929 | 0.0011574 | 0
2013-11-29 09:40 | BGE11 | SHORT RURAL |  | 182 | 230 | 41860 | 0.36426 | 0.0015838 | 0
2013-11-29 09:00 | BWN14 | SHORT RURAL |  | 8 | 180 | 1440 | 0.012531 | 6.9616e-05 | 0
2013-11-29 13:10 | UWY1 | SHORT RURAL |  | 31 | 55 | 1705 | 0.014837 | 0.00026976 | 0
2013-11-29 12:00 | PHM14 | LONG RURAL |  | 133 | 169 | 22477 | 0.087038 | 0.00051502 | 0
2013-11-30 08:05 | BGE11 | SHORT RURAL |  | 293 | 129.2048 | 37857 | 0.32943 | 0.0025497 | 0
2013-11-30 08:30 | BGE11 | SHORT RURAL |  | 45 | 295 | 13275 | 0.11552 | 0.00039159 | 0
2013-11-30 10:45 | PHM14 | LONG RURAL |  | 41 | 43 | 1763 | 0.0068269 | 0.00015876 | 0
2013-12-03 08:45 | SLE31 | LONG RURAL |  | 1097 | 559 | 613223 | 2.3746 | 0.0042479 | 0
2013-12-04 09:50 | MOE22 | LONG RURAL |  | 4 | 220 | 880 | 0.0034076 | 1.5489e-05 | 0
2013-12-05 09:30 | WGL23 | SHORT RURAL |  | 2 | 55 | 110 | 0.00095722 | 1.7404e-05 | 0
2013-11-28 08:30 | KLK2 | SHORT RURAL |  | 2 | 135 | 270 | 0.0023495 | 1.7404e-05 | 0
2013-12-05 09:25 | MOE22 | LONG RURAL |  | 1 | 55 | 55 | 0.00021298 | 3.8723e-06 | 0
2013-12-05 09:20 | MOE22 | LONG RURAL |  | 3 | 145 | 435 | 0.0016845 | 1.1617e-05 | 0
2013-11-28 08:30 | KLK1 | SHORT RURAL |  | 158 | 450 | 71100 | 0.61871 | 0.0013749 | 0
2013-12-04 13:05 | LGA12 | SHORT RURAL |  | 4 | 25 | 100 | 0.0008702 | 3.4808e-05 | 0
2013-11-30 08:45 | BN6 | LONG RURAL |  | 1 | 110 | 110 | 0.00042595 | 3.8723e-06 | 0
2013-12-05 09:20 | LGA12 | SHORT RURAL |  | 11 | 370 | 4070 | 0.035417 | 9.5722e-05 | 0
2013-12-04 08:50 | RWN33 | URBAN |  | 70 | 145 | 10150 | 0.035357 | 0.00024384 | 0
2013-12-05 09:15 | LGA23 | LONG RURAL |  | 19 | 275 | 5225 | 0.020233 | 7.3574e-05 | 0
2013-11-25 09:15 | TGN31 | LONG RURAL |  | 2 | 105 | 210 | 0.00081319 | 7.7446e-06 | 0
2013-12-05 09:15 | LGA13 | LONG RURAL |  | 2 | 78 | 156 | 0.00060408 | 7.7446e-06 | 0
2013-12-04 09:30 | BN2 | LONG RURAL |  | 110 | 195 | 21450 | 0.083061 | 0.00042595 | 0
2013-11-21 09:30 | DRN12 | URBAN |  | 16 | 582 | 9312 | 0.032438 | 5.5736e-05 | 0
2013-12-06 09:00 | LGA13 | LONG RURAL |  | 19 | 315 | 5985 | 0.023176 | 7.3574e-05 | 0
2013-12-06 09:49 | WYK24 | SHORT RURAL |  | 177 | 199 | 35223 | 0.30651 | 0.0015402 | 0
2013-12-06 09:20 | LDL23 | LONG RURAL |  | 58 | 489 | 28362 | 0.10983 | 0.00022459 | 0
2013-12-06 12:30 | MOE31 | LONG RURAL |  | 3 | 50 | 150 | 0.00058085 | 1.1617e-05 | 0
2013-12-06 14:05 | MOE31 | LONG RURAL |  | 3 | 40 | 120 | 0.00046468 | 1.1617e-05 | 0
2013-12-06 10:00 | MOE31 | LONG RURAL |  | 4 | 75 | 300 | 0.0011617 | 1.5489e-05 | 0
2013-12-05 11:45 | WN3 | LONG RURAL |  | 1 | 135 | 135 | 0.00052276 | 3.8723e-06 | 0
2013-12-05 13:10 | WN6 | LONG RURAL |  | 3 | 30 | 90 | 0.00034851 | 1.1617e-05 | 0
2013-12-06 09:35 | BRA11 | URBAN |  | 97 | 205 | 19885 | 0.069269 | 0.0003379 | 0
2013-12-06 10:20 | BN2 | LONG RURAL |  | 2 | 65 | 130 | 0.0005034 | 7.7446e-06 | 0
2013-12-06 08:15 | WYK23 | SHORT RURAL |  | 241 | 298 | 71818 | 0.62496 | 0.0020972 | 0
2013-12-05 13:30 | MOE22 | LONG RURAL |  | 2 | 40 | 80 | 0.00030979 | 7.7446e-06 | 0
2013-12-06 09:15 | WN2 | LONG RURAL |  | 1 | 165 | 165 | 0.00063893 | 3.8723e-06 | 0
2013-12-05 11:02 | LGA13 | LONG RURAL |  | 1 | 68 | 68 | 0.00026332 | 3.8723e-06 | 0
2013-12-05 13:15 | LGA13 | LONG RURAL |  | 3 | 40 | 120 | 0.00046468 | 1.1617e-05 | 0
2013-12-06 09:27 | LGA13 | LONG RURAL |  | 7 | 113 | 791 | 0.003063 | 2.7106e-05 | 0
2013-12-03 13:10 | BWA22 | LONG RURAL |  | 10 | 10 | 100 | 0.00038723 | 3.8723e-05 | 0
2013-12-06 11:00 | BN2 | LONG RURAL |  | 1 | 55 | 55 | 0.00021298 | 3.8723e-06 | 0
2013-11-27 09:00 | SMR8 | LONG RURAL |  | 1 | 240 | 240 | 0.00092936 | 3.8723e-06 | 0
2013-12-02 08:40 | BWN14 | SHORT RURAL |  | 36 | 180 | 6480 | 0.056389 | 0.00031327 | 0
2013-11-22 09:07 | SMR8 | LONG RURAL |  | 30 | 243 | 7290 | 0.028229 | 0.00011617 | 0
2013-11-27 09:45 | MSD1 | LONG RURAL |  | 1 | 105 | 105 | 0.00040659 | 3.8723e-06 | 0
2013-11-27 08:53 | MSD1 | LONG RURAL |  | 55 | 212 | 11660 | 0.045151 | 0.00021298 | 0
2013-12-02 09:00 | SMR1 | SHORT RURAL |  | 8 | 610 | 4880 | 0.042466 | 6.9616e-05 | 0
2013-12-02 08:39 | TRC01 | SHORT RURAL |  | 66 | 427 | 28182 | 0.24524 | 0.00057433 | 0
2013-12-04 08:45 | RWN31 | SHORT RURAL |  | 61 | 182 | 11102 | 0.096609 | 0.00053082 | 0
2013-11-22 09:05 | BN1 | LONG RURAL |  | 13 | 240 | 3120 | 0.012082 | 5.034e-05 | 0
2013-11-29 09:41 | ELM15 | SHORT RURAL |  | 22 | 145 | 3190 | 0.027759 | 0.00019144 | 0
2013-11-29 09:15 | BDL8 | LONG RURAL |  | 69 | 400 | 27600 | 0.10688 | 0.00026719 | 0
2013-11-27 09:37 | BN2 | LONG RURAL |  | 32 | 278 | 8896 | 0.034448 | 0.00012391 | 0
2013-12-03 08:30 | SMR3 | LONG RURAL |  | 1 | 110 | 110 | 0.00042595 | 3.8723e-06 | 0
2013-12-02 09:17 | BDL4 | SHORT RURAL |  | 4 | 23 | 92 | 0.00080058 | 3.4808e-05 | 0
2013-12-03 09:05 | SMR5 | LONG RURAL |  | 53 | 355 | 18815 | 0.072858 | 0.00020523 | 0
2013-12-04 09:25 | MFA34 | SHORT RURAL |  | 5 | 155 | 775 | 0.006744 | 4.351e-05 | 0
2013-11-27 09:00 | LLG14 | SHORT RURAL |  | 34 | 180 | 6120 | 0.053256 | 0.00029587 | 0
2013-12-06 08:05 | TGN41 | LONG RURAL |  | 45 | 375 | 16875 | 0.065345 | 0.00017425 | 0
2013-12-01 08:35 | BN6 | LONG RURAL |  | 26 | 360 | 9360 | 0.036245 | 0.00010068 | 0
2013-12-02 09:55 | MYT8 | SHORT RURAL |  | 1 | 365 | 365 | 0.0031762 | 8.702e-06 | 0
2013-11-30 08:40 | WYK23 | SHORT RURAL |  | 42 | 205 | 8610 | 0.074924 | 0.00036548 | 0
2013-12-02 09:10 | BRT22 | SHORT RURAL |  | 52 | 204 | 10608 | 0.092311 | 0.0004525 | 0
2013-12-01 12:00 | PHM14 | LONG RURAL |  | 213 | 103 | 21939 | 0.084955 | 0.0008248 | 0
2013-12-05 08:55 | WGI22 | LONG RURAL |  | 17 | 415 | 7055 | 0.027319 | 6.5829e-05 | 0
2013-12-04 08:55 | WGI34 | SHORT RURAL |  | 2 | 10 | 20 | 0.00017404 | 1.7404e-05 | 0
2013-12-01 09:30 | WGL12 | LONG RURAL |  | 47 | 75 | 3525 | 0.01365 | 0.000182 | 0
2013-12-04 12:55 | OFR24 | URBAN |  | 1 | 115 | 115 | 0.0004006 | 3.4835e-06 | 0
2013-12-04 11:05 | LLG13 | SHORT RURAL |  | 8 | 45 | 360 | 0.0031327 | 6.9616e-05 | 0
2013-12-05 09:30 | FTR23 | LONG RURAL |  | 16 | 335 | 5360 | 0.020756 | 6.1957e-05 | 0
2013-12-05 08:32 | CLN22 | SHORT RURAL |  | 108 | 301 | 32508 | 0.28288 | 0.00093981 | 0
2013-12-05 13:30 | LLG13 | SHORT RURAL |  | 2 | 30 | 60 | 0.00052212 | 1.7404e-05 | 0
2013-12-06 09:20 | LGA13 | LONG RURAL |  | 6 | 265 | 1590 | 0.006157 | 2.3234e-05 | 0
2013-12-03 09:30 | ELM15 | SHORT RURAL |  | 127 | 375 | 47625 | 0.41443 | 0.0011052 | 0
2013-12-05 09:17 | YN38 | SHORT RURAL |  | 3 | 348 | 1044 | 0.0090849 | 2.6106e-05 | 0
2013-12-06 11:18 | BN6 | LONG RURAL |  | 2 | 51 | 102 | 0.00039498 | 7.7446e-06 | 0
2013-12-06 09:00 | WGL12 | LONG RURAL |  | 16 | 200 | 3200 | 0.012391 | 6.1957e-05 | 0
2013-12-03 10:15 | WOTS24 | LONG RURAL |  | 4 | 55 | 220 | 0.00085191 | 1.5489e-05 | 0
2013-12-06 09:25 | LGA13 | LONG RURAL |  | 2 | 60 | 120 | 0.00046468 | 7.7446e-06 | 0
2013-12-03 09:30 | WOTS24 | LONG RURAL |  | 2 | 25 | 50 | 0.00019362 | 7.7446e-06 | 0
2013-12-06 09:00 | LGA12 | SHORT RURAL |  | 19 | 210 | 3990 | 0.034721 | 0.00016534 | 0
2013-12-03 11:20 | MBY12 | SHORT RURAL |  | 2 | 50 | 100 | 0.0008702 | 1.7404e-05 | 0
2013-12-02 12:54 | MSD1 | LONG RURAL |  | 44 | 78 | 3432 | 0.01329 | 0.00017038 | 0
2013-12-03 09:00 | FTR12 | LONG RURAL |  | 44 | 344 | 15136 | 0.058611 | 0.00017038 | 0
2013-12-03 09:30 | BWA23 | SHORT RURAL |  | 6 | 20 | 120 | 0.0010442 | 5.2212e-05 | 0
2013-12-02 09:10 | BGE11 | SHORT RURAL |  | 73 | 260 | 18980 | 0.16516 | 0.00063524 | 0
2013-12-03 09:45 | UWY1 | SHORT RURAL |  | 67 | 125 | 8375 | 0.072879 | 0.00058303 | 0
2013-12-03 09:14 | BGE22 | SHORT RURAL |  | 3128 | 221 | 691288 | 6.0156 | 0.02722 | 0
2013-12-03 12:15 | BGE12 | SHORT RURAL |  | 1 | 105 | 105 | 0.00091371 | 8.702e-06 | 0
2013-12-03 10:13 | DRN23 | LONG RURAL |  | 62 | 339 | 21018 | 0.081388 | 0.00024008 | 0
2013-12-03 12:30 | UWY1 | SHORT RURAL |  | 2 | 95 | 190 | 0.0016534 | 1.7404e-05 | 0
2013-12-05 09:10 | FTR12 | LONG RURAL |  | 17 | 225 | 3825 | 0.014812 | 6.5829e-05 | 0
2013-12-07 09:10 | TGN31 | LONG RURAL |  | 12 | 535 | 6420 | 0.02486 | 4.6468e-05 | 0
2013-12-07 09:00 | RWN33 | URBAN |  | 311 | 400 | 124400 | 0.43335 | 0.0010834 | 0
2013-12-06 10:30 | WN3 | LONG RURAL |  | 2 | 75 | 150 | 0.00058085 | 7.7446e-06 | 0
2013-11-30 09:05 | WYK23 | SHORT RURAL |  | 3 | 245 | 735 | 0.0063959 | 2.6106e-05 | 0
2013-12-06 13:00 | WN3 | LONG RURAL |  | 3 | 110 | 330 | 0.0012779 | 1.1617e-05 | 0
2013-12-04 22:15 | NRN12 | URBAN |  | 10 | 265 | 2650 | 0.0092312 | 3.4835e-05 | 0
2013-12-06 09:45 | WN5 | LONG RURAL |  | 3 | 80 | 240 | 0.00092936 | 1.1617e-05 | 0
2013-12-03 09:50 | NLA32 | SHORT RURAL |  | 8 | 140 | 1120 | 0.0097462 | 6.9616e-05 | 0
2013-12-05 09:42 | WGI23 | SHORT RURAL |  | 45 | 373.7556 | 16819 | 0.14636 | 0.00039159 | 0
2013-12-07 09:00 | TGN41 | LONG RURAL |  | 937 | 430 | 402910 | 1.5602 | 0.0036284 | 0
2013-12-03 09:00 | TRC01 | SHORT RURAL |  | 47 | 325 | 15275 | 0.13292 | 0.00040899 | 0
2013-12-01 09:36 | RWN24 | SHORT RURAL |  | 116 | 340 | 39440 | 0.34321 | 0.0010094 | 0
2013-12-03 09:35 | FTR23 | LONG RURAL |  | 32 | 276 | 8832 | 0.0342 | 0.00012391 | 0
2013-12-07 09:10 | LLG12 | SHORT RURAL |  | 28 | 313 | 8764 | 0.076264 | 0.00024366 | 0
2013-12-04 10:24 | DRN22 | SHORT RURAL |  | 25 | 144 | 3600 | 0.031327 | 0.00021755 | 0
2013-12-07 09:23 | FTR23 | LONG RURAL |  | 60 | 267 | 16020 | 0.062034 | 0.00023234 | 0
2013-12-04 11:00 | DRN23 | LONG RURAL |  | 188 | 95 | 17860 | 0.06916 | 0.000728 | 0
2013-12-06 12:50 | FTR23 | LONG RURAL |  | 2 | 55 | 110 | 0.00042595 | 7.7446e-06 | 0
2013-12-03 12:30 | NLA32 | SHORT RURAL |  | 1 | 165 | 165 | 0.0014358 | 8.702e-06 | 0
2013-12-04 09:18 | NLA32 | SHORT RURAL |  | 98 | 164 | 16072 | 0.13986 | 0.00085279 | 0
2013-12-05 13:00 | BRT21 | SHORT RURAL |  | 3 | 50 | 150 | 0.0013053 | 2.6106e-05 | 0
2013-12-04 09:20 | WOTS24 | LONG RURAL |  | 1 | 90 | 90 | 0.00034851 | 3.8723e-06 | 0
2013-12-04 08:00 | LDL11 | URBAN |  | 207 | 410 | 84870 | 0.29564 | 0.00072108 | 0
2013-11-30 09:25 | KLK1 | SHORT RURAL |  | 3 | 282 | 846 | 0.0073619 | 2.6106e-05 | 0
2013-12-05 08:30 | WOTS24 | LONG RURAL |  | 2 | 175 | 350 | 0.0013553 | 7.7446e-06 | 0
2013-12-05 09:15 | WOTS24 | LONG RURAL |  | 6 | 155 | 930 | 0.0036013 | 2.3234e-05 | 0
2013-11-28 09:34 | MDI1 | SHORT RURAL |  | 31 | 351 | 10881 | 0.094686 | 0.00026976 | 0
2013-12-03 11:50 | NLA32 | SHORT RURAL |  | 2 | 374 | 748 | 0.0065091 | 1.7404e-05 | 0
2013-12-03 12:35 | NLA32 | SHORT RURAL |  | 1 | 55 | 55 | 0.00047861 | 8.702e-06 | 0
2013-12-03 15:10 | NLA32 | SHORT RURAL |  | 2 | 30 | 60 | 0.00052212 | 1.7404e-05 | 0
2013-12-06 09:55 | FTR12 | LONG RURAL |  | 2 | 49 | 98 | 0.00037949 | 7.7446e-06 | 0
2013-12-04 10:35 | NLA32 | SHORT RURAL |  | 4 | 332 | 1328 | 0.011556 | 3.4808e-05 | 0
2013-12-04 09:55 | BDL8 | LONG RURAL |  | 2 | 27 | 54 | 0.0002091 | 7.7446e-06 | 0
2013-11-28 09:45 | MVE01 | SHORT RURAL |  | 11 | 295 | 3245 | 0.028238 | 9.5722e-05 | 0
2013-12-04 14:00 | KLK2 | SHORT RURAL |  | 1 | 175 | 175 | 0.0015228 | 8.702e-06 | 0
2013-11-29 10:00 | KLO24 | SHORT RURAL |  | 216 | 200 | 43200 | 0.37593 | 0.0018796 | 0
2013-12-01 08:35 | WOTS13 | LONG RURAL |  | 1 | 170 | 170 | 0.00065829 | 3.8723e-06 | 0
2013-12-05 09:39 | DRN23 | LONG RURAL |  | 21 | 297 | 6237 | 0.024152 | 8.1319e-05 | 0
2013-12-05 12:00 | WOTS24 | LONG RURAL |  | 2 | 50 | 100 | 0.00038723 | 7.7446e-06 | 0
2013-11-15 14:00 | ALA01 | LONG RURAL |  | 8 | 21.875 | 175 | 0.00067766 | 3.0979e-05 | 0
2013-11-18 09:00 | ALA01 | LONG RURAL |  | 12 | 15.4167 | 185 | 0.00071638 | 4.6468e-05 | 0
2013-11-19 08:50 | ALA01 | LONG RURAL |  | 8 | 20.625 | 165 | 0.00063893 | 3.0979e-05 | 0
2013-12-08 09:00 | FTR22 | SHORT RURAL |  | 1 | 180 | 180 | 0.0015664 | 8.702e-06 | 0
2013-12-08 09:03 | FTR22 | SHORT RURAL |  | 169 | 60 | 10140 | 0.088238 | 0.0014706 | 0
2013-12-06 11:10 | BRT21 | SHORT RURAL |  | 5 | 35 | 175 | 0.0015228 | 4.351e-05 | 0
2013-12-06 09:00 | WOTS24 | LONG RURAL |  | 1 | 140 | 140 | 0.00054212 | 3.8723e-06 | 0
2013-12-06 10:15 | MVE01 | SHORT RURAL |  | 1 | 50 | 50 | 0.0004351 | 8.702e-06 | 0
2013-12-06 09:38 | WOTS24 | LONG RURAL |  | 1 | 36 | 36 | 0.0001394 | 3.8723e-06 | 0
2013-12-06 09:40 | SMR5 | LONG RURAL |  | 5 | 380 | 1900 | 0.0073574 | 1.9362e-05 | 0
2013-12-06 10:15 | WGL13 | SHORT RURAL |  | 8 | 80 | 640 | 0.0055693 | 6.9616e-05 | 0
2013-12-05 09:15 | WN2 | LONG RURAL |  | 74 | 325 | 24050 | 0.093129 | 0.00028655 | 0
2013-12-08 06:40 | WGI24 | URBAN |  | 13 | 385 | 5005 | 0.017435 | 4.5285e-05 | 0
2013-12-03 08:52 | BGE12 | SHORT RURAL |  | 38 | 353 | 13414 | 0.11673 | 0.00033067 | 0
2013-12-05 08:00 | RWN33 | URBAN |  | 104 | 300 | 31200 | 0.10868 | 0.00036228 | 0
2013-12-02 10:30 | KLO14 | LONG RURAL |  | 3 | 105 | 315 | 0.0012198 | 1.1617e-05 | 0
2013-11-29 09:00 | ELM33 | SHORT RURAL |  | 9 | 57 | 513 | 0.0044641 | 7.8318e-05 | 0
2013-12-05 09:30 | ELM33 | SHORT RURAL |  | 70 | 352.8571 | 24700 | 0.21494 | 0.00060914 | 0
2013-12-05 14:40 | DRN23 | LONG RURAL |  | 1 | 48 | 48 | 0.00018587 | 3.8723e-06 | 0
2013-11-28 08:19 | MYT7 | LONG RURAL |  | 1 | 161 | 161 | 0.00062344 | 3.8723e-06 | 0
2013-12-05 10:01 | MVE01 | SHORT RURAL |  | 137 | 181 | 24797 | 0.21578 | 0.0011922 | 0
2013-12-06 09:00 | FTR12 | LONG RURAL |  | 66 | 335 | 22110 | 0.085617 | 0.00025557 | 0
2013-12-06 11:00 | WOTS24 | LONG RURAL |  | 2 | 61 | 122 | 0.00047242 | 7.7446e-06 | 0
2013-12-03 08:32 | BGE11 | SHORT RURAL |  | 260 | 419 | 108940 | 0.94799 | 0.0022625 | 0
2013-12-03 08:32 | BGE11 | SHORT RURAL |  | 64 | 1 | 64 | 0.00055693 | 0.00055693 | 0
2013-12-03 15:30 | BGE11 | SHORT RURAL |  | 324 | 1 | 324 | 0.0028194 | 0.0028194 | 0
2013-12-08 09:50 | MOE32 | SHORT RURAL |  | 10 | 130 | 1300 | 0.011313 | 8.702e-05 | 0
2013-12-04 08:50 | FGY32 | URBAN |  | 78 | 110 | 8580 | 0.029888 | 0.00027171 | 0
2013-12-04 08:15 | SFS1 | SHORT RURAL |  | 25 | 520 | 13000 | 0.11313 | 0.00021755 | 0
2013-12-08 09:30 | WOTS13 | LONG RURAL |  | 2 | 240 | 480 | 0.0018587 | 7.7446e-06 | 0
2013-12-05 11:00 | KLK2 | SHORT RURAL |  | 5 | 120 | 600 | 0.0052212 | 4.351e-05 | 0
2013-12-08 09:03 | WGL15 | SHORT RURAL |  | 87 | 152 | 13224 | 0.11507 | 0.00075707 | 0
2013-11-25 09:01 | MSD1 | LONG RURAL |  | 109 | 491 | 53519 | 0.20724 | 0.00042208 | 0
2013-11-20 09:00 | ALA01 | LONG RURAL |  | 22 | 541.1818 | 11906 | 0.046104 | 8.5191e-05 | 0
2013-12-09 09:05 | WYK24 | SHORT RURAL |  | 223 | 340 | 75820 | 0.65978 | 0.0019405 | 0
2013-12-09 09:08 | WYK12 | SHORT RURAL |  | 69 | 352 | 24288 | 0.21135 | 0.00060044 | 0
2013-12-09 09:20 | WN3 | LONG RURAL |  | 7 | 270 | 1890 | 0.0073187 | 2.7106e-05 | 0
2013-12-09 09:40 | WN3 | LONG RURAL |  | 3 | 125 | 375 | 0.0014521 | 1.1617e-05 | 0
2013-12-08 11:35 | LGA23 | LONG RURAL |  | 15 | 120 | 1800 | 0.0069702 | 5.8085e-05 | 0
2013-12-09 08:40 | LGA12 | SHORT RURAL |  | 2 | 90 | 180 | 0.0015664 | 1.7404e-05 | 0
2013-12-09 08:32 | LGA12 | SHORT RURAL |  | 2 | 140 | 280 | 0.0024366 | 1.7404e-05 | 0
2013-12-09 10:30 | LGA12 | SHORT RURAL |  | 1 | 165 | 165 | 0.0014358 | 8.702e-06 | 0
2013-12-09 10:00 | SMR1 | SHORT RURAL |  | 27 | 280 | 7560 | 0.065787 | 0.00023495 | 0
2013-12-09 10:00 | SMR8 | LONG RURAL |  | 4 | 95 | 380 | 0.0014715 | 1.5489e-05 | 0
2013-12-05 10:26 | WYK11 | SHORT RURAL |  | 394 | 353 | 139082 | 1.2103 | 0.0034286 | 0
2013-12-09 10:06 | ALA01 | LONG RURAL |  | 44 | 99 | 4356 | 0.016868 | 0.00017038 | 0
2013-11-30 08:40 | KMS1 | SHORT RURAL |  | 4 | 170 | 680 | 0.0059173 | 3.4808e-05 | 0
2013-12-01 08:55 | SMR3 | LONG RURAL |  | 375 | 715 | 268125 | 1.0383 | 0.0014521 | 0
2013-12-05 09:20 | SFS1 | SHORT RURAL |  | 25 | 95 | 2375 | 0.020667 | 0.00021755 | 0
2013-12-05 08:30 | BGE22 | SHORT RURAL |  | 100 | 275 | 27500 | 0.2393 | 0.0008702 | 0
2013-12-05 19:30 | HPK24 | URBAN |  | 3 | 150 | 450 | 0.0015676 | 1.045e-05 | 0
2013-12-05 13:15 | SFS1 | SHORT RURAL |  | 81 | 75 | 6075 | 0.052864 | 0.00070486 | 0
2013-12-06 08:45 | BGE22 | SHORT RURAL |  | 52 | 265 | 13780 | 0.11991 | 0.0004525 | 0
2013-12-09 10:20 | WGI22 | LONG RURAL |  | 10 | 350 | 3500 | 0.013553 | 3.8723e-05 | 0
2013-12-06 09:30 | BGE24 | SHORT RURAL |  | 17 | 80 | 1360 | 0.011835 | 0.00014793 | 0
2013-12-06 11:20 | BGE24 | SHORT RURAL |  | 4 | 70 | 280 | 0.0024366 | 3.4808e-05 | 0
2013-12-04 09:15 | SMR3 | LONG RURAL |  | 3 | 156 | 468 | 0.0018122 | 1.1617e-05 | 0
2013-12-07 09:00 | RWN24 | SHORT RURAL |  | 73 | 446 | 32558 | 0.28332 | 0.00063524 | 0
2013-12-06 09:15 | BGE12 | SHORT RURAL |  | 425 | 350 | 148750 | 1.2944 | 0.0036983 | 0
2013-12-04 08:05 | EPG31 | URBAN |  | 125 | 340 | 42500 | 0.14805 | 0.00043544 | 0
2013-11-20 13:30 | ALA01 | LONG RURAL |  | 28 | 12.6786 | 355 | 0.0013747 | 0.00010842 | 0
2013-11-21 07:45 | ALA01 | LONG RURAL |  | 5 | 13.4 | 67 | 0.00025945 | 1.9362e-05 | 0
2013-11-20 09:00 | ALA01 | LONG RURAL |  | 10 | 12.4 | 124 | 0.00048017 | 3.8723e-05 | 0
2013-11-21 08:30 | ALA01 | LONG RURAL |  | 18 | 18.6111 | 335 | 0.0012972 | 6.9702e-05 | 0
2013-12-09 12:10 | LDL23 | LONG RURAL |  | 12 | 70 | 840 | 0.0032527 | 4.6468e-05 | 0
2013-12-10 09:18 | WN6 | LONG RURAL |  | 40 | 402 | 16080 | 0.062267 | 0.00015489 | 0
2013-12-10 10:00 | WGL23 | SHORT RURAL |  | 4 | 35 | 140 | 0.0012183 | 3.4808e-05 | 0
2013-12-12 09:30 | TGN41 | LONG RURAL |  | 6 | 296 | 1776 | 0.0068772 | 2.3234e-05 | 0
2013-12-11 09:36 | MFA34 | SHORT RURAL |  | 58 | 304 | 17632 | 0.15343 | 0.00050471 | 0
2013-12-12 09:15 | MOE32 | SHORT RURAL |  | 3 | 200 | 600 | 0.0052212 | 2.6106e-05 | 0
2013-12-10 09:05 | WYK23 | SHORT RURAL |  | 1 | 435 | 435 | 0.0037854 | 8.702e-06 | 0
2013-12-10 08:00 | LDL23 | LONG RURAL |  | 148 | 465 | 68820 | 0.26649 | 0.0005731 | 0
2013-12-10 08:30 | WYK24 | SHORT RURAL |  | 167 | 340 | 56780 | 0.4941 | 0.0014532 | 0
2013-12-10 10:45 | LDL13 | SHORT RURAL |  | 1 | 83 | 83 | 0.00072226 | 8.702e-06 | 0
2013-12-10 09:02 | WYK12 | SHORT RURAL |  | 3 | 318 | 954 | 0.0083017 | 2.6106e-05 | 0
2013-12-10 09:00 | BGE12 | SHORT RURAL |  | 139 | 395 | 54905 | 0.47778 | 0.0012096 | 0
2013-12-11 08:55 | OFR23 | LONG RURAL |  | 29 | 355 | 10295 | 0.039865 | 0.0001123 | 0
2013-12-11 08:55 | WYK24 | SHORT RURAL |  | 13 | 360 | 4680 | 0.040725 | 0.00011313 | 0
2013-12-11 09:15 | WYK12 | SHORT RURAL |  | 5 | 200 | 1000 | 0.008702 | 4.351e-05 | 0
2013-12-11 10:02 | WYK12 | SHORT RURAL |  | 3 | 124 | 372 | 0.0032371 | 2.6106e-05 | 0
2013-12-09 11:50 | WN3 | LONG RURAL |  | 2 | 130 | 260 | 0.0010068 | 7.7446e-06 | 0
2013-12-10 09:00 | TGN31 | LONG RURAL |  | 82 | 241 | 19762 | 0.076525 | 0.00031753 | 0
2013-12-12 08:43 | MOE32 | SHORT RURAL |  | 3 | 287 | 861 | 0.0074924 | 2.6106e-05 | 0
2013-12-12 09:57 | TGN31 | LONG RURAL |  | 9 | 119 | 1071 | 0.0041472 | 3.4851e-05 | 0
2013-12-09 11:35 | LGA12 | SHORT RURAL |  | 3 | 110 | 330 | 0.0028717 | 2.6106e-05 | 0
2013-12-10 09:10 | LGA12 | SHORT RURAL |  | 1 | 125 | 125 | 0.0010877 | 8.702e-06 | 0
2013-12-10 09:10 | LGA12 | SHORT RURAL |  | 14 | 280 | 3920 | 0.034112 | 0.00012183 | 0
2013-12-10 09:25 | WGL13 | SHORT RURAL |  | 6 | 275 | 1650 | 0.014358 | 5.2212e-05 | 0
2013-12-11 08:45 | LDL24 | URBAN |  | 51 | 340 | 17340 | 0.060404 | 0.00017766 | 0
2013-12-12 07:35 | WYK23 | SHORT RURAL |  | 650 | 760 | 494000 | 4.2988 | 0.0056563 | 0
2013-12-12 09:23 | WYK11 | SHORT RURAL |  | 105 | 423 | 44415 | 0.3865 | 0.00091371 | 0
2013-12-12 09:02 | WYK12 | SHORT RURAL |  | 7 | 366 | 2562 | 0.022294 | 6.0914e-05 | 0
2013-12-05 09:50 | KLK2 | SHORT RURAL |  | 3 | 45 | 135 | 0.0011748 | 2.6106e-05 | 0
2013-12-10 09:50 | BRT22 | SHORT RURAL |  | 3 | 185 | 555 | 0.0048296 | 2.6106e-05 | 0
2013-12-10 11:20 | WOTS13 | LONG RURAL |  | 2 | 65 | 130 | 0.0005034 | 7.7446e-06 | 0
2013-12-11 09:30 | WOTS13 | LONG RURAL |  | 4 | 165 | 660 | 0.0025557 | 1.5489e-05 | 0
2013-12-10 11:29 | DRN14 | SHORT RURAL |  | 49 | 231 | 11319 | 0.098498 | 0.0004264 | 0
2013-12-10 09:02 | WOTS13 | LONG RURAL |  | 143 | 353 | 50479 | 0.19547 | 0.00055374 | 0
2013-12-10 10:45 | BRT21 | SHORT RURAL |  | 27 | 180 | 4860 | 0.042292 | 0.00023495 | 0
2013-12-10 14:00 | BRT22 | SHORT RURAL |  | 3 | 130 | 390 | 0.0033938 | 2.6106e-05 | 0
2013-12-09 12:50 | SMR8 | LONG RURAL |  | 1 | 130 | 130 | 0.0005034 | 3.8723e-06 | 0
2013-12-09 12:20 | SMR8 | LONG RURAL |  | 3 | 70 | 210 | 0.00081319 | 1.1617e-05 | 0
2013-12-10 09:10 | WGL23 | SHORT RURAL |  | 10 | 195 | 1950 | 0.016969 | 8.702e-05 | 0
2013-12-12 09:20 | WGI14 | SHORT RURAL |  | 87 | 155 | 13485 | 0.11735 | 0.00075707 | 0
2013-12-11 09:30 | WOTS13 | LONG RURAL |  | 15 | 360 | 5400 | 0.02091 | 5.8085e-05 | 0
2013-12-10 09:10 | WN3 | LONG RURAL |  | 57 | 172 | 9804 | 0.037964 | 0.00022072 | 0
2013-12-12 06:35 | WGI24 | URBAN |  | 1 | 240 | 240 | 0.00083604 | 3.4835e-06 | 0
2013-12-10 09:35 | LLG12 | SHORT RURAL |  | 4 | 215 | 860 | 0.0074837 | 3.4808e-05 | 0
2013-12-11 09:10 | BRT21 | SHORT RURAL |  | 186 | 355 | 66030 | 0.57459 | 0.0016186 | 0
2013-12-10 10:05 | LGA13 | LONG RURAL |  | 39 | 230 | 8970 | 0.034735 | 0.00015102 | 0
2013-12-10 09:00 | BN6 | LONG RURAL |  | 14 | 330 | 4620 | 0.01789 | 5.4212e-05 | 0
2013-12-10 09:48 | LGA11 | LONG RURAL |  | 2 | 137 | 274 | 0.001061 | 7.7446e-06 | 0
2013-12-11 09:15 | CRE31 | URBAN |  | 268 | 518 | 138824 | 0.48359 | 0.00093357 | 0
2013-12-11 12:45 | LLG13 | SHORT RURAL |  | 2 | 32 | 64 | 0.00055693 | 1.7404e-05 | 0
2013-12-11 11:00 | LLG13 | SHORT RURAL |  | 2 | 92 | 184 | 0.0016012 | 1.7404e-05 | 0
2013-12-12 09:20 | WGI22 | LONG RURAL |  | 13 | 170 | 2210 | 0.0085578 | 5.034e-05 | 0
2013-12-10 14:05 | LLG12 | SHORT RURAL |  | 2 | 40 | 80 | 0.00069616 | 1.7404e-05 | 0
2013-12-11 09:02 | LGA12 | SHORT RURAL |  | 27 | 243 | 6561 | 0.057094 | 0.00023495 | 0
2013-12-11 09:00 | LGA23 | LONG RURAL |  | 267 | 340.5243 | 90920 | 0.35207 | 0.0010339 | 0
2013-12-05 08:30 | BDL8 | LONG RURAL |  | 1 | 34 | 34 | 0.00013166 | 3.8723e-06 | 0
2013-12-04 10:17 | BDL8 | LONG RURAL |  | 3 | 88 | 264 | 0.0010223 | 1.1617e-05 | 0
2013-12-04 14:30 | NLA32 | SHORT RURAL |  | 2 | 70 | 140 | 0.0012183 | 1.7404e-05 | 0
2013-12-05 09:20 | NLA32 | SHORT RURAL |  | 4 | 55 | 220 | 0.0019144 | 3.4808e-05 | 0
2013-12-05 11:00 | NLA32 | SHORT RURAL |  | 1 | 210 | 210 | 0.0018274 | 8.702e-06 | 0
2013-12-05 08:30 | BDL8 | LONG RURAL |  | 3 | 40 | 120 | 0.00046468 | 1.1617e-05 | 0
2013-12-05 08:30 | BDL8 | LONG RURAL |  | 1 | 20 | 20 | 7.7446e-05 | 3.8723e-06 | 0
2013-12-05 12:30 | BDL8 | LONG RURAL |  | 1 | 30 | 30 | 0.00011617 | 3.8723e-06 | 0
2013-12-05 09:40 | NLA32 | SHORT RURAL |  | 2 | 340 | 680 | 0.0059173 | 1.7404e-05 | 0
2013-12-05 12:35 | BDL8 | LONG RURAL |  | 2 | 20 | 40 | 0.00015489 | 7.7446e-06 | 0
2013-11-30 09:40 | RWN22 | URBAN |  | 2865 | 300 | 859500 | 2.9941 | 0.0099802 | 0
2013-12-04 12:10 | NLA32 | SHORT RURAL |  | 17 | 125 | 2125 | 0.018492 | 0.00014793 | 0
2013-12-04 09:10 | NLA32 | SHORT RURAL |  | 83 | 145 | 12035 | 0.10473 | 0.00072226 | 0
2013-12-04 14:00 | MFA21 | LONG RURAL |  | 5 | 30 | 150 | 0.00058085 | 1.9362e-05 | 0
2013-12-05 10:10 | NLA32 | SHORT RURAL |  | 9 | 195 | 1755 | 0.015272 | 7.8318e-05 | 0
2013-12-06 08:25 | DRN23 | LONG RURAL |  | 135 | 465 | 62775 | 0.24308 | 0.00052276 | 0
2013-12-04 09:15 | MFA23 | SHORT RURAL |  | 18 | 180 | 3240 | 0.028194 | 0.00015664 | 0
2013-12-09 10:30 | ELM33 | SHORT RURAL |  | 10 | 135 | 1350 | 0.011748 | 8.702e-05 | 0
2013-12-09 12:20 | DRN13 | SHORT RURAL |  | 9 | 5 | 45 | 0.00039159 | 7.8318e-05 | 0
2013-12-10 09:10 | ELM33 | SHORT RURAL |  | 3 | 205 | 615 | 0.0053517 | 2.6106e-05 | 0
2013-12-10 09:10 | ELM33 | SHORT RURAL |  | 54 | 282 | 15228 | 0.13251 | 0.00046991 | 0
2013-12-10 09:55 | ELM33 | SHORT RURAL |  | 2 | 200 | 400 | 0.0034808 | 1.7404e-05 | 0
2013-12-12 09:11 | TRC01 | SHORT RURAL |  | 19 | 429 | 8151 | 0.07093 | 0.00016534 | 0
2013-12-12 08:30 | LDL22 | SHORT RURAL |  | 185 | 445 | 82325 | 0.71639 | 0.0016099 | 0
2013-12-12 09:00 | LGA12 | SHORT RURAL |  | 2 | 40 | 80 | 0.00069616 | 1.7404e-05 | 0
2013-12-12 09:56 | LDL22 | SHORT RURAL |  | 69 | 349 | 24081 | 0.20955 | 0.00060044 | 0
2013-12-06 13:10 | BN6 | LONG RURAL |  | 9 | 115 | 1035 | 0.0040078 | 3.4851e-05 | 0
2013-12-05 09:30 | KLK1 | SHORT RURAL |  | 2 | 340 | 680 | 0.0059173 | 1.7404e-05 | 0
2013-12-07 08:40 | LDL22 | SHORT RURAL |  | 9 | 2800 | 25200 | 0.21929 | 7.8318e-05 | 0
2013-12-07 08:15 | CYN13 | URBAN |  | 1 | 345 | 345 | 0.0012018 | 3.4835e-06 | 0
2013-12-08 08:30 | WGL24 | LONG RURAL |  | 20 | 313 | 6260 | 0.024241 | 7.7446e-05 | 0
2013-12-12 09:20 | WGI23 | SHORT RURAL |  | 23 | 320 | 7360 | 0.064047 | 0.00020015 | 0
2013-12-12 08:30 | MSD1 | LONG RURAL |  | 714 | 500 | 357000 | 1.3824 | 0.0027648 | 0
2013-12-05 10:18 | BDL3 | SHORT RURAL |  | 88 | 132 | 11616 | 0.10108 | 0.00076577 | 0
2013-12-12 09:00 | WGL23 | SHORT RURAL |  | 129 | 95 | 12255 | 0.10664 | 0.0011226 | 0
2013-12-11 13:00 | WGI23 | SHORT RURAL |  | 23 | 120 | 2760 | 0.024017 | 0.00020015 | 0
2013-12-06 10:55 | MFA34 | SHORT RURAL |  | 3 | 45 | 135 | 0.0011748 | 2.6106e-05 | 0
2013-12-06 08:40 | NLA32 | SHORT RURAL |  | 3 | 10 | 30 | 0.00026106 | 2.6106e-05 | 0
2013-12-06 08:17 | NLA32 | SHORT RURAL |  | 1 | 49 | 49 | 0.0004264 | 8.702e-06 | 0
2013-12-06 08:10 | NLA32 | SHORT RURAL |  | 1 | 10 | 10 | 8.702e-05 | 8.702e-06 | 0
2013-12-06 09:15 | NLA32 | SHORT RURAL |  | 1 | 1545 | 1545 | 0.013445 | 8.702e-06 | 0
2013-12-06 08:30 | BDL8 | LONG RURAL |  | 1 | 55 | 55 | 0.00021298 | 3.8723e-06 | 0
2013-12-05 13:19 | BDL8 | LONG RURAL |  | 2 | 48 | 96 | 0.00037174 | 7.7446e-06 | 0
2013-12-10 08:50 | CYN23 | URBAN |  | 1 | 150 | 150 | 0.00052252 | 3.4835e-06 | 0
2013-12-11 08:35 | BN6 | LONG RURAL |  | 2 | 47 | 94 | 0.000364 | 7.7446e-06 | 0
2013-12-07 08:30 | UWY1 | SHORT RURAL |  | 9 | 327 | 2943 | 0.02561 | 7.8318e-05 | 0
2013-12-10 12:03 | LGA12 | SHORT RURAL |  | 19 | 139 | 2641 | 0.022982 | 0.00016534 | 0
2013-12-08 08:30 | FGY32 | URBAN |  | 37 | 185 | 6845 | 0.023844 | 0.00012889 | 0
2013-12-08 08:20 | FGY34 | URBAN |  | 95 | 375 | 35625 | 0.1241 | 0.00033093 | 0
2013-12-12 09:00 | FTR12 | LONG RURAL |  | 43 | 275 | 11825 | 0.04579 | 0.00016651 | 0
2013-12-08 10:30 | BGE12 | SHORT RURAL |  | 27 | 228 | 6156 | 0.053569 | 0.00023495 | 0
2013-12-09 08:40 | FGY21 | SHORT RURAL |  | 14 | 375 | 5250 | 0.045685 | 0.00012183 | 0
2013-12-09 10:45 | BGE22 | SHORT RURAL |  | 87 | 205 | 17835 | 0.1552 | 0.00075707 | 0
2013-12-09 09:02 | LYD14 | SHORT RURAL |  | 2 | 527 | 1054 | 0.0091719 | 1.7404e-05 | 0
2013-12-09 08:55 | LYD14 | SHORT RURAL |  | 413 | 13 | 5369 | 0.046721 | 0.0035939 | 0
2013-12-09 17:45 | LYD14 | SHORT RURAL |  | 413 | 10 | 4130 | 0.035939 | 0.0035939 | 0
2013-12-09 10:14 | ELM33 | SHORT RURAL |  | 90 | 108 | 9720 | 0.084583 | 0.00078318 | 0
2013-12-13 09:10 | TGN23 | SHORT RURAL |  | 35 | 326 | 11410 | 0.099289 | 0.00030457 | 0
2013-12-13 09:36 | RWN26 | SHORT RURAL |  | 1 | 253 | 253 | 0.0022016 | 8.702e-06 | 0
2013-12-13 08:50 | RWN26 | SHORT RURAL |  | 1 | 340 | 340 | 0.0029587 | 8.702e-06 | 0
2013-12-13 08:40 | RWN26 | SHORT RURAL |  | 40 | 140 | 5600 | 0.048731 | 0.00034808 | 0
2013-12-13 09:00 | WGL24 | LONG RURAL |  | 190 | 278 | 52820 | 0.20454 | 0.00073574 | 0
2013-12-12 12:45 | WGI14 | SHORT RURAL |  | 81 | 150 | 12150 | 0.10573 | 0.00070486 | 0
2013-11-30 12:26 | SMR3 | LONG RURAL |  | 3 | 109 | 327 | 0.0012662 | 1.1617e-05 | 0
2013-12-13 09:00 | BRT22 | SHORT RURAL |  | 86 | 258 | 22188 | 0.19308 | 0.00074837 | 0
2013-12-13 09:10 | MYT1 | SHORT RURAL |  | 6 | 120 | 720 | 0.0062654 | 5.2212e-05 | 0
2013-12-13 09:08 | WGI14 | SHORT RURAL |  | 2491 | 362 | 901742 | 7.8469 | 0.021677 | 0
2013-12-13 09:05 | LGA12 | SHORT RURAL |  | 3 | 125 | 375 | 0.0032632 | 2.6106e-05 | 0
2013-12-09 12:45 | DRN13 | SHORT RURAL |  | 10 | 105 | 1050 | 0.0091371 | 8.702e-05 | 0
2013-12-13 09:30 | WOTS13 | LONG RURAL |  | 30 | 279 | 8370 | 0.032411 | 0.00011617 | 0
2013-12-05 09:30 | MFA23 | SHORT RURAL |  | 32 | 440 | 14080 | 0.12252 | 0.00027846 | 0
2013-12-06 10:17 | BDL8 | LONG RURAL |  | 2 | 35 | 70 | 0.00027106 | 7.7446e-06 | 0
2013-12-10 09:30 | SMR8 | LONG RURAL |  | 2 | 90 | 180 | 0.00069702 | 7.7446e-06 | 0
2013-12-06 11:30 | BDL8 | LONG RURAL |  | 6 | 50 | 300 | 0.0011617 | 2.3234e-05 | 0
2013-12-10 11:30 | SMR8 | LONG RURAL |  | 9 | 105 | 945 | 0.0036593 | 3.4851e-05 | 0
2013-12-10 14:15 | SMR8 | LONG RURAL |  | 1 | 75 | 75 | 0.00029042 | 3.8723e-06 | 0
2013-12-11 09:30 | WN3 | LONG RURAL |  | 11 | 230 | 2530 | 0.009797 | 4.2595e-05 | 0
2013-12-06 12:55 | MFA34 | SHORT RURAL |  | 1 | 50 | 50 | 0.0004351 | 8.702e-06 | 0
2013-11-29 09:05 | SMR3 | LONG RURAL |  | 15 | 105 | 1575 | 0.0060989 | 5.8085e-05 | 0
2013-11-29 12:10 | SMR3 | LONG RURAL |  | 1 | 130 | 130 | 0.0005034 | 3.8723e-06 | 0
2013-12-10 13:50 | SMR8 | LONG RURAL |  | 2 | 95 | 190 | 0.00073574 | 7.7446e-06 | 0
2013-12-07 10:20 | NLA32 | SHORT RURAL |  | 1 | 72 | 72 | 0.00062654 | 8.702e-06 | 0
2013-12-07 12:25 | NLA32 | SHORT RURAL |  | 6 | 110 | 660 | 0.0057433 | 5.2212e-05 | 0
2013-12-11 09:35 | SMR8 | LONG RURAL |  | 36 | 300 | 10800 | 0.041821 | 0.0001394 | 0
2013-12-11 09:17 | SMR8 | LONG RURAL |  | 21 | 330 | 6930 | 0.026835 | 8.1319e-05 | 0
2013-12-11 09:00 | LGA13 | LONG RURAL |  | 115 | 484 | 55660 | 0.21553 | 0.00044532 | 0
2013-12-10 09:00 | CYN14 | URBAN |  | 183 | 370 | 67710 | 0.23587 | 0.00063748 | 0
2013-12-12 10:10 | FTR12 | LONG RURAL |  | 1 | 240 | 240 | 0.00092936 | 3.8723e-06 | 0
2013-12-12 09:00 | LGA14 | LONG RURAL |  | 54 | 104 | 5616 | 0.021747 | 0.0002091 | 0
2013-12-09 09:10 | BGE12 | SHORT RURAL |  | 51 | 351 | 17901 | 0.15577 | 0.0004438 | 0
2013-12-09 09:35 | MDG1 | SHORT RURAL |  | 71 | 195 | 13845 | 0.12048 | 0.00061784 | 0
2013-12-10 09:14 | BGE11 | SHORT RURAL |  | 251 | 386 | 96886 | 0.8431 | 0.0021842 | 0
2013-12-12 09:22 | CYN33 | SHORT RURAL |  | 89 | 318 | 28302 | 0.24628 | 0.00077448 | 0
2013-12-01 09:30 | LDL13 | SHORT RURAL |  | 15 | 305 | 4575 | 0.039812 | 0.00013053 | 0
2013-12-01 07:25 | LDL13 | SHORT RURAL |  | 2 | 145 | 290 | 0.0025236 | 1.7404e-05 | 0
2013-11-25 08:15 | ALA01 | LONG RURAL |  | 20 | 23.75 | 475 | 0.0018393 | 7.7446e-05 | 0
2013-11-25 10:00 | ALA01 | LONG RURAL |  | 9 | 43.3333 | 390 | 0.0015102 | 3.4851e-05 | 0
2013-11-26 09:00 | ALA01 | LONG RURAL |  | 14 | 10.7143 | 150 | 0.00058085 | 5.4212e-05 | 0
2013-11-26 10:50 | ALA01 | LONG RURAL |  | 6 | 39.8333 | 239 | 0.00092548 | 2.3234e-05 | 0
2013-11-26 09:10 | ALA01 | LONG RURAL |  | 7 | 27.8571 | 195 | 0.0007551 | 2.7106e-05 | 0
2013-12-06 09:15 | MFA23 | SHORT RURAL |  | 1 | 305 | 305 | 0.0026541 | 8.702e-06 | 0
2013-12-12 09:15 | KLK1 | SHORT RURAL |  | 6 | 295 | 1770 | 0.015402 | 5.2212e-05 | 0
2013-12-07 09:10 | SLE31 | LONG RURAL |  | 4 | 235 | 940 | 0.00364 | 1.5489e-05 | 0
2013-12-12 09:00 | KMS1 | SHORT RURAL |  | 9 | 315 | 2835 | 0.02467 | 7.8318e-05 | 0
2013-12-11 09:28 | WGL21 | LONG RURAL |  | 210 | 277 | 58170 | 0.22525 | 0.00081319 | 0
2013-12-12 11:30 | CYN33 | SHORT RURAL |  | 154 | 195 | 30030 | 0.26132 | 0.0013401 | 0
2013-12-12 08:40 | SLE31 | LONG RURAL |  | 40 | 402 | 16080 | 0.062267 | 0.00015489 | 0
2013-12-08 08:45 | NLA32 | SHORT RURAL |  | 2 | 73 | 146 | 0.0012705 | 1.7404e-05 | 0
2013-12-08 10:41 | NLA32 | SHORT RURAL |  | 1 | 59 | 59 | 0.00051342 | 8.702e-06 | 0
2013-12-09 08:45 | MFA22 | LONG RURAL |  | 9 | 360 | 3240 | 0.012546 | 3.4851e-05 | 0
2013-12-08 11:58 | NLA32 | SHORT RURAL |  | 2 | 37 | 74 | 0.00064395 | 1.7404e-05 | 0
2013-12-10 09:10 | BDL6 | SHORT RURAL |  | 4 | 310 | 1240 | 0.01079 | 3.4808e-05 | 0
2013-12-09 13:05 | NLA31 | LONG RURAL |  | 9 | 199 | 1791 | 0.0069353 | 3.4851e-05 | 0
2013-12-12 09:10 | WO31 | URBAN |  | 22 | 10 | 220 | 0.00076637 | 7.6637e-05 | 0
2013-12-13 09:00 | LGA21 | SHORT RURAL |  | 354 | 322 | 113988 | 0.99192 | 0.0030805 | 0
2013-12-06 13:12 | MYT1 | SHORT RURAL |  | 1 | 49 | 49 | 0.0004264 | 8.702e-06 | 0
2013-12-09 10:30 | NLA32 | SHORT RURAL |  | 1 | 50 | 50 | 0.0004351 | 8.702e-06 | 0
2013-12-09 09:30 | NLA32 | SHORT RURAL |  | 1 | 35 | 35 | 0.00030457 | 8.702e-06 | 0
2013-12-09 13:00 | NLA32 | SHORT RURAL |  | 52 | 20 | 1040 | 0.00905 | 0.0004525 | 0
2013-12-13 08:35 | CYN33 | SHORT RURAL |  | 50 | 195 | 9750 | 0.084844 | 0.0004351 | 0
2013-12-14 09:00 | WGI23 | SHORT RURAL |  | 10 | 330 | 3300 | 0.028717 | 8.702e-05 | 0
2013-12-12 09:02 | BWA22 | LONG RURAL |  | 5 | 101 | 505 | 0.0019555 | 1.9362e-05 | 0
2013-12-10 10:10 | NLA31 | LONG RURAL |  | 207 | 380 | 78660 | 0.3046 | 0.00080157 | 0
2013-12-14 09:25 | WGI22 | LONG RURAL |  | 109 | 181 | 19729 | 0.076397 | 0.00042208 | 0
2013-12-12 11:20 | BWA23 | SHORT RURAL |  | 2 | 23 | 46 | 0.00040029 | 1.7404e-05 | 0
2013-12-09 09:21 | MSD1 | LONG RURAL |  | 46 | 24 | 1104 | 0.004275 | 0.00017813 | 0
2013-12-13 10:20 | LGA12 | SHORT RURAL |  | 2 | 35 | 70 | 0.00060914 | 1.7404e-05 | 0
2013-12-13 12:45 | LGA12 | SHORT RURAL |  | 3 | 75 | 225 | 0.0019579 | 2.6106e-05 | 0
2013-12-12 09:00 | CLN23 | SHORT RURAL |  | 22 | 210 | 4620 | 0.040203 | 0.00019144 | 0
2013-12-13 09:50 | LLG12 | SHORT RURAL |  | 1 | 35 | 35 | 0.00030457 | 8.702e-06 | 0
2013-12-13 10:10 | FTR12 | LONG RURAL |  | 12 | 240 | 2880 | 0.011152 | 4.6468e-05 | 0
2013-12-13 10:00 | FTR12 | LONG RURAL |  | 6 | 240 | 1440 | 0.0055761 | 2.3234e-05 | 0
2013-12-15 09:00 | MOE32 | SHORT RURAL |  | 51 | 350 | 17850 | 0.15533 | 0.0004438 | 0
2013-12-15 09:04 | WYK12 | SHORT RURAL |  | 12 | 259 | 3108 | 0.027046 | 0.00010442 | 0
2013-12-15 08:40 | WYK24 | SHORT RURAL |  | 4 | 170 | 680 | 0.0059173 | 3.4808e-05 | 0
2013-12-15 14:30 | WYK11 | SHORT RURAL |  | 1 | 30 | 30 | 0.00026106 | 8.702e-06 | 0
2013-12-15 12:30 | WYK24 | SHORT RURAL |  | 1 | 75 | 75 | 0.00065265 | 8.702e-06 | 0
2013-12-15 09:14 | WGL24 | LONG RURAL |  | 30 | 390 | 11700 | 0.045306 | 0.00011617 | 0
2013-12-10 09:01 | BDL5 | LONG RURAL |  | 121 | 414 | 50094 | 0.19398 | 0.00046855 | 0
2013-12-13 09:40 | SMR8 | LONG RURAL |  | 1 | 75 | 75 | 0.00029042 | 3.8723e-06 | 0
2013-12-13 09:50 | SMR8 | LONG RURAL |  | 1 | 85 | 85 | 0.00032915 | 3.8723e-06 | 0
2013-12-13 11:12 | SMR8 | LONG RURAL |  | 1 | 23 | 23 | 8.9063e-05 | 3.8723e-06 | 0
2013-12-10 08:40 | OFR23 | LONG RURAL |  | 1 | 100 | 100 | 0.00038723 | 3.8723e-06 | 0
2013-12-13 12:35 | SMR8 | LONG RURAL |  | 2 | 25 | 50 | 0.00019362 | 7.7446e-06 | 0
2013-12-13 11:50 | SMR8 | LONG RURAL |  | 1 | 25 | 25 | 9.6808e-05 | 3.8723e-06 | 0
2013-12-11 09:15 | NLA31 | LONG RURAL |  | 5 | 423 | 2115 | 0.0081899 | 1.9362e-05 | 0
2013-12-12 09:10 | WGL11 | SHORT RURAL |  | 16 | 155 | 2480 | 0.021581 | 0.00013923 | 0
2013-12-11 09:50 | NLA31 | LONG RURAL |  | 1 | 260 | 260 | 0.0010068 | 3.8723e-06 | 0
2013-12-14 10:22 | MWTS32 | SHORT RURAL |  | 18 | 205 | 3690 | 0.03211 | 0.00015664 | 0
2013-12-12 09:05 | BDL5 | LONG RURAL |  | 3 | 85 | 255 | 0.00098744 | 1.1617e-05 | 0
2013-12-05 09:00 | FGY13 | SHORT RURAL |  | 53 | 295 | 15635 | 0.13606 | 0.0004612 | 0
2013-12-10 09:40 | NLA32 | SHORT RURAL |  | 296 | 250 | 74000 | 0.64395 | 0.0025758 | 0
2013-12-11 09:00 | BDL1 | LONG RURAL |  | 21 | 350 | 7350 | 0.028462 | 8.1319e-05 | 0
2013-12-12 08:57 | BDL5 | LONG RURAL |  | 13 | 233 | 3029 | 0.011729 | 5.034e-05 | 0
2013-12-12 08:43 | SLE31 | LONG RURAL |  | 2 | 307 | 614 | 0.0023776 | 7.7446e-06 | 0
2013-12-12 12:40 | ELM33 | SHORT RURAL |  | 2 | 85 | 170 | 0.0014793 | 1.7404e-05 | 0
2013-12-12 13:10 | BDL5 | LONG RURAL |  | 2 | 25 | 50 | 0.00019362 | 7.7446e-06 | 0
2013-12-13 09:00 | WGL21 | LONG RURAL |  | 4 | 25 | 100 | 0.00038723 | 1.5489e-05 | 0
2013-12-10 11:15 | NLA32 | SHORT RURAL |  | 278 | 313 | 87014 | 0.75719 | 0.0024191 | 0
2013-12-12 09:40 | ELM33 | SHORT RURAL |  | 3 | 200 | 600 | 0.0052212 | 2.6106e-05 | 0
2013-12-13 11:25 | BDL5 | LONG RURAL |  | 1 | 30 | 30 | 0.00011617 | 3.8723e-06 | 0
2013-12-12 11:05 | CNR2 | SHORT RURAL |  | 58 | 10 | 580 | 0.0050471 | 0.00050471 | 0
2013-12-13 11:05 | BDL5 | LONG RURAL |  | 2 | 45 | 90 | 0.00034851 | 7.7446e-06 | 0
2013-12-13 09:35 | WGL21 | LONG RURAL |  | 4 | 25 | 100 | 0.00038723 | 1.5489e-05 | 0
2013-12-14 12:15 | WGI22 | LONG RURAL |  | 2 | 85 | 170 | 0.00065829 | 7.7446e-06 | 0
2013-12-13 10:50 | WYK11 | SHORT RURAL |  | 2 | 68 | 136 | 0.0011835 | 1.7404e-05 | 0
2013-12-11 09:00 | NLA34 | SHORT RURAL |  | 42 | 525 | 22050 | 0.19188 | 0.00036548 | 0
2013-12-14 14:00 | WGI22 | LONG RURAL |  | 3 | 90 | 270 | 0.0010455 | 1.1617e-05 | 0
2013-12-10 08:45 | HPK24 | URBAN |  | 220 | 185 | 40700 | 0.14178 | 0.00076637 | 0
2013-12-10 08:59 | BGE12 | SHORT RURAL |  | 145 | 449 | 65105 | 0.56654 | 0.0012618 | 0
2013-12-10 09:10 | BGE11 | SHORT RURAL |  | 37 | 110 | 4070 | 0.035417 | 0.00032197 | 0
2013-12-12 08:45 | CLN12 | SHORT RURAL |  | 85 | 430 | 36550 | 0.31806 | 0.00073967 | 0
2013-12-10 12:20 | BGE11 | SHORT RURAL |  | 32 | 90 | 2880 | 0.025062 | 0.00027846 | 0
2013-12-12 09:30 | CLN22 | SHORT RURAL |  | 1 | 165 | 165 | 0.0014358 | 8.702e-06 | 0
2013-12-14 09:00 | LGA13 | LONG RURAL |  | 102 | 394.0784 | 40196 | 0.15565 | 0.00039498 | 0
2013-12-12 09:01 | WGL12 | LONG RURAL |  | 335 | 112 | 37520 | 0.14529 | 0.0012972 | 0
2013-12-12 09:00 | LLG11 | SHORT RURAL |  | 21 | 123 | 2583 | 0.022477 | 0.00018274 | 0
2013-12-12 10:45 | WGL12 | LONG RURAL |  | 4 | 58 | 232 | 0.00089838 | 1.5489e-05 | 0
2013-12-12 11:45 | OFR22 | SHORT RURAL |  | 100 | 105 | 10500 | 0.091371 | 0.0008702 | 0
2013-12-15 09:10 | LLG12 | SHORT RURAL |  | 154 | 135 | 20790 | 0.18091 | 0.0013401 | 0
2013-12-13 09:00 | LLG11 | SHORT RURAL |  | 7 | 300 | 2100 | 0.018274 | 6.0914e-05 | 0
2013-12-13 09:00 | LLG11 | SHORT RURAL |  | 61 | 30 | 1830 | 0.015925 | 0.00053082 | 0
2013-12-11 09:50 | BGE12 | SHORT RURAL |  | 131 | 251 | 32881 | 0.28613 | 0.00114 | 0
2013-12-11 12:35 | BGE22 | SHORT RURAL |  | 20 | 100 | 2000 | 0.017404 | 0.00017404 | 0
2013-11-27 10:20 | ALA01 | LONG RURAL |  | 2 | 15 | 30 | 0.00011617 | 7.7446e-06 | 0
2013-11-27 08:40 | ALA01 | LONG RURAL |  | 30 | 32.3333 | 970 | 0.0037561 | 0.00011617 | 0
2013-11-27 12:30 | ALA01 | LONG RURAL |  | 16 | 17.8125 | 285 | 0.0011036 | 6.1957e-05 | 0
2013-12-16 09:45 | TGN31 | LONG RURAL |  | 163 | 297 | 48411 | 0.18746 | 0.00063119 | 0
2013-12-16 10:40 | WGL12 | LONG RURAL |  | 15 | 350 | 5250 | 0.02033 | 5.8085e-05 | 0
2013-12-16 11:00 | MOE22 | LONG RURAL |  | 3 | 91.6667 | 275 | 0.0010649 | 1.1617e-05 | 0
2013-12-16 09:50 | WN3 | LONG RURAL |  | 1 | 92 | 92 | 0.00035625 | 3.8723e-06 | 0
2013-12-16 09:00 | WN3 | LONG RURAL |  | 14 | 120 | 1680 | 0.0065055 | 5.4212e-05 | 0
2013-12-16 10:05 | LDL23 | LONG RURAL |  | 259 | 77 | 19943 | 0.077226 | 0.0010029 | 0
2013-12-16 10:05 | WOTS13 | LONG RURAL |  | 2 | 102 | 204 | 0.00078995 | 7.7446e-06 | 0
2013-12-16 08:48 | BN6 | LONG RURAL |  | 61 | 287 | 17507 | 0.067793 | 0.00023621 | 0
2013-12-16 09:30 | MYT8 | SHORT RURAL |  | 10 | 230 | 2300 | 0.020015 | 8.702e-05 | 0
2013-12-16 09:25 | FTR12 | LONG RURAL |  | 3 | 215 | 645 | 0.0024976 | 1.1617e-05 | 0
2013-12-16 09:00 | LGA12 | SHORT RURAL |  | 38 | 275 | 10450 | 0.090936 | 0.00033067 | 0
2013-12-16 09:05 | LGA23 | LONG RURAL |  | 149 | 272 | 40528 | 0.15694 | 0.00057697 | 0
2013-12-16 09:05 | WGL23 | SHORT RURAL |  | 1 | 220 | 220 | 0.0019144 | 8.702e-06 | 0
2013-12-16 09:03 | LGA13 | LONG RURAL |  | 19 | 202 | 3838 | 0.014862 | 7.3574e-05 | 0
2013-12-16 09:16 | LGA24 | SHORT RURAL |  | 242 | 346 | 83732 | 0.72863 | 0.0021059 | 0
2013-12-16 10:28 | LGA12 | SHORT RURAL |  | 198 | 383.9394 | 76020 | 0.66152 | 0.001723 | 0
2013-12-11 08:34 | HPK13 | URBAN |  | 121 | 346 | 41866 | 0.14584 | 0.0004215 | 0
2013-12-13 09:18 | LDL21 | SHORT RURAL |  | 73 | 93.4658 | 6823 | 0.059374 | 0.00063524 | 0
2013-12-12 09:30 | NLA32 | SHORT RURAL |  | 74 | 390 | 28860 | 0.25114 | 0.00064395 | 0
2013-12-16 09:50 | SMR5 | LONG RURAL |  | 12 | 362 | 4344 | 0.016821 | 4.6468e-05 | 0
2013-12-10 08:55 | SLE31 | LONG RURAL |  | 31 | 460 | 14260 | 0.055219 | 0.00012004 | 0
2013-12-12 13:10 | WGL23 | SHORT RURAL |  | 1 | 90 | 90 | 0.00078318 | 8.702e-06 | 0
2013-12-14 09:15 | WGI22 | LONG RURAL |  | 1 | 145 | 145 | 0.00056149 | 3.8723e-06 | 0
2013-12-13 08:52 | BDL5 | LONG RURAL |  | 3 | 118 | 354 | 0.0013708 | 1.1617e-05 | 0
2013-12-13 09:15 | BDL1 | LONG RURAL |  | 20 | 325 | 6500 | 0.02517 | 7.7446e-05 | 0
2013-12-13 08:55 | BDL1 | LONG RURAL |  | 105 | 215 | 22575 | 0.087417 | 0.00040659 | 0
2013-12-13 08:40 | SLE24 | URBAN |  | 17 | 310 | 5270 | 0.018358 | 5.9219e-05 | 0
2013-12-13 08:40 | SLE31 | LONG RURAL |  | 9 | 270 | 2430 | 0.0094097 | 3.4851e-05 | 0
2013-12-15 08:35 | SLE24 | URBAN |  | 21 | 145 | 3045 | 0.010607 | 7.3153e-05 | 0
2013-12-08 13:40 | WGL13 | SHORT RURAL |  | 2 | 130 | 260 | 0.0022625 | 1.7404e-05 | 0
2013-12-09 12:08 | MSD4 | LONG RURAL |  | 3 | 174 | 522 | 0.0020213 | 1.1617e-05 | 0
2013-12-15 08:40 | BDL1 | LONG RURAL |  | 1 | 155 | 155 | 0.00060021 | 3.8723e-06 | 0
2013-12-11 07:05 | KMS1 | SHORT RURAL |  | 19 | 40 | 760 | 0.0066135 | 0.00016534 | 0
2013-12-14 08:45 | TT12 | URBAN |  | 38 | 84 | 3192 | 0.011119 | 0.00013237 | 0
2013-12-15 11:55 | SLE24 | URBAN |  | 19 | 160 | 3040 | 0.01059 | 6.6186e-05 | 0
2013-12-15 08:31 | BDL1 | LONG RURAL |  | 98 | 421 | 41258 | 0.15976 | 0.00037949 | 0
2013-12-10 10:10 | CYN14 | URBAN |  | 292 | 290 | 84680 | 0.29498 | 0.0010172 | 0
2013-12-12 08:45 | FGY34 | URBAN |  | 70 | 425 | 29750 | 0.10363 | 0.00024384 | 0
2013-12-09 11:50 | TGN31 | LONG RURAL |  | 1 | 70 | 70 | 0.00027106 | 3.8723e-06 | 0
2013-12-12 08:30 | BGE11 | SHORT RURAL |  | 273 | 345 | 94185 | 0.8196 | 0.0023756 | 0
2013-12-12 13:00 | CLN22 | SHORT RURAL |  | 1 | 110 | 110 | 0.00095722 | 8.702e-06 | 0
2013-12-13 08:35 | CLN22 | SHORT RURAL |  | 52 | 316 | 16432 | 0.14299 | 0.0004525 | 0
2013-12-11 11:00 | KLO24 | SHORT RURAL |  | 45 | 390 | 17550 | 0.15272 | 0.00039159 | 0
2013-11-29 08:40 | ALA01 | LONG RURAL |  | 9 | 23.8889 | 215 | 0.00083255 | 3.4851e-05 | 0
2013-11-29 08:45 | ALA01 | LONG RURAL |  | 8 | 16.875 | 135 | 0.00052276 | 3.0979e-05 | 0
2013-12-11 08:50 | DRN23 | LONG RURAL |  | 733 | 353 | 258749 | 1.002 | 0.0028384 | 0
2013-12-12 09:20 | DRN23 | LONG RURAL |  | 128 | 358 | 45824 | 0.17744 | 0.00049566 | 0
2013-11-30 10:55 | ALA01 | LONG RURAL |  | 8 | 18.125 | 145 | 0.00056149 | 3.0979e-05 | 0
2013-11-30 08:15 | ALA01 | LONG RURAL |  | 6 | 10 | 60 | 0.00023234 | 2.3234e-05 | 0
2013-12-19 11:00 | WN3 | LONG RURAL |  | 4 | 40 | 160 | 0.00061957 | 1.5489e-05 | 0
2013-12-19 08:39 | WN3 | LONG RURAL |  | 1 | 55 | 55 | 0.00021298 | 3.8723e-06 | 0
2013-12-18 09:10 | MOE32 | SHORT RURAL |  | 24 | 215 | 5160 | 0.044902 | 0.00020885 | 0
2013-12-17 09:04 | SMR8 | LONG RURAL |  | 294 | 428 | 125832 | 0.48726 | 0.0011385 | 0
2013-12-17 09:13 | SMR8 | LONG RURAL |  | 1284 | 178 | 228552 | 0.88503 | 0.0049721 | 0
2013-12-16 08:30 | SLE31 | LONG RURAL |  | 11 | 210 | 2310 | 0.008945 | 4.2595e-05 | 0
2013-12-18 09:35 | SMR8 | LONG RURAL |  | 2 | 80 | 160 | 0.00061957 | 7.7446e-06 | 0
2013-12-15 09:00 | SMR3 | LONG RURAL |  | 23 | 370 | 8510 | 0.032953 | 8.9063e-05 | 0
2013-12-17 09:06 | BDL4 | SHORT RURAL |  | 99 | 24 | 2376 | 0.020676 | 0.0008615 | 0
2013-12-18 10:20 | PHI12 | SHORT RURAL |  | 12 | 157 | 1884 | 0.016395 | 0.00010442 | 0
2013-12-18 09:30 | LGA13 | LONG RURAL |  | 36 | 335 | 12060 | 0.0467 | 0.0001394 | 0
2013-12-17 15:00 | LDL24 | URBAN |  | 22 | 50 | 1100 | 0.0038318 | 7.6637e-05 | 0
2013-12-17 11:58 | FTR21 | LONG RURAL |  | 176 | 69 | 12144 | 0.047025 | 0.00068153 | 0
2013-12-13 08:52 | MDG1 | SHORT RURAL |  | 108 | 398 | 42984 | 0.37405 | 0.00093981 | 0
2013-12-17 08:15 | UWY1 | SHORT RURAL |  | 227 | 545 | 123715 | 1.0766 | 0.0019753 | 0
2013-12-16 09:00 | LYD14 | SHORT RURAL |  | 17 | 150 | 2550 | 0.02219 | 0.00014793 | 0
2013-12-17 09:55 | FGY12 | URBAN |  | 67 | 270 | 18090 | 0.063016 | 0.00023339 | 0
2013-12-19 09:05 | LGA13 | LONG RURAL |  | 9 | 150 | 1350 | 0.0052276 | 3.4851e-05 | 0
2013-12-18 09:00 | LGA13 | LONG RURAL |  | 27 | 357 | 9639 | 0.037325 | 0.00010455 | 0
2013-12-19 09:00 | LGA22 | SHORT RURAL |  | 144 | 195 | 28080 | 0.24435 | 0.0012531 | 0
2013-12-19 09:10 | FTR23 | LONG RURAL |  | 16 | 295 | 4720 | 0.018277 | 6.1957e-05 | 0
2013-12-05 09:00 | SMR4 | SHORT RURAL |  | 2 | 190 | 380 | 0.0033067 | 1.7404e-05 | 0
2013-12-03 08:50 | ALA01 | LONG RURAL |  | 18 | 12.2222 | 220 | 0.00085191 | 6.9702e-05 | 0
2013-12-18 09:50 | SMR8 | LONG RURAL |  | 1 | 100 | 100 | 0.00038723 | 3.8723e-06 | 0
2013-12-15 09:00 | MOE31 | LONG RURAL |  | 184 | 279 | 51336 | 0.19879 | 0.00071251 | 0
2013-12-17 08:50 | LDL13 | SHORT RURAL |  | 7 | 135 | 945 | 0.0082234 | 6.0914e-05 | 0
2013-12-17 08:35 | LDL13 | SHORT RURAL |  | 2 | 325 | 650 | 0.0056563 | 1.7404e-05 | 0
2013-12-19 08:00 | WYK12 | SHORT RURAL |  | 9 | 245 | 2205 | 0.019188 | 7.8318e-05 | 0
2013-12-05 11:20 | BN1 | LONG RURAL |  | 1 | 160 | 160 | 0.00061957 | 3.8723e-06 | 0
2013-12-17 09:10 | TGN23 | SHORT RURAL |  | 16 | 327 | 5232 | 0.045529 | 0.00013923 | 0
2013-12-20 09:14 | FTR12 | LONG RURAL |  | 1 | 29 | 29 | 0.0001123 | 3.8723e-06 | 0
2013-12-20 10:10 | FTR12 | LONG RURAL |  | 1 | 33 | 33 | 0.00012779 | 3.8723e-06 | 0
2013-12-18 11:50 | SMR8 | LONG RURAL |  | 2 | 95 | 190 | 0.00073574 | 7.7446e-06 | 0
2013-12-18 08:40 | LDL24 | URBAN |  | 203 | 218 | 44254 | 0.15416 | 0.00070715 | 0
2013-12-18 11:30 | SMR8 | LONG RURAL |  | 1 | 70 | 70 | 0.00027106 | 3.8723e-06 | 0
2013-12-18 08:30 | MFA22 | LONG RURAL |  | 9 | 310 | 2790 | 0.010804 | 3.4851e-05 | 0
2013-12-19 08:01 | WYK12 | SHORT RURAL |  | 14 | 224 | 3136 | 0.027289 | 0.00012183 | 0
2013-12-18 12:05 | KLO14 | LONG RURAL |  | 1 | 70 | 70 | 0.00027106 | 3.8723e-06 | 0
2013-12-18 14:05 | KLO14 | LONG RURAL |  | 1 | 35 | 35 | 0.00013553 | 3.8723e-06 | 0
2013-12-19 09:20 | KLK1 | SHORT RURAL |  | 14 | 154.4286 | 2162 | 0.018814 | 0.00012183 | 0
2013-12-19 08:00 | LDL13 | SHORT RURAL |  | 139 | 199 | 27661 | 0.24071 | 0.0012096 | 0
2013-12-18 09:26 | KLO14 | LONG RURAL |  | 6 | 109 | 654 | 0.0025325 | 2.3234e-05 | 0
2013-12-15 09:00 | BRT22 | SHORT RURAL |  | 99 | 372 | 36828 | 0.32048 | 0.0008615 | 0
2013-12-19 08:40 | DRN23 | LONG RURAL |  | 188 | 285 | 53580 | 0.20748 | 0.000728 | 0
2013-12-19 08:21 | LDL23 | LONG RURAL |  | 45 | 134 | 6030 | 0.02335 | 0.00017425 | 0
2013-12-19 08:57 | LDL13 | SHORT RURAL |  | 427 | 411.0937 | 175537 | 1.5275 | 0.0037157 | 0
2013-12-09 08:42 | BN6 | LONG RURAL |  | 4 | 368 | 1472 | 0.0057 | 1.5489e-05 | 0
2013-12-19 09:53 | LDL13 | SHORT RURAL |  | 15 | 92 | 1380 | 0.012009 | 0.00013053 | 0
2013-12-19 08:35 | WN3 | LONG RURAL |  | 3 | 155 | 465 | 0.0018006 | 1.1617e-05 | 0
2013-12-18 09:00 | KMS1 | SHORT RURAL |  | 1 | 145 | 145 | 0.0012618 | 8.702e-06 | 0
2013-12-18 09:30 | WGI22 | LONG RURAL |  | 3 | 280 | 840 | 0.0032527 | 1.1617e-05 | 0
2013-12-19 09:00 | LGA23 | LONG RURAL |  | 46 | 281 | 12926 | 0.050054 | 0.00017813 | 0
2013-12-02 08:40 | ALA01 | LONG RURAL |  | 42 | 30.3571 | 1275 | 0.0049372 | 0.00016264 | 0
2013-12-03 09:30 | ALA01 | LONG RURAL |  | 9 | 42.7778 | 385 | 0.0014908 | 3.4851e-05 | 0
2013-12-17 08:47 | BGE11 | SHORT RURAL |  | 203 | 371 | 75313 | 0.65537 | 0.0017665 | 0
2013-12-19 08:40 | BN2 | LONG RURAL |  | 3 | 25 | 75 | 0.00029042 | 1.1617e-05 | 0
2013-12-19 08:30 | BN2 | LONG RURAL |  | 2 | 26 | 52 | 0.00020136 | 7.7446e-06 | 0
2013-12-19 09:30 | BN2 | LONG RURAL |  | 2 | 25 | 50 | 0.00019362 | 7.7446e-06 | 0
2013-12-19 09:35 | BN2 | LONG RURAL |  | 1 | 45 | 45 | 0.00017425 | 3.8723e-06 | 0
2013-12-15 08:15 | SMG22 | URBAN |  | 103 | 260 | 26780 | 0.093288 | 0.0003588 | 0
2013-12-18 13:35 | LGA12 | SHORT RURAL |  | 37 | 78 | 2886 | 0.025114 | 0.00032197 | 0
2013-12-18 11:00 | LGA12 | SHORT RURAL |  | 1 | 160 | 160 | 0.0013923 | 8.702e-06 | 0
2013-12-18 09:04 | SMR3 | LONG RURAL |  | 3 | 347 | 1041 | 0.0040311 | 1.1617e-05 | 0
2013-12-19 08:35 | BDL1 | LONG RURAL |  | 26 | 182 | 4732 | 0.018324 | 0.00010068 | 0
2013-12-12 08:45 | CYN33 | SHORT RURAL |  | 30 | 105 | 3150 | 0.027411 | 0.00026106 | 0
2013-12-18 10:00 | MOE14 | SHORT RURAL |  | 25 | 395 | 9875 | 0.085932 | 0.00021755 | 0
2013-12-18 09:30 | MWTS24 | SHORT RURAL |  | 6 | 318 | 1908 | 0.016603 | 5.2212e-05 | 0
2013-12-18 11:10 | MOE31 | LONG RURAL |  | 2 | 220 | 440 | 0.0017038 | 7.7446e-06 | 0
2013-12-19 10:55 | BN2 | LONG RURAL |  | 1 | 35 | 35 | 0.00013553 | 3.8723e-06 | 0
2013-12-18 14:00 | MOE32 | SHORT RURAL |  | 1 | 70 | 70 | 0.00060914 | 8.702e-06 | 0
2013-12-19 09:05 | TGN23 | SHORT RURAL |  | 27 | 108 | 2916 | 0.025375 | 0.00023495 | 0
2013-12-19 11:30 | BN2 | LONG RURAL |  | 1 | 30 | 30 | 0.00011617 | 3.8723e-06 | 0
2013-12-19 08:00 | SLE31 | LONG RURAL |  | 9 | 247 | 2223 | 0.0086082 | 3.4851e-05 | 0
2013-12-19 10:35 | WGL21 | LONG RURAL |  | 2 | 16 | 32 | 0.00012391 | 7.7446e-06 | 0
2013-12-19 09:13 | WGI22 | LONG RURAL |  | 17 | 217 | 3689 | 0.014285 | 6.5829e-05 | 0
2013-12-13 09:40 | CYN23 | URBAN |  | 69 | 140 | 9660 | 0.03365 | 0.00024036 | 0
2013-12-14 08:05 | CYN11 | URBAN |  | 15 | 1800 | 27000 | 0.094054 | 5.2252e-05 | 0
2013-12-11 11:25 | DRN11 | URBAN |  | 53 | 110 | 5830 | 0.020309 | 0.00018462 | 0
2013-12-17 09:22 | MDG1 | SHORT RURAL |  | 148 | 328 | 48544 | 0.42243 | 0.0012879 | 0
2013-12-17 09:45 | BGE12 | SHORT RURAL |  | 169 | 445 | 75205 | 0.65443 | 0.0014706 | 0
2013-12-11 09:00 | WN3 | LONG RURAL |  | 1 | 175 | 175 | 0.00067766 | 3.8723e-06 | 0
2013-12-18 08:45 | UWY1 | SHORT RURAL |  | 302 | 302 | 91204 | 0.79365 | 0.002628 | 0
2013-12-18 08:32 | BGE12 | SHORT RURAL |  | 51 | 190 | 9690 | 0.084322 | 0.0004438 | 0
2013-12-18 10:00 | BGE12 | SHORT RURAL |  | 16 | 80 | 1280 | 0.011139 | 0.00013923 | 0
2013-12-18 08:30 | LYD14 | SHORT RURAL |  | 8 | 280 | 2240 | 0.019492 | 6.9616e-05 | 0
2013-12-04 10:30 | ALA01 | LONG RURAL |  | 2 | 45 | 90 | 0.00034851 | 7.7446e-06 | 0
2013-12-10 11:05 | LGA13 | LONG RURAL |  | 3 | 75 | 225 | 0.00087127 | 1.1617e-05 | 0
2013-12-23 08:15 | LDL24 | URBAN |  | 84 | 195 | 16380 | 0.057059 | 0.00029261 | 0
2013-12-23 10:12 | KLK1 | SHORT RURAL |  | 66 | 135 | 8910 | 0.077535 | 0.00057433 | 0
2013-12-23 09:00 | LGA23 | LONG RURAL |  | 149 | 463 | 68987 | 0.26714 | 0.00057697 | 0
2013-12-20 09:00 | WGI14 | SHORT RURAL |  | 227 | 390 | 88530 | 0.77039 | 0.0019753 | 0
2013-12-19 09:20 | UWY1 | SHORT RURAL |  | 25 | 75 | 1875 | 0.016316 | 0.00021755 | 0
2013-12-19 10:25 | BGE12 | SHORT RURAL |  | 119 | 275 | 32725 | 0.28477 | 0.0010355 | 0
2013-12-19 09:05 | BGE12 | SHORT RURAL |  | 91 | 260 | 23660 | 0.20589 | 0.00079188 | 0
2013-12-19 10:29 | BGE22 | SHORT RURAL |  | 1 | 12 | 12 | 0.00010442 | 8.702e-06 | 0
2013-12-12 14:20 | KLO14 | LONG RURAL |  | 2 | 95 | 190 | 0.00073574 | 7.7446e-06 | 0
2013-12-12 11:50 | KLO14 | LONG RURAL |  | 7 | 70 | 490 | 0.0018974 | 2.7106e-05 | 0
2013-12-15 09:30 | SMR4 | SHORT RURAL |  | 23 | 375 | 8625 | 0.075054 | 0.00020015 | 0
2013-12-15 12:10 | SMR4 | SHORT RURAL |  | 96 | 245 | 23520 | 0.20467 | 0.00083539 | 0
2013-12-13 08:33 | NLA34 | SHORT RURAL |  | 9 | 402 | 3618 | 0.031484 | 7.8318e-05 | 0
2013-12-19 07:49 | DRN23 | LONG RURAL |  | 657 | 373.8052 | 245590 | 0.951 | 0.0025441 | 0
2013-12-18 08:50 | ELM15 | SHORT RURAL |  | 153 | 404 | 61812 | 0.53789 | 0.0013314 | 0
2013-12-19 11:00 | BDL1 | LONG RURAL |  | 1 | 65 | 65 | 0.0002517 | 3.8723e-06 | 0
2013-12-16 13:05 | WO31 | URBAN |  | 1 | 223 | 223 | 0.00077682 | 3.4835e-06 | 0
2013-12-20 09:30 | UWY1 | SHORT RURAL |  | 25 | 60 | 1500 | 0.013053 | 0.00021755 | 0
2013-12-20 08:36 | BGE22 | SHORT RURAL |  | 2 | 38 | 76 | 0.00066135 | 1.7404e-05 | 0
2013-12-22 23:00 | LYD11 | SHORT RURAL |  | 74 | 165 | 12210 | 0.10625 | 0.00064395 | 0
2013-12-18 09:00 | DRN12 | URBAN |  | 64 | 105 | 6720 | 0.023409 | 0.00022294 | 0
2013-12-13 13:45 | LLG11 | SHORT RURAL |  | 61 | 15 | 915 | 0.0079623 | 0.00053082 | 0
2013-12-08 08:45 | WO11 | URBAN |  | 1 | 273 | 273 | 0.00095099 | 3.4835e-06 | 0
2013-12-05 09:15 | MVE01 | SHORT RURAL |  | 8 | 16.25 | 130 | 0.0011313 | 6.9616e-05 | 0
2013-12-05 12:05 | MVE01 | SHORT RURAL |  | 5 | 33 | 165 | 0.0014358 | 4.351e-05 | 0
2013-12-06 08:20 | ALA01 | LONG RURAL |  | 23 | 10.1304 | 233 | 0.00090225 | 8.9063e-05 | 0
2013-12-06 08:50 | MVE01 | SHORT RURAL |  | 21 | 28.0952 | 590 | 0.0051342 | 0.00018274 | 0
2013-12-24 09:05 | WOTS11 | LONG RURAL |  | 1 | 34 | 34 | 0.00013166 | 3.8723e-06 | 0
2013-12-24 10:25 | WOTS11 | LONG RURAL |  | 2 | 40 | 80 | 0.00030979 | 7.7446e-06 | 0
2013-12-24 09:00 | LGA23 | LONG RURAL |  | 78 | 305 | 23790 | 0.092122 | 0.00030204 | 0
2013-12-23 12:00 | KLK1 | SHORT RURAL |  | 1 | 65 | 65 | 0.00056563 | 8.702e-06 | 0
2013-12-24 09:10 | KLK2 | SHORT RURAL |  | 3 | 115 | 345 | 0.0030022 | 2.6106e-05 | 0
2013-12-19 10:22 | BDL1 | LONG RURAL |  | 3 | 13 | 39 | 0.00015102 | 1.1617e-05 | 0
2013-12-19 08:30 | OFR23 | LONG RURAL |  | 63 | 64 | 4032 | 0.015613 | 0.00024396 | 0
2013-12-19 08:45 | BWN14 | SHORT RURAL |  | 30 | 280 | 8400 | 0.073097 | 0.00026106 | 0
2013-12-20 08:50 | BWN14 | SHORT RURAL |  | 8 | 224 | 1792 | 0.015594 | 6.9616e-05 | 0
2013-12-24 08:30 | BDL3 | SHORT RURAL |  | 2 | 143 | 286 | 0.0024888 | 1.7404e-05 | 0
2013-12-20 08:34 | BDL1 | LONG RURAL |  | 1 | 59 | 59 | 0.00022847 | 3.8723e-06 | 0
2013-12-23 13:30 | LLG13 | SHORT RURAL |  | 1 | 85 | 85 | 0.00073967 | 8.702e-06 | 0
2013-12-24 08:30 | BDL3 | SHORT RURAL |  | 1 | 175 | 175 | 0.0015228 | 8.702e-06 | 0
2013-12-23 09:24 | SMR4 | SHORT RURAL |  | 30 | 226 | 6780 | 0.058999 | 0.00026106 | 0
2013-12-24 09:00 | SMR8 | LONG RURAL |  | 30 | 250 | 7500 | 0.029042 | 0.00011617 | 0
2013-12-22 08:30 | KLK1 | SHORT RURAL |  | 23 | 245 | 5635 | 0.049036 | 0.00020015 | 0
2013-12-22 08:40 | KLK1 | SHORT RURAL |  | 72 | 296 | 21312 | 0.18546 | 0.00062654 | 0
2013-12-13 16:35 | MOE32 | SHORT RURAL |  | 10 | 130 | 1300 | 0.011313 | 8.702e-05 | 0
2013-12-18 09:45 | DRN23 | LONG RURAL |  | 43 | 290 | 12470 | 0.048288 | 0.00016651 | 0
2013-12-07 17:20 | MVE01 | SHORT RURAL |  | 14 | 40 | 560 | 0.0048731 | 0.00012183 | 0
2013-12-09 08:00 | MVE01 | SHORT RURAL |  | 7 | 41.4286 | 290 | 0.0025236 | 6.0914e-05 | 0
2013-12-08 14:15 | MVE01 | SHORT RURAL |  | 11 | 25 | 275 | 0.002393 | 9.5722e-05 | 0
2013-12-08 09:00 | ALA01 | LONG RURAL |  | 111 | 36.4865 | 4050 | 0.015683 | 0.00042983 | 0
2013-12-07 09:20 | ALA01 | LONG RURAL |  | 300 | 815.4733 | 244642 | 0.94733 | 0.0011617 | 0
2013-12-17 09:40 | MOE22 | LONG RURAL |  | 32 | 260 | 8320 | 0.032218 | 0.00012391 | 0
2013-12-18 11:28 | MWTS32 | SHORT RURAL |  | 3 | 52 | 156 | 0.0013575 | 2.6106e-05 | 0
2013-12-19 09:20 | TGN11 | SHORT RURAL |  | 22 | 123 | 2706 | 0.023548 | 0.00019144 | 0
2013-12-16 12:40 | WN3 | LONG RURAL |  | 11 | 135 | 1485 | 0.0057504 | 4.2595e-05 | 0
2013-12-18 09:50 | BRT21 | SHORT RURAL |  | 4 | 100 | 400 | 0.0034808 | 3.4808e-05 | 0
2013-12-18 13:20 | BRT21 | SHORT RURAL |  | 14 | 40 | 560 | 0.0048731 | 0.00012183 | 0
2013-12-18 09:40 | MYT1 | SHORT RURAL |  | 3 | 190 | 570 | 0.0049601 | 2.6106e-05 | 0
2013-12-18 10:13 | BN6 | LONG RURAL |  | 2 | 32 | 64 | 0.00024783 | 7.7446e-06 | 0
2013-12-18 08:54 | BN6 | LONG RURAL |  | 1 | 26 | 26 | 0.00010068 | 3.8723e-06 | 0
2013-12-17 09:53 | BRT21 | SHORT RURAL |  | 236 | 232 | 54752 | 0.47645 | 0.0020537 | 0
2013-12-18 09:00 | MWTS14 | SHORT RURAL |  | 70 | 430 | 30100 | 0.26193 | 0.00060914 | 0
2013-12-17 09:30 | DRN11 | URBAN |  | 113 | 155 | 17515 | 0.061013 | 0.00039363 | 0
2013-12-16 12:50 | WN3 | LONG RURAL |  | 29 | 25 | 725 | 0.0028074 | 0.0001123 | 0
2013-12-17 09:07 | WN3 | LONG RURAL |  | 92 | 278 | 25576 | 0.099038 | 0.00035625 | 0
2013-12-17 09:07 | WN3 | LONG RURAL |  | 14 | 4 | 56 | 0.00021685 | 5.4212e-05 | 0
2013-12-17 13:40 | WN3 | LONG RURAL |  | 106 | 5 | 530 | 0.0020523 | 0.00041047 | 0
2013-12-18 09:40 | LDL22 | SHORT RURAL |  | 11 | 209 | 2299 | 0.020006 | 9.5722e-05 | 0
2013-12-18 08:33 | BN6 | LONG RURAL |  | 54 | 361 | 19494 | 0.075487 | 0.0002091 | 0
2013-12-18 09:05 | WYK24 | SHORT RURAL |  | 6 | 192 | 1152 | 0.010025 | 5.2212e-05 | 0
2013-12-18 09:31 | BN6 | LONG RURAL |  | 3 | 6 | 18 | 6.9702e-05 | 1.1617e-05 | 0
2013-12-18 11:20 | BN6 | LONG RURAL |  | 1 | 210 | 210 | 0.00081319 | 3.8723e-06 | 0
2013-12-18 12:23 | BN6 | LONG RURAL |  | 1 | 27 | 27 | 0.00010455 | 3.8723e-06 | 0
2013-12-17 09:30 | FTR21 | LONG RURAL |  | 1 | 255 | 255 | 0.00098744 | 3.8723e-06 | 0
2013-12-19 09:00 | BWA22 | LONG RURAL |  | 36 | 110 | 3960 | 0.015334 | 0.0001394 | 0
2013-12-17 09:10 | WGL24 | LONG RURAL |  | 10 | 220 | 2200 | 0.0085191 | 3.8723e-05 | 0
2013-12-18 09:17 | TGN31 | LONG RURAL |  | 9 | 345 | 3105 | 0.012024 | 3.4851e-05 | 0
2013-12-18 09:45 | WGL24 | LONG RURAL |  | 27 | 441 | 11907 | 0.046108 | 0.00010455 | 0
2013-12-17 09:46 | FTR12 | LONG RURAL |  | 2 | 67 | 134 | 0.00051889 | 7.7446e-06 | 0
2013-12-17 08:30 | LGA12 | SHORT RURAL |  | 4 | 155 | 620 | 0.0053952 | 3.4808e-05 | 0
2013-12-17 09:00 | LGA23 | LONG RURAL |  | 17 | 343 | 5831 | 0.022579 | 6.5829e-05 | 0
2013-12-17 12:30 | LGA12 | SHORT RURAL |  | 2 | 90 | 180 | 0.0015664 | 1.7404e-05 | 0
2013-12-17 09:15 | PHI12 | SHORT RURAL |  | 6 | 75 | 450 | 0.0039159 | 5.2212e-05 | 0
2013-12-18 10:00 | WOTS11 | LONG RURAL |  | 3 | 35 | 105 | 0.00040659 | 1.1617e-05 | 0
2013-12-18 09:00 | BWA23 | SHORT RURAL |  | 34 | 305 | 10370 | 0.090239 | 0.00029587 | 0
2013-12-17 09:35 | WGL23 | SHORT RURAL |  | 1 | 205 | 205 | 0.0017839 | 8.702e-06 | 0
2013-12-17 14:10 | WGL23 | SHORT RURAL |  | 1 | 45 | 45 | 0.00039159 | 8.702e-06 | 0
2013-12-17 09:25 | TGN41 | LONG RURAL |  | 37 | 302 | 11174 | 0.043269 | 0.00014328 | 0
2013-12-17 08:00 | SLE31 | LONG RURAL |  | 31 | 406 | 12586 | 0.048737 | 0.00012004 | 0
2013-12-17 09:30 | WGL13 | SHORT RURAL |  | 2 | 155 | 310 | 0.0026976 | 1.7404e-05 | 0
2013-12-18 09:15 | WOTS11 | LONG RURAL |  | 2 | 45 | 90 | 0.00034851 | 7.7446e-06 | 0
2013-12-13 09:00 | NLA32 | SHORT RURAL |  | 181 | 434 | 78554 | 0.68357 | 0.0015751 | 0
2013-12-17 09:25 | MFA22 | LONG RURAL |  | 1 | 335 | 335 | 0.0012972 | 3.8723e-06 | 0
2013-12-17 09:45 | SLE32 | SHORT RURAL |  | 3 | 295 | 885 | 0.0077012 | 2.6106e-05 | 0
2013-12-15 08:45 | MFA34 | SHORT RURAL |  | 21 | 145 | 3045 | 0.026498 | 0.00018274 | 0
2013-12-17 09:20 | MFA22 | LONG RURAL |  | 6 | 130 | 780 | 0.0030204 | 2.3234e-05 | 0
2013-12-18 08:45 | BDL5 | LONG RURAL |  | 39 | 185 | 7215 | 0.027939 | 0.00015102 | 0
2013-12-18 08:35 | BDL3 | SHORT RURAL |  | 2 | 340 | 680 | 0.0059173 | 1.7404e-05 | 0
2013-12-19 08:40 | BDL5 | LONG RURAL |  | 24 | 245 | 5880 | 0.022769 | 9.2936e-05 | 0
2013-12-18 09:50 | SLE31 | LONG RURAL |  | 7 | 330 | 2310 | 0.008945 | 2.7106e-05 | 0
2013-12-16 11:40 | WGL21 | LONG RURAL |  | 1 | 140 | 140 | 0.00054212 | 3.8723e-06 | 0
2013-12-17 11:00 | WGL21 | LONG RURAL |  | 9 | 90 | 810 | 0.0031366 | 3.4851e-05 | 0
2013-12-17 09:10 | WGL21 | LONG RURAL |  | 4 | 30 | 120 | 0.00046468 | 1.5489e-05 | 0
2013-12-19 09:00 | TGN41 | LONG RURAL |  | 12 | 35 | 420 | 0.0016264 | 4.6468e-05 | 0
2013-12-17 09:35 | DRN23 | LONG RURAL |  | 3 | 130 | 390 | 0.0015102 | 1.1617e-05 | 0
2013-12-13 09:07 | WN6 | LONG RURAL |  | 28 | 138 | 3864 | 0.014963 | 0.00010842 | 0
2013-12-17 09:00 | SLE31 | LONG RURAL |  | 28 | 230 | 6440 | 0.024938 | 0.00010842 | 0
2013-12-17 09:20 | SLE31 | LONG RURAL |  | 10 | 440 | 4400 | 0.017038 | 3.8723e-05 | 0
2013-12-18 08:30 | BDL1 | LONG RURAL |  | 913 | 237 | 216381 | 0.8379 | 0.0035354 | 0
2013-12-18 12:10 | MOE31 | LONG RURAL |  | 12 | 110 | 1320 | 0.0051115 | 4.6468e-05 | 0
2013-12-19 09:05 | SLE31 | LONG RURAL |  | 6 | 490 | 2940 | 0.011385 | 2.3234e-05 | 0
2013-12-21 08:41 | CYN22 | URBAN |  | 442 | 456 | 201552 | 0.7021 | 0.0015397 | 0
2013-12-18 14:05 | BDL1 | LONG RURAL |  | 6 | 73 | 438 | 0.0016961 | 2.3234e-05 | 0
2013-12-19 09:15 | BDL1 | LONG RURAL |  | 2 | 50 | 100 | 0.00038723 | 7.7446e-06 | 0
2013-12-18 08:46 | BDL1 | LONG RURAL |  | 228 | 229 | 52212 | 0.20218 | 0.00088289 | 0
2013-12-19 09:10 | WGL21 | LONG RURAL |  | 14 | 110 | 1540 | 0.0059634 | 5.4212e-05 | 0
2013-12-16 11:57 | WT9 | URBAN |  | 57 | 145 | 8265 | 0.028791 | 0.00019856 | 0
2013-12-13 11:25 | WN3 | LONG RURAL |  | 1 | 147 | 147 | 0.00056923 | 3.8723e-06 | 0
2013-12-16 09:40 | ELM15 | SHORT RURAL |  | 69 | 390 | 26910 | 0.23417 | 0.00060044 | 0
2013-12-16 11:50 | LGA11 | LONG RURAL |  | 76 | 219 | 16644 | 0.064451 | 0.0002943 | 0
2013-12-12 10:15 | BGE12 | SHORT RURAL |  | 132 | 295 | 38940 | 0.33885 | 0.0011487 | 0
2013-12-17 09:15 | FTR12 | LONG RURAL |  | 43 | 300 | 12900 | 0.049953 | 0.00016651 | 0
2013-12-15 09:55 | BGE12 | SHORT RURAL |  | 1 | 55 | 55 | 0.00047861 | 8.702e-06 | 0
2013-12-15 11:45 | BGE12 | SHORT RURAL |  | 1 | 125 | 125 | 0.0010877 | 8.702e-06 | 0
2013-12-16 08:40 | FGY13 | SHORT RURAL |  | 54 | 430 | 23220 | 0.20206 | 0.00046991 | 0
2013-12-18 09:00 | WGI34 | SHORT RURAL |  | 2 | 220 | 440 | 0.0038289 | 1.7404e-05 | 0
2013-12-17 08:50 | PHM31 | SHORT RURAL |  | 5 | 220 | 1100 | 0.0095722 | 4.351e-05 | 0
2013-12-16 08:46 | BGE24 | SHORT RURAL |  | 35 | 398 | 13930 | 0.12122 | 0.00030457 | 0
2013-12-18 08:51 | LGA24 | SHORT RURAL |  | 2 | 49 | 98 | 0.00085279 | 1.7404e-05 | 0
2013-12-16 09:20 | FGY21 | SHORT RURAL |  | 10 | 365 | 3650 | 0.031762 | 8.702e-05 | 0
2013-12-18 09:29 | WN5 | LONG RURAL |  | 156 | 30 | 4680 | 0.018122 | 0.00060408 | 0
2013-12-18 09:00 | LGA24 | SHORT RURAL |  | 3 | 55 | 165 | 0.0014358 | 2.6106e-05 | 0
2013-12-18 10:00 | PHM14 | LONG RURAL |  | 34 | 255 | 8670 | 0.033573 | 0.00013166 | 0
2013-12-27 09:05 | LGA23 | LONG RURAL |  | 78 | 392 | 30576 | 0.1184 | 0.00030204 | 0
2013-12-13 09:00 | OFR23 | LONG RURAL |  | 1 | 215 | 215 | 0.00083255 | 3.8723e-06 | 0
2013-12-17 09:40 | DRN13 | SHORT RURAL |  | 9 | 50 | 450 | 0.0039159 | 7.8318e-05 | 0
2013-12-19 09:55 | WN3 | LONG RURAL |  | 3 | 21 | 63 | 0.00024396 | 1.1617e-05 | 0
2013-12-18 09:05 | LDL14 | SHORT RURAL |  | 10 | 190 | 1900 | 0.016534 | 8.702e-05 | 0
2013-12-18 09:35 | CYN32 | URBAN |  | 174 | 562.2069 | 97824 | 0.34077 | 0.00060613 | 0
2013-12-13 13:15 | WYK11 | SHORT RURAL |  | 1 | 75 | 75 | 0.00065265 | 8.702e-06 | 0
2013-12-17 08:35 | LDL14 | SHORT RURAL |  | 40 | 345 | 13800 | 0.12009 | 0.00034808 | 0
2013-12-17 12:10 | LDL11 | URBAN |  | 87 | 185 | 16095 | 0.056067 | 0.00030306 | 0
2013-12-17 09:57 | KLK1 | SHORT RURAL |  | 300 | 278 | 83400 | 0.72574 | 0.0026106 | 0
2013-12-18 08:30 | BWN14 | SHORT RURAL |  | 60 | 353 | 21180 | 0.18431 | 0.00052212 | 0
2013-12-17 09:05 | CRE31 | URBAN |  | 143 | 260 | 37180 | 0.12952 | 0.00049814 | 0
2013-12-17 10:40 | LGA13 | LONG RURAL |  | 1 | 55 | 55 | 0.00021298 | 3.8723e-06 | 0
2013-12-15 09:15 | BGE12 | SHORT RURAL |  | 1 | 75 | 75 | 0.00065265 | 8.702e-06 | 0
2013-12-17 11:15 | KLO24 | SHORT RURAL |  | 5 | 350 | 1750 | 0.015228 | 4.351e-05 | 0
2013-12-14 08:15 | MDG1 | SHORT RURAL |  | 86 | 43 | 3698 | 0.03218 | 0.00074837 | 0
2013-12-20 09:10 | WGI34 | SHORT RURAL |  | 1 | 100 | 100 | 0.0008702 | 8.702e-06 | 0
2013-12-24 11:31 | WOTS11 | LONG RURAL |  | 1 | 27 | 27 | 0.00010455 | 3.8723e-06 | 0
2013-12-16 08:50 | BGE22 | SHORT RURAL |  | 34 | 387 | 13158 | 0.1145 | 0.00029587 | 0
2013-12-16 10:35 | OFR23 | LONG RURAL |  | 15 | 220 | 3300 | 0.012779 | 5.8085e-05 | 0
2013-12-18 14:25 | BRT21 | SHORT RURAL |  | 21 | 105 | 2205 | 0.019188 | 0.00018274 | 0
2013-12-17 09:10 | BRA21 | URBAN |  | 91 | 310 | 28210 | 0.098269 | 0.000317 | 0
2013-12-17 09:10 | BWR34 | URBAN |  | 117 | 310 | 36270 | 0.12635 | 0.00040757 | 0
2013-12-17 10:20 | DRN23 | LONG RURAL |  | 5 | 165 | 825 | 0.0031947 | 1.9362e-05 | 0
2013-12-23 12:00 | MSD4 | LONG RURAL |  | 36 | 55 | 1980 | 0.0076672 | 0.0001394 | 0
2013-12-18 09:05 | MOE31 | LONG RURAL |  | 4 | 60 | 240 | 0.00092936 | 1.5489e-05 | 0
2013-12-17 08:30 | BDL1 | LONG RURAL |  | 34 | 430 | 14620 | 0.056613 | 0.00013166 | 0
2013-12-16 08:36 | BDL1 | LONG RURAL |  | 4 | 229 | 916 | 0.003547 | 1.5489e-05 | 0
2013-12-19 08:33 | BN6 | LONG RURAL |  | 8 | 78 | 624 | 0.0024163 | 3.0979e-05 | 0
2013-12-24 08:30 | BWN11 | SHORT RURAL |  | 4 | 179 | 716 | 0.0062306 | 3.4808e-05 | 0
2013-12-17 09:20 | BDL1 | LONG RURAL |  | 1 | 165 | 165 | 0.00063893 | 3.8723e-06 | 0
2013-12-19 08:35 | WN6 | LONG RURAL |  | 42 | 183 | 7686 | 0.029763 | 0.00016264 | 0
2013-12-19 06:47 | MYT1 | SHORT RURAL |  | 179 | 383 | 68557 | 0.59658 | 0.0015577 | 0
2013-12-19 08:00 | KLO24 | SHORT RURAL |  | 3 | 150 | 450 | 0.0039159 | 2.6106e-05 | 0
2013-12-18 10:00 | BGE23 | SHORT RURAL |  | 58 | 135 | 7830 | 0.068136 | 0.00050471 | 0
2013-12-18 09:15 | SFS1 | SHORT RURAL |  | 29 | 245 | 7105 | 0.061828 | 0.00025236 | 0
2013-12-22 09:02 | KLK1 | SHORT RURAL |  | 95 | 179 | 17005 | 0.14798 | 0.00082669 | 0
2013-12-27 09:00 | LLG13 | SHORT RURAL |  | 10 | 50 | 500 | 0.004351 | 8.702e-05 | 0
2013-12-27 12:30 | LLG13 | SHORT RURAL |  | 1 | 35 | 35 | 0.00030457 | 8.702e-06 | 0
2013-12-10 15:00 | MVE01 | SHORT RURAL |  | 1 | 30 | 30 | 0.00026106 | 8.702e-06 | 0
2013-12-10 08:30 | MVE01 | SHORT RURAL |  | 12 | 26.6667 | 320 | 0.0027846 | 0.00010442 | 0
2013-12-11 08:50 | MVE01 | SHORT RURAL |  | 15 | 32.3333 | 485 | 0.0042205 | 0.00013053 | 0
2013-12-11 08:00 | ALA01 | LONG RURAL |  | 31 | 9.4194 | 292 | 0.0011307 | 0.00012004 | 0
2013-12-18 09:20 | BGE11 | SHORT RURAL |  | 7 | 235 | 1645 | 0.014315 | 6.0914e-05 | 0
2013-12-18 10:10 | LDL13 | SHORT RURAL |  | 5 | 330 | 1650 | 0.014358 | 4.351e-05 | 0
2013-12-24 09:00 | LDL24 | URBAN |  | 7 | 188 | 1316 | 0.0045843 | 2.4384e-05 | 0
2013-12-14 09:05 | WOTS11 | LONG RURAL |  | 65 | 135 | 8775 | 0.03398 | 0.0002517 | 0
2013-12-14 10:45 | BRT21 | SHORT RURAL |  | 105 | 245 | 25725 | 0.22386 | 0.00091371 | 0
2013-12-27 09:12 | WGL23 | SHORT RURAL |  | 129 | 96 | 12384 | 0.10777 | 0.0011226 | 0
2013-12-16 09:16 | OFR21 | SHORT RURAL |  | 83 | 444 | 36852 | 0.32069 | 0.00072226 | 0
2013-12-12 08:20 | MVE01 | SHORT RURAL |  | 21 | 31.6667 | 665 | 0.0057868 | 0.00018274 | 0
2013-12-15 07:42 | LLG12 | SHORT RURAL |  | 1695 | 1.6442 | 2787 | 0.024252 | 0.01475 | 0
2013-12-30 09:30 | SMR8 | LONG RURAL |  | 29 | 280 | 8120 | 0.031443 | 0.0001123 | 0
2013-12-30 11:20 | LGA23 | LONG RURAL |  | 1 | 180 | 180 | 0.00069702 | 3.8723e-06 | 0
2013-12-30 09:30 | DRN23 | LONG RURAL |  | 164 | 356 | 58384 | 0.22608 | 0.00063506 | 0
2013-12-20 09:10 | MOE31 | LONG RURAL |  | 1 | 40 | 40 | 0.00015489 | 3.8723e-06 | 0
2013-12-20 11:40 | MOE31 | LONG RURAL |  | 4 | 80 | 320 | 0.0012391 | 1.5489e-05 | 0
2013-12-16 08:50 | BDL3 | SHORT RURAL |  | 56 | 304 | 17024 | 0.14814 | 0.00048731 | 0
2013-12-20 09:10 | KLO14 | LONG RURAL |  | 2 | 308 | 616 | 0.0023853 | 7.7446e-06 | 0
2013-12-23 09:05 | WGI22 | LONG RURAL |  | 4 | 355 | 1420 | 0.0054987 | 1.5489e-05 | 0
2013-12-14 09:40 | MOE31 | LONG RURAL |  | 427 | 515 | 219905 | 0.85154 | 0.0016535 | 0
2013-12-17 08:42 | WOTS11 | LONG RURAL |  | 100 | 381.86 | 38186 | 0.14787 | 0.00038723 | 0
2013-12-16 13:40 | CF2 | SHORT RURAL |  | 74 | 62.9189 | 4656 | 0.040516 | 0.00064395 | 0
2013-12-31 09:56 | LGA13 | LONG RURAL |  | 1 | 65 | 65 | 0.0002517 | 3.8723e-06 | 0
2013-12-31 09:30 | ALA01 | LONG RURAL |  | 9 | 301 | 2709 | 0.01049 | 3.4851e-05 | 0
2013-12-31 09:47 | LGA12 | SHORT RURAL |  | 218 | 278 | 60604 | 0.52737 | 0.001897 | 0
2013-12-17 17:15 | BDL3 | SHORT RURAL |  | 4 | 90 | 360 | 0.0031327 | 3.4808e-05 | 0
2013-12-31 09:00 | FTR23 | LONG RURAL |  | 31 | 10 | 310 | 0.0012004 | 0.00012004 | 0
2013-12-14 12:20 | ALA01 | LONG RURAL |  | 18 | 11.3889 | 205 | 0.00079382 | 6.9702e-05 | 0
2013-12-14 08:45 | MVE01 | SHORT RURAL |  | 27 | 32.963 | 890 | 0.0077448 | 0.00023495 | 0
2013-12-14 08:15 | ALA01 | LONG RURAL |  | 16 | 12.1875 | 195 | 0.0007551 | 6.1957e-05 | 0
2013-12-21 08:10 | KLO14 | LONG RURAL |  | 3 | 133 | 399 | 0.0015451 | 1.1617e-05 | 0
2013-12-22 10:50 | KLO14 | LONG RURAL |  | 1 | 115 | 115 | 0.00044532 | 3.8723e-06 | 0
2013-12-16 14:20 | MVE01 | SHORT RURAL |  | 16 | 30 | 480 | 0.0041769 | 0.00013923 | 0
2013-12-13 08:40 | MVE01 | SHORT RURAL |  | 14 | 34.2857 | 480 | 0.0041769 | 0.00012183 | 0
2013-12-22 08:30 | BWA22 | LONG RURAL |  | 7 | 125 | 875 | 0.0033883 | 2.7106e-05 | 0
2013-12-16 10:35 | ALA01 | LONG RURAL |  | 17 | 15.8824 | 270 | 0.0010455 | 6.5829e-05 | 0
2013-12-16 08:30 | MVE01 | SHORT RURAL |  | 80 | 30.6875 | 2455 | 0.021363 | 0.00069616 | 0
2013-12-18 08:50 | MVE01 | SHORT RURAL |  | 7 | 14.2857 | 100 | 0.0008702 | 6.0914e-05 | 0
2013-12-17 08:15 | MVE01 | SHORT RURAL |  | 87 | 19.7701 | 1720 | 0.014967 | 0.00075707 | 0
2013-12-17 08:55 | ALA01 | LONG RURAL |  | 22 | 12.2727 | 270 | 0.0010455 | 8.5191e-05 | 0
2013-12-27 08:50 | MOE32 | SHORT RURAL |  | 1 | 110 | 110 | 0.00095722 | 8.702e-06 | 0
Contents

## 6b. Annual Feeder Reliability
SP AusNet
Annual Feeder Reliability
2013
Table 1 Annual Feeder Reliability Data
Feeder ID / name | Description of the service area for the feeder | Feeder classification | Number of distribution customers | Length of high voltage distribution lines (overhead) | Length of high voltage distribution lines (underground) | Maximum demand (MVA) | Energy not supplied (unplanned) (MWh) | Energy not supplied (planned) (MWh) | Total number of unplanned outages | Total unplanned minutes off-supply | Unplanned minutes off-supply (after removing excluded events and MED) | Unplanned interruptions (SAIFI) | Unplanned interruptions (SAIFI) (after removing excluded events) | Total number of planned outages | Total planned minutes off-supply | Planned interruptions (SAIFI) | Total number of momentary feeder outages | Total number of momentary feeder section outages | Momentary interruptions due to feeder outages (MAIFI) | Momentary interruptions due to feeder outages (MAIFI) (after removing excluded events) | Momentary interruptions due to feeder section outages (MAIFI) | Monetary interruptions due to feeder section outages (MAIFI) (after removing excluded events) | Low Reliability Feeder (SAIDI) | Low Reliability Feeder (MAIFI)
ALA01 | North | LONG RURAL | 2564 | 431.1279 | 1.3239 | 7.8878 | 3.6587 | 10.6441 | 45 | 201818 | 201677 | 2304 | 2303 | 113 | 587132 | 2102 | 4 | 24 | 10248 | 7685 | 8410 | 8410 | No | No
BDL1 | East | LONG RURAL | 2210 | 655.9234 | 4.9127 | 6.516 | 15.2192 | 26.3293 | 90 | 807873 | 807729 | 14502 | 14486 | 119 | 1397630 | 4740 | 6 | 49 | 13206 | 13206 | 18069 | 16864 | Yes | No
BDL2 | East | SHORT RURAL | 3920.5 | 43.186 | 6.8222 | 9.2595 | 1.5619 | 4.8881 | 13 | 100275 | 100275 | 9939 | 9939 | 23 | 313811 | 1564 | 1 | 6 | 3925 | 3925 | 8065 | 8065 | No | No
BDL3 | East | SHORT RURAL | 2022.5 | 68.4267 | 4.1552 | 12.1555 | 1.7418 | 9.8133 | 8 | 42858 | 42858 | 4098 | 4098 | 26 | 241468 | 1250 | 0 | 0 | 0 | 0 | 0 | 0 | No | No
BDL4 | East | SHORT RURAL | 4475.5 | 97.0717 | 8.7042 | 9.2595 | 4.1906 | 15.0399 | 25 | 206969 | 198907 | 9910 | 9879 | 21 | 742805 | 2233 | 8 | 13 | 35851 | 35851 | 6659 | 6659 | No | No
BDL5 | East | LONG RURAL | 3987.5 | 399.1604 | 3.2364 | 9.793 | 10.206 | 43.7143 | 61 | 645720 | 362492 | 16107 | 11399 | 76 | 2765732 | 6996 | 3 | 35 | 7992 | 7992 | 35136 | 23149 | Yes | No
BDL6 | East | SHORT RURAL | 3041.5 | 163.7165 | 13.0586 | 9.1452 | 6.3771 | 27.0678 | 31 | 433473 | 433473 | 10922 | 10922 | 49 | 1839878 | 5934 | 2 | 32 | 6086 | 6086 | 30146 | 30146 | Yes | No
BDL8 | East | LONG RURAL | 2068 | 582.4999 | 3.7554 | 4.7631 | 2.9482 | 27.9101 | 64 | 223788 | 218336 | 6309 | 6280 | 50 | 2118596 | 5309 | 1 | 40 | 2075 | 2075 | 11520 | 11520 | Yes | No
BGE11 | Central | SHORT RURAL | 3139 | 59.6226 | 3.895 | 7.8497 | 69.511 | 27.4787 | 88 | 4046241 | 2113349 | 35750 | 27501 | 54 | 1599540 | 6089 | 6 | 7 | 14637 | 13877 | 9422 | 7958 | Yes | No
BGE12 | Central | SHORT RURAL | 2270 | 102.3349 | 0.6211 | 5.3347 | 17.5225 | 44.0077 | 32 | 978967 | 740153 | 5810 | 3911 | 80 | 2458667 | 9380 | 5 | 11 | 5824 | 4647 | 5147 | 4297 | Yes | No
BGE21 | Central | URBAN | 16 | 7.7881 | 1.309 | 3.8105 | 2.0054 | 0.010838 | 3 | 14803 | 6867 | 1225 | 1209 | 1 | 80 | 2 | 2 | 0 | 16 | 16 | 0 | 0 | Yes | No
BGE22 | Central | SHORT RURAL | 3237 | 99.0328 | 3.8616 | 8.4974 | 56.5022 | 36.1792 | 96 | 4273180 | 2209074 | 32467 | 19936 | 87 | 2736183 | 9642 | 9 | 28 | 20577 | 19544 | 40976 | 36592 | Yes | Yes
BGE23 | Central | SHORT RURAL | 1979.5 | 29.7705 | 1.0991 | 7.621 | 6.4805 | 3.7271 | 25 | 393785 | 233418 | 7137 | 4548 | 10 | 226478 | 855 | 1 | 0 | 1973 | 1973 | 0 | 0 | No | No
BGE24 | Central | SHORT RURAL | 1543.5 | 41.4885 | 3.1965 | 4.7631 | 38.0326 | 8.7016 | 79 | 1492508 | 1153458 | 13810 | 11339 | 29 | 341474 | 1149 | 8 | 37 | 12251 | 7613 | 28179 | 25086 | Yes | Yes
BN1 | North | LONG RURAL | 4482.5 | 1192.25 | 3.4616 | 11.3553 | 57.8038 | 18.9522 | 110 | 4362956 | 1296305 | 21855 | 12694 | 180 | 1430489 | 6557 | 1 | 54 | 4493 | 4493 | 30633 | 26916 | Yes | No
BN2 | North | LONG RURAL | 1099 | 381.1238 | 1.6622 | 9.8692 | 9.7757 | 20.1285 | 35 | 134489 | 133300 | 2276 | 1175 | 63 | 276918 | 1395 | 1 | 15 | 1096 | 1096 | 3042 | 3042 | No | No
BN3 | North | SHORT RURAL | 645 | 149.5261 | 1.6445 | 4.1916 | 0.3131 | 1.7411 | 17 | 9781 | 9135 | 733 | 87 | 18 | 54391 | 181 | 0 | 2 | 0 | 0 | 182 | 182 | No | No
BN4 | North | URBAN | 3312 | 16.988 | 2.1322 | 8.5737 | 0.78109 | 2.0377 | 9 | 49874 | 22050 | 4132 | 787 | 8 | 130112 | 490 | 4 | 0 | 13288 | 13288 | 0 | 0 | No | No
BN6 | North | LONG RURAL | 2305 | 496.2539 | 2.2944 | 6.2873 | 5.6423 | 10.8839 | 41 | 405861 | 126261 | 3370 | 842 | 72 | 782899 | 2157 | 0 | 23 | 0 | 0 | 14071 | 12599 | No | No
BRA11 | Central | URBAN | 2078 | 9.2579 | 1.9368 | 6.5922 | 4.314 | 7.6604 | 14 | 282597 | 105708 | 3602 | 1437 | 16 | 501808 | 2573 | 1 | 1 | 2149 | 2149 | 1003 | 1003 | Yes | No
BRA12 | Central | URBAN | 292 | 2.7852 | 1.0777 | 6.1349 | 0 | 13.5667 | 0 | 0 | 0 | 0 | 0 | 4 | 69229 | 132 | 1 | 0 | 169 | 169 | 0 | 0 | No | No
BRA13 | Central | URBAN | 1575.5 | 7.9215 | 4.0045 | 6.897 | 0.45551 | 11.0455 | 3 | 18006 | 18006 | 159 | 159 | 11 | 436624 | 2276 | 2 | 0 | 3164 | 3164 | 0 | 0 | Yes | No
BRA14 | Central | URBAN | 3724 | 15.6578 | 0.6641 | 7.2781 | 4.005 | 16.74 | 14 | 488510 | 488510 | 3791 | 3791 | 33 | 2041865 | 6901 | 3 | 0 | 9229 | 9229 | 0 | 0 | Yes | No
BRA21 | Central | URBAN | 4613 | 18.8927 | 10.306 | 15.0515 | 3.632 | 15.3054 | 13 | 192436 | 192436 | 1158 | 1158 | 17 | 810939 | 2752 | 1 | 0 | 4667 | 4667 | 0 | 0 | No | No
BRA22 | Central | URBAN | 2 | 0 | 1.0586 | 3.8867 | 0 | 17.1407 | 0 | 0 | 0 | 0 | 0 | 1 | 796 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Yes | No
BRA23 | Central | URBAN | 1759.5 | 7.8659 | 4.5359 | 5.8682 | 9.6256 | 3.5989 | 13 | 463919 | 442028 | 6053 | 6042 | 5 | 173456 | 685 | 6 | 0 | 7097 | 7097 | 0 | 0 | Yes | No
BRA24 | Central | URBAN | 1738 | 9.1666 | 2.1855 | 5.3728 | 1.6449 | 6.6918 | 10 | 103145 | 102619 | 637 | 636 | 4 | 419624 | 1634 | 1 | 0 | 1735 | 1735 | 0 | 0 | Yes | No
BRA31 | Central | URBAN | 933.5 | 1.5453 | 3.8293 | 7.0113 | 0.093471 | 0.027284 | 1 | 2518 | 2518 | 15 | 15 | 1 | 735 | 1 | 1 | 0 | 1056 | 1056 | 0 | 0 | No | No
BRA32 | Central | URBAN | 2150 | 8.9564 | 1.8962 | 5.792 | 0.89318 | 3.3679 | 10 | 49746 | 49746 | 336 | 336 | 11 | 187577 | 940 | 1 | 0 | 2086 | 2086 | 0 | 0 | No | No
BRA33 | Central | URBAN | 3928.5 | 14.2017 | 7.5859 | 9.9835 | 4.4913 | 5.5047 | 17 | 337527 | 264052 | 1848 | 1805 | 12 | 413689 | 1636 | 9 | 0 | 30523 | 30523 | 0 | 0 | No | Yes
BRA34 | Central | URBAN | 66 | 0 | 1.7894 | 4.9156 | 0.013549 | 0 | 0 | 84 | 84 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | No | No
BRT11 | North | SHORT RURAL | 1030.5 | 25.0609 | 1.1351 | 3.0865 | 0.90852 | 2.6246 | 8 | 51286 | 51286 | 747 | 747 | 16 | 148161 | 619 | 1 | 2 | 334 | 334 | 597 | 597 | No | No
BRT21 | North | SHORT RURAL | 1528 | 43.5244 | 45.8908 | 5.068 | 2.7279 | 4.2639 | 10 | 163865 | 163865 | 3353 | 3353 | 37 | 256137 | 1123 | 0 | 0 | 0 | 0 | 0 | 0 | No | No
BRT22 | North | SHORT RURAL | 1500 | 93.3495 | 3.3339 | 5.3347 | 1.9423 | 6.7183 | 19 | 86992 | 86992 | 2127 | 2127 | 26 | 300905 | 1051 | 2 | 10 | 1745 | 1745 | 7499 | 7499 | No | No
BWA21 | North | URBAN | 4 | 0 | 1.9729 | 1.7909 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 4 | 4 | 0 | 0 | No | No
BWA22 | North | LONG RURAL | 1385 | 229.5057 | 4.7368 | 3.8105 | 1.5741 | 2.7485 | 24 | 78768 | 45897 | 545 | 506 | 35 | 137534 | 1990 | 2 | 7 | 2762 | 2762 | 5130 | 5130 | No | No
BWA23 | North | SHORT RURAL | 420.5 | 173.6444 | 1.739 | 7.3162 | 13.284 | 15.6195 | 24 | 109686 | 109079 | 667 | 661 | 17 | 128971 | 432 | 6 | 4 | 2513 | 2097 | 156 | 156 | No | No
BWA24 | North | SHORT RURAL | 1 | 1.2538 | 0.2786 | 0.01 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 1 | 0 | 0 | No | No
BWN11 | Central | SHORT RURAL | 2078 | 8.556 | 14.1201 | 4.1535 | 1.6867 | 5.1595 | 4 | 75300 | 75300 | 1689 | 1689 | 10 | 230339 | 910 | 3 | 0 | 7025 | 7025 | 0 | 0 | No | No
BWN12 | Central | URBAN | 1452.5 | 3.7471 | 7.1467 | 9.5263 | 1.6224 | 6.4646 | 4 | 72199 | 72199 | 343 | 343 | 9 | 287681 | 1404 | 1 | 0 | 1078 | 1078 | 0 | 0 | No | No
BWN13 | Central | URBAN | 2041 | 10.6784 | 4.9048 | 9.9454 | 4.3944 | 3.2233 | 18 | 295971 | 295971 | 8606 | 8606 | 16 | 217094 | 1450 | 3 | 0 | 7010 | 7010 | 0 | 0 | No | No
BWN14 | Central | SHORT RURAL | 1652.5 | 72.7612 | 5.3194 | 5.5252 | 17.9771 | 9.2064 | 29 | 943658 | 911661 | 6546 | 6483 | 31 | 483267 | 1762 | 2 | 6 | 2330 | 677 | 3291 | 2193 | Yes | No
BWR12 | Central | URBAN | 761.5 | 5.9911 | 0.4349 | 7.621 | 1.5319 | 15.3003 | 5 | 28584 | 28584 | 262 | 262 | 17 | 285498 | 1167 | 3 | 0 | 2292 | 2292 | 0 | 0 | Yes | No
BWR13 | Central | SHORT RURAL | 4392 | 37.7119 | 5.4553 | 11.5077 | 7.9566 | 22.3862 | 27 | 530590 | 500764 | 8374 | 8291 | 28 | 1492843 | 4807 | 8 | 1 | 27834 | 23446 | 315 | 315 | No | No
BWR21 | Central | URBAN | 0.5 | 0 | 1.1428 | 4.9537 | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | No | No
BWR22 | Central | URBAN | 1059.5 | 9.727 | 0.5413 | 8.0021 | 2.9393 | 0.88076 | 10 | 73833 | 62591 | 1690 | 1632 | 3 | 22124 | 80 | 0 | 0 | 640 | 640 | 0 | 0 | No | No
BWR23 | Central | URBAN | 3554.5 | 17.6957 | 2.266 | 8.7642 | 5.7154 | 8.7904 | 15 | 395974 | 311484 | 3931 | 2724 | 18 | 609022 | 2565 | 5 | 0 | 14487 | 12202 | 0 | 0 | Yes | No
BWR24 | Central | URBAN | 641.5 | 5.6875 | 3.4277 | 8.3069 | 1.0091 | 6.3982 | 5 | 9649 | 9507 | 105 | 104 | 8 | 61182 | 244 | 2 | 0 | 1283 | 1283 | 0 | 0 | No | No
BWR32 | Central | URBAN | 2720.5 | 12.9697 | 0.9118 | 7.7734 | 2.431 | 23.2036 | 16 | 130194 | 66505 | 4675 | 1973 | 30 | 1242671 | 4278 | 3 | 0 | 8192 | 8192 | 0 | 0 | Yes | No
BWR33 | Central | URBAN | 158.5 | 1.6731 | 1.1911 | 8.0021 | 4.2275 | 6.0007 | 3 | 22137 | 22137 | 357 | 357 | 4 | 31422 | 233 | 2 | 0 | 445 | 445 | 0 | 0 | Yes | No
BWR34 | Central | URBAN | 2939 | 10.4078 | 1.5517 | 7.7734 | 0.80696 | 14.6297 | 8 | 47818 | 47818 | 311 | 311 | 15 | 866915 | 2724 | 4 | 0 | 11812 | 8851 | 0 | 0 | Yes | No
CF1 | North | SHORT RURAL | 67.5 | 6.3313 | 18.8626 | 4.9537 | 1.6044 | 2.3116 | 4 | 21364 | 17068 | 920 | 204 | 6 | 30781 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | Yes | No
CF2 | North | SHORT RURAL | 643 | 15.782 | 5.7061 | 5.2585 | 6.2759 | 0.46379 | 5 | 205775 | 205775 | 2627 | 2627 | 4 | 15207 | 115 | 0 | 1 | 0 | 0 | 644 | 644 | No | No
CLN12 | Central | SHORT RURAL | 2674.5 | 3.9452 | 12.8579 | 4.725 | 0.58885 | 1.2284 | 3 | 77968 | 77968 | 2763 | 2763 | 5 | 162654 | 570 | 0 | 0 | 0 | 0 | 0 | 0 | No | No
CLN13 | Central | SHORT RURAL | 2217 | 11.1778 | 19.0868 | 4.8012 | 0.9629 | 0.42165 | 6 | 72386 | 72386 | 2640 | 2640 | 8 | 31698 | 158 | 1 | 0 | 2079 | 2079 | 0 | 0 | No | No
CLN14 | Central | SHORT RURAL | 3567.5 | 17.6283 | 18.0948 | 9.6025 | 1.9822 | 1.2895 | 17 | 143710 | 142379 | 3896 | 3889 | 7 | 93487 | 949 | 0 | 0 | 0 | 0 | 0 | 0 | No | No
CLN21 | Central | SHORT RURAL | 4908 | 13.9395 | 23.4834 | 10.7456 | 2.1342 | 3.6745 | 3 | 178561 | 178561 | 6437 | 6437 | 10 | 307425 | 951 | 0 | 0 | 0 | 0 | 0 | 0 | No | No
CLN22 | Central | SHORT RURAL | 897.5 | 79.532 | 0.6487 | 6.6303 | 10.689 | 6.609 | 36 | 222241 | 156025 | 2862 | 2707 | 13 | 137411 | 466 | 0 | 12 | 0 | 0 | 10000 | 10000 | No | No
CLN23 | Central | SHORT RURAL | 3367 | 14.1029 | 22.0869 | 7.8497 | 3.4625 | 11.1555 | 14 | 299045 | 299045 | 9281 | 9281 | 20 | 963478 | 3826 | 1 | 0 | 3255 | 3255 | 0 | 0 | No | No
CNR1 | East | SHORT RURAL | 155 | 9.0282 | 2.0256 | 0.87642 | 2.8544 | 19.0823 | 10 | 113398 | 76122 | 1130 | 816 | 6 | 758082 | 1611 | 13 | 0 | 2033 | 1723 | 0 | 0 | Yes | Yes
CNR2 | East | SHORT RURAL | 1188.5 | 143.5195 | 1.0027 | 2.3244 | 10.1148 | 12.7365 | 18 | 926163 | 628257 | 9962 | 7478 | 25 | 1166216 | 2783 | 13 | 28 | 15374 | 13010 | 28850 | 26747 | Yes | Yes
CNR3 | East | SHORT RURAL | 64.5 | 86.2678 | 0.126 | 0.19053 | 0.6633 | 1.1975 | 15 | 57581 | 42650 | 527 | 401 | 16 | 103955 | 274 | 13 | 3 | 820 | 694 | 68 | 68 | Yes | Yes
CRE21 | Central | SHORT RURAL | 2041 | 17.7927 | 9.9475 | 5.2204 | 1.8343 | 1.0621 | 14 | 111250 | 111250 | 2231 | 2231 | 6 | 64415 | 178 | 1 | 0 | 2089 | 2089 | 0 | 0 | No | No
CRE22 | Central | URBAN | 2651.5 | 8.8768 | 1.8466 | 8.1164 | 1.6663 | 12.9523 | 6 | 98806 | 88017 | 3735 | 3670 | 16 | 768031 | 3063 | 2 | 0 | 5334 | 5334 | 0 | 0 | Yes | No
CRE23 | Central | URBAN | 2043.5 | 4.106 | 10.1395 | 7.0113 | 0.61707 | 2.2253 | 1 | 35166 | 35166 | 1839 | 1839 | 5 | 126815 | 464 | 0 | 0 | 0 | 0 | 0 | 0 | No | No
CRE31 | Central | URBAN | 4829 | 14.6554 | 16.5547 | 9.3739 | 4.4797 | 4.6045 | 10 | 435445 | 434856 | 9900 | 9899 | 7 | 447571 | 1661 | 1 | 0 | 4710 | 4710 | 0 | 0 | No | No
CRE32 | Central | URBAN | 1964.5 | 11.9847 | 2.6787 | 7.8115 | 3.5216 | 3.1928 | 8 | 151619 | 151619 | 3616 | 3616 | 11 | 137464 | 750 | 3 | 0 | 4331 | 4331 | 0 | 0 | No | No
CRE33 | Central | SHORT RURAL | 1978.5 | 76.2011 | 4.0322 | 7.621 | 31.8577 | 3.7429 | 35 | 1648707 | 1028457 | 9553 | 7900 | 12 | 193706 | 788 | 0 | 10 | 0 | 0 | 14361 | 9318 | Yes | No
CYN11 | Central | URBAN | 1440.5 | 5.2803 | 3.3589 | 8.9928 | 1.9112 | 6.3 | 5 | 50292 | 49808 | 245 | 238 | 7 | 165785 | 560 | 0 | 0 | 0 | 0 | 0 | 0 | No | No
CYN12 | Central | URBAN | 2650 | 9.9628 | 3.2968 | 11.241 | 4.1338 | 5.1976 | 10 | 243201 | 166613 | 5879 | 3195 | 7 | 305785 | 1246 | 4 | 0 | 10570 | 10570 | 0 | 0 | No | No
CYN13 | Central | URBAN | 1033.5 | 9.9389 | 1.8194 | 8.4974 | 0.84695 | 9.8097 | 8 | 17559 | 16925 | 194 | 192 | 16 | 203375 | 1738 | 4 | 0 | 4133 | 4133 | 0 | 0 | No | No
CYN14 | Central | URBAN | 3424.5 | 14.3728 | 0.726 | 7.6972 | 2.7423 | 25.4571 | 17 | 227738 | 227738 | 6327 | 6327 | 30 | 2114148 | 6624 | 4 | 0 | 11444 | 11444 | 0 | 0 | Yes | No
CYN21 | Central | URBAN | 2278 | 14.637 | 4.2101 | 8.9547 | 6.6322 | 23.7661 | 15 | 409013 | 381129 | 7073 | 7062 | 22 | 1465675 | 3995 | 1 | 0 | 2249 | 2249 | 0 | 0 | Yes | No
CYN22 | Central | URBAN | 1967.5 | 10.7437 | 1.6159 | 5.792 | 6.8617 | 13.9589 | 14 | 353554 | 332597 | 7184 | 7167 | 13 | 719247 | 2305 | 1 | 1 | 893 | 893 | 590 | 590 | Yes | No
CYN23 | Central | URBAN | 2976 | 16.5481 | 3.1153 | 7.8497 | 22.4649 | 7.5984 | 21 | 1510425 | 480937 | 18317 | 12325 | 13 | 510875 | 2227 | 2 | 2 | 5311 | 2966 | 120 | 120 | Yes | No
CYN24 | Central | URBAN | 1248.5 | 12.2649 | 2.2368 | 12.7271 | 7.0885 | 10.5253 | 14 | 121972 | 121972 | 2768 | 2768 | 7 | 181110 | 768 | 4 | 0 | 5001 | 5001 | 0 | 0 | No | No
CYN31 | Central | URBAN | 2797.5 | 13.6125 | 0.7988 | 6.173 | 1.0953 | 21.0852 | 10 | 96057 | 96057 | 960 | 960 | 17 | 1849112 | 6154 | 4 | 0 | 11170 | 11170 | 0 | 0 | Yes | No
CYN32 | Central | URBAN | 3896 | 18.599 | 1.5407 | 10.2503 | 5.1133 | 15.5874 | 24 | 289587 | 261404 | 1454 | 1413 | 20 | 882773 | 2962 | 8 | 0 | 30662 | 22860 | 0 | 0 | Yes | Yes
CYN33 | Central | SHORT RURAL | 3286 | 24.8782 | 0.5663 | 7.621 | 2.9541 | 4.8945 | 19 | 268718 | 213473 | 5561 | 5493 | 17 | 445222 | 1720 | 3 | 1 | 8626 | 8626 | 630 | 630 | No | No
DRN11 | Central | URBAN | 4794 | 14.7995 | 22.6783 | 17.5284 | 13.8256 | 22.5026 | 23 | 1492659 | 1492211 | 31330 | 31326 | 64 | 2429459 | 9906 | 6 | 3 | 30047 | 30047 | 128 | 86 | Yes | Yes
DRN12 | Central | URBAN | 6348 | 12.8108 | 23.1827 | 19.4336 | 11.5959 | 9.8721 | 79 | 1261167 | 1145500 | 22862 | 22621 | 78 | 1073687 | 4001 | 2 | 30 | 17037 | 17037 | 21613 | 21613 | Yes | Yes
DRN13 | Central | SHORT RURAL | 2454.5 | 23.1415 | 13.1753 | 6.5922 | 4.4399 | 2.7206 | 13 | 292310 | 292310 | 5877 | 5877 | 21 | 179113 | 893 | 0 | 0 | 0 | 0 | 0 | 0 | No | No
DRN14 | Central | SHORT RURAL | 3834 | 69.501 | 20.747 | 8.7642 | 4.2725 | 3.344 | 11 | 396664 | 396664 | 3906 | 3906 | 36 | 310459 | 1147 | 0 | 6 | 0 | 0 | 285 | 285 | No | No
DRN21 | Central | URBAN | 3115.5 | 9.0073 | 13.3338 | 12.1936 | 6.4521 | 0.53753 | 8 | 959238 | 959238 | 12570 | 12570 | 4 | 79915 | 198 | 3 | 0 | 868 | 868 | 0 | 0 | Yes | No
DRN22 | Central | SHORT RURAL | 1273 | 81.3886 | 10.6805 | 5.1823 | 0 | 0 | 5 | 50688 | 50688 | 2648 | 2648 | 5 | 356067 | 3975 | 0 | 0 | 0 | 0 | 0 | 0 | No | No
DRN23 | Central | LONG RURAL | 1294 | 227.794 | 5.003 | 7.6591 | 0 | 0 | 9 | 132212 | 132212 | 2789 | 2789 | 20 | 1781380 | 4905 | 0 | 5 | 0 | 0 | 2932 | 2932 | Yes | No
ELD01 | North | SHORT RURAL | 1017.5 | 74.6715 | 0.2553 | 3.2389 | 7.4517 | 0.36606 | 15 | 436610 | 436610 | 3166 | 3166 | 7 | 21448 | 162 | 2 | 19 | 2046 | 2046 | 7504 | 7504 | No | No
ELM11 | Central | URBAN | 2195 | 6.8466 | 4.2716 | 9.7168 | 1.7001 | 3.6603 | 13 | 80463 | 80463 | 508 | 508 | 9 | 173242 | 675 | 1 | 0 | 2190 | 2190 | 0 | 0 | No | No
ELM12 | Central | SHORT RURAL | 2858.5 | 20.348 | 6.6202 | 7.6591 | 3.1358 | 12.867 | 9 | 223842 | 223842 | 2888 | 2888 | 16 | 918483 | 2734 | 0 | 0 | 0 | 0 | 0 | 0 | No | No
ELM13 | Central | URBAN | 2023.5 | 9.056 | 1.9728 | 4.9537 | 1.1554 | 6.7969 | 7 | 93317 | 93317 | 1147 | 1147 | 23 | 548979 | 2627 | 5 | 0 | 9185 | 7163 | 0 | 0 | Yes | No
ELM15 | Central | SHORT RURAL | 6690.5 | 80.0172 | 15.6518 | 19.0526 | 2.5823 | 11.1653 | 42 | 187428 | 177849 | 1648 | 1642 | 35 | 810393 | 3065 | 6 | 17 | 40212 | 40212 | 21517 | 18247 | No | No
ELM31 | Central | URBAN | 3242 | 14.4456 | 0.9294 | 8.2307 | 4.5975 | 11.8329 | 15 | 304293 | 84858 | 6992 | 3694 | 16 | 783173 | 2451 | 1 | 0 | 3230 | 3230 | 0 | 0 | Yes | No
ELM32 | Central | URBAN | 3276.5 | 21.0347 | 5.1442 | 9.7168 | 7.5384 | 4.7135 | 18 | 471028 | 136882 | 12115 | 8839 | 19 | 294517 | 1559 | 10 | 0 | 39152 | 32600 | 0 | 0 | No | Yes
ELM33 | Central | SHORT RURAL | 2219.5 | 113.1912 | 6.078 | 6.9732 | 23.0614 | 25.4103 | 48 | 1132137 | 782032 | 11768 | 8057 | 105 | 1247447 | 4423 | 12 | 18 | 19549 | 14812 | 4445 | 3942 | Yes | No
ELM34 | Central | URBAN | 3176 | 30.8156 | 1.8292 | 9.9835 | 5.3841 | 13.0072 | 25 | 334967 | 185978 | 7740 | 7426 | 14 | 809224 | 2276 | 3 | 0 | 9544 | 9544 | 0 | 0 | Yes | No
EPG11 | Central | URBAN | 2343.5 | 2.6819 | 4.1746 | 10.2884 | 0.15875 | 1.0966 | 4 | 27659 | 27659 | 108 | 108 | 4 | 191053 | 840 | 0 | 0 | 0 | 0 | 0 | 0 | No | No
EPG12 | Central | URBAN | 3623 | 5.9183 | 2.6 | 12.0412 | 6.4424 | 2.1721 | 14 | 1758391 | 1757679 | 17327 | 17326 | 14 | 592850 | 2065 | 5 | 0 | 30989 | 30989 | 0 | 0 | Yes | Yes
EPG13 | Central | SHORT RURAL | 3686.5 | 27.1689 | 26.0127 | 6.173 | 3.0808 | 1.9087 | 22 | 282074 | 282074 | 742 | 742 | 4 | 174759 | 315 | 5 | 0 | 17933 | 17933 | 0 | 0 | No | No
EPG14 | Central | URBAN | 3105 | 10.7231 | 1.2864 | 11.0505 | 1.8089 | 2.3587 | 8 | 211295 | 80207 | 6110 | 4304 | 5 | 275512 | 963 | 2 | 0 | 6204 | 4016 | 0 | 0 | No | No
EPG22 | Central | URBAN | 236.5 | 1.6093 | 1.7168 | 8.8785 | 0.11229 | 0 | 1 | 536 | 536 | 11 | 11 | 0 | 0 | 0 | 2 | 0 | 475 | 475 | 0 | 0 | No | No
EPG23 | Central | URBAN | 696 | 10.1543 | 5.2279 | 7.9259 | 21.4033 | 0.11662 | 5 | 366709 | 366709 | 2003 | 2003 | 3 | 1998 | 14 | 2 | 0 | 708 | 708 | 0 | 0 | Yes | No
EPG24 | Central | URBAN | 1 | 0 | 0.2154 | 7.621 | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | No | No
EPG31 | Central | URBAN | 2967.5 | 13.6081 | 1.799 | 6.0206 | 0.7346 | 3.4569 | 4 | 78011 | 77859 | 205 | 204 | 9 | 367104 | 1126 | 5 | 0 | 14908 | 14908 | 0 | 0 | No | Yes
EPG32 | Central | SHORT RURAL | 2278.5 | 25.475 | 9.5268 | 5.7158 | 1.4884 | 7.533 | 19 | 105844 | 105155 | 367 | 364 | 26 | 535691 | 1530 | 4 | 0 | 8889 | 8889 | 0 | 0 | No | No
EPG34 | Central | URBAN | 3654.5 | 8.1682 | 8.7002 | 11.8507 | 1.9796 | 1.2879 | 10 | 221749 | 220988 | 8230 | 8229 | 4 | 144262 | 373 | 1 | 0 | 4015 | 4015 | 0 | 0 | No | No
EPG35 | Central | URBAN | 74.5 | 2.1438 | 10.084 | 6.8589 | 0.013545 | 1.9233 | 1 | 21 | 21 | 1 | 1 | 3 | 2982 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | No | No
FGY12 | Central | URBAN | 3983 | 2.147 | 24.2247 | 10.5932 | 0.66679 | 1.4063 | 9 | 57943 | 57943 | 329 | 329 | 5 | 122201 | 606 | 0 | 0 | 0 | 0 | 0 | 0 | No | No
FGY13 | Central | SHORT RURAL | 1544.5 | 18.2595 | 0.7297 | 3.5438 | 3.2826 | 5.5738 | 11 | 299151 | 299151 | 6410 | 6410 | 11 | 507949 | 3327 | 3 | 0 | 4631 | 4631 | 0 | 0 | No | No
FGY14 | Central | URBAN | 2496.5 | 10.9918 | 0.1956 | 10.2884 | 3.4166 | 6.083 | 9 | 220700 | 44080 | 2861 | 318 | 9 | 392942 | 1114 | 1 | 0 | 2483 | 2483 | 0 | 0 | No | No
FGY21 | Central | SHORT RURAL | 2500.5 | 20.623 | 12.5621 | 8.9547 | 3.4547 | 1.6977 | 14 | 150623 | 22460 | 2648 | 147 | 7 | 74020 | 199 | 12 | 0 | 30050 | 25048 | 0 | 0 | No | Yes
FGY22 | Central | URBAN | 3310.5 | 6.1188 | 15.0322 | 9.8311 | 0.089377 | 15.429 | 4 | 4440 | 4440 | 63 | 63 | 9 | 766471 | 1962 | 10 | 0 | 33340 | 33340 | 0 | 0 | No | Yes
FGY23 | Central | URBAN | 992 | 10.0976 | 0.2703 | 4.0772 | 1.952 | 3.0101 | 10 | 89664 | 31956 | 244 | 196 | 7 | 138270 | 535 | 1 | 0 | 995 | 995 | 0 | 0 | No | No
FGY31 | Central | URBAN | 1167 | 9.6856 | 6.2424 | 9.5263 | 4.883 | 7.3771 | 7 | 131138 | 129168 | 781 | 762 | 3 | 198121 | 750 | 2 | 0 | 2896 | 2896 | 0 | 0 | Yes | No
FGY32 | Central | URBAN | 1328 | 8.8205 | 0.635 | 5.6777 | 5.0589 | 0.48027 | 9 | 193701 | 192127 | 839 | 821 | 4 | 18389 | 139 | 1 | 0 | 718 | 718 | 0 | 0 | No | No
FGY33 | Central | URBAN | 1887.5 | 16.0707 | 0.8486 | 6.7827 | 31.0538 | 2.205 | 30 | 1529952 | 1048714 | 11328 | 7912 | 9 | 108634 | 513 | 5 | 0 | 5577 | 5225 | 0 | 0 | Yes | No
FGY34 | Central | URBAN | 3563.5 | 24.1991 | 1.1752 | 9.2595 | 7.8729 | 4.7051 | 32 | 763598 | 763598 | 6537 | 6537 | 20 | 456348 | 1983 | 3 | 0 | 10275 | 10275 | 0 | 0 | Yes | No
FTR12 | East | LONG RURAL | 1654.5 | 465.0014 | 1.1492 | 4.0772 | 20.3326 | 21.7532 | 127 | 1074639 | 652539 | 10435 | 8556 | 84 | 1149720 | 5603 | 5 | 64 | 6788 | 6547 | 16140 | 13712 | Yes | No
FTR21 | East | LONG RURAL | 2387 | 396.2121 | 0.6587 | 4.9918 | 18.6859 | 17.4485 | 91 | 1699167 | 1334785 | 11958 | 9467 | 132 | 1586640 | 6548 | 3 | 76 | 4790 | 4790 | 59841 | 56611 | Yes | Yes
FTR22 | East | SHORT RURAL | 1259.5 | 125.7317 | 0.9428 | 3.1627 | 12.7082 | 4.8897 | 43 | 679481 | 347277 | 4529 | 2674 | 32 | 261441 | 1594 | 5 | 22 | 5038 | 5038 | 7440 | 7440 | Yes | No
FTR23 | East | LONG RURAL | 3389 | 417.0862 | 3.8743 | 9.5644 | 12.1353 | 23.785 | 91 | 745660 | 684211 | 19184 | 15499 | 92 | 1461486 | 6806 | 7 | 58 | 22936 | 22936 | 48369 | 48369 | No | No
HPK11 | Central | URBAN | 4035 | 5.741 | 10.0819 | 8.0402 | 0.81287 | 5.4706 | 6 | 85505 | 61247 | 4327 | 284 | 2 | 575445 | 1722 | 0 | 0 | 0 | 0 | 0 | 0 | No | No
HPK12 | Central | URBAN | 1570.5 | 8.6655 | 7.4422 | 8.7642 | 0.49077 | 2.3821 | 10 | 20807 | 11543 | 1885 | 341 | 4 | 100992 | 308 | 1 | 0 | 1594 | 1594 | 0 | 0 | No | No
HPK13 | Central | URBAN | 1930.5 | 8.6354 | 6.7197 | 5.068 | 5.3129 | 6.1478 | 4 | 294910 | 30183 | 3984 | 106 | 10 | 341252 | 1339 | 0 | 0 | 0 | 0 | 0 | 0 | Yes | No
HPK14 | Central | URBAN | 3962 | 9.423 | 11.7603 | 9.3358 | 0.72316 | 1.1414 | 6 | 60281 | 36431 | 4075 | 100 | 7 | 95144 | 488 | 2 | 0 | 7921 | 7921 | 0 | 0 | No | No
HPK21 | Central | URBAN | 3121.5 | 9.616 | 10.3121 | 7.4305 | 0.85872 | 1.4609 | 4 | 91751 | 74135 | 4975 | 2039 | 7 | 156093 | 829 | 0 | 0 | 0 | 0 | 0 | 0 | No | No
HPK22 | Central | URBAN | 4035.5 | 8.3511 | 20.0802 | 9.2214 | 2.9059 | 2.2855 | 9 | 210515 | 40097 | 8206 | 130 | 8 | 165575 | 645 | 0 | 0 | 0 | 0 | 0 | 0 | No | No
HPK23 | Central | URBAN | 3010.5 | 8.4389 | 13.3851 | 10.6694 | 0.3744 | 1.0616 | 6 | 23411 | 5051 | 3162 | 102 | 6 | 66379 | 451 | 1 | 0 | 3000 | 3000 | 0 | 0 | No | No
HPK24 | Central | URBAN | 1442.5 | 8.6775 | 3.7649 | 7.3924 | 0.80269 | 4.1728 | 5 | 24026 | 15344 | 1562 | 115 | 7 | 124900 | 736 | 0 | 0 | 0 | 0 | 0 | 0 | No | No
KLK1 | Central | SHORT RURAL | 1419.5 | 182.7492 | 8.6428 | 3.0484 | 10.1658 | 29.9694 | 46 | 610875 | 426153 | 2719 | 1409 | 88 | 1800900 | 5555 | 3 | 30 | 4277 | 4277 | 3412 | 2539 | Yes | No
KLK2 | Central | SHORT RURAL | 775 | 86.541 | 0.3388 | 1.6385 | 7.1356 | 0.78185 | 28 | 490679 | 344179 | 2914 | 2039 | 25 | 53764 | 528 | 2 | 6 | 1553 | 1553 | 993 | 993 | Yes | No
KLK3 | Central | SHORT RURAL | 138.5 | 59.2753 | 0 | 0.53347 | 0.10712 | 0.74205 | 6 | 6386 | 6386 | 57 | 57 | 13 | 44236 | 307 | 3 | 2 | 420 | 420 | 62 | 62 | No | No
KLO11 | Central | URBAN | 0.5 | 0 | 0.1297 | 0.5 | 0.043792 | 0.059601 | 1 | 313 | 313 | 1 | 1 | 2 | 426 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Yes | No
KLO14 | Central | LONG RURAL | 2995 | 250.1541 | 17.6292 | 6.6684 | 21.2192 | 15.0098 | 70 | 1172116 | 1172116 | 13289 | 13289 | 45 | 829118 | 3124 | 7 | 39 | 21336 | 21336 | 23505 | 23505 | No | No
KLO24 | Central | SHORT RURAL | 3429 | 75.2733 | 26.588 | 7.621 | 3.8697 | 6.0278 | 20 | 252268 | 252268 | 4036 | 4036 | 22 | 392957 | 1452 | 8 | 0 | 27288 | 27288 | 0 | 0 | No | No
KMS1 | North | SHORT RURAL | 2433 | 182.6513 | 9.3889 | 7.1638 | 1.176 | 17.9157 | 39 | 63542 | 56671 | 787 | 683 | 68 | 968053 | 2999 | 6 | 26 | 14321 | 14321 | 6557 | 6203 | No | No
KMS21 | North | SHORT RURAL | 1110.5 | 79.1469 | 3.9888 | 2.6674 | 5.4759 | 2.4623 | 13 | 342589 | 342434 | 1253 | 1252 | 29 | 154052 | 556 | 2 | 6 | 2222 | 2222 | 1020 | 1020 | No | No
LDL11 | Central | URBAN | 2453 | 15.3258 | 5.509 | 7.8115 | 1.6719 | 27.5982 | 6 | 98658 | 98658 | 2743 | 2743 | 24 | 1628542 | 4775 | 4 | 0 | 9798 | 9798 | 0 | 0 | Yes | No
LDL12 | Central | URBAN | 935.5 | 5.878 | 0.763 | 8.1926 | 2.0629 | 16.2139 | 6 | 30631 | 30631 | 293 | 293 | 8 | 240748 | 631 | 1 | 0 | 929 | 929 | 0 | 0 | Yes | No
LDL13 | Central | SHORT RURAL | 3914.5 | 135.2086 | 0.5644 | 8.7261 | 38.3573 | 21.0959 | 64 | 2727246 | 728917 | 10086 | 3477 | 48 | 1499940 | 5302 | 0 | 26 | 0 | 0 | 22806 | 20224 | Yes | No
LDL14 | Central | SHORT RURAL | 2371 | 133.6444 | 3.9992 | 8.1545 | 4.4757 | 10.0713 | 44 | 203748 | 202142 | 940 | 938 | 16 | 458471 | 1823 | 2 | 11 | 4727 | 4727 | 2396 | 2396 | No | No
LDL21 | Central | SHORT RURAL | 2340.5 | 37.8323 | 1.6396 | 7.4686 | 6.9804 | 12.2355 | 33 | 331153 | 272371 | 1726 | 1640 | 12 | 580455 | 2089 | 2 | 10 | 4690 | 4690 | 7457 | 6711 | No | No
LDL22 | Central | SHORT RURAL | 3307 | 110.0261 | 7.671 | 11.241 | 2.9699 | 16.9069 | 41 | 79548 | 79548 | 1485 | 1485 | 32 | 452850 | 1852 | 3 | 12 | 9912 | 9912 | 8115 | 8115 | No | No
LDL23 | Central | LONG RURAL | 4555.5 | 211.6683 | 8.2566 | 13.9084 | 13.7085 | 39.8596 | 68 | 711885 | 377339 | 8926 | 6598 | 67 | 2069918 | 6713 | 12 | 26 | 52779 | 50069 | 10166 | 7244 | No | No
LDL24 | Central | URBAN | 6367 | 44.6261 | 15.7673 | 19.0526 | 8.0276 | 12.6459 | 37 | 692076 | 409795 | 9987 | 8123 | 32 | 1090229 | 4825 | 1 | 10 | 6409 | 6409 | 18074 | 18074 | Yes | No
LGA11 | East | LONG RURAL | 1668 | 251.1107 | 0.1939 | 3.2008 | 12.866 | 44.1437 | 70 | 846212 | 580440 | 5358 | 4146 | 64 | 2903382 | 6696 | 4 | 25 | 4903 | 3635 | 7868 | 5868 | Yes | No
LGA12 | East | SHORT RURAL | 968 | 182.4012 | 1.6785 | 4.0772 | 5.2528 | 30.2631 | 39 | 155197 | 112410 | 3803 | 2820 | 63 | 894137 | 3507 | 7 | 27 | 5798 | 5798 | 13186 | 13168 | Yes | Yes
LGA13 | East | LONG RURAL | 923 | 288.9234 | 0.1403 | 2.3244 | 7.8659 | 11.0354 | 55 | 479390 | 153180 | 2651 | 1528 | 95 | 672556 | 2555 | 0 | 17 | 0 | 0 | 817 | 817 | Yes | No
LGA14 | East | LONG RURAL | 1466 | 210.5545 | 1.1615 | 3.1627 | 9.8112 | 2.6392 | 52 | 588072 | 119646 | 4979 | 3395 | 27 | 158191 | 700 | 3 | 25 | 4417 | 4417 | 3546 | 3337 | No | No
LGA21 | East | SHORT RURAL | 1688 | 82.9811 | 1.8291 | 3.5438 | 5.7402 | 7.6579 | 13 | 359535 | 359535 | 5108 | 5108 | 17 | 479649 | 1722 | 6 | 2 | 8450 | 6770 | 59 | 59 | No | No
LGA22 | East | SHORT RURAL | 1971.5 | 56.8601 | 1.2226 | 5.9444 | 3.3829 | 13.0208 | 18 | 150935 | 150935 | 2365 | 2365 | 23 | 580954 | 2353 | 4 | 3 | 6518 | 6518 | 71 | 71 | No | No
LGA23 | East | LONG RURAL | 1496.5 | 322.9873 | 0.518 | 3.6962 | 12.2964 | 18.0101 | 55 | 622999 | 129017 | 2368 | 1024 | 56 | 912483 | 2925 | 1 | 28 | 706 | 0 | 11190 | 10068 | Yes | No
LGA24 | East | SHORT RURAL | 1086 | 174.4892 | 17.2181 | 5.0299 | 9.6128 | 27.7024 | 37 | 228985 | 219545 | 1737 | 1663 | 30 | 659894 | 1907 | 0 | 8 | 0 | 0 | 3300 | 2812 | Yes | No
LGA25 | East | SHORT RURAL | 1 | 0 | 1.3046 | 0.02 | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | No | No
LGA41 | East | URBAN | 2 | 0 | 1.3198 | 9.0309 | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | No | No
LLG11 | Central | SHORT RURAL | 963 | 156.4018 | 0.4629 | 2.9341 | 6.1189 | 6.5936 | 31 | 304173 | 94236 | 3455 | 2282 | 54 | 327771 | 1601 | 3 | 7 | 2881 | 2881 | 805 | 769 | Yes | No
LLG12 | East | SHORT RURAL | 1361 | 188.2085 | 2.9879 | 4.4202 | 7.1849 | 19.9339 | 36 | 275105 | 274869 | 5804 | 5803 | 73 | 763253 | 7275 | 1 | 10 | 1358 | 1358 | 3634 | 3634 | Yes | No
LLG13 | East | SHORT RURAL | 1233 | 110.9468 | 3.3641 | 7.3924 | 10.7393 | 12.7775 | 42 | 285705 | 195780 | 5195 | 5099 | 43 | 339930 | 3483 | 5 | 14 | 4922 | 4922 | 11076 | 10319 | No | Yes
LLG14 | Central | SHORT RURAL | 2289 | 134.5075 | 3.6072 | 7.3543 | 12.1576 | 1.4334 | 61 | 560400 | 436399 | 9669 | 9433 | 28 | 66074 | 339 | 3 | 2 | 6852 | 6852 | 1833 | 1833 | No | No
LYD11 | Central | SHORT RURAL | 2324 | 10.5844 | 9.8524 | 4.6488 | 3.7916 | 0.72332 | 4 | 334110 | 11348 | 2904 | 86 | 4 | 63738 | 591 | 4 | 0 | 9227 | 9227 | 0 | 0 | No | No
LYD12 | Central | URBAN | 2004.5 | 0 | 10.1166 | 4.0772 | 2.3214 | 0 | 3 | 264440 | 114065 | 4026 | 2021 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | No | No
LYD13 | Central | URBAN | 1971.5 | 10.2116 | 9.6064 | 7.2019 | 10.2417 | 0.33114 | 11 | 621855 | 134995 | 6111 | 2168 | 4 | 20106 | 155 | 1 | 0 | 1968 | 1968 | 0 | 0 | Yes | No
LYD14 | Central | SHORT RURAL | 1077.5 | 31.7695 | 10.344 | 4.9537 | 8.8864 | 4.385 | 25 | 333102 | 248175 | 3001 | 1909 | 24 | 164369 | 2560 | 1 | 10 | 631 | 631 | 510 | 510 | No | No
LYS36 | East | SHORT RURAL | 1.5 | 4.1692 | 1.0036 | 0.01 | 0 | 1.5591 | 0 | 0 | 0 | 0 | 0 | 2 | 1057 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Yes | No
MBY11 | North | SHORT RURAL | 1124 | 107.7583 | 1.4878 | 3.1246 | 7.4194 | 7.3189 | 18 | 545729 | 544505 | 4393 | 4387 | 36 | 538342 | 2225 | 7 | 0 | 5743 | 4627 | 0 | 0 | Yes | No
MBY12 | North | SHORT RURAL | 703.5 | 22.0002 | 0.5647 | 2.0577 | 0.52886 | 1.5321 | 12 | 32719 | 22891 | 267 | 225 | 14 | 94786 | 444 | 1 | 0 | 701 | 701 | 0 | 0 | No | No
MBY13 | North | SHORT RURAL | 199 | 0 | 51.317 | 4.1535 | 0.019695 | 0 | 1 | 573 | 573 | 7 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | No | No
MBY14 | North | SHORT RURAL | 2 | 8.7908 | 0.0986 | 1.2956 | 0.68544 | 0.0035763 | 1 | 15333 | 0 | 646 | 0 | 1 | 80 | 1 | 2 | 0 | 1431 | 1431 | 0 | 0 | Yes | Yes
MDG1 | Central | SHORT RURAL | 759 | 11.8143 | 0.101 | 1.1432 | 5.5815 | 21.7693 | 12 | 272987 | 145092 | 993 | 914 | 24 | 1064727 | 3561 | 12 | 0 | 8840 | 8840 | 0 | 0 | Yes | No
MDI1 | North | SHORT RURAL | 56 | 24.7961 | 0 | 0.22863 | 0 | 0.56914 | 0 | 0 | 0 | 0 | 0 | 3 | 32613 | 88 | 2 | 0 | 110 | 110 | 0 | 0 | No | No
MFA14 | East | URBAN | 29 | 0.8698 | 0.0777 | 7.6591 | 15.4171 | 10.4577 | 3 | 7666 | 6390 | 60 | 31 | 1 | 5200 | 26 | 1 | 0 | 29 | 29 | 0 | 0 | Yes | No
MFA21 | East | LONG RURAL | 2375 | 432.8184 | 1.3081 | 7.5448 | 14.5721 | 15.9224 | 33 | 806309 | 66609 | 6184 | 408 | 54 | 881025 | 2853 | 1 | 38 | 2385 | 2385 | 26606 | 26296 | No | No
MFA22 | East | LONG RURAL | 1588 | 319.0159 | 0.2458 | 6.2111 | 23.6172 | 34.375 | 49 | 863940 | 544215 | 6667 | 4158 | 56 | 1257470 | 4864 | 3 | 26 | 4744 | 4744 | 8093 | 8093 | Yes | No
MFA23 | East | SHORT RURAL | 472 | 126.3895 | 1.2095 | 2.0196 | 2.7051 | 20.0237 | 22 | 77843 | 8447 | 553 | 86 | 22 | 576207 | 1532 | 2 | 9 | 944 | 944 | 592 | 592 | Yes | No
MFA31 | East | SHORT RURAL | 2110 | 25.5089 | 0.6233 | 4.6869 | 1.3256 | 9.4239 | 9 | 108499 | 10749 | 2257 | 132 | 18 | 771345 | 2503 | 1 | 0 | 2101 | 2101 | 0 | 0 | No | No
MFA34 | East | SHORT RURAL | 1495 | 183.7489 | 1.5858 | 7.4686 | 6.8511 | 8.2407 | 56 | 205255 | 76208 | 2312 | 554 | 37 | 246886 | 806 | 4 | 0 | 5739 | 4488 | 0 | 0 | No | No
MJG11 | North | SHORT RURAL | 1315 | 77.4636 | 22.8062 | 13.2987 | 10.5618 | 0.23904 | 13 | 310700 | 79691 | 3348 | 1190 | 12 | 7032 | 98 | 9 | 5 | 10834 | 9504 | 914 | 914 | No | No
MOE13 | East | SHORT RURAL | 3020.5 | 32.8113 | 0.3707 | 5.7158 | 5.2356 | 14.8839 | 19 | 443776 | 443776 | 6972 | 6972 | 33 | 1261572 | 4404 | 1 | 0 | 4006 | 4006 | 0 | 0 | No | No
MOE14 | East | SHORT RURAL | 1810.5 | 151.4454 | 10.1119 | 3.3914 | 14.9468 | 4.1315 | 44 | 990781 | 359694 | 10996 | 9836 | 22 | 273862 | 1034 | 8 | 9 | 11518 | 4055 | 3429 | 2966 | Yes | No
MOE21 | East | SHORT RURAL | 685.5 | 187.5574 | 0.5684 | 2.5149 | 25.0214 | 6.111 | 45 | 982978 | 307805 | 6493 | 4689 | 27 | 240074 | 918 | 4 | 31 | 2171 | 2171 | 5525 | 5161 | Yes | No
MOE22 | East | LONG RURAL | 2538.5 | 258.092 | 3.1097 | 5.1061 | 12.02 | 8.7861 | 49 | 807855 | 807855 | 16851 | 16851 | 127 | 590503 | 2431 | 5 | 11 | 10170 | 10170 | 5326 | 5326 | No | No
MOE23 | East | SHORT RURAL | 1077.5 | 9.5229 | 0.7374 | 1.6766 | 2.0321 | 2.4231 | 6 | 217499 | 217499 | 4181 | 4181 | 11 | 259345 | 2989 | 2 | 0 | 998 | 998 | 0 | 0 | No | No
MOE24 | East | SHORT RURAL | 2067.5 | 17.3281 | 1.5097 | 4.6488 | 6.8988 | 3.7228 | 13 | 467637 | 294937 | 7330 | 5247 | 15 | 252348 | 1146 | 2 | 0 | 4133 | 4133 | 0 | 0 | No | No
MOE31 | East | LONG RURAL | 2374.5 | 217.4182 | 0.7938 | 7.0113 | 15.0915 | 13.0782 | 73 | 827316 | 568104 | 7785 | 7193 | 82 | 716951 | 2364 | 1 | 45 | 0 | 0 | 13282 | 12172 | No | No
MOE32 | East | SHORT RURAL | 986.5 | 136.6437 | 3.4535 | 3.277 | 4.816 | 3.4833 | 26 | 333088 | 307608 | 2459 | 2438 | 37 | 240914 | 882 | 3 | 9 | 2964 | 2964 | 244 | 221 | No | No
MSD1 | North | LONG RURAL | 1927.5 | 317.7006 | 3.1023 | 4.7631 | 2.6138 | 46.7123 | 39 | 230978 | 37468 | 4129 | 220 | 35 | 4127913 | 10620 | 6 | 24 | 11569 | 9646 | 10873 | 8011 | Yes | No
MSD2 | North | LONG RURAL | 1600 | 399.6675 | 1.6741 | 4.6107 | 1.5148 | 4.6508 | 57 | 137948 | 123172 | 2924 | 1263 | 30 | 423545 | 2316 | 5 | 12 | 8002 | 8002 | 8058 | 7990 | No | No
MSD4 | North | LONG RURAL | 2411 | 220.1383 | 1.9641 | 8.6499 | 12.1624 | 7.7129 | 30 | 596909 | 591795 | 10203 | 7783 | 34 | 378533 | 1316 | 5 | 7 | 10793 | 10793 | 2845 | 2845 | No | No
MVE01 | North | SHORT RURAL | 1126.5 | 168.3312 | 6.7376 | 2.7055 | 10.0012 | 0.6711 | 29 | 711120 | 153413 | 6175 | 3633 | 25 | 47717 | 559 | 6 | 18 | 6769 | 6769 | 6186 | 5388 | Yes | No
MWE1 | East | URBAN | 1 | 1.0696 | 0.3018 | 1.01 | 0 | 0.0024771 | 0 | 0 | 0 | 0 | 0 | 2 | 224 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | No | No
MWE2 | East | SHORT RURAL | 5 | 2.0761 | 0.138 | 0.425 | 0 | 0.11506 | 0 | 0 | 0 | 0 | 0 | 2 | 2925 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | No | No
MWE3 | East | URBAN | 8 | 1.7221 | 0.3014 | 1 | 0 | 1.0957 | 0 | 0 | 0 | 0 | 0 | 0 | 4736 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Yes | No
MWE6 | East | URBAN | 20 | 3.0744 | 0.1826 | 1.0605 | 0 | 0.22893 | 0 | 0 | 0 | 0 | 0 | 0 | 8037 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | Yes | No
MWTS11 | East | SHORT RURAL | 1958.5 | 22.3974 | 3.5718 | 4.4583 | 6.4928 | 7.1149 | 12 | 425371 | 423987 | 3333 | 3329 | 13 | 466129 | 1321 | 3 | 0 | 4083 | 4083 | 0 | 0 | No | No
MWTS12 | East | URBAN | 1077.5 | 8.1149 | 1.2808 | 4.344 | 1.5963 | 3.0567 | 4 | 49540 | 48321 | 812 | 811 | 4 | 94866 | 420 | 1 | 0 | 1082 | 1082 | 0 | 0 | No | No
MWTS13 | East | SHORT RURAL | 873.5 | 17.7146 | 0.2332 | 2.6293 | 0 | 0.2171 | 0 | 0 | 0 | 0 | 0 | 1 | 18685 | 101 | 1 | 0 | 860 | 860 | 0 | 0 | No | No
MWTS14 | East | SHORT RURAL | 1272 | 197.5429 | 2.2744 | 1.9815 | 8.4749 | 7.6062 | 33 | 596292 | 287633 | 3740 | 2461 | 47 | 535171 | 1542 | 1 | 6 | 1274 | 1274 | 3175 | 2386 | Yes | No
MWTS21 | East | URBAN | 2916 | 17.9946 | 0.649 | 8.2688 | 3.8622 | 3.5233 | 10 | 250609 | 250609 | 2340 | 2340 | 10 | 228616 | 985 | 1 | 0 | 955 | 955 | 0 | 0 | No | No
MWTS22 | East | SHORT RURAL | 888 | 23.6792 | 0.8168 | 6.1349 | 0.26524 | 0.84338 | 5 | 6374 | 6374 | 67 | 67 | 6 | 20267 | 82 | 0 | 0 | 0 | 0 | 0 | 0 | No | No
MWTS24 | East | SHORT RURAL | 756 | 51.4054 | 4.3444 | 5.8682 | 6.1636 | 12.147 | 26 | 87831 | 56103 | 643 | 619 | 14 | 173094 | 524 | 5 | 2 | 3798 | 3798 | 24 | 24 | No | No
MWTS31 | East | SHORT RURAL | 700.5 | 124.0294 | 0.1293 | 1.3337 | 7.451 | 3.7702 | 50 | 581837 | 499683 | 3227 | 2908 | 38 | 294414 | 1254 | 0 | 39 | 0 | 0 | 8269 | 7004 | Yes | No
MWTS32 | East | SHORT RURAL | 523 | 53.5768 | 3.5706 | 4.7631 | 386.3439 | 691.3969 | 19 | 487200 | 278966 | 4432 | 2531 | 31 | 871888 | 2525 | 10 | 0 | 13039 | 13039 | 0 | 0 | Yes | Yes
MWTS34 | East | SHORT RURAL | 1582 | 24.2436 | 1.0659 | 3.0865 | 1.7798 | 2.8615 | 10 | 180757 | 48689 | 1323 | 716 | 3 | 290617 | 790 | 3 | 0 | 4219 | 2621 | 0 | 0 | No | No
MWTS35 | East | SHORT RURAL | 0.5 | 0 | 6.0281 | 0.038105 | 46.589 | 0 | 1 | 807 | 807 | 3 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Yes | No
MYT1 | North | SHORT RURAL | 326.5 | 52.1073 | 1.0059 | 0.83831 | 0.33992 | 0.8784 | 8 | 30856 | 30530 | 1015 | 689 | 9 | 79736 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | No | No
MYT2 | North | SHORT RURAL | 1723 | 102.2144 | 1.3588 | 5.9063 | 2.4445 | 6.4322 | 15 | 64044 | 58572 | 2342 | 570 | 22 | 168515 | 2070 | 1 | 4 | 1726 | 1726 | 163 | 163 | No | No
MYT7 | North | LONG RURAL | 3002 | 352.4798 | 5.1382 | 8.4974 | 4.5534 | 8.2091 | 61 | 252532 | 115152 | 6430 | 813 | 74 | 455274 | 2138 | 0 | 38 | 0 | 0 | 19714 | 19714 | No | No
MYT8 | North | SHORT RURAL | 690.5 | 103.0085 | 0.6257 | 2.0196 | 1.7567 | 1.0081 | 29 | 112887 | 112200 | 1690 | 1003 | 27 | 64779 | 314 | 15 | 0 | 10329 | 10329 | 0 | 0 | No | Yes
NLA31 | East | LONG RURAL | 895 | 209.9418 | 0.2372 | 2.4006 | 13.56 | 11.1666 | 28 | 886765 | 522269 | 6304 | 4840 | 39 | 730251 | 1827 | 9 | 14 | 7879 | 6089 | 5429 | 5429 | Yes | No
NLA32 | East | SHORT RURAL | 1454.5 | 79.4143 | 0.0265 | 3.5438 | 9.9217 | 18.3006 | 28 | 608959 | 481874 | 10400 | 8946 | 38 | 1123224 | 2934 | 9 | 17 | 13081 | 10165 | 12821 | 12821 | Yes | Yes
NLA34 | East | SHORT RURAL | 1246.5 | 136.0259 | 1.4438 | 2.5911 | 6.5124 | 3.2999 | 29 | 516308 | 317193 | 7934 | 6622 | 42 | 261621 | 841 | 9 | 5 | 11209 | 8711 | 1451 | 1451 | Yes | No
NRN11 | Central | URBAN | 68.5 | 2.2201 | 4.7282 | 4.1535 | 0.0037325 | 0.0037744 | 1 | 178 | 178 | 2 | 2 | 1 | 180 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | No | No
NRN12 | Central | URBAN | 917.5 | 3.7115 | 6.1945 | 11.2791 | 0.28414 | 17.6138 | 1 | 2631 | 2631 | 7 | 7 | 7 | 163095 | 748 | 0 | 0 | 0 | 0 | 0 | 0 | No | No
NRN13 | Central | URBAN | 2569 | 0 | 10.9939 | 6.173 | 0.109 | 0.40491 | 6 | 10539 | 10539 | 176 | 176 | 2 | 39150 | 87 | 0 | 0 | 0 | 0 | 0 | 0 | No | No
NRN14 | Central | URBAN | 2116 | 11.2348 | 9.5635 | 6.3254 | 1.8009 | 4.6201 | 8 | 105424 | 50671 | 536 | 324 | 7 | 270462 | 818 | 0 | 0 | 0 | 0 | 0 | 0 | No | No
NRN15 | Central | URBAN | 3.5 | 0.044 | 0.1311 | 4.001 | 0 | 0.01754 | 0 | 0 | 0 | 0 | 0 | 1 | 417 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | No | No
NW13 | Central | URBAN | 18 | 0.1103 | 0 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | No | No
OFR21 | Central | SHORT RURAL | 2749 | 24.5844 | 13.7752 | 9.9073 | 1.142 | 2.1892 | 6 | 50881 | 49937 | 2822 | 2820 | 10 | 97541 | 267 | 6 | 0 | 16452 | 16452 | 0 | 0 | No | No
OFR22 | Central | SHORT RURAL | 3761 | 26.2515 | 17.9454 | 7.24 | 0.10027 | 1.4223 | 4 | 10226 | 10226 | 112 | 112 | 7 | 145047 | 542 | 0 | 0 | 0 | 0 | 0 | 0 | No | No
OFR23 | Central | LONG RURAL | 6094.5 | 299.8219 | 20.9819 | 19.0526 | 84.3132 | 21.7206 | 127 | 5126419 | 1823519 | 38686 | 27691 | 122 | 1320659 | 4651 | 9 | 34 | 49518 | 44016 | 13193 | 12702 | Yes | No
OFR24 | Central | URBAN | 819.5 | 7.7637 | 4.1245 | 4.6869 | 3.0773 | 0.87037 | 3 | 80732 | 80732 | 869 | 869 | 6 | 22834 | 118 | 1 | 0 | 796 | 796 | 0 | 0 | No | No
PHI11 | East | SHORT RURAL | 1309 | 25.5782 | 0.5419 | 2.8579 | 2.9048 | 4.303 | 18 | 304945 | 296173 | 5800 | 5794 | 14 | 451730 | 1708 | 7 | 0 | 9141 | 5220 | 0 | 0 | No | No
PHI12 | East | SHORT RURAL | 4124 | 61.3538 | 10.586 | 8.5737 | 6.8519 | 5.4001 | 42 | 846112 | 608267 | 16220 | 15620 | 20 | 666841 | 2482 | 5 | 30 | 20678 | 8246 | 94677 | 91495 | No | Yes
PHI13 | East | URBAN | 4201.5 | 24.7714 | 4.0585 | 10.5932 | 4.4272 | 3.5573 | 22 | 345503 | 271492 | 11438 | 11226 | 8 | 277614 | 1136 | 6 | 6 | 25175 | 12530 | 11929 | 11929 | No | Yes
PHM11 | Central | URBAN | 1572 | 6.5613 | 4.4697 | 9.7549 | 0.91612 | 4.145 | 7 | 23758 | 23758 | 237 | 237 | 5 | 107492 | 346 | 1 | 0 | 1568 | 1568 | 0 | 0 | No | No
PHM12 | Central | SHORT RURAL | 660 | 50.4553 | 5.2034 | 7.1638 | 2.715 | 1.0626 | 26 | 35123 | 25738 | 346 | 284 | 4 | 13746 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | No | No
PHM14 | Central | LONG RURAL | 2478 | 209.8798 | 3.3002 | 9.7168 | 27.656 | 26.6528 | 68 | 1211970 | 480143 | 3053 | 1997 | 95 | 1168006 | 6464 | 3 | 34 | 6824 | 6824 | 15237 | 13153 | Yes | No
PHM31 | Central | SHORT RURAL | 546.5 | 50.4159 | 1.6489 | 2.0958 | 0.030378 | 0.91438 | 8 | 1301 | 1301 | 14 | 14 | 13 | 39160 | 156 | 5 | 0 | 3194 | 3194 | 0 | 0 | No | No
PHM32 | Central | URBAN | 3621 | 10.9971 | 17.0635 | 9.9073 | 0.003696 | 3.5124 | 0 | 296 | 296 | 3 | 3 | 4 | 281291 | 1046 | 0 | 0 | 0 | 0 | 0 | 0 | No | No
PHM33 | Central | SHORT RURAL | 2111 | 28.1036 | 7.1654 | 3.3151 | 2.5692 | 0.5233 | 7 | 263340 | 202968 | 2283 | 2244 | 14 | 53638 | 287 | 0 | 0 | 0 | 0 | 0 | 0 | No | No
PHM34 | Central | URBAN | 2529 | 9.8058 | 4.0113 | 5.7158 | 0.76426 | 4.7962 | 4 | 55865 | 55865 | 2647 | 2647 | 8 | 350586 | 2725 | 3 | 0 | 11058 | 11058 | 0 | 0 | No | No
RWN22 | Central | URBAN | 2874 | 15.1981 | 1.5631 | 6.9351 | 4.9417 | 16.0707 | 15 | 468544 | 226914 | 7672 | 4950 | 18 | 1523719 | 5182 | 8 | 0 | 18741 | 18516 | 0 | 0 | Yes | Yes
RWN24 | Central | SHORT RURAL | 4499 | 52.1729 | 7.926 | 12.7652 | 27.5423 | 49.9865 | 59 | 1719447 | 1204176 | 21475 | 17099 | 67 | 3120625 | 10157 | 18 | 17 | 74060 | 74060 | 7633 | 5875 | Yes | Yes
RWN26 | Central | SHORT RURAL | 2754 | 41.798 | 6.9312 | 10.4408 | 19.7961 | 22.8336 | 51 | 1220245 | 806177 | 17394 | 14421 | 64 | 1407481 | 4706 | 5 | 6 | 11405 | 8508 | 10162 | 8503 | Yes | No
RWN31 | Central | SHORT RURAL | 2513.5 | 51.1029 | 3.8794 | 7.8497 | 16.8361 | 10.4739 | 23 | 1092665 | 937172 | 11482 | 9909 | 42 | 679756 | 2694 | 5 | 3 | 11614 | 4162 | 2102 | 1403 | Yes | No
RWN32 | Central | URBAN | 2317.5 | 10.8637 | 0.3948 | 5.2585 | 5.7432 | 3.4714 | 11 | 501689 | 501689 | 8186 | 8186 | 11 | 303240 | 1426 | 2 | 0 | 2315 | 2315 | 0 | 0 | Yes | No
RWN33 | Central | URBAN | 4834.5 | 43.0536 | 7.8378 | 16.6519 | 19.3451 | 27.1739 | 24 | 937992 | 404135 | 14011 | 8362 | 25 | 1317589 | 3633 | 1 | 9 | 4860 | 4860 | 14342 | 12811 | Yes | No
RWT11 | Central | URBAN | 2440.5 | 16.7141 | 1.1672 | 6.2873 | 2.898 | 22.0944 | 16 | 207487 | 163216 | 5357 | 2924 | 26 | 1581896 | 5105 | 4 | 0 | 8404 | 8404 | 0 | 0 | Yes | No
RWT14 | Central | URBAN | 1094 | 4.9291 | 4.2556 | 9.2214 | 3.3982 | 48.8381 | 14 | 68383 | 57853 | 1109 | 362 | 11 | 982784 | 3247 | 2 | 0 | 2175 | 2175 | 0 | 0 | Yes | No
RWT15 | Central | URBAN | 2520 | 12.5227 | 1.5496 | 5.7539 | 9.746 | 28.5266 | 17 | 867437 | 514801 | 9831 | 4739 | 33 | 2538984 | 8027 | 11 | 0 | 27466 | 27466 | 0 | 0 | Yes | Yes
RWT17 | Central | URBAN | 0 | 0.3216 | 0.0906 | 7.621 | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | No | No
RWT21 | Central | URBAN | 2490.5 | 10.0765 | 9.948 | 8.0402 | 3.2755 | 0.20302 | 5 | 166844 | 145456 | 6715 | 4238 | 3 | 10341 | 309 | 3 | 0 | 3310 | 3310 | 0 | 0 | No | No
RWT22 | Central | URBAN | 3748.5 | 13.5964 | 0.701 | 6.897 | 8.0046 | 12.605 | 25 | 784370 | 741978 | 15324 | 7821 | 24 | 1235161 | 4491 | 7 | 0 | 20599 | 20599 | 0 | 0 | Yes | Yes
RWT25 | Central | URBAN | 1267.5 | 8.3741 | 0.4241 | 7.3543 | 3.0682 | 17.5495 | 11 | 64502 | 37397 | 2905 | 368 | 8 | 368944 | 2604 | 1 | 0 | 1265 | 1265 | 0 | 0 | Yes | No
RWT26 | Central | URBAN | 1019.5 | 2.2849 | 1.3944 | 7.6591 | 2.5489 | 2.118 | 9 | 182733 | 94073 | 2260 | 1154 | 6 | 151845 | 857 | 1 | 0 | 592 | 592 | 0 | 0 | Yes | No
RWT27 | Central | URBAN | 0 | 0.3905 | 0 | 11.4315 | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | No | No
RWT29 | Central | URBAN | 1 | 0.4374 | 0.2633 | 4.7631 | 3.4759 | 0 | 1 | 86 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | No | No
RWT36 | Central | URBAN | 109 | 0.5809 | 3.1308 | 8.3831 | 4.5191 | 1.2784 | 1 | 10340 | 0 | 220 | 0 | 1 | 2925 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | No | No
SFS1 | Central | SHORT RURAL | 1092 | 20.019 | 0.2946 | 1.4289 | 4.953 | 33.9148 | 18 | 324096 | 241812 | 4385 | 4327 | 37 | 2219180 | 4887 | 1 | 4 | 1095 | 1095 | 1128 | 847 | Yes | No
SLE21 | East | SHORT RURAL | 4412.5 | 59.5041 | 4.4249 | 8.6499 | 0.59844 | 1.604 | 12 | 47695 | 15377 | 572 | 346 | 13 | 127841 | 640 | 4 | 10 | 17669 | 17669 | 1485 | 1485 | No | No
SLE24 | East | URBAN | 1735 | 13.5292 | 1.0731 | 7.8878 | 0.93986 | 3.2484 | 9 | 32257 | 30140 | 170 | 144 | 12 | 111489 | 539 | 4 | 0 | 6927 | 6927 | 0 | 0 | No | No
SLE31 | East | LONG RURAL | 4680 | 459.0244 | 17.5022 | 8.3069 | 2.8346 | 65.8502 | 81 | 275141 | 274760 | 2382 | 2378 | 117 | 6391793 | 17774 | 4 | 53 | 18726 | 18726 | 74572 | 74524 | Yes | No
SLE32 | East | SHORT RURAL | 1273.5 | 165.5279 | 3.146 | 5.2204 | 4.8748 | 14.4739 | 43 | 161745 | 161745 | 1061 | 1061 | 24 | 480243 | 1586 | 2 | 17 | 2574 | 2574 | 7265 | 7265 | No | No
SMG21 | Central | URBAN | 1323 | 4.966 | 12.1727 | 5.2204 | 7.9248 | 0.0009494 | 1 | 367274 | 367274 | 6691 | 6691 | 1 | 44 | 22 | 2 | 0 | 5305 | 5305 | 0 | 0 | Yes | No
SMG22 | Central | URBAN | 1225 | 0 | 13.6776 | 10.0216 | 0.26448 | 3.9791 | 3 | 5141 | 5141 | 46 | 46 | 2 | 77346 | 296 | 0 | 0 | 0 | 0 | 0 | 0 | No | No
SMG23 | Central | URBAN | 503.5 | 2.6272 | 6.0878 | 8.345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 195936 | 471 | 0 | 0 | 0 | 0 | 0 | 0 | Yes | No
SMG31 | Central | URBAN | 1391 | 3.9773 | 14.7532 | 9.4882 | 0.27741 | 1.7874 | 0 | 7157 | 7157 | 20 | 20 | 1 | 46115 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | No | No
SMG32 | Central | URBAN | 135.5 | 1.9035 | 3.6136 | 6.6303 | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | No | No
SMG33 | Central | URBAN | 1349 | 2.1803 | 12.3086 | 6.516 | 2.2232 | 0 | 1 | 111127 | 111127 | 2708 | 2708 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | No | No
SMR1 | North | SHORT RURAL | 474.5 | 73.8991 | 1.1078 | 4.725 | 0.5813 | 1.9924 | 3 | 6038 | 6006 | 45 | 44 | 7 | 20695 | 102 | 1 | 0 | 475 | 475 | 0 | 0 | No | No
SMR2 | North | SHORT RURAL | 2707 | 42.7175 | 1.486 | 8.1545 | 3.6904 | 10.8743 | 12 | 198218 | 195307 | 2885 | 2807 | 16 | 584071 | 1709 | 3 | 0 | 5806 | 5806 | 0 | 0 | No | No
SMR3 | North | LONG RURAL | 1943.5 | 228.4743 | 4.8928 | 6.2111 | 6.8092 | 13.9094 | 43 | 319734 | 305279 | 5865 | 5704 | 75 | 653132 | 1914 | 3 | 14 | 5834 | 5834 | 5707 | 5707 | No | No
SMR4 | North | SHORT RURAL | 855 | 170.2929 | 2.029 | 2.3625 | 2.5703 | 0.73403 | 21 | 204813 | 203224 | 1096 | 1092 | 10 | 58490 | 242 | 3 | 3 | 1910 | 1910 | 163 | 163 | No | No
SMR5 | North | LONG RURAL | 2140 | 466.1999 | 4.7657 | 5.7539 | 9.7061 | 9.3301 | 44 | 526860 | 519142 | 4611 | 4594 | 108 | 506450 | 3305 | 1 | 29 | 2086 | 2086 | 18267 | 17033 | No | No
SMR8 | North | LONG RURAL | 3004.5 | 464.5531 | 13.9955 | 10.4408 | 3.0013 | 35.6665 | 55 | 130896 | 130896 | 1050 | 1050 | 98 | 1555524 | 5069 | 1 | 35 | 3018 | 3018 | 20916 | 20916 | No | No
TGN11 | East | SHORT RURAL | 5031 | 45.8387 | 6.1596 | 6.9732 | 0.78074 | 6.7002 | 26 | 97106 | 93254 | 2033 | 2025 | 33 | 833358 | 2984 | 6 | 0 | 36281 | 36281 | 0 | 0 | No | No
TGN12 | East | SHORT RURAL | 2946 | 29.5062 | 5.4806 | 8.8404 | 1.248 | 10.136 | 5 | 64083 | 64083 | 2341 | 2341 | 16 | 520476 | 1615 | 6 | 0 | 13727 | 11443 | 0 | 0 | No | No
TGN23 | East | SHORT RURAL | 2357 | 169.214 | 5.2585 | 5.6015 | 10.4253 | 15.0156 | 43 | 676544 | 674904 | 13781 | 13745 | 63 | 974431 | 3554 | 14 | 18 | 32902 | 32902 | 4541 | 4149 | Yes | Yes
TGN31 | East | LONG RURAL | 1905 | 337.9025 | 5.8868 | 4.2297 | 11.5066 | 15.3967 | 73 | 693220 | 646184 | 7190 | 6788 | 132 | 927585 | 3668 | 1 | 48 | 19 | 19 | 24186 | 22248 | Yes | No
TGN41 | East | LONG RURAL | 1721.5 | 340.3522 | 1.8775 | 3.6962 | 5.4386 | 19.0814 | 47 | 306848 | 304882 | 3464 | 3446 | 32 | 1076576 | 3217 | 1 | 34 | 1730 | 1730 | 16218 | 15630 | No | No
TGN42 | East | URBAN | 672 | 3.8605 | 2.1696 | 8.0021 | 0.033624 | 0.050875 | 1 | 499 | 499 | 10 | 10 | 2 | 755 | 31 | 2 | 0 | 1334 | 1334 | 0 | 0 | No | No
TGN43 | East | SHORT RURAL | 1887 | 20.4127 | 3.9474 | 6.9351 | 0.051389 | 0.1491 | 0 | 2485 | 2485 | 4 | 4 | 1 | 7210 | 92 | 0 | 0 | 0 | 0 | 0 | 0 | No | No
TRC01 | North | SHORT RURAL | 237 | 114.4108 | 1.2547 | 0.47392 | 0.15997 | 1.5074 | 7 | 10228 | 10228 | 773 | 773 | 11 | 96375 | 290 | 2 | 5 | 240 | 240 | 238 | 238 | No | No
TT1 | Central | URBAN | 199 | 4.8412 | 0.4969 | 8.3069 | 5.1734 | 6.0233 | 1 | 18810 | 18810 | 33 | 33 | 5 | 21900 | 93 | 0 | 0 | 0 | 0 | 0 | 0 | No | No
TT12 | Central | URBAN | 322.5 | 7.4568 | 1.2247 | 7.3543 | 7.453 | 6.3955 | 4 | 58299 | 58299 | 818 | 818 | 5 | 50027 | 219 | 5 | 0 | 1612 | 1289 | 0 | 0 | Yes | No
TT2 | Central | URBAN | 387 | 5.3539 | 1.4953 | 9.3358 | 0.25476 | 0.32394 | 1 | 2158 | 2158 | 28 | 28 | 2 | 2744 | 25 | 1 | 0 | 387 | 387 | 0 | 0 | No | No
TT4 | Central | URBAN | 2414.5 | 9.2184 | 0.6926 | 4.3821 | 0.12855 | 1.1195 | 2 | 12853 | 12853 | 146 | 146 | 2 | 111934 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | No | No
TT5 | Central | URBAN | 1589 | 7.1328 | 3.0341 | 6.6684 | 0.36011 | 3.4113 | 6 | 21802 | 21802 | 126 | 126 | 9 | 206527 | 793 | 0 | 0 | 0 | 0 | 0 | 0 | No | No
TT6 | Central | URBAN | 4355 | 19.8914 | 3.9916 | 9.2214 | 10.0483 | 13.3619 | 4 | 878890 | 878809 | 8371 | 8370 | 20 | 1168722 | 4229 | 7 | 0 | 27103 | 27103 | 0 | 0 | Yes | Yes
TT7 | Central | URBAN | 433.5 | 7.8926 | 1.0475 | 9.8311 | 20.0599 | 0.1675 | 8 | 176642 | 176642 | 537 | 537 | 3 | 1475 | 9 | 1 | 0 | 440 | 440 | 0 | 0 | Yes | No
TT9 | Central | URBAN | 3377.5 | 14.1734 | 0.6118 | 7.6591 | 5.5716 | 18.482 | 11 | 459847 | 458429 | 5377 | 5374 | 12 | 1525392 | 6929 | 2 | 0 | 5777 | 2373 | 0 | 0 | Yes | No
UWY1 | Central | SHORT RURAL | 1066.5 | 19.1522 | 0 | 1.4861 | 20.4301 | 4.974 | 36 | 1707471 | 839629 | 12120 | 9114 | 20 | 415710 | 1352 | 4 | 0 | 4058 | 4058 | 0 | 0 | Yes | No
WGI14 | East | SHORT RURAL | 3317.5 | 148.0795 | 0.7996 | 7.2781 | 4.4244 | 16.1657 | 53 | 534229 | 150404 | 4811 | 1526 | 36 | 1951958 | 7612 | 5 | 27 | 16528 | 13198 | 44704 | 44704 | Yes | Yes
WGI22 | East | LONG RURAL | 798.5 | 211.1637 | 0.3641 | 3.9629 | 12.799 | 20.9684 | 53 | 332942 | 123146 | 4057 | 3491 | 58 | 545451 | 1750 | 2 | 13 | 1040 | 803 | 3150 | 2584 | Yes | No
WGI23 | East | SHORT RURAL | 2254.5 | 124.443 | 2.2052 | 4.1916 | 4.1073 | 4.2747 | 48 | 432732 | 398126 | 9526 | 9463 | 26 | 450371 | 1496 | 1 | 14 | 0 | 0 | 20371 | 12296 | No | No
WGI24 | East | URBAN | 2608.5 | 18.9398 | 2.4574 | 7.8497 | 2.8096 | 12.0593 | 13 | 121510 | 119375 | 4029 | 4015 | 17 | 521539 | 2046 | 1 | 0 | 2280 | 2280 | 0 | 0 | No | No
WGI31 | East | SHORT RURAL | 3468.5 | 65.3458 | 5.5304 | 8.9547 | 13.9051 | 4.2767 | 28 | 1241509 | 898150 | 17745 | 13282 | 16 | 381844 | 2325 | 6 | 14 | 17414 | 13931 | 20681 | 18725 | No | No
WGI33 | East | SHORT RURAL | 2707.5 | 46.1704 | 2.1215 | 5.5252 | 7.2683 | 10.6031 | 22 | 554444 | 504503 | 5534 | 4997 | 12 | 808835 | 1865 | 0 | 11 | 0 | 0 | 12547 | 12547 | No | No
WGI34 | East | SHORT RURAL | 3225 | 49.5125 | 6.6674 | 8.0021 | 5.0499 | 1.7461 | 16 | 481188 | 481188 | 6800 | 6800 | 21 | 166378 | 1361 | 2 | 2 | 6450 | 6450 | 63 | 63 | No | No
WGL11 | East | SHORT RURAL | 3576.5 | 54.3491 | 4.184 | 11.3934 | 19.0917 | 27.0764 | 20 | 860644 | 508148 | 13891 | 12623 | 54 | 1220589 | 5519 | 2 | 9 | 3583 | 3583 | 11131 | 11131 | No | No
WGL12 | East | LONG RURAL | 2463 | 285.5396 | 2.7428 | 7.9259 | 39.6636 | 19.7323 | 92 | 2210849 | 860049 | 16449 | 12600 | 66 | 1099880 | 6446 | 8 | 100 | 10583 | 8690 | 26253 | 22201 | Yes | No
WGL13 | East | SHORT RURAL | 3298.5 | 137.0864 | 7.6847 | 7.7734 | 7.1529 | 11.2784 | 31 | 489159 | 430753 | 10116 | 10049 | 101 | 771291 | 2995 | 2 | 25 | 6550 | 6550 | 11626 | 11130 | No | No
WGL14 | East | URBAN | 1 | 7.4109 | 0.1724 | 4.5726 | 14.8567 | 0 | 1 | 193 | 193 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | No | No
WGL15 | East | SHORT RURAL | 2291 | 111.382 | 4.1105 | 6.516 | 6.3799 | 6.31 | 30 | 344273 | 319958 | 6442 | 6319 | 47 | 340500 | 1365 | 2 | 1 | 4120 | 4120 | 34 | 34 | No | No
WGL21 | East | LONG RURAL | 4486 | 241.8245 | 15.174 | 12.1555 | 5.6249 | 11.1831 | 51 | 329578 | 325524 | 11920 | 11908 | 115 | 655246 | 2627 | 10 | 27 | 41200 | 41200 | 13634 | 12397 | No | No
WGL22 | East | URBAN | 0 | 9.2676 | 0.6238 | 3.8105 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | No | No
WGL23 | East | SHORT RURAL | 1312 | 166.0472 | 0.8072 | 4.1154 | 19.8588 | 7.6866 | 43 | 876972 | 540131 | 6841 | 6137 | 63 | 339444 | 1372 | 4 | 48 | 3682 | 3682 | 29379 | 28729 | Yes | Yes
WGL24 | East | LONG RURAL | 2834.5 | 418.9276 | 3.3531 | 6.6684 | 35.9896 | 8.6212 | 92 | 2034939 | 608089 | 20785 | 14322 | 95 | 487463 | 1771 | 4 | 61 | 11324 | 8483 | 32009 | 27454 | Yes | No
WN1 | North | URBAN | 1551.5 | 11.4728 | 2.781 | 9.6025 | 2.472 | 1.3573 | 5 | 64717 | 63161 | 1733 | 177 | 6 | 35535 | 100 | 3 | 0 | 4656 | 4656 | 0 | 0 | No | No
WN2 | North | LONG RURAL | 3285 | 310.1738 | 5.9787 | 9.7168 | 1.183 | 6.1259 | 27 | 77686 | 74394 | 3454 | 162 | 48 | 402296 | 1392 | 4 | 28 | 13153 | 13153 | 15472 | 15472 | No | No
WN3 | North | LONG RURAL | 2807.5 | 545.6723 | 5.229 | 9.2976 | 23.4312 | 19.5384 | 60 | 573475 | 355499 | 7460 | 4466 | 81 | 478200 | 1818 | 0 | 48 | 0 | 0 | 13657 | 12838 | No | No
WN4 | North | SHORT RURAL | 2559 | 84.8757 | 3.2129 | 5.9063 | 1.4888 | 24.1387 | 21 | 93339 | 90456 | 3203 | 640 | 18 | 1513320 | 4220 | 1 | 6 | 2518 | 2518 | 2683 | 2683 | Yes | No
WN5 | North | LONG RURAL | 2436 | 654.046 | 1.2876 | 9.7549 | 12.7315 | 21.3534 | 88 | 634136 | 509226 | 9027 | 5010 | 82 | 1063576 | 3054 | 0 | 50 | 0 | 0 | 39546 | 34752 | No | No
WN6 | North | LONG RURAL | 4215.5 | 466.1346 | 5.2104 | 9.412 | 3.5987 | 5.7128 | 48 | 282248 | 277923 | 6584 | 2376 | 37 | 448058 | 1542 | 3 | 36 | 12614 | 12614 | 20822 | 20822 | No | No
WN7 | North | URBAN | 103.5 | 2.5713 | 0.8922 | 3.62 | 0.039914 | 0 | 1 | 183 | 80 | 104 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | No | No
WO11 | North | URBAN | 201.5 | 3.3239 | 1.7385 | 4.8775 | 9.4735 | 21.0427 | 2 | 41190 | 117 | 449 | 2 | 5 | 91492 | 263 | 1 | 0 | 204 | 204 | 0 | 0 | Yes | No
WO12 | North | URBAN | 1 | 0 | 0.9178 | 5.0299 | 0.23058 | 0 | 1 | 6 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | No | No
WO13 | North | SHORT RURAL | 229 | 11.8352 | 10.5737 | 3.8105 | 0 | 1.3982 | 0 | 0 | 0 | 0 | 0 | 1 | 9628 | 83 | 2 | 0 | 469 | 469 | 0 | 0 | No | No
WO14 | North | URBAN | 566 | 12.3181 | 2.1362 | 6.8589 | 1.9084 | 7.2471 | 6 | 32495 | 16232 | 688 | 70 | 9 | 123401 | 703 | 2 | 0 | 1129 | 1129 | 0 | 0 | Yes | No
WO22 | North | URBAN | 4017 | 14.3852 | 19.1221 | 10.9362 | 9.63 | 10.0816 | 11 | 703764 | 691584 | 9427 | 5396 | 20 | 736770 | 3004 | 2 | 0 | 8054 | 8054 | 0 | 0 | Yes | No
WO23 | North | URBAN | 605 | 0.9791 | 3.4245 | 5.3728 | 16.0968 | 1.9711 | 4 | 325838 | 324014 | 3044 | 2436 | 1 | 39900 | 114 | 0 | 0 | 0 | 0 | 0 | 0 | Yes | No
WO31 | North | URBAN | 4599 | 8.9735 | 13.4715 | 11.241 | 1.0712 | 3.3776 | 12 | 112363 | 84408 | 6171 | 580 | 24 | 354272 | 1467 | 5 | 1 | 27659 | 22134 | 38 | 38 | No | Yes
WO32 | North | URBAN | 2495.5 | 12.4317 | 2.0513 | 8.2688 | 4.7994 | 14.3811 | 12 | 233637 | 223593 | 8170 | 5659 | 28 | 700079 | 2596 | 2 | 0 | 2539 | 2539 | 0 | 0 | Yes | No
WO33 | North | URBAN | 86.5 | 4.7825 | 2.1893 | 6.0206 | 0.19473 | 8.6597 | 1 | 340 | 0 | 85 | 0 | 1 | 15120 | 56 | 0 | 0 | 0 | 0 | 0 | 0 | No | No
WOTS11 | North | LONG RURAL | 2804.5 | 390.0748 | 10.9644 | 9.3358 | 12.0758 | 18.86 | 41 | 502617 | 476417 | 6345 | 5999 | 63 | 784983 | 3382 | 2 | 27 | 5619 | 5619 | 18828 | 18257 | No | No
WOTS12 | North | URBAN | 2035.5 | 21.49 | 5.035 | 10.0979 | 10.3128 | 3.9363 | 14 | 420903 | 344432 | 2374 | 1639 | 14 | 160655 | 934 | 3 | 2 | 5602 | 4219 | 232 | 232 | Yes | No
WOTS13 | North | LONG RURAL | 2147 | 468.3381 | 1.9805 | 6.7065 | 1.4535 | 7.6161 | 50 | 88648 | 88232 | 3578 | 3576 | 58 | 464493 | 1509 | 2 | 31 | 3743 | 3743 | 9740 | 9740 | No | No
WOTS23 | North | URBAN | 3 | 0 | 0.9663 | 2.7436 | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | No | No
WOTS24 | North | LONG RURAL | 2031 | 692.9639 | 1.3439 | 5.4109 | 7.266 | 13.6812 | 51 | 486867 | 432592 | 5033 | 4933 | 77 | 916725 | 2955 | 2 | 61 | 4613 | 2582 | 20932 | 20785 | No | No
WOTS25 | North | SHORT RURAL | 1325 | 152.8191 | 12.7162 | 4.6107 | 0.87641 | 4.8435 | 6 | 18423 | 18423 | 380 | 380 | 4 | 101816 | 312 | 0 | 10 | 0 | 0 | 1696 | 1696 | No | No
WT10 | Central | URBAN | 926.5 | 2.9653 | 2.2905 | 6.3254 | 2.7612 | 7.2046 | 6 | 73583 | 62302 | 1593 | 1470 | 4 | 191995 | 773 | 2 | 0 | 2796 | 2796 | 0 | 0 | Yes | No
WT11 | Central | URBAN | 2241 | 10.2579 | 0.8014 | 6.0968 | 3.8913 | 20.1942 | 13 | 233381 | 233381 | 3275 | 3275 | 19 | 1211135 | 3643 | 4 | 0 | 10070 | 7835 | 0 | 0 | Yes | No
WT12 | Central | URBAN | 2582 | 14.0725 | 0.6573 | 7.6591 | 2.7081 | 11.0604 | 15 | 159422 | 159422 | 3672 | 3672 | 20 | 651108 | 2866 | 5 | 0 | 12980 | 10391 | 0 | 0 | Yes | Yes
WT13 | Central | URBAN | 3655.5 | 12.9553 | 14.3426 | 16.6138 | 8.0801 | 24.8965 | 10 | 365543 | 365543 | 8672 | 8672 | 37 | 1126312 | 4595 | 5 | 0 | 14870 | 14870 | 0 | 0 | Yes | No
WT15 | Central | URBAN | 1890.5 | 7.6982 | 0.2884 | 4.001 | 0.77164 | 3.5719 | 10 | 88405 | 88405 | 3113 | 3113 | 12 | 409222 | 1602 | 4 | 0 | 7584 | 7584 | 0 | 0 | No | No
WT5 | Central | URBAN | 1389 | 6.0907 | 0.9982 | 5.6396 | 1.8935 | 6.4237 | 5 | 60621 | 59330 | 1956 | 1947 | 5 | 205661 | 630 | 1 | 0 | 1397 | 1397 | 0 | 0 | No | No
WT6 | Central | URBAN | 2863.5 | 13.1113 | 4.2933 | 7.5067 | 0.85844 | 1.5226 | 8 | 71167 | 70336 | 3316 | 3315 | 9 | 126227 | 819 | 3 | 0 | 8612 | 8612 | 0 | 0 | No | No
WT7 | Central | URBAN | 2362.5 | 10.4518 | 0.4914 | 4.9918 | 4.1526 | 2.6344 | 8 | 368918 | 368918 | 6237 | 6237 | 7 | 234040 | 936 | 5 | 0 | 11824 | 11824 | 0 | 0 | No | Yes
WT8 | Central | URBAN | 1854.5 | 8.0211 | 2.647 | 8.7642 | 0.87997 | 0.68614 | 4 | 68415 | 68415 | 3818 | 3818 | 3 | 53345 | 236 | 2 | 0 | 3720 | 3720 | 0 | 0 | No | No
WT9 | Central | URBAN | 2629.5 | 4.0195 | 10.0837 | 7.24 | 0.99888 | 1.407 | 6 | 70842 | 52282 | 3276 | 2867 | 7 | 99789 | 746 | 4 | 0 | 10338 | 8055 | 0 | 0 | No | No
WYK11 | Central | SHORT RURAL | 3669 | 190.0422 | 5.8707 | 9.2595 | 21.299 | 52.8517 | 61 | 1193210 | 903776 | 16114 | 11679 | 147 | 2960856 | 11919 | 1 | 24 | 3663 | 3663 | 21555 | 18992 | Yes | No
WYK12 | Central | SHORT RURAL | 2045.5 | 105.4075 | 1.3537 | 5.5633 | 16.0575 | 10.9289 | 50 | 919285 | 860600 | 5749 | 5205 | 97 | 625674 | 2861 | 1 | 9 | 2036 | 2036 | 3686 | 3162 | Yes | No
WYK23 | Central | SHORT RURAL | 3505.5 | 126.6914 | 2.4695 | 6.1349 | 55.9775 | 83.816 | 95 | 4319469 | 3037190 | 33991 | 26069 | 85 | 6467609 | 16768 | 4 | 31 | 10903 | 10903 | 24262 | 20026 | Yes | No
WYK24 | Central | SHORT RURAL | 3329.5 | 94.1324 | 8.7775 | 8.5737 | 14.1929 | 19.1124 | 65 | 872918 | 656872 | 8687 | 8012 | 101 | 1175487 | 4506 | 2 | 9 | 6687 | 6687 | 857 | 758 | Yes | No
YN31 | East | URBAN | 19 | 5.9444 | 0.2783 | 3.39 | 0 | 0.34237 | 0 | 0 | 0 | 0 | 0 | 4 | 2808 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | No | No
YN35 | East | URBAN | 2 | 0.335 | 0 | 0.42 | 0 | 0.029073 | 0 | 0 | 0 | 0 | 0 | 2 | 312 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | No | No
YN38 | East | SHORT RURAL | 3 | 0.7305 | 0.2796 | 0.21 | 0 | 0.01119 | 0 | 0 | 0 | 0 | 0 | 1 | 1044 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | No | No
Contents
Contents

## 6c. Causes of Outages and Worst
SP AusNet
Cause of Outages and Worst Served 15 per cent customers
2013
Table 1 Causes of Unplanned Sustained Outages
Cause of outage | Number of outages
Weather | 121209
Equipment failure | 405837
Operational error | 41957
Vegetation | 464839
Animals | 225411
Third party impacts | 66682
Transmission failure | 79082
Load shedding | 0
Inter-distributor connection failure | 0
Other | 184482
Table 2 Minutes off Supply for Worst Served 15 per cent customers
Minutes off supply (worst 15%) | 1360.0243
The AER will use the ESCV's definition of minutes of supply for worst served 15% of customers. This is defined as the total annual minutes off supply (SAIDI for planned and unplanned sustained interruptions) experienced by the 15% of customers in the distribution business area connected by those feeders experiencing the longest time off supply.
Contents